{"text_format":"1","workbook":"xlsx","n_sheets":27,"sheets":["AER only","Instructions","Contents","Business & other details","2.1 Expenditure summary","2.2 Repex","2.3(a) Augex","2.3(b) Augex","2.5 Connections","2.6 Non-network","2.7 Vegetation management","2.8 Maintenance","2.9 Emergency Response","2.10 Overheads","2.10(A) Overheads","2.11 Labour","2.12 Input tables","4.1 Public lighting","4.2 Metering","4.3 Fee-based services","4.4 Quoted services","5.2 Asset Age Profile","5.3 MD - Network level","5.4 MD & utilisation-Spatial","6.3 Sustained interruptionss","Amendments","unlocked"],"not_rendered":{"charts":0,"images":7,"macros":1,"external_links":4,"defined_names":835,"comments":2,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"AER only","index":0,"n_rows":130,"n_cols":32,"rows_kept":130,"cut":false,"hidden":true,"merged":[[0,1,0,11],[46,4,46,5],[100,1,102,1],[103,1,107,1],[111,1,112,1]]}
[null,"Data in these columns used for data validation and database purposes."]
[null,"Date last modified:"]
[null,"14 April 2015","merged cell C46/47"]
[null,"17 April 2015","adjusted dms_RYE to automate based on dms_Model (NB: EB & CA refer to CRCP_y5)"]
[null,"14 May 2015","adapted this cover for use in CA & EB RINs"]
[null,"October 2015","added full Trading Name for worksheet headings"]
[null,null,"added new formulas for distinguishing RYE for RFM vs PTRM and Reset (set by ref to CRCP or FRCP) and EB & CA (set by ref to CRY)"]
[]
[]
[]
[null,"dms_TradingName_List","dms_TradingNameFull_List","dms_ABN_List","dms_JurisdictionList","dms_Sector_List","dms_Segment_List","dms_FormControl_List","dms_RPT_List","dms_RPTMonth_List","dms_CRCPlength_List","dms_FRCPlength_List","dms_663_List","dms_DeterminationRef_List",null,null,null,"dms_Addr1_List","dms_Addr2_List","dms_Suburb_List","dms_State_List","dms_PostCode_List","dms_PAddr1_List","dms_PAddr2_List","dms_PSuburb_List","dms_PState_List","dms_PPostCode_List","dms_ContactName1_List","dms_ContactPh1_List","dms_ContactEmail_List"]
[null,"ActewAGL Distribution","ActewAGL Distribution",76670568688,"ACT","Electricity","Distribution","Revenue cap","Calendar","December",5,5,5,"2014-19 Distribution Determination",null,null,null,"40 Bunda Street",null,"CANBERRA","ACT","2601","GPO BOX 366",null,"CANBERRA","ACT",2601,"Robert Walker","02 6248 3847","robert.walker@actewagle.com.au"]
[null,"ActewAGL Distribution (Tx Assets)","ActewAGL Distribution (Tx Assets)",76670568688,"ACT","Electricity","Distribution","Revenue cap","Calendar","December",5,5,5,"distribution determination",null,null,null,null,null,null,"ACT"]
[null,"AGN","AGN",78551685,"SA","Gas","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination",null,null,null,null,null,null,"SA"]
[null,"Ausgrid","Ausgrid",67505337385,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination",null,null,null,"570 George St",null,"SYDNEY","NSW",2000,null,null,null,null,null,"John Thomson","(02) 9269 2312","john.thomson@ausgrid.com.au"]
[null,"Ausgrid (Tx Assets)","Ausgrid (Tx Assets)",67505337385,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination",null,null,null,null,null,null,"NSW"]
[null,"AusNet (D)","AusNet Services (D)",91064651118,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination",null,null,null,"Level 32","2 Southbank Boulevard","SOUTHBANK","Vic","3006","Locked Bag 14051",null,"MELBOURNE CITY MAIL CENTRE","VIC",null,"Tom Hallam","03 9695 6617","Thomas.hallam@SP-Ausnet.com.au"]
[null,"AusNet (T)","AusNet (T)",48116124362,"Vic","Electricity","Transmission","Revenue cap","Financial","March",5,5,2,"transmission determination",null,null,null,"Level 32","2 Southbank Boulevard","SOUTHBANK","Vic","3006",null,null,null,null,null,"Tom Hallam","03 9695 6617","Thomas.hallam@SP-Ausnet.com.au"]
[null,"Australian Distribution Co.","Australian Distribution Co.",11222333444,"-","Electricity","Distribution","Revenue cap","Financial","June",5,5,2,"distribution determination",null,null,null,null,null,null,"-"]
[null,"Australian Transmission Co.","Australian Transmission Co.",11222333444,"-","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination",null,null,null,null,null,null,"-"]
[null,"CitiPower","CitiPower",76064651056,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination",null,null,null,"40 Market Street",null,"MELBOURNE","Vic","3000","Locked Bag 14090",null,"MELBOURNE","VIC",null,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au"]
[null,"Directlink","Directlink",16779340889,"Qld","Electricity","Transmission","Revenue cap","Financial","June",10,5,5,"transmission determination",null,null,null,null,null,null,"NSW"]
[null,"ElectraNet","ElectraNet",41094482416,"SA","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination",null,null,null,"52-55 East Terrace","Rymill Park","ADELAIDE","SA","5000","PO Box 7096","Hutt Street Post Office","ADELAIDE","SA",null,"Bill Jackson","08 8404 7969","jackson.bill@electranet.com.au"]
[null,"Endeavour Energy","Endeavour Energy",59253130878,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination",null,null,null,"51 Huntingwood Drive",null,"HUNTINGWOOD","NSW","2148","PO Box 811",null,"SEVEN HILLS","NSW",null,"Jon Hocking","02 9853 4386 / 0407 348 156","Jon.Hocking@Endeavourenergy.com.au"]
[null,"Energex","Energex",40078849055,"Qld","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination",null,null,null,"26 Reddacliff Street",null,"NEWSTEAD","Qld","4006","26 Reddacliff Street",null,"NEWSTEAD","QLD","4006","Nicola Roscoe","07 3664 5891","nicolaroscoe@energex.com.au"]
[null,"Ergon Energy","Ergon Energy",50087646062,"Qld","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination",null,null,null,"22 Walker Street",null,"TOWNSVILLE","Qld","4810",null,null,null,null,null,"Jenny Doyle, Group Manager Regulatory Affairs","(07) 3851 6416","jenny.doyle@ergon.com.au"]
[null,"Essential Energy","Essential Energy",37428185226,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination",null,null,null,"8 Buller Street",null,"PORT MACQUARIE","NSW","2444","PO Box 5730",null,"Port MacQuarie","NSW",null,"Catherine Waddell","02 6338 3553","Catherine.waddell@essentialenergy.com.au"]
[null,"Jemena Electricity","Jemena Electricity",82064651083,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination",null,null,null,"321 Ferntree Gully Road",null,"MT WAVERLEY","Vic","3149","321 Ferntree Gully Road",null,"MT WAVERLEY","VIC","3149","Anton Murashev","03 8544 9036","anton.murashev@jemena.com.au"]
[null,"Murraylink","Murraylink",79181207909,"SA","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination",null,null,null,null,null,null,"NSW"]
[null,"Powercor Australia","Powercor Australia",89064651109,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination",null,null,null,"40 Market Street",null,"MELBOURNE","Vic","3000","Locked bag 14090",null,"MELBOURNE","VIC",3001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au"]
[null,"Powerlink","Queensland Electricity Transmission Corporation Limited trading as Powerlink Queensland",82078849233,"Qld","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination",null,null,null,"33 Harold St",null,"VIRGINIA","Qld","4014","PO Box 1193",null,"VIRGINIA","QLD",4014,"Jennifer Harris","07 3860 2667","jharris@powerlink.com.au"]
[null,"Qld,SA &ACT Gas Reset","Qld,SA &ACT Gas Reset",22222222222,"-","Gas","Distribution","?",null,null,5,5,"x","n/a",null,null,null,null,null,null,"-"]
[null,"Roma to Brisbane Pipeline","APT Petroleum Pipelines Limited t/a Roma to Brisbane Pipeline","009 737 393","Qld","Gas","Distribution","?","Financial","June",5,5,"x","n/a"]
[null,"SA Power Networks","SA Power Networks",13332330749,"SA","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination",null,null,null,"1 Anzac Highway",null,"KESWICK","SA","5035","GPO Box 77",null,"ADELAIDE","SA",null,"Damien O'Connor","08 8404 5066","damien.oconnor@sapowernetworks.com.au"]
[null,"TasNetworks (D)","TasNetworks (D)",24167357299,"Tas","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination",null,null,null,"21 Kirksway Place",null,"HOBART","Tas","7000","GPO Box 191",null,"HOBART","Tas",null,"Leigh Mayne","03 6270 3691","rrp2012@auroraenergy.com.au"]
[null,"TasNetworks (T)","TasNetworks (T)",24167357299,"Tas","Electricity","Transmission","Revenue cap","Financial","March",5,5,5,"transmission determination",null,null,null,"1-7 Maria Street",null,"LENAH VALLEY","Tas","7008","PO Box 606",null,"MOONAH","Tas",null,"Heath Dillon","03 6274 3664","heath.dillon@transend.com.au"]
[null,"TransGrid","TransGrid",19622755774,"NSW","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination",null,null,null,"180 Thomas Street",null,"HAYMARKET","NSW","2000","PO Box A1000",null,"SYDNEY SOUTH","NSW",null,"Andrew Kingsmill","02 9284 3149","andrew.kingsmill@transgrid.com.au"]
[null,"United Energy","United Energy",70064651029,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination",null,null,null,"6 Nexus Court",null,"MULGRAVE","Vic","3170","PO Box 449",null,"MOUNT WAVERLEY","VIC",null,"Mathew Abraham","03 8846 9758","mathew.abraham@ue.com.au"]
[null,"Victorian DNSP Backcasting","Victorian DNSP Backcasting",33333333666,"Vic","Electricity","Distribution","?","Calendar",null,5,5,"x","distribution determination",null,null,null,null,null,null,"Vic"]
[null,"Victorian DNSP Reset ","Victorian DNSP Reset ",33333333333,"Vic","Electricity","Distribution","?","Calendar",null,5,5,"x","distribution determination",null,null,null,null,null,null,"Vic"]
[null,"Western Power (D)","Western Power (D)",18540492861,"WA","Electricity","Distribution","Revenue cap","Financial","June",5,4,"x","distribution determination",null,null,null,null,null,null,"WA",null,null,null,null,null,null,"Judy Hunter","08 9326 6239"]
[null,"Western Power (T)","Western Power (T)",18540492861,"WA","Electricity","Transmission","Revenue cap","Financial","June",5,4,"x","transmission determination",null,null,null,null,null,null,"WA",null,null,null,null,null,null,"Judy Hunter","08 9326 6239"]
[]
[]
[]
[]
[null,"dms_Model_List ","DELETE NR 'CRY' IF NOT AN ANNUAL RIN (EB, CA , ARR)",null,"dms_RYE_Formula_Result",null,null,null,null,null,null,null,null,"dms_0203_ProjectType",null,null,null,"dms_020303_01_UOM","dms_020501_01_UOM","dms_020501_02_UOM","dms_020501_03_UOM","dms_020501_04_UOM","dms_020603_01_UOM","dms_040102_01_UOM","dms_040102_04_UOM"]
[null,"ARR","ANNUAL REPORTING STATEMENT",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2017"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"New line on new route - single circuit",null,null,null,"Circuit line length in km","0's","0's","0's","0's","0's","0's","days"]
[null,"CA","CATEGORY ANALYSIS",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2017"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"New line on new route - dual circuit",null,null,null,"Circuit line length in km","0's","0's","0's","0's","0's","0's","0's"]
[null,"CPI","CPI",null,null,null,null,null,null,null,null,null,null,"New line on new route - other",null,null,null,"Circuit line length in km","MVA added","MVA added","MVA added","MVA added","0's","0's","$0s"]
[null,"EB","ECONOMIC BENCHMARKING",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2017"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"Line rebuild over existing route - single circuit",null,null,null,"Circuit line length in km","0's","0's","0's","0's","0's","$0s","0's"]
[null,"PTRM","POST TAX REVENUE MODEL",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2019"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,null,null,null,null,null,null,"Line rebuild over existing route - dual circuit",null,null,null,"Number","total spend $0s","total spend $0s","total spend $0s","total spend $0s","(per cent)"]
[null,"Reset","REGULATORY REPORTING STATEMENT",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2019"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"Reconductor - Single circuit",null,null,null,"Number","net circuit km added","net circuit km added","net circuit km added","net circuit km added"]
[null,"RFM","ROLL FORWARD MODEL",null,{"$f":"LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)","v":"2017"},"=LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)",null,null,null,null,null,null,null,"Reconductor - Dual circuit",null,null,null,"Number","total spend $0s","total spend $0s","total spend $0s","total spend $0s"]
[null,"WACC","WEIGHTED AVERAGE COST OF CAPITAL",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2019"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,null,null,null,null,null,null,"Other",null,null,null,null,"net circuit km added","net circuit km added","net circuit km added","net circuit km added"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"total spend $0s","total spend $0s","total spend $0s","total spend $0s"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,"$0s"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0's"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0's"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"$0s"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[]
[]
[]
[null,"dms_SourceList","dms_FormControl_Choices",null,"dms_FRCPlength_Num_List","dms_FinalYear_List","dms_CRCPlength_Num_List","dms_CFinalYear_List","dms_RCP_fyear_list","dms_CRY_ListF","dms_CRY_ListC","dms_RCP_cyear_list"]
[null,"After appeal","Revenue cap",null,1,"FRCP_y1",1,"CRCP_y1","dms_fy1","2005-06",2006,"dms_cy1"]
[null,"Draft decision","Revenue yield",null,2,"FRCP_y2",2,"CRCP_y2","dms_fy2","2006-07",2007,"dms_cy2"]
[null,"Final decision","Weighted average price cap",null,3,"FRCP_y3",3,"CRCP_y3","dms_fy3","2007-08","2008","dms_cy3"]
[null,"Pass through decision",null,null,4,"FRCP_y4",4,"CRCP_y4","dms_fy4","2008-09","2009","dms_cy4"]
[null,"PTRM annual update",null,null,5,"FRCP_y5",5,"CRCP_y5","dms_fy5","2009-10","2010","dms_cy5"]
[null,"PTRM interim update 1",null,null,6,"FRCP_y6",6,"CRCP_y6","dms_fy6","2010-11","2011","dms_cy6"]
[null,"PTRM interim update 2",null,null,7,"FRCP_y7",7,"CRCP_y7","dms_fy7","2011-12","2012","dms_cy7"]
[null,"PTRM interim update 3",null,null,8,"FRCP_y8",8,"CRCP_y8","dms_fy8","2012-13","2013","dms_cy8"]
[null,"PTRM interim update 4",null,null,9,"FRCP_y9",9,"CRCP_y9","dms_fy9","2013-14","2014","dms_cy9"]
[null,"Regulatory proposal",null,null,10,"FRCP_y10",10,"CRCP_y10","dms_fy10","2014-15","2015","dms_cy10"]
[null,"Reporting",null,null,null,null,null,null,"dms_fy11","2015-16","2016","dms_cy11"]
[null,"Revised regulatory proposal",null,null,null,null,null,null,"dms_fy12","2016-17","2017","dms_cy12"]
[null,"RFM annual update",null,"dms_FRCP_years",null,"dms_CRCP_years",null,"dms_CRCP_index","dms_fy13","2017-18","2018","dms_cy13"]
[null,"WACC annual update",null,{"$f":"FRCP_y1","v":"2015-16"},"dms_FRCP_y1",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y1,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y1,2)-1),\"0#\"),VALUE(LEFT(dms_FRCP_y1,4)-1))","v":2014},"dms_CRCP_yZ",1,"dms_fy14","2018-19",2019,"dms_cy14"]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y1,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y1,3,2)+2),VALUE(LEFT(dms_FRCP_y1,4)+1))","v":2016},"dms_FRCP_y2",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yZ,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yZ,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yZ,4)-1))","v":2013},"dms_CRCP_yY",2,"dms_fy15","2019-20","2020","dms_cy15"]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y2,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y2,3,2)+2),VALUE(LEFT(dms_FRCP_y2,4)+1))","v":2017},"dms_FRCP_y3",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yY,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yY,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yY,4)-1))","v":2012},"dms_CRCP_yX",3]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y3,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y3,3,2)+2),VALUE(LEFT(dms_FRCP_y3,4)+1))","v":2018},"dms_FRCP_y4",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yX,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yX,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yX,4)-1))","v":2011},"dms_CRCP_yW",4]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y4,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y4,3,2)+2),VALUE(LEFT(dms_FRCP_y4,4)+1))","v":2019},"dms_FRCP_y5",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yW,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yW,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yW,4)-1))","v":2010},"dms_CRCP_yV",5]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y5,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y5,3,2)+2),VALUE(LEFT(dms_FRCP_y5,4)+1))","v":2020},"dms_FRCP_y6",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yV,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yV,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yV,4)-1))","v":2009},"dms_CRCP_yU",6]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y6,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y6,3,2)+2),VALUE(LEFT(dms_FRCP_y6,4)+1))","v":2021},"dms_FRCP_y7",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yU,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yU,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yU,4)-1))","v":2008},"dms_CRCP_yT",7]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y7,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y7,3,2)+2),VALUE(LEFT(dms_FRCP_y7,4)+1))","v":2022},"dms_FRCP_y8",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yT,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yT,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yT,4)-1))","v":2007},"dms_CRCP_yS",8]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y8,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y8,3,2)+2),VALUE(LEFT(dms_FRCP_y8,4)+1))","v":2023},"dms_FRCP_y9",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yS,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yS,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yS,4)-1))","v":2006},"dms_CRCP_yR",9]
[null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y9,4)+1)&\"-\"&VALUE(MID(dms_FRCP_y9,3,2)+2),VALUE(LEFT(dms_FRCP_y9,4)+1))","v":2024},"dms_FRCP_y10",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yR,4)-1)&\"-\"&TEXT(VALUE(RIGHT(dms_CRCP_yR,2)-1),\"0#\"),VALUE(LEFT(dms_CRCP_yR,4)-1))","v":2005},"dms_CRCP_yQ",10]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Reason for interruption","Detailed reason for interruption","dms_Reason_Interruption"]
[null,"Animal","Animal impact","Animal"]
[null,null,"Animal nesting/burrowing, etc and other","Asset failure"]
[null,null,"Other","Other"]
[null,"Asset failure","LV","Overloads"]
[null,null,"Distribution substation","Planned"]
[null,null,"HV","Network business"]
[null,null,"Zone substation","Third party"]
[null,null,"Subtransmission","Unknown"]
[null,"Other","insert description of 'other'","Vegetation"]
[null,"Overloads","-","Weather"]
[null,"Planned","-","2 - STPIS Exclusion (3.3)(a)"]
[null,"Network business","Network error","3 - STPIS Exclusion (3.3)(a)"]
[null,null,"Switching and protection error","4 - STPIS Exclusion (3.3)(a)"]
[null,"Third party","Fire","5 - STPIS Exclusion (3.3)(a)"]
[null,null,"Other","6 - STPIS Exclusion (3.3)(a)"]
[null,null,"Dig-in","7 - STPIS Exclusion (3.3)(a)"]
[null,null,"Unauthorised access"]
[null,null,"Vehicle impact"]
[null,"Unknown","Unknown"]
[null,"Vegetation","Blow-in/Fall-in - NSP responsibility"]
[null,null,"Grow-in - NSP responsibility"]
[null,null,"Blow-in/Fall-in - Other responsible party"]
[null,null,"Grow-in - Other responsible party"]
[null,"Weather","-"]
[null,"2 - STPIS Exclusion (3.3)(a)","-"]
[null,"3 - STPIS Exclusion (3.3)(a)","-"]
[null,"4 - STPIS Exclusion (3.3)(a)","-"]
[null,"5 - STPIS Exclusion (3.3)(a)","-"]
[null,"6 - STPIS Exclusion (3.3)(a)","-"]
[null,"7 - STPIS Exclusion (3.3)(a)","-"]

{"sheet":"Instructions","index":1,"n_rows":27,"n_cols":4,"rows_kept":27,"cut":false,"hidden":true,"merged":[[7,2,7,3],[1,1,1,5],[2,1,2,5],[3,2,3,4],[4,2,4,4],[5,2,5,4],[24,2,24,4],[25,2,25,3],[26,2,26,4],[8,2,8,4],[10,2,10,4],[12,2,12,4],[20,2,20,4],[22,2,22,4]]}
[]
[null,{"$f":"CONCATENATE(dms_Segment,\" Network Service Provider\")","v":"Distribution Network Service Provider"}]
[null,"Annual Reporting RIN Template"]
[null,null,{"$f":"CONCATENATE(\"This template is to be used by \",dms_TradingName,\" to fulfil its reporting obligations to the AER.\")","v":"This template is to be used by AusNet (D) to fulfil its reporting obligations to the AER."}]
[null,null,"INSTRUCTIONS"]
[null,null,"Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting."]
[]
[null,null,"Identifying CONFIDENTIAL INFORMATION:\n\nPlease use the macro at the top of each \nworksheet to identify confidential information. \n\n"]
[null,null,"-Do this by selecting the cell or cells that contain confidential information and then run the Mark selected cells as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential.\n\n-To reverse this, select the cell or cells and run the Return cells to NON-CONFIDENTIAL macro"]
[]
[null,null,"UNITS OF MEASURE\n\nAll amounts are to be unrounded and reported in nominal terms on a one for one basis: that is 1000 is to be entered as '1000'.\n\n"]
[]
[null,null,"COLOUR CODING OF INPUT / NON-INPUT CELLS:"]
[null,null,null,"Yellow = Input cell (mandatory)"]
[null,null,null,"Darker yellow = input cell (mandatory)"]
[null,null,null,"Orange = input cell (if data available)"]
[null,null,null,"Grey = Not applicable/No inputs required"]
[null,null,null,"Leave coloured cells blank if no information exists. \nPLEASE DO NOT ENTER TEXT into cells that are to contain numeric data."]
[]
[]
[null,null,"WORKSHEET NAVIGATION\n\nMany tables in the worksheets have been \"grouped\" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin of excel (for Row groupings) or above the columns (for column groupings). \n\n\n\n"]
[]
[null,null,"RETURNING COMPLETED RESPONSES\n\nPlease return four (4) files to the AER: \n1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. \n\n2. An actual and an estimate version with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER.\n\n3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response.\n\n\nUse the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public. "]
[]
[null,null,"SUBMITTING AMENDED DATA TO THE AER\n\nIf an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. \n\nNSPs must identify the reason for the amendments in the Amendment Reason box on the  Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. \n\n."]
[null,null,"NSP may use Amended Data macro to highlight cells\nthat contain amended data."]
[null,null,"Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER"]

{"sheet":"Contents","index":2,"n_rows":27,"n_cols":19,"rows_kept":27,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"AusNet Services (D)"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017"}]
[null,"CONTENTS"]
[]
[]
[null,null,null,null,"1. Business details",null,null,null,null,null,null,"2. Expenditure"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,"4. Alternative control services",null,null,null,null,null,null,"5. Network information",null,null,null,null,null,null,"6. Service & quality"]

{"sheet":"Business & other details","index":3,"n_rows":88,"n_cols":27,"rows_kept":88,"cut":false,"hidden":false,"merged":[[23,4,23,7],[7,1,7,8],[11,1,11,8],[13,2,13,4],[14,2,14,4],[17,2,17,3],[17,4,17,7],[18,4,18,7],[19,2,19,3],[19,4,19,7],[22,2,22,3],[22,4,22,7],[54,0,87,0],[82,4,82,8],[24,2,24,3],[24,4,24,7],[32,1,32,8],[49,2,49,3],[51,2,51,8]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"AusNet Services (D)"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017"}]
[null,"BUSINESS & OTHER DETAILS"]
[]
[]
[null,"Instructions"]
[null,"Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings."]
[]
[null,"SUBMISSION PARTICULARS INPUT SHEETS"]
[]
[null,"ENTITY DETAILS"]
[]
[null,"Short name","AusNet (D)"]
[null,"ACN / ABN",{"$f":"INDEX(dms_ABN_List,MATCH(dms_TradingName,dms_TradingName_List))","v":91064651118}]
[]
[]
[null,"Business address","Address 1",null,{"$f":"INDEX(dms_Addr1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Level 32"}]
[null,null,null,"Address 2",{"$f":"IF(ISBLANK(INDEX(dms_Addr2_List,MATCH(dms_TradingName,dms_TradingName_List))),\"\",INDEX(dms_Addr2_List,MATCH(dms_TradingName,dms_TradingName_List)))","v":"2 Southbank Boulevard"}]
[null,null,"Suburb",null,{"$f":"INDEX(dms_Suburb_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SOUTHBANK"}]
[null,null,null,"State",{"$f":"INDEX(dms_State_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Vic"},"p/code",{"$f":"INDEX(dms_PostCode_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"3006"}]
[]
[null,"Postal address","Address 1",null,{"$f":"INDEX(dms_PAddr1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Locked Bag 14051"}]
[null,null,null,"Address 2",{"$f":"IF(ISBLANK(INDEX(dms_PAddr2_List,MATCH(dms_TradingName,dms_TradingName_List))),\"\",INDEX(dms_PAddr2_List,MATCH(dms_TradingName,dms_TradingName_List)))","v":""}]
[null,null,"Suburb",null,{"$f":"INDEX(dms_PSuburb_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"MELBOURNE CITY MAIL CENTRE"}]
[null,null,null,"State",{"$f":"INDEX(dms_PState_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"VIC"},"p/code",{"$f":"INDEX(dms_PPostCode_List,MATCH(dms_TradingName,dms_TradingName_List))","v":0}]
[]
[]
[null,"Contact name/s","Clare Thompson"]
[null,"Contact phone/s",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Tom Hallam"]
[null,"Contact email address/s","Clare.E.Thompson@ausnetservices.com.au",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Tom Hallam"]
[]
[null,"REGULATORY CONTROL PERIODS"]
[]
[null,"Forthcoming regulatory control period","2015-16",{"$f":"dms_FRCP_y2","v":2016},{"$f":"dms_FRCP_y3","v":2017},{"$f":"dms_FRCP_y4","v":2018},{"$f":"dms_FRCP_y5","v":2019},{"$f":"dms_FRCP_y6","v":2020},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(FRCP_y6,4)+1)&\"-\"&VALUE(MID(FRCP_y6,3,2)+2),VALUE(LEFT(FRCP_y6,4)+1))","v":2021}]
[]
[]
[null,"Current regulatory control period",{"$f":"dms_CRCP_FirstYear_Result","v":2010},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y1,2)+1),\"0#\"),VALUE(LEFT(CRCP_y1,4)+1))","v":2011},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y2,4)+1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y2,2)+1),\"0#\"),VALUE(LEFT(CRCP_y2,4)+1))","v":2012},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y3,4)+1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y3,2)+1),\"0#\"),VALUE(LEFT(CRCP_y3,4)+1))","v":2013},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y4,4)+1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y4,2)+1),\"0#\"),VALUE(LEFT(CRCP_y4,4)+1))","v":2014},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y5,4)+1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y5,2)+1),\"0#\"),VALUE(LEFT(CRCP_y5,4)+1))","v":2015}]
[]
[]
[null,"Previous regulatory control period",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y2,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y2,3,2)),\"0#\"),VALUE(LEFT(PRCP_y2,4)-1))","v":2005},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y3,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y3,3,2)),\"0#\"),VALUE(LEFT(PRCP_y3,4)-1))","v":2006},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y4,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y4,3,2)),\"0#\"),VALUE(LEFT(PRCP_y4,4)-1))","v":2007},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y5,4)-1)&\"-\"&TEXT(VALUE(RIGHT(PRCP_y5,2)-1),\"0#\"),VALUE(LEFT(PRCP_y5,4)-1))","v":2008},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)-1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y1,2)-1),\"0#\"),VALUE(LEFT(CRCP_y1,4)-1))","v":2009}]
[]
[]
[null,"Current regulatory year","2017","CRY"]
[]
[]
[null,null,"DELETE NR 'CRY' IF NOT AN ANNUAL RIN (EB, CA , ARR)"]
[null,null,"APPLY NR 'CRY' IF AN ANNUAL RIN (EB, CA , ARR)"]
[]
[null,"Source","Reporting",null,"Please select the correct submission type from the dropdown list."]
[null,"Data quality (actual, estimate, public, consolidated)","Consolidated"]
[null,"Amended RIN submission - amendment reason","Correction to Public lighting opex"]
[null,"Submission Date","dd/mm/yyyy","dms_SubmissionDate","Please enter date this file submitted to AER (dd/mm/yyyy)"]
[null,"EBSS - First application of scheme in forthcoming period?","No"]
["HIDE THESE ROWS","Sector",{"$f":"INDEX(dms_Sector_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Electricity"},"dms_Sector","=INDEX(dms_Sector_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Segment",{"$f":"INDEX(dms_Segment_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Distribution"},"dms_Segment","=INDEX(dms_Segment_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Regulatory Year Ending",{"$f":"IF(dms_MultiYear_Flag=1,LEFT(dms_Specified_FinalYear,2)&RIGHT(dms_Specified_FinalYear,2),INDEX(dms_RYE_Formula_Result,MATCH(dms_Model,dms_Model_List)))","v":"2017"},"dms_RYE","=IF(dms_MultiYear_Flag=1,LEFT(dms_Specified_FinalYear,2)&RIGHT(dms_Specified_FinalYear,2),INDEX(dms_RYE_Formula_Result,MATCH(dms_Model,dms_Model_List)))"]
[null,"Reporting Period Type",{"$f":"INDEX(dms_RPT_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Calendar"},"dms_RPT","=INDEX(dms_RPT_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Model or RIN Type","CA","dms_Model","Drop down selection"]
[null,"Security Classification","Public","dms_Classification","Always Public"]
[null,"Template - version no.",5,"dms_TemplateNumber"]
[null,"Dollar $ real month",{"$f":"INDEX(dms_RPTMonth_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"December"},"dms_RPTMonth","=INDEX(dms_RPTMonth_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Dollar $ real  (the last month before the FRCP_y1)",{"$f":"IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(CRY,2))&RIGHT(CRY,2)),CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(dms_CRCP_FinalYear_Result,2))&RIGHT(dms_CRCP_FinalYear_Result,2)))","v":"December 2017"},"dms_DollarReal","=IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(CRY,2))&RIGHT(CRY,2)),CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(dms_CRCP_FinalYear_Result,2))&RIGHT(dms_CRCP_FinalYear_Result,2)))"]
[null,"Form of control",{"$f":"INDEX(dms_FormControl_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Revenue cap"},"dms_FormControl","=INDEX(dms_FormControl_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"RIN response - version no.",1,"dms_RINversion"]
[null,"Jurisdiction",{"$f":"INDEX(dms_JurisdictionList,MATCH(dms_TradingName,dms_TradingName_List))","v":"Vic"},"dms_Jurisdiction","=INDEX(dms_JurisdictionList,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Backcast Multiyear EB, CA or ARR?",0,"dms_MultiYear_Flag","1=y, 0-n"]
[null,null,2013,"dms_Specified_FinalYear","The result here is returned to dms_CRCP_FinalYear_Result if dms_MultiYear_Flag is set to 1"]
[null,"Single Year Model T/F",{"$f":"IF(dms_Model=\"EB\",1,0)","v":0},"dms_EB"]
[null,null,{"$f":"IF(dms_Model=\"CA\",1,0)","v":1},"dms_CA","=dms_SingleYear_Model"]
[null,null,{"$f":"IF(dms_Model=\"ARR\",1,0)","v":0},"dms_ARR"]
[null,"Single Year Final Year Reference","CRY","dms_SingleYear_FinalYear_Ref","This is the reference for EB, CA & ARR RINs"]
[null,"Single Year Final Year Result",{"$f":"INDIRECT(dms_SingleYear_FinalYear_Ref)","v":"2017"},"dms_SingleYear_FinalYear_Result","=INDIRECT(dms_SingleYear_FinalYear_Ref)",null,null,null,"Formula errors OK"]
[null,"FRCP length in years",{"$f":"INDEX(dms_FRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_FRCPlength_Num","=INDEX(dms_FRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Multi Year Final Year Reference",{"$f":"INDEX(dms_FinalYear_List,MATCH(dms_FRCPlength_Num,dms_FRCPlength_Num_List))","v":"FRCP_y5"},"dms_MultiYear_FinalYear_Ref","=INDEX(dms_FinalYear_List,MATCH(dms_FRCPlength_Num,dms_FRCPlength_Num_List))"]
[null,"Multi Year Final Year Result",{"$f":"IF(dms_MultiYear_Flag=0,INDIRECT(dms_MultiYear_FinalYear_Ref),dms_Specified_FinalYear)","v":2019},"dms_MultiYear_FinalYear_Result","=IF(dms_MultiYear_Flag=0,INDIRECT(dms_MultiYear_FinalYear_Ref),dms_Specified_FinalYear)",null,null,null,"Formula errors OK"]
[null,"CRCP length in years",{"$f":"INDEX(dms_CRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_CRCPlength_Num","=INDEX(dms_CRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"CRCP Final Year Reference",{"$f":"INDEX(dms_CFinalYear_List,MATCH(dms_CRCPlength_Num,dms_CRCPlength_Num_List))","v":"CRCP_y5"},"dms_CRCP_FinalYear_Ref","=INDEX(dms_CFinalYear_List,MATCH(dms_CRCPlength_Num,dms_CRCPlength_Num_List))"]
[null,"CRCP First Year Result",{"$f":"INDEX(dms_CRCP_years,MATCH(dms_CRCPlength_Num,dms_CRCP_index))","v":2010},"dms_CRCP_FirstYear_Result","=INDEX(dms_CRCP_years,MATCH(dms_CRCPlength_Num,dms_CRCP_index))"]
[null,"CRCP Final Year Result",{"$f":"IF(dms_MultiYear_Flag=0,(IF(SUM(dms_SingleYear_Model)>0,CRY,dms_CRCP_yZ)),dms_Specified_FinalYear)","v":"2017"},"dms_CRCP_FinalYear_Result","=IF(dms_MultiYear_Flag=0,(IF(SUM(dms_SingleYear_Model)>0,CRY,dms_CRCP_yZ)),dms_Specified_FinalYear)"]
[null,"Table 6.6.3 - Public lighting repair - no. business days",{"$f":"INDEX(dms_663_List,MATCH(dms_TradingName,dms_TradingName_List))","v":2},"dms_663"]
[null,"Distribution Determination Reference",{"$f":"INDEX(dms_DeterminationRef_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"2016-20 Distribution Determination"}]
[null,"Backcast templates only - unit of measure ","$0s","dms_Backcast_UOM","If the cover sheet is for Backcast data ensure to apply dms_Backcast_UOM named range to this field. Otherwise, do not apply this named range."]
[null,"EB/CA Unit of Measure for Monetary Values","$0s","dms_dollar_nom_UOM","If the cover sheet is attached to an EB files make sure this field is set"]
[]
[null,"discard this record?","NO","dms_DISCARD","If record is to be discarded from DB set this flag to YES"]
[]
[null,"USES NAMED RANGES FLAG","yes","dms_Defined_Names_Used"]

{"sheet":"2.1 Expenditure summary","index":4,"n_rows":126,"n_cols":3,"rows_kept":126,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.1 EXPENDITURE SUMMARY & RECONCILIATION"]
[]
[null,"There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.1.1 - STANDARD CONTROL SERVICES CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,"2017"]
[null,"Replacement expenditure",125850770.13723694]
[null,"Connections",64124286.331822619]
[null,"Augmentation Expenditure",77718815.321802899]
[null,"Non-network",40855125.569999978]
[null,"capitalised network overheads",29267094.922092617]
[null,"capitalised corporate overheads",5910615.2066409076]
[null,"Metering",0]
[null,"Public Lighting",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",0]
[null,"capcons (included in the above)",-24783646.709999997]
[null,"TOTAL GROSS CAPEX \n(including capcons)",318943060.77959597]
[]
[null,"2.1.2 - STANDARD CONTROL SERVICES OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,"2017"]
[null,"Vegetation management",37601388.829999991]
[null,"Maintenance",21655584.191300504]
[null,"Emergency response",16516475.275187489]
[null,"Non-network",35355243.42122893]
[null,"network overheads",70781271.114998654]
[null,"corporate overheads",27744532.76307033]
[null,"Metering",7074357.0495559936]
[null,"Public Lighting",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",0]
[null,"TOTAL OPEX",216728852.6453419]
[]
[null,"2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,"2017"]
[null,"Connections",3657181.2639999981]
[null,"capitalised network overheads",977782.62809922767]
[null,"capitalised corporate overheads",1138329.2199999997]
[null,"Metering",10426901.530000003]
[null,"Public lighting",7298181.3283880036]
[null,"Fee and quoted",3657181.2639999981]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-4963761.6139999982]
[null,"TOTAL CAPEX",22191795.620487228]
[]
[null,"2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,"2017"]
[null,"Connections",0]
[null,"network overheads",0]
[null,"corporate overheads",0]
[null,"Metering",25398168.566788532]
[null,"Public lighting",2338331]
[null,"Fee and quoted",5687194.2809591852]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-2068259.46]
[null,"TOTAL OPEX",{"$f":"SUM(C76:C86)","v":31355434.387747716}]
[]
[null,"2.1.5 - DUAL FUNCTION ASSETS CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,"2017"]
[null,"Replacement expenditure",0]
[null,"Connections",0]
[null,"Augmentation Expenditure",0]
[null,"Non-network",0]
[null,"Capitalised network overheads",0]
[null,"Capitalised corporate overheads",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",0]
[null,"capcons (included in the above)",0]
[null,"TOTAL GROSS CAPEX (including capcons)",0]
[]
[null,"2.1.6 - DUAL FUNCTION ASSETS OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,"2017"]
[null,"Vegetation management",0]
[null,"Maintenance",0]
[null,"Emergency response",0]
[null,"Non-network",0]
[null,"Network overheads",0]
[null,"Corporate overheads",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",0]
[null,"TOTAL OPEX",0]

{"sheet":"2.2 Repex","index":5,"n_rows":172,"n_cols":7,"rows_kept":172,"cut":false,"hidden":false,"merged":[[151,1,154,1],[155,1,158,1],[166,1,169,1],[170,1,171,1],[159,1,165,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.2 REPEX"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY"]
[null,null,null,null,"EXPENDITURE ($0's)","ASSET REPLACEMENTS\n(0's)","ASSET FAILURES\n(0's)"]
[null,"ASSET GROUP","ASSET CATEGORY",null,"2017","2017","2017"]
[null,"POLES BY: \nHIGHEST OPERATING VOLTAGE ; MATERIAL TYPE;  STAKING (IF WOOD)","Staking of a wooden pole",null,1216184.698904054,1442.4138666535689,0]
[null,null,"˂ = 1 kV; Wood",null,7333461.4930839576,1267.9673524779537,2300.7280122517909]
[null,null,"> 1 kV & < = 11 kV; Wood",null,645.50692253911643,0.32161245753290596,0.58356612154804022]
[null,null,"˃ 11 kV & < = 22 kV; Wood",null,11249386.277028237,1398.6440824375973,2537.8410677102456]
[null,null,"> 22 kV & < = 66 kV; Wood",null,503622.35372611304,39.743410981431651,72.114458443049784]
[null,null,"> 66 kV & < = 132 kV; Wood",null,0,0,0]
[null,null,"> 132 kV; Wood",null,0,0,0]
[null,null,"˂ = 1 kV; Concrete",null,2523444.279413376,403.45735248538352,732.07376420064895]
[null,null,"> 1 kV & < = 11 kV; Concrete",null,195.24592101491788,9.7277842093286354E-2,0.17651074046823437]
[null,null,"˃ 11 kV & < = 22 kV; Concrete",null,15348440.958085755,1649.6405098311177,2993.274332889237]
[null,null,"> 22 kV & < = 66 kV; Concrete",null,2269010.7814028971,178.17212302228313,323.29349303720852]
[null,null,"> 66 kV & < = 132 kV; Concrete",null,0,0,0]
[null,null,"> 132 kV; Concrete",null,0,0,0]
[null,null,"˂ = 1 kV; Steel",null,59281.229186608631,48.548522595312107,88.091342154975308]
[null,null,"> 1 kV & < = 11 kV; Steel",null,1.5938442531830035,7.9410483341458248E-4,1.4409040038223214E-3]
[null,null,"˃ 11 kV & < = 22 kV; Steel"]
[null,null,"> 22 kV & < = 66 kV; Steel",null,43.830716962532605,2.1837882918901021E-2,3.9624860105113839E-2]
[null,null,"> 66 kV & < = 132 kV; Steel",null,0,0,0]
[null,null,"> 132 kV; Steel",null,0,0,0]
[null,null,"Other",null,2.3907663797745053,1.1911572501218737E-3,2.161356005733482E-3]
[null,"POLE TOP STRUCTURES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",null,10853141.529731737,11444.847137897126,11526.592049182749]
[null,null,"> 1 kV & < = 11 kV",null,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV",null,5157333.9444092792,5088.8130109199465,5125.1598981360567]
[null,null,"> 22 kV & < = 66 kV",null,157443.60764584533,124.26034995565865,125.14788048892466]
[null,null,"> 66 kV & < = 132 kV",null,679.8409512492675,1.1722674524118741,1.1806403819709874]
[null,null,"> 132 kV",null,0,0,0]
[null,null,"Other",null,1547900.0551823508,5169.6994651363648,5206.624084492054]
[null,"OVERHEAD CONDUCTORS BY: \nHIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)","˂ = 1 kV",null,329425.17633785063,5.7171331031740182,749.53595796674051]
[null,null,"> 1 kV & < = 11 kV",null,65.431022567829515,1.1039461576741335E-3,0.14473116611131631]
[null,null,"˃ 11 kV & < = 22 kV  ; SWER",null,66780.380703738978,1.1986944002515112,157.15298898727363]
[null,null,"˃ 11 kV & < = 22 kV ; Single-Phase",null,7207241.9056956237,71.565736615583489,9382.5160239800152]
[null,null,"˃ 11 kV & < = 22 kV ; Multiple-Phase",null,2682660.367817333,26.593434240087021,3486.4913670984774]
[null,null,"> 22 kV & < = 66 kV",null,3012.4618662038047,null,0]
[null,null,"> 66 kV & < = 132 kV",null,0,0,0]
[null,null,"> 132 kV",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"UNDERGROUND CABLES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",null,0,0,0]
[null,null,"> 1 kV & < = 11 kV",null,748938.66411102796,1082.9408237431696,0]
[null,null,"> 11 kV & < = 22 kV",null,476226.68540911737,61.075549346336416,0]
[null,null,"> 22 kV & < = 33 kV",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV",null,0,0,0]
[null,null,">  132 kV",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"SERVICE LINES BY: \nCONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY ","˂ = 11 kV ; Residential ; Simple Type",null,6798946.9789036689,7732.5498033686272,7197.1650301281297]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Simple Type",null,861372.86669718509,979.65296856608427,911.82394763929472]
[null,null,"˂ = 11 kV ; Residential ; Complex Type",null,0,0,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Complex Type",null,0,0,0]
[null,null,"˂ = 11 kV ; Subdivision ; Complex Type",null,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 132 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 132 kV ; Subdivision  ",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"TRANSFORMERS BY: \nMOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV)","Pole Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",null,1666001.094894568,433.99387731298782,1942.5801025893943]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",null,24172.255150723649,1.0177913225816262,4.5556890896166617]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",null,1268989.6573270264,272.35330055866075,1219.0681256045691]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",null,1248696.6403784477,75.316557871040345,337.12099263163299]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",null,12355.596435647027,1.5266869838724393,6.8335336344249926]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",null,153040.44652895018,4.0711652903265048,18.222756358466647]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",null,112534.17134194894,3.0533739677448786,13.667067268849985]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",null,63561.43455356724,0.50889566129081309,2.2778445448083309]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ;  < = 60 kVA ; Single Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Single Phase",null,8034.2165614118567,0.50889566129081309,2.2778445448083309]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Single Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  < = 60 kVA ; Multiple Phase",null,15252.353388807056,1.0177913225816262,4.5556890896166617]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Multiple Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase",null,17689.382831249033,1.0177913225816262,4.5556890896166617]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 15 MVA and < = 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA",null,4487770.2323420085,4,17.904216664222144]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  < = 100 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  > 100 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  < = 100 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  > 100 MVA",null,0,0,0]
[null,null,"Other",null,545166.13519533852,3.5088956612908131,15.706007042974939]
[null,"SWITCHGEAR BY: \nHIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION","˂ = 11 kV ;  FUSE",null,28236.249796024505,27.008748177372354,6.4522539140418216]
[null,null,"˂ = 11 kV  ; Switch",null,6122.0113238369413,1.2591811773668278,0.30081204159471459]
[null,null,"˂ = 11 kV ;  Circuit Breaker",null,17254.035203626034,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Switch",null,10164112.1730264,3072.7306105322546,734.05986750666602]
[null,null,"> 11 kV & < = 22 kV  ; Circuit Breaker",null,3881111.5582501409,29.925496475517551,7.1490503927008753]
[null,null,"> 22 kV & < = 33 kV ; Switch",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker",null,2053504.0051493361,6,1.4333697818947684]
[null,null,"> 33 kV & < = 66 kV ; Switch",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Switch",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV  ; Circuit Breaker",null,0,0,0]
[null,null,"> 132 kV ; Switch",null,0,0,0]
[null,null,"> 132 kV ; Circuit Breaker",null,0,0,0]
[null,null,"Other",null,6214599.1926597552,2570,613.96005657825913]
[null,"PUBLIC LIGHTING BY: \nASSET TYPE ; LIGHTING OBLIGATION","Luminaires ;  Major Road",null,0,0,0]
[null,null,"Luminaires ;  Minor Road",null,0,0,0]
[null,null,"Brackets ; Major Road",null,0,0,0]
[null,null,"Brackets ; Minor Road",null,0,0,0]
[null,null,"Lamps ; Major Road",null,0,0,0]
[null,null,"Lamps ; Minor Road",null,0,0,0]
[null,null,"Poles / Columns ; Major Road",null,0,0,0]
[null,null,"Poles / Columns ; Minor Road",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: \nFUNCTION","Field Devices",null,3807534.965901128,49,0]
[null,null,"Local Network Wiring Assets",null,0,0,0]
[null,null,"Communications Network Assets",null,2207815.06,4,0]
[null,null,"Master Station Assets",null,0,0,0]
[null,null,"Communications Site Infrastructure",null,0,0,0]
[null,null,"Communications Linear Assets",null,0,0,0]
[null,null,"AFLC",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"OTHER BY: \nDNSP DEFINED","OTHER - EARTHING",null,766657.5250055847,229,0]
[null,null,"OTHER - MEASURING TRANSFORMERS",null,295880.23,8,0]
[null,null,"OTHER - REGULATORS",null,7147.52,0,0]
[null,null,"OTHER - SITE REPAIRS REFURBISHMENTS",null,2998838.9313118579,632,0]
[null,null,"OTHER - SURGE DIVERTERS",null,6383802.5271926429,6412,0]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,"","",""]
[]
[]
[null,"2.2.2 - SELECTED ASSET CHARACTERISTICS"]
[null,null,null,null,"ASSET VOLUMES CURRENTLY IN COMMISSION","ASSET REPLACEMENTS\n(0's)"]
[null,"ASSET GROUP","METRIC","UNITS","2017","2017"]
[null,"TOTAL POLES BY: \nFEEDER TYPE","Total CBD poles","Number",0,0]
[null,null,"Total urban poles","Number",20310.794215893406,418.52819434880792]
[null,null,"Total rural long poles","Number",179239.09168320248,3693.4357466036408]
[null,null,"Total rural short poles","Number",112445.11410090412,2317.0659929768285]
[null,"OVERHEAD CONDUCTORS BY:\nCONDUCTOR LENGTH BY FEEDER TYPE","Conductors CBD","KM",0,0]
[null,null,"Conductors urban","KM",2495.4394911838008,6.8404272213662747]
[null,null,"Conductors rural long","KM",22021.802938664801,60.36553513615582]
[null,null,"Conductors rural short","KM",13815.312948151097,37.870139947731623]
[null,"OVERHEAD CONDUCTORS BY: \nCONDUCTOR LENGTH MATERIAL TYPE","OH conductor LV ABC","KM",1172.5446146879074,3.2141456961445627]
[null,null,"OH conductor steel","KM",18362.162274258189,50.333833021290914]
[null,null,"OH conductor ACSR","KM",9281.0582270002506,25.440970844354506]
[null,null,"OH conductor AAAC","KM",0,0]
[null,null,"OH conductor AAC","KM",7931.6596448522805,21.742038120716625]
[null,null,"OH conductor HDBC","KM",1585.1306172010709,4.3451146227471051]
[null,null,"Other","KM",0,0]
[null,"UNDERGROUND CABLES BY: \nCABLE LENGTH BY FEEDER TYPE","Cable CBD","KM"]
[null,null,"Cable urban","KM",2632.1096724722952,457.98135942582405]
[null,null,"Cable rural long","KM",726.21320162261691,126.35951791465743]
[null,null,"Cable rural short","KM",3216.5660359050621,559.67549574902444]
[null,"TRANSFORMERS BY: \nTOTAL MVA","Total MVA replaced","MVA",8975.2230000025629,212.78600000256242]
[null,null,"Total MVA disposed of","MVA",0,116.75300000000001]

{"sheet":"2.3(a) Augex","index":6,"n_rows":131,"n_cols":34,"rows_kept":131,"cut":false,"hidden":false,"merged":[[11,6,12,6],[11,16,11,19],[12,23,12,24],[10,30,10,31],[10,23,10,24],[10,25,12,25],[10,26,12,26],[10,27,10,28],[10,29,11,29],[11,7,11,8],[11,9,11,10],[11,11,11,13],[10,1,10,10],[11,1,12,1],[11,2,12,2],[12,27,12,29],[12,30,12,31],[72,23,72,24],[72,25,74,25],[72,26,74,26],[72,30,72,31],[74,23,74,24],[74,27,74,29],[74,30,74,31],[72,29,73,29],[72,27,72,28],[74,7,74,10],[73,7,73,10],[72,11,72,22],[73,17,73,19],[73,21,73,22],[6,1,6,3],[11,21,11,22],[10,11,10,22],[12,17,12,19],[73,11,73,13],[73,14,73,16],[72,1,72,10],[73,1,74,1],[73,2,74,2],[73,3,74,3],[73,4,74,4],[73,6,74,6],[11,3,12,3],[11,4,12,4],[11,5,12,5],[11,14,11,15]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.3 AUGEX PROJECT DATA"]
[]
[]
[null,"There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped.  See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS. "]
[null,"PROJECT DESCRIPTION AND CHANGES",null,null,null,null,null,null,null,null,null,"PLANT AND EQUIPMENT EXPENDITURE AND VOLUME",null,null,null,null,null,null,null,null,null,null,null,"OTHER EXPENDITURE",null,"TOTAL DIRECT EXPENDITURE ($0's)","YEARS INCURRED","ALL RELATED PARTY CONTRACTS",null,"ALL NON RELATED PARTYCONTRACTS","LAND AND EASEMENTS"]
[null,"SUBSTATION ID","SUBSTATION TYPE\n(drop down)","PROJECT ID","PROJECT TYPE\n(drop down)","PROJECT TRIGGER\n(drop down)","VOLTAGE (KV)","SUBSTATION RATING\nNORMAL CYCLIC\n(MVA)",null,"SUBSTATION RATING\nN-1 EMERGENCY\n(MVA)",null,"TRANSFORMERS",null,null,"SWITCHGEAR",null,"CAPACITORS",null,null,null,"OTHER PLANT ITEM","INSTALLATION (LABOUR)",null,"CIVIL WORKS","OTHER DIRECT",null,null,"RELATED PARTY MARGINS","TOTAL",null,"LAND PURCHASE","EASEMENTS"]
[null,null,null,null,null,null,null,"PRE","POST","PRE","POST","UNITS ADDED ","MVA ADDED","EXPENDITURE ($0's)","UNITS ADDED ","EXPENDITURE ($0's)","MVAR ADDED","EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)","VOLUME","EXPENDITURE ($0's)","EXPENDITURE ($0's)",null,null,null,"EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)"]
[null,"Worri Yallock Zone Sub Station GFN Installation","Zone substation","DD-0001410","Other","Safety","22",null,88.4,null,43.2,0,0,0,10,251630.87487976713,0,null,null,0,2011147.8937724917,25093.241968897,2337347.1725855116,0,0,4600125.94123777,"2015, 2016, 2017",0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,"Non material projects - [actual]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4460271.6758404803,"2015, 2016, 2017",null,null,null,0,0]
[null,null,null,"Non material projects - [forecast]"]
[]
[]
[null,"AUG232_1","AUG232_2","AUG232_3","AUG232_4","AUG232_5","AUG232_6","ED_AUG232_00001","ED_AUG232_00002","ED_AUG232_00003","ED_AUG232_00004","ED_AUG232_00005","ED_AUG232_00006","ED_AUG232_00007","ED_AUG232_00008","ED_AUG232_00009","ED_AUG232_00010","ED_AUG232_00011","ED_AUG232_00012","ED_AUG232_00013","ED_AUG232_00014","ED_AUG232_00015","ED_AUG232_00016","ED_AUG232_00017","ED_AUG232_00018","ED_AUG232_00019","ED_AUG232_00020","ED_AUG232_00021"]
[null,"2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS."]
[null,"PROJECT DESCRIPTION AND CHANGES",null,null,null,null,null,null,null,null,null,"PLANT AND EQUIPMENT EXPENDITURE AND VOLUME",null,null,null,null,null,null,null,null,null,null,null,"OTHER EXPENDITURE",null,"TOTAL DIRECT EXPENDITURE ($0's)","YEARS INCURRED","ALL RELATED PARTY CONTRACTS",null,"ALL NON RELATED PARTYCONTRACTS","LAND AND EASEMENTS"]
[null,"LINE ID","PROJECT ID","PROJECT TYPE","PROJECT TRIGGER",null,"VOLTAGE (KV)","ROUTE LINE LENGTH ADDED",null,null,null,"POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS)",null,null,"OVERHEAD LINES",null,null,"UNDERGROUND CABLES",null,null,"OTHER PLANT ITEM","INSTALLATION (LABOUR)",null,"CIVIL WORKS","OTHER DIRECT",null,null,"RELATED PARTY MARGINS","TOTAL",null,"LAND PURCHASE","EASEMENTS"]
[null,null,null,null,null,null,null,"KM ADDED",null,null,null,"POLES/TOWERS ADDED","POLES/TOWERS UPGRADED","EXPENDITURE ($0's)","CIRCUIT KM ADDED","CIRCUIT KM UPGRADED","EXPENDITURE ($0's)","CIRCUIT KM ADDED","CIRCUIT KM UPGRADED","EXPENDITURE ($0's)","EXPENDITURE ($0's)","VOLUME","EXPENDITURE ($0's)","EXPENDITURE ($0's)",null,null,null,"EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"New line on new route - single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"New line on new route - dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"New line on new route - other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line rebuild over existing route - single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line rebuild over existing route - dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - raising/retensoring"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - voltage upgrade"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - capacity"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"String spare circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,"Non material projects - [actual]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3126242.3734647431,"2015, 2016, 2017",null,null,null,0,0]
[null,null,"Non material projects - [actual]"]

{"sheet":"2.3(b) Augex","index":7,"n_rows":46,"n_cols":5,"rows_kept":46,"cut":false,"hidden":false,"merged":[[10,1,11,1],[21,1,22,1],[35,1,36,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.3 AUGEX  DATA"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS."]
[null,"DESCRIPTOR METRICS"]
[null,"PROJECT TYPE",null,"UNITS ADDED\n(0's)","UNITS UPGRADED\n(0's)"]
[null,null,"UNITS","2017","2017"]
[null,"HV Feeder Augmentations - Overhead Lines","Circuit line length in km",14.518000000000001,2.5270999999999999]
[null,"HV Feeder Augmentations - Underground Cables","Circuit line length in km",34.146267999999999,0.40100000000000002]
[null,"LV Feeder Augmentations - Overhead Lines","Circuit line length in km",0.128,13.669400000000001]
[null,"LV Feeder Augmentations - Underground Cables","Circuit line length in km",1.8106049999999998,1E-3]
[null,"Distribution Substation Augmentations - Pole Mounted","Number",54.475674725274843,17.750927472527462]
[null,"Distribution Substation Augmentations - Ground Mounted","Number",29.885960439560506,9.7383560439560384]
[null,"Distribution Substation Augmentations - Indoor","Number",1.7023648351648388,0.55471648351648317]
[]
[null,"COST METRICS"]
[null,"TOTAL DIRECT EXPENDITURE - Project Type",null,"EXPENDITURE\n($0's)"]
[null,null,null,"2017"]
[null,"HV Feeder Augmentations - Overhead Lines",null,26897371.223923124]
[null,"HV Feeder Augmentations - Underground Cables",null,14546137.862064121]
[null,"HV Feeder Non-Material Projects",null,1956870.7573966419]
[null,"LV Feeder Augmentations - Overhead Lines",null,6727578.8214378376]
[null,"LV Feeder Augmentations - Underground Cables",null,849154.29455084866]
[null,"LV Feeder Non-Material Projects",null,22298.844129302259]
[null,"Distribution Substation Augmentations - Pole Mounted",null,4227584.3622183697]
[null,"Distribution Substation Augmentations - Ground Mounted",null,2319299.7542725778]
[null,"Distribution Substation Augmentations - Indoor",null,132112.01131932405]
[]
[]
[null,"2.3.4 - AUGEX DATA - TOTAL EXPENDITURE"]
[null,"AUGMENTATION CAPEX (As incurred)",null,"EXPENDITURE\n ($0's)"]
[null,null,null,"2017"]
[null,"Subtransmission Substations, Switching Stations, Zone Substations",null,10078907.695467733]
[null,"Subtransmission Lines",null,3477673.8999200789]
[null,"HV Feeders",null,48279163.9922271]
[null,"HV Feeders - Land Purchases and Easements",null,0]
[null,"Distribution Substations",null,7429804.7740971176]
[null,"Distribution Substations - Land Purchases And Easements",null,0]
[null,"LV Feeders",null,8453264.9600908756]
[null,"LV Feeders - Land Purchases And Easements",null,0]
[null,"Other Assets",null,0]

{"sheet":"2.5 Connections","index":8,"n_rows":73,"n_cols":5,"rows_kept":73,"cut":false,"hidden":false,"merged":[[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.5 CONNECTIONS"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.5.1 - DESCRIPTOR METRICS"]
[null,"<<<GROUP-ROW>>>"]
[]
[null,null,null,null,"VOLUMES AND EXPENDITURE"]
[null,"CONNECTION SUBCATEGORY","DESCRIPTOR METRIC","UNITS","2017"]
[null,"RESIDENTIAL","Underground connections","0's",16673.670181073714]
[null,null,"Overhead connections","0's",1005.8211629271611]
[null,null,"Distribution substation installed","MVA added",177.36008836952377]
[null,null,"Distribution substations installed","0's",886.8004418476188]
[null,null,"Distribution substation installed","total spend $0s",6828548.7992959106]
[null,null,"Augmentation HV","net circuit km added",166.37656649907933]
[null,null,"Augmentation HV","total spend $0s",3024621.6224236717]
[null,null,"Augmentation LV","net circuit km added",36.87846473168495]
[null,null,"Augmentation LV","total spend $0s",2432277.1581105618]
[null,null,"Mean days to connect residential customer with LV single phase connection","0's",9.7200000000000006]
[null,null,"Volume of GSL breaches for residential customers","0's",587]
[null,null,"Volume of customer complaints relating to connection services","0's",307]
[null,null,"GSL payments","$0s",127360]
[null,"COMMERCIAL/INDUSTRIAL","Underground connections","0's",1990.3665721475136]
[null,null,"Overhead connections","0's",326.14208385161226]
[null,null,"Distribution substation installed","MVA added",752]
[null,null,"Distribution substations installed","0's",752]
[null,null,"Distribution substation installed","total spend $0s",17170447.820974048]
[null,null,"Augmentation HV","net circuit km added",205.05361666588749]
[null,null,"Augmentation HV","total spend $0s",8783603.4036582951]
[null,null,"Augmentation LV","net circuit km added",33.51827999999999]
[null,null,"Augmentation LV","total spend $0s",3543355.75489834]
[null,"SUBDIVISION","Underground connections","0's",353.36397955225027]
[null,null,"Overhead connections","0's",37.636020447749708]
[null,null,"Distribution substation installed","MVA added",199.43991163047625]
[null,null,"Distribution substations installed","0's",559.19955815238131]
[null,null,"Distribution substation installed","total spend $0s",11332378.572952682]
[null,null,"Augmentation HV","net circuit km added",157.42654035355602]
[null,null,"Augmentation HV","total spend $0s",6995074.4111350682]
[null,null,"Augmentation LV","net circuit km added",201.68583426831498]
[null,null,"Augmentation LV","total spend $0s",9284460.835859254]
[null,null,"Cost per lot ($)","$0s",2006.6432646949663]
[null,"EMBEDDED GENERATION","Underground connections","0's",0]
[null,null,"Overhead connections","0's",0]
[null,null,"Distribution substation installed","MVA added",2.5]
[null,null,"Distribution substations installed","0's",5]
[null,null,"Distribution substation installed","total spend $0s",230782.8755207303]
[null,null,"Augmentation HV","net circuit km added",3.6255337300482902]
[null,null,"Augmentation HV","total spend $0s",141087.95473343358]
[null,null,"Augmentation LV","net circuit km added",5.0000000000000001E-3]
[null,null,"Augmentation LV","total spend $0s",9084.0151674607696]
[]
[]
[]
[null,"2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION"]
[null,null,null,"EXPENDITURE\n($0's)","VOLUMES\n(0's)"]
[null,"CONNECTION SUBCATEGORY","CONNECTION CLASSIFICATION","2017","2017"]
[null,"RESIDENTIAL","Simple connection LV",12217185.923490586,15667.856561629622]
[null,null,"Complex connection LV",12340978.118436754,1628.9777711796787]
[null,null,"Complex connection HV",4315410.9233957846,382.65701119157342]
[null,"COMMERCIAL/INDUSTRIAL","Simple connection LV",1014513.8234186918,1851.1434383703784]
[null,null,"Complex connection HV (customer connected at LV, minor HV works)",3766643.8792507979,210.4805578824963]
[null,null,"Complex connection HV (customer connected at LV, upstream asset works)",8114210.7054326115,128.36678200692043]
[null,null,"Complex connection HV (customer connected at HV)",3535296.0295397425,117.00922722029989]
[null,null,"Complex connection sub-transmission",25291.100709484046,9.508650519031141]
[null,"SUBDIVISION","Complex connection LV",15905032.013648696,254.19512636376885]
[null,null,"Complex connection HV (no upstream asset works)",6391295.9063161425,133.47040791199512]
[null,null,"Complex connection HV (with upstream asset works)",29455.739109951246,3.3344657242360132]
[null,"EMBEDDED GENERATION","Simple connection LV",0,0]
[null,null,"Complex connection HV (small capacity)",126153.43307337137,0]
[null,null,"Complex connection HV (large capacity)",0,0]

{"sheet":"2.6 Non-network","index":9,"n_rows":94,"n_cols":6,"rows_kept":94,"cut":false,"hidden":false,"merged":[[58,5,59,5],[61,2,61,4],[62,2,62,4],[63,2,63,4],[5,1,5,2],[60,2,60,4],[9,2,9,4],[89,2,93,2],[69,2,73,2],[74,2,78,2],[79,2,83,2],[84,2,88,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.6 NON NETWORK EXPENDITURE"]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.6.1 - NON-NETWORK EXPENDITURE"]
[null,null,null,null,null,"EXPENDITURE\n($0's)"]
[null,"SERVICE SUBCATEGORY","ASSET CATEGORY",null,null,"2017"]
[null,"OPEX"]
[null,"IT & COMMUNICATIONS","Client device expenditure",null,null,0]
[null,null,"Recurrent expenditure",null,null,22714400.775228925]
[null,null,"Non-recurrent expenditure",null,null,1434813.9360000005]
[null,"MOTOR VEHICLES","Car",null,null,182280.91535722997]
[null,null,"Light commercial vehicle",null,null,1549775.7364250151]
[null,null,"Elevated work platform (LCV)  ",null,null,0]
[null,null,"Elevated work platform (HCV)",null,null,522379.6873073554]
[null,null,"Heavy commercial vehicle",null,null,151703.11091039926]
[null,"BUILDINGS AND PROPERTY","Total buildings and property expenditure",null,null,8799889.2600000035]
[null,"OTHER","Other expenditure",null,null,0]
[null,"OTHER - DNSP nominated","General Equipment",null,null,0]
[null,null,"Motor Vehcile",null,null,0]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"CAPEX"]
[null,"IT & COMMUNICATIONS","Client device expenditure",null,null,0]
[null,null,"Recurrent expenditure",null,null,29012499.004999995]
[null,null,"Non-recurrent expenditure",null,null,6528583.8149999995]
[null,"MOTOR VEHICLES","Car",null,null,95710.321901451316]
[null,null,"Light commercial vehicle",null,null,1819894.6628918145]
[null,null,"Elevated work platform (LCV)  ",null,null,0]
[null,null,"Elevated work platform (HCV)",null,null,20668.427967080734]
[null,null,"Heavy commercial vehicle",null,null,0]
[null,"BUILDINGS AND PROPERTY","Total buildings and property expenditure",null,null,263409.26]
[null,"OTHER","Other expenditure",null,null,0]
[null,"OTHER - DNSP nominated","General Equipment",null,null,2082261.5499999998]
[null,null,"Motor Vehcile",null,null,1032098.5272396499]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[]
[]
[]
[null,"2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE"]
[null,null,null,null,null,"VOLUMES\n(0's)"]
[]
[null,"NON-NETWORK CATEGORY","DESCRIPTOR METRIC",null,null,"2017"]
[null,"IT & COMMUNICATIONS","Employee numbers",null,null,757]
[null,null,"User numbers",null,null,1384]
[null,null,"Number of devices",null,null,1624]
[]
[]
[null,"2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES"]
[null,null,null,null,null,"VOLUMES / %"]
[null,"NON-NETWORK CATEGORY","ASSET CATEGORY","DESCRIPTOR METRIC","UNITS","2017"]
[null,"MOTOR VEHICLES","CAR","Average kilometres travelled","0's",23677.617016180116]
[null,null,null,"Number purchased","0's",3.8113772394384799]
[null,null,null,"Number leased","0's",47.070508907065225]
[null,null,null,"Number in fleet","0's",66.889670552145319]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.76227544788769597]
[null,null,"LIGHT COMMERCIAL VEHICLE","Average kilometres travelled","0's",25631.427540442048]
[null,null,null,"Number purchased","0's",50.310179560587933]
[null,null,null,"Number leased","0's",237.95698564894244]
[null,null,null,"Number in fleet","0's",355.5470481933325]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.76227544788769597]
[null,null,"ELEVATED WORK PLATFORM (LCV) ","Average kilometres travelled","0's",0]
[null,null,null,"Number purchased","0's",0]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",0]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0]
[null,null,"ELEVATED WORK PLATFORM (HCV)","Average kilometres travelled","0's",16931.243926589366]
[null,null,null,"Number purchased","0's",0.76227544788769597]
[null,null,null,"Number leased","0's",19.183932105173682]
[null,null,null,"Number in fleet","0's",30.872155639451687]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.76227544788769597]
[null,null,"HEAVY COMMERCIAL VEHICLE ","Average kilometres travelled","0's",12943.344395956985]
[null,null,null,"Number purchased","0's",0]
[null,null,null,"Number leased","0's",7.6227544788769599]
[null,null,null,"Number in fleet","0's",28.204191571844749]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.76227544788769597]

{"sheet":"2.7 Vegetation management","index":10,"n_rows":410,"n_cols":5,"rows_kept":410,"cut":false,"hidden":false,"merged":[[405,1,405,3],[5,1,5,2],[7,1,7,2],[12,4,13,4],[124,4,125,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.7 VEGETATION MANAGEMENT"]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"Please enter a description for each Zone in table 2.7.1 - Urban and CBD.  The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2."]
[]
[]
["`","2.7.1 - DESCRIPTOR METRICS BY ZONE"]
[null,"URBAN AND CBD"]
[null,null,null,null,"2017"]
[null,"ZONES","ASSET","UNITS"]
[null,"HBRA","Route line length within zone","km",560.45633400000008]
[null,null,"Number of maintenance spans","0's",1647]
[null,null,"Total length of maintenance spans","km",233.03287807307385]
[null,null,"Length of vegetation corridors","km",266.70733161368804]
[null,null,"Average number of trees per maintenance span","0's",7.9848208864602306]
[null,null,"Average frequency of cutting cycle","years",1]
[null,"LBRA","Route line length within zone","km",131.46506600000001]
[null,null,"Number of maintenance spans","0's",8784]
[null,null,"Total length of maintenance spans","km",482.95514333394527]
[null,null,"Length of vegetation corridors","km",979.60061347687872]
[null,null,"Average number of trees per maintenance span","0's",5.9200819672131146]
[null,null,"Average frequency of cutting cycle","years",1]
[null,"ZONE 3","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's"]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 4","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 5","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 6","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 7","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 8","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 9","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 10","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 11","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 12","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 13","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 14","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 15","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 16","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 17","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 18","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[]
[null,"RURAL"]
[null,null,null,null,"2017"]
[null,"ZONES","ASSET","UNITS"]
[null,"HBRA","Route line length within zone","km",27462.360366000001]
[null,null,"Number of maintenance spans","0's",51269]
[null,null,"Total length of maintenance spans","km",7254.0149519905426]
[null,null,"Length of vegetation corridors","km",11331.595105717266]
[null,null,"Average number of trees per maintenance span","0's",7.5064854005344364]
[null,null,"Average frequency of cutting cycle","years",1]
[null,"LBRA","Route line length within zone","km",6441.7882340000006]
[null,null,"Number of maintenance spans","0's",12071]
[null,null,"Total length of maintenance spans","km",663.67845345902242]
[null,null,"Length of vegetation corridors","km",421.26620084525143]
[null,null,"Average number of trees per maintenance span","0's",6.856349929583299]
[null,null,"Average frequency of cutting cycle","years",1]
[null,"ZONE 3","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's"]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 4","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 5","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 6","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 7","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 8","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 9","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 10","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 11","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 12","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 13","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 14","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 15","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 16","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 17","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 18","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[]
[]
[]
[null,"2.7.2 - EXPENDITURE METRICS BY ZONE"]
[null,null,null,null,"EXPENDITURE\n($0's)"]
[null,"ZONES","SERVICE SUBCATEGORY",null,"2017"]
[null,"HBRA","Tree trimming (excluding hazard trees) "]
[null,null,"Hazard tree cutting "]
[null,null,"Ground clearance "]
[null,null,"Vegetation corridor clearance "]
[null,null,"Inspection "]
[null,null,"Audit "]
[null,null,"Contractor liaison expenditure "]
[null,null,"Tree replacement program costs "]
[null,null,"Other vegetation management costs not specified in sheet "]
[null,"LBRA","Tree trimming (excluding hazard trees) "]
[null,null,"Hazard tree cutting "]
[null,null,"Ground clearance "]
[null,null,"Vegetation corridor clearance "]
[null,null,"Inspection "]
[null,null,"Audit "]
[null,null,"Contractor liaison expenditure "]
[null,null,"Tree replacement program costs "]
[null,null,"Other vegetation management costs not specified in sheet "]
[null,"ZONE 3","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 4","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 5","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 6","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 7","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 8","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 9","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 10","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 11","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 12","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 13","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 14","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 15","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 16","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 17","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,"ZONE 18","Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[]
[null,"2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS"]
[null,null,null,null,"VOLUMES\n(0's)"]
[null,"DESCRIPTOR METRIC",null,null,"2017"]
[null,"Number of fire starts caused by vegetation grow-ins (NSP responsibility)",null,null,0]
[null,"Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility)",null,null,9]
[null,"Number of fire starts caused by vegetation grow-ins (other party responsibility)",null,null,0]
[null,"Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility)",null,null,0]

{"sheet":"2.8 Maintenance","index":11,"n_rows":85,"n_cols":10,"rows_kept":85,"cut":false,"hidden":false,"merged":[[8,7,9,7],[8,8,10,8],[8,9,10,9],[68,1,69,1],[5,1,5,2],[28,1,29,1],[48,5,48,6],[8,5,8,6]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.8 MAINTENANCE"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE"]
[null,null,null,null,null,"ASSET QUANTITY\n(0's)",null,"AVERAGE AGE OF ASSET GROUP ","INSPECTION \nCYCLE \n(YEARS)","MAINTENANCE \nCYCLE \n(YEARS)"]
[null,null,null,null,null," AT YEAR END","INSPECTED / MAINTAINED"]
[null,"MAINTENANCE ACTIVITY","MAINTENANCE ASSET CATEGORY","ASSET QUANTITY","Units","2017","2017","2017"]
[null,"Pole top, overhead line & service line maintenance","Pole tops and overhead lines","Number of poles","Number",405037,127774.54402093566,23.71612074279232,3,0]
[null,null,"Service lines","Number of customers","Number",259055,41564.630041781013,19.645352304887375,3,0]
[null,"Pole inspection and treatment","All poles","Number of poles","Number",311995,95318.86256637123,33.288728933030683,5,0]
[null,"Overhead asset inspection","All overhead assets","Line patrolled (route KM)","KM",34596.073426572701,7469,39.469350597697442,5,0]
[null,"Network underground cable maintenance: by voltage","LV - 11 to 22 KV","Length (KM)","KM",6563.7098209999749,1524,18.559069300484349,0,0]
[null,null,"33 KV and above","Length (KM)","KM",11.179088999999999,0,28.580615073751755,0,0]
[null,"Network underground cable maintenance: by location","Cbd","Length (KM)","KM",0,0,0,0,0]
[null,null,"Non-CBD","Length (KM)","KM",6574.8889099999751,1524,18.559069300484349,0,0]
[null,"Distribution substation equipment & property maintenance","Distribution substation transformers","Number of installed transformers","Number",60821.999999999985,20273.999999999996,25.409709350035772,3,0]
[null,null,"Distribution substation switchgear\n (within-substations and stand-alone switchgear)","Number of switches","Number",161040,16104,29.650852171020382,0,10]
[null,null,"Distribution substation - other equipment","Earth mat","Number",213700,858,28.496393275900491,0,0]
[null,null,"Distribution substation - property","Number of distribution substation properties maintained","Number",4395,288,40,3,0]
[null,"Zone substation equipment maintenance","Transformers - zone substation","Number","Number",141,1495,37.560283687943262,1,4]
[null,null,"Transformers - distribution","Number of distribution transformers within zone substation","Number",0,0,0,0,0]
[null,null,"Transformers - HV","Number of HV transformers","Number",0,0,0,0,0]
[null,null,"Zone substation - other equipment","Other","Other",2598,2270,25.549849246333924,1,4]
[null,"Zone substation property maintenance","All zone substation properties","Number of zone substation properties maintained","Number",71,1624,40,0,1]
[null,"Public lighting maintenance","Minor roads","Number of public lights maintained","Number",0,0,0,0,0]
[null,null,"Major roads","Number of public lights maintained","Number",0,0,0,0,0]
[null,"SCADA & network control maintenance","SCADA & network control","Number of systems","Number",9031.2154057456792,3010.4051352485599,8.4468882495150606,6,6]
[null,"Protection systems maintenance","Protection systems","Number of systems","Number",327.78459425432146,675,10.066466483565703,6,6]
[null,"Subtransmission asset maintenance","Subtransmission asset maintenance\n- for DNSPs with dual function assets","<DNSP to nominate>","<DNSP to nominate>",0,0,0,0,0]
[null,"Various assets"," includes rates, electricity, communications equip, metering","Various","Number",0,0,0,0,0]
[null,"Ground clearance - access tracks","Access tracks","Number","Number",0,0,0,0,0]
[null,"Other","Duplicates","Duplicates",null,0,0,0,0,0]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[]
[]
[null,"2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE"]
[null,null,null,null,null,"EXPENDITURE ($0'S)"]
[null,null,null,null,null," ROUTINE MAINTENANCE ","NON-ROUTINE MAINTENANCE"]
[null,"MAINTENANCE ACTIVITY","MAINTENANCE ASSET CATEGORY","ASSET QUANTITY","Units","2017","2017"]
[null,"Pole top, overhead line & service line maintenance","Pole tops and overhead lines","Number of poles","Number",688644.75946015946,676376.80176049017]
[null,null,"Service lines","Number of customers","Number",78.180000000000007,328641.90145071462]
[null,"Pole inspection and treatment","All poles","Number of poles","Number",7155486.8852226101,150508.45244451106]
[null,"Overhead asset inspection","All overhead assets","Line patrolled (route KM)","KM",831841.53251482651,5449771.5719497362]
[null,"Network underground cable maintenance: by voltage","LV - 11 to 22 KV","Length (KM)","KM",0,686702.35161613894]
[null,null,"33 KV and above","Length (KM)","KM",0,0]
[null,"Network underground cable maintenance: by location","Cbd","Length (KM)","KM",0,0]
[null,null,"Non-CBD","Length (KM)","KM",0,686702.35161613894]
[null,"Distribution substation equipment & property maintenance","Distribution substation transformers","Number of installed transformers","Number",293807.86561933527,230178.3098066168]
[null,null,"Distribution substation switchgear\n (within-substations and stand-alone switchgear)","Number of switches","Number",120779.71999999948,778552.95439867198]
[null,null,"Distribution substation - other equipment","Earth mat","Number",164887.4369093102,80436.47510198169]
[null,null,"Distribution substation - property","Number of distribution substation properties maintained","Number",15325.320000000002,365833.35234625731]
[null,"Zone substation equipment maintenance","Transformers - zone substation","Number","Number",330545.32460670365,80176.639999999999]
[null,null,"Transformers - distribution","Number of distribution transformers within zone substation","Number",0,0]
[null,null,"Transformers - HV","Number of HV transformers","Number",0,0]
[null,null,"Zone substation - other equipment","Other","Other",939532.25289854873,571129.32277230115]
[null,"Zone substation property maintenance","All zone substation properties","Number of zone substation properties maintained","Number",428925.67999999982,542487.30999999982]
[null,"Public lighting maintenance","Minor roads","Number of public lights maintained","Number",0,0]
[null,null,"Major roads","Number of public lights maintained","Number",0,0]
[null,"SCADA & network control maintenance","SCADA & network control","Number of systems","Number",1358.01,145682.68933549785]
[null,"Protection systems maintenance","Protection systems","Number of systems","Number",332626.54000000044,265266.55108609574]
[null,"Subtransmission asset maintenance","Subtransmission asset maintenance\n- for DNSPs with dual function assets","<DNSP to nominate>","<DNSP to nominate>",0,0]
[null,"Various assets"," includes rates, electricity, communications equip, metering","Various","Number",0,0]
[null,"Ground clearance - access tracks","Access tracks","Number","Number",0,0]
[null,"Other","Duplicates","Duplicates",null,0,-686702.35161613894]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]
[null,null,"< DNSP to nominate >","< DNSP to nominate >"]

{"sheet":"2.9 Emergency Response","index":12,"n_rows":377,"n_cols":4,"rows_kept":377,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.9 EMERGENCY RESPONSE"]
[]
[]
[null,"There is ONE table on this worksheet. It has been sub-grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,"2017"]
[null,"(A) TOTAL EMERGENCY RESPONSE EXPENDITURE","Total Expenditure",16516475.275187489]
[null,"(B) MAJOR EVENTS O&M EXPENDITURE","19/12/2017 Major Event Day",135284.83499999996]
[]
[]
[]
[]
[]
[]
[null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"(C) MAJOR EVENT DAYS O&M EXPENDITURE","2017-12-19",135284.83499999996]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]

{"sheet":"2.10 Overheads","index":13,"n_rows":174,"n_cols":4,"rows_kept":174,"cut":false,"hidden":true,"merged":[[5,1,5,2],[106,1,106,3],[152,1,152,3],[10,1,10,3],[70,1,70,3]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"AusNet Services (D)"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017"}]
[null,"2.10 OVERHEADS"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped (and sub-grouped)  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.10.1 - NETWORK OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2017"}]
[null,"NETWORK OVERHEADS"]
[null,"Standard Control Services","Network management",""]
[null,null,"Network planning",""]
[null,null,"Network control and operational switching",""]
[null,null,"Quality and standard functions",""]
[null,null,"Project governance and related functions",""]
[null,null,null,""]
[]
[null,null,null,""]
[]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Alternative Control Services","Network management",""]
[null,null,"Network planning",""]
[null,null,"Network control and operational switching"]
[null,null,"Quality and standard functions",""]
[null,null,"Project governance and related functions",""]
[null,null,null,""]
[null,null,null,""]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Negotiated Services","Total  ",""]
[null,"Unregulated Services","Total  ",""]
[]
[null,"CAPITALISED NETWORK OVERHEADS"]
[null,"Standard Control Services","Network management",""]
[null,null,"Network planning",""]
[null,null,"Network control and operational switching",""]
[null,null,"Quality and standard functions",""]
[null,null,"Project governance and related functions",""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[]
[]
[]
[null,"2.10.2 - CORPORATE OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2017"}]
[null,"CORPORATE OVERHEADS"]
[null,"Standard Control Services",null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Alternative Control Services",null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Negotiated Services","Total",""]
[null,"Unregulated Services","Total",""]
[]
[null,"CAPITALISED CORPORATE OVERHEADS"]
[null,"Standard Control Services",null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]

{"sheet":"2.10(A) Overheads","index":14,"n_rows":37,"n_cols":4,"rows_kept":37,"cut":false,"hidden":false,"merged":[[5,1,5,2],[8,1,8,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"Australian Distribution Co. (Victoria)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.10(A) OVERHEADS"]
[]
[null,"This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options."]
[]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped (and sub-grouped)  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.10.1 - NETWORK OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,2017]
[null,"OPEX"]
[null,"Standard Control Services","Total  ",70781271.114998654]
[null,"Alternative Control Services","Total  ",0]
[null,"CAPEX"]
[null,"Standard Control Services","Total  ",29267094.922092617]
[null,"Alternative Control Services","Total  ",977782.62809922767]
[null,"OTHER DISTRIBUTION SERVICES"]
[null,"Negotiated Services","Total  ",114015.92840983468]
[null,"Unregulated Services","Total  ",4072393.5899999994]
[]
[]
[]
[null,"2.10.2 - CORPORATE OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,2017]
[null,"OPEX"]
[null,"Standard Control Services","Total",27744532.76307033]
[null,"Alternative Control Services","Total",0]
[null,"CAPEX"]
[null,"Standard Control Services","Total",5910615.2066409076]
[null,"Alternative Control Services","Total",1138329.2199999997]
[null,"OTHER DISTRIBUTION SERVICES"]
[null,"Negotiated Services","Total",0]
[null,"Unregulated Services","Total",0]

{"sheet":"2.11 Labour","index":15,"n_rows":55,"n_cols":7,"rows_kept":55,"cut":false,"hidden":false,"merged":[[36,1,36,2],[5,1,5,2],[11,1,11,2],[33,5,33,6],[8,3,9,3],[8,4,9,4],[8,5,9,5],[8,6,9,6],[33,3,33,4],[10,1,10,2],[35,1,35,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.11 LABOUR"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.11.1 - COST METRICS PER ANNUM"]
[null,null,null,"ASL \n(0's)","TOTAL LABOUR EXPENDITURE\n($0's)","AVERAGE PRODUCTIVE WORK HOURS \nPER ASL \n(0's)","STAND-DOWN OCCURENCES \nPER ASL \n(0's)"]
[]
[null,null,null,"2017","2017","2017","2017"]
[null,"INTERNAL LABOUR EXPENDITURE"]
[null,"CORPORATE OVERHEADS","Executive manager"]
[null,null,"Senior manager"]
[null,null,"Manager"]
[null,null,"Professional"]
[null,null,"Semi professional"]
[null,null,"Support staff"]
[null,null,"Intern, junior staff, apprentice"]
[null,"NETWORK OVERHEADS ","Executive manager"]
[null,null,"Senior manager"]
[null,null,"Manager"]
[null,null,"Professional"]
[null,null,"Semi professional"]
[null,null,"Support staff"]
[null,null,"Intern, junior staff, apprentice"]
[null,"TOTAL DIRECT NETWORK LABOUR ","Skilled electrical worker"]
[null,null,"Skilled non electical worker"]
[null,null,"Apprentice"]
[null,null,"Unskilled worker"]
[]
[]
[null,"2.11.2 - DESCRIPTOR METRICS"]
[null,null,null,"ORDINARY TIME (0's)",null,"OVERTIME (0's)"]
[null,null,null,"PER ASL","HOURLY RATE\nPER ASL","PER ASL","HOURLY RATE\nPER ASL"]
[null,null,null,"2017","2017","2017","2017"]
[null,"AVERAGE PRODUCTIVE WORK HOURS PER ASL"]
[null,"CORPORATE OVERHEADS","Executive manager"]
[null,null,"Senior manager"]
[null,null,"Manager"]
[null,null,"Professional"]
[null,null,"Semi professional"]
[null,null,"Support staff"]
[null,null,"Intern, junior staff, apprentice"]
[null,"NETWORK OVERHEADS ","Executive manager"]
[null,null,"Senior manager"]
[null,null,"Manager"]
[null,null,"Professional"]
[null,null,"Semi professional"]
[null,null,"Support staff"]
[null,null,"Intern, junior staff, apprentice"]
[null,"TOTAL DIRECT NETWORK LABOUR ","Skilled electrical worker"]
[null,null,"Skilled non electical worker"]
[null,null,"Apprentice"]
[null,null,"Unskilled worker"]

{"sheet":"2.12 Input tables","index":16,"n_rows":82,"n_cols":9,"rows_kept":82,"cut":false,"hidden":false,"merged":[[9,3,9,8],[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"2.12 INPUT TABLES"]
[]
[null,"There is ONE table on this worksheet. It has been sub-grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.12.1 - INPUT TABLES"]
[null,null,null,"DIRECT MATERIAL EXPENDITURE","DIRECT LABOUR EXPENDITURE","CONTRACT EXPENDITURE","OTHER EXPENDITURE","RELATED PARTY CONTRACT EXPENDITURE","RELATED PARTY CONTRACT MARGIN\nEXPENDITURE"]
[null,null,null,"EXPENDITURE ($0's)"]
[null,null,null,"2017","2017","2017","2017","2017","2017"]
[null,"VEGETATION MANAGEMENT","HBRA",7168.9978530809412,3434687.3989175661,26713736.397006392,581424.0544827634]
[null,null,"LBRA",1601.0821469190585,767083.04108243447,5966090.0029935995,129597.85551723668]
[null,null,"ZONE 3",0,0,0,0]
[null,null,"ZONE 4",0,0,0,0]
[null,null,"ZONE 5",0,0,0,0]
[null,null,"ZONE 6",0,0,0,0]
[null,null,"ZONE 7",0,0,0,0]
[null,null,"ZONE 8",0,0,0,0]
[null,null,"ZONE 9",0,0,0,0]
[null,null,"ZONE 10",0,0,0,0]
[null,null,"ZONE 11",0,0,0,0]
[null,null,"ZONE 12",0,0,0,0]
[null,null,"ZONE 13",0,0,0,0]
[null,null,"ZONE 14",0,0,0,0]
[null,null,"ZONE 15",0,0,0,0]
[null,null,"ZONE 16",0,0,0,0]
[null,null,"ZONE 17",0,0,0,0]
[null,null,"ZONE 18",0,0,0,0]
[null,"ROUTINE MAINTENANCE","Pole top, overhead line & service line maintenance",326730.73533615173,289697.57576702192,22914.136616030071,49380.494827228104]
[null,null,"Pole inspection and treatment",3394568.9300395586,3009812.9237665986,238066.4192348817,513038.64424639707]
[null,null,"Overhead asset inspection",394626.3149224504,349897.55906890286,27675.75962240063,59641.902628681142]
[null,null,"Network underground cable maintenance",0,0,0,0]
[null,null,"Distribution substation equipment & property maintenance",282173.7772302283,250190.90758180039,19789.287574254326,42646.37280775269]
[null,null,"Zone substation equipment maintenance",602525.85917570454,534232.81577890227,42256.079268571215,91062.828973485215]
[null,null,"Zone substation property maintenance",203482.69935775199,180419.0372657238,14270.559417328859,30753.385881276456]
[null,null,"Public lighting maintenance",0,0,0,0]
[null,null,"Scada & network control maintenance",644.24107354640284,571.21983649294589,45.181632385187967,97.367463660912676]
[null,null,"Protection systems maintenance",157798.30724341192,139912.72361176618,11066.641668203505,23848.86896716899]
[null,null,"Subtransmission asset maintenance - for dnsps with dual function assets",0,0,0,0]
[null,null,"Other",0,0,0,0]
[null,"NON-ROUTINE MAINTENANCE","Pole top, overhead line & service line maintenance",476781.7087436766,422741.0838805731,33437.445665883897,72058.469424713039]
[null,null,"Pole inspection and treatment",71401.335027473688,63308.380347832455,5007.4871092344274,10791.250634421789]
[null,null,"Overhead asset inspection",2585376.1666670833,2292337.7782586534,181316.46729190578,390741.18415335001]
[null,null,"Network underground cable maintenance",325772.16678229236,288847.65576799319,22846.910706669671,49235.621436401561]
[null,null,"Distribution substation equipment & property maintenance",690253.7281007187,612017.20581688359,48408.571691767276,104321.59256423968]
[null,null,"Zone substation equipment maintenance",308980.09047326667,273958.87037773995,21669.256176507559,46697.748663388171]
[null,null,"Zone substation property maintenance",257356.43108644278,228186.473234879,18048.808340181218,38895.599769465058]
[null,null,"Public lighting maintenance",0,0,0,0]
[null,null,"SCADA & network control maintenance",69111.988994652638,61278.519290782635,4846.931697441114,10445.250005447762]
[null,null,"Protection systems maintenance",125842.67247491407,111579.0870011615,8825.5431073840864,19019.249691335895]
[null,null,"Subtransmission asset maintenance - for DNSP with dual function assets",0,0,0,0]
[null,null,"Other",0,0,0,0]
[null,"OVERHEADS","Network overheads",-127.65168784884389,60712473.87327607,1314953.902110365,38021053.48101452]
[null,null,"Corporate overheads",53997.35,22372373.641374752,909940.63692105992,10318848.341415273]
[null,"AUGMENTATION","Subtransmission substations, switching stations, zone substations",4152424.9734612862,1450994.7699278141,2766323.9479247094,1709164.0041539236]
[null,null,"Subtransmission lines",1432772.3189762267,500658.08644796046,954505.47649600042,589738.01799989131]
[null,null,"HV feeders",19890608.418738298,6950437.1471434357,13251020.008600665,8187098.4177447045]
[null,null,"Distribution substations",3061016.9101733221,1069620.6567748832,2039233.5653825407,1259933.6417663714]
[null,null,"LV feeders",3482673.8757961821,1216961.5613625976,2320139.245621596,1433490.2773105006]
[null,null,"Other assets",0,0,0,0]
[null,"CONNECTIONS","Simple and complex customer connections",7162321.3447053581,6357600.3454938699,49106059.976618595,5155485.9290048005]
[null,"EMERGENCY RESPONSE","Major storms",30558.128405140138,1424.5091370425175,85874.176977420939,17428.025480396402]
[null,null,"Major event days",30558.128405140138,1424.5091370425175,85874.176977420939,17428.025480396402]
[null,"PUBLIC LIGHTING","All public lighting services",2727350.270690945,379183.48479104083,6164088.8497202601,365780.75903082913]
[null,"METERING","All metering services",6594331.450000002,16546612.342302157,1961593.62,17796889.769999996]
[null,"FEE-BASED SERVICES","All fee-based services",425977.23581540055,2367130.6023886167,4649041.999162457,1594540.950823616]
[null,"QUOTED SERVICES","All quoted services",22990.558930134026,137210.40583732742,63954.690663143403,83529.101338488719]
[null,"REPLACEMENT","Poles",9123305.9669947494,3487649.4464185257,24408156.810336113,3484608.5641191644]
[null,null,"Pole top structures",3990572.6755353236,1525512.6412589464,10676231.179780705,1524182.546460279]
[null,null,"Overhead conductors",2317599.1742303362,885969.7905853556,6200419.4831090756,885197.31333517598]
[null,null,"Underground cables",275963.74277451372,105495.17885303989,738303.23481153359,105403.19758400162]
[null,null,"Service lines",1725457.3321632587,659606.32375023339,4616225.0049866447,659031.21285527269]
[null,null,"Transformers",2167602.8027350404,828629.30853828916,5799124.7145587876,827906.8264666883]
[null,null,"Switchgear",5037615.8107848521,1925775.3776222896,13477451.825543486,1924096.2936580535]
[null,null,"Public lighting",0,0,0,0]
[null,null,"SCADA network control and protection systems",1354934.2608298664,517963.08726379223,3624941.2247790792,517511.47513706301]
[null,null,"Other",2354346.0539520597,900017.35570952436,6298730.7318804273,899232.6303843041]
[null,"NON-NETWORK EXPENDITURE","IT and communications",13544.03,32709927.580000006,333317.21000000002,26633508.711228922]
[null,null,"Motor vehicles",265134.55783158442,148.97261224151308,636431.72311379667,3440697.5292027239]
[null,null,"Buildings and property",88527.62,682856.79999999981,649159.66,7642754.4400000013]
[null,null,"Other",1105278.432168415,225956.42738775848,765131.34688620199,1017993.8707972742]

{"sheet":"4.1 Public lighting","index":17,"n_rows":231,"n_cols":5,"rows_kept":231,"cut":false,"hidden":false,"merged":[[9,2,10,2],[6,1,6,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"4.1 PUBLIC LIGHTING"]
[]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"4.1.1 - DESCRIPTOR METRICS OVER YEAR"]
[null,null,"LIGHT TYPE",null,"VOLUME \n(0's)"]
[null,null,null,null,"2017"]
[null,"POPULATION OF LIGHTS","CC Mercury Vapour 125W",null,395]
[null,null,"CC Mercury Vapour 250W",null,966]
[null,null,"CC Mercury Vapour 400W",null,233]
[null,null,"CC Mercury Vapour 50W",null,217]
[null,null,"CC Mercury Vapour 80W",null,32028]
[null,null,"Compact Flourescent 32W",null,3662]
[null,null,"Compact Flourescent 42W",null,4349]
[null,null,"HP Sodium 100W",null,3158]
[null,null,"HP Sodium 150W",null,21026]
[null,null,"HP Sodium 250W",null,11903]
[null,null,"HP Sodium 400W",null,636]
[null,null,"HP Sodium 50W",null,0]
[null,null,"LED 18W",null,36275]
[null,null,"Metal Halide 100W",null,34]
[null,null,"Metal Halide 150W",null,33]
[null,null,"Metal Halide 70W",null,31]
[null,null,"T5 Fluor 14W",null,29088]
[null,null,"T5 Fluor 24W",null,2719]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"4.1.2 - DESCRIPTOR METRICS ANNUALLY"]
[]
[]
[null,null,null,null,"VOLUMES \n& EXPENDITURE"]
[null,"SERVICE/SERVICE QUALITY ","DESCRIPTOR METRIC","UNITS","2017"]
[null,"LIGHT INSTALLATION","Major road light installation","0's",0]
[null,null,"Minor road light installation","0's",0]
[null,null,"Number of poles installed","0's",2309]
[null,null,"Total cost","$0s",1969723.861561574]
[null,"LIGHT REPLACEMENT","Major road light replacement","0's",1122]
[null,null,"Minor road light replacement","0's",1098]
[null,null,"Number of poles replaced","0's",301]
[null,null,"Total cost","$0s",5328457.4668264296]
[null,"LIGHT MAINTENANCE","Major road light maintenance","0's",2090]
[null,null,"Minor road light maintenance","0's",5219]
[null,null,"Number of poles installed","0's",0]
[null,null,"Total cost","$0s",2338331]
[null,"QUALITY OF SUPPLY","Mean days to rectify/replace public lighting assets","days",1.76]
[null,null,"GSO breaches","0's",33]
[null,null,"GSL payments","$0s",825]
[null,null,"Customer complaints","0's",9]
[]
[]
[null,"4.1.3 - COST METRICS"]
[null,null,null,null,"AVERAGE UNIT COST \n($)"]
[null,"ACTIVITY TYPE","LIGHT TYPE",null,"2017"]
[null,"LIGHT INSTALLATION","Major Road - all light types"]
[null,null,"CC Mercury Vapour 125W"]
[null,null,"CC Mercury Vapour 80W"]
[null,null,"CC Mercury Vapour 50W"]
[null,null,"Compact Fluorescent 32W"]
[null,null,"Compact Fluorescent 42W"]
[null,null,"Fluorescent 20W"]
[null,null,"HP Sodium 100W"]
[null,null,"HP Sodium 50W"]
[null,null,"Metal halide 100W"]
[null,null,"Metal halide 70W"]
[null,null,"T5 Fluor 14W"]
[null,null,"T5 Fluor 24W"]
[null,null,"LED 20W"]
[null,null,"LED 18W"]
[null,null,"Other minor"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"LIGHT REPLACEMENT","Major Road - all light types"]
[null,null,"CC Mercury Vapour 125W"]
[null,null,"CC Mercury Vapour 80W"]
[null,null,"CC Mercury Vapour 50W"]
[null,null,"Compact Fluorescent 32W"]
[null,null,"Compact Fluorescent 42W"]
[null,null,"Fluorescent 20W"]
[null,null,"HP Sodium 100W"]
[null,null,"HP Sodium 50W"]
[null,null,"Metal halide 100W"]
[null,null,"Metal halide 70W"]
[null,null,"T5 Fluor 14W"]
[null,null,"T5 Fluor 24W"]
[null,null,"LED 20W"]
[null,null,"LED 18W"]
[null,null,"Other minor"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"LIGHT MAINTENANCE","Major Road - all light types"]
[null,null,"CC Mercury Vapour 125W"]
[null,null,"CC Mercury Vapour 80W"]
[null,null,"CC Mercury Vapour 50W"]
[null,null,"Compact Fluorescent 32W"]
[null,null,"Compact Fluorescent 42W"]
[null,null,"Fluorescent 20W"]
[null,null,"HP Sodium 100W"]
[null,null,"HP Sodium 50W"]
[null,null,"Metal halide 100W"]
[null,null,"Metal halide 70W"]
[null,null,"T5 Fluor 14W"]
[null,null,"T5 Fluor 24W"]
[null,null,"LED 20W"]
[null,null,"LED 18W"]
[null,null,"Other minor"]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]

{"sheet":"4.2 Metering","index":18,"n_rows":61,"n_cols":5,"rows_kept":61,"cut":false,"hidden":false,"merged":[[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"4.2 METERING"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"4.2.1 - METERING DESCRIPTOR METRIC"]
[null,null,null,"VOLUMES\n(0's)"]
[null,"ASSET CATEGORY","ASSET SUBCATEGORY","2017"]
[null,"Meter Type 4","Single phase meter population ",595374]
[null,null,"Multi phase meter population ",130861]
[null,null,"Current transformer connected meter population ",3985]
[null,null,"Direct connect meter population ",722250]
[null,"Meter Type 5","Single phase meter population ",1029]
[null,null,"Multi phase meter population ",498]
[null,null,"Current transformer connected meter population ",99]
[null,null,"Direct connect meter population ",1428]
[null,"Meter Type 6","Single phase meter population ",15947]
[null,null,"Multi phase meter population ",6264]
[null,null,"Current transformer connected meter population ",146]
[null,null,"Direct connect meter population ",22065]
[]
[]
[null,"4.2.2 - COST METRICS"]
[null,null,null,"VOLUMES\n(0's)","EXPENDITURE\n($0's)"]
[null,"SERVICE SUBCATEGORY","METER TYPE","2017","2017"]
[null,"Meter purchase ","Meter Type 4",53663,4705758.3500000006]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",0,0]
[null,"Meter testing ","Meter Type 4",328,287109.56438321882]
[null,null,"Meter Type 5",3,2626.0021132611478]
[null,null,"Meter Type 6",136,119045.42913450536]
[null,"Meter investigation ","Meter Type 4",2839,2485073.3331828001]
[null,null,"Meter Type 5",4,3501.3361510148648]
[null,null,"Meter Type 6",48,42016.033812178379]
[null,"Scheduled meter reading ","Meter Type 4",0,0]
[null,null,"Meter Type 5",4116,59817.976323342722]
[null,null,"Meter Type 6",71420,1037949.4336766612]
[null,"Special meter reading ","Meter Type 4",51587,1696376.570259158]
[null,null,"Meter Type 5",424,13942.731032816077]
[null,null,"Meter Type 6",10885,357940.15870802593]
[null,"New meter installation ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",0,0]
[null,"Meter replacement ","Meter Type 4",60,19494.372937293731]
[null,null,"Meter Type 5",333,108193.7698019802]
[null,null,"Meter Type 6",5970,1939690.1072607262]
[null,"Meter maintenance ","Meter Type 4",9127,1999599.5715696092]
[null,null,"Meter Type 5",53,11611.567578962342]
[null,null,"Meter Type 6",182,39873.684893795202]
[null,"Remote meter reading ","Meter Type 4",751563,3732959.1592752314]
[null,"Remote meter re-configuration ","Meter Type 4",6666,33109.540724767838]
[null,"Other metering ","Meter Type 4",0,7074357.0495559936]
[null,null,"Meter Type 5",10,857742.02352517797]
[null,null,"Meter Type 6",0,0]
[null,null,"Meter Type 7",0,0]
[null,"IT infrastructure capex ","Meter Type 4",null,1829950.4100000001]
[null,"IT infrastructure opex ","Meter Type 4",null,7983998.8858367503]
[null,"Communications infrastructure capex ","Meter Type 4",null,1823814.5200000012]
[null,"Communications infrastructure opex ","Meter Type 4",null,4633875.564607257]

{"sheet":"4.3 Fee-based services","index":19,"n_rows":479,"n_cols":6,"rows_kept":479,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"4.3 ANCILLARY SERVICES - FEE BASED SERVICES"]
[]
[null,"4.3.1 - COST METRICS FOR FEE-BASED SERVICES"]
[null,null,null,"EXPENDITURE \n($0's)",null,"VOLUMES \n(0's)"]
[null,"SERVICE","SERVICE SUBCATEGORY","2017",null,"2017"]
[null,"Common Fee-Based Services","Energisation",0,"ED_FEE431_00001",0]
[null,null,"De-energisation",0,"ED_FEE431_00002",0]
[null,null,"Re-energisation",0,"ED_FEE431_00003",0]
[null,"Miscellaneous Fee-Based Services","FIELD OFFICER VISITS",2068259.4599999997,"ED_FEE431_00004",206041]
[null,null,"NEW CONNECTIONS",3657181.2639999981,"ED_FEE431_00005",16397]
[null,null,"SERVICE TRUCK VISITS",1844045.0985811881,"ED_FEE431_00006",7191]
[null,null,"METER EQUIPMENT TESTS",1467204.9656089037,"ED_FEE431_00007",11020]
[null,null,null,null,"ED_FEE431_00008"]
[null,null,null,null,"ED_FEE431_00009"]
[null,null,null,null,"ED_FEE431_00010"]
[null,null,null,null,"ED_FEE431_00011"]
[null,null,null,null,"ED_FEE431_00012"]
[null,null,null,"","ED_FEE431_00013",""]
[null,null,null,"","ED_FEE431_00014",""]
[null,null,null,"","ED_FEE431_00015",""]
[null,null,null,"","ED_FEE431_00016",""]
[null,null,null,"","ED_FEE431_00017",""]
[null,null,null,"","ED_FEE431_00018",""]
[null,null,null,"","ED_FEE431_00019",""]
[null,null,null,"","ED_FEE431_00020",""]
[null,null,null,"","ED_FEE431_00021",""]
[null,null,null,"","ED_FEE431_00022",""]
[null,null,null,"","ED_FEE431_00023",""]
[null,null,null,"","ED_FEE431_00024",""]
[null,null,null,"","ED_FEE431_00025",""]
[null,null,null,"","ED_FEE431_00026",""]
[null,null,null,"","ED_FEE431_00027",""]
[null,null,null,"","ED_FEE431_00028",""]
[null,null,null,"","ED_FEE431_00029",""]
[null,null,null,"","ED_FEE431_00030",""]
[null,null,null,"","ED_FEE431_00031",""]
[null,null,null,"","ED_FEE431_00032",""]
[null,null,null,"","ED_FEE431_00033",""]
[null,null,null,"","ED_FEE431_00034",""]
[null,null,null,"","ED_FEE431_00035",""]
[null,null,null,"","ED_FEE431_00036",""]
[null,null,null,"","ED_FEE431_00037",""]
[null,null,null,"","ED_FEE431_00038",""]
[null,null,null,"","ED_FEE431_00039",""]
[null,null,null,"","ED_FEE431_00040",""]
[null,null,null,"","ED_FEE431_00041",""]
[null,null,null,"","ED_FEE431_00042",""]
[null,null,null,"","ED_FEE431_00043",""]
[null,null,null,"","ED_FEE431_00044",""]
[null,null,null,"","ED_FEE431_00045",""]
[null,null,null,"","ED_FEE431_00046",""]
[null,null,null,"","ED_FEE431_00047",""]
[null,null,null,"","ED_FEE431_00048",""]
[null,null,null,"","ED_FEE431_00049",""]
[null,null,null,"","ED_FEE431_00050",""]
[null,null,null,"","ED_FEE431_00051",""]
[null,null,null,"","ED_FEE431_00052",""]
[null,null,null,"","ED_FEE431_00053",""]
[null,null,null,"","ED_FEE431_00054",""]
[null,null,null,"","ED_FEE431_00055",""]
[null,null,null,"","ED_FEE431_00056",""]
[null,null,null,"","ED_FEE431_00057",""]
[null,null,null,"","ED_FEE431_00058",""]
[null,null,null,"","ED_FEE431_00059",""]
[null,null,null,"","ED_FEE431_00060",""]
[null,null,null,"","ED_FEE431_00061",""]
[null,null,null,"","ED_FEE431_00062",""]
[null,null,null,"","ED_FEE431_00063",""]
[null,null,null,"","ED_FEE431_00064",""]
[null,null,null,"","ED_FEE431_00065",""]
[null,null,null,"","ED_FEE431_00066",""]
[null,null,null,"","ED_FEE431_00067",""]
[null,null,null,"","ED_FEE431_00068",""]
[null,null,null,"","ED_FEE431_00069",""]
[null,null,null,"","ED_FEE431_00070",""]
[null,null,null,"","ED_FEE431_00071",""]
[null,null,null,"","ED_FEE431_00072",""]
[null,null,null,"","ED_FEE431_00073",""]
[null,null,null,"","ED_FEE431_00074",""]
[null,null,null,"","ED_FEE431_00075",""]
[null,null,null,"","ED_FEE431_00076",""]
[null,null,null,"","ED_FEE431_00077",""]
[null,null,null,"","ED_FEE431_00078",""]
[null,null,null,"","ED_FEE431_00079",""]
[null,null,null,"","ED_FEE431_00080",""]
[null,null,null,"","ED_FEE431_00081",""]
[null,null,null,"","ED_FEE431_00082",""]
[null,null,null,"","ED_FEE431_00083",""]
[null,null,null,"","ED_FEE431_00084",""]
[null,null,null,"","ED_FEE431_00085",""]
[null,null,null,"","ED_FEE431_00086",""]
[null,null,null,"","ED_FEE431_00087",""]
[null,null,null,"","ED_FEE431_00088",""]
[null,null,null,"","ED_FEE431_00089",""]
[null,null,null,"","ED_FEE431_00090",""]
[null,null,null,"","ED_FEE431_00091",""]
[null,null,null,"","ED_FEE431_00092",""]
[null,null,null,"","ED_FEE431_00093",""]
[null,null,null,"","ED_FEE431_00094",""]
[null,null,null,"","ED_FEE431_00095",""]
[null,null,null,"","ED_FEE431_00096",""]
[null,null,null,"","ED_FEE431_00097",""]
[null,null,null,"","ED_FEE431_00098",""]
[null,null,null,"","ED_FEE431_00099",""]
[null,null,null,"","ED_FEE431_00100",""]
[null,null,null,"","ED_FEE431_00101",""]
[null,null,null,"","ED_FEE431_00102",""]
[null,null,null,"","ED_FEE431_00103",""]
[null,null,null,"","ED_FEE431_00104",""]
[null,null,null,"","ED_FEE431_00105",""]
[null,null,null,"","ED_FEE431_00106",""]
[null,null,null,"","ED_FEE431_00107",""]
[null,null,null,"","ED_FEE431_00108",""]
[null,null,null,"","ED_FEE431_00109",""]
[null,null,null,"","ED_FEE431_00110",""]
[null,null,null,"","ED_FEE431_00111",""]
[null,null,null,"","ED_FEE431_00112",""]
[null,null,null,"","ED_FEE431_00113",""]
[null,null,null,"","ED_FEE431_00114",""]
[null,null,null,"","ED_FEE431_00115",""]
[null,null,null,"","ED_FEE431_00116",""]
[null,null,null,"","ED_FEE431_00117",""]
[null,null,null,"","ED_FEE431_00118",""]
[null,null,null,"","ED_FEE431_00119",""]
[null,null,null,"","ED_FEE431_00120",""]
[null,null,null,"","ED_FEE431_00121",""]
[null,null,null,"","ED_FEE431_00122",""]
[null,null,null,"","ED_FEE431_00123",""]
[null,null,null,"","ED_FEE431_00124",""]
[null,null,null,"","ED_FEE431_00125",""]
[null,null,null,"","ED_FEE431_00126",""]
[null,null,null,"","ED_FEE431_00127",""]
[null,null,null,"","ED_FEE431_00128",""]
[null,null,null,"","ED_FEE431_00129",""]
[null,null,null,"","ED_FEE431_00130",""]
[null,null,null,"","ED_FEE431_00131",""]
[null,null,null,"","ED_FEE431_00132",""]
[null,null,null,"","ED_FEE431_00133",""]
[null,null,null,"","ED_FEE431_00134",""]
[null,null,null,"","ED_FEE431_00135",""]
[null,null,null,"","ED_FEE431_00136",""]
[null,null,null,"","ED_FEE431_00137",""]
[null,null,null,"","ED_FEE431_00138",""]
[null,null,null,"","ED_FEE431_00139",""]
[null,null,null,"","ED_FEE431_00140",""]
[null,null,null,"","ED_FEE431_00141",""]
[null,null,null,"","ED_FEE431_00142",""]
[null,null,null,"","ED_FEE431_00143",""]
[null,null,null,"","ED_FEE431_00144",""]
[null,null,null,"","ED_FEE431_00145",""]
[null,null,null,"","ED_FEE431_00146",""]
[null,null,null,"","ED_FEE431_00147",""]
[null,null,null,"","ED_FEE431_00148",""]
[null,null,null,"","ED_FEE431_00149",""]
[null,null,null,"","ED_FEE431_00150",""]
[null,null,null,"","ED_FEE431_00151",""]
[null,null,null,"","ED_FEE431_00152",""]
[null,null,null,"","ED_FEE431_00153",""]
[null,null,null,"","ED_FEE431_00154",""]
[null,null,null,"","ED_FEE431_00155",""]
[null,null,null,"","ED_FEE431_00156",""]
[null,null,null,"","ED_FEE431_00157",""]
[null,null,null,"","ED_FEE431_00158",""]
[null,null,null,"","ED_FEE431_00159",""]
[null,null,null,"","ED_FEE431_00160",""]
[null,null,null,"","ED_FEE431_00161",""]
[null,null,null,"","ED_FEE431_00162",""]
[null,null,null,"","ED_FEE431_00163",""]
[null,null,null,"","ED_FEE431_00164",""]
[null,null,null,"","ED_FEE431_00165",""]
[null,null,null,"","ED_FEE431_00166",""]
[null,null,null,"","ED_FEE431_00167",""]
[null,null,null,"","ED_FEE431_00168",""]
[null,null,null,"","ED_FEE431_00169",""]
[null,null,null,"","ED_FEE431_00170",""]
[null,null,null,"","ED_FEE431_00171",""]
[null,null,null,"","ED_FEE431_00172",""]
[null,null,null,"","ED_FEE431_00173",""]
[null,null,null,"","ED_FEE431_00174",""]
[null,null,null,"","ED_FEE431_00175",""]
[null,null,null,"","ED_FEE431_00176",""]
[null,null,null,"","ED_FEE431_00177",""]
[null,null,null,"","ED_FEE431_00178",""]
[null,null,null,"","ED_FEE431_00179",""]
[null,null,null,"","ED_FEE431_00180",""]
[null,null,null,"","ED_FEE431_00181",""]
[null,null,null,"","ED_FEE431_00182",""]
[null,null,null,"","ED_FEE431_00183",""]
[null,null,null,"","ED_FEE431_00184",""]
[null,null,null,"","ED_FEE431_00185",""]
[null,null,null,"","ED_FEE431_00186",""]
[null,null,null,"","ED_FEE431_00187",""]
[null,null,null,"","ED_FEE431_00188",""]
[null,null,null,"","ED_FEE431_00189",""]
[null,null,null,"","ED_FEE431_00190",""]
[null,null,null,"","ED_FEE431_00191",""]
[null,null,null,"","ED_FEE431_00192",""]
[null,null,null,"","ED_FEE431_00193",""]
[null,null,null,"","ED_FEE431_00194",""]
[null,null,null,"","ED_FEE431_00195",""]
[null,null,null,"","ED_FEE431_00196",""]
[null,null,null,"","ED_FEE431_00197",""]
[null,null,null,"","ED_FEE431_00198",""]
[null,null,null,"","ED_FEE431_00199",""]
[null,null,null,"","ED_FEE431_00200",""]
[null,null,null,"","ED_FEE431_00201",""]
[null,null,null,"","ED_FEE431_00202",""]
[null,null,null,"","ED_FEE431_00203",""]
[null,null,null,"","ED_FEE431_00204",""]
[null,null,null,"","ED_FEE431_00205",""]
[null,null,null,"","ED_FEE431_00206",""]
[null,null,null,"","ED_FEE431_00207",""]
[null,null,null,"","ED_FEE431_00208",""]
[null,null,null,"","ED_FEE431_00209",""]
[null,null,null,"","ED_FEE431_00210",""]
[null,null,null,"","ED_FEE431_00211",""]
[null,null,null,"","ED_FEE431_00212",""]
[null,null,null,"","ED_FEE431_00213",""]
[null,null,null,"","ED_FEE431_00214",""]
[null,null,null,"","ED_FEE431_00215",""]
[null,null,null,"","ED_FEE431_00216",""]
[null,null,null,"","ED_FEE431_00217",""]
[null,null,null,"","ED_FEE431_00218",""]
[null,null,null,"","ED_FEE431_00219",""]
[null,null,null,"","ED_FEE431_00220",""]
[null,null,null,"","ED_FEE431_00221",""]
[null,null,null,"","ED_FEE431_00222",""]
[null,null,null,"","ED_FEE431_00223",""]
[null,null,null,"","ED_FEE431_00224",""]
[null,null,null,"","ED_FEE431_00225",""]
[null,null,null,"","ED_FEE431_00226",""]
[null,null,null,"","ED_FEE431_00227",""]
[null,null,null,"","ED_FEE431_00228",""]
[null,null,null,"","ED_FEE431_00229",""]
[null,null,null,"","ED_FEE431_00230",""]
[null,null,null,"","ED_FEE431_00231",""]
[null,null,null,"","ED_FEE431_00232",""]
[null,null,null,null,"ED_FEE431_00233"]
[null,null,null,"","ED_FEE431_00234",""]
[null,null,null,"","ED_FEE431_00235",""]
[null,null,null,"","ED_FEE431_00236",""]
[null,null,null,"","ED_FEE431_00237",""]
[null,null,null,"","ED_FEE431_00238",""]
[null,null,null,"","ED_FEE431_00239",""]
[null,null,null,"","ED_FEE431_00240",""]
[null,null,null,"","ED_FEE431_00241",""]
[null,null,null,"","ED_FEE431_00242",""]
[null,null,null,"","ED_FEE431_00243",""]
[null,null,null,"","ED_FEE431_00244",""]
[null,null,null,"","ED_FEE431_00245",""]
[null,null,null,"","ED_FEE431_00246",""]
[null,null,null,"","ED_FEE431_00247",""]
[null,null,null,"","ED_FEE431_00248",""]
[null,null,null,"","ED_FEE431_00249",""]
[null,null,null,"","ED_FEE431_00250",""]
[null,null,null,"","ED_FEE431_00251",""]
[null,null,null,"","ED_FEE431_00252",""]
[null,null,null,"","ED_FEE431_00253",""]
[null,null,null,"","ED_FEE431_00254",""]
[null,null,null,"","ED_FEE431_00255",""]
[null,null,null,"","ED_FEE431_00256",""]
[null,null,null,"","ED_FEE431_00257",""]
[null,null,null,"","ED_FEE431_00258",""]
[null,null,null,"","ED_FEE431_00259",""]
[null,null,null,"","ED_FEE431_00260",""]
[null,null,null,"","ED_FEE431_00261",""]
[null,null,null,"","ED_FEE431_00262",""]
[null,null,null,"","ED_FEE431_00263",""]
[null,null,null,"","ED_FEE431_00264",""]
[null,null,null,"","ED_FEE431_00265",""]
[null,null,null,"","ED_FEE431_00266",""]
[null,null,null,"","ED_FEE431_00267",""]
[null,null,null,"","ED_FEE431_00268",""]
[null,null,null,"","ED_FEE431_00269",""]
[null,null,null,"","ED_FEE431_00270",""]
[null,null,null,"","ED_FEE431_00271",""]
[null,null,null,"","ED_FEE431_00272",""]
[null,null,null,"","ED_FEE431_00273",""]
[null,null,null,"","ED_FEE431_00274",""]
[null,null,null,"","ED_FEE431_00275",""]
[null,null,null,"","ED_FEE431_00276",""]
[null,null,null,"","ED_FEE431_00277",""]
[null,null,null,"","ED_FEE431_00278",""]
[null,null,null,"","ED_FEE431_00279",""]
[null,null,null,"","ED_FEE431_00280",""]
[null,null,null,"","ED_FEE431_00281",""]
[null,null,null,"","ED_FEE431_00282",""]
[null,null,null,"","ED_FEE431_00283",""]
[null,null,null,"","ED_FEE431_00284",""]
[null,null,null,"","ED_FEE431_00285",""]
[null,null,null,"","ED_FEE431_00286",""]
[null,null,null,"","ED_FEE431_00287",""]
[null,null,null,"","ED_FEE431_00288",""]
[null,null,null,"","ED_FEE431_00289",""]
[null,null,null,"","ED_FEE431_00290",""]
[null,null,null,"","ED_FEE431_00291",""]
[null,null,null,"","ED_FEE431_00292",""]
[null,null,null,"","ED_FEE431_00293",""]
[null,null,null,"","ED_FEE431_00294",""]
[null,null,null,"","ED_FEE431_00295",""]
[null,null,null,"","ED_FEE431_00296",""]
[null,null,null,"","ED_FEE431_00297",""]
[null,null,null,"","ED_FEE431_00298",""]
[null,null,null,"","ED_FEE431_00299",""]
[null,null,null,"","ED_FEE431_00300",""]
[null,null,null,"","ED_FEE431_00301",""]
[null,null,null,"","ED_FEE431_00302",""]
[null,null,null,"","ED_FEE431_00303",""]
[null,null,null,"","ED_FEE431_00304",""]
[null,null,null,"","ED_FEE431_00305",""]
[null,null,null,"","ED_FEE431_00306",""]
[null,null,null,"","ED_FEE431_00307",""]
[null,null,null,"","ED_FEE431_00308",""]
[null,null,null,"","ED_FEE431_00309",""]
[null,null,null,"","ED_FEE431_00310",""]
[null,null,null,"","ED_FEE431_00311",""]
[null,null,null,"","ED_FEE431_00312",""]
[null,null,null,"","ED_FEE431_00313",""]
[null,null,null,"","ED_FEE431_00314",""]
[null,null,null,"","ED_FEE431_00315",""]
[null,null,null,"","ED_FEE431_00316",""]
[null,null,null,"","ED_FEE431_00317",""]
[null,null,null,"","ED_FEE431_00318",""]
[null,null,null,"","ED_FEE431_00319",""]
[null,null,null,"","ED_FEE431_00320",""]
[null,null,null,"","ED_FEE431_00321",""]
[null,null,null,"","ED_FEE431_00322",""]
[null,null,null,"","ED_FEE431_00323",""]
[null,null,null,"","ED_FEE431_00324",""]
[null,null,null,"","ED_FEE431_00325",""]
[null,null,null,"","ED_FEE431_00326",""]
[null,null,null,"","ED_FEE431_00327",""]
[null,null,null,"","ED_FEE431_00328",""]
[null,null,null,"","ED_FEE431_00329",""]
[null,null,null,"","ED_FEE431_00330",""]
[null,null,null,"","ED_FEE431_00331",""]
[null,null,null,"","ED_FEE431_00332",""]
[null,null,null,"","ED_FEE431_00333",""]
[null,null,null,"","ED_FEE431_00334",""]
[null,null,null,"","ED_FEE431_00335",""]
[null,null,null,"","ED_FEE431_00336",""]
[null,null,null,"","ED_FEE431_00337",""]
[null,null,null,"","ED_FEE431_00338",""]
[null,null,null,"","ED_FEE431_00339",""]
[null,null,null,"","ED_FEE431_00340",""]
[null,null,null,"","ED_FEE431_00341",""]
[null,null,null,"","ED_FEE431_00342",""]
[null,null,null,"","ED_FEE431_00343",""]
[null,null,null,"","ED_FEE431_00344",""]
[null,null,null,"","ED_FEE431_00345",""]
[null,null,null,"","ED_FEE431_00346",""]
[null,null,null,"","ED_FEE431_00347",""]
[null,null,null,"","ED_FEE431_00348",""]
[null,null,null,"","ED_FEE431_00349",""]
[null,null,null,"","ED_FEE431_00350",""]
[null,null,null,"","ED_FEE431_00351",""]
[null,null,null,"","ED_FEE431_00352",""]
[null,null,null,"","ED_FEE431_00353",""]
[null,null,null,"","ED_FEE431_00354",""]
[null,null,null,"","ED_FEE431_00355",""]
[null,null,null,"","ED_FEE431_00356",""]
[null,null,null,"","ED_FEE431_00357",""]
[null,null,null,"","ED_FEE431_00358",""]
[null,null,null,"","ED_FEE431_00359",""]
[null,null,null,"","ED_FEE431_00360",""]
[null,null,null,"","ED_FEE431_00361",""]
[null,null,null,"","ED_FEE431_00362",""]
[null,null,null,"","ED_FEE431_00363",""]
[null,null,null,"","ED_FEE431_00364",""]
[null,null,null,"","ED_FEE431_00365",""]
[null,null,null,"","ED_FEE431_00366",""]
[null,null,null,"","ED_FEE431_00367",""]
[null,null,null,"","ED_FEE431_00368",""]
[null,null,null,"","ED_FEE431_00369",""]
[null,null,null,"","ED_FEE431_00370",""]
[null,null,null,"","ED_FEE431_00371",""]
[null,null,null,"","ED_FEE431_00372",""]
[null,null,null,"","ED_FEE431_00373",""]
[null,null,null,"","ED_FEE431_00374",""]
[null,null,null,"","ED_FEE431_00375",""]
[null,null,null,"","ED_FEE431_00376",""]
[null,null,null,"","ED_FEE431_00377",""]
[null,null,null,"","ED_FEE431_00378",""]
[null,null,null,"","ED_FEE431_00379",""]
[null,null,null,"","ED_FEE431_00380",""]
[null,null,null,"","ED_FEE431_00381",""]
[null,null,null,"","ED_FEE431_00382",""]
[null,null,null,"","ED_FEE431_00383",""]
[null,null,null,"","ED_FEE431_00384",""]
[null,null,null,"","ED_FEE431_00385",""]
[null,null,null,"","ED_FEE431_00386",""]
[null,null,null,"","ED_FEE431_00387",""]
[null,null,null,"","ED_FEE431_00388",""]
[null,null,null,"","ED_FEE431_00389",""]
[null,null,null,"","ED_FEE431_00390",""]
[null,null,null,"","ED_FEE431_00391",""]
[null,null,null,"","ED_FEE431_00392",""]
[null,null,null,"","ED_FEE431_00393",""]
[null,null,null,"","ED_FEE431_00394",""]
[null,null,null,"","ED_FEE431_00395",""]
[null,null,null,"","ED_FEE431_00396",""]
[null,null,null,"","ED_FEE431_00397",""]
[null,null,null,"","ED_FEE431_00398",""]
[null,null,null,"","ED_FEE431_00399",""]
[null,null,null,"","ED_FEE431_00400",""]
[null,null,null,"","ED_FEE431_00401",""]
[null,null,null,"","ED_FEE431_00402",""]
[null,null,null,"","ED_FEE431_00403",""]
[null,null,null,"","ED_FEE431_00404",""]
[null,null,null,"","ED_FEE431_00405",""]
[null,null,null,"","ED_FEE431_00406",""]
[null,null,null,"","ED_FEE431_00407",""]
[null,null,null,"","ED_FEE431_00408",""]
[null,null,null,"","ED_FEE431_00409",""]
[null,null,null,"","ED_FEE431_00410",""]
[null,null,null,"","ED_FEE431_00411",""]
[null,null,null,"","ED_FEE431_00412",""]
[null,null,null,"","ED_FEE431_00413",""]
[null,null,null,"","ED_FEE431_00414",""]
[null,null,null,"","ED_FEE431_00415",""]
[null,null,null,"","ED_FEE431_00416",""]
[null,null,null,"","ED_FEE431_00417",""]
[null,null,null,"","ED_FEE431_00418",""]
[null,null,null,"","ED_FEE431_00419",""]
[null,null,null,"","ED_FEE431_00420",""]
[null,null,null,"","ED_FEE431_00421",""]
[null,null,null,"","ED_FEE431_00422",""]
[null,null,null,"","ED_FEE431_00423",""]
[null,null,null,"","ED_FEE431_00424",""]
[null,null,null,"","ED_FEE431_00425",""]
[null,null,null,"","ED_FEE431_00426",""]
[null,null,null,"","ED_FEE431_00427",""]
[null,null,null,"","ED_FEE431_00428",""]
[null,null,null,"","ED_FEE431_00429",""]
[null,null,null,"","ED_FEE431_00430",""]
[null,null,null,"","ED_FEE431_00431",""]
[null,null,null,"","ED_FEE431_00432",""]
[null,null,null,"","ED_FEE431_00433",""]
[null,null,null,"","ED_FEE431_00434",""]
[null,null,null,"","ED_FEE431_00435",""]
[null,null,null,"","ED_FEE431_00436",""]
[null,null,null,"","ED_FEE431_00437",""]
[null,null,null,"","ED_FEE431_00438",""]
[null,null,null,"","ED_FEE431_00439",""]
[null,null,null,"","ED_FEE431_00440",""]
[null,null,null,"","ED_FEE431_00441",""]
[null,null,null,"","ED_FEE431_00442",""]
[null,null,null,"","ED_FEE431_00443",""]
[null,null,null,"","ED_FEE431_00444",""]
[null,null,null,"","ED_FEE431_00445",""]
[null,null,null,"","ED_FEE431_00446",""]
[null,null,null,"","ED_FEE431_00447",""]
[null,null,null,"","ED_FEE431_00448",""]
[null,null,null,"","ED_FEE431_00449",""]
[null,null,null,"","ED_FEE431_00450",""]
[null,null,null,"","ED_FEE431_00451",""]
[null,null,null,"","ED_FEE431_00452",""]
[null,null,null,"","ED_FEE431_00453",""]
[null,null,null,"","ED_FEE431_00454",""]
[null,null,null,"","ED_FEE431_00455",""]
[null,null,null,"","ED_FEE431_00456",""]
[null,null,null,"","ED_FEE431_00457",""]
[null,null,null,"","ED_FEE431_00458",""]
[null,null,null,"","ED_FEE431_00459",""]
[null,null,null,"","ED_FEE431_00460",""]
[null,null,null,"","ED_FEE431_00461",""]
[null,null,null,"","ED_FEE431_00462",""]
[null,null,null,"","ED_FEE431_00463",""]
[null,null,null,"","ED_FEE431_00464",""]
[null,null,null,"","ED_FEE431_00465",""]
[null,null,null,"","ED_FEE431_00466",""]
[null,null,null,"","ED_FEE431_00467",""]
[null,null,null,"","ED_FEE431_00468",""]
[null,null,null,"","ED_FEE431_00469",""]
[null,null,null,"","ED_FEE431_00470",""]
[null,null,null,"","ED_FEE431_00471",""]

{"sheet":"4.4 Quoted services","index":20,"n_rows":481,"n_cols":6,"rows_kept":481,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"4.4 ANCILLARY SERVICES - QUOTED SERVICES"]
[]
[null,"4.4.1 - COST METRICS FOR QUOTED SERVICES"]
[null,null,null,"EXPENDITURE \n($0's)",null,"VOLUMES \n(0's)"]
[null,"SERVICE","SERVICE SUBCATEGORY","2017",null,"2017"]
[null,"Quoted Services ","Recoverable Works",307684.75676909363,"ED_QUO441_00001",122]
[null,null,null,null,"ED_QUO441_00002"]
[null,null,null,null,"ED_QUO441_00003"]
[null,null,null,null,"ED_QUO441_00004"]
[null,null,null,null,"ED_QUO441_00005"]
[null,null,null,null,"ED_QUO441_00006"]
[null,null,null,null,"ED_QUO441_00007"]
[null,null,null,null,"ED_QUO441_00008"]
[null,null,null,null,"ED_QUO441_00009"]
[null,null,null,null,"ED_QUO441_00010"]
[null,null,null,null,"ED_QUO441_00011"]
[null,null,null,null,"ED_QUO441_00012"]
[null,null,null,null,"ED_QUO441_00013"]
[null,null,null,null,"ED_QUO441_00014"]
[null,null,null,null,"ED_QUO441_00015"]
[null,null,null,null,"ED_QUO441_00016"]
[null,null,null,null,"ED_QUO441_00017"]
[null,null,null,null,"ED_QUO441_00018"]
[null,null,null,null,"ED_QUO441_00019"]
[null,null,null,null,"ED_QUO441_00020"]
[null,null,null,null,"ED_QUO441_00021"]
[null,null,null,null,"ED_QUO441_00022"]
[null,null,null,null,"ED_QUO441_00023"]
[null,null,null,null,"ED_QUO441_00024"]
[null,null,null,null,"ED_QUO441_00025"]
[null,null,null,null,"ED_QUO441_00026"]
[null,null,null,null,"ED_QUO441_00027"]
[null,null,null,null,"ED_QUO441_00028"]
[null,null,null,null,"ED_QUO441_00029"]
[null,null,null,null,"ED_QUO441_00030"]
[null,null,null,null,"ED_QUO441_00031"]
[null,null,null,null,"ED_QUO441_00032"]
[null,null,null,null,"ED_QUO441_00033"]
[null,null,null,"","ED_QUO441_00034",""]
[null,null,null,"","ED_QUO441_00035",""]
[null,null,null,"","ED_QUO441_00036",""]
[null,null,null,"","ED_QUO441_00037",""]
[null,null,null,"","ED_QUO441_00038",""]
[null,null,null,"","ED_QUO441_00039",""]
[null,null,null,"","ED_QUO441_00040",""]
[null,null,null,"","ED_QUO441_00041",""]
[null,null,null,"","ED_QUO441_00042",""]
[null,null,null,"","ED_QUO441_00043",""]
[null,null,null,"","ED_QUO441_00044",""]
[null,null,null,"","ED_QUO441_00045",""]
[null,null,null,"","ED_QUO441_00046",""]
[null,null,null,"","ED_QUO441_00047",""]
[null,null,null,"","ED_QUO441_00048",""]
[null,null,null,"","ED_QUO441_00049",""]
[null,null,null,"","ED_QUO441_00050",""]
[null,null,null,"","ED_QUO441_00051",""]
[null,null,null,"","ED_QUO441_00052",""]
[null,null,null,"","ED_QUO441_00053",""]
[null,null,null,"","ED_QUO441_00054",""]
[null,null,null,"","ED_QUO441_00055",""]
[null,null,null,"","ED_QUO441_00056",""]
[null,null,null,"","ED_QUO441_00057",""]
[null,null,null,"","ED_QUO441_00058",""]
[null,null,null,"","ED_QUO441_00059",""]
[null,null,null,"","ED_QUO441_00060",""]
[null,null,null,"","ED_QUO441_00061",""]
[null,null,null,"","ED_QUO441_00062",""]
[null,null,null,"","ED_QUO441_00063",""]
[null,null,null,"","ED_QUO441_00064",""]
[null,null,null,"","ED_QUO441_00065",""]
[null,null,null,"","ED_QUO441_00066",""]
[null,null,null,"","ED_QUO441_00067",""]
[null,null,null,"","ED_QUO441_00068",""]
[null,null,null,"","ED_QUO441_00069",""]
[null,null,null,"","ED_QUO441_00070",""]
[null,null,null,"","ED_QUO441_00071",""]
[null,null,null,"","ED_QUO441_00072",""]
[null,null,null,"","ED_QUO441_00073",""]
[null,null,null,"","ED_QUO441_00074",""]
[null,null,null,"","ED_QUO441_00075",""]
[null,null,null,"","ED_QUO441_00076",""]
[null,null,null,"","ED_QUO441_00077",""]
[null,null,null,"","ED_QUO441_00078",""]
[null,null,null,"","ED_QUO441_00079",""]
[null,null,null,"","ED_QUO441_00080",""]
[null,null,null,"","ED_QUO441_00081",""]
[null,null,null,"","ED_QUO441_00082",""]
[null,null,null,"","ED_QUO441_00083",""]
[null,null,null,"","ED_QUO441_00084",""]
[null,null,null,"","ED_QUO441_00085",""]
[null,null,null,"","ED_QUO441_00086",""]
[null,null,null,"","ED_QUO441_00087",""]
[null,null,null,"","ED_QUO441_00088",""]
[null,null,null,"","ED_QUO441_00089",""]
[null,null,null,"","ED_QUO441_00090",""]
[null,null,null,"","ED_QUO441_00091",""]
[null,null,null,"","ED_QUO441_00092",""]
[null,null,null,"","ED_QUO441_00093",""]
[null,null,null,"","ED_QUO441_00094",""]
[null,null,null,"","ED_QUO441_00095",""]
[null,null,null,"","ED_QUO441_00096",""]
[null,null,null,"","ED_QUO441_00097",""]
[null,null,null,"","ED_QUO441_00098",""]
[null,null,null,"","ED_QUO441_00099",""]
[null,null,null,"","ED_QUO441_00100",""]
[null,null,null,"","ED_QUO441_00101",""]
[null,null,null,"","ED_QUO441_00102",""]
[null,null,null,"","ED_QUO441_00103",""]
[null,null,null,"","ED_QUO441_00104",""]
[null,null,null,"","ED_QUO441_00105",""]
[null,null,null,"","ED_QUO441_00106",""]
[null,null,null,"","ED_QUO441_00107",""]
[null,null,null,"","ED_QUO441_00108",""]
[null,null,null,"","ED_QUO441_00109",""]
[null,null,null,"","ED_QUO441_00110",""]
[null,null,null,"","ED_QUO441_00111",""]
[null,null,null,"","ED_QUO441_00112",""]
[null,null,null,"","ED_QUO441_00113",""]
[null,null,null,"","ED_QUO441_00114",""]
[null,null,null,"","ED_QUO441_00115",""]
[null,null,null,"","ED_QUO441_00116",""]
[null,null,null,"","ED_QUO441_00117",""]
[null,null,null,"","ED_QUO441_00118",""]
[null,null,null,"","ED_QUO441_00119",""]
[null,null,null,"","ED_QUO441_00120",""]
[null,null,null,"","ED_QUO441_00121",""]
[null,null,null,"","ED_QUO441_00122",""]
[null,null,null,"","ED_QUO441_00123",""]
[null,null,null,"","ED_QUO441_00124",""]
[null,null,null,"","ED_QUO441_00125",""]
[null,null,null,"","ED_QUO441_00126",""]
[null,null,null,"","ED_QUO441_00127",""]
[null,null,null,"","ED_QUO441_00128",""]
[null,null,null,"","ED_QUO441_00129",""]
[null,null,null,"","ED_QUO441_00130",""]
[null,null,null,"","ED_QUO441_00131",""]
[null,null,null,"","ED_QUO441_00132",""]
[null,null,null,"","ED_QUO441_00133",""]
[null,null,null,"","ED_QUO441_00134",""]
[null,null,null,"","ED_QUO441_00135",""]
[null,null,null,"","ED_QUO441_00136",""]
[null,null,null,"","ED_QUO441_00137",""]
[null,null,null,"","ED_QUO441_00138",""]
[null,null,null,"","ED_QUO441_00139",""]
[null,null,null,"","ED_QUO441_00140",""]
[null,null,null,"","ED_QUO441_00141",""]
[null,null,null,"","ED_QUO441_00142",""]
[null,null,null,"","ED_QUO441_00143",""]
[null,null,null,"","ED_QUO441_00144",""]
[null,null,null,"","ED_QUO441_00145",""]
[null,null,null,"","ED_QUO441_00146",""]
[null,null,null,"","ED_QUO441_00147",""]
[null,null,null,"","ED_QUO441_00148",""]
[null,null,null,"","ED_QUO441_00149",""]
[null,null,null,"","ED_QUO441_00150",""]
[null,null,null,"","ED_QUO441_00151",""]
[null,null,null,"","ED_QUO441_00152",""]
[null,null,null,"","ED_QUO441_00153",""]
[null,null,null,"","ED_QUO441_00154",""]
[null,null,null,"","ED_QUO441_00155",""]
[null,null,null,"","ED_QUO441_00156",""]
[null,null,null,"","ED_QUO441_00157",""]
[null,null,null,"","ED_QUO441_00158",""]
[null,null,null,"","ED_QUO441_00159",""]
[null,null,null,"","ED_QUO441_00160",""]
[null,null,null,"","ED_QUO441_00161",""]
[null,null,null,"","ED_QUO441_00162",""]
[null,null,null,"","ED_QUO441_00163",""]
[null,null,null,"","ED_QUO441_00164",""]
[null,null,null,"","ED_QUO441_00165",""]
[null,null,null,"","ED_QUO441_00166",""]
[null,null,null,"","ED_QUO441_00167",""]
[null,null,null,"","ED_QUO441_00168",""]
[null,null,null,"","ED_QUO441_00169",""]
[null,null,null,"","ED_QUO441_00170",""]
[null,null,null,"","ED_QUO441_00171",""]
[null,null,null,"","ED_QUO441_00172",""]
[null,null,null,"","ED_QUO441_00173",""]
[null,null,null,"","ED_QUO441_00174",""]
[null,null,null,"","ED_QUO441_00175",""]
[null,null,null,"","ED_QUO441_00176",""]
[null,null,null,"","ED_QUO441_00177",""]
[null,null,null,"","ED_QUO441_00178",""]
[null,null,null,"","ED_QUO441_00179",""]
[null,null,null,"","ED_QUO441_00180",""]
[null,null,null,"","ED_QUO441_00181",""]
[null,null,null,"","ED_QUO441_00182",""]
[null,null,null,"","ED_QUO441_00183",""]
[null,null,null,"","ED_QUO441_00184",""]
[null,null,null,"","ED_QUO441_00185",""]
[null,null,null,"","ED_QUO441_00186",""]
[null,null,null,"","ED_QUO441_00187",""]
[null,null,null,"","ED_QUO441_00188",""]
[null,null,null,"","ED_QUO441_00189",""]
[null,null,null,"","ED_QUO441_00190",""]
[null,null,null,"","ED_QUO441_00191",""]
[null,null,null,"","ED_QUO441_00192",""]
[null,null,null,"","ED_QUO441_00193",""]
[null,null,null,"","ED_QUO441_00194",""]
[null,null,null,"","ED_QUO441_00195",""]
[null,null,null,"","ED_QUO441_00196",""]
[null,null,null,"","ED_QUO441_00197",""]
[null,null,null,"","ED_QUO441_00198",""]
[null,null,null,"","ED_QUO441_00199",""]
[null,null,null,"","ED_QUO441_00200",""]
[null,null,null,"","ED_QUO441_00201",""]
[null,null,null,"","ED_QUO441_00202",""]
[null,null,null,"","ED_QUO441_00203",""]
[null,null,null,"","ED_QUO441_00204",""]
[null,null,null,"","ED_QUO441_00205",""]
[null,null,null,"","ED_QUO441_00206",""]
[null,null,null,"","ED_QUO441_00207",""]
[null,null,null,"","ED_QUO441_00208",""]
[null,null,null,"","ED_QUO441_00209",""]
[null,null,null,"","ED_QUO441_00210",""]
[null,null,null,"","ED_QUO441_00211",""]
[null,null,null,"","ED_QUO441_00212",""]
[null,null,null,"","ED_QUO441_00213",""]
[null,null,null,"","ED_QUO441_00214",""]
[null,null,null,"","ED_QUO441_00215",""]
[null,null,null,"","ED_QUO441_00216",""]
[null,null,null,"","ED_QUO441_00217",""]
[null,null,null,"","ED_QUO441_00218",""]
[null,null,null,"","ED_QUO441_00219",""]
[null,null,null,"","ED_QUO441_00220",""]
[null,null,null,"","ED_QUO441_00221",""]
[null,null,null,"","ED_QUO441_00222",""]
[null,null,null,"","ED_QUO441_00223",""]
[null,null,null,"","ED_QUO441_00224",""]
[null,null,null,"","ED_QUO441_00225",""]
[null,null,null,"","ED_QUO441_00226",""]
[null,null,null,"","ED_QUO441_00227",""]
[null,null,null,"","ED_QUO441_00228",""]
[null,null,null,"","ED_QUO441_00229",""]
[null,null,null,"","ED_QUO441_00230",""]
[null,null,null,"","ED_QUO441_00231",""]
[null,null,null,"","ED_QUO441_00232",""]
[null,null,null,"","ED_QUO441_00233",""]
[null,null,null,"","ED_QUO441_00234",""]
[null,null,null,"","ED_QUO441_00235",""]
[null,null,null,"","ED_QUO441_00236",""]
[null,null,null,"","ED_QUO441_00237",""]
[null,null,null,"","ED_QUO441_00238",""]
[null,null,null,"","ED_QUO441_00239",""]
[null,null,null,"","ED_QUO441_00240",""]
[null,null,null,"","ED_QUO441_00241",""]
[null,null,null,"","ED_QUO441_00242",""]
[null,null,null,"","ED_QUO441_00243",""]
[null,null,null,"","ED_QUO441_00244",""]
[null,null,null,"","ED_QUO441_00245",""]
[null,null,null,"","ED_QUO441_00246",""]
[null,null,null,"","ED_QUO441_00247",""]
[null,null,null,"","ED_QUO441_00248",""]
[null,null,null,"","ED_QUO441_00249",""]
[null,null,null,"","ED_QUO441_00250",""]
[null,null,null,"","ED_QUO441_00251",""]
[null,null,null,"","ED_QUO441_00252",""]
[null,null,null,"","ED_QUO441_00253",""]
[null,null,null,"","ED_QUO441_00254",""]
[null,null,null,"","ED_QUO441_00255",""]
[null,null,null,"","ED_QUO441_00256",""]
[null,null,null,"","ED_QUO441_00257",""]
[null,null,null,"","ED_QUO441_00258",""]
[null,null,null,"","ED_QUO441_00259",""]
[null,null,null,"","ED_QUO441_00260",""]
[null,null,null,"","ED_QUO441_00261",""]
[null,null,null,"","ED_QUO441_00262",""]
[null,null,null,"","ED_QUO441_00263",""]
[null,null,null,"","ED_QUO441_00264",""]
[null,null,null,"","ED_QUO441_00265",""]
[null,null,null,"","ED_QUO441_00266",""]
[null,null,null,"","ED_QUO441_00267",""]
[null,null,null,"","ED_QUO441_00268",""]
[null,null,null,"","ED_QUO441_00269",""]
[null,null,null,"","ED_QUO441_00270",""]
[null,null,null,"","ED_QUO441_00271",""]
[null,null,null,"","ED_QUO441_00272",""]
[null,null,null,"","ED_QUO441_00273",""]
[null,null,null,"","ED_QUO441_00274",""]
[null,null,null,"","ED_QUO441_00275",""]
[null,null,null,"","ED_QUO441_00276",""]
[null,null,null,"","ED_QUO441_00277",""]
[null,null,null,"","ED_QUO441_00278",""]
[null,null,null,"","ED_QUO441_00279",""]
[null,null,null,"","ED_QUO441_00280",""]
[null,null,null,"","ED_QUO441_00281",""]
[null,null,null,"","ED_QUO441_00282",""]
[null,null,null,"","ED_QUO441_00283",""]
[null,null,null,"","ED_QUO441_00284",""]
[null,null,null,"","ED_QUO441_00285",""]
[null,null,null,"","ED_QUO441_00286",""]
[null,null,null,"","ED_QUO441_00287",""]
[null,null,null,"","ED_QUO441_00288",""]
[null,null,null,"","ED_QUO441_00289",""]
[null,null,null,"","ED_QUO441_00290",""]
[null,null,null,"","ED_QUO441_00291",""]
[null,null,null,"","ED_QUO441_00292",""]
[null,null,null,"","ED_QUO441_00293",""]
[null,null,null,"","ED_QUO441_00294",""]
[null,null,null,"","ED_QUO441_00295",""]
[null,null,null,"","ED_QUO441_00296",""]
[null,null,null,"","ED_QUO441_00297",""]
[null,null,null,"","ED_QUO441_00298",""]
[null,null,null,"","ED_QUO441_00299",""]
[null,null,null,"","ED_QUO441_00300",""]
[null,null,null,"","ED_QUO441_00301",""]
[null,null,null,"","ED_QUO441_00302",""]
[null,null,null,"","ED_QUO441_00303",""]
[null,null,null,"","ED_QUO441_00304",""]
[null,null,null,"","ED_QUO441_00305",""]
[null,null,null,"","ED_QUO441_00306",""]
[null,null,null,"","ED_QUO441_00307",""]
[null,null,null,"","ED_QUO441_00308",""]
[null,null,null,"","ED_QUO441_00309",""]
[null,null,null,"","ED_QUO441_00310",""]
[null,null,null,"","ED_QUO441_00311",""]
[null,null,null,"","ED_QUO441_00312",""]
[null,null,null,"","ED_QUO441_00313",""]
[null,null,null,"","ED_QUO441_00314",""]
[null,null,null,"","ED_QUO441_00315",""]
[null,null,null,"","ED_QUO441_00316",""]
[null,null,null,"","ED_QUO441_00317",""]
[null,null,null,"","ED_QUO441_00318",""]
[null,null,null,"","ED_QUO441_00319",""]
[null,null,null,"","ED_QUO441_00320",""]
[null,null,null,"","ED_QUO441_00321",""]
[null,null,null,"","ED_QUO441_00322",""]
[null,null,null,"","ED_QUO441_00323",""]
[null,null,null,"","ED_QUO441_00324",""]
[null,null,null,"","ED_QUO441_00325",""]
[null,null,null,"","ED_QUO441_00326",""]
[null,null,null,"","ED_QUO441_00327",""]
[null,null,null,"","ED_QUO441_00328",""]
[null,null,null,"","ED_QUO441_00329",""]
[null,null,null,"","ED_QUO441_00330",""]
[null,null,null,"","ED_QUO441_00331",""]
[null,null,null,"","ED_QUO441_00332",""]
[null,null,null,"","ED_QUO441_00333",""]
[null,null,null,"","ED_QUO441_00334",""]
[null,null,null,"","ED_QUO441_00335",""]
[null,null,null,"","ED_QUO441_00336",""]
[null,null,null,"","ED_QUO441_00337",""]
[null,null,null,"","ED_QUO441_00338",""]
[null,null,null,"","ED_QUO441_00339",""]
[null,null,null,"","ED_QUO441_00340",""]
[null,null,null,"","ED_QUO441_00341",""]
[null,null,null,"","ED_QUO441_00342",""]
[null,null,null,"","ED_QUO441_00343",""]
[null,null,null,"","ED_QUO441_00344",""]
[null,null,null,"","ED_QUO441_00345",""]
[null,null,null,"","ED_QUO441_00346",""]
[null,null,null,"","ED_QUO441_00347",""]
[null,null,null,"","ED_QUO441_00348",""]
[null,null,null,"","ED_QUO441_00349",""]
[null,null,null,"","ED_QUO441_00350",""]
[null,null,null,"","ED_QUO441_00351",""]
[null,null,null,"","ED_QUO441_00352",""]
[null,null,null,"","ED_QUO441_00353",""]
[null,null,null,"","ED_QUO441_00354",""]
[null,null,null,"","ED_QUO441_00355",""]
[null,null,null,"","ED_QUO441_00356",""]
[null,null,null,"","ED_QUO441_00357",""]
[null,null,null,"","ED_QUO441_00358",""]
[null,null,null,"","ED_QUO441_00359",""]
[null,null,null,"","ED_QUO441_00360",""]
[null,null,null,"","ED_QUO441_00361",""]
[null,null,null,"","ED_QUO441_00362",""]
[null,null,null,"","ED_QUO441_00363",""]
[null,null,null,"","ED_QUO441_00364",""]
[null,null,null,"","ED_QUO441_00365",""]
[null,null,null,"","ED_QUO441_00366",""]
[null,null,null,"","ED_QUO441_00367",""]
[null,null,null,"","ED_QUO441_00368",""]
[null,null,null,"","ED_QUO441_00369",""]
[null,null,null,"","ED_QUO441_00370",""]
[null,null,null,"","ED_QUO441_00371",""]
[null,null,null,"","ED_QUO441_00372",""]
[null,null,null,"","ED_QUO441_00373",""]
[null,null,null,"","ED_QUO441_00374",""]
[null,null,null,"","ED_QUO441_00375",""]
[null,null,null,"","ED_QUO441_00376",""]
[null,null,null,"","ED_QUO441_00377",""]
[null,null,null,"","ED_QUO441_00378",""]
[null,null,null,"","ED_QUO441_00379",""]
[null,null,null,"","ED_QUO441_00380",""]
[null,null,null,"","ED_QUO441_00381",""]
[null,null,null,"","ED_QUO441_00382",""]
[null,null,null,"","ED_QUO441_00383",""]
[null,null,null,"","ED_QUO441_00384",""]
[null,null,null,"","ED_QUO441_00385",""]
[null,null,null,"","ED_QUO441_00386",""]
[null,null,null,"","ED_QUO441_00387",""]
[null,null,null,"","ED_QUO441_00388",""]
[null,null,null,"","ED_QUO441_00389",""]
[null,null,null,"","ED_QUO441_00390",""]
[null,null,null,"","ED_QUO441_00391",""]
[null,null,null,"","ED_QUO441_00392",""]
[null,null,null,"","ED_QUO441_00393",""]
[null,null,null,"","ED_QUO441_00394",""]
[null,null,null,"","ED_QUO441_00395",""]
[null,null,null,"","ED_QUO441_00396",""]
[null,null,null,"","ED_QUO441_00397",""]
[null,null,null,"","ED_QUO441_00398",""]
[null,null,null,"","ED_QUO441_00399",""]
[null,null,null,"","ED_QUO441_00400",""]
[null,null,null,"","ED_QUO441_00401",""]
[null,null,null,"","ED_QUO441_00402",""]
[null,null,null,"","ED_QUO441_00403",""]
[null,null,null,"","ED_QUO441_00404",""]
[null,null,null,"","ED_QUO441_00405",""]
[null,null,null,"","ED_QUO441_00406",""]
[null,null,null,"","ED_QUO441_00407",""]
[null,null,null,"","ED_QUO441_00408",""]
[null,null,null,"","ED_QUO441_00409",""]
[null,null,null,"","ED_QUO441_00410",""]
[null,null,null,"","ED_QUO441_00411",""]
[null,null,null,"","ED_QUO441_00412",""]
[null,null,null,"","ED_QUO441_00413",""]
[null,null,null,"","ED_QUO441_00414",""]
[null,null,null,"","ED_QUO441_00415",""]
[null,null,null,"","ED_QUO441_00416",""]
[null,null,null,"","ED_QUO441_00417",""]
[null,null,null,"","ED_QUO441_00418",""]
[null,null,null,"","ED_QUO441_00419",""]
[null,null,null,"","ED_QUO441_00420",""]
[null,null,null,"","ED_QUO441_00421",""]
[null,null,null,"","ED_QUO441_00422",""]
[null,null,null,"","ED_QUO441_00423",""]
[null,null,null,"","ED_QUO441_00424",""]
[null,null,null,"","ED_QUO441_00425",""]
[null,null,null,"","ED_QUO441_00426",""]
[null,null,null,"","ED_QUO441_00427",""]
[null,null,null,"","ED_QUO441_00428",""]
[null,null,null,"","ED_QUO441_00429",""]
[null,null,null,"","ED_QUO441_00430",""]
[null,null,null,"","ED_QUO441_00431",""]
[null,null,null,"","ED_QUO441_00432",""]
[null,null,null,"","ED_QUO441_00433",""]
[null,null,null,"","ED_QUO441_00434",""]
[null,null,null,"","ED_QUO441_00435",""]
[null,null,null,"","ED_QUO441_00436",""]
[null,null,null,"","ED_QUO441_00437",""]
[null,null,null,"","ED_QUO441_00438",""]
[null,null,null,"","ED_QUO441_00439",""]
[null,null,null,"","ED_QUO441_00440",""]
[null,null,null,"","ED_QUO441_00441",""]
[null,null,null,"","ED_QUO441_00442",""]
[null,null,null,"","ED_QUO441_00443",""]
[null,null,null,"","ED_QUO441_00444",""]
[null,null,null,"","ED_QUO441_00445",""]
[null,null,null,"","ED_QUO441_00446",""]
[null,null,null,"","ED_QUO441_00447",""]
[null,null,null,"","ED_QUO441_00448",""]
[null,null,null,"","ED_QUO441_00449",""]
[null,null,null,"","ED_QUO441_00450",""]
[null,null,null,"","ED_QUO441_00451",""]
[null,null,null,"","ED_QUO441_00452",""]
[null,null,null,"","ED_QUO441_00453",""]
[null,null,null,"","ED_QUO441_00454",""]
[null,null,null,"","ED_QUO441_00455",""]
[null,null,null,"","ED_QUO441_00456",""]
[null,null,null,"","ED_QUO441_00457",""]
[null,null,null,"","ED_QUO441_00458",""]
[null,null,null,"","ED_QUO441_00459",""]
[null,null,null,"","ED_QUO441_00460",""]
[null,null,null,"","ED_QUO441_00461",""]
[null,null,null,"","ED_QUO441_00462",""]
[null,null,null,"","ED_QUO441_00463",""]
[null,null,null,"","ED_QUO441_00464",""]
[null,null,null,"","ED_QUO441_00465",""]
[null,null,null,"","ED_QUO441_00466",""]
[null,null,null,"","ED_QUO441_00467",""]
[null,null,null,"","ED_QUO441_00468",""]
[null,null,null,"","ED_QUO441_00469",""]
[null,null,null,"","ED_QUO441_00470",""]
[null,null,null,"","ED_QUO441_00471",""]
[null,null,null,"","ED_QUO441_00472",""]
[null,null,null,"","ED_QUO441_00473",""]

{"sheet":"5.2 Asset Age Profile","index":21,"n_rows":136,"n_cols":112,"rows_kept":136,"cut":false,"hidden":false,"merged":[[8,3,8,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"5.2 ASSET AGE PROFILE"]
[]
[null,"There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data."]
[]
[null,"5.2.1 - ASSET AGE PROFILE"]
[null,null,null,"ECONOMIC LIFE (YEARS)",null,"INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR"]
[null,"ASSET GROUP","ASSET CATEGORY","MEAN ","STANDARD DEVIATION ","2017",2016,2015,2014,2013,2012,2011,2010,2009,2008,2007,2006,2005,2004,2003,2002,2001,2000,1999,1998,1997,1996,1995,1994,1993,1992,1991,1990,1989,1988,1987,1986,1985,1984,1983,1982,1981,1980,1979,1978,1977,1976,1975,1974,1973,1972,1971,1970,1969,1968,1967,1966,1965,1964,1963,1962,1961,1960,1959,1958,1957,1956,1955,1954,1953,1952,1951,1950,1949,1948,1947,1946,1945,1944,1943,1942,1941,1940,1939,1938,1937,1936,1935,1934,1933,1932,1931,1930,1929,1928,1927,1926,1925,1924,1923,1922,1921,1920,1919,1918,1917,1916,1915,1914,1913,1912,1911]
[null,"POLES BY: \nHIGHEST OPERATING VOLTAGE ; MATERIAL TYPE;  STAKING (IF WOOD)","Staking of a wooden pole",65,8.0622577482985491,2060,1381.5857117842761,900.00350201365779,1233.7950446506741,946.36534757485549,678.54307476799158,347.57292943442479,404.28734022062685,378.0194361758011,481.25196988268254,432.29662055682019,500.03335668009106,923.83417965330068,567.48450358956404,206.02320084048327,114.19252320084048,463.58684993871475,1057.0536683593066,1049.0583085274031,1115.9159516722116,718.28445105935907,508.81474347749958,700.01654701453333,640.96261600420246,555.93101033094024,604.56075993696379,718.5923656102259,1116.6387672911924,1633.5651374540362,437.91708982665034,81.964629662055685,6.1339520224128874,1.0223253370688146,0,0,0,0,0,1.0223253370688146,0,0,0,0,2.0446506741376291,2.2325337068814559E-2,0,1.0223253370688146,1.0223253370688146,1.0446506741376291,3.0669760112064437,4.1116266853440724,1.0223253370688146,2.0446506741376291,1.0223253370688146,0,1.0446506741376291,1.0223253370688146,4.0893013482752583,2.2325337068814559E-2,1.0223253370688146,0,0,0,0,0,0,0,1.0223253370688146,0,0,0,0,0,0,0,0,1.0223253370688146,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 1 kV; Wood",55,7.416198487095663,1339,980.87955683191308,750.71707232867254,683.67037019600457,274.27534799052148,242.26075357406273,157.15275489226809,151.1508089700736,182.17513299750482,338.33080677306469,367.35804968378767,334.32788788977291,389.38334667231612,316.31621235660594,206.20237590822779,210.2082136748113,144.1391334369066,1383.4000910189413,356.34832007281517,238.22475401346452,258.25102396309023,132.13134974812863,90.091458343141412,50.048648054862454,90.088539459849656,50.049621015959701,92.091458343141412,506.49426423740249,695.67426204039361,686.66453242942112,567.55069598104296,1556.5090626618332,1261.23079578802,1412.3709021860238,1180.1480940947538,849.83674654363415,1325.2911193760494,2255.2164053795332,1233.2093906438806,1423.4117665521082,1318.3193352478697,1905.8632205012318,1974.9566247665678,1693.6793308538518,2101.1142444643219,1931.9284088947477,1391.4214961630807,2086.1375955306562,2325.3506740109538,2500.5326177361394,2224.2319727570894,1226.2590116598403,1878.8904634119549,1501.4934952842773,1001.031338763084,1181.207444721686,1143.1704721999906,1265.2920923371466,1023.031338763084,695.71804528976975,990.01771730772248,407.41934623291434,248.26367245735449,220.24713211870124,138.1508089700736,295.30064497904993,175.18097076408833,309.31621235660594,152.16248450324059,117.12551198154513,173.1907003750608,130.14010639800387,54.062269510223935,26.028215871820223,32.033080677306465,92.090485382044164,247.24615915760401,249.24907804089574,305.29967201795267,569.55653374762642,322.30940162892517,333.32983381196743,233.22572697456178,264.26075357406273,145.13426863142035,26.025296988528474,9.0097296109724905,32.032107716209218,12.011675533166988,30.028215871820223,0,38.039891404987209,0,0,0,0,0,9.7296109724903082E-4,0,0,0,0,0,0,0,0,1.0009729610972491]
[null,null,"> 1 kV & < = 11 kV; Wood",55,7.416198487095663,8,3,2,5,9,5,12,1,2,7,3,0,2,1,1,0,1,3,3,4,7,6,7,2,2,0,2,6,14,21,10,32,7,17,29,18,20,11,2,9,30,47,43,39,8,4,6,17,8,11,21,10,21,13,10,10,8,26,6,16,5,6,0,5,0,1,1,0,13,0,2,1,0,0,5,2,14,10,28,31,5,3,9,14,6,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; Wood",55,7.416198487095663,1534,1250.2059212106653,934.1639442709585,1014.1855632957003,600.10899591640646,366.06737929377852,357.06647850108095,409.07512611097764,780.14268556329569,1620.2954600048042,1790.3248258467452,1368.2495195772281,1420.2578068700457,1128.2057410521259,789.14250540475621,516.09386259908717,472.08647609896707,1832.3374369445112,713.1307950996877,548.10088878212832,508.09278164785013,252.04594042757626,203.03693250060053,218.03945472015374,539.09728561133795,268.04882296420851,751.13565938025465,1674.3039274561613,1292.2345664184481,1724.3131155416768,1195.2165505644969,3523.6419048762909,2565.4680518856594,3002.5476819601249,2772.5048042277203,2274.4170670189769,3649.6723516694692,3936.7226159019938,1795.3286091760749,3304.6141604612058,4023.7492793658421,3990.7436944511169,3012.5682200336296,2408.4498558731684,1955.3664424693729,2584.4806629834252,3031.5811914484748,2764.543538313716,3602.7018976699496,3239.6165025222194,2870.547321643046,2997.5689406677875,3033.5750660581311,2563.4905717030988,1594.3006846024502,1389.2693370165746,1839.3561734326206,1269.2430338698055,988.19132836896472,696.14070381936108,1319.2617703579149,688.13656017295216,502.09620466010091,609.11638241652656,599.11241892865723,300.05711025702618,193.03639202498198,323.06233485467209,175.0329690127312,318.06305548883017,103.02288013451837,204.03981503723276,66.013331731924097,48.009728561133798,46.008467451357191,123.02269997597887,176.03278885419169,576.10737448955081,445.08413403795339,528.0999879894307,484.09350228200816,552.10196973336531,367.06791976939707,228.04323804948353,249.04864280566898,9.0018015853951479,3.0007206341580592,12.002161902474178,5.0010809512370891,65.011890463607969,1.0001801585395147,10.001801585395148,0,0,1.0001801585395147,0,0,2.0003603170790294,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV; Wood",55,7.416198487095663,33,48.012776831345825,33.011179727427596,84.026511925042584,50.017248722316864,63.017887563884159,37.012137989778537,44.014373935264054,84.027150766609878,100.03194207836457,180.05781516183987,115.03737223168655,126.040566439523,32.010221465076661,30.00958262350937,38.012137989778537,51.01629045996593,141.04599659284497,41.013096252129472,21.007027257240203,11.003513628620102,6.0019165247018735,4.0012776831345827,21.00670783645656,26.007985519591141,5.0015971039182281,21.00670783645656,118.03769165247019,48.015651618398635,35.011499148211243,42.013096252129472,72.022998296422486,86.027789608177173,114.0364139693356,172.05494037478707,119.03864991482112,811.26160562180576,236.07634156729131,261.08464650766609,187.06100936967633,867.27949318568994,1371.4427172061328,244.07985519591142,193.06516183986372,235.09071550255535,241.08017461669505,110.03673339011925,133.04439948892676,292.09838160136286,134.0440800681431,340.11211669505963,174.05749574105621,146.04887137989778,44.01629045996593,71.024275979557075,23.007985519591141,117.03801107325383,24.008304940374789,22.007666098807494,30.00958262350937,54.019804088586028,50.016929301533217,142.04759369676322,3.0009582623509368,12.003833049403747,1.0003194207836457,0,1.0003194207836457,11.003513628620102,6.0019165247018735,1.0006388415672913,1.0003194207836457,7.0025553662691653,0,113.03673339011925,14.00447189097104,26.008304940374789,21.00670783645656,94.030344974446336,86.027470187393533,1.0003194207836457,4.0012776831345827,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV; Wood",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV; Wood",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 1 kV; Concrete",100,10,445,312.52918254243161,306.54009352268793,500.90197436785593,629.14201593349503,492.89651887772777,191.34733287149291,176.31641842743332,198.3600623484586,155.28550398337376,54.103654312435054,50.090924835469345,50.092743332178735,50.090924835469345,25.045462417734672,22.040006927606512,32.058191894700379,178.32732940768963,104.18912365777624,72.130931763075864,116.21094561828887,147.26731901627988,596.08564253550401,714.29658815379287,1283.322220297887,1652.9950640803602,1087.9694319362661,1108.0094388638724,1723.1296328368549,1535.7859369587807,1091.9803429165224,1142.0803602355386,1543.8023034291652,1230.2276584689989,494.90197436785593,147.26550051957048,1070.9512469691722,635.15110841704188,12.021821960512643,785.42751991686873,619.1238309664011,435.79104606858328,179.3200554208521,3.0090924835469344,53.096380325597508,68.123657776238304,3.0054554901281607,26.047280914444059,3.0054554901281607,6.012729476965708,6.0109109802563214,6.0109109802563214,5.0090924835469348,2.0036369934187737,1,5.0090924835469348,2.0054554901281607,1.0018184967093868,3.0054554901281607,1.0036369934187739,2.0036369934187737,2.0036369934187737,0,2.0036369934187737,1.0018184967093868,0,2.0018184967093871,0,1.0018184967093868,0,0,2.0036369934187737,0,0,0,0,0,0,0,2.0036369934187737,2.0036369934187737,2.0036369934187737,1.0018184967093868,0,0,0,0,0,0,1.0018184967093868,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV; Concrete",100,10,5,24,4,7,13,14,5,2,1,1,0,0,0,1,2,1,0,0,3,2,1,0,15,18,15,22,3,5,5,6,4,3,5,21,2,3,6,8,0,4,4,1,0,0,0,0,0,0,5,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; Concrete",100,10,2043,2049.7288365511677,1690.1708862979897,2830.591290213184,2361.6463110872032,1561.0923017552886,1230.4361208237344,1478.9017342392385,1192.3516424403308,736.44792019926797,357.70136704360738,337.66207477225686,372.73476547425537,386.7583408370657,282.55402102604285,217.42632114415352,264.52651643609744,1020.9999766117433,993.95086127255502,1028.0156935202835,1114.1885795142259,941.84870136704365,1927.785810344626,2687.2907043373521,4485.8387964403073,4767.3692421035394,3966.8230912258955,4760.3653128764045,6049.893770537813,4766.3790651713771,4798.4753312361863,4045.9566849484872,4448.7523534433358,4451.7464596026339,2027.9783424742436,864.69742612234393,4106.070632535404,1706.3634184276075,70.137522949726943,1154.2710932840621,836.64831078315581,343.67975629436461,171.34184276074984,21.045186112053138,69.139487563294466,56.113947586916609,16.033398430647971,108.22003671956311,37.082513769836169,16.035363044215501,49.098230678376389,21.045186112053138,29.058938407025831,12.025539976377861,16.035363044215501,22.045186112053138,21.043221498485611,32.060903020593358,3.005893840702583,4.007858454270111,10.021610749242805,10.033398430647972,13.027504589945389,19.037327657783027,3.005893840702583,3.007858454270111,2.005893840702583,11.019646135675277,4.007858454270111,1,6.0117876814051661,1.0019646135675278,0,0,0,0,0,5.0098230678376385,1.0019646135675278,2.005893840702583,6.0117876814051661,0,5.0098230678376385,38.074655315566055,1.0019646135675278,0,0,0,0,4.007858454270111,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV; Concrete",100,10,148,232.22784810126583,395.40717299578057,596.63080168776366,337.35970464135022,132.14240506329114,272.28797468354429,344.36603375527426,222.23628691983123,321.33966244725741,133.14029535864978,205.21729957805908,299.31540084388183,88.092827004219416,53.058016877637129,25.026371308016877,38.036919831223628,171.18143459915612,188.20042194092827,60.063291139240505,79.083333333333329,74.078059071729953,317.3354430379747,210.22151898734177,340.35970464135022,257.27320675105483,187.1993670886076,611.64451476793249,628.66561181434599,593.62658227848101,560.59177215189868,456.48101265822783,600.63291139240505,1206.2710970464136,220.23206751054852,155.16350210970464,854.90611814345993,387.40822784810126,8.0084388185654003,240.25316455696202,31.032700421940927,29.031645569620252,14.014767932489452,11.012658227848101,5.0042194092827001,28.029535864978904,15.015822784810126,30.031645569620252,3.0031645569620253,4.0042194092827001,8.0084388185654003,2.0021097046413501,23.024261603375528,2.0021097046413501,0,0,2.0021097046413501,0,2.0021097046413501,0,2.0021097046413501,1.001054852320675,3.0031645569620253,1.001054852320675,1.001054852320675,1.001054852320675,0,0,0,0,0,1.001054852320675,0,0,0,0,0,2.0021097046413501,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV; Concrete",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV; Concrete",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 1 kV; Steel",35,5.9160797830996161,7,12.062176165803109,2.0103626943005182,9.0466321243523318,5.0310880829015545,5.0362694300518136,10.051813471502591,0,3.0155440414507773,39.222797927461137,3.0207253886010363,7.0414507772020727,12.139896373056995,7.0466321243523318,9.0518134715025909,2.0103626943005182,1.0051813471502591,98.512953367875653,16.088082901554404,10.051813471502591,2.072538860103627E-2,3.0207253886010363,3.0155440414507773,15.077720207253886,10.05699481865285,5.0259067357512954,8.0414507772020727,9.0466321243523318,9.0466321243523318,10.051813471502591,1.0051813471502591,3.0155440414507773,11.051813471502591,1.0051813471502591,1.0051813471502591,1.0051813471502591,0,1.0051813471502591,0,0,1.0051813471502591,0,7.0362694300518136,0,0,0,0,1.0051813471502591,0,0,0,0,0,0,0,1.0051813471502591,0,0,1.0051813471502591,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV; Steel",35,5.9160797830996161,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; Steel",35,5.9160797830996161,1,4.1714285714285717,1.0857142857142856,1.0285714285714285,0,0,0,3.1142857142857143,2.0571428571428569,2.0857142857142859,1.0571428571428572,0,2.8571428571428571E-2,1.0285714285714285,0,0,0,2.0857142857142859,0,0,0,0,0,1.0285714285714285,0,0,0,2.0571428571428569,1.0285714285714285,0,0,0,5.7142857142857141E-2,0,0,0,0,0,0,0,0,2.8571428571428571E-2,0,0,0,0,0,1.0285714285714285,0,0,0,0,0,0,0,2.8571428571428571E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV; Steel",35,5.9160797830996161,0,6,0,30,0,0,0,0,0,10,0,1,0,0,0,1,0,4,2,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV; Steel",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV; Steel",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",35,5.9160797830996161,0,1,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"OVERHEAD CONDUCTORS BY: \nHIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)","˂ = 1 kV",55,7.416198487095663,22.685804999999998,0,106.17572955408258,18.248474567227088,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,6496.2077678787527,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV",60,7.745966692414834,0.62297999999999998,0,1.6289376991150466,1.4264489171350363,0.3846719946077819,9.9561352715071605E-2,2.3426200638840379E-3,7.1863315489148594E-2,8.8743960067136488E-2,0,1.3648517895729091,1.1006869270749264,0.82660037960049426,0,5.2157746716476966E-2,4.1340354068541843E-3,0,0.48588696148559518,0.15364831595474715,1.9720726902496746,3.3374067839533827,1.8339270070706308,1.0846330895783094,7.0347502506635365E-2,0.8582257504629287,1.6035923343187382,0.97563235601758747,1.8867737596882499,1.3427347001462391,1.844193194997652,1.1533958785123173,0.63485003731257428,0.72800363514702182,0.84244751532676843,0.26581847666072406,0.30901914666235031,0.35035950073089206,1.807538081056878,1.5158129825132011E-2,8.7503749445080256E-2,1.3813190306102112,1.6170279493910145,1.4597279021602125,0.78622463379355167,0.23439980756863224,0.2709860209192918,0.95751150081754333,2.058542930843041,0.84733945722487936,0.42670135457746605,0.44737153161173698,0.3733033972389328,0.74791590569003619,0.4202935996968421,0.29799505224407252,6.3526344085325981E-2,0.41946679261547121,0.71436131830440319,0.24838662736182227,0.23763813530400135,0.17679891423313063,0.17673001364301638,0,6.3044039954526315E-2,1.4951428054789301E-2,0.11058544713334946,0,4.0237944626714067E-2,0.24845552795193646,4.5612190655624496E-2,4.2580564690598101E-2,0.38605000641006659,0,0,0,0,0.45260797646041906,0.35380453023660396,0.50228530193278342,0.58152098056415535,0,0.19629778123545955,0.18548038858752441,0.22096419249635618,3.5139300958260578E-3,0.32824241130422227,1.4813626874560825E-2,2.3632902409183084E-2,8.6125737642795512E-3,6.2010531102812752E-3,4.3407371771968933E-3,4.1340354068541843E-3,1.6053837496617082E-2,6.3092270367606282,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV  ; SWER",46,6.7823299831252681,58.178741000000002,2.6944066081732365,346.31240360398425,206.06126177192371,4.4946836092361648,63.851642452413444,15.290907723591189,12.833397500495497,14.185628868457623,22.828042593981436,35.715507167831987,31.63219542783234,28.239371046867966,29.175424583517568,28.357764074163395,39.483566280115227,30.327284301849335,45.328447965665987,57.983193068220743,54.547392295615168,69.007238269447939,26.352661242645489,20.808337031540287,58.804458049131931,46.307477893956793,53.220299806204459,47.969601393473638,112.86607848568013,78.108713795577842,68.684037319836591,40.24697487141912,138.4293604573418,86.918689237328536,90.025096763032536,77.038832699581008,53.416050338454042,110.90524595867005,110.12510892244775,43.852185807203881,88.940243246721991,105.20860971869453,113.09140416916669,130.17706146110291,91.461524889672361,66.206471447308346,96.292810688924106,88.502253741372215,76.110912329521582,113.35462301517558,270.13573450443812,207.97209380887384,340.31895472494551,249.60900836608212,292.56155504159693,265.76600590917803,150.74389889832395,178.18529539587985,236.87089830597827,139.10727837710132,183.29893146709688,247.42830307409491,73.745269919955675,41.480720789738207,3.757985076393151,0.88559093485155727,1.7673001311032643,0.38604814598987214,1.1427099059178307,5.9943286216449927,0.43050329519291936,0.39686156066088363,19.036138516013406,0.21266382186322622,1.0665538914826729,0,0.39630702657519068,5.6142879282501257,24.682959110624179,6.9316760711612179E-3,0.30055747444555048,0.12745041736175095,0.13724718620899215,0,0,0,0,0,0,0,0,0,0,0,90.929726701492868,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Single-Phase",56,7.4833147735478827,73.824333999999993,0,131.40997484341173,137.28438314988799,11.621241212093068,102.43588670885448,50.163932319462596,67.53388306022336,62.287940823694306,69.02822988681919,52.422761447116656,60.01222685675512,72.090361025942755,51.366842194013628,130.75442213046102,83.669775638436803,64.305100870347218,92.661569355553226,125.55570347412443,120.78184284007428,180.1459308774208,41.411803090555487,51.511249974749049,78.520632103836903,107.30338495620052,107.47389099309127,107.47408374239816,160.79413176303265,177.84650874573191,164.91746348626853,157.83731884520355,181.35439193201077,195.46950077660142,220.96371915394741,134.26519655634351,92.499428638582273,266.16470376928316,198.88216580526773,72.345445458704717,153.05096805606578,197.217197292197,197.46060111696039,179.28954570682885,158.44498031016153,123.96598429047056,126.16856917036887,175.67480230480021,199.66881427662037,246.24822628537754,271.72744876664615,262.11550342948408,246.51167603805931,266.60544433445887,193.68340859906971,115.56361795387858,108.98616350522954,152.61859281080993,104.06639164585008,74.574321344065282,75.02385127763597,119.93181839661028,104.99220511679026,123.08357796344606,115.85717514829936,91.246596693542102,66.535094701687825,40.135764128963594,52.27939451263854,57.054064693777697,75.819096368076714,48.04727508058383,33.810965471809453,12.567023511228912,7.9452806301905046,5.4833708327782462,9.4158421923138871,20.662610050946224,65.514140172857907,2.6851905945344079,11.387590502259272,3.8830118873830641,6.4055991666099397,10.450289172627379,4.1303477980073229,1.9167376577538626,0.1048556229579153,1.6306591364411087E-2,0.2136433317767524,7.0160747714487449E-3,0.45334636984745724,0,0.28719646729281945,0,99.122795972136799,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Multiple-Phase",56,7.4833147735478827,146.57860600000001,0,269.39346548627873,202.80825481510971,17.167893353439659,151.32706967244019,74.106459416187349,99.766839097625208,92.01708369616972,101.97441628183782,77.443395364720473,88.655204016167033,106.49805879740798,75.883500961336736,193.16163683879725,123.60416231375984,94.99700536940027,136.88761050782591,185.48164415663445,178.42928815147107,266.12700596399117,61.177064141176331,76.096832509475732,115.99740624956463,158.51775518385816,158.76964131237361,158.76992605816662,237.53887003860618,262.73010255144573,243.63020899228908,233.17081262434832,267.91224818797991,288.76429650997505,326.4265405202039,198.3480536622269,136.64808234672799,393.20130830826423,293.80577772475175,106.87489137990552,226.1000050917965,291.3461435645479,291.70572055198778,264.86188040555339,234.06850221145856,183.13317475402997,186.38702188015657,259.52187170136278,294.96788225527081,363.77898110761481,401.41907189514592,387.21948258658108,364.16817165752991,393.85240803860944,286.12572809343021,170.72047919505346,161.00369985533814,225.46126332886882,153.73579128485008,110.16757783220159,110.83166197070908,177.17355920420326,155.10348227793779,181.82960851353297,171.15414703784,134.79729164118356,98.291343347295921,59.2919900421509,77.231601443863852,84.285153381357958,112.00646616359735,70.979551964594066,49.948455487940947,18.565084010685364,11.737449385382233,8.1005052693113857,13.909888938734793,30.524578165473351,96.783101830768032,3.966793642718236,16.822724503127183,5.7363178989315884,9.4628999906486673,15.438062660774865,6.1017037005492778,2.8315691150612801,0.15490171140899578,2.4089494090443097E-2,0.31561223699582902,1.0364746866337222E-2,0.66972210520948183,0,0.42427123161655106,0,146.43268813434338,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV",61,7.810249675906654,0.37363099999999999,105.18261080445357,26.819590866717622,60.82300767882716,0,39.643857853022695,8.3985636862590152,0.83897192372707308,2.9124145153341052,10.939422006216601,3.3083599488298332,7.6574167286144839,21.480039767143282,7.234848610285332,60.915829724269869,13.160450756698847,17.280355903605219,18.678404208834152,3.0765281798944968,75.093124101015732,29.661244419175059,1.6845548497282175,4.0311926434178176,0.23102772811822078,0.74891935220999406,6.9027797528161035,2.9155413407340034,27.443074480487009,6.0526405955179632,11.838607653358864,39.699694020878027,11.008390840751508,50.349929346538296,104.4304294087613,15.172607570467866,0,54.021090379624944,31.066797105363761,33.259863102984049,33.0084663408322,3.0583925925750846,34.858564261017904,73.723931927334434,65.317238495035681,96.221708693210388,7.5238566151045294,65.952788092032208,73.620657351269216,49.091784143487679,59.553963255811183,108.88186738592549,56.110703125442861,51.72912736149928,12.618973935304979,25.401078818616099,24.397278527380085,70.631233593229027,28.006528417548733,11.948761245303862,30.094801095338148,69.630470789524352,5.8568119876157452,65.043060576398858,11.583369362858571,7.5108132862935237,12.726536729061493,21.585905141396989,7.8370751823057994,42.253059642435204,30.291344406188912,12.484877794583616,4.044057296491685,39.67003384851327,1.035872586052115,23.44556221351953,8.3925780490649249,22.964209777672281,39.150534142787272,0,0,0,0,0,2.4210562382071855E-2,0,0,0,0,0,0,0,0,0,249.45339549687452,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"UNDERGROUND CABLES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",50,7.0710678118654755,170.02588976500459,196.07370034613527,149.30808146854582,142.03420489981622,126.08104632591879,172.71559090911836,198.72681307106558,124.56529204594111,105.53397282777328,77.440798615047683,79.507360292035401,94.530473948746589,98.035908947964174,152.13228751178872,165.65634933979678,169.35114059551708,138.4175441365264,152.68728703820224,173.39688108656657,138.82883792505956,99.884249544686654,60.801604098381702,41.84341855523779,35.791308106941742,33.168884077158587,40.607170693390728,27.879299857096072,27.928653173774045,25.414717999877713,21.429738720407617,20.309411296651284,19.114454455965898,7.3780583397837107,7.5806675038030269,3.3870987353466271,3.0324378931169704,3.1824683818094308,1072.7335651062383,0.64054750689631468,3.2664113907072547,4.0313138049178843,3.6147488034516027,1.5538934963470448,1.9150653964635398,5.2431290134363495,2.1243538673119162,0.84657582415757227,5.2308402340207643,0.1578954660776527,9.622386035278474E-2,2.8413810890593486E-2,5.9627072767369574E-2,4.2733909995967156E-2,0,4.4238020303993203E-3,1.7739252347308145E-2,0.1280374450259999,0.19297140654927167,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV",50,7.0710678118654755,0,0,0.10365644654376803,0.37325689031565923,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,7.5925895843361492E-3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0.34212221237531248,10.339648287065595,0,0,0,0,3.5362712970453574,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0.13291327706997857]
[null,null,"> 11 kV & < = 22 kV",50,7.0710678118654755,121.74444316657886,116.14194346489184,97.1778302953295,85.633551371212775,62.821817485627193,86.580985173105177,69.35347664657597,49.190327603495916,44.901324553781379,34.264487751885405,36.571975646778299,30.929880028336921,41.297947449124898,44.262947422546553,50.186262237107591,57.393204964332192,47.388158900823967,54.473171565861271,78.785195548788607,61.444860234560842,85.181627513801644,28.072312023548122,12.542181755091892,12.358740135412194,6.1426936633587879,6.221274835128102,1.5527434586568871,4.8538820718136098,5.4855565422820929,5.4089746869075999,3.9473779528592354,6.1703987633103416,1.911949282412257,3.2007247054196406,0.77490087545808284,1.1216958673414803,4.7358068661345376,211.29908540189214,0,1.1341348302984047,1.2519538421680898,417.75954319067193,0.23535470352663662,1.1925309439328688,1.8391299596501289,1.4405345888719665,0.19500769493386197,43.266537165016125,0,0.21120416709512396,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.2602042256856398,0,0,0,0,0,0,0,0,1.8508937765681996]
[null,null,"> 22 kV & < = 33 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV",50,7.0710678118654755,0,0,0,0.7574183852768539,0,1.2241582248976759,0,0,0,0,0,0,0.36031488892404873,0,0,0,0,0,0,0.70093612879080558,0,0,0,0,0,0,0,0,0,0,0,0,0,0,5.730869723822229,0,0,0,0,0,0,2.4053916482883859,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,">  132 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"SERVICE LINES BY: \nCONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY ","˂ = 11 kV ; Residential ; Simple Type",40,6.324555320336759,5877.9124999999995,7166.6433285713601,5071.4962407004114,1666.3232037062612,2445.3362645620418,2364.6000922570311,1844.3953682886822,1785.8415967901308,1649.4437209051023,2270.6725724617218,2361.9375922570312,1855.9286225883925,2616.3296576459111,3214.6046617122329,2868.9467230347918,2640.2836662453319,2950.4543420236419,3457.4634728014025,3214.6046617122329,10155.147954805336,1071.5718719449508,865.8635161390406,679.78262305517103,553.02948686747993,841.13381515549099,668.24936875546064,610.69490487278028,587.62924976661054,449.34371277246032,368.72359378361023,265.0378196885905,195.83914738358001,149.81793780060974,92.152519795309388,23.954008599420508,23.066508599420509,30693.991721382561,11.533254299710254,23.066508599420509,11.533254299710254,23.066508599420509,11.533254299710254,11.533254299710254,34.599762899130759,11.533254299710254,0,4897.6471309140934,0,0,0,0,11.533254299710254,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,51306.472513758046,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Simple Type",40,6.324555320336759,745.08750000000032,908.44774587524319,642.86572065216501,211.22406807544164,309.97220255011814,299.73803986356739,233.7965959802556,226.37428691705892,209.08441532599892,287.83173453740142,299.40053986356742,235.25855779289492,331.64742139173541,407.48509796352261,363.66930291990332,334.68384501701399,374.00125462271535,438.27001767905119,407.48509796352261,1287.27227596124,135.83305419020508,109.75734711621645,86.169628274599148,70.102329321229874,106.62259628731579,84.707666461959832,77.412030195141199,74.488214759147851,56.95906218242456,46.739610479612573,33.596343340807259,24.824680654256628,18.991006200077301,11.681305326165983,3.0364236252786565,2.9239236252786567,3890.787682992157,1.4619618126393283,2.9239236252786567,1.4619618126393283,2.9239236252786567,1.4619618126393283,1.4619618126393283,4.3858854379179855,1.4619618126393283,0,620.82850955249091,0,0,0,0,1.4619618126393283,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,6503.6373608989106,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Residential ; Complex Type",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Complex Type",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Subdivision ; Complex Type",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"TRANSFORMERS BY: \nMOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV)","Pole Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",58,7.6157731058639087,365,283.01939280460061,352.24715795104964,447.94436271231757,463.21519325932837,465.25130399892981,508.00962953056012,582.32767152601275,610.83322188043303,586.39989300521563,566.03878560920123,533.46101377557818,623.04988631804156,599.63461281262505,685.15126387588566,640.35682760465397,500.88324194195508,574.18322856760699,691.25959609468998,693.29570683429142,571.12906245820488,536.51517988498028,590.47211448441851,757.43319513173697,781.86652400695425,877.56372876822195,835.82345860639259,1078.1206366189642,1305.1469840845252,1162.6192323124242,1262.3886585528949,1269.5150461414996,1237.9553296776776,1146.3303463956124,886.7262270964286,1022.1275912799246,1436.4761267888182,1089.3192456867721,1055.7234184833483,910.14150060184511,838.8776247157947,846.00401230439968,361.40965627925618,322.72355222682882,335.95827203423812,371.59020997726338,374.64437608666555,362.4277116490569,353.26521332085042,424.52908920690095,607.77905577103081,435.72769827470881,387.87909589407496,447.94436271231757,331.88605055503518,294.21800187240859,206.66524006954648,145.58191788150319,95.697204761267827,88.570817172662771,72.281931255851248,28.505550354420205,26.469439614818761,11.198609067807938,12.21666443760866,2.0361107396014431,3.054166109402165,29.523605724220925,1.0180553698007215,3.054166109402165,4.0722214792028861,0,3.054166109402165,0,0,0,0,1.0180553698007215,3.054166109402165,1.0180553698007215,0,2.0361107396014431,0,0,0,0,0,0,1.0180553698007215,0,0,0,0,0,0,0,0,0,1.0180553698007215,0,0,0,0,0,0,1.0180553698007215,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",58,7.6157731058639087,7,5.1581722319859393,9.2847100175746924,15.474516695957822,33.012302284710017,19.601054481546573,17.537785588752197,10.316344463971879,27.854130052724077,12.379613356766255,21.664323374340949,18.569420035149385,11.347978910369068,10.316344463971879,14.442882249560633,8.2530755711775043,8.2530755711775043,7.2214411247803163,11.347978910369068,14.442882249560633,15.474516695957822,15.474516695957822,14.442882249560633,14.442882249560633,10.316344463971879,12.379613356766255,7.2214411247803163,10.316344463971879,11.347978910369068,13.411247803163446,14.442882249560633,9.2847100175746924,10.316344463971879,8.2530755711775043,10.316344463971879,9.2847100175746924,13.411247803163446,17.537785588752197,15.474516695957822,7.2214411247803163,8.2530755711775043,13.411247803163446,5.1581722319859393,4.1265377855887522,1.031634446397188,2.0632688927943761,0,2.0632688927943761,0,4.1265377855887522,5.1581722319859393,4.1265377855887522,1.031634446397188,0,3.0949033391915637,3.0949033391915637,4.1265377855887522,6.1898066783831274,1.031634446397188,1.031634446397188,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.031634446397188,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",58,7.6157731058639087,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,1,0,0,0,1,0,1,0,0,0,0,0,0,0,0,1,0,0,0,1,0,1,0,0,0,0,1,0,0,0,1,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",58,7.6157731058639087,27,34.395278125558939,45.523162225004469,36.418529780003581,45.523162225004469,38.441781434448217,58.67429797889465,63.73242711500626,76.883562868896433,81.941692005008051,80.930066177785719,71.82543373278483,92.057950277231257,98.127705240565206,79.918440350563401,97.116079413342874,167.92988731890537,200.30191379001968,223.56930781613306,196.25541048113041,148.70899660168129,131.51135753890182,132.52298336612412,179.05777141835091,156.80200321945986,158.8252548739045,165.90663566446074,237.7320693972456,267.06921838669291,181.08102307279557,151.74387408334823,151.74387408334823,154.7787515650152,138.59273832945806,133.53460919334645,137.58111250223575,177.0345197639063,129.48810588445716,113.30209264890001,97.116079413342874,80.930066177785719,73.848685387229466,35.406903952781256,35.406903952781256,59.685923806116975,46.534788052226794,42.488284743337509,59.685923806116975,37.430155607225899,56.651046324450007,39.453407261670542,27.313897335002682,31.360400643891968,20.23251654444643,20.23251654444643,19.220890717224108,10.116258272223215,5.0581291361116074,3.0348774816669648,8.0930066177785722,1.0116258272223215,0,1.0116258272223215,0,0,0,0,5.0581291361116074,0,0,1.0116258272223215,0,0,0,0,0,0,0,0,1.0116258272223215,0,0,0,0,0,0,0,0,0,0,0,0,1.0116258272223215,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",58,7.6157731058639087,368,217.35814679854244,253.5845045982995,365.20085025160512,371.07539475967371,358.3472149921916,466.04719764011799,649.13716814159284,494.44082942911677,408.28084331077565,421.00902307825788,350.51448898143326,343.66085372201979,280.01995488460875,327.99540170050318,266.31268436578176,216.37905604719765,207.56723928509453,191.901787263578,157.6336109665105,156.65452021516572,114.55361790733993,120.42816241540864,122.38634391809821,130.2190699288565,135.11452368558042,127.28179767482216,224.21178205795593,256.52177685233386,224.21178205795593,209.52542078778416,221.27450980392157,215.39996529585287,157.6336109665105,183.08997050147491,211.48360229047373,278.06177338191918,194.83905951761233,220.29541905257679,213.4417837931633,248.68905084157555,232.04450806871421,93.013621377754646,80.285441610272414,62.66180808606628,70.494534096824566,66.578171091445441,49.933628318584077,41.121811556480999,38.184539302446645,47.9754468158945,33.28908554572272,32.309994794377928,17.623633524206141,21.539996529585284,15.66545202151657,13.707270518827,19.581815026895715,5.8745445080687144,9.7909075134478574,2.9372722540343572,3.9163630053791425,1.9581815026895713,2.9372722540343572,0,1.9581815026895713,0,4.8954537567239287,0,0,0.97909075134478563,0,0,0.97909075134478563,0,0,0,0,0,0,0,0.97909075134478563,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",58,7.6157731058639087,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",58,7.6157731058639087,1,0,0.99999999999999989,3.9999999999999996,0.99999999999999989,0,0.99999999999999989,3.9999999999999996,0.99999999999999989,1.9999999999999998,0,6,3,1.9999999999999998,3,1.9999999999999998,3,5,5,6.9999999999999991,3.9999999999999996,0.99999999999999989,1.9999999999999998,1.9999999999999998,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",58,7.6157731058639087,1,0,0,4,2,1,40,1,2,0,1,3,3,0,2,1,1,9,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",58,7.6157731058639087,121,87.471289274106184,97.52546045503793,138.74756229685809,116.62838569880826,160.86673889490794,181.98049837486462,195.05092091007586,227.22426868905745,183.99133261105098,109.59046587215605,117.63380281690142,108.58504875406285,71.384615384615401,74.400866738894919,41.222101841820162,70.379198266522224,88.476706392199361,57.308775731310952,38.205850487540637,28.151679306608887,25.135427952329369,31.167930660888409,47.254604550379199,25.135427952329369,36.195016251354289,45.243770314192858,49.265438786565561,52.281690140845079,55.297941495124604,30.162513542795239,33.178764897074764,31.167930660888409,19.102925243770319,6.032502708559047,8.0433369447453966,10.054171180931746,12.065005417118094,18.097508125677145,18.097508125677145,23.124593716143011,11.05958829902492,0,0,0,0,0,1.0054171180931746,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.0054171180931746,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",58,7.6157731058639087,30,15,21,23,20,21,16,18,13,17,13,12,9,10,7,7,8,10,3,1,1,1,1,0,3,0,2,0,2,0,1,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ;  < = 60 kVA ; Single Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Single Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Single Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  < = 60 kVA ; Multiple Phase",50,7.0710678118654755,0,0,0,0,0,0,0,0,0,0,1,0,0,1,0,0,0,0,0,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Multiple Phase",50,7.0710678118654755,1,3.019354838709678,4.0258064516129037,6.038709677419356,3.019354838709678,7.0451612903225813,7.0451612903225813,5.032258064516129,2.0129032258064519,9.0580645161290345,8.0516129032258075,10.064516129032258,6.038709677419356,13.083870967741937,6.038709677419356,6.038709677419356,5.032258064516129,7.0451612903225813,6.038709677419356,19.122580645161293,6.038709677419356,9.0580645161290345,9.0580645161290345,12.077419354838712,18.116129032258069,10.064516129032258,11.070967741935487,23.148387096774197,24.154838709677424,17.109677419354842,13.083870967741937,11.070967741935487,11.070967741935487,7.0451612903225813,11.070967741935487,10.064516129032258,24.154838709677424,10.064516129032258,15.09677419354839,14.090322580645163,15.09677419354839,13.083870967741937,4.0258064516129037,2.0129032258064519,4.0258064516129037,5.032258064516129,8.0516129032258075,6.038709677419356,1.0064516129032259,0,3.019354838709678,2.0129032258064519,2.0129032258064519,0,0,0,0,0,0,0,0,1.0064516129032259,0,0,0,0,0,1.0064516129032259,0,0,0,0,0,0,1.0064516129032259,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase",50,7.0710678118654755,9,1.0062499999999999,11.06875,6.0375000000000005,13.081250000000001,20.125,17.106249999999999,10.0625,29.181250000000002,26.162500000000001,24.150000000000002,41.256250000000001,17.106249999999999,16.099999999999998,18.112500000000001,26.162500000000001,18.112500000000001,10.0625,22.137499999999999,33.206250000000004,14.0875,16.099999999999998,18.112500000000001,16.099999999999998,18.112500000000001,9.0562500000000004,4.0249999999999995,12.075000000000001,12.075000000000001,22.137499999999999,13.081250000000001,18.112500000000001,12.075000000000001,9.0562500000000004,5.03125,10.0625,5.03125,7.0437500000000002,8.0499999999999989,11.06875,6.0375000000000005,8.0499999999999989,1.0062499999999999,2.0124999999999997,2.0124999999999997,1.0062499999999999,2.0124999999999997,1.0062499999999999,1.0062499999999999,2.0124999999999997,1.0062499999999999,1.0062499999999999,1.0062499999999999,0,0,3.0187500000000003,0,0,2.0124999999999997,0,0,0,1.0062499999999999,0,0,0,0,1.0062499999999999,0,0,0,0,0,0,0,0,3.0187500000000003,0,0,0,1.0062499999999999,0,1.0062499999999999,0,0,0,0,0,0,2.0124999999999997,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA",50,7.0710678118654755,0,0,1,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 15 MVA and < = 40 MVA",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 40 MVA",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA",50,7.0710678118654755,0,1,0,1,3,2,0,3,3,0,1,3,1,2,0,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,1,1,2,3,2,0,0,0,0,0,0,3,3,2,3,1,1,7,0,3,0,0,0,0,2,0,0,2,0,3,4,0,1,2,1,0,1,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA",50,7.0710678118654755,0,0,0,3,0,0,2,3,0,1,0,0,3,0,1,2,2,0,1,0,0,1,0,0,0,0,0,0,1,0,0,2,2,2,6,2,6,2,0,3,2,0,0,0,0,0,0,0,3,2,1,2,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 40 MVA",50,7.0710678118654755,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,1,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  < = 100 MVA",50,7.0710678118654755,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  > 100 MVA",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  < = 100 MVA",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  > 100 MVA",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"SWITCHGEAR BY: \nHIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION","˂ = 11 kV ;  Fuse",50,7.0710678118654755,55.000000000000114,6.4786430298035489,12.761244004289665,5.9553032941492887,14.462518836271844,12.761244004289665,5.1046658781581993,0,12.761244004289665,0,0,1.7012748319821787,5.1046658781581993,2.5519122479732683,2.5519122479732683,0,0,2.5519122479732683,0,0,2.5519122479732683,7.6565781261314658,5.1046658781581993,5.1046658781581993,5.1046658781581993,1.7012748319821787,8.507215542122557,17.015272466456778,74.866189193755829,7.6565781261314658,141.22432146317743,5.1046658781581993,24.671850592588243,9.3578529581136447,7.6565781261314658,15.313156252262932,10.209331756316399,2.5519122479732683,2.5519122479732683,10.209331756316399,10.209331756316399,2.5519122479732683,2.5519122479732683,0,7.6565781261314658,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,16.163793668254023,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV  ; Switch",47,6.8556546004010439,701.00000000000045,55.957132364003229,0,104.61319126717936,52.30659563358968,0,26.139974690041505,0,0,52.30659563358968,313.81292754803138,0,0,26.139974690041505,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,78.446570323631178,0,0,0,0,52.30659563358968,0,0,0,0,78.446570323631178,78.446570323631178,0,0,0,0,287.67295285798991,26.139974690041505,0,0,0,52.30659563358968,0,0,0,0,0,0,0,0,0,0,627.62585509606276,0,0,0,0,0,0,0,0,0,0,0,0,967.57875733413573,0,0,0,0,0,0,0,0,0,0,0,0,130.75316595722086,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ;  Circuit Breaker",45,6.7082039324993694,0,0,0.99999999999999989,0,0,0.99999999999999989,0,0,0,0,0,0,0,0.99999999999999989,0,0,0,0,0,0,0,0,0,0,1.9999999999999998,0,0,0,0,0.99999999999999989,0,0.99999999999999989,0,0,0.99999999999999989,0,0,0,0,0,0,0,10,3.9999999999999996,0,0,3.9999999999999996,0,0,0,0,0,0,0,0,0,0,0,0,0,6,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.9999999999999998,0,0,15,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Switch",47,6.8556546004010439,8486,1532.1740510323689,1901.6446369396626,4588.545516993714,3143.7280920551925,1766.4886570576684,2128.706683141414,1624.5748781815744,3000.4627533802782,1731.3481022883498,1485.36421890312,2024.6365786322781,1397.5128319798234,1400.2159515774631,641.99090443947398,910.95130440464322,2001.6600620523391,1515.0985344771584,1585.3796440157957,2127.3551233425942,1335.3410812341058,1713.7778249036905,2334.1437725620453,3399.1728940321627,3508.649237736578,3291.0481101265673,4912.9198687104999,5999.5739469617374,22149.361983061262,3397.8213342333424,18548.806679004927,2189.5268740883112,2612.5650911189541,1206.9429003462112,2044.9099756145772,1670.5279113414526,2532.8230629885775,641.99090443947398,1185.317943565092,2020.5818992358186,1027.1854471031584,633.8815456465544,425.7413366282828,286.53067734982841,2294.9485383962674,181.10901304187266,1169.0992259792529,177.05433364541284,629.82686625009455,375.7336240719448,579.81915369375656,340.59306930262619,331.13215071088661,1128.5524320146544,64.874870343357372,102.71854471031584,21.624956781119124,70.281109538637153,0,4.0546793964598358,17.570277384659288,79.742028130376781,0,0,27.031195976398909,4.0546793964598358,114.88258289969535,0,62.171750745717482,0,0,0,0,0,0,2.7031195976398905,0,17.570277384659288,0,0,0,0,0,0,0,0,0,0,0,0,0,0,13881.870693679657,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Circuit Breaker",45,6.7082039324993694,100,48.046395381198479,70.622119388161607,19.617931143622688,58.851766156801339,7.8475779122624179,100.04800246656228,29.42588307840067,1.9624012965822837,60.814167453383632,33.348658397498518,82.392472619521897,7.8475779122624179,19.617931143622688,7.8475779122624179,66.69934406906377,9.807951934777984,35.311059694080804,76.507296003841745,0,33.348658397498518,0,1.9624012965822837,3.9227753190978505,0,0,0,9.807951934777984,1.9624012965822837,51.004188244538923,11.77035323136027,5.8851766156801348,13.732754527942554,27.463481781818388,0,82.392472619521897,0,15.69312855045812,78.469697300424031,0,78.469697300424031,0,0,0,0,0,7.8475779122624179,60.814167453383632,15.69312855045812,21.57830516613825,11.77035323136027,31.388284374982955,23.540706462720539,7.8475779122624179,49.043814222023357,23.540706462720539,7.8475779122624179,1.9624012965822837,7.8475779122624179,0,7.8475779122624179,3.9227753190978505,1.9624012965822837,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,49.043814222023357,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Switch",47,6.8556546004010439,0,6.1284464881435392,7.606268614911861,18.353434220060958,12.574399998781088,7.0656667233047639,8.5144797928117857,6.4980347371173117,12.001361993677563,6.9251102314869186,5.9412147887620019,8.0982163362743194,5.5898235592173879,5.6006355970495294,2.5678589851337126,3.6436567494318375,8.0063140147011147,6.0601472049155625,6.3412601885512538,8.5090737738957163,5.3411466890781227,6.854831985577996,9.3361946680545724,13.596137573918503,14.03402510612025,13.163656060632825,19.650878759917994,23.997317968439056,88.593837996571125,13.59073155500243,74.192203604158053,8.7577506440349797,10.449834564765194,4.8275748920513806,8.1793066200153852,6.6818393802637255,10.130879448717007,2.5678589851337126,4.7410785893942444,8.0819982795261076,4.1085743762139408,2.5354228716372877,1.7028959585623571,1.1460760102070466,9.1794201194885154,0.72440653475351069,4.6762063624013939,0.70818847800529772,2.5192048148890742,1.5028732586677311,2.3191821149944483,1.3623167668498857,1.3244746344373888,4.5140257949192639,0.25948890797140678,0.41085743762139409,8.6496302657135593E-2,0.28111298363569065,0,1.6218056748212924E-2,7.0278245908922662E-2,0.31895511604818755,0,0,0.10812037832141951,1.6218056748212924E-2,0.45951160786603285,0,0.24867687013926482,0,0,0,0,0,0,1.0812037832141949E-2,0,7.0278245908922662E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,55.525220286964981,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker",45,6.7082039324993694,0,7.3421588594704685,0,35.661914460285132,9.4399185336048888,29.368635437881874,4.1955193482688387,48.248472505091648,14.684317718940937,0,31.466395112016293,14.684317718940937,27.270875763747455,4.1955193482688387,10.488798370672098,4.1955193482688387,33.564154786150709,3.1466395112016294,15.733197556008147,11.537678207739308,0,16.782077393075355,0,0,0,0,0,0,5.2443991853360492,0,27.270875763747455,4.1955193482688387,3.1466395112016294,7.3421588594704685,14.684317718940937,0,29.368635437881874,0,0,14.684317718940937,0,0,0,0,0,0,0,4.1955193482688387,0,6.2932790224032589,0,6.2932790224032589,13.635437881873727,11.537678207739308,2.0977596741344193,16.782077393075355,11.537678207739308,4.1955193482688387,0,4.1955193482688387,0,3.1466395112016294,2.0977596741344193,1.0488798370672097,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Switch",47,6.8556546004010439,0,4.6815101645692163,29.649564375605031,5.4617618586640848,6.2420135527589551,27.308809293320422,39.012584704743468,21.847047434656339,14.824782187802516,14.824782187802516,15.605033881897384,21.066795740561471,9.3630203291384326,17.165537270087125,3.1210067763794775,48.375605033881897,0,33.550822846079384,3.1210067763794775,0,9.3630203291384326,0,0,0.78025169409486939,0,0,0.78025169409486939,0,3.901258470474346,7.8025169409486921,3.1210067763794775,3.901258470474346,20.286544046466602,10.143272023233301,22.627299128751211,24.187802516940948,2.3407550822846082,42.133591481122942,17.945788964181993,17.165537270087125,15.605033881897384,0,0,0,0,0,53.057115198451108,7.8025169409486921,19.506292352371734,31.990319457889644,31.990319457889644,17.165537270087125,42.913843175217814,26.528557599225554,0,21.066795740561471,0,1.5605033881897388,3.1210067763794775,0,0,0,0,0,0,3.1210067763794775,24.187802516940948,0,3.901258470474346,0.78025169409486939,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker",45,6.7082039324993694,0,2,2,0,0,0,0,0,3,3,0,2,0,0,0,0,1,0,7,0,0,1,0,0,0,0,0,0,0,0,1,0,0,0,2,4,1,0,0,2,5,0,2,0,0,0,0,0,0,0,4,11,0,1,2,1,0,3,0,0,0,0,0,1,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Switch",47,6.8556546004010439,0,1.9873230547290595,2.4665489056844914,5.9516229813780024,4.0776067907762101,2.2912433686777756,2.7610622078557743,2.1071725548207243,3.8917829215490913,2.2456639290560299,1.9266078517038068,2.6260769443606029,1.8126592526494416,1.8161653633895756,0.83270130078190019,1.1815593194252647,2.5962750030694615,1.9651750698452841,2.0563339490887769,2.7593091524857076,1.7320187056263525,2.2228742092451568,3.0275266241059819,4.4089342557189033,4.5509317406943426,4.2686898261135306,6.3723562701941194,7.781812787728116,28.729071404660587,4.4071812003488358,24.058931898801678,2.8399496995087965,3.3886560303398165,1.5654784454699724,2.6523727749116106,2.1667764374030076,3.2852257635058546,0.83270130078190019,1.5374295595488976,2.6208177782504016,1.3323220812510401,0.82218296856149731,0.5522124415711549,0.37164773845423754,2.9766880183740345,0.23490941958899922,1.5163928951080921,0.22965025347879772,0.8169238024512957,0.48734939287867007,0.75206075375881087,0.44176995325692381,0.42949856566645384,1.4638012340060771,8.4146657763223595E-2,0.13323220812510403,2.8048885921074532E-2,9.1158879243492225E-2,0,5.2591661102014747E-3,2.2789719810873056E-2,0.10343026683396234,0,0,3.5061107401343168E-2,5.2591661102014747E-3,0.14900970645570846,0,8.0640547023089273E-2,0,0,0,0,0,0,3.5061107401343165E-3,0,2.2789719810873056E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,18.005631705959782,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV  ; Circuit Breaker",45,6.7082039324993694,0,2,2,10,3,0,7,11,4,2,4,0,13,2,3,0,6,1,1,0,0,0,0,0,0,0,0,0,0,0,0,2,1,0,0,8,3,0,0,0,3,0,0,0,0,0,0,0,8,0,3,0,3,2,7,4,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Switch",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Circuit Breaker",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"PUBLIC LIGHTING BY: \nASSET TYPE ; LIGHTING OBLIGATION","Luminaires ;  Major Road",35,5.9160797830996161,1953.7955695777791,2288.6404069993378,9658.6212624185155,8047.4664385401529,3129.0985772138961,6234.4232506211738,1398.6980072893518,105.85047647232246,16.415314533140918,31.132493080094839,107.54861245850947,82.076572665704589,126.79415363529537,10.188815917121948,6.7925439447479645,52.642215571796733,313.5891121158644,721.14174880074222,142.64342283970726,85.47284463807857,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1282.6587148999074,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Luminaires ;  Minor Road",35,5.9160797830996161,3930.6648744695067,4983.3024535756831,20093.33545789446,31835.59676757329,12377.959493037059,24665.225660073571,5532.2928860331167,417.63716787904326,63.82122940778946,123.16377605012001,426.59453340996106,323.58482980440618,500.49279904003311,40.308144889130176,26.872096592753451,208.25874859383924,1239.4754553407531,2854.0405922886898,563.19435775645775,339.26021948351234,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,5073.2279025735788,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Brackets ; Major Road",35,5.9160797830996161,1593.2525335524624,4146.7042538239693,2949.4930088064193,1950.4126925037535,3543.0180363982031,1276.501892335893,258.68504257564501,12.692490406748936,58.022813287995135,67.088877864244381,67.088877864244381,105.16634908449119,25.989385118581154,15.714511932165347,16.318916237248633,77.968155355743463,129.94692559290579,32.637832474497266,33.84664108466383,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,535.50221430378838,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Brackets ; Minor Road",35,5.9160797830996161,5179.7474664475449,8292.8148067024431,10961.328438631488,7248.0225857658561,13168.420392920951,4744.4053002130759,960.33772056869793,47.174484519164103,215.65478637332163,249.35084674415313,248.22764473179208,389.75109828928436,97.718575075411366,57.283302630413559,61.776110679857759,288.6629171767899,481.85366330289048,121.30581733499339,125.7986253844376,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1990.3139659037806,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Lamps ; Major Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Lamps ; Minor Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Poles / Columns ; Major Road",35,5.9160797830996161,613.80599624971046,1022.9101448586589,2285.0332677892475,830.96591437098493,781.52122852475406,652.86664793978525,941.90896569760241,939.44903107838695,645.97883100598165,788.16305199663577,970.93619420434493,506.00855117262171,402.44530370365055,1278.4280216062784,736.504424993111,508.96047271568028,312.90368356420748,161.37171102053466,1051.6220497146126,420.15683296200183,304.53990585887487,124.47269173230266,112.41901209814688,123.24272442269491,309.70576855922735,302.81795162542409,200.7306649279821,190.15294606535565,379.56791174494663,494.93884538615197,409.33312063745376,141.44624060488937,391.37559791718093,336.51905590867597,106.76116247395129,36.899019288232012,64.450287023445256,60.268398170778951,92.001554758658486,11.807686172234241,36.899019288232012,48.21471853662316,51.16664007968172,22.877391958703846,10.331725400704961,15.497588101057447,17.957522720272916,7.3798038576464027,23.36937888254694,20.909444263331476,11.069705786469601,13.037653481841977,3.935895390744748,4.6738757765093881,3.1979150049801075,3.1979150049801075,2.4599346192154674,2.2139411572939207,3.6899019288232013,2.4599346192154674,0.73798038576464009,1.967947695372374,0,0.73798038576464009,0.4919869238430935,0.24599346192154675,0.4919869238430935,0,0,0.24599346192154675,0.73798038576464009,0.98397384768618701,0.4919869238430935,0.24599346192154675,0,0,0,0.73798038576464009,0.73798038576464009,0.98397384768618701,1.4759607715292802,0.73798038576464009,0.4919869238430935,0.24599346192154675,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Poles / Columns ; Minor Road",35,5.9160797830996161,1996.1940037502895,3325.4993312493002,7428.6843689144616,2701.4851758201148,2540.7396102961834,2122.4812482612747,3062.1630367718235,3054.1657449547129,2100.0888311733638,2562.3322982023828,3156.5310802137346,1645.0429267797447,1308.356941279369,4156.1925573526178,2394.3891700430509,1654.6396769602779,1017.2555191365265,524.62234320248535,3418.8422518149773,1365.9374423625684,990.06472695834896,404.66296594581951,365.47623604197531,400.66432003726402,1006.8590397742822,984.46662268637135,652.57901227626235,618.19065746268473,1233.9821273802361,1609.0551136027448,1330.7493583672799,459.84427948388577,1272.3691281023694,1094.0295205807927,347.08246486261987,119.95937725666586,209.52904560830973,195.93364951922089,299.09871395995361,38.387000722133074,119.95937725666586,156.74691961537673,166.34366979590999,74.374813899132846,33.588625631866442,50.382938447799667,58.380230264910715,23.991875451333172,75.974272262555047,67.976980445443999,35.987813176999758,42.385646630688605,12.795666907377692,15.194854452511008,10.396479362244374,10.396479362244374,7.9972918171110559,7.1975626353999518,11.995937725666586,7.9972918171110559,2.3991875451333171,6.3978334536888459,0,2.3991875451333171,1.5994583634222115,0.79972918171110574,1.5994583634222115,0,0,0.79972918171110574,2.3991875451333171,3.198916726844423,1.5994583634222115,0.79972918171110574,0,0,0,2.3991875451333171,2.3991875451333171,3.198916726844423,4.7983750902666342,2.3991875451333171,1.5994583634222115,0.79972918171110574,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: \nFUNCTION","Field Devices",20,4.4721359549995796,231,238.87805391743893,438.69313395113733,558.82666385846676,461.22283066554337,429.00800336983991,271.14111204717778,567.38226621735464,396.0598146588037,401.42649536647008,297.17818028643637,263.88163437236733,127.1594355518113,45.2259898904802,19.125947767481044,19.429654591406909,100.05939342881213,42.744524010109522,76.085299073294024,23.670387531592251,54.137110362257793,30.251895534962088,23.885214827295705,67.111204717775905,59.503791069924176,44.074136478517275,43.922283066554343,9.2148272957034543,24.251895534962088,4.6074136478517271,9.2148272957034543,5.7592670598146594,41.466722830665546,6.9111204717775907,90.237152485256956,1.3037068239258636,0,0,132.07055602358889,8.062973883740522,133.61499578770008,4.7592670598146594,3.4555602358887954,0,11.518534119629319,29.948188711036227,0,0,3.4555602358887954,2.3037068239258636,0,1.1518534119629318,0,0,2.3037068239258636,0,0,1.1518534119629318,0,0,0,0,0,0,0,0,0,0,1.1518534119629318,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Local Network Wiring Assets",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Communications Network Assets",20,4.4721359549995796,20,311,123,618,82,1,23,1959,176,94,17,19,1,2,1,53,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Master Station Assets",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Communications Site Infrastructure",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Communications Linear Assets",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"AFLC",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"OTHER BY: \nDNSP DEFINED","OTHER – MEASURING TRANSFORMERS",45,6.7082039324993694,17,29.042654028436019,20.631911532385466,57.169036334913109,78.695102685624008,46.584518167456558,40.721958925750393,115.7740916271722,49.12638230647709,10.137440758293838,73.837282780410746,54.353870458135859,150.61611374407582,40.33175355450237,19.173775671406002,12.563981042654028,102.26856240126382,18.916271721958925,60.058451816745659,86.41074249605056,27.142180094786731,9.0157977883096372,1,0,0,0,0,4.7393364928909963E-2,3.0789889415481833,9.3475513428120056,23.126382306477094,8,0.14218009478672988,9.37914691943128,25.753554502369667,111.10584518167457,67.426540284360186,23.537124802527646,34.300157977883096,20.726698262243286,45.695102685624015,46.394944707740919,22.047393364928912,1.3475513428120065,22.205371248025276,13.105845181674566,67.41074249605056,27.679304897314378,44.600315955766192,37.315955766192737,19.363349131121645,24.679304897314378,44.094786729857823,2.0473933649289098,3.0157977883096367,1.1579778830963665,10.063191153238547,4,0,0,0,1.0426540284360191,65,1.5797788309636653E-2,1,0,4.7393364928909963E-2,3.126382306477093,8,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER - CAPACITOR BANK",30,5.4772255750516612,0,0,0,2.032258064516129,2.032258064516129,3.0483870967741935,0,2.032258064516129,1.0161290322580645,1.0161290322580645,1.0161290322580645,3.0483870967741935,2.032258064516129,0,19.306451612903224,2.032258064516129,2.032258064516129,0,5.080645161290323,0,0,0,0,0,0,1.0161290322580645,0,0,1.0161290322580645,0,2.032258064516129,1.0161290322580645,2.032258064516129,3.0483870967741935,0,3.0483870967741935,1.0161290322580645,0,0,0,0,0,0,0,0,1.0161290322580645,0,0,0,0,0,0,2.032258064516129,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER - CAPACITORS",30,5.4772255750516612,2,3,1,2,0,0,42,3,0,3,4,3,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER - EARTHING",60,7.745966692414834,0,2.777777777777778E-2,1.388888888888889E-2,2.0138888888888888,1,1.388888888888889E-2,1.0277777777777777,2.0277777777777777,2.0416666666666665,3,1.388888888888889E-2,1.0416666666666667,4.0138888888888893,1,1.388888888888889E-2,1.0277777777777777,2,1.388888888888889E-2,1.0138888888888888,1,0,0,0,0,0,0,0,1.388888888888889E-2,1,1.388888888888889E-2,1.0138888888888888,1.0138888888888888,2.0138888888888888,2,1.388888888888889E-2,1.0277777777777777,3,4.1666666666666671E-2,3.0277777777777777,2,4.1666666666666671E-2,3,0,0,1.388888888888889E-2,1.0138888888888888,1.0277777777777777,2.0416666666666665,4.041666666666667,4.0138888888888893,1.0138888888888888,1.0138888888888888,1.0138888888888888,1.0277777777777777,2.0416666666666665,3.0277777777777777,2.0416666666666665,4,2.777777777777778E-2,2.0277777777777777,2,0,0,0,0,0,0,0,0,1.388888888888889E-2,1.0138888888888888,1,0,1.388888888888889E-2,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.388888888888889E-2,1,2.777777777777778E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER - NEUTRAL EARTH RESISTORS",30,5.4772255750516612,1,5.7692307692307709E-2,3.8461538461538478E-2,3.1153846153846154,6.0961538461538458,5,5.7692307692307709E-2,3.0192307692307692,1,0,5.7692307692307709E-2,3.0961538461538463,5,0,1.9230769230769239E-2,1.0384615384615385,2,5.7692307692307709E-2,3.0192307692307692,1,0,1.9230769230769239E-2,1.0384615384615385,1,1.9230769230769239E-2,1,0,1.9230769230769239E-2,1.0384615384615385,3.0192307692307692,1,1.9230769230769239E-2,1,0,0,0,0,0,0,1.9230769230769239E-2,2.0192307692307692,2.0192307692307692,2,0,0,0,0,0,0,7.6923076923076955E-2,4,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.9230769230769239E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER - REGULATORS",50,7.0710678118654755,10,16.597938144329895,0.3195876288659793,2,1.5979381443298966,9,9.1958762886597931,12.31958762886598,4,1.2783505154639172,12.515463917525771,9.31958762886598,3,0,3.3195876288659791,0,0.95876288659793807,0,2,0.3195876288659793,1,0,0,0,0,0,0,0,0,0,0,0,0,1,0.3195876288659793,0,2,0,2,0,0.6391752577319586,3,0,0,0,0,0,0.95876288659793807,4.6391752577319583,3,0.3195876288659793,1.3195876288659794,3,0.3195876288659793,3,0,0.3195876288659793,1,0,0,0,0,1.3195876288659794,1,0,0.3195876288659793,1,0.3195876288659793,1.3195876288659794,1.3195876288659794,0,0,0,0,0,0,0,0.3195876288659793,0,0,0,0,0,0,0,0,0,0,0,0,0,0,11.505154639175256,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER - SUPPLY TRANSFORMERS (LINES)",58,7.6157731058639087,24,14.388349514563107,52.970873786407765,52.194174757281552,42.776699029126213,12.194174757281553,6.5533980582524274,9.3883495145631066,7.1941747572815533,9,1.165048543689321,0.3883495145631069,0.19417475728155345,1,0,0.3883495145631069,1.3883495145631068,0,0.58252427184466049,0.3883495145631069,0,0,0,0,0,0,0,0,0,0,0,0.19417475728155345,0,0.19417475728155345,0,0.58252427184466049,0.7766990291262138,0,1.165048543689321,0,0,0,0,0,0.19417475728155345,0,0,0.19417475728155345,0,0,0,0.3883495145631069,1.3592233009708743,0.19417475728155345,0.97087378640776745,0,0,0.3883495145631069,0,0.3883495145631069,0,0.19417475728155345,0,0,0,0.19417475728155345,0.58252427184466049,0,0.19417475728155345,0,0.19417475728155345,0,0,0,0,0.58252427184466049,0.3883495145631069,0,0,0.19417475728155345,0,0,0.19417475728155345,0,0,0,0,0,0.3883495145631069,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.7475728155339811,0]
[null,null,"OTHER - STATION SUPPLIES TRANSFORMERS",50,7.0710678118654755,0,3.1844660194174756,7.9611650485436893,1.5922330097087378,6.3689320388349513,1.5922330097087378,12.737864077669903,3.1844660194174756,1.5922330097087378,0,9.5533980582524283,3.1844660194174756,1.5922330097087378,0,0,3.1844660194174756,3.1844660194174756,0,4.7766990291262141,3.1844660194174756,0,0,0,0,0,0,0,0,0,0,0,1.5922330097087378,0,1.5922330097087378,0,4.7766990291262141,6.3689320388349513,0,9.5533980582524283,0,0,0,0,0,1.5922330097087378,0,0,1.5922330097087378,0,0,0,3.1844660194174756,11.145631067961165,1.5922330097087378,7.9611650485436893,0,0,3.1844660194174756,0,3.1844660194174756,0,1.5922330097087378,0,0,0,1.5922330097087378,4.7766990291262141,0,1.5922330097087378,0,1.5922330097087378,0,0,0,0,4.7766990291262141,3.1844660194174756,0,0,1.5922330097087378,0,0,1.5922330097087378,0,0,0,0,0,3.1844660194174756,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,14.330097087378642,0]
[null,null,"OTHER - SURGE DIVERTERS",45,6.7082039324993694,9259,6983.3973404255321,8388.6514285714293,6544.7796352583591,7317.1687537993921,6357.3558054711248,3983.2133282674772,4232.298541033435,3680.8882978723404,2086.5293617021275,2077.3114133738604,1589.4969452887537,1186.0482370820669,992.1568389057752,885.30917933130706,1120.9464285714284,2566.2518237082068,1793.6522948328268,2507.6560486322187,637.26996960486315,551.54825227963522,1121.1764437689969,1318.021838905775,2328.8445896656535,2258.3868237082065,2006.7156382978724,3006.0444224924013,3644.3603951367782,3250.4056534954407,3022.3083738601827,3443.929027355623,3555.546671732523,3886.6756231003037,2185.6070364741645,1379.8016261398177,4102.1869300911849,2468.9441337386015,730.7616717325227,1713.3785410334347,1998.6236322188452,1885.0979939209726,4428.5458966565348,620.09802431610944,590.52411854103343,651.57992401215802,736.48565349544072,710.72773556231004,821.43738601823713,763.19756838905778,649.67193009118546,536.23829787234047,591.47811550151971,466.50451367781159,318.63498480243157,317.6809878419453,504.75639817629178,332.94493920972644,291.92306990881463,190.79939209726444,339.62291793313074,183.16741641337384,135.46756838905776,165.04147416413372,117.47963525835866,91.583708206686921,67.73378419452888,109.70965045592705,49.607841945288754,75.365759878419453,47.699848024316111,63.917796352583586,21.941930091185412,10.493966565349544,25.757917933130699,41.02186930091186,61.055805471124629,113.52563829787235,114.47963525835866,165.99547112462005,120.20361702127659,132.60557750759878,57.239817629179328,73.45776595744681,68.687781155015188,5.7239817629179326,1.9079939209726446,4.7699848024316109,2.8619908814589663,14.309954407294832,0,8.5859726443768984,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER< = 11 kV ; REACTOR ;",62,7.8740078740118111,0,0.16154577130186884,0.1938549255622426,0.58346531517263212,0.6803927779537533,0.58441558441558428,9.6927462781121299E-2,0.29173265758631606,0.19480519480519476,0.1938549255622426,0.6803927779537533,0.97212543554006947,0.77922077922077904,0.51694646816598022,1.0389610389610386,0.54925562242635395,1.1688311688311686,0.61387393094710152,1.2337662337662334,0,0,0,0,0,0,0,0,0.12923661704149506,0.32467532467532456,0,0,0,0,0,9.6927462781121299E-2,0.38866012036743736,0.58441558441558428,0,0,0,0,0,0,0,0,0,0,0,0,0,6.4618308520747528E-2,0.12987012987012983,0.12987012987012983,0,0,0,0,0.32309154260373768,0.45454545454545442,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2.2293316439657898,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER> 11 kV & < = 22 kV ; REACTOR ;",62,7.8740078740118111,0,2.2077922077922074,2.6493506493506493,2.6493506493506493,9.2987012987012978,5.324675324675324,9.3116883116883109,1.3246753246753247,2.662337662337662,5.3116883116883109,3.9740259740259734,10.623376623376622,7.987012987012986,17.714285714285712,0,21.705627705627705,0,24.36363636363636,0,16.861471861471859,0,0,0,0,0,0,0,1.7662337662337662,0,4.437229437229437,0,0,0,0,1.3246753246753247,2.6493506493506493,2.662337662337662,7.987012987012986,0,0,0,0,0,0,0,0,0,0,0,0,0.88311688311688308,0,1.7748917748917747,1.7748917748917747,0,0,0,4.4155844155844148,0,6.2121212121212119,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,30.467532467532465,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER> 22 kV & < = 66 kV ; REACTOR ;",62,7.8740078740118111,0,0.11846689895470379,0.14216027874564457,0.42787456445993027,0.49895470383275253,0.42857142857142855,7.1080139372822287E-2,0.21393728222996514,0.14285714285714285,0.14216027874564457,0.49895470383275253,0.71289198606271764,0.5714285714285714,0.37909407665505218,0.76190476190476186,0.40278745644599295,0.8571428571428571,0.45017421602787444,0.90476190476190466,0,0,0,0,0,0,0,0,9.4773519163763045E-2,0.23809523809523808,0,0,0,0,0,7.1080139372822287E-2,0.28501742160278742,0.42857142857142855,0,0,0,0,0,0,0,0,0,0,0,0,0,4.7386759581881523E-2,9.5238095238095233E-2,9.5238095238095233E-2,0,0,0,0,0.23693379790940758,0.33333333333333331,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.6348432055749127,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"OTHER - CROSS ARMS",45,6.7082039324993694,13152,13171.729208760487,13513.350029824593,18112.435475577389,17777.744112035736,19859.419477890307,17851.17748922035,11804.827122315153,12354.220744450877,10745.249690257688,6226.076065362834,5842.7257849280522,4711.1450628142666,3340.9148609641516,2802.795760617324,2615.6316498885458,3371.7145824986078,7628.1502417981274,5443.3943024576738,6996.0773604388387,2204.4046610854743,1912.2282163309392,3775.5936601122971,4594.5371500450947,7912.0357833504622,7587.7305707245496,6774.887823667239,10181.965184106077,12275.085886245857,10826.036233964744,10144.925822904626,11415.356667364151,11690.254936129606,12803.983694935892,7017.599903804412,4452.6260865183822,13238.361089016784,7581.1374476969495,2270.3531766436586,5155.8887350170198,5917.2974340289029,5714.1163372539859,13362.770785848863,1560.5381478652919,1470.1845104861331,1699.5660958519063,1878.6268640920484,1725.9247588564519,1983.574094695447,1776.0034238324349,1482.3227256355301,1345.6733897965348,1518.2247924985045,1121.0822327057517,730.99283549696395,747.97547584582037,1156.1206156693636,774.05360373710619,684.3860739064628,432.61573867188042,729.82447605638572,417.2371265242611,317.44913438272772,375.63714571057227,305.94776768809572,229.13919338723542,156.29789476440331,244.76614394970019,116.66182322322547,164.58276505987911,109.80223467718922,125.64353330002132,33.811451587458222,25.939231759857794,43.11285665471263,110.60051789838604,138.54545626566176,276.65777583567717,283.53853159151549,407.06579386552903,278.03540974545791,331.32774179977719,133.52428905585967,162.20566823479555,133.45157051618438,13.158164292470671,2.3369587100462121,12.178794417575542,7.0819354499443001,32,0.67850189233795122,21,1072.9384231624542,0,1,0,0,5,0,0,0,0,0,0,0,0,1]

{"sheet":"5.3 MD - Network level","index":22,"n_rows":15,"n_cols":4,"rows_kept":15,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"5.3 MAXIMUM DEMAND AT NETWORK LEVEL"]
[]
[]
[null,"5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL  (Summed at transmission connection point)"]
[null,null,"UNIT","2017"]
[null,"Raw network coincident MD","MW",1669.9741040000001]
[null,"Date MD occurred",null,"2017-01-23"]
[null,"Half hour time period MD occurred",null,"17:30:00"]
[null,"Winter/summer peaking",null,"Summer"]
[null,"Embedded generation","MW",133.554372]
[null,"Weather corrected (10% POE) network coincident MD","MW",1993.3484941369686]
[null,"Weather corrected (50% POE) network coincident MD","MW",1784.5130255574315]

{"sheet":"5.4 MD & utilisation-Spatial","index":23,"n_rows":11431,"n_cols":7,"rows_kept":11431,"cut":false,"hidden":false,"merged":[[11425,3,11426,3],[11425,4,11426,4],[11427,3,11428,3],[11427,4,11428,4],[11429,3,11430,3],[11429,4,11430,4],[11417,4,11418,4],[11419,3,11420,3],[11419,4,11420,4],[11421,3,11422,3],[11421,4,11422,4],[11423,3,11424,3],[11423,4,11424,4],[11409,2,11430,2],[11409,3,11410,3],[11409,4,11410,4],[11411,3,11412,3],[11411,4,11412,4],[11413,3,11414,3],[11413,4,11414,4],[11415,3,11416,3],[11415,4,11416,4],[11417,3,11418,3],[11403,3,11404,3],[11403,4,11404,4],[11405,3,11406,3],[11405,4,11406,4],[11407,3,11408,3],[11407,4,11408,4],[11395,4,11396,4],[11397,3,11398,3],[11397,4,11398,4],[11399,3,11400,3],[11399,4,11400,4],[11401,3,11402,3],[11401,4,11402,4],[11387,2,11408,2],[11387,3,11388,3],[11387,4,11388,4],[11389,3,11390,3],[11389,4,11390,4],[11391,3,11392,3],[11391,4,11392,4],[11393,3,11394,3],[11393,4,11394,4],[11395,3,11396,3],[11381,3,11382,3],[11381,4,11382,4],[11383,3,11384,3],[11383,4,11384,4],[11385,3,11386,3],[11385,4,11386,4],[11373,4,11374,4],[11375,3,11376,3],[11375,4,11376,4],[11377,3,11378,3],[11377,4,11378,4],[11379,3,11380,3],[11379,4,11380,4],[11365,2,11386,2],[11365,3,11366,3],[11365,4,11366,4],[11367,3,11368,3],[11367,4,11368,4],[11369,3,11370,3],[11369,4,11370,4],[11371,3,11372,3],[11371,4,11372,4],[11373,3,11374,3],[11359,3,11360,3],[11359,4,11360,4],[11361,3,11362,3],[11361,4,11362,4],[11363,3,11364,3],[11363,4,11364,4],[11351,4,11352,4],[11353,3,11354,3],[11353,4,11354,4],[11355,3,11356,3],[11355,4,11356,4],[11357,3,11358,3],[11357,4,11358,4],[11343,2,11364,2],[11343,3,11344,3],[11343,4,11344,4],[11345,3,11346,3],[11345,4,11346,4],[11347,3,11348,3],[11347,4,11348,4],[11349,3,11350,3],[11349,4,11350,4],[11351,3,11352,3],[11337,3,11338,3],[11337,4,11338,4],[11339,3,11340,3],[11339,4,11340,4],[11341,3,11342,3],[11341,4,11342,4],[11329,4,11330,4],[11331,3,11332,3],[11331,4,11332,4],[11333,3,11334,3],[11333,4,11334,4],[11335,3,11336,3],[11335,4,11336,4],[11321,2,11342,2],[11321,3,11322,3],[11321,4,11322,4],[11323,3,11324,3],[11323,4,11324,4],[11325,3,11326,3],[11325,4,11326,4],[11327,3,11328,3],[11327,4,11328,4],[11329,3,11330,3],[11315,3,11316,3],[11315,4,11316,4],[11317,3,11318,3],[11317,4,11318,4],[11319,3,11320,3],[11319,4,11320,4],[11307,4,11308,4],[11309,3,11310,3],[11309,4,11310,4],[11311,3,11312,3],[11311,4,11312,4],[11313,3,11314,3],[11313,4,11314,4],[11299,2,11320,2],[11299,3,11300,3],[11299,4,11300,4],[11301,3,11302,3],[11301,4,11302,4],[11303,3,11304,3],[11303,4,11304,4],[11305,3,11306,3],[11305,4,11306,4],[11307,3,11308,3],[11293,3,11294,3],[11293,4,11294,4],[11295,3,11296,3],[11295,4,11296,4],[11297,3,11298,3],[11297,4,11298,4],[11285,4,11286,4],[11287,3,11288,3],[11287,4,11288,4],[11289,3,11290,3],[11289,4,11290,4],[11291,3,11292,3],[11291,4,11292,4],[11277,2,11298,2],[11277,3,11278,3],[11277,4,11278,4],[11279,3,11280,3],[11279,4,11280,4],[11281,3,11282,3],[11281,4,11282,4],[11283,3,11284,3],[11283,4,11284,4],[11285,3,11286,3],[11271,3,11272,3],[11271,4,11272,4],[11273,3,11274,3],[11273,4,11274,4],[11275,3,11276,3],[11275,4,11276,4],[11263,4,11264,4],[11265,3,11266,3],[11265,4,11266,4],[11267,3,11268,3],[11267,4,11268,4],[11269,3,11270,3],[11269,4,11270,4],[11255,2,11276,2],[11255,3,11256,3],[11255,4,11256,4],[11257,3,11258,3],[11257,4,11258,4],[11259,3,11260,3],[11259,4,11260,4],[11261,3,11262,3],[11261,4,11262,4],[11263,3,11264,3],[11249,3,11250,3],[11249,4,11250,4],[11251,3,11252,3],[11251,4,11252,4],[11253,3,11254,3],[11253,4,11254,4],[11241,4,11242,4],[11243,3,11244,3],[11243,4,11244,4],[11245,3,11246,3],[11245,4,11246,4],[11247,3,11248,3],[11247,4,11248,4],[11233,2,11254,2],[11233,3,11234,3],[11233,4,11234,4],[11235,3,11236,3],[11235,4,11236,4],[11237,3,11238,3],[11237,4,11238,4],[11239,3,11240,3],[11239,4,11240,4],[11241,3,11242,3],[11227,3,11228,3],[11227,4,11228,4],[11229,3,11230,3],[11229,4,11230,4],[11231,3,11232,3],[11231,4,11232,4],[11219,4,11220,4],[11221,3,11222,3],[11221,4,11222,4],[11223,3,11224,3],[11223,4,11224,4],[11225,3,11226,3],[11225,4,11226,4],[11211,2,11232,2],[11211,3,11212,3],[11211,4,11212,4],[11213,3,11214,3],[11213,4,11214,4],[11215,3,11216,3],[11215,4,11216,4],[11217,3,11218,3],[11217,4,11218,4],[11219,3,11220,3],[11205,3,11206,3],[11205,4,11206,4],[11207,3,11208,3],[11207,4,11208,4],[11209,3,11210,3],[11209,4,11210,4],[11197,4,11198,4],[11199,3,11200,3],[11199,4,11200,4],[11201,3,11202,3],[11201,4,11202,4],[11203,3,11204,3],[11203,4,11204,4],[11189,2,11210,2],[11189,3,11190,3],[11189,4,11190,4],[11191,3,11192,3],[11191,4,11192,4],[11193,3,11194,3],[11193,4,11194,4],[11195,3,11196,3],[11195,4,11196,4],[11197,3,11198,3],[11183,3,11184,3],[11183,4,11184,4],[11185,3,11186,3],[11185,4,11186,4],[11187,3,11188,3],[11187,4,11188,4],[11175,4,11176,4],[11177,3,11178,3],[11177,4,11178,4],[11179,3,11180,3],[11179,4,11180,4],[11181,3,11182,3],[11181,4,11182,4],[11167,2,11188,2],[11167,3,11168,3],[11167,4,11168,4],[11169,3,11170,3],[11169,4,11170,4],[11171,3,11172,3],[11171,4,11172,4],[11173,3,11174,3],[11173,4,11174,4],[11175,3,11176,3],[11161,3,11162,3],[11161,4,11162,4],[11163,3,11164,3],[11163,4,11164,4],[11165,3,11166,3],[11165,4,11166,4],[11153,4,11154,4],[11155,3,11156,3],[11155,4,11156,4],[11157,3,11158,3],[11157,4,11158,4],[11159,3,11160,3],[11159,4,11160,4],[11145,2,11166,2],[11145,3,11146,3],[11145,4,11146,4],[11147,3,11148,3],[11147,4,11148,4],[11149,3,11150,3],[11149,4,11150,4],[11151,3,11152,3],[11151,4,11152,4],[11153,3,11154,3],[11139,3,11140,3],[11139,4,11140,4],[11141,3,11142,3],[11141,4,11142,4],[11143,3,11144,3],[11143,4,11144,4],[11131,4,11132,4],[11133,3,11134,3],[11133,4,11134,4],[11135,3,11136,3],[11135,4,11136,4],[11137,3,11138,3],[11137,4,11138,4],[11123,2,11144,2],[11123,3,11124,3],[11123,4,11124,4],[11125,3,11126,3],[11125,4,11126,4],[11127,3,11128,3],[11127,4,11128,4],[11129,3,11130,3],[11129,4,11130,4],[11131,3,11132,3],[11117,3,11118,3],[11117,4,11118,4],[11119,3,11120,3],[11119,4,11120,4],[11121,3,11122,3],[11121,4,11122,4],[11109,4,11110,4],[11111,3,11112,3],[11111,4,11112,4],[11113,3,11114,3],[11113,4,11114,4],[11115,3,11116,3],[11115,4,11116,4],[11101,2,11122,2],[11101,3,11102,3],[11101,4,11102,4],[11103,3,11104,3],[11103,4,11104,4],[11105,3,11106,3],[11105,4,11106,4],[11107,3,11108,3],[11107,4,11108,4],[11109,3,11110,3],[11095,3,11096,3],[11095,4,11096,4],[11097,3,11098,3],[11097,4,11098,4],[11099,3,11100,3],[11099,4,11100,4],[11087,4,11088,4],[11089,3,11090,3],[11089,4,11090,4],[11091,3,11092,3],[11091,4,11092,4],[11093,3,11094,3],[11093,4,11094,4],[11079,2,11100,2],[11079,3,11080,3],[11079,4,11080,4],[11081,3,11082,3],[11081,4,11082,4],[11083,3,11084,3],[11083,4,11084,4],[11085,3,11086,3],[11085,4,11086,4],[11087,3,11088,3],[11073,3,11074,3],[11073,4,11074,4],[11075,3,11076,3],[11075,4,11076,4],[11077,3,11078,3],[11077,4,11078,4],[11065,4,11066,4],[11067,3,11068,3],[11067,4,11068,4],[11069,3,11070,3],[11069,4,11070,4],[11071,3,11072,3],[11071,4,11072,4],[11057,2,11078,2],[11057,3,11058,3],[11057,4,11058,4],[11059,3,11060,3],[11059,4,11060,4],[11061,3,11062,3],[11061,4,11062,4],[11063,3,11064,3],[11063,4,11064,4],[11065,3,11066,3],[11051,3,11052,3],[11051,4,11052,4],[11053,3,11054,3],[11053,4,11054,4],[11055,3,11056,3],[11055,4,11056,4],[11043,4,11044,4],[11045,3,11046,3],[11045,4,11046,4],[11047,3,11048,3],[11047,4,11048,4],[11049,3,11050,3],[11049,4,11050,4],[11035,2,11056,2],[11035,3,11036,3],[11035,4,11036,4],[11037,3,11038,3],[11037,4,11038,4],[11039,3,11040,3],[11039,4,11040,4],[11041,3,11042,3],[11041,4,11042,4],[11043,3,11044,3],[11029,3,11030,3],[11029,4,11030,4],[11031,3,11032,3],[11031,4,11032,4],[11033,3,11034,3],[11033,4,11034,4],[11021,4,11022,4],[11023,3,11024,3],[11023,4,11024,4],[11025,3,11026,3],[11025,4,11026,4],[11027,3,11028,3],[11027,4,11028,4],[11013,2,11034,2],[11013,3,11014,3],[11013,4,11014,4],[11015,3,11016,3],[11015,4,11016,4],[11017,3,11018,3],[11017,4,11018,4],[11019,3,11020,3],[11019,4,11020,4],[11021,3,11022,3],[11007,3,11008,3],[11007,4,11008,4],[11009,3,11010,3],[11009,4,11010,4],[11011,3,11012,3],[11011,4,11012,4],[10999,4,11000,4],[11001,3,11002,3],[11001,4,11002,4],[11003,3,11004,3],[11003,4,11004,4],[11005,3,11006,3],[11005,4,11006,4],[10991,2,11012,2],[10991,3,10992,3],[10991,4,10992,4],[10993,3,10994,3],[10993,4,10994,4],[10995,3,10996,3],[10995,4,10996,4],[10997,3,10998,3],[10997,4,10998,4],[10999,3,11000,3],[10985,3,10986,3],[10985,4,10986,4],[10987,3,10988,3],[10987,4,10988,4],[10989,3,10990,3],[10989,4,10990,4],[10977,4,10978,4],[10979,3,10980,3],[10979,4,10980,4],[10981,3,10982,3],[10981,4,10982,4],[10983,3,10984,3],[10983,4,10984,4],[10969,2,10990,2],[10969,3,10970,3],[10969,4,10970,4],[10971,3,10972,3],[10971,4,10972,4],[10973,3,10974,3],[10973,4,10974,4],[10975,3,10976,3],[10975,4,10976,4],[10977,3,10978,3],[10963,3,10964,3],[10963,4,10964,4],[10965,3,10966,3],[10965,4,10966,4],[10967,3,10968,3],[10967,4,10968,4],[10955,4,10956,4],[10957,3,10958,3],[10957,4,10958,4],[10959,3,10960,3],[10959,4,10960,4],[10961,3,10962,3],[10961,4,10962,4],[10947,2,10968,2],[10947,3,10948,3],[10947,4,10948,4],[10949,3,10950,3],[10949,4,10950,4],[10951,3,10952,3],[10951,4,10952,4],[10953,3,10954,3],[10953,4,10954,4],[10955,3,10956,3],[10941,3,10942,3],[10941,4,10942,4],[10943,3,10944,3],[10943,4,10944,4],[10945,3,10946,3],[10945,4,10946,4],[10933,4,10934,4],[10935,3,10936,3],[10935,4,10936,4],[10937,3,10938,3],[10937,4,10938,4],[10939,3,10940,3],[10939,4,10940,4],[10925,2,10946,2],[10925,3,10926,3],[10925,4,10926,4],[10927,3,10928,3],[10927,4,10928,4],[10929,3,10930,3],[10929,4,10930,4],[10931,3,10932,3],[10931,4,10932,4],[10933,3,10934,3],[10919,3,10920,3],[10919,4,10920,4],[10921,3,10922,3],[10921,4,10922,4],[10923,3,10924,3],[10923,4,10924,4],[10911,4,10912,4],[10913,3,10914,3],[10913,4,10914,4],[10915,3,10916,3],[10915,4,10916,4],[10917,3,10918,3],[10917,4,10918,4],[10903,2,10924,2],[10903,3,10904,3],[10903,4,10904,4],[10905,3,10906,3],[10905,4,10906,4],[10907,3,10908,3],[10907,4,10908,4],[10909,3,10910,3],[10909,4,10910,4],[10911,3,10912,3],[10897,3,10898,3],[10897,4,10898,4],[10899,3,10900,3],[10899,4,10900,4],[10901,3,10902,3],[10901,4,10902,4],[10889,4,10890,4],[10891,3,10892,3],[10891,4,10892,4],[10893,3,10894,3],[10893,4,10894,4],[10895,3,10896,3],[10895,4,10896,4],[10881,2,10902,2],[10881,3,10882,3],[10881,4,10882,4],[10883,3,10884,3],[10883,4,10884,4],[10885,3,10886,3],[10885,4,10886,4],[10887,3,10888,3],[10887,4,10888,4],[10889,3,10890,3],[10875,3,10876,3],[10875,4,10876,4],[10877,3,10878,3],[10877,4,10878,4],[10879,3,10880,3],[10879,4,10880,4],[10867,4,10868,4],[10869,3,10870,3],[10869,4,10870,4],[10871,3,10872,3],[10871,4,10872,4],[10873,3,10874,3],[10873,4,10874,4],[10859,2,10880,2],[10859,3,10860,3],[10859,4,10860,4],[10861,3,10862,3],[10861,4,10862,4],[10863,3,10864,3],[10863,4,10864,4],[10865,3,10866,3],[10865,4,10866,4],[10867,3,10868,3],[10853,3,10854,3],[10853,4,10854,4],[10855,3,10856,3],[10855,4,10856,4],[10857,3,10858,3],[10857,4,10858,4],[10845,4,10846,4],[10847,3,10848,3],[10847,4,10848,4],[10849,3,10850,3],[10849,4,10850,4],[10851,3,10852,3],[10851,4,10852,4],[10837,2,10858,2],[10837,3,10838,3],[10837,4,10838,4],[10839,3,10840,3],[10839,4,10840,4],[10841,3,10842,3],[10841,4,10842,4],[10843,3,10844,3],[10843,4,10844,4],[10845,3,10846,3],[10831,3,10832,3],[10831,4,10832,4],[10833,3,10834,3],[10833,4,10834,4],[10835,3,10836,3],[10835,4,10836,4],[10823,4,10824,4],[10825,3,10826,3],[10825,4,10826,4],[10827,3,10828,3],[10827,4,10828,4],[10829,3,10830,3],[10829,4,10830,4],[10815,2,10836,2],[10815,3,10816,3],[10815,4,10816,4],[10817,3,10818,3],[10817,4,10818,4],[10819,3,10820,3],[10819,4,10820,4],[10821,3,10822,3],[10821,4,10822,4],[10823,3,10824,3],[10809,3,10810,3],[10809,4,10810,4],[10811,3,10812,3],[10811,4,10812,4],[10813,3,10814,3],[10813,4,10814,4],[10801,4,10802,4],[10803,3,10804,3],[10803,4,10804,4],[10805,3,10806,3],[10805,4,10806,4],[10807,3,10808,3],[10807,4,10808,4],[10793,2,10814,2],[10793,3,10794,3],[10793,4,10794,4],[10795,3,10796,3],[10795,4,10796,4],[10797,3,10798,3],[10797,4,10798,4],[10799,3,10800,3],[10799,4,10800,4],[10801,3,10802,3],[10787,3,10788,3],[10787,4,10788,4],[10789,3,10790,3],[10789,4,10790,4],[10791,3,10792,3],[10791,4,10792,4],[10779,4,10780,4],[10781,3,10782,3],[10781,4,10782,4],[10783,3,10784,3],[10783,4,10784,4],[10785,3,10786,3],[10785,4,10786,4],[10771,2,10792,2],[10771,3,10772,3],[10771,4,10772,4],[10773,3,10774,3],[10773,4,10774,4],[10775,3,10776,3],[10775,4,10776,4],[10777,3,10778,3],[10777,4,10778,4],[10779,3,10780,3],[10765,3,10766,3],[10765,4,10766,4],[10767,3,10768,3],[10767,4,10768,4],[10769,3,10770,3],[10769,4,10770,4],[10757,4,10758,4],[10759,3,10760,3],[10759,4,10760,4],[10761,3,10762,3],[10761,4,10762,4],[10763,3,10764,3],[10763,4,10764,4],[10749,2,10770,2],[10749,3,10750,3],[10749,4,10750,4],[10751,3,10752,3],[10751,4,10752,4],[10753,3,10754,3],[10753,4,10754,4],[10755,3,10756,3],[10755,4,10756,4],[10757,3,10758,3],[10743,3,10744,3],[10743,4,10744,4],[10745,3,10746,3],[10745,4,10746,4],[10747,3,10748,3],[10747,4,10748,4],[10735,4,10736,4],[10737,3,10738,3],[10737,4,10738,4],[10739,3,10740,3],[10739,4,10740,4],[10741,3,10742,3],[10741,4,10742,4],[10727,2,10748,2],[10727,3,10728,3],[10727,4,10728,4],[10729,3,10730,3],[10729,4,10730,4],[10731,3,10732,3],[10731,4,10732,4],[10733,3,10734,3],[10733,4,10734,4],[10735,3,10736,3],[10721,3,10722,3],[10721,4,10722,4],[10723,3,10724,3],[10723,4,10724,4],[10725,3,10726,3],[10725,4,10726,4],[10713,4,10714,4],[10715,3,10716,3],[10715,4,10716,4],[10717,3,10718,3],[10717,4,10718,4],[10719,3,10720,3],[10719,4,10720,4],[10705,2,10726,2],[10705,3,10706,3],[10705,4,10706,4],[10707,3,10708,3],[10707,4,10708,4],[10709,3,10710,3],[10709,4,10710,4],[10711,3,10712,3],[10711,4,10712,4],[10713,3,10714,3],[10699,3,10700,3],[10699,4,10700,4],[10701,3,10702,3],[10701,4,10702,4],[10703,3,10704,3],[10703,4,10704,4],[10691,4,10692,4],[10693,3,10694,3],[10693,4,10694,4],[10695,3,10696,3],[10695,4,10696,4],[10697,3,10698,3],[10697,4,10698,4],[10683,2,10704,2],[10683,3,10684,3],[10683,4,10684,4],[10685,3,10686,3],[10685,4,10686,4],[10687,3,10688,3],[10687,4,10688,4],[10689,3,10690,3],[10689,4,10690,4],[10691,3,10692,3],[10677,3,10678,3],[10677,4,10678,4],[10679,3,10680,3],[10679,4,10680,4],[10681,3,10682,3],[10681,4,10682,4],[10669,4,10670,4],[10671,3,10672,3],[10671,4,10672,4],[10673,3,10674,3],[10673,4,10674,4],[10675,3,10676,3],[10675,4,10676,4],[10661,2,10682,2],[10661,3,10662,3],[10661,4,10662,4],[10663,3,10664,3],[10663,4,10664,4],[10665,3,10666,3],[10665,4,10666,4],[10667,3,10668,3],[10667,4,10668,4],[10669,3,10670,3],[10655,3,10656,3],[10655,4,10656,4],[10657,3,10658,3],[10657,4,10658,4],[10659,3,10660,3],[10659,4,10660,4],[10647,4,10648,4],[10649,3,10650,3],[10649,4,10650,4],[10651,3,10652,3],[10651,4,10652,4],[10653,3,10654,3],[10653,4,10654,4],[10639,2,10660,2],[10639,3,10640,3],[10639,4,10640,4],[10641,3,10642,3],[10641,4,10642,4],[10643,3,10644,3],[10643,4,10644,4],[10645,3,10646,3],[10645,4,10646,4],[10647,3,10648,3],[10633,3,10634,3],[10633,4,10634,4],[10635,3,10636,3],[10635,4,10636,4],[10637,3,10638,3],[10637,4,10638,4],[10625,4,10626,4],[10627,3,10628,3],[10627,4,10628,4],[10629,3,10630,3],[10629,4,10630,4],[10631,3,10632,3],[10631,4,10632,4],[10617,2,10638,2],[10617,3,10618,3],[10617,4,10618,4],[10619,3,10620,3],[10619,4,10620,4],[10621,3,10622,3],[10621,4,10622,4],[10623,3,10624,3],[10623,4,10624,4],[10625,3,10626,3],[10611,3,10612,3],[10611,4,10612,4],[10613,3,10614,3],[10613,4,10614,4],[10615,3,10616,3],[10615,4,10616,4],[10603,4,10604,4],[10605,3,10606,3],[10605,4,10606,4],[10607,3,10608,3],[10607,4,10608,4],[10609,3,10610,3],[10609,4,10610,4],[10595,2,10616,2],[10595,3,10596,3],[10595,4,10596,4],[10597,3,10598,3],[10597,4,10598,4],[10599,3,10600,3],[10599,4,10600,4],[10601,3,10602,3],[10601,4,10602,4],[10603,3,10604,3],[10589,3,10590,3],[10589,4,10590,4],[10591,3,10592,3],[10591,4,10592,4],[10593,3,10594,3],[10593,4,10594,4],[10581,4,10582,4],[10583,3,10584,3],[10583,4,10584,4],[10585,3,10586,3],[10585,4,10586,4],[10587,3,10588,3],[10587,4,10588,4],[10573,2,10594,2],[10573,3,10574,3],[10573,4,10574,4],[10575,3,10576,3],[10575,4,10576,4],[10577,3,10578,3],[10577,4,10578,4],[10579,3,10580,3],[10579,4,10580,4],[10581,3,10582,3],[10567,3,10568,3],[10567,4,10568,4],[10569,3,10570,3],[10569,4,10570,4],[10571,3,10572,3],[10571,4,10572,4],[10559,4,10560,4],[10561,3,10562,3],[10561,4,10562,4],[10563,3,10564,3],[10563,4,10564,4],[10565,3,10566,3],[10565,4,10566,4],[10551,2,10572,2],[10551,3,10552,3],[10551,4,10552,4],[10553,3,10554,3],[10553,4,10554,4],[10555,3,10556,3],[10555,4,10556,4],[10557,3,10558,3],[10557,4,10558,4],[10559,3,10560,3],[10545,3,10546,3],[10545,4,10546,4],[10547,3,10548,3],[10547,4,10548,4],[10549,3,10550,3],[10549,4,10550,4],[10537,4,10538,4],[10539,3,10540,3],[10539,4,10540,4],[10541,3,10542,3],[10541,4,10542,4],[10543,3,10544,3],[10543,4,10544,4],[10529,2,10550,2],[10529,3,10530,3],[10529,4,10530,4],[10531,3,10532,3],[10531,4,10532,4],[10533,3,10534,3],[10533,4,10534,4],[10535,3,10536,3],[10535,4,10536,4],[10537,3,10538,3],[10523,3,10524,3],[10523,4,10524,4],[10525,3,10526,3],[10525,4,10526,4],[10527,3,10528,3],[10527,4,10528,4],[10515,4,10516,4],[10517,3,10518,3],[10517,4,10518,4],[10519,3,10520,3],[10519,4,10520,4],[10521,3,10522,3],[10521,4,10522,4],[10507,2,10528,2],[10507,3,10508,3],[10507,4,10508,4],[10509,3,10510,3],[10509,4,10510,4],[10511,3,10512,3],[10511,4,10512,4],[10513,3,10514,3],[10513,4,10514,4],[10515,3,10516,3],[10501,3,10502,3],[10501,4,10502,4],[10503,3,10504,3],[10503,4,10504,4],[10505,3,10506,3],[10505,4,10506,4],[10493,4,10494,4],[10495,3,10496,3],[10495,4,10496,4],[10497,3,10498,3],[10497,4,10498,4],[10499,3,10500,3],[10499,4,10500,4],[10485,2,10506,2],[10485,3,10486,3],[10485,4,10486,4],[10487,3,10488,3],[10487,4,10488,4],[10489,3,10490,3],[10489,4,10490,4],[10491,3,10492,3],[10491,4,10492,4],[10493,3,10494,3],[10479,3,10480,3],[10479,4,10480,4],[10481,3,10482,3],[10481,4,10482,4],[10483,3,10484,3],[10483,4,10484,4],[10471,4,10472,4],[10473,3,10474,3],[10473,4,10474,4],[10475,3,10476,3],[10475,4,10476,4]],"merged_total":11916,"flags":["merged_cut"]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL"]
[]
[null,"There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data."]
[]
[null,"5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND"]
[null,"NETWORK LEVEL","SUBSTATION","FORECASTING ELEMENTS","UNIT","MAX DEMAND","2017"]
[null,"SUBTRANSMISSION SUBSTATION","<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[]
[]
[]
[null,"NETWORK LEVEL","SUBSTATION","FORECASTING ELEMENTS","UNIT","MAX DEMAND","2017"]
[null,"ZONE SUBSTATION","BDL","Substation Rating","MVA","Non-Coincident",81]
[null,null,null,null,null,"Coincident",81]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",50]
[null,null,null,null,null,"Coincident",36.199996949999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",50.000399999999999]
[null,null,null,null,null,"Coincident",36.750990000000002]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-13"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4799500000000001]
[null,null,null,null,null,"Coincident",0.35892000000000002]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",50]
[null,null,null,null,null,"Coincident",43.209777466133303]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",50.000399999999999]
[null,null,null,null,null,"Coincident",43.867465009830354]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",50]
[null,null,null,null,null,"Coincident",38.682854978219645]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",50.000399999999999]
[null,null,null,null,null,"Coincident",39.271639123052481]
[null,null,"BGE","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.856000000000002]
[null,null,null,null,null,"Coincident",19.992000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.113230000000001]
[null,null,null,null,null,"Coincident",20.171900000000001]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.4389999999999997E-2]
[null,null,null,null,null,"Coincident",2.9654799999999999]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.475484477411708]
[null,null,null,null,null,"Coincident",23.863258118394317]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.78252458774557]
[null,null,null,null,null,"Coincident",24.077994019529726]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.492217295902506]
[null,null,null,null,null,"Coincident",21.363196184594351]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.767089992709387]
[null,null,null,null,null,"Coincident",21.555435029812863]
[null,null,"BN","Substation Rating","MVA","Non-Coincident",40.5]
[null,null,null,null,null,"Coincident",40.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",32.340000000000003]
[null,null,null,null,null,"Coincident",28.77]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",32.564]
[null,null,null,null,null,"Coincident",29.01726]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.22022]
[null,null,null,null,null,"Coincident",0.18362999999999999]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.703751609626018]
[null,null,null,null,null,"Coincident",30.505283476261223]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.930271101294416]
[null,null,null,null,null,"Coincident",30.767457143009239]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.277505114448061]
[null,null,null,null,null,"Coincident",27.309362046739786]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.480293028660686]
[null,null,null,null,null,"Coincident",27.544068784997584]
[null,null,"BRA","Substation Rating","MVA","Non-Coincident",99]
[null,null,null,null,null,"Coincident",99]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",66.155000000000001]
[null,null,null,null,null,"Coincident",60.527200000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",66.519490000000005]
[null,null,null,null,null,"Coincident",62.716059999999999]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.56176000000000004]
[null,null,null,null,null,"Coincident",6.6379999999999995E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",78.965278152379753]
[null,null,null,null,null,"Coincident",72.247708922752921]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",79.400348127948661]
[null,null,null,null,null,"Coincident",74.860420565661514]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",70.69238913524606]
[null,null,null,null,null,"Coincident",64.678593842746054]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",71.08187849985805]
[null,null,null,null,null,"Coincident",67.017581717926689]
[null,null,"BRT","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.577]
[null,null,null,null,null,"Coincident",6.4848999999999997]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.61126]
[null,null,null,null,null,"Coincident",6.5029620000000001]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-16"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.3999999999999999E-4]
[null,null,null,null,null,"Coincident",5.6579999999999998E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.577]
[null,null,null,null,null,"Coincident",6.8760414603825648]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.611259999999998]
[null,null,null,null,null,"Coincident",6.8951928830502132]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.577]
[null,null,null,null,null,"Coincident",6.1556649960689205]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.611259999999998]
[null,null,null,null,null,"Coincident",6.1728099977125845]
[null,null,"BWA","Substation Rating","MVA","Non-Coincident",33]
[null,null,null,null,null,"Coincident",33]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.5]
[null,null,null,null,null,"Coincident",8.34]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.811999999999999]
[null,null,null,null,null,"Coincident",8.4001199999999994]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.20280999999999999]
[null,null,null,null,null,"Coincident",1.426E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.533223801677687]
[null,null,null,null,null,"Coincident",8.843033166215454]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.905639594641823]
[null,null,null,null,null,"Coincident",8.9067793477445747]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.22016606333737]
[null,null,null,null,null,"Coincident",7.9165825328401045]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.553565283505108]
[null,null,null,null,null,"Coincident",7.9736502716739581]
[null,null,"BWN","Substation Rating","MVA","Non-Coincident",33]
[null,null,null,null,null,"Coincident",33]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.52]
[null,null,null,null,null,"Coincident",18.262499999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.957999999999998]
[null,null,null,null,null,"Coincident",18.492889999999999]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.5212]
[null,null,null,null,null,"Coincident",1.1900000000000001E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.493500229564393]
[null,null,null,null,null,"Coincident",21.798857112203692]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.016314708148663]
[null,null,null,null,null,"Coincident",22.073859915219742]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.927410249493601]
[null,null,null,null,null,"Coincident",19.515074545876068]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.395451462421388]
[null,null,null,null,null,"Coincident",19.761266361050573]
[null,null,"BWR","Substation Rating","MVA","Non-Coincident",81]
[null,null,null,null,null,"Coincident",81]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",57.155999999999999]
[null,null,null,null,null,"Coincident",48.45]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",59.816200000000002]
[null,null,null,null,null,"Coincident",50.992280000000001]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7155]
[null,null,null,null,null,"Coincident",9.3969999999999998E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",68.223708534160949]
[null,null,null,null,null,"Coincident",57.831875542027049]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",71.399030625325054]
[null,null,null,null,null,"Coincident",60.866443561696492]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",61.076172525343871]
[null,null,null,null,null,"Coincident",51.773051977971008]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",63.918828312171506]
[null,null,null,null,null,"Coincident",54.489699956971137]
[null,null,"CF","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.3279999999999994]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.4997399999999992]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-15"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.3279999999999994]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.4997399999999992]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.3279999999999994]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.4997399999999992]
[null,null,null,null,null,"Coincident"]
[null,null,"CLN","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",50.584000000000003]
[null,null,null,null,null,"Coincident",45.640625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",51.136980000000001]
[null,null,null,null,null,"Coincident",46.123989999999999]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.0000000000000001E-4]
[null,null,null,null,null,"Coincident",7.3730000000000004E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",62.691409163741127]
[null,null,null,null,null,"Coincident",54.478492149851974]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",63.376746334375426]
[null,null,null,null,null,"Coincident",55.055456123461298]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",56.123470919560845]
[null,null,null,null,null,"Coincident",48.770989689000679]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",56.737007946073149]
[null,null,null,null,null,"Coincident",49.287507362258303]
[null,null,"CNR","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.415]
[null,null,null,null,null,"Coincident",1.8772115707397461]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4167000000000001]
[null,null,null,null,null,"Coincident",1.8894457013129098]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-03"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",1.439E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.415]
[null,null,null,null,null,"Coincident",2.2407154989695375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.4167000000000001]
[null,null,null,null,null,"Coincident",2.2553186510164331]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.415]
[null,null,null,null,null,"Coincident",2.0059643390207937]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.4167000000000001]
[null,null,null,null,null,"Coincident",2.0190375748942651]
[null,null,"CPK","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",38]
[null,null,null,null,null,"Coincident",34.200000000000003]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.029589999999999]
[null,null,null,null,null,"Coincident",34.206000000000003]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.39533000000000001]
[null,null,null,null,null,"Coincident",2.7300000000000001E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",47.095396730629496]
[null,null,null,null,null,"Coincident",40.82250038260733]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",47.132069172452105]
[null,null,null,null,null,"Coincident",40.829662224779717]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",42.161392830604775]
[null,null,null,null,null,"Coincident",36.545683749156005]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",42.194223241495756]
[null,null,null,null,null,"Coincident",36.552095272620768]
[null,null,"CRE","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",42.51]
[null,null,null,null,null,"Coincident",39.51]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.52646]
[null,null,null,null,null,"Coincident",40.169670000000004]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.61499999999999999]
[null,null,null,null,null,"Coincident",5.1090000000000003E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",52.68487671102789]
[null,null,null,null,null,"Coincident",47.160730705170039]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",52.705276453927532]
[null,null,null,null,null,"Coincident",47.948139442813165]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",47.165284453394968]
[null,null,null,null,null,"Coincident",42.219882015472329]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",47.183546993552653]
[null,null,null,null,null,"Coincident",42.924796962805836]
[null,null,"CYN","Substation Rating","MVA","Non-Coincident",99]
[null,null,null,null,null,"Coincident",99]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",66.05]
[null,null,null,null,null,"Coincident",54.024999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",67.067819999999998]
[null,null,null,null,null,"Coincident",54.490070000000003]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.48948000000000003]
[null,null,null,null,null,"Coincident",3.2349999999999997E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",78.839945914362971]
[null,null,null,null,null,"Coincident",64.486420560536857]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",80.054856947679511]
[null,null,null,null,null,"Coincident",65.041546883722219]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",70.580187474612686]
[null,null,null,null,null,"Coincident",57.730425863981083]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",71.66781694343041]
[null,null,null,null,null,"Coincident",58.2273937336074]
[null,null,"DRN","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",56.88]
[null,null,null,null,null,"Coincident",48.659999847412109]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",57.812199999999997]
[null,null,null,null,null,"Coincident",49.237648043578211]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.13889000000000001]
[null,null,null,null,null,"Coincident",0.18099999999999999]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",70.494372790479105]
[null,null,null,null,null,"Coincident",58.08253983592553]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",71.649697233434168]
[null,null,null,null,null,"Coincident",58.772044037943168]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",63.108948005389465]
[null,null,null,null,null,"Coincident",51.997455136184279]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",64.143233542144458]
[null,null,null,null,null,"Coincident",52.614722630200561]
[null,null,"ELM","Substation Rating","MVA","Non-Coincident",99]
[null,null,null,null,null,"Coincident",99]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",64.349999999999994]
[null,null,null,null,null,"Coincident",58.450000762939453]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",64.535529999999994]
[null,null,null,null,null,"Coincident",59.107247343426501]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.11081000000000001]
[null,null,null,null,null,"Coincident",6.6449999999999995E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",79.752336305684423]
[null,null,null,null,null,"Coincident",69.768280073347782]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",79.982273383458988]
[null,null,null,null,null,"Coincident",70.552796119646018]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",71.396990227616243]
[null,null,null,null,null,"Coincident",62.458925234512058]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",71.602837680559972]
[null,null,null,null,null,"Coincident",63.161250546666849]
[null,null,"EPG","Substation Rating","MVA","Non-Coincident",99]
[null,null,null,null,null,"Coincident",99]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",51.194000000000003]
[null,null,null,null,null,"Coincident",44.652000427246094]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",52.245869999999996]
[null,null,null,null,null,"Coincident",45.022556613680131]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.9127200000000002]
[null,null,null,null,null,"Coincident",6.0542499999999997]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",61.107224695532146]
[null,null,null,null,null,"Coincident",53.2984299568841]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",62.362779183176968]
[null,null,null,null,null,"Coincident",53.740740777424485]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",54.70525537585651]
[null,null,null,null,null,"Coincident",47.714558081324988]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",55.829270240336754]
[null,null,null,null,null,"Coincident",48.110529695380883]
[null,null,"FGY","Substation Rating","MVA","Non-Coincident",93]
[null,null,null,null,null,"Coincident",93]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",68.813000000000002]
[null,null,null,null,null,"Coincident",59.5]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",69.4559]
[null,null,null,null,null,"Coincident",60.048813528493717]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.78359000000000001]
[null,null,null,null,null,"Coincident",5.185E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",82.137974234747304]
[null,null,null,null,null,"Coincident",71.02160154284023]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",82.905365623518591]
[null,null,null,null,null,"Coincident",71.676687521697389]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",73.532694030136611]
[null,null,null,null,null,"Coincident",63.580941025578426]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",74.219688769386096]
[null,null,null,null,null,"Coincident",64.167396161531343]
[null,null,"FTR","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18]
[null,null,null,null,null,"Coincident",15.315428733825684]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.123480000000001]
[null,null,null,null,null,"Coincident",15.777883943051046]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-28"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.14327000000000001]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.33836240216921]
[null,null,null,null,null,"Coincident",18.281113899017374]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.519043568248094]
[null,null,null,null,null,"Coincident",18.83311910239577]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.578993295335689]
[null,null,null,null,null,"Coincident",16.365871783307899]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.740745189341695]
[null,null,null,null,null,"Coincident",16.860045520866375]
[null,null,"HPK","Substation Rating","MVA","Non-Coincident",99]
[null,null,null,null,null,"Coincident",99]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",45.43]
[null,null,null,null,null,"Coincident",43.416751861572266]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.637430000000002]
[null,null,null,null,null,"Coincident",43.707440972306053]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.2295400000000001]
[null,null,null,null,null,"Coincident",5.2668999999999997]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",56.30378614401311]
[null,null,null,null,null,"Coincident",51.823987411713482]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",56.560865042535077]
[null,null,null,null,null,"Coincident",52.170965667097981]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",50.405054639325655]
[null,null,null,null,null,"Coincident",46.394587220719302]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",50.635200368663881]
[null,null,null,null,null,"Coincident",46.705213896456158]
[null,null,"KLK","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.18]
[null,null,null,null,null,"Coincident",3.6180000305175781]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.1844659999999996]
[null,null,null,null,null,"Coincident",3.6334761904292301]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-20"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",3.6339999999999997E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.18]
[null,null,null,null,null,"Coincident",4.3185908663765247]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.1844660000000005]
[null,null,null,null,null,"Coincident",4.3370638354968376]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.18]
[null,null,null,null,null,"Coincident",3.866148681863514]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.1844660000000005]
[null,null,null,null,null,"Coincident",3.8826863089331805]
[null,null,"KLO","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.5]
[null,null,null,null,null,"Coincident",20.849989999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.521270000000001]
[null,null,null,null,null,"Coincident",20.857641333150191]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.0189999999999997E-2]
[null,null,null,null,null,"Coincident",7.8899999999999998E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",29.124784820257716]
[null,null,null,null,null,"Coincident",24.887389612642071]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",29.151145848901415]
[null,null,null,null,null,"Coincident",24.896522552713744]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.073492934716111]
[null,null,null,null,null,"Coincident",22.280033354183189]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.097092219597876]
[null,null,null,null,null,"Coincident",22.288209471188054]
[null,null,"KMS","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.04]
[null,null,null,null,null,"Coincident",5.5894729999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.05899]
[null,null,null,null,null,"Coincident",5.6602802700554466]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-23"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.6000000000000001E-3]
[null,null,null,null,null,"Coincident",5.1330000000000001E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.04]
[null,null,null,null,null,"Coincident",5.9266061295762338]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.05899]
[null,null,null,null,null,"Coincident",6.0016841916277315]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.04]
[null,null,null,null,null,"Coincident",5.3056983596620357]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.05899]
[null,null,null,null,null,"Coincident",5.3729107814029282]
[null,null,"LDL","Substation Rating","MVA","Non-Coincident",99]
[null,null,null,null,null,"Coincident",99]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",58.241999999999997]
[null,null,null,null,null,"Coincident",52.762500762939453]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",58.996200000000002]
[null,null,null,null,null,"Coincident",54.477106183599652]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.5007299999999999]
[null,null,null,null,null,"Coincident",2.0079799999999999]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",69.520001967363029]
[null,null,null,null,null,"Coincident",62.979450514105707]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",70.420245528432105]
[null,null,null,null,null,"Coincident",65.026072749220376]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",62.236658272466194]
[null,null,null,null,null,"Coincident",56.381335283537652]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",63.042586771987054]
[null,null,null,null,null,"Coincident",58.213540764766776]
[null,null,"LGA","Substation Rating","MVA","Non-Coincident",73]
[null,null,null,null,null,"Coincident",73]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",38.46]
[null,null,null,null,null,"Coincident",33.463000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",39.639200000000002]
[null,null,null,null,null,"Coincident",33.463700000000003]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-05"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.0000000000000002E-4]
[null,null,null,null,null,"Coincident",0.15944]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",38.46]
[null,null,null,null,null,"Coincident",39.942787435765759]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",39.639200000000002]
[null,null,null,null,null,"Coincident",39.943622984019207]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",38.46]
[null,null,null,null,null,"Coincident",35.758134950234137]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",39.639200000000002]
[null,null,null,null,null,"Coincident",35.758882961305027]
[null,null,"LLG","Substation Rating","MVA","Non-Coincident",33]
[null,null,null,null,null,"Coincident",33]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.2]
[null,null,null,null,null,"Coincident",16.649999618530273]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.568560000000002]
[null,null,null,null,null,"Coincident",16.66779491317568]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-05"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.6000000000000002E-4]
[null,null,null,null,null,"Coincident",2.843E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.2]
[null,null,null,null,null,"Coincident",19.874111573036956]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.568560000000002]
[null,null,null,null,null,"Coincident",19.895352754980543]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.2]
[null,null,null,null,null,"Coincident",17.791977207087001]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.568560000000002]
[null,null,null,null,null,"Coincident",17.81099303195057]
[null,null,"LYD","Substation Rating","MVA","Non-Coincident",33]
[null,null,null,null,null,"Coincident",33]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.8]
[null,null,null,null,null,"Coincident",16.7]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.087430000000001]
[null,null,null,null,null,"Coincident",16.97803]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.19083]
[null,null,null,null,null,"Coincident",0.21423]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.299827856206175]
[null,null,null,null,null,"Coincident",19.933794046477846]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.656054958371566]
[null,null,null,null,null,"Coincident",20.265661876342651]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.858794347772889]
[null,null,null,null,null,"Coincident",17.845406976927052]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.177700904122908]
[null,null,null,null,null,"Coincident",18.142506288411784]
[null,null,"MBY","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.3000000000000007]
[null,null,null,null,null,"Coincident",2.5439999103546143]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.3193350000000006]
[null,null,null,null,null,"Coincident",3.2696867031023187]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-22"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",4.9509999999999998E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.3000000000000007]
[null,null,null,null,null,"Coincident",2.6974431153615099]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.3193350000000024]
[null,null,null,null,null,"Coincident",3.4669002348522135]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.3000000000000007]
[null,null,null,null,null,"Coincident",2.4148423565779535]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.3193350000000024]
[null,null,null,null,null,"Coincident",3.1036864078704274]
[null,null,"MDI","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.45700000000000002]
[null,null,null,null,null,"Coincident",0.45700000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.66132043986373235]
[null,null,null,null,null,"Coincident",0.66132043986373235]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-23"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",1E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.4845642874053312]
[null,null,null,null,null,"Coincident",0.4845642874053312]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.70120846321476937]
[null,null,null,null,null,"Coincident",0.70120846321476937]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.43379834742301299]
[null,null,null,null,null,"Coincident",0.43379834742301299]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.62774554470447941]
[null,null,null,null,null,"Coincident",0.62774554470447941]
[null,null,"MFA","Substation Rating","MVA","Non-Coincident",40.5]
[null,null,null,null,null,"Coincident",40.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.164000000000001]
[null,null,null,null,null,"Coincident",24.732000350952148]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",26.00299]
[null,null,null,null,null,"Coincident",25.386421037013012]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.9769080000000001]
[null,null,null,null,null,"Coincident",1.12266]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.108857031622911]
[null,null,null,null,null,"Coincident",29.521113853490895]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",29.046031167728508]
[null,null,null,null,null,"Coincident",30.302256798143112]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.164000000000001]
[null,null,null,null,null,"Coincident",26.428300096781069]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.00299]
[null,null,null,null,null,"Coincident",27.127605694198788]
[null,null,"MJG","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.8]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.00714]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-19"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.0000000000000001E-4]
[null,null,null,null,null,"Coincident",4.0499999999999998E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.8]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.00714]
[null,null,null,null,null,"Coincident",{"$error":"#DIV/0!"}]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.8]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.00714]
[null,null,null,null,null,"Coincident",{"$error":"#DIV/0!"}]
[null,null,"MOE","Substation Rating","MVA","Non-Coincident",40.5]
[null,null,null,null,null,"Coincident",40.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.64]
[null,null,null,null,null,"Coincident",26.190000534057617]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.643660000000001]
[null,null,null,null,null,"Coincident",26.190069262485299]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.23733]
[null,null,null,null,null,"Coincident",0.66518999999999995]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",38.766364037841804]
[null,null,null,null,null,"Coincident",31.261441719943075]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",38.771497355221641]
[null,null,null,null,null,"Coincident",31.261523756968373]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",34.704960915016194]
[null,null,null,null,null,"Coincident",27.986300494382938]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",34.709556434442717]
[null,null,null,null,null,"Coincident",27.986373936704066]
[null,null,"MSD","Substation Rating","MVA","Non-Coincident",26]
[null,null,null,null,null,"Coincident",26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.32]
[null,null,null,null,null,"Coincident",10.751999855041504]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.322379999999999]
[null,null,null,null,null,"Coincident",10.794771921704218]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-11"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",9.0660000000000004E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.32]
[null,null,null,null,null,"Coincident",11.400514546915559]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.322379999999999]
[null,null,null,null,null,"Coincident",11.445866441889894]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.32]
[null,null,null,null,null,"Coincident",10.206126408335841]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.322379999999999]
[null,null,null,null,null,"Coincident",10.246726959395254]
[null,null,"MYT","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.2]
[null,null,null,null,null,"Coincident",10.560000419616699]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.26746]
[null,null,null,null,null,"Coincident",10.568845670245558]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-02"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.8100000000000001E-3]
[null,null,null,null,null,"Coincident",6.191E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.2]
[null,null,null,null,null,"Coincident",11.196934525889638]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.26746]
[null,null,null,null,null,"Coincident",11.206313284243894]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.2]
[null,null,null,null,null,"Coincident",10.02387468449901]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.26746]
[null,null,null,null,null,"Coincident",10.032270866348773]
[null,null,"NLA","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.5359999999999996]
[null,null,null,null,null,"Coincident",4.5079998970031738]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.5361709999999995]
[null,null,null,null,null,"Coincident",4.5079998970031738]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-18"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident","0.053.50"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.5359999999999996]
[null,null,null,null,null,"Coincident",5.3809306292457846]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.5361709999999995]
[null,null,null,null,null,"Coincident",5.3809306292457846]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.5359999999999996]
[null,null,null,null,null,"Coincident",4.8171911864650827]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.5361709999999995]
[null,null,null,null,null,"Coincident",4.8171911864650827]
[null,null,"NRN","Substation Rating","MVA","Non-Coincident",33]
[null,null,null,null,null,"Coincident",33]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.05]
[null,null,null,null,null,"Coincident",19.020000457763672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.369]
[null,null,null,null,null,"Coincident",19.971192234612605]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.26817]
[null,null,null,null,null,"Coincident",1.7979000000000001]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.319769983523145]
[null,null,null,null,null,"Coincident",22.703040232872777]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.894181621086275]
[null,null,null,null,null,"Coincident",23.838421129783551]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.562348733008477]
[null,null,null,null,null,"Coincident",20.324529872462971]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.971815308012474]
[null,null,null,null,null,"Coincident",21.340961271922588]
[null,null,"OFR","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",38.1]
[null,null,null,null,null,"Coincident",33.5]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.426679999999998]
[null,null,null,null,null,"Coincident",33.828094872300476]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.6000000000000003E-2]
[null,null,null,null,null,"Coincident",4.8489999999999998E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",47.219331985183786]
[null,null,null,null,null,"Coincident",39.986952129162148]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",47.624203674761723]
[null,null,null,null,null,"Coincident",40.378579411326413]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",42.272343864369525]
[null,null,null,null,null,"Coincident",35.797672678266842]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",42.634798701472199]
[null,null,null,null,null,"Coincident",36.14827067367073]
[null,null,"PHI","Substation Rating","MVA","Non-Coincident",26]
[null,null,null,null,null,"Coincident",26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.997]
[null,null,null,null,null,"Coincident",13.637286186218262]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.39171]
[null,null,null,null,null,"Coincident",13.841950254468907]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-10"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1E-4]
[null,null,null,null,null,"Coincident",3.2739999999999998E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.997]
[null,null,null,null,null,"Coincident",16.278015220895337]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.39171]
[null,null,null,null,null,"Coincident",16.522310513423641]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.997]
[null,null,null,null,null,"Coincident",14.572630063107203]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.39171]
[null,null,null,null,null,"Coincident",14.791331475771056]
[null,null,"PHM","Substation Rating","MVA","Non-Coincident",39.5]
[null,null,null,null,null,"Coincident",39.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",40.83]
[null,null,null,null,null,"Coincident",35.430000305175781]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",40.893610000000002]
[null,null,null,null,null,"Coincident",35.47569479873642]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",7.6990000000000003E-2]
[null,null,null,null,null,"Coincident",9.6659999999999996E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",50.602764434515855]
[null,null,null,null,null,"Coincident",42.29067839221684]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",50.681599649937837]
[null,null,null,null,null,"Coincident",42.345221184054921]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",45.301307086147183]
[null,null,null,null,null,"Coincident",37.860046385539611]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",45.371883038724945]
[null,null,null,null,null,"Coincident",37.908874938485376]
[null,null,"RUBA","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.3]
[null,null,null,null,null,"Coincident",0.78774833679199197]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.32227]
[null,null,null,null,null,"Coincident",1.8584367464388396]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-23"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.2291299999999996]
[null,null,null,null,null,"Coincident",1.92269]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.3]
[null,null,null,null,null,"Coincident",0.83526195070535325]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.32227]
[null,null,null,null,null,"Coincident",1.9705297105602158]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.3]
[null,null,null,null,null,"Coincident",0.74775476298816879]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.32227]
[null,null,null,null,null,"Coincident",1.7640848783268481]
[null,null,"RWN","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.64]
[null,null,null,null,null,"Coincident",27.857999801635742]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",35.849499999999999]
[null,null,null,null,null,"Coincident",27.913856378104406]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.3600000000000001E-3]
[null,null,null,null,null,"Coincident",3.0300000000000001E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",44.170524723148297]
[null,null,null,null,null,"Coincident",33.252432969618418]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",44.43016908143953]
[null,null,null,null,null,"Coincident",33.319105633778157]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",39.542948433756692]
[null,null,null,null,null,"Coincident",29.768703234930715]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",39.775390849493839]
[null,null,null,null,null,"Coincident",29.828390860045751]
[null,null,"SLE","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",26.639999389648437]
[null,null,null,null,null,"Coincident",26.639999389648437]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",26.825586071534094]
[null,null,null,null,null,"Coincident",26.825586071534094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-23"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.89217000000000002]
[null,null,null,null,null,"Coincident",0.28142]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",31.798578516859131]
[null,null,null,null,null,"Coincident",31.798578516859131]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.020102271019482]
[null,null,null,null,null,"Coincident",32.020102271019482]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.467163531339203]
[null,null,null,null,null,"Coincident",28.467163531339203]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.665479092282141]
[null,null,null,null,null,"Coincident",28.665479092282141]
[null,null,"SMG","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",32.32]
[null,null,null,null,null,"Coincident",29.2299995422363]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",32.349879999999999]
[null,null,null,null,null,"Coincident",29.821485064220848]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.77917999999999998]
[null,null,null,null,null,"Coincident",6.3829999999999998E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",38.578456501925984]
[null,null,null,null,null,"Coincident",34.890107236741322]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",38.61412247594447]
[null,null,null,null,null,"Coincident",35.596128229358889]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",34.536739730196551]
[null,null,null,null,null,"Coincident",31.234804656682531]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",34.568669117051073]
[null,null,null,null,null,"Coincident",31.866858540561235]
[null,null,"SMR","Substation Rating","MVA","Non-Coincident",38.5]
[null,null,null,null,null,"Coincident",38.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",31.59]
[null,null,null,null,null,"Coincident",26.639999389648437]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",32.188830000000003]
[null,null,null,null,null,"Coincident",26.825586071534094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.1234]
[null,null,null,null,null,"Coincident",9.2920000000000003E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.830134615749635]
[null,null,null,null,null,"Coincident",28.246810329810618]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.452472998527398]
[null,null,null,null,null,"Coincident",28.443590807403272]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.39064745824799]
[null,null,null,null,null,"Coincident",25.287500460786795]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.947785838033454]
[null,null,null,null,null,"Coincident",25.463665003250075]
[null,null,"TGN","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",38.799999999999997]
[null,null,null,null,null,"Coincident",34.917000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.841729999999998]
[null,null,null,null,null,"Coincident",35.04]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.32563999999999999]
[null,null,null,null,null,"Coincident",0.2306]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",44.730010379207883]
[null,null,null,null,null,"Coincident",41.678340522207606]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",44.778118197071912]
[null,null,null,null,null,"Coincident",41.825158286741541]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",40.043818925688981]
[null,null,null,null,null,"Coincident",37.31186080319533]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",40.086886672177869]
[null,null,null,null,null,"Coincident",37.443297034222994]
[null,null,"TT","Substation Rating","MVA","Non-Coincident",84]
[null,null,null,null,null,"Coincident",84]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",70.7]
[null,null,null,null,null,"Coincident",57.799999237060547]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",70.772379999999998]
[null,null,null,null,null,"Coincident",57.959726650878189]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.80691000000000002]
[null,null,null,null,null,"Coincident",0.11819]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",84.390373597963105]
[null,null,null,null,null,"Coincident",68.99241201665518]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",84.476769287369322]
[null,null,null,null,null,"Coincident",69.183069104716111]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",75.549118159804962]
[null,null,null,null,null,"Coincident",61.764341895294535]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",75.626462504534885]
[null,null,null,null,null,"Coincident",61.935024572237523]
[null,null,"WGI","Substation Rating","MVA","Non-Coincident",40.5]
[null,null,null,null,null,"Coincident",40.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",32.01]
[null,null,null,null,null,"Coincident",27.98]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.907550000000001]
[null,null,null,null,null,"Coincident",28.1]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-11"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Winter"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",14.62238]
[null,null,null,null,null,"Coincident",4.0716599999999996]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.01]
[null,null,null,null,null,"Coincident",33.398057330565877]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.907550000000001]
[null,null,null,null,null,"Coincident",33.541294174013622]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",32.01]
[null,null,null,null,null,"Coincident",29.899071090683773]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",33.907550000000001]
[null,null,null,null,null,"Coincident",30.027301559979058]
[null,null,"WGL","Substation Rating","MVA","Non-Coincident",84]
[null,null,null,null,null,"Coincident",84]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",53.25]
[null,null,null,null,null,"Coincident",47.450000762939453]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",54.565649999999998]
[null,null,null,null,null,"Coincident",48.630495209052206]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.40111999999999998]
[null,null,null,null,null,"Coincident",0.46922000000000003]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",61.388480739505674]
[null,null,null,null,null,"Coincident",56.638236090637825]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",62.905208527016107]
[null,null,null,null,null,"Coincident",58.047321908711027]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",54.957045303941712]
[null,null,null,null,null,"Coincident",50.704465549111006]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",56.314871344394874]
[null,null,null,null,null,"Coincident",51.965926855990297]
[null,null,"WN","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",47.04]
[null,null,null,null,null,"Coincident",41.459999084472656]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",47.870829999999998]
[null,null,null,null,null,"Coincident",41.682388675851982]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.26229000000000002]
[null,null,null,null,null,"Coincident",0.40162999999999999]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",47.569093250365107]
[null,null,null,null,null,"Coincident",43.960689085761871]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",48.409268202431448]
[null,null,null,null,null,"Coincident",44.196492267103423]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",42.585461984651722]
[null,null,null,null,null,"Coincident",39.355096470467984]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",43.337615032710993]
[null,null,null,null,null,"Coincident",39.566195457829984]
[null,null,"WO","Substation Rating","MVA","Non-Coincident",99]
[null,null,null,null,null,"Coincident",99]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",42.75]
[null,null,null,null,null,"Coincident",39.674999237060547]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.751049999999999]
[null,null,null,null,null,"Coincident",39.685205863367266]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.28111000000000003]
[null,null,null,null,null,"Coincident",3.8260000000000002E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",43.230840485822881]
[null,null,null,null,null,"Coincident",42.068025674208542]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",43.231902295940081]
[null,null,null,null,null,"Coincident",42.078847920604879]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",38.70171130620453]
[null,null,null,null,null,"Coincident",37.660720137956595]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",38.702661874552405]
[null,null,null,null,null,"Coincident",37.670408579148322]
[null,null,"WT","Substation Rating","MVA","Non-Coincident",109]
[null,null,null,null,null,"Coincident",109]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",60.01]
[null,null,null,null,null,"Coincident",57.115000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",61.547289999999997]
[null,null,null,null,null,"Coincident",57.262999999999998]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.3139999999999998E-2]
[null,null,null,null,null,"Coincident",8.0430000000000001E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",74.373546258028313]
[null,null,null,null,null,"Coincident",68.174769279316294]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",76.278790532765939]
[null,null,null,null,null,"Coincident",68.351428052901838]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",66.58171536222612]
[null,null,null,null,null,"Coincident",61.032360448334657]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",68.287354509188248]
[null,null,null,null,null,"Coincident",61.1905113604655]
[null,null,"WYK","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",28.2]
[null,null,null,null,null,"Coincident",23.520000457763672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.204080000000001]
[null,null,null,null,null,"Coincident",23.915447944150145]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-01-23"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","17:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.71696000000000004]
[null,null,null,null,null,"Coincident",0.11987]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.660658210220078]
[null,null,null,null,null,"Coincident",28.074421862163216]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.665528262897304]
[null,null,null,null,null,"Coincident",28.546443942991079]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",30.13416028439179]
[null,null,null,null,null,"Coincident",25.133172471036129]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.138520120347831]
[null,null,null,null,null,"Coincident",25.555742610710947]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]

{"sheet":"6.3 Sustained interruptionss","index":24,"n_rows":60015,"n_cols":12,"rows_kept":4500,"cut":true,"hidden":false,"merged":[[7,1,7,4],[11,1,11,4],[11,7,11,8],[11,10,11,11],[10,5,10,6],[10,1,10,4],[10,10,10,11],[10,7,10,9]],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
[null,"REGULATORY REPORTING STATEMENT"]
[null,"AusNet Services (D)"]
[null,"CATEGORY ANALYSIS 2017"]
[null,"6.3 SUSTAINED INTERRUPTIONS TO SUPPLY"]
[]
[null,"6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2015-16)"]
[]
[null,"There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data."]
[]
[null,"Definitions:"]
[null,"Feeder classification definitions\n(column E)",null,null,null,"Average duration of sustained customer interruption \n(column I)",null,"Average duration of sustained customer interruption \n(column J)",null,null,"Effect on unplanned SAIFI \n(column K)"]
[null,"CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas.\nUrban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km.\nShort rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km.\nLong rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km.\n",null,null,null,"The average duration of an  interruption experienced by an affected customer.",null,"The sum of the duration of each unplanned sustained customer\ninterruption (in minutes) divided by the total number of distribution\ncustomers. Unplanned SAIDI excludes momentary interruptions (one minute or less).",null,null,"The total number of unplanned sustained customer interruptions\ndivided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions."]
[]
[null,"Date of event\n(DD/MM/YYYY)","Time of interruption\n(HH:MM)","Asset ID\n(eg. feeder ID)","Feeder classification\n(CBD, Urban, Short rural, Long rural)","Reason for interruption\n(select from options in drop-down box)","Detailed reason for interruption\n(select from options in column 'O' that correspond with reason in column 'F')","Number of customers affected by the interruption","Average duration of sustained customer interruption\n(minutes)"," Average duration of sustained customer\ninterruption","Effect on unplanned SAIFI\n(by feeder classification)","MED"]
[null,"2017-01-01",42736.006620370368,"WYK12","RURAL SHORT","Unknown","Unknown",3969,0,0,0,"NO"]
[null,"2017-01-01",42736.014826388891,"FTR22","RURAL SHORT","Unknown","Unknown",362,0,0,0,"NO"]
[null,"2017-01-01",42736.022222222222,"WN1","URBAN","Asset failure","LV",1,78,2.6536749996597853E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-01",42736.034722222219,"ELM15","RURAL SHORT","Animal","Animal impact",9,98,2.9948811979524791E-3,3.0560012224004888E-5,"NO"]
[null,"2017-01-01",42736.044351851851,"RWN34","RURAL SHORT","Unknown","Unknown",2098,32.856053384175404,0.23406252918056722,7.1238784051069178E-3,"NO"]
[null,"2017-01-01",42736.054224537038,"BGE24","RURAL SHORT","Unknown","Unknown",795,0,0,0,"NO"]
[null,"2017-01-01",42736.094502314816,"EPG35","URBAN","Unknown","Unknown",148,0,0,0,"NO"]
[null,"2017-01-01",42736.173136574071,"SMR5","RURAL LONG","Animal","Animal impact",80,18.462499999999999,1.228948944951075E-2,6.656460094521733E-4,"NO"]
[null,"2017-01-01",42736.218055555553,"RWN34","RURAL SHORT","Animal","Animal impact",24,193,1.5728219624621183E-2,8.1493365930679706E-5,"NO"]
[null,"2017-01-01",42736.236805555556,"WGL24","RURAL LONG","Animal","Animal impact",95,59,4.6636823537242897E-2,7.9045463622445583E-4,"NO"]
[null,"2017-01-01",42736.281944444447,"MWT14","RURAL SHORT","Third Party","Dig-in",1,63,2.1392008556803422E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-01",42736.296527777777,"PHI12","RURAL SHORT","Overload","-",1,128,4.3463128496362512E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-01",42736.326388888891,"DRN23","RURAL LONG","Overload","-",6,105,5.2419623244358646E-3,4.9923450708912997E-5,"NO"]
[null,"2017-01-01",42736.326562499999,"ELM33","RURAL SHORT","Unknown","Unknown",65,0,0,0,"NO"]
[null,"2017-01-01",42736.330555555556,"MOE22","RURAL LONG","Asset failure","LV",1,151,1.2564068428409772E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-01",42736.340520833335,"CNR1","RURAL SHORT","Unknown","Unknown",141,0,0,0,"NO"]
[null,"2017-01-01",42736.340520833335,"CNR2","RURAL SHORT","Unknown","Unknown",1176,0,0,0,"NO"]
[null,"2017-01-01",42736.340520833335,"CNR3","RURAL SHORT","Unknown","Unknown",59,0,0,0,"NO"]
[null,"2017-01-01",42736.375914351855,"EPG14","URBAN","Unknown","Unknown",2223,0,0,0,"NO"]
[null,"2017-01-01",42736.377141203702,"LLG12","RURAL SHORT","Unknown","Unknown",49,0,0,0,"NO"]
[null,"2017-01-01",42736.387499999997,"SMR1","RURAL SHORT","Animal","Animal impact",52,162,2.8604171441668578E-2,1.765689595164727E-4,"NO"]
[null,"2017-01-01",42736.429166666669,"LDL24","URBAN","Third Party","Unauthorised access",1,130,4.4227916660996423E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-01",42736.466296296298,"TGN41","RURAL LONG","Unknown","Unknown",579,0,0,0,"NO"]
[null,"2017-01-01",42736.538194444445,"FTR22","RURAL SHORT","Animal","Animal impact",2,200,1.3582227655113284E-3,6.7911138275566425E-6,"NO"]
[null,"2017-01-01",42736.619444444441,"MWT31","RURAL SHORT","Animal","Animal impact",2,76,5.1612465089430478E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-01",42736.71875,"WGL24","RURAL LONG","Vegetation","Grow-in - NSP responsibility",64,45,2.3963256340278238E-2,5.3251680756173864E-4,"NO"]
[null,"2017-01-01",42736.722916666666,"FTR12","RURAL LONG","Weather","-",1,69,5.7411968315249952E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-01",42736.748055555552,"WN5","RURAL LONG","Unknown","Unknown",1219,0,0,0,"NO"]
[null,"2017-01-01",42736.775000000001,"MSD4","RURAL LONG","Weather","-",1,69,5.7411968315249952E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-01",42736.820416666669,"BDL44","RURAL LONG","Unknown","Unknown",318,0,0,0,"NO"]
[null,"2017-01-01",42736.820428240739,"BDL44","RURAL LONG","Unknown","Unknown",406,0,0,0,"NO"]
[null,"2017-01-01",42736.831944444442,"FTR12","RURAL LONG","Weather","-",1,112,9.3190441323304262E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-01",42736.924305555556,"BGE11","RURAL SHORT","Animal","Animal impact",12,60,2.4448009779203914E-3,4.0746682965339853E-5,"NO"]
[null,"2017-01-01",42736.96875,"RUBA24","RURAL SHORT","Animal","Animal impact",3,90,9.1680036672014671E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-02",42737.100694444445,"BRA33","URBAN","Animal","Animal impact",39,69,9.1551787488262596E-3,1.3268374998298926E-4,"NO"]
[null,"2017-01-02",42737.125254629631,"NLA34","RURAL SHORT","Unknown","Unknown",147,0,0,0,"NO"]
[null,"2017-01-02",42737.183333333334,"BWN14","RURAL SHORT","Animal","Animal impact",14,59,2.8047300107808932E-3,4.7537796792896496E-5,"NO"]
[null,"2017-01-02",42737.395057870373,"OFR23","RURAL LONG","Unknown","Unknown",35,0,0,0,"NO"]
[null,"2017-01-02",42737.411805555559,"WT11","URBAN","Asset failure","LV",1,173,5.885715063347985E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-02",42737.429166666669,"MWT14","RURAL SHORT","Weather","-",1,85,2.886223376711573E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-02",42737.474305555559,"LLG12","RURAL SHORT","Animal","Animal impact",2,68,4.6179574027385169E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-02",42737.488194444442,"RWN34","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",22,114,8.51605673975603E-3,7.4702252103123063E-5,"NO"]
[null,"2017-01-02",42737.635416666664,"BDL8","RURAL LONG","Asset failure","LV",1,205,1.7057178992211941E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-02",42737.658333333333,"MOE22","RURAL LONG","Animal","Animal impact",3,65,1.6225121480396725E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-02",42737.699305555558,"MFA22","RURAL LONG","Animal","Animal impact",1,888,7.3886707049191239E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-02",42737.721909722219,"BN1","RURAL LONG","Unknown","Unknown",70,0,0,0,"NO"]
[null,"2017-01-02",42737.948611111111,"BRA14","URBAN","Asset failure","HV",113,0,0,0,"NO"]
[null,"2017-01-02",42737.722222222219,"BRA14","URBAN","Asset failure","HV",113,291,0.11187281412027271,3.8444266020712273E-4,"NO"]
[null,"2017-01-02",42737.724305555559,"BN1","RURAL LONG","Weather","-",2,137,2.2798375823736938E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-02",42737.74722222222,"BDL2","RURAL SHORT","Asset failure","LV",1,209,7.0967139497966913E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-02",42737.842361111114,"LGA12","RURAL SHORT","Overload","-",1,57,1.9354674408536429E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-02",42737.861111111109,"MFA22","RURAL LONG","Vegetation","Grow-in - NSP responsibility",15,45,5.6163882047527121E-3,1.248086267722825E-4,"NO"]
[null,"2017-01-02",42737.862361111111,"WGI23","RURAL SHORT","Unknown","Unknown",2330,0,0,0,"NO"]
[null,"2017-01-02",42737.944953703707,"BWN13","URBAN","Unknown","Unknown",1754,0,0,0,"NO"]
[null,"2017-01-02",42737.944965277777,"BWN12","URBAN","Unknown","Unknown",1097,0,0,0,"NO"]
[null,"2017-01-02",42737.990532407406,"TGN31","RURAL LONG","Unknown","Unknown",882,0,0,0,"NO"]
[null,"2017-01-03",42738.041273148148,"FTR23","RURAL LONG","Unknown","Unknown",1945,0,0,0,"NO"]
[null,"2017-01-03",42738.138888888891,"MOE14","RURAL SHORT","Animal","Animal impact",4,134,1.8200185057851801E-3,1.3582227655113285E-5,"NO"]
[null,"2017-01-03",42738.15,"MOE31","RURAL LONG","Animal","Animal impact",3,81,2.0218997537109766E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-03",42738.270833333336,"BN6","RURAL LONG","Animal","Animal impact",1,345,2.8705984157624976E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-03",42738.281412037039,"WN4","RURAL SHORT","Animal","Animal impact",2,200,1.3582227655113284E-3,6.7911138275566425E-6,"NO"]
[null,"2017-01-03",42738.285833333335,"LGA11","RURAL LONG","Unknown","Unknown",661,0,0,0,"NO"]
[null,"2017-01-03",42738.288888888892,"LGA11","RURAL LONG","Animal","Animal impact",260,161,0.34829927444584968,2.1633495307195635E-3,"NO"]
[null,"2017-01-03",42738.291666666664,"WGL24","RURAL LONG","Unknown","Unknown",1,102,8.4869866205152097E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-03",42738.325092592589,"TGN31","RURAL LONG","Animal","Animal impact",36,17,5.0921919723091258E-3,2.9954070425347801E-4,"NO"]
[null,"2017-01-03",42738.346354166664,"MWT31","RURAL SHORT","Planned","-",155,288,0,0,"NO"]
[null,"2017-01-03",42738.359027777777,"EPG34","URBAN","Unknown","Unknown",1,1,3.402147435461263E-6,3.402147435461263E-6,"NO"]
[null,"2017-01-03",42738.361111111109,"BRT21","RURAL SHORT","Animal","Animal impact",7,170,4.0407127273962024E-3,2.3768898396448248E-5,"NO"]
[null,"2017-01-03",42738.378472222219,"LDL14","RURAL SHORT","Planned","-",3,194,0,0,"NO"]
[null,"2017-01-03",42738.385416666664,"WO13","RURAL SHORT","Animal","Animal impact",1,50,1.6977784568891606E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-03",42738.386111111111,"BRA33","URBAN","Asset failure","LV",1,149,5.0691996788372823E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-03",42738.390486111108,"WN5","RURAL LONG","Unknown","Unknown",253,0,0,0,"NO"]
[null,"2017-01-03",42738.392361111109,"KMS21","RURAL SHORT","Planned","-",1,40,0,0,"NO"]
[null,"2017-01-03",42738.402777777781,"BN1","RURAL LONG","Planned","-",2,140,0,0,"NO"]
[null,"2017-01-03",42738.408333333333,"WGI33","RURAL SHORT","Asset Failure","LV",1,210,7.1306695189344747E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-03",42738.410416666666,"FTR12","RURAL LONG","Weather","-",2,249,4.1436464088397788E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-03",42738.436111111114,"MOE22","RURAL LONG","Asset Failure","LV",1,1,8.3205751181521662E-6,8.3205751181521662E-6,"NO"]
[null,"2017-01-03",42738.440972222219,"WT8","URBAN","Asset failure","LV",1,193,6.5661445504402375E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-03",42738.511354166665,"PHI11","RURAL SHORT","Unknown","Unknown",1333,0,0,0,"NO"]
[null,"2017-01-03",42738.511354166665,"PHI12","RURAL SHORT","Unknown","Unknown",4436,0,0,0,"NO"]
[null,"2017-01-03",42738.511354166665,"PHI13","URBAN","Unknown","Unknown",4306,0,0,0,"NO"]
[null,"2017-01-03",42738.581250000003,"MWT11","RURAL SHORT","Asset failure","LV",1,73,2.4787565470581744E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-03",42738.588888888888,"BN1","RURAL LONG","Planned","-",2,102,0,0,"NO"]
[null,"2017-01-03",42738.591666666667,"BRA11","URBAN","Overload","-",8,118,3.2116271790754323E-3,2.7217179483690104E-5,"NO"]
[null,"2017-01-03",42738.65902777778,"SFS1","RURAL SHORT","Asset failure","LV",1,314,1.0662048709263929E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-03",42738.717361111114,"TT9","URBAN","Asset failure","LV",1,4,1.3608589741845052E-5,3.402147435461263E-6,"NO"]
[null,"2017-01-03",42738.736111111109,"LGA14","RURAL LONG","Overload","-",3,95,2.3713639086733675E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-03",42738.767361111109,"ELM33","RURAL SHORT","Asset failure","LV",1,130,4.4142239879118173E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-03",42738.773611111108,"RWN32","URBAN","Unknown","Unknown",1,1,3.402147435461263E-6,3.402147435461263E-6,"NO"]
[null,"2017-01-03",42738.82916666667,"WN3","RURAL LONG","Asset Failure","LV",1,126,1.048392464887173E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-03",42738.947500000002,"CYN13","URBAN","Unknown","Unknown",1059,0,0,0,"NO"]
[null,"2017-01-03",42738.966666666667,"SLE14","RURAL SHORT","Animal","Animal impact",82,28,7.7961986740350256E-3,2.7843566692982235E-4,"NO"]
[null,"2017-01-04",42739.029166666667,"CYN33","RURAL SHORT","Animal","Animal impact",94,91,2.9045593840459759E-2,3.1918234989516215E-4,"NO"]
[null,"2017-01-04",42739.037743055553,"RWN22","URBAN","Unknown","Unknown",1098,0,0,0,"NO"]
[null,"2017-01-04",42739.087696759256,"CYN33","RURAL SHORT","Unknown","Unknown",514,8,1.3962530029456455E-2,1.7453162536820569E-3,"NO"]
[null,"2017-01-04",42739.171701388892,"MJG11","RURAL SHORT","Unknown","Unknown",1227,0,0,0,"NO"]
[null,"2017-01-04",42739.171701388892,"MSD1","RURAL LONG","Unknown","Unknown",2072,0,0,0,"NO"]
[null,"2017-01-04",42739.171701388892,"MSD2","RURAL LONG","Unknown","Unknown",1625,0,0,0,"NO"]
[null,"2017-01-04",42739.171701388892,"MSD4","RURAL LONG","Unknown","Unknown",2540,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"CNR1","RURAL SHORT","Unknown","Unknown",141,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"CNR2","RURAL SHORT","Unknown","Unknown",1176,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"CNR3","RURAL SHORT","Unknown","Unknown",59,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"NLA31","RURAL LONG","Unknown","Unknown",912,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"NLA32","RURAL SHORT","Unknown","Unknown",1437,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"NLA34","RURAL SHORT","Unknown","Unknown",1286,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"BDL2","RURAL SHORT","Unknown","Unknown",3549,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"BDL4","RURAL SHORT","Unknown","Unknown",1025,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"BDL41","RURAL LONG","Unknown","Unknown",4042,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"BDL43","URBAN","Unknown","Unknown",1598,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"BDL44","RURAL LONG","Unknown","Unknown",2331,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"BDL6","RURAL SHORT","Unknown","Unknown",3163,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"BDL8","RURAL LONG","Unknown","Unknown",2049,0,0,0,"NO"]
[null,"2017-01-04",42739.262430555558,"BDL42","RURAL SHORT","Unknown","Unknown",4601,0,0,0,"NO"]
[null,"2017-01-04",42739.270833333336,"BRA32","URBAN","Overload","-",25,114,9.6961201910646007E-3,8.5053685886531585E-5,"NO"]
[null,"2017-01-04",42739.331250000003,"MWT12","URBAN","Animal","Animal impact",21,53,3.7865900956683858E-3,7.1445096144686523E-5,"NO"]
[null,"2017-01-04",42739.342870370368,"RUBA12","RURAL LONG","Unknown","Unknown",484,0,0,0,"NO"]
[null,"2017-01-04",42739.350694444445,"CYN13","URBAN","Third Party","Unauthorised access",1,459,1.5615856728767197E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-04",42739.354166666664,"SMR8","RURAL LONG","Planned","-",7,315,0,0,"NO"]
[null,"2017-01-04",42739.357638888891,"KLK1","RURAL SHORT","Planned","-",9,185,0,0,"NO"]
[null,"2017-01-04",42739.363194444442,"BWN12","URBAN","Planned","-",20,73,0,0,"NO"]
[null,"2017-01-04",42739.366666666669,"MWT14","RURAL SHORT","Planned","-",57,166,0,0,"NO"]
[null,"2017-01-04",42739.366666666669,"MWT14","RURAL SHORT","Planned","-",14,166,0,0,"NO"]
[null,"2017-01-04",42739.368055555555,"MWT14","RURAL SHORT","Planned","-",24,280,0,0,"NO"]
[null,"2017-01-04",42739.37222222222,"WYK24","RURAL SHORT","Animal","Animal impact",220,210,0.15687472941655844,7.470225210312306E-4,"NO"]
[null,"2017-01-04",42739.378472222219,"WGL21","RURAL LONG","Overload","-",1,121,1.0067895892964121E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.378472222219,"WN5","RURAL LONG","Planned","-",4,190,0,0,"NO"]
[null,"2017-01-04",42739.383333333331,"SLE11","URBAN","Asset failure","LV",1,73,2.4835676278867221E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-04",42739.385046296295,"KMS1","RURAL SHORT","Unknown","Unknown",1360,0,0,0,"NO"]
[null,"2017-01-04",42739.395138888889,"KMS1","RURAL SHORT","Third Party","Vehicle impact",2,60,4.0746682965339854E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-04",42739.395833333336,"RUBA12","RURAL LONG","Planned","-",1,103,0,0,"NO"]
[null,"2017-01-04",42739.40625,"ELM15","RURAL SHORT","Planned","-",10,435,0,0,"NO"]
[null,"2017-01-04",42739.412627314814,"MWT24","RURAL SHORT","Weather","-",24,82,6.6824560063157359E-3,8.1493365930679706E-5,"NO"]
[null,"2017-01-04",42739.413888888892,"LGA13","RURAL LONG","Animal","Animal impact",36,98,2.9354989016840843E-2,2.9954070425347801E-4,"NO"]
[null,"2017-01-04",42739.440972222219,"PHI12","RURAL SHORT","Planned","-",2,175,0,0,"NO"]
[null,"2017-01-04",42739.444062499999,"WN3","RURAL LONG","Overload","-",2,131,2.1799906809558678E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-04",42739.454861111109,"WGL11","RURAL SHORT","Asset failure","LV",1,59,2.0033785791292094E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-04",42739.465277777781,"FTR12","RURAL LONG","Weather","-",1,1,8.3205751181521662E-6,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.501840277779,"KLK1","RURAL SHORT","Planned","-",67,129,0,0,"NO"]
[null,"2017-01-04",42739.510416666664,"FTR12","RURAL LONG","Asset failure","HV",1,83,6.9060773480662981E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.534722222219,"EPG32","RURAL SHORT","Overload","-",20,115,7.809780901690138E-3,6.791113827556642E-5,"NO"]
[null,"2017-01-04",42739.551388888889,"WOTS24","RURAL LONG","Weather","-",1,200,1.6641150236304334E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.558333333334,"TGN41","RURAL LONG","Planned","-",2,35,0,0,"NO"]
[null,"2017-01-04",42739.600694444445,"WGI22","RURAL LONG","Weather","-",1,215,1.7889236504027158E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.605555555558,"TGN41","RURAL LONG","Planned","-",2,11,0,0,"NO"]
[null,"2017-01-04",42739.606249999997,"FTR23","RURAL LONG","Animal","Animal impact",1,1,8.3205751181521662E-6,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.615972222222,"KLK1","RURAL SHORT","Other","Poor Work Practice",10,79,2.6824899618848735E-3,3.395556913778321E-5,"NO"]
[null,"2017-01-04",42739.625,"SLE31","RURAL LONG","Asset failure","LV",1,145,1.2064833921320642E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.703472222223,"WT8","URBAN","Asset failure","LV",1,132,4.4908346148088673E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-04",42739.711111111108,"BGE22","RURAL SHORT","Other","High/Low volt or Tap change",18,7,4.2784017113606845E-4,6.1120024448009776E-5,"NO"]
[null,"2017-01-04",42739.729166666664,"RUBA12","RURAL LONG","Animal","Animal impact",1,70,5.8244025827065165E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.731944444444,"WGL15","RURAL SHORT","Animal","Animal impact",2,61,4.1425794348095516E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-04",42739.787499999999,"WGL21","RURAL LONG","Asset Failure","LV",1,86,7.1556946016108631E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-04",42739.787789351853,"WYK13","RURAL SHORT","Unknown","Unknown",566,0,0,0,"NO"]
[null,"2017-01-04",42739.854861111111,"HPK24","URBAN","Animal","Animal impact",13,47,2.078712083066832E-3,4.4227916660996419E-5,"NO"]
[null,"2017-01-04",42739.899421296293,"MWT14","RURAL SHORT","Unknown","Unknown",13,73,3.2223835111756267E-3,4.4142239879118175E-5,"NO"]
[null,"2017-01-04",42739.9,"MWT14","RURAL SHORT","Animal","Animal impact",172,57,3.3290039982682658E-2,5.8403578916987127E-4,"NO"]
[null,"2017-01-04",42739.900995370372,"MWT14","RURAL SHORT","Asset failure","HV",26,70,6.1799135830765441E-3,8.828447975823635E-5,"NO"]
[null,"2017-01-04",42739.928229166668,"RWN34","RURAL SHORT","Unknown","Unknown",2097,0,0,0,"NO"]
[null,"2017-01-05",42740.078472222223,"ELM15","RURAL SHORT","Asset Failure","LV",41,97,1.3504129846096382E-2,1.3921783346491117E-4,"NO"]
[null,"2017-01-05",42740.131249999999,"MWT14","RURAL SHORT","Weather","-",1,521,1.7690851520785053E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.298726851855,"WGL23","RURAL SHORT","Unknown","Unknown",390,0,0,0,"NO"]
[null,"2017-01-05",42740.320833333331,"ELM34","RURAL SHORT","Asset failure","LV",1,215,7.3004473646233903E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.324305555558,"WYK23","RURAL SHORT","Asset Failure","LV",1,87,2.9541345149871392E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.34375,"WGL23","RURAL SHORT","Animal","Animal impact",6,75,1.5280006112002446E-3,2.0373341482669927E-5,"NO"]
[null,"2017-01-05",42740.354166666664,"SMR8","RURAL LONG","Planned","-",12,353,0,0,"NO"]
[null,"2017-01-05",42740.354166666664,"LDL14","RURAL SHORT","Planned","-",73,345,0,0,"NO"]
[null,"2017-01-05",42740.364583333336,"LGA21","RURAL SHORT","Other","Other",1,205,6.9608916732455579E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.364583333336,"LGA21","RURAL SHORT","Other","Other",1,205,6.9608916732455579E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.364583333336,"MWT14","RURAL SHORT","Planned","-",2,285,0,0,"NO"]
[null,"2017-01-05",42740.364583333336,"LGA21","RURAL SHORT","Planned","-",46,205,0,0,"NO"]
[null,"2017-01-05",42740.370138888888,"MWT34","RURAL SHORT","Planned","-",111,187,0,0,"NO"]
[null,"2017-01-05",42740.37259259259,"WOTS24","RURAL LONG","Unknown","Unknown",89,0,0,0,"NO"]
[null,"2017-01-05",42740.37777777778,"FTR23","RURAL LONG","Weather","-",1,54,4.4931105638021699E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-05",42740.381944444445,"MWT14","RURAL SHORT","Asset failure","HV",115,43,1.6791028938633799E-2,3.9048904508450692E-4,"NO"]
[null,"2017-01-05",42740.389050925929,"MWT14","RURAL SHORT","Asset failure","HV",39,27.333333333333332,3.6196636700876902E-3,1.3242671963735453E-4,"NO"]
[null,"2017-01-05",42740.395833333336,"BN1","RURAL LONG","Planned","-",1,15,0,0,"NO"]
[null,"2017-01-05",42740.399305555555,"WO32","URBAN","Asset failure","LV",1,1,3.402147435461263E-6,3.402147435461263E-6,"NO"]
[null,"2017-01-05",42740.404861111114,"OFR21","URBAN","Planned","-",9,280,0,0,"NO"]
[null,"2017-01-05",42740.413194444445,"KLK3","RURAL SHORT","Planned","-",4,65,0,0,"NO"]
[null,"2017-01-05",42740.414733796293,"TGN23","RURAL SHORT","Weather","-",41,98,1.3643347679561295E-2,1.3921783346491117E-4,"NO"]
[null,"2017-01-05",42740.416666666664,"BDL41","RURAL LONG","Planned","-",1,150,0,0,"NO"]
[null,"2017-01-05",42740.42083333333,"MSD2","RURAL LONG","Asset failure","LV",1,210,1.747320774811955E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-05",42740.433333333334,"MFA31","RURAL SHORT","Asset failure","LV",1,25,8.4888922844458028E-5,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.436111111114,"CF2","RURAL SHORT","Overload","-",1,167,5.670580046009796E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.447916666664,"LGA14","RURAL LONG","Planned","-",3,15,0,0,"NO"]
[null,"2017-01-05",42740.479166666664,"DRN23","RURAL LONG","Planned","-",3,5,0,0,"NO"]
[null,"2017-01-05",42740.489583333336,"BN1","RURAL LONG","Planned","-",36,165,0,0,"NO"]
[null,"2017-01-05",42740.5,"LGA14","RURAL LONG","Planned","-",2,30,0,0,"NO"]
[null,"2017-01-05",42740.5,"DRN23","RURAL LONG","Planned","-",1,5,0,0,"NO"]
[null,"2017-01-05",42740.512499999997,"FTR12","RURAL LONG","Weather","-",1,87,7.2389003527923855E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-05",42740.513888888891,"DRN23","RURAL LONG","Planned","-",1,20,0,0,"NO"]
[null,"2017-01-05",42740.548611111109,"RWN33","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",72,90,2.2003208801283522E-2,2.4448009779203911E-4,"NO"]
[null,"2017-01-05",42740.558333333334,"TGN23","RURAL SHORT","Animal","Animal impact",2,55,3.735112605156153E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-05",42740.563888888886,"LDL23","RURAL LONG","Asset failure","HV",1,82,6.8228715968847767E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-05",42740.651099537034,"TGN31","RURAL LONG","Unknown","Unknown",883,0,0,0,"NO"]
[null,"2017-01-05",42740.652083333334,"WOTS13","RURAL LONG","Weather","-",13,173.69230769230768,1.8787858616787591E-2,1.0816747653597817E-4,"NO"]
[null,"2017-01-05",42740.655555555553,"BWR13","URBAN","Overload","-",1,58,1.9732455125675327E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-05",42740.661111111112,"TGN31","RURAL LONG","Animal","Animal impact",1,281,2.338081608200759E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-05",42740.68136574074,"BM8B31","RURAL SHORT","Unknown","Unknown",57,0,0,0,"NO"]
[null,"2017-01-05",42740.69027777778,"BM8B31","RURAL SHORT","Weather","-",1,136,4.6179574027385169E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.708935185183,"FTR12","RURAL LONG","Unknown","Unknown",867,0,0,0,"NO"]
[null,"2017-01-05",42740.722812499997,"MFA22","RURAL LONG","Unknown","Unknown",476,0,0,0,"NO"]
[null,"2017-01-05",42740.722939814812,"TGN31","RURAL LONG","Unknown","Unknown",881,0,0,0,"NO"]
[null,"2017-01-05",42740.740682870368,"TGN31","RURAL LONG","Unknown","Unknown",881,0,0,0,"NO"]
[null,"2017-01-05",42740.743275462963,"TGN31","RURAL LONG","Weather","-",50,115,4.7843306929374961E-2,4.1602875590760835E-4,"NO"]
[null,"2017-01-05",42740.748530092591,"TGN31","RURAL LONG","Unknown","Unknown",831,0,0,0,"NO"]
[null,"2017-01-05",42740.753576388888,"TGN31","RURAL LONG","Unknown","Unknown",36,110,3.2949477467882578E-2,2.9954070425347801E-4,"NO"]
[null,"2017-01-05",42740.785752314812,"MFA22","RURAL LONG","Unknown","Unknown",406,0,0,0,"NO"]
[null,"2017-01-05",42740.790277777778,"LLG14","RURAL SHORT","Overload","-",1,82,2.7843566692982235E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.800555555557,"BWA22","RURAL LONG","Unknown","Unknown",84,0,0,0,"NO"]
[null,"2017-01-05",42740.800694444442,"MFA22","RURAL LONG","Weather","-",30,140,3.49464154962391E-2,2.49617253544565E-4,"NO"]
[null,"2017-01-05",42740.808333333334,"BWA22","RURAL LONG","Weather","-",1,281,2.338081608200759E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-05",42740.82708333333,"MFA22","RURAL LONG","Weather","-",2,135,2.2465552819010848E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-05",42740.845138888886,"TGN31","RURAL LONG","Weather","-",1,53,4.4099048126206486E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-05",42740.867361111108,"BM8B31","RURAL SHORT","Unknown","Unknown",121,75,3.0814678992538265E-2,4.1086238656717683E-4,"NO"]
[null,"2017-01-05",42740.87222222222,"BM8B33","RURAL SHORT","Unknown","Unknown",1,68,2.3089787013692585E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-05",42740.877083333333,"WO23","URBAN","Overload","-",1,142,4.8310493583549936E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-05",42740.882638888892,"TGN12","URBAN","Overload","-",1,54,1.8371596151490821E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-05",42740.886805555558,"RUBA22","RURAL SHORT","Animal","Animal impact",2,73,4.9575130941163488E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-05",42740.941666666666,"WOTS13","RURAL LONG","Weather","-",1,669,5.5664647540437998E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.029861111114,"RWN31","RURAL SHORT","Animal","Animal impact",5,57,9.6773372042682152E-4,1.6977784568891605E-5,"NO"]
[null,"2017-01-06",42741.034722222219,"CYN22","URBAN","Animal","Animal impact",44,100,1.4969448716029558E-2,1.4969448716029558E-4,"NO"]
[null,"2017-01-06",42741.109224537038,"WGI33","RURAL SHORT","Asset failure","LV",130,411,0.18142460590317569,4.4142239879118173E-4,"NO"]
[null,"2017-01-06",42741.118402777778,"RWN26","RURAL SHORT","Unknown","Unknown",1255,0,0,0,"NO"]
[null,"2017-01-06",42741.156944444447,"WOTS11","RURAL LONG","Unknown","Unknown",1252,0,0,0,"NO"]
[null,"2017-01-06",42741.174305555556,"WGL12","RURAL LONG","Animal","Animal impact",7,304,1.7706183851427811E-2,5.8244025827065164E-5,"NO"]
[null,"2017-01-06",42741.235011574077,"MFA22","RURAL LONG","Unknown","Unknown",406,0,0,0,"NO"]
[null,"2017-01-06",42741.235127314816,"RUBA12","RURAL LONG","Unknown","Unknown",49,0,0,0,"NO"]
[null,"2017-01-06",42741.238194444442,"MOE13","RURAL SHORT","Animal","Animal impact",41,113,1.5731615181534962E-2,1.3921783346491117E-4,"NO"]
[null,"2017-01-06",42741.261805555558,"RUBA12","RURAL LONG","Animal","Animal impact",12,235,2.346402183318911E-2,9.9846901417825995E-5,"NO"]
[null,"2017-01-06",42741.283472222225,"MBY11","RURAL SHORT","Unknown","Unknown",1130,0,0,0,"NO"]
[null,"2017-01-06",42741.29755787037,"MFA22","RURAL LONG","Overload","-",6,187,9.3356852825667302E-3,4.9923450708912997E-5,"NO"]
[null,"2017-01-06",42741.328472222223,"MSD2","RURAL LONG","Overload","-",1,231,1.9220528522931506E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.334027777775,"FGY34","URBAN","Planned","-",340,414,0,0,"NO"]
[null,"2017-01-06",42741.377303240741,"KLK1","RURAL SHORT","Planned","-",81,314,0,0,"NO"]
[null,"2017-01-06",42741.381249999999,"MFA34","RURAL SHORT","Animal","Animal impact",2,0,0,0,"NO"]
[null,"2017-01-06",42741.381377314814,"TGN41","RURAL LONG","Planned","-",20,188,0,0,"NO"]
[null,"2017-01-06",42741.395138888889,"CLN23","RURAL SHORT","Asset Failure","LV",4,101,1.3718049931664418E-3,1.3582227655113285E-5,"NO"]
[null,"2017-01-06",42741.395833333336,"MWT21","URBAN","Planned","-",10,215,0,0,"NO"]
[null,"2017-01-06",42741.395833333336,"CRE21","RURAL SHORT","Planned","-",4,18,0,0,"NO"]
[null,"2017-01-06",42741.411111111112,"LGA23","RURAL LONG","Overload","-",1,228,1.897091126938694E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.426388888889,"LGA14","RURAL LONG","Planned","-",2,253,0,0,"NO"]
[null,"2017-01-06",42741.429861111108,"BGE22","RURAL SHORT","Third Party","Dig-in",1,76,2.5806232544715239E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-06",42741.466666666667,"LDL21","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1,445,1.5110228266313529E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-06",42741.468055555553,"WOTS13","RURAL LONG","Asset Failure","LV",1,106,8.8198096252412972E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.470138888886,"LDL23","RURAL LONG","Asset failure","LV",1,457,3.8025028289955403E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.521134259259,"CRE22","URBAN","Unknown","Unknown",2590,0,0,0,"NO"]
[null,"2017-01-06",42741.541666666664,"TGN31","RURAL LONG","Animal","Animal impact",1,0,0,0,"NO"]
[null,"2017-01-06",42741.544444444444,"MYT7","RURAL LONG","Asset failure","LV",1,141,1.1732010916594554E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.554166666669,"LDL21","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1,317,1.0763915416677277E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-06",42741.560416666667,"FGY32","URBAN","Overload","-",3,93,9.491991344936924E-4,1.020644230638379E-5,"NO"]
[null,"2017-01-06",42741.609722222223,"WOTS11","RURAL LONG","Asset Failure","LV",46,162,6.2004925780469948E-2,3.8274645543499966E-4,"NO"]
[null,"2017-01-06",42741.65,"SMR8","RURAL LONG","Overload","-",1,31,2.5793782866271719E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.665972222225,"PHM33","RURAL LONG","Animal","Animal impact",2,164,2.7291486387539107E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-06",42741.67796296296,"PHI12","RURAL SHORT","Unknown","Unknown",144,354,0.17309190923676371,4.8896019558407821E-4,"NO"]
[null,"2017-01-06",42741.752083333333,"BRA14","URBAN","Overload","-",10,82,2.789760897078236E-3,3.4021474354612629E-5,"NO"]
[null,"2017-01-06",42741.763194444444,"KLO14","RURAL LONG","Animal","Animal impact",2,191,3.1784596951341276E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-06",42741.771527777775,"OFR23","RURAL LONG","Overload","-",1,73,6.0740198362510816E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.780555555553,"WT9","URBAN","Overload","-",14,86,4.0961855122953611E-3,4.7630064096457684E-5,"NO"]
[null,"2017-01-06",42741.787499999999,"WT8","URBAN","Overload","-",1,179,6.0898439094756612E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-06",42741.789953703701,"KLO14","RURAL LONG","Weather","-",1949,16,0.25946881448445719,1.6216800905278574E-2,"NO"]
[null,"2017-01-06",42741.801388888889,"FGY34","URBAN","Overload","-",16,76,4.1370112815208963E-3,5.4434358967380209E-5,"NO"]
[null,"2017-01-06",42741.808310185188,"SMR8","RURAL LONG","Unknown","Unknown",699,0,0,0,"NO"]
[null,"2017-01-06",42741.814212962963,"SMR8","RURAL LONG","Overload","-",10,306,2.5460959861545632E-2,8.3205751181521662E-5,"NO"]
[null,"2017-01-06",42741.838194444441,"BDL8","RURAL LONG","Overload","-",1,179,1.4893829461492378E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-06",42741.862870370373,"WOTS24","RURAL LONG","Unknown","Unknown",1471,0,0,0,"NO"]
[null,"2017-01-06",42741.881249999999,"SMR1","RURAL SHORT","Weather","-",2,821,5.575504452424003E-3,6.7911138275566425E-6,"NO"]
[null,"2017-01-06",42741.881249999999,"CPK23","URBAN","Overload","-",1,169,5.7496291659295349E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-06",42741.936261574076,"CLN22","RURAL SHORT","Unknown","Unknown",588,0,0,0,"NO"]
[null,"2017-01-06",42741.956944444442,"CLN22","RURAL SHORT","Animal","Animal impact",16,63,3.4227213690885476E-3,5.432891062045314E-5,"NO"]
[null,"2017-01-06",42741.963888888888,"CPK13","URBAN","Overload","-",87,90,2.6638814419661691E-2,2.959868268851299E-4,"NO"]
[null,"2017-01-06",42741.978368055556,"WYK13","RURAL SHORT","Unknown","Unknown",2611,0,0,0,"NO"]
[null,"2017-01-06",42741.983171296299,"WT12","URBAN","Animal","Animal impact",2715,104.67845303867404,0.96689710545296192,9.2368302872773301E-3,"NO"]
[null,"2017-01-06",42741.986076388886,"FTR21","RURAL LONG","Unknown","Unknown",2038,0,0,0,"NO"]
[null,"2017-01-07",42742.005555555559,"WN6","RURAL LONG","Animal","Animal impact",2,0,0,0,"NO"]
[null,"2017-01-07",42742.128020833334,"SMR5","RURAL LONG","Unknown","Unknown",528,0,0,0,"NO"]
[null,"2017-01-07",42742.16233796296,"MOE22","RURAL LONG","Unknown","Unknown",29,0,0,0,"NO"]
[null,"2017-01-07",42742.213194444441,"MOE22","RURAL LONG","Animal","Animal impact",3,86,2.1467083804832588E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-07",42742.284733796296,"MOE31","RURAL LONG","Unknown","Unknown",272,0,0,0,"NO"]
[null,"2017-01-07",42742.288194444445,"BN1","RURAL LONG","Animal","Animal impact",2,90,1.4977035212673899E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-07",42742.306250000001,"LDL13","RURAL SHORT","Animal","Animal impact",11,100,3.7351126051561531E-3,3.7351126051561531E-5,"NO"]
[null,"2017-01-07",42742.310428240744,"WN5","RURAL LONG","Unknown","Unknown",1219,0,0,0,"NO"]
[null,"2017-01-07",42742.31527777778,"LGA23","RURAL LONG","Animal","Animal impact",24,166,3.3149171270718231E-2,1.9969380283565199E-4,"NO"]
[null,"2017-01-07",42742.321782407409,"MWT24","RURAL SHORT","Animal","Animal impact",788,0,0,0,"NO"]
[null,"2017-01-07",42742.373622685183,"WOTS11","RURAL LONG","Unknown","Unknown",544,0,0,0,"NO"]
[null,"2017-01-07",42742.397222222222,"WGI31","RURAL SHORT","Asset failure","LV",1,191,6.4855137053165931E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-07",42742.399305555555,"BDL6","RURAL SHORT","Animal","Animal impact",1,135,4.5840018336007336E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-07",42742.402777777781,"TGN23","RURAL SHORT","Planned","-",3,81,0,0,"NO"]
[null,"2017-01-07",42742.421736111108,"NLA31","RURAL LONG","Unknown","Unknown",593,0,0,0,"NO"]
[null,"2017-01-07",42742.44027777778,"BGE11","RURAL SHORT","Asset failure","LV",3,106,1.079787098581506E-3,1.0186670741334963E-5,"NO"]
[null,"2017-01-07",42742.441666666666,"ELM11","URBAN","Overload","-",1,179,6.0898439094756612E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-07",42742.498611111114,"WT11","URBAN","Asset failure","LV",1,64,2.1773743586952083E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-07",42742.507638888892,"WN6","RURAL LONG","Animal","Animal impact",3,206,5.1421154230180391E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-07",42742.530358796299,"WYK24","RURAL SHORT","Other","Poor Work Practice",69,0,0,0,"NO"]
[null,"2017-01-07",42742.530358796299,"WYK24","RURAL SHORT","Other","Poor Work Practice",23,368.73913043478262,2.879771818575394E-2,7.8097809016901385E-5,"NO"]
[null,"2017-01-07",42742.632233796299,"SMG23","URBAN","Unknown","Unknown",1255,233.38167330677291,0.99646857096199126,4.269695031503885E-3,"NO"]
[null,"2017-01-07",42742.640972222223,"BDL41","RURAL LONG","Asset failure","HV",40,37,1.2314451174865206E-2,3.3282300472608665E-4,"NO"]
[null,"2017-01-07",42742.661111111112,"LDL14","RURAL SHORT","Overload","-",1,433,1.4702761436660131E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-07",42742.663194444445,"CPK23","URBAN","Weather","-",91,114,3.5293877495475141E-2,3.0959541662697496E-4,"NO"]
[null,"2017-01-07",42742.677083333336,"TGN12","URBAN","Other","High/Low volt or Tap change",1,115,3.9124695507804528E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-07",42742.693055555559,"BRA24","URBAN","Asset failure","LV",62,80,1.6874651279887864E-2,2.109331409985983E-4,"NO"]
[null,"2017-01-07",42742.706250000003,"BWN14","RURAL SHORT","Overload","-",1,138,4.6858685410140831E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-07",42742.719444444447,"ELM34","RURAL SHORT","Asset failure","LV",1,389,1.320871639459767E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-07",42742.770138888889,"CPK23","URBAN","Overload","-",1,311,1.0580678524284529E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-07",42742.777777777781,"ELM32","URBAN","Overload","-",9,143,4.3785637494386459E-3,3.061932691915137E-5,"NO"]
[null,"2017-01-07",42742.805555555555,"DRN21","RURAL SHORT","Overload","-",1,380,1.290311627235762E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-07",42742.810416666667,"PHM32","URBAN","Overload","-",1,208,7.076466665759427E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-07",42742.822025462963,"MSD4","RURAL LONG","Weather","-",48,109,4.3533249018172133E-2,3.9938760567130398E-4,"NO"]
[null,"2017-01-07",42742.843055555553,"CRE33","RURAL SHORT","Overload","-",6,76,1.5483739526829144E-3,2.0373341482669927E-5,"NO"]
[null,"2017-01-07",42742.847916666666,"CYN11","URBAN","Overload","-",1,107,3.6402977559435516E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-07",42742.856944444444,"EPG34","URBAN","Overload","-",1,121,4.1165983969081285E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-07",42742.85833333333,"BRA14","URBAN","Overload","-",1,458,1.5581835254412585E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-07",42742.875,"ELM34","RURAL SHORT","Asset failure","LV",57,80,1.5483739526829144E-2,1.9354674408536429E-4,"NO"]
[null,"2017-01-07",42742.925694444442,"DRN13","RURAL SHORT","Overload","-",1,257,8.7265812684102846E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-07",42742.943749999999,"PHI13","URBAN","Animal","Animal impact",12,51,2.082114230502293E-3,4.082576922553516E-5,"NO"]
[null,"2017-01-07",42742.963194444441,"RWT22","URBAN","Unknown","Unknown",2645,0,0,0,"NO"]
[null,"2017-01-07",42742.97152777778,"WGL24","RURAL LONG","Overload","-",3,661,1.6499700459295746E-2,2.4961725354456499E-5,"NO"]
[null,"2017-01-08",42743.035474537035,"LLG14","RURAL SHORT","Unknown","Unknown",2507,0,0,0,"NO"]
[null,"2017-01-08",42743.534895833334,"ELM32","URBAN","Asset failure","LV",78,0,0,0,"NO"]
[null,"2017-01-08",42743.039583333331,"ELM32","URBAN","Asset failure","LV",3220,41.36149068322981,0.45311160404447287,1.0954914742185268E-2,"NO"]
[null,"2017-01-08",42743.369386574072,"MOE31","RURAL LONG","Other","Cause Not In List",552,0,0,0,"NO"]
[null,"2017-01-08",42743.080509259256,"MOE31","RURAL LONG","Other","Cause Not In List",842,143.21258907363421,1.003336550622379,7.0059242494841245E-3,"NO"]
[null,"2017-01-08",42743.081886574073,"WGL21","RURAL LONG","Unknown","Unknown",438,0,0,0,"NO"]
[null,"2017-01-08",42743.157187500001,"CPK12","RURAL SHORT","Unknown","Unknown",53,0,0,0,"NO"]
[null,"2017-01-08",42743.290277777778,"WOTS13","RURAL LONG","Animal","Animal impact",1,92,7.6549291086999932E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-08",42743.301388888889,"RWT14","URBAN","Asset failure","LV",155,270,0.14237987017405387,5.2733285249649574E-4,"NO"]
[null,"2017-01-08",42743.339583333334,"BWR24","URBAN","Planned","-",48,300,0,0,"NO"]
[null,"2017-01-08",42743.357638888891,"WN3","RURAL LONG","Planned","-",5,125,0,0,"NO"]
[null,"2017-01-08",42743.364583333336,"ELM34","RURAL SHORT","Asset failure","LV",1,454,1.5415828388553577E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-08",42743.367361111108,"ELM13","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",1,236,8.0290679476885808E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-08",42743.386319444442,"ELM31","URBAN","Unknown","Unknown",1533,0,0,0,"NO"]
[null,"2017-01-08",42743.397222222222,"FTR23","RURAL LONG","Asset failure","LV",1,78,6.4900485921586904E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-08",42743.4375,"CPK23","URBAN","Overload","-",1,135,4.5928990378727054E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-08",42743.45,"CYN31","URBAN","Overload","-",1,162,5.5114788454472467E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-08",42743.53125,"WYK24","RURAL SHORT","Overload","-",1,302,1.0254581879610529E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-08",42743.557638888888,"LDL23","RURAL LONG","Overload","-",1,87,7.2389003527923855E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-08",42743.563472222224,"ELM12","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",868,16,4.7157494418553325E-2,2.9473434011595828E-3,"NO"]
[null,"2017-01-08",42743.569444444445,"ELM32","URBAN","Overload","-",28,184,1.7527863587496428E-2,9.5260128192915368E-5,"NO"]
[null,"2017-01-08",42743.602083333331,"ELM15","RURAL SHORT","Overload","-",29,118,1.1619595758949415E-2,9.8471150499571315E-5,"NO"]
[null,"2017-01-08",42743.632638888892,"MFA31","RURAL SHORT","Overload","-",1,121,4.1086238656717683E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-08",42743.681944444441,"RWT14","URBAN","Overload","-",1,51,1.7350951920852442E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-08",42743.7,"MFA34","RURAL SHORT","Asset failure","LV",1,93,3.1578679298138387E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-08",42743.700173611112,"WGL21","RURAL LONG","Asset failure","LV",10,275.2,2.2898222725154762E-2,8.3205751181521662E-5,"NO"]
[null,"2017-01-08",42743.707638888889,"ELM32","URBAN","Overload","-",28,161,1.5336880639059374E-2,9.5260128192915368E-5,"NO"]
[null,"2017-01-08",42743.715277777781,"NLA31","RURAL LONG","Animal","Animal impact",3,110,2.745789788990215E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-08",42743.75072916667,"MJG11","RURAL SHORT","Asset failure","HV",1308,0,0,0,"NO"]
[null,"2017-01-08",42743.75072916667,"MJG11","RURAL SHORT","Asset failure","HV",23,620.6521739130435,4.8471574944185532E-2,7.8097809016901385E-5,"NO"]
[null,"2017-01-08",42743.829861111109,"SMR8","RURAL LONG","Animal","Animal impact",11,70,6.4068428409771684E-3,9.1526326299673836E-5,"NO"]
[null,"2017-01-08",42743.869444444441,"ELM11","URBAN","Asset failure","LV",1,128,4.3547487173904167E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-08",42743.884722222225,"BWR23","URBAN","Asset failure","LV",1,46,1.5649878203121811E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-08",42743.95275462963,"KLK2","RURAL SHORT","Unknown","Unknown",364,0,0,0,"NO"]
[null,"2017-01-08",42743.961111111108,"LDL23","RURAL LONG","Animal","Animal impact",37,131,4.0329827597683554E-2,3.0786127937163014E-4,"NO"]
[null,"2017-01-08",42743.971203703702,"DRN22","RURAL SHORT","Unknown","Unknown",3628,0,0,0,"NO"]
[null,"2017-01-09",42744.083657407406,"KLK1","RURAL SHORT","Unknown","Unknown",95,0,0,0,"NO"]
[null,"2017-01-09",42744.083657407406,"WYK24","RURAL SHORT","Other","Poor Work Practice",23,474.21739130434781,3.7035339258580151E-2,7.8097809016901385E-5,"NO"]
[null,"2017-01-09",42744.161805555559,"RWT32","URBAN","Animal","Animal impact",92,312,9.7655239987480102E-2,3.1299756406243622E-4,"NO"]
[null,"2017-01-09",42744.181620370371,"BN6","RURAL LONG","Unknown","Unknown",410,0,0,0,"NO"]
[null,"2017-01-09",42744.21298611111,"RWN34","RURAL SHORT","Unknown","Unknown",2097,0,0,0,"NO"]
[null,"2017-01-09",42744.213287037041,"RWN24","URBAN","Unknown","Unknown",1770,24.901694915254236,0.14995305036539064,6.0218009607664359E-3,"NO"]
[null,"2017-01-09",42744.224618055552,"WGL12","RURAL LONG","Unknown","Unknown",3259,0,0,0,"NO"]
[null,"2017-01-09",42744.24391203704,"WOTS24","RURAL LONG","Unknown","Unknown",27,0,0,0,"NO"]
[null,"2017-01-09",42744.252175925925,"RWN24","URBAN","Asset failure","HV",2429,14.804857966241251,0.12234462392662249,8.263816120735408E-3,"NO"]
[null,"2017-01-09",42744.271365740744,"RWN32","URBAN","Unknown","Unknown",3497,0,0,0,"NO"]
[null,"2017-01-09",42744.292361111111,"RWN24","URBAN","Unknown","Unknown",71,104,2.5121456663445969E-2,2.4155246791774968E-4,"NO"]
[null,"2017-01-09",42744.292361111111,"RWN26","RURAL SHORT","Animal","Animal impact",30,214,2.179947538645682E-2,1.0186670741334964E-4,"NO"]
[null,"2017-01-09",42744.309027777781,"RWN24","URBAN","Unknown","Unknown",1,80,2.7217179483690103E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-09",42744.35428240741,"WN3","RURAL LONG","Planned","-",58,351.4655172413793,0,0,"NO"]
[null,"2017-01-09",42744.368715277778,"WYK13","RURAL SHORT","Planned","-",1,561,0,0,"NO"]
[null,"2017-01-09",42744.378495370373,"LGA14","RURAL LONG","Planned","-",210,241,0,0,"NO"]
[null,"2017-01-09",42744.388888888891,"ELM33","RURAL SHORT","Asset failure","LV",1,506,1.7181517983718305E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-09",42744.396527777775,"BWN13","URBAN","Planned","-",49,207,0,0,"NO"]
[null,"2017-01-09",42744.404340277775,"MFA21","RURAL LONG","Unknown","Unknown",1359,0,0,0,"NO"]
[null,"2017-01-09",42744.414583333331,"LLG11","RURAL SHORT","Animal","Animal impact",1,210,7.1306695189344747E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-09",42744.418055555558,"LGA14","RURAL LONG","Planned","-",73,53,0,0,"NO"]
[null,"2017-01-09",42744.421261574076,"WO33","URBAN","Unknown","Unknown",2,3,2.041288461276758E-5,6.8042948709225261E-6,"NO"]
[null,"2017-01-09",42744.423611111109,"LGA14","RURAL LONG","Planned","-",152,176,0,0,"NO"]
[null,"2017-01-09",42744.430555555555,"RWN26","RURAL SHORT","Planned","-",36,150,0,0,"NO"]
[null,"2017-01-09",42744.447916666664,"EPG23","URBAN","Planned","-",3,160,0,0,"NO"]
[null,"2017-01-09",42744.551388888889,"BN4","URBAN","Overload","-",1,159,5.4094144223834086E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-09",42744.556250000001,"RWN32","URBAN","Planned","-",117,34,0,0,"NO"]
[null,"2017-01-09",42744.587407407409,"RUBA24","RURAL SHORT","Unknown","Unknown",330,0,0,0,"NO"]
[null,"2017-01-09",42744.597916666666,"RUBA24","RURAL SHORT","Weather","-",1,91,3.089956791538272E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-09",42744.6,"LDL23","RURAL LONG","Overload","-",1,149,1.2397656926046729E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-09",42744.616666666669,"MOE21","RURAL SHORT","Unknown","Unknown",1,168,5.7045356151475793E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-09",42744.680555555555,"CNR2","RURAL SHORT","Animal","Animal impact",5,260,4.4142239879118176E-3,1.6977784568891605E-5,"NO"]
[null,"2017-01-09",42744.689583333333,"HPK24","URBAN","Third Party","Vehicle impact",6,380,7.7568961528516802E-3,2.041288461276758E-5,"NO"]
[null,"2017-01-09",42744.71875,"BGE22","RURAL SHORT","Third Party","Dig-in",1,125,4.2444461422229011E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-09",42744.727083333331,"BWR34","URBAN","Asset failure","HV",108,0,0,0,"NO"]
[null,"2017-01-09",42744.736307870371,"BWR34","URBAN","Asset failure","HV",725,4,9.8662275628376636E-3,2.4665568907094159E-3,"NO"]
[null,"2017-01-09",42744.742962962962,"MWT31","RURAL SHORT","Unknown","Unknown",253,0,0,0,"NO"]
[null,"2017-01-09",42744.761805555558,"WOTS11","RURAL LONG","Asset failure","LV",1,118,9.8182786394195574E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-09",42744.838912037034,"RWN22","URBAN","Unknown","Unknown",1096,0,0,0,"NO"]
[null,"2017-01-09",42744.856249999997,"CLN23","RURAL SHORT","Asset failure","LV",1,171,5.8064023225609294E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-09",42744.863194444442,"DRN23","RURAL LONG","Asset failure","LV",1,1067,8.878053651068361E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-09",42744.872916666667,"WN3","RURAL LONG","Animal","Animal impact",75,93,5.8036011449111365E-2,6.2404313386141253E-4,"NO"]
[null,"2017-01-09",42744.897581018522,"WN5","RURAL LONG","Unknown","Unknown",178,0,0,0,"NO"]
[null,"2017-01-09",42744.94027777778,"BWN11","URBAN","Animal","Animal impact",50,40,6.8042948709225266E-3,1.7010737177306317E-4,"NO"]
[null,"2017-01-09",42744.98510416667,"WGI14","RURAL SHORT","Unknown","Unknown",811,0,0,0,"NO"]
[null,"2017-01-10",42745.000694444447,"BRA14","URBAN","Other","Fuse Insertion",1,59,2.0072669869221452E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-10",42745.02815972222,"MYT8","RURAL SHORT","Unknown","Unknown",659,0,0,0,"NO"]
[null,"2017-01-10",42745.106932870367,"WT10","URBAN","Asset Failure","HV",410,0,0,0,"NO"]
[null,"2017-01-10",42745.106932870367,"WT10","URBAN","Asset Failure","HV",549,209.58652094717669,0.39146129036647931,1.8677789420682334E-3,"NO"]
[null,"2017-01-10",42745.163657407407,"RWN34","RURAL SHORT","Unknown","Unknown",2098,0,0,0,"NO"]
[null,"2017-01-10",42745.174131944441,"KLO14","RURAL LONG","Unknown","Unknown",20,0,0,0,"NO"]
[null,"2017-01-10",42745.188611111109,"DRN23","RURAL LONG","Unknown","Unknown",59,0,0,0,"NO"]
[null,"2017-01-10",42745.211111111108,"LGA11","RURAL LONG","Animal","Animal impact",1,86,7.1556946016108631E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-10",42745.211805555555,"BN1","RURAL LONG","Animal","Animal impact",1,537,4.4681488384477131E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-10",42745.243750000001,"ELM33","RURAL SHORT","Animal","Animal impact",6,396,8.0678432271372915E-3,2.0373341482669927E-5,"NO"]
[null,"2017-01-10",42745.246527777781,"KLO14","RURAL LONG","Animal","Animal impact",2,788,1.3113226386207814E-2,1.6641150236304332E-5,"NO"]
[null,"2017-01-10",42745.273564814815,"MFA22","RURAL LONG","Unknown","Unknown",20,0,0,0,"NO"]
[null,"2017-01-10",42745.275150462963,"MOE22","RURAL LONG","Unknown","Unknown",1043,0,0,0,"NO"]
[null,"2017-01-10",42745.279166666667,"MFA22","RURAL LONG","Animal","Animal impact",10,188,1.5642681222126073E-2,8.3205751181521662E-5,"NO"]
[null,"2017-01-10",42745.318055555559,"WGL23","RURAL SHORT","Animal","Animal impact",17,156,9.0050169353401068E-3,5.7724467534231461E-5,"NO"]
[null,"2017-01-10",42745.31890046296,"WN3","RURAL LONG","Unknown","Unknown",177,0,0,0,"NO"]
[null,"2017-01-10",42745.323912037034,"BDL8","RURAL LONG","Unknown","Unknown",616,0,0,0,"NO"]
[null,"2017-01-10",42745.324999999997,"WN3","RURAL LONG","Animal","Animal impact",103,173,0.14826432803035347,8.5701923716967321E-4,"NO"]
[null,"2017-01-10",42745.340277777781,"CPK12","RURAL SHORT","Planned","-",3,464,0,0,"NO"]
[null,"2017-01-10",42745.341666666667,"PHM24","RURAL SHORT","Planned","-",91,318,0,0,"NO"]
[null,"2017-01-10",42745.35833333333,"BWN14","RURAL SHORT","Planned","-",806,279.01985111662532,0,0,"NO"]
[null,"2017-01-10",42745.364583333336,"WO32","URBAN","Planned","-",258,71,0,0,"NO"]
[null,"2017-01-10",42745.368750000001,"FTR21","RURAL LONG","Asset Failure","LV",1,174,1.4477800705584771E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-10",42745.371527777781,"CRE31","RURAL SHORT","Planned","-",36,245,0,0,"NO"]
[null,"2017-01-10",42745.375,"MBY11","RURAL SHORT","Planned","-",38,345,0,0,"NO"]
[null,"2017-01-10",42745.375,"MBY11","RURAL SHORT","Planned","-",29,234,0,0,"NO"]
[null,"2017-01-10",42745.375023148146,"MOE21","RURAL SHORT","Planned","-",25,155,0,0,"NO"]
[null,"2017-01-10",42745.375694444447,"MOE24","RURAL SHORT","Unknown","Unknown",1,206,6.9948472423833413E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-10",42745.375833333332,"MSD4","RURAL LONG","Planned","-",32,353.375,0,0,"NO"]
[null,"2017-01-10",42745.376168981478,"WGL24","RURAL LONG","Planned","-",59,368.69491525423729,0,0,"NO"]
[null,"2017-01-10",42745.37777777778,"CYN14","URBAN","Asset failure","LV",1,294,1.0002313460256115E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-10",42745.378113425926,"WT6","URBAN","Unknown","Unknown",3456,0,0,0,"NO"]
[null,"2017-01-10",42745.381944444445,"MWT14","RURAL SHORT","Planned","-",212,404,0,0,"NO"]
[null,"2017-01-10",42745.387442129628,"WN5","RURAL LONG","Unknown","Unknown",178,0,0,0,"NO"]
[null,"2017-01-10",42745.388888888891,"KMS21","RURAL SHORT","Planned","-",29,357,0,0,"NO"]
[null,"2017-01-10",42745.398611111108,"LDL23","RURAL LONG","Planned","-",121,366.97520661157023,0,0,"NO"]
[null,"2017-01-10",42745.4,"BN1","RURAL LONG","Unknown","Unknown",1,318,2.6459428875723889E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-10",42745.405555555553,"BN1","RURAL LONG","Planned","-",1,171,0,0,"NO"]
[null,"2017-01-10",42745.406944444447,"MYT7","RURAL LONG","Other","Cause Not In List",41,10,3.4114357984423881E-3,3.4114357984423884E-4,"NO"]
[null,"2017-01-10",42745.427083333336,"KLO14","RURAL LONG","Planned","-",12,10,0,0,"NO"]
[null,"2017-01-10",42745.4375,"BDL8","RURAL LONG","Planned","-",1,90,0,0,"NO"]
[null,"2017-01-10",42745.494467592594,"KLO14","RURAL LONG","Unknown","Unknown",3359,0,0,0,"NO"]
[null,"2017-01-10",42745.520138888889,"MFA34","RURAL SHORT","Asset failure","LV",1,1,3.3955569137783212E-6,3.3955569137783212E-6,"NO"]
[null,"2017-01-10",42745.548611111109,"WGI22","RURAL LONG","Animal","Animal impact",2,97,1.6141915729215204E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-10",42745.554907407408,"CNR3","RURAL SHORT","Unknown","Unknown",59,0,0,0,"NO"]
[null,"2017-01-10",42745.65347222222,"CYN22","URBAN","Asset Failure","LV",1,78,2.6536749996597853E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-10",42745.65625,"MOE32","RURAL SHORT","Unknown","Unknown",1,161,5.4668466311830969E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-10",42745.65892361111,"KLO14","RURAL LONG","Third Party","Vehicle impact",2,1601,2.6642481528323238E-2,1.6641150236304332E-5,"NO"]
[null,"2017-01-10",42745.677083333336,"BWA23","RURAL SHORT","Animal","Animal impact",1,155,5.2631132163563979E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-10",42745.752083333333,"MWT14","RURAL SHORT","Asset failure","HV",1,1,3.3955569137783212E-6,3.3955569137783212E-6,"NO"]
[null,"2017-01-10",42745.791967592595,"WYK13","RURAL SHORT","Other","Other",1,86,2.9201789458493564E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-10",42745.813194444447,"WGL24","RURAL LONG","Overload","-",10,114,9.4854556346934699E-3,8.3205751181521662E-5,"NO"]
[null,"2017-01-10",42745.826388888891,"WT10","URBAN","Unknown","Unknown",1,130,4.4227916660996423E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-10",42745.861331018517,"MFA21","RURAL LONG","Unknown","Unknown",1358,0,0,0,"NO"]
[null,"2017-01-10",42745.879166666666,"EPG34","URBAN","Third Party","Vehicle impact",38,266.5263157894737,3.4456949226351674E-2,1.2928160254752801E-4,"NO"]
[null,"2017-01-11",42746.132337962961,"RWT36","URBAN","Unknown","Unknown",638,0,0,0,"NO"]
[null,"2017-01-11",42746.279166666667,"MDG1","RURAL SHORT","Asset failure","LV",1,413,1.4023650053904466E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-11",42746.297222222223,"BRA23","URBAN","Asset Failure","Distribution substation",1,167,5.6815862172203099E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-11",42746.302523148152,"RUBA24","RURAL SHORT","Unknown","Unknown",330,0,0,0,"NO"]
[null,"2017-01-11",42746.314583333333,"PHI11","RURAL SHORT","Overload","-",1,322,1.0933693262366194E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-11",42746.334722222222,"RWN34","RURAL SHORT","Planned","-",311,507,0,0,"NO"]
[null,"2017-01-11",42746.336805555555,"FGY33","URBAN","Planned","-",316,165,0,0,"NO"]
[null,"2017-01-11",42746.336805555555,"RWT14","URBAN","Planned","-",104,565,0,0,"NO"]
[null,"2017-01-11",42746.350694444445,"WYK12","RURAL SHORT","Planned","-",40,298,0,0,"NO"]
[null,"2017-01-11",42746.350694444445,"WYK23","RURAL SHORT","Planned","-",135,310.66666666666669,0,0,"NO"]
[null,"2017-01-11",42746.354166666664,"WT11","URBAN","Planned","-",89,810,0,0,"NO"]
[null,"2017-01-11",42746.354166666664,"WT13","URBAN","Planned","-",36,810,0,0,"NO"]
[null,"2017-01-11",42746.354861111111,"WYK24","RURAL SHORT","Other","Other",1,403,1.3684094362526635E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-11",42746.354861111111,"WYK24","RURAL SHORT","Planned","-",220,403,0,0,"NO"]
[null,"2017-01-11",42746.356249999997,"RUBA12","RURAL LONG","Planned","-",16,155.4375,0,0,"NO"]
[null,"2017-01-11",42746.358738425923,"PHM33","RURAL LONG","Planned","-",457,441,0,0,"NO"]
[null,"2017-01-11",42746.364583333336,"WGL12","RURAL LONG","Planned","-",38,333,0,0,"NO"]
[null,"2017-01-11",42746.365277777775,"BDL4","RURAL SHORT","Asset failure","LV",1,112,3.8030237434317197E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-11",42746.366666666669,"TT12","URBAN","Network business","Switching and protection error",1,482,1.6398350638923288E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-11",42746.368055555555,"MFA34","RURAL SHORT","Planned","-",74,384.59459459459458,0,0,"NO"]
[null,"2017-01-11",42746.370138888888,"WOTS25","RURAL SHORT","Planned","-",70,32.714285714285715,0,0,"NO"]
[null,"2017-01-11",42746.372916666667,"WGI33","RURAL SHORT","Asset failure","LV",1,243,8.2512033004813199E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-11",42746.375,"MBY11","RURAL SHORT","Planned","-",67,373,0,0,"NO"]
[null,"2017-01-11",42746.375,"BN1","RURAL LONG","Planned","-",21,350,0,0,"NO"]
[null,"2017-01-11",42746.375,"WGL15","RURAL SHORT","Planned","-",28,360,0,0,"NO"]
[null,"2017-01-11",42746.375,"LDL23","RURAL LONG","Planned","-",2,150,0,0,"NO"]
[null,"2017-01-11",42746.378472222219,"MFA22","RURAL LONG","Planned","-",1,235,0,0,"NO"]
[null,"2017-01-11",42746.380555555559,"RUBA12","RURAL LONG","Planned","-",5,102,0,0,"NO"]
[null,"2017-01-11",42746.381701388891,"WGI23","RURAL SHORT","Planned","-",1643,5.2586731588557516,0,0,"NO"]
[null,"2017-01-11",42746.381944444445,"FTR21","RURAL LONG","Planned","-",1,260,0,0,"NO"]
[null,"2017-01-11",42746.38653935185,"BDL6","RURAL SHORT","Unknown","Unknown",901,0,0,0,"NO"]
[null,"2017-01-11",42746.388888888891,"MOE32","RURAL SHORT","Planned","-",1,90,0,0,"NO"]
[null,"2017-01-11",42746.388888888891,"WYK12","RURAL SHORT","Planned","-",134,423,0,0,"NO"]
[null,"2017-01-11",42746.392361111109,"PHM33","RURAL LONG","Planned","-",12,275,0,0,"NO"]
[null,"2017-01-11",42746.393750000003,"MWT14","RURAL SHORT","Planned","-",30,278,0,0,"NO"]
[null,"2017-01-11",42746.397916666669,"BDL6","RURAL SHORT","Animal","Animal impact",4,67,9.1000925289259004E-4,1.3582227655113285E-5,"NO"]
[null,"2017-01-11",42746.40625,"BN1","RURAL LONG","Planned","-",3,255,0,0,"NO"]
[null,"2017-01-11",42746.40625,"LGA11","RURAL LONG","Planned","-",9,125,0,0,"NO"]
[null,"2017-01-11",42746.409722222219,"RUBA12","RURAL LONG","Planned","-",2,60,0,0,"NO"]
[null,"2017-01-11",42746.417361111111,"WGI22","RURAL LONG","Vegetation","Grow-in - NSP responsibility",1,6,4.9923450708912997E-5,8.3205751181521662E-6,"NO"]
[null,"2017-01-11",42746.425000000003,"FTR21","RURAL LONG","Asset Failure","Distribution substation",1,33,2.7457897889902151E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-11",42746.431250000001,"BWR13","URBAN","Overload","-",1,199,6.7702733965679138E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-11",42746.438888888886,"BRA21","URBAN","Asset failure","LV",6,123,2.5107848073704121E-3,2.041288461276758E-5,"NO"]
[null,"2017-01-11",42746.458333333336,"SMR1","RURAL SHORT","Asset failure","HV",4,47,6.3836469979032431E-4,1.3582227655113285E-5,"NO"]
[null,"2017-01-11",42746.467974537038,"WN2","RURAL LONG","Unknown","Unknown",6,105,5.2419623244358646E-3,4.9923450708912997E-5,"NO"]
[null,"2017-01-11",42746.475694444445,"RUBA12","RURAL LONG","Planned","-",2,28,0,0,"NO"]
[null,"2017-01-11",42746.520833333336,"MOE32","RURAL SHORT","Planned","-",3,70,0,0,"NO"]
[null,"2017-01-11",42746.548611111109,"LDL23","RURAL LONG","Planned","-",2,10,0,0,"NO"]
[null,"2017-01-11",42746.568055555559,"LGA14","RURAL LONG","Asset failure","HV",18,120,1.7972442255208679E-2,1.4977035212673901E-4,"NO"]
[null,"2017-01-11",42746.576388888891,"MFA21","RURAL LONG","Third Party","Vehicle impact",5,80,3.3282300472608668E-3,4.1602875590760831E-5,"NO"]
[null,"2017-01-11",42746.644884259258,"BRT21","RURAL SHORT","Unknown","Unknown",1477,0,0,0,"NO"]
[null,"2017-01-11",42746.659722222219,"TT7","URBAN","Overload","-",1,130,4.4227916660996423E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-11",42746.682638888888,"MFA22","RURAL LONG","Animal","Animal impact",1,162,1.3479331691406511E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-11",42746.720833333333,"WN3","RURAL LONG","Animal","Animal impact",2,96,1.5975504226852159E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-11",42746.729166666664,"LDL23","RURAL LONG","Unknown","Unknown",2,75,1.2480862677228251E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-11",42746.768750000003,"WOTS11","RURAL LONG","Overload","-",1,78,6.4900485921586904E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-11",42746.803472222222,"TGN31","RURAL LONG","Asset failure","LV",1,100,8.3205751181521671E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-11",42746.856944444444,"WT13","URBAN","Animal","Animal impact",75,114,2.9088360573193799E-2,2.5516105765959471E-4,"NO"]
[null,"2017-01-11",42746.90625,"TGN23","RURAL SHORT","Animal","Animal impact",3,48,4.8896019558407821E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-11",42746.977083333331,"SMR8","RURAL LONG","Animal","Animal impact",17,64.764705882352942,9.1609532050855348E-3,1.4144977700858685E-4,"NO"]
[null,"2017-01-12",42747.072152777779,"WGI14","RURAL SHORT","Unknown","Unknown",2068,0,0,0,"NO"]
[null,"2017-01-12",42747.077094907407,"WGI14","RURAL SHORT","Asset failure","HV",1160,93.604310344827582,0.36869296525496387,3.9388460199828524E-3,"NO"]
[null,"2017-01-12",42747.234027777777,"CLN22","RURAL SHORT","Unknown","Unknown",6,258,5.2563221025288412E-3,2.0373341482669927E-5,"NO"]
[null,"2017-01-12",42747.243750000001,"BWN14","RURAL SHORT","Asset Failure","LV",1,264,8.9642702523747681E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-12",42747.255370370367,"LGA11","RURAL LONG","Unknown","Unknown",129,0,0,0,"NO"]
[null,"2017-01-12",42747.268136574072,"MSD4","RURAL LONG","Unknown","Unknown",590,0,0,0,"NO"]
[null,"2017-01-12",42747.289583333331,"BN4","URBAN","Overload","-",1,271,9.2198195501000228E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-12",42747.29928240741,"WOTS25","RURAL SHORT","Unknown","Unknown",191,0,0,0,"NO"]
[null,"2017-01-12",42747.303472222222,"FTR12","RURAL LONG","Asset Failure","LV",2,71,1.1815216667776076E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-12",42747.340277777781,"BGE22","RURAL SHORT","Planned","-",384,323,0,0,"NO"]
[null,"2017-01-12",42747.348611111112,"RWN34","RURAL SHORT","Other","Other",1,490,1.6638228877513773E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-12",42747.348611111112,"RWN34","RURAL SHORT","Other","Other",1,490,1.6638228877513773E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-12",42747.348611111112,"RWN24","URBAN","Planned","-",166,490,0,0,"NO"]
[null,"2017-01-12",42747.357268518521,"WYK13","RURAL SHORT","Planned","-",291,437.26116838487974,0,0,"NO"]
[null,"2017-01-12",42747.357812499999,"WOTS25","RURAL SHORT","Planned","-",1,170,0,0,"NO"]
[null,"2017-01-12",42747.361111111109,"WGL12","RURAL LONG","Planned","-",40,292,0,0,"NO"]
[null,"2017-01-12",42747.361805555556,"WT8","URBAN","Planned","-",49,180,0,0,"NO"]
[null,"2017-01-12",42747.362685185188,"MSD4","RURAL LONG","Planned","-",32,376.625,0,0,"NO"]
[null,"2017-01-12",42747.364583333336,"WN3","RURAL LONG","Planned","-",133,305,0,0,"NO"]
[null,"2017-01-12",42747.364583333336,"MSD4","RURAL LONG","Other","Other",1,368,3.0619716434799973E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-12",42747.364583333336,"BDL8","RURAL LONG","Planned","-",479,420.03131524008353,0,0,"NO"]
[null,"2017-01-12",42747.364583333336,"RUBA22","RURAL SHORT","Planned","-",12,235,0,0,"NO"]
[null,"2017-01-12",42747.364583333336,"WGL24","RURAL LONG","Planned","-",278,375,0,0,"NO"]
[null,"2017-01-12",42747.375,"MOE21","RURAL SHORT","Planned","-",26,195,0,0,"NO"]
[null,"2017-01-12",42747.375,"ELM31","URBAN","Planned","-",135,380,0,0,"NO"]
[null,"2017-01-12",42747.376388888886,"MBY11","RURAL SHORT","Planned","-",12,324,0,0,"NO"]
[null,"2017-01-12",42747.381249999999,"CRE32","URBAN","Planned","-",339,446,0,0,"NO"]
[null,"2017-01-12",42747.384027777778,"BGE24","RURAL SHORT","Planned","-",180,343.74444444444447,0,0,"NO"]
[null,"2017-01-12",42747.387499999997,"NLA31","RURAL LONG","Weather","-",1,0,0,0,"NO"]
[null,"2017-01-12",42747.392361111109,"BN6","RURAL LONG","Animal","Animal impact",34,101,2.8572854955734542E-2,2.8289955401717369E-4,"NO"]
[null,"2017-01-12",42747.393055555556,"WGL15","RURAL SHORT","Animal","Animal impact",1,91,3.089956791538272E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-12",42747.395833333336,"WGI14","RURAL SHORT","Planned","-",5,39,0,0,"NO"]
[null,"2017-01-12",42747.400694444441,"OFR23","RURAL LONG","Overload","-",1,134,1.1149570658323903E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-12",42747.40625,"BGE24","RURAL SHORT","Planned","-",189,328,0,0,"NO"]
[null,"2017-01-12",42747.409722222219,"MWT14","RURAL SHORT","Planned","-",36,275,0,0,"NO"]
[null,"2017-01-12",42747.415277777778,"WN5","RURAL LONG","Animal","Animal impact",1,362,3.0120481927710845E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-12",42747.415277777778,"TT7","URBAN","Asset Failure","LV",1,167,5.6815862172203099E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-12",42747.434027777781,"WGI14","RURAL SHORT","Planned","-",3,25,0,0,"NO"]
[null,"2017-01-12",42747.439004629632,"BDL44","RURAL LONG","Planned","-",43,13,0,0,"NO"]
[null,"2017-01-12",42747.46875,"MWT32","RURAL SHORT","Planned","-",147,315.79591836734693,0,0,"NO"]
[null,"2017-01-12",42747.549305555556,"MYT7","RURAL LONG","Unknown","Unknown",1,1531,1.2738800505890968E-2,8.3205751181521662E-6,"NO"]
[null,"2017-01-12",42747.583333333336,"LGA14","RURAL LONG","Planned","-",7,20,0,0,"NO"]
[null,"2017-01-12",42747.629861111112,"WT6","URBAN","Animal","Animal impact",28,48,4.5724861532599375E-3,9.5260128192915368E-5,"NO"]
[null,"2017-01-12",42747.656678240739,"BDL8","RURAL LONG","Unknown","Unknown",61,0,0,0,"NO"]
[null,"2017-01-12",42747.670138888891,"BDL8","RURAL LONG","Planned","-",549,5,0,0,"NO"]
[null,"2017-01-12",42747.680555555555,"LDL22","URBAN","Third Party","Unauthorised access",1,147,5.0011567301280573E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-12",42747.690972222219,"TT9","URBAN","Asset failure","LV",1,195,6.6341874991494637E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-12",42747.708333333336,"RWN24","URBAN","Planned","-",364,8,0,0,"NO"]
[null,"2017-01-12",42747.71607638889,"MFA21","RURAL LONG","Unknown","Unknown",1359,0,0,0,"NO"]
[null,"2017-01-12",42747.719444444447,"MFA21","RURAL LONG","Animal","Animal impact",30,101,2.5211342608001064E-2,2.49617253544565E-4,"NO"]
[null,"2017-01-12",42747.75675925926,"WYK13","RURAL SHORT","Other","Other",1,305,1.0356448587023879E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-12",42747.86041666667,"WGI33","RURAL SHORT","Animal","Animal impact",47,116,1.8512576293919406E-2,1.5959117494758108E-4,"NO"]
[null,"2017-01-12",42747.90347222222,"SLE32","RURAL SHORT","Weather","-",1,59,2.0033785791292094E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-12",42747.938888888886,"BGE12","RURAL SHORT","Third Party","Unauthorised access",130,38,1.6774051154064905E-2,4.4142239879118173E-4,"NO"]
[null,"2017-01-12",42747.979861111111,"MSD4","RURAL LONG","Weather","-",1,44,3.6610530519869534E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-13",42748.133796296293,"SLE31","RURAL LONG","Unknown","Unknown",1116,0,0,0,"NO"]
[null,"2017-01-13",42748.175891203704,"DRN23","RURAL LONG","Unknown","Unknown",2585,0,0,0,"NO"]
[null,"2017-01-13",42748.193101851852,"BN1","RURAL LONG","Animal","Animal impact",277,214.78339350180505,0.49503261665446313,2.30479930772815E-3,"NO"]
[null,"2017-01-13",42748.202939814815,"FGY31","URBAN","Unknown","Unknown",1178,0,0,0,"NO"]
[null,"2017-01-13",42748.296932870369,"BN2","RURAL LONG","Unknown","Unknown",35,0,0,0,"NO"]
[null,"2017-01-13",42748.336805555555,"LGA21","RURAL SHORT","Asset failure","LV",7,235,5.5856911231653384E-3,2.3768898396448248E-5,"NO"]
[null,"2017-01-13",42748.338194444441,"PHM22","RURAL SHORT","Animal","Animal impact",1,45,1.5280006112002446E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.344444444447,"TGN43","RURAL SHORT","Asset failure","LV",1,104,3.531379190329454E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.35,"SMR5","RURAL LONG","Unknown","Unknown",1,176,1.4644212207947814E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-13",42748.355555555558,"BWA22","RURAL LONG","Planned","-",17,188,0,0,"NO"]
[null,"2017-01-13",42748.35833333333,"FTR21","RURAL LONG","Planned","-",3,204,0,0,"NO"]
[null,"2017-01-13",42748.362881944442,"BDL41","RURAL LONG","Planned","-",5,194,0,0,"NO"]
[null,"2017-01-13",42748.364583333336,"WGL12","RURAL LONG","Planned","-",50,47,0,0,"NO"]
[null,"2017-01-13",42748.365277777775,"MOE21","RURAL SHORT","Asset failure","LV",1,134,4.5500462644629502E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.372824074075,"FTR22","RURAL SHORT","Unknown","Unknown",361,0,0,0,"NO"]
[null,"2017-01-13",42748.372916666667,"SMR8","RURAL LONG","Planned","-",3,303,0,0,"NO"]
[null,"2017-01-13",42748.375,"MBY11","RURAL SHORT","Planned","-",1,170,0,0,"NO"]
[null,"2017-01-13",42748.376944444448,"WOTS24","RURAL LONG","Unknown","Unknown",1471,0,0,0,"NO"]
[null,"2017-01-13",42748.378472222219,"OFR23","RURAL LONG","Animal","Animal impact",6,25,1.2480862677228251E-3,4.9923450708912997E-5,"NO"]
[null,"2017-01-13",42748.378472222219,"WN3","RURAL LONG","Planned","-",3,270,0,0,"NO"]
[null,"2017-01-13",42748.379976851851,"MFA34","RURAL SHORT","Planned","-",142,373,0,0,"NO"]
[null,"2017-01-13",42748.393055555556,"BWR32","URBAN","Planned","-",2,404,0,0,"NO"]
[null,"2017-01-13",42748.393634259257,"MOE21","RURAL SHORT","Animal","Animal impact",365,18,2.230880892352357E-2,1.2393782735290871E-3,"NO"]
[null,"2017-01-13",42748.397222222222,"TGN31","RURAL LONG","Planned","-",32,309,0,0,"NO"]
[null,"2017-01-13",42748.411111111112,"WYK24","RURAL SHORT","Planned","-",228,274,0,0,"NO"]
[null,"2017-01-13",42748.412499999999,"WYK23","RURAL SHORT","Other","Other",1,312,1.0594137570988362E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.412499999999,"WYK23","RURAL SHORT","Planned","-",124,312,0,0,"NO"]
[null,"2017-01-13",42748.423611111109,"ELM32","URBAN","Overload","-",1,75,2.5516105765959471E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-13",42748.425694444442,"MOE32","RURAL SHORT","Animal","Animal impact",8,112,3.0424189947453758E-3,2.716445531022657E-5,"NO"]
[null,"2017-01-13",42748.428993055553,"CRE31","RURAL SHORT","Planned","-",289,404.81314878892732,0,0,"NO"]
[null,"2017-01-13",42748.430555555555,"WGL12","RURAL LONG","Unknown","Unknown",50,192.04,7.9894162284497111E-2,4.1602875590760835E-4,"NO"]
[null,"2017-01-13",42748.447916666664,"LGA11","RURAL LONG","Planned","-",5,30,0,0,"NO"]
[null,"2017-01-13",42748.475694444445,"LGA11","RURAL LONG","Planned","-",3,25,0,0,"NO"]
[null,"2017-01-13",42748.4768287037,"RWN24","URBAN","Third Party","Vehicle impact",76,386.15789473684208,9.9846222935917148E-2,2.5856320509505602E-4,"NO"]
[null,"2017-01-13",42748.498611111114,"WYK23","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",101,257.43564356435644,8.828787531515013E-2,3.4295124829161045E-4,"NO"]
[null,"2017-01-13",42748.507638888892,"RWN26","RURAL SHORT","Asset Failure","Distribution substation",30,173,1.7622940382509486E-2,1.0186670741334964E-4,"NO"]
[null,"2017-01-13",42748.517361111109,"BWA22","RURAL LONG","Planned","-",6,30,0,0,"NO"]
[null,"2017-01-13",42748.524305555555,"LGA11","RURAL LONG","Planned","-",2,30,0,0,"NO"]
[null,"2017-01-13",42748.543055555558,"PHM24","RURAL SHORT","Animal","Animal impact",1,93,3.1578679298138387E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.548611111109,"FGY34","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",10,178,6.0558224351210483E-3,3.4021474354612629E-5,"NO"]
[null,"2017-01-13",42748.548611111109,"BDL41","RURAL LONG","Planned","-",7,45,0,0,"NO"]
[null,"2017-01-13",42748.565972222219,"PHM22","RURAL SHORT","Animal","Animal impact",1,196,6.6552915510055088E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.575694444444,"WN6","RURAL LONG","Unknown","Unknown",1336,47.107784431137723,0.52366371563602476,1.1116288357851294E-2,"NO"]
[null,"2017-01-13",42748.587233796294,"BDL44","RURAL LONG","Vegetation","Grow-in - NSP responsibility",160,150.69374999999999,0.20061738667376688,1.3312920189043466E-3,"NO"]
[null,"2017-01-13",42748.594224537039,"RUBA22","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",490,148,0.24624578738720385,1.6638228877513773E-3,"NO"]
[null,"2017-01-13",42748.597916666666,"MOE21","RURAL SHORT","Animal","Animal impact",4,303,4.1154149794993249E-3,1.3582227655113285E-5,"NO"]
[null,"2017-01-13",42748.604467592595,"WGI14","RURAL SHORT","Unknown","Unknown",2070,0,0,0,"NO"]
[null,"2017-01-13",42748.607638888891,"ELM32","URBAN","Asset Failure","LV",64,426,9.2756147680415874E-2,2.1773743586952083E-4,"NO"]
[null,"2017-01-13",42748.618055555555,"BRA11","URBAN","Other","Poor Work Practice",56,145,2.7625437175945455E-2,1.9052025638583074E-4,"NO"]
[null,"2017-01-13",42748.61923611111,"WGI14","RURAL SHORT","Asset failure","HV",76,201,5.1870527414877632E-2,2.5806232544715239E-4,"NO"]
[null,"2017-01-13",42748.64634259259,"WYK23","RURAL SHORT","Unknown","Unknown",33,0,0,0,"NO"]
[null,"2017-01-13",42748.654166666667,"WYK23","RURAL SHORT","Other","Cause Not In List",2,1318,8.9506880247196552E-3,6.7911138275566425E-6,"NO"]
[null,"2017-01-13",42748.710416666669,"BDL44","RURAL LONG","Vegetation","Blow-in/Fall-in - NSP responsibility",7,77,4.4847899886840178E-3,5.8244025827065164E-5,"NO"]
[null,"2017-01-13",42748.755995370368,"WYK24","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1663,0,0,0,"NO"]
[null,"2017-01-13",42748.755995370368,"WYK24","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1719,52.171029668411869,0.30452033514146737,5.8369623347849335E-3,"NO"]
[null,"2017-01-13",42748.760416666664,"WYK23","RURAL SHORT","Unknown","Unknown",1,120,4.0746682965339854E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.771527777775,"FTR22","RURAL SHORT","Animal","Animal impact",1,107,3.6332458977428035E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.773923611108,"WYK24","RURAL SHORT","Unknown","Unknown",187,0,0,0,"NO"]
[null,"2017-01-13",42748.789583333331,"CYN32","URBAN","Asset failure","LV",1,38,1.2928160254752801E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-13",42748.809027777781,"WN6","RURAL LONG","Asset Failure","HV",1336,55.32934131736527,0.61505691273380814,1.1116288357851294E-2,"NO"]
[null,"2017-01-13",42748.817361111112,"WYK23","RURAL SHORT","Unknown","Unknown",1,38,1.290311627235762E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-13",42748.868750000001,"LGA23","RURAL LONG","Planned","-",1,57,0,0,"NO"]
[null,"2017-01-13",42748.887650462966,"PHM33","RURAL LONG","Unknown","Unknown",456,0,0,0,"NO"]
[null,"2017-01-13",42748.89166666667,"SFS1","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",90,223.88888888888889,6.8420471812633166E-2,3.0560012224004892E-4,"NO"]
[null,"2017-01-13",42748.892361111109,"PHM33","RURAL LONG","Animal","Animal impact",149,71,8.802336417493177E-2,1.2397656926046729E-3,"NO"]
[null,"2017-01-13",42748.918749999997,"BDL8","RURAL LONG","Animal","Animal impact",66,75,4.1186846834853227E-2,5.4915795779804301E-4,"NO"]
[null,"2017-01-13",42748.925694444442,"FGY14","URBAN","Animal","Animal impact",24,132,1.0778003075541281E-2,8.165153845107032E-5,"NO"]
[null,"2017-01-13",42748.926018518519,"WT13","URBAN","Unknown","Unknown",3367,0,0,0,"NO"]
[null,"2017-01-14",42749.011990740742,"UWY1","RURAL SHORT","Unknown","Unknown",2958,0,0,0,"NO"]
[null,"2017-01-14",42749.013194444444,"RUBA22","RURAL SHORT","Animal","Animal impact",2,193,1.310684968718432E-3,6.7911138275566425E-6,"NO"]
[null,"2017-01-14",42749.032638888886,"CRE32","URBAN","Asset failure","HV",9,190,5.8176721146387597E-3,3.061932691915137E-5,"NO"]
[null,"2017-01-14",42749.037847222222,"WGL12","RURAL LONG","Unknown","Unknown",226,0,0,0,"NO"]
[null,"2017-01-14",42749.07135416667,"FTR22","RURAL SHORT","Unknown","Unknown",1284,0,0,0,"NO"]
[null,"2017-01-14",42749.142939814818,"MOE21","RURAL SHORT","Unknown","Unknown",365,0,0,0,"NO"]
[null,"2017-01-14",42749.170046296298,"MOE31","RURAL LONG","Unknown","Unknown",272,0,0,0,"NO"]
[null,"2017-01-14",42749.262199074074,"WN5","RURAL LONG","Unknown","Unknown",1221,0,0,0,"NO"]
[null,"2017-01-14",42749.291666666664,"HPK11","URBAN","Third Party","Unauthorised access",1,520,1.7691166664398569E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-14",42749.311018518521,"FTR21","RURAL LONG","Unknown","Unknown",198,0,0,0,"NO"]
[null,"2017-01-14",42749.314375000002,"SMR5","RURAL LONG","Animal","Animal impact",80,18,1.1981628170139119E-2,6.656460094521733E-4,"NO"]
[null,"2017-01-14",42749.334027777775,"RUBA22","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",6,404,8.2308299589986499E-3,2.0373341482669927E-5,"NO"]
[null,"2017-01-14",42749.417916666665,"FTR22","RURAL SHORT","Unknown","Unknown",1284,0,0,0,"NO"]
[null,"2017-01-14",42749.427083333336,"BWR12","URBAN","Asset failure","LV",1,147,5.0011567301280573E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-14",42749.43472222222,"BDL41","RURAL LONG","Asset failure","LV",1,137,1.1399187911868469E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-14",42749.498611111114,"WGL12","RURAL LONG","Animal","Animal impact",1,96,7.9877521134260796E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-14",42749.502372685187,"FTR12","RURAL LONG","Unknown","Unknown",324,0,0,0,"NO"]
[null,"2017-01-14",42749.524305555555,"BWR23","URBAN","Overload","-",1,480,1.6330307690214064E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-14",42749.623622685183,"WN5","RURAL LONG","Unknown","Unknown",178,0,0,0,"NO"]
[null,"2017-01-14",42749.636805555558,"WN5","RURAL LONG","Animal","Animal impact",3,76,1.897091126938694E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-14",42749.645138888889,"WGI23","RURAL SHORT","Asset failure","LV",1,164,5.568713338596447E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-14",42749.651388888888,"BGE24","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",14,262,1.2454902759738882E-2,4.7537796792896496E-5,"NO"]
[null,"2017-01-14",42749.662499999999,"WYK23","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1,191,6.4855137053165931E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-14",42749.674247685187,"MFA23","RURAL SHORT","Unknown","Unknown",31,0,0,0,"NO"]
[null,"2017-01-14",42749.764976851853,"LGA13","RURAL LONG","Asset failure","HV",49,95.020408163265301,3.8740597750116491E-2,4.0770818078945617E-4,"NO"]
[null,"2017-01-14",42749.941724537035,"SMR5","RURAL LONG","Unknown","Unknown",50,0,0,0,"NO"]
[null,"2017-01-15",42750.018680555557,"MOE14","RURAL SHORT","Unknown","Unknown",449,0,0,0,"NO"]
[null,"2017-01-15",42750.018726851849,"MOE21","RURAL SHORT","Unknown","Unknown",684,0,0,0,"NO"]
[null,"2017-01-15",42750.018796296295,"MOE21","RURAL SHORT","Unknown","Unknown",365,0,0,0,"NO"]
[null,"2017-01-15",42750.207407407404,"MOE14","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",449,263,0.40097112927734058,1.5246050542864662E-3,"NO"]
[null,"2017-01-15",42750.020902777775,"MOE21","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",44,182.81818181818181,2.7313859814432816E-2,1.4940450420624613E-4,"NO"]
[null,"2017-01-15",42750.057395833333,"CYN33","RURAL SHORT","Unknown","Unknown",5333,0,0,0,"NO"]
[null,"2017-01-15",42750.086111111108,"CYN31","URBAN","Asset failure","LV",115,91,3.560347291210212E-2,3.9124695507804528E-4,"NO"]
[null,"2017-01-15",42750.107928240737,"MOE14","RURAL SHORT","Unknown","Unknown",449,0,0,0,"NO"]
[null,"2017-01-15",42750.107974537037,"MOE21","RURAL SHORT","Unknown","Unknown",365,0,0,0,"NO"]
[null,"2017-01-15",42750.107974537037,"MOE21","RURAL SHORT","Unknown","Unknown",275,0,0,0,"NO"]
[null,"2017-01-15",42750.116412037038,"BGE22","RURAL SHORT","Unknown","Unknown",1291,0,0,0,"NO"]
[null,"2017-01-15",42750.120833333334,"BGE22","RURAL SHORT","Animal","Animal impact",384,121,0.1577711564417959,1.3038938548908753E-3,"NO"]
[null,"2017-01-15",42750.162499999999,"BGE12","RURAL SHORT","Animal","Animal impact",88,154.63636363636363,4.6206738482695395E-2,2.9880900841249225E-4,"NO"]
[null,"2017-01-15",42750.25136574074,"MSD1","RURAL LONG","Unknown","Unknown",1445,0,0,0,"NO"]
[null,"2017-01-15",42750.251481481479,"WN5","RURAL LONG","Unknown","Unknown",1221,0,0,0,"NO"]
[null,"2017-01-15",42750.271134259259,"CLN22","RURAL SHORT","Unknown","Unknown",585,0,0,0,"NO"]
[null,"2017-01-15",42750.275694444441,"SMR5","RURAL LONG","Animal","Animal impact",2,78,1.2980097184317381E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-15",42750.279861111114,"CLN22","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",56,69,1.3120431914839432E-2,1.9015118717158599E-4,"NO"]
[null,"2017-01-15",42750.29791666667,"MJG11","RURAL SHORT","Animal","Animal impact",117,90,3.5755214302085718E-2,3.9728015891206354E-4,"NO"]
[null,"2017-01-15",42750.304629629631,"WOTS25","RURAL SHORT","Unknown","Unknown",191,0,0,0,"NO"]
[null,"2017-01-15",42750.313888888886,"WOTS25","RURAL SHORT","Animal","Animal impact",31,80,8.4209811461702366E-3,1.0526226432712796E-4,"NO"]
[null,"2017-01-15",42750.327777777777,"WGI33","RURAL SHORT","Asset failure","HV",47,68,1.0852199896435514E-2,1.5959117494758108E-4,"NO"]
[null,"2017-01-15",42750.340277777781,"KLO14","RURAL LONG","Planned","-",503,500,0,0,"NO"]
[null,"2017-01-15",42750.352083333331,"MSD2","RURAL LONG","Animal","Animal impact",132,163,0.17902549424216202,1.098315915596086E-3,"NO"]
[null,"2017-01-15",42750.355486111112,"MWT14","RURAL SHORT","Planned","-",40,342.6,0,0,"NO"]
[null,"2017-01-15",42750.36041666667,"FGY33","URBAN","Asset failure","LV",1,129,4.3887701917450292E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-15",42750.364583333336,"LGA21","RURAL SHORT","Planned","-",242,394,0,0,"NO"]
[null,"2017-01-15",42750.367025462961,"WO14","URBAN","Unknown","Unknown",553,0,0,0,"NO"]
[null,"2017-01-15",42750.370138888888,"MYT2","RURAL SHORT","Animal","Animal impact",19,74,4.7741530207723194E-3,6.4515581361788098E-5,"NO"]
[null,"2017-01-15",42750.377083333333,"WO14","URBAN","Animal","Animal impact",38,48,6.2055169222813436E-3,1.2928160254752801E-4,"NO"]
[null,"2017-01-15",42750.449305555558,"MSD2","RURAL LONG","Animal","Animal impact",3,60,1.4977035212673899E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-15",42750.517361111109,"SLE14","RURAL SHORT","Asset failure","LV",1,45,1.5280006112002446E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-15",42750.550694444442,"WT7","URBAN","Animal","Animal impact",66,71,1.5942462882571479E-2,2.2454173074044337E-4,"NO"]
[null,"2017-01-15",42750.638726851852,"LGA24","RURAL SHORT","Unknown","Unknown",787,0,0,0,"NO"]
[null,"2017-01-15",42750.666666666664,"WYK24","RURAL SHORT","Third Party","Vehicle impact",39,375,4.9660019864007948E-2,1.3242671963735453E-4,"NO"]
[null,"2017-01-15",42750.788194444445,"LDL22","URBAN","Animal","Animal impact",43,60,8.7775403834900595E-3,1.4629233972483432E-4,"NO"]
[null,"2017-01-15",42750.81486111111,"WN4","RURAL SHORT","Asset Failure","HV",2626,43.489718202589486,0.38778618178113938,8.916732455581871E-3,"NO"]
[null,"2017-01-15",42750.814884259256,"WN5","RURAL LONG","Unknown","Unknown",727,0,0,0,"NO"]
[null,"2017-01-15",42750.829861111109,"WGI23","RURAL SHORT","Animal","Animal impact",28,93,8.8420302034787485E-3,9.5075593585792993E-5,"NO"]
[null,"2017-01-15",42750.89980324074,"WN2","RURAL LONG","Asset failure","LV",53,139,6.1297676895427013E-2,4.4099048126206486E-4,"NO"]
[null,"2017-01-16",42751.043055555558,"WT12","URBAN","Animal","Animal impact",100,48,1.6330307690214062E-2,3.4021474354612634E-4,"NO"]
[null,"2017-01-16",42751.105555555558,"SMR2","RURAL SHORT","Unknown","Unknown",1,385,1.3072894118046536E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-16",42751.146956018521,"BDL6","RURAL SHORT","Unknown","Unknown",1296,0,0,0,"NO"]
[null,"2017-01-16",42751.263101851851,"WYK13","RURAL SHORT","Unknown","Unknown",613,0,0,0,"NO"]
[null,"2017-01-16",42751.288194444445,"SLE14","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",276,363.55072463768118,0.34071018072851672,9.3717370820281662E-4,"NO"]
[null,"2017-01-16",42751.298495370371,"CLN22","RURAL SHORT","Unknown","Unknown",585,0,0,0,"NO"]
[null,"2017-01-16",42751.305555555555,"WGL12","RURAL LONG","Unknown","Unknown",1,182,1.5143446715036944E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-16",42751.32708333333,"CYN33","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",31,529,5.5683737829050686E-2,1.0526226432712796E-4,"NO"]
[null,"2017-01-16",42751.328472222223,"CLN22","RURAL SHORT","Animal","Animal impact",3,54,5.5008022003208803E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-16",42751.354166666664,"RUBA22","RURAL SHORT","Planned","-",55,240,0,0,"NO"]
[null,"2017-01-16",42751.354166666664,"WN3","RURAL LONG","Planned","-",8,350,0,0,"NO"]
[null,"2017-01-16",42751.361111111109,"EPG12","URBAN","Planned","-",2,3020,0,0,"NO"]
[null,"2017-01-16",42751.364583333336,"RWN34","RURAL SHORT","Planned","-",5,20,0,0,"NO"]
[null,"2017-01-16",42751.364583333336,"SMR3","RURAL LONG","Planned","-",28,355,0,0,"NO"]
[null,"2017-01-16",42751.364583333336,"LDL23","RURAL LONG","Planned","-",2,285,0,0,"NO"]
[null,"2017-01-16",42751.368055555555,"MSD4","RURAL LONG","Planned","-",2,370,0,0,"NO"]
[null,"2017-01-16",42751.375,"BDL4","RURAL SHORT","Asset failure","HV",1,75,2.5466676853337406E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-16",42751.375,"SLE31","RURAL LONG","Planned","-",18,195,0,0,"NO"]
[null,"2017-01-16",42751.378472222219,"MSD4","RURAL LONG","Planned","-",33,314.78787878787881,0,0,"NO"]
[null,"2017-01-16",42751.396527777775,"BGE11","RURAL SHORT","Asset failure","LV",9,0,0,0,"NO"]
[null,"2017-01-16",42751.417361111111,"PHM32","URBAN","Planned","-",1,154,0,0,"NO"]
[null,"2017-01-16",42751.420138888891,"KMS21","RURAL SHORT","Other","High/Low volt or Tap change",2,5,3.395556913778321E-5,6.7911138275566425E-6,"NO"]
[null,"2017-01-16",42751.423611111109,"RWN34","RURAL SHORT","Unknown","Unknown",44,0,0,0,"NO"]
[null,"2017-01-16",42751.423611111109,"RWN34","RURAL SHORT","Unknown","Unknown",95,0,0,0,"NO"]
[null,"2017-01-16",42751.444444444445,"ELM31","URBAN","Planned","-",134,180,0,0,"NO"]
[null,"2017-01-16",42751.447916666664,"WN4","RURAL SHORT","Asset failure","LV",1,154,5.2291576472186145E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-16",42751.475694444445,"BN6","RURAL LONG","Other","High/Low volt or Tap change",4,5,1.6641150236304332E-4,3.3282300472608665E-5,"NO"]
[null,"2017-01-16",42751.481944444444,"MFA34","RURAL SHORT","Animal","Animal impact",53,97,1.7456558093734347E-2,1.7996451643025101E-4,"NO"]
[null,"2017-01-16",42751.486111111109,"BDL6","RURAL SHORT","Other","High/Low volt or Tap change",2,13,8.828447975823635E-5,6.7911138275566425E-6,"NO"]
[null,"2017-01-16",42751.510393518518,"MFA23","RURAL SHORT","Unknown","Unknown",464,0,0,0,"NO"]
[null,"2017-01-16",42751.549305555556,"LGA13","RURAL LONG","Asset Failure","LV",1,69,5.7411968315249952E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-16",42751.577777777777,"PHM22","RURAL SHORT","Animal","Animal impact",1,36,1.2224004889601955E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-16",42751.627256944441,"BN3","RURAL SHORT","Unknown","Unknown",34,0,0,0,"NO"]
[null,"2017-01-16",42751.644444444442,"WN5","RURAL LONG","Animal","Animal impact",1,123,1.0234307395327164E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-16",42751.706250000003,"LLG14","RURAL SHORT","Overload","-",2,150,1.0186670741334962E-3,6.7911138275566425E-6,"NO"]
[null,"2017-01-16",42751.731249999997,"MSD4","RURAL LONG","Other","Other",1,144,1.198162817013912E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-16",42751.786111111112,"RWN24","URBAN","Overload","-",16,217,1.1812255895921506E-2,5.4434358967380209E-5,"NO"]
[null,"2017-01-16",42751.790277777778,"RWN24","URBAN","Overload","-",18,211,1.2921355959881878E-2,6.123865383830274E-5,"NO"]
[null,"2017-01-16",42751.81622685185,"LGA11","RURAL LONG","Unknown","Unknown",129,0,0,0,"NO"]
[null,"2017-01-16",42751.847222222219,"TT9","URBAN","Overload","-",15,103,5.2563177877876519E-3,5.103221153191895E-5,"NO"]
[null,"2017-01-16",42751.854166666664,"LGA11","RURAL LONG","Animal","Animal impact",1,92,7.6549291086999932E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-16",42751.861111111109,"ELM32","URBAN","Overload","-",3,125,1.2758052882979737E-3,1.020644230638379E-5,"NO"]
[null,"2017-01-16",42751.866863425923,"BN6","RURAL LONG","Unknown","Unknown",716,0,0,0,"NO"]
[null,"2017-01-17",42752.15625,"SMR5","RURAL LONG","Overload","-",1,50,4.1602875590760835E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-17",42752.251377314817,"SLE32","RURAL SHORT","Unknown","Unknown",166,0,0,0,"NO"]
[null,"2017-01-17",42752.256944444445,"FTR23","RURAL LONG","Vegetation","Grow-in - NSP responsibility",1,105,8.7366038740597748E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-17",42752.288483796299,"WN5","RURAL LONG","Unknown","Unknown",1221,0,0,0,"NO"]
[null,"2017-01-17",42752.334027777775,"LDL23","RURAL LONG","Planned","-",13,161,0,0,"NO"]
[null,"2017-01-17",42752.334722222222,"LDL23","RURAL LONG","Unknown","Unknown",6,213,1.0633695000998469E-2,4.9923450708912997E-5,"NO"]
[null,"2017-01-17",42752.344444444447,"LDL23","RURAL LONG","Unknown","Unknown",2,47,7.821340611063037E-4,1.6641150236304332E-5,"NO"]
[null,"2017-01-17",42752.350694444445,"ELM32","URBAN","Planned","-",36,335,0,0,"NO"]
[null,"2017-01-17",42752.352777777778,"BWN13","URBAN","Planned","-",640,406.80624999999998,0,0,"NO"]
[null,"2017-01-17",42752.354166666664,"WGL24","RURAL LONG","Planned","-",80,397,0,0,"NO"]
[null,"2017-01-17",42752.354166666664,"KMS21","RURAL SHORT","Planned","-",106,345,0,0,"NO"]
[null,"2017-01-17",42752.354166666664,"LGA14","RURAL LONG","Planned","-",3,140,0,0,"NO"]
[null,"2017-01-17",42752.361111111109,"BDL44","RURAL LONG","Planned","-",1,255,0,0,"NO"]
[null,"2017-01-17",42752.364583333336,"MFA34","RURAL SHORT","Planned","-",57,285.61403508771929,0,0,"NO"]
[null,"2017-01-17",42752.364594907405,"MFA34","RURAL SHORT","Other","Other",1,285,9.6773372042682152E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.366111111114,"LGA11","RURAL LONG","Planned","-",129,240,0,0,"NO"]
[null,"2017-01-17",42752.366666666669,"MWT14","RURAL SHORT","Planned","-",122,275.49180327868851,0,0,"NO"]
[null,"2017-01-17",42752.368055555555,"EPG13","RURAL SHORT","Planned","-",113,340.65486725663715,0,0,"NO"]
[null,"2017-01-17",42752.373611111114,"RWN26","RURAL SHORT","Asset Failure","LV",1,172,5.8403578916987127E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.375,"WN6","RURAL LONG","Planned","-",1,65,0,0,"NO"]
[null,"2017-01-17",42752.381944444445,"RUBA22","RURAL SHORT","Planned","-",21,175,0,0,"NO"]
[null,"2017-01-17",42752.384027777778,"LLG11","RURAL SHORT","Planned","-",1,59,0,0,"NO"]
[null,"2017-01-17",42752.385416666664,"UWY1","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",25,220,1.8675563025780766E-2,8.4888922844458028E-5,"NO"]
[null,"2017-01-17",42752.385416666664,"OFR23","RURAL LONG","Planned","-",17,286.47058823529414,0,0,"NO"]
[null,"2017-01-17",42752.392361111109,"BDL8","RURAL LONG","Planned","-",6,260,0,0,"NO"]
[null,"2017-01-17",42752.392361111109,"BRA21","URBAN","Other","Other",1,270,9.1857980757454108E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-17",42752.392361111109,"BRA21","URBAN","Planned","-",103,270,0,0,"NO"]
[null,"2017-01-17",42752.396527777775,"TT4","URBAN","Other","Fuse Insertion",1,89,3.0279112175605241E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-17",42752.40625,"WGL12","RURAL LONG","Planned","-",99,305,0,0,"NO"]
[null,"2017-01-17",42752.418749999997,"SLE32","RURAL SHORT","Animal","Animal impact",1,88,2.9880900841249225E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.431250000001,"PHI13","URBAN","Third Party","Vehicle impact",1,93,3.1639971149789747E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-17",42752.445833333331,"FTR21","RURAL LONG","Planned","-",175,395.25142857142856,0,0,"NO"]
[null,"2017-01-17",42752.453472222223,"MWT31","RURAL SHORT","Animal","Animal impact",1,118,4.0067571582584187E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.465254629627,"WGL21","RURAL LONG","Animal","Animal impact",4469,20.1850525844708,0.75057411968315246,3.7184650203022036E-2,"NO"]
[null,"2017-01-17",42752.465277777781,"WN2","RURAL LONG","Planned","-",2,30,0,0,"NO"]
[null,"2017-01-17",42752.478472222225,"MFA31","RURAL SHORT","Asset failure","LV",1,220,7.470225210312306E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.481249999997,"FTR22","RURAL SHORT","Animal","Animal impact",36,86,1.0512644205057682E-2,1.2224004889601955E-4,"NO"]
[null,"2017-01-17",42752.504166666666,"MWT14","RURAL SHORT","Animal","Animal impact",1,480,1.6298673186135942E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.511805555558,"BDL43","URBAN","Overload","-",1,86,2.9258467944966865E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-17",42752.512499999997,"TGN11","RURAL SHORT","Unknown","Unknown",1,157,5.3310243546319646E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.515972222223,"MWT13","RURAL SHORT","Asset failure","LV",1,195,6.6213359818677266E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.522916666669,"WN5","RURAL LONG","Animal","Animal impact",1,106,8.8198096252412972E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-17",42752.532638888886,"ELM32","URBAN","Overload","-",75,163,4.1591252398513939E-2,2.5516105765959471E-4,"NO"]
[null,"2017-01-17",42752.538391203707,"NLA31","RURAL LONG","Unknown","Unknown",593,0,0,0,"NO"]
[null,"2017-01-17",42752.559027777781,"SLE14","RURAL SHORT","Unknown","Unknown",1,106,3.5992903286050201E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.572222222225,"KLK3","RURAL SHORT","Other","Cause Not In List",1,465,1.5789339649069194E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.583333333336,"MYT7","RURAL LONG","Planned","-",1,70,0,0,"NO"]
[null,"2017-01-17",42752.59375,"WGL21","RURAL LONG","Animal","Animal impact",1,251,2.0884643546561937E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-17",42752.597916666666,"MOE21","RURAL SHORT","Weather","-",1,223,7.5720919177256561E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.616261574076,"BGE12","RURAL SHORT","Unknown","Unknown",578,0,0,0,"NO"]
[null,"2017-01-17",42752.62222222222,"BGE12","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",50,22.6,3.8369793125695027E-3,1.6977784568891606E-4,"NO"]
[null,"2017-01-17",42752.632638888892,"LDL14","RURAL SHORT","Animal","Animal impact",2,99,6.7232026892810755E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-17",42752.640277777777,"SMG21","URBAN","Overload","-",4,78,1.0614699998639141E-3,1.3608589741845052E-5,"NO"]
[null,"2017-01-17",42752.643750000003,"CRE32","URBAN","Overload","-",79,81,2.1770341439516623E-2,2.6876964740143978E-4,"NO"]
[null,"2017-01-17",42752.683333333334,"CRE22","URBAN","Overload","-",46,135,2.1127335574214444E-2,1.5649878203121811E-4,"NO"]
[null,"2017-01-17",42752.688888888886,"LLG14","RURAL SHORT","Other","Cause Not In List",2,87,5.9082690299742783E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-17",42752.701388888891,"LLG12","RURAL SHORT","Other","High/Low volt or Tap change",1,58,1.9694230099914263E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.706944444442,"PHM31","RURAL SHORT","Overload","-",1,162,5.5008022003208803E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-17",42752.717361111114,"NLA31","RURAL LONG","Animal","Animal impact",1,147,1.2231245423683684E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-17",42752.717361111114,"YN31","URBAN","Asset failure","LV",1,107,3.6402977559435516E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-17",42752.720729166664,"CF2","RURAL SHORT","Unknown","Unknown",635,0,0,0,"NO"]
[null,"2017-01-17",42752.721574074072,"FTR21","RURAL LONG","Unknown","Unknown",157,0,0,0,"NO"]
[null,"2017-01-17",42752.724409722221,"CF2","RURAL SHORT","Unknown","Unknown",635,0,0,0,"NO"]
[null,"2017-01-17",42752.763796296298,"WGL21","RURAL LONG","Vegetation","Blow-in/Fall-in - NSP responsibility",417,104.13189448441247,0.36130433335552153,3.4696798242694533E-3,"NO"]
[null,"2017-01-17",42752.765277777777,"BRA24","URBAN","Overload","-",50,61,1.0376549678156852E-2,1.7010737177306317E-4,"NO"]
[null,"2017-01-17",42752.767361111109,"FTR23","RURAL LONG","Other","High/Low volt or Tap change",2,5,8.3205751181521662E-5,1.6641150236304332E-5,"NO"]
[null,"2017-01-17",42752.768055555556,"CRE32","URBAN","Animal","Animal impact",82,99,2.7618632881074533E-2,2.7897608970782359E-4,"NO"]
[null,"2017-01-17",42752.772916666669,"WT10","URBAN","Overload","-",185,195,0.12273246873426506,6.2939727556033363E-4,"NO"]
[null,"2017-01-17",42752.777777777781,"KMS1","RURAL SHORT","Overload","-",17,91,5.2529265456150625E-3,5.7724467534231461E-5,"NO"]
[null,"2017-01-17",42752.794444444444,"FGY14","URBAN","Unknown","Unknown",1,97,3.3000830123974253E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-17",42752.798773148148,"FTR12","RURAL LONG","Unknown","Unknown",363,0,0,0,"NO"]
[null,"2017-01-17",42752.803472222222,"RWN34","RURAL SHORT","Asset Failure","LV",18,68,4.156161662464665E-3,6.1120024448009776E-5,"NO"]
[null,"2017-01-17",42752.843055555553,"WT8","URBAN","Overload","-",19,106,6.8519249350189838E-3,6.4640801273764005E-5,"NO"]
[null,"2017-01-17",42752.89603009259,"LDL24","URBAN","Third Party","Vehicle impact",1,645,2.1943850958725149E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-17",42752.902083333334,"FTR12","RURAL LONG","Asset failure","HV",2,86,1.4311389203221726E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-17",42752.906944444447,"TGN12","URBAN","Overload","-",1,50,1.7010737177306317E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-17",42752.97896990741,"LDL22","URBAN","Unknown","Unknown",1783,0,0,0,"NO"]
[null,"2017-01-18",42753.027083333334,"LDL21","RURAL SHORT","Animal","Animal impact",17,64,3.6943659221908135E-3,5.7724467534231461E-5,"NO"]
[null,"2017-01-18",42753.094444444447,"CYN13","URBAN","Animal","Animal impact",139,59,2.7901011118217821E-2,4.728984935291156E-4,"NO"]
[null,"2017-01-18",42753.277303240742,"OFR23","RURAL LONG","Unknown","Unknown",59,0,0,0,"NO"]
[null,"2017-01-18",42753.286805555559,"DRN23","RURAL LONG","Asset failure","LV",1,202,1.6807561738667377E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-18",42753.333333333336,"FGY14","URBAN","Planned","-",114,466,0,0,"NO"]
[null,"2017-01-18",42753.333333333336,"EPG14","URBAN","Planned","-",39,370,0,0,"NO"]
[null,"2017-01-18",42753.343969907408,"BDL8","RURAL LONG","Planned","-",75,372.64,0,0,"NO"]
[null,"2017-01-18",42753.347002314818,"BGE12","RURAL SHORT","Planned","-",426,613,0,0,"NO"]
[null,"2017-01-18",42753.3518287037,"KLK1","RURAL SHORT","Asset failure","HV",345,206.04347826086956,0.24137316321593194,1.1714671352535207E-3,"NO"]
[null,"2017-01-18",42753.354166666664,"OFR23","RURAL LONG","Planned","-",144,375,0,0,"NO"]
[null,"2017-01-18",42753.354166666664,"WGL24","RURAL LONG","Planned","-",31,480,0,0,"NO"]
[null,"2017-01-18",42753.364583333336,"MWT14","RURAL SHORT","Planned","-",6,210,0,0,"NO"]
[null,"2017-01-18",42753.36519675926,"MYT7","RURAL LONG","Planned","-",266,147.05263157894737,0,0,"NO"]
[null,"2017-01-18",42753.368055555555,"FTR21","RURAL LONG","Planned","-",32,370.3125,0,0,"NO"]
[null,"2017-01-18",42753.368055555555,"BN1","RURAL LONG","Planned","-",1,65,0,0,"NO"]
[null,"2017-01-18",42753.372916666667,"BDL44","RURAL LONG","Planned","-",239,438,0,0,"NO"]
[null,"2017-01-18",42753.375,"MBY11","RURAL SHORT","Planned","-",175,330,0,0,"NO"]
[null,"2017-01-18",42753.375,"LGA14","RURAL LONG","Planned","-",168,410,0,0,"NO"]
[null,"2017-01-18",42753.375821759262,"RUBA12","RURAL LONG","Planned","-",248,370.28225806451616,0,0,"NO"]
[null,"2017-01-18",42753.377083333333,"BWR13","URBAN","Overload","-",1,159,5.4094144223834086E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-18",42753.378472222219,"LDL23","RURAL LONG","Planned","-",52,343,0,0,"NO"]
[null,"2017-01-18",42753.381944444445,"MFA21","RURAL LONG","Planned","-",327,318.18348623853211,0,0,"NO"]
[null,"2017-01-18",42753.381944444445,"WYK24","RURAL SHORT","Planned","-",60,467,0,0,"NO"]
[null,"2017-01-18",42753.381944444445,"RUBA12","RURAL LONG","Planned","-",10,322,0,0,"NO"]
[null,"2017-01-18",42753.383333333331,"LLG13","RURAL SHORT","Planned","-",1,107,0,0,"NO"]
[null,"2017-01-18",42753.385416666664,"LGA14","RURAL LONG","Planned","-",2,261,0,0,"NO"]
[null,"2017-01-18",42753.386805555558,"FGY34","URBAN","Asset failure","LV",1,194,6.6001660247948506E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-18",42753.395833333336,"MWT14","RURAL SHORT","Planned","-",26,133,0,0,"NO"]
[null,"2017-01-18",42753.40625,"WYK24","RURAL SHORT","Planned","-",3,358,0,0,"NO"]
[null,"2017-01-18",42753.40625,"LLG12","RURAL SHORT","Planned","-",1,61,0,0,"NO"]
[null,"2017-01-18",42753.408333333333,"MJG11","RURAL SHORT","Third Party","Vehicle impact",1,320,1.0865782124090627E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-18",42753.408333333333,"LLG14","RURAL SHORT","Animal","Animal impact",33,70,7.8437364708279222E-3,1.120533781546846E-4,"NO"]
[null,"2017-01-18",42753.413194444445,"WYK24","RURAL SHORT","Planned","-",46,338,0,0,"NO"]
[null,"2017-01-18",42753.413888888892,"BWR34","URBAN","Planned","-",37,29,0,0,"NO"]
[null,"2017-01-18",42753.418055555558,"MOE32","RURAL SHORT","Network business","Switching and protection error",1,119,4.0407127273962021E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-18",42753.427083333336,"WGL24","RURAL LONG","Planned","-",20,100.25,0,0,"NO"]
[null,"2017-01-18",42753.427083333336,"WGI23","RURAL SHORT","Planned","-",8,30,0,0,"NO"]
[null,"2017-01-18",42753.427974537037,"EPG32","RURAL SHORT","Third Party","Dig-in",26,0,0,0,"NO"]
[null,"2017-01-18",42753.427974537037,"EPG32","RURAL SHORT","Third Party","Dig-in",3152,65.654505076142129,0.70268673440802709,1.0702795392229267E-2,"NO"]
[null,"2017-01-18",42753.43577546296,"WOTS13","RURAL LONG","Unknown","Unknown",149,0,0,0,"NO"]
[null,"2017-01-18",42753.479166666664,"LLG12","RURAL SHORT","Planned","-",2,51,0,0,"NO"]
[null,"2017-01-18",42753.493750000001,"WOTS13","RURAL LONG","Animal","Animal impact",2,105,1.747320774811955E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-18",42753.502083333333,"PHM22","RURAL SHORT","Animal","Animal impact",1,70,2.3768898396448246E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-18",42753.509722222225,"WYK24","RURAL SHORT","Animal","Animal impact",1,173,5.874313460836495E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-18",42753.526388888888,"TT1","URBAN","Overload","-",1,277,9.423948396227699E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-18",42753.541666666664,"WGL24","RURAL LONG","Planned","-",2,75,0,0,"NO"]
[null,"2017-01-18",42753.548611111109,"TGN42","URBAN","Unknown","Unknown",1,52,1.7691166664398567E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-18",42753.5625,"LLG13","RURAL SHORT","Planned","-",1,50,0,0,"NO"]
[null,"2017-01-18",42753.572916666664,"LLG12","RURAL SHORT","Planned","-",1,62,0,0,"NO"]
[null,"2017-01-18",42753.576388888891,"MOE31","RURAL LONG","Asset Failure","LV",1,89,7.4053118551554282E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-18",42753.606249999997,"WYK23","RURAL SHORT","Unknown","Unknown",1,1,3.3955569137783212E-6,3.3955569137783212E-6,"NO"]
[null,"2017-01-18",42753.609722222223,"OFR23","RURAL LONG","Asset failure","LV",1,313,2.6043400119816281E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-18",42753.649305555555,"LLG12","RURAL SHORT","Planned","-",1,52,0,0,"NO"]
[null,"2017-01-18",42753.676307870373,"RWN24","URBAN","Asset failure","HV",1584,0,0,0,"NO"]
[null,"2017-01-18",42753.677210648151,"RWN24","URBAN","Asset failure","HV",391,1,1.3302396472653539E-3,1.3302396472653539E-3,"NO"]
[null,"2017-01-18",42753.678865740738,"RWN24","URBAN","Asset failure","HV",634,434.12618296529968,0.93639345154661624,2.156961474082441E-3,"NO"]
[null,"2017-01-18",42753.714583333334,"BDL2","RURAL SHORT","Other","Cause Not In List",11,221,8.2545988573950978E-3,3.7351126051561531E-5,"NO"]
[null,"2017-01-18",42753.743055555555,"SLE31","RURAL LONG","Third Party","Vehicle impact",140,16.928571428571427,1.9719763030020637E-2,1.1648805165413033E-3,"NO"]
[null,"2017-01-18",42753.744814814818,"SMR5","RURAL LONG","Unknown","Unknown",526,0,0,0,"NO"]
[null,"2017-01-18",42753.838171296295,"TGN31","RURAL LONG","Unknown","Unknown",884,0,0,0,"NO"]
[null,"2017-01-18",42753.894988425927,"CLN22","RURAL SHORT","Asset failure","HV",148,194,9.7493230108403148E-2,5.0254242323919155E-4,"NO"]
[null,"2017-01-18",42753.919444444444,"MBY12","RURAL SHORT","Asset Failure","Distribution substation",12,49,1.9965874653016529E-3,4.0746682965339853E-5,"NO"]
[null,"2017-01-18",42753.939583333333,"CYN22","URBAN","Animal","Animal impact",19,50,3.2320400636881999E-3,6.4640801273764005E-5,"NO"]
[null,"2017-01-18",42753.975925925923,"ELM33","RURAL SHORT","Unknown","Unknown",697,0,0,0,"NO"]
[null,"2017-01-19",42754.015277777777,"LDL21","RURAL SHORT","Asset failure","LV",1,96,3.2597346372271883E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-19",42754.070833333331,"MFA31","RURAL SHORT","Animal","Animal impact",84,68,1.9395421091501771E-2,2.8522678075737897E-4,"NO"]
[null,"2017-01-19",42754.185370370367,"ELM15","RURAL SHORT","Unknown","Unknown",1704,0,0,0,"NO"]
[null,"2017-01-19",42754.275000000001,"MOE31","RURAL LONG","Animal","Animal impact",4,192,6.3902016907408637E-3,3.3282300472608665E-5,"NO"]
[null,"2017-01-19",42754.303472222222,"MOE31","RURAL LONG","Unknown","Unknown",2,163,2.7125074885176064E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-19",42754.304594907408,"BN3","RURAL SHORT","Animal","Animal impact",143,100,4.8556463867029991E-2,4.8556463867029993E-4,"NO"]
[null,"2017-01-19",42754.352696759262,"SFS1","RURAL SHORT","Planned","-",140,552.4,0,0,"NO"]
[null,"2017-01-19",42754.354166666664,"WGL24","RURAL LONG","Planned","-",145,519.89655172413791,0,0,"NO"]
[null,"2017-01-19",42754.354166666664,"WOTS11","RURAL LONG","Vegetation","Grow-in - NSP responsibility",1,49,4.0770818078945617E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-19",42754.354166666664,"BDL44","RURAL LONG","Planned","-",11,464,0,0,"NO"]
[null,"2017-01-19",42754.354166666664,"MSD4","RURAL LONG","Planned","-",360,182,0,0,"NO"]
[null,"2017-01-19",42754.354166666664,"KLO14","RURAL LONG","Planned","-",51,251,0,0,"NO"]
[null,"2017-01-19",42754.354861111111,"WYK24","RURAL SHORT","Planned","-",124,439,0,0,"NO"]
[null,"2017-01-19",42754.354861111111,"CLN13","RURAL SHORT","Planned","-",1,244,0,0,"NO"]
[null,"2017-01-19",42754.358032407406,"RUBA22","RURAL SHORT","Planned","-",122,347,0,0,"NO"]
[null,"2017-01-19",42754.364583333336,"CRE22","URBAN","Other","Other",1,420,1.4289019228937306E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-19",42754.364583333336,"LDL24","URBAN","Planned","-",10,295,0,0,"NO"]
[null,"2017-01-19",42754.364583333336,"CRE22","URBAN","Planned","-",80,420,0,0,"NO"]
[null,"2017-01-19",42754.365972222222,"WGL24","RURAL LONG","Planned","-",183,382,0,0,"NO"]
[null,"2017-01-19",42754.368055555555,"MWT14","RURAL SHORT","Planned","-",1,275,0,0,"NO"]
[null,"2017-01-19",42754.368055555555,"OFR23","RURAL LONG","Planned","-",31,221,0,0,"NO"]
[null,"2017-01-19",42754.371655092589,"KLK1","RURAL SHORT","Planned","-",94,385,0,0,"NO"]
[null,"2017-01-19",42754.378472222219,"TGN31","RURAL LONG","Planned","-",7,253.57142857142858,0,0,"NO"]
[null,"2017-01-19",42754.379166666666,"BGE24","RURAL SHORT","Planned","-",14,599.85714285714289,0,0,"NO"]
[null,"2017-01-19",42754.380555555559,"LYD14","RURAL SHORT","Planned","-",420,281,0,0,"NO"]
[null,"2017-01-19",42754.381261574075,"BDL41","RURAL LONG","Unknown","Unknown",12,0,0,0,"NO"]
[null,"2017-01-19",42754.395833333336,"ELM33","RURAL SHORT","Planned","-",51,160,0,0,"NO"]
[null,"2017-01-19",42754.381944444445,"ELM34","RURAL SHORT","Planned","-",136,210,0,0,"NO"]
[null,"2017-01-19",42754.395833333336,"ELM33","RURAL SHORT","Other","Other",1,160,5.4328910620453136E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-19",42754.399305555555,"TGN41","RURAL LONG","Planned","-",1,48,0,0,"NO"]
[null,"2017-01-19",42754.40625,"WN5","RURAL LONG","Planned","-",3,2,0,0,"NO"]
[null,"2017-01-19",42754.453472222223,"FTR22","RURAL SHORT","Planned","-",9,473,0,0,"NO"]
[null,"2017-01-19",42754.495833333334,"BN4","URBAN","Asset failure","LV",1,121,4.1165983969081285E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-19",42754.503472222219,"MWT14","RURAL SHORT","Planned","-",2,40,0,0,"NO"]
[null,"2017-01-19",42754.52134259259,"OFR23","RURAL LONG","Unknown","Unknown",49,0,0,0,"NO"]
[null,"2017-01-19",42754.575694444444,"BDL43","URBAN","Asset failure","LV",7,116,2.7625437175945455E-3,2.3815032048228842E-5,"NO"]
[null,"2017-01-19",42754.57916666667,"EPG13","RURAL SHORT","Asset failure","LV",1,106,3.5992903286050201E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-19",42754.595833333333,"BDL41","RURAL LONG","Animal","Animal impact",1,147,1.2231245423683684E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-19",42754.62300925926,"MFA21","RURAL LONG","Unknown","Unknown",1022,0,0,0,"NO"]
[null,"2017-01-19",42754.634027777778,"MOE24","RURAL SHORT","Unknown","Unknown",2,7,4.7537796792896496E-5,6.7911138275566425E-6,"NO"]
[null,"2017-01-19",42754.634826388887,"BRT22","RURAL SHORT","Unknown","Unknown",770,0,0,0,"NO"]
[null,"2017-01-19",42754.648645833331,"BRT22","RURAL SHORT","Third Party","Vehicle impact",15,146,7.4362696411745229E-3,5.0933353706674818E-5,"NO"]
[null,"2017-01-19",42754.731944444444,"RWN24","URBAN","Third Party","Vehicle impact",1,146,4.9671352557734442E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-19",42754.779861111114,"FTR21","RURAL LONG","Asset failure","HV",1345,77.049070631970267,0.86226952006922719,1.1191173533914665E-2,"NO"]
[null,"2017-01-19",42754.802083333336,"WGL12","RURAL LONG","Asset Failure","LV",4,1135,3.7775411036410834E-2,3.3282300472608665E-5,"NO"]
[null,"2017-01-19",42754.833726851852,"FTR21","RURAL LONG","Unknown","Unknown",866,0,0,0,"NO"]
[null,"2017-01-19",42754.849305555559,"PHM33","RURAL LONG","Asset failure","LV",1,246,2.0468614790654328E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-19",42754.902777777781,"CRE31","RURAL SHORT","Unknown","Unknown",13,4,1.765689595164727E-4,4.4142239879118175E-5,"NO"]
[null,"2017-01-19",42754.96875,"RWT32","URBAN","Asset failure","HV",211,76,5.4556836275056815E-2,7.1785310888232651E-4,"NO"]
[null,"2017-01-20",42755.013229166667,"MWT14","RURAL SHORT","Unknown","Unknown",792,0,0,0,"NO"]
[null,"2017-01-20",42755.017361111109,"MWT14","RURAL SHORT","Unknown","Unknown",122,100,4.142579434809552E-2,4.1425794348095516E-4,"NO"]
[null,"2017-01-20",42755.040277777778,"LDL23","RURAL LONG","Vegetation","Grow-in - NSP responsibility",45,142,5.3168475004992347E-2,3.7442588031684747E-4,"NO"]
[null,"2017-01-20",42755.047476851854,"MDG1","RURAL SHORT","Unknown","Unknown",1486,0,0,0,"NO"]
[null,"2017-01-20",42755.0625,"RWT32","URBAN","Asset failure","LV",67,105,2.3934107208469987E-2,2.2794387817590464E-4,"NO"]
[null,"2017-01-20",42755.076388888891,"PHI11","RURAL SHORT","Asset failure","LV",1,213,7.2325362263478236E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-20",42755.077650462961,"WGL21","RURAL LONG","Unknown","Unknown",417,0,0,0,"NO"]
[null,"2017-01-20",42755.098611111112,"FGY34","URBAN","Animal","Animal impact",95,123,3.9754092783364857E-2,3.2320400636881997E-4,"NO"]
[null,"2017-01-20",42755.100347222222,"FTR21","RURAL LONG","Unknown","Unknown",1435,0,0,0,"NO"]
[null,"2017-01-20",42755.100358796299,"FTR21","RURAL LONG","Weather","-",866,0,0,0,"NO"]
[null,"2017-01-20",42755.10056712963,"FTR21","RURAL LONG","Vegetation","Grow-in - NSP responsibility",569,127,0.60126971976303001,4.7344072422285831E-3,"NO"]
[null,"2017-01-20",42755.10056712963,"FTR21","RURAL LONG","Unknown","Unknown",599,0,0,0,"NO"]
[null,"2017-01-20",42755.107974537037,"SMR3","RURAL LONG","Unknown","Unknown",62,0,0,0,"NO"]
[null,"2017-01-20",42755.113703703704,"KLO24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",1071,0,0,0,"NO"]
[null,"2017-01-20",42755.113703703704,"KLO24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",3126,54.443058221369164,0.57788643559901864,1.0614510912471032E-2,"NO"]
[null,"2017-01-20",42755.279826388891,"WYK13","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",2273,0,0,0,"NO"]
[null,"2017-01-20",42755.129166666666,"WYK13","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",3497,62.442951100943667,0.74146399436337551,1.1874262527482788E-2,"NO"]
[null,"2017-01-20",42755.129560185182,"BN1","RURAL LONG","Unknown","Unknown",3426,0,0,0,"NO"]
[null,"2017-01-20",42755.134027777778,"CYN12","URBAN","Animal","Animal impact",235,190,0.1519058829933454,7.9950464733339688E-4,"NO"]
[null,"2017-01-20",42755.152256944442,"WN6","RURAL LONG","Unknown","Unknown",51,0,0,0,"NO"]
[null,"2017-01-20",42755.167210648149,"FTR23","RURAL LONG","Unknown","Unknown",1803,0,0,0,"NO"]
[null,"2017-01-20",42755.181956018518,"WOTS11","RURAL LONG","Unknown","Unknown",1251,0,0,0,"NO"]
[null,"2017-01-20",42755.216921296298,"NLA34","RURAL SHORT","Unknown","Unknown",148,0,0,0,"NO"]
[null,"2017-01-20",42755.229861111111,"TGN31","RURAL LONG","Overload","-",1,159,1.3229714437861945E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-20",42755.252222222225,"PHI12","RURAL SHORT","Unknown","Unknown",2330,0,0,0,"NO"]
[null,"2017-01-20",42755.265810185185,"BGE24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",794,51.81738035264484,0.13970339810358146,2.6960721895399869E-3,"NO"]
[null,"2017-01-20",42755.267858796295,"WYK24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",69,0,0,0,"NO"]
[null,"2017-01-20",42755.267858796295,"WYK24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",23,460,3.5924992147774636E-2,7.8097809016901385E-5,"NO"]
[null,"2017-01-20",42755.277870370373,"KLK1","RURAL SHORT","Unknown","Unknown",345,0,0,0,"NO"]
[null,"2017-01-20",42755.281087962961,"LDL23","RURAL LONG","Weather","-",385,415.13246753246756,1.3298442388337881,3.2034214204885842E-3,"NO"]
[null,"2017-01-20",42755.281099537038,"LDL23","RURAL LONG","Unknown","Unknown",281,0,0,0,"NO"]
[null,"2017-01-20",42755.286678240744,"FGY34","URBAN","Vegetation","Grow-in - NSP responsibility",928,0,0,0,"NO"]
[null,"2017-01-20",42755.286678240744,"FGY34","URBAN","Vegetation","Grow-in - NSP responsibility",2689,42.225734473782076,0.38629683055944913,9.1483744539553359E-3,"NO"]
[null,"2017-01-20",42755.286678240744,"SFS1","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",1073,5,1.8217162842420694E-2,3.6434325684841385E-3,"NO"]
[null,"2017-01-20",42755.287604166668,"SLE32","RURAL SHORT","Unknown","Unknown",354,0,0,0,"NO"]
[null,"2017-01-20",42755.295138888891,"RWN31","RURAL SHORT","Animal","Animal impact",19,273,1.761275371176815E-2,6.4515581361788098E-5,"NO"]
[null,"2017-01-20",42755.297222222223,"LLG14","RURAL SHORT","Asset failure","LV",1,222,7.5381363485878727E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-20",42755.301921296297,"BGE24","RURAL SHORT","Asset failure","HV",306,70,7.273282909313164E-2,1.0390404156161662E-3,"NO"]
[null,"2017-01-20",42755.303530092591,"FTR12","RURAL LONG","Unknown","Unknown",324,0,0,0,"NO"]
[null,"2017-01-20",42755.308379629627,"KLK1","RURAL SHORT","Unknown","Unknown",95,0,0,0,"NO"]
[null,"2017-01-20",42755.311030092591,"WYK13","RURAL SHORT","Weather","-",240,22,1.7928540504749534E-2,8.1493365930679709E-4,"NO"]
[null,"2017-01-20",42755.312442129631,"FTR23","RURAL LONG","Planned","-",75,115,0,0,"NO"]
[null,"2017-01-20",42755.3125,"WGL21","RURAL LONG","Animal","Animal impact",1,100,8.3205751181521671E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-20",42755.334027777775,"RUBA12","RURAL LONG","Animal","Animal impact",1,153,1.2730479930772815E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-20",42755.357638888891,"ELM33","RURAL SHORT","Planned","-",26,342,0,0,"NO"]
[null,"2017-01-20",42755.340277777781,"RWN34","RURAL SHORT","Planned","-",143,451.03496503496501,0,0,"NO"]
[null,"2017-01-20",42755.349305555559,"WN5","RURAL LONG","Weather","-",3,607,1.5151767290155096E-2,2.4961725354456499E-5,"NO"]
[null,"2017-01-20",42755.351388888892,"MWT31","RURAL SHORT","Overload","-",2,99,6.7232026892810755E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-20",42755.356249999997,"FTR12","RURAL LONG","Planned","-",2,58,0,0,"NO"]
[null,"2017-01-20",42755.361111111109,"BN6","RURAL LONG","Animal","Animal impact",1,541,4.5014311389203225E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-20",42755.364583333336,"SLE31","RURAL LONG","Planned","-",2,128,0,0,"NO"]
[null,"2017-01-20",42755.364583333336,"FTR12","RURAL LONG","Planned","-",1,30,0,0,"NO"]
[null,"2017-01-20",42755.367314814815,"LGA14","RURAL LONG","Planned","-",67,383.35820895522386,0,0,"NO"]
[null,"2017-01-20",42755.367361111108,"NLA34","RURAL SHORT","Overload","-",4,56,7.6060474868634394E-4,1.3582227655113285E-5,"NO"]
[null,"2017-01-20",42755.369722222225,"MOE21","RURAL SHORT","Planned","-",4,125,0,0,"NO"]
[null,"2017-01-20",42755.371527777781,"CRE33","RURAL SHORT","Planned","-",58,335,0,0,"NO"]
[null,"2017-01-20",42755.378472222219,"BDL44","RURAL LONG","Planned","-",5,103,0,0,"NO"]
[null,"2017-01-20",42755.38108796296,"WGL24","RURAL LONG","Unknown","Unknown",665,0,0,0,"NO"]
[null,"2017-01-20",42755.381701388891,"ELM32","URBAN","Weather","-",1331,30.884297520661157,0.13985207462950613,4.5282582365989412E-3,"NO"]
[null,"2017-01-20",42755.384722222225,"BGE24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",33,19,2.1290141849390075E-3,1.120533781546846E-4,"NO"]
[null,"2017-01-20",42755.469837962963,"LGA24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",260,0,0,0,"NO"]
[null,"2017-01-20",42755.392604166664,"LGA24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",476,139.92436974789916,0.2261576726852913,1.6162850909584808E-3,"NO"]
[null,"2017-01-20",42755.397222222222,"WN6","RURAL LONG","Weather","-",1,436,3.6277707515143445E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-20",42755.399305555555,"SLE32","RURAL SHORT","Animal","Animal impact",4,55,7.470225210312306E-4,1.3582227655113285E-5,"NO"]
[null,"2017-01-20",42755.401388888888,"WYK13","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",9,182,5.5619222247688897E-3,3.0560012224004888E-5,"NO"]
[null,"2017-01-20",42755.411805555559,"LGA11","RURAL LONG","Overload","-",1,72,5.9908140850695602E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-20",42755.416666666664,"RUBA12","RURAL LONG","Planned","-",5,85,0,0,"NO"]
[null,"2017-01-20",42755.419444444444,"MFA22","RURAL LONG","Animal","Animal impact",1,156,1.2980097184317381E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-20",42755.42083333333,"WGL21","RURAL LONG","Weather","-",2,0,0,0,"NO"]
[null,"2017-01-20",42755.423611111109,"LLG12","RURAL SHORT","Planned","-",2,25,0,0,"NO"]
[null,"2017-01-20",42755.427083333336,"MOE14","RURAL SHORT","Overload","-",8,135,3.6672014668805868E-3,2.716445531022657E-5,"NO"]
[null,"2017-01-20",42755.430555555555,"WN6","RURAL LONG","Planned","-",2,55,0,0,"NO"]
[null,"2017-01-20",42755.431250000001,"BGE24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",79,2,5.3649799237697469E-4,2.6824899618848734E-4,"NO"]
[null,"2017-01-20",42755.437025462961,"LDL13","RURAL SHORT","Weather","-",506,395,0.67866996035687299,1.7181517983718305E-3,"NO"]
[null,"2017-01-20",42755.437025462961,"WYK12","RURAL SHORT","Weather","-",48,395,6.4379759085236965E-2,1.6298673186135941E-4,"NO"]
[null,"2017-01-20",42755.444444444445,"FTR12","RURAL LONG","Planned","-",1,20,0,0,"NO"]
[null,"2017-01-20",42755.446527777778,"MWT11","RURAL SHORT","Planned","-",41,119.1219512195122,0,0,"NO"]
[null,"2017-01-20",42755.460416666669,"OFR23","RURAL LONG","Vegetation","Grow-in - NSP responsibility",15,315,3.9314717433268989E-2,1.248086267722825E-4,"NO"]
[null,"2017-01-20",42755.465173611112,"KLK1","RURAL SHORT","Unknown","Unknown",95,0,0,0,"NO"]
[null,"2017-01-20",42755.465277777781,"BDL44","RURAL LONG","Planned","-",1,105,0,0,"NO"]
[null,"2017-01-20",42755.465277777781,"LLG12","RURAL SHORT","Planned","-",3,40,0,0,"NO"]
[null,"2017-01-20",42755.479155092595,"OFR23","RURAL LONG","Unknown","Unknown",191,0,0,0,"NO"]
[null,"2017-01-20",42755.484143518515,"TGN31","RURAL LONG","Unknown","Unknown",884,0,0,0,"NO"]
[null,"2017-01-20",42755.491053240738,"OFR23","RURAL LONG","Unknown","Unknown",87,716.75862068965512,0.51885442321773279,7.2389003527923855E-4,"NO"]
[null,"2017-01-20",42755.491666666669,"FTR12","RURAL LONG","Planned","-",1,76,0,0,"NO"]
[null,"2017-01-20",42755.496527777781,"RUBA12","RURAL LONG","Planned","-",1,105,0,0,"NO"]
[null,"2017-01-20",42755.502083333333,"SMG21","URBAN","Asset Failure","LV",1,290,9.8662275628376623E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-20",42755.513888888891,"RUBA12","RURAL LONG","Planned","-",2,135,0,0,"NO"]
[null,"2017-01-20",42755.526388888888,"SFS1","RURAL SHORT","Planned","-",30,22,0,0,"NO"]
[null,"2017-01-20",42755.528020833335,"WGI33","RURAL SHORT","Asset Failure","LV",3,278,2.8318944660911199E-3,1.0186670741334963E-5,"NO"]
[null,"2017-01-20",42755.541666666664,"LDL14","RURAL SHORT","Planned","-",2,45,0,0,"NO"]
[null,"2017-01-20",42755.549305555556,"RWN32","URBAN","Overload","-",1,631,2.1467550317760572E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-20",42755.559027777781,"BDL41","RURAL LONG","Other","Pollution",191,162,0.25745523530586434,1.5892298475670638E-3,"NO"]
[null,"2017-01-20",42755.565972222219,"BGE11","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",42,393,5.6047062418824969E-2,1.4261339037868948E-4,"NO"]
[null,"2017-01-20",42755.604166666664,"MWT31","RURAL SHORT","Overload","-",2,140,9.5075593585792985E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-20",42755.606249999997,"BDL6","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",27,91,8.3428833371533354E-3,9.1680036672014671E-5,"NO"]
[null,"2017-01-20",42755.609131944446,"NLA34","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",148,273,0.1371940815442993,5.0254242323919155E-4,"NO"]
[null,"2017-01-20",42755.614583333336,"FTR21","RURAL LONG","Asset failure","LV",1,210,1.747320774811955E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-20",42755.615972222222,"WO31","URBAN","Asset failure","LV",45,26,3.9805124994896782E-3,1.5309663459575683E-4,"NO"]
[null,"2017-01-20",42755.619155092594,"KLK1","RURAL SHORT","Unknown","Unknown",95,0,0,0,"NO"]
[null,"2017-01-20",42755.66982638889,"BDL8","RURAL LONG","Unknown","Unknown",184,0,0,0,"NO"]
[null,"2017-01-20",42755.686111111114,"WN5","RURAL LONG","Asset failure","HV",62,101,5.2103441389868867E-2,5.1587565732543438E-4,"NO"]
[null,"2017-01-20",42755.686631944445,"BDL8","RURAL LONG","Unknown","Unknown",184,0,0,0,"NO"]
[null,"2017-01-20",42755.6875,"FGY22","URBAN","Asset Failure","LV",1,442,1.5037491664738783E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-20",42755.69027777778,"KLK1","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",9,216,6.6009626403850559E-3,3.0560012224004888E-5,"NO"]
[null,"2017-01-20",42755.711157407408,"WYK12","RURAL SHORT","Unknown","Unknown",48,0,0,0,"NO"]
[null,"2017-01-20",42755.717361111114,"KLK1","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",3,232,2.3633076119897113E-3,1.0186670741334963E-5,"NO"]
[null,"2017-01-20",42755.723611111112,"BGE24","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",9,398,1.2162884865153946E-2,3.0560012224004888E-5,"NO"]
[null,"2017-01-20",42755.724826388891,"BDL8","RURAL LONG","Unknown","Unknown",184,0,0,0,"NO"]
[null,"2017-01-20",42755.755277777775,"BDL44","RURAL LONG","Unknown","Unknown",155,0,0,0,"NO"]
[null,"2017-01-20",42755.759722222225,"BDL8","RURAL LONG","Unknown","Unknown",184,0,0,0,"NO"]
[null,"2017-01-20",42755.76394675926,"BDL8","RURAL LONG","Unknown","Unknown",184,0,0,0,"NO"]
[null,"2017-01-20",42755.768275462964,"BDL8","RURAL LONG","Unknown","Unknown",184,0,0,0,"NO"]
[null,"2017-01-20",42755.7812962963,"BN1","RURAL LONG","Unknown","Unknown",243,0,0,0,"NO"]
[null,"2017-01-20",42755.781307870369,"BN1","RURAL LONG","Unknown","Unknown",2652,0,0,0,"NO"]
[null,"2017-01-20",42755.781400462962,"BN1","RURAL LONG","Vegetation","Blow-in/Fall-in - NSP responsibility",606,258,1.300905278572855,5.0422685216002126E-3,"NO"]
[null,"2017-01-20",42755.797002314815,"BDL8","RURAL LONG","Asset failure","HV",368,0,0,0,"NO"]
[null,"2017-01-20",42755.815682870372,"BDL8","RURAL LONG","Asset failure","HV",184,146,0.2235239299740398,1.5309858217399986E-3,"NO"]
[null,"2017-01-20",42755.8125,"WN4","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1,254,8.6247145609969357E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-20",42755.843055555553,"SFS1","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",687,7.1761280931586606,1.6740095584927124E-2,2.3327475997657067E-3,"NO"]
[null,"2017-01-20",42755.844074074077,"WOTS24","RURAL LONG","Unknown","Unknown",141,0,0,0,"NO"]
[null,"2017-01-20",42755.852777777778,"WOTS24","RURAL LONG","Animal","Animal impact",4,107,3.5612061505691274E-3,3.3282300472608665E-5,"NO"]
[null,"2017-01-20",42755.854166666664,"WN2","RURAL LONG","Weather","-",66,53,2.9105371763296278E-2,5.4915795779804301E-4,"NO"]
[null,"2017-01-20",42755.856249999997,"SMG21","URBAN","Asset failure","LV",1,207,7.042445191404815E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-20",42755.915277777778,"ELM12","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1,120,4.0746682965339854E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-20",42755.960763888892,"BN1","RURAL LONG","Unknown","Unknown",70,14,8.1541636157891235E-3,5.8244025827065165E-4,"NO"]
[null,"2017-01-20",42755.968148148146,"FGY22","URBAN","Vegetation","Grow-in - NSP responsibility",1,3,1.020644230638379E-5,3.402147435461263E-6,"NO"]
[null,"2017-01-20",42755.976388888892,"BGE24","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1,784,2.6621166204022035E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-20",42755.984027777777,"LDL13","RURAL SHORT","Animal","Animal impact",1,143,4.8556463867029993E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-20",42755.985532407409,"ELM33","RURAL SHORT","Unknown","Unknown",2222,0,0,0,"NO"]
[null,"2017-01-21",42756.041666666664,"FTR23","RURAL LONG","Third Party","Vehicle impact",55,176.36363636363637,8.0709578646076016E-2,4.5763163149836918E-4,"NO"]
[null,"2017-01-21",42756.131469907406,"MYT7","RURAL LONG","Unknown","Unknown",522,0,0,0,"NO"]
[null,"2017-01-21",42756.160798611112,"DRN23","RURAL LONG","Unknown","Unknown",53,0,0,0,"NO"]
[null,"2017-01-21",42756.171527777777,"WGI31","RURAL SHORT","Animal","Animal impact",13,112,4.9439308664612353E-3,4.4142239879118175E-5,"NO"]
[null,"2017-01-21",42756.220833333333,"KLO14","RURAL LONG","Asset failure","LV",1,141,1.1732010916594554E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-21",42756.291898148149,"MOE31","RURAL LONG","Unknown","Unknown",267,0,0,0,"NO"]
[null,"2017-01-21",42756.305555555555,"FTR23","RURAL LONG","Network business","Switching and protection error",1,270,2.2465552819010848E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-21",42756.316666666666,"BWA23","RURAL SHORT","Animal","Animal impact",2,174,1.1816538059948557E-3,6.7911138275566425E-6,"NO"]
[null,"2017-01-21",42756.34097222222,"FTR21","RURAL LONG","Asset failure","LV",1,114,9.4854556346934699E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-21",42756.345833333333,"RWN33","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",1,222,7.5381363485878727E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-21",42756.380347222221,"LDL21","RURAL SHORT","Unknown","Unknown",738,0,0,0,"NO"]
[null,"2017-01-21",42756.380462962959,"MDG1","RURAL SHORT","Animal","Animal impact",749,7,1.7802904898939736E-2,2.5432721284199627E-3,"NO"]
[null,"2017-01-21",42756.414583333331,"TGN31","RURAL LONG","Third Party","Vehicle impact",6,146,7.2888238035012983E-3,4.9923450708912997E-5,"NO"]
[null,"2017-01-21",42756.454861111109,"LDL14","RURAL SHORT","Other","High/Low volt or Tap change",19,10,6.4515581361788098E-4,6.4515581361788098E-5,"NO"]
[null,"2017-01-21",42756.461805555555,"WGI24","URBAN","Animal","Animal impact",26,120,1.0614699998639142E-2,8.8455833321992837E-5,"NO"]
[null,"2017-01-21",42756.490972222222,"LDL24","URBAN","Asset failure","LV",1,55,1.8711810895036948E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-21",42756.534722222219,"FTR12","RURAL LONG","Animal","Animal impact",2,5,8.3205751181521662E-5,1.6641150236304332E-5,"NO"]
[null,"2017-01-21",42756.542094907411,"RWN26","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",1,179,6.0780468756631951E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-21",42756.642361111109,"BGE11","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",4,20,2.7164455310226568E-4,1.3582227655113285E-5,"NO"]
[null,"2017-01-21",42756.750694444447,"BGE11","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",4,0,0,0,"NO"]
[null,"2017-01-21",42756.768055555556,"FTR23","RURAL LONG","Weather","-",1,149,1.2397656926046729E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-21",42756.78125,"NLA34","RURAL SHORT","Animal","Animal impact",3,15,1.5280006112002446E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-21",42756.820752314816,"MFA21","RURAL LONG","Unknown","Unknown",516,0,0,0,"NO"]
[null,"2017-01-21",42756.823611111111,"BWN14","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1,229,7.7758253325523551E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-21",42756.832638888889,"FTR23","RURAL LONG","Third Party","Vehicle impact",1,1,8.3205751181521662E-6,8.3205751181521662E-6,"NO"]
[null,"2017-01-21",42756.836111111108,"CRE22","URBAN","Asset Failure","LV",1,120,4.082576922553516E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-21",42756.879166666666,"SLE32","RURAL SHORT","Asset failure","LV",1,84,2.8522678075737897E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-22",42757.168009259258,"DRN22","RURAL SHORT","Unknown","Unknown",41,0,0,0,"NO"]
[null,"2017-01-22",42757.179861111108,"DRN22","RURAL SHORT","Animal","Animal impact",1,101,3.4295124829161045E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-22",42757.181967592594,"BGE24","RURAL SHORT","Unknown","Unknown",1559,0,0,0,"NO"]
[null,"2017-01-22",42757.257094907407,"LGA11","RURAL LONG","Unknown","Unknown",143,0,0,0,"NO"]
[null,"2017-01-22",42757.295138888891,"CRE32","URBAN","Other","Other",1,200,6.8042948709225268E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-22",42757.295138888891,"CRE32","URBAN","Other","Other",1,200,6.8042948709225268E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-22",42757.295138888891,"CRE32","URBAN","Planned","-",168,200,0,0,"NO"]
[null,"2017-01-22",42757.33090277778,"PHM24","RURAL SHORT","Asset failure","LV",6,389,7.9252298367586006E-3,2.0373341482669927E-5,"NO"]
[null,"2017-01-22",42757.346863425926,"TGN11","RURAL SHORT","Planned","-",933,277.59163987138265,0,0,"NO"]
[null,"2017-01-22",42757.354166666664,"FTR22","RURAL SHORT","Planned","-",168,387,0,0,"NO"]
[null,"2017-01-22",42757.368055555555,"PHM33","RURAL LONG","Overload","-",1,132,1.098315915596086E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-22",42757.390972222223,"LGA11","RURAL LONG","Animal","Animal impact",1,72,5.9908140850695602E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-22",42757.402083333334,"SMR2","RURAL SHORT","Third Party","Unauthorised access",1,119,4.0407127273962021E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-22",42757.430555555555,"MOE22","RURAL LONG","Overload","-",1,310,2.5793782866271719E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-22",42757.430555555555,"NLA34","RURAL SHORT","Asset failure","LV",2,62,4.2104905730851183E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-22",42757.439583333333,"SMR4","RURAL SHORT","Animal","Animal impact",1,0,0,0,"NO"]
[null,"2017-01-22",42757.448611111111,"BGE24","RURAL SHORT","Asset failure","LV",1,119,4.0407127273962021E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-22",42757.483946759261,"SMR8","RURAL LONG","Unknown","Unknown",700,0,0,0,"NO"]
[null,"2017-01-22",42757.486805555556,"TGN41","RURAL LONG","Overload","-",2,139,2.3131198828463023E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-22",42757.522916666669,"SLE31","RURAL LONG","Asset failure","LV",1,125,1.0400718897690209E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-22",42757.524305555555,"SMR8","RURAL LONG","Animal","Animal impact",1,58,4.8259335685282568E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-22",42757.54791666667,"LGA12","RURAL SHORT","Animal","Animal impact",1,40,1.3582227655113284E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-22",42757.581250000003,"WN4","RURAL SHORT","Overload","-",1,120,4.0746682965339854E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-22",42757.696527777778,"LLG11","RURAL SHORT","Asset Failure","LV",1,86,2.9201789458493564E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-22",42757.724340277775,"MFA22","RURAL LONG","Unknown","Unknown",276,0,0,0,"NO"]
[null,"2017-01-22",42757.742094907408,"MFA22","RURAL LONG","Animal","Animal impact",1,101,8.4037808693336884E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-22",42757.865277777775,"RUBA24","RURAL SHORT","Animal","Animal impact",36,125,1.5280006112002444E-2,1.2224004889601955E-4,"NO"]
[null,"2017-01-22",42757.935844907406,"WOTS24","RURAL LONG","Unknown","Unknown",1472,0,0,0,"NO"]
[null,"2017-01-22",42757.943749999999,"CLN22","RURAL SHORT","Animal","Animal impact",2,70,4.7537796792896492E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-22",42757.978437500002,"ELM15","RURAL SHORT","Unknown","Unknown",4384,0,0,0,"NO"]
[null,"2017-01-22",42757.978449074071,"ELM15","RURAL SHORT","Unknown","Unknown",1702,0,0,0,"NO"]
[null,"2017-01-22",42757.995833333334,"TGN23","RURAL SHORT","Animal","Animal impact",3,600,6.1120024448009782E-3,1.0186670741334963E-5,"NO"]
[null,"2017-01-23",42758.031990740739,"WGL13","RURAL SHORT","Unknown","Unknown",485,0,0,0,"NO"]
[null,"2017-01-23",42758.124490740738,"BN1","RURAL LONG","Unknown","Unknown",277,0,0,0,"NO"]
[null,"2017-01-23",42758.301388888889,"BN1","RURAL LONG","Animal","Animal impact",1,221,1.8388471011116288E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-23",42758.331250000003,"PHM22","RURAL SHORT","Animal","Animal impact",1,183,6.2138691522143274E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.335416666669,"ELM34","RURAL SHORT","Planned","-",231,547,0,0,"NO"]
[null,"2017-01-23",42758.34375,"BDL44","RURAL LONG","Planned","-",22,428,0,0,"NO"]
[null,"2017-01-23",42758.348611111112,"LGA14","RURAL LONG","Overload","-",1,143,1.1898422418957599E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-23",42758.356944444444,"RWN24","URBAN","Planned","-",195,453.89230769230767,0,0,"NO"]
[null,"2017-01-23",42758.364583333336,"BGE11","RURAL SHORT","Planned","-",264,210.625,0,0,"NO"]
[null,"2017-01-23",42758.37222222222,"LGA22","RURAL SHORT","Planned","-",144,263,0,0,"NO"]
[null,"2017-01-23",42758.381249999999,"BWN14","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",3,38,3.8709348817072859E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-23",42758.388888888891,"WGL24","RURAL LONG","Planned","-",20,70,0,0,"NO"]
[null,"2017-01-23",42758.392361111109,"WYK24","RURAL SHORT","Planned","-",5,119,0,0,"NO"]
[null,"2017-01-23",42758.393611111111,"MYT7","RURAL LONG","Animal","Animal impact",522,25,0.10858350529188578,4.3433402116754309E-3,"NO"]
[null,"2017-01-23",42758.393622685187,"MYT7","RURAL LONG","Animal","Animal impact",2542,23,0.48647074485788455,2.1150901950342808E-2,"NO"]
[null,"2017-01-23",42758.39984953704,"BN4","URBAN","Planned","-",10,224,0,0,"NO"]
[null,"2017-01-23",42758.400185185186,"WN3","RURAL LONG","Planned","-",28,378,0,0,"NO"]
[null,"2017-01-23",42758.416666666664,"BGE24","RURAL SHORT","Planned","-",21,57,0,0,"NO"]
[null,"2017-01-23",42758.416666666664,"PHI13","URBAN","Planned","-",5,266,0,0,"NO"]
[null,"2017-01-23",42758.423611111109,"BDL8","RURAL LONG","Planned","-",3,130,0,0,"NO"]
[null,"2017-01-23",42758.427083333336,"PHM24","RURAL SHORT","Third Party","Unauthorised access",1,603,2.0475208190083275E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.429351851853,"MSD4","RURAL LONG","Planned","-",19,414,0,0,"NO"]
[null,"2017-01-23",42758.429861111108,"RWN24","URBAN","Asset failure","LV",1,229,7.7909176272062926E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-23",42758.439976851849,"YN31","URBAN","Unknown","Unknown",18,3,1.8371596151490821E-4,6.123865383830274E-5,"NO"]
[null,"2017-01-23",42758.439976851849,"YN35","URBAN","Unknown","Unknown",2,3,2.041288461276758E-5,6.8042948709225261E-6,"NO"]
[null,"2017-01-23",42758.439976851849,"YN38","RURAL SHORT","Unknown","Unknown",2,3,2.0373341482669927E-5,6.7911138275566425E-6,"NO"]
[null,"2017-01-23",42758.447916666664,"WN2","RURAL LONG","Asset failure","LV",101,63,5.294381947680224E-2,8.4037808693336884E-4,"NO"]
[null,"2017-01-23",42758.458333333336,"WGL24","RURAL LONG","Planned","-",15,15,0,0,"NO"]
[null,"2017-01-23",42758.486111111109,"TGN23","RURAL SHORT","Animal","Animal impact",1,95,3.2257790680894049E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.506249999999,"LLG11","RURAL SHORT","Third Party","Vehicle impact",3,491,5.0016553339954665E-3,1.0186670741334963E-5,"NO"]
[null,"2017-01-23",42758.506944444445,"WYK24","RURAL SHORT","Other","High/Low volt or Tap change",5,11,1.8675563025780765E-4,1.6977784568891605E-5,"NO"]
[null,"2017-01-23",42758.508703703701,"OFR23","RURAL LONG","Vegetation","Blow-in/Fall-in - NSP responsibility",144,58.472222222222221,7.0059242494841245E-2,1.198162817013912E-3,"NO"]
[null,"2017-01-23",42758.509027777778,"CYN12","URBAN","Asset failure","LV",1,168,5.7156076915749218E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-23",42758.517361111109,"WYK23","RURAL SHORT","Planned","-",59,148,0,0,"NO"]
[null,"2017-01-23",42758.518750000003,"BN6","RURAL LONG","Animal","Animal impact",1,118,9.8182786394195574E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-23",42758.529803240737,"WGL11","RURAL SHORT","Other","Other",1,11,3.7351126051561531E-5,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.536111111112,"LLG13","RURAL SHORT","Overload","-",1,173,5.874313460836495E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.54791666667,"LDL23","RURAL LONG","Overload","-",1,167,1.3895360447314117E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-23",42758.548611111109,"BDL8","RURAL LONG","Planned","-",5,110,0,0,"NO"]
[null,"2017-01-23",42758.549467592595,"ELM34","RURAL SHORT","Planned","-",23,306,0,0,"NO"]
[null,"2017-01-23",42758.579861111109,"TGN23","RURAL SHORT","Unknown","Unknown",2,5,3.395556913778321E-5,6.7911138275566425E-6,"NO"]
[null,"2017-01-23",42758.580555555556,"CRE33","RURAL SHORT","Third Party","Unauthorised access",1,325,1.1035559969779544E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.586111111108,"BRT21","RURAL SHORT","Animal","Animal impact",1,101,3.4295124829161045E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.637499999997,"CRE32","URBAN","Overload","-",9,67,2.0514949035831415E-3,3.061932691915137E-5,"NO"]
[null,"2017-01-23",42758.638888888891,"CRE33","RURAL SHORT","Overload","-",1,60,2.0373341482669927E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.647222222222,"WOTS11","RURAL LONG","Animal","Animal impact",1,93,7.7381348598815145E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-23",42758.719444444447,"FTR21","RURAL LONG","Unknown","Unknown",2,60,9.9846901417826E-4,1.6641150236304332E-5,"NO"]
[null,"2017-01-23",42758.734027777777,"RWT32","URBAN","Asset failure","LV",1,76,2.5856320509505602E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-23",42758.736111111109,"RWN24","URBAN","Planned","-",258,5,0,0,"NO"]
[null,"2017-01-23",42758.737500000003,"CYN33","RURAL SHORT","Asset Failure","LV",1,71,2.410845408782608E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.769444444442,"BRA24","URBAN","Asset Failure","LV",50,89,1.5139556087802621E-2,1.7010737177306317E-4,"NO"]
[null,"2017-01-23",42758.779166666667,"ELM12","RURAL SHORT","Overload","-",35,65,7.7248919788456801E-3,1.1884449198224123E-4,"NO"]
[null,"2017-01-23",42758.798611111109,"KLO14","RURAL LONG","Overload","-",1,200,1.6641150236304334E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-23",42758.819907407407,"BWR32","URBAN","Vegetation","Grow-in - NSP responsibility",193,299,0.19632772205816312,6.5661445504402375E-4,"NO"]
[null,"2017-01-23",42758.821527777778,"WYK12","RURAL SHORT","Asset failure","LV",12,111,4.5228818091527234E-3,4.0746682965339853E-5,"NO"]
[null,"2017-01-23",42758.824999999997,"CPK12","RURAL SHORT","Overload","-",2,147,9.9829373265082643E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-23",42758.82916666667,"SMR1","RURAL SHORT","Animal","Animal impact",1,76,2.5806232544715239E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-23",42758.861805555556,"KLO14","RURAL LONG","Asset Failure","LV",1,99,8.2373693669706447E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-23",42758.87222222222,"SMG31","URBAN","Asset Failure","LV",1,961,3.2694636854782738E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-23",42758.875,"PHI13","URBAN","Asset failure","LV",1,9,3.061932691915137E-5,3.402147435461263E-6,"NO"]
[null,"2017-01-23",42758.878472222219,"ELM31","URBAN","Vegetation","Grow-in - NSP responsibility",14,220,1.047861410122069E-2,4.7630064096457684E-5,"NO"]
[null,"2017-01-23",42758.897916666669,"MYT7","RURAL LONG","Overload","-",52,142,6.1439126672435597E-2,4.3266990614391267E-4,"NO"]
[null,"2017-01-23",42758.90625,"CPK11","URBAN","Animal","Animal impact",17,55,3.1810078521562809E-3,5.7836506402841474E-5,"NO"]
[null,"2017-01-23",42758.9143287037,"FTR23","RURAL LONG","Unknown","Unknown",516,0,0,0,"NO"]
[null,"2017-01-23",42758.94027777778,"CLN23","RURAL SHORT","Overload","-",3,21,2.1392008556803422E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-23",42758.972071759257,"TGN31","RURAL LONG","Unknown","Unknown",885,0,0,0,"NO"]
[null,"2017-01-24",42759.048611111109,"RWT32","URBAN","Animal","Animal impact",107,65,2.3661935413633085E-2,3.6402977559435516E-4,"NO"]
[null,"2017-01-24",42759.064166666663,"ELM13","URBAN","Animal","Animal impact",1050,0,0,0,"NO"]
[null,"2017-01-24",42759.064166666663,"ELM13","URBAN","Animal","Animal impact",982,36.54786150712831,0.12210307145870473,3.3409087816229604E-3,"NO"]
[null,"2017-01-24",42759.10833333333,"RWT32","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",95,789,0.25500796102499895,3.2320400636881997E-4,"NO"]
[null,"2017-01-24",42759.183321759258,"FTR21","RURAL LONG","Unknown","Unknown",14,0,0,0,"NO"]
[null,"2017-01-24",42759.203472222223,"OFR23","RURAL LONG","Animal","Animal impact",125,133,0.13832956133927976,1.0400718897690209E-3,"NO"]
[null,"2017-01-24",42759.216122685182,"MOE31","RURAL LONG","Unknown","Unknown",268,0,0,0,"NO"]
[null,"2017-01-24",42759.226388888892,"MOE31","RURAL LONG","Vegetation","Grow-in - NSP responsibility",60,99,4.942421620182387E-2,4.9923450708913E-4,"NO"]
[null,"2017-01-24",42759.237835648149,"LGA24","RURAL SHORT","Unknown","Unknown",476,0,0,0,"NO"]
[null,"2017-01-24",42759.25,"MWT14","RURAL SHORT","Animal","Animal impact",3,422,4.2987750528433542E-3,1.0186670741334963E-5,"NO"]
[null,"2017-01-24",42759.265972222223,"MWT31","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",5,234,3.9728015891206357E-3,1.6977784568891605E-5,"NO"]
[null,"2017-01-24",42759.30972222222,"WGL15","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",2,64,4.3463128496362512E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-24",42759.320138888892,"TGN41","RURAL LONG","Asset failure","LV",1,261,2.1716701058377154E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-24",42759.323611111111,"BWR23","URBAN","Asset failure","LV",1,309,1.0512635575575303E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-24",42759.32916666667,"LGA14","RURAL LONG","Animal","Animal impact",2,31,5.1587565732543438E-4,1.6641150236304332E-5,"NO"]
[null,"2017-01-24",42759.332233796296,"WGL24","RURAL LONG","Unknown","Unknown",50,0,0,0,"NO"]
[null,"2017-01-24",42759.333333333336,"LYD13","URBAN","Planned","-",20,230,0,0,"NO"]
[null,"2017-01-24",42759.333333333336,"LYD14","RURAL SHORT","Planned","-",341,219,0,0,"NO"]
[null,"2017-01-24",42759.338888888888,"BDL44","RURAL LONG","Planned","-",26,420,0,0,"NO"]
[null,"2017-01-24",42759.340277777781,"LDL14","RURAL SHORT","Planned","-",128,442.703125,0,0,"NO"]
[null,"2017-01-24",42759.340277777781,"RWN24","URBAN","Planned","-",240,500,0,0,"NO"]
[null,"2017-01-24",42759.341666666667,"LYD13","URBAN","Asset failure","LV",1,198,6.7362519222133007E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-24",42759.34447916667,"DRN14","RURAL SHORT","Planned","-",49,393,0,0,"NO"]
[null,"2017-01-24",42759.354166666664,"FGY21","URBAN","Planned","-",15,535,0,0,"NO"]
[null,"2017-01-24",42759.35601851852,"MYT7","RURAL LONG","Planned","-",100,422,0,0,"NO"]
[null,"2017-01-24",42759.36041666667,"MSD1","RURAL LONG","Animal","Animal impact",1,376,3.1285362444252148E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-24",42759.366666666669,"RUBA12","RURAL LONG","Planned","-",2,42,0,0,"NO"]
[null,"2017-01-24",42759.368055555555,"BDL8","RURAL LONG","Planned","-",2,100,0,0,"NO"]
[null,"2017-01-24",42759.369444444441,"LGA14","RURAL LONG","Planned","-",72,249,0,0,"NO"]
[null,"2017-01-24",42759.375,"WGL24","RURAL LONG","Planned","-",68,410,0,0,"NO"]
[null,"2017-01-24",42759.375821759262,"BDL8","RURAL LONG","Planned","-",51,296.05882352941177,0,0,"NO"]
[null,"2017-01-24",42759.381944444445,"WYK13","RURAL SHORT","Planned","-",64,355,0,0,"NO"]
[null,"2017-01-24",42759.393750000003,"LLG13","RURAL SHORT","Planned","-",2,48,0,0,"NO"]
[null,"2017-01-24",42759.423611111109,"MWT14","RURAL SHORT","Planned","-",37,287,0,0,"NO"]
[null,"2017-01-24",42759.436111111114,"LLG14","RURAL SHORT","Planned","-",102,8,0,0,"NO"]
[null,"2017-01-24",42759.479166666664,"SMR5","RURAL LONG","Planned","-",1,7,0,0,"NO"]
[null,"2017-01-24",42759.484224537038,"MWT31","RURAL SHORT","Weather","-",4,165,2.2410675630936917E-3,1.3582227655113285E-5,"NO"]
[null,"2017-01-24",42759.506944444445,"RUBA12","RURAL LONG","Planned","-",1,125,0,0,"NO"]
[null,"2017-01-24",42759.511111111111,"BGE24","RURAL SHORT","Asset failure","LV",1,110,3.735112605156153E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-24",42759.59375,"KMS1","RURAL SHORT","Asset failure","LV",1,20,6.791113827556642E-5,3.3955569137783212E-6,"NO"]
[null,"2017-01-24",42759.611805555556,"CPK13","URBAN","Unknown","Unknown",1,72,2.4495461535321096E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-24",42759.620138888888,"WGI31","RURAL SHORT","Other","High/Low volt or Tap change",15,7,3.5653347594672373E-4,5.0933353706674818E-5,"NO"]
[null,"2017-01-24",42759.648877314816,"MYT7","RURAL LONG","Unknown","Unknown",59,0,0,0,"NO"]
[null,"2017-01-24",42759.663935185185,"WYK13","RURAL SHORT","Unknown","Unknown",2599,0,0,0,"NO"]
[null,"2017-01-24",42759.707638888889,"TGN11","RURAL SHORT","Asset failure","LV",1,96,3.2597346372271883E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-24",42759.786805555559,"MFA21","RURAL LONG","Overload","-",1,85,7.0724888504293418E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-24",42759.818749999999,"EPG14","URBAN","Network business","Switching and protection error",1,147,5.0011567301280573E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-24",42759.821203703701,"WN3","RURAL LONG","Unknown","Unknown",177,0,0,0,"NO"]
[null,"2017-01-24",42759.82708333333,"BWA23","RURAL SHORT","Animal","Animal impact",1,71,2.410845408782608E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-24",42759.840277777781,"FTR23","RURAL LONG","Overload","-",1,0,0,0,"NO"]
[null,"2017-01-24",42759.886111111111,"TGN31","RURAL LONG","Overload","-",2,54,8.9862211276043398E-4,1.6641150236304332E-5,"NO"]
[null,"2017-01-24",42759.972916666666,"WT11","URBAN","Unknown","Unknown",1,84,2.8578038457874609E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-25",42760.0862037037,"SLE14","RURAL SHORT","Unknown","Unknown",155,0,0,0,"NO"]
[null,"2017-01-25",42760.08730324074,"BWR13","URBAN","Unknown","Unknown",312,0,0,0,"NO"]
[null,"2017-01-25",42760.162129629629,"CYN33","RURAL SHORT","Unknown","Unknown",1618,0,0,0,"NO"]
[null,"2017-01-25",42760.173807870371,"CYN33","RURAL SHORT","Animal","Animal impact",41,65,9.0491591752192256E-3,1.3921783346491117E-4,"NO"]
[null,"2017-01-25",42760.202777777777,"RWT32","URBAN","Animal","Animal impact",131,56,2.4958153586543828E-2,4.4568131404542548E-4,"NO"]
[null,"2017-01-25",42760.317361111112,"LGA22","RURAL SHORT","Asset failure","LV",1,113,3.8369793125695031E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-25",42760.334027777775,"BN6","RURAL LONG","Other","Vibration",2,69,1.148239366304999E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-25",42760.334027777775,"BGE11","RURAL SHORT","Planned","-",44,273.77272727272725,0,0,"NO"]
[null,"2017-01-25",42760.335416666669,"RWN31","RURAL SHORT","Planned","-",100,327,0,0,"NO"]
[null,"2017-01-25",42760.342361111114,"WT7","URBAN","Other","Other",1,557,1.8949961215519236E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-25",42760.342361111114,"WT10","URBAN","Planned","-",44,557,0,0,"NO"]
[null,"2017-01-25",42760.345555555556,"WT8","URBAN","Planned","-",219,522,0,0,"NO"]
[null,"2017-01-25",42760.347222222219,"WYK24","RURAL SHORT","Planned","-",41,305,0,0,"NO"]
[null,"2017-01-25",42760.347916666666,"MFA22","RURAL LONG","Planned","-",13,256.46153846153845,0,0,"NO"]
[null,"2017-01-25",42760.350694444445,"BGE24","RURAL SHORT","Planned","-",355,685.08450704225356,0,0,"NO"]
[null,"2017-01-25",42760.355914351851,"BDL8","RURAL LONG","Planned","-",6,320.66666666666669,0,0,"NO"]
[null,"2017-01-25",42760.356249999997,"LLG13","RURAL SHORT","Planned","-",1,62,0,0,"NO"]
[null,"2017-01-25",42760.356249999997,"MSD4","RURAL LONG","Planned","-",361,556.58171745152356,0,0,"NO"]
[null,"2017-01-25",42760.362500000003,"LDL14","RURAL SHORT","Planned","-",12,319,0,0,"NO"]
[null,"2017-01-25",42760.364583333336,"BDL8","RURAL LONG","Planned","-",4,325,0,0,"NO"]
[null,"2017-01-25",42760.368055555555,"SLE31","RURAL LONG","Planned","-",1,170,0,0,"NO"]
[null,"2017-01-25",42760.368750000001,"BN6","RURAL LONG","Asset failure","LV",4,71,2.3630433335552151E-3,3.3282300472608665E-5,"NO"]
[null,"2017-01-25",42760.378472222219,"WYK23","RURAL SHORT","Planned","-",30,390,0,0,"NO"]
[null,"2017-01-25",42760.380509259259,"SMR2","RURAL SHORT","Asset failure","HV",2678,0,0,0,"NO"]
[null,"2017-01-25",42760.385416666664,"WGL15","RURAL SHORT","Planned","-",18,75,0,0,"NO"]
[null,"2017-01-25",42760.388888888891,"MWT11","RURAL SHORT","Other","Other",1,45,1.5280006112002446E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-25",42760.388888888891,"TGN11","RURAL SHORT","Planned","-",6,244,0,0,"NO"]
[null,"2017-01-25",42760.388888888891,"MWT11","RURAL SHORT","Planned","-",111,45,0,0,"NO"]
[null,"2017-01-25",42760.409722222219,"MSD1","RURAL LONG","Planned","-",1,190,0,0,"NO"]
[null,"2017-01-25",42760.418749999997,"LLG13","RURAL SHORT","Planned","-",2,60,0,0,"NO"]
[null,"2017-01-25",42760.435543981483,"WN3","RURAL LONG","Unknown","Unknown",77,0,0,0,"NO"]
[null,"2017-01-25",42760.458333333336,"WGL24","RURAL LONG","Planned","-",68,225,0,0,"NO"]
[null,"2017-01-25",42760.463194444441,"SLE14","RURAL SHORT","Animal","Animal impact",1,62,2.1052452865425592E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-25",42760.465277777781,"WGL13","RURAL SHORT","Animal","Animal impact",1,80,2.7164455310226568E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-25",42760.465277777781,"KLK1","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",4,39,5.2970687854941812E-4,1.3582227655113285E-5,"NO"]
[null,"2017-01-25",42760.46875,"TGN41","RURAL LONG","Planned","-",3,25,0,0,"NO"]
[null,"2017-01-25",42760.472222222219,"WN3","RURAL LONG","Planned","-",1,50,0,0,"NO"]
[null,"2017-01-25",42760.479166666664,"LLG13","RURAL SHORT","Planned","-",11,96,0,0,"NO"]
[null,"2017-01-25",42760.496527777781,"BN1","RURAL LONG","Planned","-",3,5,0,0,"NO"]
[null,"2017-01-25",42760.5,"RWN24","URBAN","Network business","Switching and protection error",257,70,6.1204632363948124E-2,8.7435189091354464E-4,"NO"]
[null,"2017-01-25",42760.509375000001,"FGY22","URBAN","Network business","Switching and protection error",1,172,5.851693588993373E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-25",42760.509502314817,"BGE11","RURAL SHORT","Unknown","Unknown",439,0,0,0,"NO"]
[null,"2017-01-25",42760.515277777777,"PHM21","URBAN","Unknown","Unknown",1,60,2.041288461276758E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-25",42760.516585648147,"BGE11","RURAL SHORT","Animal","Animal impact",252,180,0.15402246160898464,8.556803422721369E-4,"NO"]
[null,"2017-01-25",42760.538958333331,"FTR12","RURAL LONG","Unknown","Unknown",324,0,0,0,"NO"]
[null,"2017-01-25",42760.558333333334,"BN1","RURAL LONG","Planned","-",1,36,0,0,"NO"]
[null,"2017-01-25",42760.559027777781,"OFR23","RURAL LONG","Third Party","Vehicle impact",1,459,3.8191439792318446E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-25",42760.575694444444,"BN1","RURAL LONG","Planned","-",2,13,0,0,"NO"]
[null,"2017-01-25",42760.58185185185,"CPK12","RURAL SHORT","Unknown","Unknown",25,152,1.290311627235762E-2,8.4888922844458028E-5,"NO"]
[null,"2017-01-25",42760.604166666664,"CYN24","URBAN","Planned","-",33,20,0,0,"NO"]
[null,"2017-01-25",42760.65902777778,"TT9","URBAN","Overload","-",110,206,7.709266088755222E-2,3.7423621790073897E-4,"NO"]
[null,"2017-01-25",42760.669444444444,"FTR12","RURAL LONG","Animal","Animal impact",3,173,4.3183784863209743E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-25",42760.684027777781,"TGN41","RURAL LONG","Animal","Animal impact",2,67,1.1149570658323903E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-25",42760.703472222223,"MWT11","RURAL SHORT","Asset Failure","LV",1,146,4.9575130941163488E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-25",42760.756944444445,"BWR13","URBAN","Asset failure","HV",10,10,3.4021474354612634E-4,3.4021474354612629E-5,"NO"]
[null,"2017-01-25",42760.762523148151,"WN2","RURAL LONG","Third Party","Vehicle impact",17,100,1.4144977700858683E-2,1.4144977700858685E-4,"NO"]
[null,"2017-01-25",42760.803807870368,"LGA11","RURAL LONG","Unknown","Unknown",26,0,0,0,"NO"]
[null,"2017-01-25",42760.844444444447,"CLN22","RURAL SHORT","Animal","Animal impact",2,64,4.3463128496362512E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-25",42760.866620370369,"SMR5","RURAL LONG","Animal","Animal impact",80,25,1.6641150236304334E-2,6.656460094521733E-4,"NO"]
[null,"2017-01-25",42760.876388888886,"MFA22","RURAL LONG","Animal","Animal impact",34,63,1.7822671903081941E-2,2.8289955401717369E-4,"NO"]
[null,"2017-01-25",42760.897222222222,"LDL23","RURAL LONG","Overload","-",1,73,6.0740198362510816E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-25",42760.913888888892,"RWN31","RURAL SHORT","Other","High/Low volt or Tap change",5,9,1.5280006112002446E-4,1.6977784568891605E-5,"NO"]
[null,"2017-01-25",42760.920925925922,"ELM32","URBAN","Unknown","Unknown",3317,0,0,0,"NO"]
[null,"2017-01-25",42760.925000000003,"FGY22","URBAN","Overload","-",26,116,1.026087666535117E-2,8.8455833321992837E-5,"NO"]
[null,"2017-01-25",42760.932847222219,"WYK13","RURAL SHORT","Unknown","Unknown",559,0,0,0,"NO"]
[null,"2017-01-25",42760.979166666664,"WN5","RURAL LONG","Asset failure","LV",5,55,2.2881581574918457E-3,4.1602875590760831E-5,"NO"]
[null,"2017-01-26",42761.001828703702,"PHI12","RURAL SHORT","Unknown","Unknown",3463,0,0,0,"NO"]
[null,"2017-01-26",42761.009652777779,"WYK13","RURAL SHORT","Unknown","Unknown",614,0,0,0,"NO"]
[null,"2017-01-26",42761.011805555558,"PHI12","RURAL SHORT","Third Party","Unauthorised access",342,121,0.14051493620597449,1.1612804645121859E-3,"NO"]
[null,"2017-01-26",42761.020138888889,"WYK13","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",19,71,4.5806062766869556E-3,6.4515581361788098E-5,"NO"]
[null,"2017-01-26",42761.065937500003,"RUBA24","RURAL SHORT","Unknown","Unknown",529,0,0,0,"NO"]
[null,"2017-01-26",42761.178865740738,"BGE11","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",545,0,0,0,"NO"]
[null,"2017-01-26",42761.099259259259,"BGE11","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",3095,53.912439418416803,0.56657923107613684,1.0509248648143904E-2,"NO"]
[null,"2017-01-26",42761.104432870372,"RUBA24","RURAL SHORT","Unknown","Unknown",331,0,0,0,"NO"]
[null,"2017-01-26",42761.26458333333,"PHM31","RURAL SHORT","Animal","Animal impact",1,157,5.3310243546319646E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-26",42761.264780092592,"SMR5","RURAL LONG","Unknown","Unknown",1268,0,0,0,"NO"]
[null,"2017-01-26",42761.276388888888,"RUBA24","RURAL SHORT","Animal","Animal impact",67,135,3.0712812285124912E-2,2.2750231322314751E-4,"NO"]
[null,"2017-01-26",42761.311805555553,"WOTS24","RURAL LONG","Animal","Animal impact",2,160,2.6625840378086932E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-26",42761.338888888888,"SLE14","RURAL SHORT","Asset failure","LV",1,126,4.2784017113606845E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-26",42761.402777777781,"WN2","RURAL LONG","Asset failure","LV",65,190,0.10275910270917926,5.4083738267989088E-4,"NO"]
[null,"2017-01-26",42761.459965277776,"BN1","RURAL LONG","Asset failure","HV",56,510,0.23763562537442587,4.6595220661652131E-4,"NO"]
[null,"2017-01-26",42761.51458333333,"BRA24","URBAN","Asset failure","LV",1,75,2.5516105765959471E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-26",42761.520138888889,"WN3","RURAL LONG","Animal","Animal impact",3,0,0,0,"NO"]
[null,"2017-01-26",42761.532638888886,"LDL23","RURAL LONG","Asset failure","LV",1,76,6.3236370897956466E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-26",42761.697222222225,"MOE13","RURAL SHORT","Animal","Animal impact",27,59,5.4091221636488659E-3,9.1680036672014671E-5,"NO"]
[null,"2017-01-26",42761.724490740744,"BDL8","RURAL LONG","Animal","Animal impact",60,0,0,0,"NO"]
[null,"2017-01-26",42761.819699074076,"BRA32","URBAN","Unknown","Unknown",2135,0,0,0,"NO"]
[null,"2017-01-26",42761.900243055556,"LDL24","URBAN","Unknown","Unknown",1970,0,0,0,"NO"]
[null,"2017-01-26",42761.95784722222,"DRN23","RURAL LONG","Unknown","Unknown",1882,0,0,0,"NO"]
[null,"2017-01-26",42761.959270833337,"DRN23","RURAL LONG","Unknown","Unknown",1882,0,0,0,"NO"]
[null,"2017-01-26",42761.959374999999,"DRN23","RURAL LONG","Unknown","Unknown",957,0,0,0,"NO"]
[null,"2017-01-27",42762.215636574074,"FTR23","RURAL LONG","Unknown","Unknown",516,0,0,0,"NO"]
[null,"2017-01-27",42762.227916666663,"CPK13","URBAN","Unknown","Unknown",4621,0,0,0,"NO"]
[null,"2017-01-27",42762.238888888889,"BGE24","RURAL SHORT","Animal","Animal impact",96,141,4.5962258384903351E-2,3.2597346372271883E-4,"NO"]
[null,"2017-01-27",42762.291666666664,"MWT14","RURAL SHORT","Asset Failure","Distribution substation",2,168,1.1409071230295159E-3,6.7911138275566425E-6,"NO"]
[null,"2017-01-27",42762.361111111109,"SMR3","RURAL LONG","Planned","-",1,138,0,0,"NO"]
[null,"2017-01-27",42762.371527777781,"BWR34","URBAN","Planned","-",2,185,0,0,"NO"]
[null,"2017-01-27",42762.381944444445,"SMR5","RURAL LONG","Planned","-",1,125,0,0,"NO"]
[null,"2017-01-27",42762.39166666667,"EPG34","URBAN","Third Party","Vehicle impact",1,66,2.2454173074044337E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-27",42762.427905092591,"WYK13","RURAL SHORT","Other","Other",1,410,1.3921783346491116E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-27",42762.445138888892,"BWA23","RURAL SHORT","Animal","Animal impact",1,45,1.5280006112002446E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-27",42762.447222222225,"WT12","URBAN","Asset failure","LV",1,83,2.8237823714328484E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-27",42762.460416666669,"WGL11","RURAL SHORT","Animal","Animal impact",17,37,2.1358052987665637E-3,5.7724467534231461E-5,"NO"]
[null,"2017-01-27",42762.484722222223,"SMR5","RURAL LONG","Planned","-",1,89,0,0,"NO"]
[null,"2017-01-27",42762.486319444448,"BWN11","URBAN","Unknown","Unknown",2894,0,0,0,"NO"]
[null,"2017-01-27",42762.489583333336,"SMR3","RURAL LONG","Planned","-",4,77,0,0,"NO"]
[null,"2017-01-27",42762.513078703705,"MOE14","RURAL SHORT","Unknown","Unknown",449,0,0,0,"NO"]
[null,"2017-01-27",42762.518750000003,"WN5","RURAL LONG","Unknown","Unknown",1,4,3.3282300472608665E-5,8.3205751181521662E-6,"NO"]
[null,"2017-01-27",42762.563888888886,"BN1","RURAL LONG","Planned","-",2,13,0,0,"NO"]
[null,"2017-01-27",42762.620324074072,"BDL8","RURAL LONG","Unknown","Unknown",60,0,0,0,"NO"]
[null,"2017-01-27",42762.65828703704,"SMR8","RURAL LONG","Unknown","Unknown",32,0,0,0,"NO"]
[null,"2017-01-27",42762.685173611113,"FTR21","RURAL LONG","Other","Cause Not In List",1,1223,1.01760633695001E-2,8.3205751181521662E-6,"NO"]
[null,"2017-01-27",42762.73541666667,"BN1","RURAL LONG","Animal","Animal impact",1,131,1.0899953404779339E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-27",42762.745833333334,"WO14","URBAN","Unknown","Unknown",1,86,2.9258467944966865E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-27",42762.823611111111,"BDL4","RURAL SHORT","Asset failure","LV",1,104,3.531379190329454E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-27",42762.859027777777,"BWR22","URBAN","Asset failure","HV",8,123,3.3477130764938828E-3,2.7217179483690104E-5,"NO"]
[null,"2017-01-27",42762.995138888888,"HPK12","URBAN","Overload","-",1,82,2.7897608970782359E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-28",42763.027418981481,"SMR8","RURAL LONG","Unknown","Unknown",285,0,0,0,"NO"]
[null,"2017-01-28",42763.043321759258,"KLK1","RURAL SHORT","Unknown","Unknown",346,0,0,0,"NO"]
[null,"2017-01-28",42763.049942129626,"BGE22","RURAL SHORT","Unknown","Unknown",1289,0,0,0,"NO"]
[null,"2017-01-28",42763.055555555555,"BGE22","RURAL SHORT","Animal","Animal impact",383,91,0.11834534511591582,1.300498297977097E-3,"NO"]
[null,"2017-01-28",42763.056967592594,"WYK12","RURAL SHORT","Unknown","Unknown",505,0,0,0,"NO"]
[null,"2017-01-28",42763.057060185187,"WYK12","RURAL SHORT","Unknown","Unknown",71,0,0,0,"NO"]
[null,"2017-01-28",42763.092731481483,"BN6","RURAL LONG","Unknown","Unknown",717,0,0,0,"NO"]
[null,"2017-01-28",42763.186724537038,"MOE21","RURAL SHORT","Unknown","Unknown",364,0,0,0,"NO"]
[null,"2017-01-28",42763.22152777778,"WYK12","RURAL SHORT","Animal","Animal impact",3,45,4.5840018336007336E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-28",42763.230983796297,"WGI14","RURAL SHORT","Unknown","Unknown",3357,0,0,0,"NO"]
[null,"2017-01-28",42763.236840277779,"LGA24","RURAL SHORT","Unknown","Unknown",477,0,0,0,"NO"]
[null,"2017-01-28",42763.245138888888,"MOE21","RURAL SHORT","Animal","Animal impact",2,72,4.8896019558407821E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-28",42763.247349537036,"LGA13","RURAL LONG","Animal","Animal impact",584,0,0,0,"NO"]
[null,"2017-01-28",42763.247349537036,"LGA13","RURAL LONG","Animal","Animal impact",321,186.99065420560748,0.49943420089196566,2.6709046129268455E-3,"NO"]
[null,"2017-01-28",42763.29791666667,"TGN31","RURAL LONG","Unknown","Unknown",5,69,2.8705984157624976E-3,4.1602875590760831E-5,"NO"]
[null,"2017-01-28",42763.304861111108,"BN6","RURAL LONG","Animal","Animal impact",2,116,1.9303734274113027E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-28",42763.31527777778,"BN6","RURAL LONG","Animal","Animal impact",34,58,1.6408174132996074E-2,2.8289955401717369E-4,"NO"]
[null,"2017-01-28",42763.320138888892,"WGI23","RURAL SHORT","Animal","Animal impact",8,135,3.6672014668805868E-3,2.716445531022657E-5,"NO"]
[null,"2017-01-28",42763.320162037038,"WGL21","RURAL LONG","Unknown","Unknown",417,0,0,0,"NO"]
[null,"2017-01-28",42763.321550925924,"WYK13","RURAL SHORT","Animal","Animal impact",239,147,0.11929610105177375,8.1153810239301875E-4,"NO"]
[null,"2017-01-28",42763.329861111109,"SMR5","RURAL LONG","Animal","Animal impact",8,90,5.9908140850695596E-3,6.656460094521733E-5,"NO"]
[null,"2017-01-28",42763.338888888888,"WGL21","RURAL LONG","Animal","Animal impact",2,62,1.0317513146508688E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-28",42763.344108796293,"WYK13","RURAL SHORT","Unknown","Unknown",1,0,0,0,"NO"]
[null,"2017-01-28",42763.352013888885,"FTR12","RURAL LONG","Unknown","Unknown",324,0,0,0,"NO"]
[null,"2017-01-28",42763.356249999997,"LDL14","RURAL SHORT","Asset failure","LV",1,259,8.7944924066858513E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-28",42763.357638888891,"FTR12","RURAL LONG","Animal","Animal impact",2,61,1.0151101644145643E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-28",42763.367106481484,"WOTS24","RURAL LONG","Unknown","Unknown",1476,0,0,0,"NO"]
[null,"2017-01-28",42763.418749999997,"CPK12","RURAL SHORT","Animal","Animal impact",3,254,2.5874143682990806E-3,1.0186670741334963E-5,"NO"]
[null,"2017-01-28",42763.443055555559,"RWT22","URBAN","Overload","-",1,77,2.6196535253051727E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-28",42763.496527777781,"WGL12","RURAL LONG","Overload","-",1,165,1.3728948944951075E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-28",42763.563888888886,"BRA14","URBAN","Asset failure","LV",1,58,1.9732455125675327E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-28",42763.651388888888,"BDL44","RURAL LONG","Asset failure","LV",1,82,6.8228715968847767E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-28",42763.667361111111,"SLE31","RURAL LONG","Animal","Animal impact",4,94,3.1285362444252148E-3,3.3282300472608665E-5,"NO"]
[null,"2017-01-28",42763.679166666669,"SMR8","RURAL LONG","Asset failure","LV",79,42,2.7607668242028888E-2,6.5732543433402117E-4,"NO"]
[null,"2017-01-28",42763.745833333334,"FTR12","RURAL LONG","Animal","Animal impact",3,106,2.6459428875723889E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-28",42763.818009259259,"WGL21","RURAL LONG","Unknown","Unknown",417,0,0,0,"NO"]
[null,"2017-01-28",42763.898460648146,"BDL44","RURAL LONG","Unknown","Unknown",1167,0,0,0,"NO"]
[null,"2017-01-28",42763.934120370373,"WOTS24","RURAL LONG","Unknown","Unknown",89,0,0,0,"NO"]
[null,"2017-01-29",42764.023125,"ELM15","RURAL SHORT","Unknown","Unknown",1703,0,0,0,"NO"]
[null,"2017-01-29",42764.098622685182,"MDG1","RURAL SHORT","Unknown","Unknown",3084,0,0,0,"NO"]
[null,"2017-01-29",42764.127453703702,"DRN23","RURAL LONG","Unknown","Unknown",58,0,0,0,"NO"]
[null,"2017-01-29",42764.177835648145,"SLE11","URBAN","Unknown","Unknown",1707,0,0,0,"NO"]
[null,"2017-01-29",42764.196504629632,"RWN31","RURAL SHORT","Unknown","Unknown",2337,0,0,0,"NO"]
[null,"2017-01-29",42764.380231481482,"LLG13","RURAL SHORT","Unknown","Unknown",1294,0,0,0,"NO"]
[null,"2017-01-29",42764.297222222223,"LLG13","RURAL SHORT","Unknown","Unknown",5,119,2.0203563636981012E-3,1.6977784568891605E-5,"NO"]
[null,"2017-01-29",42764.333657407406,"BWR32","URBAN","Planned","-",2,240,0,0,"NO"]
[null,"2017-01-29",42764.335416666669,"MOE14","RURAL SHORT","Animal","Animal impact",1,63,2.1392008556803422E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-29",42764.339861111112,"WGL13","RURAL SHORT","Unknown","Unknown",485,0,0,0,"NO"]
[null,"2017-01-29",42764.361111111109,"WGL13","RURAL SHORT","Animal","Animal impact",2,65,4.4142239879118173E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-29",42764.361111111109,"EPG23","URBAN","Planned","-",94,86,0,0,"NO"]
[null,"2017-01-29",42764.375208333331,"WYK13","RURAL SHORT","Unknown","Unknown",1,0,0,0,"NO"]
[null,"2017-01-29",42764.390972222223,"LDL23","RURAL LONG","Overload","-",2,54,8.9862211276043398E-4,1.6641150236304332E-5,"NO"]
[null,"2017-01-29",42764.393055555556,"UWY1","RURAL SHORT","Asset failure","LV",1,224,7.6060474868634394E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-29",42764.399305555555,"KMS21","RURAL SHORT","Animal","Animal impact",6,120,2.4448009779203914E-3,2.0373341482669927E-5,"NO"]
[null,"2017-01-29",42764.432511574072,"MSD1","RURAL LONG","Unknown","Unknown",191,0,0,0,"NO"]
[null,"2017-01-29",42764.439583333333,"MSD1","RURAL LONG","Animal","Animal impact",1,71,5.9076083338880378E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-29",42764.447222222225,"ELM15","RURAL SHORT","Asset failure","LV",1,56,1.9015118717158599E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-29",42764.490277777775,"WGI34","RURAL SHORT","Asset failure","LV",1,74,2.5127121161959578E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-29",42764.497916666667,"DRN23","RURAL LONG","Animal","Animal impact",2,68,1.1315982160686948E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-29",42764.511805555558,"MFA22","RURAL LONG","Animal","Animal impact",3,56,1.3978566198495641E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-29",42764.586805555555,"FTR23","RURAL LONG","Overload","-",1,55,4.5763163149836918E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-29",42764.621527777781,"FGY12","URBAN","Third Party","Dig-in",26,110,9.7301416654192122E-3,8.8455833321992837E-5,"NO"]
[null,"2017-01-29",42764.696527777778,"MFA34","RURAL SHORT","Overload","-",1,137,4.6519129718762997E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-29",42764.772916666669,"KLK1","RURAL SHORT","Animal","Animal impact",1,103,3.4974236211916706E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-29",42764.78496527778,"WN5","RURAL LONG","Unknown","Unknown",1175,0,0,0,"NO"]
[null,"2017-01-29",42764.785081018519,"WN5","RURAL LONG","Unknown","Unknown",43,142.7906976744186,5.1088331225454302E-2,3.5778473008054316E-4,"NO"]
[null,"2017-01-29",42764.821527777778,"CLN21","RURAL SHORT","Animal","Animal impact",2,40,2.7164455310226568E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-29",42764.855555555558,"SMG32","URBAN","Planned","-",21,588,0,0,"NO"]
[null,"2017-01-29",42764.932372685187,"FGY21","URBAN","Unknown","Unknown",2491,0,0,0,"NO"]
[null,"2017-01-29",42764.984965277778,"MJG11","RURAL SHORT","Unknown","Unknown",1225,0,0,0,"NO"]
[null,"2017-01-29",42764.984965277778,"MSD1","RURAL LONG","Unknown","Unknown",2075,0,0,0,"NO"]
[null,"2017-01-29",42764.984965277778,"MSD2","RURAL LONG","Unknown","Unknown",1622,0,0,0,"NO"]
[null,"2017-01-29",42764.984965277778,"MSD4","RURAL LONG","Unknown","Unknown",2535,0,0,0,"NO"]
[null,"2017-01-30",42765.011805555558,"MFA21","RURAL LONG","Animal","Animal impact",2,53,8.8198096252412972E-4,1.6641150236304332E-5,"NO"]
[null,"2017-01-30",42765.020833333336,"WYK24","RURAL SHORT","Animal","Animal impact",276,124,0.11620953981714927,9.3717370820281662E-4,"NO"]
[null,"2017-01-30",42765.023356481484,"ELM34","RURAL SHORT","Unknown","Unknown",3204,0,0,0,"NO"]
[null,"2017-01-30",42765.161944444444,"RWT32","URBAN","Unknown","Unknown",3796,0,0,0,"NO"]
[null,"2017-01-30",42765.202962962961,"BGE24","RURAL SHORT","Unknown","Unknown",795,0,0,0,"NO"]
[null,"2017-01-30",42765.238912037035,"PHM22","RURAL SHORT","Unknown","Unknown",743,0,0,0,"NO"]
[null,"2017-01-30",42765.247812499998,"BDL8","RURAL LONG","Unknown","Unknown",2049,0,0,0,"NO"]
[null,"2017-01-30",42765.253472222219,"MSD2","RURAL LONG","Animal","Animal impact",144,46,5.5115489582639954E-2,1.198162817013912E-3,"NO"]
[null,"2017-01-30",42765.302083333336,"MOE14","RURAL SHORT","Animal","Animal impact",12,139,5.6637889321822397E-3,4.0746682965339853E-5,"NO"]
[null,"2017-01-30",42765.302777777775,"MOE14","RURAL SHORT","Animal","Animal impact",1,138,4.6858685410140831E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-30",42765.304861111108,"KLO24","RURAL SHORT","Unknown","Unknown",3,251,2.5568543560750756E-3,1.0186670741334963E-5,"NO"]
[null,"2017-01-30",42765.354861111111,"MSD2","RURAL LONG","Unknown","Unknown",6,119,5.9408906343606472E-3,4.9923450708912997E-5,"NO"]
[null,"2017-01-30",42765.363194444442,"CYN22","URBAN","Asset failure","LV",1,332,1.1295129485731394E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-30",42765.371527777781,"TT4","URBAN","Planned","-",146,300,0,0,"NO"]
[null,"2017-01-30",42765.375,"FTR21","RURAL LONG","Planned","-",23,200,0,0,"NO"]
[null,"2017-01-30",42765.375,"BN3","RURAL SHORT","Planned","-",1,30,0,0,"NO"]
[null,"2017-01-30",42765.377569444441,"WYK13","RURAL SHORT","7 - STPIS Exclusion (3.3)(a)","-",3488,52.092603211009177,0.61696929567660719,1.1843702515258785E-2,"NO"]
[null,"2017-01-30",42765.381944444445,"SMR5","RURAL LONG","Planned","-",3,80,0,0,"NO"]
[null,"2017-01-30",42765.384027777778,"LDL14","RURAL SHORT","Overload","-",4,197,2.6756988480573169E-3,1.3582227655113285E-5,"NO"]
[null,"2017-01-30",42765.388888888891,"CRE33","RURAL SHORT","Planned","-",65,310,0,0,"NO"]
[null,"2017-01-30",42765.388958333337,"SMR5","RURAL LONG","Planned","-",1,41,0,0,"NO"]
[null,"2017-01-30",42765.417916666665,"OFR23","RURAL LONG","Other","High/Low volt or Tap change",1,388,3.2283831458430408E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-30",42765.423611111109,"LDL23","RURAL LONG","Overload","-",3,60,1.4977035212673899E-3,2.4961725354456499E-5,"NO"]
[null,"2017-01-30",42765.444444444445,"CRE33","RURAL SHORT","Planned","-",36,260,0,0,"NO"]
[null,"2017-01-30",42765.458333333336,"MOE21","RURAL SHORT","Asset failure","LV",1,23,7.8097809016901385E-5,3.3955569137783212E-6,"NO"]
[null,"2017-01-30",42765.463194444441,"HPK22","URBAN","Third Party","Vehicle impact",2,0,0,0,"NO"]
[null,"2017-01-30",42765.46875,"SMR5","RURAL LONG","Planned","-",1,45,0,0,"NO"]
[null,"2017-01-30",42765.469421296293,"CLN21","RURAL SHORT","Unknown","Unknown",3790,0,0,0,"NO"]
[null,"2017-01-30",42765.469421296293,"CLN23","RURAL SHORT","Unknown","Unknown",5423,0,0,0,"NO"]
[null,"2017-01-30",42765.472222222219,"SMR5","RURAL LONG","Planned","-",1,65,0,0,"NO"]
[null,"2017-01-30",42765.499305555553,"CLN13","RURAL SHORT","Third Party","Unauthorised access",1,65,2.2071119939559087E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-30",42765.509513888886,"WGL24","RURAL LONG","Unknown","Unknown",246,0,0,0,"NO"]
[null,"2017-01-30",42765.509525462963,"WGL24","RURAL LONG","Unknown","Unknown",2664,0,0,0,"NO"]
[null,"2017-01-30",42765.512499999997,"WGL24","RURAL LONG","Animal","Animal impact",20,47,7.8213406110630365E-3,1.6641150236304332E-4,"NO"]
[null,"2017-01-30",42765.555555555555,"BDL41","RURAL LONG","Planned","-",6,60,0,0,"NO"]
[null,"2017-01-30",42765.569444444445,"KMS1","RURAL SHORT","Asset failure","LV",2,135,9.1680036672014671E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-30",42765.626562500001,"WGL21","RURAL LONG","Unknown","Unknown",416,0,0,0,"NO"]
[null,"2017-01-30",42765.633402777778,"SMR3","RURAL LONG","Unknown","Unknown",1436,0,0,0,"NO"]
[null,"2017-01-30",42765.633668981478,"SMR3","RURAL LONG","7 - STPIS Exclusion (3.3)(a)","-",898,66.684855233853,0.49826099980030619,7.4718764561006457E-3,"NO"]
[null,"2017-01-30",42765.667361111111,"FGY22","URBAN","Unknown","Unknown",1,490,1.667052243376019E-3,3.402147435461263E-6,"NO"]
[null,"2017-01-30",42765.691180555557,"WO22","RURAL SHORT","Unknown","Unknown",4089,0,0,0,"NO"]
[null,"2017-01-30",42765.695833333331,"WN5","RURAL LONG","Animal","Animal impact",1,180,1.4977035212673899E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-30",42765.714583333334,"MOE14","RURAL SHORT","Asset failure","LV",1,52,1.765689595164727E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-30",42765.871527777781,"RWN31","RURAL SHORT","Animal","Animal impact",555,0,0,0,"NO"]
[null,"2017-01-30",42765.789097222223,"RWN31","RURAL SHORT","Animal","Animal impact",89,119,3.5962343273826199E-2,3.0220456532627059E-4,"NO"]
[null,"2017-01-30",42765.843402777777,"BWR13","URBAN","Unknown","Unknown",312,0,0,0,"NO"]
[null,"2017-01-30",42765.852083333331,"BWR13","URBAN","Animal","Animal impact",6,81.333333333333329,1.6602479485050964E-3,2.041288461276758E-5,"NO"]
[null,"2017-01-30",42765.885682870372,"CPK13","URBAN","Unknown","Unknown",4618,0,0,0,"NO"]
[null,"2017-01-30",42765.897222222222,"BGE11","RURAL SHORT","Animal","Animal impact",17,80,4.6179574027385168E-3,5.7724467534231461E-5,"NO"]
[null,"2017-01-30",42765.964201388888,"ELM12","RURAL SHORT","Unknown","Unknown",869,0,0,0,"NO"]
[null,"2017-01-30",42765.996747685182,"RWN24","URBAN","Animal","Animal impact",2303,0,0,0,"NO"]
[null,"2017-01-30",42765.997662037036,"RWN24","URBAN","Animal","Animal impact",1087,36.867525298988042,0.13634105847611011,3.6981342623463929E-3,"NO"]
[null,"2017-01-31",42766.057870370372,"RWN24","URBAN","Other","High/Low volt or Tap change",608,0,0,0,"NO"]
[null,"2017-01-31",42766.013333333336,"RWN24","URBAN","Other","High/Low volt or Tap change",1085,127.07649769585254,0.46908128410652805,3.6913299674754705E-3,"NO"]
[null,"2017-01-31",42766.069189814814,"BGE24","RURAL SHORT","Unknown","Unknown",795,0,0,0,"NO"]
[null,"2017-01-31",42766.076979166668,"BRA23","URBAN","Animal","Animal impact",1781,40.266704098820888,0.2439850033341045,6.0592245825565093E-3,"NO"]
[null,"2017-01-31",42766.081666666665,"BN1","RURAL LONG","Unknown","Unknown",41,0,0,0,"NO"]
[null,"2017-01-31",42766.103472222225,"ELM34","RURAL SHORT","Unknown","Unknown",110,136,5.0797531430123687E-2,3.735112605156153E-4,"NO"]
[null,"2017-01-31",42766.117673611108,"FTR22","RURAL SHORT","Unknown","Unknown",363,0,0,0,"NO"]
[null,"2017-01-31",42766.194282407407,"MFA21","RURAL LONG","Unknown","Unknown",1363,0,0,0,"NO"]
[null,"2017-01-31",42766.260416666664,"ELM34","RURAL SHORT","Animal","Animal impact",7,227,5.3955399359937525E-3,2.3768898396448248E-5,"NO"]
[null,"2017-01-31",42766.310416666667,"FGY14","URBAN","Overload","-",1,176,5.9877794864118231E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-31",42766.319444444445,"TGN11","RURAL SHORT","Animal","Animal impact",1,61,2.0712897174047758E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-31",42766.322916666664,"LGA21","RURAL SHORT","Network business","Switching and protection error",1,192,6.5194692744543765E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-31",42766.334027777775,"FTR22","RURAL SHORT","Animal","Animal impact",3,45,4.5840018336007336E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-31",42766.347222222219,"LDL14","RURAL SHORT","Planned","-",163,390.08588957055213,0,0,"NO"]
[null,"2017-01-31",42766.354166666664,"FTR21","RURAL LONG","Planned","-",156,416,0,0,"NO"]
[null,"2017-01-31",42766.354166666664,"WGL12","RURAL LONG","Planned","-",220,330,0,0,"NO"]
[null,"2017-01-31",42766.355555555558,"RWN34","RURAL SHORT","Planned","-",199,471.63316582914575,0,0,"NO"]
[null,"2017-01-31",42766.355949074074,"SMR8","RURAL LONG","Planned","-",35,133,0,0,"NO"]
[null,"2017-01-31",42766.357638888891,"NLA31","RURAL LONG","Planned","-",14,455,0,0,"NO"]
[null,"2017-01-31",42766.357638888891,"MSD4","RURAL LONG","Planned","-",9,215,0,0,"NO"]
[null,"2017-01-31",42766.364583333336,"MYT8","RURAL SHORT","Planned","-",23,418,0,0,"NO"]
[null,"2017-01-31",42766.364583333336,"MYT8","RURAL SHORT","Planned","-",2,40,0,0,"NO"]
[null,"2017-01-31",42766.368055555555,"SLE31","RURAL LONG","Planned","-",1,405,0,0,"NO"]
[null,"2017-01-31",42766.368055555555,"RUBA24","RURAL SHORT","Planned","-",3,75,0,0,"NO"]
[null,"2017-01-31",42766.371527777781,"MFA34","RURAL SHORT","Planned","-",49,260,0,0,"NO"]
[null,"2017-01-31",42766.371527777781,"TGN31","RURAL LONG","Planned","-",3,230,0,0,"NO"]
[null,"2017-01-31",42766.371527777781,"SMR8","RURAL LONG","Planned","-",6,250,0,0,"NO"]
[null,"2017-01-31",42766.371770833335,"WN3","RURAL LONG","Planned","-",40,250,0,0,"NO"]
[null,"2017-01-31",42766.375,"OFR22","RURAL SHORT","Other","Other",1,298,1.0118759603059398E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-31",42766.375,"WGL11","RURAL SHORT","Planned","-",2,75,0,0,"NO"]
[null,"2017-01-31",42766.375648148147,"OFR22","RURAL SHORT","Planned","-",85,297,0,0,"NO"]
[null,"2017-01-31",42766.375694444447,"MOE24","RURAL SHORT","Planned","-",49,139,0,0,"NO"]
[null,"2017-01-31",42766.375694444447,"TGN31","RURAL LONG","Planned","-",1,1449,0,0,"NO"]
[null,"2017-01-31",42766.376608796294,"DRN22","RURAL SHORT","Planned","-",92,172.95652173913044,0,0,"NO"]
[null,"2017-01-31",42766.378472222219,"WGL24","RURAL LONG","Planned","-",35,380,0,0,"NO"]
[null,"2017-01-31",42766.378472222219,"WYK13","RURAL SHORT","Planned","-",25,325,0,0,"NO"]
[null,"2017-01-31",42766.379074074073,"MOE32","RURAL SHORT","Planned","-",29,339,0,0,"NO"]
[null,"2017-01-31",42766.379166666666,"TGN12","URBAN","Planned","-",1,259,0,0,"NO"]
[null,"2017-01-31",42766.381944444445,"WGL12","RURAL LONG","Planned","-",27,159.92592592592592,0,0,"NO"]
[null,"2017-01-31",42766.382106481484,"SMR8","RURAL LONG","Unknown","Unknown",663,0,0,0,"NO"]
[null,"2017-01-31",42766.385416666664,"LGA13","RURAL LONG","Planned","-",1,225,0,0,"NO"]
[null,"2017-01-31",42766.399687500001,"SMR3","RURAL LONG","Unknown","Unknown",482,0,0,0,"NO"]
[null,"2017-01-31",42766.402777777781,"MFA22","RURAL LONG","Unknown","Unknown",1,121,1.0067895892964121E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-31",42766.409722222219,"LGA24","RURAL SHORT","Planned","-",68,257,0,0,"NO"]
[null,"2017-01-31",42766.416666666664,"EPG32","RURAL SHORT","Planned","-",2,271,0,0,"NO"]
[null,"2017-01-31",42766.427476851852,"OFR22","RURAL SHORT","Planned","-",89,166,0,0,"NO"]
[null,"2017-01-31",42766.449305555558,"PHM33","RURAL LONG","Unknown","Unknown",33,0,0,0,"NO"]
[null,"2017-01-31",42766.453321759262,"RUBA22","RURAL SHORT","Unknown","Unknown",254,0,0,0,"NO"]
[null,"2017-01-31",42766.461805555555,"RUBA24","RURAL SHORT","Planned","-",2,70,0,0,"NO"]
[null,"2017-01-31",42766.476006944446,"MWT14","RURAL SHORT","Third Party","Vehicle impact",212,12,8.6382967886520483E-3,7.1985806572100403E-4,"NO"]
[null,"2017-01-31",42766.491666666669,"BDL44","RURAL LONG","Unknown","Unknown",1,0,0,0,"NO"]
[null,"2017-01-31",42766.506655092591,"BN1","RURAL LONG","Animal","Animal impact",1,125,1.0400718897690209E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-31",42766.538194444445,"SMR8","RURAL LONG","Animal","Animal impact",2,135,2.2465552819010848E-3,1.6641150236304332E-5,"NO"]
[null,"2017-01-31",42766.541666666664,"WGL12","RURAL LONG","Planned","-",7,64,0,0,"NO"]
[null,"2017-01-31",42766.541666666664,"BN3","RURAL SHORT","Planned","-",2,80,0,0,"NO"]
[null,"2017-01-31",42766.576655092591,"LGA13","RURAL LONG","Overload","-",1,39,3.2450242960793452E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-31",42766.578472222223,"MWT31","RURAL SHORT","Animal","Animal impact",3,69,7.0288028115211246E-4,1.0186670741334963E-5,"NO"]
[null,"2017-01-31",42766.620138888888,"BRT11","RURAL SHORT","Overload","-",1,249,8.45493671530802E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-31",42766.636111111111,"BGE12","RURAL SHORT","Animal","Animal impact",1,661,2.24446312000747E-3,3.3955569137783212E-6,"NO"]
[null,"2017-01-31",42766.651608796295,"UWY1","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",315,26.6,2.8451371380548551E-2,1.069600427840171E-3,"NO"]
[null,"2017-01-31",42766.675000000003,"MWT31","RURAL SHORT","Animal","Animal impact",1,64,2.1731564248181256E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-31",42766.675000000003,"RUBA22","RURAL SHORT","Animal","Animal impact",1,158,5.3649799237697469E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-31",42766.698611111111,"PHM33","RURAL LONG","Animal","Animal impact",1,158,1.3146508686680423E-3,8.3205751181521662E-6,"NO"]
[null,"2017-01-31",42766.740972222222,"UWY1","RURAL SHORT","Asset failure","LV",1,155,5.2631132163563979E-4,3.3955569137783212E-6,"NO"]
[null,"2017-01-31",42766.74722222222,"BDL44","RURAL LONG","Animal","Animal impact",4,110,3.6610530519869534E-3,3.3282300472608665E-5,"NO"]
[null,"2017-01-31",42766.768750000003,"MFA21","RURAL LONG","Animal","Animal impact",1,58,4.8259335685282568E-4,8.3205751181521662E-6,"NO"]
[null,"2017-01-31",42766.798611111109,"BGE12","RURAL SHORT","Asset failure","HV",2,50,3.3955569137783211E-4,6.7911138275566425E-6,"NO"]
[null,"2017-01-31",42766.8,"DRN22","RURAL SHORT","Asset failure","HV",690,38.073913043478264,8.920467568187028E-2,2.3429342705070413E-3,"NO"]
[null,"2017-01-31",42766.818055555559,"RWT15","URBAN","Asset failure","LV",1,52,1.7691166664398567E-4,3.402147435461263E-6,"NO"]
[null,"2017-01-31",42766.911863425928,"DRN23","RURAL LONG","Unknown","Unknown",1882,0,0,0,"NO"]
[null,"2017-01-31",42766.916666666664,"DRN23","RURAL LONG","Animal","Animal impact",25,128,2.6625840378086935E-2,2.0801437795380418E-4,"NO"]
[null,"2017-02-01",42767.019502314812,"WGI23","RURAL SHORT","Unknown","Unknown",1435,0,0,0,"NO"]
[null,"2017-02-01",42767.033819444441,"PHI12","RURAL SHORT","Unknown","Unknown",3463,0,0,0,"NO"]
[null,"2017-02-01",42767.03402777778,"MOE13","RURAL SHORT","Asset failure","LV",1,64,2.1731564248181256E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.049097222225,"BWA22","RURAL LONG","Unknown","Unknown",84,0,0,0,"NO"]
[null,"2017-02-01",42767.090949074074,"WYK24","RURAL SHORT","Unknown","Unknown",92,0,0,0,"NO"]
[null,"2017-02-01",42767.134305555555,"DRN23","RURAL LONG","Unknown","Unknown",47,0,0,0,"NO"]
[null,"2017-02-01",42767.142557870371,"RWT31","URBAN","Other","Other",1106,0,0,0,"NO"]
[null,"2017-02-01",42767.15625,"DRN23","RURAL LONG","Animal","Animal impact",5,154,6.4068428409771684E-3,4.1602875590760831E-5,"NO"]
[null,"2017-02-01",42767.157187500001,"FTR21","RURAL LONG","Unknown","Unknown",52,0,0,0,"NO"]
[null,"2017-02-01",42767.160636574074,"WGI14","RURAL SHORT","Unknown","Unknown",2071,0,0,0,"NO"]
[null,"2017-02-01",42767.197916666664,"WGI14","RURAL SHORT","Animal","Animal impact",31,84,8.8420302034787485E-3,1.0526226432712796E-4,"NO"]
[null,"2017-02-01",42767.252083333333,"FTR21","RURAL LONG","Animal","Animal impact",1,192,1.5975504226852159E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-01",42767.259386574071,"WGI23","RURAL SHORT","Unknown","Unknown",1641,0,0,0,"NO"]
[null,"2017-02-01",42767.273611111108,"WYK24","RURAL SHORT","Overload","-",12,196,7.9863498612066115E-3,4.0746682965339853E-5,"NO"]
[null,"2017-02-01",42767.298900462964,"MSD1","RURAL LONG","Unknown","Unknown",191,0,0,0,"NO"]
[null,"2017-02-01",42767.305555555555,"FTR12","RURAL LONG","Overload","-",1,160,1.3312920189043466E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-01",42767.313194444447,"WGI23","RURAL SHORT","Animal","Animal impact",1,71,2.410845408782608E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.313194444447,"MSD1","RURAL LONG","Animal","Animal impact",1,79,6.5732543433402117E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-01",42767.319444444445,"CRE21","RURAL SHORT","Overload","-",10,140,4.7537796792896493E-3,3.395556913778321E-5,"NO"]
[null,"2017-02-01",42767.335451388892,"BWR13","URBAN","Planned","-",217,364,0,0,"NO"]
[null,"2017-02-01",42767.338194444441,"MFA34","RURAL SHORT","Animal","Animal impact",1,73,2.4787565470581744E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.34375,"LDL23","RURAL LONG","Planned","-",576,425.86805555555554,0,0,"NO"]
[null,"2017-02-01",42767.347222222219,"NLA31","RURAL LONG","Planned","-",71,535.42253521126759,0,0,"NO"]
[null,"2017-02-01",42767.348611111112,"WYK24","RURAL SHORT","Planned","-",227,396,0,0,"NO"]
[null,"2017-02-01",42767.354826388888,"LGA14","RURAL LONG","Planned","-",29,345.86206896551727,0,0,"NO"]
[null,"2017-02-01",42767.355370370373,"WN3","RURAL LONG","Planned","-",50,440.72,0,0,"NO"]
[null,"2017-02-01",42767.356030092589,"WGL12","RURAL LONG","Planned","-",323,357,0,0,"NO"]
[null,"2017-02-01",42767.356249999997,"SMR8","RURAL LONG","Animal","Animal impact",1,42,3.4946415496239102E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-01",42767.357071759259,"WGL24","RURAL LONG","Planned","-",20,268.39999999999998,0,0,"NO"]
[null,"2017-02-01",42767.357141203705,"MSD4","RURAL LONG","Planned","-",35,435.71428571428572,0,0,"NO"]
[null,"2017-02-01",42767.361111111109,"FTR21","RURAL LONG","Planned","-",6,354,0,0,"NO"]
[null,"2017-02-01",42767.368055555555,"PHI12","RURAL SHORT","Planned","-",54,314.64814814814815,0,0,"NO"]
[null,"2017-02-01",42767.371527777781,"OFR23","RURAL LONG","Planned","-",54,553.42592592592598,0,0,"NO"]
[null,"2017-02-01",42767.372916666667,"WN3","RURAL LONG","Planned","-",20,378,0,0,"NO"]
[null,"2017-02-01",42767.375,"TT5","URBAN","Planned","-",102,335,0,0,"NO"]
[null,"2017-02-01",42767.375,"CLN14","URBAN","Planned","-",2,190,0,0,"NO"]
[null,"2017-02-01",42767.375787037039,"CRE31","RURAL SHORT","Unknown","Unknown",5970,0,0,0,"NO"]
[null,"2017-02-01",42767.378472222219,"RUBA12","RURAL LONG","Planned","-",1,45,0,0,"NO"]
[null,"2017-02-01",42767.381944444445,"LGA14","RURAL LONG","Overload","-",1,382,3.1784596951341276E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-01",42767.381944444445,"CRE22","URBAN","Third Party","Unauthorised access",1,94,3.1980185893335872E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-01",42767.381944444445,"BGE23","URBAN","Planned","-",188,320,0,0,"NO"]
[null,"2017-02-01",42767.383333333331,"WGL11","RURAL SHORT","Planned","-",51,248,0,0,"NO"]
[null,"2017-02-01",42767.385416666664,"SLE31","RURAL LONG","Planned","-",1,295,0,0,"NO"]
[null,"2017-02-01",42767.402777777781,"TGN31","RURAL LONG","Planned","-",4,270,0,0,"NO"]
[null,"2017-02-01",42767.402777777781,"KLK1","RURAL SHORT","Planned","-",10,20,0,0,"NO"]
[null,"2017-02-01",42767.40625,"DRN23","RURAL LONG","Planned","-",2,30,0,0,"NO"]
[null,"2017-02-01",42767.413194444445,"TGN11","RURAL SHORT","Planned","-",125,210,0,0,"NO"]
[null,"2017-02-01",42767.416666666664,"MOE32","RURAL SHORT","Animal","Animal impact",8,138,3.7486948328112665E-3,2.716445531022657E-5,"NO"]
[null,"2017-02-01",42767.423611111109,"SLE32","RURAL SHORT","Overload","-",1,245,8.3191144387568866E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.434027777781,"DRN23","RURAL LONG","Planned","-",2,22,0,0,"NO"]
[null,"2017-02-01",42767.440972222219,"KLK1","RURAL SHORT","Planned","-",1,10,0,0,"NO"]
[null,"2017-02-01",42767.443055555559,"LGA21","RURAL SHORT","Animal","Animal impact",1,187,6.3496914287654608E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.444444444445,"RUBA12","RURAL LONG","Planned","-",1,60,0,0,"NO"]
[null,"2017-02-01",42767.454861111109,"MWT31","RURAL SHORT","Animal","Animal impact",2,215,1.4600894729246781E-3,6.7911138275566425E-6,"NO"]
[null,"2017-02-01",42767.458333333336,"KLK1","RURAL SHORT","Planned","-",2,40,0,0,"NO"]
[null,"2017-02-01",42767.462500000001,"LDL23","RURAL LONG","Asset Failure","Distribution substation",3,4,9.9846901417825995E-5,2.4961725354456499E-5,"NO"]
[null,"2017-02-01",42767.486111111109,"BWR32","URBAN","Unknown","Unknown",1,175,5.95375801205721E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-01",42767.498981481483,"CLN22","RURAL SHORT","Unknown","Unknown",587,0,0,0,"NO"]
[null,"2017-02-01",42767.505543981482,"WN5","RURAL LONG","Unknown","Unknown",24,0,0,0,"NO"]
[null,"2017-02-01",42767.51,"CLN22","RURAL SHORT","Other","Cause Not In List",5,231,3.9218682354139611E-3,1.6977784568891605E-5,"NO"]
[null,"2017-02-01",42767.524305555555,"RUBA12","RURAL LONG","Planned","-",1,50,0,0,"NO"]
[null,"2017-02-01",42767.531793981485,"WYK23","RURAL SHORT","Animal","Animal impact",104,37.346153846153847,1.3188343053114998E-2,3.531379190329454E-4,"NO"]
[null,"2017-02-01",42767.534722222219,"WGL23","RURAL SHORT","Asset failure","LV",1,40,1.3582227655113284E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.546527777777,"BDL44","RURAL LONG","Asset failure","LV",1,158,1.3146508686680423E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-01",42767.556944444441,"WN3","RURAL LONG","Unknown","Unknown",1,105,8.7366038740597748E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-01",42767.566423611112,"LGA12","RURAL SHORT","Unknown","Unknown",980,0,0,0,"NO"]
[null,"2017-02-01",42767.568055555559,"BWN12","URBAN","Asset Failure","LV",3,72,7.3486384605963282E-4,1.020644230638379E-5,"NO"]
[null,"2017-02-01",42767.597430555557,"BGE24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",1,153,5.1952020780808312E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.599305555559,"EPG13","RURAL SHORT","Asset failure","LV",1,372,1.2631471719255355E-3,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.614583333336,"PHI12","RURAL SHORT","Asset failure","HV",1,210,7.1306695189344747E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.618055555555,"FGY34","URBAN","Overload","-",1,40,1.3608589741845051E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-01",42767.655555555553,"LDL23","RURAL LONG","Overload","-",5,86,3.5778473008054317E-3,4.1602875590760831E-5,"NO"]
[null,"2017-02-01",42767.659722222219,"CLN12","RURAL SHORT","Network business","Switching and protection error",1,335,1.1375115661157375E-3,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.661805555559,"WYK24","RURAL SHORT","Network business","Switching and protection error",26,116,1.0240999651955416E-2,8.828447975823635E-5,"NO"]
[null,"2017-02-01",42767.67083333333,"WYK24","RURAL SHORT","Network business","Switching and protection error",38,114,1.4709552550487687E-2,1.290311627235762E-4,"NO"]
[null,"2017-02-01",42767.690972222219,"TGN41","RURAL LONG","Asset failure","HV",7,90,5.2419623244358646E-3,5.8244025827065164E-5,"NO"]
[null,"2017-02-01",42767.70208333333,"MFA21","RURAL LONG","Asset failure","HV",105,52,4.5430340145110833E-2,8.7366038740597748E-4,"NO"]
[null,"2017-02-01",42767.704861111109,"MWT31","RURAL SHORT","Animal","Animal impact",2,85,5.772446753423146E-4,6.7911138275566425E-6,"NO"]
[null,"2017-02-01",42767.728472222225,"LYD14","RURAL SHORT","Asset failure","LV",1,76,2.5806232544715239E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-01",42767.797835648147,"BN1","RURAL LONG","Unknown","Unknown",617,0,0,0,"NO"]
[null,"2017-02-01",42767.843055555553,"TGN41","RURAL LONG","Animal","Animal impact",1,0,0,0,"NO"]
[null,"2017-02-01",42767.988888888889,"LLG14","RURAL SHORT","Animal","Animal impact",32,56,6.0848379894907515E-3,1.0865782124090628E-4,"NO"]
[null,"2017-02-01",42767.995138888888,"MOE21","RURAL SHORT","Animal","Animal impact",21,74,5.2766954440115112E-3,7.1306695189344741E-5,"NO"]
[null,"2017-02-02",42768.034583333334,"WN5","RURAL LONG","Unknown","Unknown",1218,0,0,0,"NO"]
[null,"2017-02-02",42768.060706018521,"CYN14","URBAN","Animal","Animal impact",2053,27.738918655625913,0.19374549215464801,6.9846086850019733E-3,"NO"]
[null,"2017-02-02",42768.060706018521,"CYN23","URBAN","Asset failure","HV",1719,13.722513089005236,8.025325585509574E-2,5.8482914415579111E-3,"NO"]
[null,"2017-02-02",42768.068506944444,"DRN23","RURAL LONG","Unknown","Unknown",58,0,0,0,"NO"]
[null,"2017-02-02",42768.248449074075,"BRT22","RURAL SHORT","Unknown","Unknown",773,0,0,0,"NO"]
[null,"2017-02-02",42768.254166666666,"TGN23","RURAL SHORT","Unknown","Unknown",19,53,3.4193258121747692E-3,6.4515581361788098E-5,"NO"]
[null,"2017-02-02",42768.262499999997,"DRN23","RURAL LONG","Animal","Animal impact",2,192,3.1951008453704318E-3,1.6641150236304332E-5,"NO"]
[null,"2017-02-02",42768.276388888888,"LLG14","RURAL SHORT","Animal","Animal impact",33,132,1.4791045916418366E-2,1.120533781546846E-4,"NO"]
[null,"2017-02-02",42768.277777777781,"WYK23","RURAL SHORT","Asset failure","LV",1,260,8.8284479758236347E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-02",42768.320300925923,"TGN31","RURAL LONG","Animal","Animal impact",50,139,5.7827997071157558E-2,4.1602875590760835E-4,"NO"]
[null,"2017-02-02",42768.330254629633,"BN1","RURAL LONG","Unknown","Unknown",43,0,0,0,"NO"]
[null,"2017-02-02",42768.34375,"BDL8","RURAL LONG","Planned","-",81,412.01234567901236,0,0,"NO"]
[null,"2017-02-02",42768.345833333333,"BRA32","URBAN","Planned","-",107,392,0,0,"NO"]
[null,"2017-02-02",42768.347222222219,"CRE33","RURAL SHORT","Planned","-",81,490,0,0,"NO"]
[null,"2017-02-02",42768.351388888892,"KLK2","RURAL SHORT","Planned","-",788,387,0,0,"NO"]
[null,"2017-02-02",42768.354166666664,"NLA31","RURAL LONG","Planned","-",20,474,0,0,"NO"]
[null,"2017-02-02",42768.355995370373,"WGL24","RURAL LONG","Planned","-",30,391.43333333333334,0,0,"NO"]
[null,"2017-02-02",42768.357638888891,"FTR21","RURAL LONG","Planned","-",157,624.86624203821657,0,0,"NO"]
[null,"2017-02-02",42768.361111111109,"MYT8","RURAL SHORT","Animal","Animal impact",4,174,2.3633076119897113E-3,1.3582227655113285E-5,"NO"]
[null,"2017-02-02",42768.364583333336,"SMR8","RURAL LONG","Planned","-",105,480,0,0,"NO"]
[null,"2017-02-02",42768.366932870369,"WGL12","RURAL LONG","Other","Other",2191,2,3.6460760167742794E-2,1.8230380083871397E-2,"NO"]
[null,"2017-02-02",42768.366932870369,"WGL12","RURAL LONG","Planned","-",92,402,0,0,"NO"]
[null,"2017-02-02",42768.368055555555,"BGE11","RURAL SHORT","Planned","-",36,390,0,0,"NO"]
[null,"2017-02-02",42768.368055555555,"RUBA12","RURAL LONG","Planned","-",134,358,0,0,"NO"]
[null,"2017-02-02",42768.388888888891,"WGL15","RURAL SHORT","Planned","-",1,120,0,0,"NO"]
[null,"2017-02-02",42768.388958333337,"MYT2","RURAL SHORT","Planned","-",6,51,0,0,"NO"]
[null,"2017-02-02",42768.392361111109,"WGL21","RURAL LONG","Planned","-",206,382,0,0,"NO"]
[null,"2017-02-02",42768.395833333336,"WN4","RURAL SHORT","Planned","-",4,290,0,0,"NO"]
[null,"2017-02-02",42768.396527777775,"LGA11","RURAL LONG","Asset failure","LV",1,90,7.4885176063369495E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-02",42768.40625,"DRN22","RURAL SHORT","Planned","-",70,323,0,0,"NO"]
[null,"2017-02-02",42768.406481481485,"TT1","URBAN","Asset failure","HV",190,72.863157894736844,4.7099329096525727E-2,6.4640801273763994E-4,"NO"]
[null,"2017-02-02",42768.406481481485,"TT2","URBAN","Asset failure","HV",329,39,4.3652953744403471E-2,1.1193065062667555E-3,"NO"]
[null,"2017-02-02",42768.416666666664,"MWT14","RURAL SHORT","Planned","-",101,345.79207920792078,0,0,"NO"]
[null,"2017-02-02",42768.420138888891,"WOTS11","RURAL LONG","Unknown","Unknown",30,0,0,0,"NO"]
[null,"2017-02-02",42768.425000000003,"LGA24","RURAL SHORT","Planned","-",1,56,0,0,"NO"]
[null,"2017-02-02",42768.428472222222,"WGL12","RURAL LONG","Planned","-",95,249,0,0,"NO"]
[null,"2017-02-02",42768.430555555555,"MFA21","RURAL LONG","Planned","-",5,150,0,0,"NO"]
[null,"2017-02-02",42768.4375,"SLE31","RURAL LONG","Planned","-",29,245,0,0,"NO"]
[null,"2017-02-02",42768.451388888891,"MFA21","RURAL LONG","Planned","-",1,90,0,0,"NO"]
[null,"2017-02-02",42768.456944444442,"BN1","RURAL LONG","Planned","-",9,307,0,0,"NO"]
[null,"2017-02-02",42768.461805555555,"WGL15","RURAL SHORT","Planned","-",4,55,0,0,"NO"]
[null,"2017-02-02",42768.462500000001,"WOTS25","RURAL SHORT","Planned","-",1,296,0,0,"NO"]
[null,"2017-02-02",42768.471053240741,"CPK12","RURAL SHORT","Unknown","Unknown",770,0,0,0,"NO"]
[null,"2017-02-02",42768.497916666667,"TGN31","RURAL LONG","Unknown","Unknown",886,0,0,0,"NO"]
[null,"2017-02-02",42768.53297453704,"TGN31","RURAL LONG","Unknown","Unknown",886,0,0,0,"NO"]
[null,"2017-02-02",42768.541666666664,"WGL15","RURAL SHORT","Planned","-",2,60,0,0,"NO"]
[null,"2017-02-02",42768.541666666664,"LGA23","RURAL LONG","Planned","-",1,24,0,0,"NO"]
[null,"2017-02-02",42768.545138888891,"WGL15","RURAL SHORT","Planned","-",1,70,0,0,"NO"]
[null,"2017-02-02",42768.550694444442,"LDL14","RURAL SHORT","Asset Failure","Distribution substation",1,212,7.1985806572100403E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-02",42768.565972222219,"MFA21","RURAL LONG","Planned","-",32,100,0,0,"NO"]
[null,"2017-02-02",42768.569444444445,"MFA21","RURAL LONG","Planned","-",2,20,0,0,"NO"]
[null,"2017-02-02",42768.570613425924,"PHI13","URBAN","Planned","-",3,60,0,0,"NO"]
[null,"2017-02-02",42768.594444444447,"MFA21","RURAL LONG","Planned","-",2,5,0,0,"NO"]
[null,"2017-02-02",42768.607638888891,"MSD2","RURAL LONG","Other","High/Low volt or Tap change",1,5,4.1602875590760831E-5,8.3205751181521662E-6,"NO"]
[null,"2017-02-02",42768.620405092595,"KLK2","RURAL SHORT","Unknown","Unknown",68,0,0,0,"NO"]
[null,"2017-02-02",42768.630474537036,"BDL8","RURAL LONG","Unknown","Unknown",60,0,0,0,"NO"]
[null,"2017-02-02",42768.642361111109,"CPK12","RURAL SHORT","Animal","Animal impact",3,150,1.5280006112002446E-3,1.0186670741334963E-5,"NO"]
[null,"2017-02-02",42768.659722222219,"WGL23","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",5,130,2.2071119939559088E-3,1.6977784568891605E-5,"NO"]
[null,"2017-02-02",42768.670775462961,"MOE32","RURAL SHORT","Unknown","Unknown",8,0,0,0,"NO"]
[null,"2017-02-02",42768.697962962964,"SMR8","RURAL LONG","Unknown","Unknown",47,0,0,0,"NO"]
[null,"2017-02-02",42768.711284722223,"ELM13","URBAN","Network business","Switching and protection error",2036,7,4.8487405250193925E-2,6.9267721785991315E-3,"NO"]
[null,"2017-02-02",42768.711284722223,"ELM33","RURAL SHORT","Network business","Switching and protection error",2502,12.134292565947241,0.10308910790230982,8.4956833982733591E-3,"NO"]
[null,"2017-02-02",42768.732638888891,"PHM31","RURAL SHORT","Overload","-",1,205,6.9608916732455579E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-02",42768.814571759256,"TGN41","RURAL LONG","Unknown","Unknown",579,0,0,0,"NO"]
[null,"2017-02-02",42768.868750000001,"BDL44","RURAL LONG","Animal","Animal impact",1,0,0,0,"NO"]
[null,"2017-02-02",42768.910601851851,"KMS21","RURAL SHORT","Unknown","Unknown",298,0,0,0,"NO"]
[null,"2017-02-02",42768.913194444445,"BDL44","RURAL LONG","Animal","Animal impact",4,0,0,0,"NO"]
[null,"2017-02-02",42768.97152777778,"BDL41","RURAL LONG","Unknown","Unknown",424,0,0,0,"NO"]
[null,"2017-02-03",42769.027696759258,"HPK24","URBAN","Unknown","Unknown",1491,0,0,0,"NO"]
[null,"2017-02-03",42769.035069444442,"RWT32","URBAN","Unknown","Unknown",3795,0,0,0,"NO"]
[null,"2017-02-03",42769.051226851851,"LGA13","RURAL LONG","Unknown","Unknown",19,0,0,0,"NO"]
[null,"2017-02-03",42769.054861111108,"PHM24","RURAL SHORT","Animal","Animal impact",2,511,3.4702591658814443E-3,6.7911138275566425E-6,"NO"]
[null,"2017-02-03",42769.133969907409,"SMR8","RURAL LONG","Unknown","Unknown",36,0,0,0,"NO"]
[null,"2017-02-03",42769.147129629629,"LGA14","RURAL LONG","Unknown","Unknown",209,0,0,0,"NO"]
[null,"2017-02-03",42769.1719212963,"MJG11","RURAL SHORT","Unknown","Unknown",1226,0,0,0,"NO"]
[null,"2017-02-03",42769.1719212963,"MSD1","RURAL LONG","Unknown","Unknown",106,0,0,0,"NO"]
[null,"2017-02-03",42769.241377314815,"CRE31","RURAL SHORT","Animal","Animal impact",691,37.261939218523878,8.7428799415964209E-2,2.3463298274208197E-3,"NO"]
[null,"2017-02-03",42769.262361111112,"MSD2","RURAL LONG","Unknown","Unknown",1007,0,0,0,"NO"]
[null,"2017-02-03",42769.274224537039,"BDL44","RURAL LONG","Unknown","Unknown",318,0,0,0,"NO"]
[null,"2017-02-03",42769.277777777781,"TGN41","RURAL LONG","Animal","Animal impact",1,174,1.4477800705584771E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-03",42769.305555555555,"SMR2","RURAL SHORT","Animal","Animal impact",25,103,8.7435590529791763E-3,8.4888922844458028E-5,"NO"]
[null,"2017-02-03",42769.335416666669,"MOE21","RURAL SHORT","Animal","Animal impact",1,109,3.7011570360183702E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-03",42769.347222222219,"BGE22","RURAL SHORT","Planned","-",383,415.78851174934726,0,0,"NO"]
[null,"2017-02-03",42769.354166666664,"WGL12","RURAL LONG","Planned","-",82,479.95121951219511,0,0,"NO"]
[null,"2017-02-03",42769.354166666664,"LLG14","RURAL SHORT","Planned","-",13,430,0,0,"NO"]
[null,"2017-02-03",42769.355555555558,"BDL8","RURAL LONG","Animal","Animal impact",3,63,1.5725886973307595E-3,2.4961725354456499E-5,"NO"]
[null,"2017-02-03",42769.364583333336,"MOE31","RURAL LONG","Planned","-",2,270,0,0,"NO"]
[null,"2017-02-03",42769.364583333336,"LYD14","RURAL SHORT","Planned","-",421,510,0,0,"NO"]
[null,"2017-02-03",42769.368055555555,"SLE31","RURAL LONG","Planned","-",5,329,0,0,"NO"]
[null,"2017-02-03",42769.372916666667,"FTR23","RURAL LONG","Planned","-",3,45,0,0,"NO"]
[null,"2017-02-03",42769.375,"BDL44","RURAL LONG","Planned","-",6,150,0,0,"NO"]
[null,"2017-02-03",42769.377083333333,"LLG13","RURAL SHORT","Planned","-",24,207,0,0,"NO"]
[null,"2017-02-03",42769.386805555558,"WGI14","RURAL SHORT","Planned","-",64,368,0,0,"NO"]
[null,"2017-02-03",42769.391261574077,"WGL15","RURAL SHORT","Planned","-",36,335.61111111111109,0,0,"NO"]
[null,"2017-02-03",42769.739583333336,"HPK12","URBAN","Third Party","Vehicle impact",86,115,3.3647238136711895E-2,2.9258467944966865E-4,"NO"]
[null,"2017-02-03",42769.395833333336,"LDL13","RURAL SHORT","Planned","-",63,278.73015873015873,0,0,"NO"]
[null,"2017-02-03",42769.397962962961,"WN3","RURAL LONG","Planned","-",35,214.4,0,0,"NO"]
[null,"2017-02-03",42769.398611111108,"BGE12","RURAL SHORT","Planned","-",8,221,0,0,"NO"]
[null,"2017-02-03",42769.402777777781,"WGL24","RURAL LONG","Planned","-",24,305,0,0,"NO"]
[null,"2017-02-03",42769.404166666667,"WN3","RURAL LONG","Planned","-",8,118,0,0,"NO"]
[null,"2017-02-03",42769.40625,"FTR12","RURAL LONG","Planned","-",1,123,0,0,"NO"]
[null,"2017-02-03",42769.420138888891,"MWT14","RURAL SHORT","Planned","-",122,389,0,0,"NO"]
[null,"2017-02-03",42769.45,"WGL24","RURAL LONG","Unknown","Unknown",1,1,8.3205751181521662E-6,8.3205751181521662E-6,"NO"]
[null,"2017-02-03",42769.454641203702,"BN1","RURAL LONG","Animal","Animal impact",1,756,6.2903547893230381E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-03",42769.459710648145,"BM8B31","RURAL SHORT","Unknown","Unknown",121,0,0,0,"NO"]
[null,"2017-02-03",42769.477962962963,"WOTS13","RURAL LONG","Unknown","Unknown",551,0,0,0,"NO"]
[null,"2017-02-03",42769.481944444444,"FTR23","RURAL LONG","Planned","-",2,47,0,0,"NO"]
[null,"2017-02-03",42769.486956018518,"BN2","RURAL LONG","Unknown","Unknown",595,0,0,0,"NO"]
[null,"2017-02-03",42769.493750000001,"RWN32","URBAN","Asset Failure","LV",1,69,2.3474817304682715E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-03",42769.5,"SMR8","RURAL LONG","Animal","Animal impact",1,30,2.49617253544565E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-03",42769.500694444447,"CNR3","RURAL SHORT","Animal","Animal impact",2,225,1.5280006112002446E-3,6.7911138275566425E-6,"NO"]
[null,"2017-02-03",42769.501388888886,"MOE22","RURAL LONG","Animal","Animal impact",1,125,1.0400718897690209E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-03",42769.506377314814,"ELM33","RURAL SHORT","Unknown","Unknown",34,0,0,0,"NO"]
[null,"2017-02-03",42769.509722222225,"ELM33","RURAL SHORT","Animal","Animal impact",12,121,4.9303486388061219E-3,4.0746682965339853E-5,"NO"]
[null,"2017-02-03",42769.53125,"LGA23","RURAL LONG","Unknown","Unknown",1,111,9.2358383811489049E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-03",42769.536805555559,"MWT24","RURAL SHORT","Animal","Animal impact",518,62,0.10905170584290456,1.7588984813371703E-3,"NO"]
[null,"2017-02-03",42769.541666666664,"MWT24","RURAL SHORT","Planned","-",14,92,0,0,"NO"]
[null,"2017-02-03",42769.568749999999,"MFA22","RURAL LONG","Animal","Animal impact",1,103,8.5701923716967321E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-03",42769.636701388888,"CYN21","URBAN","Asset failure","HV",70,0,0,0,"NO"]
[null,"2017-02-03",42769.636701388888,"CYN21","URBAN","Asset failure","HV",1,102,3.4701903841704884E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-03",42769.706469907411,"CYN21","URBAN","Unknown","Unknown",71,5.971830985915493,1.4425105126355756E-3,2.4155246791774968E-4,"NO"]
[null,"2017-02-03",42769.706944444442,"WN6","RURAL LONG","Animal","Animal impact",2,0,0,0,"NO"]
[null,"2017-02-03",42769.708333333336,"RWN26","RURAL SHORT","Other","High/Low volt or Tap change",14,9,4.2784017113606845E-4,4.7537796792896496E-5,"NO"]
[null,"2017-02-03",42769.75,"MBY11","RURAL SHORT","Animal","Animal impact",1,33,1.120533781546846E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-03",42769.752083333333,"MFA34","RURAL SHORT","Asset failure","HV",2,47,3.1918234989516215E-4,6.7911138275566425E-6,"NO"]
[null,"2017-02-03",42769.754861111112,"WT6","URBAN","Other","Cause Not In List",12,143,5.8380849992515273E-3,4.082576922553516E-5,"NO"]
[null,"2017-02-03",42769.768750000003,"HPK23","URBAN","Third Party","Vehicle impact",11,0,0,0,"NO"]
[null,"2017-02-03",42769.774305555555,"BDL2","RURAL SHORT","Asset failure","LV",48,70,1.1409071230295159E-2,1.6298673186135941E-4,"NO"]
[null,"2017-02-03",42769.915995370371,"BN1","RURAL LONG","Unknown","Unknown",277,0,0,0,"NO"]
[null,"2017-02-03",42769.995138888888,"MOE22","RURAL LONG","Animal","Animal impact",2,87,1.4477800705584771E-3,1.6641150236304332E-5,"NO"]
[null,"2017-02-04",42770.16715277778,"WGL11","RURAL SHORT","Unknown","Unknown",1301,0,0,0,"NO"]
[null,"2017-02-04",42770.246493055558,"CPK11","URBAN","Unknown","Unknown",3488,0,0,0,"NO"]
[null,"2017-02-04",42770.268657407411,"MSD2","RURAL LONG","Animal","Animal impact",56,16,7.455235305864341E-3,4.6595220661652131E-4,"NO"]
[null,"2017-02-04",42770.28125,"MOE21","RURAL SHORT","Animal","Animal impact",3,147,1.4974405989762395E-3,1.0186670741334963E-5,"NO"]
[null,"2017-02-04",42770.29583333333,"FGY33","URBAN","Planned","-",26,50,0,0,"NO"]
[null,"2017-02-04",42770.306469907409,"MJG11","RURAL SHORT","Unknown","Unknown",1332,0,0,0,"NO"]
[null,"2017-02-04",42770.30972222222,"WGL11","RURAL SHORT","Unknown","Unknown",2,82,5.568713338596447E-4,6.7911138275566425E-6,"NO"]
[null,"2017-02-04",42770.322314814817,"SMR5","RURAL LONG","Animal","Animal impact",73,17,1.0325833721626839E-2,6.0740198362510816E-4,"NO"]
[null,"2017-02-04",42770.328564814816,"TGN41","RURAL LONG","Unknown","Unknown",18,0,0,0,"NO"]
[null,"2017-02-04",42770.330555555556,"FGY33","URBAN","Planned","-",1,74,0,0,"NO"]
[null,"2017-02-04",42770.357118055559,"SMR3","RURAL LONG","Unknown","Unknown",1438,0,0,0,"NO"]
[null,"2017-02-04",42770.368750000001,"RUBA12","RURAL LONG","Overload","-",1,93,7.7381348598815145E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-04",42770.370636574073,"FGY13","RURAL SHORT","Planned","-",202,413,0,0,"NO"]
[null,"2017-02-04",42770.373402777775,"FGY33","URBAN","Planned","-",28,474,0,0,"NO"]
[null,"2017-02-04",42770.37572916667,"WGL24","RURAL LONG","Unknown","Unknown",664,0,0,0,"NO"]
[null,"2017-02-04",42770.393750000003,"PHM22","RURAL SHORT","Animal","Animal impact",1,133,4.5160906953251669E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-04",42770.436805555553,"NLA31","RURAL LONG","Asset failure","LV",1,216,1.797244225520868E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-04",42770.447916666664,"BDL44","RURAL LONG","Other","Cause Not In List",3,85,2.1217466551288026E-3,2.4961725354456499E-5,"NO"]
[null,"2017-02-04",42770.453414351854,"LGA11","RURAL LONG","Unknown","Unknown",663,0,0,0,"NO"]
[null,"2017-02-04",42770.502800925926,"PHM33","RURAL LONG","Unknown","Unknown",455,0,0,0,"NO"]
[null,"2017-02-04",42770.520138888889,"BDL4","RURAL SHORT","Unknown","Unknown",1,136,4.6179574027385169E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-04",42770.550694444442,"PHM33","RURAL LONG","Animal","Animal impact",1,77,6.4068428409771679E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-04",42770.57916666667,"CYN23","URBAN","Asset failure","LV",1,115,3.9124695507804528E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-04",42770.587500000001,"BGE24","RURAL SHORT","Asset failure","LV",1,245,8.3191144387568866E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-04",42770.59375,"MSD2","RURAL LONG","Asset Failure","LV",1,15,1.248086267722825E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-04",42770.607638888891,"MOE14","RURAL SHORT","Animal","Animal impact",2,70,4.7537796792896492E-4,6.7911138275566425E-6,"NO"]
[null,"2017-02-04",42770.644444444442,"FGY13","RURAL SHORT","Third Party","Dig-in",340,73.752941176470586,8.5146985169905182E-2,1.1544893506846292E-3,"NO"]
[null,"2017-02-04",42770.67083333333,"WOTS25","RURAL SHORT","Unknown","Unknown",1,0,0,0,"NO"]
[null,"2017-02-04",42770.725694444445,"FGY14","URBAN","Asset failure","LV",1,160,5.4434358967380206E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-04",42770.732638888891,"CPK13","URBAN","Overload","-",7,115,2.7387286855463169E-3,2.3815032048228842E-5,"NO"]
[null,"2017-02-04",42770.734722222223,"CLN13","RURAL SHORT","Unknown","Unknown",5,97,1.6468451031824856E-3,1.6977784568891605E-5,"NO"]
[null,"2017-02-04",42770.738888888889,"SLE14","RURAL SHORT","Animal","Animal impact",1,66,2.241067563093692E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-04",42770.745138888888,"LLG13","RURAL SHORT","Asset failure","HV",2,200,1.3582227655113284E-3,6.7911138275566425E-6,"NO"]
[null,"2017-02-04",42770.760405092595,"FTR12","RURAL LONG","Unknown","Unknown",417,0,0,0,"NO"]
[null,"2017-02-04",42770.788113425922,"WOTS11","RURAL LONG","Unknown","Unknown",2946,0,0,0,"NO"]
[null,"2017-02-04",42770.788240740738,"WOTS11","RURAL LONG","Vegetation","Grow-in - NSP responsibility",2946,81.306856754921924,1.9930273580509885,2.4512414298076282E-2,"NO"]
[null,"2017-02-04",42770.811874999999,"NLA32","RURAL SHORT","Unknown","Unknown",96,0,0,0,"NO"]
[null,"2017-02-04",42770.831736111111,"MOE14","RURAL SHORT","Unknown","Unknown",450,0,0,0,"NO"]
[null,"2017-02-04",42770.875,"WOTS11","RURAL LONG","Unknown","Unknown",99,0,0,0,"NO"]
[null,"2017-02-04",42770.875,"WOTS11","RURAL LONG","Unknown","Unknown",70,0,0,0,"NO"]
[null,"2017-02-04",42770.892384259256,"SLE14","RURAL SHORT","Unknown","Unknown",154,0,0,0,"NO"]
[null,"2017-02-04",42770.907638888886,"SLE14","RURAL SHORT","Animal","Animal impact",5,53,8.9982258215125504E-4,1.6977784568891605E-5,"NO"]
[null,"2017-02-05",42771.026388888888,"PHI11","RURAL SHORT","Animal","Animal impact",72,47,1.1490564596225838E-2,2.4448009779203911E-4,"NO"]
[null,"2017-02-05",42771.04010416667,"BDL44","RURAL LONG","Unknown","Unknown",1168,0,0,0,"NO"]
[null,"2017-02-05",42771.050011574072,"MOE31","RURAL LONG","Unknown","Unknown",271,0,0,0,"NO"]
[null,"2017-02-05",42771.066689814812,"WOTS11","RURAL LONG","Animal","Animal impact",545,196.5211009174312,0.89116687745456968,4.534713439392931E-3,"NO"]
[null,"2017-02-05",42771.195833333331,"EPG13","RURAL SHORT","Asset Failure","Distribution substation",9,878,2.6831690732676293E-2,3.0560012224004888E-5,"NO"]
[null,"2017-02-05",42771.20108796296,"WOTS11","RURAL LONG","Asset failure","HV",289,1,2.404646209145976E-3,2.404646209145976E-3,"NO"]
[null,"2017-02-05",42771.204305555555,"DRN23","RURAL LONG","Unknown","Unknown",2583,0,0,0,"NO"]
[null,"2017-02-05",42771.205543981479,"BN1","RURAL LONG","Unknown","Unknown",618,0,0,0,"NO"]
[null,"2017-02-05",42771.211111111108,"LDL23","RURAL LONG","Asset Failure","LV",1,78,6.4900485921586904E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-05",42771.263888888891,"TGN23","RURAL SHORT","Unknown","Unknown",1,335,1.1375115661157375E-3,3.3955569137783212E-6,"NO"]
[null,"2017-02-05",42771.269062500003,"WGL21","RURAL LONG","Unknown","Unknown",418,0,0,0,"NO"]
[null,"2017-02-05",42771.269328703704,"LGA13","RURAL LONG","Unknown","Unknown",24,0,0,0,"NO"]
[null,"2017-02-05",42771.274305555555,"WGL21","RURAL LONG","Animal","Animal impact",138,75,8.6117952472874931E-2,1.148239366304999E-3,"NO"]
[null,"2017-02-05",42771.28125,"WYK23","RURAL SHORT","Third Party","Vehicle impact",1,135,4.5840018336007336E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-05",42771.282152777778,"WOTS24","RURAL LONG","Unknown","Unknown",77,0,0,0,"NO"]
[null,"2017-02-05",42771.317199074074,"BDL41","RURAL LONG","Unknown","Unknown",114,0,0,0,"NO"]
[null,"2017-02-05",42771.335416666669,"LGA11","RURAL LONG","Animal","Animal impact",3,108,2.6958663382813022E-3,2.4961725354456499E-5,"NO"]
[null,"2017-02-05",42771.351388888892,"LGA13","RURAL LONG","Animal","Animal impact",1,139,1.1565599414231512E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-05",42771.36041666667,"OFR21","URBAN","Planned","-",581,353.55077452667814,0,0,"NO"]
[null,"2017-02-05",42771.440972222219,"OFR23","RURAL LONG","Planned","-",64,360.71875,0,0,"NO"]
[null,"2017-02-05",42771.368055555555,"MWT21","URBAN","Planned","-",324,230,0,0,"NO"]
[null,"2017-02-05",42771.375694444447,"WGL11","RURAL SHORT","Planned","-",51,394.1764705882353,0,0,"NO"]
[null,"2017-02-05",42771.378831018519,"BWA23","RURAL SHORT","Unknown","Unknown",10,0,0,0,"NO"]
[null,"2017-02-05",42771.381249999999,"BWA23","RURAL SHORT","Planned","-",286,6,0,0,"NO"]
[null,"2017-02-05",42771.385416666664,"LGA11","RURAL LONG","Overload","-",22,915,0.16749317712840311,1.8305265259934767E-4,"NO"]
[null,"2017-02-05",42771.393750000003,"SLE31","RURAL LONG","Animal","Animal impact",1,33,2.7457897889902151E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-05",42771.405555555553,"RWT22","URBAN","Overload","-",1,98,3.3341044867520378E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-05",42771.416620370372,"WO22","RURAL SHORT","Planned","-",10,79,0,0,"NO"]
[null,"2017-02-05",42771.451388888891,"CRE32","URBAN","Planned","-",6,176,0,0,"NO"]
[null,"2017-02-05",42771.461099537039,"TGN23","RURAL SHORT","Unknown","Unknown",2411,0,0,0,"NO"]
[null,"2017-02-05",42771.539583333331,"MFA22","RURAL LONG","Overload","-",1,83,6.9060773480662981E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-05",42771.556284722225,"BWA23","RURAL SHORT","Unknown","Unknown",10,0,0,0,"NO"]
[null,"2017-02-05",42771.578472222223,"CRE32","URBAN","Overload","-",20,128,8.7094974347808329E-3,6.8042948709225257E-5,"NO"]
[null,"2017-02-05",42771.625694444447,"FGY13","RURAL SHORT","Unknown","Unknown",1,91,3.089956791538272E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-05",42771.689722222225,"SMR3","RURAL LONG","Unknown","Unknown",482,0,0,0,"NO"]
[null,"2017-02-05",42771.715277777781,"PHM33","RURAL LONG","Asset failure","LV",1,80,6.656460094521733E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-05",42771.765347222223,"FTR21","RURAL LONG","Unknown","Unknown",26,0,0,0,"NO"]
[null,"2017-02-05",42771.774340277778,"WGL12","RURAL LONG","Unknown","Unknown",323,0,0,0,"NO"]
[null,"2017-02-05",42771.804236111115,"FTR21","RURAL LONG","Unknown","Unknown",26,0,0,0,"NO"]
[null,"2017-02-05",42771.808333333334,"FTR21","RURAL LONG","Vegetation","Grow-in - NSP responsibility",17,92,1.3013379484789988E-2,1.4144977700858685E-4,"NO"]
[null,"2017-02-05",42771.822916666664,"WGL13","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",32,81,8.8012835205134084E-3,1.0865782124090628E-4,"NO"]
[null,"2017-02-05",42771.850694444445,"SMR1","RURAL SHORT","Animal","Animal impact",5,95,1.6128895340447025E-3,1.6977784568891605E-5,"NO"]
[null,"2017-02-05",42771.854166666664,"FTR22","RURAL SHORT","Asset failure","HV",1,980,3.3276457755027546E-3,3.3955569137783212E-6,"NO"]
[null,"2017-02-05",42771.978078703702,"FTR22","RURAL SHORT","Other","Cause Not In List",157,0,0,0,"NO"]
[null,"2017-02-05",42771.854386574072,"FTR22","RURAL SHORT","Other","Cause Not In List",363,186.73553719008265,0.23016782540046349,1.2325871597015305E-3,"NO"]
[null,"2017-02-05",42771.855798611112,"WN6","RURAL LONG","Unknown","Unknown",292,0,0,0,"NO"]
[null,"2017-02-05",42771.859988425924,"WGL23","RURAL SHORT","Unknown","Unknown",390,0,0,0,"NO"]
[null,"2017-02-05",42771.868159722224,"WYK23","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",440,235.27272727272728,0.3515080517143318,1.4940450420624612E-3,"NO"]
[null,"2017-02-05",42771.873090277775,"LGA24","RURAL SHORT","Unknown","Unknown",477,0,0,0,"NO"]
[null,"2017-02-05",42771.883159722223,"WYK23","RURAL SHORT","Unknown","Unknown",37,0,0,0,"NO"]
[null,"2017-02-05",42771.88826388889,"WYK23","RURAL SHORT","Unknown","Unknown",79,0,0,0,"NO"]
[null,"2017-02-05",42771.88826388889,"WYK23","RURAL SHORT","Unknown","Unknown",59,0,0,0,"NO"]
[null,"2017-02-05",42771.895138888889,"BGE22","RURAL SHORT","Asset Failure","LV",1,171,5.8064023225609294E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-05",42771.895833333336,"CYN22","URBAN","Asset Failure","LV",1,118,4.0145339738442904E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-05",42771.911481481482,"SLE32","RURAL SHORT","Unknown","Unknown",358,0,0,0,"NO"]
[null,"2017-02-05",42771.949386574073,"BDL44","RURAL LONG","Unknown","Unknown",25,0,0,0,"NO"]
[null,"2017-02-05",42771.951203703706,"BDL44","RURAL LONG","Unknown","Unknown",25,0,0,0,"NO"]
[null,"2017-02-06",42772.002372685187,"BDL6","RURAL SHORT","Unknown","Unknown",1298,0,0,0,"NO"]
[null,"2017-02-06",42772.003148148149,"WOTS24","RURAL LONG","Unknown","Unknown",166,0,0,0,"NO"]
[null,"2017-02-06",42772.009305555555,"FTR23","RURAL LONG","Unknown","Unknown",516,0,0,0,"NO"]
[null,"2017-02-06",42772.086805555555,"LGA24","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",3,85,8.658670130134719E-4,1.0186670741334963E-5,"NO"]
[null,"2017-02-06",42772.121076388888,"FTR22","RURAL SHORT","Weather","-",52,86,1.5184930518416653E-2,1.765689595164727E-4,"NO"]
[null,"2017-02-06",42772.14335648148,"FTR21","RURAL LONG","Unknown","Unknown",868,0,0,0,"NO"]
[null,"2017-02-06",42772.15,"TGN31","RURAL LONG","Weather","-",28,132,3.075284563669041E-2,2.3297610330826065E-4,"NO"]
[null,"2017-02-06",42772.205925925926,"RUBA24","RURAL SHORT","Unknown","Unknown",531,0,0,0,"NO"]
[null,"2017-02-06",42772.255555555559,"FTR21","RURAL LONG","Overload","-",3,82,2.0468614790654328E-3,2.4961725354456499E-5,"NO"]
[null,"2017-02-06",42772.277071759258,"MSD4","RURAL LONG","Unknown","Unknown",594,0,0,0,"NO"]
[null,"2017-02-06",42772.284351851849,"MYT7","RURAL LONG","Unknown","Unknown",2448,0,0,0,"NO"]
[null,"2017-02-06",42772.286805555559,"TT2","URBAN","Animal","Animal impact",1,112,3.8104051277166147E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-06",42772.3125,"BGE23","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1,3.402147435461263E-6,3.402147435461263E-6,"NO"]
[null,"2017-02-06",42772.330555555556,"SLE32","RURAL SHORT","Animal","Animal impact",4,264,3.5857081009499072E-3,1.3582227655113285E-5,"NO"]
[null,"2017-02-06",42772.364583333336,"TGN12","URBAN","Overload","-",1,60,2.041288461276758E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-06",42772.375,"MOE21","RURAL SHORT","Planned","-",4,58.75,0,0,"NO"]
[null,"2017-02-06",42772.375,"LDL14","RURAL SHORT","Planned","-",33,300,0,0,"NO"]
[null,"2017-02-06",42772.376388888886,"LDL21","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",18,261,1.5952326380930554E-2,6.1120024448009776E-5,"NO"]
[null,"2017-02-06",42772.386805555558,"WGI33","RURAL SHORT","Planned","-",106,318,0,0,"NO"]
[null,"2017-02-06",42772.387499999997,"WGL23","RURAL SHORT","Planned","-",1,27,0,0,"NO"]
[null,"2017-02-06",42772.38958333333,"WOTS24","RURAL LONG","Weather","-",5,183,7.6133262331092326E-3,4.1602875590760831E-5,"NO"]
[null,"2017-02-06",42772.39166666667,"FGY33","URBAN","Planned","-",18,432,0,0,"NO"]
[null,"2017-02-06",42772.399305555555,"SMR2","RURAL SHORT","Animal","Animal impact",1,0,0,0,"NO"]
[null,"2017-02-06",42772.399305555555,"SMR8","RURAL LONG","Planned","-",1,125,0,0,"NO"]
[null,"2017-02-06",42772.400694444441,"BDL44","RURAL LONG","Weather","-",1,356,2.9621247420621713E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-06",42772.409722222219,"WGL21","RURAL LONG","Planned","-",6,175,0,0,"NO"]
[null,"2017-02-06",42772.420138888891,"WGI33","RURAL SHORT","Overload","-",1,66,2.241067563093692E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-06",42772.42083333333,"PHM22","RURAL SHORT","Asset failure","LV",1,92,3.1239123606760554E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-06",42772.427083333336,"WGL23","RURAL SHORT","Planned","-",1,40,0,0,"NO"]
[null,"2017-02-06",42772.432928240742,"MOE22","RURAL LONG","Unknown","Unknown",1048,0,0,0,"NO"]
[null,"2017-02-06",42772.436111111114,"TT6","URBAN","Asset failure","LV",1,219,7.4507028836601663E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-06",42772.448680555557,"FTR12","RURAL LONG","Unknown","Unknown",41,0,0,0,"NO"]
[null,"2017-02-06",42772.452777777777,"FGY22","URBAN","Asset failure","LV",1,223,7.5867887810786164E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-06",42772.460625,"BDL44","RURAL LONG","Unknown","Unknown",24,0,0,0,"NO"]
[null,"2017-02-06",42772.488680555558,"CF2","RURAL SHORT","Unknown","Unknown",635,0,0,0,"NO"]
[null,"2017-02-06",42772.493055555555,"CF2","RURAL SHORT","Other","Cause Not In List",2,256,1.7385251398545005E-3,6.7911138275566425E-6,"NO"]
[null,"2017-02-06",42772.522222222222,"CYN33","RURAL SHORT","Unknown","Unknown",1,91,3.089956791538272E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-06",42772.523611111108,"BGE12","RURAL SHORT","Asset failure","LV",1,207,7.0288028115211246E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-06",42772.534375000003,"TT5","URBAN","Unknown","Unknown",1705,0,0,0,"NO"]
[null,"2017-02-06",42772.535416666666,"EPG23","URBAN","Unknown","Unknown",1,133,4.5248560891634798E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-06",42772.559942129628,"FTR12","RURAL LONG","Unknown","Unknown",324,0,0,0,"NO"]
[null,"2017-02-06",42772.5625,"TGN41","RURAL LONG","Overload","-",4,215,7.1556946016108633E-3,3.3282300472608665E-5,"NO"]
[null,"2017-02-06",42772.574305555558,"LDL13","RURAL SHORT","Asset failure","LV",1,195,6.6213359818677266E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-06",42772.579861111109,"SMR1","RURAL SHORT","Planned","-",1,40,0,0,"NO"]
[null,"2017-02-06",42772.586516203701,"MYT7","RURAL LONG","Unknown","Unknown",521,0,0,0,"NO"]
[null,"2017-02-06",42772.590277777781,"SMR3","RURAL LONG","Planned","-",1,40,0,0,"NO"]
[null,"2017-02-06",42772.597222222219,"WGL12","RURAL LONG","Planned","-",1,35,0,0,"NO"]
[null,"2017-02-06",42772.606249999997,"MOE22","RURAL LONG","Weather","-",1,0,0,0,"NO"]
[null,"2017-02-06",42772.615787037037,"MFA21","RURAL LONG","Unknown","Unknown",1363,0,0,0,"NO"]
[null,"2017-02-06",42772.625,"WO23","URBAN","Unknown","Unknown",1,30,1.020644230638379E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-06",42772.635081018518,"WGI33","RURAL SHORT","Unknown","Unknown",2826,0,0,0,"NO"]
[null,"2017-02-06",42772.651388888888,"NRN14","URBAN","Unknown","Unknown",1,118,4.0145339738442904E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-06",42772.683333333334,"WN5","RURAL LONG","Animal","Animal impact",1,85,7.0724888504293418E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-06",42772.70208333333,"FTR12","RURAL LONG","Animal","Animal impact",3,0,0,0,"NO"]
[null,"2017-02-06",42772.745798611111,"MSD2","RURAL LONG","Unknown","Unknown",1004,0,0,0,"NO"]
[null,"2017-02-06",42772.813194444447,"FTR21","RURAL LONG","Animal","Animal impact",15,74,9.2358383811489055E-3,1.248086267722825E-4,"NO"]
[null,"2017-02-06",42772.839583333334,"RUBA24","RURAL SHORT","Asset failure","LV",1,109,3.7011570360183702E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-06",42772.955555555556,"RWT32","URBAN","Asset failure","LV",1,68,2.313460256113659E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-07",42773.234432870369,"TGN41","RURAL LONG","Unknown","Unknown",579,0,0,0,"NO"]
[null,"2017-02-07",42773.267511574071,"TGN41","RURAL LONG","Asset failure","LV",1,315,2.6209811622179323E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-07",42773.313888888886,"LDL23","RURAL LONG","Network business","Switching and protection error",1,222,1.847167676229781E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-07",42773.347581018519,"FTR12","RURAL LONG","Unknown","Unknown",41,0,0,0,"NO"]
[null,"2017-02-07",42773.354166666664,"MFA22","RURAL LONG","Planned","-",10,353,0,0,"NO"]
[null,"2017-02-07",42773.354166666664,"WGL12","RURAL LONG","Planned","-",64,382,0,0,"NO"]
[null,"2017-02-07",42773.364583333336,"MSD2","RURAL LONG","Planned","-",4,245,0,0,"NO"]
[null,"2017-02-07",42773.368055555555,"KLK1","RURAL SHORT","Planned","-",289,380,0,0,"NO"]
[null,"2017-02-07",42773.368055555555,"WYK13","RURAL SHORT","Planned","-",191,365,0,0,"NO"]
[null,"2017-02-07",42773.369444444441,"FTR12","RURAL LONG","Planned","-",47,541.12765957446811,0,0,"NO"]
[null,"2017-02-07",42773.37300925926,"WN5","RURAL LONG","Unknown","Unknown",254,0,0,0,"NO"]
[null,"2017-02-07",42773.374212962961,"SMR8","RURAL LONG","Planned","-",11,195.90909090909091,0,0,"NO"]
[null,"2017-02-07",42773.375,"LLG14","RURAL SHORT","Other","Other",1,600,2.0373341482669925E-3,3.3955569137783212E-6,"NO"]
[null,"2017-02-07",42773.375,"LLG14","RURAL SHORT","Planned","-",46,600,0,0,"NO"]
[null,"2017-02-07",42773.375694444447,"WGI33","RURAL SHORT","Planned","-",138,262,0,0,"NO"]
[null,"2017-02-07",42773.376388888886,"MOE24","RURAL SHORT","Planned","-",33,210.72727272727272,0,0,"NO"]
[null,"2017-02-07",42773.376388888886,"SMR8","RURAL LONG","Asset failure","HV",1,0,0,0,"NO"]
[null,"2017-02-07",42773.381296296298,"TGN31","RURAL LONG","Planned","-",21,253.95238095238096,0,0,"NO"]
[null,"2017-02-07",42773.385717592595,"OFR23","RURAL LONG","Planned","-",59,336,0,0,"NO"]
[null,"2017-02-07",42773.386111111111,"RUBA22","RURAL SHORT","Planned","-",44,173,0,0,"NO"]
[null,"2017-02-07",42773.388888888891,"WYK24","RURAL SHORT","Planned","-",61,213,0,0,"NO"]
[null,"2017-02-07",42773.393055555556,"LGA14","RURAL LONG","Animal","Animal impact",1,129,1.0733541902416294E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-07",42773.394444444442,"WN5","RURAL LONG","Animal","Animal impact",2,106,1.7639619250482594E-3,1.6641150236304332E-5,"NO"]
[null,"2017-02-07",42773.395833333336,"WN3","RURAL LONG","Other","Other",1,295,2.4545696598548892E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-07",42773.395833333336,"WN3","RURAL LONG","Other","Other",1,295,2.4545696598548892E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-07",42773.395833333336,"WGL24","RURAL LONG","Planned","-",2,135,0,0,"NO"]
[null,"2017-02-07",42773.395833333336,"WN3","RURAL LONG","Planned","-",36,295,0,0,"NO"]
[null,"2017-02-07",42773.395833333336,"LGA23","RURAL LONG","Planned","-",2,60,0,0,"NO"]
[null,"2017-02-07",42773.397222222222,"WYK24","RURAL SHORT","Planned","-",4,313,0,0,"NO"]
[null,"2017-02-07",42773.399305555555,"WGL24","RURAL LONG","Planned","-",1,50,0,0,"NO"]
[null,"2017-02-07",42773.402777777781,"RUBA22","RURAL SHORT","Planned","-",1,80,0,0,"NO"]
[null,"2017-02-07",42773.409722222219,"WGL12","RURAL LONG","Planned","-",5,130,0,0,"NO"]
[null,"2017-02-07",42773.414583333331,"TGN31","RURAL LONG","Planned","-",68,328,0,0,"NO"]
[null,"2017-02-07",42773.416666666664,"BDL43","URBAN","Planned","-",3,100,0,0,"NO"]
[null,"2017-02-07",42773.420138888891,"WGL23","RURAL SHORT","Planned","-",1,70,0,0,"NO"]
[null,"2017-02-07",42773.428472222222,"DRN23","RURAL LONG","Other","Other",1,345,2.8705984157624976E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-07",42773.428472222222,"DRN23","RURAL LONG","Planned","-",203,318.20197044334975,0,0,"NO"]
[null,"2017-02-07",42773.430902777778,"WYK13","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1877,168,1.0707413349632007,6.3734603271619087E-3,"NO"]
[null,"2017-02-07",42773.458333333336,"WN3","RURAL LONG","Planned","-",1,40,0,0,"NO"]
[null,"2017-02-07",42773.472222222219,"RUBA22","RURAL SHORT","Planned","-",1,45,0,0,"NO"]
[null,"2017-02-07",42773.479166666664,"WGL23","RURAL SHORT","Planned","-",2,50,0,0,"NO"]
[null,"2017-02-07",42773.479166666664,"WN2","RURAL LONG","Asset failure","LV",5,110,4.5763163149836915E-3,4.1602875590760831E-5,"NO"]
[null,"2017-02-07",42773.492002314815,"MSD2","RURAL LONG","Asset failure","HV",36,217,6.5000332823004728E-2,2.9954070425347801E-4,"NO"]
[null,"2017-02-07",42773.493055555555,"WGL24","RURAL LONG","Planned","-",1,58,0,0,"NO"]
[null,"2017-02-07",42773.493750000001,"WOTS24","RURAL LONG","Planned","-",1,24,0,0,"NO"]
[null,"2017-02-07",42773.510416666664,"TT9","URBAN","Asset failure","LV",1,154,5.2393070506103455E-4,3.402147435461263E-6,"NO"]
[null,"2017-02-07",42773.51458333333,"RUBA22","RURAL SHORT","Planned","-",2,54,0,0,"NO"]
[null,"2017-02-07",42773.517361111109,"WT12","URBAN","Overload","-",1,376,1.2792074357334349E-3,3.402147435461263E-6,"NO"]
[null,"2017-02-07",42773.559027777781,"WOTS24","RURAL LONG","Planned","-",1,15,0,0,"NO"]
[null,"2017-02-07",42773.570138888892,"PHM33","RURAL LONG","Other","Cause Not In List",1,64,5.3251680756173864E-4,8.3205751181521662E-6,"NO"]
[null,"2017-02-07",42773.588888888888,"MYT2","RURAL SHORT","Overload","-",1,175,5.9422245991120617E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-07",42773.590277777781,"WN2","RURAL LONG","Asset failure","LV",52,182,7.8745922918192102E-2,4.3266990614391267E-4,"NO"]
[null,"2017-02-07",42773.590277777781,"RUBA22","RURAL SHORT","Planned","-",3,32,0,0,"NO"]
[null,"2017-02-07",42773.59375,"WGL13","RURAL SHORT","Asset failure","HV",32,37,4.0203393859135324E-3,1.0865782124090628E-4,"NO"]
[null,"2017-02-07",42773.622916666667,"BGE12","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",30,283,2.8828278197977945E-2,1.0186670741334964E-4,"NO"]
[null,"2017-02-07",42773.631782407407,"KLK1","RURAL SHORT","Unknown","Unknown",66,0,0,0,"NO"]
[null,"2017-02-07",42773.651388888888,"CRE32","URBAN","Vegetation","Grow-in - NSP responsibility",5,92,1.5649878203121811E-3,1.7010737177306314E-5,"NO"]
[null,"2017-02-07",42773.666666666664,"BDL6","RURAL SHORT","Asset Failure","Distribution substation",2,103,6.9948472423833413E-4,6.7911138275566425E-6,"NO"]
[null,"2017-02-07",42773.667118055557,"LGA12","RURAL SHORT","Unknown","Unknown",687,0,0,0,"NO"]
[null,"2017-02-07",42773.693055555559,"MFA21","RURAL LONG","Animal","Animal impact",1,168,1.3978566198495641E-3,8.3205751181521662E-6,"NO"]
[null,"2017-02-07",42773.704652777778,"LGA12","RURAL SHORT","Unknown","Unknown",687,0,0,0,"NO"]
[null,"2017-02-07",42773.884918981479,"WGL23","RURAL SHORT","Unknown","Unknown",32,0,0,0,"NO"]
[null,"2017-02-08",42774.053171296298,"LGA12","RURAL SHORT","Unknown","Unknown",183,0,0,0,"NO"]
[null,"2017-02-08",42774.402777777781,"WGI14","RURAL SHORT","Planned","-",3,285,0,0,"NO"]
[null,"2017-02-08",42774.741666666669,"SMR2","RURAL SHORT","Asset failure","LV",1,202,6.8590249658322089E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-09",42775.344618055555,"WGL24","RURAL LONG","Unknown","Unknown",657,0,0,0,"NO"]
[null,"2017-02-09",42775.410752314812,"WGL24","RURAL LONG","Unknown","Unknown",657,0,0,0,"NO"]
[null,"2017-02-09",42775.750694444447,"ELM12","RURAL SHORT","Overload","-",19,425.05263157894734,2.7422517635673722E-2,6.4515581361788098E-5,"NO"]
[null,"2017-02-10",42776.321527777778,"MYT1","RURAL SHORT","Animal","Animal impact",61,156,3.2312119591514504E-2,2.0712897174047758E-4,"NO"]
[null,"2017-02-10",42776.622685185182,"BDL44","RURAL LONG","Animal","Animal impact",43,147.97674418604652,5.294381947680224E-2,3.5778473008054316E-4,"NO"]
[null,"2017-02-11",42777.367847222224,"BDL43","URBAN","Unknown","Unknown",53,0,0,0,"NO"]
[null,"2017-02-12",42778.115590277775,"WOTS24","RURAL LONG","Unknown","Unknown",166,0,0,0,"NO"]
[null,"2017-02-12",42778.357638888891,"RWN31","RURAL SHORT","Planned","-",222,250,0,0,"NO"]
[null,"2017-02-12",42778.631249999999,"SLE14","RURAL SHORT","Animal","Animal impact",63,47,1.0054244021697609E-2,2.1392008556803422E-4,"NO"]
[null,"2017-02-13",42779.463194444441,"WN6","RURAL LONG","Planned","-",8,253,0,0,"NO"]
[null,"2017-02-14",42780.385034722225,"FTR23","RURAL LONG","Planned","-",159,365.00628930817612,0,0,"NO"]
[null,"2017-02-14",42780.388888888891,"MOE32","RURAL SHORT","Planned","-",3,33,0,0,"NO"]
[null,"2017-02-14",42780.836574074077,"RUBA12","RURAL LONG","Unknown","Unknown",483,0,0,0,"NO"]
[null,"2017-02-15",42781.502083333333,"LDL13","RURAL SHORT","Asset failure","LV",25,252,2.1392008556803423E-2,8.4888922844458028E-5,"NO"]
[null,"2017-02-16",42782.37358796296,"LDL11","URBAN","Unknown","Unknown",1295,0,0,0,"NO"]
[null,"2017-02-16",42782.441666666666,"WN5","RURAL LONG","Planned","-",10,44,0,0,"NO"]
[null,"2017-02-17",42783.371527777781,"RUBA22","RURAL SHORT","Planned","-",20,205,0,0,"NO"]
[null,"2017-02-17",42783.456944444442,"ELM33","RURAL SHORT","Animal","Animal impact",2,225,1.5280006112002446E-3,6.7911138275566425E-6,"NO"]
[null,"2017-02-17",42783.885289351849,"LDL14","RURAL SHORT","Unknown","Unknown",2219,0,0,0,"NO"]
[null,"2017-02-19",42785.224305555559,"LDL21","RURAL SHORT","Animal","Animal impact",518,18.567567567567568,3.265846639671989E-2,1.7588984813371703E-3,"NO"]
[null,"2017-02-19",42785.713182870371,"MSD4","RURAL LONG","Unknown","Unknown",594,0,0,0,"NO"]
[null,"2017-02-20",42786.89166666667,"WN6","RURAL LONG","Animal","Animal impact",2,0,0,0,"NO"]
[null,"2017-02-21",42787.006203703706,"BWN14","RURAL SHORT","Unknown","Unknown",2698,0,0,0,"NO"]
[null,"2017-02-21",42787.500138888892,"CLN22","RURAL SHORT","Unknown","Unknown",587,0,0,0,"NO"]
[null,"2017-02-22",42788.030671296299,"DRN22","RURAL SHORT","Asset failure","HV",3622,9,0.11068836427534572,1.2298707141705079E-2,"NO"]
[null,"2017-02-22",42788.375,"FGY34","URBAN","Planned","-",1,30,0,0,"NO"]
[null,"2017-02-22",42788.659722222219,"KLO14","RURAL LONG","Vegetation","Blow-in/Fall-in - NSP responsibility",10,359,2.9870864674166279E-2,8.3205751181521662E-5,"NO"]
[null,"2017-02-23",42789.350694444445,"FGY23","URBAN","Planned","-",109,445,0,0,"NO"]
[null,"2017-02-23",42789.519120370373,"FTR22","RURAL SHORT","Unknown","Unknown",364,0,0,0,"NO"]
[null,"2017-02-23",42789.583333333336,"RUBA24","RURAL SHORT","Planned","-",1,35,0,0,"NO"]
[null,"2017-02-24",42790.371527777781,"SLE32","RURAL SHORT","Planned","-",17,315,0,0,"NO"]
[null,"2017-02-25",42791.365277777775,"PHM31","RURAL SHORT","Asset failure","LV",1,134,4.5500462644629502E-4,3.3955569137783212E-6,"NO"]
[null,"2017-02-26",42792.565972222219,"RWT21","URBAN","Animal","Animal impact",3,0,0,0,"NO"]
[null,"2017-02-26",42792.997939814813,"ELM31","URBAN","Animal","Animal impact",3575,0,0,0,"NO"]
[null,"2017-02-27",42793.506944444445,"RUBA12","RURAL LONG","Planned","-",3,50,0,0,"NO"]
[null,"2017-02-27",42793.99722222222,"OFR23","RURAL LONG","Animal","Animal impact",4,121,4.0271583571856485E-3,3.3282300472608665E-5,"NO"]
[null,"2017-02-28",42794.350706018522,"WGI31","RURAL SHORT","Unknown","Unknown",2215,0,0,0,"NO"]
[null,"2017-02-28",42794.62777777778,"FTR12","RURAL LONG","Animal","Animal impact",2,61,1.0151101644145643E-3,1.6641150236304332E-5,"NO"]
[null,"2017-03-01",42795.206250000003,"ELM33","RURAL SHORT","Animal","Animal impact",2,52,3.531379190329454E-4,6.7911138275566425E-6,"NO"]
[null,"2017-03-01",42795.279166666667,"BN1","RURAL LONG","Asset failure","HV",12,16,1.5975504226852159E-3,9.9846901417825995E-5,"NO"]
[null,"2017-03-01",42795.408333333333,"PHI12","RURAL SHORT","Other","Other",1,345,1.1714671352535207E-3,3.3955569137783212E-6,"NO"]
[null,"2017-03-01",42795.611805555556,"KLO24","RURAL SHORT","Animal","Animal impact",31,189,1.9894567957827184E-2,1.0526226432712796E-4,"NO"]
[null,"2017-03-02",42796.374305555553,"WYK24","RURAL SHORT","Other","Other",1,400,1.3582227655113284E-3,3.3955569137783212E-6,"NO"]
[null,"2017-03-02",42796.47152777778,"FGY22","URBAN","Animal","Animal impact",1,76,2.5856320509505602E-4,3.402147435461263E-6,"NO"]
[null,"2017-03-02",42796.722986111112,"WN3","RURAL LONG","Unknown","Unknown",178,0,0,0,"NO"]
[null,"2017-03-03",42797.279166666667,"BGE12","RURAL SHORT","Animal","Animal impact",25,133,1.1290226738312918E-2,8.4888922844458028E-5,"NO"]
[null,"2017-03-03",42797.397916666669,"MWT31","RURAL SHORT","Planned","-",1,22,0,0,"NO"]
[null,"2017-03-03",42797.739583333336,"RUBA12","RURAL LONG","Unknown","Unknown",2,22,3.6610530519869534E-4,1.6641150236304332E-5,"NO"]
[null,"2017-03-04",42798.92,"BGE23","URBAN","Unknown","Unknown",1848,0,0,0,"NO"]
[null,"2017-03-06",42800.117592592593,"WN2","RURAL LONG","Unknown","Unknown",630,0,0,0,"NO"]
[null,"2017-03-06",42800.18409722222,"FTR22","RURAL SHORT","Unknown","Unknown",366,0,0,0,"NO"]
[null,"2017-03-06",42800.818055555559,"BGE11","RURAL SHORT","Other","High/Low volt or Tap change",6,17,3.4634680520538873E-4,2.0373341482669927E-5,"NO"]
[null,"2017-03-07",42801.375,"WGI31","RURAL SHORT","Planned","-",2,287,0,0,"NO"]
[null,"2017-03-07",42801.392361111109,"MJG11","RURAL SHORT","Planned","-",10,20,0,0,"NO"]
[null,"2017-03-08",42802.077002314814,"CYN33","RURAL SHORT","Unknown","Unknown",1617,0,0,0,"NO"]
[null,"2017-03-08",42802.385416666664,"TGN31","RURAL LONG","Planned","-",72,295,0,0,"NO"]
[null,"2017-03-08",42802.578472222223,"BN6","RURAL LONG","Planned","-",2,77,0,0,"NO"]
[null,"2017-03-09",42803.369444444441,"LDL23","RURAL LONG","Planned","-",110,306,0,0,"NO"]
[null,"2017-03-09",42803.420138888891,"SMR5","RURAL LONG","Planned","-",2,135,0,0,"NO"]
[null,"2017-03-09",42803.795138888891,"WGI22","RURAL LONG","Asset Failure","LV",1,145,1.2064833921320642E-3,8.3205751181521662E-6,"NO"]
[null,"2017-03-10",42804.375,"WOTS11","RURAL LONG","Planned","-",4,250,0,0,"NO"]
[null,"2017-03-10",42804.482638888891,"WN3","RURAL LONG","Animal","Animal impact",2,162,2.6958663382813022E-3,1.6641150236304332E-5,"NO"]
[null,"2017-03-11",42805.422048611108,"KLO14","RURAL LONG","Unknown","Unknown",718,0,0,0,"NO"]
[null,"2017-03-12",42806.333333333336,"WYK24","RURAL SHORT","Planned","-",31,10,0,0,"NO"]
[null,"2017-03-12",42806.562916666669,"ELM33","RURAL SHORT","Asset failure","LV",3,414,4.217281686912675E-3,1.0186670741334963E-5,"NO"]
[null,"2017-03-12",42806.793055555558,"WGI22","RURAL LONG","Weather","-",5,218,9.069426878785862E-3,4.1602875590760831E-5,"NO"]
[null,"2017-03-13",42807.363402777781,"WT11","URBAN","Unknown","Unknown",2181,0,0,0,"NO"]
[null,"2017-03-14",42808.143912037034,"WGL11","RURAL SHORT","Unknown","Unknown",1303,0,0,0,"NO"]
[null,"2017-03-14",42808.402777777781,"KLO14","RURAL LONG","Planned","-",15,110,0,0,"NO"]
[null,"2017-03-14",42808.600694444445,"RUBA22","RURAL SHORT","Planned","-",3,22,0,0,"NO"]
[null,"2017-03-15",42809.373877314814,"SMR3","RURAL LONG","Planned","-",52,351,0,0,"NO"]
[null,"2017-03-15",42809.51666666667,"KLO24","RURAL SHORT","Weather","-",4,194,2.6349521650919773E-3,1.3582227655113285E-5,"NO"]
[null,"2017-03-15",42809.870763888888,"MDG1","RURAL SHORT","Unknown","Unknown",1484,0,0,0,"NO"]
[null,"2017-03-16",42810.402071759258,"SFS1","RURAL SHORT","Planned","-",498,565,0,0,"NO"]
[null,"2017-03-17",42811.084918981483,"NLA32","RURAL SHORT","Unknown","Unknown",96,0,0,0,"NO"]
[null,"2017-03-17",42811.353472222225,"CLN14","URBAN","Planned","-",85,251,0,0,"NO"]
[null,"2017-03-17",42811.444444444445,"BGE24","RURAL SHORT","Planned","-",1,210,0,0,"NO"]
[null,"2017-03-17",42811.758333333331,"CLN22","RURAL SHORT","Animal","Animal impact",4,66,8.9642702523747681E-4,1.3582227655113285E-5,"NO"]
[null,"2017-03-18",42812.501388888886,"CYN12","URBAN","Asset Failure","LV",1,212,7.2125525631778781E-4,3.402147435461263E-6,"NO"]
[null,"2017-03-18",42812.990972222222,"BGE12","RURAL SHORT","Animal","Animal impact",1,86,2.9201789458493564E-4,3.3955569137783212E-6,"NO"]
[null,"2017-03-20",42814.177083333336,"CRE22","URBAN","Overload","-",1,231,7.8589605759155177E-4,3.402147435461263E-6,"NO"]
[null,"2017-03-20",42814.513888888891,"BDL41","RURAL LONG","Planned","-",63,195,0,0,"NO"]
[null,"2017-03-20",42814.763888888891,"KLO14","RURAL LONG","Weather","-",2,330,5.4915795779804299E-3,1.6641150236304332E-5,"NO"]
[null,"2017-03-21",42815.152951388889,"SLE31","RURAL LONG","Unknown","Unknown",568,0,0,0,"NO"]
[null,"2017-03-21",42815.397222222222,"RWN34","RURAL SHORT","Animal","Animal impact",1,221,7.5041807794500894E-4,3.3955569137783212E-6,"NO"]
[null,"2017-03-21",42815.696527777778,"BWN12","URBAN","Animal","Animal impact",20,109,7.4166814093055535E-3,6.8042948709225257E-5,"NO"]
[null,"2017-03-21",42815.869444444441,"UWY1","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",22,393,2.9357985076527364E-2,7.4702252103123063E-5,"NO"]
[null,"2017-03-22",42816.375,"MWT14","RURAL SHORT","Planned","-",1,85,0,0,"NO"]
[null,"2017-03-22",42816.605555555558,"BWA22","RURAL LONG","Planned","-",6,18,0,0,"NO"]
[null,"2017-03-23",42817.333333333336,"LLG14","RURAL SHORT","Planned","-",170,283,0,0,"NO"]
[null,"2017-03-23",42817.368055555555,"SMR5","RURAL LONG","Planned","-",2,50,0,0,"NO"]
[null,"2017-03-23",42817.458333333336,"SMR5","RURAL LONG","Planned","-",1,40,0,0,"NO"]
[null,"2017-03-24",42818.047488425924,"RWN22","URBAN","Unknown","Unknown",2596,0,0,0,"NO"]
[null,"2017-03-24",42818.375,"WGL13","RURAL SHORT","Planned","-",110,310,0,0,"NO"]
[null,"2017-03-24",42818.527777777781,"MSD2","RURAL LONG","Planned","-",1,77,0,0,"NO"]
[null,"2017-03-25",42819.001504629632,"CPK11","URBAN","Unknown","Unknown",3494,0,0,0,"NO"]
[null,"2017-03-25",42819.40625,"SMG33","URBAN","Other","Work Standard Change",61,295,6.1221643101125434E-2,2.0753099356313705E-4,"NO"]
[null,"2017-03-26",42820.354583333334,"LLG12","RURAL SHORT","Planned","-",400,482,0,0,"NO"]
[null,"2017-03-26",42820.805810185186,"RWT26","URBAN","Animal","Animal impact",1,2,6.8042948709225261E-6,3.402147435461263E-6,"NO"]
[null,"2017-03-27",42821.375567129631,"TGN23","RURAL SHORT","Planned","-",17,186.94117647058823,0,0,"NO"]
[null,"2017-03-27",42821.57408564815,"LGA11","RURAL LONG","Unknown","Unknown",39,0,0,0,"NO"]
[null,"2017-03-27",42821.607592592591,"TGN23","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1978,45.458038422649139,0.30531489545929152,6.7164115754535193E-3,"NO"]
[null,"2017-03-27",42821.670081018521,"SLE32","RURAL SHORT","Weather","-",1419,72.268498942917546,0.34821096595105305,4.8182952606514373E-3,"NO"]
[null,"2017-03-27",42821.745833333334,"LGA13","RURAL LONG","Unknown","Unknown",2,346,5.757837981761299E-3,1.6641150236304332E-5,"NO"]
[null,"2017-03-27",42821.778622685182,"CNR3","RURAL SHORT","Unknown","Unknown",58,0,0,0,"NO"]
[null,"2017-03-27",42821.907048611109,"WT6","URBAN","Unknown","Unknown",3460,0,0,0,"NO"]
[null,"2017-03-28",42822.368055555555,"SLE32","RURAL SHORT","Planned","-",4,230,0,0,"NO"]
[null,"2017-03-28",42822.453472222223,"MOE21","RURAL SHORT","Animal","Animal impact",1,132,4.482135126187384E-4,3.3955569137783212E-6,"NO"]
[null,"2017-03-29",42823.26458333333,"SLE14","RURAL SHORT","Animal","Animal impact",1,71,2.410845408782608E-4,3.3955569137783212E-6,"NO"]
[null,"2017-03-29",42823.555555555555,"BN4","URBAN","Planned","-",29,125,0,0,"NO"]
[null,"2017-03-30",42824.340277777781,"WGI22","RURAL LONG","Planned","-",52,539.23076923076928,0,0,"NO"]
[null,"2017-03-30",42824.37222222222,"BN4","URBAN","Planned","-",60,132,0,0,"NO"]
[null,"2017-03-30",42824.789548611108,"ELM32","URBAN","Animal","Animal impact",417,147,0.20854823564633998,1.4186954805873468E-3,"NO"]
[null,"2017-03-31",42825.390972222223,"WOTS11","RURAL LONG","Planned","-",36,275.97222222222223,0,0,"NO"]
[null,"2017-03-31",42825.633333333331,"MFA22","RURAL LONG","Vegetation","Grow-in - NSP responsibility",592,54,0.26599214537708848,4.9257804699460823E-3,"NO"]
[null,"2017-04-02",42827.380555555559,"KLO14","RURAL LONG","Asset failure","LV",2,182,3.0286893430073888E-3,1.6641150236304332E-5,"NO"]
[null,"2017-04-03",42828.245879629627,"LDL14","RURAL SHORT","Unknown","Unknown",129,0,0,0,"NO"]
[null,"2017-04-03",42828.520833333336,"BWA22","RURAL LONG","Planned","-",3,30,0,0,"NO"]
[null,"2017-04-03",42828.53125,"BWA22","RURAL LONG","Planned","-",2,30,0,0,"NO"]
[null,"2017-04-03",42828.928506944445,"ELM15","RURAL SHORT","Unknown","Unknown",442,0,0,0,"NO"]
[null,"2017-04-04",42829.4375,"WGL15","RURAL SHORT","Planned","-",25,205,0,0,"NO"]
[null,"2017-04-04",42829.927488425928,"TT7","URBAN","Animal","Animal impact",437,159.48741418764303,0.23711606766190821,1.4867384292965721E-3,"NO"]
[null,"2017-04-05",42830.328576388885,"BN3","RURAL SHORT","Unknown","Unknown",14,0,0,0,"NO"]
[null,"2017-04-05",42830.375,"MOE22","RURAL LONG","Planned","-",19,180,0,0,"NO"]
[null,"2017-04-05",42830.559027777781,"MOE14","RURAL SHORT","Planned","-",1,50,0,0,"NO"]
[null,"2017-04-05",42830.654166666667,"FTR12","RURAL LONG","Animal","Animal impact",2,73,1.2148039672502163E-3,1.6641150236304332E-5,"NO"]
[null,"2017-04-06",42831.356377314813,"WYK23","RURAL SHORT","Planned","-",394,262,0,0,"NO"]
[null,"2017-04-06",42831.62908564815,"LLG13","RURAL SHORT","Unknown","Unknown",812,0,0,0,"NO"]
[null,"2017-04-07",42832.332638888889,"BGE12","RURAL SHORT","Animal","Animal impact",7,121,2.8760367059702378E-3,2.3768898396448248E-5,"NO"]
[null,"2017-04-07",42832.336805555555,"BWR32","URBAN","Animal","Animal impact",11,143.09090909090909,5.3549800634160281E-3,3.7423621790073894E-5,"NO"]
[null,"2017-04-07",42832.572916666664,"BWR13","URBAN","Planned","-",8,35,0,0,"NO"]
[null,"2017-04-08",42833.520833333336,"BRT22","RURAL SHORT","Animal","Animal impact",1,141,4.7877352484274326E-4,3.3955569137783212E-6,"NO"]
[null,"2017-04-08",42833.712488425925,"KMS1","RURAL SHORT","Unknown","Unknown",1367,0,0,0,"NO"]
[null,"2017-04-08",42833.893437500003,"MFA22","RURAL LONG","Unknown","Unknown",405,0,0,0,"NO"]
[null,"2017-04-09",42834.218113425923,"KLO14","RURAL LONG","Unknown","Unknown",3153,0,0,0,"NO"]
[null,"2017-04-09",42834.295138888891,"MFA34","RURAL SHORT","Weather","-",1,6,2.0373341482669927E-5,3.3955569137783212E-6,"NO"]
[null,"2017-04-09",42834.445451388892,"FTR22","RURAL SHORT","Weather","-",1284,26.803738317757009,0.11686148674459469,4.3598950772913642E-3,"NO"]
[null,"2017-04-09",42834.571527777778,"BRT21","RURAL SHORT","Weather","-",5,182,3.089956791538272E-3,1.6977784568891605E-5,"NO"]
[null,"2017-04-10",42835.343055555553,"RWT32","URBAN","Asset Failure","LV",1,264,8.9816692296177346E-4,3.402147435461263E-6,"NO"]
[null,"2017-04-10",42835.45585648148,"KLK1","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",1,227,7.7079141942767884E-4,3.3955569137783212E-6,"NO"]
[null,"2017-04-10",42835.47152777778,"TT9","URBAN","Overload","-",1,204,6.9403807683409769E-4,3.402147435461263E-6,"NO"]
[null,"2017-04-11",42836.322916666664,"WYK12","RURAL SHORT","Asset failure","LV",1,357,1.2122138182188607E-3,3.3955569137783212E-6,"NO"]
[null,"2017-04-11",42836.395833333336,"MFA21","RURAL LONG","Planned","-",1,285,0,0,"NO"]
[null,"2017-04-11",42836.535416666666,"WGI22","RURAL LONG","Animal","Animal impact",1,69,5.7411968315249952E-4,8.3205751181521662E-6,"NO"]
[null,"2017-04-12",42837.248611111114,"BRT11","RURAL SHORT","Asset failure","LV",1,581,1.9728185669052045E-3,3.3955569137783212E-6,"NO"]
[null,"2017-04-12",42837.364583333336,"OFR23","RURAL LONG","Planned","-",56,335,0,0,"NO"]
[null,"2017-04-12",42837.409722222219,"MOE14","RURAL SHORT","Planned","-",113,291,0,0,"NO"]
[null,"2017-04-12",42837.679861111108,"DRN14","RURAL SHORT","Asset failure","LV",1,191,6.4855137053165931E-4,3.3955569137783212E-6,"NO"]
[null,"2017-04-13",42838.420138888891,"MOE23","RURAL SHORT","Animal","Animal impact",8,112,3.0424189947453758E-3,2.716445531022657E-5,"NO"]
[null,"2017-04-13",42838.785416666666,"WGI22","RURAL LONG","Animal","Animal impact",63,109,5.713738933635093E-2,5.2419623244358651E-4,"NO"]
[null,"2017-04-15",42840.267361111109,"LDL23","RURAL LONG","Animal","Animal impact",18,156,2.3364174931771283E-2,1.4977035212673901E-4,"NO"]
[null,"2017-04-16",42841.306250000001,"MSD2","RURAL LONG","Animal","Animal impact",2,97,1.6141915729215204E-3,1.6641150236304332E-5,"NO"]
[null,"2017-04-16",42841.840277777781,"BN6","RURAL LONG","Animal","Animal impact",1,0,0,0,"NO"]
[null,"2017-04-18",42843.40425925926,"WOTS24","RURAL LONG","Planned","-",28,317.67857142857144,0,0,"NO"]
[null,"2017-04-18",42843.555555555555,"RUBA12","RURAL LONG","Planned","-",2,160,0,0,"NO"]
[null,"2017-04-19",42844.361111111109,"SMR5","RURAL LONG","Planned","-",1,40,0,0,"NO"]
[null,"2017-04-19",42844.558333333334,"CLN21","RURAL SHORT","Animal","Animal impact",3,156,1.5891206356482542E-3,1.0186670741334963E-5,"NO"]
[null,"2017-04-19",42844.795532407406,"UWY1","RURAL SHORT","Unknown","Unknown",2927,0,0,0,"NO"]
[null,"2017-04-20",42845.375,"MOE22","RURAL LONG","Planned","-",2,620,0,0,"NO"]
[null,"2017-04-21",42846.333333333336,"WYK24","RURAL SHORT","Planned","-",161,545,0,0,"NO"]
[null,"2017-04-21",42846.543055555558,"CRE33","RURAL SHORT","Animal","Animal impact",10,348,1.1816538059948558E-2,3.395556913778321E-5,"NO"]
[null,"2017-04-22",42847.157638888886,"LGA23","RURAL LONG","Asset failure","HV",48,0,0,0,"NO"]
[null,"2017-04-23",42848.375,"NLA32","RURAL SHORT","Planned","-",12,350,0,0,"NO"]
[null,"2017-04-24",42849.492395833331,"SMG31","URBAN","Unknown","Unknown",1,22,7.4847243580147788E-5,3.402147435461263E-6,"NO"]
[null,"2017-04-25",42850.32708333333,"RUBA12","RURAL LONG","Animal","Animal impact",47,28,1.0949876855488252E-2,3.9106703055315185E-4,"NO"]
[null,"2017-04-26",42851.388888888891,"SMR5","RURAL LONG","Planned","-",1,50,0,0,"NO"]
[null,"2017-04-26",42851.541666666664,"LGA13","RURAL LONG","Planned","-",2,105,0,0,"NO"]
[null,"2017-04-27",42852.364803240744,"FTR21","RURAL LONG","Planned","-",157,428.35668789808915,0,0,"NO"]
[null,"2017-04-27",42852.444444444445,"WN5","RURAL LONG","Planned","-",1,10,0,0,"NO"]
[null,"2017-04-27",42852.645138888889,"TGN23","RURAL SHORT","Network business","Switching and protection error",1,84,2.8522678075737897E-4,3.3955569137783212E-6,"NO"]
[null,"2017-04-28",42853.34952546296,"BWN14","RURAL SHORT","Planned","-",365,522,0,0,"NO"]
[null,"2017-04-28",42853.552777777775,"SLE31","RURAL LONG","Asset Failure","LV",1,56,4.6595220661652131E-4,8.3205751181521662E-6,"NO"]
[null,"2017-04-29",42854.152870370373,"BGE22","RURAL SHORT","Unknown","Unknown",51,0,0,0,"NO"]
[null,"2017-04-30",42855.376388888886,"MWT11","RURAL SHORT","Planned","-",51,90,0,0,"NO"]
[null,"2017-04-30",42855.754166666666,"SMR3","RURAL LONG","Animal","Animal impact",1,69,5.7411968315249952E-4,8.3205751181521662E-6,"NO"]
[null,"2017-05-01",42856.40347222222,"LYD13","URBAN","Planned","-",16,173,0,0,"NO"]
[null,"2017-05-02",42857.107638888891,"WGL15","RURAL SHORT","Third Party","Vehicle impact",703,52,0.1241279785400803,2.3870765103861597E-3,"NO"]
[null,"2017-05-02",42857.375,"BN3","RURAL SHORT","Other","Other",3,350,3.5653347594672372E-3,1.0186670741334963E-5,"NO"]
[null,"2017-05-03",42858.357638888891,"MFA21","RURAL LONG","Planned","-",18,405,0,0,"NO"]
[null,"2017-05-03",42858.708333333336,"LGA24","RURAL SHORT","Unknown","Unknown",3,10,1.0186670741334964E-4,1.0186670741334963E-5,"NO"]
[null,"2017-05-04",42859.341666666667,"WN3","RURAL LONG","Animal","Animal impact",1,78,6.4900485921586904E-4,8.3205751181521662E-6,"NO"]
[null,"2017-05-04",42859.482638888891,"BDL41","RURAL LONG","Planned","-",12,125,0,0,"NO"]
[null,"2017-05-04",42859.744328703702,"ELM11","URBAN","Asset failure","LV",1,1191,4.051957595634364E-3,3.402147435461263E-6,"NO"]
[null,"2017-05-05",42860.365972222222,"LGA21","RURAL SHORT","Other","Other",1,123,4.176535003947335E-4,3.3955569137783212E-6,"NO"]
[null,"2017-05-05",42860.584722222222,"BDL41","RURAL LONG","Animal","Animal impact",1,184,1.5309858217399986E-3,8.3205751181521662E-6,"NO"]
[null,"2017-05-06",42861.493055555555,"LDL13","RURAL SHORT","Unknown","Unknown",1,25,8.4888922844458028E-5,3.3955569137783212E-6,"NO"]
[null,"2017-05-07",42862.336805555555,"CYN32","URBAN","Planned","-",189,228,0,0,"NO"]
[null,"2017-05-08",42863.409722222219,"DRN23","RURAL LONG","Planned","-",1,5,0,0,"NO"]
[null,"2017-05-09",42864.365972222222,"BN3","RURAL SHORT","Planned","-",3,117,0,0,"NO"]
[null,"2017-05-09",42864.419444444444,"LGA21","RURAL SHORT","Asset Failure","LV",1,116,3.9388460199828526E-4,3.3955569137783212E-6,"NO"]
[null,"2017-05-10",42865,"FGY13","RURAL SHORT","Planned","-",51,711,0,0,"NO"]
[null,"2017-05-10",42865.385416666664,"BDL6","RURAL SHORT","Planned","-",83,240,0,0,"NO"]
[null,"2017-05-11",42866.281851851854,"WOTS11","RURAL LONG","Unknown","Unknown",545,0,0,0,"NO"]
[null,"2017-05-11",42866.378472222219,"LDL23","RURAL LONG","Planned","-",1,126,0,0,"NO"]
[null,"2017-05-11",42866.424305555556,"PHI12","RURAL SHORT","Planned","-",4,79,0,0,"NO"]
[null,"2017-05-12",42867.364861111113,"LLG11","RURAL SHORT","Planned","-",222,382,0,0,"NO"]
[null,"2017-05-12",42867.581250000003,"WGI33","RURAL SHORT","Overload","-",1,138,4.6858685410140831E-4,3.3955569137783212E-6,"NO"]
[null,"2017-05-12",42867.621527777781,"KLK1","RURAL SHORT","Unknown","Unknown",14,50,2.3768898396448247E-3,4.7537796792896496E-5,"NO"]
[null,"2017-05-14",42869.595833333333,"FTR12","RURAL LONG","Animal","Animal impact",1,127,1.0567130400053251E-3,8.3205751181521662E-6,"NO"]
[null,"2017-05-15",42870.818055555559,"LLG14","RURAL SHORT","Overload","-",1,70,2.3768898396448246E-4,3.3955569137783212E-6,"NO"]
[null,"2017-05-16",42871.408333333333,"WGL12","RURAL LONG","Planned","-",127,352,0,0,"NO"]
[null,"2017-05-16",42871.481944444444,"BWA23","RURAL SHORT","Planned","-",1,46,0,0,"NO"]
[null,"2017-05-17",42872.272222222222,"BWR32","URBAN","Overload","-",1,425,1.4459126600710368E-3,3.402147435461263E-6,"NO"]
[null,"2017-05-17",42872.385416666664,"BDL8","RURAL LONG","Planned","-",1,196,0,0,"NO"]
[null,"2017-05-17",42872.5625,"RWN31","RURAL SHORT","Planned","-",63,165,0,0,"NO"]
[null,"2017-05-18",42873.378472222219,"WN2","RURAL LONG","Planned","-",1,100,0,0,"NO"]
[null,"2017-05-19",42874.375,"SMR5","RURAL LONG","Planned","-",6,65,0,0,"NO"]
[null,"2017-05-19",42874.709027777775,"FTR23","RURAL LONG","Asset Failure","LV",1,91,7.5717233575184719E-4,8.3205751181521662E-6,"NO"]
[null,"2017-05-19",42874.779027777775,"SMR4","RURAL SHORT","Unknown","Unknown",58,0,0,0,"NO"]
[null,"2017-05-22",42877.296099537038,"MSD2","RURAL LONG","Unknown","Unknown",66,0,0,0,"NO"]
[null,"2017-05-22",42877.465277777781,"KLK3","RURAL SHORT","Planned","-",1,50,0,0,"NO"]
[null,"2017-05-23",42878.378472222219,"KLO14","RURAL LONG","Other","Other",1,125,1.0400718897690209E-3,8.3205751181521662E-6,"NO"]
[null,"2017-05-23",42878.545138888891,"BDL8","RURAL LONG","Planned","-",1,65,0,0,"NO"]
[null,"2017-05-24",42879.251597222225,"WOTS24","RURAL LONG","Planned","-",973,2.487153134635149,0,0,"NO"]
[null,"2017-05-24",42879.40625,"BN1","RURAL LONG","Planned","-",13,379,0,0,"NO"]
[null,"2017-05-24",42879.634722222225,"MOE23","RURAL SHORT","Asset failure","LV",1,248,8.4209811461702366E-4,3.3955569137783212E-6,"NO"]
[null,"2017-05-25",42880.43472222222,"LGA13","RURAL LONG","Planned","-",1,49,0,0,"NO"]
[null,"2017-05-26",42881.053206018521,"MOE22","RURAL LONG","Unknown","Unknown",100,0,0,0,"NO"]
[null,"2017-05-26",42881.590277777781,"MSD2","RURAL LONG","Planned","-",1,40,0,0,"NO"]
[null,"2017-05-27",42882.359189814815,"WYK13","RURAL SHORT","Planned","-",154,596.14935064935059,0,0,"NO"]
[null,"2017-05-28",42883.114652777775,"MOE14","RURAL SHORT","Unknown","Unknown",1785,0,0,0,"NO"]
[null,"2017-05-28",42883.367696759262,"KMS1","RURAL SHORT","Unknown","Unknown",1361,0,0,0,"NO"]
[null,"2017-05-28",42883.731249999997,"LYD13","URBAN","Unknown","Unknown",1,303,1.0308506729447627E-3,3.402147435461263E-6,"NO"]
[null,"2017-05-29",42884.479166666664,"WO31","URBAN","Planned","-",1,30,0,0,"NO"]
[null,"2017-05-30",42885.429166666669,"KLO24","RURAL SHORT","Animal","Animal impact",7,89,2.1154319572838942E-3,2.3768898396448248E-5,"NO"]
[null,"2017-05-30",42885.45,"WYK13","RURAL SHORT","Planned","-",287,208.79094076655053,0,0,"NO"]
[null,"2017-05-31",42886.364583333336,"TGN41","RURAL LONG","Planned","-",13,145,0,0,"NO"]
[null,"2017-05-31",42886.447916666664,"WYK12","RURAL SHORT","Planned","-",3,41,0,0,"NO"]
[null,"2017-06-01",42887.159722222219,"MBY11","RURAL SHORT","Overload","-",4,322,4.3734773049464775E-3,1.3582227655113285E-5,"NO"]
[null,"2017-06-01",42887.420138888891,"LDL23","RURAL LONG","Unknown","Unknown",2,80,1.3312920189043466E-3,1.6641150236304332E-5,"NO"]
[null,"2017-06-01",42887.545138888891,"WYK12","RURAL SHORT","Planned","-",1,135,0,0,"NO"]
[null,"2017-06-02",42888.087233796294,"MBY11","RURAL SHORT","Unknown","Unknown",1135,0,0,0,"NO"]
[null,"2017-06-02",42888.465277777781,"KMS21","RURAL SHORT","Planned","-",3,70,0,0,"NO"]
[null,"2017-06-03",42889.496527777781,"PHM33","RURAL LONG","Overload","-",1,170,1.4144977700858684E-3,8.3205751181521662E-6,"NO"]
[null,"2017-06-05",42891.132986111108,"BGE24","RURAL SHORT","Overload","-",982,0,0,0,"NO"]
[null,"2017-06-05",42891.643750000003,"MSD2","RURAL LONG","Unknown","Unknown",26,8,1.7306796245756507E-3,2.1633495307195634E-4,"NO"]
[null,"2017-06-06",42892.318749999999,"OFR23","RURAL LONG","Animal","Animal impact",2,205,3.4114357984423881E-3,1.6641150236304332E-5,"NO"]
[null,"2017-06-06",42892.559027777781,"MOE14","RURAL SHORT","Unknown","Unknown",1,97,3.2936902063649716E-4,3.3955569137783212E-6,"NO"]
[null,"2017-06-07",42893.364583333336,"BGE11","RURAL SHORT","Planned","-",39,180,0,0,"NO"]
[null,"2017-06-07",42893.631944444445,"FGY12","URBAN","Asset failure","LV",1,249,8.4713471142985452E-4,3.402147435461263E-6,"NO"]
[null,"2017-06-08",42894.333333333336,"RWN26","RURAL SHORT","Planned","-",97,344.89690721649487,0,0,"NO"]
[null,"2017-06-08",42894.400694444441,"WN3","RURAL LONG","Planned","-",6,221,0,0,"NO"]
[null,"2017-06-09",42895.354166666664,"BRA14","URBAN","Planned","-",324,378,0,0,"NO"]
[null,"2017-06-09",42895.541666666664,"LDL23","RURAL LONG","Planned","-",1,75,0,0,"NO"]
[null,"2017-06-10",42896.740972222222,"BRA21","URBAN","Other","Fuse Insertion",1,99,3.3681259611066503E-4,3.402147435461263E-6,"NO"]
[null,"2017-06-12",42898.490972222222,"WGI14","RURAL SHORT","Asset failure","LV",1,103,3.4974236211916706E-4,3.3955569137783212E-6,"NO"]
[null,"2017-06-13",42899.423611111109,"WN5","RURAL LONG","Planned","-",1,100,0,0,"NO"]
[null,"2017-06-13",42899.728472222225,"LDL14","RURAL SHORT","Unknown","Unknown",1,3,1.0186670741334963E-5,3.3955569137783212E-6,"NO"]
[null,"2017-06-14",42900.375,"MOE22","RURAL LONG","Planned","-",66,480,0,0,"NO"]
[null,"2017-06-14",42900.583333333336,"WN3","RURAL LONG","Planned","-",6,60,0,0,"NO"]
[null,"2017-06-15",42901.354166666664,"OFR22","RURAL SHORT","Planned","-",172,470,0,0,"NO"]
[null,"2017-06-15",42901.388888888891,"LYD14","RURAL SHORT","Planned","-",23,295,0,0,"NO"]
[null,"2017-06-16",42902.364583333336,"SMR5","RURAL LONG","Planned","-",35,305,0,0,"NO"]
[null,"2017-06-16",42902.464432870373,"WYK13","RURAL SHORT","Planned","-",14,214,0,0,"NO"]
[null,"2017-06-17",42903.508564814816,"KLO14","RURAL LONG","Animal","Animal impact",1722,63.304297328687575,0.90702589362976771,1.432803035345803E-2,"NO"]
[null,"2017-06-18",42904.912499999999,"MYT8","RURAL SHORT","Animal","Animal impact",2,1560,1.0594137570988362E-2,6.7911138275566425E-6,"NO"]
[null,"2017-06-20",42906.350694444445,"WOTS11","RURAL LONG","Planned","-",8,105,0,0,"NO"]
[null,"2017-06-20",42906.5,"WOTS11","RURAL LONG","Planned","-",7,85,0,0,"NO"]
[null,"2017-06-20",42906.745833333334,"LGA14","RURAL LONG","Asset Failure","LV",1,96,7.9877521134260796E-4,8.3205751181521662E-6,"NO"]
[null,"2017-06-21",42907.388888888891,"BDL41","RURAL LONG","Planned","-",139,318,0,0,"NO"]
[null,"2017-06-21",42907.72152777778,"WO11","URBAN","Unknown","Unknown",1,62,2.109331409985983E-4,3.402147435461263E-6,"NO"]
[null,"2017-06-22",42908.365289351852,"WOTS11","RURAL LONG","Planned","-",71,322,0,0,"NO"]
[null,"2017-06-22",42908.515972222223,"MSD4","RURAL LONG","Animal","Animal impact",2,97,1.6141915729215204E-3,1.6641150236304332E-5,"NO"]
[null,"2017-06-23",42909.364583333336,"MYT2","RURAL SHORT","Planned","-",98,370,0,0,"NO"]
[null,"2017-06-23",42909.643750000003,"WOTS25","RURAL SHORT","Overload","-",2,133,9.0321813906503337E-4,6.7911138275566425E-6,"NO"]
[null,"2017-06-24",42910.707638888889,"BRT22","RURAL SHORT","Asset failure","LV",2,211,1.4329250176144514E-3,6.7911138275566425E-6,"NO"]
[null,"2017-06-26",42912.410416666666,"BGE12","RURAL SHORT","Planned","-",1,3199,0,0,"NO"]
[null,"2017-06-27",42913.354166666664,"BDL41","RURAL LONG","Planned","-",65,360,0,0,"NO"]
[null,"2017-06-27",42913.399305555555,"WN3","RURAL LONG","Other","Other",1,70,5.8244025827065165E-4,8.3205751181521662E-6,"NO"]
[null,"2017-06-27",42913.775694444441,"PHM33","RURAL LONG","Unknown","Unknown",1,165,1.3728948944951075E-3,8.3205751181521662E-6,"NO"]
[null,"2017-06-28",42914.388888888891,"MSD2","RURAL LONG","Planned","-",1,321,0,0,"NO"]
[null,"2017-06-28",42914.521967592591,"MBY11","RURAL SHORT","Unknown","Unknown",1133,19,7.3096153682905923E-2,3.8471659833108377E-3,"NO"]
[null,"2017-06-29",42915.388888888891,"LGA24","RURAL SHORT","Planned","-",2,36,0,0,"NO"]
[null,"2017-06-29",42915.513888888891,"TGN44","RURAL SHORT","Overload","-",1,113,3.8369793125695031E-4,3.3955569137783212E-6,"NO"]
[null,"2017-06-30",42916.568055555559,"WT11","URBAN","Animal","Animal impact",36,291,3.5640896533892193E-2,1.2247730767660548E-4,"NO"]
[null,"2017-07-01",42917.751388888886,"BWN12","URBAN","Animal","Animal impact",1,58,1.9732455125675327E-4,3.402147435461263E-6,"NO"]
[null,"2017-07-02",42918.039583333331,"LLG14","RURAL SHORT","Overload","-",46,58,9.0593458459605602E-3,1.5619561803380277E-4,"NO"]
[null,"2017-07-03",42919.326388888891,"RWN31","RURAL SHORT","Asset Failure","LV",1,88,2.9880900841249225E-4,3.3955569137783212E-6,"NO"]
[null,"2017-07-03",42919.54583333333,"FTR12","RURAL LONG","Asset Failure","LV",1,44,3.6610530519869534E-4,8.3205751181521662E-6,"NO"]
[null,"2017-07-04",42920.324999999997,"SMR3","RURAL LONG","Unknown","Unknown",2,82,1.3645743193769553E-3,1.6641150236304332E-5,"NO"]
[null,"2017-07-04",42920.679861111108,"WGL24","RURAL LONG","Unknown","Unknown",2,0,0,0,"NO"]
[null,"2017-07-05",42921.364583333336,"TGN11","RURAL SHORT","Planned","-",110,315,0,0,"NO"]
[null,"2017-07-05",42921.40625,"WYK12","RURAL SHORT","Planned","-",1,65,0,0,"NO"]
[null,"2017-07-06",42922.336805555555,"SLE32","RURAL SHORT","Planned","-",64,300,0,0,"NO"]
[null,"2017-07-06",42922.385416666664,"TGN11","RURAL SHORT","Planned","-",1,30,0,0,"NO"]
[null,"2017-07-07",42923.378472222219,"BRA21","URBAN","Planned","-",122,196,0,0,"NO"]
[null,"2017-07-07",42923.85665509259,"NLA31","RURAL LONG","Unknown","Unknown",587,0,0,0,"NO"]
[null,"2017-07-09",42925.450995370367,"BWR32","URBAN","Unknown","Unknown",2841,0,0,0,"NO"]
[null,"2017-07-10",42926.375,"LDL13","RURAL SHORT","Planned","-",25,203,0,0,"NO"]
[null,"2017-07-11",42927.366666666669,"WGI14","RURAL SHORT","Asset failure","LV",1,177,6.0101357373876284E-4,3.3955569137783212E-6,"NO"]
[null,"2017-07-11",42927.520138888889,"BGE12","RURAL SHORT","Overload","-",8,261,7.0899228359691344E-3,2.716445531022657E-5,"NO"]
[null,"2017-07-12",42928.376388888886,"UWY1","RURAL SHORT","Planned","-",319,237,0,0,"NO"]
[null,"2017-07-13",42929.354166666664,"NLA32","RURAL SHORT","Planned","-",75,377,0,0,"NO"]
[null,"2017-07-13",42929.378865740742,"BRA24","URBAN","Planned","-",95,28,0,0,"NO"]
[null,"2017-07-14",42930.354166666664,"WOTS11","RURAL LONG","Planned","-",5,92,0,0,"NO"]
[null,"2017-07-15",42931.054166666669,"TGN44","RURAL SHORT","Overload","-",1,427,1.4499028021833431E-3,3.3955569137783212E-6,"NO"]
[null,"2017-07-16",42932.355555555558,"EPG22","URBAN","Planned","-",3,256,0,0,"NO"]
[null,"2017-07-16",42932.505555555559,"WYK24","RURAL SHORT","Other","Other",1,126,4.2784017113606845E-4,3.3955569137783212E-6,"NO"]
[null,"2017-07-17",42933.517361111109,"SMR8","RURAL LONG","Planned","-",3,55,0,0,"NO"]
[null,"2017-07-18",42934.29546296296,"MFA21","RURAL LONG","Unknown","Unknown",521,0,0,0,"NO"]
[null,"2017-07-18",42934.381944444445,"RWT14","URBAN","Planned","-",387,316,0,0,"NO"]
[null,"2017-07-19",42935.334722222222,"CPK13","URBAN","Planned","-",21,189,0,0,"NO"]
[null,"2017-07-19",42935.425694444442,"CYN14","URBAN","Planned","-",117,172,0,0,"NO"]
[null,"2017-07-20",42936.359143518515,"RWT15","URBAN","Other","Other",1,413,1.4050868908455016E-3,3.402147435461263E-6,"NO"]
[null,"2017-07-20",42936.371527777781,"LDL23","RURAL LONG","Vegetation","Grow-in - NSP responsibility",11,251.81818181818181,2.3047993077281503E-2,9.1526326299673836E-5,"NO"]
[null,"2017-07-20",42936.826597222222,"RWT25","RURAL SHORT","Unknown","Unknown",2529,0,0,0,"NO"]
[null,"2017-07-21",42937.35833333333,"SMG32","URBAN","Planned","-",139,249,0,0,"NO"]
[null,"2017-07-21",42937.590277777781,"WYK24","RURAL SHORT","Planned","-",240,27,0,0,"NO"]
[null,"2017-07-22",42938.30641203704,"DRN14","RURAL SHORT","Overload","-",2600,40.830769230769228,0.36047232196670659,8.8284479758236351E-3,"NO"]
[null,"2017-07-22",42938.688194444447,"FGY14","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",303,136.52475247524754,0.14073663296272607,1.0308506729447627E-3,"NO"]
[null,"2017-07-23",42939.643634259257,"LYD13","URBAN","Unknown","Unknown",1218,16.029556650246306,6.6423526529945695E-2,4.1438155763918183E-3,"NO"]
[null,"2017-07-24",42940.385416666664,"DRN22","RURAL SHORT","Planned","-",49,216,0,0,"NO"]
[null,"2017-07-25",42941.293449074074,"SMR8","RURAL LONG","Unknown","Unknown",286,0,0,0,"NO"]
[null,"2017-07-25",42941.525694444441,"CYN21","URBAN","Unknown","Unknown",1,220,7.4847243580147794E-4,3.402147435461263E-6,"NO"]
[null,"2017-07-26",42942.354166666664,"RUBA12","RURAL LONG","Planned","-",19,234,0,0,"NO"]
[null,"2017-07-26",42942.358900462961,"NLA32","RURAL SHORT","Unknown","Unknown",97,0,0,0,"NO"]
[null,"2017-07-26",42942.737754629627,"BDL41","RURAL LONG","Unknown","Unknown",1255,0,0,0,"NO"]
[null,"2017-07-27",42943.392465277779,"ELM33","RURAL SHORT","Planned","-",50,211.7,0,0,"NO"]
[null,"2017-07-27",42943.656944444447,"LDL22","URBAN","Asset failure","LV",1,78,2.6536749996597853E-4,3.402147435461263E-6,"NO"]
[null,"2017-07-28",42944.317361111112,"BN6","RURAL LONG","Unknown","Unknown",77,0,0,0,"NO"]
[null,"2017-07-28",42944.438888888886,"LGA23","RURAL LONG","Planned","-",2,83,0,0,"NO"]
[null,"2017-07-29",42945.293055555558,"OFR23","RURAL LONG","Vegetation","Grow-in - NSP responsibility",14,535,6.2321107634959731E-2,1.1648805165413033E-4,"NO"]
[null,"2017-07-29",42945.499305555553,"FGY34","URBAN","Asset failure","LV",1,418,1.422097628022808E-3,3.402147435461263E-6,"NO"]
[null,"2017-07-30",42946.052627314813,"MJG11","RURAL SHORT","Unknown","Unknown",1365,0,0,0,"NO"]
[null,"2017-07-31",42947.548738425925,"MYT8","RURAL SHORT","Animal","Animal impact",660,8,1.7928540504749534E-2,2.2410675630936917E-3,"NO"]
[null,"2017-08-01",42948.339583333334,"ELM11","URBAN","Planned","-",83,85,0,0,"NO"]
[null,"2017-08-01",42948.388888888891,"WGL24","RURAL LONG","Planned","-",1,45,0,0,"NO"]
[null,"2017-08-02",42949.357638888891,"LYD14","RURAL SHORT","Planned","-",129,343,0,0,"NO"]
[null,"2017-08-02",42949.625,"LLG12","RURAL SHORT","Planned","-",1,32,0,0,"NO"]
[null,"2017-08-03",42950.333333333336,"FTR12","RURAL LONG","Planned","-",117,387,0,0,"NO"]
[null,"2017-08-03",42950.375,"TT9","URBAN","Planned","-",135,380,0,0,"NO"]
[null,"2017-08-03",42950.645057870373,"MSD1","RURAL LONG","Unknown","Unknown",51,0,0,0,"NO"]
[null,"2017-08-03",42950.937372685185,"PHI13","URBAN","Unknown","Unknown",4340,0,0,0,"NO"]
[null,"2017-08-04",42951.375,"BDL8","RURAL LONG","Planned","-",4,72,0,0,"NO"]
[null,"2017-08-05",42952.354861111111,"FTR22","RURAL SHORT","Planned","-",62,99,0,0,"NO"]
[null,"2017-08-06",42953.526701388888,"SMR8","RURAL LONG","Unknown","Unknown",36,0,0,0,"NO"]
[null,"2017-08-06",42953.93472222222,"MYT8","RURAL SHORT","Weather","-",62,84,1.7684060406957497E-2,2.1052452865425592E-4,"NO"]
[null,"2017-08-07",42954.402777777781,"BDL8","RURAL LONG","Planned","-",67,292,0,0,"NO"]
[null,"2017-08-08",42955.368055555555,"WN5","RURAL LONG","Planned","-",22,380,0,0,"NO"]
[null,"2017-08-08",42955.391226851854,"SMR8","RURAL LONG","Planned","-",35,194.14285714285714,0,0,"NO"]
[null,"2017-08-08",42955.859965277778,"PHI12","RURAL SHORT","Unknown","Unknown",3505,0,0,0,"NO"]
[null,"2017-08-09",42956.382638888892,"WN5","RURAL LONG","Planned","-",7,32,0,0,"NO"]
[null,"2017-08-09",42956.53125,"CYN13","URBAN","Other","Other",1,100,3.4021474354612634E-4,3.402147435461263E-6,"NO"]
[null,"2017-08-10",42957.107905092591,"BGE23","URBAN","Unknown","Unknown",1852,0,0,0,"NO"]
[null,"2017-08-10",42957.381944444445,"SLE31","RURAL LONG","Planned","-",7,115,0,0,"NO"]
[null,"2017-08-11",42958.248379629629,"OFR23","RURAL LONG","Unknown","Unknown",31,0,0,0,"NO"]
[null,"2017-08-11",42958.373611111114,"BRA14","URBAN","Planned","-",88,277,0,0,"NO"]
[null,"2017-08-11",42958.503472222219,"SMR8","RURAL LONG","Planned","-",11,40,0,0,"NO"]
[null,"2017-08-12",42959.165347222224,"TGN41","RURAL LONG","Vegetation","Grow-in - NSP responsibility",37,499,0.15362277840644345,3.0786127937163014E-4,"NO"]
[null,"2017-08-13",42960.297222222223,"BWR12","URBAN","Asset failure","LV",1,102,3.4701903841704884E-4,3.402147435461263E-6,"NO"]
[null,"2017-08-14",42961.618055555555,"SMR8","RURAL LONG","Planned","-",1,40,0,0,"NO"]
[null,"2017-08-14",42961.708333333336,"BN4","URBAN","Asset Failure","Distribution substation",104,100,3.5382333328797137E-2,3.5382333328797135E-4,"NO"]
[null,"2017-08-15",42962.386064814818,"NRN14","URBAN","Planned","-",98,145,0,0,"NO"]
[null,"2017-08-16",42963.006944444445,"KLO14","RURAL LONG","Overload","-",1,130,1.0816747653597818E-3,8.3205751181521662E-6,"NO"]
[null,"2017-08-16",42963.334722222222,"LDL14","RURAL SHORT","Other","Other",1,330,1.1205337815468458E-3,3.3955569137783212E-6,"NO"]
[null,"2017-08-16",42963.500694444447,"DRN23","RURAL LONG","Planned","-",46,49,0,0,"NO"]
[null,"2017-08-17",42964.293749999997,"FTR23","RURAL LONG","Animal","Animal impact",31,142,3.6627171670105839E-2,2.5793782866271719E-4,"NO"]
[null,"2017-08-17",42964.427083333336,"WT11","URBAN","Planned","-",110,371,0,0,"NO"]
[null,"2017-08-17",42964.702777777777,"WOTS13","RURAL LONG","Weather","-",5,203,8.4453837449244493E-3,4.1602875590760831E-5,"NO"]
[null,"2017-08-18",42965.333333333336,"LDL14","RURAL SHORT","Planned","-",139,370,0,0,"NO"]
[null,"2017-08-18",42965.411805555559,"LYD11","RURAL SHORT","Planned","-",56,427,0,0,"NO"]
[null,"2017-08-18",42965.821527777778,"MOE31","RURAL LONG","Overload","-",1,61,5.0755508220728213E-4,8.3205751181521662E-6,"NO"]
[null,"2017-08-20",42967.269143518519,"TGN23","RURAL SHORT","Unknown","Unknown",377,0,0,0,"NO"]
[null,"2017-08-21",42968.195497685185,"KLK1","RURAL SHORT","Unknown","Unknown",277,0,0,0,"NO"]
[null,"2017-08-22",42969.354166666664,"LDL14","RURAL SHORT","Planned","-",157,277.24840764331208,0,0,"NO"]
[null,"2017-08-22",42969.435416666667,"CPK11","URBAN","Asset failure","LV",1,431,1.4663255446838044E-3,3.402147435461263E-6,"NO"]
[null,"2017-08-22",42969.543749999997,"WYK23","RURAL SHORT","Asset failure","LV",1,297,1.0084804033921614E-3,3.3955569137783212E-6,"NO"]
[null,"2017-08-23",42970.350694444445,"BGE24","RURAL SHORT","Planned","-",35,455,0,0,"NO"]
[null,"2017-08-23",42970.405555555553,"RWT32","URBAN","Planned","-",135,376,0,0,"NO"]
[null,"2017-08-23",42970.693749999999,"CPK12","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",1,311,1.0560182001850579E-3,3.3955569137783212E-6,"NO"]
[null,"2017-08-24",42971.375798611109,"WGL13","RURAL SHORT","Unknown","Unknown",481,0,0,0,"NO"]
[null,"2017-08-24",42971.857638888891,"KLO14","RURAL LONG","Other","High/Low volt or Tap change",3,0,0,0,"NO"]
[null,"2017-08-25",42972.08011574074,"RWN26","RURAL SHORT","Animal","Animal impact",322,510.60869565217394,0.55828388553577646,1.0933693262366194E-3,"NO"]
[null,"2017-08-25",42972.667361111111,"TGN23","RURAL SHORT","Asset failure","LV",1,89,3.0220456532627059E-4,3.3955569137783212E-6,"NO"]
[null,"2017-08-27",42974.277777777781,"DRN13","RURAL SHORT","Asset failure","LV",1,79,2.6824899618848734E-4,3.3955569137783212E-6,"NO"]
[null,"2017-08-27",42974.48333333333,"MOE22","RURAL LONG","Asset Failure","Distribution substation",14,64,7.455235305864341E-3,1.1648805165413033E-4,"NO"]
[null,"2017-08-28",42975.440972222219,"BDL42","RURAL SHORT","Animal","Animal impact",1,205,6.9608916732455579E-4,3.3955569137783212E-6,"NO"]
[null,"2017-08-28",42975.972488425927,"FTR23","RURAL LONG","Unknown","Unknown",1802,0,0,0,"NO"]
[null,"2017-08-29",42976.392361111109,"BRA31","URBAN","Planned","-",32,325,0,0,"NO"]
[null,"2017-08-29",42976.708333333336,"BWR34","URBAN","Asset failure","LV",70,335,7.978035736156662E-2,2.3815032048228843E-4,"NO"]
[null,"2017-08-30",42977.376388888886,"FGY13","RURAL SHORT","Planned","-",30,258,0,0,"NO"]
[null,"2017-08-30",42977.706944444442,"PHM33","RURAL LONG","Unknown","Unknown",458,0,0,0,"NO"]
[null,"2017-08-31",42978.375,"BGE21","RURAL SHORT","Unknown","Unknown",1,0,0,0,"NO"]
[null,"2017-08-31",42978.465277777781,"LLG13","RURAL SHORT","Planned","-",4,19,0,0,"NO"]
[null,"2017-08-31",42978.910555555558,"LDL23","RURAL LONG","Asset Failure","HV",662,8,4.4065765825733877E-2,5.5082207282167346E-3,"NO"]
[null,"2017-09-01",42979.454861111109,"LDL14","RURAL SHORT","Overload","-",3,59,6.0101357373876284E-4,1.0186670741334963E-5,"NO"]
[null,"2017-09-02",42980.67083333333,"FTR21","RURAL LONG","Asset failure","LV",1,279,2.3214404579644547E-3,8.3205751181521662E-6,"NO"]
[null,"2017-09-03",42981.242025462961,"WYK23","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",188,0,0,0,"NO"]
[null,"2017-09-03",42981.934212962966,"MWT31","RURAL SHORT","Unknown","Unknown",249,0,0,0,"NO"]
[null,"2017-09-04",42982.385416666664,"WT7","URBAN","Planned","-",192,309.32291666666669,0,0,"NO"]
[null,"2017-09-04",42982.650347222225,"LGA14","RURAL LONG","Unknown","Unknown",1526,0,0,0,"NO"]
[null,"2017-09-05",42983.392361111109,"WOTS24","RURAL LONG","Planned","-",4,85,0,0,"NO"]
[null,"2017-09-05",42983.784583333334,"DRN22","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",3774,15.189189189189189,0.19464690452542849,1.2814831792599384E-2,"NO"]
[null,"2017-09-06",42984.399305555555,"RWN31","RURAL SHORT","Planned","-",2,15,0,0,"NO"]
[null,"2017-09-06",42984.489583333336,"MWT14","RURAL SHORT","Overload","-",1,75,2.5466676853337406E-4,3.3955569137783212E-6,"NO"]
[null,"2017-09-07",42985.364583333336,"BRA23","URBAN","Planned","-",60,227,0,0,"NO"]
[null,"2017-09-07",42985.385416666664,"CYN12","URBAN","Planned","-",105,240,0,0,"NO"]
[null,"2017-09-08",42986.354166666664,"FTR23","RURAL LONG","Planned","-",2,62,0,0,"NO"]
[null,"2017-09-08",42986.461805555555,"SMR3","RURAL LONG","Planned","-",2,70,0,0,"NO"]
[null,"2017-09-08",42986.873657407406,"WYK24","RURAL SHORT","Unknown","Unknown",14,0,0,0,"NO"]
[null,"2017-09-10",42988.415277777778,"RUBA22","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",27,674.2962962962963,6.1819509172248113E-2,9.1680036672014671E-5,"NO"]
[null,"2017-09-11",42989.380555555559,"MWT24","RURAL SHORT","Asset Failure","LV",1,68,2.3089787013692585E-4,3.3955569137783212E-6,"NO"]
[null,"2017-09-12",42990.373368055552,"DRN12","RURAL SHORT","Planned","-",21,535,0,0,"NO"]
[null,"2017-09-12",42990.527777777781,"SMR5","RURAL LONG","Planned","-",35,100,0,0,"NO"]
[null,"2017-09-13",42991.335416666669,"RWT32","URBAN","Planned","-",19,385,0,0,"NO"]
[null,"2017-09-13",42991.381944444445,"WOTS24","RURAL LONG","Planned","-",28,305,0,0,"NO"]
[null,"2017-09-13",42991.797222222223,"WGL11","RURAL SHORT","Asset failure","LV",31,277,2.9157647218614444E-2,1.0526226432712796E-4,"NO"]
[null,"2017-09-14",42992.378472222219,"WOTS24","RURAL LONG","Planned","-",24,200,0,0,"NO"]
[null,"2017-09-14",42992.4375,"WOTS24","RURAL LONG","Planned","-",1,300,0,0,"NO"]
[null,"2017-09-15",42993.354861111111,"FTR21","RURAL LONG","Planned","-",3,44,0,0,"NO"]
[null,"2017-09-16",42994.299305555556,"LLG11","RURAL SHORT","Overload","-",3,252,2.5670410268164106E-3,1.0186670741334963E-5,"NO"]
[null,"2017-09-16",42994.30972222222,"LDL23","RURAL LONG","Weather","-",4,269,8.9529388271317317E-3,3.3282300472608665E-5,"NO"]
[null,"2017-09-17",42995.762499999997,"WGI22","RURAL LONG","Animal","Animal impact",12,78,7.788058310590428E-3,9.9846901417825995E-5,"NO"]
[null,"2017-09-18",42996.416666666664,"NLA31","RURAL LONG","Planned","-",31,205,0,0,"NO"]
[null,"2017-09-18",42996.930150462962,"OFR23","RURAL LONG","Vegetation","Blow-in/Fall-in - NSP responsibility",60,896.81666666666672,0.44772182653264991,4.9923450708913E-4,"NO"]
[null,"2017-09-19",42997.354166666664,"CLN13","RURAL SHORT","Planned","-",7,65,0,0,"NO"]
[null,"2017-09-20",42998.334027777775,"ELM31","URBAN","Planned","-",87,165,0,0,"NO"]
[null,"2017-09-20",42998.385416666664,"LLG11","RURAL SHORT","Planned","-",2,23,0,0,"NO"]
[null,"2017-09-20",42998.486111111109,"WGI14","RURAL SHORT","Planned","-",1,35,0,0,"NO"]
[null,"2017-09-21",42999.354861111111,"FTR21","RURAL LONG","Planned","-",88,408,0,0,"NO"]
[null,"2017-09-21",42999.457638888889,"CYN12","URBAN","Asset failure","LV",1,73,2.4835676278867221E-4,3.402147435461263E-6,"NO"]
[null,"2017-09-22",43000.375,"WGI31","RURAL SHORT","Planned","-",2,32,0,0,"NO"]
[null,"2017-09-22",43000.378750000003,"WGL24","RURAL LONG","Planned","-",29,185.24137931034483,0,0,"NO"]
[null,"2017-09-23",43001.710833333331,"LDL13","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",1605,11.494080996884735,6.2641233945382471E-2,5.449868846614205E-3,"NO"]
[null,"2017-09-24",43002.36041666667,"SLE32","RURAL SHORT","Animal","Animal impact",3,156,1.5891206356482542E-3,1.0186670741334963E-5,"NO"]
[null,"2017-09-25",43003.33390046296,"CYN14","URBAN","Planned","-",71,539,0,0,"NO"]
[null,"2017-09-25",43003.404988425929,"MOE14","RURAL SHORT","Vegetation","Grow-in - NSP responsibility",1794,9.5016722408026748,5.7880663152265262E-2,6.0916291033183082E-3,"NO"]
[null,"2017-09-26",43004.334027777775,"WT5","URBAN","Planned","-",433,405,0,0,"NO"]
[null,"2017-09-26",43004.380555555559,"SLE31","RURAL LONG","Planned","-",17,137,0,0,"NO"]
[null,"2017-09-26",43004.779166666667,"WGI14","RURAL SHORT","Asset failure","LV",1,252,8.556803422721369E-4,3.3955569137783212E-6,"NO"]
[null,"2017-09-27",43005.357638888891,"HPK22","URBAN","Planned","-",79,106,0,0,"NO"]
[null,"2017-09-27",43005.569444444445,"SLE31","RURAL LONG","Weather","-",1,200,1.6641150236304334E-3,8.3205751181521662E-6,"NO"]
[null,"2017-09-28",43006.377083333333,"MSD4","RURAL LONG","Planned","-",59,209.23728813559322,0,0,"NO"]
[null,"2017-09-28",43006.5,"WGI14","RURAL SHORT","Planned","-",1,15,0,0,"NO"]
[null,"2017-09-29",43007.76935185185,"LLG11","RURAL SHORT","Unknown","Unknown",221,0,0,0,"NO"]
[null,"2017-09-30",43008.757638888892,"MOE32","RURAL SHORT","Asset Failure","LV",1,77,2.6145788236093073E-4,3.3955569137783212E-6,"NO"]
[null,"2017-10-01",43009.786805555559,"CLN22","RURAL SHORT","Unknown","Unknown",4,77,1.0458315294437229E-3,1.3582227655113285E-5,"NO"]
[null,"2017-10-02",43010.693749999999,"NLA32","RURAL SHORT","Other","Poor Work Practice",1,166,5.6366244768720126E-4,3.3955569137783212E-6,"NO"]
[null,"2017-10-03",43011.362500000003,"NRN14","URBAN","Planned","-",7,323,0,0,"NO"]
[null,"2017-10-03",43011.397916666669,"ELM11","URBAN","Planned","-",11,63,0,0,"NO"]
[null,"2017-10-04",43012.1172337963,"CYN13","URBAN","Unknown","Unknown",1084,0,0,0,"NO"]
[null,"2017-10-04",43012.384027777778,"EPG13","RURAL SHORT","Other","Other",1,657,2.2308808923523571E-3,3.3955569137783212E-6,"NO"]
[null,"2017-10-05",43013.358252314814,"LDL22","URBAN","Planned","-",67,287,0,0,"NO"]
[null,"2017-10-05",43013.458333333336,"PHI11","RURAL SHORT","Planned","-",2,90,0,0,"NO"]
[null,"2017-10-05",43013.793055555558,"SLE31","RURAL LONG","Animal","Animal impact",1,88,7.3221061039739068E-4,8.3205751181521662E-6,"NO"]
[null,"2017-10-06",43014.376388888886,"WOTS24","RURAL LONG","Planned","-",64,223,0,0,"NO"]
[null,"2017-10-06",43014.823611111111,"SMR3","RURAL LONG","Unknown","Unknown",1,84,6.9892830992478205E-4,8.3205751181521662E-6,"NO"]
[null,"2017-10-07",43015.53402777778,"SMR8","RURAL LONG","Asset failure","LV",1,189,1.5725886973307595E-3,8.3205751181521662E-6,"NO"]
[null,"2017-10-08",43016.718252314815,"KLK1","RURAL SHORT","Unknown","Unknown",537,0,0,0,"NO"]
[null,"2017-10-09",43017.354166666664,"SMR1","RURAL SHORT","Planned","-",2,105,0,0,"NO"]
[null,"2017-10-09",43017.361111111109,"CYN14","URBAN","Planned","-",77,315,0,0,"NO"]
[null,"2017-10-09",43017.477777777778,"PHM33","RURAL LONG","Animal","Animal impact",4,82,2.7291486387539107E-3,3.3282300472608665E-5,"NO"]
[null,"2017-10-10",43018.404861111114,"BWN14","RURAL SHORT","Other","High/Low volt or Tap change",2,2,1.3582227655113285E-5,6.7911138275566425E-6,"NO"]
[null,"2017-10-10",43018.463888888888,"WGL21","RURAL LONG","Weather","-",1,112,9.3190441323304262E-4,8.3205751181521662E-6,"NO"]
[null,"2017-10-11",43019.35833333333,"BDL4","RURAL SHORT","Animal","Animal impact",1,39,1.3242671963735453E-4,3.3955569137783212E-6,"NO"]
[null,"2017-10-11",43019.384027777778,"BWN13","URBAN","Asset failure","LV",1,74,2.5175891022413346E-4,3.402147435461263E-6,"NO"]
[null,"2017-10-11",43019.5625,"BDL4","RURAL SHORT","Planned","-",1,90,0,0,"NO"]
[null,"2017-10-12",43020.296527777777,"BWR24","URBAN","Animal","Animal impact",3,103,1.0512635575575303E-3,1.020644230638379E-5,"NO"]
[null,"2017-10-12",43020.364247685182,"SMR3","RURAL LONG","Planned","-",491,397.05498981670058,0,0,"NO"]
[null,"2017-10-12",43020.459027777775,"WGI33","RURAL SHORT","Asset Failure","Distribution substation",4,159,2.1595741971630121E-3,1.3582227655113285E-5,"NO"]
[null,"2017-10-13",43021.407638888886,"FTR21","RURAL LONG","Planned","-",32,333,0,0,"NO"]
[null,"2017-10-14",43022.342361111114,"WOTS25","RURAL SHORT","Planned","-",192,4.557291666666667,0,0,"NO"]
[null,"2017-10-14",43022.365972222222,"WGL23","RURAL SHORT","Asset failure","LV",1,164,5.568713338596447E-4,3.3955569137783212E-6,"NO"]
[null,"2017-10-15",43023.765300925923,"SMR3","RURAL LONG","Animal","Animal impact",14,7,8.1541636157891233E-4,1.1648805165413033E-4,"NO"]
[null,"2017-10-16",43024.409722222219,"WGL12","RURAL LONG","Planned","-",23,160,0,0,"NO"]
[null,"2017-10-16",43024.765972222223,"WGL12","RURAL LONG","Unknown","Unknown",1,149,1.2397656926046729E-3,8.3205751181521662E-6,"NO"]
[null,"2017-10-17",43025.381944444445,"ELM15","RURAL SHORT","Planned","-",16,300,0,0,"NO"]
[null,"2017-10-17",43025.5625,"RWT22","URBAN","Planned","-",86,75,0,0,"NO"]
[null,"2017-10-18",43026.287499999999,"MYT2","RURAL SHORT","Animal","Animal impact",197,97,6.4885697065389936E-2,6.6892471201432922E-4,"NO"]
[null,"2017-10-18",43026.427083333336,"LLG13","RURAL SHORT","Planned","-",2,23,0,0,"NO"]
[null,"2017-10-19",43027.368055555555,"MOE22","RURAL LONG","Planned","-",31,234,0,0,"NO"]
[null,"2017-10-19",43027.57708333333,"WOTS11","RURAL LONG","Animal","Animal impact",1,74,6.1572255874326029E-4,8.3205751181521662E-6,"NO"]
[null,"2017-10-20",43028.355555555558,"BDL4","RURAL SHORT","Planned","-",49,357,0,0,"NO"]
[null,"2017-10-20",43028.406944444447,"MSD4","RURAL LONG","Planned","-",6,159,0,0,"NO"]
[null,"2017-10-20",43028.571527777778,"OFR23","RURAL LONG","Planned","-",44,20,0,0,"NO"]
[null,"2017-10-23",43031.008715277778,"BGE23","URBAN","Unknown","Unknown",1852,0,0,0,"NO"]
[null,"2017-10-23",43031.400694444441,"MOE14","RURAL SHORT","Planned","-",42,163,0,0,"NO"]
[null,"2017-10-23",43031.600694444445,"WN3","RURAL LONG","Planned","-",2,36,0,0,"NO"]
[null,"2017-10-24",43032.355509259258,"LGA23","RURAL LONG","Unknown","Unknown",617,0,0,0,"NO"]
[null,"2017-10-24",43032.381944444445,"SMR1","RURAL SHORT","Planned","-",1,40,0,0,"NO"]
[null,"2017-10-24",43032.51321759259,"WN3","RURAL LONG","Planned","-",676,1.3550295857988166,0,0,"NO"]
[null,"2017-10-25",43033.364583333336,"TGN31","RURAL LONG","Planned","-",32,415,0,0,"NO"]
[null,"2017-10-25",43033.444444444445,"WYK23","RURAL SHORT","Asset failure","HV",3,105,1.069600427840171E-3,1.0186670741334963E-5,"NO"]
[null,"2017-10-25",43033.5625,"MYT7","RURAL LONG","Planned","-",1,25,0,0,"NO"]
[null,"2017-10-26",43034.309351851851,"BRT11","RURAL SHORT","Unknown","Unknown",302,0,0,0,"NO"]
[null,"2017-10-26",43034.390277777777,"MWT34","RURAL SHORT","Planned","-",149,323,0,0,"NO"]
[null,"2017-10-26",43034.470138888886,"CLN13","RURAL SHORT","Third Party","Unauthorised access",1,60,2.0373341482669927E-4,3.3955569137783212E-6,"NO"]
[null,"2017-10-27",43035.117245370369,"WYK24","RURAL SHORT","Unknown","Unknown",630,0,0,0,"NO"]
[null,"2017-10-27",43035.390972222223,"FTR21","RURAL LONG","Planned","-",2,113,0,0,"NO"]
[null,"2017-10-28",43036.167361111111,"PHI11","RURAL SHORT","Unknown","Unknown",13,167,7.371754059812735E-3,4.4142239879118175E-5,"NO"]
[null,"2017-10-28",43036.368055555555,"LLG11","RURAL SHORT","Animal","Animal impact",2,107,7.266491795485607E-4,6.7911138275566425E-6,"NO"]
[null,"2017-10-28",43036.780046296299,"RUBA22","RURAL SHORT","Unknown","Unknown",497,0,0,0,"NO"]
[null,"2017-10-29",43037.302581018521,"SMR5","RURAL LONG","Unknown","Unknown",535,0,0,0,"NO"]
[null,"2017-10-29",43037.582638888889,"MSD2","RURAL LONG","Weather","-",3,0,0,0,"NO"]
[null,"2017-10-30",43038.361724537041,"LDL21","RURAL SHORT","Planned","-",735,460.21768707482994,0,0,"NO"]
[null,"2017-10-30",43038.392361111109,"WT7","URBAN","Planned","-",111,310,0,0,"NO"]
[null,"2017-10-30",43038.631249999999,"NLA31","RURAL LONG","Animal","Animal impact",1,196,1.6308327231578247E-3,8.3205751181521662E-6,"NO"]
[null,"2017-10-30",43038.74559027778,"NLA32","RURAL SHORT","Unknown","Unknown",1435,0,0,0,"NO"]
[null,"2017-10-31",43039.357499999998,"OFR23","RURAL LONG","Planned","-",89,2.6853932584269664,0,0,"NO"]
[null,"2017-10-31",43039.451909722222,"FTR12","RURAL LONG","Unknown","Unknown",325,0,0,0,"NO"]
[null,"2017-11-01",43040.375,"CYN31","URBAN","Planned","-",163,350,0,0,"NO"]
[null,"2017-11-01",43040.37777777778,"WN5","RURAL LONG","Planned","-",1,44,0,0,"NO"]
[null,"2017-11-02",43041.197916666664,"LDL23","RURAL LONG","Asset Failure","LV",1,390,3.2450242960793451E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-02",43041.388888888891,"SMR4","RURAL SHORT","Planned","-",1,35,0,0,"NO"]
[null,"2017-11-02",43041.479166666664,"SLE31","RURAL LONG","Planned","-",1,150,0,0,"NO"]
[null,"2017-11-02",43041.862500000003,"MWT31","RURAL SHORT","Animal","Animal impact",2,60,4.0746682965339854E-4,6.7911138275566425E-6,"NO"]
[null,"2017-11-03",43042.395833333336,"PHI13","URBAN","Planned","-",1,45,0,0,"NO"]
[null,"2017-11-03",43042.482638888891,"MSD2","RURAL LONG","Unknown","Unknown",3,10,2.49617253544565E-4,2.4961725354456499E-5,"NO"]
[null,"2017-11-04",43043.32708333333,"FGY23","URBAN","Overload","-",1,92,3.1299756406243622E-4,3.402147435461263E-6,"NO"]
[null,"2017-11-05",43044.8125,"FTR12","RURAL LONG","Animal","Animal impact",1,405,3.3698329228516277E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-07",43046.733425925922,"WOTS13","RURAL LONG","Unknown","Unknown",558,0,0,0,"NO"]
[null,"2017-11-08",43047.354166666664,"WO31","URBAN","Planned","-",3,240,0,0,"NO"]
[null,"2017-11-08",43047.465277777781,"BDL44","RURAL LONG","Planned","-",1,296,0,0,"NO"]
[null,"2017-11-08",43047.946527777778,"LLG13","RURAL SHORT","Asset failure","LV",1,104,3.531379190329454E-4,3.3955569137783212E-6,"NO"]
[null,"2017-11-09",43048.381944444445,"HPK24","URBAN","Planned","-",92,80,0,0,"NO"]
[null,"2017-11-09",43048.879166666666,"BWR13","URBAN","Asset failure","LV",1,82,2.7897608970782359E-4,3.402147435461263E-6,"NO"]
[null,"2017-11-10",43049.336805555555,"WYK24","RURAL SHORT","Planned","-",227,417.95154185022028,0,0,"NO"]
[null,"2017-11-10",43049.654861111114,"MOE13","RURAL SHORT","Asset failure","LV",1,62,2.1052452865425592E-4,3.3955569137783212E-6,"NO"]
[null,"2017-11-10",43049.663194444445,"TGN43","RURAL SHORT","Unknown","Unknown",1,50,1.6977784568891606E-4,3.3955569137783212E-6,"NO"]
[null,"2017-11-11",43050.888194444444,"WGL24","RURAL LONG","Animal","Animal impact",13,96,1.0384077747453905E-2,1.0816747653597817E-4,"NO"]
[null,"2017-11-13",43052.409722222219,"WN4","RURAL SHORT","Planned","-",126,115,0,0,"NO"]
[null,"2017-11-13",43052.904861111114,"CYN23","URBAN","Asset failure","LV",1,65,2.2113958330498211E-4,3.402147435461263E-6,"NO"]
[null,"2017-11-14",43053.368750000001,"RWN26","RURAL SHORT","Planned","-",28,294,0,0,"NO"]
[null,"2017-11-14",43053.400185185186,"BDL8","RURAL LONG","Planned","-",61,243.91803278688525,0,0,"NO"]
[null,"2017-11-14",43053.77847222222,"WOTS13","RURAL LONG","Animal","Animal impact",1,79,6.5732543433402117E-4,8.3205751181521662E-6,"NO"]
[null,"2017-11-15",43054.333333333336,"RWT15","URBAN","Planned","-",88,585,0,0,"NO"]
[null,"2017-11-15",43054.400000000001,"WN6","RURAL LONG","Animal","Animal impact",31,309,7.9702789056779605E-2,2.5793782866271719E-4,"NO"]
[null,"2017-11-15",43054.902777777781,"WOTS24","RURAL LONG","Weather","-",1,165,1.3728948944951075E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-16",43055.364583333336,"SLE31","RURAL LONG","Planned","-",9,250,0,0,"NO"]
[null,"2017-11-16",43055.368715277778,"BDL2","RURAL SHORT","Planned","-",44,305,0,0,"NO"]
[null,"2017-11-16",43055.52857638889,"BDL44","RURAL LONG","Unknown","Unknown",1176,0,0,0,"NO"]
[null,"2017-11-16",43055.753472222219,"DRN12","RURAL SHORT","Overload","-",1,1247,4.2342594714815662E-3,3.3955569137783212E-6,"NO"]
[null,"2017-11-16",43055.872314814813,"WGL21","RURAL LONG","Unknown","Unknown",12,0,0,0,"NO"]
[null,"2017-11-17",43056.316666666666,"MWT22","RURAL SHORT","Animal","Animal impact",7,134,3.185032385124065E-3,2.3768898396448248E-5,"NO"]
[null,"2017-11-17",43056.45208333333,"BRA23","URBAN","Unknown","Unknown",1,125,4.2526842943265791E-4,3.402147435461263E-6,"NO"]
[null,"2017-11-17",43056.571192129632,"BDL44","RURAL LONG","Unknown","Unknown",318,0,0,0,"NO"]
[null,"2017-11-17",43056.674305555556,"BDL8","RURAL LONG","Weather","-",1,104,8.6533981228782534E-4,8.3205751181521662E-6,"NO"]
[null,"2017-11-17",43056.703472222223,"MFA22","RURAL LONG","Weather","-",3,0,0,0,"NO"]
[null,"2017-11-18",43057.163888888892,"WGL12","RURAL LONG","Weather","-",1,517,4.3017373360846704E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-18",43057.627442129633,"RUBA22","RURAL SHORT","Unknown","Unknown",1233,0,0,0,"NO"]
[null,"2017-11-18",43057.679131944446,"WYK12","RURAL SHORT","Unknown","Unknown",488,0,0,0,"NO"]
[null,"2017-11-20",43059.159722222219,"BRA33","URBAN","Animal","Animal impact",55,74,1.3846740062327341E-2,1.8711810895036948E-4,"NO"]
[null,"2017-11-20",43059.46875,"MFA31","RURAL SHORT","Planned","-",1,20,0,0,"NO"]
[null,"2017-11-21",43060.166817129626,"SMR8","RURAL LONG","Unknown","Unknown",1672,0,0,0,"NO"]
[null,"2017-11-21",43060.361111111109,"BDL4","RURAL SHORT","Planned","-",1,170,0,0,"NO"]
[null,"2017-11-21",43060.425000000003,"RWN24","URBAN","Overload","-",34,5,5.7836506402841469E-4,1.1567301280568295E-4,"NO"]
[null,"2017-11-21",43060.578657407408,"WGL11","RURAL SHORT","Unknown","Unknown",1159,0,0,0,"NO"]
[null,"2017-11-22",43061.263194444444,"WOTS13","RURAL LONG","Animal","Animal impact",1,170,1.4144977700858684E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-22",43061.392361111109,"KMS1","RURAL SHORT","Planned","-",3,125,0,0,"NO"]
[null,"2017-11-22",43061.75,"TGN11","RURAL SHORT","Animal","Animal impact",48,85,1.385387220821555E-2,1.6298673186135941E-4,"NO"]
[null,"2017-11-23",43062.3753125,"FTR21","RURAL LONG","Planned","-",30,334.26666666666665,0,0,"NO"]
[null,"2017-11-23",43062.506215277775,"CYN24","URBAN","Network business","Switching and protection error",1261,18,7.7221942490099754E-2,4.2901079161166526E-3,"NO"]
[null,"2017-11-23",43062.540972222225,"LDL13","RURAL SHORT","Other","High/Low volt or Tap change",1,97,3.2936902063649716E-4,3.3955569137783212E-6,"NO"]
[null,"2017-11-24",43063.09747685185,"OFR23","RURAL LONG","Unknown","Unknown",4225,0,0,0,"NO"]
[null,"2017-11-24",43063.361111111109,"CYN21","URBAN","Planned","-",61,365,0,0,"NO"]
[null,"2017-11-24",43063.521527777775,"KLO14","RURAL LONG","Unknown","Unknown",1,369,3.0702922185981496E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-24",43063.809027777781,"SLE31","RURAL LONG","Weather","-",1,175,1.4561006456766292E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-24",43063.864583333336,"RWN22","URBAN","Weather","-",43,1080,0.15799572690282107,1.4629233972483432E-4,"NO"]
[null,"2017-11-25",43064.392361111109,"BWN12","URBAN","Planned","-",1,1730,0,0,"NO"]
[null,"2017-11-25",43064.765821759262,"PHI12","RURAL SHORT","Unknown","Unknown",4541,0,0,0,"NO"]
[null,"2017-11-25",43064.824780092589,"LGA13","RURAL LONG","Weather","-",1,1202,1.0001331292018904E-2,8.3205751181521662E-6,"NO"]
[null,"2017-11-25",43064.970138888886,"RUBA12","RURAL LONG","Weather","-",1,693,5.7661585568794518E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-26",43065.339583333334,"SFS1","RURAL SHORT","Vegetation","Blow-in/Fall-in - NSP responsibility",31,270,2.8420811368324549E-2,1.0526226432712796E-4,"NO"]
[null,"2017-11-26",43065.631944444445,"LGA22","RURAL SHORT","Weather","-",1,145,4.9235575249785655E-4,3.3955569137783212E-6,"NO"]
[null,"2017-11-26",43065.958078703705,"BN6","RURAL LONG","Unknown","Unknown",716,0,0,0,"NO"]
[null,"2017-11-27",43066.301388888889,"RUBA12","RURAL LONG","Overload","-",1,229,1.9054117020568461E-3,8.3205751181521662E-6,"NO"]
[null,"2017-11-27",43066.458333333336,"WT15","URBAN","Planned","-",803,180,0,0,"NO"]
[null,"2017-11-28",43067.357638888891,"CRE31","RURAL SHORT","Planned","-",107,424,0,0,"NO"]
[null,"2017-11-28",43067.532638888886,"WOTS13","RURAL LONG","Overload","-",1,68,5.6579910803434739E-4,8.3205751181521662E-6,"NO"]
[null,"2017-11-28",43067.854166666664,"LGA23","RURAL LONG","Animal","Animal impact",1,12,9.9846901417825995E-5,8.3205751181521662E-6,"NO"]
[null,"2017-11-29",43068.393055555556,"WN1","URBAN","Planned","-",45,254,0,0,"NO"]
[null,"2017-11-29",43068.6090625,"DRN11","RURAL SHORT","Unknown","Unknown",4170,43.610071942446041,0.6174956069982428,1.4159472330455598E-2,"NO"]
[null,"2017-11-29",43068.788888888892,"OFR23","RURAL LONG","Overload","-",26,145,3.1368568195433669E-2,2.1633495307195634E-4,"NO"]
[null,"2017-11-30",43069.344918981478,"MYT7","RURAL LONG","Planned","-",256,449,0,0,"NO"]
[null,"2017-11-30",43069.68472222222,"WOTS24","RURAL LONG","Asset Failure","LV",2,84,1.3978566198495641E-3,1.6641150236304332E-5,"NO"]
[null,"2017-11-30",43069.76458333333,"FTR21","RURAL LONG","Weather","-",1,174,1.4477800705584771E-3,8.3205751181521662E-6,"NO"]
[null,"2017-12-01",43070.282349537039,"SMR5","RURAL LONG","Unknown","Unknown",541,0,0,0,"NO"]
[null,"2017-12-01",43070.53125,"TGN41","RURAL LONG","Weather","-",1,120,9.9846901417826E-4,8.3205751181521662E-6,"NO"]
[null,"2017-12-02",43071.237395833334,"WGL24","RURAL LONG","Unknown","Unknown",241,0,0,0,"NO"]
[null,"2017-12-02",43071.717442129629,"WOTS13","RURAL LONG","Unknown","Unknown",36,0,0,0,"NO"]
[null,"2017-12-02",43071.899988425925,"RUBA12","RURAL LONG","Unknown","Unknown",471,0,0,0,"NO"]
[null,"2017-12-03",43072.379363425927,"TGN31","RURAL LONG","Vegetation","Grow-in - NSP responsibility",260,159,0.34397257538441056,2.1633495307195635E-3,"NO"]
[null,"2017-12-03",43072.796527777777,"TGN31","RURAL LONG","Animal","Animal impact",4,103,3.4280769486786928E-3,3.3282300472608665E-5,"NO"]
[null,"2017-12-04",43073.276388888888,"FTR12","RURAL LONG","Animal","Animal impact",2,107,1.7806030752845637E-3,1.6641150236304332E-5,"NO"]
[null,"2017-12-04",43073.500694444447,"WN5","RURAL LONG","Planned","-",1,29,0,0,"NO"]
[null,"2017-12-04",43073.941666666666,"BGE23","URBAN","Animal","Animal impact",2,879,5.9809751915409007E-3,6.8042948709225261E-6,"NO"]
[null,"2017-12-05",43074.382638888892,"WT15","URBAN","Planned","-",61,301,0,0,"NO"]
[null,"2017-12-05",43074.649548611109,"MSD1","RURAL LONG","Unknown","Unknown",52,0,0,0,"NO"]
[null,"2017-12-06",43075.364583333336,"BWA22","RURAL LONG","Planned","-",19,325,0,0,"NO"]
[null,"2017-12-06",43075.416666666664,"HPK21","RURAL SHORT","Planned","-",18,170,0,0,"NO"]
[null,"2017-12-07",43076.11445601852,"SMR2","RURAL SHORT","Unknown","Unknown",2690,0,0,0,"NO"]
[null,"2017-12-07",43076.359479166669,"DRN21","RURAL SHORT","Unknown","Unknown",4441,0,0,0,"NO"]
[null,"2017-12-07",43076.426724537036,"ELM12","RURAL SHORT","Unknown","Unknown",1,25,8.4888922844458028E-5,3.3955569137783212E-6,"NO"]
[null,"2017-12-07",43076.898611111108,"OFR23","RURAL LONG","Asset Failure","LV",1,117,9.735072888238035E-4,8.3205751181521662E-6,"NO"]
[null,"2017-12-08",43077.236111111109,"LLG12","RURAL SHORT","Animal","Animal impact",2,226,1.5347917250278012E-3,6.7911138275566425E-6,"NO"]
[null,"2017-12-08",43077.378472222219,"HPK21","RURAL SHORT","Planned","-",228,185,0,0,"NO"]
[null,"2017-12-09",43078.24722222222,"SLE32","RURAL SHORT","Animal","Animal impact",7,244,5.7996112087333723E-3,2.3768898396448248E-5,"NO"]
[null,"2017-12-09",43078.253576388888,"MYT7","RURAL LONG","Unknown","Unknown",325,0,0,0,"NO"]
[null,"2017-12-10",43079.159328703703,"WYK12","RURAL SHORT","Animal","Animal impact",39,80,1.0594137570988362E-2,1.3242671963735453E-4,"NO"]
[null,"2017-12-11",43080.380486111113,"WGL12","RURAL LONG","Unknown","Unknown",228,0,0,0,"NO"]
[null,"2017-12-11",43080.746527777781,"TT6","URBAN","Asset failure","LV",50,60,1.0206442306383789E-2,1.7010737177306317E-4,"NO"]
[null,"2017-12-12",43081.344444444447,"BWR32","URBAN","Planned","-",313,427,0,0,"NO"]
[null,"2017-12-12",43081.429861111108,"LGA11","RURAL LONG","Planned","-",1,53,0,0,"NO"]
[null,"2017-12-13",43082,"CLN13","RURAL SHORT","Planned","-",144,797,0,0,"NO"]
[null,"2017-12-13",43082.322916666664,"TGN31","RURAL LONG","Planned","-",564,286.46276595744683,0,0,"NO"]
[null,"2017-12-13",43082.395833333336,"BDL44","RURAL LONG","Planned","-",18,489,0,0,"NO"]
[null,"2017-12-13",43082.790277777778,"WN1","URBAN","Overload","-",5,202,3.4361689098158757E-3,1.7010737177306314E-5,"NO"]
[null,"2017-12-14",43083.357638888891,"BDL6","RURAL SHORT","Planned","-",38,325,0,0,"NO"]
[null,"2017-12-14",43083.361111111109,"WN5","RURAL LONG","Planned","-",3,50,0,0,"NO"]
[null,"2017-12-14",43083.53125,"WN6","RURAL LONG","Planned","-",2,20,0,0,"NO"]
[null,"2017-12-15",43084.125520833331,"BWR23","URBAN","Unknown","Unknown",3641,0,0,0,"NO"]
[null,"2017-12-15",43084.468055555553,"MWT31","RURAL SHORT","Other","High/Low volt or Tap change",2,10,6.791113827556642E-5,6.7911138275566425E-6,"NO"]
[null,"2017-12-15",43084.907638888886,"RWT36","URBAN","Unknown","Unknown",633,77.266982622432863,0.16639903106841039,2.1535593266469796E-3,"NO"]
[null,"2017-12-16",43085.793055555558,"BRA14","URBAN","Other","Poor Work Practice",1,97,3.3000830123974253E-4,3.402147435461263E-6,"NO"]
[null,"2017-12-17",43086.8125,"ELM31","URBAN","Overload","-",82,96,2.6781704611951063E-2,2.7897608970782359E-4,"NO"]
[null,"2017-12-18",43087.070138888892,"CLN22","RURAL SHORT","Animal","Animal impact",70,41,9.7452483425437813E-3,2.3768898396448246E-4,"NO"]
[null,"2017-12-18",43087.395833333336,"WYK24","RURAL SHORT","Unknown","Unknown",1,150,5.0933353706674811E-4,3.3955569137783212E-6,"NO"]
[null,"2017-12-19",43088.196643518517,"WYK12","RURAL SHORT","Animal","Animal impact",236,5,4.0067571582584191E-3,8.0135143165168375E-4,"YES"]
[null,"2017-12-19",43088.333333333336,"FGY33","URBAN","Planned","-",46,510,0,0,"YES"]
[null,"2017-12-19",43088.694965277777,"KLO14","RURAL LONG","Weather","-",1280,105.06796875000001,1.1190091859149305,1.0650336151234773E-2,"YES"]
[null,"2017-12-19",43088.710416666669,"WGI23","RURAL SHORT","Weather","-",3,132,1.3446405378562151E-3,1.0186670741334963E-5,"YES"]
[null,"2017-12-19",43088.76458333333,"RWN34","RURAL SHORT","Unknown","Unknown",1,176,5.976180168249845E-4,3.3955569137783212E-6,"YES"]
[null,"2017-12-19",43088.798784722225,"BN4","URBAN","Weather","-",2332,395.03602058319041,3.1341398690853666,7.9338078194956651E-3,"YES"]
[null,"2017-12-19",43088.804803240739,"RUBA12","RURAL LONG","Weather","-",373,555,1.7224838580842707,3.1035745190707582E-3,"YES"]
[null,"2017-12-19",43088.81554398148,"DRN22","RURAL SHORT","Weather","-",43,1560.1395348837209,0.22779433111773245,1.4600894729246782E-4,"YES"]
[null,"2017-12-19",43088.820127314815,"DRN23","RURAL LONG","Unknown","Unknown",1890,0,0,0,"YES"]
[null,"2017-12-19",43088.875543981485,"FTR23","RURAL LONG","Weather","-",2572,2,4.2801038407774744E-2,2.1400519203887372E-2,"YES"]
[null,"2017-12-19",43088.94222222222,"BN1","RURAL LONG","Unknown","Unknown",32,0,0,0,"YES"]
[null,"2017-12-20",43089.100844907407,"DRN23","RURAL LONG","Unknown","Unknown",936,0,0,0,"NO"]
[null,"2017-12-20",43089.302083333336,"MWT13","RURAL SHORT","Weather","-",1,104,3.531379190329454E-4,3.3955569137783212E-6,"NO"]
[null,"2017-12-20",43089.356944444444,"KLO24","RURAL SHORT","Overload","-",2,1786,1.2128929296016163E-2,6.7911138275566425E-6,"NO"]
[null,"2017-12-20",43089.458333333336,"LLG14","RURAL SHORT","Weather","-",2,220,1.4940450420624612E-3,6.7911138275566425E-6,"NO"]
[null,"2017-12-20",43089.783414351848,"NLA31","RURAL LONG","Overload","-",1,70,5.8244025827065165E-4,8.3205751181521662E-6,"NO"]
[null,"2017-12-21",43090.209722222222,"DRN23","RURAL LONG","Weather","-",1,425,3.5362444252146708E-3,8.3205751181521662E-6,"NO"]
[null,"2017-12-21",43090.405555555553,"WT6","URBAN","Unknown","Unknown",1,60,2.041288461276758E-4,3.402147435461263E-6,"NO"]
[null,"2017-12-21",43090.779039351852,"MYT7","RURAL LONG","Unknown","Unknown",59,0,0,0,"NO"]
[null,"2017-12-21",43090.940115740741,"DRN22","RURAL SHORT","Unknown","Unknown",44,0,0,0,"NO"]
[null,"2017-12-22",43091.555555555555,"WN5","RURAL LONG","Vegetation","Blow-in/Fall-in - NSP responsibility",3,45,1.1232776409505424E-3,2.4961725354456499E-5,"NO"]
[null,"2017-12-23",43092.660416666666,"MFA22","RURAL LONG","Overload","-",1,70,5.8244025827065165E-4,8.3205751181521662E-6,"NO"]
[null,"2017-12-23",43092.818055555559,"BDL44","RURAL LONG","Other","Cause Not In List",2,1164,1.9370298875058246E-2,1.6641150236304332E-5,"NO"]
[null,"2017-12-26",43095.163888888892,"WN4","RURAL SHORT","Asset failure","HV",2,0,0,0,"NO"]
[null,"2017-12-26",43095.761111111111,"WN6","RURAL LONG","Vegetation","Grow-in - NSP responsibility",1,7,5.8244025827065164E-5,8.3205751181521662E-6,"NO"]
[null,"2017-12-27",43096.737662037034,"MOE31","RURAL LONG","Unknown","Unknown",267,0,0,0,"NO"]
[null,"2017-12-28",43097.506944444445,"WN5","RURAL LONG","Other","High/Low volt or Tap change",2,5,8.3205751181521662E-5,1.6641150236304332E-5,"NO"]
[null,"2017-12-28",43097.888194444444,"MFA21","RURAL LONG","Weather","-",17,129,1.8247021234107701E-2,1.4144977700858685E-4,"NO"]
[null,"2017-12-29",43098.395833333336,"PHM33","RURAL LONG","Other","Other",1,180,1.4977035212673899E-3,8.3205751181521662E-6,"NO"]
[null,"2017-12-29",43098.898587962962,"RWN34","RURAL SHORT","Unknown","Unknown",2097,0,0,0,"NO"]
[null,"2017-12-30",43099.490925925929,"LLG13","RURAL SHORT","Unknown","Unknown",222,0,0,0,"NO"]
[null,"2017-12-31",43100.576388888891,"MFA21","RURAL LONG","Weather","-",1,0,0,0,"NO"]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]

{"sheet":"Amendments","index":25,"n_rows":3,"n_cols":4,"rows_kept":3,"cut":false,"hidden":false,"merged":[[1,1,1,3]]}
[null,"This sheet may be used to identify amendments made to data resubmitted to the AER."]
[null,"NSP data amendments"]
[null,"Worksheet","Table","Comments"]

{"sheet":"unlocked","index":26,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}