## Instructions
Electricity Distribution Network Service Provider
Annual Reporting RIN
This template is to be used by Ausgrid to fulfil its reporting obligations to the AER.
INSTRUCTIONS
GENERAL | Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting.
CONFIDENTIAL INFORMATION | Please use the macro at the top of each worksheet to identify confidential information in the confidential workbook.
-Do this by selecting the cell or cells that contain confidential information and then run the Mark selection as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential. -To reverse this, select the cell or cells and run the Return selection to NON-CONFIDENTIAL macro.
RESPONSES | Please return four (4) files to the AER: 1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 2. An actual and an estimate version with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response. Use the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public.
AMENDMENTS | If an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. NSPs must identify the reason for the amendments in the Amendment Reason box on the Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. .
NSP may use Amended Data macro to highlight cells that contain amended data. NB: if data is also CONFIDENTIAL, re-apply the Confidentiality macro after applying the Amended macro
Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER
UNITS OF MEASURE | All amounts are to be unrounded and reported on a one for one basis: that is 1000 is to be entered as '1000'. Applicable units of measure may be identified in the table column headings or row descriptors.
INPUT / NON-INPUT CELLS
Yellow = Input cell (mandatory)
Darker yellow = input cell (mandatory)
Orange = input cell (if data available)
Grey = Not applicable/No inputs required
PLEASE DO NOT ENTER TEXT into cells that are to contain numeric data.
NAVIGATION | Many tables in the worksheets have been "grouped" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin (for Row groupings) or above the columns (for column groupings).

## Business & other details
CATEGORY ANALYSIS
Ausgrid
2016-17
BUSINESS & OTHER DETAILS
INSTRUCTIONS
Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells.
SUBMISSION PARTICULARS INPUT SHEET
ENTITY DETAILS
Business Name
| Short name |  |  | Ausgrid
| ACN/ABN |  |  | 67505337385
| Business Address | [10 empty] | Postal Address
| Address 1 |  |  | 24-28 Campbell St. | [5 empty] | Address 1 |  | GPO Box 4009
| Address 2 | [8 empty] | Address 2
| Suburb |  |  | SYDNEY | [5 empty] | Suburb |  | SYDNEY
| State |  |  | NSW |  | Post code | 2000 |  |  | State |  | NSW |  | Post code | 2001
`
Contact Names
Name
Phone
Email
REGULATORY CONTROL PERIODS
|  |  | Forthcoming period | 2020-21 | 2021-22 |  |  |  | 2022-23 |  | 2023-24 |  | 2024-25
|  |  |  | 2025-26 | 2026-27 |  |  |  | 2027-28 |  | 2028-29 |  | 2029-30
|  |  |  | 2030-31 | 2031-32 |  |  |  | 2032-33 |  | 2033-34 |  | 2034-35
|  | RESETS | Current period | 2015-16 | 2016-17 |  |  |  | 2017-18 |  | 2018-19 |  | 2019-20
|  |  |  | 2020-21 | 2021-22 |  |  |  | 2022-23 |  | 2023-24 |  | 2024-25
|  |  |  | 2025-26 | 2026-27 |  |  |  | 2027-28 |  | 2028-29 |  | 2029-30
|  |  | Previous period | 2010-11 | 2011-12 |  |  |  | 2012-13 |  | 2013-14 |  | 2014-15
|  |  |  | 2015-16 | 2016-17 |  |  |  | 2017-18 |  | 2018-19 |  | 2019-20
|  |  |  | 2020-21 | 2021-22 |  |  |  | 2022-23 |  | 2023-24 |  | 2024-25
|  |  | Commencing year | 2016-17
ANNUAL RINS
|  |  | Final year | 2020-21
SUBMISSION DETAILS
|  |  | RIN type | Category Analysis
|  |  | Source | Reporting
|  | THIS FILE | Data Quality | Consolidated
|  |  | Confidentiality Status | Public
|  |  | Amended RIN Amendment Reason | .Recast historical CA RIN data - Revised tab 2.2 repex – see D18/83676 & D18/83677 – 31 May 2018 20220207 - 2.6 amended to update costs #13526897
|  |  | Submission Date | dd/mm/yy
Contents
Instructions

## Contents
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
CONTENTS
| 1. Business details | 2. Expenditure
| 4. Alternative control services | 5. Network information | 6. Service & quality
Business & other details
2.1 Expenditure summary & reconciliation
2.3 Augex project data
2.5 Connections
2.2 Repex
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency response
2.10 Overheads
2.6 Non-network
4.3 Ancillary services - Fee-based services
4.4 Ancillary services - Quoted services
4.1 Public lighting
4.2 Metering
5.4 Maximum demand & utilisation - Spatial
5.2 Asset age profile
5.3 Maximum demand - network level
6.3 Sustained interruptions
2.11 Labour
2.12 Input tables
2.3 (b) Augex data
2.1 Expenditure summary & reconciliation
2.3 (a) Augex project data
2.5 Connections
2.2 Repex
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency response
2.6 Non-network
2.3 (b) Augex data

## 2.1 Expenditure summary
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.1 EXPENDITURE SUMMARY & RECONCILIATION
There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.1.1 - STANDARD CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2016-17
Replacement expenditure | 205058795.68
Connections | 7788341.37
Augmentation Expenditure | 9797568.4
Non-network | 34954368.14
Capitalised network overheads | 107667426.16
Capitalised corporate overheads | 3297479.12
Metering
Public Lighting
Captial Contributions | 115937401.87
balancing item
capcons (included in the above)
TOTAL GROSS CAPEX (including capcons) | 484501380.74
2.1.2 - STANDARD CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2016-17
Vegetation management | 46969401
Maintenance | 44342651
Emergency response | 27572563
Non-network | 115137652
Network overheads | 125230334
Corporate overheads | 133791123
Metering | 1470768
Public Lighting
balancing item
TOTAL OPEX | 494514492
2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2016-17
Connections
Capitalised network overheads | 7484733
Capitalised corporate overheads | 492327
Metering | 14269325
Public lighting | 9817377
Fee and quoted | 9826108
balancing item | -7977060
TOTAL CAPEX | 33912810
2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2016-17
Connections
Network overheads | 31981794
Corporate overheads | 17603073
Metering | 24433492
Public lighting | 21032476
Fee and quoted | 45962897
balancing item | -49584867
TOTAL OPEX | 91428865
2.1.5 - DUAL FUNCTION ASSETS CAPEX
EXPENDITURE ($0's)
2016-17
Replacement expenditure | 69288701
Connections | 277395
Augmentation Expenditure | 5900979
Non-network | 3217917
Capitalised network overheads | 10520696
Capitalised corporate overheads | 311804
balancing item
capcons (included in the above)
TOTAL GROSS CAPEX (including capcons) | 89517492
2.1.6 - DUAL FUNCTION ASSETS OPEX
EXPENDITURE ($0's)
2016-17
Vegetation management | 3488835
Maintenance | 3293723
Emergency response | 2048059
Non-network | 8552296
Network overheads | 9301969
Corporate overheads | 9937855
balancing item
TOTAL OPEX | 36622737
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.2 Repex
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.2 REPEX
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY
|  |  | EXPENDITURE ($0's) | ASSET REPLACEMENTS (0's) | ASSET FAILURES (0's)
ASSET GROUP | ASSET CATEGORY |  | 2016-17 | 2016-17 | 2016-17
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole |  | 611515 | 1081 | 0
| ˂ = 1 kV; Wood |  | 12998920 | 1328.55 | 166
| > 1 kV & < = 11 kV; Wood |  | 6512567 | 831.08 | 0
| ˃ 11 kV & < = 22 kV; Wood |  | 45202 | 12.17 | 0
| > 22 kV & < = 66 kV; Wood |  | 1644046 | 74.9 | 11
| > 66 kV & < = 132 kV; Wood |  | 435704 | 19.61 | 0
| > 132 kV; Wood |  | 0 |  | 0
| ˂ = 1 kV; Concrete |  | 23675 | 2.43 | 0
| > 1 kV & < = 11 kV; Concrete |  | 11737 | 1.21 | 0
| ˃ 11 kV & < = 22 kV; Concrete |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; Concrete |  | 348486 | 15.69 | 0
| > 66 kV & < = 132 kV; Concrete |  | 256353 | 11.54 | 1
| > 132 kV; Concrete |  | 0 | 0 | 0
| ˂ = 1 kV; Steel |  | 301022 | 30.95 | 0
| > 1 kV & < = 11 kV; Steel |  | 1781 | 0.18 | 0
| ˃ 11 kV & < = 22 kV; Steel |  | 324 | 0.03 | 0
| > 22 kV & < = 66 kV; Steel |  | 22840 | 1.03 | 0
| > 66 kV & < = 132 kV; Steel |  | 57351 | 1.22 | 0
| > 132 kV; Steel |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
POLE TOP STRUCTURES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 811575 | 515.45 | 31
| > 1 kV & < = 11 kV |  | 387059 | 245.83 | 1
| ˃ 11 kV & < = 22 kV |  | 49943 | 31.72 | 1
| > 22 kV & < = 66 kV |  | 594028 | 134 | 1
| > 66 kV & < = 132 kV |  | 537454 | 179 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 528126 | 130 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV |  | 4294908 | 38.4 | 1432
| > 1 kV & < = 11 kV |  | 7514601 | 159.3 | 280
| ˃ 11 kV & < = 22 kV ; SWER |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Single-Phase |  |  |  | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase |  | 0 | 0 | 0
| > 22 kV & < = 66 kV |  | 1858336 | 13.71 | 65
| > 66 kV & < = 132 kV |  | 6 | 0 | 7
| > 132 kV |  | 0 | 0 | 0
| Other |  | 25171 | 107 | 19
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 19159608 | 23.08 | 489
| > 1 kV & < = 11 kV |  | 0 | 0 | 313
| > 11 kV & < = 22 kV |  |  |  | 0
| > 22 kV & < = 33 kV |  | 22840977 | 21.43 | 15
| > 33 kV & < = 66 kV |  | 0 | 0 | 0
| > 66 kV & < = 132 kV |  | 29806075 | 14.1 | 5
| > 132 kV |  | 7242800 | 4.79 | 0
| Other |  | 3276701 | 162.93 | 114
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type |  | 5400608 | 16171.69 | 2737
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type |  | 387825 | 1161.31 | 1
| ˂ = 11 kV ; Residential ; Complex Type |  | 115384 | 10 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type |  |  |  | 0
| ˂ = 11 kV ; Subdivision ; Complex Type |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial |  |  |  | 1
| > 11 kV & < = 22 kV ; Subdivision |  |  |  | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial |  |  |  | 0
| > 22 kV & < = 33 kV ; Subdivision |  |  |  | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial |  |  |  | 0
| > 33 kV & < = 66 kV ; Subdivision |  |  |  | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial |  |  |  | 0
| > 66 kV & < = 132 kV ; Subdivision |  |  |  | 0
| > 132 kV ; Commercial & Industrial |  |  |  | 0
| > 132 kV ; Subdivision |  |  |  | 0
| Other |  |  |  | 23
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 120398 | 7.2 | 8
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 24712 | 0.96 | 4
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 216717 | 12.96 | 9
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 1072522 | 43.88 | 28
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 0 | 0 | 9
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 506150 | 10.65 | 12
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 61692 | 1.35 | 6
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase |  | 0 | 0 | 1
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 503842 | 5.87 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase |  | 410321 | 2.13 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 0 | 0 | 1
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase |  | 0 | 0 | 13
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA |  | 277312 | 0.58 | 14
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA |  | 6415494 | 6.68 | 5
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA |  | 50775 | 0.11 | 4
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA |  | 146373 | 0.29 | 2
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA |  | 4573348 | 2.43 | 17
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA |  | 1418989 | 0.51 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA |  | 7257243 | 0.62 | 2
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA |  | 0 | 0 | 0
| Other |  | 599119 | 15.08 | 2
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; FUSE |  | 3252976 | 699 | 448
| ˂ = 11 kV ; Switch |  | 5627030 | 350 | 427
| ˂ = 11 kV ; Circuit Breaker |  | 15771036 | 187.86 | 144
| > 11 kV & < = 22 kV ; Switch |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Switch |  | 1166617 | 28 | 22
| > 22 kV & < = 33 kV ; Circuit Breaker |  | 13306394 | 42.55 | 33
| > 33 kV & < = 66 kV ; Switch |  | 0 | 0 | 4
| > 33 kV & < = 66 kV ; Circuit Breaker |  | 1269379 | 3.03 | 0
| > 66 kV & < = 132 kV ; Switch |  | 1565651 | 9 | 11
| > 66 kV & < = 132 kV ; Circuit Breaker |  | 1741137 | 12.14 | 17
| > 132 kV ; Switch |  | 0 | 0 | 0
| > 132 kV ; Circuit Breaker |  | 0 | 0 | 0
| Other |  | 3305013 | 114.52 | 0
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road |  | 550 | 640 | 0
| Luminaires ; Minor Road |  | 7957838.5 | 16405 | 0
| Brackets ; Major Road |  | 0 | 1000 | 0
| Brackets ; Minor Road |  | 912231.5 | 7616.45 | 0
| Lamps ; Major Road |  | 5985317.76 | 31000 | 0
| Lamps ; Minor Road |  | 14673682.24 | 76000 | 0
| Poles / Columns ; Major Road |  | 1620260.34 | 145.92 | 0
| Poles / Columns ; Minor Road |  | 3443053.23 | 310.08 | 0
| Other |  | 0 | 0 | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices |  | 431095 | 11 | 347
| Local Network Wiring Assets |  | 0 | 0 | 0
| Communications Network Assets |  | 1529115 | 1.88 | 76
| Master Station Assets |  | 0 | 0 | 0
| Communications Site Infrastructure |  | 0 | 0 | 2
| Communications Linear Assets |  | 36887 | 2 | 26
| AFLC |  | 1288451 | 3.94 | 67
| Other |  | 169544514 | 802.42 | 90
OTHER BY: DNSP DEFINED | balancing item (i.e. multi-node discrepancy)
| distribution substations - not age related |  | 4007905 | 1047 | 19
| distribution substations - other |  | 5066361 | 1165 | 29
| distribution voltage regulation |  | 370963 | 3
| field devices - not age related |  | 1752253 | 63
| land (i.e. strategic system property) |  | 332994 | 0
| overhead conductors - not age related |  | 1336734 | 286.1 | 39
| overhead conductors - other |  | 2349038 | 120.96
| support costs (i.e. gis data capture and switching) |  | 0 | 0
| switchgear - not age related |  | 0 | 0
| towers - > = 33 kv ; refurbishment |  | 3893177 | 46
| transformers - not age related |  | 0 | 0
| transformers - other |  | 1635881 | 39
| underground cables - not age related |  | 851553 | 23
| underground cables - other |  | 2063645 | 8.55
zone & subtransmision substations - other
| zone & subtransmission substations - not age related |  | 3080986 | 30 | 1
| zone & subtransmission substations - other |  | 22615725 | 76.15 | 48
2.2.2 - SELECTED ASSET CHARACTERISTICS
|  |  | ASSET VOLUMES CURRENTLY IN COMMISSION | ASSET REPLACEMENTS (0's)
ASSET GROUP | METRIC | UNITS | 2016-17 | 2016-17
TOTAL POLES BY: FEEDER TYPE | Total CBD poles | Number | 63 | 0.47593
| Total urban poles | Number | 312711 | 2362.3626
| Total rural long poles | Number | 8919 | 67.3782
| Total rural short poles | Number | 112620 | 850.7832
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH BY FEEDER TYPE | Conductors CBD | KM | 2.0193 | 0.03407
| Conductors urban | KM | 12103.362 | 204.2131
| Conductors rural long | KM | 1273.0653 | 21.4797
| Conductors rural short | KM | 9736.193 | 164.2732
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH MATERIAL TYPE | OH conductor LV ABC | KM | 1434.3481 | 18.6012
| OH conductor steel | KM | 598.3354 | 90.518
| OH conductor ACSR | KM | 4840.2663 | 33.308
| OH conductor AAAC | KM | 779.2251 | 10.1053
| OH conductor AAC | KM | 9298.8105 | 120.5909
| OH conductor HDBC | KM | 7978.8171 | 103.4726
| Other | KM | 1033.5852 | 13.404
UNDERGROUND CABLES BY: CABLE LENGTH BY FEEDER TYPE | Cable CBD | KM | 417.5904 | 3.1424
| Cable urban | KM | 11376.5418 | 85.6101
| Cable rural long | KM | 16.8739 | 0.12698
| Cable rural short | KM | 2673.7719 | 20.1205
TRANSFORMERS BY: TOTAL MVA | Total MVA replaced | MVA | 37020.256 | 676.18
| Total MVA disposed of | MVA | 0 | 582.738
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(a) Augex
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.3 AUGEX PROJECT DATA
There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped. See the Instructions sheet on how to group or ungroup tables.
2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
SUBSTATION ID | SUBSTATION TYPE (drop down) | PROJECT ID | PROJECT TYPE (drop down) | PROJECT TRIGGER (drop down) | VOLTAGE (KV) | SUBSTATION RATING NORMAL CYCLIC (MVA) |  | SUBSTATION RATING N-1 EMERGENCY (MVA) |  | TRANSFORMERS |  |  | SWITCHGEAR |  | CAPACITORS |  |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | PRE | POST | PRE | POST | UNITS ADDED | MVA ADDED | EXPENDITURE ($0's) | UNITS ADDED | EXPENDITURE ($0's) | MVAR ADDED | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
NEW ALEXANDRIA 132/33KV STS (SJ-00091 & SJ-00175) | Subtransmission substation | ARA_03.1A.0028A | New substation establishment | Other | 132/33 | 0 | 280 | 0 | 140 | 2 | 280 | 4263355 | 32 | 5652447 | 0 | 0 |  |  | 284294 | 21932.64 | 2267835 | 16379333 | 157019 | 29004284 | FY2012-2018 |  |  |  | 14220958 | 0
NEW ROCKDALE 132/11KV ZN (SJ-05993) | Zone substation | ARA_04.1.0008 | New substation establishment | Other | 132/11 | 58 | 75 | 27.1 | 65 | 2 | 75 | 2254444 | 37 | 3166051 | 0 | 0 |  |  | 2991633 | 30733.7 | 2641222 | 7984020 | 1175102 | 20212472 | FY2010-2019 |  |  |  | 1541377 | 0
ENGADINE ZN 132KV CONVERSION (SJ-04726 & SJ-05749) | Zone substation | ARA_04.2.0015 | Substation upgrade - capacity | Other | 132/11 | 48 | 75 | 31.7 | 60.1 | 2 | 75 | 1215481 | 6 | 1717765 | 0 | 0 |  |  | 2359717 | 30182.86 | 3090132 | 12475506 | 3010830 | 23869432 | FY2009-2017 |  |  |  | 0 | 0
CROWS NEST ZN 132KV CONVERSION (SJ-05651) | Zone substation | ARA_05.1.0006 | Substation upgrade - capacity | Other | 132/11 | 94.5 | 114.3 | 50.8 | 57.1 | 2 | 114.3 | 1151215 | 6 | 3992573 | 12 | 573844 |  |  | 3812833 | 33186.77 | 3698405 | 2097438 | 417920 | 15744228 | FY2009-2018 |  |  |  | 6319600 | 0
NEW BROADMEADOW 132/11KV ZN (SJ-04866 & SJ-00008) | Zone substation | ARA_07.1.0006 | New substation establishment | Other | 132/11 | 38 | 81.3 | 22.9 | 40.7 | 2 | 81.3 | 3149681 | 28 | 4415553 | 12 | 549967 |  |  | 5579467 | 68384.59 | 7046161 | 7852140 | 974988 | 29567957 | FY2009-2017 |  |  |  | 791819 | 0
NEW KOORAGANG 132/33KV STS (SJ-04087 & SJ-05642) | Subtransmission substation | ARA_07.2.0007C | New substation establishment | Demand growth | 132/33 | 0 | 285.8 | 0 | 142.9 | 2 | 285.8 | 3857136 | 26 | 1337699 | 0 | 0 |  |  | 11195561 | 139390.274 | 9074108 | 13452790 | 1392308 | 40309602 | FY2008-2017 |  |  |  | 2247799 | 0
NEW RATHMINES 132/11KV ZN (SJ-03278 & SJ-00039) | Zone substation | ARA_07.4.0010 | New substation establishment | Demand growth | 132/11 | 37.5 | 76.2 | 0 | 38.1 | 2 | 76.2 | 2133339 | 20 | 1097124 | 0 | 0 |  |  | 4843767 | 78433.185 | 7377151 | 8859847 | 1870469 | 26181697 | FY2008-2017 |  |  |  | 412244 | 491970
NEW CHARLESTOWN 132/11KV ZN (SJ-05319 & SJ-06071) | Zone substation | ARA_07.5.0005 | New substation establishment | Other | 132/11 | 75 | 113 | 36.1 | 60.2 | 2 | 113 | 3363772 | 28 | 4634442 | 12 | 589227 |  |  | 3393630 | 57009.28 | 5990055 | 8468800 | 1041262 | 27481187 | FY2008-2017 |  |  |  | 1216740 | 0
NEW BRANDY HILL 132/11KV ZN (SJ-05807 & SJ-00006) | Zone substation | ARA_07.6.0008 | New substation establishment | Demand growth | 132/11 | 4.8 | 76.2 | 0 | 38.1 | 2 | 76.2 | 2035376 | 19 | 907903 | 0 | 0 |  |  | 3755589 | 39507.056 | 3468476 | 13709517 | 355913 | 24232774 | FY2009-2017 |  |  |  | 296514 | 0
NEW MAITLAND 33/11KV ZN (SJ-5126 & SJ-00051) | Zone substation | ARA_07.6.0009 | New substation establishment | Demand growth | 33/11 | 38.4 | 73.3 | 23.8 | 36.7 | 2 | 73.3 | 1307192 | 20 | 1687923 | 0 | 0 |  |  | 1427119 | 48783.307 | 3696937 | 9235129 | 377091 | 17731391 | FY2010-2017 |  |  |  | 0 | 0
TANILBA BAY 33/11KV ZN UPRATE (SJ-05537) | Zone substation | ARA_07.8.0003 | Substation upgrade - capacity | Demand growth | 33/11 | 10 | 38.8 | 0 | 18.7 | 1 | 38.8 | 451853 | 7 | 12212 | 0 | 0 |  |  | 2602397 | 54983.209 | 4394386 | 3547618 | 750867 | 11759334 | FY2009-2017 |  |  |  | 0 | 0
NEW MEDOWIE 33/11KV ZN (SJ-00041) | Zone substation | ARA_07.8.0032A | New substation establishment | Demand growth | 33/11 | 0 | 73 | 0 | 38.1 | 2 | 73 | 1178862 | 19 | 854691 | 0 | 0 |  |  | 3074638 | 49091.81 | 4700891 | 7161533 | 626400 | 17597015 | FY2010-2017 |  |  |  | 461445 | 0
NEW SCONE 66/11KV ZN (SJ-05132 & SJ-05702) | Zone substation | ARA_08.2.0013C | New substation establishment | Demand growth | 66/11 | 23.7 | 76.2 | 14.2 | 38.1 | 2 | 76.2 | 2090373 | 20 | 729710 | 12 | 517564 |  |  | 3492708 | 102038.203 | 3892822 | 8449674 | 268261 | 19441113 | FY2008-2017 |  |  |  | 789113 | 0
NEW ABERDEEN 66/11KV ZN (SJ-05634 & SJ-06031) | Zone substation | ARA_08.2.0014 | New substation establishment | Other | 66/11 | 12.5 | 46.4 | 6.3 | 25.5 | 2 | 46.4 | 2550397 | 9 | 2390186 | 0 | 0 |  |  | 1473299 | 56894.69 | 5945683 | 5147023 | 491100 | 17997689 | FY2008-2016 |  |  |  | 1158497 | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
|  | Non material projects - [actual] | [21 empty] | 167664.47
AUG232_1 | AUG232_2 | AUG232_3 | AUG232_4 | AUG232_5 | AUG232_6 | ED_AUG232_00001 | ED_AUG232_00002 | ED_AUG232_00003 | ED_AUG232_00004 | ED_AUG232_00005 | ED_AUG232_00006 | ED_AUG232_00007 | ED_AUG232_00008 | ED_AUG232_00009 | ED_AUG232_00010 | ED_AUG232_00011 | ED_AUG232_00012 | ED_AUG232_00013 | ED_AUG232_00014 | ED_AUG232_00015 | ED_AUG232_00016 | ED_AUG232_00017 | ED_AUG232_00018 | ED_AUG232_00019 | ED_AUG232_00020 | ED_AUG232_00021
2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
LINE ID | PROJECT ID | PROJECT TYPE | PROJECT TRIGGER |  | VOLTAGE (KV) | ROUTE LINE LENGTH ADDED |  |  |  | POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS) |  |  | OVERHEAD LINES |  |  | UNDERGROUND CABLES |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | KM ADDED |  |  |  | POLES/TOWERS ADDED | POLES/TOWERS UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
ROOKWOOD ROAD BSP 132KV CONNECTIONS (SJ-05197) | ARA_01.1.0008 | New line on new route - other |  | Demand growth | 132 | 2.6 |  |  |  | 22 | 7 | 210160 | 3 | 0 | 210160 | 0 | 0 | 80716 | 1287680 | 35336.15 | 3280489 | 2548031 | 305027 | 7922263 | FY2009-2017 |  |  |  |  | 0 | New line on new route - single circuit
NEW ALEXANDRIA STS 132KV CONNECTION WORKS (SJ-000172) | ARA_03.1A.0028A | New line on new route - single circuit |  | Other | 132 | 0.1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136585 | 0 | 358.27 | 33849 | 510459 | 0 | 680893 | FY2016-2018 |  |  |  |  | 366808 | New line on new route - dual circuit
NEW ROCKDALE 132KV CONNECTION WORKS (SJ-06161) | ARA_04.1.0008 | New line on new route - dual circuit |  | Other | 132 | 0.1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398095 | 0 | 1525.69 | 138966 | 548535 | 0 | 1085596 | FY2011-2019 |  |  |  |  | 0 | New line on new route - other
ENGADINE ZN NEW 132KV FEEDERS 285, 286 & 289 (SI-05747) | ARA_04.2.0013 | New line on new route - other |  | Other | 132 | 5.8 |  |  |  | 3 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3867271 | 0 | 4789.6 | 471475 | 8937679 | 184338 | 13460762 | FY2009-2017 |  |  |  |  | 0 | Line rebuild over existing route - single circuit
CROWS NEST ZN 132KV CONNECTION WORKS (SJ-05651) | ARA_05.1.0006 | Other |  | Other | 132 | 0.1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2281851 | 0 | 6541.54 | 667037 | 0 | 0 | 2948888 | FY2009-2017 |  |  |  |  | 0 | Line rebuild over existing route - dual circuit
132KV FEEDERS 9E3 & 9E4/2 LINDFIELD - WILLOUGHBY STS REPLACEMENT (SJ-06046) | ARA_05.1.0008 | New line on new route - dual circuit |  | Other | 132 | 8.9 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 10126199 | 0 | 20307.16 | 2236233 | 21356361 | 67654 | 33786447 | FY2010-2017 |  |  |  |  | 0 | Reconductor - Single circuit
EMPIRE BAY ZN 66KV FEEDERS 883 & 884 (SI-05733) | ARA_06.1.0025 | New line on new route - single circuit |  | Demand growth | 66 | 15.9 |  |  |  | 85 | 26 | 172176 | 8 | 0 | 172176 | 8 | 0 | 3874 | 1470695 | 55106.83 | 5465743 | 23754278 | 1009643 | 32048584 | FY2010-2017 |  |  |  |  | 141587 | Reconductor - Dual circuit
NEW BROADMEADOW ZN 132KV CONNECTION WORKS (SJ-04866) | ARA_07.1.0006 | New line on new route - single circuit |  | Other | 132 | 0.3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 255386 | 0 | 0 | 1382169 | 0 | 1777.09 | 182972 | 4648946 | 0 | 6469473 | FY2009-2017 |  |  |  |  | 0 | Reconductor - Other
NEW KOORAGANG STS 132KV FEEDERS 96X & 97M (SJ-04087) | ARA_07.2.0007C | New line on new route - single circuit |  | Demand growth | 132 | 16 |  |  |  | 150 | 0 | 1587 | 16 | 0 | 1587 | 0 | 0 | 2368 | 155328 | 139040.27 | 990732 | 380914 | 22312 | 1554829 | FY2008-2014 |  |  |  |  | 154 | Line upgrade - raising/retensoring
NEW CHARLESTOWN ZN 132KV CONNEXTION WORKS (SJ-05319) | ARA_07.5.0005 | New line on new route - dual circuit |  | Other | 132 | 0.1 |  |  |  | 2 | 0 | 0 | 0 | 3 | 235754 | 0 | 0 | 1907466 | 0 | 4944.44 | 516675 | 3191518 | 0 | 5851413 | FY2008-2016 |  |  |  |  | 0 | Line upgrade - voltage upgrade
NEW MAITLAND ZN 33KV CONNECTION WORKS (SJ-5126) | ARA_07.6.0009 | New line on new route - single circuit |  | Demand growth | Other | 0.1 |  |  |  | 2 | 0 | 0 | 0 | 0 |  | 0 | 0 | 466420 | 0 | 1587.64 | 153014 | 1601106 | 0 | 2220539 | FY2010-2016 |  |  |  |  | 0 | Line upgrade - capacity
TANILBA BAY ZN 33KV FEEDERS 81401(1) & 3300(3) (SJ-05573) | ARA_07.8.0003 | New line on new route - single circuit |  | Demand growth | Other | 5 |  |  |  | 50 | 0 | 1167564 | 5 | 0 | 1167564 | 0 | 0 | 0 | 0 | 16045.72 | 1592957 | 1150068 | 0 | 5078154 | FY2009-2016 |  |  |  |  | 0 | String spare circuit
NEW MEDOWIE ZN 33KV FEEDERS TM13, TM4, 81401(3) (SJ-00166) | ARA_07.8.0032A | New line on new route - single circuit |  | Demand growth | Other | 12 |  |  |  | 130 | 0 | 407054 | 12 | 0 | 407054 | 0 | 0 | 36542 | 1664048 | 60264.21 | 3982440 | 3054798 | 398541 | 9950478 | FY2010-2017 |  |  |  |  | 46915 | Other
NEW SCONE ZN 66KV FEEDERS 6028(7) & 82244 (SJ-05702) | ARA_08.2.0013C | Line upgrade - voltage upgrade |  | Voltage issues | 66 | 37.5 |  |  |  | 270 | 0 | 432 | 38 | 0 | 432 | 0 | 0 | 38 | 3150505 | 102038.2 | 3354698 | 2379737 | 1191462 | 10077306 | FY2009-2017 |  |  |  |  | 1175
NEW ABERDEEN ZN 66KV FEEDERS 82257 & 82244 (SJ-05634) | ARA_08.2.0014 | Line rebuild over existing route - single circuit |  | Other | 66 | 30.8 |  |  |  | 10 | 191 | 184123 | 1 | 31 | 184123 | 0 | 0 | 0 | 0 | 2400.47 | 273496 | 290011 | 0 | 931754 | FY2008-2017 |  |  |  |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
| Non material projects - [actual] | [22 empty] | 49427.221
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(b) Augex
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.3 AUGEX DATA
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS.
DESCRIPTOR METRICS
PROJECT TYPE |  | UNITS ADDED (0's) | UNITS UPGRADED (0's)
| UNITS | 2016-17 | 2016-17
HV Feeder Augmentations - Overhead Lines | Circuit line length in km | 5
HV Feeder Augmentations - Underground Cables | Circuit line length in km | 11
LV Feeder Augmentations - Overhead Lines | Circuit line length in km | 3
LV Feeder Augmentations - Underground Cables | Circuit line length in km | 6
Distribution Substation Augmentations - Pole Mounted | Number | 4
Distribution Substation Augmentations - Ground Mounted | Number | 4
Distribution Substation Augmentations - Indoor | Number
COST METRICS
TOTAL DIRECT EXPENDITURE - Project Type |  | EXPENDITURE ($0's)
2016-17
HV Feeder Augmentations - Overhead Lines |  | 580850
HV Feeder Augmentations - Underground Cables |  | 1806910
HV Feeder Non-Material Projects |  | 1506635
LV Feeder Augmentations - Overhead Lines |  | 320535
LV Feeder Augmentations - Underground Cables |  | 1272570
LV Feeder Non-Material Projects |  | 1132627
Distribution Substation Augmentations - Pole Mounted |  | 299728
Distribution Substation Augmentations - Ground Mounted |  | 369928
Distribution Substation Augmentations - Indoor |  | 62979
2.3.4 - AUGEX DATA - TOTAL EXPENDITURE
AUGMENTATION CAPEX (As incurred) |  | EXPENDITURE ($0's)
2016-17
Subtransmission Substations, Switching Stations, Zone Substations |  | 2654904
Subtransmission Lines |  | 5647862
HV Feeders |  | 3894395
HV Feeders - Land Purchases and Easements
Distribution Substations |  | 732636
Distribution Substations - Land Purchases And Easements
LV Feeders |  | 2725732
LV Feeders - Land Purchases And Easements
Other Assets |  | 43019
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.5 Connections
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.5 CONNECTIONS
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.5.1 - DESCRIPTOR METRICS
<<<GROUP-ROW>>>
VOLUMES AND EXPENDITURE
CONNECTION SUBCATEGORY | DESCRIPTOR METRIC | UNITS | 2016-17
RESIDENTIAL | Underground connections | 0's | 55
| Overhead connections | 0's | 52
| Distribution substation installed | MVA added | 88.5027
| Distribution substations installed | 0's | 90
| Distribution substation installed | total spend $0s | 1532258.5972
| Augmentation HV | net circuit km added | 0.5013
| Augmentation HV | total spend $0s | 4386.4126
| Augmentation LV | net circuit km added | 1.723
| Augmentation LV | total spend $0s | 331661.9702
| Mean days to connect residential customer with LV single phase connection | 0's | 0
| Volume of GSL breaches for residential customers | 0's | 0
| Volume of customer complaints relating to connection services | 0's | 0
| GSL payments | $0s | 0
COMMERCIAL/INDUSTRIAL | Underground connections | 0's | 32
| Overhead connections | 0's | 31
| Distribution substation installed | MVA added | 45.8922
| Distribution substations installed | 0's | 42
| Distribution substation installed | total spend $0s | 1736540.2926
| Augmentation HV | net circuit km added | 5.7745
| Augmentation HV | total spend $0s | 3702748.0536
| Augmentation LV | net circuit km added | 2.9866
| Augmentation LV | total spend $0s | 330752.8739
SUBDIVISION | Underground connections | 0's | 0
| Overhead connections | 0's | 4
| Distribution substation installed | MVA added | 0.62248
| Distribution substations installed | 0's | 1
| Distribution substation installed | total spend $0s | 85218.18
| Augmentation HV | net circuit km added | 1.9076
| Augmentation HV | total spend $0s | 12436.36
| Augmentation LV | net circuit km added | 0
| Augmentation LV | total spend $0s | 0
| Cost per lot ($) | $0s | 0
EMBEDDED GENERATION | Underground connections | 0's | 2
| Overhead connections | 0's | 0
| Distribution substation installed | MVA added | 3.245
| Distribution substations installed | 0's | 4
| Distribution substation installed | total spend $0s | 0
| Augmentation HV | net circuit km added | 0
| Augmentation HV | total spend $0s | 329733.77
| Augmentation LV | net circuit km added | 0
| Augmentation LV | total spend $0s | 0
2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION
|  | EXPENDITURE ($0's) | VOLUMES (0's)
CONNECTION SUBCATEGORY | CONNECTION CLASSIFICATION | 2016-17 | 2016-17
RESIDENTIAL | Simple connection LV | 310149.0406 | 6.0566
| Complex connection LV |  | 0
| Complex connection HV | 1558157.9394 | 100.9434
COMMERCIAL/INDUSTRIAL | Simple connection LV | 364150.0803 | 9.1636
| Complex connection HV (customer connected at LV, minor HV works) | 433934.8944 | 1.1455
| Complex connection HV (customer connected at LV, upstream asset works) | 4280142.761 | 49.2545
| Complex connection HV (customer connected at HV) | -61752.8166 | 2.2909
| Complex connection sub-transmission | 753566.301 | 1.1455
SUBDIVISION | Complex connection LV |  | 0
| Complex connection HV (no upstream asset works) |  | 0
| Complex connection HV (with upstream asset works) | 97654.54 | 4
EMBEDDED GENERATION | Simple connection LV | 288501.52 | 1
| Complex connection HV (small capacity) |  | 0
| Complex connection HV (large capacity) | 41232.25 | 1
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.6 Non-network
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.6 NON NETWORK EXPENDITURE
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.6.1 - NON-NETWORK EXPENDITURE
EXPENDITURE ($0's)
SERVICE SUBCATEGORY | ASSET CATEGORY |  |  | 2016-17
OPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 4671229.5942
| Recurrent expenditure |  |  | 46396136.6651
| Non-recurrent expenditure |  |  | 6161347.1803
MOTOR VEHICLES | Car |  |  | 2776776.22
| Light commercial vehicle |  |  | 5865502.79
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 4190548.26
| Heavy commercial vehicle |  |  | 2324958.44
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 48776327.1986
OTHER | Other expenditure
OTHER - DNSP nominated | Motor vehicles - Cable handling equipment |  |  | 241359.62
| Motor vehicles - Crane borer (HCV) |  |  | 1245227.69
| Motor vehicles - Material handling |  |  | 385757.61
| Motor vehicles - Vehicle loading cranes |  |  | 194361.4
| Motor vehicles - Other plant |  |  | 460414.98
CAPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 1012636.21
| Recurrent expenditure |  |  | 9976830.9
| Non-recurrent expenditure |  |  | 12634583.98
MOTOR VEHICLES | Car |  |  | 0
| Light commercial vehicle |  |  | 1892757.12
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 46300.16
| Heavy commercial vehicle |  |  | 0
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 11185038.58
OTHER | Other expenditure |  |  | 1301367.38
OTHER - DNSP nominated | Motor vehicles - Cable handling equipment |  |  | 0
| Motor vehicles - Crane borer (HCV) |  |  | 70961.44
| Motor vehicles - Material handling |  |  | 0
| Motor vehicles - Vehicle loading cranes |  |  | 1785.68
| Motor vehicles - Other plant |  |  | 50024.59
| Motor vehicles - BlueWorx Project |  |  | 0
Fleet - Telematics
2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE
VOLUMES (0's)
NON-NETWORK CATEGORY | DESCRIPTOR METRIC |  |  | 2016-17
IT & COMMUNICATIONS | Employee numbers |  |  | 3,176
| User numbers |  |  | 4,249
| Number of devices |  |  | 6,301
2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES
VOLUMES / %
NON-NETWORK CATEGORY | ASSET CATEGORY | DESCRIPTOR METRIC | UNITS | 2016-17
MOTOR VEHICLES | CAR | Average kilometres travelled | 0's | 13355
|  | Number purchased | 0's | 1
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 354.8696
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 97.22%
| LIGHT COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 12643
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 1020.8576
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 97.22%
| ELEVATED WORK PLATFORM (LCV) | Average kilometres travelled | 0's
|  | Number purchased | 0's
|  | Number leased | 0's
|  | Number in fleet | 0's
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent)
| ELEVATED WORK PLATFORM (HCV) | Average kilometres travelled | 0's | 4643
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 203.1993
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 97.22%
| HEAVY COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 6805
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 338.3414
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 97.22%
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.7 Vegetation management
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.7 VEGETATION MANAGEMENT
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Please enter a description for each Zone in table 2.7.1 - Urban and CBD. The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2.
` | 2.7.1 - DESCRIPTOR METRICS BY ZONE
URBAN AND CBD
2016-17
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km | 9963
|  | Number of maintenance spans | 0's | 894932
|  | Total length of maintenance spans | km | 9963
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's | 0.92
|  | Average frequency of cutting cycle | years | 1
| ZONE 2 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
RURAL
2016-17
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 2 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
2.7.2 - EXPENDITURE METRICS BY ZONE
EXPENDITURE ($0's)
| ZONES | SERVICE SUBCATEGORY |  | 2016-17
| ZONE 1 | Tree trimming (excluding hazard trees) |  | 43730490.74
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 465217.987
|  | Vegetation corridor clearance |  | 465217.987
|  | Inspection |  | 2730501.971
|  | Audit |  | 1159874.895
|  | Contractor liaison expenditure |  | 773249.93
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 1133682.504
| ZONE 2 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 3 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 4 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 5 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 6 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 7 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 8 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 9 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 10 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 11 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 12 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 13 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 14 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 15 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 16 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 17 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 18 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS
VOLUMES (0's)
| DESCRIPTOR METRIC |  |  | 2016-17
Number of fire starts caused by vegetation grow-ins (NSP responsibility)
| Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility) |  |  | 11
Number of fire starts caused by vegetation grow-ins (other party responsibility)
Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility)
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.8 Maintenance
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.8 MAINTENANCE
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
|  |  |  | ASSET QUANTITY (0's) |  | AVERAGE AGE OF ASSET GROUP | INSPECTION CYCLE (YEARS) | MAINTENANCE CYCLE (YEARS)
|  |  |  | AT YEAR END | INSPECTED / MAINTAINED
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2016-17 | 2016-17 | 2016-17
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 504013 | 1379 | 34.5209 | 5 | 0
| Service lines | Number of customers | Number | 720016 | 0 | 28.353 | 0 | 0
Pole inspection and treatment | All poles | Number of poles | Number | 509257 | 110880 | 34.4575 | 5 | 0
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 22013.833 | 4793.0491 | 40 | 5 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 14484.7779 | 20041 | 31.0953 | 0 | 0
| 33 KV and above | Length (KM) | KM | 1036.5378 | 337 | 37.9293 | 5 | 0
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 399.5873 | 525.1385 | 40.1888 | 0 | 0
| Non-CBD | Length (KM) | KM | 15121.7284 | 19852.8615 | 30.5953 | 0 | 0
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 33524 | 0 | 25.1922 | 0 | 0
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 22664 | 3838 | 24.7667 | 10 | 20
| Distribution substation - other equipment | Earth mat | Number | 31778 | 10114 | 28.178 | 10 | 0
| Distribution substation - property | Number of distribution substation properties maintained | Number | 2889 | 14058 | 36.2007 | 0 | 0
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 504 | 2245 | 26.9099 | 6 | 0
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 41 | 0 | 41.435 | 3 | 0
| Transformers - HV | Number of HV transformers | Number |  | 0 |  | 0 | 0
| Zone substation - other equipment | <DNSP to nominate> | Number | 208 | 18468 | 37.6762 | 0.5 | 0
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 208 | 16548 | 37.6762 | 0.083333 | 0
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 196237 | 17720.2254 | 11.5698 | 2.5 | 2.5
| Major roads | Number of public lights maintained | Number | 54979 | 42586.7746 | 18.0945 | 2.5 | 2.5
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 864 | 0 | 28.9082 | 0 | 0
Protection systems maintenance | Protection systems | Number of systems | Number | 23415 | 0 | 30.1456 | 0 | 0
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets | <DNSP to nominate> | Number | 933.039 | 7223 | 34.5007 | 6 | 0
Various assets | includes rates, electricity, communications equip, metering | Various | Number
Ground clearance - access tracks | Access tracks | Number | Number
Other | < DNSP to nominate > | < DNSP to nominate >
2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
EXPENDITURE ($0'S)
|  |  |  | ROUTINE MAINTENANCE | NON-ROUTINE MAINTENANCE
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2016-17 | 2016-17
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 1296648.495 | 5598876.47
| Service lines | Number of customers | Number | 23814.2 | 104746.26
Pole inspection and treatment | All poles | Number of poles | Number | 8014295.22 | 522789.91
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 700810.45 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 403158.85 | 1455288.69
| 33 KV and above | Length (KM) | KM | 729081.67 | 1886853.35
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 29178 | 86126.58
| Non-CBD | Length (KM) | KM | 1103063 | 3256015.46
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 0 | 598913.91
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 1300822.52 | 1485152.89
| Distribution substation - other equipment | Earth mat | Number | 8221535.5 | 2000785.3
| Distribution substation - property | Number of distribution substation properties maintained | Number | 20515 | 555899.05
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 926720.58 | 533493.37
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 0 | 0
| Transformers - HV | Number of HV transformers | Number | 0 | 0
| Zone substation - other equipment | <DNSP to nominate> | Number | 3600765.11 | 1830556.79
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 1853676.85 | 848581.21
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 1346863 | 43702.87
| Major roads | Number of public lights maintained | Number | 3236898 | 105030.5
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 22191.11 | 41017.41
Protection systems maintenance | Protection systems | Number of systems | Number | 39275.31 | 198546.97
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets | <DNSP to nominate> | Number | 1711410.04 | 1110151.08
Various assets | includes rates, electricity, communications equip, metering | Various | Number
Ground clearance - access tracks | Access tracks | Number | Number
Other | < DNSP to nominate > | < DNSP to nominate >
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.9 Emergency Response
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.9 EMERGENCY RESPONSE
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)
EXPENDITURE ($0's)
2016-17
(A) TOTAL EMERGENCY RESPONSE EXPENDITURE
Total Expenditure | 29,620,622
(B) MAJOR EVENTS O&M EXPENDITURE
(C) MAJOR EVENT DAYS O&M EXPENDITURE
2017Ã¥Â¹Â´2Ã¦ÅË17Ã¦âÂ¥ | 401,590
2017Ã¥Â¹Â´5Ã¦ÅË26Ã¦âÂ¥ | 244,736
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10 Overheads
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.10 OVERHEADS
Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. Ausgrid is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If Ausgrid is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. Ausgrid is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN. |  | Choose Response drop down selection
Worksheet 2.10A
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Instructions Please enter a description for each expenditure category as currently reported under Ausgrid's annual RIN.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2016-17
NETWORK OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED NETWORK OVERHEADS
Standard Control Services
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2016-17
CORPORATE OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED CORPORATE OVERHEADS
Standard Control Services
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10(A) Overheads
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.10(A) OVERHEADS
This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options.
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2016-17
OPEX
Standard Control Services | Total | 134532303
Alternative Control Services | Total | 31981794
CAPEX
Standard Control Services | Total | 118188122
Alternative Control Services | Total | 7484733
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total
Unregulated Services | Total | 3531796
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2016-17
OPEX
Standard Control Services | Total | 143728978
Alternative Control Services | Total | 17603073
CAPEX
Standard Control Services | Total | 3609284
Alternative Control Services | Total | 492327
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total
Unregulated Services | Total | 2573922
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.11 Labour
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.11 LABOUR
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.11.1 - COST METRICS PER ANNUM
|  | ASL (0's) | TOTAL LABOUR EXPENDITURE ($0's) | AVERAGE PRODUCTIVE WORK HOURS PER ASL (0's) | STAND-DOWN OCCURENCES PER ASL (0's)
|  | 2016-17 | 2016-17 | 2016-17 | 2016-17
INTERNAL LABOUR EXPENDITURE
CORPORATE OVERHEADS | Executive manager | 6 | 2780679 | 1467 | 0
| Senior manager | 15 | 4196303 | 2769.1 | 0
| Manager | 121 | 27346391 | 2861.4 | 0.1
| Professional | 292 | 52590734 | 2745.4 | 0
| Semi professional | 137 | 17753013 | 2585.6 | 0
| Support staff | 197 | 22600852 | 2763 | 0.1
| Intern, junior staff, apprentice | 2 | 167681 | 1311.9 | 0
NETWORK OVERHEADS | Executive manager | 1 | 657801 | 1586.5 | 0
| Senior manager | 12 | 2722457 | 1411.3 | 0
| Manager | 248 | 58129177 | 2977 | 3
| Professional | 421 | 85337847 | 2998.4 | 0.1
| Semi professional | 377 | 68323344 | 2999 | 0.5
| Support staff | 155 | 20552090 | 3059.7 | 0.1
| Intern, junior staff, apprentice | 37 | 6096663 | 1504 | 0.4
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker | 1073 | 149022253 | 1454.4 | 4.1
| Skilled non electical worker | 37 | 4504953 | 1417.6 | 4.6
| Apprentice | 29 | 2366743 | 1386.4 | 0.2
| Unskilled worker | 173 | 18240332 | 2925.7 | 5.9
2.11.2 - DESCRIPTOR METRICS
|  | ORDINARY TIME (0's) |  | OVERTIME (0's)
|  | PER ASL | HOURLY RATE PER ASL | PER ASL | HOURLY RATE PER ASL
|  | 2016-17 | 2016-17 | 2016-17 | 2016-17
AVERAGE PRODUCTIVE WORK HOURS PER ASL
CORPORATE OVERHEADS | Executive manager | 1466.98 | 311.19 | 0 | 0
| Senior manager | 2769.07 | 169.64 | 0 | 0
| Manager | 2855.31 | 104.14 | 6.13 | 96.11
| Professional | 2742.85 | 85.66 | 2.55 | 84.16
| Semi professional | 2576.57 | 75.93 | 9.04 | 85.91
| Support staff | 2751.22 | 60.76 | 11.73 | 69.53
| Intern, junior staff, apprentice | 1311.9 | 42.5 | 0 | 0
NETWORK OVERHEADS | Executive manager | 1586.47 | 278 | 0 | 0
| Senior manager | 1411.32 | 168.22 | 0 | 0
| Manager | 2923.25 | 97.75 | 53.78 | 94.07
| Professional | 2964.33 | 91.37 | 34.07 | 121.76
| Semi professional | 2975.67 | 81.32 | 23.35 | 97.14
| Support staff | 3032.1 | 58.77 | 27.62 | 72.1
| Intern, junior staff, apprentice | 1364.56 | 65.8 | 139.46 | 73.52
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker | 1320.79 | 62.98 | 133.59 | 78.96
| Skilled non electical worker | 1350.21 | 57.66 | 67.34 | 68.32
| Apprentice | 1357.16 | 38.4 | 29.26 | 48.35
| Unskilled worker | 2822.49 | 50.91 | 103.24 | 65.3
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.12 Input tables
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
2.12 INPUT TABLES
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.12.1 - INPUT TABLES
|  | DIRECT MATERIAL EXPENDITURE | DIRECT LABOUR EXPENDITURE | CONTRACT EXPENDITURE | OTHER EXPENDITURE | RELATED PARTY CONTRACT EXPENDITURE | RELATED PARTY CONTRACT MARGIN EXPENDITURE
EXPENDITURE ($0's)
|  | 2016-17 | 2016-17 | 2016-17 | 2016-17 | 2016-17 | 2016-17
VEGETATION MANAGEMENT | ZONE 1 | 38272.37 | 3027795.43 | 47391428.685 | 739.53
ZONE 2
ZONE 3
ZONE 4
ZONE 5
ZONE 6
ZONE 7
ZONE 8
ZONE 9
ZONE 10
ZONE 11
ZONE 12
ZONE 13
ZONE 14
ZONE 15
ZONE 16
ZONE 17
ZONE 18
ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 501.74 | 442497.53 | 877463.425 | 0
| Pole inspection and treatment | 1272591.72 | 710486.48 | 6031217.02 | 0
| Overhead asset inspection | 0 | 680877.11 | 19933.34 | 0
| Network underground cable maintenance | 7584.52 | 910656.14 | 213999.86 | 0
| Distribution substation equipment & property maintenance | 70267.09 | 5977770.03 | 3492740.39 | 2095.51
| Zone substation equipment maintenance | 133869.89 | 3644786.69 | 748685.27 | 143.84
| Zone substation property maintenance | 10041.66 | 664244.99 | 1179390.2 | 0
| Public lighting maintenance | 730236 | 304128 | 3549397 | 0
| Scada & network control maintenance | 0 | 21394.44 | 796.67 | 0
| Protection systems maintenance | 0 | 39275.31 | 0 | 0
| Subtransmission asset maintenance - for dnsps with dual function assets | 22656.17 | 1326960.03 | 361793.84 | 0
Other
NON-ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 129071.52 | 4811372.86 | 762944.35 | 234
| Pole inspection and treatment | 56147.85 | 20360.17 | 446281.89 | 0
| Overhead asset inspection | 0 | 0 | 0 | 0
| Network underground cable maintenance | 493089.54 | 1568526.13 | 1266095.47 | 14430.9
| Distribution substation equipment & property maintenance | 376334.19 | 2957051.91 | 1307231.17 | 133.88
| Zone substation equipment maintenance | 243675.88 | 1435065.59 | 683263.21 | 2045.48
| Zone substation property maintenance | 19710.31 | 200833.79 | 628037.11 | 0
| Public lighting maintenance | 5267.37 | 98697.51 | 44768.49 | 0
| SCADA & network control maintenance | 3878.15 | 27382.78 | 9756.48 | 0
| Protection systems maintenance | 15068.98 | 180039.57 | 3438.42 | 0
| Subtransmission asset maintenance - for DNSP with dual function assets | 66647.68 | 681640.98 | 361862.42 | 0
Other
OVERHEADS | Network overheads | 20781816.9634 | 172509531.8187 | 53077262.2539 | 45818341.6674
| Corporate overheads | 2861979.2244 | 114160507.5397 | 15445024.4417 | 32966149.8426
AUGMENTATION | Subtransmission substations, switching stations, zone substations | 962574.33 | 14190.75 | 1444345.01 | 233793.82
| Subtransmission lines | 100905.96 | 1403283.96 | 4072213.78 | 71458.01
| HV feeders | 621986.16 | 2637481.99 | 199863 | 435064.05
| Distribution substations | 145303.3 | 364419.31 | 101004.2 | 121909.01
| LV feeders | 87386.11 | 1987791.9 | 387721.16 | 262832.64
| Other assets | 3304.73 | 25364.29 | 13269.64 | 1080.48
CONNECTIONS | Simple and complex customer connections | 1546546.17 | 3601837.2 | 2362445.82 | 554907.32
EMERGENCY RESPONSE | Major storms | 8603.62 | 477089.8 | 158354.8 | 2277.77
Major event days
PUBLIC LIGHTING | All public lighting services | 3991435.5694 | 8968857.2625 | 9088618.156 | 8800941.2545
METERING | All metering services | 4880453.81 | 18052690.17 | 12963622.31 | 2806051.17
FEE-BASED SERVICES | All fee-based services | 251558.5999 | 19077628.1491 | 3923870.2057 | 6223659.4209
QUOTED SERVICES | All quoted services | 1131855.0237 | 21539103.064 | 568158.925 | 3073172.1391
REPLACEMENT | Poles | 2861901.3888 | 12112372.403 | 14969954.6015 | 189743.2773
| Pole top structures | 295811.862 | 2111744.7789 | 474746.531 | 47132.398
| Overhead conductors | 1842408.368 | 6453394.1371 | 1087360.574 | 99764.552
| Underground cables | 7518674.8 | 24332672.1522 | 47215447.45 | 1489777.8
| Service lines | 1751022.89 | 4657226.518 | 58454.13 | 4002.41
| Transformers | 3462238.5362 | 4082139.2348 | 2301663.9895 | 366448.3807
| Switchgear | 19886900.1587 | 25477875.7732 | 16569115.3462 | 625753.3849
Public lighting
| SCADA network control and protection systems | 3941582.5813 | 2776144.8237 | 4087462.2299 | 67222.5141
| Other | 15058138.9551 | 24089635.0257 | 20934967.4179 | 1046595.313
NON-NETWORK EXPENDITURE | IT and communications | 200609.07 | 24934266.36 | 21996302.78 | 33721586.88
| Motor vehicles | 1910892.19 | 3913837.79 | 5071037.53 | 8850967.75
| Buildings and property | 322432.33 | 5851256.43 | 11859930.31 | 41927746.5
| Other | 782766.08 | 11300.41 | 6284.04 | 501016.85
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.1 Public lighting
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
4.1 PUBLIC LIGHTING
There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.1.1 - DESCRIPTOR METRICS OVER YEAR
VOLUME (0's)
| LIGHT TYPE |  | 2016-17
POPULATION OF LIGHTS | DNSP to enter description for type of light
| 1000W/1500W MBI FLOODLIG |  | 14
| 1000W MBF |  | 8
| 1000W SON |  | 40
| 1000W SON FLOODLIGHT |  | 8
| 100W LED ALD |  | 10
| 100W MBI |  | 26
| 100W MBI FLOODLIGHT |  | 6
| 100W SON |  | 952
| 100W SON FLOODLIGHT |  | 8
| 100W SON - PARKVILLE |  | 14
| 100W SON -PLAIN |  | 454
| 1*17W LED |  | 1257
| 1*22W LED |  | 14099
| 125W/250W MBF FLOODLIGHT |  | 49
| 1*25W LED GE |  | 3389
| 125W MBF |  | 3638
| 125W MBF - BOURKE HILL |  | 26
| 125W MBF - HYDE PARK |  | 13
| 125W MBF - PARKVILLE |  | 5
| 125W MBF -PLAIN |  | 809
| 1*29W LED |  | 15570
| 135W SOX |  | 28
| 1*40W TF |  | 313
| 150W/250W MBI FLOODLIGHT |  | 38
| 150W SON |  | 19369
| 150W SON ACTIVE REACTOR |  | 2513
| 150W SON FLOODLIGHT |  | 181
| 150W SON GEC 'BOSTON 3' |  | 81
| 150W SON - HYDE PARK |  | 6
| 150W SON - PARKVILLE |  | 25
| 150W SON - PARKWAY 1 |  | 238
| 17W LED SY RRW |  | 47
| 180W SOX |  | 1
| 1*80W TF |  | 97
| 200W LED ALD |  | 14
| 2*14W TF - T5 PIERLITE M |  | 134
| 2*20W TF |  | 10411
| 2*250W SON FLOODLIGHT |  | 24
| 2*26W TF MACQUARIE DEC. |  | 14
| 2*400W SON FLOODLIGHT |  | 4
| 2*40W TF |  | 14
| 250W MBF |  | 14506
| 250W MBF - PARKWAY 1 |  | 727
| 250W MBI - SMARTPOLE |  | 18
| 250W SON |  | 23072
| 250W SON ACTIVE REACTOR |  | 3028
| 250W SON FLOODLIGHT |  | 1548
| 250W SON GEC 'BOSTON 3' |  | 93
| 250W SON - PARKVILLE |  | 13
| 250W SON - PARKWAY 1 |  | 55
| 2*80W MBF - BOURKE HILL |  | 15
| 2X14W TF - T5 PIERLIGHT |  | 91
| 400W MBF |  | 5148
| 400W MBF - B2229 |  | 123
| 400W MBF FLOODLIGHT |  | 87
| 400W MBF - PARKWAY 1 |  | 211
| 400W MBI |  | 25
| 400W MBI FLOODLIGHT |  | 86
| 400W MBI - SMARTPOLE |  | 15
| 400W SON |  | 1652
| 400W SON ACTIVE REACTOR |  | 315
| 400W SON FLOODLIGHT |  | 465
| 400W SON - PARKWAY 1 |  | 16
| 4*20W TF |  | 2
| 4*20W TF - WAVERLEY |  | 10
| 4*250W SON |  | 5
| 42W MBF SYLVANIA SUB ECO |  | 42382
| 4*40W TF - WAVERLEY |  | 2
| 4*600W SON |  | 2
| 500W MBI FLOODLIGHT |  | 1
| 50W MBF |  | 9298
| 50W MBF - BOURKE HILL |  | 18
| 50W MBF - NOSTALGIA |  | 101
| 50W MBF - PLAIN |  | 135
| 50W SON |  | 463
| 50W SON - NOSTALGIA |  | 3
| 50W SON -PLAIN |  | 2
| 600W SON |  | 1
| 700W MBF |  | 1
| 700W MBF FLOODLIGHT |  | 1
| 70W MBI |  | 178
| 70W MBI II |  | 368
| 70W MBI II AERO |  | 17
| 70W MBI - MACQUARIE DEC. |  | 119
| 70W SON |  | 1662
| 70W SON BOLLARD |  | 10
| 70W SON - BOURKE HILL |  | 7
| 70W SON FLOODLIGHT |  | 36
| 70W SON - GEC BOSTON 2 |  | 1
| 70W SON - NOSTALGIA |  | 112
| 70W SON - PARKVILLE |  | 7
| 70W SON -PLAIN |  | 179
| 70W SON - REGAL/FLINDERS |  | 5
| 80W MBF |  | 16658
| 80W MBF - BEGA+CURVE BRA |  | 59
| 80W MBF BOLLARD |  | 69
| 80W MBF - BOURKE HILL |  | 1245
| 80W MBF - GEC BOSTON 2 |  | 12
| 80W MBF - NOSTALGIA |  | 613
| 80W MBF - PLAIN |  | 507
| 80W MBF - REGAL/FLINDERS |  | 49
| 80W MBF - SYLVANIA SUBUR |  | 51609
| 80W MBF TOORAK |  | 145
| LED TRIAL |  | 67
| TH FLOODLIGHT |  | 28
4.1.2 - DESCRIPTOR METRICS ANNUALLY
VOLUMES & EXPENDITURE
SERVICE/SERVICE QUALITY | DESCRIPTOR METRIC | UNITS | 2016-17
LIGHT INSTALLATION | Major road light installation | 0's | 569
| Minor road light installation | 0's | 1056
| Number of poles installed | 0's | 1070
| Total cost | $0s | 1894598.65
LIGHT REPLACEMENT | Major road light replacement | 0's | 1662
| Minor road light replacement | 0's | 5703
| Number of poles replaced | 0's | 402
| Total cost | $0s | 7922777.86
LIGHT MAINTENANCE | Major road light maintenance | 0's | 27465
| Minor road light maintenance | 0's | 55457
| Number of poles installed | 0's | 251445
| Total cost | $0s | 21032475.73
QUALITY OF SUPPLY | Mean days to rectify/replace public lighting assets | days | 7
| GSO breaches | 0's | 431
| GSL payments | $0s | 6465
| Customer complaints | 0's | 3755
4.1.3 - COST METRICS
AVERAGE UNIT COST ($)
ACTIVITY TYPE | LIGHT TYPE |  | 2016-17
LIGHT INSTALLATION | DNSP to enter description for type of light
LED
| LRL P3 2016 |  | 499.4435
| Gerard P3 2016 |  | 453.7777
| LRL P3 Cut Off 2016 |  | 499.4435
| Gerard P3 Cut Off 2016 |  | 433.7294
| Gerard P4/P5 2016 |  | 423.7052
| GE Evolve P4/P5 2016 |  | 359.1049
| Gerard P4/P5 Cut off 16 |  | 433.7294
| Gerard P4/P5 RRRW 2016 |  | 433.7294
| LRL V5 2016 |  | 638.7729
| LRL V5 Cut Off 2016 |  | 638.7729
| Aldridge V3 2016 |  | 1117.7061
| Aldridge V1 2016 |  | 1117.7061
| Aldridge V1 Cut Off 2016 |  | 1105.4543
| Aldridge V1 High Cut Off 2016 |  | 1251.3619
HID
| 100W SON (P09) |  | 520.7103
| 150W SON Active Reactor |  | 761.2907
| 250W SON Active Reactor |  | 761.2907
| 400W SON Active Reactor |  | 850.3945
LIGHT REPLACEMENT | DNSP to enter description for type of light
LED
| LRL P3 2016 |  | 499.4435
| Gerard P3 2016 |  | 453.7777
| LRL P3 Cut Off 2016 |  | 499.4435
| Gerard P3 Cut Off 2016 |  | 433.7294
| Gerard P4/P5 2016 |  | 423.7052
| GE Evolve P4/P5 2016 |  | 359.1049
| Gerard P4/P5 Cut off 16 |  | 433.7294
| Gerard P4/P5 RRRW 2016 |  | 433.7294
| LRL V5 2016 |  | 638.7729
| LRL V5 Cut Off 2016 |  | 638.7729
| Aldridge V3 2016 |  | 1117.7061
| Aldridge V1 2016 |  | 1117.7061
| Aldridge V1 Cut Off 2016 |  | 1105.4543
| Aldridge V1 High Cut Off 2016 |  | 1251.3619
HID
| 100W SON (P09) |  | 520.7103
| 150W SON Active Reactor |  | 761.2907
| 250W SON Active Reactor |  | 761.2907
| 400W SON Active Reactor |  | 850.3945
LIGHT MAINTENANCE | DNSP to enter description for type of light
| LED1x29 |  | 29.7067
| MBF1x1000 (P09) |  | 88.7456
| MBF1x125 (P09) |  | 45.9827
| MBF1x250 (P09) |  | 52.4756
| MBF1x400 (P09) |  | 52.4756
| MBF1x42 (P09) |  | 42.885
| MBF1x50 (P09) |  | 46.1707
| MBF1x80 (P09) |  | 44.9095
| MBI1x100 (P09) |  | 61.2876
| MBI1x1000 (P09) |  | 112.0269
| MBI1x150 (P09) |  | 93.8699
| MBI1x250 (P09) |  | 60.63
| MBI1x400 (P09) |  | 61.6081
| MBI1x70 (P09) |  | 56.7666
| MBI1x70 II |  | 68.2908
| SON1x100 (P09) |  | 84.6534
| SON1x1000 (P09) |  | 87.7465
| SON1x150 (P09) |  | 72.7692
| SON1x150 AR |  | 65.3386
| SON1x250 (P09) |  | 76.1962
| SON1x250 AR |  | 66.3895
| SON1x400 (P09) |  | 74.1565
| SON1x400 AR |  | 92.7856
| SON1x50 (P09) |  | 48.624
| SON1x70 (P09) |  | 64.9997
| SON2x250 (P09) |  | 122.7677
| TF1x40 (P09) |  | 67.3877
| TF2x14 T5 (P09) |  | 53.5268
| TF2x20 (P09) |  | 55.9476
| TF2x26 (P09) |  | 46.6043
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.2 Metering
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
4.2 METERING
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.2.1 - METERING DESCRIPTOR METRIC
VOLUMES (0's)
Asset Category | Asset Subcategory | 2016-17
Meter Type 4 | Single phase meter population
Multi phase meter population
Current transformer connected meter population
Direct connect meter population
Meter Type 5 | Single phase meter population | 471605
| Multi phase meter population | 134610
| Current transformer connected meter population | 8317
| Direct connect meter population | 597898
Meter Type 6 | Single phase meter population | 1637498
| Multi phase meter population | 73643
| Current transformer connected meter population | 2549
| Direct connect meter population | 1708592
4.2.2 - COST METRICS
|  | VOLUMES (0's) | EXPENDITURE ($0's)
Service Subcategory | Meter Type | 2016-17 | 2016-17
Meter purchase | Meter Type 4
| Meter Type 5 | 64605 | 4326303
Meter Type 6
Meter testing | Meter Type 4
| Meter Type 5 | 459 | 11295
Meter Type 6
Meter investigation | Meter Type 4
| Meter Type 5 | 4464 | 763507
Meter Type 6
Scheduled meter reading | Meter Type 4
| Meter Type 5 | 2109965 | 2945442
| Meter Type 6 | 4560136 | 3701542
Special meter reading | Meter Type 4
| Meter Type 5 | 56788 | 554047
Meter Type 6
New meter installation | Meter Type 4
| Meter Type 5 | 0 | 0
Meter Type 6
Meter replacement | Meter Type 4
| Meter Type 5 | 64605 | 7638227
Meter Type 6
Meter maintenance | Meter Type 4
| Meter Type 5 | 7631 | 708588
Meter Type 6
Remote meter reading | Meter Type 4
Remote meter re-configuration | Meter Type 4
Other metering | Meter Type 4
| Meter Type 5 |  | 2398970
Meter Type 6
Meter Type 7
IT infrastructure capex | Meter Type 4 |  | 2304795
IT infrastructure opex | Meter Type 4 |  | 13350101
Communications infrastructure capex | Meter Type 4
Communications infrastructure opex | Meter Type 4
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.3 Fee-based services
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
4.3 ANCILLARY SERVICES - FEE BASED SERVICES
4.3.1 - COST METRICS FOR FEE-BASED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2016-17 |  | 2016-17
Common Fee-Based Services | Energisation |  | ED_FEE431_00001
| De-energisation |  | ED_FEE431_00002
| Re-energisation |  | ED_FEE431_00003
Miscellaneous Fee-Based Services | Site Establishment | 1038549.6894 | ED_FEE431_00004 | 31357
| Special meter reading for types 5 and 6 meters & MIMO Read | 4836883.247 | ED_FEE431_00005 | 599772
| Meter Test (for Type 5 and 6 meter) | 214999.5083 | ED_FEE431_00006 | 333
| Franchise current transformer (CT) meter install | 133275.8499 | ED_FEE431_00007 | 166
| Types 5-7 non-standard Meter Data Services | 0 | ED_FEE431_00008 | 0
| Emergency maintenance of failed metering equipment not owned by the DNSP | 0 | ED_FEE431_00009 | 13
| Off peak conversion | 141208.1769 | ED_FEE431_00010 | 1188
| Disconnection Visit (Site Visit Only - Payment Received) | 545303.0622 | ED_FEE431_00011 | 10338
| Disconnection Completed | 1422792.4203 | ED_FEE431_00012 | 10980
| Disconnection Visit (Disconnection Completed – Technical/Advanced) | 146739.6246 | ED_FEE431_00013 | 244
| Pillar/Pole Top Disconnection Completed | 54727.0836 | ED_FEE431_00014 | 68
| Pillar/Pole Top Site Visit | 11766.1443 | ED_FEE431_00015 | 29
| Reconnection/Disconnection Outside Normal Business Hours | 116149.0585 | ED_FEE431_00016 | 3931
| Recovery of Debt Collection Costs - Dishonoured Transactions | 0 | ED_FEE431_00017 | 0
| Retailer of Last Resort (ROLR) | 0 | ED_FEE431_00018 | 0
| Perform a statutory right where access is prevented | 0 | ED_FEE431_00019 | 2
| Vacant Property Disconnection | 2088865.8585 | ED_FEE431_00020 | 23435
| Vacant Property Site Visit | 588173.6367 | ED_FEE431_00021 | 26777
| Supply & connect temporary supply to one or more customers: Install & remove HV LL links - New | 0 | ED_FEE431_00022 | 0
| Supply & connect temporary supply to one or more customers: Break & remake HV bonds - New | 85657.4 | ED_FEE431_00023 | 10
| Supply & connect temporary supply to one or more customers: Break & remake LV bonds - New | 296270.11 | ED_FEE431_00024 | 89
| Design Information - underground urban residential subdivision (vacant lots) up to 5 lots | 32858.77 | ED_FEE431_00025 | 6
| Design Information - underground urban residential subdivision (vacant lots) 6 to 10 lots | 9442.71 | ED_FEE431_00026 | 11
| Design Information - underground urban residential subdivision (vacant lots) 11 to 40 lots | 46191.68 | ED_FEE431_00027 | 57
| Design Information - underground urban residential subdivision (vacant lots) over 40 lots | 23411.21 | ED_FEE431_00028 | 26
| Design Information - URD including Kisosk/HVC/PT (NOTE: Subset of overall Des Info costs.) | 36017.52 | ED_FEE431_00029 | 30
| Design Certification - underground urban residential subdivision (vacant lots) up to 5 lots | 20235.47 | ED_FEE431_00030 | 5
| Design Certification - underground urban residential subdivision (vacant lots) 6 to 10 lots | 17390.78 | ED_FEE431_00031 | 10
| Design Certification - underground urban residential subdivision (vacant lots) 11 to 40 lots | 112354.21 | ED_FEE431_00032 | 69
| Design Certification - underground urban residential subdivision (vacant lots) over 40 lots | 36114.14 | ED_FEE431_00033 | 25
| Design Certification - rural overhead subdivisions and rural extensions 1 to 5 poles | 40919.16 | ED_FEE431_00034 | 48
| Design Certification - rural overhead subdivisions and rural extensions 6 to 10 poles | 9133.34 | ED_FEE431_00035 | 6
| Design Certification - rural overhead subdivisions and rural extensions 11 or more poles | 2091.62 | ED_FEE431_00036 | 0
| Design Certification - underground commercial and industrial or rural subdivisions (vacant lots - no developments) up to 10 lots | 10430.26 | ED_FEE431_00037 | 11
| Design Certification - underground commercial and industrial or rural subdivisions (vacant lots - no developments) 11 to 40 lots | 9977.59 | ED_FEE431_00038 | 4
| Design Certification - underground commercial and industrial or rural subdivisions (vacant lots - no developments) over 40 lots | 1434.86 | ED_FEE431_00039 | 4
| Design Certification - Kisosk/HVC/PT (NOTE: Subset of overall Des Cert costs.) | 36838.39 | ED_FEE431_00040 | 104
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) first 10 lots - A Grade | 96276.68 | ED_FEE431_00041 | 422
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) first 10 lots - B Grade | 105664.87 | ED_FEE431_00042 | 560
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) first 10 lots - C Grade | 0 | ED_FEE431_00043 | 0
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) next 40 lots - A Grade | 57521.29 | ED_FEE431_00044 | 723
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) next 40 lots - B Grade | 198221.99 | ED_FEE431_00045 | 821
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) next 40 lots - C Grade | 0 | ED_FEE431_00046 | 0
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) remainder lots - A Grade | 2773.57 | ED_FEE431_00047 | 143
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) remainder lots - B Grade | 3100.99 | ED_FEE431_00048 | 34
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) remainder lots - C Grade | 0 | ED_FEE431_00049 | 0
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) travel | 49484.23 | ED_FEE431_00050 | 299
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 1-5 poles - A Grade | 14023.83 | ED_FEE431_00051 | 43
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 1-5 poles - B Grade | 98876.55 | ED_FEE431_00052 | 60
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 1-5 poles - C Grade | 0 | ED_FEE431_00053 | 0
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 6-10 poles - A Grade | 284.97 | ED_FEE431_00054 | 12
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 6-10 poles - B Grade | 12795.27 | ED_FEE431_00055 | 8
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 6-10 poles - C Grade | 0 | ED_FEE431_00056 | 0
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 11+ poles - A Grade | 1615.6 | ED_FEE431_00057 | 27
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 11+ poles - B Grade | 3771.77 | ED_FEE431_00058 | 50
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 11+ poles - C Grade | 0 | ED_FEE431_00059 | 0
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions - travel | 13986.99 | ED_FEE431_00060 | 131
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) first 10 lots A | 21551.15 | ED_FEE431_00061 | 20
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) first 10 lots B | 20642.81 | ED_FEE431_00062 | 18
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) first 10 lots C | 0 | ED_FEE431_00063 | 1
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) next 40 lots A | 3849.28 | ED_FEE431_00064 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) next 40 lots B | 4409.43 | ED_FEE431_00065 | 4
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) next 40 lots C | 0 | ED_FEE431_00066 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) remainder A | 169 | ED_FEE431_00067 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) remainder B | 1368.04 | ED_FEE431_00068 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) remainder C | 0 | ED_FEE431_00069 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) travel | 5346.03 | ED_FEE431_00070 | 56
| Inspection of service works by level 1 ASPs - HV or LV UG joint, ABS/enclosed switch | 7506.07 | ED_FEE431_00071 | 174
| Inspection of service works by level 1 ASPs - decommission substation | 103322.14 | ED_FEE431_00072 | 13
| Inspection of service works by level 1 ASPs - substation (kiosk/PT) or HV Sw cubicle | 243461.47 | ED_FEE431_00073 | 89
| Inspection of service work by level 2 ASPs - NOSW A Grade | 494383.12 | ED_FEE431_00074 | 5276
| Inspection of service work by level 2 ASPs - NOSW B Grade | 451536.76 | ED_FEE431_00075 | 5396
| Inspection of service work by level 2 ASPs - NOSW C Grade | 9970.97 | ED_FEE431_00076 | 126
| Contestable substation commissioning - underground urban residential subdivisions (vacant lots) | 96081.69 | ED_FEE431_00077 | 64
| Contestable substation commissioning - rural overhead subdivisions and rural extensions | 25046.74 | ED_FEE431_00078 | 41
| Contestable substation commissioning - underground commercial and industrial or rural subdivisions (vacant lots - no developments) | 54535.69 | ED_FEE431_00079 | 8
| Access Permits - underground residential urban subdivisions (vacant lots) | 754815.2 | ED_FEE431_00080 | 129
| Access Permits - rural overhead subdivisions and rural extensions | 271818.34 | ED_FEE431_00081 | 55
| Access Permits - underground commercial and industrial or rural subdivisions (vacant lots - no developments) | 109230.19 | ED_FEE431_00082 | 14
| Access Permits - commercial and industrial developments | 4160530.99 | ED_FEE431_00083 | 715
| Access Permits - asset relocation or street lighting | 1437727.25 | ED_FEE431_00084 | 440
| Clearance to Work | 1298263.46 | ED_FEE431_00085 | 413
| Notices of Arrangement | 130103.1 | ED_FEE431_00086 | 419
| Authorisation of ASP Level 1 | 323385 | ED_FEE431_00087 | 940
| Authorisation of ASP Level 2 | 380224 | ED_FEE431_00088 | 715
| Administration relating to work performed by ASPs - underground urban residential subdivision (vacant lots) up to 5 lots | 8012.76 | ED_FEE431_00089 | 6
| Administration relating to work performed by ASPs - underground urban residential subdivision (vacant lots) 6 to 10 lots | 15357.16 | ED_FEE431_00090 | 12
| Administration relating to work performed by ASPs - underground urban residential subdivision (vacant lots) 11 to 40 lots | 115312.12 | ED_FEE431_00091 | 61
| Administration relating to work performed by ASPs - underground urban residential subdivision (vacant lots) over 40 lots | 35895.48 | ED_FEE431_00092 | 24
| Administration relating to work perfromed by ASPs - rural overhead subdivisions and rural extensions up to 5 lots | 58636.03 | ED_FEE431_00093 | 46
| Administration relating to work perfromed by ASPs - rural overhead subdivisions and rural extensions 6 to 10 lots | 9811.06 | ED_FEE431_00094 | 6
| Administration relating to work perfromed by ASPs - rural overhead subdivisions and rural extensions 11 or more | 7047.51 | ED_FEE431_00095 | 1
| Administration relating to work perfromed by ASPs - subdivision involving substation/s (NOTE: Subset of overall Admin costs.) | 17738.07 | ED_FEE431_00096 | 106
| Supply of conveyancing information: Desk enquiry | 5323.77 | ED_FEE431_00097 | 0
| Supply of conveyancing information: Field visit | 57275.27 | ED_FEE431_00098 | 35
| Connection offer service: Basic 100A Connections NOT requiring a load slip | 711415.94 | ED_FEE431_00099 | 25831
| Connection offer service: Basic 100A Connections requiring a load slip or Basic Micro EG Connections >5kW or Basic Over 100A Connection Offer (new or existing site) | 1909108.29 | ED_FEE431_00100 | 15937
| Connection Offer Service: Standard Off-site or On-site augmentation work | 60512.38 | ED_FEE431_00101 | 1
| Connection Offer Service: Standard ASP 1 Connections | 192085.46 | ED_FEE431_00102 | 726
| Indirect costs - corporate allocations | 2753461.971 | ED_FEE431_00103
ED_FEE431_00104
ED_FEE431_00108
ED_FEE431_00109
ED_FEE431_00110
ED_FEE431_00111
ED_FEE431_00112
ED_FEE431_00113
ED_FEE431_00114
ED_FEE431_00115
ED_FEE431_00116
ED_FEE431_00117
ED_FEE431_00118
ED_FEE431_00119
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00471
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.4 Quoted services
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
4.4 ANCILLARY SERVICES - QUOTED SERVICES
4.4.1 - COST METRICS FOR QUOTED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2016-17 |  | 2016-17
Quoted Services | Access Stand-by-person | 299,869 | ED_QUO441_00001 | 126
| Rectification Works - Provision of service/additional crew | 111,204 | ED_QUO441_00002 | 48
| Rectification Works - fitting of tigrer tails | 3,375,763 | ED_QUO441_00003 | 2360
| Rectification Works - high load escorts | 93,620 | ED_QUO441_00004 | 5
| Design Information - rural overhead subdivisions and rural extensions | 27,527 | ED_QUO441_00005 | 51
| Design Information - underground commercial and industrial or rural subdivisions (vacant lots - no development) | 44,243 | ED_QUO441_00006 | 19
| Design Information - commercial and industrial developments | 995,038 | ED_QUO441_00007 | 670
| Design Information - asset relocation or street lighting | 496,169 | ED_QUO441_00008 | 433
| "Design Information - chambers, multi-kiosk, CBD Chambers |  | ED_QUO441_00009
| (NOTE: Subset of overall Des Info costs.)" | 162,236 | ED_QUO441_00010 | 127
| Design Certification - commercial and industrial development | 2,058,692 | ED_QUO441_00011 | 671
| Design Certification - asset relocation or street lighting | 846,917 | ED_QUO441_00012 | 472
| "Design Certification - chambers, multi-kiosks, CBD chambers |  | ED_QUO441_00013
| (NOTE: Subset of overall Des Cert costs.)" | 473,098 | ED_QUO441_00014 | 123
| Design Rechecking - underground urban residential subdivision (vacant lots) | 42,354 | ED_QUO441_00015 | 60
| Design Rechecking - rural overhead subdivisions and rural extensions | 13,738 | ED_QUO441_00016 | 12
| Design Rechecking - underground commercial and industrial or rural subdivisions (vacant lots - no development) | 5,679 | ED_QUO441_00017 | 7
| Design Rechecking - commercial and industrial developments | 228,202 | ED_QUO441_00018 | 200
| Design Rechecking - asset relocation or street lighting | 69,765 | ED_QUO441_00019 | 66
| Inspection of service works by level 1 ASPs - commercial and industrial developments | 2,102,427 | ED_QUO441_00020 | 1084
| Inspection of service works by level 1 ASPs - asset relocation or street lighting | 1,078,154 | ED_QUO441_00021 | 593
| Level 1 Reinspections | 2,358 | ED_QUO441_00022 | 124
| Level 2 Reinspections | 24,522 | ED_QUO441_00023 | 235
| Reinspection of Installation (CoCEW) | 224,615 | ED_QUO441_00024 | 1027
| Contestable substation commissioning - commercial and industrial developments | 824,492 | ED_QUO441_00025 | 215
| Contestable substation commissioning - asset relocation or street lighting. Volumes are a subset of the figures above. | 251,429 | ED_QUO441_00026 | 8
| "Contestable substation commissioning - complex and chamber substations. |  | ED_QUO441_00027
| (NOTE: Subset of overall Sub Commissioning costs.)" | 875,689 | ED_QUO441_00028 | 97
| Access Permits - complex and chamber substations | 1,026,089 | ED_QUO441_00029 | 168
| Access Stand-by-person |  | ED_QUO441_00030
| Administration relating to work perfromed by ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) | 58,144 | ED_QUO441_00031 | 21
| Administration relating to work perfromed by ASPs - commercial and industrial developments | 1,116,301 | ED_QUO441_00032 | 808
| Administration relating to work perfromed by ASPs - asset relocation or street lighting | 455,213 | ED_QUO441_00033 | 720
| "Administration relating to work perfromed by ASPs - guarantee of revenue, clarification meetings, variations to contract, reinspections etc. |  | ED_QUO441_00034
| (NOTE: Forecast volumes in addition to overall Admin volumes)" | 49,392 | ED_QUO441_00035 | 66
| Customer interface coodrination for contestable works | 77,319 | ED_QUO441_00036 | 7
| Preliminary enquiry service | 230,472 | ED_QUO441_00037 | 235
| "Connection Offer Service: |  | ED_QUO441_00038
| Standard Embedded Generation >5MVA capacity" | - | ED_QUO441_00039 | 0
| Rectification Works - Provision of service/additional crew |  | ED_QUO441_00040
| Rectification Works - fitting of tigrer tails |  | ED_QUO441_00041
| Rectification Works - high load escorts |  | ED_QUO441_00042
| Connection/relocation process facilitation | 1,975,344 | ED_QUO441_00043 | 1976
| Carrying out planning studies and analysis relating to distribution (including subtransmission and dual function assets) connection applications | 501,121 | ED_QUO441_00044 | 39
| Services involved in obtaining deeds of agreement in relation to property rights associated with contestable connection works | 122,621 | ED_QUO441_00045 | 300
| Investigation review and implementation of remedial actions associated with ASPs connection works | 27,472 | ED_QUO441_00046 | 18
| Indirect costs - corporate allocations | 5,385,884 | ED_QUO441_00047
ED_QUO441_00048
ED_QUO441_00049
ED_QUO441_00050
ED_QUO441_00051
ED_QUO441_00052
ED_QUO441_00053
ED_QUO441_00054
ED_QUO441_00055
ED_QUO441_00056
ED_QUO441_00057
ED_QUO441_00058
ED_QUO441_00059
ED_QUO441_00060
ED_QUO441_00061
ED_QUO441_00062
ED_QUO441_00063
ED_QUO441_00064
ED_QUO441_00065
ED_QUO441_00066
ED_QUO441_00067
ED_QUO441_00068
ED_QUO441_00069
ED_QUO441_00070
ED_QUO441_00071
ED_QUO441_00072
ED_QUO441_00073
ED_QUO441_00074
ED_QUO441_00075
ED_QUO441_00076
ED_QUO441_00077
ED_QUO441_00078
ED_QUO441_00079
ED_QUO441_00080
ED_QUO441_00081
ED_QUO441_00082
ED_QUO441_00083
ED_QUO441_00084
ED_QUO441_00085
ED_QUO441_00086
ED_QUO441_00087
ED_QUO441_00088
ED_QUO441_00089
ED_QUO441_00090
ED_QUO441_00091
ED_QUO441_00092
ED_QUO441_00093
ED_QUO441_00094
ED_QUO441_00095
ED_QUO441_00096
ED_QUO441_00097
ED_QUO441_00098
ED_QUO441_00099
ED_QUO441_00100
ED_QUO441_00101
ED_QUO441_00102
ED_QUO441_00103
ED_QUO441_00104
ED_QUO441_00105
ED_QUO441_00106
ED_QUO441_00107
ED_QUO441_00108
ED_QUO441_00109
ED_QUO441_00110
ED_QUO441_00111
ED_QUO441_00112
ED_QUO441_00113
ED_QUO441_00114
ED_QUO441_00115
ED_QUO441_00116
ED_QUO441_00117
ED_QUO441_00118
ED_QUO441_00119
ED_QUO441_00120
ED_QUO441_00121
ED_QUO441_00122
ED_QUO441_00123
ED_QUO441_00124
ED_QUO441_00125
ED_QUO441_00126
ED_QUO441_00127
ED_QUO441_00128
ED_QUO441_00129
ED_QUO441_00130
ED_QUO441_00131
ED_QUO441_00132
ED_QUO441_00133
ED_QUO441_00134
ED_QUO441_00135
ED_QUO441_00136
ED_QUO441_00137
ED_QUO441_00138
ED_QUO441_00139
ED_QUO441_00140
ED_QUO441_00141
ED_QUO441_00142
ED_QUO441_00143
ED_QUO441_00144
ED_QUO441_00145
ED_QUO441_00146
ED_QUO441_00147
ED_QUO441_00148
ED_QUO441_00149
ED_QUO441_00150
ED_QUO441_00151
ED_QUO441_00152
ED_QUO441_00153
ED_QUO441_00154
ED_QUO441_00155
ED_QUO441_00156
ED_QUO441_00157
ED_QUO441_00158
ED_QUO441_00159
ED_QUO441_00160
ED_QUO441_00161
ED_QUO441_00162
ED_QUO441_00163
ED_QUO441_00164
ED_QUO441_00165
ED_QUO441_00166
ED_QUO441_00167
ED_QUO441_00168
ED_QUO441_00169
ED_QUO441_00170
ED_QUO441_00171
ED_QUO441_00172
ED_QUO441_00173
ED_QUO441_00174
ED_QUO441_00175
ED_QUO441_00176
ED_QUO441_00177
ED_QUO441_00178
ED_QUO441_00179
ED_QUO441_00180
ED_QUO441_00181
ED_QUO441_00182
ED_QUO441_00183
ED_QUO441_00184
ED_QUO441_00185
ED_QUO441_00186
ED_QUO441_00187
ED_QUO441_00188
ED_QUO441_00189
ED_QUO441_00190
ED_QUO441_00191
ED_QUO441_00192
ED_QUO441_00193
ED_QUO441_00194
ED_QUO441_00195
ED_QUO441_00196
ED_QUO441_00197
ED_QUO441_00198
ED_QUO441_00199
ED_QUO441_00200
ED_QUO441_00201
ED_QUO441_00202
ED_QUO441_00203
ED_QUO441_00204
ED_QUO441_00205
ED_QUO441_00206
ED_QUO441_00207
ED_QUO441_00208
ED_QUO441_00209
ED_QUO441_00210
ED_QUO441_00211
ED_QUO441_00212
ED_QUO441_00213
ED_QUO441_00214
ED_QUO441_00215
ED_QUO441_00216
ED_QUO441_00217
ED_QUO441_00218
ED_QUO441_00219
ED_QUO441_00220
ED_QUO441_00221
ED_QUO441_00222
ED_QUO441_00223
ED_QUO441_00224
ED_QUO441_00225
ED_QUO441_00226
ED_QUO441_00227
ED_QUO441_00228
ED_QUO441_00229
ED_QUO441_00230
ED_QUO441_00231
ED_QUO441_00232
ED_QUO441_00233
ED_QUO441_00234
ED_QUO441_00235
ED_QUO441_00236
ED_QUO441_00237
ED_QUO441_00238
ED_QUO441_00239
ED_QUO441_00240
ED_QUO441_00241
ED_QUO441_00242
ED_QUO441_00243
ED_QUO441_00244
ED_QUO441_00245
ED_QUO441_00246
ED_QUO441_00247
ED_QUO441_00248
ED_QUO441_00249
ED_QUO441_00250
ED_QUO441_00251
ED_QUO441_00252
ED_QUO441_00253
ED_QUO441_00254
ED_QUO441_00255
ED_QUO441_00256
ED_QUO441_00257
ED_QUO441_00258
ED_QUO441_00259
ED_QUO441_00260
ED_QUO441_00261
ED_QUO441_00262
ED_QUO441_00263
ED_QUO441_00264
ED_QUO441_00265
ED_QUO441_00266
ED_QUO441_00267
ED_QUO441_00268
ED_QUO441_00269
ED_QUO441_00270
ED_QUO441_00271
ED_QUO441_00272
ED_QUO441_00273
ED_QUO441_00274
ED_QUO441_00275
ED_QUO441_00276
ED_QUO441_00277
ED_QUO441_00278
ED_QUO441_00279
ED_QUO441_00280
ED_QUO441_00281
ED_QUO441_00282
ED_QUO441_00283
ED_QUO441_00284
ED_QUO441_00285
ED_QUO441_00286
ED_QUO441_00287
ED_QUO441_00288
ED_QUO441_00289
ED_QUO441_00290
ED_QUO441_00291
ED_QUO441_00292
ED_QUO441_00293
ED_QUO441_00294
ED_QUO441_00295
ED_QUO441_00296
ED_QUO441_00297
ED_QUO441_00298
ED_QUO441_00299
ED_QUO441_00300
ED_QUO441_00301
ED_QUO441_00302
ED_QUO441_00303
ED_QUO441_00304
ED_QUO441_00305
ED_QUO441_00306
ED_QUO441_00307
ED_QUO441_00308
ED_QUO441_00309
ED_QUO441_00310
ED_QUO441_00311
ED_QUO441_00312
ED_QUO441_00313
ED_QUO441_00314
ED_QUO441_00315
ED_QUO441_00316
ED_QUO441_00317
ED_QUO441_00318
ED_QUO441_00319
ED_QUO441_00320
ED_QUO441_00321
ED_QUO441_00322
ED_QUO441_00323
ED_QUO441_00324
ED_QUO441_00325
ED_QUO441_00326
ED_QUO441_00327
ED_QUO441_00328
ED_QUO441_00329
ED_QUO441_00330
ED_QUO441_00331
ED_QUO441_00332
ED_QUO441_00333
ED_QUO441_00334
ED_QUO441_00335
ED_QUO441_00336
ED_QUO441_00337
ED_QUO441_00338
ED_QUO441_00339
ED_QUO441_00340
ED_QUO441_00341
ED_QUO441_00342
ED_QUO441_00343
ED_QUO441_00344
ED_QUO441_00345
ED_QUO441_00346
ED_QUO441_00347
ED_QUO441_00348
ED_QUO441_00349
ED_QUO441_00350
ED_QUO441_00351
ED_QUO441_00352
ED_QUO441_00353
ED_QUO441_00354
ED_QUO441_00355
ED_QUO441_00356
ED_QUO441_00357
ED_QUO441_00358
ED_QUO441_00359
ED_QUO441_00360
ED_QUO441_00361
ED_QUO441_00362
ED_QUO441_00363
ED_QUO441_00364
ED_QUO441_00365
ED_QUO441_00366
ED_QUO441_00367
ED_QUO441_00368
ED_QUO441_00369
ED_QUO441_00370
ED_QUO441_00371
ED_QUO441_00372
ED_QUO441_00373
ED_QUO441_00374
ED_QUO441_00375
ED_QUO441_00376
ED_QUO441_00377
ED_QUO441_00378
ED_QUO441_00379
ED_QUO441_00380
ED_QUO441_00381
ED_QUO441_00382
ED_QUO441_00383
ED_QUO441_00384
ED_QUO441_00385
ED_QUO441_00386
ED_QUO441_00387
ED_QUO441_00388
ED_QUO441_00389
ED_QUO441_00390
ED_QUO441_00391
ED_QUO441_00392
ED_QUO441_00393
ED_QUO441_00394
ED_QUO441_00395
ED_QUO441_00396
ED_QUO441_00397
ED_QUO441_00398
ED_QUO441_00399
ED_QUO441_00400
ED_QUO441_00401
ED_QUO441_00402
ED_QUO441_00403
ED_QUO441_00404
ED_QUO441_00405
ED_QUO441_00406
ED_QUO441_00407
ED_QUO441_00408
ED_QUO441_00409
ED_QUO441_00410
ED_QUO441_00411
ED_QUO441_00412
ED_QUO441_00413
ED_QUO441_00414
ED_QUO441_00415
ED_QUO441_00416
ED_QUO441_00417
ED_QUO441_00418
ED_QUO441_00419
ED_QUO441_00420
ED_QUO441_00421
ED_QUO441_00422
ED_QUO441_00423
ED_QUO441_00424
ED_QUO441_00425
ED_QUO441_00426
ED_QUO441_00427
ED_QUO441_00428
ED_QUO441_00429
ED_QUO441_00430
ED_QUO441_00431
ED_QUO441_00432
ED_QUO441_00433
ED_QUO441_00434
ED_QUO441_00435
ED_QUO441_00436
ED_QUO441_00437
ED_QUO441_00438
ED_QUO441_00439
ED_QUO441_00440
ED_QUO441_00441
ED_QUO441_00442
ED_QUO441_00443
ED_QUO441_00444
ED_QUO441_00445
ED_QUO441_00446
ED_QUO441_00447
ED_QUO441_00448
ED_QUO441_00449
ED_QUO441_00450
ED_QUO441_00451
ED_QUO441_00452
ED_QUO441_00453
ED_QUO441_00454
ED_QUO441_00455
ED_QUO441_00456
ED_QUO441_00457
ED_QUO441_00458
ED_QUO441_00459
ED_QUO441_00460
ED_QUO441_00461
ED_QUO441_00462
ED_QUO441_00463
ED_QUO441_00464
ED_QUO441_00465
ED_QUO441_00466
ED_QUO441_00467
ED_QUO441_00468
ED_QUO441_00469
ED_QUO441_00470
ED_QUO441_00471
ED_QUO441_00472
ED_QUO441_00473
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.2 Asset Age Profile
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
5.2 ASSET AGE PROFILE
There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data.
5.2.1 - ASSET AGE PROFILE
|  | ECONOMIC LIFE (YEARS) |  | INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR
ASSET GROUP | ASSET CATEGORY | MEAN | STANDARD DEVIATION | 2016-17 | 2015-16 | 2014-15 | 2013-14 | 2012-13 | 2011-12 | 2010-11 | 2009-10 | 2008-09 | 2007-08 | 2006-07 | 2005-06 | 2004-05 | 2003-04 | 2002-03 | 2001-02 | 2000-01 | 1999-00 | 1998-99 | 1997-98 | 1996-97 | 1995-96 | 1994-95 | 1993-94 | 1992-93 | 1991-92 | 1990-91 | 1989-90 | 1988-89 | 1987-88 | 1986-87 | 1985-86 | 1984-85 | 1983-84 | 1982-83 | 1981-82 | 1980-81 | 1979-80 | 1978-79 | 1977-78 | 1976-77 | 1975-76 | 1974-75 | 1973-74 | 1972-73 | 1971-72 | 1970-71 | 1969-70 | 1968-69 | 1967-68 | 1966-67 | 1965-66 | 1964-65 | 1963-64 | 1962-63 | 1961-62 | 1960-61 | 1959-60 | 1958-59 | 1957-58 | 1956-57 | 1955-56 | 1954-55 | 1953-54 | 1952-53 | 1951-52 | 1950-51 | 1949-50 | 1948-49 | 1947-48 | 1946-47 | 1945-46 | 1944-45 | 1943-44 | 1942-43 | 1941-42 | 1940-41 | 1939-40 | 1938-39 | 1937-38 | 1936-37 | 1935-36 | 1934-35 | 1933-34 | 1932-33 | 1931-32 | 1930-31 | 1929-30 | 1928-29 | 1927-28 | 1926-27 | 1925-26 | 1924-25 | 1923-24 | 1922-23 | 1921-22 | 1920-21 | 1919-20 | 1918-19 | 1917-18 | 1916-17 | 1915-16 | 1914-15 | 1913-14 | 1912-13 | 1911-12 | 1910-11 | 1909-10 | 1908-09
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole | 6.4 | 3.67 | 802 | 585 | 1241 | 1486 | 1895 | 2162 | 1823 | 2930 | 2349 | 2780 | 1400 | 1081 | 1041 | 855 | 990 | 519 | 344 | 320 | 303 | 301 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Wood | 40.99 | 13.26 | 2135 | 2021 | 2697 | 3178 | 3503 | 4192 | 3844 | 3655 | 3055 | 3018 | 2633 | 2237 | 1926 | 2205 | 1744 | 1682 | 1455 | 1492 | 1528 | 1893 | 2056 | 2979 | 3019 | 2649 | 1801 | 1541 | 3769 | 3867 | 3270 | 2786 | 4454 | 3724 | 3255 | 2388 | 3640 | 6186 | 5631 | 5413 | 4451 | 3351 | 3774 | 2595 | 3612 | 4484 | 3381 | 6643 | 6521 | 5604 | 6737 | 9785 | 12219 | 10843 | 13629 | 9410 | 13923 | 7458 | 9137 | 5863 | 7357 | 4532 | 2323 | 625 | 3226 | 646 | 1250 | 548 | 861 | 154 | 26 | 720 | 626 |  | 8 |  | 880 | [11 empty] | 347 | [19 empty] | 1.21
| > 1 kV & < = 11 kV; Wood | 40.99 | 13.26 | 1231 | 2005 | 2019 | 2611 | 2940 | 2902 | 2809 | 2701 | 2897 | 2230 | 2121 | 1886 | 1935 | 1996 | 1492 | 1580 | 1520 | 2149 | 1416 | 1505 | 1177 | 1499 | 1916 | 1635 | 1370 | 1518 | 2475 | 2473 | 1957 | 1931 | 2484 | 2633 | 2281 | 1463 | 2420 | 3632 | 2776 | 2070 | 2039 | 1759 | 1884 | 1770 | 3049 | 2839 | 2094 | 3031 | 2809 | 3162 | 1878 | 3280 | 3802 | 3209 | 3666 | 2337 | 1789 | 902 | 1773 | 1162 | 623 | 222 | 109 | 108 | 39 | 35 | 17 | 1 | 1 | 0 | 24 | 1 | 0 |  | 8 |  | 0 | [11 empty] | 0
| ˃ 11 kV & < = 22 kV; Wood | 40.99 | 13.26 | 24 | 22 | 33 | 27 | 22 | 10 | 9 | 9 | 38 | 53 | 11 | 27 | 17 | 67 | 58 | 34 | 62 | 81 | 40 | 35 | 23 | 28 | 28 | 6 | 29 | 12 | 14 | 28 | 17 | 14 | 32 | 8 | 14 | 12 | 22 | 14 | 11 | 1 | 0 | 0 | 0 | 19 | 5 | 9 | 38 | 108 | 33 | 188 | 0 | 0 | 81 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 22 kV & < = 66 kV; Wood | 40.99 | 13.26 | 125 | 175 | 218 | 192 | 299 | 264 | 288 | 351 | 361 | 259 | 209 | 126 | 194 | 201 | 202 | 224 | 133 | 114 | 92 | 114 | 90 | 121 | 189 | 217 | 197 | 320 | 185 | 219 | 141 | 108 | 316 | 271 | 250 | 252 | 546 | 634 | 307 | 359 | 243 | 244 | 390 | 196 | 217 | 343 | 199 | 463 | 582 | 525 | 424 | 610 | 699 | 753 | 569 | 396 | 228 | 110 | 248 | 229 | 43 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 |  | 65 |  | 0 | [11 empty] | 0
| > 66 kV & < = 132 kV; Wood | 40.99 | 13.26 | 19 | 28 | 20 | 11 | 17 | 21 | 22 | 48 | 35 | 55 | 16 | 9 | 18 | 11 | 13 | 11 | 34 | 79 | 12 | 8 | 16 | 19 | 35 | 61 | 13 | 14 | 32 | 40 | 11 | 15 | 17 | 18 | 19 | 30 | 406 | 328 | 48 | 32 | 77 | 107 | 72 | 502 | 129 | 122 | 17 | 166 | 141 | 373 | 240 | 186 | 64 | 165 | 117 | 104 | 67 | 0 | 46 | 99 | 14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 132 kV; Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Concrete | 40.38 | 17.3 | 5 | 1 | 2 | 12 | 50 | 47 | 25 | 19 | 2 | 6 | 5 | 7 | 2 | 14 | 0 | 0 | 11 | 6 | 0 | 1 | 0 | 21 | 17 | 42 | 5 | 59 | 12 | 44 | 0 | 0 | 2 | 23 | 7 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 11 | 6 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 1 | 16 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 1 kV & < = 11 kV; Concrete | 40.38 | 17.3 | 18 | 5 | 9 | 21 | 16 | 13 | 19 | 7 | 2 | 3 | 9 | 8 | 3 | 7 | 3 | 0 | 9 | 0 | 3 | 0 | 0 | 52 | 8 | 62 | 29 | 2 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| ˃ 11 kV & < = 22 kV; Concrete | 40.38 | 17.3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 22 kV & < = 66 kV; Concrete | 40.38 | 17.3 | 59 | 36 | 42 | 90 | 148 | 160 | 346 | 327 | 100 | 112 | 415 | 408 | 306 | 153 | 114 | 101 | 74 | 85 | 13 | 59 | 6 | 60 | 10 | 50 | 15 | 85 | 41 | 46 | 38 | 0 | 38 | 6 | 0 | 57 | 4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 20 | 0 | 0 | 0 | 2 | 1 | 0 | 7 | 1 | 45 | 22 | 1 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 66 kV & < = 132 kV; Concrete | 40.38 | 17.3 | 28 | 30 | 40 | 31 | 33 | 245 | 286 | 404 | 183 | 64 | 81 | 34 | 44 | 142 | 257 | 62 | 139 | 66 | 2 | 1 | 17 | 30 | 2 | 1 | 4 | 0 | 99 | 28 | 2 | 46 | 14 | 100 | 28 | 8 | 15 | 17 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 7 | 2 | 7 | 6 | 2 | 10 | 0 | 3 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 132 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Steel | 31.97 | 16.38 | 114 | 32 | 26 | 92 | 10 | 40 | 50 | 46 | 22 | 155 | 430 | 337 | 279 | 205 | 151 | 102 | 99 | 536 | 11 | 47 | 33 | 43 | 10 | 24 | 10 | 166 | 111 | 184 | 4 | 114 | 10 | 2 | 152 | 271 | 946 | 605 | 334 | 80 | 53 | 13 | 78 | 13 | 11 | 28 | 24 | 203 | 15 | 45 | 44 | 99 | 30 | 103 | 60 | 78 | 33 | 18 | 20 | 44 | 16 | 3 | 8 | 1 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 3 |  | 0 |  | 0 | [11 empty] | 0
| > 1 kV & < = 11 kV; Steel | 31.97 | 16.38 | 3 | 0 | 1 | 20 | 0 | 6 | 4 | 38 | 0 | 1 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 2 | 0 | 0 | 0 | 7 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| ˃ 11 kV & < = 22 kV; Steel | 31.97 | 16.38 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 22 kV & < = 66 kV; Steel | 31.97 | 16.38 | 2 | 0 | 5 | 1 | 9 | 24 | 100 | 2 | 1 | 21 | 46 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 66 kV & < = 132 kV; Steel | 31.97 | 16.38 | 7 | 10 | 68 | 73 | 8 | 8 | 9 | 14 | 7 | 6 | 0 | 14 | 11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 2 | 0 | 36 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | [11 empty] | 0
| > 132 kV; Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV | 40.99 | 13.26 | 48.9 | 69.98 | 90.73 | 138.45 | 105.68 | 148.01 | 156.87 | 127.04 | 137.99 | 121.27 | 104.09 | 117.78 | 106.26 | 86.63 | 101.22 | 71.56 | 64.95 | 70.33 | 59.48 | 47.31 | 54.39 | 51.97 | 64.79 | 64.59 | 46.08 | 38.76 | 87.03 | 99.39 | 91.69 | 68.22 | 105.11 | 100.93 | 116.39 | 95.6 | 86.6 | 167.31 | 162.92 | 339.35 | 218.58 | 146.2 | 148.74 | 150.72 | 163.53 | 268.2 | 170.13 | 282.04 | 191.84 | 226.85 | 307.88 | 425.26 | 346.65 | 509.74 | 514.54 | 535.37 | 863.74 | 507.95 | 459.32 | 595.33 | 540.23 | 289.91 | 359.42 | 365.95 | 103.99 | 59.29 | 50.72 | 39.97 | 56.14 | 22.06 | 40.64 | 19.73 | 6.08 | 9.69 | 22.74 | 40.5 | 0 | 0 | 0 | 52.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.34 | 65.03 | 0 | 0 | 0 | 0 | 0 | 0 | 2.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 40.99 | 13.26 | 151.37 | 195.28 | 114.79 | 162 | 162.49 | 131.55 | 168 | 143.34 | 162.84 | 128.27 | 138.58 | 117.92 | 179.28 | 105.21 | 135.63 | 119.21 | 118.94 | 154.3 | 139.52 | 101.04 | 69.35 | 62.06 | 62.55 | 63.2 | 56.69 | 52.08 | 77.21 | 83.7 | 70.67 | 64.86 | 83.53 | 96.77 | 83.06 | 61.6 | 57.23 | 112.85 | 103.2 | 263.98 | 174.44 | 121.24 | 174.63 | 156.9 | 139.84 | 201.79 | 231.8 | 351.55 | 186.63 | 169.92 | 323.76 | 341.14 | 252.98 | 252.86 | 296.04 | 211.4 | 510.09 | 179.72 | 284.12 | 215.6 | 212.35 | 102.14 | 83.4 | 151.37 | 15.8 | 31.19 | 13.59 | 27.65 | 1.18 | 0 | 0 | 0 | 9.63 | 0 | 0 | 0 | 0 | 0 | 0 | 9.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; SWER | 40.99 | 13.26 | 0 | 0 | 0.11 | 0 | 0 | 6.83 | 0 | 0 | 0 | 0 | 0.34 | 0.12 | 0 | 0.27 | 0 | 0 | 0.19 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 0 | 0.93 | 0.11 | 0.11 | 3.69 | 0.11 | 39.36 | 1.58 | 0.11 | 0.12 | 0 | 0 | 0 | 0.11 | 2.36 | 0 | 0 | 4.48 | 0.11 | 0 | 0.51 | 1.12 | 0 | 0 | 0 | 0 | 0 | 0 | 11.25 | 6.17 | 0 | 0 | 0 | 0 | 42.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Single-Phase | 40.99 | 13.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.04 | 0.27 | 0 | 0 | 2.08 | 5.73 | 0.25 | 0.37 | 2.18 | 11.4 | 2.95 | 3.56 | 0.69 | 0 | 0.5 | 0 | 0 | 0.23 | 1.21 | 1.22 | 0 | 0.77 | 0 | 0.18 | 0 | 0.19 | 0.85 | 0.56 | 0 | 1.12 | 0 | 0 | 0 | 0 | 0 | 6.21 | 6.13 | 7.17 | 5.64 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase | 40.99 | 13.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0.74 | 2.87 | 5.18 | 0 | 0.66 | 0 | 1.18 | 0 | 0 | 2.67 | 0 | 0 | 0 | 0.09 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.77 | 1.82 | 0 | 0 | 25.32 | 0 | 0 | 0 | 0 | 0 | 11.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV | 40.99 | 13.26 | 18.51 | 10.87 | 6.3 | 12.94 | 31.67 | 21.39 | 49.31 | 70.02 | 21.09 | 58.94 | 34.74 | 78.5 | 31.57 | 5.84 | 15.98 | 19.12 | 25.09 | 12.97 | 2.67 | 24.81 | 1.83 | 6.93 | 4.59 | 30.42 | 1.86 | 20.74 | 1.59 | 15.15 | 6.41 | 0.89 | 0.96 | 1.05 | 25.11 | 8.28 | 12.23 | 25.57 | 41.62 | 70.4 | 15.86 | 9.76 | 38.46 | 18.72 | 12.32 | 20.71 | 7.19 | 16.05 | 13.11 | 23.23 | 59.28 | 95.36 | 48.22 | 10.1 | 129.2 | 96.8 | 87.19 | 25.86 | 25.21 | 85 | 0 | 0 | 3.13 | 19.97 | 11.22 | 5.38 | 4.69 | 6.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 40.99 | 13.26 | 6.27 | 3.44 | 16.4 | 49.42 | 12.02 | 20.62 | 73.65 | 19.25 | 0.34 | 10.45 | 7.64 | 0 | 4.27 | 10.53 | 19.59 | 13.52 | 3.54 | 3.92 | 0 | 4.67 | 1.7 | 0 | 35.47 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 3.94 | 4.51 | 50.68 | 0.05 | 8.79 | 16.2 | 2.13 | 0.71 | 29.02 | 28.83 | 20.68 | 0.49 | 12.69 | 27.49 | 24.79 | 32.18 | 4.35 | 3.74 | 13.09 | 115.94 | 8.57 | 0.4 | 14.64 | 48.49 | 42.55 | 10.3 | 53.19 | 189 | 0 | 0 | 0 | 11.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV | 43.58 | 16.79 | 151.41 | 153.79 | 154.87 | 174.66 | 172.07 | 223.09 | 188.2 | 133.63 | 152.9 | 132.91 | 123.39 | 148.7 | 171.05 | 136.65 | 140.84 | 100.93 | 97.57 | 99.82 | 100.99 | 65 | 65.32 | 63.03 | 75.57 | 53.13 | 70.29 | 50.82 | 42.76 | 26.8 | 52.98 | 75.49 | 33.93 | 39.35 | 49.45 | 44.79 | 59.57 | 118.4 | 118.61 | 99.09 | 138.66 | 99.34 | 108.69 | 70.57 | 53.33 | 94.51 | 45.05 | 85.66 | 47.14 | 58.43 | 71.07 | 108.28 | 38.19 | 94.76 | 99.83 | 84.47 | 123.65 | 75.27 | 104.81 | 102.11 | 85.67 | 56.63 | 73.13 | 48.08 | 82.03 | 13.38 | 6.26 | 15.61 | 14.02 | 4.86 | 19.7 | 8.34 | 0.87 | 2.8 | 4.98 | 11.29 | 0.57 | 0.63 | 0.8 | 4.04 | 0.83 | 0.82 | 0.62 | 0.59 | 0.48 | 0.71 | 0.54 | 0.61 | 1.04 | 0.79 | 0.74 | 20.72 | 13.38 | 0.59 | 0.47 | 0 | 0 | 0.47 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 46.12 | 18.57 | 116.4 | 123.05 | 120.6 | 255.3 | 268.71 | 284.43 | 288.05 | 236.07 | 215.17 | 160.82 | 188.73 | 144.09 | 129.1 | 104.61 | 112.81 | 91.9 | 120.18 | 115.92 | 110.07 | 84.8 | 51.23 | 61.13 | 89.39 | 55.42 | 70.94 | 84.32 | 63.55 | 50.79 | 59.52 | 84.99 | 44.14 | 43.7 | 71.57 | 38.59 | 71.12 | 92 | 106.39 | 131.55 | 154.95 | 133.33 | 118.43 | 90.64 | 91.27 | 110.6 | 70.56 | 94.17 | 62.3 | 115.35 | 72.8 | 137.87 | 87.39 | 125.76 | 122.86 | 176.81 | 239.77 | 132.88 | 162.08 | 159.95 | 178.68 | 150.49 | 162.06 | 182.15 | 197.46 | 25.64 | 34.42 | 24.27 | 25.61 | 16.74 | 29.63 | 15.72 | 1.56 | 4.15 | 13.65 | 29.68 | 2.18 | 1.73 | 1.56 | 27.35 | 3.96 | 6.53 | 2.73 | 1.9 | 0.94 | 0.8 | 0.66 | 1.84 | 2.63 | 17.22 | 10.48 | 62.66 | 51.45 | 2.79 | 0.47 | 0.48 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV | 48.93 | 11.86 | 14.81 | 7.14 | 2.63 | 7.33 | 15.4 | 20.25 | 20.35 | 29.42 | 19.39 | 8.15 | 18.23 | 5.58 | 10.97 | 0.92 | 0.88 | 5.41 | 6.24 | 9.62 | 1 | 2.55 | 0.71 | 7.3 | 0.23 | 2.52 | 0.33 | 0.47 | 0.87 | 0.55 | 0.69 | 0.21 | 1.28 | 0.49 | 0.1 | 0.52 | 0.25 | 0.03 | 0.21 | 0.2 | 0.31 | 0.27 | 0.62 | 3.73 | 9.36 | 11.49 | 6.67 | 12.99 | 10.03 | 2.96 | 0.66 | 13.45 | 16.77 | 13.47 | 28.21 | 27.27 | 26.46 | 0.04 | 0.1 | 0.35 | 0.06 | 0.49 | 2.57 | 43.66 | 15.2 | 0.06 | 19.77 | 7.06 | 4.12 | 1.39 | 19.17 | 16.36 | 42.27 | 0.65 | 0 | 0.91 | 2.59 | 0.02 | 3.2 | 1.05 | 0.24 | 0.21 | 20.55 | 0 | 0 | 0 | 0 | 9.96 | 1.42 | 8.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV | 48.93 | 11.86 | 0 | 0 | 0.55 | 6.85 | 0.48 | 0.58 | 0.83 | 0.13 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 49.62 | 7.81 | 36.12 | 17.71 | 39.14 | 32.26 | 23.22 | 19.22 | 27.17 | 24.15 | 0.38 | 18.84 | 0.25 | 0.31 | 5.61 | 4.31 | 16.4 | 8.29 | 0 | 6.61 | 0.57 | 9.46 | 0.24 | 0 | 0.45 | 0.45 | 0 | 0 | 0.13 | 0.97 | 0 | 11.15 | 0 | 0.14 | 0.13 | 0 | 3.24 | 3.4 | 14.68 | 27.22 | 7.51 | 13.81 | 9.5 | 4.77 | 10.48 | 3.03 | 77.42 | 42.07 | 27.16 | 8.88 | 37.6 | 18.56 | 5.09 | 16.23 | 0 | 0 | 26.84 | 0 | 0.17 | 2.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 38.15 | 20.5 | 1745 | 2163 | 2354 | 2496 | 2396 | 2135 | 1437 | 1424 | 3575 | 1422 | 1700 | 1715 | 2045 | 1716 | 896 | 739 | 708 | 975 | 999 | 716 | 429 | 871 | 1117 | 1216 | 1377 | 934 | 1120 | 727 | 459 | 481 | 316 | 769 | 477 | 859 | 552 | 1681 | 1137 | 665 | 435 | 620 | 765 | 588 | 336 | 391 | 687 | 441 | 432 | 491 | 229 | 268 | 111 | 243 | 161 | 193 | 11712 | 105 | 83 | 3175 | 8 | 8 | 6 | 8 | 7 | 13 | 7 | 7 | 4 | 3 | 1 | 2 | 1 | 2 | 3 | 0 | 5 | 1 | 0 | 5 | 1 | 7 | 4 | 1 | 1 | 0 | 1 | 12 | 15 | 4 | 11 | 9 | 11 | 11 | 0 | 4 | 3 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type | 30 | 5 | 19947 | 24226 | 25455 | 26781 | 19589 | 24355 | 19616 | 22037 | 26175 | 20693 | 16482 | 15422 | 9762 | 9613 | 7896 | 7207 | 5932 | 4290 | 4076 | 4436 | 4508 | 5678 | 6154 | 5587 | 4311 | 3700 | 8390 | 8276 | 6780 | 5786 | 7881 | 7791 | 6365 | 5080 | 3684 | 6208 | 6039 | 12311 | 6151 | 4449 | 4069 | 3990 | 3857 | 7588 | 3532 | 6161 | 4630 | 6405 | 8948 | 10256 | 7223 | 11331 | 14735 | 12987 | 23262 | 12282 | 14798 | 19693 | 16356 | 7942 | 9235 | 11462 | 3430 | 2003 | 1391 | 1335 | 1551 | 668 | 981 | 318 | 41 | 272 | 907 | 0 | 0 | 1 | 0 | 1466 | 1 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3049 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 3576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type | 30 | 5 | 837 | 800 | 771 | 810 | 654 | 754 | 563 | 684 | 663 | 612 | 560 | 1123 | 1639 | 701 | 495 | 439 | 515 | 384 | 369 | 358 | 382 | 424 | 440 | 402 | 321 | 326 | 516 | 528 | 484 | 395 | 526 | 492 | 456 | 337 | 309 | 465 | 432 | 804 | 454 | 345 | 279 | 243 | 265 | 336 | 341 | 438 | 300 | 475 | 515 | 898 | 383 | 708 | 973 | 1055 | 1253 | 760 | 1086 | 1283 | 928 | 594 | 575 | 670 | 237 | 121 | 67 | 56 | 73 | 60 | 77 | 9 | 9 | 6 | 51 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| ˂ = 11 kV ; Residential ; Complex Type | 44.88 | 21.5 | 9600.04 | 5245.04 | 4876.04 | 5453.04 | 5079.04 | 7001.04 | 4709.04 | 3950.04 | 3657.04 | 3432.04 | 3738.04 | 3522.04 | 2718.04 | 3042.04 | 2732.04 | 2132.04 | 2545.04 | 2376.04 | 2972.04 | 2032.04 | 3334.04 | 2434.04 | 3275.04 | 2468.04 | 2476.04 | 2293.04 | 2129.04 | 1943.04 | 3526.04 | 1509.04 | 2190.04 | 1853.04 | 2431.04 | 1106.04 | 3015.04 | 4343.04 | 6247.04 | 8381.04 | 6540.04 | 5163.04 | 4177.04 | 627.04 | 1170.04 | 2571.04 | 251.04 | 3831.04 | 1245.04 | 1430.04 | 2134.04 | 2827.04 | 940.04 | 3258.04 | 2742.04 | 2039.04 | 3916.04 | 1428.04 | 4336.04 | 3446.04 | 2146.04 | 2658.04 | 1009.02 | 1078.04 | 543.04 | 401.04 | 145.04 | 270.02 | 486.04 | 502.02 | 144.02 | 486.04 | 34.04 | 201.04 | 711.02 | 0 | 0 | 0 | 0 | 23.02 | 1.02 | 1.01 | 4.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1163.02 | 28.02 | 0 | 0 | 0 | 0 | 0 | 0 | 1347.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3451.08
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type | 44.88 | 21.5 | 927.01 | 900.01 | 1117.01 | 691.01 | 799.01 | 886.01 | 697.01 | 633.01 | 762.01 | 765.01 | 757.01 | 943.01 | 800.01 | 514.01 | 394.01 | 308.01 | 437.01 | 213.01 | 123.01 | 149.01 | 130.01 | 106.01 | 173.01 | 116.01 | 89.01 | 99.01 | 98.01 | 142.01 | 120.01 | 143.01 | 97.01 | 141.01 | 250.01 | 80.01 | 251.01 | 70.01 | 86.01 | 444.01 | 194.01 | 101.01 | 147.01 | 60.01 | 95.01 | 209.01 | 66.01 | 192.01 | 78.01 | 209.01 | 144.01 | 714.01 | 138.01 | 407.01 | 616.01 | 566.01 | 560.01 | 411.01 | 616.01 | 464.01 | 534.01 | 521.01 | 588.01 | 253.01 | 713.01 | 71.01 | 53.01 | 106.01 | 156.01 | 56.01 | 67.01 | 88.01 | 1.01 | 12.01 | 84.01 | 0 | 0 | 0 | 0 | 18.01 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191.01 | 136.01 | 0 | 0 | 0 | 0 | 0 | 0 | 34.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267.03
| ˂ = 11 kV ; Subdivision ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 33.81 | 14.11 | 34 | 56 | 65 | 96 | 73 | 71 | 79 | 80 | 129 | 200 | 106 | 68 | 45 | 57 | 50 | 20 | 187 | 42 | 21 | 11 | 7 | 8 | 3 | 16 | 7 | 9 | 8 | 14 | 17 | 11 | 15 | 26 | 22 | 16 | 68 | 33 | 52 | 72 | 53 | 40 | 42 | 25 | 30 | 26 | 38 | 18 | 17 | 24 | 17 | 17 | 15 | 9 | 17 | 11 | 12 | 11 | 29 | 7 | 10 | 17 | 12 | 4 | 2 | 0 | 0 | 0 | 1 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 33.81 | 14.11 | 5 | 4 | 6 | 19 | 5 | 19 | 26 | 25 | 27 | 28 | 39 | 18 | 14 | 12 | 8 | 3 | 53 | 2 | 0 | 0 | 0 | 1 | 41 | 2 | 14 | 5 | 0 | 5 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 32.35 | 11.68 | 11 | 22 | 27 | 27 | 16 | 18 | 33 | 23 | 42 | 76 | 30 | 25 | 16 | 15 | 14 | 5 | 79 | 17 | 15 | 59 | 137 | 116 | 243 | 170 | 253 | 102 | 124 | 399 | 103 | 84 | 135 | 114 | 87 | 57 | 150 | 151 | 109 | 60 | 48 | 34 | 42 | 32 | 38 | 44 | 30 | 27 | 55 | 31 | 25 | 38 | 27 | 18 | 33 | 27 | 18 | 23 | 29 | 17 | 15 | 21 | 12 | 18 | 5 | 1 | 0 | 0 | 1 | 134 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 34.75 | 13.76 | 119 | 201 | 161 | 218 | 181 | 189 | 225 | 313 | 315 | 486 | 278 | 230 | 93 | 94 | 75 | 47 | 451 | 48 | 44 | 87 | 117 | 126 | 299 | 89 | 176 | 168 | 91 | 167 | 71 | 78 | 83 | 107 | 85 | 124 | 286 | 83 | 88 | 107 | 81 | 55 | 52 | 122 | 92 | 117 | 152 | 140 | 145 | 213 | 162 | 179 | 137 | 148 | 167 | 115 | 106 | 78 | 86 | 49 | 64 | 11 | 17 | 12 | 3 | 6 | 1 | 5 | 2 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 34.75 | 13.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 33.14 | 13.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 33.14 | 13.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 33.14 | 13.87 | 157 | 111 | 131 | 161 | 144 | 195 | 196 | 161 | 229 | 196 | 177 | 205 | 155 | 182 | 121 | 77 | 110 | 30 | 30 | 36 | 33 | 94 | 242 | 483 | 202 | 120 | 90 | 62 | 122 | 88 | 177 | 107 | 27 | 69 | 169 | 145 | 316 | 196 | 250 | 256 | 193 | 211 | 182 | 139 | 151 | 157 | 124 | 97 | 62 | 106 | 40 | 40 | 68 | 74 | 45 | 20 | 8 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 33.14 | 13.87 | 132 | 166 | 177 | 285 | 314 | 332 | 372 | 279 | 291 | 282 | 288 | 219 | 134 | 130 | 123 | 101 | 182 | 40 | 23 | 19 | 10 | 28 | 42 | 552 | 17 | 31 | 47 | 21 | 38 | 12 | 25 | 18 | 22 | 14 | 11 | 25 | 15 | 11 | 2 | 3 | 1 | 5 | 10 | 4 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase | 55.74 | 10.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 55.74 | 10.48 | 1 | 0 | 2 | 5 | 2 | 8 | 6 | 0 | 3 | 2 | 3 | 4 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 2 | 5 | 1 | 1 | 0 | 3 | 2 | 1 | 2 | 1 | 0 | 1 | 10 | 11 | 4 | 6 | 4 | 3 | 9 | 9 | 4 | 12 | 44 | 37 | 36 | 23 | 44 | 17 | 13 | 25 | 7 | 20 | 29 | 18 | 33 | 16 | 14 | 5 | 9 | 1 | 3 | 3 | 65 | 3 | 1 | 89 | 9 | 18 | 2 | 0 | 0 | 23 | 8 | 1 | 2 | 1 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase | 37.81 | 11.39 | 78 | 90 | 94 | 96 | 90 | 78 | 86 | 87 | 54 | 77 | 70 | 63 | 54 | 56 | 40 | 13 | 45 | 9 | 19 | 41 | 18 | 34 | 132 | 557 | 48 | 91 | 91 | 164 | 112 | 128 | 107 | 49 | 38 | 38 | 63 | 47 | 73 | 40 | 31 | 22 | 18 | 43 | 15 | 43 | 115 | 184 | 99 | 93 | 32 | 49 | 62 | 48 | 70 | 85 | 15 | 29 | 19 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA | 51.83 | 7.41 | 0 | 3 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 0 | 3 | 5 | 1 | 11 | 6 | 5 | 2 | 4 | 2 | 1 | 0 | 0 | 0 | 2 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA | 48.57 | 4.48 | 1 | 0 | 1 | 2 | 0 | 7 | 12 | 2 | 5 | 16 | 14 | 17 | 10 | 5 | 12 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 3 | 3 | 4 | 3 | 2 | 4 | 9 | 5 | 3 | 10 | 3 | 3 | 5 | 3 | 11 | 3 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA | 43.72 | 10.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA | 43.72 | 10.39 | 0 | 0 | 0 | 0 | 4 | 0 | 4 | 0 | 2 | 5 | 1 | 2 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA | 43.72 | 10.39 | 4 | 8 | 8 | 1 | 6 | 17 | 8 | 20 | 8 | 11 | 7 | 7 | 8 | 6 | 4 | 6 | 3 | 1 | 4 | 4 | 1 | 0 | 0 | 4 | 3 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 3 | 2 | 2 | 3 | 4 | 4 | 2 | 1 | 0 | 3 | 3 | 6 | 4 | 1 | 2 | 2 | 1 | 0 | 1 | 0 | 2 | 3 | 2 | 3 | 2 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA | 43.72 | 10.39 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 6 | 6 | 1 | 1 | 2 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 2 | 2 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 22.68 | 9.68 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 3 | 1 | 0 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; Fuse | 28.64 | 18.77 | 2820 | 1903 | 2192 | 2884 | 2798 | 2963 | 2725 | 3025 | 3207 | 3185 | 2428 | 2557 | 2104 | 1935 | 1459 | 791 | 632 | 780 | 732 | 677 | 666 | 820 | 860 | 749 | 760 | 911 | 785 | 558 | 389 | 399 | 421 | 438 | 423 | 427 | 2299 | 552 | 320 | 251 | 266 | 249 | 328 | 338 | 347 | 351 | 373 | 395 | 452 | 490 | 356 | 318 | 356 | 363 | 328 | 361 | 299 | 291 | 277 | 195 | 281 | 140 | 90 | 83 | 92 | 151 | 112 | 90 | 45 | 54 | 14 | 33 | 30 | 1 | 9 | 8 | 13 | 18 | 18 | 46 | 34 | 57 | 51 | 26 | 6 | 5 | 9 | 62 | 67 | 30 | 31 | 28 | 41 | 5 | 0 | 7 | 10 | 1 | 17 | 12 | 4 | 0 | 0 | 6 | 43 | 20 | 0 | 0 | 11
| ˂ = 11 kV ; Switch | 28.49 | 19.85 | 1967 | 2443 | 2530 | 2998 | 3461 | 3307 | 3067 | 2842 | 3018 | 2339 | 2011 | 2158 | 1464 | 1616 | 1243 | 908 | 736 | 972 | 850 | 856 | 715 | 908 | 667 | 861 | 827 | 881 | 839 | 774 | 686 | 735 | 708 | 662 | 672 | 696 | 2016 | 1044 | 982 | 995 | 1152 | 1144 | 1383 | 1429 | 1350 | 1061 | 1201 | 1175 | 1329 | 1477 | 1288 | 1111 | 1073 | 1029 | 1086 | 1253 | 1233 | 524 | 450 | 274 | 469 | 242 | 139 | 117 | 133 | 124 | 140 | 85 | 71 | 67 | 44 | 40 | 44 | 6 | 16 | 6 | 23 | 25 | 15 | 49 | 31 | 68 | 43 | 18 | 4 | 17 | 11 | 77 | 88 | 41 | 112 | 82 | 39 | 31 | 0 | 21 | 11 | 9 | 18 | 13 | 4 | 0 | 0 | 2 | 37 | 30 | 8 | 0 | 0
| ˂ = 11 kV ; Circuit Breaker | 49.48 | 18.42 | 317 | 285 | 271 | 371 | 428 | 373 | 407 | 474 | 237 | 243 | 251 | 186 | 167 | 126 | 93 | 205 | 138 | 88 | 112 | 108 | 70 | 61 | 65 | 49 | 47 | 54 | 48 | 55 | 35 | 47 | 84 | 14 | 89 | 39 | 46 | 42 | 40 | 64 | 57 | 69 | 42 | 86 | 81 | 85 | 109 | 153 | 108 | 81 | 66 | 38 | 100 | 79 | 101 | 67 | 56 | 69 | 12 | 30 | 39 | 40 | 18 | 26 | 42 | 61 | 30 | 39 | 59 | 37 | 12 | 7 | 9 | 29 | 3 | 4 | 16 | 18 | 9 | 34 | 25 | 40 | 30 | 9 | 7 | 0 | 8 | 21 | 13 | 4 | 15 | 2 | 11 | 0 | 0 | 1 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 24 | 9 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Switch | 49.48 | 18.42 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 4 | 3 | 1 | 0 | 1 | 20 | 1 | 1 | 6 | 1 | 0 | 0 | 0 | 1 | 0 | 13 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker | 46.34 | 13.18 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Switch | 47.03 | 17.23 | 87 | 148 | 72 | 48 | 87 | 77 | 46 | 120 | 53 | 28 | 48 | 52 | 85 | 23 | 5 | 3 | 3 | 2 | 1 | 0 | 0 | 87 | 1 | 7 | 0 | 7 | 2 | 4 | 1 | 2 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 1 | 47 | 24 | 11 | 8 | 0 | 18 | 10 | 33 | 44 | 0 | 0 | 172 | 129 | 29 | 51 | 466 | 23 | 82 | 105 | 113 | 34 | 24 | 99 | 0 | 0 | 13 | 0 | 54 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker | 46.34 | 13.18 | 34 | 35 | 32 | 39 | 59 | 64 | 35 | 57 | 22 | 21 | 21 | 15 | 23 | 15 | 9 | 2 | 14 | 28 | 1 | 0 | 0 | 29 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 1 | 12 | 4 | 9 | 0 | 0 | 10 | 2 | 9 | 26 | 19 | 2 | 3 | 73 | 5 | 18 | 30 | 32 | 18 | 2 | 9 | 0 | 0 | 4 | 0 | 18 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Switch | 46.5 | 17.49 | 0 | 1 | 0 | 13 | 58 | 6 | 30 | 54 | 5 | 30 | 13 | 9 | 18 | 6 | 1 | 7 | 3 | 15 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 10 | 7 | 9 | 43 | 19 | 0 | 8 | 0 | 45 | 0 | 3 | 0 | 9 | 0 | 2 | 0 | 11 | 2 | 0 | 0 | 10 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 21 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker | 30.84 | 11.84 | 3 | 4 | 7 | 7 | 19 | 11 | 19 | 19 | 2 | 12 | 2 | 4 | 7 | 5 | 2 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Switch | 47.42 | 10.64 | 130 | 72 | 166 | 233 | 193 | 153 | 187 | 190 | 50 | 26 | 82 | 77 | 46 | 44 | 40 | 45 | 54 | 0 | 10 | 25 | 0 | 24 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 6 | 37 | 28 | 0 | 26 | 33 | 36 | 9 | 11 | 5 | 1 | 15 | 11 | 12 | 30 | 2 | 37 | 30 | 2 | 6 | 100 | 14 | 4 | 13 | 46 | 4 | 2 | 0 | 18 | 27 | 3 | 0 | 31 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Circuit Breaker | 34.65 | 12.48 | 30 | 21 | 40 | 59 | 41 | 37 | 41 | 62 | 33 | 38 | 40 | 30 | 16 | 14 | 23 | 9 | 19 | 5 | 10 | 5 | 3 | 8 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 23.77 | 16.6 | 14 | 3 | 7 | 14 | 4 | 8 | 2 | 26 | 2 | 2 | 2 | 2 | 2 | 6 | 2 | 1 | 4 | 3 | 1 | 1 | 0 | 0 | 1 | 3 | 3 | 2 | 1 | 2 | 2 | 0 | 0 | 3 | 0 | 1 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road | 18.08 | 16.61 | 1949 | 2503 | 2664 | 2643 | 2798 | 3050 | 3116 | 3747 | 4340 | 2564 | 1360 | 649 | 591 | 548 | 309 | 381 | 514 | 548 | 1666 | 218 | 412 | 482 | 498 | 459 | 493 | 723 | 468 | 507 | 614 | 617 | 680 | 490 | 290 | 300 | 195 | 249 | 300 | 300 | 645 | 368 | 202 | 360 | 257 | 323 | 285 | 626 | 1158 | 1150 | 1680 | 1781 | 1362 | 317 | 96 | 62 | 27 | 30 | 0 | 2 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Luminaires ; Minor Road | 11.56 | 11.88 | 9517 | 13669 | 14036 | 13840 | 12792 | 12282 | 11681 | 9744 | 8372 | 10771 | 13318 | 7820 | 9171 | 8900 | 1406 | 1255 | 1493 | 2053 | 4954 | 834 | 953 | 1710 | 1212 | 1144 | 1154 | 1175 | 1000 | 907 | 708 | 638 | 769 | 625 | 329 | 439 | 372 | 500 | 669 | 888 | 1073 | 563 | 602 | 567 | 452 | 386 | 444 | 719 | 845 | 1022 | 1993 | 1008 | 1002 | 726 | 556 | 507 | 348 | 209 | 45 | 16 | 11 | 12 | 2 | 1 | 0 | 2 | 0 | 0 | 20 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets ; Major Road | 28.82 | 17.1 | 259 | 305 | 371 | 482 | 689 | 1038 | 988 | 1250 | 1923 | 1308 | 874 | 1519 | 440 | 443 | 260 | 260 | 326 | 366 | 2340 | 340 | 552 | 684 | 614 | 565 | 661 | 1460 | 616 | 638 | 1001 | 827 | 950 | 766 | 470 | 540 | 475 | 571 | 629 | 760 | 1475 | 984 | 552 | 1044 | 831 | 825 | 765 | 1272 | 2012 | 2315 | 2842 | 2850 | 2552 | 876 | 324 | 193 | 103 | 110 | 7 | 8 | 0 | 12 | 1 | 1 | 0 | 0 | 0 | 1 | 14 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets ; Minor Road | 22.87 | 16.57 | 1123 | 955 | 1429 | 2543 | 3313 | 4551 | 4845 | 5374 | 7802 | 7879 | 7811 | 5421 | 6242 | 7295 | 1030 | 926 | 1301 | 1817 | 10512 | 1644 | 2283 | 3284 | 2445 | 2385 | 2489 | 4467 | 2181 | 2344 | 1719 | 1549 | 2121 | 2250 | 1348 | 1079 | 1298 | 1640 | 2105 | 3241 | 3900 | 2255 | 2050 | 2296 | 2481 | 1475 | 1670 | 2301 | 2506 | 2934 | 5577 | 3156 | 3657 | 2922 | 2456 | 3463 | 1427 | 911 | 122 | 41 | 26 | 17 | 3 | 4 | 1 | 4 | 1 | 1 | 73 | 3 | 2 | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 7 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
| Lamps ; Major Road | 2.44 | 4.97 | 12691 | 21159 | 16409 | 1707 | 1222 | 391 | 382 | 271 | 126 | 50 | 26 | 8 | 19 | 20 | 11 | 16 | 24 | 25 | 139 | 5 | 9 | 12 | 11 | 11 | 6 | 9 | 8 | 12 | 11 | 8 | 18 | 17 | 7 | 6 | 8 | 7 | 8 | 12 | 24 | 11 | 4 | 8 | 6 | 14 | 9 | 27 | 45 | 66 | 82 | 117 | 84 | 14 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamps ; Minor Road | 2.05 | 2.43 | 49640 | 69030 | 64416 | 11084 | 6172 | 2274 | 1337 | 784 | 162 | 159 | 125 | 104 | 78 | 94 | 39 | 43 | 26 | 46 | 142 | 16 | 27 | 33 | 9 | 27 | 21 | 18 | 17 | 15 | 16 | 12 | 19 | 13 | 10 | 23 | 6 | 9 | 18 | 18 | 34 | 13 | 31 | 16 | 21 | 15 | 16 | 34 | 13 | 29 | 43 | 27 | 11 | 12 | 3 | 7 | 10 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns ; Major Road | 37.93 | 18.03 | 195 | 173 | 239 | 322 | 245 | 306 | 298 | 389 | 366 | 255 | 267 | 222 | 208 | 133 | 131 | 149 | 98 | 89 | 69 | 134 | 114 | 140 | 100 | 105 | 111 | 59 | 152 | 195 | 104 | 265 | 214 | 311 | 180 | 80 | 199 | 284 | 398 | 311 | 216 | 229 | 313 | 228 | 119 | 206 | 226 | 269 | 483 | 235 | 219 | 628 | 588 | 496 | 435 | 449 | 690 | 418 | 396 | 377 | 272 | 443 | 96 | 34 | 388 | 104 | 169 | 37 | 41 | 2 | 16 | 31 | 67 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns ; Minor Road | 40.37 | 17.73 | 1142 | 1501 | 1705 | 1887 | 1825 | 2054 | 1423 | 1296 | 1366 | 1117 | 838 | 1094 | 1232 | 1112 | 754 | 595 | 570 | 817 | 359 | 580 | 216 | 384 | 404 | 303 | 291 | 273 | 308 | 328 | 258 | 371 | 258 | 348 | 195 | 378 | 601 | 548 | 868 | 807 | 570 | 413 | 734 | 591 | 247 | 339 | 196 | 485 | 333 | 610 | 366 | 595 | 877 | 1006 | 814 | 846 | 996 | 468 | 1136 | 609 | 447 | 793 | 257 | 250 | 674 | 48 | 238 | 240 | 130 | 113 | 54 | 161 | 32 | 0 | 1 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices | 49.27 | 15.55 | 1916 | 1691 | 1404 | 1002 | 1901 | 1336 | 1882 | 3748 | 723 | 995 | 894 | 1354 | 953 | 1093 | 500 | 1651 | 1198 | 834 | 892 | 929 | 379 | 969 | 530 | 835 | 412 | 552 | 554 | 664 | 451 | 525 | 679 | 291 | 612 | 267 | 1295 | 856 | 335 | 903 | 1010 | 1614 | 1228 | 1958 | 1181 | 620 | 1922 | 1354 | 1107 | 2007 | 1666 | 613 | 1654 | 1408 | 1095 | 2317 | 1018 | 826 | 651 | 935 | 937 | 1101 | 555 | 285 | 893 | 349 | 220 | 707 | 500 | 45 | 140 | 228 | 35 | 212 | 32 | 8 | 22 | 148 | 9 | 178 | 37 | 282 | 86 | 20 | 8 | 9 | 8 | 132 | 41 | 347 | 40 | 24 | 22 | 14 | 0 | 13 | 126 | 6 | 17 | 1 | 0 | 0 | 0 | 0 | 37 | 161 | 0 | 0 | 7
| Local Network Wiring Assets | 40 | 10 | 129.55 | 35.72 | 160.4 | 146.87 | 240.93 | 198.98 | 243.3 | 404.9 | 110.07 | 102.08 | 79.53 | 128.65 | 192.93 | 128.83 | 28.2 | 235.32 | 109.9 | 77.95 | 70.35 | 93.92 | 24 | 24 | 55.55 | 35.97 | 13.2 | 24.8 | 26 | 399.35 | 82.3 | 45.57 | 90.48 | 65.3 | 79.9 | 27.37 | 224.08 | 112.23 | 7.2 | 73.3 | 133.6 | 188.13 | 118.62 | 151.38 | 102.67 | 90.08 | 212.7 | 272.2 | 142.02 | 170.75 | 243.85 | 220.1 | 360.27 | 209.28 | 232.05 | 452.97 | 228.47 | 149.4 | 158.77 | 304.93 | 231.45 | 283.57 | 150.77 | 64.9 | 111.65 | 126.42 | 59.32 | 80.3 | 73.1 | 4.6 | 32.35 | 32.15 | 32.95 | 34.95 | 0.6 | 0.6 | 3 | 25.37 | 3 | 36.15 | 5.4 | 39.55 | 7.2 | 2.4 | 0.6 | 0 | 0.6 | 31.55 | 6 | 93.25 | 7.8 | 4.8 | 3 | 2.4 | 0 | 1.8 | 29.35 | 0.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Network Assets | 8 | 2 | 892 | 450 | 50 | 150 | 150 | 150 | 150 | 150 | 150 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Master Station Assets | 5.6 | 2 | 2 | 19 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Site Infrastructure | 10 | 2 | 0 | 1 | 0 | 0 | 0 | 2 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Linear Assets | 36.55 | 13.27 | 110.79 | 280.2 | 162.15 | 437.63 | 176.32 | 239.09 | 247.62 | 235.97 | 229.69 | 230.84 | 230.76 | 231.11 | 96.38 | 13.28 | 5.9 | 10.45 | 9.41 | 4.32 | 2.53 | 0.18 | 0.22 | 49.68 | 69.42 | 46.45 | 46.81 | 58.62 | 61.15 | 35.59 | 51.58 | 31.13 | 69.43 | 33.52 | 41.17 | 43.16 | 47 | 58.49 | 65.67 | 117.46 | 105.3 | 126.33 | 86.52 | 82.56 | 75.17 | 75.81 | 62.42 | 66.2 | 56.31 | 92.21 | 43.8 | 100.2 | 88.58 | 81.9 | 89.9 | 98.26 | 180.75 | 151.72 | 96.12 | 172.09 | 132.65 | 146.99 | 91.51 | 143.82 | 207.01 | 25.39 | 9.01 | 39.22 | 25.44 | 15.2 | 17.95 | 17.61 | 9.89 | 4.11 | 10.15 | 30.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AFLC | 36.31 | 23.11 | 2 | 3 | 6 | 10 | 4 | 7 | 4 | 9 | 7 | 8 | 6 | 8 | 34 | 5 | 4 | 4 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 3 | 2 | 2 | 1 | 4 | 1 | 5 | 7 | 3 | 8 | 6 | 0 | 5 | 2 | 2 | 3 | 6 | 0 | 4 | 4 | 2 | 1 | 3 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BY: DNSP DEFINED | Distribution Voltage Regulator | 14.57 | 12.58 | 3 | 11 | 18 | 34 | 37 | 17 | 8 | 18 | 8 | 12 | 7 | 11 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Towers | 51.06 | 1.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 26 | 0 | 1 | 0 | 23 | 12 | 98 | 7 | 0 | 0 | 81 | 43 | 1 | 97 | 42 | 15 | 121 | 73 | 40 | 38 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Zone / STS Substations | 48.66 | 18.33 | 4 | 1 | 6 | 4 | 7 | 4 | 7 | 10 | 3 | 3 | 3 | 4 | 4 | 3 | 0 | 3 | 2 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 2 | 3 | 2 | 1 | 3 | 4 | 0 | 2 | 3 | 5 | 4 | 4 | 3 | 3 | 6 | 8 | 5 | 4 | 9 | 2 | 9 | 6 | 5 | 10 | 6 | 3 | 4 | 6 | 3 | 7 | 4 | 2 | 2 | 2 | 1 | 1 | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
| Distribution Substation | 39.47 | 14.88 | 508 | 522 | 551 | 781 | 734 | 771 | 817 | 784 | 671 | 558 | 523 | 592 | 524 | 571 | 516 | 479 | 436 | 557 | 487 | 496 | 445 | 483 | 502 | 525 | 473 | 543 | 540 | 531 | 480 | 492 | 515 | 521 | 456 | 453 | 1137 | 626 | 567 | 546 | 548 | 478 | 553 | 565 | 559 | 479 | 529 | 501 | 542 | 489 | 486 | 479 | 420 | 432 | 438 | 441 | 368 | 219 | 304 | 180 | 213 | 132 | 99 | 112 | 69 | 46 | 37 | 28 | 33 | 25 | 17 | 15 | 17 | 3 | 6 | 2 | 3 | 9 | 3 | 16 | 9 | 11 | 9 | 5 | 1 | 3 | 3 | 15 | 21 | 12 | 19 | 14 | 9 | 4 | 0 | 6 | 1 | 2 | 3 | 2 | 1 | 0 | 0 | 1 | 6 | 5 | 1 | 0 | 7
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.3 MD - Network level
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
5.3 MAXIMUM DEMAND AT NETWORK LEVEL
5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL (Summed at transmission connection point)
| UNIT | 2016-17
Raw network coincident MD | MW | 5,631
Date MD occurred |  | 10/02/2017
Half hour time period MD occurred |  | 16:30:00
Winter/summer peaking |  | Summer
Embedded generation | MW | -90.39
Weather corrected (10% POE) network coincident MD | MW | 5,968
Weather corrected (50% POE) network coincident MD | MW | 5,353
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.4 MD & utilisation-Spatial
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL
There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data.
5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2016-17
SUBTRANSMISSION SUBSTATION | Alexandria 132_33kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Argenton 132_33kV | Substation Rating | MVA | Non-Coincident | 142.9
|  |  |  | Coincident | 142.9
|  | Raw Adjusted MD | MW | Non-Coincident | 99.08
|  |  |  | Coincident | 92
|  | Raw Adjusted MD | MVA | Non-Coincident | 105.1
|  |  |  | Coincident | 97.59
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -3.827
|  |  |  | Coincident | -2.221
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 103.1
|  |  |  | Coincident | 95.75
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 109.4
|  |  |  | Coincident | 101.6
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 86.72
|  |  |  | Coincident | 80.52
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 91.99
|  |  |  | Coincident | 85.41
| Awaba 132_33kV | Substation Rating | MVA | Non-Coincident | 68.59
|  |  |  | Coincident | 68.59
|  | Raw Adjusted MD | MW | Non-Coincident | 20.44
|  |  |  | Coincident | 19.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.36
|  |  |  | Coincident | 20.27
|  | Date MD occurred |  | Non-Coincident | 2017-01-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0189
|  |  |  | Coincident | -0.3166
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.18
|  |  |  | Coincident | 21.05
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.17
|  |  |  | Coincident | 21.99
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.82
|  |  |  | Coincident | 18.81
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.71
|  |  |  | Coincident | 19.66
| Bankstown 132_33kV | Substation Rating | MVA | Non-Coincident | 137.4
|  |  |  | Coincident | 137.4
|  | Raw Adjusted MD | MW | Non-Coincident | 73.16
|  |  |  | Coincident | 57.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 74.68
|  |  |  | Coincident | 58.82
|  | Date MD occurred |  | Non-Coincident | 2017-01-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.27
|  |  |  | Coincident | -0.9225
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 68.69
|  |  |  | Coincident | 54.11
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 70.11
|  |  |  | Coincident | 55.23
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 61.8
|  |  |  | Coincident | 48.68
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 63.08
|  |  |  | Coincident | 49.69
| Beresfield 132_33kV | Substation Rating | MVA | Non-Coincident | 150.1
|  |  |  | Coincident | 150.1
|  | Raw Adjusted MD | MW | Non-Coincident | 93.17
|  |  |  | Coincident | 86.59
|  | Raw Adjusted MD | MVA | Non-Coincident | 99.2
|  |  |  | Coincident | 92.2
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.633
|  |  |  | Coincident | -1.292
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 105.8
|  |  |  | Coincident | 98.31
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 112.6
|  |  |  | Coincident | 104.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 91.91
|  |  |  | Coincident | 85.42
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 97.86
|  |  |  | Coincident | 90.95
| Bunnerong North 132_33kV | Substation Rating | MVA | Non-Coincident | 312.6
|  |  |  | Coincident | 312.6
|  | Raw Adjusted MD | MW | Non-Coincident | 214.3
|  |  |  | Coincident | 208
|  | Raw Adjusted MD | MVA | Non-Coincident | 216.2
|  |  |  | Coincident | 209.9
|  | Date MD occurred |  | Non-Coincident | 2017-01-24
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.625
|  |  |  | Coincident | -0.9619
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 223.4
|  |  |  | Coincident | 216.9
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 225.3
|  |  |  | Coincident | 218.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 209.4
|  |  |  | Coincident | 203.3
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 211.2
|  |  |  | Coincident | 205
| Canterbury 132_33kV | Substation Rating | MVA | Non-Coincident | 176.8
|  |  |  | Coincident | 176.8
|  | Raw Adjusted MD | MW | Non-Coincident | 149.9
|  |  |  | Coincident | 140.7
|  | Raw Adjusted MD | MVA | Non-Coincident | 152.5
|  |  |  | Coincident | 143.2
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.276
|  |  |  | Coincident | -1.91
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 154.2
|  |  |  | Coincident | 144.8
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 156.9
|  |  |  | Coincident | 147.3
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 133.6
|  |  |  | Coincident | 125.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 136
|  |  |  | Coincident | 127.7
| Eraring 132_33kV | Substation Rating | MVA | Non-Coincident | 69.5
|  |  |  | Coincident | 69.5
|  | Raw Adjusted MD | MW | Non-Coincident | 29.52
|  |  |  | Coincident | 21.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.05
|  |  |  | Coincident | 22.95
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.244
|  |  |  | Coincident | -0.4657
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.52
|  |  |  | Coincident | 21.82
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.05
|  |  |  | Coincident | 22.95
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.52
|  |  |  | Coincident | 21.82
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.05
|  |  |  | Coincident | 22.95
| Gosford 132_33kV | Substation Rating | MVA | Non-Coincident | 0.06
|  |  |  | Coincident | 0.06
|  | Raw Adjusted MD | MW | Non-Coincident | 24.93
|  |  |  | Coincident | 23.81
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.34
|  |  |  | Coincident | 24.2
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.228
|  |  |  | Coincident | -0.5498
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.21
|  |  |  | Coincident | 25.99
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.66
|  |  |  | Coincident | 26.41
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.81
|  |  |  | Coincident | 22.74
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.2
|  |  |  | Coincident | 23.11
| Gosford 132_66kV | Substation Rating | MVA | Non-Coincident | 225.4
|  |  |  | Coincident | 225.4
|  | Raw Adjusted MD | MW | Non-Coincident | 132.9
|  |  |  | Coincident | 128.8
|  | Raw Adjusted MD | MVA | Non-Coincident | 138.2
|  |  |  | Coincident | 134
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -4.02
|  |  |  | Coincident | -3.374
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 140.3
|  |  |  | Coincident | 136.1
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 146
|  |  |  | Coincident | 141.5
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 122.7
|  |  |  | Coincident | 119
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 127.6
|  |  |  | Coincident | 123.7
| Homebush 132_33kV | Substation Rating | MVA | Non-Coincident | 140.3
|  |  |  | Coincident | 140.3
|  | Raw Adjusted MD | MW | Non-Coincident | 123.6
|  |  |  | Coincident | 123
|  | Raw Adjusted MD | MVA | Non-Coincident | 124.1
|  |  |  | Coincident | 123.5
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.894
|  |  |  | Coincident | -1.213
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 135.4
|  |  |  | Coincident | 134.8
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 136
|  |  |  | Coincident | 135.3
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 119.5
|  |  |  | Coincident | 118.9
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 120
|  |  |  | Coincident | 119.4
| Kooragang 132_33kV | Substation Rating | MVA | Non-Coincident | 142.9
|  |  |  | Coincident | 142.9
|  | Raw Adjusted MD | MW | Non-Coincident | 62.78
|  |  |  | Coincident | 41.02
|  | Raw Adjusted MD | MVA | Non-Coincident | 66.13
|  |  |  | Coincident | 43.21
|  | Date MD occurred |  | Non-Coincident | 2017-02-03
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 10:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 62.78
|  |  |  | Coincident | 41.02
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 66.13
|  |  |  | Coincident | 43.21
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 62.78
|  |  |  | Coincident | 41.02
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 66.13
|  |  |  | Coincident | 43.21
| Kuring-gai 132_33kV | Substation Rating | MVA | Non-Coincident | 261
|  |  |  | Coincident | 261
|  | Raw Adjusted MD | MW | Non-Coincident | 154.1
|  |  |  | Coincident | 144.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 166.5
|  |  |  | Coincident | 155.8
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.659
|  |  |  | Coincident | -1.931
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 162.7
|  |  |  | Coincident | 152.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 175.9
|  |  |  | Coincident | 164.5
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 138.1
|  |  |  | Coincident | 129.2
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 149.3
|  |  |  | Coincident | 139.7
| Kurri 132_33kV | Substation Rating | MVA | Non-Coincident | 156.2
|  |  |  | Coincident | 156.2
|  | Raw Adjusted MD | MW | Non-Coincident | 128.6
|  |  |  | Coincident | 125.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 129
|  |  |  | Coincident | 125.8
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -5.677
|  |  |  | Coincident | -3.015
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 146
|  |  |  | Coincident | 142.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 146.6
|  |  |  | Coincident | 142.8
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 131
|  |  |  | Coincident | 127.7
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 131.5
|  |  |  | Coincident | 128.1
| Merewether 132_33kV | Substation Rating | MVA | Non-Coincident | 274.4
|  |  |  | Coincident | 274.4
|  | Raw Adjusted MD | MW | Non-Coincident | 164.1
|  |  |  | Coincident | 142.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 166.9
|  |  |  | Coincident | 144.8
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -7.496
|  |  |  | Coincident | -2.948
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 178.1
|  |  |  | Coincident | 154.5
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 181.1
|  |  |  | Coincident | 157.1
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 155.3
|  |  |  | Coincident | 134.7
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 157.9
|  |  |  | Coincident | 137
| Mitchell Line 132_66kV | Substation Rating | MVA | Non-Coincident | 141.3
|  |  |  | Coincident | 141.3
|  | Raw Adjusted MD | MW | Non-Coincident | 74.09
|  |  |  | Coincident | 63.07
|  | Raw Adjusted MD | MVA | Non-Coincident | 77.87
|  |  |  | Coincident | 66.29
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0113
|  |  |  | Coincident | -0.9935
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 79.39
|  |  |  | Coincident | 67.59
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 83.44
|  |  |  | Coincident | 71.04
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 73.95
|  |  |  | Coincident | 62.95
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 77.72
|  |  |  | Coincident | 66.17
| Morisset 132_33kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Munmorah 132_33kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident | 26.3
|  |  |  | Coincident | 22.81
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.22
|  |  |  | Coincident | 25.34
|  | Date MD occurred |  | Non-Coincident | 2017-01-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0442
|  |  |  | Coincident | -0.7404
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.96
|  |  |  | Coincident | 23.38
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.96
|  |  |  | Coincident | 25.98
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.9
|  |  |  | Coincident | 20.73
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.56
|  |  |  | Coincident | 23.03
| Munmorah 330_33kV | Substation Rating | MVA | Non-Coincident | 69
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident | 26.06
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.95
Coincident
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.49
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.99
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.31
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.57
Coincident
| Muswellbrook 132_33kV | Substation Rating | MVA | Non-Coincident | 50.87
|  |  |  | Coincident | 47.1
|  | Raw Adjusted MD | MW | Non-Coincident | 16.39
|  |  |  | Coincident | 13.58
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.97
|  |  |  | Coincident | 18.36
|  | Date MD occurred |  | Non-Coincident | 2016-05-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.3593
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.95
|  |  |  | Coincident | 15.03
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.55
|  |  |  | Coincident | 20.32
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.79
|  |  |  | Coincident | 13.56
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.34
|  |  |  | Coincident | 18.33
| Muswellbrook North 132_33kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Ourimbah 132_33kV | Substation Rating | MVA | Non-Coincident | 21.7
|  |  |  | Coincident | 21.7
|  | Raw Adjusted MD | MW | Non-Coincident | 14.14
|  |  |  | Coincident | 9.305
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.17
|  |  |  | Coincident | 11.3
|  | Date MD occurred |  | Non-Coincident | 2016-12-14
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6365
|  |  |  | Coincident | -0.2359
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.45
|  |  |  | Coincident | 10.17
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.77
|  |  |  | Coincident | 12.35
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.93
|  |  |  | Coincident | 9.171
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.93
|  |  |  | Coincident | 11.14
| Ourimbah 132_66kV | Substation Rating | MVA | Non-Coincident | 0.01
|  |  |  | Coincident | 0.01
|  | Raw Adjusted MD | MW | Non-Coincident | 47.1
|  |  |  | Coincident | 39.31
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.4
|  |  |  | Coincident | 40.91
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.9333
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.21
|  |  |  | Coincident | 39.16
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 52.63
|  |  |  | Coincident | 40.75
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 48.66
|  |  |  | Coincident | 35.88
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 50.01
|  |  |  | Coincident | 37.33
| Peakhurst 132_33kV | Substation Rating | MVA | Non-Coincident | 233.2
|  |  |  | Coincident | 233.2
|  | Raw Adjusted MD | MW | Non-Coincident | 155.2
|  |  |  | Coincident | 143.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 157.9
|  |  |  | Coincident | 145.7
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.376
|  |  |  | Coincident | -2.607
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 163.1
|  |  |  | Coincident | 150.5
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 166
|  |  |  | Coincident | 153.2
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 137.6
|  |  |  | Coincident | 126.9
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 140
|  |  |  | Coincident | 129.2
| Port Hacking 132_33kV | Substation Rating | MVA | Non-Coincident | 155.8
|  |  |  | Coincident | 137.4
|  | Raw Adjusted MD | MW | Non-Coincident | 124.1
|  |  |  | Coincident | 95.78
|  | Raw Adjusted MD | MVA | Non-Coincident | 125.9
|  |  |  | Coincident | 99.3
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -1.924
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 129.5
|  |  |  | Coincident | 107.6
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 131.4
|  |  |  | Coincident | 111.6
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 124
|  |  |  | Coincident | 92.79
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 125.7
|  |  |  | Coincident | 96.2
| Pyrmont 132_33kV | Substation Rating | MVA | Non-Coincident | 131.7
|  |  |  | Coincident | 131.7
|  | Raw Adjusted MD | MW | Non-Coincident | 99.18
|  |  |  | Coincident | 92.91
|  | Raw Adjusted MD | MVA | Non-Coincident | 102.4
|  |  |  | Coincident | 95.95
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2323
|  |  |  | Coincident | -0.2323
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 101
|  |  |  | Coincident | 94.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 104.2
|  |  |  | Coincident | 97.66
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 95.99
|  |  |  | Coincident | 89.92
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 99.12
|  |  |  | Coincident | 92.86
| Rozelle 132_33kV | Substation Rating | MVA | Non-Coincident | 40
|  |  |  | Coincident | 40
|  | Raw Adjusted MD | MW | Non-Coincident | 11.91
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.23
Coincident
|  | Date MD occurred |  | Non-Coincident | 2016-12-14
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 9:00
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.44
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.93
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.91
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.23
Coincident
| Singleton 132_66kV | Substation Rating | MVA | Non-Coincident | 284.4
|  |  |  | Coincident | 284.4
|  | Raw Adjusted MD | MW | Non-Coincident | 144.2
|  |  |  | Coincident | 130.9
|  | Raw Adjusted MD | MVA | Non-Coincident | 159.8
|  |  |  | Coincident | 145
|  | Date MD occurred |  | Non-Coincident | 2017-01-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.251
|  |  |  | Coincident | -1.548
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 146.6
|  |  |  | Coincident | 133.1
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 162.5
|  |  |  | Coincident | 147.5
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 139.5
|  |  |  | Coincident | 126.6
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 154.6
|  |  |  | Coincident | 140.3
| Strathfield 132_33kV | Substation Rating | MVA | Non-Coincident | 68.59
|  |  |  | Coincident | 68.59
|  | Raw Adjusted MD | MW | Non-Coincident | 51.73
|  |  |  | Coincident | 49.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 53.88
|  |  |  | Coincident | 51.09
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.209
|  |  |  | Coincident | -0.1518
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 53.02
|  |  |  | Coincident | 50.28
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 55.23
|  |  |  | Coincident | 52.37
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 49.6
|  |  |  | Coincident | 47.03
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 51.66
|  |  |  | Coincident | 48.99
| Surry Hills 132_33kV | Substation Rating | MVA | Non-Coincident | 231.2
|  |  |  | Coincident | 231.2
|  | Raw Adjusted MD | MW | Non-Coincident | 159.5
|  |  |  | Coincident | 149
|  | Raw Adjusted MD | MVA | Non-Coincident | 159.6
|  |  |  | Coincident | 149.1
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.8125
|  |  |  | Coincident | -0.2981
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 164.4
|  |  |  | Coincident | 153.6
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 164.5
|  |  |  | Coincident | 153.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 153.1
|  |  |  | Coincident | 143
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 153.1
|  |  |  | Coincident | 143.1
| Sydney East 132_33kV | Substation Rating | MVA | Non-Coincident | 149
|  |  |  | Coincident | 141
|  | Raw Adjusted MD | MW | Non-Coincident | 76.56
|  |  |  | Coincident | 73.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 76.92
|  |  |  | Coincident | 73.91
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -1.503
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 79.7
|  |  |  | Coincident | 79.1
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 80.08
|  |  |  | Coincident | 79.85
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 76.32
|  |  |  | Coincident | 69.63
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 76.67
|  |  |  | Coincident | 70.3
| Tomago 132_33kV | Substation Rating | MVA | Non-Coincident | 153.1
|  |  |  | Coincident | 153.1
|  | Raw Adjusted MD | MW | Non-Coincident | 124.3
|  |  |  | Coincident | 106.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 129
|  |  |  | Coincident | 110.6
|  | Date MD occurred |  | Non-Coincident | 2017-01-24
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -6.284
|  |  |  | Coincident | -2.584
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 132.6
|  |  |  | Coincident | 113.6
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 137.6
|  |  |  | Coincident | 118
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 115.6
|  |  |  | Coincident | 99.11
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 120
|  |  |  | Coincident | 102.9
| Waratah (Comsteel) 132_33kV | Substation Rating | MVA | Non-Coincident | 60
|  |  |  | Coincident | 60
|  | Raw Adjusted MD | MW | Non-Coincident | 55.95
|  |  |  | Coincident | 10.22
|  | Raw Adjusted MD | MVA | Non-Coincident | 57.03
|  |  |  | Coincident | 10.38
|  | Date MD occurred |  | Non-Coincident | 2016-06-08
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 3:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 55.96
|  |  |  | Coincident | 10.22
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.03
|  |  |  | Coincident | 10.38
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 55.96
|  |  |  | Coincident | 10.22
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 57.03
|  |  |  | Coincident | 10.38
| Waratah (Domestic) 132_33kV | Substation Rating | MVA | Non-Coincident | 45.73
|  |  |  | Coincident | 45.73
|  | Raw Adjusted MD | MW | Non-Coincident | 4.698
|  |  |  | Coincident | 1.178
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.005
|  |  |  | Coincident | 1.193
|  | Date MD occurred |  | Non-Coincident | 2016-08-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.694
|  |  |  | Coincident | 1.178
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6
|  |  |  | Coincident | 1.192
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.694
|  |  |  | Coincident | 1.178
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6
|  |  |  | Coincident | 1.192
| Warringah 132_33kV | Substation Rating | MVA | Non-Coincident | 217.4
|  |  |  | Coincident | 217.4
|  | Raw Adjusted MD | MW | Non-Coincident | 157.4
|  |  |  | Coincident | 153.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 160.6
|  |  |  | Coincident | 156.7
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.88
|  |  |  | Coincident | -2.88
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 165.1
|  |  |  | Coincident | 161
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 168.4
|  |  |  | Coincident | 164.3
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 147.2
|  |  |  | Coincident | 143.6
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 150.2
|  |  |  | Coincident | 146.5
| Willoughby 132_33kV | Substation Rating | MVA | Non-Coincident | 313.6
|  |  |  | Coincident | 313.6
|  | Raw Adjusted MD | MW | Non-Coincident | 145.7
|  |  |  | Coincident | 134.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 146.4
|  |  |  | Coincident | 137.8
|  | Date MD occurred |  | Non-Coincident | 2016-08-03
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.8758
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 159.3
|  |  |  | Coincident | 141
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 160
|  |  |  | Coincident | 144.9
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 153
|  |  |  | Coincident | 128.8
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 153.6
|  |  |  | Coincident | 132.3
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2016-17
ZONE SUBSTATION | Aberdeen 66_11kV | Substation Rating | MVA | Non-Coincident | 25.53
|  |  |  | Coincident | 25.53
|  | Raw Adjusted MD | MW | Non-Coincident | 6.38
|  |  |  | Coincident | 5.381
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.578
|  |  |  | Coincident | 5.548
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0003
|  |  |  | Coincident | -0.1335
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.784
|  |  |  | Coincident | 5.722
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.994
|  |  |  | Coincident | 5.899
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.013
|  |  |  | Coincident | 5.072
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.2
|  |  |  | Coincident | 5.229
| Adamstown 132_11kV | Substation Rating | MVA | Non-Coincident | 63.03
|  |  |  | Coincident | 63.03
|  | Raw Adjusted MD | MW | Non-Coincident | 25.41
|  |  |  | Coincident | 24.57
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.21
|  |  |  | Coincident | 25.34
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.8452
|  |  |  | Coincident | -0.6139
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.21
|  |  |  | Coincident | 29.22
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.16
|  |  |  | Coincident | 30.13
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.82
|  |  |  | Coincident | 24.97
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.63
|  |  |  | Coincident | 25.75
| Argenton 132_11kV | Substation Rating | MVA | Non-Coincident | 60.8
|  |  |  | Coincident | 60.8
|  | Raw Adjusted MD | MW | Non-Coincident | 35.64
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.38
|  |  |  | Coincident | 36.7
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.511
|  |  |  | Coincident | -1.009
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 40.91
|  |  |  | Coincident | 40.17
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 42.9
|  |  |  | Coincident | 42.13
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.4
|  |  |  | Coincident | 34.75
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 37.12
|  |  |  | Coincident | 36.45
| Arncliffe 33_11kV | Substation Rating | MVA | Non-Coincident | 39.06
|  |  |  | Coincident | 39.06
|  | Raw Adjusted MD | MW | Non-Coincident | 23.09
|  |  |  | Coincident | 20.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.28
|  |  |  | Coincident | 21.09
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1231
|  |  |  | Coincident | -0.2332
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.11
|  |  |  | Coincident | 20.94
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.31
|  |  |  | Coincident | 21.11
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.96
|  |  |  | Coincident | 18.08
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.13
|  |  |  | Coincident | 18.24
| Auburn 33_11kV | Substation Rating | MVA | Non-Coincident | 41.01
|  |  |  | Coincident | 41.01
|  | Raw Adjusted MD | MW | Non-Coincident | 29.16
|  |  |  | Coincident | 20.97
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.38
|  |  |  | Coincident | 22.56
|  | Date MD occurred |  | Non-Coincident | 2017-01-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5534
|  |  |  | Coincident | -0.2026
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.74
|  |  |  | Coincident | 21.38
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32
|  |  |  | Coincident | 23
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.71
|  |  |  | Coincident | 19.2
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.74
|  |  |  | Coincident | 20.66
| Avoca 66_11kV | Substation Rating | MVA | Non-Coincident | 59.83
|  |  |  | Coincident | 59.83
|  | Raw Adjusted MD | MW | Non-Coincident | 36.19
|  |  |  | Coincident | 33.03
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.63
|  |  |  | Coincident | 33.43
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.217
|  |  |  | Coincident | -0.8837
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.57
|  |  |  | Coincident | 34.29
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.03
|  |  |  | Coincident | 34.71
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.1
|  |  |  | Coincident | 30.21
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.5
|  |  |  | Coincident | 30.58
| Avondale 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 12.93
|  |  |  | Coincident | 10.25
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.21
|  |  |  | Coincident | 10.47
|  | Date MD occurred |  | Non-Coincident | 2017-01-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1404
|  |  |  | Coincident | -0.4657
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.06
|  |  |  | Coincident | 11.14
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.37
|  |  |  | Coincident | 11.39
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.08
|  |  |  | Coincident | 9.577
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.35
|  |  |  | Coincident | 9.788
| Baerami 33_11kV | Substation Rating | MVA | Non-Coincident | 2.44
|  |  |  | Coincident | 2.44
|  | Raw Adjusted MD | MW | Non-Coincident | 0.93
|  |  |  | Coincident | 0.688
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.97
|  |  |  | Coincident | 0.717
|  | Date MD occurred |  | Non-Coincident | 2017-01-17
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.0169
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.93
|  |  |  | Coincident | 0.688
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.97
|  |  |  | Coincident | 0.717
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.93
|  |  |  | Coincident | 0.688
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.97
|  |  |  | Coincident | 0.717
| Balgowlah North 132_11kV | Substation Rating | MVA | Non-Coincident | 43.92
|  |  |  | Coincident | 43.92
|  | Raw Adjusted MD | MW | Non-Coincident | 34.56
|  |  |  | Coincident | 28.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.79
|  |  |  | Coincident | 28.89
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.5464
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.12
|  |  |  | Coincident | 28.78
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.35
|  |  |  | Coincident | 29.27
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.59
|  |  |  | Coincident | 25.3
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.81
|  |  |  | Coincident | 25.74
| Bankstown 132_11kV | Substation Rating | MVA | Non-Coincident | 63.52
|  |  |  | Coincident | 63.52
|  | Raw Adjusted MD | MW | Non-Coincident | 44.83
|  |  |  | Coincident | 44.64
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.81
|  |  |  | Coincident | 49.6
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.754
|  |  |  | Coincident | -0.9315
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.32
|  |  |  | Coincident | 49.11
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 54.8
|  |  |  | Coincident | 54.56
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.84
|  |  |  | Coincident | 43.65
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 48.71
|  |  |  | Coincident | 48.5
| Bass Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 31.78
|  |  |  | Coincident | 31.78
|  | Raw Adjusted MD | MW | Non-Coincident | 25.24
|  |  |  | Coincident | 24.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.62
|  |  |  | Coincident | 25.53
|  | Date MD occurred |  | Non-Coincident | 2017-01-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.8594
|  |  |  | Coincident | -0.3922
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.16
|  |  |  | Coincident | 26.05
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.65
|  |  |  | Coincident | 27.48
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.61
|  |  |  | Coincident | 22.64
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.9
|  |  |  | Coincident | 23.88
| Beacon Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 26.67
|  |  |  | Coincident | 26.67
|  | Raw Adjusted MD | MW | Non-Coincident | 20.9
|  |  |  | Coincident | 19.81
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.33
|  |  |  | Coincident | 21.17
|  | Date MD occurred |  | Non-Coincident | 2017-01-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5408
|  |  |  | Coincident | -0.2872
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.45
|  |  |  | Coincident | 21.28
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.99
|  |  |  | Coincident | 22.74
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.84
|  |  |  | Coincident | 18.81
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.2
|  |  |  | Coincident | 20.1
| Belmore Park 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Belrose 33_11kV | Substation Rating | MVA | Non-Coincident | 40.29
|  |  |  | Coincident | 40.29
|  | Raw Adjusted MD | MW | Non-Coincident | 28.66
|  |  |  | Coincident | 26.41
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.57
|  |  |  | Coincident | 27.25
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2652
|  |  |  | Coincident | -0.6395
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.42
|  |  |  | Coincident | 27.11
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.36
|  |  |  | Coincident | 27.97
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.53
|  |  |  | Coincident | 23.52
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.34
|  |  |  | Coincident | 24.27
| Berkeley Vale 132_11kV | Substation Rating | MVA | Non-Coincident | 59.9
|  |  |  | Coincident | 59.9
|  | Raw Adjusted MD | MW | Non-Coincident | 46.38
|  |  |  | Coincident | 40.76
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.53
|  |  |  | Coincident | 42.64
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.034
|  |  |  | Coincident | -0.7445
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.71
|  |  |  | Coincident | 41.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 49.92
|  |  |  | Coincident | 43.86
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.22
|  |  |  | Coincident | 37.98
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.22
|  |  |  | Coincident | 39.74
| Berowra 132_11kV | Substation Rating | MVA | Non-Coincident | 42.33
|  |  |  | Coincident | 42.33
|  | Raw Adjusted MD | MW | Non-Coincident | 24.38
|  |  |  | Coincident | 21.15
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.2
|  |  |  | Coincident | 22.73
|  | Date MD occurred |  | Non-Coincident | 2017-01-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.7197
|  |  |  | Coincident | -0.604
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.29
|  |  |  | Coincident | 21.94
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.18
|  |  |  | Coincident | 23.58
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.81
|  |  |  | Coincident | 18.93
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.44
|  |  |  | Coincident | 20.34
| Blackwattle Bay 33_5kV | Substation Rating | MVA | Non-Coincident | 41.67
|  |  |  | Coincident | 41.67
|  | Raw Adjusted MD | MW | Non-Coincident | 17.99
|  |  |  | Coincident | 17.89
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.87
|  |  |  | Coincident | 19.75
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0512
|  |  |  | Coincident | -0.0188
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.01
|  |  |  | Coincident | 18.9
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.99
|  |  |  | Coincident | 20.87
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.79
|  |  |  | Coincident | 17.69
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.65
|  |  |  | Coincident | 19.53
| Blakehurst 33_11kV | Substation Rating | MVA | Non-Coincident | 31.59
|  |  |  | Coincident | 31.59
|  | Raw Adjusted MD | MW | Non-Coincident | 23.06
|  |  |  | Coincident | 19.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.57
|  |  |  | Coincident | 20.37
|  | Date MD occurred |  | Non-Coincident | 2017-02-05
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 21:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0006
|  |  |  | Coincident | -0.3428
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.24
|  |  |  | Coincident | 20.08
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.76
|  |  |  | Coincident | 20.53
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.78
|  |  |  | Coincident | 17.09
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.22
|  |  |  | Coincident | 17.47
| Botany 33_11kV | Substation Rating | MVA | Non-Coincident | 53.11
|  |  |  | Coincident | 53.11
|  | Raw Adjusted MD | MW | Non-Coincident | 25.93
|  |  |  | Coincident | 25.93
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.21
|  |  |  | Coincident | 27.21
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5091
|  |  |  | Coincident | -0.2323
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.33
|  |  |  | Coincident | 27.33
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.68
|  |  |  | Coincident | 28.68
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.63
|  |  |  | Coincident | 24.63
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.85
|  |  |  | Coincident | 25.85
| Brandy Hill 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 10.25
|  |  |  | Coincident | 7.789
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.33
|  |  |  | Coincident | 7.852
|  | Date MD occurred |  | Non-Coincident | 2017-01-30
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0037
|  |  |  | Coincident | -0.3274
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.59
|  |  |  | Coincident | 8.047
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.68
|  |  |  | Coincident | 8.112
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.222
|  |  |  | Coincident | 7.007
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.297
|  |  |  | Coincident | 7.064
| Branxton 66_11kV | Substation Rating | MVA | Non-Coincident | 15.07
|  |  |  | Coincident | 15.07
|  | Raw Adjusted MD | MW | Non-Coincident | 14.43
|  |  |  | Coincident | 12.26
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.68
|  |  |  | Coincident | 12.47
|  | Date MD occurred |  | Non-Coincident | 2017-02-05
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1194
|  |  |  | Coincident | -0.3961
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.83
|  |  |  | Coincident | 13.45
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.11
|  |  |  | Coincident | 13.69
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.08
|  |  |  | Coincident | 11.97
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.33
|  |  |  | Coincident | 12.17
| Broadmeadow 132_11kV | Substation Rating | MVA | Non-Coincident | 40.66
|  |  |  | Coincident | 40.66
|  | Raw Adjusted MD | MW | Non-Coincident | 28.83
|  |  |  | Coincident | 26.59
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.11
|  |  |  | Coincident | 27.77
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.276
|  |  |  | Coincident | -0.4729
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.22
|  |  |  | Coincident | 29.71
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.65
|  |  |  | Coincident | 31.03
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.35
|  |  |  | Coincident | 26.15
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.61
|  |  |  | Coincident | 27.31
| Brookvale 33_11kV | Substation Rating | MVA | Non-Coincident | 54.33
|  |  |  | Coincident | 54.33
|  | Raw Adjusted MD | MW | Non-Coincident | 42.71
|  |  |  | Coincident | 39.19
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.83
|  |  |  | Coincident | 41.13
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 11:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.9297
|  |  |  | Coincident | -0.3745
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.34
|  |  |  | Coincident | 40.68
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.54
|  |  |  | Coincident | 42.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.28
|  |  |  | Coincident | 37.88
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 43.33
|  |  |  | Coincident | 39.76
| Burwood 132_11kV | Substation Rating | MVA | Non-Coincident | 83.6
|  |  |  | Coincident | 83.6
|  | Raw Adjusted MD | MW | Non-Coincident | 82.71
|  |  |  | Coincident | 82.71
|  | Raw Adjusted MD | MVA | Non-Coincident | 83.47
|  |  |  | Coincident | 83.47
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.129
|  |  |  | Coincident | -0.6556
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 88.92
|  |  |  | Coincident | 88.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 89.74
|  |  |  | Coincident | 89.74
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 79.38
|  |  |  | Coincident | 79.38
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 80.11
|  |  |  | Coincident | 80.11
| Campbell St 132_11kV | Substation Rating | MVA | Non-Coincident | 62.8
|  |  |  | Coincident | 62.8
|  | Raw Adjusted MD | MW | Non-Coincident | 42.62
|  |  |  | Coincident | 41.94
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.43
|  |  |  | Coincident | 43.73
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.155
|  |  |  | Coincident | -0.0569
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.85
|  |  |  | Coincident | 44.13
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.75
|  |  |  | Coincident | 46.01
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.42
|  |  |  | Coincident | 40.76
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 43.18
|  |  |  | Coincident | 42.49
| Camperdown 33_11kV | Substation Rating | MVA | Non-Coincident | 60.8
|  |  |  | Coincident | 60.8
|  | Raw Adjusted MD | MW | Non-Coincident | 16.33
|  |  |  | Coincident | 15.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.46
|  |  |  | Coincident | 15.3
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.543
|  |  |  | Coincident | -0.2136
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.88
|  |  |  | Coincident | 15.69
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.01
|  |  |  | Coincident | 15.81
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.14
|  |  |  | Coincident | 14.07
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.27
|  |  |  | Coincident | 14.19
| Camperdown 33_5kV | Substation Rating | MVA | Non-Coincident | 13.86
|  |  |  | Coincident | 13.86
|  | Raw Adjusted MD | MW | Non-Coincident | 9.92
|  |  |  | Coincident | 9.599
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.7
|  |  |  | Coincident | 10.35
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5762
|  |  |  | Coincident | -0.2136
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.85
|  |  |  | Coincident | 10.5
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.7
|  |  |  | Coincident | 11.32
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.883
|  |  |  | Coincident | 9.563
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.66
|  |  |  | Coincident | 10.31
| Campsie 33_11kV | Substation Rating | MVA | Non-Coincident | 87.01
|  |  |  | Coincident | 87.01
|  | Raw Adjusted MD | MW | Non-Coincident | 73.37
|  |  |  | Coincident | 69.98
|  | Raw Adjusted MD | MVA | Non-Coincident | 74.3
|  |  |  | Coincident | 70.86
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6386
|  |  |  | Coincident | -0.9558
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 79.09
|  |  |  | Coincident | 75.43
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 80.09
|  |  |  | Coincident | 76.38
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 65.68
|  |  |  | Coincident | 62.64
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 66.51
|  |  |  | Coincident | 63.44
| Cardiff 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 18.14
|  |  |  | Coincident | 17.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.82
|  |  |  | Coincident | 17.82
|  | Date MD occurred |  | Non-Coincident | 2017-01-31
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.07
|  |  |  | Coincident | -0.4302
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.77
|  |  |  | Coincident | 19.66
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.54
|  |  |  | Coincident | 20.4
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.67
|  |  |  | Coincident | 16.73
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.33
|  |  |  | Coincident | 17.36
| Careel Bay 33_11kV | Substation Rating | MVA | Non-Coincident | 15.26
|  |  |  | Coincident | 15.24
|  | Raw Adjusted MD | MW | Non-Coincident | 13.41
|  |  |  | Coincident | 9.555
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.55
|  |  |  | Coincident | 9.85
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.2112
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.87
|  |  |  | Coincident | 9.545
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.01
|  |  |  | Coincident | 9.841
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.34
|  |  |  | Coincident | 8.779
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.48
|  |  |  | Coincident | 9.051
| Caringbah 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 19.03
|  |  |  | Coincident | 17.98
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.46
|  |  |  | Coincident | 19.32
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.1792
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.18
|  |  |  | Coincident | 20.6
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.7
|  |  |  | Coincident | 22.13
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.5
|  |  |  | Coincident | 19.03
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.96
|  |  |  | Coincident | 20.45
| Carrington 33_11kV | Substation Rating | MVA | Non-Coincident | 30.48
|  |  |  | Coincident | 30.48
|  | Raw Adjusted MD | MW | Non-Coincident | 24.53
|  |  |  | Coincident | 20.69
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.97
|  |  |  | Coincident | 21.91
|  | Date MD occurred |  | Non-Coincident | 2017-01-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 14:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.032
|  |  |  | Coincident | -0.3875
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.78
|  |  |  | Coincident | 22.59
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.36
|  |  |  | Coincident | 23.92
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.63
|  |  |  | Coincident | 19.93
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.03
|  |  |  | Coincident | 21.11
| Castle Cove 132_11kV | Substation Rating | MVA | Non-Coincident | 90.65
|  |  |  | Coincident | 90.65
|  | Raw Adjusted MD | MW | Non-Coincident | 64.39
|  |  |  | Coincident | 63.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 71.54
|  |  |  | Coincident | 70.91
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.7225
|  |  |  | Coincident | -0.5248
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 68.03
|  |  |  | Coincident | 67.43
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 75.59
|  |  |  | Coincident | 74.92
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 61.12
|  |  |  | Coincident | 60.58
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 67.91
|  |  |  | Coincident | 67.32
| Cessnock 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 21.69
|  |  |  | Coincident | 20.65
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.25
|  |  |  | Coincident | 21.18
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0061
|  |  |  | Coincident | -0.5342
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.46
|  |  |  | Coincident | 23.29
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.09
|  |  |  | Coincident | 23.89
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.8
|  |  |  | Coincident | 20.76
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.36
|  |  |  | Coincident | 21.29
| Cessnock South 33_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Charlestown 132_11kV | Substation Rating | MVA | Non-Coincident | 60.17
|  |  |  | Coincident | 60.17
|  | Raw Adjusted MD | MW | Non-Coincident | 36.93
|  |  |  | Coincident | 34.36
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.13
|  |  |  | Coincident | 34.54
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.032
|  |  |  | Coincident | -0.6605
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 43.64
|  |  |  | Coincident | 40.6
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 43.87
|  |  |  | Coincident | 40.82
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 37.66
|  |  |  | Coincident | 35.04
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 37.86
|  |  |  | Coincident | 35.22
| Charmhaven 132_11kV | Substation Rating | MVA | Non-Coincident | 63.25
|  |  |  | Coincident | 63.25
|  | Raw Adjusted MD | MW | Non-Coincident | 46.53
|  |  |  | Coincident | 45.51
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.36
|  |  |  | Coincident | 47.29
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.349
|  |  |  | Coincident | -1.349
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.93
|  |  |  | Coincident | 48.83
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.88
|  |  |  | Coincident | 50.74
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.44
|  |  |  | Coincident | 42.48
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.14
|  |  |  | Coincident | 44.14
| Chatswood 33_11kV | Substation Rating | MVA | Non-Coincident | 67.14
|  |  |  | Coincident | 67.14
|  | Raw Adjusted MD | MW | Non-Coincident | 47.25
|  |  |  | Coincident | 46.36
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.65
|  |  |  | Coincident | 50.68
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.3615
|  |  |  | Coincident | -0.541
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.6
|  |  |  | Coincident | 49.65
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 55.31
|  |  |  | Coincident | 54.27
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.64
|  |  |  | Coincident | 43.8
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 48.8
|  |  |  | Coincident | 47.88
| City Central 132_11kV | Substation Rating | MVA | Non-Coincident | 128
|  |  |  | Coincident | 128
|  | Raw Adjusted MD | MW | Non-Coincident | 106.3
|  |  |  | Coincident | 100.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 115.6
|  |  |  | Coincident | 109.2
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0978
|  |  |  | Coincident | -0.0358
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 112.6
|  |  |  | Coincident | 106.4
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 122.4
|  |  |  | Coincident | 115.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 104.9
|  |  |  | Coincident | 99.09
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 114.1
|  |  |  | Coincident | 107.7
| City East 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| City East 33_11kV | Substation Rating | MVA | Non-Coincident | 70.66
|  |  |  | Coincident | 70.66
|  | Raw Adjusted MD | MW | Non-Coincident | 39.09
|  |  |  | Coincident | 35.39
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.45
|  |  |  | Coincident | 36.62
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 12:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0627
|  |  |  | Coincident | -0.024
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 40.37
|  |  |  | Coincident | 36.54
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.77
|  |  |  | Coincident | 37.81
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 37.9
|  |  |  | Coincident | 34.31
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 39.21
|  |  |  | Coincident | 35.5
| City North 132_11kV | Substation Rating | MVA | Non-Coincident | 167.9
|  |  |  | Coincident | 167.9
|  | Raw Adjusted MD | MW | Non-Coincident | 76.43
|  |  |  | Coincident | 70.56
|  | Raw Adjusted MD | MVA | Non-Coincident | 79.09
|  |  |  | Coincident | 73.01
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0279
|  |  |  | Coincident | -0.0102
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 79
|  |  |  | Coincident | 72.93
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 81.74
|  |  |  | Coincident | 75.46
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 74.04
|  |  |  | Coincident | 68.35
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 76.61
|  |  |  | Coincident | 70.72
| City South 132_11kV | Substation Rating | MVA | Non-Coincident | 130.3
|  |  |  | Coincident | 130.3
|  | Raw Adjusted MD | MW | Non-Coincident | 128.8
|  |  |  | Coincident | 121
|  | Raw Adjusted MD | MVA | Non-Coincident | 135.6
|  |  |  | Coincident | 127.3
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 133
|  |  |  | Coincident | 124.8
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 140
|  |  |  | Coincident | 131.4
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 125.8
|  |  |  | Coincident | 118.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 132.4
|  |  |  | Coincident | 124.3
| Clovelly 132_11kV | Substation Rating | MVA | Non-Coincident | 92.98
|  |  |  | Coincident | 87.64
|  | Raw Adjusted MD | MW | Non-Coincident | 74.86
|  |  |  | Coincident | 57.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 75.62
|  |  |  | Coincident | 58.59
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.5249
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 75.05
|  |  |  | Coincident | 58.24
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 75.81
|  |  |  | Coincident | 59.21
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 72.55
|  |  |  | Coincident | 54.58
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 73.28
|  |  |  | Coincident | 55.49
| Concord 33_11kV | Substation Rating | MVA | Non-Coincident | 54.41
|  |  |  | Coincident | 54.41
|  | Raw Adjusted MD | MW | Non-Coincident | 46.14
|  |  |  | Coincident | 44.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 47.23
|  |  |  | Coincident | 45.88
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4418
|  |  |  | Coincident | -0.3209
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.07
|  |  |  | Coincident | 48.64
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.26
|  |  |  | Coincident | 49.79
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.58
|  |  |  | Coincident | 42.34
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.61
|  |  |  | Coincident | 43.34
| Cronulla 132_11kV | Substation Rating | MVA | Non-Coincident | 64.17
|  |  |  | Coincident | 53.46
|  | Raw Adjusted MD | MW | Non-Coincident | 58.33
|  |  |  | Coincident | 51.16
|  | Raw Adjusted MD | MVA | Non-Coincident | 59.2
|  |  |  | Coincident | 52.07
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.705
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 59.25
|  |  |  | Coincident | 52.03
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 60.13
|  |  |  | Coincident | 52.96
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 56.71
|  |  |  | Coincident | 44.53
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 57.55
|  |  |  | Coincident | 45.33
| Croudace Bay 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 24.79
|  |  |  | Coincident | 22.33
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.68
|  |  |  | Coincident | 23.13
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.9776
|  |  |  | Coincident | -0.5675
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.31
|  |  |  | Coincident | 27.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.4
|  |  |  | Coincident | 28.28
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.44
|  |  |  | Coincident | 22.91
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.36
|  |  |  | Coincident | 23.74
| Crows Nest 132_11kV | Substation Rating | MVA | Non-Coincident
|  |  |  | Coincident | 57.1
|  | Raw Adjusted MD | MW | Non-Coincident | 23.16
|  |  |  | Coincident | 21.79
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.73
|  |  |  | Coincident | 24.21
|  | Date MD occurred |  | Non-Coincident | 2016-06-28
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.1846
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.78
|  |  |  | Coincident | 22.8
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.54
|  |  |  | Coincident | 25.34
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.91
|  |  |  | Coincident | 20.3
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.57
|  |  |  | Coincident | 22.55
| Crows Nest 33_11kV | Substation Rating | MVA | Non-Coincident | 60.85
|  |  |  | Coincident | 60.85
|  | Raw Adjusted MD | MW | Non-Coincident | 13.19
|  |  |  | Coincident | 12.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.6
|  |  |  | Coincident | 13.32
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2883
|  |  |  | Coincident | -0.1846
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.04
|  |  |  | Coincident | 13.74
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.48
|  |  |  | Coincident | 14.17
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.44
|  |  |  | Coincident | 12.18
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.82
|  |  |  | Coincident | 12.56
| Croydon 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Dalley St 132_11kV | Substation Rating | MVA | Non-Coincident | 123.6
|  |  |  | Coincident | 123.6
|  | Raw Adjusted MD | MW | Non-Coincident | 100.1
|  |  |  | Coincident | 93.23
|  | Raw Adjusted MD | MVA | Non-Coincident | 102.3
|  |  |  | Coincident | 95.32
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 12:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0241
|  |  |  | Coincident | -0.0092
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 103.6
|  |  |  | Coincident | 96.49
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 105.9
|  |  |  | Coincident | 98.65
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 97.97
|  |  |  | Coincident | 91.25
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 100.2
|  |  |  | Coincident | 93.3
| Darling Harbour 132_11kV | Substation Rating | MVA | Non-Coincident | 70.3
|  |  |  | Coincident | 70.3
|  | Raw Adjusted MD | MW | Non-Coincident | 57.63
|  |  |  | Coincident | 57.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 59.22
|  |  |  | Coincident | 59.22
|  | Date MD occurred |  | Non-Coincident | 2017-02-10
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1979
|  |  |  | Coincident | -0.1149
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 60.06
|  |  |  | Coincident | 60.06
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 61.7
|  |  |  | Coincident | 61.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 55.19
|  |  |  | Coincident | 55.19
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 56.7
|  |  |  | Coincident | 56.7
| Darlinghurst 33_11kV | Substation Rating | MVA | Non-Coincident | 85.16
|  |  |  | Coincident | 85.16
|  | Raw Adjusted MD | MW | Non-Coincident | 45.16
|  |  |  | Coincident | 42.28
|  | Raw Adjusted MD | MVA | Non-Coincident | 46.93
|  |  |  | Coincident | 43.94
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2212
|  |  |  | Coincident | -0.082
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 46.07
|  |  |  | Coincident | 43.13
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 47.87
|  |  |  | Coincident | 44.82
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 42.91
|  |  |  | Coincident | 40.18
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.6
|  |  |  | Coincident | 41.75
| Dee Why West 33_11kV | Substation Rating | MVA | Non-Coincident | 58.78
|  |  |  | Coincident | 53.45
|  | Raw Adjusted MD | MW | Non-Coincident | 42.69
|  |  |  | Coincident | 30.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.47
|  |  |  | Coincident | 32.98
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.6209
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.61
|  |  |  | Coincident | 32.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 47.52
|  |  |  | Coincident | 34.93
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.62
|  |  |  | Coincident | 29.42
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.44
|  |  |  | Coincident | 31.81
| Denman 66_11kV | Substation Rating | MVA | Non-Coincident | 13.36
|  |  |  | Coincident | 13.36
|  | Raw Adjusted MD | MW | Non-Coincident | 6.091
|  |  |  | Coincident | 4.807
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.326
|  |  |  | Coincident | 4.992
|  | Date MD occurred |  | Non-Coincident | 2017-02-11
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0004
|  |  |  | Coincident | -0.1781
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.489
|  |  |  | Coincident | 5.121
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.739
|  |  |  | Coincident | 5.318
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.941
|  |  |  | Coincident | 4.689
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.17
|  |  |  | Coincident | 4.869
| Double Bay 132_11kV | Substation Rating | MVA | Non-Coincident | 81.28
|  |  |  | Coincident | 81.28
|  | Raw Adjusted MD | MW | Non-Coincident | 63.54
|  |  |  | Coincident | 63.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 66
|  |  |  | Coincident | 65.58
|  | Date MD occurred |  | Non-Coincident | 2017-02-06
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.3073
|  |  |  | Coincident | -0.2232
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 64.67
|  |  |  | Coincident | 64.26
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 67.18
|  |  |  | Coincident | 66.75
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 58.63
|  |  |  | Coincident | 58.26
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 60.91
|  |  |  | Coincident | 60.52
| Drummoyne 132_11kV | Substation Rating | MVA | Non-Coincident | 61.77
|  |  |  | Coincident | 56.15
|  | Raw Adjusted MD | MW | Non-Coincident | 59.65
|  |  |  | Coincident | 52.38
|  | Raw Adjusted MD | MVA | Non-Coincident | 60.59
|  |  |  | Coincident | 53.84
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.4814
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 61.24
|  |  |  | Coincident | 55.36
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 62.19
|  |  |  | Coincident | 56.91
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 58.52
|  |  |  | Coincident | 47.25
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 59.43
|  |  |  | Coincident | 48.58
| Dulwich Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 61.9
|  |  |  | Coincident | 61.9
|  | Raw Adjusted MD | MW | Non-Coincident | 44.83
|  |  |  | Coincident | 39.27
|  | Raw Adjusted MD | MVA | Non-Coincident | 45.9
|  |  |  | Coincident | 39.8
|  | Date MD occurred |  | Non-Coincident | 2016-06-27
|  |  |  | Coincident | 2017-02-10
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 16:30
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.5837
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.11
|  |  |  | Coincident | 40.52
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.28
|  |  |  | Coincident | 41.06
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 46.29
|  |  |  | Coincident | 35.35
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 47.39
|  |  |  | Coincident | 35.82
| Edgeworth 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 25.14
|  |  |  | Coincident | 22.51
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.81
|  |  |  | Coincident | 23.11
|  | Date MD occurred |  | Non-Coincident | 42748
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1515
|  |  |  | Coincident | -0.74
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.3
|  |  |  | Coincident | 26.23
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.08
|  |  |  | Coincident | 26.93
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.64
|  |  |  | Coincident | 22.06
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.29
|  |  |  | Coincident | 22.64
| Empire Bay 66_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 12.36
|  |  |  | Coincident | 11.2
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.69
|  |  |  | Coincident | 11.49
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0008
|  |  |  | Coincident | -0.3978
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.41
|  |  |  | Coincident | 11.23
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.73
|  |  |  | Coincident | 11.53
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.74
|  |  |  | Coincident | 9.726
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.02
|  |  |  | Coincident | 9.981
| Enfield 33_11kV | Substation Rating | MVA | Non-Coincident | 44.76
|  |  |  | Coincident | 44.76
|  | Raw Adjusted MD | MW | Non-Coincident | 21.19
|  |  |  | Coincident | 20.58
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.22
|  |  |  | Coincident | 21.57
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.158
|  |  |  | Coincident | -0.2993
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.08
|  |  |  | Coincident | 22.41
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.19
|  |  |  | Coincident | 23.49
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.66
|  |  |  | Coincident | 19.08
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.6
|  |  |  | Coincident | 20
| Engadine 132_11kV | Substation Rating | MVA | Non-Coincident | 60.1
|  |  |  | Coincident | 60.1
|  | Raw Adjusted MD | MW | Non-Coincident | 30.48
|  |  |  | Coincident | 26.62
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.87
|  |  |  | Coincident | 29.58
|  | Date MD occurred |  | Non-Coincident | 42771
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1401
|  |  |  | Coincident | -0.6845
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.01
|  |  |  | Coincident | 26.21
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.34
|  |  |  | Coincident | 29.12
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.52
|  |  |  | Coincident | 23.16
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.47
|  |  |  | Coincident | 25.74
| Engadine 33_11kV | Substation Rating | MVA | Non-Coincident | 30.85
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident | 27.86
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.96
Coincident
|  | Date MD occurred |  | Non-Coincident | 42548
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.59
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.87
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 27.97
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.08
Coincident
| Epping 66_11kV | Substation Rating | MVA | Non-Coincident | 74.91
|  |  |  | Coincident | 74.91
|  | Raw Adjusted MD | MW | Non-Coincident | 57.65
|  |  |  | Coincident | 56.52
|  | Raw Adjusted MD | MVA | Non-Coincident | 64.06
|  |  |  | Coincident | 62.8
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4557
|  |  |  | Coincident | -0.5636
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 62.01
|  |  |  | Coincident | 60.79
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 68.9
|  |  |  | Coincident | 67.54
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 55
|  |  |  | Coincident | 53.92
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 61.11
|  |  |  | Coincident | 59.91
| Erina 66_11kV | Substation Rating | MVA | Non-Coincident | 49.26
|  |  |  | Coincident | 49.26
|  | Raw Adjusted MD | MW | Non-Coincident | 35.6
|  |  |  | Coincident | 34.37
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.83
|  |  |  | Coincident | 35.55
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.66667
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.101
|  |  |  | Coincident | -0.5405
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.35
|  |  |  | Coincident | 36.06
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.64
|  |  |  | Coincident | 37.3
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.11
|  |  |  | Coincident | 31.96
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.24
|  |  |  | Coincident | 33.06
| Five Dock 33_11kV | Substation Rating | MVA | Non-Coincident | 44.16
|  |  |  | Coincident | 41.25
|  | Raw Adjusted MD | MW | Non-Coincident | 38.3
|  |  |  | Coincident | 36.73
|  | Raw Adjusted MD | MVA | Non-Coincident | 39.52
|  |  |  | Coincident | 40.12
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.4123
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.69
|  |  |  | Coincident | 38.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.95
|  |  |  | Coincident | 42.14
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 38.06
|  |  |  | Coincident | 34
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 39.27
|  |  |  | Coincident | 37.14
| Flemington 132_11kV | Substation Rating | MVA | Non-Coincident | 98.69
|  |  |  | Coincident | 98.69
|  | Raw Adjusted MD | MW | Non-Coincident | 79.18
|  |  |  | Coincident | 77.73
|  | Raw Adjusted MD | MVA | Non-Coincident | 83.53
|  |  |  | Coincident | 82
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.406
|  |  |  | Coincident | -0.553
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 85.77
|  |  |  | Coincident | 84.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 90.48
|  |  |  | Coincident | 88.83
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 79.63
|  |  |  | Coincident | 78.18
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 84.01
|  |  |  | Coincident | 82.48
| Galston 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 11.6
|  |  |  | Coincident | 11.39
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.37
|  |  |  | Coincident | 12.14
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4462
|  |  |  | Coincident | -0.2856
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.73
|  |  |  | Coincident | 12.49
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.57
|  |  |  | Coincident | 13.32
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.94
|  |  |  | Coincident | 10.74
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.67
|  |  |  | Coincident | 11.45
| Gateshead 33_11kV | Substation Rating | MVA | Non-Coincident | 24.08
|  |  |  | Coincident | 24.08
|  | Raw Adjusted MD | MW | Non-Coincident | 17.03
|  |  |  | Coincident | 15.61
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.7
|  |  |  | Coincident | 16.23
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.236
|  |  |  | Coincident | -0.4581
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.48
|  |  |  | Coincident | 17.86
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.26
|  |  |  | Coincident | 18.57
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.69
|  |  |  | Coincident | 15.3
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.35
|  |  |  | Coincident | 15.91
| Gore Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 96.9
|  |  |  | Coincident | 96.9
|  | Raw Adjusted MD | MW | Non-Coincident | 59.08
|  |  |  | Coincident | 53.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 61.98
|  |  |  | Coincident | 55.82
|  | Date MD occurred |  | Non-Coincident | 42753
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.41667
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2433
|  |  |  | Coincident | -0.1502
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 61.99
|  |  |  | Coincident | 55.83
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 65.03
|  |  |  | Coincident | 58.56
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 57.44
|  |  |  | Coincident | 51.73
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 60.25
|  |  |  | Coincident | 54.26
| Graving Dock No 1 33_11kV | Substation Rating | MVA | Non-Coincident | 22.18
|  |  |  | Coincident | 22.18
|  | Raw Adjusted MD | MW | Non-Coincident | 5.899
|  |  |  | Coincident | 1.303
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.554
|  |  |  | Coincident | 1.448
|  | Date MD occurred |  | Non-Coincident | 42569
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.9375
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.529
|  |  |  | Coincident | 1.303
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.144
|  |  |  | Coincident | 1.448
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.788
|  |  |  | Coincident | 1.303
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.32
|  |  |  | Coincident | 1.448
| Graving Dock No 2 33_11kV | Substation Rating | MVA | Non-Coincident | 20.75
|  |  |  | Coincident | 18.69
|  | Raw Adjusted MD | MW | Non-Coincident | 6.122
|  |  |  | Coincident | 3.635
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.802
|  |  |  | Coincident | 4.039
|  | Date MD occurred |  | Non-Coincident | 42613
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.02
|  |  |  | Coincident | 3.635
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.8
|  |  |  | Coincident | 4.039
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.496
|  |  |  | Coincident | 3.635
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.218
|  |  |  | Coincident | 4.039
| Green Square 132_11kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 54.41
|  |  |  | Coincident | 52.32
|  | Raw Adjusted MD | MVA | Non-Coincident | 56.15
|  |  |  | Coincident | 53.99
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.60417
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.483
|  |  |  | Coincident | -0.1813
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 58.06
|  |  |  | Coincident | 55.83
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 59.92
|  |  |  | Coincident | 57.62
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 53.32
|  |  |  | Coincident | 51.28
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 55.02
|  |  |  | Coincident | 52.91
| Greenacre Park 132_11kV | Substation Rating | MVA | Non-Coincident | 86.16
|  |  |  | Coincident | 86.16
|  | Raw Adjusted MD | MW | Non-Coincident | 64.73
|  |  |  | Coincident | 63.88
|  | Raw Adjusted MD | MVA | Non-Coincident | 66.72
|  |  |  | Coincident | 65.85
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.66667
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.188
|  |  |  | Coincident | -0.5422
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 69.28
|  |  |  | Coincident | 68.37
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 71.41
|  |  |  | Coincident | 70.47
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 62.53
|  |  |  | Coincident | 61.71
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 64.45
|  |  |  | Coincident | 63.6
| Gwawley Bay 132_11kV | Substation Rating | MVA | Non-Coincident | 40.2
|  |  |  | Coincident | 40.2
|  | Raw Adjusted MD | MW | Non-Coincident | 36.63
|  |  |  | Coincident | 36.59
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.76
|  |  |  | Coincident | 37.72
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5574
|  |  |  | Coincident | -0.3568
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.41
|  |  |  | Coincident | 38.37
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.59
|  |  |  | Coincident | 39.55
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.79
|  |  |  | Coincident | 32.75
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.8
|  |  |  | Coincident | 33.77
| Harbord 33_11kV | Substation Rating | MVA | Non-Coincident | 37.49
|  |  |  | Coincident | 37.27
|  | Raw Adjusted MD | MW | Non-Coincident | 22.99
|  |  |  | Coincident | 12.62
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.95
|  |  |  | Coincident | 13.72
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.4774
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.42
|  |  |  | Coincident | 11.71
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.4
|  |  |  | Coincident | 12.73
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.25
|  |  |  | Coincident | 10.77
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.18
|  |  |  | Coincident | 11.71
| Homebush Bay 132_11kV | Substation Rating | MVA | Non-Coincident | 53.18
|  |  |  | Coincident | 53.18
|  | Raw Adjusted MD | MW | Non-Coincident | 51.71
|  |  |  | Coincident | 44.99
|  | Raw Adjusted MD | MVA | Non-Coincident | 53.06
|  |  |  | Coincident | 46.16
|  | Date MD occurred |  | Non-Coincident | 42753
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.39583
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5863
|  |  |  | Coincident | -0.4062
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 54.06
|  |  |  | Coincident | 47.03
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 55.47
|  |  |  | Coincident | 48.26
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 50.18
|  |  |  | Coincident | 43.66
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 51.49
|  |  |  | Coincident | 44.79
| Hornsby 132_11kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 76.25
|  |  |  | Coincident | 75.48
|  | Raw Adjusted MD | MVA | Non-Coincident | 77.75
|  |  |  | Coincident | 76.97
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.35
|  |  |  | Coincident | -0.9809
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 81.75
|  |  |  | Coincident | 80.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 83.36
|  |  |  | Coincident | 82.52
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 72.57
|  |  |  | Coincident | 71.84
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 74.01
|  |  |  | Coincident | 73.26
| Hunters Hill 66_11kV | Substation Rating | MVA | Non-Coincident | 72.25
|  |  |  | Coincident | 69.83
|  | Raw Adjusted MD | MW | Non-Coincident | 45.31
|  |  |  | Coincident | 40.04
|  | Raw Adjusted MD | MVA | Non-Coincident | 46.89
|  |  |  | Coincident | 43.87
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.3846
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 46.86
|  |  |  | Coincident | 43.48
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 48.49
|  |  |  | Coincident | 47.63
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.48
|  |  |  | Coincident | 37.31
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.03
|  |  |  | Coincident | 40.88
| Hurstville North 132_11kV | Substation Rating | MVA | Non-Coincident | 60
|  |  |  | Coincident | 60
|  | Raw Adjusted MD | MW | Non-Coincident | 23.24
|  |  |  | Coincident | 22.79
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.14
|  |  |  | Coincident | 23.66
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.3512
|  |  |  | Coincident | -0.2248
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.84
|  |  |  | Coincident | 25.33
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.84
|  |  |  | Coincident | 26.31
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.33
|  |  |  | Coincident | 21.89
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.19
|  |  |  | Coincident | 22.73
| Jannali 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 33.29
|  |  |  | Coincident | 28.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.38
|  |  |  | Coincident | 28.53
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.177
|  |  |  | Coincident | -0.5869
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.78
|  |  |  | Coincident | 30.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.88
|  |  |  | Coincident | 30.66
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.65
|  |  |  | Coincident | 25.34
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.73
|  |  |  | Coincident | 25.4
| Jesmond 132_11kV | Substation Rating | MVA | Non-Coincident | 57.48
|  |  |  | Coincident | 57.48
|  | Raw Adjusted MD | MW | Non-Coincident | 44.62
|  |  |  | Coincident | 43.43
|  | Raw Adjusted MD | MVA | Non-Coincident | 46.27
|  |  |  | Coincident | 45.04
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.9392
|  |  |  | Coincident | -0.9392
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.29
|  |  |  | Coincident | 49.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 53.18
|  |  |  | Coincident | 51.77
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.59
|  |  |  | Coincident | 43.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.24
|  |  |  | Coincident | 45.01
| Jewells 33_11kV | Substation Rating | MVA | Non-Coincident | 16.92
|  |  |  | Coincident | 16.92
|  | Raw Adjusted MD | MW | Non-Coincident | 15.21
|  |  |  | Coincident | 13.01
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.6
|  |  |  | Coincident | 13.34
|  | Date MD occurred |  | Non-Coincident | 42746
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.027
|  |  |  | Coincident | -0.4533
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.74
|  |  |  | Coincident | 15.17
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.2
|  |  |  | Coincident | 15.57
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.99
|  |  |  | Coincident | 12.82
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.38
|  |  |  | Coincident | 13.15
| Killarney 33_11kV | Substation Rating | MVA | Non-Coincident | 21.09
|  |  |  | Coincident | 21.09
|  | Raw Adjusted MD | MW | Non-Coincident | 15.45
|  |  |  | Coincident | 14.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.64
|  |  |  | Coincident | 14.38
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2227
|  |  |  | Coincident | -0.3333
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.73
|  |  |  | Coincident | 14.46
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.92
|  |  |  | Coincident | 14.64
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.52
|  |  |  | Coincident | 12.44
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.69
|  |  |  | Coincident | 12.59
| Kingsford 132_11kV | Substation Rating | MVA | Non-Coincident | 65.01
|  |  |  | Coincident | 62.24
|  | Raw Adjusted MD | MW | Non-Coincident | 56.01
|  |  |  | Coincident | 48.55
|  | Raw Adjusted MD | MVA | Non-Coincident | 56.19
|  |  |  | Coincident | 49.25
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.3859
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 55.91
|  |  |  | Coincident | 48.47
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 56.08
|  |  |  | Coincident | 49.17
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 54.2
|  |  |  | Coincident | 45.11
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 54.37
|  |  |  | Coincident | 45.76
| Kirrawee 132_11kV | Substation Rating | MVA | Non-Coincident | 44.56
|  |  |  | Coincident | 44.56
|  | Raw Adjusted MD | MW | Non-Coincident | 36.44
|  |  |  | Coincident | 34.8
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.51
|  |  |  | Coincident | 38.77
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.5528
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.45
|  |  |  | Coincident | 38.03
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.63
|  |  |  | Coincident | 42.37
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.83
|  |  |  | Coincident | 32.07
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 39.83
|  |  |  | Coincident | 35.73
| Kogarah 132_11kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 72.73
|  |  |  | Coincident | 71.65
|  | Raw Adjusted MD | MVA | Non-Coincident | 80.92
|  |  |  | Coincident | 79.72
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.7272
|  |  |  | Coincident | -0.8995
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 77.65
|  |  |  | Coincident | 76.5
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 86.39
|  |  |  | Coincident | 85.11
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 68.14
|  |  |  | Coincident | 67.13
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 75.81
|  |  |  | Coincident | 74.68
| Kotara 33_11kV | Substation Rating | MVA | Non-Coincident | 30.48
|  |  |  | Coincident | 30.48
|  | Raw Adjusted MD | MW | Non-Coincident | 24.71
|  |  |  | Coincident | 23.64
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.6
|  |  |  | Coincident | 24.49
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.9168
|  |  |  | Coincident | -0.3686
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.84
|  |  |  | Coincident | 28.54
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.92
|  |  |  | Coincident | 29.58
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.79
|  |  |  | Coincident | 24.67
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.72
|  |  |  | Coincident | 25.56
| Kurnell South 132_11kV | Substation Rating | MVA | Non-Coincident | 38.1
|  |  |  | Coincident | 38.1
|  | Raw Adjusted MD | MW | Non-Coincident | 6.563
|  |  |  | Coincident | 6.117
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.767
|  |  |  | Coincident | 6.307
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0354
|  |  |  | Coincident | -0.0854
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.56
|  |  |  | Coincident | 6.114
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.764
|  |  |  | Coincident | 6.304
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.56
|  |  |  | Coincident | 6.114
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.764
|  |  |  | Coincident | 6.304
| Kurri 132_11kV | Substation Rating | MVA | Non-Coincident | 57.27
|  |  |  | Coincident | 57.27
|  | Raw Adjusted MD | MW | Non-Coincident | 30.94
|  |  |  | Coincident | 28.8
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.7
|  |  |  | Coincident | 29.51
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2209
|  |  |  | Coincident | -0.7326
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.03
|  |  |  | Coincident | 31.68
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.87
|  |  |  | Coincident | 32.46
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.98
|  |  |  | Coincident | 27.9
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.72
|  |  |  | Coincident | 28.59
| Lake Munmorah 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 20.37
|  |  |  | Coincident | 18.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.5
|  |  |  | Coincident | 18.52
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.177
|  |  |  | Coincident | -0.8548
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.78
|  |  |  | Coincident | 18.77
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.91
|  |  |  | Coincident | 18.89
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.18
|  |  |  | Coincident | 16.42
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.29
|  |  |  | Coincident | 16.53
| Leichhardt 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Leichhardt 33_11kV | Substation Rating | MVA | Non-Coincident | 69.07
|  |  |  | Coincident | 65.83
|  | Raw Adjusted MD | MW | Non-Coincident | 23.06
|  |  |  | Coincident | 21.88
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.63
|  |  |  | Coincident | 23.83
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.3037
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.99
|  |  |  | Coincident | 23.06
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.66
|  |  |  | Coincident | 25.12
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.05
|  |  |  | Coincident | 20.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.61
|  |  |  | Coincident | 22.23
| Leightonfield 33_11kV | Substation Rating | MVA | Non-Coincident | 38.8
|  |  |  | Coincident | 38.8
|  | Raw Adjusted MD | MW | Non-Coincident | 23.29
|  |  |  | Coincident | 22.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.67
|  |  |  | Coincident | 23.63
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.66667
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6481
|  |  |  | Coincident | -0.2957
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.17
|  |  |  | Coincident | 24.1
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.66
|  |  |  | Coincident | 25.53
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.07
|  |  |  | Coincident | 22.09
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.44
|  |  |  | Coincident | 23.4
| Lemington 66_11kV | Substation Rating | MVA | Non-Coincident | 13.36
|  |  |  | Coincident | 13.36
|  | Raw Adjusted MD | MW | Non-Coincident | 2.458
|  |  |  | Coincident | 2.406
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.662
|  |  |  | Coincident | 2.605
|  | Date MD occurred |  | Non-Coincident | 42733
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0285
|  |  |  | Coincident | -0.0207
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.457
|  |  |  | Coincident | 2.405
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.66
|  |  |  | Coincident | 2.604
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.457
|  |  |  | Coincident | 2.405
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.66
|  |  |  | Coincident | 2.604
| Lidcombe 33_11kV | Substation Rating | MVA | Non-Coincident | 33.41
|  |  |  | Coincident | 33.41
|  | Raw Adjusted MD | MW | Non-Coincident | 19.87
|  |  |  | Coincident | 19.87
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.99
|  |  |  | Coincident | 21.99
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4771
|  |  |  | Coincident | -0.277
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.4
|  |  |  | Coincident | 21.4
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.68
|  |  |  | Coincident | 23.68
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.18
|  |  |  | Coincident | 19.18
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.22
|  |  |  | Coincident | 21.22
| Lindfield 33_11kV | Substation Rating | MVA | Non-Coincident | 36.81
|  |  |  | Coincident | 36.81
|  | Raw Adjusted MD | MW | Non-Coincident | 33.69
|  |  |  | Coincident | 31.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.65
|  |  |  | Coincident | 31.98
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0874
|  |  |  | Coincident | -0.427
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.79
|  |  |  | Coincident | 32.11
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.79
|  |  |  | Coincident | 33.03
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.56
|  |  |  | Coincident | 27.29
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.41
|  |  |  | Coincident | 28.07
| Lisarow 33_11kV | Substation Rating | MVA | Non-Coincident | 30.48
|  |  |  | Coincident | 30.48
|  | Raw Adjusted MD | MW | Non-Coincident | 25.06
|  |  |  | Coincident | 23.95
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.8
|  |  |  | Coincident | 24.65
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.228
|  |  |  | Coincident | -0.5498
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.02
|  |  |  | Coincident | 25.83
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.82
|  |  |  | Coincident | 26.59
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.98
|  |  |  | Coincident | 22.92
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.69
|  |  |  | Coincident | 23.59
| Long Jetty 66_11kV | Substation Rating | MVA | Non-Coincident | 71.69
|  |  |  | Coincident | 71.69
|  | Raw Adjusted MD | MW | Non-Coincident | 35.65
|  |  |  | Coincident | 34.23
|  | Raw Adjusted MD | MVA | Non-Coincident | 39.61
|  |  |  | Coincident | 38.03
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.112
|  |  |  | Coincident | -0.9333
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.41
|  |  |  | Coincident | 35.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.57
|  |  |  | Coincident | 39.91
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.69
|  |  |  | Coincident | 32.35
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 37.44
|  |  |  | Coincident | 35.94
| Lucas Heights 33_11kV | Substation Rating | MVA | Non-Coincident | 19.22
|  |  |  | Coincident | 19.22
|  | Raw Adjusted MD | MW | Non-Coincident | 7.857
|  |  |  | Coincident | 6.975
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.65
|  |  |  | Coincident | 7.678
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.857
|  |  |  | Coincident | 6.975
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.65
|  |  |  | Coincident | 7.678
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.857
|  |  |  | Coincident | 6.975
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.65
|  |  |  | Coincident | 7.678
| Macquarie Park 132_11kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 81.3
|  |  |  | Coincident | 71.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 84.16
|  |  |  | Coincident | 74.34
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.66667
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4042
|  |  |  | Coincident | -0.1844
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 86.88
|  |  |  | Coincident | 76.75
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 89.93
|  |  |  | Coincident | 79.44
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 81.43
|  |  |  | Coincident | 71.93
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 84.28
|  |  |  | Coincident | 74.46
| Maitland 33_11kV | Substation Rating | MVA | Non-Coincident | 36.66
|  |  |  | Coincident | 36.66
|  | Raw Adjusted MD | MW | Non-Coincident | 26.81
|  |  |  | Coincident | 25.42
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.57
|  |  |  | Coincident | 27.09
|  | Date MD occurred |  | Non-Coincident | 42748
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6653
|  |  |  | Coincident | -0.4833
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.24
|  |  |  | Coincident | 28.68
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.23
|  |  |  | Coincident | 30.56
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.67
|  |  |  | Coincident | 25.29
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.43
|  |  |  | Coincident | 26.96
| Manly 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 19.58
|  |  |  | Coincident | 14.29
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.54
|  |  |  | Coincident | 15.64
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.1047
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.74
|  |  |  | Coincident | 14.52
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.71
|  |  |  | Coincident | 15.89
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19
|  |  |  | Coincident | 13.6
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.93
|  |  |  | Coincident | 14.88
| Maroubra 132_11kV | Substation Rating | MVA | Non-Coincident | 102.8
|  |  |  | Coincident | 102.8
|  | Raw Adjusted MD | MW | Non-Coincident | 44.92
|  |  |  | Coincident | 40.57
|  | Raw Adjusted MD | MVA | Non-Coincident | 45.69
|  |  |  | Coincident | 42.05
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.3534
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.07
|  |  |  | Coincident | 42.94
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 47.87
|  |  |  | Coincident | 44.5
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 45.49
|  |  |  | Coincident | 39.83
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.27
|  |  |  | Coincident | 41.28
| Marrickville 132_11kV | Substation Rating | MVA | Non-Coincident | 72.67
|  |  |  | Coincident | 71.89
|  | Raw Adjusted MD | MW | Non-Coincident | 55.67
|  |  |  | Coincident | 49.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 56.55
|  |  |  | Coincident | 52.05
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -1.007
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 56.57
|  |  |  | Coincident | 54.01
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.47
|  |  |  | Coincident | 56.86
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 54.51
|  |  |  | Coincident | 48.55
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 55.38
|  |  |  | Coincident | 51.11
| Maryland 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 23.6
|  |  |  | Coincident | 20.32
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.22
|  |  |  | Coincident | 22.58
|  | Date MD occurred |  | Non-Coincident | 42752
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2951
|  |  |  | Coincident | -0.7116
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.81
|  |  |  | Coincident | 23.09
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.79
|  |  |  | Coincident | 25.65
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.27
|  |  |  | Coincident | 19.17
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.74
|  |  |  | Coincident | 21.3
| Mascot 33_11kV | Substation Rating | MVA | Non-Coincident | 78.44
|  |  |  | Coincident | 78.44
|  | Raw Adjusted MD | MW | Non-Coincident | 46.75
|  |  |  | Coincident | 43.43
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.94
|  |  |  | Coincident | 46.39
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.60417
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5291
|  |  |  | Coincident | -0.1986
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.73
|  |  |  | Coincident | 46.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 53.12
|  |  |  | Coincident | 49.35
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 46.04
|  |  |  | Coincident | 42.78
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 49.19
|  |  |  | Coincident | 45.7
| Matraville 33_11kV | Substation Rating | MVA | Non-Coincident | 72.67
|  |  |  | Coincident | 68.09
|  | Raw Adjusted MD | MW | Non-Coincident | 40.5
|  |  |  | Coincident | 34.52
|  | Raw Adjusted MD | MVA | Non-Coincident | 41.86
|  |  |  | Coincident | 36.9
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.4324
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 42.46
|  |  |  | Coincident | 35.26
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 43.89
|  |  |  | Coincident | 37.69
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.06
|  |  |  | Coincident | 32.92
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.44
|  |  |  | Coincident | 35.19
| Mayfield West 132_11kV | Substation Rating | MVA | Non-Coincident | 62.59
|  |  |  | Coincident | 62.59
|  | Raw Adjusted MD | MW | Non-Coincident | 25.17
|  |  |  | Coincident | 20.55
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.06
|  |  |  | Coincident | 22.1
|  | Date MD occurred |  | Non-Coincident | 42753
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.54167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.391
|  |  |  | Coincident | -0.5154
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.77
|  |  |  | Coincident | 21.86
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.78
|  |  |  | Coincident | 23.5
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.05
|  |  |  | Coincident | 19.63
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.85
|  |  |  | Coincident | 21.11
| Meadowbank 132_11kV | Substation Rating | MVA | Non-Coincident | 103.8
|  |  |  | Coincident | 103.8
|  | Raw Adjusted MD | MW | Non-Coincident | 78.94
|  |  |  | Coincident | 71.98
|  | Raw Adjusted MD | MVA | Non-Coincident | 82.97
|  |  |  | Coincident | 75.66
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5762
|  |  |  | Coincident | -0.8623
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 84.4
|  |  |  | Coincident | 76.96
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 88.71
|  |  |  | Coincident | 80.89
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 73.88
|  |  |  | Coincident | 67.37
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 77.65
|  |  |  | Coincident | 70.81
| Medowie 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 13.01
|  |  |  | Coincident | 11.48
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.42
|  |  |  | Coincident | 11.84
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.3233
|  |  |  | Coincident | -0.4839
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.16
|  |  |  | Coincident | 12.5
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.61
|  |  |  | Coincident | 12.89
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.2
|  |  |  | Coincident | 10.77
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.59
|  |  |  | Coincident | 11.11
| Menai 132_11kV | Substation Rating | MVA | Non-Coincident | 60.72
|  |  |  | Coincident | 60.72
|  | Raw Adjusted MD | MW | Non-Coincident | 49.27
|  |  |  | Coincident | 42.01
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.78
|  |  |  | Coincident | 42.45
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2748
|  |  |  | Coincident | -0.9111
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.02
|  |  |  | Coincident | 41.8
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 49.54
|  |  |  | Coincident | 42.24
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.06
|  |  |  | Coincident | 36.71
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 43.51
|  |  |  | Coincident | 37.1
| Merriwa 33_11kV | Substation Rating | MVA | Non-Coincident | 6.94
|  |  |  | Coincident | 6.94
|  | Raw Adjusted MD | MW | Non-Coincident | 3.692
|  |  |  | Coincident | 3.146
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.789
|  |  |  | Coincident | 3.229
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0008
|  |  |  | Coincident | -0.1146
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.904
|  |  |  | Coincident | 3.327
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.007
|  |  |  | Coincident | 3.414
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.537
|  |  |  | Coincident | 3.014
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.63
|  |  |  | Coincident | 3.093
| Metford 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 33.08
|  |  |  | Coincident | 30.79
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.76
|  |  |  | Coincident | 34.21
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2151
|  |  |  | Coincident | -0.7132
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.59
|  |  |  | Coincident | 34.98
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.77
|  |  |  | Coincident | 38.87
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.85
|  |  |  | Coincident | 30.57
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.5
|  |  |  | Coincident | 33.96
| Milperra 132_11kV | Substation Rating | MVA | Non-Coincident | 61.18
|  |  |  | Coincident | 61.18
|  | Raw Adjusted MD | MW | Non-Coincident | 46.73
|  |  |  | Coincident | 42.47
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.97
|  |  |  | Coincident | 45.42
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.64583
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.627
|  |  |  | Coincident | -0.7038
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.6
|  |  |  | Coincident | 45.08
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 53.04
|  |  |  | Coincident | 48.21
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 45.77
|  |  |  | Coincident | 41.6
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 48.95
|  |  |  | Coincident | 44.49
| Miranda 33_11kV | Substation Rating | MVA | Non-Coincident | 41.97
|  |  |  | Coincident | 41.97
|  | Raw Adjusted MD | MW | Non-Coincident | 36.94
|  |  |  | Coincident | 34.17
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.34
|  |  |  | Coincident | 35.46
|  | Date MD occurred |  | Non-Coincident | 42771
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4074
|  |  |  | Coincident | -0.2959
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 41.5
|  |  |  | Coincident | 38.39
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 43.07
|  |  |  | Coincident | 39.84
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.38
|  |  |  | Coincident | 32.73
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.72
|  |  |  | Coincident | 33.97
| Mitchell Line 66_11kV | Substation Rating | MVA | Non-Coincident | 23.95
|  |  |  | Coincident | 23.95
|  | Raw Adjusted MD | MW | Non-Coincident | 12.24
|  |  |  | Coincident | 11.68
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.63
|  |  |  | Coincident | 12.04
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0552
|  |  |  | Coincident | -0.183
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.72
|  |  |  | Coincident | 13.09
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.16
|  |  |  | Coincident | 13.5
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.45
|  |  |  | Coincident | 11.87
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.84
|  |  |  | Coincident | 12.25
| Mitchells Flat 66_11kV | Substation Rating | MVA | Non-Coincident | 6.04
|  |  |  | Coincident | 6.04
|  | Raw Adjusted MD | MW | Non-Coincident | 1.684
|  |  |  | Coincident | 1.323
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.696
|  |  |  | Coincident | 1.331
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0055
|  |  |  | Coincident | -0.0513
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.82
|  |  |  | Coincident | 1.429
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.832
|  |  |  | Coincident | 1.438
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.613
|  |  |  | Coincident | 1.266
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.624
|  |  |  | Coincident | 1.275
| Mona Vale 33_11kV | Substation Rating | MVA | Non-Coincident | 57.41
|  |  |  | Coincident | 57.41
|  | Raw Adjusted MD | MW | Non-Coincident | 33.85
|  |  |  | Coincident | 31.68
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.58
|  |  |  | Coincident | 34.24
|  | Date MD occurred |  | Non-Coincident | 42759
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.34
|  |  |  | Coincident | -0.5387
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.83
|  |  |  | Coincident | 34.47
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.8
|  |  |  | Coincident | 37.25
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32
|  |  |  | Coincident | 29.95
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.58
|  |  |  | Coincident | 32.36
| Moonan 33_11kV | Substation Rating | MVA | Non-Coincident | 2.86
|  |  |  | Coincident | 2.86
|  | Raw Adjusted MD | MW | Non-Coincident | 1.012
|  |  |  | Coincident | 0.702
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.069
|  |  |  | Coincident | 0.742
|  | Date MD occurred |  | Non-Coincident | 42767
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0061
|  |  |  | Coincident | -0.0202
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.043
|  |  |  | Coincident | 0.724
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.101
|  |  |  | Coincident | 0.764
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.942
|  |  |  | Coincident | 0.654
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.995
|  |  |  | Coincident | 0.69
| Morisset 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 22.03
|  |  |  | Coincident | 21.03
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.83
|  |  |  | Coincident | 21.79
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.7555
|  |  |  | Coincident | -0.7555
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.82
|  |  |  | Coincident | 23.69
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.72
|  |  |  | Coincident | 24.55
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.45
|  |  |  | Coincident | 20.47
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.23
|  |  |  | Coincident | 21.22
| Mortdale 33_11kV | Substation Rating | MVA | Non-Coincident | 64.25
|  |  |  | Coincident | 64.25
|  | Raw Adjusted MD | MW | Non-Coincident | 49.73
|  |  |  | Coincident | 44.48
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.46
|  |  |  | Coincident | 46.03
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2534
|  |  |  | Coincident | -0.8403
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.27
|  |  |  | Coincident | 45.86
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 53.05
|  |  |  | Coincident | 47.45
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.45
|  |  |  | Coincident | 38.87
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.97
|  |  |  | Coincident | 40.22
| Mosman 132_11kV | Substation Rating | MVA | Non-Coincident | 89.05
|  |  |  | Coincident | 82.46
|  | Raw Adjusted MD | MW | Non-Coincident | 81.83
|  |  |  | Coincident | 64.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 82.46
|  |  |  | Coincident | 65.37
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.6085
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 82.85
|  |  |  | Coincident | 66.7
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 83.49
|  |  |  | Coincident | 67.27
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 79.61
|  |  |  | Coincident | 58.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 80.22
|  |  |  | Coincident | 58.9
| Mt Hutton 33_11kV | Substation Rating | MVA | Non-Coincident | 32.68
|  |  |  | Coincident | 32.68
|  | Raw Adjusted MD | MW | Non-Coincident | 19.65
|  |  |  | Coincident | 17.29
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.24
|  |  |  | Coincident | 17.81
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6659
|  |  |  | Coincident | -0.4836
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.75
|  |  |  | Coincident | 20.9
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.45
|  |  |  | Coincident | 21.52
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.07
|  |  |  | Coincident | 17.66
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.67
|  |  |  | Coincident | 18.19
| Mt Thorley 66_11kV | Substation Rating | MVA | Non-Coincident | 20.25
|  |  |  | Coincident | 20.25
|  | Raw Adjusted MD | MW | Non-Coincident | 6.945
|  |  |  | Coincident | 5.872
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.36
|  |  |  | Coincident | 6.223
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5079
|  |  |  | Coincident | -0.2042
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.409
|  |  |  | Coincident | 6.264
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.851
|  |  |  | Coincident | 6.639
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.811
|  |  |  | Coincident | 5.759
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.218
|  |  |  | Coincident | 6.103
| Muswellbrook 33_11kV | Substation Rating | MVA | Non-Coincident | 23.82
|  |  |  | Coincident | 23.82
|  | Raw Adjusted MD | MW | Non-Coincident | 14.58
|  |  |  | Coincident | 13.17
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.2
|  |  |  | Coincident | 14.63
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2561
|  |  |  | Coincident | -0.3168
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.55
|  |  |  | Coincident | 14.04
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.28
|  |  |  | Coincident | 15.6
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.16
|  |  |  | Coincident | 12.79
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.74
|  |  |  | Coincident | 14.21
| Narrabeen 33_11kV | Substation Rating | MVA | Non-Coincident | 19.62
|  |  |  | Coincident | 19.62
|  | Raw Adjusted MD | MW | Non-Coincident | 12.38
|  |  |  | Coincident | 12.04
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.11
|  |  |  | Coincident | 12.75
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2928
|  |  |  | Coincident | -0.2928
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.98
|  |  |  | Coincident | 11.65
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.68
|  |  |  | Coincident | 12.33
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.65
|  |  |  | Coincident | 10.35
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.27
|  |  |  | Coincident | 10.96
| Nelson Bay 33_11kV | Substation Rating | MVA | Non-Coincident | 44.32
|  |  |  | Coincident | 44.32
|  | Raw Adjusted MD | MW | Non-Coincident | 26.7
|  |  |  | Coincident | 21.11
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.11
|  |  |  | Coincident | 21.44
|  | Date MD occurred |  | Non-Coincident | 42746
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0493
|  |  |  | Coincident | -0.8259
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29
|  |  |  | Coincident | 22.93
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.44
|  |  |  | Coincident | 23.28
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.48
|  |  |  | Coincident | 20.15
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.87
|  |  |  | Coincident | 20.45
| New Lambton 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 16.77
|  |  |  | Coincident | 16.17
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.23
|  |  |  | Coincident | 16.61
|  | Date MD occurred |  | Non-Coincident | 42759
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5749
|  |  |  | Coincident | -0.2261
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.97
|  |  |  | Coincident | 18.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.5
|  |  |  | Coincident | 18.8
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.75
|  |  |  | Coincident | 16.15
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.21
|  |  |  | Coincident | 16.6
| Newcastle CBD 33_11kV | Substation Rating | MVA | Non-Coincident | 76.21
|  |  |  | Coincident | 76.21
|  | Raw Adjusted MD | MW | Non-Coincident | 46.89
|  |  |  | Coincident | 40.61
|  | Raw Adjusted MD | MVA | Non-Coincident | 47.12
|  |  |  | Coincident | 40.81
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.133
|  |  |  | Coincident | -0.4554
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.1
|  |  |  | Coincident | 44.25
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.35
|  |  |  | Coincident | 44.47
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.83
|  |  |  | Coincident | 38.83
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.05
|  |  |  | Coincident | 39.01
| Newdell 66_11kV | Substation Rating | MVA | Non-Coincident | 26.83
|  |  |  | Coincident | 26.83
|  | Raw Adjusted MD | MW | Non-Coincident | 4.159
|  |  |  | Coincident | 2.527
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.356
|  |  |  | Coincident | 2.646
|  | Date MD occurred |  | Non-Coincident | 42782
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0367
|  |  |  | Coincident | -0.0146
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.163
|  |  |  | Coincident | 2.529
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.36
|  |  |  | Coincident | 2.649
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.163
|  |  |  | Coincident | 2.529
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.36
|  |  |  | Coincident | 2.649
| Newport 33_11kV | Substation Rating | MVA | Non-Coincident | 22.38
|  |  |  | Coincident | 20.75
|  | Raw Adjusted MD | MW | Non-Coincident | 15.2
|  |  |  | Coincident | 10.93
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.51
|  |  |  | Coincident | 11.07
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.2377
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.17
|  |  |  | Coincident | 11.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.48
|  |  |  | Coincident | 11.21
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.6
|  |  |  | Coincident | 9.905
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.9
|  |  |  | Coincident | 10.03
| Noraville 33_11kV | Substation Rating | MVA | Non-Coincident | 37.5
|  |  |  | Coincident | 34.37
|  | Raw Adjusted MD | MW | Non-Coincident | 21.9
|  |  |  | Coincident | 18.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.35
|  |  |  | Coincident | 20.02
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.7404
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.96
|  |  |  | Coincident | 19.27
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.47
|  |  |  | Coincident | 20.49
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.46
|  |  |  | Coincident | 16.99
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.94
|  |  |  | Coincident | 18.08
| North Head 33_11kV | Substation Rating | MVA | Non-Coincident | 23.64
|  |  |  | Coincident | 23.64
|  | Raw Adjusted MD | MW | Non-Coincident | 19.26
|  |  |  | Coincident | 6.606
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.28
|  |  |  | Coincident | 7.259
|  | Date MD occurred |  | Non-Coincident | 42560
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.4375
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.0422
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.26
|  |  |  | Coincident | 6.606
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.28
|  |  |  | Coincident | 7.259
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.26
|  |  |  | Coincident | 6.606
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.28
|  |  |  | Coincident | 7.259
| North Sydney 132_11kV | Substation Rating | MVA | Non-Coincident | 136.8
|  |  |  | Coincident | 136.8
|  | Raw Adjusted MD | MW | Non-Coincident | 68.99
|  |  |  | Coincident | 65.26
|  | Raw Adjusted MD | MVA | Non-Coincident | 76.66
|  |  |  | Coincident | 72.51
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2137
|  |  |  | Coincident | -0.0784
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 72.1
|  |  |  | Coincident | 68.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 80.11
|  |  |  | Coincident | 75.78
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 66.17
|  |  |  | Coincident | 62.59
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 73.52
|  |  |  | Coincident | 69.55
| North Sydney 33_11kV | Substation Rating | MVA | Non-Coincident | 119.7
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident | 16.64
|  |  |  | Coincident | 0.034
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.96
|  |  |  | Coincident | 0.038
|  | Date MD occurred |  | Non-Coincident | 42566
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.45833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.11
|  |  |  | Coincident | 0.048
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.43
|  |  |  | Coincident | 0.053
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.72
|  |  |  | Coincident | 0.045
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.03
|  |  |  | Coincident | 0.05
| Nulkaba 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 22.31
|  |  |  | Coincident | 21.43
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.25
|  |  |  | Coincident | 22.34
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.398
|  |  |  | Coincident | -0.7421
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.61
|  |  |  | Coincident | 23.64
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.64
|  |  |  | Coincident | 24.63
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.08
|  |  |  | Coincident | 21.21
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.02
|  |  |  | Coincident | 22.11
| Olympic Park 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Paddington 33_11kV | Substation Rating | MVA | Non-Coincident | 66.47
|  |  |  | Coincident | 66.47
|  | Raw Adjusted MD | MW | Non-Coincident | 34.18
|  |  |  | Coincident | 33.29
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.07
|  |  |  | Coincident | 35.13
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1893
|  |  |  | Coincident | -0.0701
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.79
|  |  |  | Coincident | 33.89
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.71
|  |  |  | Coincident | 35.76
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.79
|  |  |  | Coincident | 30.97
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.55
|  |  |  | Coincident | 32.69
| Paxton 33_11kV | Substation Rating | MVA | Non-Coincident | 25.45
|  |  |  | Coincident | 25.45
|  | Raw Adjusted MD | MW | Non-Coincident | 6.519
|  |  |  | Coincident | 5.147
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.878
|  |  |  | Coincident | 5.43
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0988
|  |  |  | Coincident | -0.2383
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.545
|  |  |  | Coincident | 5.167
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.906
|  |  |  | Coincident | 5.452
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.868
|  |  |  | Coincident | 4.632
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.191
|  |  |  | Coincident | 4.888
| Peats Ridge 33_11kV | Substation Rating | MVA | Non-Coincident | 17.09
|  |  |  | Coincident | 17.09
|  | Raw Adjusted MD | MW | Non-Coincident | 13.26
|  |  |  | Coincident | 10.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.73
|  |  |  | Coincident | 11.31
|  | Date MD occurred |  | Non-Coincident | 42705
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6438
|  |  |  | Coincident | -0.2359
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.03
|  |  |  | Coincident | 9.234
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.36
|  |  |  | Coincident | 10.26
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.18
|  |  |  | Coincident | 8.584
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.42
|  |  |  | Coincident | 9.538
| Pelican 33_11kV | Substation Rating | MVA | Non-Coincident | 25.64
|  |  |  | Coincident | 25.64
|  | Raw Adjusted MD | MW | Non-Coincident | 11.73
|  |  |  | Coincident | 10.98
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.13
|  |  |  | Coincident | 11.36
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6012
|  |  |  | Coincident | -0.2364
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.53
|  |  |  | Coincident | 12.66
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.99
|  |  |  | Coincident | 13.1
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.73
|  |  |  | Coincident | 10.98
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.13
|  |  |  | Coincident | 11.35
| Pennant Hills 132_11kV | Substation Rating | MVA | Non-Coincident | 106.9
|  |  |  | Coincident | 106.9
|  | Raw Adjusted MD | MW | Non-Coincident | 88.71
|  |  |  | Coincident | 82.69
|  | Raw Adjusted MD | MVA | Non-Coincident | 91.89
|  |  |  | Coincident | 85.66
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2988
|  |  |  | Coincident | -1.459
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 98.46
|  |  |  | Coincident | 91.78
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 102
|  |  |  | Coincident | 95.08
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 82.62
|  |  |  | Coincident | 77.02
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 85.58
|  |  |  | Coincident | 79.78
| Port Botany 33_11kV | Substation Rating | MVA | Non-Coincident | 59.16
|  |  |  | Coincident | 59.16
|  | Raw Adjusted MD | MW | Non-Coincident | 6.645
|  |  |  | Coincident | 6.057
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.545
|  |  |  | Coincident | 6.878
|  | Date MD occurred |  | Non-Coincident | 42752
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.64583
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0632
|  |  |  | Coincident | -0.0273
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.496
|  |  |  | Coincident | 6.833
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.511
|  |  |  | Coincident | 7.759
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.645
|  |  |  | Coincident | 6.057
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.545
|  |  |  | Coincident | 6.878
| Potts Hill 132_11kV | Substation Rating | MVA | Non-Coincident | 54.87
|  |  |  | Coincident | 54.87
|  | Raw Adjusted MD | MW | Non-Coincident | 41.55
|  |  |  | Coincident | 40.86
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.68
|  |  |  | Coincident | 41.97
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.929
|  |  |  | Coincident | -0.7062
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.94
|  |  |  | Coincident | 44.19
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.16
|  |  |  | Coincident | 45.39
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.67
|  |  |  | Coincident | 39.99
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.77
|  |  |  | Coincident | 41.08
| Punchbowl 33_11kV | Substation Rating | MVA | Non-Coincident | 35.36
|  |  |  | Coincident | 35.36
|  | Raw Adjusted MD | MW | Non-Coincident | 32.62
|  |  |  | Coincident | 30.26
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.99
|  |  |  | Coincident | 32.83
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.5304
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.72
|  |  |  | Coincident | 33.26
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.13
|  |  |  | Coincident | 36.09
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.17
|  |  |  | Coincident | 29.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.52
|  |  |  | Coincident | 31.89
| Pymble 33_11kV | Substation Rating | MVA | Non-Coincident | 19
|  |  |  | Coincident | 19
|  | Raw Adjusted MD | MW | Non-Coincident | 35.8
|  |  |  | Coincident | 34.15
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.97
|  |  |  | Coincident | 36.22
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.243
|  |  |  | Coincident | -0.3637
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.88
|  |  |  | Coincident | 36.13
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.18
|  |  |  | Coincident | 38.33
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.54
|  |  |  | Coincident | 31.03
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.51
|  |  |  | Coincident | 32.92
| RNS Hospital 132_11kV | Substation Rating | MVA | Non-Coincident | 53.54
|  |  |  | Coincident | 53.54
|  | Raw Adjusted MD | MW | Non-Coincident | 13.15
|  |  |  | Coincident | 12.23
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.32
|  |  |  | Coincident | 12.38
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0225
|  |  |  | Coincident | -0.0082
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.15
|  |  |  | Coincident | 12.23
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.32
|  |  |  | Coincident | 12.38
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.15
|  |  |  | Coincident | 12.23
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.32
|  |  |  | Coincident | 12.38
| Rathmines 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 16.95
|  |  |  | Coincident | 14.19
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.45
|  |  |  | Coincident | 14.61
|  | Date MD occurred |  | Non-Coincident | 42746
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0076
|  |  |  | Coincident | -0.6647
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.96
|  |  |  | Coincident | 15.88
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.52
|  |  |  | Coincident | 16.35
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.88
|  |  |  | Coincident | 13.3
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.35
|  |  |  | Coincident | 13.69
| Raymond Terr NEW 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 23.44
|  |  |  | Coincident | 20.95
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.9
|  |  |  | Coincident | 21.36
|  | Date MD occurred |  | Non-Coincident | 42752
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.8337
|  |  |  | Coincident | -0.5337
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.88
|  |  |  | Coincident | 24.02
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.41
|  |  |  | Coincident | 24.49
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.39
|  |  |  | Coincident | 20.9
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.85
|  |  |  | Coincident | 21.31
| Revesby 132_11kV | Substation Rating | MVA | Non-Coincident | 44.93
|  |  |  | Coincident | 44.93
|  | Raw Adjusted MD | MW | Non-Coincident | 47.15
|  |  |  | Coincident | 42.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.08
|  |  |  | Coincident | 43.82
|  | Date MD occurred |  | Non-Coincident | 42771
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0014
|  |  |  | Coincident | -0.7346
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 48.24
|  |  |  | Coincident | 43.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.22
|  |  |  | Coincident | 44.84
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.61
|  |  |  | Coincident | 37.15
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 43.31
|  |  |  | Coincident | 38.67
| Riverwood 33_11kV | Substation Rating | MVA | Non-Coincident | 42.81
|  |  |  | Coincident | 42.81
|  | Raw Adjusted MD | MW | Non-Coincident | 28.58
|  |  |  | Coincident | 26.31
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.73
|  |  |  | Coincident | 28.29
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.308
|  |  |  | Coincident | -0.5834
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.84
|  |  |  | Coincident | 27.47
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.08
|  |  |  | Coincident | 29.54
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.67
|  |  |  | Coincident | 23.63
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 27.6
|  |  |  | Coincident | 25.41
| Rockdale 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Rockdale 33_11kV | Substation Rating | MVA | Non-Coincident | 27.09
|  |  |  | Coincident | 27.09
|  | Raw Adjusted MD | MW | Non-Coincident | 19.37
|  |  |  | Coincident | 16.54
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.95
|  |  |  | Coincident | 18.16
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.1775
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.58
|  |  |  | Coincident | 18.67
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.19
|  |  |  | Coincident | 20.5
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.42
|  |  |  | Coincident | 16.03
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20
|  |  |  | Coincident | 17.59
| Rose Bay 132_11kV | Substation Rating | MVA | Non-Coincident | 59.25
|  |  |  | Coincident | 59.25
|  | Raw Adjusted MD | MW | Non-Coincident | 41.04
|  |  |  | Coincident | 32.17
|  | Raw Adjusted MD | MVA | Non-Coincident | 41.2
|  |  |  | Coincident | 32.84
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.3471
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 42.05
|  |  |  | Coincident | 32.12
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 42.21
|  |  |  | Coincident | 32.79
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.15
|  |  |  | Coincident | 28.79
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 40.3
|  |  |  | Coincident | 29.39
| Rothbury 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 12.78
|  |  |  | Coincident | 11.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.01
|  |  |  | Coincident | 12.04
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.64583
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.7414
|  |  |  | Coincident | -0.3049
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.31
|  |  |  | Coincident | 11.39
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.54
|  |  |  | Coincident | 11.6
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.15
|  |  |  | Coincident | 10.31
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.35
|  |  |  | Coincident | 10.5
| Rouchel 33_11kV | Substation Rating | MVA | Non-Coincident | 5.77
|  |  |  | Coincident | 5.77
|  | Raw Adjusted MD | MW | Non-Coincident | 1.504
|  |  |  | Coincident | 1.174
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.613
|  |  |  | Coincident | 1.259
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0003
|  |  |  | Coincident | -0.0223
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.501
|  |  |  | Coincident | 1.172
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.61
|  |  |  | Coincident | 1.257
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.501
|  |  |  | Coincident | 1.172
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.61
|  |  |  | Coincident | 1.257
| Rutherford 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 31.35
|  |  |  | Coincident | 30.07
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.7
|  |  |  | Coincident | 30.4
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.932
|  |  |  | Coincident | -0.7599
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.26
|  |  |  | Coincident | 32.86
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.64
|  |  |  | Coincident | 33.22
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.12
|  |  |  | Coincident | 29.85
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.47
|  |  |  | Coincident | 30.18
| Sans Souci 33_11kV | Substation Rating | MVA | Non-Coincident | 24.29
|  |  |  | Coincident | 24.29
|  | Raw Adjusted MD | MW | Non-Coincident | 16.84
|  |  |  | Coincident | 15.04
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.15
|  |  |  | Coincident | 15.32
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0618
|  |  |  | Coincident | -0.2049
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.25
|  |  |  | Coincident | 15.41
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.56
|  |  |  | Coincident | 15.69
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.67
|  |  |  | Coincident | 13.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.93
|  |  |  | Coincident | 13.34
| Scone 66_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 16.23
|  |  |  | Coincident | 15.49
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.33
|  |  |  | Coincident | 15.58
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1108
|  |  |  | Coincident | -0.3676
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.31
|  |  |  | Coincident | 17.48
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.42
|  |  |  | Coincident | 17.58
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.9
|  |  |  | Coincident | 16.13
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17
|  |  |  | Coincident | 16.23
| Sefton 132_11kV | Substation Rating | MVA | Non-Coincident | 94.58
|  |  |  | Coincident | 94.58
|  | Raw Adjusted MD | MW | Non-Coincident | 48.64
|  |  |  | Coincident | 46.61
|  | Raw Adjusted MD | MVA | Non-Coincident | 50.93
|  |  |  | Coincident | 48.79
|  | Date MD occurred |  | Non-Coincident | 42752
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6417
|  |  |  | Coincident | -0.9604
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 54.7
|  |  |  | Coincident | 52.4
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.26
|  |  |  | Coincident | 54.86
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 47.39
|  |  |  | Coincident | 45.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 49.61
|  |  |  | Coincident | 47.53
| Singleton 66_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 21.74
|  |  |  | Coincident | 20.42
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.11
|  |  |  | Coincident | 21.7
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4839
|  |  |  | Coincident | -0.3515
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.79
|  |  |  | Coincident | 21.4
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.22
|  |  |  | Coincident | 22.75
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.84
|  |  |  | Coincident | 19.57
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.15
|  |  |  | Coincident | 20.8
| Singleton North 66_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 18.26
|  |  |  | Coincident | 15.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.27
|  |  |  | Coincident | 16.5
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2689
|  |  |  | Coincident | -0.5095
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.02
|  |  |  | Coincident | 17.14
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.14
|  |  |  | Coincident | 18.1
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.85
|  |  |  | Coincident | 15.28
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.85
|  |  |  | Coincident | 16.13
| Somersby 132_11kV | Substation Rating | MVA | Non-Coincident | 51.9
|  |  |  | Coincident | 51.9
|  | Raw Adjusted MD | MW | Non-Coincident | 18.3
|  |  |  | Coincident | 14.41
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.46
|  |  |  | Coincident | 15.32
|  | Date MD occurred |  | Non-Coincident | 42752
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.047
|  |  |  | Coincident | -0.3879
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.6
|  |  |  | Coincident | 15.43
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.84
|  |  |  | Coincident | 16.4
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.76
|  |  |  | Coincident | 13.98
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.89
|  |  |  | Coincident | 14.87
| St Ives 33_11kV | Substation Rating | MVA | Non-Coincident | 58.47
|  |  |  | Coincident | 58.47
|  | Raw Adjusted MD | MW | Non-Coincident | 52.82
|  |  |  | Coincident | 47.36
|  | Raw Adjusted MD | MVA | Non-Coincident | 54.74
|  |  |  | Coincident | 49.08
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6675
|  |  |  | Coincident | -0.6675
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 53.68
|  |  |  | Coincident | 48.13
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 55.63
|  |  |  | Coincident | 49.87
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 45.21
|  |  |  | Coincident | 40.54
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.85
|  |  |  | Coincident | 42.01
| St Peters 132_11kV | Substation Rating | MVA | Non-Coincident | 87.45
|  |  |  | Coincident | 87.45
|  | Raw Adjusted MD | MW | Non-Coincident | 58.21
|  |  |  | Coincident | 56.22
|  | Raw Adjusted MD | MVA | Non-Coincident | 63.18
|  |  |  | Coincident | 61.03
|  | Date MD occurred |  | Non-Coincident | 42772
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.518
|  |  |  | Coincident | -0.5627
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 63.9
|  |  |  | Coincident | 61.72
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 69.36
|  |  |  | Coincident | 67
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 58.8
|  |  |  | Coincident | 56.8
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 63.82
|  |  |  | Coincident | 61.65
| Stockton 33_11kV | Substation Rating | MVA | Non-Coincident | 20.01
|  |  |  | Coincident | 20.01
|  | Raw Adjusted MD | MW | Non-Coincident | 9.121
|  |  |  | Coincident | 7.436
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.349
|  |  |  | Coincident | 7.622
|  | Date MD occurred |  | Non-Coincident | 42746
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0879
|  |  |  | Coincident | -0.212
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.58
|  |  |  | Coincident | 8.622
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.84
|  |  |  | Coincident | 8.837
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.945
|  |  |  | Coincident | 7.292
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.169
|  |  |  | Coincident | 7.475
| Surry Hills 33_11kV | Substation Rating | MVA | Non-Coincident | 77.75
|  |  |  | Coincident | 77.75
|  | Raw Adjusted MD | MW | Non-Coincident | 37.37
|  |  |  | Coincident | 32.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.89
|  |  |  | Coincident | 34.87
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.0507
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.61
|  |  |  | Coincident | 35.24
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.18
|  |  |  | Coincident | 37.44
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 37.47
|  |  |  | Coincident | 32.78
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 39
|  |  |  | Coincident | 34.83
| Swansea 33_11kV | Substation Rating | MVA | Non-Coincident | 16.42
|  |  |  | Coincident | 16.42
|  | Raw Adjusted MD | MW | Non-Coincident | 13.14
|  |  |  | Coincident | 10.47
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.38
|  |  |  | Coincident | 10.66
|  | Date MD occurred |  | Non-Coincident | 42746
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0216
|  |  |  | Coincident | -0.3627
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.91
|  |  |  | Coincident | 11.08
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.16
|  |  |  | Coincident | 11.28
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.07
|  |  |  | Coincident | 9.613
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.29
|  |  |  | Coincident | 9.786
| Tanilba Bay 33_11kV | Substation Rating | MVA | Non-Coincident | 18.73
|  |  |  | Coincident | 18.73
|  | Raw Adjusted MD | MW | Non-Coincident | 11.42
|  |  |  | Coincident | 9.126
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.83
|  |  |  | Coincident | 9.455
|  | Date MD occurred |  | Non-Coincident | 42746
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1648
|  |  |  | Coincident | -0.3973
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.25
|  |  |  | Coincident | 9.796
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.7
|  |  |  | Coincident | 10.15
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.65
|  |  |  | Coincident | 8.511
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.03
|  |  |  | Coincident | 8.817
| Tarro 33_11kV | Substation Rating | MVA | Non-Coincident | 23.82
|  |  |  | Coincident | 23.82
|  | Raw Adjusted MD | MW | Non-Coincident | 22.07
|  |  |  | Coincident | 20.31
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.8
|  |  |  | Coincident | 21.9
|  | Date MD occurred |  | Non-Coincident | 42753
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.9802
|  |  |  | Coincident | -0.3633
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.76
|  |  |  | Coincident | 21.86
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.62
|  |  |  | Coincident | 23.57
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.67
|  |  |  | Coincident | 19.94
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.37
|  |  |  | Coincident | 21.51
| Telarah 33_11kV | Substation Rating | MVA | Non-Coincident | 15.24
|  |  |  | Coincident | 15.24
|  | Raw Adjusted MD | MW | Non-Coincident | 13.08
|  |  |  | Coincident | 11.73
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.36
|  |  |  | Coincident | 11.97
|  | Date MD occurred |  | Non-Coincident | 42765
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1066
|  |  |  | Coincident | -0.257
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.86
|  |  |  | Coincident | 13.32
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.17
|  |  |  | Coincident | 13.59
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.12
|  |  |  | Coincident | 11.76
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.4
|  |  |  | Coincident | 12.01
| Terrey Hills 33_11kV | Substation Rating | MVA | Non-Coincident | 30.48
|  |  |  | Coincident | 30.48
|  | Raw Adjusted MD | MW | Non-Coincident | 16.8
|  |  |  | Coincident | 16.24
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.87
|  |  |  | Coincident | 17.28
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.54167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.5947
|  |  |  | Coincident | -0.2227
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.17
|  |  |  | Coincident | 17.57
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.33
|  |  |  | Coincident | 18.69
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.23
|  |  |  | Coincident | 15.69
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.27
|  |  |  | Coincident | 16.7
| Thornton 33_11kV | Substation Rating | MVA | Non-Coincident | 54.45
|  |  |  | Coincident | 54.45
|  | Raw Adjusted MD | MW | Non-Coincident | 32.31
|  |  |  | Coincident | 29.72
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.3
|  |  |  | Coincident | 31.55
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1902
|  |  |  | Coincident | -0.929
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.04
|  |  |  | Coincident | 34.99
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.38
|  |  |  | Coincident | 37.14
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.12
|  |  |  | Coincident | 29.54
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.1
|  |  |  | Coincident | 31.36
| Tighes Hill 33_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Tomago 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 10.87
|  |  |  | Coincident | 5.857
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.56
|  |  |  | Coincident | 6.383
|  | Date MD occurred |  | Non-Coincident | 42549
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.35417
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.1481
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.13
|  |  |  | Coincident | 6.391
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.84
|  |  |  | Coincident | 6.966
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.83
|  |  |  | Coincident | 6
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.52
|  |  |  | Coincident | 6.539
| Tomalpin 33_11kV | Substation Rating | MVA | Non-Coincident | 20.77
|  |  |  | Coincident | 20.77
|  | Raw Adjusted MD | MW | Non-Coincident | 0.35
|  |  |  | Coincident | 0.027
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.351
|  |  |  | Coincident | 0.027
|  | Date MD occurred |  | Non-Coincident | 42752
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.349
|  |  |  | Coincident | 0.027
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.35
|  |  |  | Coincident | 0.027
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.349
|  |  |  | Coincident | 0.027
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.35
|  |  |  | Coincident | 0.027
| Tomaree 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 18.83
|  |  |  | Coincident | 14.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.27
|  |  |  | Coincident | 14.55
|  | Date MD occurred |  | Non-Coincident | 42746
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.0231
|  |  |  | Coincident | -0.3877
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.67
|  |  |  | Coincident | 14.85
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.13
|  |  |  | Coincident | 15.2
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.34
|  |  |  | Coincident | 13.09
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.75
|  |  |  | Coincident | 13.4
| Top Ryde 132_11kV | Substation Rating | MVA | Non-Coincident | 61.25
|  |  |  | Coincident | 61.25
|  | Raw Adjusted MD | MW | Non-Coincident | 58.68
|  |  |  | Coincident | 57.6
|  | Raw Adjusted MD | MVA | Non-Coincident | 59.98
|  |  |  | Coincident | 58.87
|  | Date MD occurred |  | Non-Coincident | 42776
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4443
|  |  |  | Coincident | -0.5495
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 64.78
|  |  |  | Coincident | 63.59
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 66.21
|  |  |  | Coincident | 64.99
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 55.78
|  |  |  | Coincident | 54.76
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 57.02
|  |  |  | Coincident | 55.97
| Toronto 33_11kV | Substation Rating | MVA | Non-Coincident | 18.86
|  |  |  | Coincident | 18.86
|  | Raw Adjusted MD | MW | Non-Coincident | 14.48
|  |  |  | Coincident | 14.24
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.08
|  |  |  | Coincident | 14.83
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.805
|  |  |  | Coincident | -0.3166
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.33
|  |  |  | Coincident | 16.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.01
|  |  |  | Coincident | 16.74
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.2
|  |  |  | Coincident | 13.97
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.79
|  |  |  | Coincident | 14.55
| Toronto West 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Turramurra 33_11kV | Substation Rating | MVA | Non-Coincident | 43.32
|  |  |  | Coincident | 43.32
|  | Raw Adjusted MD | MW | Non-Coincident | 40.53
|  |  |  | Coincident | 36.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 41.35
|  |  |  | Coincident | 37.67
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2497
|  |  |  | Coincident | -0.473
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 41.93
|  |  |  | Coincident | 38.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 42.77
|  |  |  | Coincident | 38.96
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.69
|  |  |  | Coincident | 32.51
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.41
|  |  |  | Coincident | 33.17
| Umina 66_11kV | Substation Rating | MVA | Non-Coincident | 58.82
|  |  |  | Coincident | 58.82
|  | Raw Adjusted MD | MW | Non-Coincident | 30.82
|  |  |  | Coincident | 28.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.59
|  |  |  | Coincident | 30.71
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.4527
|  |  |  | Coincident | -0.6775
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.2
|  |  |  | Coincident | 29.44
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.09
|  |  |  | Coincident | 32.08
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 27.91
|  |  |  | Coincident | 25.52
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.41
|  |  |  | Coincident | 27.81
| Vales Point 33_11kV | Substation Rating | MVA | Non-Coincident | 15.24
|  |  |  | Coincident | 15.24
|  | Raw Adjusted MD | MW | Non-Coincident | 6.891
|  |  |  | Coincident | 2.773
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.216
|  |  |  | Coincident | 3.306
|  | Date MD occurred |  | Non-Coincident | 42690
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.769
|  |  |  | Coincident | 3.126
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.264
|  |  |  | Coincident | 3.727
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.887
|  |  |  | Coincident | 2.771
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.212
|  |  |  | Coincident | 3.304
| Wamberal 132_11kV | Substation Rating | MVA | Non-Coincident | 36.9
|  |  |  | Coincident | 34.4
|  | Raw Adjusted MD | MW | Non-Coincident | 12.91
|  |  |  | Coincident | 12.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.35
|  |  |  | Coincident | 13.83
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.4305
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.44
|  |  |  | Coincident | 12.62
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.04
|  |  |  | Coincident | 14.02
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.61
|  |  |  | Coincident | 11.12
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.13
|  |  |  | Coincident | 12.35
| Wamberal 66_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Waverley 132_11kV | Substation Rating | MVA | Non-Coincident | 65.01
|  |  |  | Coincident | 61.79
|  | Raw Adjusted MD | MW | Non-Coincident | 30.05
|  |  |  | Coincident | 23.15
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.09
|  |  |  | Coincident | 23.29
|  | Date MD occurred |  | Non-Coincident | 42548
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.1255
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.57
|  |  |  | Coincident | 23.24
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.61
|  |  |  | Coincident | 23.37
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.26
|  |  |  | Coincident | 21.53
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.3
|  |  |  | Coincident | 21.66
| West Gosford 132_11kV | Substation Rating | MVA | Non-Coincident | 65.01
|  |  |  | Coincident | 65.01
|  | Raw Adjusted MD | MW | Non-Coincident | 52.25
|  |  |  | Coincident | 51.43
|  | Raw Adjusted MD | MVA | Non-Coincident | 54.62
|  |  |  | Coincident | 53.77
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.483
|  |  |  | Coincident | -0.9088
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 56.32
|  |  |  | Coincident | 55.44
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 58.87
|  |  |  | Coincident | 57.95
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 50.7
|  |  |  | Coincident | 49.91
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 53
|  |  |  | Coincident | 52.17
| Williamtown 33_11kV | Substation Rating | MVA | Non-Coincident | 24.75
|  |  |  | Coincident | 24.75
|  | Raw Adjusted MD | MW | Non-Coincident | 5.077
|  |  |  | Coincident | 4.191
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.286
|  |  |  | Coincident | 4.363
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.64583
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.1833
|  |  |  | Coincident | -0.0793
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.37
|  |  |  | Coincident | 4.433
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.591
|  |  |  | Coincident | 4.615
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.771
|  |  |  | Coincident | 3.938
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.967
|  |  |  | Coincident | 4.1
| Woy Woy 66_11kV | Substation Rating | MVA | Non-Coincident | 30.75
|  |  |  | Coincident | 30.75
|  | Raw Adjusted MD | MW | Non-Coincident | 19.47
|  |  |  | Coincident | 18.61
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.37
|  |  |  | Coincident | 19.47
|  | Date MD occurred |  | Non-Coincident | 42777
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.2964
|  |  |  | Coincident | -0.4436
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.48
|  |  |  | Coincident | 19.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.42
|  |  |  | Coincident | 20.48
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.92
|  |  |  | Coincident | 17.13
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.74
|  |  |  | Coincident | 17.92
| Wyong 132_11kV | Substation Rating | MVA | Non-Coincident | 54.01
|  |  |  | Coincident | 54.01
|  | Raw Adjusted MD | MW | Non-Coincident | 37.76
|  |  |  | Coincident | 37.35
|  | Raw Adjusted MD | MVA | Non-Coincident | 39.67
|  |  |  | Coincident | 39.23
|  | Date MD occurred |  | Non-Coincident | 42766
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.88
|  |  |  | Coincident | -1.067
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 41.82
|  |  |  | Coincident | 41.36
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 43.93
|  |  |  | Coincident | 43.44
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 36.37
|  |  |  | Coincident | 35.97
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 38.2
|  |  |  | Coincident | 37.78
| Zetland 132_11kV | Substation Rating | MVA | Non-Coincident | 83.6
|  |  |  | Coincident | 83.6
|  | Raw Adjusted MD | MW | Non-Coincident | 65.34
|  |  |  | Coincident | 61.06
|  | Raw Adjusted MD | MVA | Non-Coincident | 66.66
|  |  |  | Coincident | 62.3
|  | Date MD occurred |  | Non-Coincident | 42759
|  |  |  | Coincident | 42776
|  | Half hour time period MD occurred |  | Non-Coincident | 0.47917
|  |  |  | Coincident | 0.6875
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.6263
|  |  |  | Coincident | -0.2523
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 71.34
|  |  |  | Coincident | 66.67
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 72.78
|  |  |  | Coincident | 68.02
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 64.59
|  |  |  | Coincident | 60.36
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 65.9
|  |  |  | Coincident | 61.59
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 6.3 Sustained interruptions
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2016-17
6.3 SUSTAINED INTERRUPTIONS TO SUPPLY
6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2016-17)
There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data.
Definitions:
Feeder classification definitions (column E) |  |  |  |  | Average duration of sustained customer interruption (column I) |  | Effect on unplanned SAIDI (column J) |  | Effect on unplanned SAIFI (column K)
CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km. Short rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km. Long rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km. |  |  |  |  | The average duration of an interruption experienced by an affected customer. |  | The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less). |  | The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
Date of event | Time of interruption | Asset ID | Feeder classification | Reason for interruption | Detailed reason for interruption | Number of customers affected by the interruption | Average duration of sustained customer interruption | Effect on unplanned SAIDI | Effect on unplanned SAIFI | MED
(DD/MM/YYYY) | (HH:MM) | (eg. feeder ID) | (drop down) | (select from options in drop-down box) | (select from options in column 'O' that correspond with reason in column 'F') |  | (minutes)
22/07/2016 | 00:27 | ZN1290:PA1 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 1,133 | 98 | 0.076874 | 0.078443 | N
22/07/2016 | 00:27 | ZN1290:PA10 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 37 | 95 | 0.0024336 | 0.0025617 | N
22/07/2016 | 00:27 | ZN1290:PA11 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 7 | 95 | 0.00046041 | 0.00048464 | N
22/07/2016 | 00:27 | ZN1290:PA12 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 1,052 | 95 | 0.069193 | 0.072835 | N
22/07/2016 | 00:27 | ZN1290:PA13 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 161 | 95 | 0.010589 | 0.011147 | N
22/07/2016 | 00:27 | ZN1290:PA16 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 26 | 95 | 0.0017101 | 0.0018001 | N
22/07/2016 | 00:27 | ZN1290:PA17 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 48 | 95 | 0.0031571 | 0.0033233 | N
22/07/2016 | 00:27 | ZN1290:PA2 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 644 | 98 | 0.043696 | 0.044587 | N
22/07/2016 | 00:27 | ZN1290:PA4 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 1,171 | 98 | 0.079453 | 0.081074 | N
22/07/2016 | 00:27 | ZN1290:PA8 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 10 | 98 | 0.0006785 | 0.00069235 | N
22/07/2016 | 00:27 | ZN1290:PA9 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 75 | 98 | 0.0050888 | 0.0051926 | N
22/08/2016 | 23:41 | ZN2466:PA27 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 2 | 434 | 0.00060222 | 0.00013876 | N
25/08/2016 | 08:29 | ZN180:PA10 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,371 | 10 | 0.0094728 | 0.094728 | N
25/08/2016 | 08:29 | ZN180:PA17 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 789 | 10 | 0.0054515 | 0.054515 | N
25/08/2016 | 08:29 | ZN180:PA18 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 2,352 | 10 | 0.016251 | 0.16251 | N
25/08/2016 | 08:29 | ZN180:PA20 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 984 | 10 | 0.0067989 | 0.067989 | N
25/08/2016 | 08:29 | ZN180:PA24 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,121 | 10 | 0.0077455 | 0.077455 | N
25/08/2016 | 08:29 | ZN180:PA27 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,219 | 9 | 0.0075803 | 0.084226 | N
25/08/2016 | 08:29 | ZN180:PA28 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,281 | 9 | 0.0079659 | 0.08851 | N
25/08/2016 | 08:29 | ZN180:PA32 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 934 | 9 | 0.0058081 | 0.064534 | N
25/08/2016 | 08:29 | ZN180:PA34 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,193 | 9 | 0.0074187 | 0.08243 | N
25/08/2016 | 08:29 | ZN180:PA35 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,428 | 9 | 0.00888 | 0.098667 | N
25/08/2016 | 08:29 | ZN180:PA41 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 2,145 | 9 | 0.013339 | 0.14821 | N
25/08/2016 | 08:29 | ZN3425:PA11 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 141 | 7 | 0.00068196 | 0.0097423 | N
25/08/2016 | 08:29 | ZN3425:PA12 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,228 | 7 | 0.0059393 | 0.084848 | N
25/08/2016 | 08:29 | ZN3425:PA15 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,339 | 7 | 0.0064762 | 0.092517 | N
25/08/2016 | 08:29 | ZN3425:PA16 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 849 | 7 | 0.0041063 | 0.058661 | N
25/08/2016 | 08:29 | ZN3425:PA21 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 57 | 7 | 0.00027569 | 0.0039384 | N
25/08/2016 | 08:29 | ZN3425:PA27 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 185 | 7 | 0.00089477 | 0.012782 | N
25/08/2016 | 08:29 | ZN3425:PA30 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,481 | 7 | 0.007163 | 0.10233 | N
25/08/2016 | 08:29 | ZN3425:PA32 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 178 | 7 | 0.00086092 | 0.012299 | N
25/08/2016 | 08:29 | ZN3425:PA34 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 571 | 7 | 0.0027617 | 0.039453 | N
25/08/2016 | 08:29 | ZN3425:PA36 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 5 | 7 | 2.4183e-05 | 0.00034547 | N
25/08/2016 | 08:29 | ZN3425:PA46 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 212 | 7 | 0.0010254 | 0.014648 | N
03/10/2016 | 17:10 | ZN35800:PA15 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 1 | 144 | 9.9284e-05 | 6.9059e-05 | N
20/10/2016 | 09:09 | ZN187:PA30 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 188 | 170 | 0.022055 | 0.012987 | N
25/11/2016 | 14:57 | 213:33775 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 1 | 8 | 5.2883e-06 | 6.8978e-05 | N
25/12/2016 | 22:56 | ZN10999:PA38 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 1 | 436 | 0.00030057 | 6.8909e-05 | N
23/03/2017 | 12:54 | ZN9700:PA23 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 147 | 33 | 0.0033403 | 0.010122 | N
16/05/2017 | 10:36 | 532:83293 | URBAN | 7 - Exclusion (STPIS 3.3(a)) |  | 290 | 135 | 0.026963 | 0.019933 | N
22/05/2017 | 06:27 | ZN1290:PA10 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 35 | 80 | 0.0019242 | 0.0024053 | N
22/05/2017 | 06:27 | ZN1290:PA11 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,177 | 80 | 0.064709 | 0.080887 | N
22/05/2017 | 06:27 | ZN1290:PA12 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,037 | 80 | 0.057012 | 0.071265 | N
22/05/2017 | 06:27 | ZN1290:PA13 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 158 | 80 | 0.0086865 | 0.010858 | N
22/05/2017 | 06:27 | ZN1290:PA16 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 22 | 80 | 0.0012095 | 0.0015119 | N
22/05/2017 | 06:27 | ZN1290:PA17 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 48 | 80 | 0.0026389 | 0.0032987 | N
22/05/2017 | 06:27 | ZN1290:PA8 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 781 | 73 | 0.039154 | 0.053672 | N
22/05/2017 | 06:27 | ZN1290:PA9 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,232 | 73 | 0.061764 | 0.084666 | N
03/06/2017 | 20:10 | ZN13000:PA1 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 703 | 9 | 0.004348 | 0.048311 | N
03/06/2017 | 20:10 | ZN13000:PA10 | SHORT RURAL | 6 - Exclusion (STPIS 3.3(a)) |  | 849 | 9 | 0.034201 | 0.38002 | N
03/06/2017 | 20:10 | ZN13000:PA11 | SHORT RURAL | 6 - Exclusion (STPIS 3.3(a)) |  | 1,600 | 9 | 0.064455 | 0.71617 | N
03/06/2017 | 20:10 | ZN13000:PA2 | SHORT RURAL | 6 - Exclusion (STPIS 3.3(a)) |  | 1,370 | 9 | 0.05519 | 0.61322 | N
03/06/2017 | 20:10 | ZN13000:PA4 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 230 | 9 | 0.0014225 | 0.015806 | N
03/06/2017 | 20:10 | ZN13000:PA5 | SHORT RURAL | 6 - Exclusion (STPIS 3.3(a)) |  | 1,635 | 9 | 0.065865 | 0.73183 | N
03/06/2017 | 20:10 | ZN13000:PA7 | SHORT RURAL | 6 - Exclusion (STPIS 3.3(a)) |  | 1,400 | 9 | 0.056398 | 0.62664 | N
03/06/2017 | 20:10 | ZN13000:PA8 | SHORT RURAL | 6 - Exclusion (STPIS 3.3(a)) |  | 142 | 9 | 0.0057204 | 0.06356 | N
16/06/2017 | 14:31 | ZN129:PA12 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,291 | 4 | 0.0035488 | 0.08872 | N
16/06/2017 | 14:31 | ZN129:PA3 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,576 | 4 | 0.0043322 | 0.10831 | N
16/06/2017 | 14:31 | ZN129:PA34 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 441 | 4 | 0.0012123 | 0.030306 | N
16/06/2017 | 14:31 | ZN129:PA35 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,288 | 4 | 0.0035405 | 0.088514 | N
16/06/2017 | 14:31 | ZN129:PA38 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,219 | 4 | 0.0033509 | 0.083772 | N
16/06/2017 | 14:31 | ZN129:PA39 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 956 | 4 | 0.0026279 | 0.065698 | N
16/06/2017 | 14:31 | ZN129:PA4 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 39 | 4 | 0.00010721 | 0.0026801 | N
16/06/2017 | 14:31 | ZN129:PA40 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 458 | 4 | 0.001259 | 0.031475 | N
16/06/2017 | 14:31 | ZN129:PA41 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,072 | 4 | 0.0029468 | 0.07367 | N
16/06/2017 | 14:31 | ZN129:PA43 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 106 | 4 | 0.00029138 | 0.0072845 | N
16/06/2017 | 14:31 | ZN129:PA46 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,482 | 4 | 0.0040738 | 0.10185 | N
16/06/2017 | 14:31 | ZN129:PA47 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 871 | 4 | 0.0023943 | 0.059857 | N
16/06/2017 | 14:31 | ZN129:PA49 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 66 | 4 | 0.00018143 | 0.0045356 | N
16/06/2017 | 14:31 | ZN129:PA51 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 208 | 4 | 0.00057176 | 0.014294 | N
16/06/2017 | 14:31 | ZN129:PA52 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 940 | 4 | 0.0025839 | 0.064598 | N
16/06/2017 | 14:31 | ZN2635:PA31 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,632 | 4 | 0.0044862 | 0.11215 | N
16/06/2017 | 14:31 | ZN2635:PA32 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 494 | 4 | 0.0013579 | 0.033949 | N
16/06/2017 | 14:31 | ZN2635:PA33 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 21 | 4 | 5.7726e-05 | 0.0014432 | N
16/06/2017 | 14:31 | ZN2635:PA35 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,540 | 4 | 0.0042333 | 0.10583 | N
16/06/2017 | 14:31 | ZN2635:PA38 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,017 | 4 | 0.0027956 | 0.06989 | N
16/06/2017 | 14:31 | ZN2635:PA39 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 595 | 4 | 0.0016356 | 0.040889 | N
16/06/2017 | 14:31 | ZN2635:PA40 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 499 | 4 | 0.0013717 | 0.034292 | N
16/06/2017 | 14:31 | ZN2635:PA41 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 419 | 4 | 0.0011518 | 0.028794 | N
16/06/2017 | 14:31 | ZN2635:PA43 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 949 | 4 | 0.0026087 | 0.065217 | N
16/06/2017 | 14:31 | ZN2635:PA44 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 997 | 4 | 0.0027406 | 0.068516 | N
16/06/2017 | 14:31 | ZN2635:PA46 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 497 | 4 | 0.0013662 | 0.034155 | N
16/06/2017 | 14:31 | ZN2635:PA47 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 18 | 4 | 4.948e-05 | 0.001237 | N
16/06/2017 | 14:31 | ZN2635:PA50 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 778 | 4 | 0.0021386 | 0.053465 | N
16/06/2017 | 14:31 | ZN2635:PA51 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 408 | 4 | 0.0011215 | 0.028038 | N
16/06/2017 | 14:31 | ZN2635:PA52 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,346 | 4 | 0.0037 | 0.092499 | N
16/06/2017 | 14:31 | ZN2635:PA53 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1 | 4 | 2.7489e-06 | 6.8722e-05 | N
16/06/2017 | 14:31 | ZN2635:PA55 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,185 | 4 | 0.0032574 | 0.081435 | N
16/06/2017 | 14:31 | ZN2635:PA57 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 1,277 | 4 | 0.0035103 | 0.087758 | N
16/06/2017 | 14:31 | ZN2635:PA58 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 2,216 | 4 | 0.0060915 | 0.15229 | N
16/06/2017 | 14:31 | ZN2635:PA59 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 145 | 4 | 0.00039859 | 0.0099646 | N
16/06/2017 | 14:31 | ZN2635:PA62 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 78 | 4 | 0.00021441 | 0.0053603 | N
16/06/2017 | 14:31 | ZN2635:PA64 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 244 | 4 | 0.00067072 | 0.016768 | N
16/06/2017 | 14:31 | ZN2635:PA65 | URBAN | 6 - Exclusion (STPIS 3.3(a)) |  | 6 | 4 | 1.6493e-05 | 0.00041233 | N
01/07/2016 | 08:00 | 223:14393 | URBAN | Planned |  | 532 | 350 | 0.12896 | 0.036845 | N
03/07/2016 | 08:30 | 214:8671 | URBAN | Planned |  | 28 | 430 | 0.0083389 | 0.0019393 | N
03/07/2016 | 07:40 | 202:34254 | URBAN | Planned |  | 284 | 465 | 0.091464 | 0.01967 | N
01/07/2016 | 08:25 | 229:34995 | SHORT RURAL | Planned |  | 1 | 80 | 0.00036421 | 0.00045526 | N
01/07/2016 | 08:50 | 524:33576 | SHORT RURAL | Planned |  | 17 | 145 | 0.011222 | 0.0077394 | N
01/07/2016 | 09:00 | 504:48031 | SHORT RURAL | Planned |  | 7 | 165 | 0.0052582 | 0.0031868 | N
01/07/2016 | 09:00 | 264:81240 | SHORT RURAL | Planned |  | 6 | 210 | 0.0057363 | 0.0027316 | N
01/07/2016 | 11:30 | 229:34995 | SHORT RURAL | Planned |  | 19 | 85 | 0.0073524 | 0.0086499 | N
01/07/2016 | 08:30 | 524:33576 | SHORT RURAL | Planned |  | 31 | 390 | 0.055041 | 0.014113 | N
01/07/2016 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 7 | 115 | 0.0036648 | 0.0031868 | N
04/07/2016 | 08:00 | 227:13020 | SHORT RURAL | Planned |  | 91 | 340 | 0.14086 | 0.041429 | N
04/07/2016 | 09:00 | 243:80081 | SHORT RURAL | Planned |  | 116 | 415 | 0.21916 | 0.052811 | N
04/07/2016 | 08:53 | 235:2120 | SHORT RURAL | Planned |  | 17 | 397 | 0.030726 | 0.0077395 | N
05/07/2016 | 03:55 | 532:83306 | URBAN | Planned |  | 7 | 335 | 0.0016241 | 0.0004848 | N
04/07/2016 | 07:50 | 514:18146 | SHORT RURAL | Planned |  | 4 | 475 | 0.00865 | 0.0018211 | N
04/07/2016 | 09:25 | 515:35197 | LONG RURAL | Planned |  | 5 | 155 | 0.27639 | 0.17832 | N
05/07/2016 | 09:12 | 526:34637 | SHORT RURAL | Planned |  | 13 | 423 | 0.025038 | 0.0059192 | N
05/07/2016 | 08:30 | 213:33777 | SHORT RURAL | Planned |  | 2 | 170 | 0.0015481 | 0.00091064 | N
05/07/2016 | 09:30 | 258:80778 | URBAN | Planned |  | 1 | 285 | 0.00019738 | 6.9258e-05 | N
05/07/2016 | 09:20 | 509:33395 | LONG RURAL | Planned |  | 4 | 130 | 0.18545 | 0.14265 | N
05/07/2016 | 09:30 | 238:34140 | URBAN | Planned |  | 101 | 540 | 0.037773 | 0.006995 | N
05/07/2016 | 11:00 | 229:34992 | SHORT RURAL | Planned |  | 2 | 250 | 0.0022766 | 0.00091064 | N
05/07/2016 | 08:40 | 515:35192 | SHORT RURAL | Planned |  | 23 | 340 | 0.035606 | 0.010472 | N
06/07/2016 | 10:15 | 264:81236 | SHORT RURAL | Planned |  | 88 | 285 | 0.1142 | 0.040069 | N
06/07/2016 | 10:00 | 238:34148 | SHORT RURAL | Planned |  | 24 | 265 | 0.028959 | 0.010928 | N
06/07/2016 | 08:05 | 243:80083 | SHORT RURAL | Planned |  | 30 | 265 | 0.036198 | 0.01366 | N
06/07/2016 | 08:30 | 243:80084 | SHORT RURAL | Planned |  | 121 | 480 | 0.26445 | 0.055094 | N
06/07/2016 | 08:00 | 214:8667 | URBAN | Planned |  | 101 | 518 | 0.036235 | 0.0069952 | N
06/07/2016 | 09:30 | 223:14395 | SHORT RURAL | Planned |  | 51 | 330 | 0.076631 | 0.023222 | N
06/07/2016 | 08:00 | 526:34639 | SHORT RURAL | Planned |  | 4 | 350 | 0.0063746 | 0.0018213 | N
06/07/2016 | 09:00 | 264:81240 | SHORT RURAL | Planned |  | 5 | 285 | 0.0064884 | 0.0022766 | N
06/07/2016 | 09:45 | 230:81432 | SHORT RURAL | Planned |  | 2 | 210 | 0.0019124 | 0.00091065 | N
06/07/2016 | 11:45 | 265:81651 | SHORT RURAL | Planned |  | 20 | 175 | 0.015936 | 0.0091065 | N
06/07/2016 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 3 | 315 | 0.0043028 | 0.001366 | N
06/07/2016 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 2 | 110 | 0.0010017 | 0.00091065 | N
08/07/2016 | 09:20 | 256:80650 | URBAN | Planned |  | 24 | 210 | 0.00349 | 0.0016619 | N
08/07/2016 | 08:15 | 243:80083 | SHORT RURAL | Planned |  | 13 | 370 | 0.021898 | 0.0059183 | N
10/07/2016 | 08:05 | 213:33775 | URBAN | Planned |  | 223 | 680 | 0.10501 | 0.015443 | N
07/07/2016 | 08:00 | 239:82127 | SHORT RURAL | Planned |  | 7 | 506 | 0.016125 | 0.0031867 | N
07/07/2016 | 09:00 | 264:81236 | SHORT RURAL | Planned |  | 130 | 375 | 0.22193 | 0.059182 | N
07/07/2016 | 10:00 | 229:34983 | SHORT RURAL | Planned |  | 31 | 275 | 0.03881 | 0.014113 | N
07/07/2016 | 09:15 | 238:34141 | SHORT RURAL | Planned |  | 15 | 255 | 0.017413 | 0.0068287 | N
08/07/2016 | 08:35 | 235:2120 | SHORT RURAL | Planned |  | 14 | 300 | 0.019121 | 0.0063735 | N
10/07/2016 | 08:00 | 515:35200 | URBAN | Planned |  | 17 | 270 | 0.0031786 | 0.0011773 | N
08/07/2016 | 08:22 | 227:13015 | SHORT RURAL | Planned |  | 60 | 408 | 0.11145 | 0.027315 | N
10/07/2016 | 07:50 | 224:80329 | SHORT RURAL | Planned |  | 2 | 405 | 0.0036874 | 0.00091048 | N
07/07/2016 | 08:25 | 504:48031 | SHORT RURAL | Planned |  | 1 | 130 | 0.00059182 | 0.00045525 | N
07/07/2016 | 08:35 | 507:80917 | URBAN | Planned |  | 88 | 145 | 0.0088357 | 0.0060936 | N
07/07/2016 | 10:00 | 230:81432 | SHORT RURAL | Planned |  | 56 | 220 | 0.056087 | 0.025494 | N
07/07/2016 | 08:35 | 508:82580 | SHORT RURAL | Planned |  | 7 | 205 | 0.0065328 | 0.0031867 | N
08/07/2016 | 08:45 | 508:82578 | SHORT RURAL | Planned |  | 4 | 195 | 0.003551 | 0.001821 | N
07/07/2016 | 08:40 | 513:48059 | SHORT RURAL | Planned |  | 5 | 145 | 0.0033006 | 0.0022762 | N
11/07/2016 | 08:30 | 512:48048 | SHORT RURAL | Planned |  | 34 | 390 | 0.060365 | 0.015478 | N
11/07/2016 | 08:30 | 235:2120 | SHORT RURAL | Planned |  | 17 | 305 | 0.023604 | 0.0077391 | N
11/07/2016 | 08:10 | 243:80083 | SHORT RURAL | Planned |  | 30 | 375 | 0.051214 | 0.013657 | N
11/07/2016 | 12:15 | 216:10723 | URBAN | Planned |  | 1 | 125 | 8.6563e-05 | 6.925e-05 | N
11/07/2016 | 08:00 | 532:83314 | URBAN | Planned |  | 148 | 390 | 0.039971 | 0.010249 | N
11/07/2016 | 10:00 | 508:82580 | SHORT RURAL | Planned |  | 2 | 45 | 0.00040971 | 0.00091048 | N
11/07/2016 | 08:00 | 814:82291 | SHORT RURAL | Planned |  | 5 | 156 | 0.0035509 | 0.0022762 | N
11/07/2016 | 08:50 | 512:48046 | SHORT RURAL | Planned |  | 6 | 235 | 0.0064189 | 0.0027314 | N
12/07/2016 | 09:03 | 232:33407 | SHORT RURAL | Planned |  | 49 | 327 | 0.072945 | 0.022307 | N
12/07/2016 | 08:30 | 213:33773 | URBAN | Planned |  | 19 | 540 | 0.0071053 | 0.0013158 | N
12/07/2016 | 08:30 | 224:80329 | SHORT RURAL | Planned |  | 74 | 420 | 0.14149 | 0.033688 | N
12/07/2016 | 08:37 | 264:81244 | SHORT RURAL | Planned |  | 78 | 143 | 0.050778 | 0.035509 | N
12/07/2016 | 08:30 | 524:33572 | SHORT RURAL | Planned |  | 1 | 80 | 0.0003642 | 0.00045525 | N
12/07/2016 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 240 | 0.17118 | 0.071327 | N
12/07/2016 | 07:40 | 524:33580 | SHORT RURAL | Planned |  | 49 | 515 | 0.11488 | 0.022307 | N
12/07/2016 | 09:50 | 532:83293 | URBAN | Planned |  | 67 | 145 | 0.0067279 | 0.0046399 | N
12/07/2016 | 10:40 | 507:80922 | SHORT RURAL | Planned |  | 9 | 260 | 0.010653 | 0.0040972 | N
12/07/2016 | 12:35 | 524:33576 | SHORT RURAL | Planned |  | 1 | 75 | 0.00034144 | 0.00045525 | N
12/07/2016 | 12:55 | 511:29876 | SHORT RURAL | Planned |  | 14 | 105 | 0.0066922 | 0.0063735 | N
12/07/2016 | 08:05 | 814:82291 | SHORT RURAL | Planned |  | 1 | 355 | 0.0016161 | 0.00045525 | N
12/07/2016 | 08:30 | 516:48066 | SHORT RURAL | Planned |  | 2 | 100 | 0.0009105 | 0.0009105 | N
12/07/2016 | 08:10 | 814:82291 | SHORT RURAL | Planned |  | 4 | 65 | 0.0011836 | 0.001821 | N
12/07/2016 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 3 | 180 | 0.19258 | 0.10699 | N
13/07/2016 | 11:24 | ZN12570:PA22 | SHORT RURAL | Planned |  | 1 | 252 | 0.0011457 | 0.00045526 | N
12/07/2016 | 10:00 | 814:82291 | SHORT RURAL | Planned |  | 6 | 105 | 0.0028681 | 0.0027315 | N
12/07/2016 | 08:40 | 526:34640 | SHORT RURAL | Planned |  | 17 | 250 | 0.019348 | 0.0077392 | N
12/07/2016 | 13:00 | 523:33501 | SHORT RURAL | Planned |  | 3 | 60 | 0.00081945 | 0.0013657 | N
12/07/2016 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 25 | 375 | 0.04268 | 0.011381 | N
13/07/2016 | 09:30 | 224:80329 | SHORT RURAL | Planned |  | 155 | 210 | 0.14819 | 0.070565 | N
13/07/2016 | 09:15 | 523:33501 | SHORT RURAL | Planned |  | 26 | 185 | 0.021898 | 0.011837 | N
13/07/2016 | 08:00 | 528:83014 | SHORT RURAL | Planned |  | 37 | 160 | 0.026951 | 0.016845 | N
13/07/2016 | 08:00 | 507:80925 | SHORT RURAL | Planned |  | 19 | 360 | 0.03114 | 0.0086499 | N
13/07/2016 | 09:40 | 229:34995 | SHORT RURAL | Planned |  | 2 | 115 | 0.0010471 | 0.00091051 | N
13/07/2016 | 08:40 | 507:80925 | SHORT RURAL | Planned |  | 31 | 85 | 0.011996 | 0.014113 | N
13/07/2016 | 08:30 | 235:2120 | SHORT RURAL | Planned |  | 4 | 315 | 0.0057362 | 0.001821 | N
13/07/2016 | 09:00 | 235:2124 | SHORT RURAL | Planned |  | 10 | 420 | 0.019121 | 0.0045526 | N
13/07/2016 | 08:15 | 228:7490 | SHORT RURAL | Planned |  | 57 | 425 | 0.11029 | 0.02595 | N
13/07/2016 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 10 | 50 | 0.0022763 | 0.0045526 | N
13/07/2016 | 09:25 | 810:74050 | SHORT RURAL | Planned |  | 4 | 170 | 0.0030957 | 0.001821 | N
14/07/2016 | 12:35 | 511:29877 | SHORT RURAL | Planned |  | 1 | 90 | 0.00040973 | 0.00045526 | N
14/07/2016 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 96 | 390 | 13.3571 | 3.4249 | N
14/07/2016 | 08:30 | 216:10728 | SHORT RURAL | Planned |  | 120 | 510 | 0.27862 | 0.054631 | N
14/07/2016 | 10:17 | 243:80080 | SHORT RURAL | Planned |  | 33 | 85 | 0.01277 | 0.015024 | N
14/07/2016 | 17:00 | 216:10728 | SHORT RURAL | Planned |  | 2 | 215 | 0.0019576 | 0.00091052 | N
14/07/2016 | 09:00 | 232:11455 | SHORT RURAL | Planned |  | 144 | 145 | 0.095058 | 0.065557 | N
14/07/2016 | 08:30 | 508:82578 | SHORT RURAL | Planned |  | 30 | 360 | 0.049168 | 0.013658 | N
14/07/2016 | 08:35 | 264:81241 | SHORT RURAL | Planned |  | 4 | 160 | 0.0029137 | 0.001821 | N
14/07/2016 | 08:30 | 511:29877 | SHORT RURAL | Planned |  | 2 | 145 | 0.0013203 | 0.00091052 | N
14/07/2016 | 08:32 | 502:48010 | SHORT RURAL | Planned |  | 98 | 613 | 0.27349 | 0.044615 | N
14/07/2016 | 08:30 | 807:74179 | SHORT RURAL | Planned |  | 24 | 195 | 0.021306 | 0.010926 | N
14/07/2016 | 08:45 | 523:33501 | SHORT RURAL | Planned |  | 1 | 65 | 0.00029592 | 0.00045526 | N
15/07/2016 | 08:30 | 513:48050 | SHORT RURAL | Planned |  | 5 | 247 | 0.0056225 | 0.0022763 | N
15/07/2016 | 08:30 | 224:80340 | SHORT RURAL | Planned |  | 12 | 347 | 0.018957 | 0.0054632 | N
15/07/2016 | 08:30 | 216:10728 | SHORT RURAL | Planned |  | 43 | 390 | 0.076348 | 0.019576 | N
15/07/2016 | 09:45 | 507:80922 | SHORT RURAL | Planned |  | 2 | 155 | 0.0014113 | 0.00091053 | N
15/07/2016 | 09:50 | 528:83014 | SHORT RURAL | Planned |  | 83 | 60 | 0.022672 | 0.037787 | N
15/07/2016 | 08:15 | 509:33395 | LONG RURAL | Planned |  | 43 | 274 | 4.2034 | 1.5341 | N
17/07/2016 | 21:05 | 524:33578 | URBAN | Planned |  | 7 | 475 | 0.0023023 | 0.0004847 | N
15/07/2016 | 08:00 | 813:89062 | SHORT RURAL | Planned |  | 21 | 355 | 0.03394 | 0.0095605 | N
15/07/2016 | 09:00 | 814:82283 | SHORT RURAL | Planned |  | 5 | 195 | 0.0044388 | 0.0022763 | N
18/07/2016 | 09:00 | 222:33602 | URBAN | Planned |  | 13 | 50 | 0.00045008 | 0.00090015 | N
18/07/2016 | 08:45 | 243:80083 | SHORT RURAL | Planned |  | 5 | 315 | 0.0071517 | 0.0022704 | N
18/07/2016 | 08:00 | 507:80922 | SHORT RURAL | Planned |  | 55 | 510 | 0.12737 | 0.024974 | N
18/07/2016 | 08:45 | 509:33395 | LONG RURAL | Planned |  | 1 | 155 | 0.055298 | 0.035676 | N
18/07/2016 | 10:10 | 813:89055 | SHORT RURAL | Planned |  | 2 | 295 | 0.002679 | 0.00090815 | N
19/07/2016 | 09:43 | ZN14891:PA5 | SHORT RURAL | Planned |  | 2 | 406 | 0.0036873 | 0.00090866 | N
19/07/2016 | 21:53 | ZN35800:PA21 | URBAN | Planned |  | 252 | 81 | 0.014204 | 0.01745 | N
19/07/2016 | 08:45 | 512:48049 | SHORT RURAL | Planned |  | 8 | 210 | 0.0076327 | 0.0036346 | N
19/07/2016 | 10:40 | 524:33580 | SHORT RURAL | Planned |  | 26 | 240 | 0.02835 | 0.011813 | N
19/07/2016 | 08:00 | 227:13015 | SHORT RURAL | Planned |  | 159 | 500 | 0.36119 | 0.072238 | N
19/07/2016 | 08:30 | 264:81236 | SHORT RURAL | Planned |  | 176 | 125 | 0.099952 | 0.079962 | N
19/07/2016 | 09:00 | 265:81651 | SHORT RURAL | Planned |  | 14 | 330 | 0.02099 | 0.0063606 | N
19/07/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 25 | 170 | 0.019309 | 0.011358 | N
21/07/2016 | 09:15 | 223:14397 | URBAN | Planned |  | 56 | 270 | 0.010467 | 0.0038768 | N
20/07/2016 | 09:30 | 242:81539 | URBAN | Planned |  | 135 | 80 | 0.0074765 | 0.0093456 | N
21/07/2016 | 08:45 | 509:33395 | LONG RURAL | Planned |  | 36 | 390 | 5.0071 | 1.2839 | N
21/07/2016 | 08:10 | 232:11454 | SHORT RURAL | Planned |  | 361 | 485 | 0.79484 | 0.16389 | N
21/07/2016 | 09:20 | 511:29878 | SHORT RURAL | Planned |  | 2 | 110 | 0.00099875 | 0.00090795 | N
21/07/2016 | 08:30 | 528:83014 | SHORT RURAL | Planned |  | 10 | 240 | 0.010895 | 0.0045398 | N
22/07/2016 | 08:20 | 242:81538 | URBAN | Planned |  | 129 | 280 | 0.025008 | 0.0089313 | N
22/07/2016 | 07:45 | 511:29878 | SHORT RURAL | Planned |  | 18 | 365 | 0.029825 | 0.0081712 | N
22/07/2016 | 10:20 | 232:33407 | SHORT RURAL | Planned |  | 3 | 315 | 0.0042899 | 0.0013619 | N
21/07/2016 | 08:30 | 512:48046 | SHORT RURAL | Planned |  | 10 | 185 | 0.0083986 | 0.0045398 | N
21/07/2016 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 1 | 645 | 0.0029281 | 0.00045398 | N
21/07/2016 | 08:30 | 807:74179 | SHORT RURAL | Planned |  | 6 | 360 | 0.0098059 | 0.0027239 | N
21/07/2016 | 10:10 | 811:74234 | SHORT RURAL | Planned |  | 29 | 390 | 0.051345 | 0.013165 | N
22/07/2016 | 08:50 | 512:48046 | SHORT RURAL | Planned |  | 1 | 205 | 0.0009306 | 0.00045395 | N
22/07/2016 | 08:45 | 523:33508 | SHORT RURAL | Planned |  | 2 | 400 | 0.0036316 | 0.00090791 | N
22/07/2016 | 08:40 | 514:18137 | SHORT RURAL | Planned |  | 1 | 170 | 0.00077172 | 0.00045395 | N
25/07/2016 | 09:30 | 229:34995 | SHORT RURAL | Planned |  | 14 | 245 | 0.015569 | 0.0063547 | N
25/07/2016 | 08:00 | 528:83019 | SHORT RURAL | Planned |  | 183 | 340 | 0.28242 | 0.083065 | N
25/07/2016 | 08:30 | 205:12205 | SHORT RURAL | Planned |  | 59 | 410 | 0.1098 | 0.026781 | N
25/07/2016 | 08:30 | 524:33578 | URBAN | Planned |  | 87 | 45 | 0.0027105 | 0.0060234 | N
25/07/2016 | 08:15 | 264:81244 | SHORT RURAL | Planned |  | 1 | 405 | 0.0018383 | 0.00045391 | N
25/07/2016 | 09:00 | 515:35192 | SHORT RURAL | Planned |  | 2 | 150 | 0.0013617 | 0.00090782 | N
25/07/2016 | 09:45 | 806:82667 | SHORT RURAL | Planned |  | 8 | 160 | 0.00581 | 0.0036313 | N
25/07/2016 | 11:45 | 515:35197 | LONG RURAL | Planned |  | 1 | 45 | 0.016054 | 0.035676 | N
26/07/2016 | 08:53 | 261:81865 | URBAN | Planned |  | 25 | 427 | 0.0073908 | 0.0017309 | N
26/07/2016 | 09:50 | 239:82129 | SHORT RURAL | Planned |  | 145 | 267 | 0.17573 | 0.065817 | N
26/07/2016 | 08:40 | 206:34434 | URBAN | Planned |  | 39 | 315 | 0.0085055 | 0.0027002 | N
26/07/2016 | 08:00 | 508:82578 | SHORT RURAL | Planned |  | 30 | 430 | 0.058554 | 0.013617 | N
26/07/2016 | 08:00 | 502:48010 | SHORT RURAL | Planned |  | 63 | 450 | 0.12868 | 0.028596 | N
26/07/2016 | 09:00 | 264:81236 | SHORT RURAL | Planned |  | 28 | 270 | 0.034315 | 0.012709 | N
26/07/2016 | 08:55 | 232:33409 | SHORT RURAL | Planned |  | 25 | 85 | 0.0096455 | 0.011348 | N
26/07/2016 | 07:35 | 524:33580 | SHORT RURAL | Planned |  | 22 | 445 | 0.044438 | 0.009986 | N
26/07/2016 | 13:00 | 232:33409 | SHORT RURAL | Planned |  | 99 | 65 | 0.029209 | 0.044937 | N
26/07/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 1 | 105 | 0.0004766 | 0.00045391 | N
26/07/2016 | 08:35 | 515:35192 | SHORT RURAL | Planned |  | 10 | 205 | 0.0093051 | 0.0045391 | N
26/07/2016 | 08:48 | 810:74062 | SHORT RURAL | Planned |  | 52 | 372 | 0.087804 | 0.023603 | N
26/07/2016 | 13:00 | 513:48056 | SHORT RURAL | Planned |  | 1 | 35 | 0.00015887 | 0.00045391 | N
27/07/2016 | 09:40 | 232:33407 | SHORT RURAL | Planned |  | 37 | 180 | 0.030232 | 0.016795 | N
27/07/2016 | 08:40 | 227:13015 | SHORT RURAL | Planned |  | 3 | 435 | 0.0059237 | 0.0013618 | N
27/07/2016 | 08:15 | 213:33774 | URBAN | Planned |  | 186 | 205 | 0.0264 | 0.012878 | N
27/07/2016 | 08:30 | 232:33407 | SHORT RURAL | Planned |  | 2 | 345 | 0.0031321 | 0.00090785 | N
27/07/2016 | 08:00 | 812:19066 | SHORT RURAL | Planned |  | 9 | 150 | 0.006128 | 0.0040853 | N
27/07/2016 | 08:55 | 810:74058 | SHORT RURAL | Planned |  | 1 | 95 | 0.00043123 | 0.00045393 | N
27/07/2016 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 26 | 260 | 2.4117 | 0.92758 | N
27/07/2016 | 09:40 | 813:89061 | LONG RURAL | Planned |  | 6 | 290 | 0.62076 | 0.21406 | N
27/07/2016 | 12:35 | 812:19066 | SHORT RURAL | Planned |  | 3 | 115 | 0.001566 | 0.0013618 | N
01/07/2016 | 07:30 | ZN8100:PA20 | URBAN | Planned |  | 1 | 420 | 0.00029088 | 6.9257e-05 | N
01/07/2016 | 07:30 | ZN2635:PA39 | URBAN | Planned |  | 106 | 354 | 0.025988 | 0.0073413 | N
02/07/2016 | 06:30 | ZN35800:PA18 | URBAN | Planned |  | 47 | 660 | 0.021484 | 0.0032552 | N
02/07/2016 | 07:30 | ZN2473:PA9 | URBAN | Planned |  | 16 | 480 | 0.0053191 | 0.0011081 | N
02/07/2016 | 08:20 | ZN8100:PA4 | URBAN | Planned |  | 14 | 520 | 0.0050421 | 0.00096963 | N
03/07/2016 | 07:30 | ZN167:PA2 | URBAN | Planned |  | 7 | 495 | 0.0023998 | 0.00048482 | N
03/07/2016 | 07:35 | ZN12690:PA22 | URBAN | Planned |  | 13 | 475 | 0.0042768 | 0.00090038 | N
03/07/2016 | 07:35 | ZN12690:PA22 | URBAN | Planned |  | 19 | 475 | 0.0062507 | 0.0013159 | N
03/07/2016 | 07:30 | ZN901:PA18 | URBAN | Planned |  | 31 | 510 | 0.01095 | 0.002147 | N
03/07/2016 | 08:00 | ZN3288:PA41 42KLM | CBD | Planned |  | 11 | 330 | 0.11692 | 0.035431 | N
04/07/2016 | 07:30 | ZN847:PA21 | URBAN | Planned |  | 36 | 480 | 0.011968 | 0.0024933 | N
04/07/2016 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 14 | 480 | 0.030594 | 0.0063737 | N
04/07/2016 | 08:00 | ZN1290:PA12 | URBAN | Planned |  | 265 | 300 | 0.055061 | 0.018354 | N
04/07/2016 | 19:30 | ZN80:PA37 | URBAN | Planned |  | 49 | 620 | 0.021041 | 0.0033937 | N
05/07/2016 | 08:00 | ZN1610:PA26 | URBAN | Planned |  | 2 | 1,770 | 0.0024517 | 0.00013852 | N
05/07/2016 | 07:30 | ZN847:PA10 | URBAN | Planned |  | 1 | 1,890 | 0.001309 | 6.9258e-05 | N
06/07/2016 | 07:30 | ZN35370:PA4 | SHORT RURAL | Planned |  | 6 | 420 | 0.011474 | 0.002732 | N
06/07/2016 | 08:00 | ZN12630:PA21 | SHORT RURAL | Planned |  | 1 | 460 | 0.0020945 | 0.00045533 | N
07/07/2016 | 04:40 | ZN12640:PA19 | URBAN | Planned |  | 123 | 110 | 0.0093689 | 0.0085172 | N
07/07/2016 | 04:40 | ZN12640:PA19 | URBAN | Planned |  | 114 | 110 | 0.0086833 | 0.0078939 | N
07/07/2016 | 07:30 | ZN398:PA25 | URBAN | Planned |  | 3 | 540 | 0.0011218 | 0.00020774 | N
07/07/2016 | 08:00 | ZN3154:PA19 | URBAN | Planned |  | 27 | 420 | 0.0078524 | 0.0018696 | N
07/07/2016 | 08:30 | ZN12640:PA1 | SHORT RURAL | Planned |  | 1 | 6,155 | 0.028021 | 0.00045525 | N
08/07/2016 | 07:30 | ZN10990:PA12 | URBAN | Planned |  | 30 | 540 | 0.011218 | 0.0020774 | N
08/07/2016 | 09:00 | ZN12600:PA1 | SHORT RURAL | Planned |  | 44 | 390 | 0.078121 | 0.020031 | N
08/07/2016 | 11:25 | ZN12630:PA23 | SHORT RURAL | Planned |  | 14 | 165 | 0.010516 | 0.0063735 | N
08/07/2016 | 20:30 | ZN10996:PA9 | URBAN | Planned |  | 23 | 540 | 0.0086004 | 0.0015927 | N
08/07/2016 | 22:00 | ZN3425:PA7 | URBAN | Planned |  | 38 | 60 | 0.0015788 | 0.0026314 | N
09/07/2016 | 05:30 | ZN3425:PA7 | URBAN | Planned |  | 38 | 30 | 0.00078945 | 0.0026315 | N
09/07/2016 | 07:00 | ZN188:PA20 | URBAN | Planned |  | 7 | 450 | 0.0021814 | 0.00048475 | N
09/07/2016 | 07:50 | ZN5868:PA10 | URBAN | Planned |  | 16 | 620 | 0.0068696 | 0.001108 | N
09/07/2016 | 08:30 | ZN12600:PA2 | SHORT RURAL | Planned |  | 8 | 420 | 0.015296 | 0.0036419 | N
09/07/2016 | 09:30 | ZN8700:PA61 62ABC | CBD | Planned |  | 1 | 1,860 | 0.059905 | 0.0032207 | N
09/07/2016 | 22:30 | ZN3288:PA45 46ABC | CBD | Planned |  | 10 | 420 | 0.13527 | 0.032207 | N
11/07/2016 | 08:50 | ZN1788:PA16 | URBAN | Planned |  | 1 | 335 | 0.00023199 | 6.925e-05 | N
11/07/2016 | 08:10 | ZN12630:PA21 | SHORT RURAL | Planned |  | 104 | 425 | 0.20122 | 0.047345 | N
11/07/2016 | 10:10 | ZN9118:PA6 | URBAN | Planned |  | 104 | 385 | 0.027728 | 0.007202 | N
11/07/2016 | 19:00 | ZN262:PA15 | URBAN | Planned |  | 17 | 780 | 0.0091826 | 0.0011773 | N
12/07/2016 | 08:00 | ZN9900:PA1 | URBAN | Planned |  | 2 | 420 | 0.00058172 | 0.0001385 | N
12/07/2016 | 07:30 | ZN3922:PA2 | URBAN | Planned |  | 37 | 540 | 0.013837 | 0.0025623 | N
12/07/2016 | 07:30 | ZN129:PA5 | URBAN | Planned |  | 44 | 480 | 0.014626 | 0.0030471 | N
12/07/2016 | 08:00 | ZN35400:PA82 | URBAN | Planned |  | 43 | 540 | 0.01608 | 0.0029779 | N
13/07/2016 | 07:20 | ZN1287:PA5 | URBAN | Planned |  | 1 | 520 | 0.00036012 | 6.9254e-05 | N
13/07/2016 | 07:00 | ZN711:PA22 | URBAN | Planned |  | 1 | 510 | 0.0003532 | 6.9254e-05 | N
13/07/2016 | 07:45 | ZN847:PA21 | URBAN | Planned |  | 124 | 480 | 0.04122 | 0.0085875 | N
13/07/2016 | 08:00 | ZN12630:PA24 | SHORT RURAL | Planned |  | 14 | 550 | 0.035055 | 0.0063736 | N
13/07/2016 | 13:30 | ZN711:PA22 | URBAN | Planned |  | 34 | 120 | 0.0028256 | 0.0023546 | N
14/07/2016 | 07:00 | ZN711:PA22 | URBAN | Planned |  | 44 | 450 | 0.013712 | 0.0030472 | N
14/07/2016 | 08:30 | ZN2835:PA15 | URBAN | Planned |  | 48 | 405 | 0.013463 | 0.0033242 | N
14/07/2016 | 07:30 | ZN180:PA23 | URBAN | Planned |  | 111 | 600 | 0.046124 | 0.0076873 | N
14/07/2016 | 08:00 | ZN12690:PA19 | URBAN | Planned |  | 34 | 480 | 0.011302 | 0.0023547 | N
14/07/2016 | 09:05 | ZN12580:PA14 | URBAN | Planned |  | 52 | 415 | 0.014945 | 0.0036013 | N
14/07/2016 | 08:00 | ZN12600:PA11 | URBAN | Planned |  | 30 | 480 | 0.0099727 | 0.0020776 | N
14/07/2016 | 08:00 | ZN36100:PA27 | URBAN | Planned |  | 132 | 300 | 0.027425 | 0.0091416 | N
15/07/2016 | 09:30 | ZN9534:PA17 | URBAN | Planned |  | 1 | 375 | 0.00025971 | 6.9256e-05 | N
15/07/2016 | 22:00 | ZN3425:PA15 | URBAN | Planned |  | 113 | 300 | 0.023478 | 0.0078259 | N
16/07/2016 | 06:40 | ZN35800:PA3 | URBAN | Planned |  | 2 | 503 | 0.00069658 | 0.00013849 | N
16/07/2016 | 07:00 | ZN14143:PA14 | URBAN | Planned |  | 1 | 350 | 0.00024235 | 6.9243e-05 | N
17/07/2016 | 07:00 | ZN1648:PA10 | URBAN | Planned |  | 1 | 490 | 0.00033929 | 6.9243e-05 | N
17/07/2016 | 07:15 | ZN72:PA25 | URBAN | Planned |  | 29 | 425 | 0.0085341 | 0.002008 | N
17/07/2016 | 07:30 | ZN10996:PA9 | URBAN | Planned |  | 23 | 395 | 0.0062907 | 0.0015926 | N
18/07/2016 | 07:30 | ZN262:PA19 | URBAN | Planned |  | 91 | 480 | 0.030245 | 0.0063011 | N
18/07/2016 | 07:30 | ZN4545:PA27 | URBAN | Planned |  | 85 | 450 | 0.026485 | 0.0058856 | N
18/07/2016 | 08:00 | ZN12570:PA34 | SHORT RURAL | Planned |  | 53 | 420 | 0.10108 | 0.024066 | N
18/07/2016 | 09:15 | ZN180:PA33 | URBAN | Planned |  | 18 | 195 | 0.0024304 | 0.0012464 | N
18/07/2016 | 08:30 | ZN9245:PA43 | URBAN | Planned |  | 44 | 360 | 0.010968 | 0.0030467 | N
18/07/2016 | 10:00 | ZN10999:PA29 | URBAN | Planned |  | 47 | 300 | 0.0097632 | 0.0032544 | N
20/07/2016 | 07:00 | ZN874:PA4 | URBAN | Planned |  | 13 | 439 | 0.0039508 | 0.00089995 | N
20/07/2016 | 09:05 | ZN12630:PA22 | SHORT RURAL | Planned |  | 7 | 415 | 0.013188 | 0.0031778 | N
19/07/2016 | 08:15 | ZN2835:PA23 | URBAN | Planned |  | 53 | 365 | 0.013395 | 0.0036699 | N
19/07/2016 | 07:35 | ZN15014:PA5 | URBAN | Planned |  | 95 | 600 | 0.039469 | 0.0065782 | N
19/07/2016 | 09:05 | ZN9900:PA19 | URBAN | Planned |  | 42 | 105 | 0.0030537 | 0.0029083 | N
19/07/2016 | 08:40 | ZN14891:PA5 | SHORT RURAL | Planned |  | 14 | 440 | 0.027987 | 0.0063606 | N
19/07/2016 | 10:00 | ZN188:PA10 | URBAN | Planned |  | 202 | 80 | 0.01119 | 0.013987 | N
19/07/2016 | 11:00 | ZN10991:PA1 | URBAN | Planned |  | 68 | 150 | 0.0070629 | 0.0047086 | N
19/07/2016 | 07:35 | ZN15014:PA5 | URBAN | Planned |  | 22 | 600 | 0.0091402 | 0.0015234 | N
21/07/2016 | 07:00 | ZN3472:PA30 | URBAN | Planned |  | 87 | 540 | 0.032524 | 0.0060229 | N
21/07/2016 | 08:00 | ZN8100:PA28 | URBAN | Planned |  | 2 | 543 | 0.00075183 | 0.00013846 | N
21/07/2016 | 08:15 | ZN1193:PA28 | URBAN | Planned |  | 50 | 320 | 0.011077 | 0.0034614 | N
21/07/2016 | 09:00 | ZN180:PA18 | URBAN | Planned |  | 46 | 300 | 0.0095536 | 0.0031845 | N
28/07/2016 | 08:00 | 225:33670 | URBAN | Planned |  | 69 | 415 | 0.019823 | 0.0047767 | N
28/07/2016 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 26 | 430 | 0.050728 | 0.011797 | N
28/07/2016 | 08:45 | 235:2120 | SHORT RURAL | Planned |  | 21 | 375 | 0.035732 | 0.0095284 | N
28/07/2016 | 08:30 | 238:34143 | URBAN | Planned |  | 59 | 210 | 0.0085772 | 0.0040844 | N
28/07/2016 | 08:35 | 242:81541 | URBAN | Planned |  | 140 | 325 | 0.031498 | 0.0096918 | N
28/07/2016 | 11:55 | 232:33407 | SHORT RURAL | Planned |  | 13 | 190 | 0.011207 | 0.0058986 | N
28/07/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 44 | 330 | 0.065882 | 0.019964 | N
28/07/2016 | 08:40 | 810:74062 | SHORT RURAL | Planned |  | 62 | 145 | 0.040791 | 0.028132 | N
30/07/2016 | 08:30 | 258:80793 | URBAN | Planned |  | 124 | 45 | 0.0038629 | 0.0085843 | N
30/07/2016 | 14:40 | 258:80793 | URBAN | Planned |  | 124 | 120 | 0.010301 | 0.0085843 | N
29/07/2016 | 07:30 | 507:80931 | URBAN | Planned |  | 72 | 230 | 0.011464 | 0.0049844 | N
29/07/2016 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 1 | 290 | 0.10346 | 0.035676 | N
29/07/2016 | 08:50 | 511:29876 | SHORT RURAL | Planned |  | 3 | 350 | 0.0047639 | 0.0013611 | N
29/07/2016 | 09:40 | 511:29878 | SHORT RURAL | Planned |  | 35 | 300 | 0.047639 | 0.01588 | N
29/07/2016 | 08:30 | 232:33407 | SHORT RURAL | Planned |  | 12 | 180 | 0.0098 | 0.0054444 | N
29/07/2016 | 09:00 | 232:11457 | SHORT RURAL | Planned |  | 22 | 335 | 0.033438 | 0.0099814 | N
29/07/2016 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 2 | 315 | 0.0028583 | 0.0009074 | N
29/07/2016 | 08:50 | 511:29878 | SHORT RURAL | Planned |  | 16 | 300 | 0.021778 | 0.0072592 | N
01/08/2016 | 09:00 | 504:48031 | SHORT RURAL | Planned |  | 31 | 390 | 0.054852 | 0.014065 | N
01/08/2016 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 3 | 222 | 0.0030216 | 0.0013611 | N
01/08/2016 | 07:30 | 524:33580 | SHORT RURAL | Planned |  | 48 | 605 | 0.13175 | 0.021777 | N
01/08/2016 | 11:30 | 508:82576 | SHORT RURAL | Planned |  | 41 | 185 | 0.034413 | 0.018602 | N
02/08/2016 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 36 | 415 | 5.3319 | 1.2848 | N
02/08/2016 | 09:00 | 811:74234 | SHORT RURAL | Planned |  | 5 | 225 | 0.0051042 | 0.0022685 | N
02/08/2016 | 08:00 | 223:14395 | SHORT RURAL | Planned |  | 51 | 270 | 0.062475 | 0.023139 | N
02/08/2016 | 08:00 | 216:10727 | SHORT RURAL | Planned |  | 38 | 450 | 0.077583 | 0.017241 | N
03/08/2016 | 10:10 | 243:80074 | SHORT RURAL | Planned |  | 109 | 230 | 0.11374 | 0.049454 | N
02/08/2016 | 08:00 | 235:2120 | SHORT RURAL | Planned |  | 21 | 380 | 0.036206 | 0.0095278 | N
02/08/2016 | 09:00 | 232:33407 | SHORT RURAL | Planned |  | 31 | 345 | 0.048524 | 0.014065 | N
02/08/2016 | 08:32 | 532:83300 | URBAN | Planned |  | 86 | 203 | 0.012086 | 0.0059538 | N
02/08/2016 | 10:00 | 532:83298 | URBAN | Planned |  | 1 | 185 | 0.00012808 | 6.923e-05 | N
03/08/2016 | 09:00 | 232:33413 | URBAN | Planned |  | 20 | 180 | 0.0024923 | 0.0013846 | N
02/08/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 4 | 315 | 0.0057167 | 0.0018148 | N
02/08/2016 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 3 | 350 | 0.0047639 | 0.0013611 | N
04/08/2016 | 08:00 | 511:29877 | SHORT RURAL | Planned |  | 26 | 420 | 0.049646 | 0.01182 | N
05/08/2016 | 09:00 | 238:34144 | URBAN | Planned |  | 137 | 180 | 0.017059 | 0.0094772 | N
04/08/2016 | 08:30 | 243:80081 | SHORT RURAL | Planned |  | 232 | 430 | 0.45354 | 0.10547 | N
05/08/2016 | 09:00 | 243:80084 | SHORT RURAL | Planned |  | 3 | 270 | 0.0036825 | 0.0013639 | N
05/08/2016 | 07:50 | 258:80779 | URBAN | Planned |  | 56 | 424 | 0.016425 | 0.0038739 | N
07/08/2016 | 09:00 | 227:13015 | SHORT RURAL | Planned |  | 34 | 530 | 0.081925 | 0.015457 | N
04/08/2016 | 13:05 | 242:81538 | URBAN | Planned |  | 249 | 135 | 0.023254 | 0.017225 | N
06/08/2016 | 14:40 | 511:29882 | URBAN | Planned |  | 1 | 190 | 0.00013144 | 6.9178e-05 | N
04/08/2016 | 10:10 | 810:74058 | SHORT RURAL | Planned |  | 1 | 80 | 0.00036371 | 0.00045463 | N
21/07/2016 | 19:30 | ZN9245:PA38 | SHORT RURAL | Planned |  | 60 | 795 | 0.21655 | 0.027239 | N
05/08/2016 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 8 | 55 | 0.0020004 | 0.003637 | N
07/08/2016 | 08:30 | 513:48057 | URBAN | Planned |  | 29 | 200 | 0.0040123 | 0.0020062 | N
21/07/2016 | 21:00 | ZN10990:PA2 | URBAN | Planned |  | 28 | 184 | 0.0035667 | 0.0019384 | N
22/07/2016 | 09:30 | ZN12570:PA21 | URBAN | Planned |  | 86 | 370 | 0.022031 | 0.0059542 | N
22/07/2016 | 09:30 | ZN12570:PA41 | URBAN | Planned |  | 84 | 370 | 0.021518 | 0.0058157 | N
22/07/2016 | 22:10 | ZN965:PA4 | URBAN | Planned |  | 3 | 430 | 0.00089313 | 0.0002077 | N
23/07/2016 | 04:30 | ZN3288:PA41 42KLM | CBD | Planned |  | 11 | 175 | 0.062051 | 0.035458 | N
23/07/2016 | 06:00 | ZN10999:PA9 | URBAN | Planned |  | 1 | 275 | 0.0001904 | 6.9235e-05 | N
23/07/2016 | 06:30 | ZN847:PA19 | URBAN | Planned |  | 1 | 2,880 | 0.001994 | 6.9235e-05 | N
23/07/2016 | 08:00 | ZN129:PA21 | URBAN | Planned |  | 1 | 315 | 0.00021809 | 6.9235e-05 | N
23/07/2016 | 08:30 | ZN4990:PA55ABC | CBD | Planned |  | 39 | 510 | 0.64114 | 0.12571 | N
23/07/2016 | 17:30 | ZN4990:PA55 56DEF | CBD | Planned |  | 1 | 540 | 0.017406 | 0.0032234 | N
24/07/2016 | 02:00 | ZN12610:PA9 | URBAN | Planned |  | 5 | 455 | 0.0015751 | 0.00034617 | N
25/07/2016 | 06:00 | ZN9118:PA12 | URBAN | Planned |  | 1 | 420 | 0.00029079 | 6.9235e-05 | N
25/07/2016 | 08:30 | ZN12620:PA11 | SHORT RURAL | Planned |  | 239 | 420 | 0.45563 | 0.10848 | N
25/07/2016 | 23:45 | ZN3425:PA36 | URBAN | Planned |  | 6 | 420 | 0.0017447 | 0.00041541 | N
26/07/2016 | 07:00 | ZN4545:PA2 | URBAN | Planned |  | 54 | 480 | 0.017946 | 0.0037387 | N
26/07/2016 | 07:00 | ZN4545:PA2 | URBAN | Planned |  | 37 | 480 | 0.012296 | 0.0025617 | N
26/07/2016 | 07:35 | ZN12650:PA1 | SHORT RURAL | Planned |  | 108 | 500 | 0.24511 | 0.049022 | N
26/07/2016 | 07:30 | ZN10990:PA5 | URBAN | Planned |  | 4 | 450 | 0.0012462 | 0.00027694 | N
26/07/2016 | 07:30 | ZN965:PA33 | URBAN | Planned |  | 16 | 570 | 0.0063142 | 0.0011078 | N
26/07/2016 | 09:00 | ZN9037:PA2 | URBAN | Planned |  | 43 | 360 | 0.010718 | 0.0029771 | N
26/07/2016 | 09:00 | ZN1287:PA17 | URBAN | Planned |  | 37 | 240 | 0.0061481 | 0.0025617 | N
26/07/2016 | 09:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 19 | 390 | 0.033635 | 0.0086243 | N
26/07/2016 | 09:00 | ZN12630:PA22 | SHORT RURAL | Planned |  | 3 | 180 | 0.0024511 | 0.0013617 | N
08/08/2016 | 08:20 | 205:12203 | URBAN | Planned |  | 343 | 550 | 0.1305 | 0.023728 | N
27/07/2016 | 09:10 | ZN12570:PA39 | URBAN | Planned |  | 155 | 400 | 0.042927 | 0.010732 | N
27/07/2016 | 09:50 | ZN12630:PA23 | SHORT RURAL | Planned |  | 9 | 235 | 0.0096005 | 0.0040853 | N
27/07/2016 | 22:30 | ZN3425:PA36 | URBAN | Planned |  | 6 | 510 | 0.0021186 | 0.00041542 | N
28/07/2016 | 07:30 | ZN12600:PA9 | SHORT RURAL | Planned |  | 49 | 465 | 0.10338 | 0.022233 | N
28/07/2016 | 07:30 | ZN12600:PA9 | SHORT RURAL | Planned |  | 39 | 465 | 0.082285 | 0.017696 | N
28/07/2016 | 07:30 | ZN12600:PA9 | SHORT RURAL | Planned |  | 58 | 465 | 0.12237 | 0.026317 | N
28/07/2016 | 08:00 | ZN12570:PA21 | URBAN | Planned |  | 59 | 540 | 0.022056 | 0.0040844 | N
28/07/2016 | 08:30 | ZN12580:PA4 | URBAN | Planned |  | 152 | 435 | 0.045773 | 0.010523 | N
28/07/2016 | 22:15 | ZN384:PA37 | SHORT RURAL | Planned |  | 4 | 225 | 0.0040836 | 0.0018149 | N
29/07/2016 | 10:05 | ZN14891:PA21 | SHORT RURAL | Planned |  | 15 | 145 | 0.009868 | 0.0068055 | N
08/08/2016 | 06:30 | 202:34232 | URBAN | Planned |  | 1 | 10 | 6.9178e-06 | 6.9178e-05 | N
08/08/2016 | 08:00 | 239:82129 | SHORT RURAL | Planned |  | 212 | 480 | 0.46263 | 0.096382 | N
08/08/2016 | 08:00 | 213:33773 | URBAN | Planned |  | 1 | 565 | 0.00039086 | 6.9178e-05 | N
08/08/2016 | 08:30 | 238:34141 | SHORT RURAL | Planned |  | 55 | 185 | 0.046259 | 0.025005 | N
08/08/2016 | 11:00 | 232:33407 | SHORT RURAL | Planned |  | 2 | 30 | 0.00027278 | 0.00090926 | N
08/08/2016 | 09:00 | 526:34640 | SHORT RURAL | Planned |  | 3 | 255 | 0.0034779 | 0.0013639 | N
08/08/2016 | 17:20 | 238:34137 | SHORT RURAL | Planned |  | 1 | 125 | 0.00056829 | 0.00045463 | N
08/08/2016 | 08:45 | 516:48067 | SHORT RURAL | Planned |  | 3 | 160 | 0.0021822 | 0.0013639 | N
08/08/2016 | 08:30 | 516:48066 | SHORT RURAL | Planned |  | 4 | 305 | 0.0055465 | 0.0018185 | N
10/08/2016 | 08:30 | 213:33775 | URBAN | Planned |  | 206 | 510 | 0.072679 | 0.014251 | N
09/08/2016 | 08:15 | 801:74121 | LONG RURAL | Planned |  | 15 | 250 | 1.3379 | 0.53514 | N
09/08/2016 | 08:30 | 264:81244 | SHORT RURAL | Planned |  | 54 | 420 | 0.10345 | 0.02463 | N
27/07/2016 | 07:30 | ZN10999:PA11 | URBAN | Planned |  | 29 | 90 | 0.0018071 | 0.0020079 | N
30/07/2016 | 07:20 | ZN5868:PA13 | URBAN | Planned |  | 1 | 670 | 0.00046383 | 6.9228e-05 | N
30/07/2016 | 10:00 | ZN690:PA3 | URBAN | Planned |  | 1 | 420 | 0.00029076 | 6.9228e-05 | N
30/07/2016 | 13:20 | ZN35400:PA102 | URBAN | Planned |  | 4 | 445 | 0.0012323 | 0.00027691 | N
30/07/2016 | 16:00 | ZN630:PA26 | URBAN | Planned |  | 3 | 20 | 4.1537e-05 | 0.00020769 | N
30/07/2016 | 16:30 | ZN3288:PA41 42GHJ | CBD | Planned |  | 70 | 440 | 0.99284 | 0.22565 | N
09/08/2016 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 335 | 0.23903 | 0.071352 | N
30/07/2016 | 17:30 | ZN4990:PA55 56DEF | CBD | Planned |  | 81 | 540 | 1.41 | 0.26111 | N
09/08/2016 | 08:30 | 508:82579 | SHORT RURAL | Planned |  | 8 | 450 | 0.01642 | 0.0036489 | N
30/07/2016 | 21:00 | ZN15012:PA8 | URBAN | Planned |  | 103 | 179 | 0.012764 | 0.0071305 | N
30/07/2016 | 23:31 | ZN3288:PA41 42GHJ | CBD | Planned |  | 7 | 359 | 0.081007 | 0.022565 | N
09/08/2016 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 31 | 240 | 2.6543 | 1.106 | N
31/07/2016 | 07:30 | ZN15001:PA13 | URBAN | Planned |  | 10 | 240 | 0.0016615 | 0.0006923 | N
09/08/2016 | 09:15 | 812:19072 | SHORT RURAL | Planned |  | 2 | 200 | 0.0018245 | 0.00091223 | N
31/07/2016 | 07:45 | ZN263:PA31 32GHJ | CBD | Planned |  | 3 | 235 | 0.022726 | 0.0096706 | N
31/07/2016 | 08:05 | ZN12650:PA14 | URBAN | Planned |  | 1 | 450 | 0.00031153 | 6.923e-05 | N
31/07/2016 | 15:30 | ZN4990:PA51 52DEF | CBD | Planned |  | 1 | 125 | 0.0040294 | 0.0032235 | N
10/08/2016 | 09:35 | 814:82283 | SHORT RURAL | Planned |  | 14 | 130 | 0.0083014 | 0.0063857 | N
10/08/2016 | 08:30 | 807:74179 | SHORT RURAL | Planned |  | 12 | 275 | 0.015052 | 0.0054735 | N
10/08/2016 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 10 | 310 | 0.01414 | 0.0045612 | N
10/08/2016 | 08:30 | 504:48033 | SHORT RURAL | Planned |  | 8 | 420 | 0.015326 | 0.003649 | N
10/08/2016 | 10:40 | 508:82579 | SHORT RURAL | Planned |  | 1 | 260 | 0.0011859 | 0.00045612 | N
10/08/2016 | 09:00 | 264:81236 | SHORT RURAL | Planned |  | 28 | 180 | 0.022989 | 0.012771 | N
10/08/2016 | 09:00 | 512:48048 | SHORT RURAL | Planned |  | 33 | 495 | 0.074507 | 0.015052 | N
10/08/2016 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 4 | 140 | 0.0025543 | 0.0018245 | N
11/08/2016 | 09:00 | 806:82662 | SHORT RURAL | Planned |  | 2 | 160 | 0.0014592 | 0.000912 | N
11/08/2016 | 09:30 | 238:34141 | SHORT RURAL | Planned |  | 22 | 190 | 0.019061 | 0.010032 | N
11/08/2016 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 4 | 165 | 0.0030096 | 0.001824 | N
11/08/2016 | 09:25 | 810:74054 | LONG RURAL | Planned |  | 27 | 190 | 1.8302 | 0.96325 | N
13/08/2016 | 08:30 | 509:33397 | SHORT RURAL | Planned |  | 101 | 470 | 0.21647 | 0.046058 | N
12/08/2016 | 08:38 | 243:80083 | SHORT RURAL | Planned |  | 15 | 227 | 0.015527 | 0.0068401 | N
12/08/2016 | 08:30 | 238:34141 | SHORT RURAL | Planned |  | 23 | 410 | 0.043002 | 0.010488 | N
12/08/2016 | 08:30 | 264:81244 | SHORT RURAL | Planned |  | 1 | 290 | 0.0013224 | 0.00045601 | N
12/08/2016 | 08:16 | 232:11457 | SHORT RURAL | Planned |  | 1 | 294 | 0.0013407 | 0.00045601 | N
12/08/2016 | 10:00 | 511:29877 | SHORT RURAL | Planned |  | 1 | 165 | 0.00075241 | 0.00045601 | N
12/08/2016 | 08:00 | 238:34150 | SHORT RURAL | Planned |  | 52 | 470 | 0.11145 | 0.023712 | N
12/08/2016 | 08:50 | 507:80917 | URBAN | Planned |  | 140 | 340 | 0.032918 | 0.0096818 | N
12/08/2016 | 10:50 | 511:29878 | SHORT RURAL | Planned |  | 1 | 175 | 0.00079802 | 0.00045601 | N
12/08/2016 | 08:30 | 807:74181 | SHORT RURAL | Planned |  | 39 | 126 | 0.022408 | 0.017784 | N
12/08/2016 | 09:10 | 812:19072 | SHORT RURAL | Planned |  | 1 | 130 | 0.00059281 | 0.00045601 | N
13/08/2016 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 8 | 320 | 0.011674 | 0.0036481 | N
15/08/2016 | 08:37 | 213:33774 | URBAN | Planned |  | 1 | 333 | 0.00023029 | 6.9157e-05 | N
15/08/2016 | 09:38 | 243:80074 | SHORT RURAL | Planned |  | 157 | 277 | 0.19832 | 0.071594 | N
15/08/2016 | 18:00 | 240:34843 | URBAN | Planned |  | 2 | 330 | 0.00045644 | 0.00013831 | N
15/08/2016 | 08:20 | 509:33399 | SHORT RURAL | Planned |  | 25 | 240 | 0.027361 | 0.0114 | N
15/08/2016 | 08:30 | 512:48048 | SHORT RURAL | Planned |  | 7 | 510 | 0.01628 | 0.0031921 | N
15/08/2016 | 08:35 | 812:19072 | SHORT RURAL | Planned |  | 1 | 235 | 0.0010716 | 0.00045602 | N
15/08/2016 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 34 | 300 | 3.639 | 1.213 | N
16/08/2016 | 08:30 | 532:83309 | SHORT RURAL | Planned |  | 10 | 315 | 0.014364 | 0.0045602 | N
16/08/2016 | 09:40 | 216:10727 | SHORT RURAL | Planned |  | 131 | 510 | 0.30466 | 0.059738 | N
16/08/2016 | 08:50 | 213:33771 | URBAN | Planned |  | 65 | 373 | 0.016767 | 0.0044952 | N
16/08/2016 | 09:30 | 239:82129 | SHORT RURAL | Planned |  | 101 | 270 | 0.12436 | 0.046058 | N
16/08/2016 | 18:15 | 240:34843 | URBAN | Planned |  | 2 | 405 | 0.00056017 | 0.00013831 | N
16/08/2016 | 08:40 | 508:82578 | SHORT RURAL | Planned |  | 4 | 260 | 0.0047426 | 0.0018241 | N
17/08/2016 | 00:45 | 526:34640 | SHORT RURAL | Planned |  | 3 | 315 | 0.0043094 | 0.0013681 | N
16/08/2016 | 08:00 | 801:74119 | URBAN | Planned |  | 33 | 115 | 0.0026245 | 0.0022822 | N
16/08/2016 | 08:35 | 515:35192 | SHORT RURAL | Planned |  | 1 | 325 | 0.001482 | 0.00045602 | N
16/08/2016 | 09:40 | 813:89061 | LONG RURAL | Planned |  | 3 | 150 | 0.16054 | 0.10703 | N
18/08/2016 | 05:00 | 801:74118 | URBAN | Planned |  | 33 | 90 | 0.0020606 | 0.0022895 | N
17/08/2016 | 08:00 | 515:35192 | SHORT RURAL | Planned |  | 1 | 460 | 0.0020977 | 0.00045602 | N
17/08/2016 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 6 | 315 | 0.67428 | 0.21406 | N
17/08/2016 | 08:30 | 513:48058 | URBAN | Planned |  | 3 | 195 | 0.00040458 | 0.00020748 | N
19/08/2016 | 09:15 | 528:83019 | SHORT RURAL | Planned |  | 52 | 285 | 0.068695 | 0.024104 | N
19/08/2016 | 08:05 | 532:83307 | SHORT RURAL | Planned |  | 4 | 405 | 0.0075092 | 0.0018541 | N
18/08/2016 | 08:30 | 507:80922 | SHORT RURAL | Planned |  | 101 | 415 | 0.19429 | 0.046817 | N
18/08/2016 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 4 | 350 | 0.0064894 | 0.0018541 | N
19/08/2016 | 08:30 | 511:29880 | URBAN | Planned |  | 71 | 435 | 0.021428 | 0.0049259 | N
19/08/2016 | 08:50 | 511:29877 | SHORT RURAL | Planned |  | 5 | 190 | 0.0044036 | 0.0023177 | N
19/08/2016 | 12:50 | 511:29877 | SHORT RURAL | Planned |  | 2 | 120 | 0.0011125 | 0.00092706 | N
18/08/2016 | 08:45 | 812:19072 | SHORT RURAL | Planned |  | 1 | 90 | 0.00041718 | 0.00046353 | N
18/08/2016 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 8 | 270 | 0.010012 | 0.0037083 | N
19/08/2016 | 08:30 | 516:48067 | SHORT RURAL | Planned |  | 23 | 18 | 0.001919 | 0.010661 | N
19/08/2016 | 08:45 | 806:82662 | SHORT RURAL | Planned |  | 2 | 240 | 0.002225 | 0.00092706 | N
19/08/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 9 | 365 | 1.1715 | 0.32097 | N
19/08/2016 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 2 | 160 | 0.0014833 | 0.00092706 | N
19/08/2016 | 08:57 | 807:74184 | SHORT RURAL | Planned |  | 1 | 83 | 0.00038473 | 0.00046353 | N
19/08/2016 | 09:15 | 514:18137 | SHORT RURAL | Planned |  | 1 | 150 | 0.0006953 | 0.00046353 | N
22/08/2016 | 08:00 | 221:11899 | SHORT RURAL | Planned |  | 1 | 420 | 0.0019468 | 0.00046353 | N
22/08/2016 | 09:45 | 223:14395 | SHORT RURAL | Planned |  | 6 | 360 | 0.010012 | 0.0027812 | N
22/08/2016 | 08:30 | 524:33574 | SHORT RURAL | Planned |  | 57 | 136 | 0.035933 | 0.026421 | N
22/08/2016 | 08:30 | 524:33574 | SHORT RURAL | Planned |  | 2 | 225 | 0.0020859 | 0.00092706 | N
22/08/2016 | 08:35 | 515:35193 | SHORT RURAL | Planned |  | 2 | 40 | 0.00037083 | 0.00092706 | N
22/08/2016 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 21 | 240 | 1.7974 | 0.74893 | N
22/08/2016 | 08:55 | 813:89061 | LONG RURAL | Planned |  | 2 | 140 | 0.099857 | 0.071327 | N
23/08/2016 | 09:05 | 515:35200 | URBAN | Planned |  | 1 | 365 | 0.00025218 | 6.909e-05 | N
23/08/2016 | 10:30 | 221:11899 | SHORT RURAL | Planned |  | 92 | 60 | 0.025217 | 0.042028 | N
23/08/2016 | 05:45 | 511:29877 | SHORT RURAL | Planned |  | 1 | 40 | 0.00018273 | 0.00045683 | N
23/08/2016 | 07:50 | 511:29877 | SHORT RURAL | Planned |  | 1 | 520 | 0.0023755 | 0.00045683 | N
23/08/2016 | 09:05 | 235:2728 | URBAN | Planned |  | 61 | 335 | 0.014118 | 0.0042145 | N
23/08/2016 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 80 | 230 | 0.084056 | 0.036546 | N
23/08/2016 | 08:20 | 507:80932 | SHORT RURAL | Planned |  | 30 | 239 | 0.032755 | 0.013705 | N
23/08/2016 | 17:00 | 511:29877 | SHORT RURAL | Planned |  | 1 | 25 | 0.00011421 | 0.00045683 | N
23/08/2016 | 10:10 | 513:48059 | SHORT RURAL | Planned |  | 1 | 45 | 0.00020557 | 0.00045683 | N
24/08/2016 | 08:40 | 532:83307 | SHORT RURAL | Planned |  | 35 | 385 | 0.061558 | 0.015989 | N
24/08/2016 | 08:20 | 213:33774 | URBAN | Planned |  | 129 | 365 | 0.032532 | 0.0089129 | N
24/08/2016 | 08:25 | 504:48033 | SHORT RURAL | Planned |  | 22 | 245 | 0.024623 | 0.01005 | N
24/08/2016 | 10:28 | 532:83293 | URBAN | Planned |  | 149 | 212 | 0.021825 | 0.010295 | N
24/08/2016 | 09:15 | 516:48067 | SHORT RURAL | Planned |  | 8 | 285 | 0.010416 | 0.0036547 | N
24/08/2016 | 08:45 | 810:74054 | LONG RURAL | Planned |  | 4 | 90 | 0.12839 | 0.14265 | N
25/08/2016 | 09:10 | 243:80084 | SHORT RURAL | Planned |  | 120 | 510 | 0.27958 | 0.054821 | N
25/08/2016 | 08:35 | 210:8679 | URBAN | Planned |  | 153 | 395 | 0.041757 | 0.010571 | N
25/08/2016 | 10:00 | 230:81432 | SHORT RURAL | Planned |  | 110 | 245 | 0.12312 | 0.050252 | N
25/08/2016 | 08:40 | 532:83314 | URBAN | Planned |  | 370 | 395 | 0.10098 | 0.025565 | N
25/08/2016 | 08:15 | 514:18137 | SHORT RURAL | Planned |  | 15 | 475 | 0.03255 | 0.0068526 | N
25/08/2016 | 12:30 | 514:18137 | SHORT RURAL | Planned |  | 1 | 100 | 0.00045684 | 0.00045684 | N
26/08/2016 | 08:30 | 224:80340 | SHORT RURAL | Planned |  | 233 | 30 | 0.031933 | 0.10644 | N
26/08/2016 | 08:30 | 224:80340 | SHORT RURAL | Planned |  | 52 | 30 | 0.0071267 | 0.023756 | N
26/08/2016 | 08:50 | 261:81870 | URBAN | Planned |  | 101 | 120 | 0.0083742 | 0.0069785 | N
26/08/2016 | 11:00 | 243:80075 | SHORT RURAL | Planned |  | 5 | 210 | 0.0047968 | 0.0022842 | N
26/08/2016 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 12 | 390 | 0.02138 | 0.0054821 | N
26/08/2016 | 08:40 | 238:34150 | SHORT RURAL | Planned |  | 2 | 390 | 0.0035633 | 0.00091368 | N
26/08/2016 | 08:35 | 528:83020 | SHORT RURAL | Planned |  | 26 | 260 | 0.030882 | 0.011878 | N
26/08/2016 | 09:40 | 532:83309 | SHORT RURAL | Planned |  | 50 | 230 | 0.052536 | 0.022842 | N
26/08/2016 | 10:00 | 512:48046 | SHORT RURAL | Planned |  | 46 | 160 | 0.033623 | 0.021015 | N
26/08/2016 | 09:07 | 524:33570 | SHORT RURAL | Planned |  | 240 | 130 | 0.14253 | 0.10964 | N
26/08/2016 | 08:30 | 523:33507 | URBAN | Planned |  | 50 | 240 | 0.0082913 | 0.0034547 | N
29/08/2016 | 08:10 | 227:13019 | SHORT RURAL | Planned |  | 76 | 450 | 0.15616 | 0.034703 | N
29/08/2016 | 08:00 | 258:80775 | URBAN | Planned |  | 89 | 260 | 0.015981 | 0.0061463 | N
29/08/2016 | 09:30 | 210:8682 | URBAN | Planned |  | 86 | 135 | 0.0080179 | 0.0059392 | N
29/08/2016 | 08:35 | 233:82819 | SHORT RURAL | Planned |  | 77 | 400 | 0.14064 | 0.035159 | N
29/08/2016 | 17:30 | 511:29872 | URBAN | Planned |  | 6 | 245 | 0.0010152 | 0.00041436 | N
29/08/2016 | 13:30 | 514:18137 | SHORT RURAL | Planned |  | 2 | 50 | 0.00045662 | 0.00091323 | N
01/08/2016 | 06:40 | ZN12630:PA22 | SHORT RURAL | Planned |  | 1 | 635 | 0.002881 | 0.0004537 | N
01/08/2016 | 08:10 | ZN15005:PA10 | URBAN | Planned |  | 5 | 470 | 0.0016269 | 0.00034615 | N
01/08/2016 | 08:00 | ZN80:PA22 | URBAN | Planned |  | 75 | 480 | 0.024923 | 0.0051922 | N
02/08/2016 | 08:10 | ZN15005:PA10 | URBAN | Planned |  | 5 | 470 | 0.0016269 | 0.00034615 | N
02/08/2016 | 07:30 | ZN8000:PA25 | URBAN | Planned |  | 1 | 10 | 6.923e-06 | 6.923e-05 | N
02/08/2016 | 07:30 | ZN2835:PA18 | URBAN | Planned |  | 47 | 510 | 0.016594 | 0.0032538 | N
02/08/2016 | 07:30 | ZN180:PA23 | URBAN | Planned |  | 69 | 450 | 0.021496 | 0.0047769 | N
02/08/2016 | 08:00 | ZN9900:PA2 | URBAN | Planned |  | 52 | 600 | 0.0216 | 0.0036 | N
02/08/2016 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 3 | 310 | 0.0042194 | 0.0013611 | N
02/08/2016 | 08:15 | ZN36800:PA57 | URBAN | Planned |  | 93 | 150 | 0.0096576 | 0.0064384 | N
02/08/2016 | 09:30 | ZN35370:PA8 | SHORT RURAL | Planned |  | 6 | 390 | 0.010617 | 0.0027222 | N
02/08/2016 | 20:00 | ZN12620:PA1 | SHORT RURAL | Planned |  | 5 | 60 | 0.0013611 | 0.0022685 | N
03/08/2016 | 06:30 | ZN10999:PA23 | URBAN | Planned |  | 5 | 120 | 0.00041539 | 0.00034615 | N
03/08/2016 | 08:10 | ZN15005:PA10 | URBAN | Planned |  | 5 | 470 | 0.0016269 | 0.00034615 | N
03/08/2016 | 07:00 | ZN72:PA13 | URBAN | Planned |  | 37 | 120 | 0.0030739 | 0.0025615 | N
03/08/2016 | 08:00 | ZN35370:PA8 | SHORT RURAL | Planned |  | 6 | 620 | 0.016878 | 0.0027222 | N
03/08/2016 | 08:45 | ZN12630:PA23 | SHORT RURAL | Planned |  | 45 | 385 | 0.078605 | 0.020417 | N
03/08/2016 | 09:28 | ZN14892:PA6 | SHORT RURAL | Planned |  | 132 | 309 | 0.18506 | 0.059889 | N
03/08/2016 | 09:00 | ZN10995:PA6 | URBAN | Planned |  | 1 | 450 | 0.00031154 | 6.9231e-05 | N
04/08/2016 | 08:10 | ZN15005:PA10 | URBAN | Planned |  | 5 | 470 | 0.0016256 | 0.00034588 | N
04/08/2016 | 08:30 | ZN14143:PA5 | URBAN | Planned |  | 1 | 2,095 | 0.0014492 | 6.9177e-05 | N
04/08/2016 | 08:10 | ZN14891:PA19 | SHORT RURAL | Planned |  | 1 | 140 | 0.00063649 | 0.00045463 | N
04/08/2016 | 08:10 | ZN14891:PA5 | SHORT RURAL | Planned |  | 1 | 140 | 0.00063649 | 0.00045463 | N
04/08/2016 | 07:30 | ZN384:PA33 | URBAN | Planned |  | 36 | 180 | 0.0044826 | 0.0024904 | N
04/08/2016 | 07:30 | ZN3155:PA36 | URBAN | Planned |  | 39 | 630 | 0.016997 | 0.0026979 | N
04/08/2016 | 08:40 | ZN12630:PA21 | SHORT RURAL | Planned |  | 48 | 425 | 0.092745 | 0.021822 | N
04/08/2016 | 09:00 | ZN2835:PA30 | URBAN | Planned |  | 48 | 360 | 0.011954 | 0.0033205 | N
04/08/2016 | 11:00 | ZN35900:PA1 | URBAN | Planned |  | 8 | 30 | 0.00016602 | 0.00055341 | N
04/08/2016 | 12:30 | ZN2602:PA28 | URBAN | Planned |  | 143 | 780 | 0.07716 | 0.0098922 | N
05/08/2016 | 08:10 | ZN12630:PA21 | SHORT RURAL | Planned |  | 1 | 485 | 0.002205 | 0.00045463 | N
05/08/2016 | 09:00 | ZN12570:PA21 | URBAN | Planned |  | 23 | 390 | 0.0062052 | 0.0015911 | N
06/08/2016 | 06:30 | ZN8700:PA65 66ABC | CBD | Planned |  | 59 | 180 | 0.34232 | 0.19018 | N
06/08/2016 | 10:15 | ZN12660:PA14 | SHORT RURAL | Planned |  | 6 | 1,785 | 0.048691 | 0.0027278 | N
06/08/2016 | 07:30 | ZN847:PA31 | URBAN | Planned |  | 1 | 330 | 0.00022829 | 6.9178e-05 | N
06/08/2016 | 08:00 | ZN8700:PA61 62ABC | CBD | Planned |  | 1 | 360 | 0.011604 | 0.0032233 | N
07/08/2016 | 06:30 | ZN8700:PA63 64DEF | CBD | Planned |  | 21 | 620 | 0.41968 | 0.06769 | N
07/08/2016 | 23:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 5 | 240 | 0.0054556 | 0.0022732 | N
08/08/2016 | 07:00 | ZN7481:PA1 | URBAN | Planned |  | 3 | 60 | 0.00012452 | 0.00020753 | N
08/08/2016 | 09:15 | ZN14891:PA12 | SHORT RURAL | Planned |  | 14 | 135 | 0.0085925 | 0.0063649 | N
08/08/2016 | 08:30 | ZN7900:PA7 | URBAN | Planned |  | 93 | 420 | 0.027021 | 0.0064336 | N
08/08/2016 | 08:30 | ZN8100:PA10 | URBAN | Planned |  | 1 | 360 | 0.00024904 | 6.9178e-05 | N
08/08/2016 | 08:30 | ZN129:PA5 | URBAN | Planned |  | 39 | 420 | 0.011331 | 0.0026979 | N
08/08/2016 | 09:00 | ZN10990:PA11 | URBAN | Planned |  | 53 | 231 | 0.0084695 | 0.0036664 | N
08/08/2016 | 19:00 | ZN2310:PA55 | URBAN | Planned |  | 1 | 810 | 0.00056034 | 6.9178e-05 | N
09/08/2016 | 05:00 | ZN10999:PA35 | URBAN | Planned |  | 53 | 210 | 0.0076994 | 0.0036664 | N
09/08/2016 | 07:30 | ZN180:PA23 | URBAN | Planned |  | 69 | 450 | 0.02148 | 0.0047732 | N
09/08/2016 | 08:10 | ZN12630:PA23 | SHORT RURAL | Planned |  | 14 | 360 | 0.022988 | 0.0063856 | N
09/08/2016 | 09:20 | ZN3155:PA29 | URBAN | Planned |  | 12 | 280 | 0.0023244 | 0.00083013 | N
09/08/2016 | 10:00 | ZN10994:PA20 | URBAN | Planned |  | 84 | 60 | 0.0034865 | 0.0058109 | N
10/08/2016 | 07:30 | ZN8100:PA20 | URBAN | Planned |  | 20 | 570 | 0.0078864 | 0.0013836 | N
10/08/2016 | 09:10 | ZN14143:PA17 | SHORT RURAL | Planned |  | 4 | 410 | 0.0074804 | 0.0018245 | N
10/08/2016 | 08:15 | ZN1287:PA4 | URBAN | Planned |  | 221 | 705 | 0.10778 | 0.015289 | N
10/08/2016 | 08:50 | ZN15012:PA8 | URBAN | Planned |  | 34 | 340 | 0.0079971 | 0.0023521 | N
10/08/2016 | 09:30 | ZN1610:PA19 | URBAN | Planned |  | 61 | 150 | 0.0063299 | 0.0042199 | N
31/08/2016 | 09:00 | 261:81870 | URBAN | Planned |  | 49 | 390 | 0.013193 | 0.0033829 | N
10/08/2016 | 09:30 | ZN12620:PA11 | SHORT RURAL | Planned |  | 3 | 220 | 0.0030104 | 0.0013684 | N
10/08/2016 | 17:30 | ZN12660:PA13 | URBAN | Planned |  | 25 | 780 | 0.01349 | 0.0017295 | N
10/08/2016 | 22:15 | ZN15008:PA10 | URBAN | Planned |  | 25 | 205 | 0.0035454 | 0.0017295 | N
11/08/2016 | 05:00 | ZN10999:PA23 | URBAN | Planned |  | 20 | 120 | 0.0016597 | 0.0013831 | N
11/08/2016 | 07:05 | ZN12610:PA25 | URBAN | Planned |  | 189 | 485 | 0.063391 | 0.01307 | N
11/08/2016 | 08:15 | ZN14892:PA16 | URBAN | Planned |  | 55 | 405 | 0.015404 | 0.0038035 | N
11/08/2016 | 08:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 41 | 120 | 0.022435 | 0.018696 | N
11/08/2016 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 11 | 250 | 0.01254 | 0.005016 | N
11/08/2016 | 08:30 | ZN12690:PA16 | SHORT RURAL | Planned |  | 44 | 455 | 0.091291 | 0.020064 | N
11/08/2016 | 09:50 | ZN13000:PA7 | SHORT RURAL | Planned |  | 105 | 260 | 0.12449 | 0.04788 | N
11/08/2016 | 09:50 | ZN384:PA37 | SHORT RURAL | Planned |  | 2 | 50 | 0.000456 | 0.000912 | N
11/08/2016 | 14:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 41 | 120 | 0.022435 | 0.018696 | N
12/08/2016 | 08:45 | ZN14891:PA12 | SHORT RURAL | Planned |  | 19 | 390 | 0.03379 | 0.0086642 | N
13/08/2016 | 06:30 | ZN263:PA33 34KLM | CBD | Planned |  | 48 | 565 | 0.87402 | 0.15469 | N
13/08/2016 | 07:30 | ZN35800:PA15 | URBAN | Planned |  | 35 | 255 | 0.0061723 | 0.0024205 | N
13/08/2016 | 07:30 | ZN129:PA11 | URBAN | Planned |  | 6 | 285 | 0.0011826 | 0.00041494 | N
14/08/2016 | 07:30 | ZN262:PA14 | URBAN | Planned |  | 2 | 270 | 0.00037345 | 0.00013831 | N
14/08/2016 | 23:59 | ZN711:PA31 | URBAN | Planned |  | 46 | 301 | 0.0095755 | 0.0031812 | N
15/08/2016 | 08:05 | ZN9900:PA20 | URBAN | Planned |  | 7 | 455 | 0.0022027 | 0.0004841 | N
15/08/2016 | 08:05 | ZN9900:PA19 | URBAN | Planned |  | 1 | 455 | 0.00031466 | 6.9157e-05 | N
15/08/2016 | 07:30 | ZN3922:PA12 | URBAN | Planned |  | 62 | 620 | 0.026584 | 0.0042877 | N
15/08/2016 | 07:30 | ZN965:PA43 | URBAN | Planned |  | 27 | 405 | 0.0075623 | 0.0018672 | N
15/08/2016 | 08:00 | ZN3155:PA29 | URBAN | Planned |  | 145 | 450 | 0.045125 | 0.010028 | N
15/08/2016 | 08:20 | ZN12630:PA21 | SHORT RURAL | Planned |  | 3 | 520 | 0.0071138 | 0.001368 | N
15/08/2016 | 08:00 | ZN12600:PA1 | SHORT RURAL | Planned |  | 57 | 270 | 0.070181 | 0.025993 | N
31/08/2016 | 12:45 | 232:33409 | SHORT RURAL | Planned |  | 57 | 180 | 0.046833 | 0.026019 | N
15/08/2016 | 21:00 | ZN180:PA32 | URBAN | Planned |  | 54 | 615 | 0.022967 | 0.0037345 | N
15/08/2016 | 20:30 | ZN2835:PA18 | URBAN | Planned |  | 47 | 510 | 0.016577 | 0.0032504 | N
15/08/2016 | 20:30 | ZN7900:PA20 | URBAN | Planned |  | 1 | 30 | 2.0747e-05 | 6.9157e-05 | N
15/08/2016 | 22:00 | ZN384:PA37 | SHORT RURAL | Planned |  | 1 | 240 | 0.0010944 | 0.00045602 | N
16/08/2016 | 08:00 | ZN12600:PA13 | SHORT RURAL | Planned |  | 19 | 480 | 0.041589 | 0.0086643 | N
16/08/2016 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 8 | 480 | 0.017511 | 0.0036481 | N
16/08/2016 | 09:30 | ZN2473:PA9 | URBAN | Planned |  | 124 | 90 | 0.0077179 | 0.0085755 | N
16/08/2016 | 08:00 | ZN15001:PA18 | URBAN | Planned |  | 32 | 480 | 0.010623 | 0.002213 | N
17/08/2016 | 07:30 | ZN398:PA29 | URBAN | Planned |  | 78 | 315 | 0.016993 | 0.0053945 | N
17/08/2016 | 08:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 41 | 480 | 0.089745 | 0.018697 | N
17/08/2016 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 33 | 455 | 0.068472 | 0.015049 | N
17/08/2016 | 08:00 | ZN384:PA66 | URBAN | Planned |  | 2 | 520 | 0.00071926 | 0.00013832 | N
18/08/2016 | 07:30 | ZN14892:PA16 | URBAN | Planned |  | 55 | 240 | 0.009158 | 0.0038158 | N
18/08/2016 | 22:00 | ZN2835:PA41 | URBAN | Planned |  | 73 | 420 | 0.021272 | 0.0050647 | N
19/08/2016 | 07:48 | ZN15013:PA10 | SHORT RURAL | Planned |  | 27 | 502 | 0.062827 | 0.012515 | N
19/08/2016 | 07:45 | ZN1290:PA11 | URBAN | Planned |  | 1 | 525 | 0.00036424 | 6.9379e-05 | N
19/08/2016 | 08:45 | ZN14892:PA19 | URBAN | Planned |  | 5 | 75 | 0.00026017 | 0.00034689 | N
19/08/2016 | 14:00 | ZN14892:PA19 | URBAN | Planned |  | 5 | 105 | 0.00036424 | 0.00034689 | N
19/08/2016 | 08:00 | ZN901:PA20 | URBAN | Planned |  | 4 | 420 | 0.0011656 | 0.00027752 | N
19/08/2016 | 09:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 3 | 240 | 0.0033374 | 0.0013906 | N
19/08/2016 | 12:30 | ZN3472:PA34 | URBAN | Planned |  | 8 | 1,290 | 0.0071599 | 0.00055503 | N
19/08/2016 | 12:30 | ZN3472:PA35 | URBAN | Planned |  | 4 | 1,290 | 0.0035799 | 0.00027752 | N
19/08/2016 | 19:00 | ZN7900:PA23 | URBAN | Planned |  | 38 | 2,340 | 0.061692 | 0.0026364 | N
20/08/2016 | 07:00 | ZN8700:PA65 66GHJ | CBD | Planned |  | 8 | 230 | 0.06015 | 0.026152 | N
20/08/2016 | 08:00 | ZN35800:PA10 | URBAN | Planned |  | 9 | 510 | 0.0031845 | 0.00062442 | N
20/08/2016 | 08:33 | ZN4545:PA26 | URBAN | Planned |  | 51 | 407 | 0.014401 | 0.0035384 | N
20/08/2016 | 23:00 | ZN9035:PA10 | URBAN | Planned |  | 1 | 450 | 0.00031221 | 6.938e-05 | N
21/08/2016 | 07:35 | ZN384:PA25 | URBAN | Planned |  | 3 | 340 | 0.00070767 | 0.00020814 | N
21/08/2016 | 16:00 | ZN12660:PA13 | URBAN | Planned |  | 25 | 660 | 0.011448 | 0.0017345 | N
22/08/2016 | 07:30 | ZN2835:PA33 | URBAN | Planned |  | 63 | 570 | 0.024914 | 0.0043709 | N
22/08/2016 | 10:12 | ZN15011:PA10 | URBAN | Planned |  | 46 | 138 | 0.0044042 | 0.0031915 | N
22/08/2016 | 07:30 | ZN965:PA8 | URBAN | Planned |  | 12 | 630 | 0.0052451 | 0.00083256 | N
22/08/2016 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 50 | 467 | 0.10823 | 0.023177 | N
22/08/2016 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 15 | 480 | 0.033374 | 0.006953 | N
22/08/2016 | 08:00 | ZN14891:PA20 | SHORT RURAL | Planned |  | 23 | 360 | 0.03838 | 0.010661 | N
22/08/2016 | 10:15 | ZN10999:PA24 | URBAN | Planned |  | 98 | 315 | 0.021417 | 0.0067992 | N
23/08/2016 | 07:30 | ZN874:PA3 | URBAN | Planned |  | 75 | 870 | 0.045081 | 0.0051817 | N
23/08/2016 | 08:00 | ZN180:PA24 | URBAN | Planned |  | 23 | 480 | 0.0076275 | 0.0015891 | N
23/08/2016 | 08:30 | ZN12630:PA22 | SHORT RURAL | Planned |  | 10 | 515 | 0.023527 | 0.0045683 | N
23/08/2016 | 08:45 | ZN195:PA28 | URBAN | Planned |  | 17 | 405 | 0.0047568 | 0.0011745 | N
23/08/2016 | 09:15 | ZN12600:PA2 | SHORT RURAL | Planned |  | 8 | 340 | 0.012426 | 0.0036546 | N
23/08/2016 | 09:30 | ZN9700:PA21 | URBAN | Planned |  | 40 | 400 | 0.011054 | 0.0027636 | N
24/08/2016 | 07:30 | ZN1648:PA8 | SHORT RURAL | Planned |  | 37 | 295 | 0.049863 | 0.016903 | N
25/08/2016 | 07:30 | ZN14891:PA19 | SHORT RURAL | Planned |  | 1 | 240 | 0.0010964 | 0.00045684 | N
25/08/2016 | 07:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 1 | 240 | 0.0010964 | 0.00045684 | N
31/08/2016 | 08:45 | 232:33407 | SHORT RURAL | Planned |  | 38 | 375 | 0.065047 | 0.017346 | N
30/08/2016 | 08:30 | 502:48010 | SHORT RURAL | Planned |  | 39 | 360 | 0.064109 | 0.017808 | N
30/08/2016 | 11:20 | 227:13015 | SHORT RURAL | Planned |  | 4 | 371 | 0.0067762 | 0.0018265 | N
31/08/2016 | 09:25 | 221:11899 | SHORT RURAL | Planned |  | 1 | 155 | 0.00070752 | 0.00045647 | N
30/08/2016 | 08:05 | 238:34150 | SHORT RURAL | Planned |  | 2 | 415 | 0.0037899 | 0.00091323 | N
30/08/2016 | 09:10 | 504:48028 | URBAN | Planned |  | 85 | 335 | 0.019665 | 0.0058702 | N
30/08/2016 | 12:20 | 232:33407 | SHORT RURAL | Planned |  | 5 | 130 | 0.002968 | 0.0022831 | N
30/08/2016 | 09:20 | 232:33407 | SHORT RURAL | Planned |  | 8 | 120 | 0.0043835 | 0.0036529 | N
30/08/2016 | 17:45 | 511:29872 | URBAN | Planned |  | 9 | 15 | 9.3233e-05 | 0.00062155 | N
31/08/2016 | 09:20 | 507:80931 | URBAN | Planned |  | 107 | 285 | 0.021054 | 0.0073872 | N
31/08/2016 | 08:40 | 242:81535 | URBAN | Planned |  | 75 | 320 | 0.016569 | 0.0051779 | N
30/08/2016 | 08:45 | 516:48066 | SHORT RURAL | Planned |  | 24 | 375 | 0.041096 | 0.010959 | N
30/08/2016 | 08:50 | 810:74054 | LONG RURAL | Planned |  | 60 | 365 | 7.8103 | 2.1398 | N
30/08/2016 | 09:05 | 515:35192 | SHORT RURAL | Planned |  | 3 | 310 | 0.0042465 | 0.0013699 | N
30/08/2016 | 14:10 | 514:18137 | SHORT RURAL | Planned |  | 2 | 30 | 0.00027397 | 0.00091323 | N
31/08/2016 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 12 | 235 | 0.012872 | 0.0054776 | N
31/08/2016 | 10:20 | 813:89061 | LONG RURAL | Planned |  | 1 | 105 | 0.037447 | 0.035663 | N
01/09/2016 | 08:30 | 243:80074 | SHORT RURAL | Planned |  | 27 | 385 | 0.04745 | 0.012325 | N
01/09/2016 | 08:30 | 515:35198 | SHORT RURAL | Planned |  | 41 | 200 | 0.037431 | 0.018715 | N
01/09/2016 | 10:45 | 243:80083 | SHORT RURAL | Planned |  | 6 | 75 | 0.0020541 | 0.0027388 | N
02/09/2016 | 09:00 | 214:8666 | URBAN | Planned |  | 35 | 345 | 0.0083365 | 0.0024164 | N
01/09/2016 | 08:35 | 507:80931 | URBAN | Planned |  | 107 | 185 | 0.013666 | 0.0073872 | N
01/09/2016 | 09:45 | 235:2123 | URBAN | Planned |  | 88 | 195 | 0.011847 | 0.0060755 | N
02/09/2016 | 09:50 | 512:48048 | SHORT RURAL | Planned |  | 83 | 45 | 0.017049 | 0.037887 | N
01/09/2016 | 08:40 | 513:48056 | SHORT RURAL | Planned |  | 17 | 320 | 0.024832 | 0.00776 | N
05/09/2016 | 08:55 | 509:33395 | LONG RURAL | Planned |  | 10 | 5 | 0.017832 | 0.35663 | N
05/09/2016 | 09:35 | 806:82662 | SHORT RURAL | Planned |  | 2 | 125 | 0.0011412 | 0.00091296 | N
05/09/2016 | 08:36 | 227:13019 | SHORT RURAL | Planned |  | 7 | 262 | 0.0083718 | 0.0031954 | N
05/09/2016 | 08:40 | 243:80083 | SHORT RURAL | Planned |  | 7 | 360 | 0.011503 | 0.0031954 | N
05/09/2016 | 08:00 | 227:13015 | SHORT RURAL | Planned |  | 2 | 460 | 0.0041996 | 0.00091296 | N
05/09/2016 | 08:40 | 229:34995 | SHORT RURAL | Planned |  | 19 | 395 | 0.034259 | 0.0086731 | N
05/09/2016 | 09:55 | 509:33395 | LONG RURAL | Planned |  | 1 | 80 | 0.028531 | 0.035663 | N
05/09/2016 | 08:20 | 509:33395 | LONG RURAL | Planned |  | 1 | 295 | 0.10521 | 0.035663 | N
05/09/2016 | 17:45 | 511:29880 | URBAN | Planned |  | 4 | 195 | 0.00053853 | 0.00027617 | N
05/09/2016 | 09:25 | 523:33501 | SHORT RURAL | Planned |  | 4 | 135 | 0.002465 | 0.0018259 | N
12/08/2016 | 08:00 | ZN1788:PA29 | SHORT RURAL | Planned |  | 15 | 480 | 0.032833 | 0.0068401 | N
22/08/2016 | 11:10 | ZN12650:PA12 | URBAN | Planned |  | 90 | 12 | 0.0007493 | 0.0062442 | N
25/08/2016 | 09:10 | ZN35370:PA8 | SHORT RURAL | Planned |  | 6 | 370 | 0.010142 | 0.002741 | N
25/08/2016 | 08:30 | ZN12630:PA22 | SHORT RURAL | Planned |  | 7 | 450 | 0.01439 | 0.0031979 | N
25/08/2016 | 20:00 | ZN3472:PA29 | URBAN | Planned |  | 2 | 570 | 0.00078768 | 0.00013819 | N
26/08/2016 | 08:30 | ZN965:PA8 | URBAN | Planned |  | 30 | 300 | 0.0062185 | 0.0020728 | N
26/08/2016 | 08:30 | ZN8000:PA34 | URBAN | Planned |  | 1 | 360 | 0.00024874 | 6.9094e-05 | N
26/08/2016 | 09:30 | ZN35500:PA27 | URBAN | Planned |  | 53 | 175 | 0.0064085 | 0.003662 | N
27/08/2016 | 06:20 | ZN188:PA2 | URBAN | Planned |  | 6 | 55 | 0.0002279 | 0.00041436 | N
27/08/2016 | 06:40 | ZN342:PA18 | URBAN | Planned |  | 1 | 20 | 1.3812e-05 | 6.9059e-05 | N
27/08/2016 | 07:00 | ZN188:PA22 | URBAN | Planned |  | 2 | 10 | 1.3812e-05 | 0.00013812 | N
27/08/2016 | 12:00 | ZN1285:PA20 | URBAN | Planned |  | 1 | 15 | 1.0359e-05 | 6.9059e-05 | N
27/08/2016 | 13:00 | ZN1285:PA20 | URBAN | Planned |  | 2 | 15 | 2.0718e-05 | 0.00013812 | N
27/08/2016 | 23:31 | ZN3288:PA45 46ABC | CBD | Planned |  | 66 | 329 | 0.69944 | 0.21259 | N
28/08/2016 | 08:10 | ZN1610:PA26 | URBAN | Planned |  | 13 | 395 | 0.0035462 | 0.00089778 | N
28/08/2016 | 07:30 | ZN263:PA31 32GHJ | CBD | Planned |  | 3 | 450 | 0.043485 | 0.0096634 | N
28/08/2016 | 22:50 | ZN9037:PA17 | URBAN | Planned |  | 32 | 4,660 | 0.10298 | 0.0022099 | N
29/08/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 6 | 480 | 0.0019889 | 0.00041436 | N
29/08/2016 | 07:30 | ZN1193:PA12 | URBAN | Planned |  | 14 | 410 | 0.0039641 | 0.00096684 | N
29/08/2016 | 07:30 | ZN3154:PA22 | SHORT RURAL | Planned |  | 10 | 500 | 0.022831 | 0.0045662 | N
29/08/2016 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 4 | 540 | 0.0098629 | 0.0018265 | N
29/08/2016 | 09:30 | ZN9118:PA6 | URBAN | Planned |  | 31 | 300 | 0.0064226 | 0.0021409 | N
30/08/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 74 | 480 | 0.024531 | 0.0051105 | N
30/08/2016 | 07:30 | ZN2466:PA22 | URBAN | Planned |  | 2 | 390 | 0.00053868 | 0.00013812 | N
30/08/2016 | 08:00 | ZN2466:PA31 | URBAN | Planned |  | 3 | 70 | 0.00014503 | 0.00020718 | N
30/08/2016 | 08:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 3 | 480 | 0.0065753 | 0.0013699 | N
30/08/2016 | 08:00 | ZN14892:PA5 | URBAN | Planned |  | 1 | 540 | 0.00037293 | 6.9061e-05 | N
30/08/2016 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 15 | 480 | 0.032876 | 0.0068493 | N
30/08/2016 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 24 | 480 | 0.052602 | 0.010959 | N
30/08/2016 | 08:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 46 | 480 | 0.10082 | 0.021004 | N
06/09/2016 | 08:00 | 243:80081 | SHORT RURAL | Planned |  | 147 | 300 | 0.20131 | 0.067102 | N
06/09/2016 | 08:40 | 814:82285 | SHORT RURAL | Planned |  | 16 | 119 | 0.0086913 | 0.0073036 | N
06/09/2016 | 08:55 | 526:34640 | SHORT RURAL | Planned |  | 15 | 225 | 0.015406 | 0.0068472 | N
06/09/2016 | 08:50 | 508:82579 | SHORT RURAL | Planned |  | 8 | 315 | 0.011503 | 0.0036518 | N
06/09/2016 | 07:45 | 504:48028 | URBAN | Planned |  | 1 | 450 | 0.00031069 | 6.9042e-05 | N
06/09/2016 | 13:30 | 526:34636 | SHORT RURAL | Planned |  | 1 | 60 | 0.00027389 | 0.00045648 | N
06/09/2016 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 2 | 100 | 0.00091295 | 0.00091295 | N
06/09/2016 | 08:35 | 801:74123 | SHORT RURAL | Planned |  | 1 | 160 | 0.00073036 | 0.00045648 | N
06/09/2016 | 08:45 | 801:74123 | SHORT RURAL | Planned |  | 2 | 180 | 0.0016433 | 0.00091295 | N
06/09/2016 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 2 | 355 | 0.25321 | 0.071327 | N
06/09/2016 | 13:03 | 801:74123 | SHORT RURAL | Planned |  | 1 | 57 | 0.00026019 | 0.00045648 | N
07/09/2016 | 09:30 | 224:80332 | URBAN | Planned |  | 67 | 297 | 0.013739 | 0.0046259 | N
07/09/2016 | 08:00 | 233:82812 | SHORT RURAL | Planned |  | 5 | 470 | 0.010727 | 0.0022824 | N
07/09/2016 | 08:30 | 511:29876 | SHORT RURAL | Planned |  | 3 | 325 | 0.0044507 | 0.0013694 | N
07/09/2016 | 08:00 | 238:34141 | SHORT RURAL | Planned |  | 9 | 420 | 0.017255 | 0.0041083 | N
07/09/2016 | 09:00 | 814:82291 | SHORT RURAL | Planned |  | 3 | 145 | 0.0019857 | 0.0013694 | N
08/09/2016 | 08:30 | 224:80332 | URBAN | Planned |  | 59 | 255 | 0.01039 | 0.0040744 | N
08/09/2016 | 08:10 | 258:80790 | URBAN | Planned |  | 218 | 447 | 0.067294 | 0.015055 | N
08/09/2016 | 14:10 | 258:80790 | URBAN | Planned |  | 66 | 87 | 0.0039653 | 0.0045578 | N
08/09/2016 | 08:30 | 507:80922 | SHORT RURAL | Planned |  | 51 | 390 | 0.090402 | 0.02318 | N
08/09/2016 | 08:45 | 511:29878 | SHORT RURAL | Planned |  | 46 | 435 | 0.090947 | 0.020907 | N
08/09/2016 | 08:00 | 264:81244 | SHORT RURAL | Planned |  | 72 | 565 | 0.18489 | 0.032725 | N
08/09/2016 | 08:51 | 264:81240 | SHORT RURAL | Planned |  | 4 | 344 | 0.006254 | 0.001818 | N
08/09/2016 | 08:25 | 229:34995 | SHORT RURAL | Planned |  | 14 | 400 | 0.025452 | 0.0063631 | N
08/09/2016 | 08:30 | 523:33509 | URBAN | Planned |  | 57 | 200 | 0.0078726 | 0.0039363 | N
08/09/2016 | 08:30 | 515:35200 | URBAN | Planned |  | 4 | 185 | 0.00051103 | 0.00027623 | N
09/09/2016 | 08:30 | 238:34150 | SHORT RURAL | Planned |  | 52 | 400 | 0.094538 | 0.023634 | N
09/09/2016 | 05:10 | 238:34136 | URBAN | Planned |  | 39 | 95 | 0.0025586 | 0.0026933 | N
09/09/2016 | 08:00 | 228:7490 | SHORT RURAL | Planned |  | 39 | 320 | 0.056723 | 0.017726 | N
09/09/2016 | 08:30 | 264:81240 | SHORT RURAL | Planned |  | 5 | 250 | 0.0056814 | 0.0022725 | N
09/09/2016 | 12:15 | 507:80926 | URBAN | Planned |  | 1 | 140 | 9.6681e-05 | 6.9058e-05 | N
09/09/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 10 | 255 | 0.91006 | 0.35689 | N
09/09/2016 | 08:30 | 516:48067 | SHORT RURAL | Planned |  | 8 | 358 | 0.013017 | 0.0036361 | N
12/09/2016 | 07:40 | 243:80083 | SHORT RURAL | Planned |  | 30 | 515 | 0.070221 | 0.013635 | N
12/09/2016 | 08:30 | 508:82578 | SHORT RURAL | Planned |  | 35 | 370 | 0.058858 | 0.015908 | N
12/09/2016 | 08:35 | 230:81434 | URBAN | Planned |  | 73 | 135 | 0.0068061 | 0.0050415 | N
12/09/2016 | 08:10 | 509:33395 | LONG RURAL | Planned |  | 43 | 255 | 3.9133 | 1.5346 | N
12/09/2016 | 08:30 | 513:48052 | URBAN | Planned |  | 79 | 274 | 0.014949 | 0.0054559 | N
12/09/2016 | 08:44 | 814:82285 | SHORT RURAL | Planned |  | 14 | 201 | 0.01279 | 0.0063631 | N
13/09/2016 | 09:00 | 227:13015 | SHORT RURAL | Planned |  | 62 | 155 | 0.043678 | 0.02818 | N
13/09/2016 | 08:30 | 507:80922 | SHORT RURAL | Planned |  | 16 | 363 | 0.026398 | 0.0072721 | N
13/09/2016 | 08:45 | 508:82579 | SHORT RURAL | Planned |  | 7 | 365 | 0.011613 | 0.0031816 | N
13/09/2016 | 09:30 | 230:81432 | SHORT RURAL | Planned |  | 61 | 225 | 0.062381 | 0.027725 | N
13/09/2016 | 08:30 | 235:2120 | SHORT RURAL | Planned |  | 2 | 390 | 0.0035452 | 0.00090902 | N
13/09/2016 | 08:50 | 508:82579 | SHORT RURAL | Planned |  | 2 | 137 | 0.0012454 | 0.00090902 | N
13/09/2016 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 5 | 85 | 0.0019317 | 0.0022725 | N
13/09/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 2 | 225 | 0.1606 | 0.071378 | N
13/09/2016 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 74 | 335 | 0.11267 | 0.033634 | N
13/09/2016 | 10:05 | 812:19071 | SHORT RURAL | Planned |  | 4 | 240 | 0.0043633 | 0.001818 | N
14/09/2016 | 09:50 | 229:34995 | SHORT RURAL | Planned |  | 8 | 340 | 0.012363 | 0.0036361 | N
14/09/2016 | 21:10 | 229:34995 | SHORT RURAL | Planned |  | 8 | 395 | 0.014362 | 0.0036361 | N
15/09/2016 | 09:00 | 264:81244 | SHORT RURAL | Planned |  | 55 | 140 | 0.034985 | 0.024989 | N
19/09/2016 | 08:39 | ZN2466:PA16 | URBAN | Planned |  | 1 | 50 | 3.4325e-05 | 6.9064e-05 | N
18/09/2016 | 07:30 | 214:8671 | URBAN | Planned |  | 28 | 730 | 0.014117 | 0.0019338 | N
15/09/2016 | 08:10 | 223:14395 | SHORT RURAL | Planned |  | 7 | 435 | 0.013835 | 0.0031804 | N
15/09/2016 | 08:15 | 223:14397 | URBAN | Planned |  | 46 | 155 | 0.0049234 | 0.0031764 | N
16/09/2016 | 07:50 | 227:13015 | SHORT RURAL | Planned |  | 54 | 490 | 0.12022 | 0.024535 | N
18/09/2016 | 08:00 | 240:34849 | SHORT RURAL | Planned |  | 61 | 410 | 0.11355 | 0.027696 | N
15/09/2016 | 21:10 | 229:34995 | SHORT RURAL | Planned |  | 8 | 395 | 0.014357 | 0.0036348 | N
15/09/2016 | 09:20 | 264:81244 | SHORT RURAL | Planned |  | 4 | 125 | 0.0022717 | 0.0018174 | N
15/09/2016 | 12:00 | 528:83024 | URBAN | Planned |  | 1 | 130 | 8.9768e-05 | 6.9052e-05 | N
15/09/2016 | 17:00 | 511:29872 | URBAN | Planned |  | 9 | 240 | 0.0014915 | 0.00062147 | N
16/09/2016 | 08:15 | 229:34989 | SHORT RURAL | Planned |  | 13 | 305 | 0.018015 | 0.0059065 | N
16/09/2016 | 08:15 | 229:34983 | SHORT RURAL | Planned |  | 1 | 305 | 0.0013858 | 0.00045435 | N
16/09/2016 | 07:50 | 229:34989 | SHORT RURAL | Planned |  | 1 | 440 | 0.0019991 | 0.00045435 | N
16/09/2016 | 09:20 | 238:34141 | SHORT RURAL | Planned |  | 4 | 200 | 0.0036348 | 0.0018174 | N
16/09/2016 | 08:25 | 504:48033 | SHORT RURAL | Planned |  | 140 | 270 | 0.17174 | 0.063608 | N
16/09/2016 | 08:00 | 238:34150 | SHORT RURAL | Planned |  | 11 | 630 | 0.031486 | 0.0049978 | N
16/09/2016 | 09:15 | 238:34141 | SHORT RURAL | Planned |  | 2 | 113 | 0.0010268 | 0.00090869 | N
16/09/2016 | 13:00 | 532:83298 | URBAN | Planned |  | 2 | 1,035 | 0.0014294 | 0.0001381 | N
15/09/2016 | 09:00 | 513:48057 | URBAN | Planned |  | 21 | 205 | 0.0029727 | 0.0014501 | N
15/09/2016 | 08:15 | 515:35193 | SHORT RURAL | Planned |  | 1 | 190 | 0.00086326 | 0.00045435 | N
16/09/2016 | 09:15 | 514:18137 | SHORT RURAL | Planned |  | 1 | 105 | 0.00047706 | 0.00045435 | N
16/09/2016 | 08:43 | 807:74179 | SHORT RURAL | Planned |  | 8 | 244 | 0.0088688 | 0.0036348 | N
19/09/2016 | 08:10 | 502:48010 | SHORT RURAL | Planned |  | 49 | 375 | 0.083429 | 0.022248 | N
19/09/2016 | 09:00 | 227:13019 | SHORT RURAL | Planned |  | 9 | 255 | 0.01042 | 0.0040863 | N
19/09/2016 | 10:05 | 257:81999 | URBAN | Planned |  | 11 | 140 | 0.0010636 | 0.00075971 | N
20/09/2016 | 10:30 | 216:10728 | SHORT RURAL | Planned |  | 120 | 200 | 0.10897 | 0.054484 | N
20/09/2016 | 09:13 | 223:14393 | URBAN | Planned |  | 114 | 197 | 0.015511 | 0.0078735 | N
20/09/2016 | 08:15 | 261:81885 | URBAN | Planned |  | 39 | 365 | 0.0098315 | 0.0026935 | N
20/09/2016 | 08:35 | 508:82579 | SHORT RURAL | Planned |  | 2 | 315 | 0.0028604 | 0.00090807 | N
20/09/2016 | 09:00 | 233:82812 | SHORT RURAL | Planned |  | 6 | 330 | 0.0089899 | 0.0027242 | N
20/09/2016 | 08:35 | 807:74184 | SHORT RURAL | Planned |  | 6 | 295 | 0.0080364 | 0.0027242 | N
20/09/2016 | 09:25 | 813:89061 | LONG RURAL | Planned |  | 6 | 110 | 0.23546 | 0.21406 | N
21/09/2016 | 09:00 | 243:80083 | SHORT RURAL | Planned |  | 2 | 390 | 0.0035415 | 0.00090808 | N
21/09/2016 | 09:45 | 232:11455 | SHORT RURAL | Planned |  | 54 | 290 | 0.071102 | 0.024518 | N
22/09/2016 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 53 | 295 | 5.578 | 1.8908 | N
22/09/2016 | 07:30 | 227:13015 | SHORT RURAL | Planned |  | 140 | 498 | 0.31647 | 0.063548 | N
22/09/2016 | 08:30 | 214:8670 | URBAN | Planned |  | 45 | 200 | 0.0062141 | 0.003107 | N
22/09/2016 | 08:05 | 528:83014 | SHORT RURAL | Planned |  | 35 | 430 | 0.068314 | 0.015887 | N
22/09/2016 | 08:30 | 238:34141 | SHORT RURAL | Planned |  | 4 | 160 | 0.002905 | 0.0018156 | N
22/09/2016 | 12:45 | 264:81244 | SHORT RURAL | Planned |  | 7 | 44 | 0.001398 | 0.0031774 | N
22/09/2016 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 3 | 155 | 0.16589 | 0.10703 | N
22/09/2016 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 205 | 0.073136 | 0.035676 | N
22/09/2016 | 13:45 | 813:89061 | LONG RURAL | Planned |  | 3 | 145 | 0.15519 | 0.10703 | N
23/09/2016 | 08:00 | 243:80083 | SHORT RURAL | Planned |  | 15 | 315 | 0.021447 | 0.0068087 | N
23/09/2016 | 09:30 | 511:29878 | SHORT RURAL | Planned |  | 3 | 80 | 0.0010894 | 0.0013617 | N
23/09/2016 | 08:45 | 507:80922 | SHORT RURAL | Planned |  | 51 | 425 | 0.098385 | 0.02315 | N
23/09/2016 | 13:10 | 526:34640 | SHORT RURAL | Planned |  | 2 | 23 | 0.0002088 | 0.00090782 | N
23/09/2016 | 09:05 | 504:48033 | SHORT RURAL | Planned |  | 3 | 170 | 0.002315 | 0.0013617 | N
23/09/2016 | 08:45 | 238:34148 | SHORT RURAL | Planned |  | 16 | 285 | 0.020698 | 0.0072626 | N
26/09/2016 | 08:50 | 513:48050 | SHORT RURAL | Planned |  | 21 | 130 | 0.012392 | 0.0095323 | N
26/09/2016 | 08:00 | 224:80337 | SHORT RURAL | Planned |  | 22 | 694 | 0.069305 | 0.0099862 | N
26/09/2016 | 08:00 | 532:83293 | URBAN | Planned |  | 95 | 135 | 0.0088552 | 0.0065594 | N
26/09/2016 | 08:55 | 230:81432 | SHORT RURAL | Planned |  | 61 | 275 | 0.076145 | 0.027689 | N
26/09/2016 | 11:15 | 532:83293 | URBAN | Planned |  | 70 | 245 | 0.011841 | 0.0048332 | N
26/09/2016 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 11 | 145 | 0.00724 | 0.0049931 | N
27/09/2016 | 08:55 | 227:13020 | SHORT RURAL | Planned |  | 166 | 360 | 0.27124 | 0.075344 | N
27/09/2016 | 08:55 | 223:14397 | URBAN | Planned |  | 132 | 333 | 0.03035 | 0.0091142 | N
27/09/2016 | 08:55 | 223:14397 | URBAN | Planned |  | 75 | 205 | 0.010616 | 0.0051785 | N
27/09/2016 | 10:00 | 224:80328 | SHORT RURAL | Planned |  | 12 | 375 | 0.020425 | 0.0054466 | N
27/09/2016 | 08:30 | 528:83019 | SHORT RURAL | Planned |  | 171 | 450 | 0.34926 | 0.077614 | N
27/09/2016 | 09:00 | 504:48033 | SHORT RURAL | Planned |  | 100 | 430 | 0.19517 | 0.045388 | N
27/09/2016 | 09:15 | 232:33407 | SHORT RURAL | Planned |  | 2 | 135 | 0.0012255 | 0.00090776 | N
27/09/2016 | 17:40 | 511:29872 | URBAN | Planned |  | 8 | 215 | 0.0011876 | 0.00055238 | N
27/09/2016 | 08:45 | 514:18137 | SHORT RURAL | Planned |  | 2 | 110 | 0.00099854 | 0.00090776 | N
27/09/2016 | 13:15 | 514:18137 | SHORT RURAL | Planned |  | 1 | 70 | 0.00031772 | 0.00045388 | N
01/09/2016 | 08:50 | ZN12630:PA23 | SHORT RURAL | Planned |  | 45 | 390 | 0.080111 | 0.020541 | N
01/09/2016 | 08:30 | ZN180:PA23 | URBAN | Planned |  | 179 | 360 | 0.044489 | 0.012358 | N
02/09/2016 | 21:00 | ZN80:PA22 | URBAN | Planned |  | 48 | 360 | 0.01193 | 0.0033139 | N
03/09/2016 | 06:30 | ZN15005:PA4 | URBAN | Planned |  | 1 | 265 | 0.00018296 | 6.9041e-05 | N
03/09/2016 | 07:00 | ZN1600:PA23DEF | CBD | Planned |  | 30 | 30 | 0.029011 | 0.096702 | N
03/09/2016 | 08:30 | ZN9035:PA8 | URBAN | Planned |  | 9 | 300 | 0.0018641 | 0.00062137 | N
03/09/2016 | 17:00 | ZN3288:PA45 46KLM | CBD | Planned |  | 20 | 720 | 0.46417 | 0.064468 | N
03/09/2016 | 19:40 | ZN4990:PA51 52GHJ | CBD | Planned |  | 25 | 350 | 0.28205 | 0.080585 | N
04/09/2016 | 12:45 | ZN188:PA20 | URBAN | Planned |  | 7 | 225 | 0.0010874 | 0.00048329 | N
04/09/2016 | 22:00 | ZN10999:PA3 | URBAN | Planned |  | 19 | 480 | 0.0062966 | 0.0013118 | N
05/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 46 | 480 | 0.015244 | 0.0031759 | N
05/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 81 | 480 | 0.026843 | 0.0055924 | N
05/09/2016 | 07:30 | ZN9252:PA24 | URBAN | Planned |  | 1 | 480 | 0.0003314 | 6.9042e-05 | N
05/09/2016 | 08:00 | ZN36800:PA57 | URBAN | Planned |  | 93 | 375 | 0.024078 | 0.0064209 | N
05/09/2016 | 08:30 | ZN342:PA23 | URBAN | Planned |  | 76 | 100 | 0.0052472 | 0.0052472 | N
05/09/2016 | 09:45 | ZN12570:PA37 | SHORT RURAL | Planned |  | 7 | 315 | 0.010065 | 0.0031954 | N
05/09/2016 | 09:00 | ZN12570:PA25 | SHORT RURAL | Planned |  | 68 | 390 | 0.12106 | 0.031041 | N
05/09/2016 | 19:30 | ZN2835:PA30 | URBAN | Planned |  | 48 | 450 | 0.014913 | 0.003314 | N
05/09/2016 | 22:00 | ZN10999:PA3 | URBAN | Planned |  | 19 | 510 | 0.0066901 | 0.0013118 | N
06/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 22 | 480 | 0.0072909 | 0.0015189 | N
06/09/2016 | 07:30 | ZN262:PA19 | URBAN | Planned |  | 91 | 435 | 0.02733 | 0.0062828 | N
06/09/2016 | 08:40 | ZN14891:PA5 | SHORT RURAL | Planned |  | 23 | 425 | 0.044621 | 0.010499 | N
06/09/2016 | 08:10 | ZN14891:PA12 | SHORT RURAL | Planned |  | 19 | 510 | 0.044233 | 0.0086731 | N
06/09/2016 | 08:30 | ZN9900:PA5 | URBAN | Planned |  | 30 | 325 | 0.0067316 | 0.0020713 | N
06/09/2016 | 08:30 | ZN35500:PA35 | URBAN | Planned |  | 5 | 360 | 0.0012428 | 0.00034521 | N
06/09/2016 | 04:00 | ZN12650:PA2 | URBAN | Planned |  | 1 | 630 | 0.00043497 | 6.9042e-05 | N
06/09/2016 | 09:00 | ZN342:PA23 | URBAN | Planned |  | 103 | 180 | 0.0128 | 0.0071113 | N
06/09/2016 | 23:50 | ZN8700:PA63 64GHJ | CBD | Planned |  | 36 | 250 | 0.29013 | 0.11605 | N
07/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 48 | 480 | 0.015907 | 0.0033141 | N
07/09/2016 | 07:30 | ZN2835:PA33 | URBAN | Planned |  | 105 | 450 | 0.032623 | 0.0072495 | N
07/09/2016 | 08:30 | ZN9900:PA5 | URBAN | Planned |  | 11 | 180 | 0.0013671 | 0.00075947 | N
07/09/2016 | 11:59 | ZN342:PA16 | URBAN | Planned |  | 164 | 2 | 0.00022646 | 0.011323 | N
08/09/2016 | 07:30 | ZN2466:PA16 | URBAN | Planned |  | 12 | 240 | 0.0019889 | 0.00082869 | N
08/09/2016 | 07:30 | ZN14143:PA12 | SHORT RURAL | Planned |  | 3 | 475 | 0.0064767 | 0.0013635 | N
08/09/2016 | 09:20 | ZN14891:PA5 | SHORT RURAL | Planned |  | 22 | 490 | 0.048996 | 0.0099992 | N
08/09/2016 | 08:00 | ZN35900:PA23 | SHORT RURAL | Planned |  | 111 | 540 | 0.27243 | 0.05045 | N
08/09/2016 | 08:00 | ZN9245:PA42 | URBAN | Planned |  | 27 | 510 | 0.0095093 | 0.0018646 | N
08/09/2016 | 10:05 | ZN12580:PA8 | URBAN | Planned |  | 80 | 285 | 0.015745 | 0.0055246 | N
10/09/2016 | 03:50 | ZN263:PA35 37GHJ | CBD | Planned |  | 27 | 865 | 0.75268 | 0.087015 | N
10/09/2016 | 06:30 | ZN10993:PA35 | URBAN | Planned |  | 1 | 600 | 0.00041436 | 6.9061e-05 | N
10/09/2016 | 15:00 | ZN690:PA6 | URBAN | Planned |  | 1 | 5 | 3.453e-06 | 6.9061e-05 | N
10/09/2016 | 15:10 | ZN690:PA6 | URBAN | Planned |  | 1 | 5 | 3.453e-06 | 6.9061e-05 | N
10/09/2016 | 15:20 | ZN690:PA5 | URBAN | Planned |  | 1 | 5 | 3.453e-06 | 6.9061e-05 | N
10/09/2016 | 15:30 | ZN690:PA5 | URBAN | Planned |  | 1 | 5 | 3.453e-06 | 6.9061e-05 | N
11/09/2016 | 01:10 | ZN263:PA31 32ABC | CBD | Planned |  | 67 | 680 | 1.4683 | 0.21593 | N
11/09/2016 | 08:00 | ZN2466:PA39 | URBAN | Planned |  | 2 | 570 | 0.00078731 | 0.00013812 | N
12/09/2016 | 07:00 | ZN12690:PA10 | URBAN | Planned |  | 1 | 630 | 0.00043509 | 6.9062e-05 | N
12/09/2016 | 07:30 | ZN35800:PA16 | URBAN | Planned |  | 1 | 450 | 0.00031078 | 6.9062e-05 | N
12/09/2016 | 07:30 | ZN15013:PA10 | SHORT RURAL | Planned |  | 6 | 450 | 0.012272 | 0.002727 | N
12/09/2016 | 08:05 | ZN12620:PA1 | SHORT RURAL | Planned |  | 17 | 350 | 0.027043 | 0.0077266 | N
12/09/2016 | 08:00 | ZN12630:PA24 | SHORT RURAL | Planned |  | 6 | 480 | 0.01309 | 0.002727 | N
12/09/2016 | 08:00 | ZN14143:PA5 | URBAN | Planned |  | 4 | 215 | 0.00059393 | 0.00027625 | N
12/09/2016 | 14:30 | ZN14143:PA5 | URBAN | Planned |  | 3 | 90 | 0.00018647 | 0.00020719 | N
12/09/2016 | 21:30 | ZN931:PA24 | URBAN | Planned |  | 5 | 725 | 0.0025035 | 0.00034531 | N
13/09/2016 | 04:10 | ZN12620:PA13 | SHORT RURAL | Planned |  | 175 | 50 | 0.039769 | 0.079539 | N
13/09/2016 | 08:40 | ZN874:PA16 | URBAN | Planned |  | 45 | 200 | 0.0062158 | 0.0031079 | N
13/09/2016 | 07:30 | ZN14891:PA16 | SHORT RURAL | Planned |  | 6 | 240 | 0.0065449 | 0.002727 | N
13/09/2016 | 08:00 | ZN12630:PA22 | SHORT RURAL | Planned |  | 279 | 496 | 0.62897 | 0.12681 | N
13/09/2016 | 08:30 | ZN12630:PA22 | SHORT RURAL | Planned |  | 11 | 490 | 0.024498 | 0.0049996 | N
13/09/2016 | 08:30 | ZN9900:PA5 | URBAN | Planned |  | 19 | 330 | 0.0043303 | 0.0013122 | N
13/09/2016 | 10:30 | ZN36300:PA5 | URBAN | Planned |  | 19 | 300 | 0.0039366 | 0.0013122 | N
13/09/2016 | 21:30 | ZN931:PA24 | URBAN | Planned |  | 5 | 725 | 0.0025036 | 0.00034532 | N
14/09/2016 | 04:10 | ZN12620:PA13 | SHORT RURAL | Planned |  | 175 | 50 | 0.039769 | 0.079539 | N
14/09/2016 | 07:30 | ZN874:PA4 | URBAN | Planned |  | 4 | 630 | 0.0017405 | 0.00027626 | N
14/09/2016 | 07:30 | ZN931:PA25 | URBAN | Planned |  | 82 | 450 | 0.025485 | 0.0056634 | N
14/09/2016 | 09:25 | ZN12630:PA22 | SHORT RURAL | Planned |  | 7 | 425 | 0.013522 | 0.0031816 | N
14/09/2016 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 6 | 240 | 0.0065449 | 0.002727 | N
14/09/2016 | 08:30 | ZN9700:PA11 | URBAN | Planned |  | 42 | 390 | 0.011313 | 0.0029008 | N
14/09/2016 | 08:30 | ZN9900:PA5 | URBAN | Planned |  | 26 | 330 | 0.0059258 | 0.0017957 | N
14/09/2016 | 09:00 | ZN14891:PA17 | SHORT RURAL | Planned |  | 32 | 300 | 0.043633 | 0.014544 | N
14/09/2016 | 15:00 | ZN12620:PA1 | SHORT RURAL | Planned |  | 155 | 25 | 0.017612 | 0.070449 | N
15/09/2016 | 08:30 | ZN965:PA28 | URBAN | Planned |  | 52 | 225 | 0.0080791 | 0.0035907 | N
15/09/2016 | 21:00 | ZN262:PA30 | URBAN | Planned |  | 50 | 390 | 0.013465 | 0.0034526 | N
16/09/2016 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 8 | 320 | 0.011631 | 0.0036348 | N
16/09/2016 | 08:15 | ZN14144:PA10 | SHORT RURAL | Planned |  | 39 | 285 | 0.0505 | 0.017719 | N
16/09/2016 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 1 | 302 | 0.0013721 | 0.00045435 | N
16/09/2016 | 09:30 | ZN12630:PA23 | SHORT RURAL | Planned |  | 10 | 125 | 0.0056793 | 0.0045435 | N
16/09/2016 | 19:00 | ZN15001:PA3 | URBAN | Planned |  | 2 | 540 | 0.00074576 | 0.0001381 | N
17/09/2016 | 07:50 | ZN263:PA33 34KLM | CBD | Planned |  | 2 | 280 | 0.01805 | 0.0064464 | N
17/09/2016 | 12:30 | ZN14143:PA8 | URBAN | Planned |  | 1 | 150 | 0.00010359 | 6.9062e-05 | N
18/09/2016 | 08:00 | ZN2466:PA39 | URBAN | Planned |  | 2 | 515 | 0.00071136 | 0.00013813 | N
19/09/2016 | 07:10 | ZN9900:PA9 | URBAN | Planned |  | 118 | 495 | 0.04034 | 0.0081496 | N
19/09/2016 | 07:45 | ZN1850:PA10 | URBAN | Planned |  | 1 | 620 | 0.0004282 | 6.9064e-05 | N
19/09/2016 | 07:45 | ZN1850:PA10 | URBAN | Planned |  | 40 | 620 | 0.017128 | 0.0027626 | N
19/09/2016 | 07:30 | ZN342:PA28 | URBAN | Planned |  | 80 | 540 | 0.029836 | 0.0055251 | N
19/09/2016 | 10:30 | ZN36200:PA8 | SHORT RURAL | Planned |  | 228 | 330 | 0.34161 | 0.10352 | N
19/09/2016 | 07:45 | ZN1850:PA10 | URBAN | Planned |  | 41 | 620 | 0.017556 | 0.0028316 | N
19/09/2016 | 08:40 | ZN9900:PA5 | URBAN | Planned |  | 14 | 290 | 0.002804 | 0.0009669 | N
19/09/2016 | 08:30 | ZN1193:PA15 | URBAN | Planned |  | 108 | 390 | 0.02909 | 0.0074589 | N
19/09/2016 | 10:25 | ZN15006:PA16 | URBAN | Planned |  | 1 | 65 | 4.4892e-05 | 6.9064e-05 | N
19/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 127 | 10 | 0.0057662 | 0.057662 | N
20/09/2016 | 20:00 | ZN7481:PA1 | URBAN | Planned |  | 3 | 500 | 0.001036 | 0.0002072 | N
04/10/2016 | 09:00 | 807:74179 | SHORT RURAL | Planned |  | 53 | 160 | 0.038387 | 0.023992 | N
30/09/2016 | 08:30 | 528:83014 | SHORT RURAL | Planned |  | 109 | 220 | 0.10881 | 0.049461 | N
30/09/2016 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 6 | 255 | 0.0069426 | 0.0027226 | N
30/09/2016 | 08:30 | 814:82283 | SHORT RURAL | Planned |  | 6 | 260 | 0.0070788 | 0.0027226 | N
28/09/2016 | 09:00 | 225:33676 | URBAN | Planned |  | 141 | 485 | 0.047219 | 0.0097358 | N
30/09/2016 | 08:30 | 227:13019 | SHORT RURAL | Planned |  | 10 | 250 | 0.011344 | 0.0045377 | N
30/09/2016 | 08:30 | 214:8665 | URBAN | Planned |  | 202 | 410 | 0.057169 | 0.013944 | N
28/09/2016 | 09:12 | 232:11460 | URBAN | Planned |  | 1 | 176 | 0.00012153 | 6.9049e-05 | N
28/09/2016 | 09:55 | 238:34141 | SHORT RURAL | Planned |  | 48 | 345 | 0.075163 | 0.021786 | N
28/09/2016 | 08:00 | 532:83314 | URBAN | Planned |  | 42 | 370 | 0.01073 | 0.0029 | N
28/09/2016 | 09:25 | 532:83298 | URBAN | Planned |  | 139 | 235 | 0.022555 | 0.0095978 | N
28/09/2016 | 14:05 | 229:34992 | SHORT RURAL | Planned |  | 1 | 115 | 0.00052197 | 0.00045388 | N
28/09/2016 | 17:50 | 528:83024 | URBAN | Planned |  | 10 | 140 | 0.00096668 | 0.00069049 | N
29/09/2016 | 08:00 | 235:2124 | SHORT RURAL | Planned |  | 67 | 215 | 0.065365 | 0.030402 | N
29/09/2016 | 09:10 | 508:82578 | SHORT RURAL | Planned |  | 30 | 350 | 0.047646 | 0.013613 | N
29/09/2016 | 08:53 | 265:81651 | SHORT RURAL | Planned |  | 9 | 110 | 0.0044923 | 0.0040839 | N
29/09/2016 | 08:15 | 228:7490 | SHORT RURAL | Planned |  | 302 | 545 | 0.74686 | 0.13704 | N
29/09/2016 | 09:05 | 507:80923 | SHORT RURAL | Planned |  | 11 | 400 | 0.019966 | 0.0049914 | N
29/09/2016 | 09:55 | 504:48031 | SHORT RURAL | Planned |  | 2 | 55 | 0.00049914 | 0.00090754 | N
30/09/2016 | 08:40 | 512:48048 | SHORT RURAL | Planned |  | 2 | 125 | 0.0011344 | 0.00090754 | N
30/09/2016 | 10:00 | 511:29876 | SHORT RURAL | Planned |  | 3 | 190 | 0.0025865 | 0.0013613 | N
30/09/2016 | 10:15 | 265:81651 | SHORT RURAL | Planned |  | 20 | 155 | 0.014067 | 0.0090754 | N
30/09/2016 | 09:45 | 509:33395 | LONG RURAL | Planned |  | 1 | 320 | 0.1142 | 0.035689 | N
30/09/2016 | 08:13 | 504:48034 | URBAN | Planned |  | 235 | 340 | 0.055153 | 0.016222 | N
28/09/2016 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 4 | 205 | 0.0037218 | 0.0018155 | N
28/09/2016 | 09:40 | 807:74181 | SHORT RURAL | Planned |  | 4 | 50 | 0.00090777 | 0.0018155 | N
28/09/2016 | 10:10 | 514:18137 | SHORT RURAL | Planned |  | 1 | 105 | 0.00047658 | 0.00045388 | N
29/09/2016 | 08:45 | 516:48067 | SHORT RURAL | Planned |  | 1 | 60 | 0.00027226 | 0.00045377 | N
29/09/2016 | 08:30 | 513:48051 | URBAN | Planned |  | 154 | 350 | 0.037206 | 0.01063 | N
30/09/2016 | 09:00 | 806:82662 | SHORT RURAL | Planned |  | 16 | 180 | 0.013069 | 0.0072603 | N
30/09/2016 | 08:50 | 813:89065 | URBAN | Planned |  | 12 | 95 | 0.00078692 | 0.00082834 | N
30/09/2016 | 09:30 | 814:82283 | SHORT RURAL | Planned |  | 1 | 170 | 0.00077141 | 0.00045377 | N
04/10/2016 | 06:35 | 213:33773 | URBAN | Planned |  | 19 | 375 | 0.0049205 | 0.0013121 | N
04/10/2016 | 07:30 | 239:82127 | SHORT RURAL | Planned |  | 84 | 475 | 0.18062 | 0.038025 | N
04/10/2016 | 08:30 | 227:13019 | SHORT RURAL | Planned |  | 10 | 350 | 0.015844 | 0.0045268 | N
04/10/2016 | 08:38 | 227:13019 | SHORT RURAL | Planned |  | 7 | 457 | 0.014481 | 0.0031688 | N
04/10/2016 | 09:35 | 507:80925 | SHORT RURAL | Planned |  | 4 | 175 | 0.0031688 | 0.0018107 | N
04/10/2016 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 6 | 315 | 0.0085557 | 0.0027161 | N
04/10/2016 | 10:15 | 232:11453 | SHORT RURAL | Planned |  | 45 | 105 | 0.021389 | 0.020371 | N
04/10/2016 | 12:45 | 232:33409 | SHORT RURAL | Planned |  | 58 | 70 | 0.018379 | 0.026256 | N
04/10/2016 | 09:25 | 802:82225 | SHORT RURAL | Planned |  | 2 | 20 | 0.00018107 | 0.00090536 | N
04/10/2016 | 08:30 | 512:48046 | SHORT RURAL | Planned |  | 100 | 390 | 0.17655 | 0.045268 | N
05/10/2016 | 08:30 | 202:34261 | URBAN | Planned |  | 84 | 410 | 0.023785 | 0.0058011 | N
05/10/2016 | 08:45 | 222:33601 | SHORT RURAL | Planned |  | 6 | 400 | 0.010864 | 0.0027161 | N
05/10/2016 | 09:30 | 507:80925 | SHORT RURAL | Planned |  | 17 | 150 | 0.011543 | 0.0076956 | N
05/10/2016 | 07:10 | 532:83309 | SHORT RURAL | Planned |  | 4 | 500 | 0.0090537 | 0.0018107 | N
05/10/2016 | 08:31 | 514:18137 | SHORT RURAL | Planned |  | 2 | 54 | 0.0004889 | 0.00090537 | N
05/10/2016 | 09:00 | 812:19066 | SHORT RURAL | Planned |  | 70 | 215 | 0.068129 | 0.031688 | N
05/10/2016 | 08:50 | 807:74183 | SHORT RURAL | Planned |  | 7 | 220 | 0.0069713 | 0.0031688 | N
05/10/2016 | 09:50 | 514:18137 | SHORT RURAL | Planned |  | 1 | 108 | 0.0004889 | 0.00045268 | N
05/10/2016 | 10:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 220 | 0.078515 | 0.035689 | N
05/10/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 7 | 240 | 0.0076051 | 0.0031688 | N
06/10/2016 | 08:30 | 265:81651 | SHORT RURAL | Planned |  | 69 | 405 | 0.1265 | 0.031236 | N
06/10/2016 | 10:40 | 258:80779 | URBAN | Planned |  | 364 | 310 | 0.07793 | 0.025139 | N
06/10/2016 | 08:48 | 206:34440 | URBAN | Planned |  | 99 | 297 | 0.020306 | 0.0068371 | N
06/10/2016 | 09:00 | 238:34150 | SHORT RURAL | Planned |  | 1 | 390 | 0.0017655 | 0.00045269 | N
06/10/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 47 | 428 | 0.091063 | 0.021276 | N
06/10/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 4 | 190 | 0.27123 | 0.14276 | N
06/10/2016 | 08:55 | 814:82283 | SHORT RURAL | Planned |  | 1 | 150 | 0.00067904 | 0.00045269 | N
06/10/2016 | 09:18 | 515:35197 | LONG RURAL | Planned |  | 22 | 217 | 1.7038 | 0.78515 | N
07/10/2016 | 08:30 | 265:81651 | SHORT RURAL | Planned |  | 14 | 420 | 0.02661 | 0.0063357 | N
10/10/2016 | 08:30 | 508:82579 | SHORT RURAL | Planned |  | 34 | 390 | 0.060007 | 0.015386 | N
10/10/2016 | 12:05 | 265:81649 | URBAN | Planned |  | 2 | 5 | 6.9086e-06 | 0.00013817 | N
10/10/2016 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 9 | 247 | 0.79336 | 0.3212 | N
07/10/2016 | 09:10 | 223:14395 | SHORT RURAL | Planned |  | 302 | 244 | 0.33348 | 0.13667 | N
10/10/2016 | 08:00 | 224:80332 | URBAN | Planned |  | 67 | 415 | 0.019209 | 0.0046288 | N
10/10/2016 | 17:10 | 202:34250 | URBAN | Planned |  | 103 | 290 | 0.020636 | 0.0071159 | N
07/10/2016 | 12:30 | 532:83298 | URBAN | Planned |  | 2 | 340 | 0.00046943 | 0.00013807 | N
07/10/2016 | 08:30 | 230:81432 | SHORT RURAL | Planned |  | 30 | 310 | 0.042087 | 0.013577 | N
07/10/2016 | 08:49 | 507:80931 | URBAN | Planned |  | 55 | 391 | 0.014846 | 0.0037969 | N
10/10/2016 | 07:10 | 532:83309 | SHORT RURAL | Planned |  | 4 | 595 | 0.01077 | 0.0018102 | N
10/10/2016 | 08:00 | 504:48031 | SHORT RURAL | Planned |  | 3 | 135 | 0.0018328 | 0.0013576 | N
07/10/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 3 | 210 | 0.22484 | 0.10707 | N
07/10/2016 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 3 | 200 | 0.21413 | 0.10707 | N
27/09/2016 | 07:54 | ZN1788:PA21 | URBAN | Planned |  | 1 | 400 | 0.00027619 | 6.9047e-05 | N
07/10/2016 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 22 | 390 | 0.038829 | 0.0099561 | N
10/10/2016 | 09:10 | 801:74121 | LONG RURAL | Planned |  | 1 | 240 | 0.085653 | 0.035689 | N
19/09/2016 | 23:30 | ZN847:PA36 | URBAN | Planned |  | 1 | 480 | 0.00033151 | 6.9064e-05 | N
20/09/2016 | 09:00 | ZN847:PA45 | SHORT RURAL | Planned |  | 11 | 450 | 0.022475 | 0.0049944 | N
20/09/2016 | 08:00 | ZN10995:PA6 | URBAN | Planned |  | 90 | 180 | 0.011189 | 0.0062159 | N
20/09/2016 | 08:05 | ZN14891:PA12 | SHORT RURAL | Planned |  | 51 | 445 | 0.10304 | 0.023156 | N
20/09/2016 | 09:00 | ZN10999:PA12 | URBAN | Planned |  | 86 | 330 | 0.019601 | 0.0059396 | N
20/09/2016 | 09:00 | ZN9900:PA1 | URBAN | Planned |  | 42 | 180 | 0.0052213 | 0.0029007 | N
20/09/2016 | 10:00 | ZN15014:PA20 | URBAN | Planned |  | 1 | 150 | 0.0001036 | 6.9065e-05 | N
20/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 75 | 30 | 0.010216 | 0.034053 | N
21/09/2016 | 07:30 | ZN874:PA25 | SHORT RURAL | Planned |  | 58 | 540 | 0.1422 | 0.026334 | N
21/09/2016 | 08:00 | ZN15010:PA9 | SHORT RURAL | Planned |  | 169 | 590 | 0.45272 | 0.076732 | N
21/09/2016 | 08:06 | ZN2400:PA11 | SHORT RURAL | Planned |  | 209 | 475 | 0.45075 | 0.094894 | N
21/09/2016 | 08:00 | ZN12610:PA24 | URBAN | Planned |  | 113 | 245 | 0.019121 | 0.0078045 | N
21/09/2016 | 08:00 | ZN12630:PA21 | SHORT RURAL | Planned |  | 18 | 480 | 0.039229 | 0.0081727 | N
21/09/2016 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 5 | 270 | 0.0061295 | 0.0022702 | N
21/09/2016 | 08:05 | ZN12660:PA14 | SHORT RURAL | Planned |  | 28 | 470 | 0.059751 | 0.012713 | N
21/09/2016 | 08:00 | ZN12630:PA23 | SHORT RURAL | Planned |  | 7 | 440 | 0.013984 | 0.0031783 | N
21/09/2016 | 08:29 | ZN36100:PA19 | URBAN | Planned |  | 87 | 331 | 0.019889 | 0.0060088 | N
21/09/2016 | 10:00 | ZN15002:PA6 | URBAN | Planned |  | 1 | 100 | 6.9066e-05 | 6.9066e-05 | N
21/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 75 | 5 | 0.0017026 | 0.034053 | N
15/09/2016 | 07:30 | ZN690:PA3 | URBAN | Planned |  | 94 | 570 | 0.036998 | 0.0064909 | N
22/09/2016 | 08:05 | ZN14891:PA20 | SHORT RURAL | Planned |  | 11 | 460 | 0.022968 | 0.004993 | N
22/09/2016 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 61 | 390 | 0.10799 | 0.027689 | N
22/09/2016 | 08:00 | ZN36200:PA8 | SHORT RURAL | Planned |  | 52 | 450 | 0.10622 | 0.023603 | N
22/09/2016 | 08:30 | ZN9900:PA5 | URBAN | Planned |  | 26 | 240 | 0.0043084 | 0.0017952 | N
22/09/2016 | 08:45 | ZN342:PA22 | URBAN | Planned |  | 22 | 435 | 0.0066076 | 0.001519 | N
22/09/2016 | 09:30 | ZN9900:PA3 | URBAN | Planned |  | 95 | 180 | 0.011807 | 0.0065593 | N
22/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 75 | 30 | 0.010213 | 0.034043 | N
23/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 75 | 105 | 0.035746 | 0.034043 | N
24/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 75 | 30 | 0.010213 | 0.034044 | N
26/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 75 | 10 | 0.0034044 | 0.034044 | N
27/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 75 | 25 | 0.0085103 | 0.034041 | N
28/09/2016 | 18:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 75 | 30 | 0.010212 | 0.034041 | N
22/09/2016 | 20:30 | ZN180:PA10 | URBAN | Planned |  | 54 | 405 | 0.0151 | 0.0037285 | N
22/09/2016 | 20:30 | ZN1287:PA24 | URBAN | Planned |  | 45 | 360 | 0.011185 | 0.003107 | N
23/09/2016 | 08:00 | ZN35900:PA3 | URBAN | Planned |  | 1 | 10 | 6.9045e-06 | 6.9045e-05 | N
23/09/2016 | 08:00 | ZN35500:PA23 | URBAN | Planned |  | 22 | 270 | 0.0041013 | 0.001519 | N
23/09/2016 | 09:30 | ZN12690:PA7 | SHORT RURAL | Planned |  | 277 | 150 | 0.1886 | 0.12573 | N
23/09/2016 | 09:30 | ZN9245:PA3 | URBAN | Planned |  | 4 | 460 | 0.0012704 | 0.00027618 | N
23/09/2016 | 15:00 | ZN14143:PA6 | URBAN | Planned |  | 1 | 120 | 8.2855e-05 | 6.9045e-05 | N
24/09/2016 | 05:00 | ZN8100:PA1 | URBAN | Planned |  | 3 | 15 | 3.1071e-05 | 0.00020714 | N
24/09/2016 | 07:00 | ZN3472:PA29 | URBAN | Planned |  | 2 | 510 | 0.00070427 | 0.00013809 | N
24/09/2016 | 09:30 | ZN2196:PA26 | URBAN | Planned |  | 15 | 1,680 | 0.0174 | 0.0010357 | N
24/09/2016 | 19:00 | ZN2473:PA33 | URBAN | Planned |  | 25 | 720 | 0.012428 | 0.0017261 | N
25/09/2016 | 08:00 | ZN4990:PA51 52DEF | CBD | Planned |  | 4 | 780 | 0.10058 | 0.012895 | N
25/09/2016 | 18:30 | ZN72:PA25 | URBAN | Planned |  | 1 | 5,450 | 0.003763 | 6.9046e-05 | N
26/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 68 | 480 | 0.022537 | 0.0046951 | N
26/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 6 | 480 | 0.0019885 | 0.00041428 | N
26/09/2016 | 07:30 | ZN2196:PA4 | URBAN | Planned |  | 4 | 360 | 0.00099427 | 0.00027619 | N
26/09/2016 | 07:30 | ZN10999:PA4 | URBAN | Planned |  | 1 | 1,740 | 0.0012014 | 6.9046e-05 | N
26/09/2016 | 08:54 | ZN12610:PA13 | URBAN | Planned |  | 137 | 471 | 0.044553 | 0.0094593 | N
26/09/2016 | 08:10 | ZN12630:PA23 | SHORT RURAL | Planned |  | 6 | 252 | 0.0068633 | 0.0027235 | N
26/09/2016 | 08:30 | ZN12630:PA25 | SHORT RURAL | Planned |  | 6 | 500 | 0.013618 | 0.0027235 | N
26/09/2016 | 08:00 | ZN12570:PA37 | SHORT RURAL | Planned |  | 3 | 390 | 0.0053109 | 0.0013618 | N
27/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 68 | 480 | 0.022537 | 0.0046952 | N
27/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 6 | 480 | 0.0019886 | 0.00041428 | N
27/09/2016 | 07:30 | ZN847:PA5 | URBAN | Planned |  | 43 | 510 | 0.015142 | 0.002969 | N
27/09/2016 | 08:00 | ZN12630:PA13 | SHORT RURAL | Planned |  | 28 | 340 | 0.043209 | 0.012709 | N
27/09/2016 | 08:10 | ZN12610:PA20 | SHORT RURAL | Planned |  | 98 | 530 | 0.23575 | 0.04448 | N
27/09/2016 | 08:00 | ZN12580:PA10 | URBAN | Planned |  | 27 | 420 | 0.0078299 | 0.0018643 | N
27/09/2016 | 08:30 | ZN9900:PA5 | URBAN | Planned |  | 26 | 360 | 0.0064628 | 0.0017952 | N
27/09/2016 | 10:05 | ZN14891:PA12 | SHORT RURAL | Planned |  | 18 | 295 | 0.024101 | 0.0081699 | N
27/09/2016 | 09:30 | ZN9900:PA6 | URBAN | Planned |  | 5 | 450 | 0.0015536 | 0.00034523 | N
27/09/2016 | 23:31 | ZN15001:PA10 | URBAN | Planned |  | 1 | 2,220 | 0.0015328 | 6.9047e-05 | N
28/09/2016 | 00:01 | ZN2602:PA18 | URBAN | Planned |  | 84 | 14 | 0.00081201 | 0.0058001 | N
28/09/2016 | 07:40 | ZN2400:PA18 | SHORT RURAL | Planned |  | 98 | 500 | 0.2224 | 0.044481 | N
28/09/2016 | 07:30 | ZN15001:PA15 | URBAN | Planned |  | 42 | 650 | 0.01885 | 0.0029 | N
28/09/2016 | 08:30 | ZN36800:PA42 | URBAN | Planned |  | 47 | 360 | 0.011683 | 0.0032453 | N
28/09/2016 | 08:30 | ZN36100:PA8 | URBAN | Planned |  | 122 | 420 | 0.03538 | 0.0084239 | N
28/09/2016 | 08:15 | ZN15013:PA10 | SHORT RURAL | Planned |  | 1 | 750 | 0.0034041 | 0.00045388 | N
28/09/2016 | 08:00 | ZN12690:PA26 | URBAN | Planned |  | 40 | 540 | 0.014914 | 0.0027619 | N
28/09/2016 | 08:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 46 | 475 | 0.099173 | 0.020879 | N
28/09/2016 | 08:30 | ZN12580:PA4 | URBAN | Planned |  | 152 | 420 | 0.044081 | 0.010495 | N
28/09/2016 | 08:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 3 | 285 | 0.0038807 | 0.0013616 | N
29/09/2016 | 09:50 | ZN965:PA29 | URBAN | Planned |  | 68 | 310 | 0.014551 | 0.0046939 | N
29/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 6 | 360 | 0.001491 | 0.00041417 | N
29/09/2016 | 08:30 | ZN129:PA16 | URBAN | Planned |  | 52 | 390 | 0.013999 | 0.0035895 | N
29/09/2016 | 08:13 | ZN12630:PA22 | SHORT RURAL | Planned |  | 157 | 47 | 0.033484 | 0.071242 | N
29/09/2016 | 16:00 | ZN12630:PA22 | SHORT RURAL | Planned |  | 157 | 50 | 0.035621 | 0.071242 | N
29/09/2016 | 08:00 | ZN36100:PA13 | URBAN | Planned |  | 3 | 430 | 0.00089046 | 0.00020708 | N
29/09/2016 | 08:00 | ZN12570:PA33 | SHORT RURAL | Planned |  | 68 | 480 | 0.14811 | 0.030856 | N
29/09/2016 | 08:00 | ZN12640:PA1 | SHORT RURAL | Planned |  | 68 | 180 | 0.055541 | 0.030856 | N
30/09/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 6 | 480 | 0.001988 | 0.00041417 | N
30/09/2016 | 07:45 | ZN2835:PA15 | URBAN | Planned |  | 52 | 585 | 0.020998 | 0.0035895 | N
30/09/2016 | 08:00 | ZN10996:PA19 | URBAN | Planned |  | 1 | 210 | 0.00014496 | 6.9028e-05 | N
30/09/2016 | 08:05 | ZN14144:PA10 | SHORT RURAL | Planned |  | 18 | 295 | 0.024095 | 0.0081678 | N
30/09/2016 | 08:05 | ZN14891:PA14 | URBAN | Planned |  | 5 | 490 | 0.0016912 | 0.00034514 | N
30/09/2016 | 09:35 | ZN12630:PA22 | SHORT RURAL | Planned |  | 8 | 375 | 0.013613 | 0.0036301 | N
11/10/2016 | 08:35 | 514:18137 | SHORT RURAL | Planned |  | 1 | 75 | 0.00033912 | 0.00045216 | N
11/10/2016 | 09:00 | 239:82127 | SHORT RURAL | Planned |  | 1 | 325 | 0.0014695 | 0.00045216 | N
11/10/2016 | 07:35 | 202:34261 | URBAN | Planned |  | 19 | 665 | 0.008724 | 0.0013119 | N
11/10/2016 | 08:40 | 532:83301 | URBAN | Planned |  | 33 | 330 | 0.0075192 | 0.0022785 | N
11/10/2016 | 09:25 | 801:74121 | LONG RURAL | Planned |  | 2 | 10 | 0.0071378 | 0.071378 | N
11/10/2016 | 09:03 | 520:48172 | SHORT RURAL | Planned |  | 5 | 102 | 0.002306 | 0.0022608 | N
11/10/2016 | 08:55 | 814:82283 | SHORT RURAL | Planned |  | 1 | 145 | 0.00065564 | 0.00045216 | N
11/10/2016 | 09:00 | 807:74179 | SHORT RURAL | Planned |  | 5 | 302 | 0.0068277 | 0.0022608 | N
11/10/2016 | 08:30 | 812:19072 | SHORT RURAL | Planned |  | 11 | 360 | 0.017906 | 0.0049738 | N
11/10/2016 | 09:10 | 813:89061 | LONG RURAL | Planned |  | 5 | 240 | 0.42827 | 0.17844 | N
16/10/2016 | 08:40 | 214:8665 | URBAN | Planned |  | 265 | 460 | 0.084195 | 0.018303 | N
17/10/2016 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 4 | 322 | 0.0058013 | 0.0018016 | N
14/10/2016 | 08:05 | 213:33773 | URBAN | Planned |  | 44 | 135 | 0.0041069 | 0.0030422 | N
14/10/2016 | 11:30 | 261:81865 | URBAN | Planned |  | 25 | 210 | 0.0036299 | 0.0017285 | N
16/10/2016 | 08:40 | 214:8665 | URBAN | Planned |  | 76 | 268 | 0.014068 | 0.0052493 | N
18/10/2016 | 04:55 | 257:81999 | URBAN | Planned |  | 4 | 95 | 0.00026248 | 0.00027629 | N
15/10/2016 | 07:40 | 229:34983 | SHORT RURAL | Planned |  | 7 | 307 | 0.0096792 | 0.0031528 | N
17/10/2016 | 08:40 | 512:48048 | SHORT RURAL | Planned |  | 88 | 215 | 0.085218 | 0.039636 | N
17/10/2016 | 08:30 | 524:33572 | SHORT RURAL | Planned |  | 39 | 130 | 0.022836 | 0.017566 | N
14/10/2016 | 08:00 | 814:82285 | SHORT RURAL | Planned |  | 3 | 285 | 0.0038645 | 0.001356 | N
14/10/2016 | 09:30 | 802:82225 | SHORT RURAL | Planned |  | 3 | 185 | 0.0025085 | 0.001356 | N
14/10/2016 | 08:10 | 813:89055 | SHORT RURAL | Planned |  | 3 | 365 | 0.0049493 | 0.001356 | N
14/10/2016 | 08:46 | 812:19072 | SHORT RURAL | Planned |  | 1 | 154 | 0.00069606 | 0.00045199 | N
14/10/2016 | 08:30 | 814:82291 | SHORT RURAL | Planned |  | 115 | 235 | 0.12215 | 0.051979 | N
14/10/2016 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 6 | 260 | 0.007051 | 0.0027119 | N
14/10/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 14 | 318 | 0.020123 | 0.0063279 | N
14/10/2016 | 09:50 | 813:89061 | LONG RURAL | Planned |  | 4 | 195 | 0.27837 | 0.14276 | N
17/10/2016 | 09:50 | 811:74234 | SHORT RURAL | Planned |  | 3 | 75 | 0.0010134 | 0.0013512 | N
17/10/2016 | 12:35 | 513:48058 | URBAN | Planned |  | 4 | 12 | 3.3153e-05 | 0.00027628 | N
17/10/2016 | 09:30 | 806:82662 | SHORT RURAL | Planned |  | 1 | 295 | 0.0013287 | 0.00045041 | N
18/10/2016 | 08:00 | 528:83019 | SHORT RURAL | Planned |  | 253 | 450 | 0.51279 | 0.11395 | N
18/10/2016 | 08:30 | 807:74179 | SHORT RURAL | Planned |  | 11 | 240 | 0.011891 | 0.0049545 | N
18/10/2016 | 08:00 | 264:81240 | SHORT RURAL | Planned |  | 9 | 320 | 0.012972 | 0.0040537 | N
18/10/2016 | 08:00 | 532:83301 | URBAN | Planned |  | 34 | 315 | 0.0073977 | 0.0023485 | N
18/10/2016 | 17:00 | 265:81651 | SHORT RURAL | Planned |  | 18 | 263 | 0.021322 | 0.0081073 | N
18/10/2016 | 09:10 | 515:35192 | SHORT RURAL | Planned |  | 1 | 165 | 0.00074317 | 0.00045041 | N
18/10/2016 | 08:30 | 814:82289 | SHORT RURAL | Planned |  | 26 | 300 | 0.035132 | 0.011711 | N
19/10/2016 | 09:00 | 813:89062 | SHORT RURAL | Planned |  | 33 | 235 | 0.034929 | 0.014864 | N
19/10/2016 | 09:00 | 814:82285 | SHORT RURAL | Planned |  | 10 | 155 | 0.0069814 | 0.0045041 | N
19/10/2016 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 8 | 320 | 0.01153 | 0.0036033 | N
19/10/2016 | 08:10 | 512:48048 | SHORT RURAL | Planned |  | 6 | 370 | 0.0099991 | 0.0027025 | N
19/10/2016 | 08:30 | 504:48031 | SHORT RURAL | Planned |  | 2 | 360 | 0.003243 | 0.00090082 | N
19/10/2016 | 08:30 | 512:48048 | SHORT RURAL | Planned |  | 27 | 350 | 0.042564 | 0.012161 | N
19/10/2016 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 1 | 60 | 0.00027025 | 0.00045041 | N
19/10/2016 | 09:05 | 514:18137 | SHORT RURAL | Planned |  | 1 | 115 | 0.00051797 | 0.00045041 | N
19/10/2016 | 08:50 | 523:33501 | SHORT RURAL | Planned |  | 1 | 205 | 0.00092334 | 0.00045041 | N
19/10/2016 | 09:40 | 813:89061 | LONG RURAL | Planned |  | 2 | 115 | 0.082084 | 0.071378 | N
19/10/2016 | 09:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 130 | 0.046395 | 0.035689 | N
19/10/2016 | 12:30 | 514:18137 | SHORT RURAL | Planned |  | 1 | 95 | 0.00042789 | 0.00045041 | N
20/10/2016 | 13:05 | 264:81238 | SHORT RURAL | Planned |  | 1 | 70 | 0.00031529 | 0.00045042 | N
20/10/2016 | 09:45 | 265:81651 | SHORT RURAL | Planned |  | 20 | 155 | 0.013963 | 0.0090084 | N
20/10/2016 | 08:30 | 526:34640 | SHORT RURAL | Planned |  | 5 | 235 | 0.0052924 | 0.0022521 | N
20/10/2016 | 08:00 | 526:34639 | SHORT RURAL | Planned |  | 16 | 405 | 0.029187 | 0.0072067 | N
20/10/2016 | 08:00 | 509:33397 | SHORT RURAL | Planned |  | 5 | 450 | 0.010134 | 0.0022521 | N
20/10/2016 | 11:00 | 243:80083 | SHORT RURAL | Planned |  | 3 | 255 | 0.0034457 | 0.0013513 | N
20/10/2016 | 09:05 | 532:83298 | URBAN | Planned |  | 139 | 270 | 0.025925 | 0.0096018 | N
20/10/2016 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 2 | 55 | 0.039258 | 0.071378 | N
20/10/2016 | 09:30 | 812:19072 | SHORT RURAL | Planned |  | 1 | 170 | 0.00076571 | 0.00045042 | N
20/10/2016 | 08:30 | 523:33503 | URBAN | Planned |  | 68 | 270 | 0.012683 | 0.0046973 | N
20/10/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 1 | 357 | 0.001608 | 0.00045042 | N
21/10/2016 | 08:30 | 524:33580 | SHORT RURAL | Planned |  | 26 | 390 | 0.045952 | 0.011782 | N
21/10/2016 | 08:40 | 526:34636 | SHORT RURAL | Planned |  | 3 | 140 | 0.0019033 | 0.0013595 | N
21/10/2016 | 09:30 | 813:89061 | LONG RURAL | Planned |  | 7 | 165 | 0.42015 | 0.25464 | N
21/10/2016 | 09:00 | 810:74054 | LONG RURAL | Planned |  | 2 | 230 | 0.16733 | 0.072754 | N
21/10/2016 | 08:08 | 243:80083 | SHORT RURAL | Planned |  | 5 | 456 | 0.010332 | 0.0022659 | N
22/10/2016 | 07:00 | 202:34231 37 42 | URBAN | Planned |  | 19 | 185 | 0.0024273 | 0.0013121 | N
23/10/2016 | 08:19 | 221:11895 | URBAN | Planned |  | 6 | 356 | 0.0014751 | 0.00041435 | N
21/10/2016 | 08:30 | 264:81232 | URBAN | Planned |  | 15 | 400 | 0.0041652 | 0.0010413 | N
21/10/2016 | 13:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.01637 | 0.036377 | N
21/10/2016 | 09:30 | 810:74054 | LONG RURAL | Planned |  | 2 | 195 | 0.14187 | 0.072754 | N
21/10/2016 | 10:45 | 813:89061 | LONG RURAL | Planned |  | 5 | 80 | 0.14551 | 0.18188 | N
21/10/2016 | 08:50 | 520:48172 | SHORT RURAL | Planned |  | 2 | 240 | 0.0021752 | 0.00090634 | N
23/10/2016 | 07:10 | 513:48052 | URBAN | Planned |  | 35 | 105 | 0.0025379 | 0.002417 | N
24/10/2016 | 11:08 | 243:80083 | SHORT RURAL | Planned |  | 15 | 222 | 0.014993 | 0.0067535 | N
24/10/2016 | 17:15 | 238:34144 | URBAN | Planned |  | 1 | 55 | 3.7982e-05 | 6.9058e-05 | N
24/10/2016 | 09:45 | 814:82283 | SHORT RURAL | Planned |  | 5 | 140 | 0.0031516 | 0.0022512 | N
24/10/2016 | 08:45 | 515:35192 | SHORT RURAL | Planned |  | 2 | 375 | 0.0033767 | 0.00090046 | N
25/10/2016 | 09:00 | 221:11898 | URBAN | Planned |  | 13 | 350 | 0.0031422 | 0.00089776 | N
25/10/2016 | 08:00 | 507:80925 | SHORT RURAL | Planned |  | 19 | 435 | 0.037212 | 0.0085545 | N
25/10/2016 | 08:00 | 524:33570 | SHORT RURAL | Planned |  | 5 | 435 | 0.0097926 | 0.0022512 | N
25/10/2016 | 08:30 | 507:80931 | URBAN | Planned |  | 113 | 250 | 0.019509 | 0.0078036 | N
25/10/2016 | 09:45 | 528:83019 | SHORT RURAL | Planned |  | 81 | 125 | 0.045586 | 0.036469 | N
25/10/2016 | 10:00 | 508:82579 | SHORT RURAL | Planned |  | 1 | 175 | 0.00078791 | 0.00045024 | N
25/10/2016 | 08:00 | 229:34995 | SHORT RURAL | Planned |  | 6 | 415 | 0.011211 | 0.0027014 | N
25/10/2016 | 17:10 | 238:34137 | SHORT RURAL | Planned |  | 1 | 75 | 0.00033768 | 0.00045024 | N
25/10/2016 | 18:45 | 238:34144 | URBAN | Planned |  | 3 | 90 | 0.00018646 | 0.00020718 | N
25/10/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 24 | 335 | 2.8694 | 0.85653 | N
25/10/2016 | 08:40 | 512:48049 | SHORT RURAL | Planned |  | 7 | 340 | 0.010716 | 0.0031516 | N
26/10/2016 | 09:45 | 814:82283 | SHORT RURAL | Planned |  | 2 | 220 | 0.001981 | 0.00090047 | N
26/10/2016 | 08:55 | 814:82283 | SHORT RURAL | Planned |  | 13 | 210 | 0.012291 | 0.0058531 | N
26/10/2016 | 10:40 | 243:80083 | SHORT RURAL | Planned |  | 12 | 150 | 0.0081042 | 0.0054028 | N
26/10/2016 | 08:30 | 221:11893 | URBAN | Planned |  | 266 | 520 | 0.095522 | 0.01837 | N
26/10/2016 | 18:30 | 258:80793 | URBAN | Planned |  | 2 | 50 | 6.9059e-05 | 0.00013812 | N
26/10/2016 | 09:05 | 232:11457 | SHORT RURAL | Planned |  | 109 | 305 | 0.14968 | 0.049076 | N
26/10/2016 | 08:00 | 229:34995 | SHORT RURAL | Planned |  | 6 | 600 | 0.016208 | 0.0027014 | N
26/10/2016 | 09:10 | 813:89061 | LONG RURAL | Planned |  | 1 | 60 | 0.021413 | 0.035689 | N
26/10/2016 | 08:30 | 812:19072 | SHORT RURAL | Planned |  | 3 | 240 | 0.0032417 | 0.0013507 | N
26/10/2016 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 6 | 195 | 0.41756 | 0.21413 | N
26/10/2016 | 08:30 | 814:82285 | SHORT RURAL | Planned |  | 22 | 190 | 0.01882 | 0.0099052 | N
26/10/2016 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 9 | 360 | 0.014588 | 0.0040521 | N
26/10/2016 | 13:15 | 813:89061 | LONG RURAL | Planned |  | 6 | 17 | 0.036403 | 0.21413 | N
28/10/2016 | 12:57 | ZN15002:PA4 | URBAN | Planned |  | 1 | 633 | 0.00043715 | 6.9037e-05 | N
31/10/2016 | 12:35 | ZN3922:PA21 | URBAN | Planned |  | 1 | 6 | 3.9812e-06 | 6.9038e-05 | N
28/10/2016 | 08:00 | 205:12210 | URBAN | Planned |  | 192 | 110 | 0.014581 | 0.013255 | N
28/10/2016 | 08:30 | 203:8090 | URBAN | Planned |  | 1 | 360 | 0.00024853 | 6.9037e-05 | N
30/10/2016 | 22:10 | 240:34849 | SHORT RURAL | Planned |  | 1 | 610 | 0.0027457 | 0.00045012 | N
27/10/2016 | 08:05 | 526:34639 | SHORT RURAL | Planned |  | 16 | 425 | 0.030608 | 0.0072019 | N
27/10/2016 | 08:45 | 264:81244 | SHORT RURAL | Planned |  | 78 | 375 | 0.13166 | 0.035109 | N
27/10/2016 | 09:47 | 528:83019 | SHORT RURAL | Planned |  | 20 | 253 | 0.022776 | 0.0090023 | N
28/10/2016 | 13:10 | 532:83298 | URBAN | Planned |  | 2 | 970 | 0.0013393 | 0.00013807 | N
29/10/2016 | 06:00 | 229:34983 | SHORT RURAL | Planned |  | 1 | 65 | 0.00029258 | 0.00045012 | N
29/10/2016 | 08:15 | 238:34147 | SHORT RURAL | Planned |  | 1 | 400 | 0.0018005 | 0.00045012 | N
27/10/2016 | 08:30 | 812:19072 | SHORT RURAL | Planned |  | 4 | 310 | 0.0055814 | 0.0018005 | N
27/10/2016 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 16 | 290 | 0.020885 | 0.0072019 | N
27/10/2016 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 17 | 364 | 0.027853 | 0.007652 | N
28/10/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 15 | 180 | 0.012153 | 0.0067517 | N
31/10/2016 | 07:45 | 243:80075 | SHORT RURAL | Planned |  | 135 | 490 | 0.29775 | 0.060766 | N
31/10/2016 | 09:50 | 243:80083 | SHORT RURAL | Planned |  | 8 | 192 | 0.0069138 | 0.0036009 | N
31/10/2016 | 08:35 | 238:34144 | URBAN | Planned |  | 10 | 165 | 0.0011391 | 0.00069038 | N
31/10/2016 | 18:00 | 229:34983 | SHORT RURAL | Planned |  | 1 | 60 | 0.00027007 | 0.00045012 | N
31/10/2016 | 09:20 | 807:74184 | SHORT RURAL | Planned |  | 6 | 205 | 0.0055364 | 0.0027007 | N
31/10/2016 | 08:30 | 516:48066 | SHORT RURAL | Planned |  | 14 | 230 | 0.014494 | 0.0063016 | N
01/11/2016 | 08:30 | 814:82283 | SHORT RURAL | Planned |  | 23 | 300 | 0.031061 | 0.010354 | N
01/11/2016 | 09:10 | 227:13019 | SHORT RURAL | Planned |  | 11 | 306 | 0.015152 | 0.0049517 | N
01/11/2016 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 1 | 175 | 0.062389 | 0.035651 | N
01/11/2016 | 08:45 | 515:35193 | SHORT RURAL | Planned |  | 3 | 165 | 0.0022283 | 0.0013505 | N
02/11/2016 | 07:10 | 203:8084 | URBAN | Planned |  | 3 | 400 | 0.00082852 | 0.00020713 | N
02/11/2016 | 08:20 | 225:33676 | URBAN | Planned |  | 58 | 365 | 0.014617 | 0.0040045 | N
02/11/2016 | 18:30 | 221:11898 | URBAN | Planned |  | 3 | 60 | 0.00012428 | 0.00020713 | N
02/11/2016 | 06:08 | 528:83024 | URBAN | Planned |  | 24 | 137 | 0.0022702 | 0.001657 | N
02/11/2016 | 09:15 | 532:83298 | URBAN | Planned |  | 136 | 210 | 0.019719 | 0.0093899 | N
02/11/2016 | 08:00 | 509:33397 | SHORT RURAL | Planned |  | 38 | 90 | 0.015396 | 0.017106 | N
02/11/2016 | 10:30 | 532:83307 | SHORT RURAL | Planned |  | 3 | 60 | 0.00081029 | 0.0013505 | N
02/11/2016 | 09:32 | 507:80914 | SHORT RURAL | Planned |  | 13 | 348 | 0.020365 | 0.0058521 | N
03/11/2016 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 250 | 288 | 25.6502 | 8.9063 | N
02/11/2016 | 09:00 | 520:48172 | SHORT RURAL | Planned |  | 2 | 310 | 0.002791 | 0.00090033 | N
02/11/2016 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 18 | 275 | 1.7647 | 0.64171 | N
03/11/2016 | 08:35 | 240:34846 | URBAN | Planned |  | 134 | 135 | 0.012486 | 0.0092491 | N
03/11/2016 | 09:43 | 222:33602 | URBAN | Planned |  | 70 | 247 | 0.011934 | 0.0048316 | N
03/11/2016 | 11:30 | 240:34846 | URBAN | Planned |  | 93 | 200 | 0.012838 | 0.0064192 | N
03/11/2016 | 08:40 | 507:80922 | SHORT RURAL | Planned |  | 16 | 305 | 0.021959 | 0.0071997 | N
03/11/2016 | 08:45 | 532:83307 | SHORT RURAL | Planned |  | 35 | 495 | 0.077959 | 0.015749 | N
03/11/2016 | 08:30 | 265:81648 | SHORT RURAL | Planned |  | 2 | 320 | 0.0028799 | 0.00089996 | N
03/11/2016 | 17:15 | 265:81641 | URBAN | Planned |  | 6 | 135 | 0.00055909 | 0.00041414 | N
03/11/2016 | 08:55 | 512:48049 | SHORT RURAL | Planned |  | 2 | 110 | 0.00098995 | 0.00089996 | N
03/11/2016 | 09:30 | 511:29878 | SHORT RURAL | Planned |  | 2 | 75 | 0.00067497 | 0.00089996 | N
03/11/2016 | 09:30 | 813:89062 | SHORT RURAL | Planned |  | 1 | 125 | 0.00056247 | 0.00044998 | N
03/11/2016 | 12:30 | 515:35197 | LONG RURAL | Planned |  | 1 | 80 | 0.0285 | 0.035625 | N
05/11/2016 | 03:29 | 261:81870 | URBAN | Planned |  | 1,763 | 1 | 0.0012169 | 0.12169 | N
04/11/2016 | 09:30 | 264:81240 | SHORT RURAL | Planned |  | 17 | 265 | 0.020272 | 0.0076496 | N
04/11/2016 | 08:50 | 512:48049 | SHORT RURAL | Planned |  | 8 | 245 | 0.0088196 | 0.0035998 | N
03/11/2016 | 09:15 | 229:34995 | SHORT RURAL | Planned |  | 167 | 560 | 0.42082 | 0.075146 | N
04/11/2016 | 08:30 | 513:48050 | SHORT RURAL | Planned |  | 11 | 280 | 0.013859 | 0.0049498 | N
04/11/2016 | 08:30 | 221:11899 | SHORT RURAL | Planned |  | 80 | 240 | 0.086396 | 0.035998 | N
04/11/2016 | 09:15 | 504:48026 | SHORT RURAL | Planned |  | 72 | 75 | 0.024299 | 0.032398 | N
04/11/2016 | 09:05 | 524:33570 | SHORT RURAL | Planned |  | 2 | 85 | 0.00076496 | 0.00089996 | N
04/11/2016 | 09:40 | 229:34995 | SHORT RURAL | Planned |  | 15 | 245 | 0.016537 | 0.0067497 | N
04/11/2016 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 4 | 26 | 0.03705 | 0.1425 | N
04/11/2016 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 1 | 210 | 0.00094495 | 0.00044998 | N
04/11/2016 | 08:40 | 811:74234 | SHORT RURAL | Planned |  | 5 | 150 | 0.0033748 | 0.0022499 | N
04/11/2016 | 09:25 | 813:89055 | SHORT RURAL | Planned |  | 7 | 225 | 0.0070872 | 0.0031498 | N
04/11/2016 | 08:51 | 516:48067 | SHORT RURAL | Planned |  | 2 | 114 | 0.001026 | 0.00089996 | N
04/11/2016 | 14:00 | 513:48058 | URBAN | Planned |  | 12 | 35 | 0.0002899 | 0.00082828 | N
07/11/2016 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 11 | 245 | 0.012127 | 0.0049499 | N
07/11/2016 | 09:10 | 243:80083 | SHORT RURAL | Planned |  | 7 | 400 | 0.0126 | 0.00315 | N
07/11/2016 | 09:00 | 243:80081 | SHORT RURAL | Planned |  | 81 | 340 | 0.12393 | 0.03645 | N
07/11/2016 | 08:35 | 221:11899 | SHORT RURAL | Planned |  | 1 | 385 | 0.0017325 | 0.00044999 | N
07/11/2016 | 07:25 | 511:29878 | SHORT RURAL | Planned |  | 1 | 455 | 0.0020475 | 0.00044999 | N
08/11/2016 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 15 | 270 | 1.4428 | 0.53438 | N
08/11/2016 | 08:30 | 526:34640 | SHORT RURAL | Planned |  | 4 | 731 | 0.013158 | 0.0018 | N
08/11/2016 | 08:10 | 227:13015 | SHORT RURAL | Planned |  | 39 | 460 | 0.08073 | 0.01755 | N
08/11/2016 | 08:45 | 532:83298 | URBAN | Planned |  | 247 | 375 | 0.063938 | 0.01705 | N
08/11/2016 | 12:20 | 229:34983 | SHORT RURAL | Planned |  | 7 | 135 | 0.0042525 | 0.00315 | N
08/11/2016 | 13:00 | 528:83019 | SHORT RURAL | Planned |  | 3 | 59 | 0.0007965 | 0.00135 | N
08/11/2016 | 17:00 | 511:29878 | SHORT RURAL | Planned |  | 13 | 165 | 0.0096525 | 0.00585 | N
08/11/2016 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 1 | 150 | 0.000675 | 0.00045 | N
08/11/2016 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 9 | 230 | 0.009315 | 0.00405 | N
08/11/2016 | 08:55 | 814:82283 | SHORT RURAL | Planned |  | 3 | 175 | 0.0023625 | 0.00135 | N
08/11/2016 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 16 | 365 | 0.02628 | 0.0072 | N
08/11/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 13 | 320 | 0.01872 | 0.00585 | N
09/11/2016 | 08:30 | 227:13019 | SHORT RURAL | Planned |  | 7 | 395 | 0.012443 | 0.00315 | N
09/11/2016 | 08:05 | 240:34846 | URBAN | Planned |  | 1 | 145 | 0.00010009 | 6.9031e-05 | N
09/11/2016 | 03:45 | 242:81539 | URBAN | Planned |  | 2 | 385 | 0.00053154 | 0.00013806 | N
09/11/2016 | 09:00 | 524:33572 | SHORT RURAL | Planned |  | 5 | 165 | 0.0037125 | 0.00225 | N
09/11/2016 | 09:05 | 504:48026 | SHORT RURAL | Planned |  | 16 | 275 | 0.0198 | 0.0072 | N
09/11/2016 | 12:30 | 524:33576 | SHORT RURAL | Planned |  | 3 | 68 | 0.00091801 | 0.00135 | N
09/11/2016 | 18:15 | 511:29880 | URBAN | Planned |  | 18 | 115 | 0.0014289 | 0.0012426 | N
09/11/2016 | 09:35 | 514:18137 | SHORT RURAL | Planned |  | 3 | 130 | 0.001755 | 0.00135 | N
09/11/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 22 | 245 | 0.024255 | 0.0099001 | N
10/11/2016 | 10:35 | 508:82574 | SHORT RURAL | Planned |  | 6 | 160 | 0.0043201 | 0.0027001 | N
01/10/2016 | 08:30 | ZN3155:PA23 | URBAN | Planned |  | 1 | 3,120 | 0.0021546 | 6.9059e-05 | N
03/10/2016 | 08:00 | ZN5868:PA7 | URBAN | Planned |  | 1 | 1,740 | 0.0012016 | 6.9059e-05 | N
04/10/2016 | 07:30 | ZN10996:PA12 | URBAN | Planned |  | 6 | 360 | 0.0014917 | 0.00041436 | N
04/10/2016 | 07:30 | ZN847:PA10 | URBAN | Planned |  | 30 | 540 | 0.011188 | 0.0020718 | N
04/10/2016 | 08:30 | ZN12630:PA23 | SHORT RURAL | Planned |  | 11 | 450 | 0.022408 | 0.0049795 | N
04/10/2016 | 09:45 | ZN10999:PA19 | URBAN | Planned |  | 215 | 405 | 0.060133 | 0.014848 | N
04/10/2016 | 12:00 | ZN874:PA17 | URBAN | Planned |  | 73 | 180 | 0.0090744 | 0.0050413 | N
05/10/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 68 | 480 | 0.022541 | 0.0046961 | N
05/10/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 6 | 480 | 0.0019889 | 0.00041436 | N
05/10/2016 | 07:30 | ZN80:PA32 | URBAN | Planned |  | 58 | 510 | 0.020428 | 0.0040055 | N
05/10/2016 | 07:30 | ZN14891:PA12 | SHORT RURAL | Planned |  | 166 | 620 | 0.4659 | 0.075145 | N
05/10/2016 | 08:15 | ZN35370:PA10 | SHORT RURAL | Planned |  | 32 | 545 | 0.078948 | 0.014486 | N
05/10/2016 | 07:30 | ZN35370:PA4 | SHORT RURAL | Planned |  | 1 | 570 | 0.0025803 | 0.00045268 | N
05/10/2016 | 08:00 | ZN14892:PA16 | URBAN | Planned |  | 56 | 480 | 0.018564 | 0.0038674 | N
06/10/2016 | 07:15 | ZN12640:PA13 | SHORT RURAL | Planned |  | 75 | 555 | 0.18843 | 0.033952 | N
06/10/2016 | 08:00 | ZN14144:PA2 | SHORT RURAL | Planned |  | 7 | 480 | 0.01521 | 0.0031688 | N
06/10/2016 | 08:00 | ZN10997:PA2 | URBAN | Planned |  | 73 | 480 | 0.024199 | 0.0050415 | N
06/10/2016 | 08:45 | ZN12580:PA4 | URBAN | Planned |  | 25 | 435 | 0.0075105 | 0.0017266 | N
06/10/2016 | 09:00 | ZN12690:PA12 | SHORT RURAL | Planned |  | 55 | 255 | 0.06349 | 0.024898 | N
06/10/2016 | 09:00 | ZN14891:PA17 | SHORT RURAL | Planned |  | 15 | 150 | 0.010186 | 0.0067904 | N
07/10/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 68 | 480 | 0.022533 | 0.0046943 | N
07/10/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 6 | 480 | 0.0019882 | 0.00041421 | N
07/10/2016 | 07:30 | ZN1068:PA18 | URBAN | Planned |  | 2 | 350 | 0.00048324 | 0.00013807 | N
07/10/2016 | 10:30 | ZN1290:PA12 | URBAN | Planned |  | 1 | 315 | 0.00021746 | 6.9034e-05 | N
08/10/2016 | 06:30 | ZN263:PA33 34ABC | CBD | Planned |  | 67 | 560 | 1.2096 | 0.216 | N
08/10/2016 | 08:00 | ZN9245:PA44 | URBAN | Planned |  | 105 | 420 | 0.030467 | 0.007254 | N
11/11/2016 | 08:00 | ZN36200:PA8 | SHORT RURAL | Planned |  | 98 | 435 | 0.19184 | 0.044101 | N
08/10/2016 | 11:00 | ZN14144:PA4 | URBAN | Planned |  | 1 | 180 | 0.00012435 | 6.9085e-05 | N
08/10/2016 | 22:00 | ZN10999:PA35 | URBAN | Planned |  | 9 | 240 | 0.0014922 | 0.00062177 | N
08/10/2016 | 22:00 | ZN10999:PA35 | URBAN | Planned |  | 45 | 210 | 0.0065286 | 0.0031088 | N
10/10/2016 | 08:00 | ZN3155:PA22 | URBAN | Planned |  | 22 | 166 | 0.002523 | 0.0015199 | N
11/10/2016 | 00:30 | ZN1285:PA31 | URBAN | Planned |  | 2 | 30 | 4.1428e-05 | 0.00013809 | N
11/10/2016 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 8 | 600 | 0.021704 | 0.0036173 | N
11/10/2016 | 08:00 | ZN12570:PA33 | SHORT RURAL | Planned |  | 61 | 480 | 0.13239 | 0.027582 | N
11/10/2016 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 7 | 590 | 0.018674 | 0.0031651 | N
11/10/2016 | 08:30 | ZN2568:PA15 | URBAN | Planned |  | 2 | 770 | 0.0010633 | 0.00013809 | N
11/10/2016 | 08:30 | ZN342:PA22 | URBAN | Planned |  | 114 | 390 | 0.030698 | 0.0078713 | N
12/10/2016 | 07:30 | ZN14892:PA1 | SHORT RURAL | Planned |  | 1 | 540 | 0.0024417 | 0.00045217 | N
12/10/2016 | 08:00 | ZN14892:PA21 | URBAN | Planned |  | 79 | 465 | 0.025365 | 0.0054548 | N
12/10/2016 | 09:45 | ZN12630:PA23 | SHORT RURAL | Planned |  | 1 | 325 | 0.0014695 | 0.00045217 | N
12/10/2016 | 09:45 | ZN12630:PA24 | SHORT RURAL | Planned |  | 4 | 325 | 0.0058782 | 0.0018087 | N
12/10/2016 | 08:40 | ZN12610:PA2 | URBAN | Planned |  | 55 | 440 | 0.01671 | 0.0037976 | N
12/10/2016 | 10:00 | ZN2400:PA11 | SHORT RURAL | Planned |  | 11 | 275 | 0.013678 | 0.0049738 | N
12/10/2016 | 09:00 | ZN12600:PA9 | SHORT RURAL | Planned |  | 238 | 55 | 0.059189 | 0.10762 | N
12/10/2016 | 09:40 | ZN874:PA22 | URBAN | Planned |  | 43 | 320 | 0.009501 | 0.0029691 | N
12/10/2016 | 16:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 16 | 150 | 0.010852 | 0.0072347 | N
12/10/2016 | 18:00 | ZN80:PA32 | URBAN | Planned |  | 1 | 780 | 0.00053857 | 6.9048e-05 | N
13/10/2016 | 09:03 | ZN2568:PA15 | URBAN | Planned |  | 2 | 527 | 0.00072874 | 0.00013828 | N
13/10/2016 | 09:00 | ZN35370:PA2 | SHORT RURAL | Planned |  | 21 | 360 | 0.03417 | 0.0094918 | N
14/10/2016 | 08:32 | ZN10993:PA35 | URBAN | Planned |  | 90 | 353 | 0.021966 | 0.0062226 | N
14/10/2016 | 09:00 | ZN14891:PA19 | SHORT RURAL | Planned |  | 1 | 390 | 0.0017628 | 0.00045199 | N
15/10/2016 | 06:45 | ZN12690:PA16 | SHORT RURAL | Planned |  | 2 | 330 | 0.0029727 | 0.00090081 | N
15/10/2016 | 08:00 | ZN711:PA34 | URBAN | Planned |  | 41 | 415 | 0.011752 | 0.0028318 | N
15/10/2016 | 08:00 | ZN129:PA27 | URBAN | Planned |  | 1 | 495 | 0.00034189 | 6.9069e-05 | N
15/10/2016 | 19:00 | ZN2473:PA10 | URBAN | Planned |  | 31 | 840 | 0.017986 | 0.0021411 | N
16/10/2016 | 06:15 | ZN12650:PA10 | URBAN | Planned |  | 28 | 375 | 0.0072523 | 0.0019339 | N
16/10/2016 | 06:15 | ZN12650:PA3 | URBAN | Planned |  | 7 | 375 | 0.0018131 | 0.00048349 | N
16/10/2016 | 06:15 | ZN12650:PA5 | URBAN | Planned |  | 5 | 375 | 0.001295 | 0.00034535 | N
17/10/2016 | 07:40 | ZN12570:PA21 | URBAN | Planned |  | 50 | 520 | 0.017958 | 0.0034535 | N
17/10/2016 | 07:30 | ZN2602:PA36 | URBAN | Planned |  | 80 | 570 | 0.031496 | 0.0055255 | N
17/10/2016 | 09:30 | ZN14891:PA20 | SHORT RURAL | Planned |  | 30 | 390 | 0.052698 | 0.013512 | N
17/10/2016 | 08:00 | ZN847:PA45 | SHORT RURAL | Planned |  | 13 | 480 | 0.028106 | 0.0058554 | N
17/10/2016 | 08:30 | ZN12570:PA33 | SHORT RURAL | Planned |  | 68 | 410 | 0.12557 | 0.030628 | N
17/10/2016 | 08:00 | ZN15008:PA5 | URBAN | Planned |  | 75 | 420 | 0.021757 | 0.0051802 | N
17/10/2016 | 08:00 | ZN15005:PA2 | URBAN | Planned |  | 25 | 420 | 0.0072523 | 0.0017267 | N
17/10/2016 | 09:00 | ZN10993:PA33 | URBAN | Planned |  | 74 | 330 | 0.016867 | 0.0051111 | N
17/10/2016 | 09:30 | ZN2635:PA39 | URBAN | Planned |  | 70 | 160 | 0.0077358 | 0.0048349 | N
18/10/2016 | 01:00 | ZN2835:PA17 | URBAN | Planned |  | 1 | 300 | 0.00020722 | 6.9073e-05 | N
18/10/2016 | 08:30 | ZN965:PA29 | URBAN | Planned |  | 22 | 285 | 0.0043309 | 0.0015196 | N
18/10/2016 | 08:30 | ZN965:PA29 | URBAN | Planned |  | 26 | 285 | 0.0051183 | 0.0017959 | N
18/10/2016 | 07:30 | ZN36100:PA19 | URBAN | Planned |  | 227 | 570 | 0.089374 | 0.01568 | N
18/10/2016 | 08:00 | ZN965:PA20 | URBAN | Planned |  | 40 | 435 | 0.012019 | 0.0027629 | N
18/10/2016 | 08:30 | ZN12630:PA13 | SHORT RURAL | Planned |  | 18 | 450 | 0.036483 | 0.0081073 | N
18/10/2016 | 09:00 | ZN9900:PA19 | URBAN | Planned |  | 27 | 360 | 0.0067139 | 0.001865 | N
18/10/2016 | 09:00 | ZN874:PA3 | URBAN | Planned |  | 62 | 360 | 0.015417 | 0.0042825 | N
18/10/2016 | 15:00 | ZN12620:PA2 | SHORT RURAL | Planned |  | 81 | 60 | 0.02189 | 0.036483 | N
19/10/2016 | 07:30 | ZN874:PA3 | URBAN | Planned |  | 62 | 450 | 0.019272 | 0.0042826 | N
19/10/2016 | 09:55 | ZN12630:PA22 | SHORT RURAL | Planned |  | 7 | 350 | 0.011035 | 0.0031529 | N
19/10/2016 | 08:00 | ZN12640:PA13 | SHORT RURAL | Planned |  | 166 | 495 | 0.3701 | 0.074768 | N
19/10/2016 | 08:00 | ZN12630:PA13 | SHORT RURAL | Planned |  | 8 | 480 | 0.017296 | 0.0036033 | N
19/10/2016 | 08:20 | ZN14891:PA20 | SHORT RURAL | Planned |  | 11 | 490 | 0.024277 | 0.0049545 | N
19/10/2016 | 08:30 | ZN9700:PA15 | URBAN | Planned |  | 36 | 390 | 0.0096981 | 0.0024867 | N
19/10/2016 | 17:30 | ZN72:PA24 | SHORT RURAL | Planned |  | 22 | 360 | 0.035672 | 0.009909 | N
20/10/2016 | 09:30 | ZN965:PA29 | URBAN | Planned |  | 26 | 330 | 0.0059269 | 0.001796 | N
20/10/2016 | 08:00 | ZN180:PA18 | URBAN | Planned |  | 89 | 480 | 0.02951 | 0.0061479 | N
20/10/2016 | 08:00 | ZN711:PA11 | URBAN | Planned |  | 209 | 510 | 0.07363 | 0.014437 | N
20/10/2016 | 08:00 | ZN14143:PA10 | SHORT RURAL | Planned |  | 2 | 470 | 0.0042339 | 0.00090084 | N
20/10/2016 | 09:30 | ZN9700:PA15 | URBAN | Planned |  | 44 | 330 | 0.01003 | 0.0030394 | N
20/10/2016 | 22:00 | ZN1648:PA16 | URBAN | Planned |  | 53 | 270 | 0.009885 | 0.0036611 | N
21/10/2016 | 08:20 | ZN847:PA31 | URBAN | Planned |  | 2 | 555 | 0.00077057 | 0.00013884 | N
21/10/2016 | 08:00 | ZN14892:PA14 | SHORT RURAL | Planned |  | 2 | 260 | 0.0023565 | 0.00090634 | N
21/10/2016 | 09:00 | ZN12630:PA24 | SHORT RURAL | Planned |  | 10 | 430 | 0.019486 | 0.0045317 | N
21/10/2016 | 22:30 | ZN4990:PA57L | URBAN | Planned |  | 29 | 240 | 0.0048317 | 0.0020132 | N
22/10/2016 | 07:55 | ZN188:PA32 | URBAN | Planned |  | 2 | 515 | 0.00071129 | 0.00013811 | N
22/10/2016 | 07:40 | ZN9534:PA17 | URBAN | Planned |  | 1 | 10,610 | 0.0073269 | 6.9057e-05 | N
22/10/2016 | 07:54 | ZN35800:PA4 | URBAN | Planned |  | 1 | 6 | 4.1434e-06 | 6.9057e-05 | N
22/10/2016 | 09:30 | ZN263:PA33 34ABC | CBD | Planned |  | 19 | 542 | 0.33188 | 0.061233 | N
22/10/2016 | 10:30 | ZN8100:PA4 | URBAN | Planned |  | 17 | 410 | 0.0048133 | 0.001174 | N
22/10/2016 | 15:00 | ZN8000:PA12 | URBAN | Planned |  | 2 | 120 | 0.00016574 | 0.00013811 | N
22/10/2016 | 16:30 | ZN35400:PA106 | URBAN | Planned |  | 9 | 310 | 0.0019267 | 0.00062151 | N
22/10/2016 | 16:30 | ZN188:PA32 | URBAN | Planned |  | 1 | 60 | 4.1434e-05 | 6.9057e-05 | N
22/10/2016 | 22:30 | ZN2473:PA9 | URBAN | Planned |  | 54 | 510 | 0.019018 | 0.0037291 | N
23/10/2016 | 07:00 | ZN7900:PA19 | URBAN | Planned |  | 23 | 437 | 0.006941 | 0.0015883 | N
23/10/2016 | 07:00 | ZN931:PA3 | URBAN | Planned |  | 72 | 234 | 0.01161 | 0.0049722 | N
23/10/2016 | 07:30 | ZN342:PA24 | URBAN | Planned |  | 43 | 320 | 0.0095024 | 0.0029695 | N
24/10/2016 | 07:00 | ZN965:PA29 | URBAN | Planned |  | 90 | 480 | 0.029833 | 0.0062152 | N
24/10/2016 | 07:30 | ZN35370:PA4 | SHORT RURAL | Planned |  | 18 | 555 | 0.044978 | 0.0081042 | N
24/10/2016 | 07:30 | ZN35370:PA8 | SHORT RURAL | Planned |  | 3 | 570 | 0.007699 | 0.0013507 | N
24/10/2016 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 7 | 450 | 0.014182 | 0.0031516 | N
24/10/2016 | 09:30 | ZN14891:PA10 | SHORT RURAL | Planned |  | 105 | 200 | 0.094549 | 0.047274 | N
25/10/2016 | 07:00 | ZN188:PA3 | URBAN | Planned |  | 1 | 370 | 0.00025552 | 6.9059e-05 | N
25/10/2016 | 07:30 | ZN8000:PA8 | URBAN | Planned |  | 1 | 480 | 0.00033148 | 6.9059e-05 | N
25/10/2016 | 07:30 | ZN72:PA24 | SHORT RURAL | Planned |  | 87 | 300 | 0.11751 | 0.03917 | N
25/10/2016 | 07:30 | ZN4545:PA27 | URBAN | Planned |  | 88 | 450 | 0.027347 | 0.0060772 | N
25/10/2016 | 08:00 | ZN35370:PA2 | SHORT RURAL | Planned |  | 50 | 515 | 0.11594 | 0.022512 | N
25/10/2016 | 08:00 | ZN12570:PA22 | SHORT RURAL | Planned |  | 9 | 355 | 0.014385 | 0.0040521 | N
25/10/2016 | 08:30 | ZN12650:PA1 | SHORT RURAL | Planned |  | 23 | 390 | 0.040386 | 0.010355 | N
25/10/2016 | 08:30 | ZN2635:PA31 | URBAN | Planned |  | 152 | 405 | 0.042513 | 0.010497 | N
25/10/2016 | 09:00 | ZN180:PA23 | URBAN | Planned |  | 32 | 580 | 0.012817 | 0.0022099 | N
26/10/2016 | 07:30 | ZN35400:PA79 | URBAN | Planned |  | 13 | 570 | 0.0051173 | 0.00089776 | N
26/10/2016 | 09:00 | ZN2466:PA22 | URBAN | Planned |  | 1 | 750 | 0.00051794 | 6.9059e-05 | N
26/10/2016 | 07:30 | ZN12580:PA10 | URBAN | Planned |  | 41 | 360 | 0.010193 | 0.0028314 | N
26/10/2016 | 08:40 | ZN12570:PA22 | SHORT RURAL | Planned |  | 51 | 400 | 0.091848 | 0.022962 | N
27/10/2016 | 07:15 | ZN36800:PA43 | URBAN | Planned |  | 17 | 330 | 0.003873 | 0.0011736 | N
27/10/2016 | 08:20 | ZN12570:PA37 | SHORT RURAL | Planned |  | 3 | 490 | 0.0066167 | 0.0013503 | N
27/10/2016 | 08:10 | ZN14891:PA5 | SHORT RURAL | Planned |  | 29 | 420 | 0.054824 | 0.013053 | N
27/10/2016 | 08:30 | ZN9700:PA17 | URBAN | Planned |  | 19 | 390 | 0.0051156 | 0.0013117 | N
28/10/2016 | 07:00 | ZN1850:PA9 | URBAN | Planned |  | 1 | 7 | 4.8326e-06 | 6.9037e-05 | N
28/10/2016 | 08:50 | ZN12600:PA2 | SHORT RURAL | Planned |  | 32 | 370 | 0.053294 | 0.014404 | N
28/10/2016 | 08:10 | ZN12650:PA1 | SHORT RURAL | Planned |  | 25 | 447 | 0.0503 | 0.011253 | N
28/10/2016 | 10:50 | ZN12580:PA10 | URBAN | Planned |  | 27 | 270 | 0.0050328 | 0.001864 | N
28/10/2016 | 08:30 | ZN10995:PA1 | URBAN | Planned |  | 40 | 135 | 0.003728 | 0.0027615 | N
28/10/2016 | 09:00 | ZN35370:PA8 | SHORT RURAL | Planned |  | 10 | 440 | 0.019805 | 0.0045012 | N
28/10/2016 | 20:00 | ZN9534:PA18 | URBAN | Planned |  | 3 | 480 | 0.00099413 | 0.00020711 | N
29/10/2016 | 06:30 | ZN263:PA33 34ABC | CBD | Planned |  | 73 | 660 | 1.5527 | 0.23526 | N
29/10/2016 | 07:00 | ZN1600:PA21DEF | CBD | Planned |  | 22 | 255 | 0.1808 | 0.070901 | N
29/10/2016 | 07:30 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 30 | 0.0012153 | 0.004051 | N
29/10/2016 | 17:30 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 30 | 0.0012153 | 0.004051 | N
29/10/2016 | 19:00 | ZN2473:PA33 | URBAN | Planned |  | 39 | 720 | 0.019386 | 0.0026925 | N
30/10/2016 | 07:30 | ZN1788:PA32 | URBAN | Planned |  | 3 | 490 | 0.0010149 | 0.00020712 | N
30/10/2016 | 09:00 | ZN188:PA15 | URBAN | Planned |  | 4 | 480 | 0.0013255 | 0.00027615 | N
31/10/2016 | 07:30 | ZN847:PA23 | URBAN | Planned |  | 1 | 4,590 | 0.0031689 | 6.9038e-05 | N
31/10/2016 | 08:30 | ZN35370:PA8 | SHORT RURAL | Planned |  | 7 | 480 | 0.015124 | 0.0031508 | N
31/10/2016 | 08:05 | ZN12690:PA16 | SHORT RURAL | Planned |  | 19 | 475 | 0.040623 | 0.0085522 | N
31/10/2016 | 09:00 | ZN36200:PA11 | SHORT RURAL | Planned |  | 29 | 400 | 0.052213 | 0.013053 | N
31/10/2016 | 09:00 | ZN3155:PA21 | URBAN | Planned |  | 14 | 420 | 0.0040595 | 0.00096654 | N
31/10/2016 | 11:00 | ZN12650:PA9 | URBAN | Planned |  | 1 | 240 | 0.00016569 | 6.9038e-05 | N
31/10/2016 | 12:30 | ZN12620:PA2 | SHORT RURAL | Planned |  | 1 | 240 | 0.0010803 | 0.00045012 | N
31/10/2016 | 23:31 | ZN3288:PA41 42GHJ | CBD | Planned |  | 240 | 299 | 2.3129 | 0.77354 | N
10/11/2016 | 08:30 | 516:48065 | SHORT RURAL | Planned |  | 5 | 285 | 0.0064127 | 0.0022501 | N
10/11/2016 | 08:00 | 206:34440 | URBAN | Planned |  | 106 | 300 | 0.021952 | 0.0073175 | N
10/11/2016 | 08:30 | 243:80083 | SHORT RURAL | Planned |  | 8 | 360 | 0.01296 | 0.0036001 | N
11/11/2016 | 08:00 | 217:33610 | URBAN | Planned |  | 96 | 227 | 0.015044 | 0.0066271 | N
11/11/2016 | 12:30 | 206:34441 | URBAN | Planned |  | 1 | 130 | 8.9742e-05 | 6.9033e-05 | N
14/11/2016 | 08:00 | 243:80083 | SHORT RURAL | Planned |  | 53 | 470 | 0.11204 | 0.023838 | N
14/11/2016 | 09:45 | 227:13015 | SHORT RURAL | Planned |  | 15 | 265 | 0.017878 | 0.0067465 | N
10/11/2016 | 09:20 | 508:82579 | SHORT RURAL | Planned |  | 2 | 45 | 0.00040501 | 0.00090002 | N
10/11/2016 | 09:40 | 509:33395 | LONG RURAL | Planned |  | 782 | 328 | 91.3773 | 27.8589 | N
10/11/2016 | 08:50 | 507:80922 | SHORT RURAL | Planned |  | 102 | 525 | 0.24098 | 0.045901 | N
10/11/2016 | 22:05 | 229:34995 | SHORT RURAL | Planned |  | 7 | 430 | 0.013545 | 0.0031501 | N
11/11/2016 | 07:10 | 232:11460 | URBAN | Planned |  | 137 | 240 | 0.022698 | 0.0094575 | N
11/11/2016 | 08:30 | 229:34995 | SHORT RURAL | Planned |  | 4 | 290 | 0.0052201 | 0.0018 | N
11/11/2016 | 08:03 | 230:81432 | SHORT RURAL | Planned |  | 1 | 492 | 0.0022141 | 0.00045001 | N
14/11/2016 | 08:30 | 229:34995 | SHORT RURAL | Planned |  | 167 | 40 | 0.030044 | 0.075111 | N
14/11/2016 | 17:00 | 532:83312 | URBAN | Planned |  | 21 | 160 | 0.0023188 | 0.0014492 | N
10/11/2016 | 09:20 | 813:89062 | SHORT RURAL | Planned |  | 3 | 260 | 0.0035101 | 0.00135 | N
11/11/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 140 | 0.049875 | 0.035625 | N
11/11/2016 | 08:40 | 807:74179 | SHORT RURAL | Planned |  | 5 | 265 | 0.0059626 | 0.0022501 | N
11/11/2016 | 08:30 | 523:33508 | SHORT RURAL | Planned |  | 4 | 325 | 0.0058501 | 0.0018 | N
14/11/2016 | 09:00 | 811:74234 | SHORT RURAL | Planned |  | 1 | 50 | 0.00022488 | 0.00044977 | N
14/11/2016 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 2 | 80 | 0.05698 | 0.071225 | N
15/11/2016 | 06:00 | 240:34840 | URBAN | Planned |  | 2 | 600 | 0.00082814 | 0.00013802 | N
15/11/2016 | 08:45 | 243:80083 | SHORT RURAL | Planned |  | 8 | 260 | 0.0093553 | 0.0035982 | N
15/11/2016 | 08:45 | 524:33576 | SHORT RURAL | Planned |  | 10 | 167 | 0.0075112 | 0.0044977 | N
15/11/2016 | 12:40 | 526:34640 | SHORT RURAL | Planned |  | 3 | 100 | 0.0013493 | 0.0013493 | N
15/11/2016 | 17:00 | 235:2123 | URBAN | Planned |  | 1 | 210 | 0.00014492 | 6.9011e-05 | N
16/11/2016 | 09:05 | 807:74184 | SHORT RURAL | Planned |  | 5 | 190 | 0.0042729 | 0.0022489 | N
16/11/2016 | 08:40 | 227:13015 | SHORT RURAL | Planned |  | 15 | 395 | 0.026649 | 0.0067467 | N
16/11/2016 | 09:45 | 224:80340 | SHORT RURAL | Planned |  | 7 | 245 | 0.0077137 | 0.0031484 | N
16/11/2016 | 08:05 | 512:48048 | SHORT RURAL | Planned |  | 2 | 355 | 0.0031934 | 0.00089956 | N
16/11/2016 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 20 | 140 | 0.012594 | 0.0089956 | N
16/11/2016 | 08:50 | 232:33413 | URBAN | Planned |  | 20 | 240 | 0.0033126 | 0.0013802 | N
16/11/2016 | 08:30 | 504:48033 | SHORT RURAL | Planned |  | 20 | 360 | 0.032384 | 0.0089956 | N
16/11/2016 | 08:30 | 504:48033 | SHORT RURAL | Planned |  | 78 | 360 | 0.1263 | 0.035083 | N
16/11/2016 | 08:30 | 813:89062 | SHORT RURAL | Planned |  | 10 | 170 | 0.0076462 | 0.0044978 | N
18/11/2016 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 12 | 280 | 0.015108 | 0.0053958 | N
17/11/2016 | 09:30 | 232:33409 | SHORT RURAL | Planned |  | 57 | 135 | 0.0346 | 0.02563 | N
17/11/2016 | 09:15 | 265:81651 | SHORT RURAL | Planned |  | 3 | 130 | 0.0017536 | 0.0013489 | N
17/11/2016 | 08:30 | 230:81434 | URBAN | Planned |  | 82 | 305 | 0.017255 | 0.0056573 | N
17/11/2016 | 12:40 | 265:81651 | SHORT RURAL | Planned |  | 6 | 100 | 0.0026979 | 0.0026979 | N
17/11/2016 | 09:50 | 806:82662 | SHORT RURAL | Planned |  | 3 | 100 | 0.0013489 | 0.0013489 | N
17/11/2016 | 08:00 | 812:19072 | SHORT RURAL | Planned |  | 3 | 285 | 0.0038445 | 0.0013489 | N
17/11/2016 | 08:30 | 514:18146 | SHORT RURAL | Planned |  | 5 | 384 | 0.0086332 | 0.0022482 | N
18/11/2016 | 09:30 | 811:74234 | SHORT RURAL | Planned |  | 1 | 45 | 0.00020234 | 0.00044965 | N
18/11/2016 | 10:50 | 811:74234 | SHORT RURAL | Planned |  | 2 | 65 | 0.00058454 | 0.00089929 | N
21/11/2016 | 08:30 | 221:11899 | SHORT RURAL | Planned |  | 1 | 350 | 0.0015738 | 0.00044965 | N
21/11/2016 | 08:00 | 528:83019 | SHORT RURAL | Planned |  | 108 | 450 | 0.21853 | 0.048562 | N
21/11/2016 | 10:30 | 511:29878 | SHORT RURAL | Planned |  | 12 | 335 | 0.018076 | 0.0053958 | N
22/11/2016 | 08:40 | 516:48066 | SHORT RURAL | Planned |  | 22 | 320 | 0.031655 | 0.0098923 | N
23/11/2016 | 08:30 | 265:81648 | SHORT RURAL | Planned |  | 75 | 290 | 0.097799 | 0.033724 | N
22/11/2016 | 08:00 | 227:13015 | SHORT RURAL | Planned |  | 139 | 507 | 0.31688 | 0.062501 | N
22/11/2016 | 09:10 | 220:8689 | URBAN | Planned |  | 1 | 400 | 0.00027598 | 6.8996e-05 | N
22/11/2016 | 08:00 | 258:80784 | URBAN | Planned |  | 95 | 400 | 0.026218 | 0.0065546 | N
22/11/2016 | 09:00 | 217:33611 | URBAN | Planned |  | 63 | 280 | 0.012171 | 0.0043467 | N
22/11/2016 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 8 | 305 | 0.86895 | 0.2849 | N
22/11/2016 | 09:30 | 511:29878 | SHORT RURAL | Planned |  | 1 | 170 | 0.0007644 | 0.00044965 | N
22/11/2016 | 08:30 | 508:82579 | SHORT RURAL | Planned |  | 12 | 420 | 0.022662 | 0.0053958 | N
22/11/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 15 | 370 | 0.024955 | 0.0067447 | N
22/11/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 24 | 230 | 1.9658 | 0.8547 | N
22/11/2016 | 12:30 | 813:89062 | SHORT RURAL | Planned |  | 2 | 30 | 0.00026979 | 0.0008993 | N
23/11/2016 | 08:35 | 239:82133 | URBAN | Planned |  | 34 | 265 | 0.0062167 | 0.0023459 | N
23/11/2016 | 08:00 | 223:14399 | SHORT RURAL | Planned |  | 2 | 442 | 0.0039749 | 0.0008993 | N
23/11/2016 | 07:20 | 524:33580 | SHORT RURAL | Planned |  | 46 | 480 | 0.099283 | 0.020684 | N
23/11/2016 | 09:10 | 524:33572 | SHORT RURAL | Planned |  | 1 | 155 | 0.00069696 | 0.00044965 | N
23/11/2016 | 09:40 | 235:2120 | SHORT RURAL | Planned |  | 3 | 147 | 0.001983 | 0.001349 | N
24/11/2016 | 07:30 | ZN965:PA38 | URBAN | Planned |  | 13 | 450 | 0.0040352 | 0.00089671 | N
23/11/2016 | 08:24 | 507:80925 | SHORT RURAL | Planned |  | 59 | 376 | 0.09975 | 0.026529 | N
23/11/2016 | 08:40 | 813:89062 | SHORT RURAL | Planned |  | 1 | 150 | 0.00067448 | 0.00044965 | N
24/11/2016 | 08:05 | 509:33395 | LONG RURAL | Planned |  | 747 | 625 | 166.2068 | 26.5931 | N
25/11/2016 | 07:30 | 228:7490 | SHORT RURAL | Planned |  | 1 | 650 | 0.0029215 | 0.00044945 | N
27/11/2016 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 138 | 450 | 0.27911 | 0.062025 | N
27/11/2016 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 321 | 450 | 51.424 | 11.4276 | N
27/11/2016 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 197 | 450 | 0.39844 | 0.088543 | N
27/11/2016 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 565 | 450 | 1.1427 | 0.25394 | N
25/11/2016 | 09:45 | 232:11454 | SHORT RURAL | Planned |  | 205 | 210 | 0.19349 | 0.092138 | N
27/11/2016 | 08:00 | 213:33775 | URBAN | Planned |  | 50 | 426 | 0.014703 | 0.0034514 | N
24/11/2016 | 08:15 | 217:33611 | URBAN | Planned |  | 87 | 240 | 0.014403 | 0.006001 | N
24/11/2016 | 08:00 | 224:80329 | SHORT RURAL | Planned |  | 1 | 620 | 0.0027866 | 0.00044945 | N
25/11/2016 | 09:55 | 206:34434 | URBAN | Planned |  | 113 | 150 | 0.011692 | 0.0077945 | N
25/11/2016 | 08:50 | 504:48033 | SHORT RURAL | Planned |  | 2 | 220 | 0.0019776 | 0.00089891 | N
25/11/2016 | 08:30 | 507:80923 | SHORT RURAL | Planned |  | 1 | 173 | 0.00077756 | 0.00044945 | N
25/11/2016 | 10:10 | 235:2120 | SHORT RURAL | Planned |  | 1 | 215 | 0.00096633 | 0.00044945 | N
25/11/2016 | 09:20 | 264:81240 | SHORT RURAL | Planned |  | 4 | 315 | 0.0056631 | 0.0017978 | N
25/11/2016 | 09:10 | 502:48004 | URBAN | Planned |  | 65 | 125 | 0.0056044 | 0.0044835 | N
25/11/2016 | 10:40 | 507:80932 | SHORT RURAL | Planned |  | 109 | 220 | 0.10778 | 0.048991 | N
26/11/2016 | 07:40 | 238:34144 | URBAN | Planned |  | 1 | 523 | 0.00036102 | 6.9028e-05 | N
28/11/2016 | 07:50 | ZN2400:PA11 | SHORT RURAL | Planned |  | 58 | 720 | 0.18769 | 0.026068 | N
24/11/2016 | 08:36 | 515:35192 | SHORT RURAL | Planned |  | 23 | 104 | 0.010751 | 0.010337 | N
24/11/2016 | 08:30 | 807:74180 | SHORT RURAL | Planned |  | 4 | 210 | 0.0037754 | 0.0017978 | N
24/11/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 23 | 200 | 0.020675 | 0.010337 | N
24/11/2016 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 11 | 135 | 0.0066744 | 0.004944 | N
25/11/2016 | 08:35 | 515:35192 | SHORT RURAL | Planned |  | 10 | 180 | 0.0080902 | 0.0044945 | N
25/11/2016 | 08:50 | 806:82662 | SHORT RURAL | Planned |  | 1 | 205 | 0.00092138 | 0.00044945 | N
27/11/2016 | 08:00 | 802:82225 | SHORT RURAL | Planned |  | 106 | 518 | 0.24679 | 0.047642 | N
27/11/2016 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 2 | 370 | 0.003326 | 0.00089891 | N
27/11/2016 | 16:30 | 810:74050 | SHORT RURAL | Planned |  | 12 | 5 | 0.00026967 | 0.0053935 | N
28/11/2016 | 08:34 | 801:74121 | LONG RURAL | Planned |  | 4 | 386 | 0.54966 | 0.1424 | N
28/11/2016 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 14 | 335 | 0.021079 | 0.0062924 | N
28/11/2016 | 07:15 | 202:34262 | URBAN | Planned |  | 3 | 935 | 0.0019362 | 0.00020709 | N
28/11/2016 | 08:45 | 243:80083 | SHORT RURAL | Planned |  | 53 | 375 | 0.089329 | 0.023821 | N
28/11/2016 | 09:00 | 227:13020 | SHORT RURAL | Planned |  | 158 | 360 | 0.25565 | 0.071014 | N
28/11/2016 | 09:30 | 223:14395 | SHORT RURAL | Planned |  | 17 | 450 | 0.034383 | 0.0076407 | N
28/11/2016 | 08:15 | 532:83309 | SHORT RURAL | Planned |  | 2 | 285 | 0.0025619 | 0.00089891 | N
28/11/2016 | 08:00 | 232:11457 | SHORT RURAL | Planned |  | 1 | 330 | 0.0014832 | 0.00044945 | N
28/11/2016 | 09:07 | 508:82579 | SHORT RURAL | Planned |  | 3 | 143 | 0.0019282 | 0.0013484 | N
28/11/2016 | 08:35 | 528:83019 | SHORT RURAL | Planned |  | 3 | 275 | 0.003708 | 0.0013484 | N
28/11/2016 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 8 | 190 | 0.54112 | 0.2848 | N
28/11/2016 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 7 | 220 | 0.0069216 | 0.0031462 | N
29/11/2016 | 09:00 | 528:83019 | SHORT RURAL | Planned |  | 208 | 231 | 0.21595 | 0.093487 | N
29/11/2016 | 08:55 | 814:82285 | SHORT RURAL | Planned |  | 15 | 215 | 0.014495 | 0.0067418 | N
29/11/2016 | 08:03 | 801:74121 | LONG RURAL | Planned |  | 10 | 462 | 1.6447 | 0.356 | N
29/11/2016 | 07:30 | 239:82127 | SHORT RURAL | Planned |  | 8 | 555 | 0.019956 | 0.0035956 | N
29/11/2016 | 07:30 | 258:80778 | URBAN | Planned |  | 1 | 175 | 0.0001208 | 6.9028e-05 | N
29/11/2016 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 16 | 360 | 0.025889 | 0.0071913 | N
29/11/2016 | 08:50 | 235:2120 | SHORT RURAL | Planned |  | 22 | 267 | 0.026401 | 0.009888 | N
29/11/2016 | 09:10 | 528:83019 | SHORT RURAL | Planned |  | 1 | 170 | 0.00076407 | 0.00044945 | N
29/11/2016 | 08:45 | 242:81538 | URBAN | Planned |  | 199 | 270 | 0.037089 | 0.013737 | N
29/11/2016 | 09:45 | 238:34141 | SHORT RURAL | Planned |  | 2 | 125 | 0.0011236 | 0.00089891 | N
29/11/2016 | 09:00 | 526:34639 | SHORT RURAL | Planned |  | 3 | 240 | 0.0032361 | 0.0013484 | N
29/11/2016 | 08:30 | 523:33509 | URBAN | Planned |  | 57 | 325 | 0.012788 | 0.0039346 | N
29/11/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 22 | 330 | 0.03263 | 0.009888 | N
29/11/2016 | 08:30 | 807:74183 | SHORT RURAL | Planned |  | 6 | 275 | 0.007416 | 0.0026967 | N
30/11/2016 | 22:43 | 261:81870 | URBAN | Planned |  | 1,763 | 1 | 0.001217 | 0.1217 | N
01/12/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 29 | 250 | 0.032572 | 0.013029 | N
30/11/2016 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 46 | 400 | 0.0827 | 0.020675 | N
30/11/2016 | 10:20 | 235:2120 | SHORT RURAL | Planned |  | 2 | 168 | 0.0015102 | 0.00089891 | N
30/11/2016 | 08:30 | 523:33507 | URBAN | Planned |  | 50 | 340 | 0.011735 | 0.0034514 | N
30/11/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 15 | 300 | 0.020225 | 0.0067418 | N
30/11/2016 | 08:30 | 807:74180 | SHORT RURAL | Planned |  | 2 | 295 | 0.0026518 | 0.00089891 | N
01/12/2016 | 08:15 | 217:33612 | URBAN | Planned |  | 39 | 485 | 0.013053 | 0.0026913 | N
01/12/2016 | 08:35 | 227:13015 | SHORT RURAL | Planned |  | 12 | 425 | 0.022913 | 0.0053912 | N
01/12/2016 | 07:30 | 206:34432 | URBAN | Planned |  | 1 | 530 | 0.00036575 | 6.9009e-05 | N
01/12/2016 | 10:00 | 202:34262 | URBAN | Planned |  | 2 | 240 | 0.00033124 | 0.00013802 | N
01/12/2016 | 09:00 | 264:81244 | SHORT RURAL | Planned |  | 1 | 261 | 0.0011726 | 0.00044927 | N
02/12/2016 | 08:08 | 509:33397 | SHORT RURAL | Planned |  | 71 | 447 | 0.14258 | 0.031898 | N
02/12/2016 | 09:00 | 232:33413 | URBAN | Planned |  | 95 | 240 | 0.015734 | 0.0065558 | N
02/12/2016 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 3 | 240 | 0.0032347 | 0.0013478 | N
02/12/2016 | 08:10 | 807:74180 | SHORT RURAL | Planned |  | 18 | 215 | 0.017387 | 0.0080868 | N
02/12/2016 | 09:00 | 523:33503 | URBAN | Planned |  | 68 | 160 | 0.0075081 | 0.0046926 | N
02/12/2016 | 09:10 | 523:33507 | URBAN | Planned |  | 62 | 155 | 0.0066317 | 0.0042785 | N
02/12/2016 | 09:15 | 515:35197 | LONG RURAL | Planned |  | 2 | 105 | 0.07476 | 0.0712 | N
02/12/2016 | 09:30 | 806:82662 | SHORT RURAL | Planned |  | 2 | 285 | 0.0025608 | 0.00089853 | N
05/12/2016 | 08:45 | 513:48059 | SHORT RURAL | Planned |  | 2 | 100 | 0.00089855 | 0.00089855 | N
05/12/2016 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 25 | 240 | 0.026956 | 0.011232 | N
05/12/2016 | 09:45 | 811:74234 | SHORT RURAL | Planned |  | 3 | 190 | 0.0025609 | 0.0013478 | N
06/12/2016 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 12 | 375 | 0.020217 | 0.0053913 | N
06/12/2016 | 09:00 | 508:82579 | SHORT RURAL | Planned |  | 37 | 360 | 0.059843 | 0.016623 | N
06/12/2016 | 09:18 | 242:81541 | URBAN | Planned |  | 141 | 277 | 0.026934 | 0.0097235 | N
06/12/2016 | 09:00 | 235:2120 | SHORT RURAL | Planned |  | 16 | 345 | 0.0248 | 0.0071884 | N
06/12/2016 | 08:45 | 523:33503 | URBAN | Planned |  | 95 | 130 | 0.0085167 | 0.0065513 | N
06/12/2016 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 43 | 420 | 0.081139 | 0.019319 | N
07/12/2016 | 09:00 | 225:33676 | URBAN | Planned |  | 108 | 300 | 0.022344 | 0.0074479 | N
07/12/2016 | 09:30 | 224:80346 | URBAN | Planned |  | 53 | 315 | 0.011513 | 0.003655 | N
12/12/2016 | 08:30 | 224:80332 | URBAN | Planned |  | 43 | 390 | 0.011561 | 0.0029645 | N
08/12/2016 | 08:35 | 806:82662 | SHORT RURAL | Planned |  | 34 | 330 | 0.050418 | 0.015278 | N
09/12/2016 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 40 | 320 | 4.5568 | 1.424 | N
09/12/2016 | 08:10 | 216:10726 | URBAN | Planned |  | 97 | 500 | 0.033435 | 0.006687 | N
09/12/2016 | 08:53 | 515:35197 | LONG RURAL | Planned |  | 8 | 277 | 0.78889 | 0.2848 | N
12/12/2016 | 08:30 | 224:80337 | SHORT RURAL | Planned |  | 204 | 390 | 0.35751 | 0.091668 | N
01/11/2016 | 07:30 | ZN9534:PA18 | URBAN | Planned |  | 3 | 480 | 0.00099419 | 0.00020712 | N
01/11/2016 | 07:30 | ZN35370:PA8 | SHORT RURAL | Planned |  | 41 | 520 | 0.095973 | 0.018456 | N
01/11/2016 | 08:00 | ZN35370:PA8 | SHORT RURAL | Planned |  | 8 | 450 | 0.016206 | 0.0036013 | N
01/11/2016 | 12:00 | ZN874:PA9 | URBAN | Planned |  | 1 | 330 | 0.00022784 | 6.9041e-05 | N
01/11/2016 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 5 | 480 | 0.010804 | 0.0022508 | N
01/11/2016 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 27 | 360 | 0.043755 | 0.012154 | N
02/11/2016 | 07:30 | ZN965:PA38 | URBAN | Planned |  | 17 | 450 | 0.0052818 | 0.0011737 | N
02/11/2016 | 07:30 | ZN2602:PA36 | URBAN | Planned |  | 80 | 540 | 0.029827 | 0.0055235 | N
08/12/2016 | 08:20 | 202:34254 | URBAN | Planned |  | 112 | 515 | 0.039762 | 0.0077207 | N
02/11/2016 | 07:30 | ZN35370:PA8 | SHORT RURAL | Planned |  | 3 | 630 | 0.0085081 | 0.0013505 | N
02/11/2016 | 08:00 | ZN14891:PA1 | SHORT RURAL | Planned |  | 84 | 480 | 0.18151 | 0.037814 | N
02/11/2016 | 08:00 | ZN14891:PA16 | SHORT RURAL | Planned |  | 24 | 480 | 0.051859 | 0.010804 | N
08/12/2016 | 09:30 | 206:34434 | URBAN | Planned |  | 145 | 116 | 0.011595 | 0.0099956 | N
02/11/2016 | 08:00 | ZN12690:PA16 | SHORT RURAL | Planned |  | 48 | 510 | 0.1102 | 0.021608 | N
09/12/2016 | 11:20 | 224:80337 | SHORT RURAL | Planned |  | 27 | 140 | 0.016985 | 0.012132 | N
12/12/2016 | 13:00 | 512:48049 | SHORT RURAL | Planned |  | 8 | 72 | 0.0025883 | 0.0035948 | N
02/11/2016 | 08:00 | ZN12640:PA13 | SHORT RURAL | Planned |  | 24 | 480 | 0.051859 | 0.010804 | N
02/11/2016 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 9 | 480 | 0.019447 | 0.0040515 | N
02/11/2016 | 08:00 | ZN12620:PA1 | SHORT RURAL | Planned |  | 15 | 480 | 0.032412 | 0.0067524 | N
02/11/2016 | 08:00 | ZN35600:PA14 | URBAN | Planned |  | 25 | 420 | 0.0072496 | 0.0017261 | N
08/12/2016 | 08:45 | 265:81651 | SHORT RURAL | Planned |  | 66 | 380 | 0.1127 | 0.029658 | N
03/11/2016 | 07:30 | ZN10996:PA8 | URBAN | Planned |  | 40 | 570 | 0.015737 | 0.0027609 | N
03/11/2016 | 08:00 | ZN13000:PA7 | SHORT RURAL | Planned |  | 35 | 480 | 0.075596 | 0.015749 | N
03/11/2016 | 08:00 | ZN15008:PA5 | URBAN | Planned |  | 73 | 420 | 0.021163 | 0.0050387 | N
08/12/2016 | 09:40 | 532:83293 | URBAN | Planned |  | 92 | 305 | 0.019343 | 0.006342 | N
09/12/2016 | 08:35 | 507:80914 | SHORT RURAL | Planned |  | 100 | 325 | 0.14604 | 0.044934 | N
03/11/2016 | 09:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 19 | 360 | 0.030779 | 0.0085496 | N
09/12/2016 | 09:00 | 508:82579 | SHORT RURAL | Planned |  | 1 | 240 | 0.0010784 | 0.00044934 | N
03/11/2016 | 09:00 | ZN2635:PA39 | URBAN | Planned |  | 67 | 480 | 0.022198 | 0.0046246 | N
03/11/2016 | 09:45 | ZN931:PA10 | URBAN | Planned |  | 121 | 285 | 0.023803 | 0.0083518 | N
04/11/2016 | 07:30 | ZN847:PA39 | URBAN | Planned |  | 1 | 510 | 0.00035202 | 6.9023e-05 | N
04/11/2016 | 08:00 | ZN10997:PA2 | URBAN | Planned |  | 73 | 480 | 0.024186 | 0.0050387 | N
10/12/2016 | 07:45 | 264:81232 | URBAN | Planned |  | 1 | 468 | 0.00032264 | 6.8939e-05 | N
04/11/2016 | 08:00 | ZN12630:PA25 | SHORT RURAL | Planned |  | 1 | 450 | 0.0020249 | 0.00044998 | N
05/11/2016 | 09:10 | ZN12650:PA14 | URBAN | Planned |  | 43 | 380 | 0.011279 | 0.0029682 | N
05/11/2016 | 08:30 | ZN129:PA27 | URBAN | Planned |  | 1 | 420 | 0.00028991 | 6.9027e-05 | N
05/11/2016 | 07:30 | ZN263:PA33 34DEF | CBD | Planned |  | 54 | 550 | 0.95705 | 0.17401 | N
08/12/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 46 | 195 | 0.040307 | 0.02067 | N
05/11/2016 | 08:00 | ZN711:PA24 | URBAN | Planned |  | 16 | 600 | 0.0066266 | 0.0011044 | N
05/11/2016 | 08:00 | ZN10996:PA9 | URBAN | Planned |  | 57 | 450 | 0.017705 | 0.0039345 | N
08/12/2016 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 2 | 265 | 0.18868 | 0.0712 | N
08/12/2016 | 10:10 | 812:19071 | SHORT RURAL | Planned |  | 1 | 200 | 0.00089871 | 0.00044936 | N
06/11/2016 | 06:30 | ZN2602:PA8 | URBAN | Planned |  | 77 | 545 | 0.028968 | 0.0053152 | N
06/11/2016 | 06:30 | ZN263:PA33 34GHJ | CBD | Planned |  | 8 | 1,170 | 0.30161 | 0.025779 | N
06/11/2016 | 07:00 | ZN10993:PA34 | URBAN | Planned |  | 28 | 660 | 0.012756 | 0.0019328 | N
06/11/2016 | 07:30 | ZN35800:PA16 | URBAN | Planned |  | 1 | 270 | 0.00018638 | 6.9028e-05 | N
07/11/2016 | 03:00 | ZN15011:PA10 | URBAN | Planned |  | 2 | 1,080 | 0.001491 | 0.00013806 | N
07/11/2016 | 08:00 | ZN711:PA11 | URBAN | Planned |  | 108 | 570 | 0.042494 | 0.007455 | N
07/11/2016 | 08:00 | ZN12610:PA10 | URBAN | Planned |  | 33 | 480 | 0.010934 | 0.0022779 | N
07/11/2016 | 08:15 | ZN14891:PA12 | SHORT RURAL | Planned |  | 18 | 495 | 0.040094 | 0.0080999 | N
07/11/2016 | 09:20 | ZN1193:PA21 | URBAN | Planned |  | 8 | 230 | 0.0012701 | 0.00055222 | N
07/11/2016 | 09:00 | ZN12570:PA26 | URBAN | Planned |  | 2 | 345 | 0.00047629 | 0.00013806 | N
07/11/2016 | 09:30 | ZN398:PA31 | URBAN | Planned |  | 95 | 330 | 0.02164 | 0.0065577 | N
08/11/2016 | 08:10 | ZN12600:PA2 | SHORT RURAL | Planned |  | 8 | 465 | 0.01674 | 0.0036 | N
08/11/2016 | 08:00 | ZN12640:PA1 | SHORT RURAL | Planned |  | 1 | 420 | 0.00189 | 0.00045 | N
08/11/2016 | 08:00 | ZN12640:PA1 | SHORT RURAL | Planned |  | 13 | 420 | 0.02457 | 0.00585 | N
08/11/2016 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 9 | 480 | 0.01944 | 0.00405 | N
08/11/2016 | 08:42 | ZN36800:PA58 | URBAN | Planned |  | 49 | 583 | 0.01972 | 0.0033824 | N
08/11/2016 | 09:10 | ZN36800:PA57 | URBAN | Planned |  | 102 | 350 | 0.024643 | 0.007041 | N
08/11/2016 | 09:30 | ZN10999:PA29 | URBAN | Planned |  | 46 | 330 | 0.010479 | 0.0031754 | N
08/11/2016 | 19:00 | ZN10999:PA16 | URBAN | Planned |  | 29 | 1,560 | 0.031229 | 0.0020019 | N
09/11/2016 | 07:40 | ZN188:PA13 | URBAN | Planned |  | 1 | 365 | 0.00025196 | 6.9031e-05 | N
09/11/2016 | 08:00 | ZN10993:PA22 | URBAN | Planned |  | 87 | 495 | 0.029728 | 0.0060057 | N
09/11/2016 | 08:30 | ZN129:PA5 | URBAN | Planned |  | 34 | 240 | 0.0056329 | 0.002347 | N
09/11/2016 | 09:30 | ZN398:PA31 | URBAN | Planned |  | 95 | 330 | 0.021641 | 0.0065579 | N
09/11/2016 | 09:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 14 | 210 | 0.01323 | 0.0063 | N
09/11/2016 | 09:30 | ZN1290:PA12 | URBAN | Planned |  | 1 | 360 | 0.00024851 | 6.9031e-05 | N
10/11/2016 | 08:00 | ZN188:PA13 | URBAN | Planned |  | 1 | 325 | 0.00022436 | 6.9033e-05 | N
10/11/2016 | 07:30 | ZN9118:PA7 | URBAN | Planned |  | 37 | 450 | 0.011494 | 0.0025542 | N
10/11/2016 | 07:30 | ZN12650:PA12 | URBAN | Planned |  | 45 | 390 | 0.012115 | 0.0031065 | N
10/11/2016 | 08:00 | ZN180:PA18 | URBAN | Planned |  | 89 | 480 | 0.029491 | 0.0061439 | N
10/11/2016 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 33 | 440 | 0.065342 | 0.01485 | N
10/11/2016 | 08:00 | ZN12600:PA1 | SHORT RURAL | Planned |  | 17 | 240 | 0.01836 | 0.0076502 | N
10/11/2016 | 08:00 | ZN12600:PA1 | SHORT RURAL | Planned |  | 27 | 240 | 0.029161 | 0.01215 | N
10/11/2016 | 08:35 | ZN12570:PA22 | SHORT RURAL | Planned |  | 51 | 400 | 0.091802 | 0.022951 | N
10/11/2016 | 09:15 | ZN263:PA33 34GHJ | CBD | Planned |  | 11 | 150 | 0.053174 | 0.03545 | N
28/11/2016 | 08:40 | ZN12570:PA33 | SHORT RURAL | Planned |  | 31 | 385 | 0.053642 | 0.013933 | N
10/11/2016 | 09:30 | ZN2602:PA21 | URBAN | Planned |  | 80 | 360 | 0.019881 | 0.0055226 | N
11/11/2016 | 08:00 | ZN2835:PA41 | URBAN | Planned |  | 1 | 420 | 0.00028994 | 6.9033e-05 | N
11/11/2016 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 7 | 480 | 0.01512 | 0.0031501 | N
11/11/2016 | 08:05 | ZN80:PA21 | URBAN | Planned |  | 31 | 232 | 0.0049648 | 0.00214 | N
11/11/2016 | 08:45 | ZN36100:PA27 | URBAN | Planned |  | 71 | 165 | 0.0080872 | 0.0049013 | N
12/11/2016 | 07:10 | ZN2466:PA19 | URBAN | Planned |  | 1 | 1 | 6.9011e-07 | 6.9011e-05 | N
12/11/2016 | 07:00 | ZN901:PA7 | URBAN | Planned |  | 5 | 12 | 4.1407e-05 | 0.00034506 | N
12/11/2016 | 10:30 | ZN4990:PA51 52KLM | CBD | Planned |  | 6 | 65 | 0.012566 | 0.019332 | N
13/11/2016 | 07:30 | ZN8700:PA61 62KLM | CBD | Planned |  | 30 | 510 | 0.49298 | 0.096662 | N
14/11/2016 | 05:00 | ZN931:PA31 | URBAN | Planned |  | 2 | 30 | 4.1406e-05 | 0.00013802 | N
14/11/2016 | 07:30 | ZN901:PA19 | URBAN | Planned |  | 67 | 300 | 0.013871 | 0.0046237 | N
14/11/2016 | 08:40 | ZN12570:PA35 | URBAN | Planned |  | 97 | 440 | 0.029454 | 0.0066941 | N
14/11/2016 | 10:45 | ZN12600:PA9 | SHORT RURAL | Planned |  | 50 | 225 | 0.050599 | 0.022488 | N
15/11/2016 | 07:35 | ZN12630:PA24 | SHORT RURAL | Planned |  | 26 | 607 | 0.070983 | 0.011694 | N
15/11/2016 | 07:00 | ZN4545:PA2 | URBAN | Planned |  | 159 | 630 | 0.069129 | 0.010973 | N
15/11/2016 | 08:00 | ZN9245:PA13 | URBAN | Planned |  | 73 | 390 | 0.019648 | 0.0050378 | N
15/11/2016 | 08:30 | ZN342:PA22 | URBAN | Planned |  | 114 | 300 | 0.023602 | 0.0078673 | N
15/11/2016 | 10:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 42 | 360 | 0.068006 | 0.01889 | N
15/11/2016 | 09:00 | ZN12570:PA33 | SHORT RURAL | Planned |  | 128 | 370 | 0.21301 | 0.057571 | N
15/11/2016 | 09:15 | ZN188:PA26 | URBAN | Planned |  | 9 | 285 | 0.0017701 | 0.0006211 | N
16/11/2016 | 07:00 | ZN12690:PA12 | SHORT RURAL | Planned |  | 3 | 1,890 | 0.025502 | 0.0013493 | N
16/11/2016 | 07:30 | ZN12620:PA2 | SHORT RURAL | Planned |  | 1 | 560 | 0.0025188 | 0.00044978 | N
16/11/2016 | 09:00 | ZN15013:PA10 | SHORT RURAL | Planned |  | 31 | 420 | 0.058561 | 0.013943 | N
16/11/2016 | 08:00 | ZN12630:PA22 | SHORT RURAL | Planned |  | 5 | 450 | 0.01012 | 0.0022489 | N
16/11/2016 | 08:30 | ZN2568:PA15 | URBAN | Planned |  | 2 | 640 | 0.00088335 | 0.00013802 | N
16/11/2016 | 09:00 | ZN12580:PA10 | URBAN | Planned |  | 10 | 390 | 0.0026915 | 0.00069012 | N
16/11/2016 | 11:25 | ZN12650:PA14 | URBAN | Planned |  | 59 | 215 | 0.0087542 | 0.0040717 | N
16/11/2016 | 17:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 14 | 240 | 0.015113 | 0.0062969 | N
16/11/2016 | 19:10 | ZN8000:PA39 | URBAN | Planned |  | 19 | 170 | 0.0022291 | 0.0013112 | N
17/11/2016 | 07:40 | ZN36100:PA23 | URBAN | Planned |  | 251 | 520 | 0.090047 | 0.017317 | N
17/11/2016 | 07:30 | ZN1648:PA21 | URBAN | Planned |  | 2 | 750 | 0.0010349 | 0.00013798 | N
17/11/2016 | 07:30 | ZN129:PA16 | URBAN | Planned |  | 74 | 510 | 0.026037 | 0.0051053 | N
17/11/2016 | 09:00 | ZN36800:PA57 | URBAN | Planned |  | 78 | 240 | 0.012915 | 0.0053813 | N
17/11/2016 | 08:30 | ZN1788:PA14 | URBAN | Planned |  | 24 | 360 | 0.0059608 | 0.0016558 | N
17/11/2016 | 09:00 | ZN14891:PA20 | SHORT RURAL | Planned |  | 41 | 290 | 0.053463 | 0.018436 | N
17/11/2016 | 09:00 | ZN8000:PA15 | URBAN | Planned |  | 2 | 7,470 | 0.010307 | 0.00013798 | N
17/11/2016 | 09:30 | ZN10996:PA11 | URBAN | Planned |  | 87 | 360 | 0.021608 | 0.0060022 | N
18/11/2016 | 09:50 | ZN14891:PA5 | SHORT RURAL | Planned |  | 3 | 150 | 0.0020234 | 0.0013489 | N
18/11/2016 | 09:00 | ZN180:PA7 | URBAN | Planned |  | 52 | 360 | 0.012915 | 0.0035875 | N
19/11/2016 | 05:30 | ZN8000:PA28 | URBAN | Planned |  | 2 | 1,800 | 0.0024838 | 0.00013799 | N
19/11/2016 | 07:30 | ZN874:PA12 | URBAN | Planned |  | 3 | 310 | 0.00064164 | 0.00020698 | N
19/11/2016 | 08:10 | ZN1068:PA17 | URBAN | Planned |  | 3 | 520 | 0.0010763 | 0.00020698 | N
19/11/2016 | 20:30 | ZN3288:PA43 44GHJ | CBD | Planned |  | 39 | 780 | 0.97968 | 0.1256 | N
20/11/2016 | 07:35 | ZN7900:PA24 | URBAN | Planned |  | 2 | 325 | 0.00044847 | 0.00013799 | N
20/11/2016 | 08:00 | ZN15001:PA8 | URBAN | Planned |  | 12 | 480 | 0.0039741 | 0.00082794 | N
21/11/2016 | 00:30 | ZN12610:PA9 | URBAN | Planned |  | 7 | 5 | 2.4148e-05 | 0.00048296 | N
21/11/2016 | 04:30 | ZN931:PA13 | URBAN | Planned |  | 1 | 70 | 4.8296e-05 | 6.8995e-05 | N
21/11/2016 | 07:30 | ZN1290:PA9 | URBAN | Planned |  | 68 | 540 | 0.025335 | 0.0046917 | N
04/12/2016 | 07:30 | ZN8100:PA2 | URBAN | Planned |  | 2 | 570 | 0.00078613 | 0.00013792 | N
21/11/2016 | 07:30 | ZN1648:PA19 | URBAN | Planned |  | 39 | 420 | 0.011301 | 0.0026908 | N
21/11/2016 | 08:00 | ZN12620:PA8 | SHORT RURAL | Planned |  | 1 | 410 | 0.0018436 | 0.00044965 | N
21/11/2016 | 08:00 | ZN15005:PA10 | URBAN | Planned |  | 8 | 390 | 0.0021526 | 0.00055196 | N
21/11/2016 | 09:00 | ZN14144:PA8 | URBAN | Planned |  | 20 | 360 | 0.0049676 | 0.0013799 | N
22/11/2016 | 00:30 | ZN3288:PA41 42DEF | CBD | Planned |  | 2 | 270 | 0.017391 | 0.006441 | N
22/11/2016 | 01:00 | ZN2835:PA17 | URBAN | Planned |  | 1 | 255 | 0.00017594 | 6.8996e-05 | N
22/11/2016 | 08:30 | ZN874:PA17 | URBAN | Planned |  | 73 | 60 | 0.003022 | 0.0050367 | N
22/11/2016 | 07:30 | ZN14892:PA10 | URBAN | Planned |  | 57 | 510 | 0.020057 | 0.0039328 | N
22/11/2016 | 08:20 | ZN72:PA31 | URBAN | Planned |  | 56 | 520 | 0.020092 | 0.0038638 | N
22/11/2016 | 08:00 | ZN15012:PA8 | URBAN | Planned |  | 21 | 450 | 0.0065201 | 0.0014489 | N
22/11/2016 | 08:00 | ZN14144:PA2 | SHORT RURAL | Planned |  | 28 | 465 | 0.058544 | 0.01259 | N
22/11/2016 | 08:10 | ZN14891:PA8 | SHORT RURAL | Planned |  | 21 | 420 | 0.039659 | 0.0094426 | N
22/11/2016 | 09:00 | ZN12600:PA9 | SHORT RURAL | Planned |  | 106 | 90 | 0.042896 | 0.047663 | N
22/11/2016 | 09:30 | ZN12570:PA21 | URBAN | Planned |  | 2 | 185 | 0.00025529 | 0.00013799 | N
24/11/2016 | 12:01 | ZN8000:PA15 | URBAN | Planned |  | 1 | 89 | 6.139e-05 | 6.8978e-05 | N
23/11/2016 | 00:45 | ZN3288:PA41 42DEF | CBD | Planned |  | 6 | 255 | 0.049274 | 0.019323 | N
23/11/2016 | 07:15 | ZN35370:PA4 | SHORT RURAL | Planned |  | 18 | 495 | 0.040064 | 0.0080937 | N
23/11/2016 | 09:30 | ZN14892:PA9 | URBAN | Planned |  | 74 | 210 | 0.010722 | 0.0051058 | N
23/11/2016 | 09:30 | ZN965:PA28 | URBAN | Planned |  | 32 | 510 | 0.01126 | 0.0022079 | N
23/11/2016 | 09:45 | ZN14891:PA12 | SHORT RURAL | Planned |  | 4 | 375 | 0.0067448 | 0.0017986 | N
23/11/2016 | 08:30 | ZN12640:PA13 | SHORT RURAL | Planned |  | 266 | 410 | 0.49039 | 0.11961 | N
23/11/2016 | 09:10 | ZN14143:PA12 | SHORT RURAL | Planned |  | 3 | 270 | 0.0036422 | 0.001349 | N
23/11/2016 | 10:00 | ZN10999:PA38 | URBAN | Planned |  | 108 | 240 | 0.017884 | 0.0074517 | N
23/11/2016 | 11:30 | ZN7481:PA9 | URBAN | Planned |  | 134 | 7 | 0.0006472 | 0.0092457 | N
24/11/2016 | 07:30 | ZN9245:PA1 | URBAN | Planned |  | 3 | 480 | 0.00099328 | 0.00020693 | N
24/11/2016 | 08:00 | ZN1287:PA11 | URBAN | Planned |  | 97 | 410 | 0.027432 | 0.0066908 | N
24/11/2016 | 07:30 | ZN9700:PA12 | URBAN | Planned |  | 134 | 330 | 0.030502 | 0.009243 | N
24/11/2016 | 08:30 | ZN12630:PA8 | SHORT RURAL | Planned |  | 38 | 435 | 0.074295 | 0.017079 | N
24/11/2016 | 20:30 | ZN72:PA31 | URBAN | Planned |  | 37 | 515 | 0.013144 | 0.0025522 | N
25/11/2016 | 03:00 | ZN15005:PA2 | URBAN | Planned |  | 3 | 150 | 0.0003104 | 0.00020693 | N
25/11/2016 | 08:15 | ZN12650:PA1 | SHORT RURAL | Planned |  | 13 | 455 | 0.026585 | 0.0058429 | N
26/11/2016 | 00:30 | ZN2835:PA20 | URBAN | Planned |  | 30 | 125 | 0.0025886 | 0.0020709 | N
26/11/2016 | 04:30 | ZN711:PA28 | URBAN | Planned |  | 79 | 15 | 0.00081799 | 0.0054532 | N
26/11/2016 | 07:00 | ZN4990:PA55ABC | CBD | Planned |  | 89 | 360 | 1.0316 | 0.28654 | N
26/11/2016 | 08:00 | ZN35800:PA21 | URBAN | Planned |  | 6 | 570 | 0.0023608 | 0.00041417 | N
26/11/2016 | 08:00 | ZN35800:PA21 | URBAN | Planned |  | 56 | 570 | 0.022034 | 0.0038656 | N
26/11/2016 | 14:50 | ZN4990:PA55ABC | CBD | Planned |  | 34 | 95 | 0.10399 | 0.10947 | N
26/11/2016 | 22:00 | ZN9700:PA11 | URBAN | Planned |  | 37 | 420 | 0.010727 | 0.0025541 | N
27/11/2016 | 07:20 | ZN8700:PA65 66GHJ | CBD | Planned |  | 8 | 605 | 0.15583 | 0.025757 | N
27/11/2016 | 08:00 | ZN2466:PA2 | URBAN | Planned |  | 3 | 645 | 0.0013357 | 0.00020709 | N
27/11/2016 | 08:40 | ZN9035:PA2 | URBAN | Planned |  | 91 | 375 | 0.023556 | 0.0062816 | N
27/11/2016 | 20:30 | ZN2835:PA15 | URBAN | Planned |  | 2 | 540 | 0.00074551 | 0.00013806 | N
27/11/2016 | 20:30 | ZN874:PA16 | URBAN | Planned |  | 3 | 540 | 0.0011183 | 0.00020709 | N
28/11/2016 | 07:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 13 | 150 | 0.0087644 | 0.0058429 | N
28/11/2016 | 09:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 19 | 415 | 0.035439 | 0.0085396 | N
28/11/2016 | 09:30 | ZN13000:PA11 | SHORT RURAL | Planned |  | 85 | 195 | 0.074497 | 0.038204 | N
29/11/2016 | 08:35 | ZN12600:PA2 | SHORT RURAL | Planned |  | 19 | 385 | 0.032878 | 0.0085396 | N
29/11/2016 | 09:00 | ZN10999:PA11 | URBAN | Planned |  | 1 | 390 | 0.00026921 | 6.9028e-05 | N
29/11/2016 | 07:30 | ZN12650:PA1 | SHORT RURAL | Planned |  | 107 | 600 | 0.28855 | 0.048092 | N
29/11/2016 | 07:30 | ZN36200:PA8 | SHORT RURAL | Planned |  | 33 | 215 | 0.031889 | 0.014832 | N
29/11/2016 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 8 | 452 | 0.016252 | 0.0035956 | N
29/11/2016 | 08:30 | ZN10999:PA32 | URBAN | Planned |  | 39 | 360 | 0.0096916 | 0.0026921 | N
29/11/2016 | 08:04 | ZN3155:PA44 | URBAN | Planned |  | 179 | 431 | 0.053255 | 0.012356 | N
29/11/2016 | 08:30 | ZN10990:PA6 | URBAN | Planned |  | 115 | 420 | 0.033341 | 0.0079383 | N
29/11/2016 | 08:00 | ZN847:PA14 | URBAN | Planned |  | 19 | 540 | 0.0070823 | 0.0013115 | N
29/11/2016 | 09:00 | ZN12600:PA3 | URBAN | Planned |  | 51 | 285 | 0.010033 | 0.0035204 | N
29/11/2016 | 20:00 | ZN8100:PA17 | URBAN | Planned |  | 2 | 120 | 0.00016567 | 0.00013806 | N
30/11/2016 | 07:45 | ZN12640:PA13 | SHORT RURAL | Planned |  | 380 | 505 | 0.8625 | 0.17079 | N
30/11/2016 | 07:30 | ZN10997:PA7 | URBAN | Planned |  | 96 | 570 | 0.037772 | 0.0066267 | N
30/11/2016 | 07:30 | ZN15005:PA8 | URBAN | Planned |  | 38 | 475 | 0.01246 | 0.0026231 | N
30/11/2016 | 08:00 | ZN129:PA12 | URBAN | Planned |  | 11 | 420 | 0.0031891 | 0.00075931 | N
30/11/2016 | 08:40 | ZN12580:PA10 | URBAN | Planned |  | 10 | 440 | 0.0030372 | 0.00069028 | N
30/11/2016 | 09:00 | ZN14892:PA9 | URBAN | Planned |  | 57 | 125 | 0.0049183 | 0.0039346 | N
01/12/2016 | 07:30 | ZN12650:PA1 | SHORT RURAL | Planned |  | 23 | 113 | 0.011676 | 0.010333 | N
12/12/2016 | 08:35 | 509:33397 | SHORT RURAL | Planned |  | 10 | 325 | 0.014604 | 0.0044935 | N
13/12/2016 | 08:20 | 801:74121 | LONG RURAL | Planned |  | 10 | 395 | 1.4062 | 0.356 | N
13/12/2016 | 08:30 | 230:81440 | SHORT RURAL | Planned |  | 95 | 420 | 0.17929 | 0.042689 | N
12/12/2016 | 08:10 | 243:80078 | SHORT RURAL | Planned |  | 143 | 160 | 0.10281 | 0.064258 | N
13/12/2016 | 08:10 | 223:14395 | SHORT RURAL | Planned |  | 115 | 170 | 0.087849 | 0.051676 | N
12/12/2016 | 08:30 | 507:80922 | SHORT RURAL | Planned |  | 1 | 165 | 0.00074143 | 0.00044935 | N
12/12/2016 | 17:28 | 532:83301 | URBAN | Planned |  | 136 | 120 | 0.011251 | 0.009376 | N
13/12/2016 | 09:19 | 509:33397 | SHORT RURAL | Planned |  | 1 | 341 | 0.0015323 | 0.00044935 | N
13/12/2016 | 09:05 | 238:34148 | SHORT RURAL | Planned |  | 6 | 265 | 0.0071447 | 0.0026961 | N
12/12/2016 | 08:45 | 812:19072 | SHORT RURAL | Planned |  | 7 | 235 | 0.0073919 | 0.0031455 | N
12/12/2016 | 07:20 | 810:74058 | SHORT RURAL | Planned |  | 1 | 100 | 0.00044935 | 0.00044935 | N
13/12/2016 | 09:10 | 806:82667 | SHORT RURAL | Planned |  | 1 | 90 | 0.00040442 | 0.00044935 | N
13/12/2016 | 08:35 | 810:74054 | LONG RURAL | Planned |  | 2 | 160 | 0.11392 | 0.0712 | N
14/12/2016 | 08:00 | 213:33769 | URBAN | Planned |  | 38 | 445 | 0.011658 | 0.0026198 | N
14/12/2016 | 08:12 | 213:33770 | URBAN | Planned |  | 63 | 433 | 0.018807 | 0.0043434 | N
14/12/2016 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 5 | 234 | 0.0052575 | 0.0022468 | N
14/12/2016 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 4 | 280 | 0.39872 | 0.1424 | N
14/12/2016 | 08:45 | 801:74121 | LONG RURAL | Planned |  | 1 | 55 | 0.01958 | 0.0356 | N
14/12/2016 | 11:30 | 801:74121 | LONG RURAL | Planned |  | 1 | 50 | 0.0178 | 0.0356 | N
14/12/2016 | 08:50 | 812:19066 | SHORT RURAL | Planned |  | 20 | 375 | 0.033702 | 0.0089872 | N
15/12/2016 | 08:30 | 516:48065 | SHORT RURAL | Planned |  | 3 | 150 | 0.0020209 | 0.0013473 | N
15/12/2016 | 08:30 | 265:81648 | SHORT RURAL | Planned |  | 77 | 475 | 0.16425 | 0.03458 | N
16/12/2016 | 07:15 | 524:33576 | SHORT RURAL | Planned |  | 6 | 255 | 0.006871 | 0.0026945 | N
19/12/2016 | 08:50 | 814:82289 | SHORT RURAL | Planned |  | 3 | 190 | 0.0025598 | 0.0013472 | N
17/12/2016 | 08:30 | 261:81885 | URBAN | Planned |  | 35 | 390 | 0.0094085 | 0.0024124 | N
15/12/2016 | 08:10 | 232:33409 | SHORT RURAL | Planned |  | 59 | 270 | 0.07154 | 0.026496 | N
15/12/2016 | 09:15 | 230:81432 | SHORT RURAL | Planned |  | 7 | 145 | 0.0045583 | 0.0031436 | N
15/12/2016 | 08:36 | 502:48010 | SHORT RURAL | Planned |  | 18 | 269 | 0.021745 | 0.0080836 | N
15/12/2016 | 08:03 | 238:34140 | URBAN | Planned |  | 5 | 347 | 0.0011958 | 0.00034462 | N
15/12/2016 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 1 | 120 | 0.00053891 | 0.00044909 | N
15/12/2016 | 08:45 | 812:19072 | SHORT RURAL | Planned |  | 2 | 85 | 0.00076345 | 0.00089818 | N
15/12/2016 | 09:00 | 810:74050 | SHORT RURAL | Planned |  | 3 | 120 | 0.0016167 | 0.0013473 | N
15/12/2016 | 08:00 | 513:48056 | SHORT RURAL | Planned |  | 1 | 30 | 0.00013473 | 0.00044909 | N
15/12/2016 | 14:15 | 513:48056 | SHORT RURAL | Planned |  | 1 | 10 | 4.4909e-05 | 0.00044909 | N
21/12/2016 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 184 | 485 | 31.7806 | 6.5527 | N
15/12/2016 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 17 | 330 | 0.025194 | 0.0076345 | N
20/12/2016 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 1 | 120 | 0.0005389 | 0.00044908 | N
20/12/2016 | 08:30 | 235:2120 | SHORT RURAL | Planned |  | 81 | 385 | 0.14005 | 0.036376 | N
20/12/2016 | 19:25 | 258:80785 | URBAN | Planned |  | 88 | 153 | 0.0092804 | 0.0060656 | N
20/12/2016 | 08:00 | 224:80337 | SHORT RURAL | Planned |  | 1 | 198 | 0.00088918 | 0.00044908 | N
20/12/2016 | 08:35 | 230:81432 | SHORT RURAL | Planned |  | 1 | 175 | 0.0007859 | 0.00044908 | N
20/12/2016 | 09:00 | 230:81432 | SHORT RURAL | Planned |  | 1 | 268 | 0.0012035 | 0.00044908 | N
20/12/2016 | 08:00 | 512:48048 | SHORT RURAL | Planned |  | 4 | 610 | 0.010958 | 0.0017963 | N
20/12/2016 | 11:50 | 230:81432 | SHORT RURAL | Planned |  | 5 | 135 | 0.0030313 | 0.0022454 | N
20/12/2016 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 23 | 365 | 2.9897 | 0.81909 | N
20/12/2016 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 23 | 350 | 2.8668 | 0.81909 | N
21/12/2016 | 07:30 | 206:34432 | URBAN | Planned |  | 1 | 500 | 0.00034464 | 6.8928e-05 | N
21/12/2016 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 170 | 0.060541 | 0.035613 | N
21/12/2016 | 08:00 | 524:33572 | SHORT RURAL | Planned |  | 5 | 300 | 0.0067365 | 0.0022455 | N
21/12/2016 | 08:00 | 235:2120 | SHORT RURAL | Planned |  | 8 | 270 | 0.0097005 | 0.0035928 | N
21/12/2016 | 09:25 | 511:29876 | SHORT RURAL | Planned |  | 3 | 120 | 0.0016168 | 0.0013473 | N
21/12/2016 | 13:00 | 511:29876 | SHORT RURAL | Planned |  | 2 | 40 | 0.00035928 | 0.0008982 | N
21/12/2016 | 08:40 | 807:74184 | SHORT RURAL | Planned |  | 9 | 280 | 0.011317 | 0.0040419 | N
21/12/2016 | 09:00 | 814:82289 | SHORT RURAL | Planned |  | 4 | 150 | 0.0026946 | 0.0017964 | N
22/12/2016 | 08:30 | 532:83307 | SHORT RURAL | Planned |  | 401 | 170 | 0.30605 | 0.18003 | N
22/12/2016 | 08:30 | 509:33399 | SHORT RURAL | Planned |  | 6 | 72 | 0.0019395 | 0.0026937 | N
22/12/2016 | 11:24 | 509:33399 | SHORT RURAL | Planned |  | 36 | 58 | 0.0093741 | 0.016162 | N
22/12/2016 | 08:30 | 230:81432 | SHORT RURAL | Planned |  | 1 | 330 | 0.0014815 | 0.00044895 | N
22/12/2016 | 08:30 | 230:81432 | SHORT RURAL | Planned |  | 3 | 395 | 0.0053201 | 0.0013469 | N
22/12/2016 | 08:35 | 512:48049 | SHORT RURAL | Planned |  | 1 | 75 | 0.00033671 | 0.00044895 | N
22/12/2016 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 17 | 390 | 0.029766 | 0.0076322 | N
22/12/2016 | 08:40 | 813:89055 | SHORT RURAL | Planned |  | 17 | 290 | 0.022133 | 0.0076322 | N
22/12/2016 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 1 | 295 | 0.10506 | 0.035613 | N
22/12/2016 | 11:15 | 511:29878 | SHORT RURAL | Planned |  | 2 | 53 | 0.00047589 | 0.0008979 | N
22/12/2016 | 12:45 | 520:48172 | SHORT RURAL | Planned |  | 4 | 75 | 0.0013469 | 0.0017958 | N
28/12/2016 | 08:02 | 504:48031 | SHORT RURAL | Planned |  | 22 | 73 | 0.0072104 | 0.0098773 | N
29/12/2016 | 08:28 | 511:29870 | URBAN | Planned |  | 1 | 15 | 1.0336e-05 | 6.891e-05 | N
30/12/2016 | 07:45 | 813:89062 | SHORT RURAL | Planned |  | 3 | 150 | 0.0020204 | 0.0013469 | N
03/01/2017 | 08:30 | 523:33503 | URBAN | Planned |  | 145 | 70 | 0.0069945 | 0.0099921 | N
04/01/2017 | 08:30 | 507:80923 | SHORT RURAL | Planned |  | 30 | 390 | 0.052531 | 0.01347 | N
04/01/2017 | 08:00 | 504:48031 | SHORT RURAL | Planned |  | 7 | 230 | 0.0072286 | 0.0031429 | N
04/01/2017 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 10 | 180 | 0.64125 | 0.35625 | N
04/01/2017 | 08:30 | 523:33503 | URBAN | Planned |  | 68 | 210 | 0.0098406 | 0.004686 | N
04/01/2017 | 12:00 | 801:74117 | SHORT RURAL | Planned |  | 1 | 70 | 0.00031429 | 0.00044898 | N
05/01/2017 | 08:40 | 511:29878 | SHORT RURAL | Planned |  | 3 | 260 | 0.0035021 | 0.001347 | N
05/01/2017 | 07:00 | 265:81641 | URBAN | Planned |  | 1 | 450 | 0.00031011 | 6.8913e-05 | N
05/01/2017 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 1 | 75 | 0.026719 | 0.035625 | N
05/01/2017 | 08:30 | 516:48066 | SHORT RURAL | Planned |  | 1 | 108 | 0.00048491 | 0.00044899 | N
05/01/2017 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 12 | 300 | 0.016164 | 0.0053879 | N
05/01/2017 | 12:20 | 812:19072 | SHORT RURAL | Planned |  | 2 | 105 | 0.00094288 | 0.00089798 | N
05/01/2017 | 12:50 | 515:35197 | LONG RURAL | Planned |  | 2 | 75 | 0.053438 | 0.07125 | N
05/01/2017 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 22 | 320 | 0.031609 | 0.0098777 | N
06/01/2017 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 5 | 300 | 0.53438 | 0.17813 | N
06/01/2017 | 08:50 | 814:82285 | SHORT RURAL | Planned |  | 3 | 260 | 0.0035022 | 0.001347 | N
06/01/2017 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 5 | 140 | 0.24938 | 0.17813 | N
06/01/2017 | 08:45 | 802:82220 | SHORT RURAL | Planned |  | 2 | 45 | 0.0004041 | 0.00089799 | N
01/12/2016 | 02:00 | ZN3155:PA11 | URBAN | Planned |  | 359 | 5 | 0.0012387 | 0.024774 | N
01/12/2016 | 07:20 | ZN12580:PA4 | URBAN | Planned |  | 103 | 505 | 0.035895 | 0.0071079 | N
01/12/2016 | 09:23 | ZN12650:PA1 | SHORT RURAL | Planned |  | 107 | 377 | 0.18123 | 0.048072 | N
01/12/2016 | 07:30 | ZN7900:PA19 | URBAN | Planned |  | 98 | 380 | 0.025699 | 0.0067629 | N
01/12/2016 | 08:00 | ZN36800:PA58 | URBAN | Planned |  | 59 | 440 | 0.017915 | 0.0040715 | N
01/12/2016 | 09:25 | ZN12570:PA37 | SHORT RURAL | Planned |  | 51 | 260 | 0.059573 | 0.022913 | N
02/12/2016 | 09:00 | ZN10997:PA12 | URBAN | Planned |  | 69 | 30 | 0.0014285 | 0.0047616 | N
03/12/2016 | 09:30 | ZN35900:PA4 | SHORT RURAL | Planned |  | 2 | 720 | 0.0064695 | 0.00089854 | N
03/12/2016 | 18:30 | ZN263:PA33 34GHJ | CBD | Planned |  | 15 | 310 | 0.14971 | 0.048294 | N
03/12/2016 | 22:00 | ZN3288:PA43 44DEF | CBD | Planned |  | 1 | 450 | 0.014488 | 0.0032196 | N
04/12/2016 | 07:00 | ZN10993:PA34 | URBAN | Planned |  | 25 | 660 | 0.011378 | 0.001724 | N
04/12/2016 | 07:00 | ZN10993:PA34 | URBAN | Planned |  | 3 | 660 | 0.0013654 | 0.00020688 | N
04/12/2016 | 08:30 | ZN188:PA3 | URBAN | Planned |  | 11 | 510 | 0.0038686 | 0.00075855 | N
09/01/2017 | 09:00 | 243:80074 | SHORT RURAL | Planned |  | 2 | 380 | 0.0034109 | 0.00089762 | N
09/01/2017 | 08:00 | 504:48031 | SHORT RURAL | Planned |  | 2 | 65 | 0.00058345 | 0.00089762 | N
09/01/2017 | 08:35 | 230:81432 | SHORT RURAL | Planned |  | 1 | 183 | 0.00082132 | 0.00044881 | N
09/01/2017 | 12:37 | 524:33570 | SHORT RURAL | Planned |  | 2 | 36 | 0.00032314 | 0.00089762 | N
09/01/2017 | 10:18 | 524:33570 | SHORT RURAL | Planned |  | 1 | 50 | 0.0002244 | 0.00044881 | N
09/01/2017 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 8 | 270 | 0.0096943 | 0.0035905 | N
09/01/2017 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 1 | 200 | 0.00089762 | 0.00044881 | N
10/01/2017 | 08:45 | 810:74054 | LONG RURAL | Planned |  | 4 | 290 | 0.41325 | 0.1425 | N
10/01/2017 | 08:30 | 202:34250 | URBAN | Planned |  | 82 | 300 | 0.016948 | 0.0056492 | N
10/01/2017 | 08:30 | 239:82127 | SHORT RURAL | Planned |  | 49 | 380 | 0.083569 | 0.021992 | N
10/01/2017 | 08:30 | 238:34148 | SHORT RURAL | Planned |  | 6 | 320 | 0.0086172 | 0.0026929 | N
10/01/2017 | 08:45 | 230:81432 | SHORT RURAL | Planned |  | 1 | 255 | 0.0011445 | 0.00044881 | N
10/01/2017 | 08:45 | 806:82667 | SHORT RURAL | Planned |  | 2 | 195 | 0.0017504 | 0.00089763 | N
10/01/2017 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 2 | 81 | 0.00072708 | 0.00089763 | N
10/01/2017 | 12:50 | 512:48049 | SHORT RURAL | Planned |  | 4 | 108 | 0.0019389 | 0.0017953 | N
07/12/2016 | 08:30 | ZN9118:PA3 | SHORT RURAL | Planned |  | 271 | 450 | 0.5479 | 0.12175 | N
05/12/2016 | 04:30 | ZN931:PA18 | URBAN | Planned |  | 1 | 60 | 4.1376e-05 | 6.8959e-05 | N
05/12/2016 | 08:05 | ZN12600:PA13 | SHORT RURAL | Planned |  | 11 | 155 | 0.0076601 | 0.004942 | N
05/12/2016 | 08:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 3 | 360 | 0.0048521 | 0.0013478 | N
05/12/2016 | 08:00 | ZN15005:PA6 | URBAN | Planned |  | 10 | 420 | 0.0028963 | 0.00068959 | N
05/12/2016 | 08:00 | ZN15005:PA6 | URBAN | Planned |  | 16 | 420 | 0.0046341 | 0.0011033 | N
05/12/2016 | 11:40 | ZN188:PA21 | URBAN | Planned |  | 69 | 365 | 0.017367 | 0.0047582 | N
06/12/2016 | 01:00 | ZN12610:PA9 | URBAN | Planned |  | 7 | 1 | 4.8273e-06 | 0.00048273 | N
06/12/2016 | 08:30 | ZN12570:PA33 | SHORT RURAL | Planned |  | 40 | 390 | 0.070087 | 0.017971 | N
06/12/2016 | 08:10 | ZN12630:PA1 | SHORT RURAL | Planned |  | 10 | 415 | 0.018645 | 0.0044927 | N
06/12/2016 | 08:30 | ZN10999:PA11 | URBAN | Planned |  | 82 | 425 | 0.024033 | 0.0056548 | N
21/12/2016 | 08:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 2 | 425 | 0.0038173 | 0.0008982 | N
07/12/2016 | 07:30 | ZN35900:PA24 | URBAN | Planned |  | 35 | 585 | 0.01412 | 0.0024137 | N
07/12/2016 | 07:30 | ZN35900:PA24 | URBAN | Planned |  | 60 | 585 | 0.024206 | 0.0041377 | N
07/12/2016 | 08:00 | ZN2466:PA16 | URBAN | Planned |  | 8 | 540 | 0.0029791 | 0.00055169 | N
07/12/2016 | 08:15 | ZN12600:PA2 | SHORT RURAL | Planned |  | 8 | 452 | 0.016246 | 0.0035942 | N
07/12/2016 | 08:30 | ZN10999:PA38 | URBAN | Planned |  | 131 | 390 | 0.035233 | 0.009034 | N
07/12/2016 | 09:15 | ZN12650:PA9 | URBAN | Planned |  | 3 | 360 | 0.00074479 | 0.00020689 | N
07/12/2016 | 16:45 | ZN711:PA31 | URBAN | Planned |  | 18 | 330 | 0.0040963 | 0.0012413 | N
11/01/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 11 | 315 | 0.015552 | 0.004937 | N
11/01/2017 | 08:50 | 810:74050 | SHORT RURAL | Planned |  | 11 | 225 | 0.011108 | 0.004937 | N
08/12/2016 | 07:30 | ZN9245:PA13 | URBAN | Planned |  | 1 | 360 | 0.00024817 | 6.8935e-05 | N
19/12/2016 | 08:30 | ZN12630:PA1 | SHORT RURAL | Planned |  | 2 | 390 | 0.0035028 | 0.00089816 | N
08/12/2016 | 08:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 7 | 450 | 0.014155 | 0.0031455 | N
08/12/2016 | 08:10 | ZN12580:PA4 | URBAN | Planned |  | 26 | 470 | 0.0084239 | 0.0017923 | N
08/12/2016 | 10:00 | ZN35500:PA23 | URBAN | Planned |  | 17 | 420 | 0.004922 | 0.0011719 | N
08/12/2016 | 10:45 | ZN167:PA21 | URBAN | Planned |  | 3 | 15 | 3.1021e-05 | 0.00020681 | N
08/12/2016 | 09:30 | ZN14891:PA12 | SHORT RURAL | Planned |  | 12 | 360 | 0.019412 | 0.0053923 | N
09/12/2016 | 07:30 | ZN72:PA31 | URBAN | Planned |  | 34 | 530 | 0.012423 | 0.0023439 | N
09/12/2016 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 7 | 240 | 0.0075489 | 0.0031454 | N
09/12/2016 | 15:30 | ZN1610:PA17 | URBAN | Planned |  | 1 | 7,280 | 0.0050187 | 6.8938e-05 | N
10/12/2016 | 07:00 | ZN188:PA27 | URBAN | Planned |  | 125 | 630 | 0.05429 | 0.0086174 | N
10/12/2016 | 10:20 | ZN384:PA33 | URBAN | Planned |  | 15 | 140 | 0.0014477 | 0.0010341 | N
10/12/2016 | 22:30 | ZN9700:PA12 | URBAN | Planned |  | 92 | 495 | 0.031395 | 0.0063424 | N
11/12/2016 | 18:30 | ZN1610:PA17 | URBAN | Planned |  | 2 | 60 | 8.273e-05 | 0.00013788 | N
12/12/2016 | 02:00 | ZN12610:PA9 | URBAN | Planned |  | 31 | 195 | 0.0041675 | 0.0021372 | N
12/12/2016 | 03:30 | ZN3288:PA43 44ABC | CBD | Planned |  | 82 | 90 | 0.2376 | 0.264 | N
16/12/2016 | 07:00 | ZN14892:PA8 | SHORT RURAL | Planned |  | 1 | 525 | 0.0023577 | 0.00044908 | N
12/12/2016 | 08:20 | ZN167:PA21 | URBAN | Planned |  | 3 | 430 | 0.00088934 | 0.00020682 | N
12/12/2016 | 08:00 | ZN15005:PA6 | URBAN | Planned |  | 10 | 420 | 0.0028955 | 0.00068941 | N
12/12/2016 | 08:00 | ZN15005:PA6 | URBAN | Planned |  | 16 | 360 | 0.003971 | 0.0011031 | N
12/12/2016 | 08:30 | ZN342:PA22 | URBAN | Planned |  | 1 | 390 | 0.00026887 | 6.8941e-05 | N
12/12/2016 | 12:00 | ZN35900:PA23 | SHORT RURAL | Planned |  | 33 | 180 | 0.026692 | 0.014829 | N
13/12/2016 | 08:15 | ZN384:PA33 | URBAN | Planned |  | 15 | 465 | 0.0048087 | 0.0010341 | N
13/12/2016 | 07:35 | ZN12630:PA3 | SHORT RURAL | Planned |  | 8 | 565 | 0.020311 | 0.0035948 | N
13/12/2016 | 09:00 | ZN3154:PA6 | URBAN | Planned |  | 21 | 60 | 0.00086867 | 0.0014478 | N
13/12/2016 | 08:05 | ZN12630:PA11 | SHORT RURAL | Planned |  | 2 | 460 | 0.0041341 | 0.00089871 | N
13/12/2016 | 10:00 | ZN72:PA30 | URBAN | Planned |  | 36 | 360 | 0.0089349 | 0.0024819 | N
13/12/2016 | 23:30 | ZN3154:PA6 | URBAN | Planned |  | 175 | 105 | 0.012668 | 0.012065 | N
14/12/2016 | 07:50 | ZN2400:PA18 | SHORT RURAL | Planned |  | 36 | 485 | 0.078459 | 0.016177 | N
14/12/2016 | 07:30 | ZN15014:PA11 | URBAN | Planned |  | 1 | 210 | 0.00014478 | 6.8943e-05 | N
14/12/2016 | 08:00 | ZN14144:PA5 | SHORT RURAL | Planned |  | 3 | 240 | 0.0032354 | 0.0013481 | N
14/12/2016 | 08:00 | ZN15013:PA10 | SHORT RURAL | Planned |  | 24 | 495 | 0.053384 | 0.010785 | N
14/12/2016 | 08:00 | ZN12640:PA13 | SHORT RURAL | Planned |  | 58 | 450 | 0.11728 | 0.026063 | N
14/12/2016 | 08:00 | ZN72:PA30 | URBAN | Planned |  | 667 | 480 | 0.22073 | 0.045985 | N
15/12/2016 | 21:00 | ZN72:PA31 | URBAN | Planned |  | 30 | 510 | 0.010545 | 0.0020677 | N
16/12/2016 | 00:50 | ZN2602:PA18 | URBAN | Planned |  | 181 | 190 | 0.023704 | 0.012476 | N
16/12/2016 | 05:30 | ZN2635:PA44 | URBAN | Planned |  | 1 | 60 | 4.1355e-05 | 6.8926e-05 | N
16/12/2016 | 09:30 | ZN14144:PA5 | SHORT RURAL | Planned |  | 3 | 80 | 0.0010778 | 0.0013473 | N
16/12/2016 | 20:30 | ZN10997:PA7 | URBAN | Planned |  | 30 | 610 | 0.012613 | 0.0020678 | N
16/12/2016 | 21:45 | ZN10997:PA2 | URBAN | Planned |  | 19 | 535 | 0.0070063 | 0.0013096 | N
17/12/2016 | 08:00 | ZN1287:PA16 | URBAN | Planned |  | 1 | 62 | 4.2735e-05 | 6.8927e-05 | N
17/12/2016 | 21:00 | ZN12690:PA10 | URBAN | Planned |  | 1 | 420 | 0.00028949 | 6.8927e-05 | N
18/12/2016 | 07:30 | ZN12690:PA22 | URBAN | Planned |  | 19 | 510 | 0.006679 | 0.0013096 | N
18/12/2016 | 08:00 | ZN8100:PA28 | URBAN | Planned |  | 10 | 520 | 0.0035842 | 0.00068926 | N
19/12/2016 | 04:30 | ZN931:PA32 | URBAN | Planned |  | 1 | 60 | 4.1356e-05 | 6.8927e-05 | N
19/12/2016 | 04:30 | ZN931:PA32 | URBAN | Planned |  | 1 | 60 | 4.1356e-05 | 6.8927e-05 | N
19/12/2016 | 08:00 | ZN847:PA39 | URBAN | Planned |  | 38 | 570 | 0.01493 | 0.0026192 | N
19/12/2016 | 07:30 | ZN2310:PA65 | URBAN | Planned |  | 1 | 470 | 0.00032396 | 6.8927e-05 | N
19/12/2016 | 07:30 | ZN263:PA33 34KLM | CBD | Planned |  | 42 | 480 | 0.649 | 0.13521 | N
19/12/2016 | 07:30 | ZN8700:PA61 62GHJ | CBD | Planned |  | 29 | 480 | 0.44812 | 0.093359 | N
19/12/2016 | 08:00 | ZN15005:PA6 | URBAN | Planned |  | 10 | 420 | 0.0028949 | 0.00068927 | N
19/12/2016 | 08:00 | ZN931:PA32 | URBAN | Planned |  | 1 | 270 | 0.0001861 | 6.8927e-05 | N
19/12/2016 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 6 | 420 | 0.011317 | 0.0026945 | N
19/12/2016 | 08:00 | ZN2635:PA57 | URBAN | Planned |  | 32 | 450 | 0.0099255 | 0.0022057 | N
19/12/2016 | 08:00 | ZN3154:PA10 | URBAN | Planned |  | 50 | 420 | 0.014475 | 0.0034463 | N
19/12/2016 | 08:30 | ZN12570:PA21 | URBAN | Planned |  | 3 | 420 | 0.00086848 | 0.00020678 | N
19/12/2016 | 09:00 | ZN14892:PA17 | URBAN | Planned |  | 28 | 360 | 0.0069478 | 0.00193 | N
19/12/2016 | 23:30 | ZN35500:PA35 | URBAN | Planned |  | 5 | 600 | 0.0020678 | 0.00034463 | N
20/12/2016 | 08:00 | ZN9118:PA17 | URBAN | Planned |  | 82 | 425 | 0.024021 | 0.0056521 | N
20/12/2016 | 08:00 | ZN263:PA33 34KLM | CBD | Planned |  | 42 | 540 | 0.73013 | 0.13521 | N
20/12/2016 | 08:10 | ZN15005:PA6 | URBAN | Planned |  | 10 | 330 | 0.0022746 | 0.00068927 | N
20/12/2016 | 08:50 | ZN384:PA81 | URBAN | Planned |  | 18 | 445 | 0.0055211 | 0.0012407 | N
20/12/2016 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 12 | 480 | 0.025867 | 0.005389 | N
20/12/2016 | 08:30 | ZN9900:PA19 | URBAN | Planned |  | 21 | 480 | 0.0069479 | 0.0014475 | N
20/12/2016 | 21:00 | ZN15005:PA2 | URBAN | Planned |  | 78 | 480 | 0.025806 | 0.0053763 | N
21/12/2016 | 04:30 | ZN931:PA18 | URBAN | Planned |  | 1 | 90 | 6.2035e-05 | 6.8928e-05 | N
21/12/2016 | 08:20 | ZN12570:PA24 | SHORT RURAL | Planned |  | 12 | 530 | 0.028563 | 0.0053892 | N
21/12/2016 | 07:30 | ZN3472:PA29 | URBAN | Planned |  | 2 | 240 | 0.00033085 | 0.00013786 | N
21/12/2016 | 08:35 | ZN2635:PA31 | URBAN | Planned |  | 47 | 475 | 0.015388 | 0.0032396 | N
21/12/2016 | 07:30 | ZN2602:PA36 | URBAN | Planned |  | 75 | 570 | 0.029467 | 0.0051696 | N
21/12/2016 | 08:00 | ZN35370:PA8 | SHORT RURAL | Planned |  | 37 | 507 | 0.084247 | 0.016617 | N
21/12/2016 | 08:00 | ZN12620:PA2 | SHORT RURAL | Planned |  | 37 | 430 | 0.071452 | 0.016617 | N
21/12/2016 | 08:30 | ZN711:PA28 | URBAN | Planned |  | 239 | 390 | 0.064248 | 0.016474 | N
21/12/2016 | 09:00 | ZN12660:PA8 | URBAN | Planned |  | 1 | 225 | 0.00015509 | 6.8928e-05 | N
21/12/2016 | 18:00 | ZN10999:PA23 | URBAN | Planned |  | 19 | 720 | 0.0094293 | 0.0013096 | N
21/12/2016 | 21:00 | ZN15011:PA10 | URBAN | Planned |  | 9 | 120 | 0.00074442 | 0.00062035 | N
22/12/2016 | 07:00 | ZN398:PA31 | URBAN | Planned |  | 25 | 210 | 0.0036176 | 0.0017227 | N
22/12/2016 | 08:30 | ZN15005:PA2 | URBAN | Planned |  | 72 | 480 | 0.023814 | 0.0049613 | N
22/12/2016 | 19:30 | ZN15005:PA2 | URBAN | Planned |  | 72 | 390 | 0.019349 | 0.0049613 | N
28/12/2016 | 21:00 | ZN711:PA33 | URBAN | Planned |  | 1 | 600 | 0.00041345 | 6.8909e-05 | N
28/12/2016 | 06:30 | ZN711:PA33 | URBAN | Planned |  | 1 | 420 | 0.00028942 | 6.8909e-05 | N
12/01/2017 | 08:00 | 243:80083 | SHORT RURAL | Planned |  | 6 | 415 | 0.011176 | 0.0026931 | N
12/01/2017 | 10:30 | 224:80329 | SHORT RURAL | Planned |  | 1 | 360 | 0.0016159 | 0.00044885 | N
12/01/2017 | 09:15 | 511:29878 | SHORT RURAL | Planned |  | 4 | 307 | 0.0055119 | 0.0017954 | N
12/01/2017 | 08:30 | 813:89062 | SHORT RURAL | Planned |  | 19 | 220 | 0.018762 | 0.0085282 | N
12/01/2017 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 24 | 245 | 2.0948 | 0.85501 | N
12/01/2017 | 08:40 | 515:35197 | LONG RURAL | Planned |  | 40 | 230 | 3.2775 | 1.425 | N
13/01/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 60 | 260 | 0.070022 | 0.026931 | N
13/01/2017 | 08:10 | 243:80083 | SHORT RURAL | Planned |  | 29 | 225 | 0.029288 | 0.013017 | N
13/01/2017 | 05:20 | 504:48027 | URBAN | Planned |  | 15 | 45 | 0.00046498 | 0.0010333 | N
13/01/2017 | 08:30 | 502:48010 | SHORT RURAL | Planned |  | 9 | 190 | 0.0076755 | 0.0040397 | N
13/01/2017 | 07:35 | 811:74234 | SHORT RURAL | Planned |  | 1 | 125 | 0.00056107 | 0.00044886 | N
13/01/2017 | 04:05 | 801:74118 | URBAN | Planned |  | 58 | 110 | 0.0043949 | 0.0039954 | N
13/01/2017 | 09:00 | 806:82662 | SHORT RURAL | Planned |  | 2 | 150 | 0.0013466 | 0.00089771 | N
13/01/2017 | 10:05 | 806:82662 | SHORT RURAL | Planned |  | 2 | 60 | 0.00053863 | 0.00089771 | N
13/01/2017 | 11:20 | 806:82662 | SHORT RURAL | Planned |  | 4 | 50 | 0.00089771 | 0.0017954 | N
16/01/2017 | 09:10 | 811:74234 | SHORT RURAL | Planned |  | 3 | 220 | 0.0029624 | 0.0013466 | N
16/01/2017 | 11:35 | 813:89061 | LONG RURAL | Planned |  | 2 | 45 | 0.032063 | 0.07125 | N
16/01/2017 | 08:40 | 502:48010 | SHORT RURAL | Planned |  | 5 | 400 | 0.008977 | 0.0022443 | N
16/01/2017 | 08:50 | 243:80083 | SHORT RURAL | Planned |  | 15 | 360 | 0.024238 | 0.0067328 | N
16/01/2017 | 08:30 | 225:33670 | URBAN | Planned |  | 110 | 375 | 0.028415 | 0.0075774 | N
16/01/2017 | 08:30 | 225:33679 | URBAN | Planned |  | 65 | 375 | 0.016791 | 0.0044776 | N
18/01/2017 | 06:00 | ZN384:PA43 | URBAN | Planned |  | 209 | 60 | 0.0086384 | 0.014397 | N
17/01/2017 | 10:20 | 515:35197 | LONG RURAL | Planned |  | 3 | 47 | 0.050232 | 0.10688 | N
17/01/2017 | 08:00 | 221:11895 | URBAN | Planned |  | 70 | 340 | 0.016395 | 0.0048221 | N
17/01/2017 | 21:15 | 214:8670 | URBAN | Planned |  | 158 | 220 | 0.023945 | 0.010884 | N
17/01/2017 | 08:55 | 242:81539 | URBAN | Planned |  | 357 | 395 | 0.09714 | 0.024592 | N
17/01/2017 | 08:55 | 242:81538 | URBAN | Planned |  | 212 | 395 | 0.057686 | 0.014604 | N
17/01/2017 | 08:30 | 235:2120 | SHORT RURAL | Planned |  | 10 | 220 | 0.0098747 | 0.0044885 | N
17/01/2017 | 08:50 | 232:11453 | SHORT RURAL | Planned |  | 46 | 150 | 0.030971 | 0.020647 | N
17/01/2017 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 2 | 90 | 0.00080793 | 0.0008977 | N
17/01/2017 | 09:30 | 516:48066 | SHORT RURAL | Planned |  | 2 | 65 | 0.00058351 | 0.0008977 | N
17/01/2017 | 08:50 | 810:74054 | LONG RURAL | Planned |  | 2 | 245 | 0.17456 | 0.07125 | N
18/01/2017 | 08:45 | 230:81432 | SHORT RURAL | Planned |  | 1 | 135 | 0.00060595 | 0.00044885 | N
18/01/2017 | 08:45 | 515:35192 | SHORT RURAL | Planned |  | 1 | 45 | 0.00020198 | 0.00044885 | N
18/01/2017 | 13:15 | 515:35197 | LONG RURAL | Planned |  | 1 | 13 | 0.0046313 | 0.035625 | N
19/01/2017 | 08:10 | 217:33612 | URBAN | Planned |  | 71 | 280 | 0.013694 | 0.0048906 | N
19/01/2017 | 08:00 | 220:8691 | URBAN | Planned |  | 1 | 405 | 0.00027897 | 6.8881e-05 | N
17/01/2017 | 08:30 | 205:12206 | URBAN | Planned |  | 1 | 3,088 | 0.0021272 | 6.8887e-05 | N
19/01/2017 | 09:10 | 217:33610 | URBAN | Planned |  | 140 | 390 | 0.037609 | 0.0096434 | N
19/01/2017 | 09:10 | 261:81882 | URBAN | Planned |  | 46 | 390 | 0.012357 | 0.0031685 | N
19/01/2017 | 08:45 | 235:2123 | URBAN | Planned |  | 76 | 345 | 0.018061 | 0.005235 | N
19/01/2017 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 19 | 280 | 0.023877 | 0.0085277 | N
20/01/2017 | 08:35 | 508:82579 | SHORT RURAL | Planned |  | 84 | 439 | 0.1655 | 0.0377 | N
20/01/2017 | 08:00 | 515:35192 | SHORT RURAL | Planned |  | 35 | 415 | 0.06519 | 0.015709 | N
20/01/2017 | 08:50 | 225:33670 | URBAN | Planned |  | 69 | 306 | 0.014544 | 0.0047529 | N
20/01/2017 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 11 | 55 | 0.0027153 | 0.004937 | N
20/01/2017 | 08:30 | 524:33572 | SHORT RURAL | Planned |  | 105 | 235 | 0.11075 | 0.047126 | N
20/01/2017 | 08:30 | 230:81432 | SHORT RURAL | Planned |  | 1 | 150 | 0.00067322 | 0.00044881 | N
20/01/2017 | 08:30 | 230:81432 | SHORT RURAL | Planned |  | 2 | 275 | 0.0024685 | 0.00089763 | N
23/01/2017 | 08:40 | 230:81432 | SHORT RURAL | Planned |  | 50 | 335 | 0.075183 | 0.022443 | N
23/01/2017 | 09:15 | 239:82132 | URBAN | Planned |  | 158 | 375 | 0.040812 | 0.010883 | N
23/01/2017 | 08:30 | 524:33570 | SHORT RURAL | Planned |  | 106 | 330 | 0.15701 | 0.047579 | N
23/01/2017 | 08:00 | 242:81535 | URBAN | Planned |  | 2 | 372 | 0.00051248 | 0.00013776 | N
23/01/2017 | 17:52 | 232:33407 | SHORT RURAL | Planned |  | 51 | 68 | 0.015566 | 0.022892 | N
23/01/2017 | 09:15 | 813:89061 | LONG RURAL | Planned |  | 1 | 135 | 0.048111 | 0.035638 | N
23/01/2017 | 08:15 | 810:74054 | LONG RURAL | Planned |  | 2 | 375 | 0.26728 | 0.071276 | N
24/01/2017 | 08:30 | 229:34995 | SHORT RURAL | Planned |  | 2 | 140 | 0.0012568 | 0.00089773 | N
24/01/2017 | 08:30 | 526:34640 | SHORT RURAL | Planned |  | 1 | 245 | 0.0010997 | 0.00044887 | N
24/01/2017 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 3 | 125 | 0.0016832 | 0.0013466 | N
24/01/2017 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 5 | 170 | 0.30292 | 0.17819 | N
24/01/2017 | 08:30 | 806:82662 | SHORT RURAL | Planned |  | 3 | 200 | 0.0026932 | 0.0013466 | N
25/01/2017 | 11:30 | 515:35192 | SHORT RURAL | Planned |  | 159 | 25 | 0.017844 | 0.071374 | N
25/01/2017 | 09:45 | 227:13020 | SHORT RURAL | Planned |  | 13 | 340 | 0.019841 | 0.0058356 | N
25/01/2017 | 08:30 | 225:33670 | URBAN | Planned |  | 63 | 380 | 0.016491 | 0.0043397 | N
25/01/2017 | 08:30 | 225:33679 | URBAN | Planned |  | 65 | 380 | 0.017015 | 0.0044775 | N
25/01/2017 | 08:00 | 511:29877 | SHORT RURAL | Planned |  | 5 | 340 | 0.0076312 | 0.0022445 | N
25/01/2017 | 08:15 | 528:83014 | SHORT RURAL | Planned |  | 19 | 105 | 0.0089554 | 0.008529 | N
25/01/2017 | 10:00 | 528:83014 | SHORT RURAL | Planned |  | 62 | 360 | 0.10019 | 0.027831 | N
25/01/2017 | 10:20 | 507:80914 | SHORT RURAL | Planned |  | 100 | 225 | 0.101 | 0.044889 | N
25/01/2017 | 08:15 | 232:11457 | SHORT RURAL | Planned |  | 1 | 245 | 0.0010998 | 0.00044889 | N
25/01/2017 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 1 | 220 | 0.00098757 | 0.00044889 | N
25/01/2017 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 1 | 360 | 0.1283 | 0.035638 | N
25/01/2017 | 11:05 | 515:35197 | LONG RURAL | Planned |  | 1 | 35 | 0.012473 | 0.035638 | N
27/01/2017 | 08:40 | 512:48049 | SHORT RURAL | Planned |  | 1 | 65 | 0.00029137 | 0.00044826 | N
30/01/2017 | 08:00 | 508:82579 | SHORT RURAL | Planned |  | 11 | 205 | 0.010108 | 0.0049308 | N
30/01/2017 | 08:50 | 512:48049 | SHORT RURAL | Planned |  | 6 | 15 | 0.00040343 | 0.0026895 | N
30/01/2017 | 08:40 | 515:35192 | SHORT RURAL | Planned |  | 5 | 165 | 0.0036981 | 0.0022413 | N
30/01/2017 | 09:10 | 811:74234 | SHORT RURAL | Planned |  | 1 | 20 | 8.9652e-05 | 0.00044826 | N
30/01/2017 | 10:00 | 811:74234 | SHORT RURAL | Planned |  | 1 | 100 | 0.00044826 | 0.00044826 | N
31/01/2017 | 18:56 | 814:82291 | SHORT RURAL | Planned |  | 35 | 177 | 0.027791 | 0.015689 | N
01/02/2017 | 08:10 | 509:33395 | LONG RURAL | Planned |  | 252 | 400 | 35.9088 | 8.9808 | N
31/01/2017 | 17:45 | 257:81997 | URBAN | Planned |  | 1 | 195 | 0.00013431 | 6.8876e-05 | N
31/01/2017 | 08:35 | 230:81432 | SHORT RURAL | Planned |  | 2 | 177 | 0.0015868 | 0.00089652 | N
31/01/2017 | 08:30 | 511:29877 | SHORT RURAL | Planned |  | 1 | 75 | 0.0003362 | 0.00044826 | N
31/01/2017 | 10:55 | 507:80925 | SHORT RURAL | Planned |  | 2 | 50 | 0.00044826 | 0.00089652 | N
31/01/2017 | 08:30 | 806:82662 | SHORT RURAL | Planned |  | 24 | 360 | 0.03873 | 0.010758 | N
31/01/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 17 | 260 | 0.019813 | 0.0076204 | N
31/01/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 24 | 255 | 2.181 | 0.85531 | N
01/02/2017 | 08:30 | 221:11893 | URBAN | Planned |  | 214 | 295 | 0.043482 | 0.01474 | N
01/02/2017 | 09:30 | 227:13015 | SHORT RURAL | Planned |  | 17 | 315 | 0.024005 | 0.0076206 | N
01/02/2017 | 08:00 | 264:81244 | SHORT RURAL | Planned |  | 22 | 495 | 0.048816 | 0.0098619 | N
01/02/2017 | 08:45 | 528:83019 | SHORT RURAL | Planned |  | 2 | 105 | 0.00094136 | 0.00089654 | N
01/02/2017 | 08:30 | 528:83019 | SHORT RURAL | Planned |  | 2 | 370 | 0.0033172 | 0.00089654 | N
01/02/2017 | 12:00 | 532:83307 | SHORT RURAL | Planned |  | 3 | 105 | 0.001412 | 0.0013448 | N
01/02/2017 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 11 | 230 | 0.011341 | 0.0049309 | N
01/02/2017 | 08:30 | 515:35198 | SHORT RURAL | Planned |  | 4 | 230 | 0.0041241 | 0.0017931 | N
01/02/2017 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 27 | 420 | 0.050834 | 0.012103 | N
01/02/2017 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 3 | 290 | 0.0038999 | 0.0013448 | N
04/02/2017 | 20:56 | ZN12610:PA10 | URBAN | Planned |  | 775 | 1 | 0.00053374 | 0.053374 | N
02/02/2017 | 09:45 | 223:14399 | SHORT RURAL | Planned |  | 69 | 200 | 0.06185 | 0.030925 | N
02/02/2017 | 08:00 | 243:80080 | SHORT RURAL | Planned |  | 1 | 450 | 0.0020169 | 0.00044819 | N
03/02/2017 | 09:51 | 243:80080 | SHORT RURAL | Planned |  | 97 | 104 | 0.045214 | 0.043475 | N
03/02/2017 | 09:00 | 227:13015 | SHORT RURAL | Planned |  | 42 | 375 | 0.070591 | 0.018824 | N
02/02/2017 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 1 | 155 | 0.00069469 | 0.00044819 | N
02/02/2017 | 09:08 | 508:82580 | SHORT RURAL | Planned |  | 57 | 292 | 0.074597 | 0.025547 | N
03/02/2017 | 09:07 | 526:34633 | SHORT RURAL | Planned |  | 1 | 63 | 0.00028236 | 0.0004482 | N
03/02/2017 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 129 | 255 | 0.14743 | 0.057817 | N
03/02/2017 | 09:55 | 532:83309 | SHORT RURAL | Planned |  | 136 | 65 | 0.039621 | 0.060955 | N
03/02/2017 | 11:35 | 526:34633 | SHORT RURAL | Planned |  | 1 | 49 | 0.00021962 | 0.0004482 | N
03/02/2017 | 08:50 | 507:80932 | SHORT RURAL | Planned |  | 25 | 360 | 0.040338 | 0.011205 | N
02/02/2017 | 08:30 | 523:33508 | SHORT RURAL | Planned |  | 18 | 225 | 0.018152 | 0.0080674 | N
02/02/2017 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 10 | 225 | 0.010084 | 0.0044819 | N
02/02/2017 | 09:40 | 515:35197 | LONG RURAL | Planned |  | 1 | 50 | 0.017806 | 0.035613 | N
02/02/2017 | 08:30 | 806:82662 | SHORT RURAL | Planned |  | 15 | 480 | 0.03227 | 0.0067228 | N
03/02/2017 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 3 | 215 | 0.0028909 | 0.0013446 | N
03/02/2017 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 12 | 360 | 0.019362 | 0.0053784 | N
03/02/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 12 | 310 | 1.3248 | 0.42735 | N
03/02/2017 | 09:45 | 806:82662 | SHORT RURAL | Planned |  | 1 | 110 | 0.00049302 | 0.0004482 | N
03/02/2017 | 08:20 | 806:82662 | SHORT RURAL | Planned |  | 6 | 270 | 0.0072608 | 0.0026892 | N
03/02/2017 | 13:00 | 806:82662 | SHORT RURAL | Planned |  | 1 | 35 | 0.00015687 | 0.0004482 | N
03/02/2017 | 10:45 | 806:82662 | SHORT RURAL | Planned |  | 1 | 70 | 0.00031374 | 0.0004482 | N
03/02/2017 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 1 | 295 | 0.0013222 | 0.0004482 | N
03/02/2017 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 1 | 270 | 0.0012101 | 0.0004482 | N
03/02/2017 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 1 | 300 | 0.0013446 | 0.0004482 | N
03/02/2017 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 1 | 240 | 0.0010757 | 0.0004482 | N
03/02/2017 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 2 | 180 | 0.0016135 | 0.00089639 | N
06/02/2017 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 3 | 80 | 0.08547 | 0.10684 | N
06/02/2017 | 08:00 | 235:2120 | SHORT RURAL | Planned |  | 1 | 30 | 0.00013443 | 0.00044811 | N
06/02/2017 | 08:30 | 807:74180 | SHORT RURAL | Planned |  | 1 | 225 | 0.0010083 | 0.00044811 | N
06/02/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 10 | 230 | 0.81909 | 0.35613 | N
07/02/2017 | 11:15 | 802:82225 | SHORT RURAL | Planned |  | 2 | 60 | 0.00053774 | 0.00089623 | N
07/02/2017 | 07:30 | 512:48048 | SHORT RURAL | Planned |  | 3 | 540 | 0.0072595 | 0.0013443 | N
07/02/2017 | 09:00 | 264:81244 | SHORT RURAL | Planned |  | 3 | 110 | 0.0014788 | 0.0013443 | N
07/02/2017 | 12:15 | 230:81432 | SHORT RURAL | Planned |  | 3 | 135 | 0.0018149 | 0.0013443 | N
07/02/2017 | 12:50 | 264:81244 | SHORT RURAL | Planned |  | 6 | 50 | 0.0013443 | 0.0026887 | N
07/02/2017 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 10 | 210 | 0.74813 | 0.35625 | N
07/02/2017 | 08:31 | 513:48059 | SHORT RURAL | Planned |  | 3 | 109 | 0.0014653 | 0.0013443 | N
07/02/2017 | 08:40 | 520:48172 | SHORT RURAL | Planned |  | 45 | 405 | 0.081669 | 0.020165 | N
07/02/2017 | 13:05 | 513:48059 | SHORT RURAL | Planned |  | 4 | 75 | 0.0013443 | 0.0017925 | N
07/02/2017 | 09:45 | 802:82225 | SHORT RURAL | Planned |  | 2 | 135 | 0.0012099 | 0.00089623 | N
07/02/2017 | 12:00 | 802:82225 | SHORT RURAL | Planned |  | 2 | 115 | 0.0010307 | 0.00089623 | N
08/02/2017 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 11 | 200 | 0.0098586 | 0.0049293 | N
08/02/2017 | 08:55 | 243:80074 | SHORT RURAL | Planned |  | 2 | 240 | 0.002151 | 0.00089624 | N
08/02/2017 | 08:40 | 233:82819 | SHORT RURAL | Planned |  | 47 | 330 | 0.069503 | 0.021062 | N
08/02/2017 | 08:15 | 235:2120 | SHORT RURAL | Planned |  | 113 | 200 | 0.10127 | 0.050637 | N
08/02/2017 | 08:30 | 232:11457 | SHORT RURAL | Planned |  | 23 | 390 | 0.040196 | 0.010307 | N
08/02/2017 | 08:35 | 524:33580 | SHORT RURAL | Planned |  | 7 | 73 | 0.0022899 | 0.0031368 | N
08/02/2017 | 08:30 | 507:80914 | SHORT RURAL | Planned |  | 2 | 118 | 0.0010576 | 0.00089624 | N
08/02/2017 | 11:15 | 235:2120 | SHORT RURAL | Planned |  | 1 | 67 | 0.00030024 | 0.00044812 | N
08/02/2017 | 12:55 | 507:80932 | SHORT RURAL | Planned |  | 1 | 112 | 0.00050189 | 0.00044812 | N
08/02/2017 | 13:20 | 235:2120 | SHORT RURAL | Planned |  | 2 | 70 | 0.00062737 | 0.00089624 | N
08/02/2017 | 08:40 | 801:74121 | LONG RURAL | Planned |  | 2 | 35 | 0.024938 | 0.07125 | N
08/02/2017 | 09:40 | 807:74181 | SHORT RURAL | Planned |  | 3 | 60 | 0.00080661 | 0.0013444 | N
04/01/2017 | 07:20 | ZN901:PA2 | URBAN | Planned |  | 1 | 130 | 8.9585e-05 | 6.8912e-05 | N
04/01/2017 | 11:25 | ZN12690:PA16 | SHORT RURAL | Planned |  | 26 | 90 | 0.010506 | 0.011674 | N
04/01/2017 | 11:01 | ZN9035:PA4 | URBAN | Planned |  | 1 | 89 | 6.1332e-05 | 6.8912e-05 | N
05/01/2017 | 10:45 | ZN14143:PA17 | SHORT RURAL | Planned |  | 9 | 115 | 0.004647 | 0.0040409 | N
05/01/2017 | 09:50 | ZN1673:PA6 | URBAN | Planned |  | 35 | 350 | 0.0084419 | 0.002412 | N
07/01/2017 | 06:30 | ZN14891:PA9 | URBAN | Planned |  | 11 | 590 | 0.0044711 | 0.00075782 | N
07/01/2017 | 06:30 | ZN14891:PA9 | URBAN | Planned |  | 29 | 570 | 0.011388 | 0.0019979 | N
07/01/2017 | 06:30 | ZN3922:PA17 | SHORT RURAL | Planned |  | 2 | 266 | 0.0023877 | 0.00089761 | N
07/01/2017 | 08:00 | ZN1610:PA4 | URBAN | Planned |  | 2 | 10 | 1.3779e-05 | 0.00013779 | N
08/01/2017 | 08:40 | ZN2835:PA35 | URBAN | Planned |  | 26 | 230 | 0.0041198 | 0.0017912 | N
08/01/2017 | 18:30 | ZN384:PA70 | URBAN | Planned |  | 30 | 800 | 0.016534 | 0.0020668 | N
08/01/2017 | 18:30 | ZN384:PA70 | URBAN | Planned |  | 6 | 800 | 0.0033068 | 0.00041335 | N
09/01/2017 | 06:30 | ZN9118:PA16 | URBAN | Planned |  | 27 | 145 | 0.0026971 | 0.0018601 | N
09/01/2017 | 07:00 | ZN9252:PA24 | URBAN | Planned |  | 1 | 540 | 0.00037202 | 6.8892e-05 | N
09/01/2017 | 07:45 | ZN15012:PA6 | URBAN | Planned |  | 4 | 465 | 0.0012814 | 0.00027557 | N
09/01/2017 | 07:30 | ZN10993:PA34 | URBAN | Planned |  | 73 | 70 | 0.0035204 | 0.0050292 | N
09/01/2017 | 07:51 | ZN2400:PA21 | URBAN | Planned |  | 6 | 511 | 0.0021122 | 0.00041335 | N
09/01/2017 | 08:30 | ZN10999:PA32 | URBAN | Planned |  | 39 | 360 | 0.0096725 | 0.0026868 | N
09/01/2017 | 08:30 | ZN3922:PA5 | URBAN | Planned |  | 1 | 2,030 | 0.0013985 | 6.8892e-05 | N
10/01/2017 | 08:25 | ZN14891:PA5 | SHORT RURAL | Planned |  | 7 | 375 | 0.011781 | 0.0031417 | N
11/01/2017 | 08:20 | ZN965:PA26 | URBAN | Planned |  | 1 | 430 | 0.00029624 | 6.8894e-05 | N
12/01/2017 | 07:30 | ZN2835:PA16 | URBAN | Planned |  | 14 | 630 | 0.0060756 | 0.00096438 | N
12/01/2017 | 08:00 | ZN14892:PA19 | URBAN | Planned |  | 62 | 480 | 0.0205 | 0.0042708 | N
12/01/2017 | 10:00 | ZN14892:PA14 | SHORT RURAL | Planned |  | 40 | 192 | 0.034472 | 0.017954 | N
12/01/2017 | 06:30 | ZN72:PA31 | URBAN | Planned |  | 61 | 810 | 0.034036 | 0.0042019 | N
13/01/2017 | 08:00 | ZN12600:PA1 | SHORT RURAL | Planned |  | 29 | 470 | 0.061179 | 0.013017 | N
13/01/2017 | 09:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 70 | 360 | 0.11311 | 0.03142 | N
14/01/2017 | 04:00 | ZN2466:PA22 | URBAN | Planned |  | 1 | 75 | 5.1664e-05 | 6.8886e-05 | N
14/01/2017 | 06:30 | ZN15009:PA1 | URBAN | Planned |  | 6 | 270 | 0.001116 | 0.00041332 | N
14/01/2017 | 11:00 | ZN1610:PA17 | URBAN | Planned |  | 1 | 270 | 0.00018599 | 6.8886e-05 | N
15/01/2017 | 07:30 | ZN1648:PA11 | URBAN | Planned |  | 1 | 360 | 0.00024799 | 6.8886e-05 | N
15/01/2017 | 10:00 | ZN1290:PA13 | URBAN | Planned |  | 2 | 210 | 0.00028932 | 0.00013777 | N
16/01/2017 | 09:20 | ZN10993:PA33 | URBAN | Planned |  | 30 | 415 | 0.0085763 | 0.0020666 | N
16/01/2017 | 08:21 | ZN188:PA43 | URBAN | Planned |  | 176 | 519 | 0.062923 | 0.012124 | N
16/01/2017 | 08:00 | ZN901:PA10 | URBAN | Planned |  | 36 | 480 | 0.011903 | 0.0024799 | N
16/01/2017 | 08:30 | ZN12630:PA11 | SHORT RURAL | Planned |  | 27 | 445 | 0.053929 | 0.012119 | N
16/01/2017 | 09:20 | ZN12630:PA8 | SHORT RURAL | Planned |  | 31 | 205 | 0.028524 | 0.013914 | N
17/01/2017 | 06:00 | ZN3154:PA11 | URBAN | Planned |  | 20 | 540 | 0.0074397 | 0.0013777 | N
17/01/2017 | 07:30 | ZN2602:PA35 | URBAN | Planned |  | 44 | 495 | 0.015003 | 0.003031 | N
17/01/2017 | 07:30 | ZN35600:PA20 | URBAN | Planned |  | 40 | 495 | 0.01364 | 0.0027555 | N
17/01/2017 | 08:00 | ZN36800:PA50 | URBAN | Planned |  | 110 | 375 | 0.028416 | 0.0075775 | N
17/01/2017 | 08:15 | ZN14891:PA5 | SHORT RURAL | Planned |  | 9 | 465 | 0.018784 | 0.0040397 | N
17/01/2017 | 08:01 | ZN12630:PA11 | SHORT RURAL | Planned |  | 6 | 464 | 0.012496 | 0.0026931 | N
18/01/2017 | 06:30 | ZN35370:PA2 | SHORT RURAL | Planned |  | 1 | 600 | 0.0026931 | 0.00044885 | N
18/01/2017 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 8 | 465 | 0.016697 | 0.0035908 | N
18/01/2017 | 19:40 | ZN1610:PA19 | URBAN | Planned |  | 7 | 560 | 0.0027004 | 0.00048221 | N
18/01/2017 | 20:30 | ZN10997:PA7 | URBAN | Planned |  | 62 | 720 | 0.030751 | 0.004271 | N
18/01/2017 | 06:00 | ZN10997:PA2 | URBAN | Planned |  | 19 | 870 | 0.011387 | 0.0013089 | N
18/01/2017 | 20:30 | ZN10997:PA1 | URBAN | Planned |  | 50 | 720 | 0.024799 | 0.0034443 | N
18/01/2017 | 20:30 | ZN10997:PA2 | URBAN | Planned |  | 19 | 720 | 0.0094237 | 0.0013089 | N
18/01/2017 | 20:30 | ZN10997:PA7 | URBAN | Planned |  | 30 | 720 | 0.01488 | 0.0020666 | N
19/01/2017 | 06:30 | ZN15005:PA10 | URBAN | Planned |  | 2 | 2,070 | 0.0028517 | 0.00013776 | N
19/01/2017 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 2 | 320 | 0.0028725 | 0.00089765 | N
19/01/2017 | 10:45 | ZN847:PA21 | URBAN | Planned |  | 43 | 165 | 0.0048871 | 0.0029619 | N
19/01/2017 | 10:45 | ZN847:PA21 | URBAN | Planned |  | 50 | 165 | 0.0056827 | 0.0034441 | N
19/01/2017 | 22:30 | ZN3155:PA16 | URBAN | Planned |  | 140 | 300 | 0.02893 | 0.0096434 | N
20/01/2017 | 07:30 | ZN12620:PA8 | SHORT RURAL | Planned |  | 13 | 570 | 0.033257 | 0.0058346 | N
20/01/2017 | 08:00 | ZN2602:PA27 | URBAN | Planned |  | 36 | 540 | 0.013391 | 0.0024798 | N
20/01/2017 | 08:00 | ZN12610:PA6 | URBAN | Planned |  | 69 | 540 | 0.025666 | 0.0047529 | N
20/01/2017 | 08:30 | ZN14891:PA12 | SHORT RURAL | Planned |  | 21 | 395 | 0.037229 | 0.0094251 | N
20/01/2017 | 08:30 | ZN36800:PA57 | URBAN | Planned |  | 78 | 225 | 0.012089 | 0.0053728 | N
20/01/2017 | 10:05 | ZN12630:PA3 | SHORT RURAL | Planned |  | 9 | 225 | 0.0090885 | 0.0040393 | N
20/01/2017 | 10:25 | ZN12600:PA2 | SHORT RURAL | Planned |  | 6 | 100 | 0.0026929 | 0.0026929 | N
20/01/2017 | 10:25 | ZN12600:PA2 | SHORT RURAL | Planned |  | 5 | 100 | 0.0022441 | 0.0022441 | N
21/01/2017 | 07:00 | ZN12690:PA1 | URBAN | Planned |  | 2 | 660 | 0.00090925 | 0.00013777 | N
22/01/2017 | 14:00 | ZN3425:PA18 | URBAN | Planned |  | 54 | 1,040 | 0.038684 | 0.0037197 | N
23/01/2017 | 07:30 | ZN2835:PA33 | URBAN | Planned |  | 62 | 570 | 0.024343 | 0.0042707 | N
24/01/2017 | 07:30 | ZN10995:PA7 | URBAN | Planned |  | 38 | 480 | 0.012564 | 0.0026176 | N
24/01/2017 | 11:00 | ZN12600:PA11 | URBAN | Planned |  | 60 | 75 | 0.0030998 | 0.004133 | N
25/01/2017 | 08:00 | ZN35900:PA25 | SHORT RURAL | Planned |  | 1 | 478 | 0.0021457 | 0.00044889 | N
25/01/2017 | 08:45 | ZN15008:PA5 | URBAN | Planned |  | 12 | 375 | 0.0030998 | 0.00082662 | N
25/01/2017 | 08:30 | ZN12610:PA10 | URBAN | Planned |  | 62 | 540 | 0.023063 | 0.0042709 | N
25/01/2017 | 08:30 | ZN12610:PA18 | URBAN | Planned |  | 15 | 540 | 0.0055797 | 0.0010333 | N
25/01/2017 | 08:12 | ZN12660:PA10 | URBAN | Planned |  | 79 | 213 | 0.011591 | 0.0054419 | N
25/01/2017 | 08:45 | ZN14891:PA20 | SHORT RURAL | Planned |  | 15 | 355 | 0.023904 | 0.0067334 | N
27/01/2017 | 09:30 | ZN10990:PA5 | URBAN | Planned |  | 1 | 2,940 | 0.0020249 | 6.8874e-05 | N
27/01/2017 | 23:31 | ZN263:PA33 34GHJ | CBD | Planned |  | 32 | 209 | 0.21522 | 0.10298 | N
28/01/2017 | 06:30 | ZN847:PA10 | URBAN | Planned |  | 1 | 615 | 0.00042358 | 6.8875e-05 | N
30/01/2017 | 07:00 | ZN262:PA19 | URBAN | Planned |  | 110 | 450 | 0.034093 | 0.0075763 | N
30/01/2017 | 07:30 | ZN35900:PA2 | URBAN | Planned |  | 44 | 450 | 0.013637 | 0.0030305 | N
30/01/2017 | 09:40 | ZN14891:PA5 | SHORT RURAL | Planned |  | 2 | 320 | 0.0028688 | 0.00089652 | N
30/01/2017 | 09:30 | ZN36200:PA8 | SHORT RURAL | Planned |  | 32 | 85 | 0.012193 | 0.014344 | N
30/01/2017 | 20:00 | ZN965:PA21 | URBAN | Planned |  | 44 | 480 | 0.014546 | 0.0030305 | N
31/01/2017 | 07:55 | ZN12630:PA1 | SHORT RURAL | Planned |  | 317 | 480 | 0.68207 | 0.1421 | N
31/01/2017 | 08:30 | ZN36100:PA13 | URBAN | Planned |  | 30 | 300 | 0.0061989 | 0.0020663 | N
31/01/2017 | 20:00 | ZN2635:PA58 | URBAN | Planned |  | 38 | 480 | 0.012563 | 0.0026173 | N
10/02/2017 | 06:06 | 202:34254 | URBAN | Planned |  | 5 | 9 | 3.0997e-05 | 0.00034442 | N
09/02/2017 | 08:40 | 239:82133 | URBAN | Planned |  | 93 | 400 | 0.025622 | 0.0064054 | N
09/02/2017 | 09:00 | 239:82127 | SHORT RURAL | Planned |  | 89 | 195 | 0.07766 | 0.039826 | N
09/02/2017 | 08:45 | 526:34640 | SHORT RURAL | Planned |  | 3 | 50 | 0.00067122 | 0.0013424 | N
09/02/2017 | 08:25 | 504:48031 | SHORT RURAL | Planned |  | 28 | 195 | 0.024432 | 0.012529 | N
09/02/2017 | 08:30 | 507:80932 | SHORT RURAL | Planned |  | 2 | 265 | 0.0023717 | 0.00089496 | N
09/02/2017 | 11:36 | 526:34635 | SHORT RURAL | Planned |  | 3 | 54 | 0.00072492 | 0.0013424 | N
09/02/2017 | 11:40 | 235:2120 | SHORT RURAL | Planned |  | 2 | 60 | 0.00053698 | 0.00089496 | N
09/02/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 12 | 310 | 1.3248 | 0.42735 | N
09/02/2017 | 09:25 | 515:35197 | LONG RURAL | Planned |  | 20 | 245 | 1.745 | 0.71225 | N
10/02/2017 | 11:00 | 526:34640 | SHORT RURAL | Planned |  | 2 | 70 | 0.00062646 | 0.00089495 | N
10/02/2017 | 07:05 | 532:83309 | SHORT RURAL | Planned |  | 4 | 535 | 0.0095759 | 0.0017899 | N
10/02/2017 | 08:05 | 504:48031 | SHORT RURAL | Planned |  | 2 | 215 | 0.0019241 | 0.00089495 | N
10/02/2017 | 08:35 | 526:34640 | SHORT RURAL | Planned |  | 2 | 55 | 0.00049222 | 0.00089495 | N
10/02/2017 | 11:00 | 512:48048 | SHORT RURAL | Planned |  | 2 | 45 | 0.00040273 | 0.00089495 | N
10/02/2017 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 1 | 50 | 0.00022374 | 0.00044747 | N
10/02/2017 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 6 | 135 | 0.0036245 | 0.0026848 | N
10/02/2017 | 08:30 | 523:33508 | SHORT RURAL | Planned |  | 3 | 150 | 0.0020136 | 0.0013424 | N
10/02/2017 | 08:30 | 807:74180 | SHORT RURAL | Planned |  | 1 | 70 | 0.00031323 | 0.00044747 | N
10/02/2017 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 16 | 110 | 0.0078755 | 0.0071596 | N
10/02/2017 | 09:50 | 807:74180 | SHORT RURAL | Planned |  | 3 | 22 | 0.00029533 | 0.0013424 | N
10/02/2017 | 09:45 | 801:74123 | SHORT RURAL | Planned |  | 2 | 50 | 0.00044747 | 0.00089495 | N
13/02/2017 | 09:00 | 243:80081 | SHORT RURAL | Planned |  | 194 | 326 | 0.283 | 0.08681 | N
13/02/2017 | 08:50 | 526:34633 | SHORT RURAL | Planned |  | 2 | 90 | 0.00080545 | 0.00089495 | N
13/02/2017 | 08:35 | 507:80932 | SHORT RURAL | Planned |  | 1 | 200 | 0.00089495 | 0.00044747 | N
13/02/2017 | 11:30 | 526:34633 | SHORT RURAL | Planned |  | 1 | 50 | 0.00022374 | 0.00044747 | N
13/02/2017 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 1 | 55 | 0.019587 | 0.035613 | N
13/02/2017 | 09:55 | 801:74121 | LONG RURAL | Planned |  | 1 | 50 | 0.017806 | 0.035613 | N
14/02/2017 | 08:45 | 511:29878 | SHORT RURAL | Planned |  | 16 | 375 | 0.026778 | 0.0071409 | N
14/02/2017 | 08:45 | 513:48050 | SHORT RURAL | Planned |  | 8 | 205 | 0.0073194 | 0.0035704 | N
14/02/2017 | 09:00 | 813:89055 | SHORT RURAL | Planned |  | 24 | 290 | 0.031063 | 0.010711 | N
14/02/2017 | 11:33 | 509:33395 | LONG RURAL | Planned |  | 1 | 67 | 0.02386 | 0.035613 | N
14/02/2017 | 08:00 | 223:14395 | SHORT RURAL | Planned |  | 117 | 480 | 0.25064 | 0.052218 | N
14/02/2017 | 08:45 | 242:81533 | SHORT RURAL | Planned |  | 3 | 90 | 0.001205 | 0.0013389 | N
14/02/2017 | 09:49 | 509:33395 | LONG RURAL | Planned |  | 1 | 37 | 0.013177 | 0.035613 | N
14/02/2017 | 09:55 | 509:33395 | LONG RURAL | Planned |  | 2 | 54 | 0.038462 | 0.071225 | N
16/02/2017 | 20:28 | ZN10999:PA36 | URBAN | Planned |  | 1 | 212 | 0.00014595 | 6.8888e-05 | N
17/02/2017 | 09:05 | 812:19066 | SHORT RURAL | Planned |  | 45 | 210 | 0.042204 | 0.020097 | Y
01/02/2017 | 09:00 | ZN12600:PA11 | URBAN | Planned |  | 56 | 360 | 0.013886 | 0.0038571 | N
01/02/2017 | 08:00 | ZN2602:PA27 | URBAN | Planned |  | 114 | 500 | 0.03926 | 0.0078519 | N
01/02/2017 | 08:20 | ZN12650:PA1 | SHORT RURAL | Planned |  | 3 | 400 | 0.0053792 | 0.0013448 | N
01/02/2017 | 20:00 | ZN965:PA3 | URBAN | Planned |  | 19 | 480 | 0.0062815 | 0.0013087 | N
02/02/2017 | 07:30 | ZN72:PA10 | URBAN | Planned |  | 44 | 300 | 0.0090903 | 0.0030301 | N
02/02/2017 | 08:15 | ZN12690:PA24 | SHORT RURAL | Planned |  | 12 | 390 | 0.020975 | 0.0053783 | N
02/02/2017 | 08:45 | ZN14891:PA12 | SHORT RURAL | Planned |  | 43 | 405 | 0.078052 | 0.019272 | N
02/02/2017 | 08:00 | ZN262:PA28 | URBAN | Planned |  | 1 | 120 | 8.2639e-05 | 6.8866e-05 | N
02/02/2017 | 08:00 | ZN2568:PA38 | URBAN | Planned |  | 81 | 390 | 0.021755 | 0.0055781 | N
03/02/2017 | 06:30 | ZN2635:PA62 | URBAN | Planned |  | 1 | 1,980 | 0.0013636 | 6.8867e-05 | N
03/02/2017 | 08:00 | ZN36300:PA19 | URBAN | Planned |  | 87 | 540 | 0.032354 | 0.0059914 | N
03/02/2017 | 08:00 | ZN14891:PA9 | URBAN | Planned |  | 65 | 420 | 0.018801 | 0.0044764 | N
03/02/2017 | 08:00 | ZN14892:PA6 | SHORT RURAL | Planned |  | 4 | 420 | 0.0075297 | 0.0017928 | N
03/02/2017 | 09:45 | ZN12640:PA13 | SHORT RURAL | Planned |  | 71 | 185 | 0.058871 | 0.031822 | N
03/02/2017 | 09:30 | ZN1290:PA12 | URBAN | Planned |  | 1 | 2,160 | 0.0014875 | 6.8867e-05 | N
04/02/2017 | 07:00 | ZN15005:PA2 | URBAN | Planned |  | 1 | 510 | 0.00035123 | 6.8869e-05 | N
04/02/2017 | 08:30 | ZN12640:PA1 | SHORT RURAL | Planned |  | 68 | 360 | 0.10972 | 0.030477 | N
05/02/2017 | 00:01 | ZN188:PA29 | URBAN | Planned |  | 1 | 299 | 0.00020593 | 6.8873e-05 | N
05/02/2017 | 00:01 | ZN188:PA41 | URBAN | Planned |  | 1 | 299 | 0.00020593 | 6.8873e-05 | N
05/02/2017 | 00:30 | ZN12610:PA9 | URBAN | Planned |  | 9 | 360 | 0.0022315 | 0.00061986 | N
05/02/2017 | 23:30 | ZN14891:PA20 | SHORT RURAL | Planned |  | 8 | 245 | 0.008783 | 0.0035849 | N
06/02/2017 | 00:30 | ZN14891:PA19 | SHORT RURAL | Planned |  | 2 | 330 | 0.0029575 | 0.00089623 | N
06/02/2017 | 08:00 | ZN15014:PA5 | URBAN | Planned |  | 178 | 600 | 0.073557 | 0.012259 | N
06/02/2017 | 07:00 | ZN15014:PA5 | URBAN | Planned |  | 12 | 660 | 0.0054548 | 0.00082648 | N
06/02/2017 | 07:30 | ZN10993:PA43 | URBAN | Planned |  | 41 | 480 | 0.013554 | 0.0028238 | N
06/02/2017 | 08:00 | ZN14143:PA12 | SHORT RURAL | Planned |  | 3 | 480 | 0.0064528 | 0.0013443 | N
07/02/2017 | 07:30 | ZN10999:PA4 | URBAN | Planned |  | 41 | 310 | 0.008754 | 0.0028239 | N
07/02/2017 | 09:00 | ZN14892:PA3 | URBAN | Planned |  | 57 | 420 | 0.016489 | 0.0039259 | N
07/02/2017 | 08:30 | ZN847:PA21 | URBAN | Planned |  | 11 | 540 | 0.0040912 | 0.00075762 | N
08/02/2017 | 07:40 | ZN1287:PA4 | URBAN | Planned |  | 78 | 860 | 0.046202 | 0.0053723 | N
08/02/2017 | 08:00 | ZN965:PA3 | URBAN | Planned |  | 24 | 360 | 0.0059509 | 0.001653 | N
08/02/2017 | 08:00 | ZN384:PA33 | URBAN | Planned |  | 192 | 210 | 0.027771 | 0.013224 | N
08/02/2017 | 18:30 | ZN12650:PA17 | URBAN | Planned |  | 47 | 710 | 0.022984 | 0.0032372 | N
08/02/2017 | 20:30 | ZN15004:PA1 | URBAN | Planned |  | 63 | 510 | 0.02213 | 0.0043392 | N
09/02/2017 | 07:40 | ZN14143:PA17 | SHORT RURAL | Planned |  | 164 | 558 | 0.4095 | 0.073387 | N
09/02/2017 | 07:30 | ZN12630:PA1 | SHORT RURAL | Planned |  | 11 | 540 | 0.02658 | 0.0049223 | N
09/02/2017 | 08:00 | ZN15001:PA11 | URBAN | Planned |  | 2 | 540 | 0.00074386 | 0.00013775 | N
09/02/2017 | 08:20 | ZN80:PA24 | URBAN | Planned |  | 2 | 105 | 0.00014464 | 0.00013775 | N
09/02/2017 | 09:00 | ZN965:PA42 | URBAN | Planned |  | 58 | 300 | 0.011984 | 0.0039948 | N
10/02/2017 | 09:00 | ZN36800:PA49 | URBAN | Planned |  | 73 | 240 | 0.012068 | 0.0050285 | N
10/02/2017 | 09:30 | ZN35900:PA10 | URBAN | Planned |  | 1 | 360 | 0.00024798 | 6.8883e-05 | N
10/02/2017 | 21:30 | ZN36800:PA42 | URBAN | Planned |  | 65 | 390 | 0.017462 | 0.0044774 | N
11/02/2017 | 07:15 | ZN12610:PA9 | URBAN | Planned |  | 30 | 665 | 0.013742 | 0.0020665 | N
15/02/2017 | 08:50 | 812:19072 | SHORT RURAL | Planned |  | 20 | 240 | 0.021423 | 0.0089261 | N
15/02/2017 | 08:15 | 502:48010 | SHORT RURAL | Planned |  | 13 | 461 | 0.026747 | 0.005802 | N
15/02/2017 | 08:30 | 264:81240 | SHORT RURAL | Planned |  | 14 | 330 | 0.020619 | 0.0062483 | N
16/02/2017 | 08:45 | 513:48059 | SHORT RURAL | Planned |  | 20 | 205 | 0.018311 | 0.008932 | N
16/02/2017 | 08:30 | 507:80923 | SHORT RURAL | Planned |  | 9 | 390 | 0.015676 | 0.0040194 | N
17/02/2017 | 08:30 | 807:74179 | SHORT RURAL | Planned |  | 5 | 320 | 0.0071456 | 0.002233 | Y
17/02/2017 | 09:00 | 512:48049 | SHORT RURAL | Planned |  | 7 | 275 | 0.008597 | 0.0031262 | Y
15/02/2017 | 08:00 | 225:33676 | URBAN | Planned |  | 2 | 480 | 0.00066149 | 0.00013781 | N
15/02/2017 | 09:00 | 227:13020 | SHORT RURAL | Planned |  | 58 | 400 | 0.10354 | 0.025886 | N
15/02/2017 | 09:10 | 217:33611 | URBAN | Planned |  | 213 | 420 | 0.061643 | 0.014677 | N
16/02/2017 | 08:20 | 224:80337 | SHORT RURAL | Planned |  | 43 | 465 | 0.089297 | 0.019204 | N
16/02/2017 | 20:35 | 221:11897 | URBAN | Planned |  | 39 | 487 | 0.013084 | 0.0026866 | N
16/02/2017 | 20:35 | 221:11894 | URBAN | Planned |  | 12 | 487 | 0.0040258 | 0.00082666 | N
17/02/2017 | 08:30 | 243:80083 | SHORT RURAL | Planned |  | 54 | 420 | 0.10129 | 0.024116 | Y
15/02/2017 | 11:00 | 507:80922 | SHORT RURAL | Planned |  | 18 | 60 | 0.0048201 | 0.0080335 | N
15/02/2017 | 09:00 | 532:83312 | URBAN | Planned |  | 31 | 360 | 0.0076898 | 0.0021361 | N
16/02/2017 | 08:50 | 509:33397 | SHORT RURAL | Planned |  | 4 | 275 | 0.0049126 | 0.0017864 | N
16/02/2017 | 09:40 | 532:83307 | SHORT RURAL | Planned |  | 99 | 280 | 0.1238 | 0.044213 | N
17/02/2017 | 07:15 | 532:83309 | SHORT RURAL | Planned |  | 4 | 617 | 0.011022 | 0.0017864 | Y
17/02/2017 | 08:30 | 265:81648 | SHORT RURAL | Planned |  | 2 | 270 | 0.0024116 | 0.0008932 | Y
18/02/2017 | 07:10 | 532:83309 | SHORT RURAL | Planned |  | 4 | 285 | 0.0050913 | 0.0017864 | N
15/02/2017 | 08:45 | 802:82225 | SHORT RURAL | Planned |  | 1 | 65 | 0.0002901 | 0.00044631 | N
15/02/2017 | 09:10 | 513:48059 | SHORT RURAL | Planned |  | 43 | 330 | 0.063331 | 0.019191 | N
15/02/2017 | 10:00 | 802:82225 | SHORT RURAL | Planned |  | 2 | 60 | 0.00053557 | 0.00089261 | N
16/02/2017 | 09:00 | 807:74184 | SHORT RURAL | Planned |  | 2 | 55 | 0.00049126 | 0.0008932 | N
16/02/2017 | 09:45 | 515:35197 | LONG RURAL | Planned |  | 4 | 150 | 0.21368 | 0.14245 | N
16/02/2017 | 10:35 | 807:74180 | SHORT RURAL | Planned |  | 1 | 25 | 0.00011165 | 0.0004466 | N
16/02/2017 | 09:45 | 515:35197 | LONG RURAL | Planned |  | 1 | 105 | 0.037393 | 0.035613 | N
17/02/2017 | 08:45 | 523:33501 | SHORT RURAL | Planned |  | 2 | 105 | 0.00093786 | 0.0008932 | Y
17/02/2017 | 08:30 | 526:34637 | SHORT RURAL | Planned |  | 24 | 250 | 0.026796 | 0.010718 | Y
17/02/2017 | 09:23 | 813:89061 | LONG RURAL | Planned |  | 22 | 372 | 2.9145 | 0.78348 | Y
20/02/2017 | 08:55 | 213:33777 | SHORT RURAL | Planned |  | 96 | 185 | 0.079317 | 0.042874 | N
20/02/2017 | 09:00 | 264:81240 | SHORT RURAL | Planned |  | 6 | 250 | 0.0066991 | 0.0026796 | N
20/02/2017 | 08:55 | 802:82225 | SHORT RURAL | Planned |  | 1 | 50 | 0.0002233 | 0.00044661 | N
20/02/2017 | 10:30 | 802:82220 | SHORT RURAL | Planned |  | 1 | 50 | 0.0002233 | 0.00044661 | N
20/02/2017 | 08:55 | 813:89061 | LONG RURAL | Planned |  | 2 | 145 | 0.10328 | 0.071225 | N
21/02/2017 | 08:45 | 507:80914 | SHORT RURAL | Planned |  | 100 | 315 | 0.14069 | 0.044663 | N
21/02/2017 | 08:30 | 213:33771 | URBAN | Planned |  | 107 | 310 | 0.022851 | 0.0073714 | N
21/02/2017 | 09:10 | 238:34148 | SHORT RURAL | Planned |  | 55 | 550 | 0.13511 | 0.024565 | N
21/02/2017 | 08:35 | 526:34639 | SHORT RURAL | Planned |  | 129 | 414 | 0.23853 | 0.057615 | N
21/02/2017 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 1 | 60 | 0.00026798 | 0.00044663 | N
21/02/2017 | 08:50 | 512:48049 | SHORT RURAL | Planned |  | 2 | 110 | 0.00098259 | 0.00089326 | N
21/02/2017 | 09:40 | 807:74184 | SHORT RURAL | Planned |  | 1 | 65 | 0.00029031 | 0.00044663 | N
21/02/2017 | 09:30 | 802:82225 | SHORT RURAL | Planned |  | 1 | 120 | 0.00053596 | 0.00044663 | N
21/02/2017 | 12:00 | 802:82225 | SHORT RURAL | Planned |  | 4 | 55 | 0.00098259 | 0.0017865 | N
21/02/2017 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 19 | 330 | 0.028004 | 0.008486 | N
22/02/2017 | 09:00 | 217:33611 | URBAN | Planned |  | 213 | 400 | 0.058697 | 0.014674 | N
22/02/2017 | 08:40 | 239:82127 | SHORT RURAL | Planned |  | 1 | 350 | 0.0015632 | 0.00044663 | N
22/02/2017 | 09:05 | 261:81870 | URBAN | Planned |  | 46 | 265 | 0.008398 | 0.0031691 | N
22/02/2017 | 08:50 | 205:12205 | SHORT RURAL | Planned |  | 217 | 280 | 0.27137 | 0.09692 | N
22/02/2017 | 08:30 | 507:80932 | SHORT RURAL | Planned |  | 7 | 180 | 0.0056276 | 0.0031264 | N
22/02/2017 | 09:40 | 235:2120 | SHORT RURAL | Planned |  | 6 | 265 | 0.0071015 | 0.0026798 | N
22/02/2017 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 18 | 315 | 0.025324 | 0.0080394 | N
22/02/2017 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 1 | 85 | 0.00037964 | 0.00044663 | N
22/02/2017 | 09:45 | 807:74184 | SHORT RURAL | Planned |  | 5 | 180 | 0.0040197 | 0.0022332 | N
22/02/2017 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 7 | 185 | 0.0057839 | 0.0031264 | N
22/02/2017 | 10:30 | 801:74123 | SHORT RURAL | Planned |  | 2 | 60 | 0.00053596 | 0.00089327 | N
22/02/2017 | 11:00 | 806:82662 | SHORT RURAL | Planned |  | 1 | 100 | 0.00044663 | 0.00044663 | N
23/02/2017 | 08:05 | 243:80083 | SHORT RURAL | Planned |  | 7 | 400 | 0.012502 | 0.0031255 | N
23/02/2017 | 08:55 | 528:83013 | URBAN | Planned |  | 1 | 550 | 0.00037886 | 6.8883e-05 | N
23/02/2017 | 08:07 | 217:33612 | URBAN | Planned |  | 145 | 455 | 0.045446 | 0.0099881 | N
23/02/2017 | 09:00 | 509:33399 | SHORT RURAL | Planned |  | 1 | 85 | 0.00037952 | 0.00044649 | N
23/02/2017 | 08:50 | 504:48033 | SHORT RURAL | Planned |  | 1 | 107 | 0.00047775 | 0.00044649 | N
23/02/2017 | 11:30 | 509:33399 | SHORT RURAL | Planned |  | 8 | 75 | 0.002679 | 0.003572 | N
23/02/2017 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 1 | 40 | 0.0001786 | 0.00044649 | N
23/02/2017 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 2 | 60 | 0.042735 | 0.071225 | N
23/02/2017 | 08:25 | 813:89055 | SHORT RURAL | Planned |  | 1 | 85 | 0.00037952 | 0.00044649 | N
23/02/2017 | 09:15 | 810:74050 | SHORT RURAL | Planned |  | 11 | 235 | 0.011542 | 0.0049114 | N
23/02/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 11 | 445 | 0.021856 | 0.0049114 | N
23/02/2017 | 09:20 | 801:74123 | SHORT RURAL | Planned |  | 1 | 40 | 0.0001786 | 0.00044649 | N
23/02/2017 | 12:30 | 515:35197 | LONG RURAL | Planned |  | 1 | 60 | 0.021368 | 0.035613 | N
24/02/2017 | 08:00 | 502:48010 | SHORT RURAL | Planned |  | 13 | 505 | 0.029311 | 0.0058042 | N
24/02/2017 | 08:30 | 512:48048 | SHORT RURAL | Planned |  | 4 | 350 | 0.0062507 | 0.0017859 | N
24/02/2017 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 35 | 330 | 0.051568 | 0.015627 | N
25/02/2017 | 08:35 | 216:10728 | SHORT RURAL | Planned |  | 44 | 360 | 0.070744 | 0.019651 | N
25/02/2017 | 11:00 | 221:11897 | URBAN | Planned |  | 111 | 360 | 0.027524 | 0.0076456 | N
24/02/2017 | 12:52 | 504:48031 | SHORT RURAL | Planned |  | 4 | 58 | 0.0010358 | 0.0017859 | N
24/02/2017 | 08:55 | 801:74123 | SHORT RURAL | Planned |  | 3 | 50 | 0.00066971 | 0.0013394 | N
24/02/2017 | 09:20 | 813:89061 | LONG RURAL | Planned |  | 1 | 55 | 0.01958 | 0.0356 | N
24/02/2017 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 3 | 60 | 0.06408 | 0.1068 | N
24/02/2017 | 09:10 | 807:74180 | SHORT RURAL | Planned |  | 1 | 40 | 0.00017859 | 0.00044648 | N
24/02/2017 | 09:55 | 807:74180 | SHORT RURAL | Planned |  | 1 | 35 | 0.00015627 | 0.00044648 | N
24/02/2017 | 10:05 | 807:74180 | SHORT RURAL | Planned |  | 1 | 35 | 0.00015627 | 0.00044648 | N
24/02/2017 | 09:00 | 807:74180 | SHORT RURAL | Planned |  | 1 | 55 | 0.00024556 | 0.00044648 | N
24/02/2017 | 10:10 | 801:74123 | SHORT RURAL | Planned |  | 2 | 40 | 0.00035718 | 0.00089295 | N
24/02/2017 | 10:55 | 813:89061 | LONG RURAL | Planned |  | 1 | 65 | 0.02314 | 0.0356 | N
27/02/2017 | 13:52 | ZN690:PA35 | URBAN | Planned |  | 61 | 237 | 0.0099487 | 0.0042016 | N
28/02/2017 | 08:45 | 523:33501 | SHORT RURAL | Planned |  | 2 | 30 | 0.00026797 | 0.00089324 | N
28/02/2017 | 08:20 | 504:48031 | SHORT RURAL | Planned |  | 6 | 270 | 0.0072352 | 0.0026797 | N
28/02/2017 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 12 | 270 | 1.1534 | 0.4272 | N
28/02/2017 | 08:30 | 225:33679 | URBAN | Planned |  | 36 | 360 | 0.0089268 | 0.0024797 | N
28/02/2017 | 19:50 | 222:33600 | URBAN | Planned |  | 76 | 175 | 0.009161 | 0.0052348 | N
28/02/2017 | 09:10 | 508:82579 | SHORT RURAL | Planned |  | 2 | 99 | 0.00088431 | 0.00089324 | N
28/02/2017 | 08:50 | 532:83307 | SHORT RURAL | Planned |  | 78 | 355 | 0.12367 | 0.034836 | N
28/02/2017 | 09:30 | 230:81432 | SHORT RURAL | Planned |  | 4 | 285 | 0.0050915 | 0.0017865 | N
28/02/2017 | 11:30 | 508:82579 | SHORT RURAL | Planned |  | 1 | 90 | 0.00040196 | 0.00044662 | N
28/02/2017 | 08:00 | 512:48046 | SHORT RURAL | Planned |  | 11 | 685 | 0.033653 | 0.0049128 | N
28/02/2017 | 08:00 | 812:19071 | SHORT RURAL | Planned |  | 31 | 505 | 0.069918 | 0.013845 | N
28/02/2017 | 10:50 | 811:74234 | SHORT RURAL | Planned |  | 3 | 165 | 0.0022108 | 0.0013399 | N
01/03/2017 | 09:15 | 814:82285 | SHORT RURAL | Planned |  | 1 | 120 | 0.00053594 | 0.00044662 | N
01/03/2017 | 08:30 | 504:48033 | SHORT RURAL | Planned |  | 1 | 93 | 0.00041536 | 0.00044662 | N
01/03/2017 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 5 | 465 | 0.010384 | 0.0022331 | N
01/03/2017 | 08:00 | 264:81244 | SHORT RURAL | Planned |  | 22 | 480 | 0.047163 | 0.0098256 | N
01/03/2017 | 08:38 | 507:80932 | SHORT RURAL | Planned |  | 48 | 327 | 0.070101 | 0.021438 | N
01/03/2017 | 11:30 | 504:48033 | SHORT RURAL | Planned |  | 1 | 125 | 0.00055827 | 0.00044662 | N
01/03/2017 | 08:30 | 807:74180 | SHORT RURAL | Planned |  | 1 | 60 | 0.00026797 | 0.00044662 | N
01/03/2017 | 08:50 | 812:19072 | SHORT RURAL | Planned |  | 3 | 85 | 0.0011389 | 0.0013399 | N
01/03/2017 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 6 | 240 | 0.0064313 | 0.0026797 | N
01/03/2017 | 10:40 | 812:19072 | SHORT RURAL | Planned |  | 1 | 70 | 0.00031263 | 0.00044662 | N
02/03/2017 | 09:55 | 813:89061 | LONG RURAL | Planned |  | 1 | 65 | 0.02314 | 0.0356 | N
02/03/2017 | 08:00 | 214:8665 | URBAN | Planned |  | 541 | 520 | 0.19377 | 0.037264 | N
02/03/2017 | 08:45 | 239:82131 | SHORT RURAL | Planned |  | 26 | 465 | 0.053998 | 0.011612 | N
03/03/2017 | 09:10 | 814:82283 | SHORT RURAL | Planned |  | 8 | 290 | 0.010362 | 0.0035732 | N
05/03/2017 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 138 | 390 | 0.24072 | 0.061723 | N
05/03/2017 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 321 | 390 | 44.5675 | 11.4276 | N
05/03/2017 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 197 | 390 | 0.34363 | 0.088111 | N
05/03/2017 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 566 | 390 | 0.98729 | 0.25315 | N
05/03/2017 | 20:05 | 202:34231 37 42 | URBAN | Planned |  | 20 | 395 | 0.0054413 | 0.0013775 | N
03/03/2017 | 08:35 | 202:34259 | URBAN | Planned |  | 134 | 60 | 0.0055366 | 0.0092276 | N
05/03/2017 | 08:25 | 202:34231 37 42 | URBAN | Planned |  | 36 | 415 | 0.01029 | 0.0024796 | N
02/03/2017 | 09:12 | 507:80923 | SHORT RURAL | Planned |  | 89 | 313 | 0.12442 | 0.03975 | N
03/03/2017 | 08:30 | 508:82579 | SHORT RURAL | Planned |  | 8 | 405 | 0.014471 | 0.0035732 | N
03/03/2017 | 09:00 | 502:48010 | SHORT RURAL | Planned |  | 5 | 326 | 0.0072804 | 0.0022332 | N
03/03/2017 | 12:45 | 228:7490 | SHORT RURAL | Planned |  | 1 | 65 | 0.00029032 | 0.00044665 | N
02/03/2017 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 22 | 350 | 2.7412 | 0.7832 | N
02/03/2017 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 51 | 425 | 0.096807 | 0.022778 | N
02/03/2017 | 08:45 | 512:48049 | SHORT RURAL | Planned |  | 3 | 80 | 0.0010719 | 0.0013399 | N
02/03/2017 | 10:35 | 806:82662 | SHORT RURAL | Planned |  | 1 | 135 | 0.00060295 | 0.00044663 | N
02/03/2017 | 10:00 | 806:82662 | SHORT RURAL | Planned |  | 1 | 200 | 0.00089326 | 0.00044663 | N
03/03/2017 | 09:10 | 515:35197 | LONG RURAL | Planned |  | 6 | 180 | 0.38448 | 0.2136 | N
03/03/2017 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 45 | 270 | 4.3254 | 1.602 | N
05/03/2017 | 15:05 | 810:74050 | SHORT RURAL | Planned |  | 12 | 25 | 0.0013418 | 0.0053672 | N
06/03/2017 | 08:34 | 221:11898 | URBAN | Planned |  | 162 | 636 | 0.070965 | 0.011158 | N
06/03/2017 | 08:45 | 508:82574 | SHORT RURAL | Planned |  | 2 | 90 | 0.00080508 | 0.00089453 | N
07/03/2017 | 09:00 | 807:74180 | SHORT RURAL | Planned |  | 7 | 225 | 0.007027 | 0.0031231 | N
07/03/2017 | 08:15 | 261:81865 | URBAN | Planned |  | 6 | 400 | 0.0016531 | 0.00041327 | N
07/03/2017 | 08:40 | 243:80083 | SHORT RURAL | Planned |  | 7 | 600 | 0.018739 | 0.0031231 | N
07/03/2017 | 08:30 | 508:82579 | SHORT RURAL | Planned |  | 3 | 44 | 0.00058893 | 0.0013385 | N
07/03/2017 | 08:45 | 507:80914 | SHORT RURAL | Planned |  | 1 | 235 | 0.0010485 | 0.00044616 | N
07/03/2017 | 08:30 | 238:34150 | SHORT RURAL | Planned |  | 1 | 600 | 0.0026769 | 0.00044616 | N
07/03/2017 | 10:30 | 508:82579 | SHORT RURAL | Planned |  | 1 | 35 | 0.00015616 | 0.00044616 | N
07/03/2017 | 13:00 | 238:34141 | SHORT RURAL | Planned |  | 1 | 55 | 0.00024539 | 0.00044616 | N
07/03/2017 | 08:30 | 528:83019 | SHORT RURAL | Planned |  | 211 | 480 | 0.45187 | 0.094139 | N
07/03/2017 | 08:30 | 513:48050 | SHORT RURAL | Planned |  | 7 | 225 | 0.007027 | 0.0031231 | N
07/03/2017 | 08:30 | 812:19072 | SHORT RURAL | Planned |  | 6 | 280 | 0.0074954 | 0.0026769 | N
07/03/2017 | 08:30 | 523:33508 | SHORT RURAL | Planned |  | 28 | 250 | 0.031231 | 0.012492 | N
08/03/2017 | 08:30 | 230:81440 | SHORT RURAL | Planned |  | 95 | 270 | 0.11444 | 0.042386 | N
08/03/2017 | 09:10 | 806:82662 | SHORT RURAL | Planned |  | 34 | 245 | 0.037166 | 0.01517 | N
08/03/2017 | 08:55 | 512:48049 | SHORT RURAL | Planned |  | 6 | 215 | 0.0057556 | 0.002677 | N
08/03/2017 | 11:15 | 812:19072 | SHORT RURAL | Planned |  | 8 | 155 | 0.0055325 | 0.0035693 | N
08/03/2017 | 08:20 | 243:80084 | SHORT RURAL | Planned |  | 95 | 410 | 0.17378 | 0.042386 | N
08/03/2017 | 08:30 | 508:82578 | SHORT RURAL | Planned |  | 1 | 115 | 0.00051309 | 0.00044617 | N
08/03/2017 | 08:55 | 507:80914 | SHORT RURAL | Planned |  | 100 | 320 | 0.14277 | 0.044617 | N
08/03/2017 | 10:30 | 508:82578 | SHORT RURAL | Planned |  | 9 | 75 | 0.0030116 | 0.0040155 | N
08/03/2017 | 12:10 | 508:82578 | SHORT RURAL | Planned |  | 9 | 80 | 0.0032124 | 0.0040155 | N
08/03/2017 | 11:50 | 511:29878 | SHORT RURAL | Planned |  | 4 | 115 | 0.0020524 | 0.0017847 | N
08/03/2017 | 13:00 | 508:82578 | SHORT RURAL | Planned |  | 1 | 100 | 0.00044617 | 0.00044617 | N
08/03/2017 | 08:30 | 807:74179 | SHORT RURAL | Planned |  | 3 | 180 | 0.0024093 | 0.0013385 | N
08/03/2017 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 4 | 285 | 0.0050863 | 0.0017847 | N
08/03/2017 | 09:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 150 | 0.053419 | 0.035613 | N
13/02/2017 | 08:50 | ZN12600:PA13 | SHORT RURAL | Planned |  | 1 | 440 | 0.0019689 | 0.00044747 | N
13/02/2017 | 08:00 | ZN35500:PA28 | URBAN | Planned |  | 78 | 135 | 0.0072534 | 0.0053729 | N
13/02/2017 | 09:00 | ZN12570:PA39 | URBAN | Planned |  | 23 | 360 | 0.0057035 | 0.0015843 | N
13/02/2017 | 17:00 | ZN35900:PA12 | URBAN | Planned |  | 1 | 270 | 0.00018598 | 6.8883e-05 | N
14/02/2017 | 05:00 | ZN2602:PA42 | URBAN | Planned |  | 108 | 240 | 0.017875 | 0.0074477 | N
14/02/2017 | 07:00 | ZN9118:PA6 | URBAN | Planned |  | 17 | 550 | 0.0064478 | 0.0011723 | N
14/02/2017 | 08:00 | ZN12630:PA13 | SHORT RURAL | Planned |  | 6 | 480 | 0.012854 | 0.0026778 | N
14/02/2017 | 08:00 | ZN12570:PA33 | SHORT RURAL | Planned |  | 11 | 410 | 0.020128 | 0.0049094 | N
14/02/2017 | 09:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 11 | 360 | 0.017674 | 0.0049094 | N
14/02/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052962 | 0.0022067 | N
14/02/2017 | 20:00 | ZN2635:PA58 | URBAN | Planned |  | 37 | 480 | 0.012247 | 0.0025515 | N
15/02/2017 | 07:00 | ZN188:PA38 | URBAN | Planned |  | 223 | 390 | 0.059927 | 0.015366 | N
15/02/2017 | 07:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 64 | 690 | 0.19709 | 0.028564 | N
15/02/2017 | 08:50 | ZN12630:PA8 | SHORT RURAL | Planned |  | 19 | 245 | 0.020775 | 0.0084798 | N
15/02/2017 | 08:00 | ZN10999:PA32 | URBAN | Planned |  | 35 | 420 | 0.010129 | 0.0024117 | N
15/02/2017 | 08:00 | ZN12620:PA11 | SHORT RURAL | Planned |  | 3 | 375 | 0.0050209 | 0.0013389 | N
15/02/2017 | 09:30 | ZN14144:PA5 | SHORT RURAL | Planned |  | 19 | 395 | 0.033495 | 0.0084798 | N
15/02/2017 | 09:30 | ZN129:PA28 | URBAN | Planned |  | 144 | 480 | 0.047627 | 0.0099224 | N
15/02/2017 | 09:30 | ZN15013:PA10 | SHORT RURAL | Planned |  | 7 | 360 | 0.011247 | 0.0031241 | N
15/02/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 33 | 240 | 0.0054573 | 0.0022739 | N
15/02/2017 | 20:30 | ZN965:PA3 | URBAN | Planned |  | 19 | 450 | 0.0058914 | 0.0013092 | N
16/02/2017 | 07:00 | ZN690:PA3 | URBAN | Planned |  | 3 | 720 | 0.001488 | 0.00020667 | N
16/02/2017 | 08:53 | ZN12570:PA24 | SHORT RURAL | Planned |  | 12 | 452 | 0.024223 | 0.0053592 | N
17/02/2017 | 07:30 | ZN9118:PA13 | URBAN | Planned |  | 11 | 510 | 0.0038647 | 0.00075779 | Y
17/02/2017 | 11:10 | ZN2400:PA18 | SHORT RURAL | Planned |  | 4 | 350 | 0.0062524 | 0.0017864 | Y
17/02/2017 | 08:10 | ZN129:PA28 | URBAN | Planned |  | 144 | 596 | 0.059124 | 0.0099202 | Y
17/02/2017 | 10:00 | ZN13000:PA11 | SHORT RURAL | Planned |  | 1 | 240 | 0.0010718 | 0.0004466 | Y
17/02/2017 | 09:45 | ZN36200:PA8 | SHORT RURAL | Planned |  | 37 | 255 | 0.042137 | 0.016524 | Y
18/02/2017 | 07:00 | ZN188:PA22 | URBAN | Planned |  | 2 | 30 | 4.1334e-05 | 0.00013778 | N
18/02/2017 | 08:00 | ZN342:PA28 | URBAN | Planned |  | 1 | 30 | 2.0667e-05 | 6.889e-05 | N
18/02/2017 | 08:30 | ZN1290:PA8 | URBAN | Planned |  | 2 | 255 | 0.00035134 | 0.00013778 | N
18/02/2017 | 19:30 | ZN4990:PA53 54ABC | CBD | Planned |  | 136 | 299 | 1.3098 | 0.43806 | N
18/02/2017 | 20:55 | ZN1673:PA21 | SHORT RURAL | Planned |  | 64 | 545 | 0.15578 | 0.028583 | N
19/02/2017 | 00:00 | ZN4990:PA53 54ABC | CBD | Planned |  | 20 | 350 | 0.22547 | 0.064421 | N
19/02/2017 | 08:00 | ZN5868:PA5 | SHORT RURAL | Planned |  | 1 | 475 | 0.0021214 | 0.00044661 | N
19/02/2017 | 20:00 | ZN2466:PA41 | URBAN | Planned |  | 39 | 420 | 0.011284 | 0.0026867 | N
20/02/2017 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 10 | 320 | 0.014291 | 0.0044661 | N
20/02/2017 | 09:00 | ZN36800:PA49 | URBAN | Planned |  | 199 | 240 | 0.032902 | 0.013709 | N
21/02/2017 | 08:54 | ZN12600:PA3 | URBAN | Planned |  | 85 | 126 | 0.0073783 | 0.0058558 | N
21/02/2017 | 08:40 | ZN14891:PA12 | SHORT RURAL | Planned |  | 8 | 440 | 0.015721 | 0.003573 | N
21/02/2017 | 08:00 | ZN10999:PA12 | URBAN | Planned |  | 67 | 450 | 0.020771 | 0.0046157 | N
21/02/2017 | 11:10 | ZN12580:PA12 | SHORT RURAL | Planned |  | 13 | 290 | 0.016838 | 0.0058062 | N
21/02/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 33 | 240 | 0.0054562 | 0.0022734 | N
22/02/2017 | 08:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 5 | 230 | 0.0051363 | 0.0022332 | N
23/02/2017 | 07:30 | ZN14891:PA12 | SHORT RURAL | Planned |  | 56 | 470 | 0.11752 | 0.025004 | N
23/02/2017 | 08:00 | ZN10994:PA10 | URBAN | Planned |  | 50 | 540 | 0.018598 | 0.0034442 | N
23/02/2017 | 08:30 | ZN12690:PA19 | URBAN | Planned |  | 4 | 360 | 0.00099192 | 0.00027553 | N
24/02/2017 | 06:50 | ZN35800:PA14 | URBAN | Planned |  | 4 | 670 | 0.001846 | 0.00027553 | N
24/02/2017 | 07:00 | ZN35500:PA15 | URBAN | Planned |  | 59 | 480 | 0.019507 | 0.004064 | N
24/02/2017 | 07:30 | ZN4545:PA4 | URBAN | Planned |  | 5 | 300 | 0.0010332 | 0.00034441 | N
24/02/2017 | 09:00 | ZN1285:PA24 | URBAN | Planned |  | 74 | 330 | 0.016821 | 0.0050972 | N
24/02/2017 | 08:30 | ZN12610:PA9 | URBAN | Planned |  | 125 | 445 | 0.038315 | 0.0086102 | N
24/02/2017 | 18:30 | ZN7900:PA23 | URBAN | Planned |  | 3 | 2,820 | 0.0058274 | 0.00020664 | N
24/02/2017 | 20:00 | ZN35400:PA59 | URBAN | Planned |  | 95 | 2,970 | 0.19435 | 0.0065437 | N
25/02/2017 | 09:05 | ZN931:PA9 | URBAN | Planned |  | 1 | 145 | 9.9874e-05 | 6.8879e-05 | N
25/02/2017 | 06:40 | ZN630:PA34 | URBAN | Planned |  | 1 | 590 | 0.00040639 | 6.8879e-05 | N
27/02/2017 | 07:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 31 | 460 | 0.063687 | 0.013845 | N
27/02/2017 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 49 | 465 | 0.10176 | 0.021884 | N
27/02/2017 | 10:25 | ZN14891:PA12 | SHORT RURAL | Planned |  | 7 | 263 | 0.0082222 | 0.0031263 | N
27/02/2017 | 20:42 | ZN8100:PA17 | URBAN | Planned |  | 92 | 108 | 0.0068438 | 0.0063368 | N
28/02/2017 | 07:30 | ZN4545:PA26 | URBAN | Planned |  | 9 | 270 | 0.0016738 | 0.00061991 | N
28/02/2017 | 09:30 | ZN72:PA16 | URBAN | Planned |  | 38 | 390 | 0.010208 | 0.0026174 | N
28/02/2017 | 09:30 | ZN72:PA31 | URBAN | Planned |  | 56 | 330 | 0.012729 | 0.0038572 | N
28/02/2017 | 08:00 | ZN12600:PA9 | SHORT RURAL | Planned |  | 23 | 440 | 0.045198 | 0.010272 | N
28/02/2017 | 08:00 | ZN14891:PA20 | SHORT RURAL | Planned |  | 12 | 200 | 0.010719 | 0.0053594 | N
28/02/2017 | 10:20 | ZN10997:PA12 | URBAN | Planned |  | 102 | 280 | 0.019672 | 0.0070257 | N
09/03/2017 | 09:05 | 813:89055 | SHORT RURAL | Planned |  | 24 | 330 | 0.035216 | 0.010671 | N
09/03/2017 | 07:30 | 220:8691 | URBAN | Planned |  | 1 | 390 | 0.00026867 | 6.8889e-05 | N
09/03/2017 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 5 | 375 | 0.0083371 | 0.0022232 | N
09/03/2017 | 09:17 | 532:83307 | SHORT RURAL | Planned |  | 99 | 323 | 0.14218 | 0.04402 | N
09/03/2017 | 08:30 | 238:34150 | SHORT RURAL | Planned |  | 1 | 386 | 0.0017163 | 0.00044464 | N
09/03/2017 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 2 | 105 | 0.00093375 | 0.00088929 | N
09/03/2017 | 09:58 | 509:33395 | LONG RURAL | Planned |  | 1 | 55 | 0.019587 | 0.035613 | N
10/03/2017 | 08:35 | 502:48010 | SHORT RURAL | Planned |  | 9 | 415 | 0.016607 | 0.0040018 | N
10/03/2017 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 4 | 220 | 0.31339 | 0.14245 | N
10/03/2017 | 07:20 | 243:80080 | SHORT RURAL | Planned |  | 1 | 355 | 0.0015785 | 0.00044464 | N
11/03/2017 | 07:46 | 239:82131 | SHORT RURAL | Planned |  | 1 | 274 | 0.0012183 | 0.00044464 | N
12/03/2017 | 08:00 | 202:34231 37 42 | URBAN | Planned |  | 36 | 430 | 0.010664 | 0.0024801 | N
10/03/2017 | 09:50 | 509:33395 | LONG RURAL | Planned |  | 1 | 70 | 0.024929 | 0.035613 | N
10/03/2017 | 11:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 105 | 0.074786 | 0.071225 | N
10/03/2017 | 21:25 | 528:83013 | URBAN | Planned |  | 10 | 65 | 0.00044779 | 0.00068891 | N
10/03/2017 | 08:35 | 528:83024 | URBAN | Planned |  | 69 | 175 | 0.0083186 | 0.0047535 | N
10/03/2017 | 09:05 | 507:80925 | SHORT RURAL | Planned |  | 2 | 65 | 0.00057804 | 0.00088929 | N
10/03/2017 | 09:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 80 | 0.02849 | 0.035613 | N
10/03/2017 | 08:30 | 814:82285 | SHORT RURAL | Planned |  | 1 | 30 | 0.00013339 | 0.00044464 | N
10/03/2017 | 09:50 | 801:74123 | SHORT RURAL | Planned |  | 1 | 25 | 0.00011116 | 0.00044464 | N
10/03/2017 | 08:45 | 514:18137 | SHORT RURAL | Planned |  | 1 | 115 | 0.00051134 | 0.00044464 | N
10/03/2017 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 44 | 310 | 0.060649 | 0.019564 | N
14/03/2017 | 08:11 | 509:33395 | LONG RURAL | Planned |  | 784 | 529 | 147.698 | 27.9202 | N
13/03/2017 | 08:05 | 227:13015 | SHORT RURAL | Planned |  | 17 | 435 | 0.032881 | 0.0075589 | N
13/03/2017 | 09:00 | 507:80922 | SHORT RURAL | Planned |  | 1 | 190 | 0.00084482 | 0.00044464 | N
13/03/2017 | 09:35 | 509:33395 | LONG RURAL | Planned |  | 1 | 115 | 0.040954 | 0.035613 | N
13/03/2017 | 13:25 | 507:80922 | SHORT RURAL | Planned |  | 5 | 65 | 0.0014451 | 0.0022232 | N
13/03/2017 | 09:10 | 801:74121 | LONG RURAL | Planned |  | 1 | 125 | 0.044516 | 0.035613 | N
14/03/2017 | 07:45 | 222:33601 | SHORT RURAL | Planned |  | 140 | 480 | 0.2988 | 0.06225 | N
14/03/2017 | 08:55 | 532:83307 | SHORT RURAL | Planned |  | 99 | 290 | 0.12766 | 0.04402 | N
14/03/2017 | 08:35 | 813:89062 | SHORT RURAL | Planned |  | 5 | 535 | 0.011894 | 0.0022232 | N
14/03/2017 | 08:55 | 813:89055 | SHORT RURAL | Planned |  | 19 | 280 | 0.023655 | 0.0084482 | N
14/03/2017 | 08:50 | 515:35192 | SHORT RURAL | Planned |  | 3 | 415 | 0.0055358 | 0.0013339 | N
16/03/2017 | 08:18 | 511:29878 | SHORT RURAL | Planned |  | 129 | 579 | 0.33201 | 0.057342 | N
15/03/2017 | 07:30 | 203:8089 | URBAN | Planned |  | 3 | 385 | 0.00079571 | 0.00020668 | N
15/03/2017 | 08:55 | 508:82580 | SHORT RURAL | Planned |  | 3 | 140 | 0.0018675 | 0.0013339 | N
15/03/2017 | 09:29 | 509:33395 | LONG RURAL | Planned |  | 1 | 80 | 0.02849 | 0.035613 | N
15/03/2017 | 09:30 | 230:81432 | SHORT RURAL | Planned |  | 5 | 155 | 0.003446 | 0.0022232 | N
15/03/2017 | 08:30 | 507:80925 | SHORT RURAL | Planned |  | 19 | 245 | 0.020698 | 0.0084483 | N
15/03/2017 | 09:10 | 532:83307 | SHORT RURAL | Planned |  | 99 | 257 | 0.11313 | 0.04402 | N
15/03/2017 | 09:00 | 532:83307 | SHORT RURAL | Planned |  | 1 | 325 | 0.0014451 | 0.00044465 | N
15/03/2017 | 10:15 | 509:33395 | LONG RURAL | Planned |  | 2 | 60 | 0.042735 | 0.071225 | N
15/03/2017 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 1 | 130 | 0.00057804 | 0.00044465 | N
15/03/2017 | 08:40 | 806:82662 | SHORT RURAL | Planned |  | 6 | 155 | 0.0041352 | 0.0026679 | N
15/03/2017 | 09:35 | 806:82662 | SHORT RURAL | Planned |  | 1 | 165 | 0.00073367 | 0.00044465 | N
15/03/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 9 | 270 | 0.86538 | 0.32051 | N
15/03/2017 | 08:50 | 515:35193 | SHORT RURAL | Planned |  | 24 | 270 | 0.028813 | 0.010672 | N
16/03/2017 | 09:20 | 532:83307 | SHORT RURAL | Planned |  | 99 | 215 | 0.094614 | 0.044007 | N
16/03/2017 | 09:05 | 507:80925 | SHORT RURAL | Planned |  | 30 | 345 | 0.046007 | 0.013335 | N
17/03/2017 | 08:35 | 511:29878 | SHORT RURAL | Planned |  | 96 | 310 | 0.13227 | 0.042667 | N
17/03/2017 | 11:10 | 509:33397 | SHORT RURAL | Planned |  | 1 | 50 | 0.00022222 | 0.00044445 | N
17/03/2017 | 09:45 | 509:33395 | LONG RURAL | Planned |  | 1 | 55 | 0.019594 | 0.035625 | N
17/03/2017 | 11:00 | 509:33395 | LONG RURAL | Planned |  | 2 | 40 | 0.0285 | 0.07125 | N
16/03/2017 | 09:15 | 813:89061 | LONG RURAL | Planned |  | 1 | 260 | 0.092626 | 0.035625 | N
17/03/2017 | 08:30 | 512:48046 | SHORT RURAL | Planned |  | 70 | 50 | 0.015556 | 0.031111 | N
17/03/2017 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 1 | 75 | 0.00033334 | 0.00044445 | N
17/03/2017 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 37 | 160 | 0.026311 | 0.016445 | N
17/03/2017 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 2 | 100 | 0.0008889 | 0.0008889 | N
17/03/2017 | 09:50 | 802:82220 | SHORT RURAL | Planned |  | 2 | 330 | 0.0029334 | 0.0008889 | N
21/03/2017 | 09:00 | ZN9252:PA30 | URBAN | Planned |  | 410 | 450 | 0.12708 | 0.02824 | N
20/03/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 3 | 115 | 0.0015334 | 0.0013334 | N
20/03/2017 | 08:00 | 221:11899 | SHORT RURAL | Planned |  | 1 | 325 | 0.0014445 | 0.00044445 | N
20/03/2017 | 08:30 | 256:80632 | URBAN | Planned |  | 36 | 394 | 0.0097697 | 0.0024796 | N
20/03/2017 | 08:55 | 264:81244 | SHORT RURAL | Planned |  | 37 | 425 | 0.06989 | 0.016445 | N
20/03/2017 | 08:05 | 232:11457 | SHORT RURAL | Planned |  | 51 | 580 | 0.13147 | 0.022667 | N
21/03/2017 | 08:15 | 227:13020 | SHORT RURAL | Planned |  | 58 | 435 | 0.11214 | 0.025778 | N
21/03/2017 | 08:50 | 225:33679 | URBAN | Planned |  | 106 | 408 | 0.029789 | 0.0073012 | N
21/03/2017 | 21:10 | 205:12213 | SHORT RURAL | Planned |  | 23 | 130 | 0.013289 | 0.010222 | N
21/03/2017 | 08:38 | 232:33413 | URBAN | Planned |  | 2 | 187 | 0.00025761 | 0.00013776 | N
21/03/2017 | 09:28 | 509:33395 | LONG RURAL | Planned |  | 2 | 71 | 0.05066 | 0.071352 | N
21/03/2017 | 11:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 150 | 0.053514 | 0.035676 | N
21/03/2017 | 09:14 | 532:83307 | SHORT RURAL | Planned |  | 177 | 288 | 0.22657 | 0.078669 | N
21/03/2017 | 08:42 | 509:33395 | LONG RURAL | Planned |  | 20 | 243 | 1.7339 | 0.71352 | N
21/03/2017 | 09:30 | 264:81240 | SHORT RURAL | Planned |  | 2 | 260 | 0.0023112 | 0.00088891 | N
21/03/2017 | 09:40 | 520:48172 | SHORT RURAL | Planned |  | 1 | 65 | 0.0002889 | 0.00044446 | N
21/03/2017 | 09:30 | 806:82662 | SHORT RURAL | Planned |  | 1 | 270 | 0.0012 | 0.00044446 | N
21/03/2017 | 08:40 | 810:74050 | SHORT RURAL | Planned |  | 11 | 270 | 0.0132 | 0.004889 | N
21/03/2017 | 08:45 | 807:74180 | SHORT RURAL | Planned |  | 1 | 400 | 0.0017778 | 0.00044446 | N
21/03/2017 | 12:56 | 515:35193 | SHORT RURAL | Planned |  | 2 | 69 | 0.00061335 | 0.00088891 | N
26/03/2017 | 08:32 | 227:13015 | SHORT RURAL | Planned |  | 46 | 293 | 0.05982 | 0.020416 | N
22/03/2017 | 08:30 | 256:80641 | URBAN | Planned |  | 79 | 380 | 0.020678 | 0.0054416 | N
22/03/2017 | 08:45 | 239:82131 | SHORT RURAL | Planned |  | 1 | 390 | 0.0017334 | 0.00044447 | N
22/03/2017 | 21:10 | 205:12213 | SHORT RURAL | Planned |  | 7 | 123 | 0.0038269 | 0.0031113 | N
23/03/2017 | 08:00 | 225:33670 | URBAN | Planned |  | 93 | 325 | 0.020812 | 0.0064038 | N
23/03/2017 | 08:35 | 243:80074 | SHORT RURAL | Planned |  | 81 | 535 | 0.19267 | 0.036013 | N
24/03/2017 | 09:00 | 203:8086 | URBAN | Planned |  | 126 | 530 | 0.045984 | 0.0086762 | N
22/03/2017 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 1 | 105 | 0.037473 | 0.035689 | N
22/03/2017 | 08:55 | 238:34141 | SHORT RURAL | Planned |  | 29 | 485 | 0.062515 | 0.01289 | N
22/03/2017 | 08:50 | 232:33413 | URBAN | Planned |  | 95 | 370 | 0.024212 | 0.0065437 | N
22/03/2017 | 11:40 | 509:33395 | LONG RURAL | Planned |  | 1 | 80 | 0.028551 | 0.035689 | N
22/03/2017 | 10:10 | 511:29878 | SHORT RURAL | Planned |  | 3 | 235 | 0.0031335 | 0.0013334 | N
22/03/2017 | 11:35 | 509:33395 | LONG RURAL | Planned |  | 1 | 60 | 0.021413 | 0.035689 | N
23/03/2017 | 08:20 | 504:48026 | SHORT RURAL | Planned |  | 2 | 95 | 0.00084475 | 0.00088921 | N
23/03/2017 | 08:30 | 507:80932 | SHORT RURAL | Planned |  | 2 | 390 | 0.0034679 | 0.00088921 | N
23/03/2017 | 09:10 | 507:80914 | SHORT RURAL | Planned |  | 100 | 285 | 0.12671 | 0.04446 | N
23/03/2017 | 09:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 60 | 0.042827 | 0.071378 | N
23/03/2017 | 12:40 | 512:48048 | SHORT RURAL | Planned |  | 4 | 50 | 0.00088921 | 0.0017784 | N
23/03/2017 | 11:40 | 509:33395 | LONG RURAL | Planned |  | 2 | 38 | 0.027123 | 0.071378 | N
23/03/2017 | 11:30 | 509:33395 | LONG RURAL | Planned |  | 4 | 55 | 0.078515 | 0.14276 | N
23/03/2017 | 10:45 | 504:48026 | SHORT RURAL | Planned |  | 1 | 75 | 0.00033345 | 0.0004446 | N
23/03/2017 | 12:30 | 504:48026 | SHORT RURAL | Planned |  | 1 | 75 | 0.00033345 | 0.0004446 | N
26/03/2017 | 09:00 | 502:48002 | URBAN | Planned |  | 139 | 300 | 0.028714 | 0.0095712 | N
22/03/2017 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 4 | 145 | 0.207 | 0.14276 | N
22/03/2017 | 10:30 | 813:89063 | SHORT RURAL | Planned |  | 76 | 180 | 0.060804 | 0.03378 | N
22/03/2017 | 13:15 | 515:35197 | LONG RURAL | Planned |  | 3 | 20 | 0.021413 | 0.10707 | N
23/03/2017 | 08:41 | 513:48059 | SHORT RURAL | Planned |  | 1 | 147 | 0.00065357 | 0.0004446 | N
23/03/2017 | 09:30 | 813:89063 | SHORT RURAL | Planned |  | 61 | 285 | 0.077294 | 0.027121 | N
23/03/2017 | 09:20 | 806:82662 | SHORT RURAL | Planned |  | 5 | 315 | 0.0070025 | 0.002223 | N
24/03/2017 | 08:30 | 523:33509 | URBAN | Planned |  | 38 | 165 | 0.0043174 | 0.0026166 | N
24/03/2017 | 08:30 | 523:33508 | SHORT RURAL | Planned |  | 13 | 115 | 0.0066469 | 0.0057799 | N
25/03/2017 | 08:20 | 811:74234 | SHORT RURAL | Planned |  | 1 | 185 | 0.00082255 | 0.00044462 | N
27/03/2017 | 08:30 | 216:10722 | URBAN | Planned |  | 62 | 510 | 0.021773 | 0.0042692 | N
27/03/2017 | 21:40 | 202:34249 | URBAN | Planned |  | 47 | 100 | 0.0032363 | 0.0032363 | N
27/03/2017 | 11:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 45 | 0.03212 | 0.071378 | N
27/03/2017 | 09:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 45 | 0.03212 | 0.071378 | N
27/03/2017 | 09:30 | 532:83309 | SHORT RURAL | Planned |  | 2 | 280 | 0.0024855 | 0.00088767 | N
27/03/2017 | 08:35 | 515:35193 | SHORT RURAL | Planned |  | 7 | 220 | 0.0068351 | 0.0031069 | N
28/03/2017 | 11:00 | 509:33395 | LONG RURAL | Planned |  | 1 | 30 | 0.01071 | 0.035702 | N
28/03/2017 | 08:15 | 225:33670 | URBAN | Planned |  | 154 | 425 | 0.045068 | 0.010604 | N
28/03/2017 | 12:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 30 | 0.01071 | 0.035702 | N
28/03/2017 | 09:15 | 813:89061 | LONG RURAL | Planned |  | 6 | 230 | 0.49268 | 0.21421 | N
28/03/2017 | 08:30 | 516:48067 | SHORT RURAL | Planned |  | 5 | 370 | 0.008211 | 0.0022192 | N
29/03/2017 | 09:00 | 528:83019 | SHORT RURAL | Planned |  | 26 | 245 | 0.028273 | 0.01154 | N
29/03/2017 | 07:55 | 202:34239 | SHORT RURAL | Planned |  | 18 | 515 | 0.041144 | 0.0079892 | N
29/03/2017 | 08:00 | 261:81865 | URBAN | Planned |  | 108 | 400 | 0.029747 | 0.0074368 | N
29/03/2017 | 08:20 | 508:82578 | SHORT RURAL | Planned |  | 4 | 70 | 0.0012428 | 0.0017754 | N
29/03/2017 | 08:30 | 504:48031 | SHORT RURAL | Planned |  | 8 | 390 | 0.013848 | 0.0035508 | N
29/03/2017 | 10:15 | 508:82574 | SHORT RURAL | Planned |  | 6 | 65 | 0.001731 | 0.0026631 | N
29/03/2017 | 08:50 | 532:83307 | SHORT RURAL | Planned |  | 102 | 430 | 0.19467 | 0.045272 | N
29/03/2017 | 13:05 | 508:82580 | SHORT RURAL | Planned |  | 1 | 40 | 0.00017754 | 0.00044384 | N
29/03/2017 | 10:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 31 | 0.011067 | 0.035702 | N
29/03/2017 | 11:35 | 509:33395 | LONG RURAL | Planned |  | 3 | 55 | 0.058908 | 0.1071 | N
29/03/2017 | 08:45 | 811:74234 | SHORT RURAL | Planned |  | 2 | 215 | 0.0019085 | 0.00088769 | N
30/03/2017 | 10:00 | 509:33395 | LONG RURAL | Planned |  | 18 | 150 | 0.96394 | 0.64263 | N
31/03/2017 | 09:05 | 238:34148 | SHORT RURAL | Planned |  | 9 | 105 | 0.0041917 | 0.0039921 | N
01/04/2017 | 12:30 | 203:8083 | URBAN | Planned |  | 1 | 12 | 8.2558e-06 | 6.8798e-05 | N
31/03/2017 | 08:15 | 224:80332 | URBAN | Planned |  | 59 | 420 | 0.017058 | 0.0040615 | N
30/03/2017 | 10:30 | 504:48033 | SHORT RURAL | Planned |  | 1 | 80 | 0.00035485 | 0.00044356 | N
30/03/2017 | 08:50 | 509:33395 | LONG RURAL | Planned |  | 12 | 225 | 0.96394 | 0.42842 | N
30/03/2017 | 09:00 | 264:81240 | SHORT RURAL | Planned |  | 14 | 315 | 0.019561 | 0.0062099 | N
31/03/2017 | 08:40 | 509:33399 | SHORT RURAL | Planned |  | 16 | 140 | 0.0099358 | 0.007097 | N
31/03/2017 | 09:03 | 508:82579 | SHORT RURAL | Planned |  | 2 | 337 | 0.0029896 | 0.00088712 | N
31/03/2017 | 08:35 | 235:2120 | SHORT RURAL | Planned |  | 1 | 145 | 0.00064316 | 0.00044356 | N
31/03/2017 | 08:30 | 235:2124 | SHORT RURAL | Planned |  | 2 | 160 | 0.0014194 | 0.00088712 | N
30/03/2017 | 08:45 | 523:33508 | SHORT RURAL | Planned |  | 13 | 151 | 0.0087071 | 0.0057663 | N
30/03/2017 | 08:40 | 813:89055 | SHORT RURAL | Planned |  | 16 | 220 | 0.015613 | 0.007097 | N
30/03/2017 | 08:35 | 515:35197 | LONG RURAL | Planned |  | 15 | 350 | 1.8743 | 0.53552 | N
30/03/2017 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 3 | 160 | 0.0021291 | 0.0013307 | N
30/03/2017 | 09:00 | 802:82225 | SHORT RURAL | Planned |  | 6 | 135 | 0.0035928 | 0.0026614 | N
30/03/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 7 | 245 | 0.61228 | 0.24991 | N
30/03/2017 | 09:30 | 802:82220 | SHORT RURAL | Planned |  | 2 | 165 | 0.0014638 | 0.00088712 | N
31/03/2017 | 08:35 | 523:33508 | SHORT RURAL | Planned |  | 2 | 140 | 0.001242 | 0.00088712 | N
31/03/2017 | 12:55 | 523:33508 | SHORT RURAL | Planned |  | 1 | 80 | 0.00035485 | 0.00044356 | N
03/04/2017 | 09:00 | 243:80083 | SHORT RURAL | Planned |  | 11 | 360 | 0.017634 | 0.0048984 | N
03/04/2017 | 08:30 | 232:33407 | SHORT RURAL | Planned |  | 2 | 90 | 0.00080156 | 0.00089062 | N
03/04/2017 | 08:20 | 232:33413 | URBAN | Planned |  | 3 | 110 | 0.00022706 | 0.00020642 | N
03/04/2017 | 10:30 | 229:34995 | SHORT RURAL | Planned |  | 2 | 85 | 0.00075703 | 0.00089062 | N
03/04/2017 | 11:00 | 232:11457 | SHORT RURAL | Planned |  | 8 | 190 | 0.0067687 | 0.0035625 | N
03/04/2017 | 08:30 | 807:74180 | SHORT RURAL | Planned |  | 4 | 145 | 0.0025828 | 0.0017812 | N
03/04/2017 | 08:00 | 514:18137 | SHORT RURAL | Planned |  | 45 | 540 | 0.10821 | 0.020039 | N
03/04/2017 | 09:50 | 806:82667 | SHORT RURAL | Planned |  | 1 | 100 | 0.00044531 | 0.00044531 | N
04/04/2017 | 08:40 | 221:11895 | URBAN | Planned |  | 78 | 380 | 0.020394 | 0.0053669 | N
04/04/2017 | 08:00 | 507:80932 | SHORT RURAL | Planned |  | 24 | 280 | 0.029925 | 0.010687 | N
04/04/2017 | 10:00 | 242:81539 | URBAN | Planned |  | 258 | 330 | 0.058582 | 0.017752 | N
04/04/2017 | 09:30 | 511:29878 | SHORT RURAL | Planned |  | 37 | 260 | 0.042839 | 0.016477 | N
04/04/2017 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 6 | 420 | 0.9 | 0.21429 | N
04/04/2017 | 08:00 | 514:18137 | SHORT RURAL | Planned |  | 45 | 455 | 0.091177 | 0.020039 | N
05/04/2017 | 09:45 | 509:33395 | LONG RURAL | Planned |  | 20 | 180 | 1.2857 | 0.71429 | N
05/04/2017 | 09:25 | 238:34141 | SHORT RURAL | Planned |  | 2 | 140 | 0.0012469 | 0.00089062 | N
05/04/2017 | 09:50 | 511:29878 | SHORT RURAL | Planned |  | 9 | 312 | 0.012504 | 0.0040078 | N
05/04/2017 | 12:50 | 238:34140 | URBAN | Planned |  | 2 | 90 | 0.00012385 | 0.00013761 | N
05/04/2017 | 09:00 | 513:48056 | SHORT RURAL | Planned |  | 6 | 40 | 0.0010687 | 0.0026719 | N
05/04/2017 | 08:40 | 814:82285 | SHORT RURAL | Planned |  | 14 | 275 | 0.017144 | 0.0062344 | N
05/04/2017 | 08:55 | 806:82667 | SHORT RURAL | Planned |  | 4 | 150 | 0.0026719 | 0.0017812 | N
05/04/2017 | 13:45 | 512:48049 | SHORT RURAL | Planned |  | 2 | 50 | 0.00044531 | 0.00089062 | N
06/04/2017 | 09:15 | 243:80074 | SHORT RURAL | Planned |  | 131 | 395 | 0.23043 | 0.058336 | N
06/04/2017 | 10:05 | 225:33670 | URBAN | Planned |  | 93 | 315 | 0.020157 | 0.006399 | N
06/04/2017 | 10:05 | 225:33679 | URBAN | Planned |  | 36 | 315 | 0.0078027 | 0.002477 | N
06/04/2017 | 08:20 | 223:14395 | SHORT RURAL | Planned |  | 50 | 120 | 0.026719 | 0.022266 | N
06/04/2017 | 08:40 | 508:82578 | SHORT RURAL | Planned |  | 9 | 420 | 0.016833 | 0.0040078 | N
06/04/2017 | 09:00 | 507:80914 | SHORT RURAL | Planned |  | 100 | 327 | 0.14562 | 0.044531 | N
06/04/2017 | 10:35 | 509:33395 | LONG RURAL | Planned |  | 2 | 35 | 0.025 | 0.071429 | N
06/04/2017 | 12:15 | 509:33395 | LONG RURAL | Planned |  | 5 | 55 | 0.098214 | 0.17857 | N
06/04/2017 | 08:40 | 807:74184 | SHORT RURAL | Planned |  | 1 | 120 | 0.00053437 | 0.00044531 | N
06/04/2017 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 3 | 100 | 0.10714 | 0.10714 | N
06/04/2017 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 2 | 220 | 0.0019594 | 0.00089062 | N
06/04/2017 | 09:05 | 512:48049 | SHORT RURAL | Planned |  | 1 | 220 | 0.00097968 | 0.00044531 | N
06/04/2017 | 08:30 | 802:82220 | SHORT RURAL | Planned |  | 1 | 240 | 0.0010687 | 0.00044531 | N
01/03/2017 | 04:00 | ZN847:PA28 | URBAN | Planned |  | 4 | 50 | 0.00013776 | 0.00027552 | N
02/03/2017 | 07:00 | ZN35500:PA15 | URBAN | Planned |  | 59 | 480 | 0.019507 | 0.004064 | N
02/03/2017 | 09:39 | ZN14891:PA5 | SHORT RURAL | Planned |  | 2 | 256 | 0.0022867 | 0.00089326 | N
02/03/2017 | 08:25 | ZN12600:PA2 | SHORT RURAL | Planned |  | 6 | 455 | 0.012193 | 0.0026798 | N
02/03/2017 | 08:30 | ZN965:PA46 | URBAN | Planned |  | 48 | 360 | 0.011903 | 0.0033063 | N
02/03/2017 | 09:30 | ZN12570:PA35 | URBAN | Planned |  | 14 | 356 | 0.003433 | 0.00096433 | N
02/03/2017 | 09:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 180 | 0.0072354 | 0.0040197 | N
02/03/2017 | 09:50 | ZN9245:PA3 | URBAN | Planned |  | 4 | 310 | 0.00085412 | 0.00027552 | N
03/03/2017 | 05:00 | ZN3288:PA45 46DEF | CBD | Planned |  | 1 | 15 | 0.00048303 | 0.0032202 | N
03/03/2017 | 09:00 | ZN14144:PA10 | SHORT RURAL | Planned |  | 4 | 410 | 0.0073251 | 0.0017866 | N
03/03/2017 | 20:00 | ZN35400:PA59 | URBAN | Planned |  | 95 | 2,970 | 0.1943 | 0.006542 | N
03/03/2017 | 20:30 | ZN10997:PA7 | URBAN | Planned |  | 13 | 540 | 0.0048342 | 0.00089522 | N
03/03/2017 | 20:30 | ZN10997:PA7 | URBAN | Planned |  | 62 | 540 | 0.023055 | 0.0042695 | N
04/03/2017 | 03:57 | ZN4990:PA51 52KLM | CBD | Planned |  | 10 | 99 | 0.03188 | 0.032202 | N
04/03/2017 | 08:30 | ZN2466:PA21 | URBAN | Planned |  | 1 | 430 | 0.00029616 | 6.8876e-05 | N
04/03/2017 | 08:00 | ZN384:PA22 | URBAN | Planned |  | 1 | 510 | 0.00035127 | 6.8876e-05 | N
04/03/2017 | 09:30 | ZN2466:PA5 | URBAN | Planned |  | 3 | 210 | 0.00043392 | 0.00020663 | N
04/03/2017 | 11:40 | ZN263:PA33 34ABC | CBD | Planned |  | 4 | 395 | 0.050879 | 0.012881 | N
06/03/2017 | 00:40 | ZN14892:PA19 | URBAN | Planned |  | 1 | 130 | 8.954e-05 | 6.8877e-05 | N
06/03/2017 | 00:50 | ZN4990:PA51 52KLM | CBD | Planned |  | 3 | 120 | 0.011593 | 0.0096606 | N
06/03/2017 | 07:50 | ZN15005:PA10 | URBAN | Planned |  | 15 | 445 | 0.0045975 | 0.0010332 | N
06/03/2017 | 08:00 | ZN12570:PA26 | URBAN | Planned |  | 2 | 395 | 0.00054413 | 0.00013775 | N
06/03/2017 | 08:40 | ZN15006:PA14 | URBAN | Planned |  | 1 | 400 | 0.00027551 | 6.8877e-05 | N
06/03/2017 | 19:00 | ZN14143:PA12 | SHORT RURAL | Planned |  | 2 | 60 | 0.00053672 | 0.00089453 | N
07/03/2017 | 01:15 | ZN4990:PA51 52KLM | CBD | Planned |  | 1 | 80 | 0.0025767 | 0.0032208 | N
07/03/2017 | 07:00 | ZN10999:PA10 | URBAN | Planned |  | 87 | 1,650 | 0.098875 | 0.0059924 | N
07/03/2017 | 08:00 | ZN2466:PA41 | URBAN | Planned |  | 17 | 555 | 0.0064987 | 0.0011709 | N
07/03/2017 | 08:30 | ZN12650:PA1 | SHORT RURAL | Planned |  | 31 | 390 | 0.05394 | 0.013831 | N
07/03/2017 | 09:30 | ZN12600:PA11 | URBAN | Planned |  | 39 | 310 | 0.0083274 | 0.0026863 | N
07/03/2017 | 10:00 | ZN10990:PA5 | URBAN | Planned |  | 55 | 45 | 0.0017047 | 0.0037883 | N
07/03/2017 | 09:00 | ZN12620:PA7 | URBAN | Planned |  | 124 | 255 | 0.021779 | 0.008541 | N
07/03/2017 | 10:50 | ZN1285:PA27 | URBAN | Planned |  | 1 | 260 | 0.00017908 | 6.8879e-05 | N
07/03/2017 | 17:00 | ZN15001:PA18 | URBAN | Planned |  | 27 | 390 | 0.0072529 | 0.0018597 | N
07/03/2017 | 17:00 | ZN15001:PA18 | URBAN | Planned |  | 72 | 390 | 0.019341 | 0.0049593 | N
08/03/2017 | 08:24 | ZN3154:PA10 | URBAN | Planned |  | 50 | 396 | 0.013638 | 0.003444 | N
08/03/2017 | 08:00 | ZN13000:PA10 | SHORT RURAL | Planned |  | 28 | 480 | 0.059965 | 0.012493 | N
08/03/2017 | 10:10 | ZN14892:PA1 | SHORT RURAL | Planned |  | 42 | 105 | 0.019676 | 0.018739 | N
08/03/2017 | 22:00 | ZN9700:PA20 | URBAN | Planned |  | 65 | 450 | 0.020147 | 0.0044772 | N
09/03/2017 | 09:45 | ZN9118:PA3 | SHORT RURAL | Planned |  | 1 | 295 | 0.0013117 | 0.00044464 | N
09/03/2017 | 07:15 | ZN931:PA25 | URBAN | Planned |  | 84 | 680 | 0.03935 | 0.0057867 | N
09/03/2017 | 07:30 | ZN2466:PA41 | URBAN | Planned |  | 111 | 590 | 0.045116 | 0.0076467 | N
09/03/2017 | 10:38 | ZN14143:PA21 | URBAN | Planned |  | 3 | 252 | 0.0005208 | 0.00020667 | N
09/03/2017 | 08:00 | ZN10999:PA4 | URBAN | Planned |  | 41 | 450 | 0.01271 | 0.0028245 | N
09/03/2017 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 31 | 480 | 0.066163 | 0.013784 | N
09/03/2017 | 08:30 | ZN36100:PA27 | URBAN | Planned |  | 132 | 270 | 0.024552 | 0.0090934 | N
09/03/2017 | 09:10 | ZN2196:PA18 | URBAN | Planned |  | 14 | 320 | 0.0030862 | 0.00096445 | N
09/03/2017 | 17:00 | ZN15001:PA18 | URBAN | Planned |  | 27 | 390 | 0.007254 | 0.00186 | N
10/03/2017 | 08:45 | ZN12600:PA2 | SHORT RURAL | Planned |  | 16 | 401 | 0.028528 | 0.0071143 | N
10/03/2017 | 09:30 | ZN9245:PA1 | URBAN | Planned |  | 3 | 315 | 0.00065102 | 0.00020667 | N
11/03/2017 | 01:00 | ZN3288:PA41 42DEF | CBD | Planned |  | 7 | 110 | 0.024785 | 0.022532 | N
11/03/2017 | 07:30 | ZN384:PA22 | URBAN | Planned |  | 1 | 285 | 0.00019634 | 6.8891e-05 | N
11/03/2017 | 08:45 | ZN12600:PA1 | SHORT RURAL | Planned |  | 67 | 485 | 0.14449 | 0.029791 | N
11/03/2017 | 09:00 | ZN384:PA22 | URBAN | Planned |  | 104 | 262 | 0.018771 | 0.0071646 | N
12/03/2017 | 01:05 | ZN3288:PA41 42DEF | CBD | Planned |  | 7 | 105 | 0.023659 | 0.022532 | N
12/03/2017 | 08:00 | ZN2400:PA13 | URBAN | Planned |  | 4 | 495 | 0.0013641 | 0.00027557 | N
12/03/2017 | 07:30 | ZN15001:PA16 | URBAN | Planned |  | 3 | 450 | 0.00093004 | 0.00020668 | N
12/03/2017 | 08:30 | ZN3288:PA45 46DEF | CBD | Planned |  | 2 | 600 | 0.038626 | 0.0064377 | N
12/03/2017 | 08:00 | ZN2400:PA13 | URBAN | Planned |  | 1 | 495 | 0.00034101 | 6.8892e-05 | N
13/03/2017 | 07:45 | ZN15005:PA10 | URBAN | Planned |  | 1 | 402 | 0.00027694 | 6.8892e-05 | N
13/03/2017 | 07:30 | ZN15004:PA9 | URBAN | Planned |  | 38 | 450 | 0.01178 | 0.0026179 | N
13/03/2017 | 08:45 | ZN14144:PA5 | SHORT RURAL | Planned |  | 4 | 443 | 0.0078791 | 0.0017786 | N
15/03/2017 | 20:30 | ZN15004:PA1 | URBAN | Planned |  | 25 | 510 | 0.0087838 | 0.0017223 | N
07/04/2017 | 08:45 | 228:7486 | URBAN | Planned |  | 1 | 400 | 0.00027566 | 6.8914e-05 | N
07/04/2017 | 07:30 | 243:80083 | SHORT RURAL | Planned |  | 3 | 465 | 0.0062125 | 0.001336 | N
09/04/2017 | 06:50 | 224:80329 | SHORT RURAL | Planned |  | 1 | 545 | 0.0024271 | 0.00044534 | N
09/04/2017 | 07:20 | 224:80329 | SHORT RURAL | Planned |  | 1 | 525 | 0.0023381 | 0.00044534 | N
08/04/2017 | 06:30 | 507:80926 | URBAN | Planned |  | 1 | 350 | 0.00024073 | 6.8781e-05 | N
07/04/2017 | 08:40 | 812:19066 | SHORT RURAL | Planned |  | 34 | 95 | 0.014384 | 0.015142 | N
07/04/2017 | 08:35 | 807:74183 | SHORT RURAL | Planned |  | 3 | 175 | 0.002338 | 0.001336 | N
07/04/2017 | 08:30 | 812:19072 | SHORT RURAL | Planned |  | 1 | 120 | 0.00053441 | 0.00044534 | N
07/04/2017 | 09:05 | 515:35197 | LONG RURAL | Planned |  | 3 | 110 | 0.11782 | 0.1071 | N
09/04/2017 | 08:40 | 513:48058 | URBAN | Planned |  | 98 | 365 | 0.024603 | 0.0067404 | N
10/04/2017 | 09:05 | 221:11899 | SHORT RURAL | Planned |  | 1 | 325 | 0.0014474 | 0.00044534 | N
10/04/2017 | 09:30 | 520:48172 | SHORT RURAL | Planned |  | 1 | 145 | 0.00064575 | 0.00044534 | N
11/04/2017 | 09:15 | 227:13019 | SHORT RURAL | Planned |  | 75 | 315 | 0.10521 | 0.033401 | N
11/04/2017 | 08:20 | 214:8670 | URBAN | Planned |  | 45 | 370 | 0.011452 | 0.0030951 | N
11/04/2017 | 08:30 | 202:34254 | URBAN | Planned |  | 151 | 490 | 0.05089 | 0.010386 | N
11/04/2017 | 08:35 | 217:33611 | URBAN | Planned |  | 38 | 385 | 0.010063 | 0.0026136 | N
11/04/2017 | 18:00 | 202:34249 | URBAN | Planned |  | 14 | 115 | 0.0011074 | 0.00096292 | N
11/04/2017 | 07:45 | 507:80932 | SHORT RURAL | Planned |  | 109 | 529 | 0.25679 | 0.048542 | N
11/04/2017 | 08:11 | 526:34639 | SHORT RURAL | Planned |  | 79 | 418 | 0.14706 | 0.035182 | N
11/04/2017 | 09:30 | 230:81432 | SHORT RURAL | Planned |  | 1 | 205 | 0.00091295 | 0.00044534 | N
11/04/2017 | 08:55 | 532:83307 | SHORT RURAL | Planned |  | 102 | 161 | 0.073134 | 0.045425 | N
11/04/2017 | 08:40 | 513:48056 | SHORT RURAL | Planned |  | 1 | 85 | 0.00037854 | 0.00044534 | N
11/04/2017 | 08:45 | 516:48067 | SHORT RURAL | Planned |  | 3 | 226 | 0.0030194 | 0.001336 | N
11/04/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 43 | 360 | 5.5266 | 1.5352 | N
11/04/2017 | 13:00 | 513:48056 | SHORT RURAL | Planned |  | 3 | 60 | 0.00080162 | 0.001336 | N
12/04/2017 | 08:30 | 256:80641 | URBAN | Planned |  | 180 | 510 | 0.063146 | 0.012382 | N
12/04/2017 | 08:00 | 524:33570 | SHORT RURAL | Planned |  | 89 | 285 | 0.11297 | 0.039639 | N
12/04/2017 | 10:00 | 504:48031 | SHORT RURAL | Planned |  | 2 | 80 | 0.00071262 | 0.00089077 | N
12/04/2017 | 08:40 | 513:48056 | SHORT RURAL | Planned |  | 1 | 55 | 0.00024496 | 0.00044539 | N
12/04/2017 | 09:50 | 515:35192 | SHORT RURAL | Planned |  | 2 | 115 | 0.0010244 | 0.00089077 | N
12/04/2017 | 09:15 | 515:35197 | LONG RURAL | Planned |  | 1 | 65 | 0.023206 | 0.035702 | N
12/04/2017 | 08:30 | 801:74120 | URBAN | Planned |  | 1 | 220 | 0.00015133 | 6.8787e-05 | N
12/04/2017 | 12:50 | 513:48056 | SHORT RURAL | Planned |  | 1 | 50 | 0.00022269 | 0.00044539 | N
12/04/2017 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 1 | 360 | 0.0016034 | 0.00044539 | N
12/04/2017 | 12:15 | 807:74180 | SHORT RURAL | Planned |  | 7 | 45 | 0.001403 | 0.0031177 | N
12/04/2017 | 09:50 | 802:82225 | SHORT RURAL | Planned |  | 4 | 65 | 0.001158 | 0.0017815 | N
13/04/2017 | 08:00 | 227:13019 | SHORT RURAL | Planned |  | 7 | 380 | 0.011848 | 0.003118 | N
13/04/2017 | 09:10 | 507:80932 | SHORT RURAL | Planned |  | 99 | 245 | 0.10804 | 0.044097 | N
13/04/2017 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 6 | 120 | 0.25705 | 0.21421 | N
13/04/2017 | 12:35 | 504:48026 | SHORT RURAL | Planned |  | 1 | 55 | 0.00024498 | 0.00044542 | N
13/04/2017 | 08:30 | 243:80078 | SHORT RURAL | Planned |  | 95 | 280 | 0.11848 | 0.042315 | N
18/04/2017 | 00:01 | 224:80344 | URBAN | Planned |  | 1 | 264 | 0.00018154 | 6.8766e-05 | N
13/04/2017 | 12:45 | 502:48010 | SHORT RURAL | Planned |  | 8 | 90 | 0.0032071 | 0.0035634 | N
13/04/2017 | 08:50 | 813:89055 | SHORT RURAL | Planned |  | 16 | 280 | 0.019955 | 0.0071268 | N
18/04/2017 | 08:00 | 227:13019 | SHORT RURAL | Planned |  | 75 | 455 | 0.15195 | 0.033396 | N
18/04/2017 | 08:00 | 243:80084 | SHORT RURAL | Planned |  | 95 | 435 | 0.18401 | 0.042302 | N
19/04/2017 | 05:00 | 261:81865 | URBAN | Planned |  | 15 | 115 | 0.0011863 | 0.0010316 | N
18/04/2017 | 09:00 | 512:48048 | SHORT RURAL | Planned |  | 8 | 375 | 0.013358 | 0.0035623 | N
18/04/2017 | 08:40 | 810:74050 | SHORT RURAL | Planned |  | 11 | 230 | 0.011266 | 0.0048981 | N
19/04/2017 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 19 | 245 | 0.020728 | 0.0084604 | N
11/03/2017 | 17:15 | ZN14892:PA8 | SHORT RURAL | Planned |  | 1 | 405 | 0.0018008 | 0.00044464 | N
13/03/2017 | 08:40 | ZN2835:PA23 | URBAN | Planned |  | 69 | 425 | 0.020202 | 0.0047535 | N
13/03/2017 | 18:00 | ZN15001:PA18 | URBAN | Planned |  | 72 | 330 | 0.016369 | 0.0049602 | N
14/03/2017 | 10:30 | ZN15013:PA6 | SHORT RURAL | Planned |  | 7 | 210 | 0.0065363 | 0.0031125 | N
14/03/2017 | 08:10 | ZN14891:PA5 | SHORT RURAL | Planned |  | 4 | 425 | 0.0075589 | 0.0017786 | N
14/03/2017 | 09:05 | ZN10997:PA2 | URBAN | Planned |  | 539 | 400 | 0.14853 | 0.037133 | N
14/03/2017 | 20:00 | ZN2635:PA58 | URBAN | Planned |  | 35 | 480 | 0.011574 | 0.0024112 | N
14/03/2017 | 22:00 | ZN72:PA14 | URBAN | Planned |  | 28 | 240 | 0.0046295 | 0.001929 | N
15/03/2017 | 07:35 | ZN116:PA85 | URBAN | Planned |  | 1 | 60 | 4.1335e-05 | 6.8892e-05 | N
15/03/2017 | 08:45 | ZN9118:PA20 | URBAN | Planned |  | 120 | 370 | 0.030588 | 0.0082671 | N
16/03/2017 | 07:30 | ZN36100:PA2 | URBAN | Planned |  | 25 | 510 | 0.0087818 | 0.0017219 | N
16/03/2017 | 08:55 | ZN12690:PA3 | SHORT RURAL | Planned |  | 184 | 395 | 0.32307 | 0.08179 | N
16/03/2017 | 08:00 | ZN10994:PA3 | URBAN | Planned |  | 53 | 390 | 0.014237 | 0.0036505 | N
16/03/2017 | 08:30 | ZN10999:PA19 | URBAN | Planned |  | 6 | 510 | 0.0021076 | 0.00041326 | N
16/03/2017 | 08:35 | ZN342:PA17 | URBAN | Planned |  | 5 | 325 | 0.0011192 | 0.00034438 | N
16/03/2017 | 09:30 | ZN1287:PA23 | URBAN | Planned |  | 1 | 1,540 | 0.0010607 | 6.8877e-05 | N
17/03/2017 | 06:30 | ZN7900:PA11 | URBAN | Planned |  | 40 | 120 | 0.0033061 | 0.0027551 | N
17/03/2017 | 08:00 | ZN36100:PA27 | URBAN | Planned |  | 41 | 420 | 0.011861 | 0.002824 | N
17/03/2017 | 09:30 | ZN12600:PA1 | SHORT RURAL | Planned |  | 8 | 520 | 0.018489 | 0.0035556 | N
17/03/2017 | 09:00 | ZN15014:PA12 | SHORT RURAL | Planned |  | 34 | 150 | 0.022667 | 0.015111 | N
19/04/2017 | 09:15 | 243:80083 | SHORT RURAL | Planned |  | 11 | 401 | 0.019642 | 0.0048981 | N
19/04/2017 | 09:00 | 238:34140 | URBAN | Planned |  | 28 | 180 | 0.003466 | 0.0019256 | N
19/04/2017 | 10:00 | 509:33395 | LONG RURAL | Planned |  | 5 | 85 | 0.15173 | 0.17851 | N
19/04/2017 | 12:30 | 509:33395 | LONG RURAL | Planned |  | 3 | 30 | 0.032131 | 0.1071 | N
19/04/2017 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 1 | 60 | 0.00026717 | 0.00044529 | N
19/04/2017 | 10:40 | 513:48059 | SHORT RURAL | Planned |  | 7 | 68 | 0.0021196 | 0.003117 | N
17/03/2017 | 14:00 | ZN35800:PA7 | URBAN | Planned |  | 1 | 330 | 0.00022729 | 6.8877e-05 | N
17/03/2017 | 17:30 | ZN15001:PA6 | URBAN | Planned |  | 27 | 360 | 0.0066949 | 0.0018597 | N
17/03/2017 | 17:30 | ZN15001:PA10 | URBAN | Planned |  | 13 | 360 | 0.0032235 | 0.0008954 | N
17/03/2017 | 17:30 | ZN15001:PA18 | URBAN | Planned |  | 8 | 360 | 0.0019837 | 0.00055102 | N
18/03/2017 | 06:30 | ZN14892:PA1 | SHORT RURAL | Planned |  | 1 | 180 | 0.00080001 | 0.00044445 | N
18/03/2017 | 08:05 | ZN9534:PA18 | URBAN | Planned |  | 11 | 275 | 0.0020836 | 0.00075766 | N
18/03/2017 | 09:50 | ZN1290:PA12 | URBAN | Planned |  | 5 | 355 | 0.0012226 | 0.00034439 | N
19/03/2017 | 08:30 | ZN8000:PA17 | URBAN | Planned |  | 4 | 240 | 0.00066123 | 0.00027551 | N
19/03/2017 | 08:30 | ZN8000:PA30 | URBAN | Planned |  | 4 | 240 | 0.00066123 | 0.00027551 | N
19/03/2017 | 07:35 | ZN1788:PA15 | URBAN | Planned |  | 1 | 295 | 0.00020319 | 6.8879e-05 | N
20/03/2017 | 07:30 | ZN965:PA28 | URBAN | Planned |  | 15 | 570 | 0.0058891 | 0.0010332 | N
20/03/2017 | 07:30 | ZN965:PA38 | URBAN | Planned |  | 32 | 570 | 0.012563 | 0.0022041 | N
20/03/2017 | 07:30 | ZN690:PA30 | URBAN | Planned |  | 43 | 1,875 | 0.055533 | 0.0029618 | N
20/03/2017 | 09:00 | ZN9252:PA30 | URBAN | Planned |  | 410 | 450 | 0.12708 | 0.02824 | N
20/03/2017 | 08:10 | ZN12570:PA41 | URBAN | Planned |  | 143 | 432 | 0.04255 | 0.0098496 | N
20/03/2017 | 08:30 | ZN3155:PA23 | URBAN | Planned |  | 19 | 390 | 0.0051039 | 0.0013087 | N
20/03/2017 | 21:00 | ZN15001:PA6 | URBAN | Planned |  | 27 | 179 | 0.0033289 | 0.0018597 | N
20/03/2017 | 21:00 | ZN15001:PA18 | URBAN | Planned |  | 8 | 179 | 0.00098634 | 0.00055103 | N
22/03/2017 | 09:00 | ZN9252:PA30 | URBAN | Planned |  | 410 | 450 | 0.12709 | 0.028241 | N
23/03/2017 | 09:00 | ZN9252:PA30 | URBAN | Planned |  | 410 | 450 | 0.12704 | 0.028232 | N
21/03/2017 | 08:30 | ZN3155:PA23 | URBAN | Planned |  | 19 | 390 | 0.0051039 | 0.0013087 | N
21/03/2017 | 09:15 | ZN14891:PA20 | SHORT RURAL | Planned |  | 5 | 225 | 0.0050001 | 0.0022223 | N
21/03/2017 | 09:30 | ZN9900:PA10 | URBAN | Planned |  | 175 | 175 | 0.021094 | 0.012054 | N
22/03/2017 | 06:30 | ZN965:PA4 | URBAN | Planned |  | 1 | 3,385 | 0.0023316 | 6.8881e-05 | N
22/03/2017 | 09:55 | ZN9700:PA20 | URBAN | Planned |  | 3 | 380 | 0.00078524 | 0.00020664 | N
22/03/2017 | 07:30 | ZN10996:PA4 | URBAN | Planned |  | 38 | 570 | 0.01492 | 0.0026175 | N
22/03/2017 | 08:30 | ZN3155:PA23 | URBAN | Planned |  | 19 | 360 | 0.0047115 | 0.0013087 | N
22/03/2017 | 09:20 | ZN14144:PA2 | SHORT RURAL | Planned |  | 80 | 483 | 0.17174 | 0.035558 | N
22/03/2017 | 09:38 | ZN14891:PA12 | SHORT RURAL | Planned |  | 6 | 469 | 0.012507 | 0.0026668 | N
22/03/2017 | 08:00 | ZN14892:PA19 | URBAN | Planned |  | 37 | 620 | 0.015801 | 0.0025486 | N
22/03/2017 | 23:59 | ZN36800:PA32 | URBAN | Planned |  | 83 | 241 | 0.013778 | 0.0057171 | N
23/03/2017 | 07:30 | ZN965:PA38 | URBAN | Planned |  | 32 | 450 | 0.0099155 | 0.0022035 | N
23/03/2017 | 07:30 | ZN35600:PA6 | URBAN | Planned |  | 100 | 420 | 0.02892 | 0.0068858 | N
23/03/2017 | 08:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 6 | 470 | 0.012538 | 0.0026676 | N
23/03/2017 | 08:00 | ZN15014:PA12 | SHORT RURAL | Planned |  | 34 | 360 | 0.05442 | 0.015117 | N
23/03/2017 | 08:00 | ZN15001:PA18 | URBAN | Planned |  | 27 | 420 | 0.0078085 | 0.0018592 | N
23/03/2017 | 08:00 | ZN15001:PA18 | URBAN | Planned |  | 24 | 420 | 0.0069409 | 0.0016526 | N
23/03/2017 | 08:30 | ZN3155:PA23 | URBAN | Planned |  | 19 | 390 | 0.0051024 | 0.0013083 | N
23/03/2017 | 19:00 | ZN35400:PA79 | URBAN | Planned |  | 20 | 600 | 0.0082629 | 0.0013772 | N
23/03/2017 | 23:30 | ZN931:PA24 | URBAN | Planned |  | 4 | 20 | 5.5086e-05 | 0.00027543 | N
24/03/2017 | 08:45 | ZN14892:PA19 | URBAN | Planned |  | 74 | 435 | 0.022166 | 0.0050955 | N
24/03/2017 | 08:00 | ZN12640:PA10 | URBAN | Planned |  | 37 | 472 | 0.012025 | 0.0025478 | N
25/03/2017 | 01:10 | ZN3155:PA28 | URBAN | Planned |  | 2 | 10 | 1.3771e-05 | 0.00013771 | N
25/03/2017 | 07:00 | ZN901:PA7 | URBAN | Planned |  | 1 | 15 | 1.0328e-05 | 6.8855e-05 | N
25/03/2017 | 07:20 | ZN384:PA65 | URBAN | Planned |  | 4 | 40 | 0.00011017 | 0.00027542 | N
25/03/2017 | 09:45 | ZN12600:PA12 | URBAN | Planned |  | 1 | 90 | 6.197e-05 | 6.8855e-05 | N
26/03/2017 | 07:35 | ZN1290:PA9 | URBAN | Planned |  | 12 | 540 | 0.004462 | 0.00082629 | N
25/03/2017 | 23:00 | ZN7481:PA9 | URBAN | Planned |  | 20 | 650 | 0.0089512 | 0.0013771 | N
26/03/2017 | 09:00 | ZN116:PA76 | URBAN | Planned |  | 1 | 150 | 0.00010329 | 6.8857e-05 | N
26/03/2017 | 07:35 | ZN342:PA15 | URBAN | Planned |  | 19 | 540 | 0.0070648 | 0.0013083 | N
26/03/2017 | 08:10 | ZN847:PA21 | URBAN | Planned |  | 35 | 542 | 0.013062 | 0.00241 | N
27/03/2017 | 09:40 | ZN8100:PA2 | URBAN | Planned |  | 1 | 166 | 0.0001143 | 6.8857e-05 | N
27/03/2017 | 08:10 | ZN3155:PA44 | URBAN | Planned |  | 99 | 590 | 0.04022 | 0.0068169 | N
27/03/2017 | 08:25 | ZN12630:PA11 | SHORT RURAL | Planned |  | 7 | 410 | 0.012738 | 0.0031069 | N
27/03/2017 | 17:30 | ZN15001:PA10 | URBAN | Planned |  | 13 | 360 | 0.0032225 | 0.00089515 | N
27/03/2017 | 17:30 | ZN15001:PA18 | URBAN | Planned |  | 8 | 360 | 0.0019831 | 0.00055086 | N
28/03/2017 | 08:30 | ZN2400:PA21 | URBAN | Planned |  | 4 | 345 | 0.00095024 | 0.00027543 | N
28/03/2017 | 08:10 | ZN12650:PA1 | SHORT RURAL | Planned |  | 6 | 425 | 0.011318 | 0.002663 | N
28/03/2017 | 08:35 | ZN14891:PA8 | SHORT RURAL | Planned |  | 1 | 400 | 0.0017754 | 0.00044384 | N
29/03/2017 | 08:50 | ZN3922:PA10 | URBAN | Planned |  | 39 | 360 | 0.0096679 | 0.0026855 | N
29/03/2017 | 09:20 | ZN9252:PA30 | URBAN | Planned |  | 37 | 385 | 0.009809 | 0.0025478 | N
29/03/2017 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 39 | 470 | 0.081357 | 0.01731 | N
29/03/2017 | 10:10 | ZN12630:PA1 | SHORT RURAL | Planned |  | 2 | 350 | 0.0031069 | 0.00088769 | N
29/03/2017 | 08:30 | ZN12690:PA12 | SHORT RURAL | Planned |  | 29 | 610 | 0.078516 | 0.012871 | N
30/03/2017 | 08:15 | ZN2466:PA20 | URBAN | Planned |  | 5 | 665 | 0.0022888 | 0.00034418 | N
30/03/2017 | 09:20 | ZN9252:PA30 | URBAN | Planned |  | 37 | 385 | 0.0098057 | 0.0025469 | N
30/03/2017 | 08:35 | ZN12630:PA1 | SHORT RURAL | Planned |  | 14 | 490 | 0.030428 | 0.0062099 | N
30/03/2017 | 08:10 | ZN14891:PA5 | SHORT RURAL | Planned |  | 4 | 425 | 0.0075405 | 0.0017742 | N
30/03/2017 | 08:30 | ZN12600:PA1 | SHORT RURAL | Planned |  | 88 | 390 | 0.15223 | 0.039033 | N
30/03/2017 | 09:10 | ZN3155:PA29 | URBAN | Planned |  | 54 | 380 | 0.014125 | 0.0037172 | N
30/03/2017 | 08:45 | ZN36100:PA27 | URBAN | Planned |  | 132 | 170 | 0.015447 | 0.0090864 | N
30/03/2017 | 10:40 | ZN14891:PA5 | SHORT RURAL | Planned |  | 31 | 150 | 0.020626 | 0.01375 | N
30/03/2017 | 09:50 | ZN10999:PA29 | URBAN | Planned |  | 64 | 30 | 0.0013217 | 0.0044055 | N
31/03/2017 | 08:10 | ZN13000:PA11 | SHORT RURAL | Planned |  | 1 | 95 | 0.00042138 | 0.00044356 | N
31/03/2017 | 09:40 | ZN12630:PA3 | SHORT RURAL | Planned |  | 22 | 200 | 0.019517 | 0.0097583 | N
31/03/2017 | 10:00 | ZN9037:PA4 | URBAN | Planned |  | 52 | 570 | 0.020404 | 0.0035797 | N
31/03/2017 | 05:30 | ZN35400:PA64 | URBAN | Planned |  | 29 | 900 | 0.017967 | 0.0019964 | N
20/04/2017 | 09:00 | 238:34148 | SHORT RURAL | Planned |  | 16 | 300 | 0.021318 | 0.0071061 | N
20/04/2017 | 08:32 | 526:34639 | SHORT RURAL | Planned |  | 1 | 158 | 0.00070172 | 0.00044413 | N
20/04/2017 | 09:07 | 511:29876 | SHORT RURAL | Planned |  | 36 | 353 | 0.05644 | 0.015989 | N
20/04/2017 | 09:30 | 526:34639 | SHORT RURAL | Planned |  | 3 | 50 | 0.00066619 | 0.0013324 | N
20/04/2017 | 12:50 | 526:34639 | SHORT RURAL | Planned |  | 1 | 100 | 0.00044413 | 0.00044413 | N
20/04/2017 | 09:10 | 813:89063 | SHORT RURAL | Planned |  | 61 | 310 | 0.083985 | 0.027092 | N
20/04/2017 | 08:05 | 807:74184 | SHORT RURAL | Planned |  | 46 | 360 | 0.073548 | 0.02043 | N
21/04/2017 | 10:32 | 515:35197 | LONG RURAL | Planned |  | 1 | 133 | 0.047328 | 0.035702 | N
20/04/2017 | 09:00 | 523:33501 | SHORT RURAL | Planned |  | 3 | 135 | 0.0017987 | 0.0013324 | N
21/04/2017 | 08:50 | 511:29878 | SHORT RURAL | Planned |  | 4 | 350 | 0.0062179 | 0.0017766 | N
22/04/2017 | 07:00 | 203:8082 | URBAN | Planned |  | 13 | 302 | 0.0027001 | 0.00089408 | N
21/04/2017 | 07:55 | 222:33596 | URBAN | Planned |  | 1 | 395 | 0.00027176 | 6.88e-05 | N
21/04/2017 | 08:25 | 202:34261 | URBAN | Planned |  | 2 | 215 | 0.00029584 | 0.0001376 | N
21/04/2017 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 18 | 340 | 2.1849 | 0.64263 | N
21/04/2017 | 09:20 | 502:48008 | URBAN | Planned |  | 128 | 330 | 0.029061 | 0.0088065 | N
21/04/2017 | 08:37 | 238:34140 | URBAN | Planned |  | 107 | 206 | 0.015165 | 0.0073617 | N
24/04/2017 | 08:10 | 532:83309 | SHORT RURAL | Planned |  | 1 | 120 | 0.00053278 | 0.00044399 | N
24/04/2017 | 08:50 | 233:82812 | SHORT RURAL | Planned |  | 68 | 380 | 0.11473 | 0.030191 | N
21/04/2017 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 24 | 335 | 0.035709 | 0.010659 | N
21/04/2017 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 7 | 395 | 0.01228 | 0.003109 | N
21/04/2017 | 09:07 | 515:35197 | LONG RURAL | Planned |  | 10 | 218 | 0.77829 | 0.35702 | N
21/04/2017 | 15:25 | 812:19066 | SHORT RURAL | Planned |  | 2 | 2,480 | 0.022029 | 0.00088828 | N
24/04/2017 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 4 | 90 | 0.0015984 | 0.0017759 | N
24/04/2017 | 13:00 | 513:48056 | SHORT RURAL | Planned |  | 5 | 60 | 0.001332 | 0.0022199 | N
26/04/2017 | 08:15 | 227:13020 | SHORT RURAL | Planned |  | 84 | 373 | 0.13911 | 0.037295 | N
26/04/2017 | 08:40 | 213:33774 | URBAN | Planned |  | 1 | 280 | 0.00019257 | 6.8776e-05 | N
26/04/2017 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 37 | 60 | 0.0098566 | 0.016428 | N
26/04/2017 | 09:40 | 509:33395 | LONG RURAL | Planned |  | 1 | 150 | 0.053552 | 0.035702 | N
26/04/2017 | 09:00 | 512:48048 | SHORT RURAL | Planned |  | 5 | 175 | 0.0038849 | 0.00222 | N
26/04/2017 | 08:40 | 528:83019 | SHORT RURAL | Planned |  | 3 | 200 | 0.002664 | 0.001332 | N
26/04/2017 | 08:55 | 511:29878 | SHORT RURAL | Planned |  | 3 | 200 | 0.002664 | 0.001332 | N
26/04/2017 | 08:30 | 528:83019 | SHORT RURAL | Planned |  | 5 | 240 | 0.0053279 | 0.00222 | N
26/04/2017 | 08:35 | 523:33501 | SHORT RURAL | Planned |  | 1 | 115 | 0.00051059 | 0.00044399 | N
26/04/2017 | 08:08 | 801:74121 | LONG RURAL | Planned |  | 6 | 182 | 0.38986 | 0.21421 | N
26/04/2017 | 10:15 | 814:82283 | SHORT RURAL | Planned |  | 1 | 155 | 0.00068819 | 0.00044399 | N
26/04/2017 | 10:30 | 515:35197 | LONG RURAL | Planned |  | 1 | 170 | 0.060693 | 0.035702 | N
26/04/2017 | 12:50 | 523:33501 | SHORT RURAL | Planned |  | 1 | 50 | 0.000222 | 0.00044399 | N
27/04/2017 | 08:30 | 504:48031 | SHORT RURAL | Planned |  | 20 | 390 | 0.034625 | 0.0088783 | N
27/04/2017 | 08:10 | 243:80081 | SHORT RURAL | Planned |  | 194 | 445 | 0.38323 | 0.086119 | N
27/04/2017 | 08:05 | 214:8667 | URBAN | Planned |  | 13 | 445 | 0.0039778 | 0.00089388 | N
27/04/2017 | 07:00 | 532:83309 | SHORT RURAL | Planned |  | 4 | 700 | 0.01243 | 0.0017757 | N
27/04/2017 | 09:10 | 264:81240 | SHORT RURAL | Planned |  | 3 | 315 | 0.004195 | 0.0013317 | N
27/04/2017 | 08:45 | 508:82579 | SHORT RURAL | Planned |  | 6 | 245 | 0.0065255 | 0.0026635 | N
27/04/2017 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 39 | 360 | 0.062325 | 0.017313 | N
27/04/2017 | 08:00 | 526:34640 | SHORT RURAL | Planned |  | 15 | 310 | 0.020642 | 0.0066587 | N
27/04/2017 | 11:53 | 507:80914 | SHORT RURAL | Planned |  | 1 | 17 | 7.5465e-05 | 0.00044391 | N
27/04/2017 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 39 | 285 | 3.9682 | 1.3924 | N
28/04/2017 | 08:45 | 511:29878 | SHORT RURAL | Planned |  | 37 | 359 | 0.058964 | 0.016424 | N
28/04/2017 | 17:00 | 243:80075 | SHORT RURAL | Planned |  | 2 | 240 | 0.0021307 | 0.00088781 | N
30/04/2017 | 08:05 | 202:34249 | URBAN | Planned |  | 28 | 400 | 0.0077014 | 0.0019253 | N
30/04/2017 | 18:50 | 261:81867 | URBAN | Planned |  | 57 | 760 | 0.029788 | 0.0039195 | N
28/04/2017 | 12:00 | 511:29872 | URBAN | Planned |  | 1 | 20 | 1.3752e-05 | 6.8761e-05 | N
28/04/2017 | 07:00 | 532:83309 | SHORT RURAL | Planned |  | 4 | 480 | 0.008523 | 0.0017756 | N
28/04/2017 | 08:30 | 807:74181 | SHORT RURAL | Planned |  | 22 | 390 | 0.038087 | 0.0097659 | N
28/04/2017 | 08:35 | 813:89061 | LONG RURAL | Planned |  | 12 | 240 | 1.0282 | 0.42842 | N
28/04/2017 | 08:35 | 813:89061 | LONG RURAL | Planned |  | 2 | 275 | 0.19636 | 0.071403 | N
28/04/2017 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 2 | 155 | 0.0013761 | 0.00088781 | N
28/04/2017 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 14 | 155 | 0.77472 | 0.49982 | N
28/04/2017 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 61 | 390 | 0.1056 | 0.027078 | N
28/04/2017 | 13:35 | 812:19065 | SHORT RURAL | Planned |  | 1 | 80 | 0.00035512 | 0.0004439 | N
30/04/2017 | 07:45 | 513:48056 | SHORT RURAL | Planned |  | 1 | 150 | 0.00066584 | 0.00044389 | N
01/05/2017 | 08:40 | 504:48031 | SHORT RURAL | Planned |  | 44 | 380 | 0.074218 | 0.019531 | N
01/05/2017 | 18:45 | 261:81867 | URBAN | Planned |  | 3 | 735 | 0.0015162 | 0.00020629 | N
01/05/2017 | 20:40 | 225:13446 | URBAN | Planned |  | 107 | 120 | 0.0088291 | 0.0073576 | N
01/05/2017 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 10 | 250 | 0.89254 | 0.35702 | N
02/05/2017 | 08:00 | 213:33773 | URBAN | Planned |  | 1 | 510 | 0.0003507 | 6.8765e-05 | N
02/05/2017 | 08:10 | 239:82132 | URBAN | Planned |  | 101 | 412 | 0.028614 | 0.0069452 | N
02/05/2017 | 08:15 | 243:80083 | SHORT RURAL | Planned |  | 14 | 505 | 0.031383 | 0.0062145 | N
02/05/2017 | 19:00 | 261:81867 | URBAN | Planned |  | 1 | 725 | 0.00049854 | 6.8765e-05 | N
02/05/2017 | 08:00 | 504:48026 | SHORT RURAL | Planned |  | 199 | 360 | 0.318 | 0.088335 | N
02/05/2017 | 11:30 | 504:48031 | SHORT RURAL | Planned |  | 1 | 115 | 0.00051048 | 0.00044389 | N
02/05/2017 | 09:35 | 508:82575 | SHORT RURAL | Planned |  | 1 | 250 | 0.0011097 | 0.00044389 | N
02/05/2017 | 08:30 | 524:33580 | SHORT RURAL | Planned |  | 46 | 300 | 0.061257 | 0.020419 | N
02/05/2017 | 08:00 | 513:48059 | SHORT RURAL | Planned |  | 44 | 375 | 0.073242 | 0.019531 | N
02/05/2017 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 39 | 315 | 0.054532 | 0.017312 | N
02/05/2017 | 09:05 | 802:82225 | SHORT RURAL | Planned |  | 8 | 150 | 0.0053267 | 0.0035511 | N
03/05/2017 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 71 | 322 | 8.1667 | 2.5348 | N
03/05/2017 | 09:10 | 227:13015 | SHORT RURAL | Planned |  | 16 | 195 | 0.01385 | 0.0071023 | N
03/05/2017 | 08:55 | 508:82575 | SHORT RURAL | Planned |  | 8 | 125 | 0.004439 | 0.0035512 | N
03/05/2017 | 10:20 | 511:29876 | SHORT RURAL | Planned |  | 4 | 105 | 0.0018644 | 0.0017756 | N
03/05/2017 | 09:20 | 526:34640 | SHORT RURAL | Planned |  | 2 | 360 | 0.0031961 | 0.00088779 | N
03/05/2017 | 12:55 | 508:82575 | SHORT RURAL | Planned |  | 4 | 95 | 0.0016868 | 0.0017756 | N
03/05/2017 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 1 | 70 | 0.00031073 | 0.0004439 | N
03/05/2017 | 08:00 | 515:35197 | LONG RURAL | Planned |  | 22 | 350 | 2.749 | 0.78543 | N
03/05/2017 | 08:35 | 813:89061 | LONG RURAL | Planned |  | 6 | 270 | 0.57836 | 0.21421 | N
03/05/2017 | 13:00 | 513:48059 | SHORT RURAL | Planned |  | 1 | 60 | 0.00026634 | 0.0004439 | N
04/05/2017 | 10:00 | 217:33612 | URBAN | Planned |  | 145 | 280 | 0.027913 | 0.0099691 | N
04/05/2017 | 08:30 | 243:80083 | SHORT RURAL | Planned |  | 53 | 419 | 0.098559 | 0.023522 | N
04/05/2017 | 09:50 | 216:10728 | SHORT RURAL | Planned |  | 1 | 105 | 0.00046601 | 0.00044382 | N
04/05/2017 | 07:00 | 532:83309 | SHORT RURAL | Planned |  | 4 | 300 | 0.0053258 | 0.0017753 | N
04/05/2017 | 08:10 | 512:48048 | SHORT RURAL | Planned |  | 8 | 470 | 0.016688 | 0.0035506 | N
04/05/2017 | 09:00 | 238:34150 | SHORT RURAL | Planned |  | 18 | 53 | 0.004234 | 0.0079887 | N
04/05/2017 | 08:40 | 532:83309 | SHORT RURAL | Planned |  | 2 | 135 | 0.0011983 | 0.00088764 | N
04/05/2017 | 08:05 | 507:80932 | SHORT RURAL | Planned |  | 30 | 420 | 0.055921 | 0.013315 | N
04/05/2017 | 09:35 | 502:48010 | SHORT RURAL | Planned |  | 5 | 250 | 0.0055477 | 0.0022191 | N
04/05/2017 | 09:00 | 232:11453 | SHORT RURAL | Planned |  | 119 | 80 | 0.042252 | 0.052814 | N
04/05/2017 | 10:38 | 507:80914 | SHORT RURAL | Planned |  | 1 | 30 | 0.00013315 | 0.00044382 | N
04/05/2017 | 08:20 | 807:74184 | SHORT RURAL | Planned |  | 6 | 380 | 0.010119 | 0.0026629 | N
04/05/2017 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 1 | 50 | 0.00022191 | 0.00044382 | N
04/05/2017 | 08:20 | 807:74184 | SHORT RURAL | Planned |  | 40 | 360 | 0.06391 | 0.017753 | N
04/05/2017 | 12:45 | 523:33501 | SHORT RURAL | Planned |  | 3 | 48 | 0.0006391 | 0.0013315 | N
07/05/2017 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 138 | 345 | 0.21166 | 0.061352 | N
07/05/2017 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 320 | 345 | 39.4145 | 11.4245 | N
07/05/2017 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 197 | 345 | 0.30216 | 0.087582 | N
07/05/2017 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 563 | 345 | 0.86353 | 0.2503 | N
05/05/2017 | 08:30 | 507:80923 | SHORT RURAL | Planned |  | 10 | 360 | 0.015977 | 0.0044382 | N
05/05/2017 | 09:38 | 243:80074 | SHORT RURAL | Planned |  | 1 | 292 | 0.0012959 | 0.00044382 | N
05/05/2017 | 09:00 | 224:80341 | URBAN | Planned |  | 93 | 365 | 0.023369 | 0.0064024 | N
05/05/2017 | 08:55 | 504:48028 | URBAN | Planned |  | 2 | 280 | 0.00038552 | 0.00013769 | N
05/05/2017 | 09:20 | 232:11454 | SHORT RURAL | Planned |  | 99 | 105 | 0.046135 | 0.043938 | N
05/05/2017 | 07:00 | 532:83309 | SHORT RURAL | Planned |  | 4 | 595 | 0.010563 | 0.0017753 | N
05/05/2017 | 08:00 | 512:48048 | SHORT RURAL | Planned |  | 3 | 390 | 0.0051926 | 0.0013314 | N
05/05/2017 | 20:10 | 502:48004 | URBAN | Planned |  | 1 | 410 | 0.00028225 | 6.8843e-05 | N
05/05/2017 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 11 | 440 | 0.021481 | 0.004882 | N
05/05/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 43 | 370 | 5.6801 | 1.5352 | N
08/05/2017 | 08:05 | 261:81882 | URBAN | Planned |  | 139 | 235 | 0.022456 | 0.0095558 | N
08/05/2017 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 3 | 195 | 0.20885 | 0.1071 | N
07/05/2017 | 18:20 | 261:81867 | URBAN | Planned |  | 57 | 765 | 0.029977 | 0.0039186 | N
08/05/2017 | 09:45 | 235:8684 | SHORT RURAL | Planned |  | 1 | 205 | 0.00091139 | 0.00044458 | N
08/05/2017 | 09:05 | 502:48010 | SHORT RURAL | Planned |  | 5 | 275 | 0.006113 | 0.0022229 | N
08/05/2017 | 07:30 | 511:29880 | URBAN | Planned |  | 1 | 570 | 0.00039186 | 6.8747e-05 | N
08/05/2017 | 08:30 | 532:83309 | SHORT RURAL | Planned |  | 103 | 220 | 0.10074 | 0.045792 | N
08/05/2017 | 10:25 | 238:34141 | SHORT RURAL | Planned |  | 2 | 20 | 0.00017783 | 0.00088916 | N
08/05/2017 | 11:00 | 508:82574 | SHORT RURAL | Planned |  | 1 | 140 | 0.00062241 | 0.00044458 | N
08/05/2017 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 3 | 120 | 0.0016005 | 0.0013337 | N
09/05/2017 | 09:18 | 532:83307 | SHORT RURAL | Planned |  | 268 | 402 | 0.47898 | 0.11915 | N
09/05/2017 | 08:00 | 514:18137 | SHORT RURAL | Planned |  | 31 | 240 | 0.033077 | 0.013782 | N
09/05/2017 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 7 | 248 | 0.61978 | 0.24991 | N
09/05/2017 | 09:00 | 813:89055 | SHORT RURAL | Planned |  | 6 | 290 | 0.0077357 | 0.0026675 | N
09/05/2017 | 09:20 | 508:82574 | SHORT RURAL | Planned |  | 1 | 95 | 0.00042235 | 0.00044458 | N
09/05/2017 | 08:15 | 507:80925 | SHORT RURAL | Planned |  | 1 | 100 | 0.00044458 | 0.00044458 | N
09/05/2017 | 11:05 | 504:48033 | SHORT RURAL | Planned |  | 3 | 80 | 0.001067 | 0.0013337 | N
09/05/2017 | 11:37 | 508:82574 | SHORT RURAL | Planned |  | 1 | 138 | 0.00061352 | 0.00044458 | N
09/05/2017 | 10:03 | 526:34639 | SHORT RURAL | Planned |  | 129 | 362 | 0.20761 | 0.057351 | N
09/05/2017 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 1 | 75 | 0.00033344 | 0.00044458 | N
10/05/2017 | 08:30 | 238:34140 | URBAN | Planned |  | 6 | 470 | 0.0019388 | 0.0004125 | N
12/05/2017 | 08:45 | 524:33570 | SHORT RURAL | Planned |  | 2 | 355 | 0.0031553 | 0.00088882 | N
12/05/2017 | 08:00 | 528:83020 | SHORT RURAL | Planned |  | 25 | 460 | 0.051107 | 0.01111 | N
10/05/2017 | 07:30 | 243:80083 | SHORT RURAL | Planned |  | 29 | 500 | 0.064466 | 0.012893 | N
10/05/2017 | 08:00 | 223:14395 | SHORT RURAL | Planned |  | 1 | 555 | 0.0024675 | 0.00044459 | N
11/05/2017 | 08:00 | 202:34249 | URBAN | Planned |  | 27 | 360 | 0.0066876 | 0.0018577 | N
11/05/2017 | 09:00 | 223:14395 | SHORT RURAL | Planned |  | 32 | 450 | 0.063998 | 0.014222 | N
11/05/2017 | 08:24 | 224:80332 | URBAN | Planned |  | 59 | 426 | 0.017293 | 0.0040593 | N
13/05/2017 | 07:00 | 220:8687 | URBAN | Planned |  | 26 | 240 | 0.0042891 | 0.0017871 | N
10/05/2017 | 08:45 | 524:33570 | SHORT RURAL | Planned |  | 1 | 205 | 0.00091142 | 0.00044459 | N
10/05/2017 | 09:42 | 233:82815 | SHORT RURAL | Planned |  | 1 | 43 | 0.00019118 | 0.00044459 | N
10/05/2017 | 10:15 | 509:33395 | LONG RURAL | Planned |  | 1 | 85 | 0.030346 | 0.035702 | N
10/05/2017 | 11:55 | 509:33395 | LONG RURAL | Planned |  | 4 | 50 | 0.071403 | 0.14281 | N
10/05/2017 | 10:00 | 265:81648 | SHORT RURAL | Planned |  | 2 | 270 | 0.0024008 | 0.00088919 | N
11/05/2017 | 07:40 | 508:82579 | SHORT RURAL | Planned |  | 7 | 470 | 0.014622 | 0.003111 | N
11/05/2017 | 08:50 | 509:33395 | LONG RURAL | Planned |  | 2 | 305 | 0.21778 | 0.071403 | N
12/05/2017 | 07:10 | 528:83014 | SHORT RURAL | Planned |  | 148 | 245 | 0.16114 | 0.065773 | N
12/05/2017 | 08:40 | 508:82579 | SHORT RURAL | Planned |  | 8 | 392 | 0.013937 | 0.0035553 | N
12/05/2017 | 08:50 | 264:81244 | SHORT RURAL | Planned |  | 190 | 375 | 0.31664 | 0.084438 | N
10/05/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 4 | 285 | 0.407 | 0.14281 | N
10/05/2017 | 08:00 | 515:35197 | LONG RURAL | Planned |  | 22 | 510 | 4.0057 | 0.78543 | N
11/05/2017 | 08:15 | 807:74184 | SHORT RURAL | Planned |  | 41 | 405 | 0.073797 | 0.018222 | N
11/05/2017 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 10 | 105 | 0.0046665 | 0.0044443 | N
11/05/2017 | 10:30 | 513:48059 | SHORT RURAL | Planned |  | 3 | 130 | 0.0017333 | 0.0013333 | N
11/05/2017 | 09:35 | 812:19066 | SHORT RURAL | Planned |  | 71 | 180 | 0.056798 | 0.031554 | N
12/05/2017 | 08:30 | 515:35198 | SHORT RURAL | Planned |  | 1 | 105 | 0.00046663 | 0.00044441 | N
12/05/2017 | 09:20 | 813:89061 | LONG RURAL | Planned |  | 1 | 230 | 0.082114 | 0.035702 | N
12/05/2017 | 09:00 | 512:48049 | SHORT RURAL | Planned |  | 11 | 105 | 0.0051329 | 0.0048885 | N
12/05/2017 | 13:00 | 515:35198 | SHORT RURAL | Planned |  | 2 | 75 | 0.00066662 | 0.00088882 | N
15/05/2017 | 08:30 | 524:33572 | SHORT RURAL | Planned |  | 17 | 390 | 0.029464 | 0.0075548 | N
15/05/2017 | 09:20 | 526:34639 | SHORT RURAL | Planned |  | 16 | 340 | 0.024175 | 0.0071104 | N
15/05/2017 | 09:00 | 243:80078 | SHORT RURAL | Planned |  | 74 | 120 | 0.039463 | 0.032886 | N
15/05/2017 | 08:00 | 261:81865 | URBAN | Planned |  | 108 | 350 | 0.025982 | 0.0074233 | N
15/05/2017 | 20:00 | 240:34849 | SHORT RURAL | Planned |  | 1 | 110 | 0.00048884 | 0.0004444 | N
15/05/2017 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 2 | 45 | 0.00039996 | 0.0008888 | N
15/05/2017 | 09:15 | 813:89061 | LONG RURAL | Planned |  | 5 | 270 | 0.48197 | 0.17851 | N
15/05/2017 | 08:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 235 | 0.083899 | 0.035702 | N
15/05/2017 | 12:45 | 513:48056 | SHORT RURAL | Planned |  | 2 | 85 | 0.00075548 | 0.0008888 | N
16/05/2017 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 11 | 330 | 0.016132 | 0.0048885 | N
16/05/2017 | 08:12 | 504:48031 | SHORT RURAL | Planned |  | 29 | 388 | 0.050004 | 0.012888 | N
16/05/2017 | 08:40 | 202:34249 | URBAN | Planned |  | 27 | 140 | 0.0025982 | 0.0018559 | N
16/05/2017 | 08:45 | 508:82580 | SHORT RURAL | Planned |  | 8 | 365 | 0.012977 | 0.0035552 | N
16/05/2017 | 08:20 | 526:34639 | SHORT RURAL | Planned |  | 43 | 420 | 0.08026 | 0.019109 | N
16/05/2017 | 08:30 | 513:48050 | SHORT RURAL | Planned |  | 2 | 120 | 0.0010666 | 0.00088881 | N
17/05/2017 | 07:30 | 243:80083 | SHORT RURAL | Planned |  | 29 | 515 | 0.066373 | 0.012888 | N
17/05/2017 | 08:00 | 235:8684 | SHORT RURAL | Planned |  | 1 | 450 | 0.0019998 | 0.00044441 | N
17/05/2017 | 08:54 | 213:33771 | URBAN | Planned |  | 107 | 96 | 0.0070606 | 0.0073548 | N
16/05/2017 | 09:00 | 227:13014 | SHORT RURAL | Planned |  | 6 | 180 | 0.0047996 | 0.0026664 | N
17/05/2017 | 08:30 | 221:11895 | URBAN | Planned |  | 78 | 366 | 0.019623 | 0.0053614 | N
17/05/2017 | 08:40 | 526:34637 | SHORT RURAL | Planned |  | 31 | 420 | 0.057862 | 0.013777 | N
17/05/2017 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 3 | 35 | 0.00046663 | 0.0013332 | N
17/05/2017 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 39 | 305 | 4.2467 | 1.3924 | N
17/05/2017 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 350 | 0.12496 | 0.035702 | N
17/05/2017 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 2 | 390 | 0.0034664 | 0.00088882 | N
16/05/2017 | 12:50 | 513:48050 | SHORT RURAL | Planned |  | 1 | 55 | 0.00024442 | 0.0004444 | N
16/05/2017 | 08:36 | 523:33508 | SHORT RURAL | Planned |  | 14 | 79 | 0.0049151 | 0.0062217 | N
16/05/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 76 | 120 | 0.04053 | 0.033775 | N
16/05/2017 | 08:35 | 515:35193 | SHORT RURAL | Planned |  | 1 | 105 | 0.00046663 | 0.0004444 | N
01/04/2017 | 07:00 | ZN3672:PA34 | URBAN | Planned |  | 1 | 600 | 0.00041279 | 6.8798e-05 | N
01/04/2017 | 08:15 | ZN12600:PA1 | SHORT RURAL | Planned |  | 23 | 210 | 0.021509 | 0.010242 | N
01/04/2017 | 07:35 | ZN1290:PA12 | URBAN | Planned |  | 1 | 20 | 1.376e-05 | 6.8798e-05 | N
01/04/2017 | 08:00 | ZN1290:PA12 | URBAN | Planned |  | 1 | 10 | 6.8798e-06 | 6.8798e-05 | N
01/04/2017 | 17:15 | ZN14892:PA8 | SHORT RURAL | Planned |  | 1 | 1,840 | 0.0081937 | 0.00044531 | N
01/04/2017 | 18:30 | ZN167:PA2 | URBAN | Planned |  | 43 | 405 | 0.011981 | 0.0029583 | N
02/04/2017 | 07:40 | ZN2196:PA10 | URBAN | Planned |  | 6 | 243 | 0.0010032 | 0.00041284 | N
02/04/2017 | 21:00 | ZN12580:PA8 | URBAN | Planned |  | 12 | 480 | 0.0039633 | 0.00082568 | N
03/04/2017 | 00:30 | ZN12580:PA2 | URBAN | Planned |  | 2 | 105 | 0.00014449 | 0.00013761 | N
03/04/2017 | 08:55 | ZN2835:PA9 | URBAN | Planned |  | 60 | 210 | 0.0086696 | 0.0041284 | N
04/04/2017 | 07:00 | ZN931:PA25 | URBAN | Planned |  | 84 | 540 | 0.031211 | 0.0057798 | N
04/04/2017 | 07:45 | ZN10994:PA11 | URBAN | Planned |  | 40 | 465 | 0.012798 | 0.0027523 | N
04/04/2017 | 08:35 | ZN12570:PA39 | URBAN | Planned |  | 47 | 355 | 0.01148 | 0.0032339 | N
04/04/2017 | 08:20 | ZN13000:PA1 | URBAN | Planned |  | 9 | 470 | 0.0029105 | 0.00061926 | N
04/04/2017 | 09:00 | ZN10990:PA5 | URBAN | Planned |  | 72 | 260 | 0.012881 | 0.0049541 | N
04/04/2017 | 10:30 | ZN15013:PA6 | SHORT RURAL | Planned |  | 7 | 210 | 0.0065461 | 0.0031172 | N
04/04/2017 | 09:30 | ZN9900:PA10 | URBAN | Planned |  | 114 | 380 | 0.029807 | 0.007844 | N
04/04/2017 | 21:00 | ZN3155:PA28 | URBAN | Planned |  | 2 | 496 | 0.00068256 | 0.00013761 | N
05/04/2017 | 08:20 | ZN12660:PA14 | SHORT RURAL | Planned |  | 23 | 475 | 0.04865 | 0.010242 | N
05/04/2017 | 08:18 | ZN12660:PA14 | SHORT RURAL | Planned |  | 152 | 452 | 0.30595 | 0.067687 | N
05/04/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 64 | 420 | 0.018495 | 0.0044036 | N
05/04/2017 | 09:30 | ZN12580:PA14 | URBAN | Planned |  | 1 | 10,200 | 0.0070183 | 6.8807e-05 | N
06/04/2017 | 07:47 | ZN1600:PA23ABC | CBD | Planned |  | 1 | 628 | 0.0202 | 0.0032166 | N
05/04/2017 | 09:30 | ZN12580:PA14 | URBAN | Planned |  | 1 | 18,960 | 0.013046 | 6.8807e-05 | N
06/04/2017 | 08:10 | ZN12640:PA10 | URBAN | Planned |  | 68 | 460 | 0.021523 | 0.0046789 | N
06/04/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 64 | 420 | 0.018495 | 0.0044036 | N
06/04/2017 | 10:15 | ZN116:PA85 | URBAN | Planned |  | 1 | 60 | 4.1284e-05 | 6.8807e-05 | N
07/04/2017 | 05:00 | ZN8000:PA28 | URBAN | Planned |  | 1 | 120 | 8.2697e-05 | 6.8914e-05 | N
08/04/2017 | 07:00 | ZN8700:PA65 66GHJ | CBD | Planned |  | 12 | 240 | 0.092619 | 0.038591 | N
08/04/2017 | 09:00 | ZN2835:PA36 | URBAN | Planned |  | 1 | 380 | 0.00026137 | 6.8781e-05 | N
08/04/2017 | 08:30 | ZN2635:PA47 | URBAN | Planned |  | 9 | 590 | 0.0036522 | 0.00061902 | N
08/04/2017 | 08:00 | ZN384:PA22 | URBAN | Planned |  | 85 | 180 | 0.010523 | 0.0058463 | N
08/04/2017 | 08:30 | ZN384:PA22 | URBAN | Planned |  | 64 | 60 | 0.0026412 | 0.004402 | N
08/04/2017 | 12:20 | ZN35900:PA10 | URBAN | Planned |  | 1 | 191 | 0.00013137 | 6.8781e-05 | N
08/04/2017 | 17:30 | ZN3288:PA41 42ABC | CBD | Planned |  | 41 | 955 | 1.2592 | 0.13185 | N
09/04/2017 | 12:30 | ZN3472:PA35 | URBAN | Planned |  | 4 | 240 | 0.00066029 | 0.00027512 | N
09/04/2017 | 07:40 | ZN8100:PA10 | URBAN | Planned |  | 2 | 455 | 0.0006259 | 0.00013756 | N
09/04/2017 | 19:30 | ZN1193:PA26 | URBAN | Planned |  | 63 | 570 | 0.024699 | 0.0043331 | N
09/04/2017 | 22:00 | ZN630:PA9 | URBAN | Planned |  | 1 | 375 | 0.00025793 | 6.878e-05 | N
10/04/2017 | 08:10 | ZN9900:PA12 | URBAN | Planned |  | 13 | 220 | 0.0019671 | 0.00089414 | N
10/04/2017 | 08:45 | ZN12690:PA16 | SHORT RURAL | Planned |  | 28 | 290 | 0.036162 | 0.01247 | N
10/04/2017 | 09:57 | ZN14144:PA2 | SHORT RURAL | Planned |  | 84 | 333 | 0.12457 | 0.037409 | N
10/04/2017 | 10:03 | ZN9900:PA20 | URBAN | Planned |  | 30 | 171 | 0.0035284 | 0.0020634 | N
10/04/2017 | 20:30 | ZN9900:PA2 | URBAN | Planned |  | 28 | 540 | 0.0104 | 0.0019258 | N
11/04/2017 | 08:20 | ZN72:PA30 | URBAN | Planned |  | 89 | 220 | 0.013467 | 0.0061214 | N
11/04/2017 | 08:00 | ZN10994:PA3 | URBAN | Planned |  | 30 | 420 | 0.0086663 | 0.0020634 | N
11/04/2017 | 09:30 | ZN12600:PA11 | URBAN | Planned |  | 71 | 315 | 0.015383 | 0.0048834 | N
11/04/2017 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 87 | 540 | 0.20922 | 0.038745 | N
11/04/2017 | 21:00 | ZN3155:PA28 | URBAN | Planned |  | 2 | 480 | 0.00066029 | 0.00013756 | N
12/04/2017 | 08:00 | ZN1193:PA28 | URBAN | Planned |  | 50 | 345 | 0.011866 | 0.0034393 | N
12/04/2017 | 08:02 | ZN12690:PA7 | SHORT RURAL | Planned |  | 17 | 481 | 0.036419 | 0.0075716 | N
12/04/2017 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 26 | 390 | 0.045162 | 0.01158 | N
12/04/2017 | 09:20 | ZN35370:PA10 | SHORT RURAL | Planned |  | 32 | 255 | 0.036344 | 0.014252 | N
12/04/2017 | 09:25 | ZN12630:PA3 | SHORT RURAL | Planned |  | 2 | 350 | 0.0031177 | 0.00089077 | N
12/04/2017 | 09:00 | ZN12640:PA13 | SHORT RURAL | Planned |  | 49 | 390 | 0.085113 | 0.021824 | N
12/04/2017 | 13:00 | ZN2835:PA19 | URBAN | Planned |  | 1 | 180 | 0.00012382 | 6.8787e-05 | N
13/04/2017 | 09:00 | ZN2602:PA28 | URBAN | Planned |  | 3 | 480 | 0.00099054 | 0.00020636 | N
13/04/2017 | 08:10 | ZN12600:PA13 | SHORT RURAL | Planned |  | 24 | 385 | 0.041157 | 0.01069 | N
13/04/2017 | 09:00 | ZN12580:PA4 | URBAN | Planned |  | 12 | 420 | 0.0034669 | 0.00082545 | N
13/04/2017 | 08:30 | ZN9900:PA21 | URBAN | Planned |  | 24 | 510 | 0.0084196 | 0.0016509 | N
13/04/2017 | 17:30 | ZN15001:PA6 | URBAN | Planned |  | 27 | 360 | 0.0066862 | 0.0018573 | N
13/04/2017 | 17:30 | ZN15001:PA18 | URBAN | Planned |  | 8 | 360 | 0.0019811 | 0.0005503 | N
14/04/2017 | 07:30 | ZN263:PA35 37DEF | CBD | Planned |  | 8 | 3,480 | 0.89506 | 0.02572 | N
14/04/2017 | 09:40 | ZN931:PA3 | URBAN | Planned |  | 63 | 683 | 0.029608 | 0.0043349 | N
18/04/2017 | 04:30 | ZN35600:PA4 | URBAN | Planned |  | 1 | 300 | 0.0002063 | 6.8766e-05 | N
18/04/2017 | 09:25 | ZN116:PA74 | URBAN | Planned |  | 46 | 260 | 0.0082244 | 0.0031632 | N
18/04/2017 | 07:30 | ZN711:PA32 | URBAN | Planned |  | 7 | 705 | 0.0033936 | 0.00048136 | N
18/04/2017 | 08:15 | ZN10995:PA1 | URBAN | Planned |  | 66 | 255 | 0.011573 | 0.0045386 | N
18/04/2017 | 11:30 | ZN12580:PA14 | URBAN | Planned |  | 1 | 120 | 8.2519e-05 | 6.8766e-05 | N
18/04/2017 | 19:45 | ZN187:PA7 | URBAN | Planned |  | 2 | 465 | 0.00063952 | 0.00013753 | N
18/04/2017 | 21:00 | ZN36800:PA54 | URBAN | Planned |  | 19 | 480 | 0.0062715 | 0.0013066 | N
19/04/2017 | 06:00 | ZN35800:PA1 | URBAN | Planned |  | 102 | 720 | 0.050505 | 0.0070146 | N
19/04/2017 | 07:00 | ZN12690:PA4 | URBAN | Planned |  | 2 | 1,710 | 0.0023519 | 0.00013754 | N
19/04/2017 | 08:20 | ZN12630:PA10 | SHORT RURAL | Planned |  | 11 | 240 | 0.011756 | 0.0048981 | N
19/04/2017 | 09:00 | ZN2835:PA10 | URBAN | Planned |  | 2 | 180 | 0.00024757 | 0.00013754 | N
18/05/2017 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 24 | 380 | 0.040517 | 0.010662 | N
18/05/2017 | 08:00 | 227:13020 | SHORT RURAL | Planned |  | 58 | 440 | 0.11338 | 0.025768 | N
18/05/2017 | 08:05 | 233:82819 | SHORT RURAL | Planned |  | 20 | 280 | 0.024879 | 0.0088854 | N
18/05/2017 | 09:50 | 508:82574 | SHORT RURAL | Planned |  | 1 | 70 | 0.00031099 | 0.00044427 | N
18/05/2017 | 09:10 | 508:82574 | SHORT RURAL | Planned |  | 3 | 80 | 0.0010662 | 0.0013328 | N
18/05/2017 | 09:10 | 508:82574 | SHORT RURAL | Planned |  | 2 | 350 | 0.0031099 | 0.00088854 | N
18/05/2017 | 09:10 | 508:82574 | SHORT RURAL | Planned |  | 1 | 335 | 0.0014883 | 0.00044427 | N
18/05/2017 | 09:50 | 508:82574 | SHORT RURAL | Planned |  | 4 | 208 | 0.0036963 | 0.0017771 | N
18/05/2017 | 08:30 | 512:48046 | SHORT RURAL | Planned |  | 4 | 390 | 0.0069306 | 0.0017771 | N
18/05/2017 | 10:30 | 508:82574 | SHORT RURAL | Planned |  | 1 | 225 | 0.0009996 | 0.00044427 | N
18/05/2017 | 12:50 | 508:82574 | SHORT RURAL | Planned |  | 1 | 60 | 0.00026656 | 0.00044427 | N
18/05/2017 | 08:40 | 513:48050 | SHORT RURAL | Planned |  | 7 | 155 | 0.0048203 | 0.0031099 | N
18/05/2017 | 08:15 | 516:48066 | SHORT RURAL | Planned |  | 4 | 405 | 0.0071972 | 0.0017771 | N
18/05/2017 | 12:45 | 515:35193 | SHORT RURAL | Planned |  | 2 | 77 | 0.00068417 | 0.00088854 | N
19/05/2017 | 08:40 | 235:2120 | SHORT RURAL | Planned |  | 50 | 140 | 0.031332 | 0.02238 | N
19/05/2017 | 09:25 | 807:74180 | SHORT RURAL | Planned |  | 8 | 145 | 0.0051922 | 0.0035808 | N
19/05/2017 | 08:44 | 223:14395 | SHORT RURAL | Planned |  | 2 | 246 | 0.0022022 | 0.00089521 | N
19/04/2017 | 10:15 | ZN14892:PA9 | URBAN | Planned |  | 51 | 105 | 0.0036826 | 0.0035073 | N
19/05/2017 | 08:00 | 524:33576 | SHORT RURAL | Planned |  | 1 | 190 | 0.00085045 | 0.00044761 | N
19/04/2017 | 19:00 | ZN12650:PA20 | URBAN | Planned |  | 233 | 610 | 0.097743 | 0.016023 | N
19/05/2017 | 08:30 | 504:48031 | SHORT RURAL | Planned |  | 2 | 355 | 0.003178 | 0.00089521 | N
19/04/2017 | 20:30 | ZN3672:PA23 | URBAN | Planned |  | 6 | 540 | 0.0022282 | 0.00041262 | N
20/04/2017 | 07:00 | ZN931:PA9 | URBAN | Planned |  | 32 | 450 | 0.0099071 | 0.0022016 | N
19/05/2017 | 08:30 | 229:34995 | SHORT RURAL | Planned |  | 6 | 380 | 0.010205 | 0.0026856 | N
20/04/2017 | 09:20 | ZN12650:PA1 | SHORT RURAL | Planned |  | 13 | 380 | 0.02194 | 0.0057737 | N
19/05/2017 | 08:00 | 507:80932 | SHORT RURAL | Planned |  | 30 | 420 | 0.056398 | 0.013428 | N
19/05/2017 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 11 | 400 | 0.019695 | 0.0049237 | N
20/04/2017 | 08:25 | ZN12640:PA13 | SHORT RURAL | Planned |  | 27 | 445 | 0.053362 | 0.011991 | N
20/04/2017 | 22:30 | ZN12580:PA7 | URBAN | Planned |  | 4 | 330 | 0.00090815 | 0.0002752 | N
21/04/2017 | 06:30 | ZN10990:PA5 | URBAN | Planned |  | 1 | 330 | 0.00022704 | 6.88e-05 | N
21/04/2017 | 07:45 | ZN9900:PA19 | URBAN | Planned |  | 1 | 510 | 0.00035088 | 6.88e-05 | N
21/05/2017 | 08:30 | 513:48058 | URBAN | Planned |  | 98 | 450 | 0.030307 | 0.0067348 | N
21/04/2017 | 08:05 | ZN12650:PA1 | SHORT RURAL | Planned |  | 18 | 470 | 0.037574 | 0.0079945 | N
21/04/2017 | 08:40 | ZN1290:PA12 | URBAN | Planned |  | 164 | 285 | 0.032157 | 0.011283 | N
21/04/2017 | 21:30 | ZN3155:PA16 | URBAN | Planned |  | 140 | 470 | 0.045271 | 0.0096321 | N
22/04/2017 | 07:40 | ZN10990:PA8 | URBAN | Planned |  | 51 | 560 | 0.019642 | 0.0035075 | N
22/04/2017 | 08:50 | ZN4990:PA51 52GHJ | CBD | Planned |  | 1 | 75 | 0.0024116 | 0.0032154 | N
23/04/2017 | 08:00 | ZN2196:PA10 | URBAN | Planned |  | 2 | 515 | 0.00070839 | 0.00013755 | N
23/04/2017 | 18:00 | ZN630:PA22 | URBAN | Planned |  | 13 | 465 | 0.0041575 | 0.00089408 | N
24/04/2017 | 07:30 | ZN15013:PA4 | URBAN | Planned |  | 1 | 530 | 0.00036451 | 6.8776e-05 | N
24/04/2017 | 17:30 | ZN15001:PA10 | URBAN | Planned |  | 13 | 360 | 0.0032187 | 0.00089408 | N
24/04/2017 | 17:30 | ZN15001:PA18 | URBAN | Planned |  | 8 | 360 | 0.0019807 | 0.0005502 | N
26/04/2017 | 09:18 | ZN1068:PA21 | URBAN | Planned |  | 89 | 282 | 0.017262 | 0.0061211 | N
26/04/2017 | 08:15 | ZN12690:PA7 | SHORT RURAL | Planned |  | 1 | 490 | 0.0021756 | 0.00044399 | N
26/04/2017 | 10:10 | ZN14891:PA12 | SHORT RURAL | Planned |  | 9 | 330 | 0.013187 | 0.0039959 | N
26/04/2017 | 08:00 | ZN1610:PA2 | URBAN | Planned |  | 1 | 120 | 8.2532e-05 | 6.8776e-05 | N
26/04/2017 | 23:00 | ZN12690:PA14 | URBAN | Planned |  | 33 | 1,080 | 0.024512 | 0.0022696 | N
27/04/2017 | 02:00 | ZN10993:PA26 | URBAN | Planned |  | 5 | 20 | 6.876e-05 | 0.0003438 | N
27/04/2017 | 05:05 | ZN35800:PA19 | URBAN | Planned |  | 1 | 10 | 6.876e-06 | 6.876e-05 | N
27/04/2017 | 07:00 | ZN874:PA4 | URBAN | Planned |  | 38 | 510 | 0.013326 | 0.0026129 | N
27/04/2017 | 07:30 | ZN965:PA38 | URBAN | Planned |  | 70 | 570 | 0.027435 | 0.0048132 | N
27/04/2017 | 07:30 | ZN15014:PA5 | URBAN | Planned |  | 6 | 450 | 0.0018565 | 0.00041256 | N
27/04/2017 | 08:24 | ZN187:PA8 | URBAN | Planned |  | 232 | 416 | 0.066362 | 0.015952 | N
27/04/2017 | 09:40 | ZN14892:PA9 | URBAN | Planned |  | 53 | 140 | 0.005102 | 0.0036443 | N
27/04/2017 | 23:20 | ZN36300:PA8 | URBAN | Planned |  | 22 | 175 | 0.0026473 | 0.0015127 | N
28/04/2017 | 09:50 | ZN14144:PA2 | SHORT RURAL | Planned |  | 1 | 330 | 0.0014649 | 0.0004439 | N
28/04/2017 | 08:50 | ZN12600:PA13 | SHORT RURAL | Planned |  | 24 | 295 | 0.031428 | 0.010654 | N
28/04/2017 | 09:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 108 | 495 | 0.23731 | 0.047942 | N
28/04/2017 | 09:40 | ZN12640:PA13 | SHORT RURAL | Planned |  | 15 | 250 | 0.016646 | 0.0066586 | N
28/04/2017 | 08:10 | ZN12570:PA37 | SHORT RURAL | Planned |  | 5 | 540 | 0.011985 | 0.0022195 | N
28/04/2017 | 13:00 | ZN12640:PA13 | SHORT RURAL | Planned |  | 2 | 130 | 0.0011542 | 0.00088781 | N
28/04/2017 | 20:00 | ZN35400:PA59 | URBAN | Planned |  | 92 | 2,880 | 0.18219 | 0.006326 | N
28/04/2017 | 19:00 | ZN36300:PA17 | URBAN | Planned |  | 20 | 540 | 0.0074262 | 0.0013752 | N
28/04/2017 | 21:20 | ZN9037:PA10 | URBAN | Planned |  | 33 | 310 | 0.0070343 | 0.0022691 | N
28/04/2017 | 23:00 | ZN3288:PA45 46KLM | CBD | Planned |  | 41 | 390 | 0.51416 | 0.13184 | N
29/04/2017 | 07:30 | ZN2466:PA11 | URBAN | Planned |  | 2 | 540 | 0.00074264 | 0.00013753 | N
29/04/2017 | 12:30 | ZN340:PA10 | URBAN | Planned |  | 16 | 20 | 0.00022004 | 0.0011002 | N
30/04/2017 | 08:15 | ZN12650:PA17 | URBAN | Planned |  | 1 | 420 | 0.0002888 | 6.8762e-05 | N
30/04/2017 | 09:45 | ZN1290:PA9 | URBAN | Planned |  | 1 | 355 | 0.00024411 | 6.8762e-05 | N
22/05/2017 | 10:30 | 509:33395 | LONG RURAL | Planned |  | 6 | 165 | 0.35319 | 0.21406 | N
22/05/2017 | 08:00 | 222:33601 | SHORT RURAL | Planned |  | 70 | 720 | 0.22559 | 0.031332 | N
22/05/2017 | 08:10 | 210:83465 | URBAN | Planned |  | 160 | 160 | 0.017593 | 0.010996 | N
22/05/2017 | 08:40 | 526:34639 | SHORT RURAL | Planned |  | 16 | 380 | 0.027214 | 0.0071617 | N
22/05/2017 | 07:00 | 508:82579 | SHORT RURAL | Planned |  | 7 | 470 | 0.014726 | 0.0031332 | N
22/05/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 1 | 50 | 0.0002238 | 0.00044761 | N
22/05/2017 | 12:45 | 520:48172 | SHORT RURAL | Planned |  | 1 | 105 | 0.00046999 | 0.00044761 | N
23/05/2017 | 09:30 | 243:80081 | SHORT RURAL | Planned |  | 200 | 314 | 0.2811 | 0.089521 | N
23/05/2017 | 08:34 | 509:33395 | LONG RURAL | Planned |  | 41 | 436 | 6.3775 | 1.4627 | N
23/05/2017 | 08:06 | 526:34639 | SHORT RURAL | Planned |  | 78 | 444 | 0.15501 | 0.034913 | N
23/05/2017 | 08:55 | 526:34639 | SHORT RURAL | Planned |  | 51 | 395 | 0.09017 | 0.022828 | N
23/05/2017 | 08:30 | 532:83312 | URBAN | Planned |  | 206 | 550 | 0.077863 | 0.014157 | N
23/05/2017 | 08:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 315 | 0.11238 | 0.035676 | N
23/05/2017 | 08:30 | 516:48066 | SHORT RURAL | Planned |  | 22 | 57 | 0.005613 | 0.0098473 | N
23/05/2017 | 08:45 | 813:89055 | SHORT RURAL | Planned |  | 6 | 335 | 0.0089969 | 0.0026856 | N
23/05/2017 | 09:45 | 806:82662 | SHORT RURAL | Planned |  | 1 | 95 | 0.00042523 | 0.00044761 | N
23/05/2017 | 08:30 | 812:19072 | SHORT RURAL | Planned |  | 1 | 95 | 0.00042523 | 0.00044761 | N
23/05/2017 | 10:35 | 812:19072 | SHORT RURAL | Planned |  | 1 | 75 | 0.0003357 | 0.00044761 | N
24/05/2017 | 08:40 | 807:74184 | SHORT RURAL | Planned |  | 22 | 360 | 0.03545 | 0.0098473 | N
24/05/2017 | 09:45 | 230:81432 | SHORT RURAL | Planned |  | 25 | 100 | 0.01119 | 0.01119 | N
24/05/2017 | 08:00 | 243:80083 | SHORT RURAL | Planned |  | 11 | 440 | 0.021664 | 0.0049237 | N
24/05/2017 | 08:30 | 243:80074 | SHORT RURAL | Planned |  | 1 | 325 | 0.0014547 | 0.00044761 | N
24/05/2017 | 13:14 | 258:80784 | URBAN | Planned |  | 97 | 46 | 0.0030664 | 0.0066661 | N
24/05/2017 | 09:15 | 508:82574 | SHORT RURAL | Planned |  | 3 | 90 | 0.0012085 | 0.0013428 | N
24/05/2017 | 11:35 | 508:82574 | SHORT RURAL | Planned |  | 1 | 55 | 0.00024618 | 0.00044761 | N
24/05/2017 | 12:15 | 264:81244 | SHORT RURAL | Planned |  | 8 | 81 | 0.0029005 | 0.0035808 | N
24/05/2017 | 10:35 | 264:81240 | SHORT RURAL | Planned |  | 1 | 217 | 0.0009713 | 0.00044761 | N
24/05/2017 | 08:00 | 515:35197 | LONG RURAL | Planned |  | 22 | 420 | 3.2965 | 0.78487 | N
24/05/2017 | 09:00 | 813:89055 | SHORT RURAL | Planned |  | 11 | 160 | 0.0078779 | 0.0049237 | N
26/05/2017 | 08:45 | 814:82289 | SHORT RURAL | Planned |  | 19 | 275 | 0.023387 | 0.0085045 | Y
28/05/2017 | 08:38 | 810:74050 | SHORT RURAL | Planned |  | 138 | 313 | 0.19334 | 0.06177 | N
28/05/2017 | 08:38 | 810:74054 | LONG RURAL | Planned |  | 322 | 313 | 35.9565 | 11.4877 | N
28/05/2017 | 08:38 | 810:74058 | SHORT RURAL | Planned |  | 197 | 313 | 0.276 | 0.088178 | N
28/05/2017 | 08:38 | 810:74062 | SHORT RURAL | Planned |  | 563 | 313 | 0.78877 | 0.252 | N
25/05/2017 | 08:30 | 243:80075 | SHORT RURAL | Planned |  | 1 | 420 | 0.0018799 | 0.00044761 | N
25/05/2017 | 07:30 | 243:80083 | SHORT RURAL | Planned |  | 53 | 494 | 0.11719 | 0.023723 | N
25/05/2017 | 22:28 | 243:80074 | SHORT RURAL | Planned |  | 38 | 72 | 0.012246 | 0.017009 | N
26/05/2017 | 08:00 | 225:13446 | URBAN | Planned |  | 59 | 300 | 0.012164 | 0.0040546 | Y
26/05/2017 | 18:00 | 203:8089 | URBAN | Planned |  | 15 | 300 | 0.0030925 | 0.0010308 | Y
25/05/2017 | 08:10 | 508:82579 | SHORT RURAL | Planned |  | 7 | 470 | 0.014726 | 0.0031332 | N
25/05/2017 | 08:05 | 264:81240 | SHORT RURAL | Planned |  | 10 | 415 | 0.018576 | 0.0044761 | N
25/05/2017 | 08:47 | 504:48031 | SHORT RURAL | Planned |  | 53 | 408 | 0.09679 | 0.023723 | N
25/05/2017 | 11:00 | 509:33395 | LONG RURAL | Planned |  | 2 | 105 | 0.07492 | 0.071352 | N
26/05/2017 | 08:45 | 508:82574 | SHORT RURAL | Planned |  | 1 | 85 | 0.00038046 | 0.00044761 | Y
26/05/2017 | 09:15 | 509:33399 | SHORT RURAL | Planned |  | 6 | 40 | 0.0010743 | 0.0026856 | Y
26/05/2017 | 09:55 | 509:33395 | LONG RURAL | Planned |  | 1 | 120 | 0.042811 | 0.035676 | Y
26/05/2017 | 09:15 | 508:82579 | SHORT RURAL | Planned |  | 1 | 280 | 0.0012533 | 0.00044761 | Y
26/05/2017 | 11:30 | 509:33399 | SHORT RURAL | Planned |  | 1 | 35 | 0.00015666 | 0.00044761 | Y
26/05/2017 | 11:30 | 508:82574 | SHORT RURAL | Planned |  | 1 | 75 | 0.0003357 | 0.00044761 | Y
25/05/2017 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 1 | 85 | 0.00038046 | 0.00044761 | N
25/05/2017 | 08:40 | 807:74184 | SHORT RURAL | Planned |  | 22 | 285 | 0.028065 | 0.0098473 | N
25/05/2017 | 12:50 | 513:48056 | SHORT RURAL | Planned |  | 5 | 135 | 0.0030213 | 0.002238 | N
26/05/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 2 | 90 | 0.00080569 | 0.00089521 | Y
26/05/2017 | 08:35 | 802:82220 | SHORT RURAL | Planned |  | 1 | 130 | 0.00058189 | 0.00044761 | Y
26/05/2017 | 12:45 | 520:48172 | SHORT RURAL | Planned |  | 3 | 85 | 0.0011414 | 0.0013428 | Y
29/05/2017 | 08:37 | 221:11899 | SHORT RURAL | Planned |  | 1,245 | 369 | 2.0563 | 0.55727 | N
29/05/2017 | 08:35 | 239:82132 | URBAN | Planned |  | 117 | 415 | 0.033368 | 0.0080405 | N
29/05/2017 | 08:56 | 508:82574 | SHORT RURAL | Planned |  | 5 | 80 | 0.0017904 | 0.002238 | N
29/05/2017 | 09:10 | 264:81240 | SHORT RURAL | Planned |  | 5 | 395 | 0.0088402 | 0.002238 | N
29/05/2017 | 11:00 | 508:82574 | SHORT RURAL | Planned |  | 1 | 222 | 0.00099368 | 0.00044761 | N
29/05/2017 | 08:30 | 504:48031 | SHORT RURAL | Planned |  | 10 | 211 | 0.0094445 | 0.0044761 | N
29/05/2017 | 09:20 | 509:33395 | LONG RURAL | Planned |  | 1 | 220 | 0.078487 | 0.035676 | N
29/05/2017 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 6 | 110 | 0.0029542 | 0.0026856 | N
29/05/2017 | 08:30 | 814:82291 | SHORT RURAL | Planned |  | 23 | 320 | 0.032944 | 0.010295 | N
29/05/2017 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 6 | 200 | 0.42811 | 0.21406 | N
29/05/2017 | 12:45 | 515:35193 | SHORT RURAL | Planned |  | 2 | 75 | 0.00067141 | 0.00089521 | N
30/05/2017 | 08:50 | 225:13446 | URBAN | Planned |  | 232 | 310 | 0.049425 | 0.015943 | N
30/05/2017 | 08:00 | 257:82006 | URBAN | Planned |  | 3 | 225 | 0.00046387 | 0.00020617 | N
30/05/2017 | 08:15 | 524:33576 | SHORT RURAL | Planned |  | 20 | 420 | 0.037599 | 0.0089521 | N
30/05/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 2 | 70 | 0.00062664 | 0.00089521 | N
30/05/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 1 | 105 | 0.00046998 | 0.0004476 | N
30/05/2017 | 08:00 | 514:18137 | SHORT RURAL | Planned |  | 31 | 275 | 0.038158 | 0.013876 | N
30/05/2017 | 12:45 | 520:48172 | SHORT RURAL | Planned |  | 3 | 55 | 0.00073855 | 0.0013428 | N
30/05/2017 | 12:45 | 520:48172 | SHORT RURAL | Planned |  | 1 | 90 | 0.00040284 | 0.0004476 | N
31/05/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 2 | 110 | 0.00098473 | 0.00089521 | N
31/05/2017 | 08:05 | 515:35197 | LONG RURAL | Planned |  | 22 | 415 | 3.2572 | 0.78487 | N
31/05/2017 | 08:28 | 243:80075 | SHORT RURAL | Planned |  | 6 | 413 | 0.011092 | 0.0026856 | N
31/05/2017 | 08:20 | 511:29878 | SHORT RURAL | Planned |  | 6 | 360 | 0.0096682 | 0.0026856 | N
31/05/2017 | 08:20 | 502:48004 | URBAN | Planned |  | 40 | 370 | 0.010171 | 0.0027489 | N
31/05/2017 | 08:45 | 507:80925 | SHORT RURAL | Planned |  | 10 | 420 | 0.018799 | 0.004476 | N
31/05/2017 | 08:46 | 502:48010 | SHORT RURAL | Planned |  | 6 | 364 | 0.0097757 | 0.0026856 | N
31/05/2017 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 1 | 95 | 0.033892 | 0.035676 | N
31/05/2017 | 12:45 | 520:48172 | SHORT RURAL | Planned |  | 5 | 110 | 0.0024618 | 0.002238 | N
31/05/2017 | 12:30 | 509:33395 | LONG RURAL | Planned |  | 3 | 55 | 0.058866 | 0.10703 | N
31/05/2017 | 09:00 | 813:89062 | SHORT RURAL | Planned |  | 2 | 80 | 0.00071617 | 0.00089521 | N
01/06/2017 | 08:05 | 258:80787 | URBAN | Planned |  | 2 | 312 | 0.00042882 | 0.00013744 | N
01/06/2017 | 08:00 | 243:80083 | SHORT RURAL | Planned |  | 8 | 435 | 0.015577 | 0.0035808 | N
01/06/2017 | 11:00 | 243:80083 | SHORT RURAL | Planned |  | 3 | 265 | 0.0035584 | 0.0013428 | N
01/06/2017 | 08:30 | 511:29876 | SHORT RURAL | Planned |  | 50 | 380 | 0.085045 | 0.02238 | N
01/06/2017 | 08:15 | 526:34639 | SHORT RURAL | Planned |  | 16 | 405 | 0.029005 | 0.0071617 | N
01/06/2017 | 08:40 | 508:82574 | SHORT RURAL | Planned |  | 13 | 275 | 0.016002 | 0.0058188 | N
01/06/2017 | 08:15 | 807:74184 | SHORT RURAL | Planned |  | 13 | 430 | 0.025021 | 0.0058188 | N
01/06/2017 | 08:30 | 516:48067 | SHORT RURAL | Planned |  | 43 | 395 | 0.076025 | 0.019247 | N
01/06/2017 | 08:30 | 513:48052 | URBAN | Planned |  | 79 | 315 | 0.017101 | 0.005429 | N
03/06/2017 | 07:00 | 240:34846 | URBAN | Planned |  | 3 | 375 | 0.00077312 | 0.00020617 | N
03/06/2017 | 07:30 | 202:34261 | URBAN | Planned |  | 1 | 840 | 0.00057726 | 6.8722e-05 | N
02/06/2017 | 09:00 | 508:82574 | SHORT RURAL | Planned |  | 2 | 75 | 0.00067141 | 0.00089521 | N
02/06/2017 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 19 | 395 | 2.6775 | 0.67785 | N
02/06/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 1 | 50 | 0.0002238 | 0.0004476 | N
02/06/2017 | 09:35 | 520:48172 | SHORT RURAL | Planned |  | 1 | 65 | 0.00029094 | 0.0004476 | N
02/06/2017 | 11:30 | 810:74062 | SHORT RURAL | Planned |  | 3 | 30 | 0.00040284 | 0.0013428 | N
02/06/2017 | 08:30 | 513:48050 | SHORT RURAL | Planned |  | 12 | 255 | 0.013697 | 0.0053712 | N
02/06/2017 | 13:10 | 513:48059 | SHORT RURAL | Planned |  | 3 | 57 | 0.0007654 | 0.0013428 | N
03/06/2017 | 08:10 | 813:89061 | LONG RURAL | Planned |  | 9 | 250 | 0.80271 | 0.32108 | N
05/06/2017 | 20:39 | ZN129:PA52 | URBAN | Planned |  | 1 | 547 | 0.00037594 | 6.8722e-05 | N
05/06/2017 | 08:00 | 507:80922 | SHORT RURAL | Planned |  | 26 | 420 | 0.048878 | 0.011638 | N
05/06/2017 | 07:50 | 213:33777 | SHORT RURAL | Planned |  | 1 | 272 | 0.0012175 | 0.0004476 | N
05/06/2017 | 08:00 | 227:13015 | SHORT RURAL | Planned |  | 93 | 473 | 0.1969 | 0.041627 | N
05/06/2017 | 08:35 | 243:80078 | SHORT RURAL | Planned |  | 95 | 415 | 0.17647 | 0.042522 | N
06/06/2017 | 09:00 | 229:34995 | SHORT RURAL | Planned |  | 38 | 340 | 0.05783 | 0.017009 | N
06/06/2017 | 08:30 | 508:82579 | SHORT RURAL | Planned |  | 248 | 211 | 0.23422 | 0.11101 | N
06/06/2017 | 08:40 | 528:83020 | SHORT RURAL | Planned |  | 194 | 270 | 0.23445 | 0.086835 | N
06/06/2017 | 08:45 | 520:48172 | SHORT RURAL | Planned |  | 52 | 215 | 0.050042 | 0.023275 | N
06/06/2017 | 08:25 | 243:80083 | SHORT RURAL | Planned |  | 6 | 385 | 0.01034 | 0.0026856 | N
06/06/2017 | 08:20 | 511:29878 | SHORT RURAL | Planned |  | 5 | 320 | 0.0071617 | 0.002238 | N
06/06/2017 | 11:00 | 508:82574 | SHORT RURAL | Planned |  | 4 | 46 | 0.00082359 | 0.0017904 | N
06/06/2017 | 09:50 | 524:33570 | SHORT RURAL | Planned |  | 1 | 30 | 0.00013428 | 0.0004476 | N
06/06/2017 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 1 | 350 | 0.12487 | 0.035676 | N
06/06/2017 | 22:05 | 528:83022 | URBAN | Planned |  | 12 | 265 | 0.0021853 | 0.00082466 | N
06/06/2017 | 22:00 | 812:19066 | SHORT RURAL | Planned |  | 2 | 150 | 0.0013428 | 0.00089521 | N
07/06/2017 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 34 | 310 | 0.047177 | 0.015219 | N
07/06/2017 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 210 | 490 | 0.46058 | 0.093997 | N
05/06/2017 | 14:00 | 240:34843 | URBAN | Planned |  | 2 | 2,805 | 0.0038553 | 0.00013744 | N
08/06/2017 | 08:40 | 511:29877 | SHORT RURAL | Planned |  | 25 | 380 | 0.042522 | 0.01119 | N
08/06/2017 | 08:30 | 512:48049 | SHORT RURAL | Planned |  | 15 | 215 | 0.014435 | 0.0067141 | N
08/06/2017 | 09:45 | 512:48049 | SHORT RURAL | Planned |  | 26 | 142 | 0.016526 | 0.011638 | N
08/06/2017 | 09:00 | 502:48004 | URBAN | Planned |  | 41 | 385 | 0.010848 | 0.0028176 | N
08/06/2017 | 08:30 | 225:13446 | URBAN | Planned |  | 1 | 390 | 0.00026801 | 6.8722e-05 | N
09/06/2017 | 18:15 | 202:34231 37 42 | URBAN | Planned |  | 3 | 225 | 0.00046387 | 0.00020617 | N
08/06/2017 | 09:00 | 508:82574 | SHORT RURAL | Planned |  | 1 | 85 | 0.00038046 | 0.0004476 | N
08/06/2017 | 10:12 | 508:82574 | SHORT RURAL | Planned |  | 1 | 163 | 0.00072959 | 0.0004476 | N
08/06/2017 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 24 | 362 | 0.038888 | 0.010742 | N
08/06/2017 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 2 | 142 | 0.0012712 | 0.00089521 | N
08/06/2017 | 09:40 | 806:82662 | SHORT RURAL | Planned |  | 7 | 45 | 0.00141 | 0.0031332 | N
08/06/2017 | 12:45 | 513:48059 | SHORT RURAL | Planned |  | 4 | 75 | 0.0013428 | 0.0017904 | N
09/06/2017 | 09:10 | 813:89061 | LONG RURAL | Planned |  | 1 | 75 | 0.026757 | 0.035676 | N
09/06/2017 | 09:45 | 806:82662 | SHORT RURAL | Planned |  | 3 | 35 | 0.00046998 | 0.0013428 | N
09/06/2017 | 10:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 135 | 0.048163 | 0.035676 | N
09/06/2017 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 10 | 230 | 0.010295 | 0.004476 | N
10/06/2017 | 08:30 | 813:89055 | SHORT RURAL | Planned |  | 11 | 180 | 0.0088625 | 0.0049236 | N
13/06/2017 | 08:30 | 504:48031 | SHORT RURAL | Planned |  | 20 | 320 | 0.028647 | 0.0089521 | N
13/06/2017 | 09:10 | 222:33596 | URBAN | Planned |  | 111 | 120 | 0.0091537 | 0.0076281 | N
13/06/2017 | 11:10 | 511:29877 | SHORT RURAL | Planned |  | 1 | 170 | 0.00076093 | 0.0004476 | N
13/06/2017 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 4 | 270 | 0.0048341 | 0.0017904 | N
13/06/2017 | 08:40 | 520:48172 | SHORT RURAL | Planned |  | 1 | 120 | 0.00053712 | 0.0004476 | N
13/06/2017 | 08:45 | 515:35197 | LONG RURAL | Planned |  | 3 | 155 | 0.16589 | 0.10703 | N
13/06/2017 | 12:45 | 520:48172 | SHORT RURAL | Planned |  | 2 | 75 | 0.00067141 | 0.00089521 | N
01/05/2017 | 08:45 | ZN9118:PA12 | URBAN | Planned |  | 1 | 200 | 0.00013752 | 6.8762e-05 | N
01/05/2017 | 07:45 | ZN167:PA20 | URBAN | Planned |  | 3 | 165 | 0.00034037 | 0.00020629 | N
01/05/2017 | 07:30 | ZN965:PA28 | URBAN | Planned |  | 15 | 570 | 0.0058792 | 0.0010314 | N
01/05/2017 | 07:30 | ZN965:PA38 | URBAN | Planned |  | 32 | 570 | 0.012542 | 0.0022004 | N
01/05/2017 | 08:50 | ZN12630:PA13 | SHORT RURAL | Planned |  | 8 | 380 | 0.013494 | 0.0035511 | N
01/05/2017 | 08:00 | ZN12640:PA16 | URBAN | Planned |  | 71 | 480 | 0.023434 | 0.0048821 | N
01/05/2017 | 19:30 | ZN72:PA16 | URBAN | Planned |  | 87 | 735 | 0.04397 | 0.0059823 | N
02/05/2017 | 07:30 | ZN847:PA39 | URBAN | Planned |  | 30 | 540 | 0.01114 | 0.0020629 | N
02/05/2017 | 07:30 | ZN195:PA9 | URBAN | Planned |  | 27 | 420 | 0.0077979 | 0.0018566 | N
02/05/2017 | 08:00 | ZN15014:PA22 | URBAN | Planned |  | 44 | 480 | 0.014523 | 0.0030256 | N
14/06/2017 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 31 | 40 | 0.44238 | 1.106 | N
14/06/2017 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 46 | 208 | 3.4135 | 1.6411 | N
14/06/2017 | 08:30 | 239:82136 | SHORT RURAL | Planned |  | 60 | 385 | 0.1034 | 0.026856 | N
13/06/2017 | 20:25 | 528:83024 | URBAN | Planned |  | 83 | 1,985 | 0.11322 | 0.0057039 | N
14/06/2017 | 08:45 | 507:80925 | SHORT RURAL | Planned |  | 255 | 235 | 0.26823 | 0.11414 | N
14/06/2017 | 15:50 | 265:81648 | SHORT RURAL | Planned |  | 1 | 80 | 0.00035808 | 0.0004476 | N
14/06/2017 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 21 | 190 | 1.4235 | 0.7492 | N
02/05/2017 | 08:55 | ZN12630:PA10 | SHORT RURAL | Planned |  | 10 | 355 | 0.015758 | 0.0044389 | N
02/05/2017 | 10:00 | ZN116:PA73 | URBAN | Planned |  | 1 | 15 | 1.0315e-05 | 6.8765e-05 | N
02/05/2017 | 21:00 | ZN3155:PA28 | URBAN | Planned |  | 69 | 510 | 0.024198 | 0.0047448 | N
02/05/2017 | 22:00 | ZN180:PA16 | URBAN | Planned |  | 49 | 360 | 0.01213 | 0.0033695 | N
03/05/2017 | 05:05 | ZN5868:PA24 | URBAN | Planned |  | 1 | 35 | 2.4068e-05 | 6.8767e-05 | N
03/05/2017 | 07:30 | ZN14143:PA17 | SHORT RURAL | Planned |  | 164 | 510 | 0.37127 | 0.072799 | N
03/05/2017 | 08:25 | ZN35370:PA8 | SHORT RURAL | Planned |  | 45 | 445 | 0.08889 | 0.019975 | N
03/05/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 64 | 420 | 0.018485 | 0.0044011 | N
03/05/2017 | 10:00 | ZN13000:PA11 | SHORT RURAL | Planned |  | 1 | 255 | 0.0011319 | 0.0004439 | N
03/05/2017 | 13:30 | ZN2635:PA62 | URBAN | Planned |  | 1 | 4,200 | 0.0028882 | 6.8767e-05 | N
03/05/2017 | 07:30 | ZN2635:PA39 | URBAN | Planned |  | 2 | 630 | 0.00086647 | 0.00013753 | N
03/05/2017 | 20:00 | ZN847:PA15 | URBAN | Planned |  | 45 | 480 | 0.014854 | 0.0030945 | N
04/05/2017 | 07:38 | ZN167:PA21 | URBAN | Planned |  | 3 | 52 | 0.00010725 | 0.00020626 | N
04/05/2017 | 08:04 | ZN10999:PA22 | URBAN | Planned |  | 67 | 314 | 0.014464 | 0.0046064 | N
04/05/2017 | 08:05 | ZN10990:PA8 | URBAN | Planned |  | 156 | 445 | 0.047728 | 0.010725 | N
04/05/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 64 | 420 | 0.018481 | 0.0044001 | N
04/05/2017 | 09:00 | ZN1788:PA20 | URBAN | Planned |  | 46 | 330 | 0.010437 | 0.0031626 | N
04/05/2017 | 10:20 | ZN12570:PA40 | SHORT RURAL | Planned |  | 35 | 280 | 0.043494 | 0.015534 | N
04/05/2017 | 09:00 | ZN12640:PA1 | SHORT RURAL | Planned |  | 54 | 360 | 0.086278 | 0.023966 | N
04/05/2017 | 20:00 | ZN35400:PA56 | URBAN | Planned |  | 3 | 210 | 0.00043314 | 0.00020626 | N
05/05/2017 | 09:00 | ZN12610:PA18 | URBAN | Planned |  | 16 | 360 | 0.0039653 | 0.0011015 | N
06/05/2017 | 07:30 | ZN384:PA29 | URBAN | Planned |  | 1 | 15 | 1.0314e-05 | 6.8759e-05 | N
06/05/2017 | 09:15 | ZN35800:PA3 | URBAN | Planned |  | 2 | 420 | 0.00057758 | 0.00013752 | N
06/05/2017 | 16:30 | ZN9700:PA12 | URBAN | Planned |  | 1 | 330 | 0.00022691 | 6.8759e-05 | N
06/05/2017 | 00:15 | ZN263:PA31 32KLM | CBD | Planned |  | 25 | 1,685 | 1.3546 | 0.080394 | N
07/05/2017 | 07:35 | ZN9550:PA11 | URBAN | Planned |  | 36 | 655 | 0.01621 | 0.0024749 | N
07/05/2017 | 10:20 | ZN3425:PA16 | URBAN | Planned |  | 136 | 325 | 0.030386 | 0.0093496 | N
07/05/2017 | 10:30 | ZN262:PA14 | URBAN | Planned |  | 2 | 15 | 2.0624e-05 | 0.00013749 | N
07/05/2017 | 22:10 | ZN1285:PA10 | URBAN | Planned |  | 22 | 530 | 0.0080159 | 0.0015124 | N
07/05/2017 | 22:10 | ZN1285:PA17 | URBAN | Planned |  | 58 | 530 | 0.021133 | 0.0039873 | N
08/05/2017 | 06:30 | ZN129:PA51 | URBAN | Planned |  | 1 | 3,355 | 0.0023065 | 6.8747e-05 | N
08/05/2017 | 08:30 | ZN12610:PA10 | URBAN | Planned |  | 21 | 450 | 0.0064966 | 0.0014437 | N
08/05/2017 | 08:30 | ZN12610:PA18 | URBAN | Planned |  | 41 | 450 | 0.012684 | 0.0028186 | N
08/05/2017 | 08:30 | ZN14891:PA16 | SHORT RURAL | Planned |  | 39 | 530 | 0.091895 | 0.017339 | N
08/05/2017 | 09:00 | ZN10999:PA36 | URBAN | Planned |  | 44 | 210 | 0.0063522 | 0.0030249 | N
08/05/2017 | 08:30 | ZN2602:PA29 | URBAN | Planned |  | 87 | 270 | 0.016149 | 0.005981 | N
08/05/2017 | 22:15 | ZN1285:PA17 | URBAN | Planned |  | 46 | 275 | 0.0086965 | 0.0031623 | N
09/05/2017 | 09:20 | ZN2466:PA40 | URBAN | Planned |  | 8 | 430 | 0.002365 | 0.00054999 | N
09/05/2017 | 07:00 | ZN931:PA9 | URBAN | Planned |  | 32 | 450 | 0.0098998 | 0.0022 | N
09/05/2017 | 07:30 | ZN711:PA22 | URBAN | Planned |  | 12 | 630 | 0.0051974 | 0.00082499 | N
09/05/2017 | 08:00 | ZN10994:PA3 | URBAN | Planned |  | 55 | 390 | 0.014747 | 0.0037812 | N
09/05/2017 | 08:00 | ZN15005:PA4 | URBAN | Planned |  | 9 | 420 | 0.0025987 | 0.00061874 | N
09/05/2017 | 08:40 | ZN10994:PA7 | URBAN | Planned |  | 136 | 560 | 0.052359 | 0.0093498 | N
09/05/2017 | 08:50 | ZN398:PA11 | URBAN | Planned |  | 32 | 520 | 0.01144 | 0.0022 | N
09/05/2017 | 20:30 | ZN15014:PA19 | URBAN | Planned |  | 25 | 570 | 0.0097967 | 0.0017187 | N
10/05/2017 | 08:30 | ZN14143:PA17 | SHORT RURAL | Planned |  | 164 | 505 | 0.36821 | 0.072914 | N
10/05/2017 | 08:45 | ZN3154:PA12 | URBAN | Planned |  | 18 | 405 | 0.0050119 | 0.0012375 | N
10/05/2017 | 08:50 | ZN12600:PA3 | URBAN | Planned |  | 36 | 470 | 0.011633 | 0.002475 | N
10/05/2017 | 08:00 | ZN15005:PA4 | URBAN | Planned |  | 9 | 420 | 0.0025988 | 0.00061875 | N
10/05/2017 | 08:30 | ZN12630:PA8 | SHORT RURAL | Planned |  | 19 | 420 | 0.035479 | 0.0084473 | N
11/05/2017 | 08:30 | ZN14143:PA17 | SHORT RURAL | Planned |  | 164 | 505 | 0.36808 | 0.072886 | N
17/05/2017 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 436 | 555 | 1.0754 | 0.19376 | N
11/05/2017 | 08:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 76 | 559 | 0.18881 | 0.033777 | N
11/05/2017 | 08:00 | ZN36100:PA27 | URBAN | Planned |  | 97 | 420 | 0.02803 | 0.0066738 | N
11/05/2017 | 08:45 | ZN4545:PA4 | URBAN | Planned |  | 5 | 435 | 0.0014965 | 0.00034401 | N
11/05/2017 | 08:30 | ZN36800:PA58 | URBAN | Planned |  | 151 | 90 | 0.0093503 | 0.010389 | N
11/05/2017 | 08:00 | ZN15005:PA4 | URBAN | Planned |  | 49 | 420 | 0.01416 | 0.0033713 | N
11/05/2017 | 10:33 | ZN4545:PA39 | URBAN | Planned |  | 82 | 192 | 0.010832 | 0.0056418 | N
12/05/2017 | 04:35 | ZN12690:PA4 | URBAN | Planned |  | 6 | 2,634 | 0.010869 | 0.00041266 | N
12/05/2017 | 09:10 | ZN12570:PA33 | SHORT RURAL | Planned |  | 1 | 530 | 0.0023554 | 0.00044441 | N
13/05/2017 | 07:30 | ZN3922:PA2 | URBAN | Planned |  | 1 | 375 | 0.00025776 | 6.8735e-05 | N
13/05/2017 | 07:50 | ZN4990:PA55 56KLM | CBD | Planned |  | 43 | 555 | 0.76724 | 0.13824 | N
13/05/2017 | 07:45 | ZN8000:PA39 | URBAN | Planned |  | 20 | 195 | 0.0026807 | 0.0013747 | N
13/05/2017 | 07:45 | ZN8700:PA63 64DEF | CBD | Planned |  | 26 | 180 | 0.15046 | 0.083588 | N
13/05/2017 | 05:30 | ZN8700:PA63 64DEF | CBD | Planned |  | 7 | 780 | 0.17553 | 0.022504 | N
13/05/2017 | 09:24 | ZN340:PA10 | URBAN | Planned |  | 1 | 2 | 1.3747e-06 | 6.8735e-05 | N
13/05/2017 | 09:36 | ZN340:PA3 | URBAN | Planned |  | 24 | 2 | 3.2993e-05 | 0.0016496 | N
14/05/2017 | 06:30 | ZN10999:PA14 | URBAN | Planned |  | 1 | 420 | 0.00028869 | 6.8735e-05 | N
14/05/2017 | 23:00 | ZN12580:PA10 | URBAN | Planned |  | 3 | 240 | 0.00049489 | 0.0002062 | N
14/05/2017 | 23:00 | ZN12580:PA10 | URBAN | Planned |  | 6 | 240 | 0.00098978 | 0.00041241 | N
15/05/2017 | 00:30 | ZN3155:PA27 | URBAN | Planned |  | 123 | 1,740 | 0.14711 | 0.0084544 | N
15/05/2017 | 06:30 | ZN384:PA29 | URBAN | Planned |  | 141 | 180 | 0.017445 | 0.0096916 | N
15/05/2017 | 08:50 | ZN15005:PA10 | URBAN | Planned |  | 1 | 340 | 0.0002337 | 6.8735e-05 | N
15/05/2017 | 09:10 | ZN12630:PA1 | SHORT RURAL | Planned |  | 2 | 380 | 0.0033774 | 0.0008888 | N
15/05/2017 | 08:00 | ZN180:PA9 | URBAN | Planned |  | 36 | 360 | 0.008908 | 0.0024744 | N
15/05/2017 | 08:00 | ZN180:PA32 | URBAN | Planned |  | 21 | 360 | 0.0051963 | 0.0014434 | N
15/05/2017 | 08:00 | ZN15005:PA4 | URBAN | Planned |  | 30 | 420 | 0.0086606 | 0.002062 | N
15/05/2017 | 11:00 | ZN35555:PA6 | URBAN | Planned |  | 1 | 210 | 0.00014434 | 6.8735e-05 | N
16/05/2017 | 05:00 | ZN3155:PA27 | URBAN | Planned |  | 23 | 30 | 0.00047428 | 0.0015809 | N
16/05/2017 | 10:00 | ZN398:PA29 | URBAN | Planned |  | 1 | 280 | 0.00019246 | 6.8736e-05 | N
16/05/2017 | 09:05 | ZN12650:PA1 | SHORT RURAL | Planned |  | 23 | 275 | 0.028109 | 0.010221 | N
16/05/2017 | 09:05 | ZN116:PA85 | URBAN | Planned |  | 1 | 10 | 6.8736e-06 | 6.8736e-05 | N
16/05/2017 | 08:00 | ZN12580:PA1 | URBAN | Planned |  | 61 | 480 | 0.020126 | 0.0041929 | N
15/06/2017 | 08:40 | 528:83013 | URBAN | Planned |  | 148 | 410 | 0.0417 | 0.010171 | N
15/06/2017 | 20:30 | 222:33602 | URBAN | Planned |  | 1 | 150 | 0.00010308 | 6.8722e-05 | N
15/06/2017 | 08:10 | 526:34640 | SHORT RURAL | Planned |  | 5 | 435 | 0.0097354 | 0.002238 | N
15/06/2017 | 08:40 | 516:48067 | SHORT RURAL | Planned |  | 21 | 92 | 0.0086477 | 0.0093997 | N
15/06/2017 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 7 | 150 | 0.0046998 | 0.0031332 | N
15/06/2017 | 09:20 | 810:74054 | LONG RURAL | Planned |  | 1 | 230 | 0.082055 | 0.035676 | N
16/05/2017 | 08:05 | ZN14892:PA14 | SHORT RURAL | Planned |  | 35 | 255 | 0.039663 | 0.015554 | N
16/05/2017 | 08:05 | ZN14892:PA6 | SHORT RURAL | Planned |  | 14 | 255 | 0.015865 | 0.0062217 | N
16/05/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 88 | 420 | 0.025405 | 0.0060487 | N
16/05/2017 | 08:00 | ZN15005:PA4 | URBAN | Planned |  | 30 | 420 | 0.0086607 | 0.0020621 | N
17/05/2017 | 10:00 | ZN2466:PA5 | URBAN | Planned |  | 27 | 270 | 0.0050109 | 0.0018559 | N
17/05/2017 | 09:05 | ZN180:PA32 | URBAN | Planned |  | 21 | 505 | 0.0072895 | 0.0014435 | N
17/05/2017 | 09:05 | ZN180:PA9 | URBAN | Planned |  | 36 | 505 | 0.012496 | 0.0024745 | N
17/05/2017 | 07:30 | ZN188:PA16 | URBAN | Planned |  | 53 | 420 | 0.015301 | 0.003643 | N
17/05/2017 | 08:38 | ZN80:PA22 | URBAN | Planned |  | 75 | 262 | 0.013507 | 0.0051552 | N
17/05/2017 | 08:00 | ZN12600:PA3 | URBAN | Planned |  | 47 | 454 | 0.014667 | 0.0032306 | N
17/05/2017 | 08:55 | ZN15005:PA4 | URBAN | Planned |  | 30 | 365 | 0.0075266 | 0.0020621 | N
17/05/2017 | 09:30 | ZN10991:PA13 | URBAN | Planned |  | 37 | 150 | 0.0038149 | 0.0025432 | N
17/05/2017 | 09:40 | ZN15005:PA2 | URBAN | Planned |  | 92 | 280 | 0.017706 | 0.0063237 | N
17/05/2017 | 13:30 | ZN15005:PA2 | URBAN | Planned |  | 30 | 50 | 0.001031 | 0.0020621 | N
17/05/2017 | 09:00 | ZN15005:PA2 | URBAN | Planned |  | 72 | 815 | 0.040334 | 0.004949 | N
17/05/2017 | 22:00 | ZN2835:PA30 | URBAN | Planned |  | 42 | 120 | 0.0034643 | 0.0028869 | N
18/05/2017 | 07:00 | ZN965:PA15 | URBAN | Planned |  | 12 | 600 | 0.0049476 | 0.00082461 | N
18/05/2017 | 08:45 | ZN8000:PA19 | URBAN | Planned |  | 45 | 90 | 0.002783 | 0.0030923 | N
18/05/2017 | 09:30 | ZN9900:PA12 | URBAN | Planned |  | 13 | 435 | 0.003886 | 0.00089332 | N
18/05/2017 | 09:05 | ZN12610:PA23 | URBAN | Planned |  | 43 | 455 | 0.013445 | 0.0029548 | N
18/05/2017 | 08:30 | ZN12640:PA13 | SHORT RURAL | Planned |  | 39 | 440 | 0.076237 | 0.017326 | N
18/05/2017 | 08:00 | ZN10999:PA7 | URBAN | Planned |  | 149 | 420 | 0.043003 | 0.010239 | N
18/05/2017 | 16:00 | ZN965:PA15 | URBAN | Planned |  | 64 | 60 | 0.0026387 | 0.0043979 | N
19/05/2017 | 07:10 | ZN2196:PA10 | URBAN | Planned |  | 1 | 410 | 0.00028176 | 6.8723e-05 | N
19/05/2017 | 07:00 | ZN965:PA15 | URBAN | Planned |  | 12 | 600 | 0.004948 | 0.00082467 | N
19/05/2017 | 10:10 | ZN12650:PA19 | URBAN | Planned |  | 8 | 80 | 0.00043982 | 0.00054978 | N
19/05/2017 | 08:15 | ZN12630:PA6 | SHORT RURAL | Planned |  | 7 | 275 | 0.0086164 | 0.0031332 | N
19/05/2017 | 08:15 | ZN3922:PA12 | URBAN | Planned |  | 40 | 195 | 0.0053604 | 0.0027489 | N
19/05/2017 | 11:10 | ZN12580:PA10 | URBAN | Planned |  | 44 | 65 | 0.0019655 | 0.0030238 | N
19/05/2017 | 10:15 | ZN116:PA73 | URBAN | Planned |  | 1 | 5 | 3.4361e-06 | 6.8723e-05 | N
19/05/2017 | 16:00 | ZN965:PA15 | URBAN | Planned |  | 64 | 60 | 0.0026389 | 0.0043982 | N
19/05/2017 | 20:30 | ZN263:PA33 34GHJ | CBD | Planned |  | 6 | 300 | 0.057556 | 0.019185 | N
19/05/2017 | 21:30 | ZN263:PA35 37DEF | CBD | Planned |  | 8 | 255 | 0.06523 | 0.02558 | N
20/05/2017 | 07:45 | ZN35400:PA88 | URBAN | Planned |  | 82 | 435 | 0.024513 | 0.0056353 | N
20/05/2017 | 07:48 | ZN2196:PA11 | URBAN | Planned |  | 1 | 307 | 0.00021098 | 6.8723e-05 | N
20/05/2017 | 16:00 | ZN965:PA15 | URBAN | Planned |  | 64 | 60 | 0.0026389 | 0.0043982 | N
21/05/2017 | 07:45 | ZN3922:PA2 | URBAN | Planned |  | 1 | 635 | 0.00043639 | 6.8723e-05 | N
21/05/2017 | 07:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 1 | 330 | 0.0014771 | 0.00044761 | N
21/05/2017 | 07:40 | ZN10993:PA35 | URBAN | Planned |  | 7 | 600 | 0.0028863 | 0.00048106 | N
22/05/2017 | 09:00 | ZN35900:PA10 | URBAN | Planned |  | 1 | 390 | 0.00026802 | 6.8723e-05 | N
22/05/2017 | 10:00 | ZN35800:PA1 | URBAN | Planned |  | 130 | 70 | 0.0062538 | 0.0089339 | N
22/05/2017 | 19:30 | ZN10995:PA7 | URBAN | Planned |  | 32 | 527 | 0.011589 | 0.0021991 | N
22/05/2017 | 22:00 | ZN9252:PA30 | URBAN | Planned |  | 33 | 2,395 | 0.054315 | 0.0022678 | N
23/05/2017 | 09:00 | ZN116:PA74 | URBAN | Planned |  | 66 | 240 | 0.010886 | 0.0045357 | N
23/05/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 19 | 420 | 0.0054841 | 0.0013057 | N
23/05/2017 | 09:00 | ZN12570:PA37 | SHORT RURAL | Planned |  | 7 | 356 | 0.011154 | 0.0031332 | N
23/05/2017 | 09:53 | ZN180:PA30 | URBAN | Planned |  | 19 | 120 | 0.0015669 | 0.0013057 | N
23/05/2017 | 10:30 | ZN10999:PA25 | URBAN | Planned |  | 64 | 150 | 0.0065974 | 0.0043982 | N
24/05/2017 | 05:00 | ZN80:PA24 | URBAN | Planned |  | 49 | 5 | 0.00016837 | 0.0033674 | N
24/05/2017 | 07:00 | ZN3472:PA20 | URBAN | Planned |  | 47 | 480 | 0.015504 | 0.00323 | N
24/05/2017 | 08:15 | ZN2835:PA24 | URBAN | Planned |  | 52 | 255 | 0.0091126 | 0.0035736 | N
24/05/2017 | 08:45 | ZN4545:PA2 | URBAN | Planned |  | 24 | 325 | 0.0053604 | 0.0016493 | N
25/05/2017 | 07:25 | ZN12690:PA11 | URBAN | Planned |  | 2 | 1,755 | 0.0024122 | 0.00013745 | N
25/05/2017 | 07:00 | ZN3672:PA43 | URBAN | Planned |  | 52 | 480 | 0.017153 | 0.0035736 | N
25/05/2017 | 07:30 | ZN5868:PA5 | SHORT RURAL | Planned |  | 1 | 480 | 0.0021485 | 0.00044761 | N
25/05/2017 | 09:15 | ZN8000:PA19 | URBAN | Planned |  | 71 | 255 | 0.012442 | 0.0048793 | N
25/05/2017 | 08:20 | ZN15013:PA10 | SHORT RURAL | Planned |  | 12 | 470 | 0.025245 | 0.0053713 | N
25/05/2017 | 08:10 | ZN12610:PA23 | URBAN | Planned |  | 43 | 380 | 0.011229 | 0.0029551 | N
25/05/2017 | 09:00 | ZN36200:PA8 | SHORT RURAL | Planned |  | 227 | 440 | 0.44707 | 0.10161 | N
25/05/2017 | 09:30 | ZN35800:PA18 | URBAN | Planned |  | 1 | 330 | 0.00022678 | 6.8723e-05 | N
26/05/2017 | 08:00 | ZN36200:PA1 | URBAN | Planned |  | 58 | 480 | 0.019132 | 0.0039859 | Y
26/05/2017 | 09:30 | ZN1788:PA20 | URBAN | Planned |  | 46 | 45 | 0.0014226 | 0.0031612 | Y
27/05/2017 | 08:00 | ZN3672:PA36 | URBAN | Planned |  | 73 | 495 | 0.024833 | 0.0050168 | N
27/05/2017 | 08:00 | ZN2466:PA22 | URBAN | Planned |  | 1 | 90 | 6.185e-05 | 6.8723e-05 | N
27/05/2017 | 08:45 | ZN4990:PA51 52KLM | CBD | Planned |  | 2 | 285 | 0.018226 | 0.0063951 | N
27/05/2017 | 09:30 | ZN195:PA22 | URBAN | Planned |  | 1 | 300 | 0.00020617 | 6.8723e-05 | N
28/05/2017 | 07:30 | ZN2196:PA1 | URBAN | Planned |  | 1 | 450 | 0.00030925 | 6.8723e-05 | N
28/05/2017 | 22:15 | ZN384:PA29 | URBAN | Planned |  | 74 | 1,525 | 0.077553 | 0.0050855 | N
29/05/2017 | 08:50 | ZN8000:PA19 | URBAN | Planned |  | 114 | 115 | 0.0090095 | 0.0078344 | N
29/05/2017 | 08:00 | ZN180:PA9 | URBAN | Planned |  | 104 | 300 | 0.021441 | 0.0071472 | N
29/05/2017 | 10:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 9 | 260 | 0.010474 | 0.0040284 | N
29/05/2017 | 05:35 | ZN12600:PA13 | SHORT RURAL | Planned |  | 67 | 925 | 0.2774 | 0.02999 | N
29/05/2017 | 21:40 | ZN9900:PA9 | URBAN | Planned |  | 23 | 290 | 0.0045838 | 0.0015806 | N
04/04/2017 | 05:40 | ZN12600:PA13 | SHORT RURAL | Planned |  | 19 | 80,150 | 6.7814 | 0.0084609 | N
30/05/2017 | 06:15 | ZN5868:PA7 | URBAN | Planned |  | 1 | 5 | 3.4361e-06 | 6.8722e-05 | N
30/05/2017 | 07:00 | ZN10999:PA10 | URBAN | Planned |  | 85 | 1,650 | 0.096382 | 0.0058413 | N
30/05/2017 | 07:32 | ZN2400:PA11 | SHORT RURAL | Planned |  | 43 | 518 | 0.099699 | 0.019247 | N
30/05/2017 | 09:30 | ZN35370:PA8 | SHORT RURAL | Planned |  | 14 | 390 | 0.024439 | 0.0062664 | N
30/05/2017 | 07:30 | ZN9900:PA13 | URBAN | Planned |  | 73 | 540 | 0.02709 | 0.0050167 | N
30/05/2017 | 08:00 | ZN7481:PA12 | URBAN | Planned |  | 22 | 180 | 0.0027214 | 0.0015119 | N
30/05/2017 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 13 | 465 | 0.027058 | 0.0058188 | N
30/05/2017 | 08:00 | ZN15004:PA3 | URBAN | Planned |  | 45 | 420 | 0.012988 | 0.0030925 | N
30/05/2017 | 11:00 | ZN847:PA46 | URBAN | Planned |  | 32 | 360 | 0.0079167 | 0.0021991 | N
30/05/2017 | 11:00 | ZN15002:PA2 | URBAN | Planned |  | 128 | 135 | 0.011875 | 0.0087964 | N
31/05/2017 | 07:05 | ZN9252:PA24 | URBAN | Planned |  | 1 | 535 | 0.00036766 | 6.8722e-05 | N
31/05/2017 | 08:30 | ZN15005:PA6 | URBAN | Planned |  | 66 | 330 | 0.014968 | 0.0045356 | N
31/05/2017 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 106 | 530 | 0.25146 | 0.047446 | N
31/05/2017 | 08:00 | ZN180:PA7 | URBAN | Planned |  | 63 | 300 | 0.012988 | 0.0043295 | N
31/05/2017 | 09:15 | ZN36100:PA8 | URBAN | Planned |  | 39 | 255 | 0.0068344 | 0.0026801 | N
16/06/2017 | 08:30 | 509:33399 | SHORT RURAL | Planned |  | 213 | 360 | 0.34322 | 0.09534 | N
16/06/2017 | 08:30 | 243:80081 | SHORT RURAL | Planned |  | 188 | 435 | 0.36605 | 0.084149 | N
16/06/2017 | 07:50 | 232:33407 | SHORT RURAL | Planned |  | 27 | 360 | 0.043507 | 0.012085 | N
16/06/2017 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 10 | 215 | 0.76704 | 0.35676 | N
17/06/2017 | 07:25 | 202:34253 | URBAN | Planned |  | 1 | 298 | 0.00020479 | 6.8722e-05 | N
17/06/2017 | 22:00 | 222:33601 | SHORT RURAL | Planned |  | 12 | 440 | 0.023633 | 0.0053712 | N
18/06/2017 | 08:30 | 227:13015 | SHORT RURAL | Planned |  | 50 | 540 | 0.12085 | 0.02238 | N
18/06/2017 | 07:42 | 213:33775 | URBAN | Planned |  | 68 | 243 | 0.011356 | 0.0046731 | N
16/06/2017 | 09:30 | 528:83011 | SHORT RURAL | Planned |  | 1 | 200 | 0.00089521 | 0.0004476 | N
16/06/2017 | 08:35 | 801:74119 | URBAN | Planned |  | 33 | 285 | 0.0064633 | 0.0022678 | N
16/06/2017 | 09:05 | 801:74122 | URBAN | Planned |  | 50 | 195 | 0.0067004 | 0.0034361 | N
19/06/2017 | 09:22 | 516:48067 | SHORT RURAL | Planned |  | 13 | 123 | 0.0071572 | 0.0058188 | N
19/06/2017 | 20:56 | 504:48028 | URBAN | Planned |  | 270 | 544 | 0.10094 | 0.018555 | N
19/06/2017 | 08:45 | 243:80081 | SHORT RURAL | Planned |  | 146 | 396 | 0.25879 | 0.06535 | N
19/06/2017 | 09:35 | 206:34434 | URBAN | Planned |  | 57 | 245 | 0.009597 | 0.0039171 | N
19/06/2017 | 08:50 | 502:48004 | URBAN | Planned |  | 42 | 175 | 0.005051 | 0.0028863 | N
19/06/2017 | 08:30 | 508:82579 | SHORT RURAL | Planned |  | 5 | 180 | 0.0040284 | 0.002238 | N
19/06/2017 | 08:30 | 230:81432 | SHORT RURAL | Planned |  | 56 | 280 | 0.070184 | 0.025066 | N
19/06/2017 | 12:30 | 508:82579 | SHORT RURAL | Planned |  | 2 | 105 | 0.00093997 | 0.00089521 | N
19/06/2017 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 3 | 170 | 0.0022828 | 0.0013428 | N
19/06/2017 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 4 | 125 | 0.002238 | 0.0017904 | N
20/06/2017 | 08:40 | 227:13015 | SHORT RURAL | Planned |  | 22 | 355 | 0.034958 | 0.0098473 | N
20/06/2017 | 08:00 | 243:80083 | SHORT RURAL | Planned |  | 6 | 460 | 0.012354 | 0.0026856 | N
20/06/2017 | 09:00 | 508:82574 | SHORT RURAL | Planned |  | 1 | 87 | 0.00038942 | 0.0004476 | N
20/06/2017 | 08:00 | 508:82579 | SHORT RURAL | Planned |  | 7 | 430 | 0.013473 | 0.0031332 | N
20/06/2017 | 09:15 | 508:82574 | SHORT RURAL | Planned |  | 1 | 75 | 0.0003357 | 0.0004476 | N
20/06/2017 | 09:10 | 801:74123 | SHORT RURAL | Planned |  | 5 | 265 | 0.0059307 | 0.002238 | N
20/06/2017 | 11:00 | 812:19071 | SHORT RURAL | Planned |  | 48 | 120 | 0.025782 | 0.021485 | N
21/06/2017 | 08:30 | 502:48010 | SHORT RURAL | Planned |  | 21 | 465 | 0.043708 | 0.0093997 | N
21/06/2017 | 09:11 | 523:33501 | SHORT RURAL | Planned |  | 2 | 139 | 0.0012443 | 0.00089521 | N
21/06/2017 | 08:50 | 814:82283 | SHORT RURAL | Planned |  | 18 | 220 | 0.017725 | 0.0080569 | N
22/06/2017 | 08:30 | 225:13446 | URBAN | Planned |  | 67 | 275 | 0.012662 | 0.0046044 | N
23/06/2017 | 09:25 | 206:34438 | URBAN | Planned |  | 57 | 167 | 0.0065341 | 0.0039126 | N
22/06/2017 | 08:35 | 524:33576 | SHORT RURAL | Planned |  | 8 | 290 | 0.010384 | 0.0035808 | N
22/06/2017 | 09:09 | 242:81539 | URBAN | Planned |  | 3 | 126 | 0.00025977 | 0.00020617 | N
22/06/2017 | 09:50 | 508:82574 | SHORT RURAL | Planned |  | 21 | 15 | 0.00141 | 0.0093997 | N
22/06/2017 | 08:55 | 511:29878 | SHORT RURAL | Planned |  | 46 | 415 | 0.085448 | 0.02059 | N
22/06/2017 | 12:30 | 508:82574 | SHORT RURAL | Planned |  | 10 | 135 | 0.0060426 | 0.004476 | N
23/06/2017 | 09:00 | 232:11454 | SHORT RURAL | Planned |  | 1 | 180 | 0.00080569 | 0.0004476 | N
25/06/2017 | 22:35 | 232:11460 | URBAN | Planned |  | 21 | 165 | 0.0023785 | 0.0014415 | N
22/06/2017 | 08:20 | 514:18146 | SHORT RURAL | Planned |  | 4 | 500 | 0.0089521 | 0.0017904 | N
22/06/2017 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 10 | 270 | 0.012085 | 0.004476 | N
23/06/2017 | 09:15 | 812:19072 | SHORT RURAL | Planned |  | 1 | 170 | 0.00076093 | 0.0004476 | N
23/06/2017 | 09:15 | 812:19072 | SHORT RURAL | Planned |  | 4 | 150 | 0.0026856 | 0.0017904 | N
26/06/2017 | 09:15 | 807:74180 | SHORT RURAL | Planned |  | 8 | 150 | 0.0053712 | 0.0035808 | N
26/06/2017 | 08:15 | 516:48066 | SHORT RURAL | Planned |  | 11 | 372 | 0.018316 | 0.0049236 | N
26/06/2017 | 09:30 | 526:34640 | SHORT RURAL | Planned |  | 18 | 330 | 0.026588 | 0.0080569 | N
26/06/2017 | 09:03 | 235:2120 | SHORT RURAL | Planned |  | 81 | 373 | 0.13523 | 0.036256 | N
26/06/2017 | 02:15 | 258:80793 | URBAN | Planned |  | 1 | 335 | 0.00022995 | 6.8642e-05 | N
26/06/2017 | 08:00 | 227:13020 | SHORT RURAL | Planned |  | 58 | 420 | 0.10904 | 0.025961 | N
26/06/2017 | 19:05 | 224:80331 | URBAN | Planned |  | 1 | 145 | 9.9531e-05 | 6.8642e-05 | N
27/06/2017 | 10:10 | 223:14399 | SHORT RURAL | Planned |  | 24 | 135 | 0.014502 | 0.010742 | N
27/06/2017 | 08:45 | 224:80340 | SHORT RURAL | Planned |  | 233 | 390 | 0.40674 | 0.10429 | N
27/06/2017 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 1 | 50 | 0.0002238 | 0.0004476 | N
27/06/2017 | 08:50 | 508:82574 | SHORT RURAL | Planned |  | 2 | 197 | 0.0017636 | 0.00089521 | N
27/06/2017 | 09:03 | 502:48004 | URBAN | Planned |  | 42 | 250 | 0.0072074 | 0.002883 | N
27/06/2017 | 08:20 | 524:33576 | SHORT RURAL | Planned |  | 5 | 285 | 0.0063784 | 0.002238 | N
27/06/2017 | 08:20 | 814:82291 | SHORT RURAL | Planned |  | 3 | 360 | 0.0048341 | 0.0013428 | N
27/06/2017 | 08:55 | 813:89055 | SHORT RURAL | Planned |  | 6 | 275 | 0.0073855 | 0.0026856 | N
01/06/2017 | 07:00 | ZN35900:PA4 | SHORT RURAL | Planned |  | 52 | 480 | 0.11172 | 0.023275 | N
01/06/2017 | 07:00 | ZN35900:PA4 | SHORT RURAL | Planned |  | 31 | 480 | 0.066603 | 0.013876 | N
01/06/2017 | 07:00 | ZN35900:PA4 | SHORT RURAL | Planned |  | 63 | 480 | 0.13536 | 0.028199 | N
01/06/2017 | 08:00 | ZN1648:PA2 | URBAN | Planned |  | 95 | 360 | 0.023503 | 0.0065286 | N
01/06/2017 | 08:15 | ZN180:PA10 | URBAN | Planned |  | 79 | 55 | 0.002986 | 0.005429 | N
01/06/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 19 | 420 | 0.005484 | 0.0013057 | N
01/06/2017 | 09:45 | ZN12650:PA16 | URBAN | Planned |  | 24 | 170 | 0.0028038 | 0.0016493 | N
01/06/2017 | 09:30 | ZN3922:PA17 | SHORT RURAL | Planned |  | 3 | 1,710 | 0.022962 | 0.0013428 | N
01/06/2017 | 10:00 | ZN2466:PA15 | URBAN | Planned |  | 1 | 240 | 0.00016493 | 6.8722e-05 | N
02/06/2017 | 07:45 | ZN35900:PA4 | SHORT RURAL | Planned |  | 63 | 435 | 0.12267 | 0.028199 | N
02/06/2017 | 07:00 | ZN35900:PA17 | URBAN | Planned |  | 65 | 480 | 0.021441 | 0.0044669 | N
02/06/2017 | 08:00 | ZN12600:PA3 | URBAN | Planned |  | 33 | 480 | 0.010886 | 0.0022678 | N
03/06/2017 | 07:00 | ZN847:PA47 | SHORT RURAL | Planned |  | 20 | 2,025 | 0.18128 | 0.0089521 | N
03/06/2017 | 07:20 | ZN3288:PA41 42KLM | CBD | Planned |  | 164 | 2 | 0.010486 | 0.52431 | N
03/06/2017 | 08:00 | ZN2196:PA9 | URBAN | Planned |  | 1 | 450 | 0.00030925 | 6.8722e-05 | N
03/06/2017 | 09:01 | ZN3288:PA41 42KLM | CBD | Planned |  | 32 | 131 | 0.13402 | 0.10231 | N
03/06/2017 | 08:00 | ZN35500:PA34 | URBAN | Planned |  | 3 | 420 | 0.00086589 | 0.00020617 | N
04/06/2017 | 08:25 | ZN3288:PA41 42KLM | CBD | Planned |  | 29 | 230 | 0.21324 | 0.092714 | N
04/06/2017 | 07:10 | ZN1287:PA18 | URBAN | Planned |  | 4 | 490 | 0.0013469 | 0.00027489 | N
04/06/2017 | 08:40 | ZN342:PA15 | URBAN | Planned |  | 1 | 415 | 0.00028519 | 6.8722e-05 | N
04/06/2017 | 08:00 | ZN9118:PA6 | URBAN | Planned |  | 12 | 390 | 0.0032162 | 0.00082466 | N
04/06/2017 | 12:17 | ZN3672:PA37 | URBAN | Planned |  | 106 | 233 | 0.016973 | 0.0072845 | N
04/06/2017 | 23:00 | ZN12650:PA14 | URBAN | Planned |  | 26 | 330 | 0.0058963 | 0.0017868 | N
05/06/2017 | 07:45 | ZN12630:PA3 | SHORT RURAL | Planned |  | 19 | 635 | 0.054003 | 0.0085045 | N
05/06/2017 | 07:30 | ZN3155:PA17 | URBAN | Planned |  | 88 | 480 | 0.029028 | 0.0060475 | N
05/06/2017 | 10:00 | ZN847:PA45 | SHORT RURAL | Planned |  | 1 | 385 | 0.0017233 | 0.0004476 | N
05/06/2017 | 07:55 | ZN340:PA3 | URBAN | Planned |  | 1 | 335 | 0.00023022 | 6.8722e-05 | N
05/06/2017 | 09:55 | ZN15005:PA2 | URBAN | Planned |  | 81 | 175 | 0.0097413 | 0.0055665 | N
05/06/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052778 | 0.0021991 | N
06/06/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052778 | 0.0021991 | N
21/06/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052778 | 0.0021991 | N
22/06/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052778 | 0.0021991 | N
29/06/2017 | 08:00 | 514:18137 | SHORT RURAL | Planned |  | 49 | 420 | 0.092117 | 0.021933 | N
03/06/2017 | 08:15 | 243:80083 | SHORT RURAL | Planned |  | 31 | 36,420 | 5.0535 | 0.013876 | N
29/06/2017 | 08:15 | 243:80083 | SHORT RURAL | Planned |  | 43 | 225 | 0.043306 | 0.019247 | N
29/06/2017 | 09:00 | 243:80081 | SHORT RURAL | Planned |  | 80 | 260 | 0.093102 | 0.035808 | N
29/06/2017 | 09:40 | 239:82127 | SHORT RURAL | Planned |  | 7 | 170 | 0.0053265 | 0.0031332 | N
30/06/2017 | 09:00 | 243:80081 | SHORT RURAL | Planned |  | 240 | 360 | 0.38673 | 0.10742 | N
28/06/2017 | 10:10 | 508:82574 | SHORT RURAL | Planned |  | 4 | 40 | 0.00071617 | 0.0017904 | N
28/06/2017 | 11:35 | 508:82574 | SHORT RURAL | Planned |  | 6 | 125 | 0.003357 | 0.0026856 | N
29/06/2017 | 09:00 | 508:82574 | SHORT RURAL | Planned |  | 2 | 90 | 0.00080569 | 0.00089521 | N
29/06/2017 | 08:25 | 508:82579 | SHORT RURAL | Planned |  | 193 | 410 | 0.35419 | 0.086387 | N
29/06/2017 | 09:05 | 512:48048 | SHORT RURAL | Planned |  | 28 | 215 | 0.026946 | 0.012533 | N
29/06/2017 | 11:45 | 508:82580 | SHORT RURAL | Planned |  | 2 | 125 | 0.001119 | 0.00089521 | N
30/06/2017 | 08:00 | 507:80922 | SHORT RURAL | Planned |  | 2 | 270 | 0.0024171 | 0.00089521 | N
30/06/2017 | 08:30 | 508:82580 | SHORT RURAL | Planned |  | 10 | 158 | 0.0070721 | 0.004476 | N
30/06/2017 | 08:35 | 526:34640 | SHORT RURAL | Planned |  | 4 | 355 | 0.006356 | 0.0017904 | N
30/06/2017 | 10:15 | 508:82574 | SHORT RURAL | Planned |  | 1 | 208 | 0.00093102 | 0.0004476 | N
30/06/2017 | 11:55 | 508:82580 | SHORT RURAL | Planned |  | 2 | 72 | 0.00064455 | 0.00089521 | N
30/06/2017 | 12:35 | 508:82580 | SHORT RURAL | Planned |  | 4 | 30 | 0.00053712 | 0.0017904 | N
30/06/2017 | 09:45 | 508:82574 | SHORT RURAL | Planned |  | 2 | 235 | 0.0021037 | 0.00089521 | N
30/06/2017 | 08:30 | 526:34637 | SHORT RURAL | Planned |  | 10 | 195 | 0.0087283 | 0.004476 | N
30/06/2017 | 08:35 | 526:34640 | SHORT RURAL | Planned |  | 17 | 355 | 0.027013 | 0.0076093 | N
30/06/2017 | 12:00 | 813:89061 | LONG RURAL | Planned |  | 8 | 130 | 0.37103 | 0.28541 | N
05/06/2017 | 22:30 | ZN2635:PA39 | URBAN | Planned |  | 168 | 1,240 | 0.14316 | 0.011545 | N
06/06/2017 | 04:40 | ZN2466:PA16 | URBAN | Planned |  | 3 | 60 | 0.0001237 | 0.00020617 | N
06/06/2017 | 10:00 | ZN35400:PA110 | URBAN | Planned |  | 42 | 480 | 0.013854 | 0.0028863 | N
06/06/2017 | 10:00 | ZN35400:PA95 | URBAN | Planned |  | 50 | 480 | 0.016493 | 0.0034361 | N
06/06/2017 | 07:45 | ZN10995:PA1 | URBAN | Planned |  | 59 | 435 | 0.017637 | 0.0040546 | N
06/06/2017 | 09:11 | ZN12600:PA3 | URBAN | Planned |  | 25 | 409 | 0.0070268 | 0.001718 | N
06/06/2017 | 08:00 | ZN15005:PA12 | URBAN | Planned |  | 45 | 420 | 0.012988 | 0.0030925 | N
06/06/2017 | 09:30 | ZN7481:PA10 | URBAN | Planned |  | 23 | 270 | 0.0042676 | 0.0015806 | N
06/06/2017 | 09:30 | ZN7481:PA2 | URBAN | Planned |  | 10 | 270 | 0.0018555 | 0.00068722 | N
06/06/2017 | 09:30 | ZN7481:PA5 | URBAN | Planned |  | 10 | 270 | 0.0018555 | 0.00068722 | N
06/06/2017 | 09:30 | ZN7481:PA8 | URBAN | Planned |  | 1 | 270 | 0.00018555 | 6.8722e-05 | N
06/06/2017 | 08:30 | ZN3922:PA13 | SHORT RURAL | Planned |  | 68 | 420 | 0.12784 | 0.030437 | N
06/06/2017 | 11:00 | ZN10997:PA2 | URBAN | Planned |  | 141 | 295 | 0.028585 | 0.0096898 | N
06/06/2017 | 22:00 | ZN10999:PA38 | URBAN | Planned |  | 3 | 480 | 0.00098959 | 0.00020617 | N
07/06/2017 | 08:30 | ZN36800:PA56 | URBAN | Planned |  | 55 | 420 | 0.015875 | 0.0037797 | N
14/06/2017 | 08:00 | ZN36800:PA56 | URBAN | Planned |  | 55 | 420 | 0.015875 | 0.0037797 | N
07/06/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052778 | 0.0021991 | N
07/06/2017 | 19:00 | ZN15009:PA9 | URBAN | Planned |  | 10 | 390 | 0.0026801 | 0.00068722 | N
08/06/2017 | 06:40 | ZN384:PA29 | URBAN | Planned |  | 179 | 5 | 0.00061506 | 0.012301 | N
08/06/2017 | 07:00 | ZN2400:PA21 | URBAN | Planned |  | 6 | 2,040 | 0.0084115 | 0.00041233 | N
08/06/2017 | 07:30 | ZN167:PA21 | URBAN | Planned |  | 17 | 480 | 0.0056077 | 0.0011683 | N
08/06/2017 | 08:30 | ZN2310:PA53 | URBAN | Planned |  | 50 | 480 | 0.016493 | 0.0034361 | N
08/06/2017 | 09:30 | ZN3155:PA23 | URBAN | Planned |  | 19 | 180 | 0.0023503 | 0.0013057 | N
08/06/2017 | 10:00 | ZN4545:PA39 | URBAN | Planned |  | 110 | 60 | 0.0045356 | 0.0075594 | N
08/06/2017 | 10:20 | ZN7900:PA6 | URBAN | Planned |  | 21 | 50 | 0.00072158 | 0.0014432 | N
08/06/2017 | 17:00 | ZN80:PA22 | URBAN | Planned |  | 56 | 90 | 0.0034636 | 0.0038484 | N
08/06/2017 | 18:00 | ZN15009:PA11 | URBAN | Planned |  | 8 | 300 | 0.0016493 | 0.00054977 | N
08/06/2017 | 20:30 | ZN10996:PA12 | URBAN | Planned |  | 6 | 570 | 0.0023503 | 0.00041233 | N
09/06/2017 | 08:35 | ZN12570:PA37 | SHORT RURAL | Planned |  | 7 | 385 | 0.012063 | 0.0031332 | N
10/06/2017 | 08:00 | ZN2466:PA22 | URBAN | Planned |  | 2 | 360 | 0.0004948 | 0.00013744 | N
11/06/2017 | 07:00 | ZN15013:PA1 | URBAN | Planned |  | 1 | 20 | 1.3744e-05 | 6.8722e-05 | N
11/06/2017 | 10:40 | ZN10993:PA23 | URBAN | Planned |  | 1 | 410 | 0.00028176 | 6.8722e-05 | N
11/06/2017 | 12:00 | ZN2466:PA44 | URBAN | Planned |  | 7 | 250 | 0.0012026 | 0.00048105 | N
13/06/2017 | 00:00 | ZN2635:PA33 | URBAN | Planned |  | 4 | 1,650 | 0.0045356 | 0.00027489 | N
13/06/2017 | 07:30 | ZN35400:PA95 | URBAN | Planned |  | 57 | 630 | 0.024678 | 0.0039171 | N
13/06/2017 | 08:05 | ZN2568:PA40 | URBAN | Planned |  | 2 | 320 | 0.00043982 | 0.00013744 | N
13/06/2017 | 08:05 | ZN12690:PA24 | SHORT RURAL | Planned |  | 1 | 425 | 0.0019023 | 0.0004476 | N
13/06/2017 | 09:30 | ZN10999:PA22 | URBAN | Planned |  | 217 | 120 | 0.017895 | 0.014913 | N
13/06/2017 | 09:00 | ZN12640:PA19 | URBAN | Planned |  | 119 | 420 | 0.034347 | 0.0081779 | N
14/06/2017 | 10:30 | ZN188:PA16 | URBAN | Planned |  | 52 | 285 | 0.010185 | 0.0035735 | N
14/06/2017 | 08:00 | ZN2602:PA42 | URBAN | Planned |  | 1 | 2,010 | 0.0013813 | 6.8722e-05 | N
14/06/2017 | 10:00 | ZN15005:PA12 | URBAN | Planned |  | 26 | 90 | 0.0016081 | 0.0017868 | N
14/06/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 65 | 420 | 0.018761 | 0.0044669 | N
14/06/2017 | 09:24 | ZN12570:PA33 | SHORT RURAL | Planned |  | 57 | 411 | 0.10486 | 0.025513 | N
14/06/2017 | 21:00 | ZN35900:PA1 | URBAN | Planned |  | 46 | 1,600 | 0.050579 | 0.0031612 | N
14/06/2017 | 21:00 | ZN3155:PA27 | URBAN | Planned |  | 23 | 480 | 0.0075869 | 0.0015806 | N
15/06/2017 | 05:00 | ZN3155:PA27 | URBAN | Planned |  | 76 | 30 | 0.0015669 | 0.0052228 | N
15/06/2017 | 00:00 | ZN2635:PA33 | URBAN | Planned |  | 12 | 1,680 | 0.013854 | 0.00082466 | N
15/06/2017 | 01:17 | ZN2835:PA17 | URBAN | Planned |  | 6 | 7 | 2.8863e-05 | 0.00041233 | N
15/06/2017 | 08:15 | ZN35500:PA31 | URBAN | Planned |  | 89 | 441 | 0.026987 | 0.0061162 | N
15/06/2017 | 08:00 | ZN80:PA32 | URBAN | Planned |  | 72 | 540 | 0.026719 | 0.004948 | N
15/06/2017 | 01:32 | ZN2835:PA30 | URBAN | Planned |  | 42 | 838 | 0.024187 | 0.0028863 | N
15/06/2017 | 09:00 | ZN9550:PA36 | URBAN | Planned |  | 17 | 360 | 0.0042058 | 0.0011683 | N
15/06/2017 | 21:45 | ZN36100:PA12 | URBAN | Planned |  | 103 | 315 | 0.022297 | 0.0070783 | N
16/06/2017 | 07:30 | ZN10999:PA15 | URBAN | Planned |  | 44 | 540 | 0.016328 | 0.0030238 | N
16/06/2017 | 07:45 | ZN35500:PA31 | URBAN | Planned |  | 109 | 545 | 0.040824 | 0.0074907 | N
16/06/2017 | 14:30 | ZN3154:PA6 | URBAN | Planned |  | 70 | 45 | 0.0021647 | 0.0048105 | N
16/06/2017 | 22:45 | ZN3154:PA6 | URBAN | Planned |  | 118 | 380 | 0.030815 | 0.0081092 | N
16/06/2017 | 20:00 | ZN12650:PA14 | URBAN | Planned |  | 59 | 600 | 0.024327 | 0.0040546 | N
16/06/2017 | 20:00 | ZN12650:PA14 | URBAN | Planned |  | 42 | 600 | 0.017318 | 0.0028863 | N
17/06/2017 | 08:05 | ZN9252:PA28 | URBAN | Planned |  | 40 | 275 | 0.0075594 | 0.0027489 | N
17/06/2017 | 20:30 | ZN8700:PA65 66ABC | CBD | Planned |  | 48 | 526 | 0.80719 | 0.15346 | N
17/06/2017 | 23:30 | ZN3154:PA6 | URBAN | Planned |  | 118 | 353 | 0.028625 | 0.0081092 | N
18/06/2017 | 06:55 | ZN263:PA31 32ABC | CBD | Planned |  | 16 | 340 | 0.17392 | 0.051153 | N
18/06/2017 | 07:35 | ZN10994:PA8 | URBAN | Planned |  | 16 | 325 | 0.0035735 | 0.0010995 | N
18/06/2017 | 09:15 | ZN35900:PA22 | URBAN | Planned |  | 1 | 435 | 0.00029894 | 6.8722e-05 | N
18/06/2017 | 07:30 | ZN3472:PA16 | URBAN | Planned |  | 1 | 270 | 0.00018555 | 6.8722e-05 | N
18/06/2017 | 09:05 | ZN12580:PA16 | URBAN | Planned |  | 27 | 545 | 0.010112 | 0.0018555 | N
18/06/2017 | 22:00 | ZN3155:PA20 | URBAN | Planned |  | 175 | 420 | 0.05051 | 0.012026 | N
19/06/2017 | 07:30 | ZN965:PA20 | URBAN | Planned |  | 30 | 620 | 0.012782 | 0.0020617 | N
19/06/2017 | 07:30 | ZN965:PA38 | URBAN | Planned |  | 32 | 620 | 0.013634 | 0.0021991 | N
19/06/2017 | 08:00 | ZN10994:PA13 | URBAN | Planned |  | 61 | 360 | 0.015091 | 0.004192 | N
19/06/2017 | 09:05 | ZN711:PA11 | URBAN | Planned |  | 206 | 440 | 0.062289 | 0.014157 | N
19/06/2017 | 08:12 | ZN12660:PA14 | SHORT RURAL | Planned |  | 247 | 438 | 0.48424 | 0.11056 | N
19/06/2017 | 09:15 | ZN12650:PA1 | SHORT RURAL | Planned |  | 9 | 404 | 0.016275 | 0.0040284 | N
19/06/2017 | 08:45 | ZN14144:PA10 | SHORT RURAL | Planned |  | 34 | 390 | 0.059352 | 0.015219 | N
19/06/2017 | 10:20 | ZN12580:PA1 | URBAN | Planned |  | 76 | 265 | 0.013841 | 0.0052228 | N
19/06/2017 | 09:03 | ZN12630:PA8 | SHORT RURAL | Planned |  | 18 | 416 | 0.033517 | 0.0080569 | N
19/06/2017 | 19:00 | ZN187:PA10 | URBAN | Planned |  | 11 | 660 | 0.0049892 | 0.00075594 | N
19/06/2017 | 22:00 | ZN72:PA10 | URBAN | Planned |  | 23 | 383 | 0.0060537 | 0.0015806 | N
20/06/2017 | 09:30 | ZN965:PA38 | URBAN | Planned |  | 32 | 450 | 0.0098959 | 0.0021991 | N
20/06/2017 | 08:03 | ZN12660:PA10 | URBAN | Planned |  | 144 | 447 | 0.044235 | 0.0098959 | N
20/06/2017 | 08:30 | ZN9245:PA21 | URBAN | Planned |  | 47 | 420 | 0.013566 | 0.0032299 | N
20/06/2017 | 08:30 | ZN3155:PA23 | URBAN | Planned |  | 19 | 360 | 0.0047006 | 0.0013057 | N
22/06/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 65 | 420 | 0.018761 | 0.0044669 | N
22/06/2017 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 19 | 420 | 0.005484 | 0.0013057 | N
21/06/2017 | 06:45 | ZN1285:PA29 | URBAN | Planned |  | 14 | 195 | 0.0018761 | 0.0009621 | N
21/06/2017 | 07:00 | ZN35900:PA17 | URBAN | Planned |  | 80 | 480 | 0.026389 | 0.0054977 | N
21/06/2017 | 07:00 | ZN35900:PA2 | URBAN | Planned |  | 56 | 480 | 0.018472 | 0.0038484 | N
21/06/2017 | 08:30 | ZN15005:PA10 | URBAN | Planned |  | 5 | 380 | 0.0013057 | 0.00034361 | N
21/06/2017 | 09:26 | ZN965:PA38 | URBAN | Planned |  | 31 | 964 | 0.020537 | 0.0021304 | N
21/06/2017 | 07:30 | ZN2835:PA15 | URBAN | Planned |  | 29 | 450 | 0.0089682 | 0.0019929 | N
21/06/2017 | 08:38 | ZN14144:PA10 | SHORT RURAL | Planned |  | 34 | 397 | 0.060418 | 0.015219 | N
21/06/2017 | 08:00 | ZN15005:PA12 | URBAN | Planned |  | 45 | 420 | 0.012988 | 0.0030925 | N
21/06/2017 | 10:00 | ZN384:PA70 | URBAN | Planned |  | 56 | 110 | 0.0042333 | 0.0038484 | N
22/06/2017 | 08:30 | ZN931:PA9 | URBAN | Planned |  | 32 | 210 | 0.0046181 | 0.0021991 | N
22/06/2017 | 08:30 | ZN15005:PA10 | URBAN | Planned |  | 5 | 390 | 0.0013401 | 0.00034361 | N
22/06/2017 | 09:00 | ZN15014:PA5 | URBAN | Planned |  | 41 | 192 | 0.0054098 | 0.0028176 | N
22/06/2017 | 08:30 | ZN14144:PA10 | SHORT RURAL | Planned |  | 34 | 410 | 0.062396 | 0.015219 | N
22/06/2017 | 08:45 | ZN12600:PA2 | SHORT RURAL | Planned |  | 11 | 365 | 0.017971 | 0.0049236 | N
22/06/2017 | 08:00 | ZN15005:PA12 | URBAN | Planned |  | 45 | 420 | 0.012988 | 0.0030925 | N
22/06/2017 | 08:00 | ZN35600:PA9 | URBAN | Planned |  | 60 | 540 | 0.022266 | 0.0041233 | N
22/06/2017 | 09:15 | ZN711:PA3 | URBAN | Planned |  | 279 | 215 | 0.041223 | 0.019173 | N
22/06/2017 | 09:38 | ZN2835:PA22 | URBAN | Planned |  | 18 | 377 | 0.0046635 | 0.001237 | N
22/06/2017 | 11:40 | ZN3155:PA17 | URBAN | Planned |  | 102 | 260 | 0.018225 | 0.0070096 | N
22/06/2017 | 21:30 | ZN35500:PA15 | URBAN | Planned |  | 78 | 230 | 0.012329 | 0.0053603 | N
22/06/2017 | 22:15 | ZN15009:PA5 | URBAN | Planned |  | 70 | 120 | 0.0057726 | 0.0048105 | N
23/06/2017 | 09:09 | ZN15010:PA11 | URBAN | Planned |  | 46 | 244 | 0.0077044 | 0.0031575 | N
23/06/2017 | 08:30 | ZN12640:PA19 | URBAN | Planned |  | 124 | 440 | 0.037451 | 0.0085116 | N
23/06/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052717 | 0.0021966 | N
23/06/2017 | 12:00 | ZN3472:PA18 | URBAN | Planned |  | 1 | 390 | 0.00026771 | 6.8642e-05 | N
23/06/2017 | 20:59 | ZN180:PA41 | URBAN | Planned |  | 37 | 482 | 0.012242 | 0.0025398 | N
24/06/2017 | 09:45 | ZN35800:PA10 | URBAN | Planned |  | 30 | 315 | 0.0064867 | 0.0020593 | N
24/06/2017 | 20:59 | ZN180:PA41 | URBAN | Planned |  | 37 | 482 | 0.012242 | 0.0025398 | N
25/06/2017 | 08:40 | ZN13000:PA4 | URBAN | Planned |  | 1 | 505 | 0.00034664 | 6.8642e-05 | N
25/06/2017 | 08:40 | ZN13000:PA4 | URBAN | Planned |  | 86 | 500 | 0.029516 | 0.0059032 | N
25/06/2017 | 21:30 | ZN7900:PA11 | URBAN | Planned |  | 19 | 390 | 0.0050864 | 0.0013042 | N
25/06/2017 | 09:00 | ZN195:PA11 | URBAN | Planned |  | 2 | 375 | 0.00051482 | 0.00013728 | N
25/06/2017 | 23:00 | ZN2635:PA40 | URBAN | Planned |  | 21 | 1,090 | 0.015712 | 0.0014415 | N
26/06/2017 | 09:15 | ZN9245:PA19 | URBAN | Planned |  | 41 | 375 | 0.010554 | 0.0028143 | N
26/06/2017 | 09:15 | ZN9245:PA19 | URBAN | Planned |  | 28 | 375 | 0.0072074 | 0.001922 | N
26/06/2017 | 08:00 | ZN2196:PA4 | URBAN | Planned |  | 11 | 495 | 0.0037376 | 0.00075507 | N
26/06/2017 | 08:40 | ZN12600:PA11 | URBAN | Planned |  | 10 | 395 | 0.0027114 | 0.00068642 | N
26/06/2017 | 09:10 | ZN12690:PA3 | SHORT RURAL | Planned |  | 130 | 375 | 0.21821 | 0.058188 | N
27/06/2017 | 05:05 | ZN180:PA15 | URBAN | Planned |  | 2 | 33 | 4.5304e-05 | 0.00013728 | N
27/06/2017 | 07:50 | ZN965:PA38 | URBAN | Planned |  | 38 | 580 | 0.015129 | 0.0026084 | N
27/06/2017 | 09:30 | ZN3472:PA30 | URBAN | Planned |  | 30 | 180 | 0.0037067 | 0.0020593 | N
27/06/2017 | 08:12 | ZN14891:PA14 | URBAN | Planned |  | 5 | 373 | 0.0012802 | 0.00034321 | N
27/06/2017 | 08:35 | ZN342:PA22 | URBAN | Planned |  | 31 | 470 | 0.010001 | 0.0021279 | N
27/06/2017 | 08:35 | ZN342:PA22 | URBAN | Planned |  | 185 | 355 | 0.045081 | 0.012699 | N
27/06/2017 | 08:20 | ZN7900:PA11 | URBAN | Planned |  | 105 | 430 | 0.030992 | 0.0072074 | N
27/06/2017 | 11:35 | ZN9700:PA20 | URBAN | Planned |  | 4 | 235 | 0.00064524 | 0.00027457 | N
28/06/2017 | 00:45 | ZN2635:PA40 | URBAN | Planned |  | 11 | 1,575 | 0.011892 | 0.00075507 | N
28/06/2017 | 07:30 | ZN15005:PA6 | URBAN | Planned |  | 66 | 375 | 0.016989 | 0.0045304 | N
28/06/2017 | 09:00 | ZN965:PA8 | URBAN | Planned |  | 39 | 480 | 0.01285 | 0.0026771 | N
28/06/2017 | 08:00 | ZN1285:PA17 | URBAN | Planned |  | 42 | 300 | 0.0086489 | 0.002883 | N
28/06/2017 | 08:00 | ZN35900:PA1 | URBAN | Planned |  | 53 | 504 | 0.018336 | 0.003638 | N
28/06/2017 | 08:00 | ZN35900:PA1 | URBAN | Planned |  | 46 | 495 | 0.01563 | 0.0031575 | N
28/06/2017 | 08:15 | ZN14144:PA2 | SHORT RURAL | Planned |  | 1 | 117 | 0.0005237 | 0.0004476 | N
28/06/2017 | 08:30 | ZN342:PA22 | URBAN | Planned |  | 114 | 280 | 0.021911 | 0.0078252 | N
28/06/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052717 | 0.0021966 | N
29/06/2017 | 05:10 | ZN15001:PA10 | URBAN | Planned |  | 77 | 10 | 0.00052855 | 0.0052855 | N
29/06/2017 | 06:00 | ZN965:PA43 | URBAN | Planned |  | 1 | 480 | 0.00032948 | 6.8642e-05 | N
29/06/2017 | 07:00 | ZN36100:PA23 | URBAN | Planned |  | 86 | 450 | 0.026565 | 0.0059032 | N
29/06/2017 | 08:15 | ZN15013:PA10 | SHORT RURAL | Planned |  | 27 | 540 | 0.065261 | 0.012085 | N
29/06/2017 | 08:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 5 | 490 | 0.010966 | 0.002238 | N
29/06/2017 | 08:00 | ZN12690:PA12 | SHORT RURAL | Planned |  | 1 | 480 | 0.0021485 | 0.0004476 | N
29/06/2017 | 08:00 | ZN1068:PA21 | URBAN | Planned |  | 66 | 360 | 0.016309 | 0.0045304 | N
29/06/2017 | 08:00 | ZN35900:PA1 | URBAN | Planned |  | 63 | 482 | 0.020844 | 0.0043245 | N
29/06/2017 | 08:00 | ZN180:PA10 | URBAN | Planned |  | 89 | 540 | 0.03299 | 0.0061092 | N
29/06/2017 | 09:45 | ZN1287:PA4 | URBAN | Planned |  | 2 | 345 | 0.00047363 | 0.00013728 | N
29/06/2017 | 10:00 | ZN965:PA3 | URBAN | Planned |  | 32 | 240 | 0.0052717 | 0.0021966 | N
29/06/2017 | 08:15 | ZN15013:PA10 | SHORT RURAL | Planned |  | 28 | 540 | 0.067678 | 0.012533 | N
30/06/2017 | 02:00 | ZN12690:PA4 | URBAN | Planned |  | 3 | 20 | 4.1185e-05 | 0.00020593 | N
30/06/2017 | 02:30 | ZN12690:PA4 | URBAN | Planned |  | 2 | 15 | 2.0593e-05 | 0.00013728 | N
30/06/2017 | 03:40 | ZN12690:PA4 | URBAN | Planned |  | 6 | 20 | 8.2371e-05 | 0.00041185 | N
30/06/2017 | 04:10 | ZN12690:PA11 | URBAN | Planned |  | 1 | 20 | 1.3728e-05 | 6.8642e-05 | N
30/06/2017 | 04:40 | ZN12690:PA11 | URBAN | Planned |  | 7 | 20 | 9.6099e-05 | 0.0004805 | N
30/06/2017 | 05:10 | ZN12690:PA11 | URBAN | Planned |  | 1 | 20 | 1.3728e-05 | 6.8642e-05 | N
30/06/2017 | 03:00 | ZN12690:PA4 | URBAN | Planned |  | 2 | 20 | 2.7457e-05 | 0.00013728 | N
30/06/2017 | 07:30 | ZN9118:PA6 | URBAN | Planned |  | 9 | 30 | 0.00018533 | 0.00061778 | N
30/06/2017 | 08:10 | ZN14892:PA5 | URBAN | Planned |  | 8 | 440 | 0.0024162 | 0.00054914 | N
30/06/2017 | 08:20 | ZN35900:PA1 | URBAN | Planned |  | 53 | 280 | 0.010187 | 0.003638 | N
30/06/2017 | 18:05 | ZN35800:PA13 | URBAN | Planned |  | 2 | 315 | 0.00043245 | 0.00013728 | N
19/06/2017 | 07:30 | ZN1788:PA36 | URBAN | Planned |  | 2 | 13,440 | 0.018472 | 0.00013744 | N
06/07/2016 | 11:52 | 813:89063 | SHORT RURAL | Animal | Animal impact | 379 | 41 | 0.070753 | 0.17257 | N
16/07/2016 | 08:48 | ZN15001:PA13 | URBAN | Animal | Animal impact | 94 | 70 | 0.0045562 | 0.0065088 | N
16/07/2016 | 08:48 | ZN15001:PA15 | URBAN | Animal | Animal impact | 2,866 | 70 | 0.13891 | 0.19845 | N
16/07/2016 | 08:48 | ZN15001:PA16 | URBAN | Animal | Animal impact | 546 | 70 | 0.026465 | 0.037806 | N
16/07/2016 | 08:48 | ZN15001:PA17 | URBAN | Animal | Animal impact | 9 | 70 | 0.00043623 | 0.00062318 | N
16/07/2016 | 08:48 | ZN15001:PA18 | URBAN | Animal | Animal impact | 1,080 | 70 | 0.052347 | 0.074782 | N
17/07/2016 | 07:25 | 512:48049 | SHORT RURAL | Animal | Animal impact | 3 | 60 | 0.00081733 | 0.0013622 | N
19/07/2016 | 02:34 | 205:12205 | SHORT RURAL | Animal | Animal impact | 31 | 87 | 0.012253 | 0.014084 | N
20/07/2016 | 06:24 | 814:82291 | SHORT RURAL | Animal | Animal impact | 1 | 175 | 0.00079558 | 0.00045397 | N
23/07/2016 | 18:49 | 233:82812 | SHORT RURAL | Animal | Animal impact | 24 | 251 | 0.02734 | 0.010894 | N
25/07/2016 | 21:31 | 223:14399 | SHORT RURAL | Animal | Animal impact | 1 | 84 | 0.00038128 | 0.00045391 | N
27/07/2016 | 05:44 | ZN15005:PA4 | URBAN | Animal | Animal impact | 52 | 126 | 0.0045304 | 0.0036003 | N
04/08/2016 | 23:30 | ZN12580:PA4 | URBAN | Animal | Animal impact | 71 | 10 | 0.00049115 | 0.0049115 | N
05/08/2016 | 14:53 | 813:89062 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 117 | 0.00053124 | 0.00045463 | N
08/08/2016 | 01:28 | ZN15014:PA11 | URBAN | Animal | Animal impact | 1,014 | 69 | 0.048401 | 0.070146 | N
08/08/2016 | 01:28 | ZN15014:PA20 | URBAN | Animal | Animal impact | 1 | 69 | 4.7733e-05 | 6.9178e-05 | N
08/08/2016 | 23:48 | ZN4545:PA29 | URBAN | Animal | Animal impact | 1,679 | 140 | 0.16218 | 0.11615 | N
08/08/2016 | 23:48 | ZN4545:PA36 | URBAN | Animal | Animal impact | 1 | 119 | 8.2322e-05 | 6.9178e-05 | N
11/08/2016 | 17:40 | 243:80083 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 85 | 0.0003876 | 0.000456 | N
17/08/2016 | 21:05 | ZN13000:PA7 | SHORT RURAL | Animal | Animal impact | 1,398 | 55 | 0.35063 | 0.63752 | N
25/08/2016 | 05:18 | 205:12205 | SHORT RURAL | Animal | Animal impact | 31 | 92 | 0.012979 | 0.014162 | N
25/08/2016 | 12:50 | 801:74120 | URBAN | Animal | Animal impact | 25 | 75 | 0.0012955 | 0.0017274 | N
25/08/2016 | 14:34 | 801:74120 | URBAN | Animal | Animal impact | 25 | 11 | 0.00019001 | 0.0017274 | N
26/08/2016 | 00:00 | ZN14891:PA16 | SHORT RURAL | Animal | Animal impact | 51 | 40 | 0.0093195 | 0.023299 | N
01/09/2016 | 02:50 | ZN12620:PA1 | SHORT RURAL | Animal | Animal impact | 2,692 | 77 | 0.94037 | 1.2288 | N
04/09/2016 | 08:28 | 812:19065 | SHORT RURAL | Animal | Animal impact | 3 | 67 | 0.00091752 | 0.0013694 | N
07/09/2016 | 23:41 | ZN10993:PA22 | URBAN | Animal | Animal impact | 1 | 84 | 5.7996e-05 | 6.9043e-05 | N
07/09/2016 | 23:41 | ZN10999:PA24 | URBAN | Animal | Animal impact | 2,519 | 84 | 0.14609 | 0.17392 | N
16/09/2016 | 04:42 | ZN15001:PA8 | URBAN | Animal | Animal impact | 686 | 46 | 0.02179 | 0.04737 | N
18/09/2016 | 08:10 | 814:82291 | SHORT RURAL | Animal | Animal impact | 6 | 170 | 0.0046311 | 0.0027242 | N
19/09/2016 | 06:54 | ZN12630:PA23 | SHORT RURAL | Animal | Animal impact | 421 | 97 | 0.18586 | 0.19115 | N
19/09/2016 | 06:54 | ZN12630:PA25 | SHORT RURAL | Animal | Animal impact | 7 | 86 | 0.0027333 | 0.0031782 | N
19/09/2016 | 19:15 | 520:48172 | SHORT RURAL | Animal | Animal impact | 4 | 70 | 0.0012713 | 0.0018161 | N
29/09/2016 | 05:18 | ZN12690:PA16 | SHORT RURAL | Animal | Animal impact | 27 | 97 | 0.011843 | 0.012252 | N
30/09/2016 | 04:25 | 205:12210 | URBAN | Animal | Animal impact | 93 | 101 | 0.0064838 | 0.0064196 | N
03/10/2016 | 22:07 | ZN14891:PA16 | SHORT RURAL | Animal | Animal impact | 51 | 68 | 0.015691 | 0.023087 | N
05/10/2016 | 03:11 | ZN10994:PA11 | URBAN | Animal | Animal impact | 125 | 91 | 0.0078916 | 0.0086326 | N
05/10/2016 | 23:11 | 224:80337 | SHORT RURAL | Animal | Animal impact | 123 | 39 | 0.021437 | 0.05568 | N
08/10/2016 | 03:39 | ZN3472:PA28 | URBAN | Animal | Animal impact | 1,505 | 140 | 0.14569 | 0.10397 | N
08/10/2016 | 04:24 | ZN12630:PA24 | SHORT RURAL | Animal | Animal impact | 2 | 149 | 0.0013486 | 0.00090508 | N
13/10/2016 | 17:23 | 813:89055 | SHORT RURAL | Animal | Animal impact | 1 | 47 | 0.00021244 | 0.00045199 | N
13/10/2016 | 18:02 | ZN2196:PA5 | URBAN | Animal | Animal impact | 16 | 153 | 0.0016926 | 0.0011062 | N
16/10/2016 | 05:27 | 264:81240 | SHORT RURAL | Animal | Animal impact | 1 | 121 | 0.00054657 | 0.00045041 | N
17/10/2016 | 02:35 | 258:80775 | URBAN | Animal | Animal impact | 2,009 | 43 | 0.059667 | 0.13876 | N
21/10/2016 | 10:53 | 814:82285 | SHORT RURAL | Animal | Animal impact | 1 | 82 | 0.00037039 | 0.00045317 | N
22/10/2016 | 23:51 | ZN14891:PA16 | SHORT RURAL | Animal | Animal impact | 120 | 54 | 0.029175 | 0.054027 | N
23/10/2016 | 04:54 | ZN9118:PA17 | URBAN | Animal | Animal impact | 1,034 | 52 | 0.037235 | 0.071406 | N
25/10/2016 | 02:56 | ZN15008:PA1 | URBAN | Animal | Animal impact | 2,309 | 100 | 0.15946 | 0.15946 | N
25/10/2016 | 02:56 | ZN15008:PA10 | URBAN | Animal | Animal impact | 1,757 | 99 | 0.12012 | 0.12134 | N
25/10/2016 | 02:56 | ZN15008:PA5 | URBAN | Animal | Animal impact | 2,115 | 99 | 0.1446 | 0.14606 | N
25/10/2016 | 02:56 | ZN15008:PA7 | URBAN | Animal | Animal impact | 2,645 | 100 | 0.18266 | 0.18266 | N
25/10/2016 | 02:56 | ZN15008:PA9 | URBAN | Animal | Animal impact | 2,216 | 99 | 0.1515 | 0.15303 | N
27/10/2016 | 17:02 | 507:80923 | SHORT RURAL | Animal | Animal impact | 835 | 45 | 0.16787 | 0.37585 | N
27/10/2016 | 17:11 | 515:35200 | URBAN | Animal | Animal impact | 2 | 59 | 8.1464e-05 | 0.00013807 | N
27/10/2016 | 21:14 | 508:82579 | SHORT RURAL | Animal | Animal impact | 376 | 195 | 0.32984 | 0.16924 | N
28/10/2016 | 03:09 | 221:11894 | URBAN | Animal | Animal impact | 57 | 46 | 0.0018101 | 0.0039351 | N
28/10/2016 | 13:57 | 264:81232 | URBAN | Animal | Animal impact | 8 | 198 | 0.0010935 | 0.0005523 | N
30/10/2016 | 23:01 | ZN3425:PA28 | URBAN | Animal | Animal impact | 640 | 61 | 0.026953 | 0.044185 | N
29/10/2016 | 05:12 | ZN195:PA25 | URBAN | Animal | Animal impact | 763 | 20 | 0.010535 | 0.052676 | N
29/10/2016 | 05:12 | ZN195:PA29 | URBAN | Animal | Animal impact | 482 | 20 | 0.0066553 | 0.033276 | N
29/10/2016 | 05:12 | ZN195:PA4 | URBAN | Animal | Animal impact | 5 | 20 | 6.9038e-05 | 0.00034519 | N
28/10/2016 | 01:55 | ZN14891:PA5 | SHORT RURAL | Animal | Animal impact | 58 | 64 | 0.016708 | 0.026107 | N
02/11/2016 | 01:57 | 520:48172 | SHORT RURAL | Animal | Animal impact | 416 | 67 | 0.12533 | 0.18727 | N
04/11/2016 | 03:32 | 205:12203 | URBAN | Animal | Animal impact | 65 | 38 | 0.0017049 | 0.0044865 | N
04/11/2016 | 22:02 | ZN12600:PA13 | SHORT RURAL | Animal | Animal impact | 39 | 34 | 0.0059667 | 0.017549 | N
05/11/2016 | 03:31 | ZN2635:PA35 | URBAN | Animal | Animal impact | 1,536 | 83 | 0.088001 | 0.10603 | N
05/11/2016 | 03:31 | ZN2635:PA52 | URBAN | Animal | Animal impact | 728 | 83 | 0.041709 | 0.050252 | N
05/11/2016 | 21:56 | ZN9118:PA22 | URBAN | Animal | Animal impact | 151 | 179 | 0.018621 | 0.010423 | N
07/11/2016 | 08:48 | 811:74234 | SHORT RURAL | Animal | Animal impact | 1 | 47 | 0.0002115 | 0.00044999 | N
08/11/2016 | 03:32 | ZN12620:PA8 | SHORT RURAL | Animal | Animal impact | 84 | 195 | 0.073804 | 0.0378 | N
08/11/2016 | 15:10 | 526:34639 | SHORT RURAL | Animal | Animal impact | 2 | 165 | 0.001485 | 0.0009 | N
08/11/2016 | 21:49 | 217:33610 | URBAN | Animal | Animal impact | 1,912 | 38 | 0.050657 | 0.13198 | N
09/11/2016 | 22:33 | 814:82289 | SHORT RURAL | Animal | Animal impact | 3 | 52 | 0.000702 | 0.00135 | N
10/11/2016 | 12:05 | ZN15011:PA2 | URBAN | Animal | Animal impact | 634 | 44 | 0.019257 | 0.043767 | N
10/11/2016 | 12:05 | ZN15011:PA8 | URBAN | Animal | Animal impact | 243 | 44 | 0.007381 | 0.016775 | N
11/11/2016 | 21:02 | ZN9550:PA4 | URBAN | Animal | Animal impact | 457 | 34 | 0.010726 | 0.031548 | N
12/11/2016 | 04:35 | ZN12690:PA16 | SHORT RURAL | Animal | Animal impact | 27 | 250 | 0.030359 | 0.012144 | N
14/11/2016 | 02:51 | ZN12570:PA21 | URBAN | Animal | Animal impact | 2,210 | 42 | 0.064056 | 0.15251 | N
14/11/2016 | 02:51 | ZN12570:PA22 | SHORT RURAL | Animal | Animal impact | 1,607 | 42 | 0.30357 | 0.72278 | N
14/11/2016 | 02:51 | ZN12570:PA24 | SHORT RURAL | Animal | Animal impact | 1,756 | 42 | 0.33171 | 0.78979 | N
14/11/2016 | 02:51 | ZN12570:PA25 | SHORT RURAL | Animal | Animal impact | 1,046 | 42 | 0.19759 | 0.47046 | N
14/11/2016 | 02:51 | ZN12570:PA26 | URBAN | Animal | Animal impact | 1,125 | 42 | 0.032608 | 0.077637 | N
14/11/2016 | 02:51 | ZN12570:PA29 | SHORT RURAL | Animal | Animal impact | 738 | 42 | 0.13941 | 0.33193 | N
14/11/2016 | 02:51 | ZN12570:PA33 | SHORT RURAL | Animal | Animal impact | 1,561 | 42 | 0.29488 | 0.70209 | N
14/11/2016 | 02:51 | ZN12570:PA34 | SHORT RURAL | Animal | Animal impact | 852 | 42 | 0.16094 | 0.3832 | N
14/11/2016 | 02:51 | ZN12570:PA35 | URBAN | Animal | Animal impact | 1,040 | 42 | 0.030144 | 0.071771 | N
14/11/2016 | 02:51 | ZN12570:PA37 | SHORT RURAL | Animal | Animal impact | 1,519 | 42 | 0.28694 | 0.6832 | N
14/11/2016 | 02:51 | ZN12570:PA39 | URBAN | Animal | Animal impact | 1,427 | 42 | 0.041361 | 0.098478 | N
14/11/2016 | 02:51 | ZN12570:PA40 | SHORT RURAL | Animal | Animal impact | 1,172 | 42 | 0.22139 | 0.52713 | N
14/11/2016 | 02:51 | ZN12570:PA41 | URBAN | Animal | Animal impact | 805 | 42 | 0.023333 | 0.055554 | N
14/11/2016 | 13:45 | 813:89055 | SHORT RURAL | Animal | Animal impact | 7 | 205 | 0.0064542 | 0.0031484 | N
17/11/2016 | 06:39 | ZN12690:PA24 | SHORT RURAL | Animal | Animal impact | 5 | 46 | 0.0010342 | 0.0022482 | N
20/11/2016 | 08:47 | 243:80075 | SHORT RURAL | Animal | Animal impact | 1 | 57 | 0.0002569 | 0.00044965 | N
20/11/2016 | 10:58 | 235:2728 | URBAN | Animal | Animal impact | 315 | 168 | 0.036436 | 0.021733 | N
20/11/2016 | 11:45 | 235:8685 | URBAN | Animal | Animal impact | 109 | 435 | 0.032714 | 0.0075205 | N
22/11/2016 | 02:00 | ZN15001:PA2 | URBAN | Animal | Animal impact | 2,293 | 44 | 0.069611 | 0.15821 | N
22/11/2016 | 02:00 | ZN15001:PA8 | URBAN | Animal | Animal impact | 232 | 44 | 0.0070431 | 0.016007 | N
22/11/2016 | 03:45 | 806:82662 | SHORT RURAL | Animal | Animal impact | 3 | 335 | 0.004519 | 0.0013489 | N
22/11/2016 | 09:55 | ZN12600:PA13 | SHORT RURAL | Animal | Animal impact | 96 | 8 | 0.0034533 | 0.043166 | N
29/11/2016 | 05:34 | 526:34639 | SHORT RURAL | Animal | Animal impact | 4 | 176 | 0.0031642 | 0.0017978 | N
29/11/2016 | 07:37 | 810:74054 | LONG RURAL | Animal | Animal impact | 1 | 142 | 0.050599 | 0.0356 | N
30/11/2016 | 00:37 | ZN9118:PA11 | URBAN | Animal | Animal impact | 794 | 138 | 0.075636 | 0.054809 | N
01/12/2016 | 08:23 | 807:74180 | SHORT RURAL | Animal | Animal impact | 1 | 92 | 0.00041198 | 0.00044927 | N
02/12/2016 | 01:55 | 214:8669 | URBAN | Animal | Animal impact | 54 | 47 | 0.0017514 | 0.0037265 | N
04/12/2016 | 22:16 | ZN12570:PA26 | URBAN | Animal | Animal impact | 1,128 | 83 | 0.064698 | 0.077786 | N
07/12/2016 | 00:06 | ZN4545:PA31 | URBAN | Animal | Animal impact | 2,989 | 57 | 0.11749 | 0.20613 | N
10/12/2016 | 08:01 | 225:33676 | URBAN | Animal | Animal impact | 42 | 63 | 0.0018357 | 0.0028954 | N
14/12/2016 | 03:46 | ZN15011:PA10 | URBAN | Animal | Animal impact | 1,477 | 69 | 0.070262 | 0.10183 | N
14/12/2016 | 03:46 | ZN15011:PA2 | URBAN | Animal | Animal impact | 1,690 | 69 | 0.080394 | 0.11651 | N
14/12/2016 | 03:46 | ZN15011:PA4 | URBAN | Animal | Animal impact | 62 | 69 | 0.0029494 | 0.0042745 | N
14/12/2016 | 03:46 | ZN15011:PA6 | URBAN | Animal | Animal impact | 1,994 | 69 | 0.094856 | 0.13747 | N
14/12/2016 | 03:46 | ZN15011:PA8 | URBAN | Animal | Animal impact | 242 | 69 | 0.011512 | 0.016684 | N
15/12/2016 | 01:31 | ZN1673:PA14 | URBAN | Animal | Animal impact | 1 | 659 | 0.00045389 | 6.8924e-05 | N
17/12/2016 | 02:55 | 513:48056 | SHORT RURAL | Animal | Animal impact | 4 | 60 | 0.0010778 | 0.0017963 | N
17/12/2016 | 23:44 | ZN15013:PA4 | URBAN | Animal | Animal impact | 90 | 61 | 0.0037841 | 0.0062034 | N
18/12/2016 | 07:48 | 528:83019 | SHORT RURAL | Animal | Animal impact | 4 | 82 | 0.001473 | 0.0017963 | N
18/12/2016 | 08:20 | 515:35197 | LONG RURAL | Animal | Animal impact | 3 | 95 | 0.1015 | 0.10684 | N
20/12/2016 | 21:57 | 520:48172 | SHORT RURAL | Animal | Animal impact | 3 | 733 | 0.0098753 | 0.0013472 | N
21/12/2016 | 02:37 | ZN10994:PA19 | URBAN | Animal | Animal impact | 903 | 85 | 0.052602 | 0.062242 | N
22/12/2016 | 08:30 | 807:74179 | SHORT RURAL | Animal | Animal impact | 1 | 10 | 4.4895e-05 | 0.00044895 | N
23/12/2016 | 14:08 | 810:74054 | LONG RURAL | Animal | Animal impact | 2 | 92 | 0.065527 | 0.071225 | N
23/12/2016 | 22:06 | ZN9550:PA4 | URBAN | Animal | Animal impact | 457 | 50 | 0.015819 | 0.031491 | N
24/12/2016 | 09:57 | 807:74184 | SHORT RURAL | Animal | Animal impact | 1 | 78 | 0.0003502 | 0.00044897 | N
25/12/2016 | 19:27 | 523:33501 | SHORT RURAL | Animal | Animal impact | 1 | 72 | 0.00032273 | 0.00044897 | N
26/12/2016 | 21:29 | ZN4545:PA31 | URBAN | Animal | Animal impact | 2,989 | 54 | 0.11083 | 0.20597 | N
26/12/2016 | 21:29 | ZN4545:PA41 | SHORT RURAL | Animal | Animal impact | 57 | 53 | 0.013563 | 0.025591 | N
27/12/2016 | 04:45 | ZN4545:PA31 | URBAN | Animal | Animal impact | 2,989 | 58 | 0.11946 | 0.20597 | N
27/12/2016 | 20:40 | 813:89061 | LONG RURAL | Animal | Animal impact | 1 | 78 | 0.027865 | 0.035625 | N
29/12/2016 | 19:10 | ZN9700:PA15 | URBAN | Animal | Animal impact | 14 | 260 | 0.0025052 | 0.00096473 | N
30/12/2016 | 20:01 | 810:74054 | LONG RURAL | Animal | Animal impact | 2 | 44 | 0.03135 | 0.07125 | N
31/12/2016 | 20:52 | 813:89063 | SHORT RURAL | Animal | Animal impact | 1 | 162 | 0.00072675 | 0.00044898 | N
01/01/2017 | 07:19 | 512:48049 | SHORT RURAL | Animal | Animal impact | 4 | 91 | 0.0016343 | 0.0017959 | N
02/01/2017 | 07:06 | 232:11457 | SHORT RURAL | Animal | Animal impact | 1 | 363 | 0.0016314 | 0.00044898 | N
09/01/2017 | 22:48 | 520:48172 | SHORT RURAL | Animal | Animal impact | 1 | 57 | 0.00025365 | 0.00044881 | N
10/01/2017 | 09:46 | 512:48049 | SHORT RURAL | Animal | Animal impact | 2 | 84 | 0.00075401 | 0.00089763 | N
11/01/2017 | 06:05 | ZN12630:PA1 | SHORT RURAL | Animal | Animal impact | 4 | 230 | 0.0041292 | 0.0017953 | N
11/01/2017 | 10:24 | 811:74234 | SHORT RURAL | Animal | Animal impact | 3 | 86 | 0.001158 | 0.0013465 | N
11/01/2017 | 22:19 | ZN129:PA16 | URBAN | Animal | Animal impact | 1,414 | 60 | 0.05845 | 0.097416 | N
11/01/2017 | 22:19 | ZN129:PA18 | URBAN | Animal | Animal impact | 873 | 60 | 0.036087 | 0.060144 | N
11/01/2017 | 22:19 | ZN129:PA21 | URBAN | Animal | Animal impact | 40 | 60 | 0.0016535 | 0.0027558 | N
11/01/2017 | 22:19 | ZN129:PA24 | URBAN | Animal | Animal impact | 1,580 | 60 | 0.065312 | 0.10885 | N
11/01/2017 | 22:19 | ZN129:PA25 | URBAN | Animal | Animal impact | 104 | 60 | 0.004299 | 0.007165 | N
11/01/2017 | 22:19 | ZN129:PA27 | URBAN | Animal | Animal impact | 207 | 60 | 0.0085566 | 0.014261 | N
11/01/2017 | 22:19 | ZN129:PA28 | URBAN | Animal | Animal impact | 941 | 60 | 0.038898 | 0.064829 | N
11/01/2017 | 22:19 | ZN129:PA4 | URBAN | Animal | Animal impact | 233 | 60 | 0.0096314 | 0.016052 | N
12/01/2017 | 06:28 | ZN35370:PA10 | SHORT RURAL | Animal | Animal impact | 19 | 291 | 0.024843 | 0.0085282 | N
16/01/2017 | 13:40 | 515:35197 | LONG RURAL | Animal | Animal impact | 3 | 62 | 0.066263 | 0.10688 | N
18/01/2017 | 07:49 | 801:74118 | URBAN | Animal | Animal impact | 73 | 101 | 0.0050547 | 0.0050287 | N
23/01/2017 | 09:42 | 806:82662 | SHORT RURAL | Animal | Animal impact | 227 | 85 | 0.086607 | 0.10189 | N
24/01/2017 | 08:46 | 515:35197 | LONG RURAL | Animal | Animal impact | 2 | 223 | 0.15918 | 0.071276 | N
27/01/2017 | 11:18 | 813:89063 | SHORT RURAL | Animal | Animal impact | 2 | 207 | 0.0018558 | 0.00089651 | N
27/01/2017 | 18:28 | ZN9035:PA1 | URBAN | Animal | Animal impact | 557 | 71 | 0.027264 | 0.038363 | N
27/01/2017 | 18:28 | ZN9035:PA10 | URBAN | Animal | Animal impact | 526 | 72 | 0.026084 | 0.036228 | N
27/01/2017 | 18:28 | ZN9035:PA11 | URBAN | Animal | Animal impact | 1,944 | 72 | 0.096402 | 0.13389 | N
27/01/2017 | 18:28 | ZN9035:PA2 | URBAN | Animal | Animal impact | 737 | 71 | 0.03604 | 0.05076 | N
27/01/2017 | 18:28 | ZN9035:PA4 | URBAN | Animal | Animal impact | 1,798 | 72 | 0.089162 | 0.12384 | N
27/01/2017 | 18:28 | ZN9035:PA5 | URBAN | Animal | Animal impact | 318 | 71 | 0.01555 | 0.021902 | N
27/01/2017 | 18:28 | ZN9035:PA7 | URBAN | Animal | Animal impact | 1,119 | 72 | 0.055491 | 0.07707 | N
27/01/2017 | 18:28 | ZN9035:PA8 | URBAN | Animal | Animal impact | 115 | 72 | 0.0057028 | 0.0079205 | N
28/01/2017 | 08:10 | 227:13018 | URBAN | Animal | Animal impact | 32 | 250 | 0.00551 | 0.002204 | N
29/01/2017 | 08:32 | 513:48056 | SHORT RURAL | Animal | Animal impact | 7 | 63 | 0.0019768 | 0.0031378 | N
31/01/2017 | 10:09 | 813:89063 | SHORT RURAL | Animal | Animal impact | 2 | 91 | 0.00081584 | 0.00089652 | N
31/01/2017 | 20:57 | ZN13000:PA2 | SHORT RURAL | Animal | Animal impact | 44 | 98 | 0.019329 | 0.019724 | N
01/02/2017 | 21:52 | ZN10997:PA1 | URBAN | Animal | Animal impact | 1,037 | 42 | 0.029998 | 0.071425 | N
01/02/2017 | 21:52 | ZN10997:PA2 | URBAN | Animal | Animal impact | 76 | 68 | 0.0035595 | 0.0052346 | N
03/02/2017 | 09:18 | 814:82285 | SHORT RURAL | Animal | Animal impact | 1 | 61 | 0.00027392 | 0.0004482 | N
08/02/2017 | 07:44 | ZN12620:PA7 | URBAN | Animal | Animal impact | 67 | 120 | 0.0055392 | 0.0046147 | N
08/02/2017 | 21:28 | ZN9700:PA17 | URBAN | Animal | Animal impact | 1 | 1,067 | 0.00073463 | 6.8876e-05 | N
09/02/2017 | 16:25 | 512:48049 | SHORT RURAL | Animal | Animal impact | 3 | 80 | 0.001074 | 0.0013424 | N
13/02/2017 | 10:21 | 807:74184 | SHORT RURAL | Animal | Animal impact | 1 | 154 | 0.00068911 | 0.00044747 | N
15/02/2017 | 02:39 | ZN9252:PA30 | URBAN | Animal | Animal impact | 1,332 | 81 | 0.074343 | 0.091782 | N
15/02/2017 | 04:37 | 524:33578 | URBAN | Animal | Animal impact | 89 | 248 | 0.015209 | 0.0061326 | N
15/02/2017 | 08:13 | ZN9700:PA23 | URBAN | Animal | Animal impact | 1 | 646 | 0.00044539 | 6.8905e-05 | N
17/02/2017 | 07:11 | 813:89062 | SHORT RURAL | Animal | Animal impact | 1 | 134 | 0.00059643 | 0.0004466 | Y
19/02/2017 | 11:14 | 233:82815 | SHORT RURAL | Animal | Animal impact | 15 | 109 | 0.0072853 | 0.0066991 | N
20/02/2017 | 21:41 | 243:80075 | SHORT RURAL | Animal | Animal impact | 30 | 104 | 0.013934 | 0.013398 | N
22/02/2017 | 14:40 | 512:48049 | SHORT RURAL | Animal | Animal impact | 4 | 95 | 0.0016972 | 0.0017865 | N
23/02/2017 | 16:41 | 813:89062 | SHORT RURAL | Animal | Animal impact | 2 | 54 | 0.00048221 | 0.00089299 | N
26/02/2017 | 02:20 | ZN12650:PA9 | URBAN | Animal | Animal impact | 60 | 85 | 0.0035128 | 0.0041327 | N
26/02/2017 | 06:40 | 221:11900 | SHORT RURAL | Animal | Animal impact | 80 | 88 | 0.031442 | 0.035729 | N
28/02/2017 | 00:47 | ZN15006:PA13 | URBAN | Animal | Animal impact | 1,310 | 99 | 0.08967 | 0.090232 | N
28/02/2017 | 22:05 | ZN12620:PA11 | SHORT RURAL | Animal | Animal impact | 40 | 100 | 0.017865 | 0.017865 | N
02/03/2017 | 13:05 | 810:74058 | SHORT RURAL | Animal | Animal impact | 2 | 110 | 0.00098259 | 0.00089326 | N
05/03/2017 | 20:52 | ZN10994:PA14 | URBAN | Animal | Animal impact | 500 | 71 | 0.024451 | 0.034438 | N
08/03/2017 | 22:53 | ZN129:PA24 | URBAN | Animal | Animal impact | 1,579 | 71 | 0.07722 | 0.10876 | N
08/03/2017 | 22:53 | ZN129:PA9 | URBAN | Animal | Animal impact | 63 | 71 | 0.003081 | 0.0043394 | N
11/03/2017 | 08:39 | 520:48172 | SHORT RURAL | Animal | Animal impact | 2 | 76 | 0.00067586 | 0.00088929 | N
13/03/2017 | 06:37 | 515:35197 | LONG RURAL | Animal | Animal impact | 1 | 233 | 0.082977 | 0.035613 | N
16/03/2017 | 13:24 | ZN9037:PA16 | URBAN | Animal | Animal impact | 1 | 95 | 6.5743e-05 | 6.8877e-05 | N
17/03/2017 | 09:26 | 813:89062 | SHORT RURAL | Animal | Animal impact | 1 | 164 | 0.0007289 | 0.00044445 | N
17/03/2017 | 11:41 | 813:89055 | SHORT RURAL | Animal | Animal impact | 6 | 29 | 0.00077334 | 0.0026667 | N
17/03/2017 | 15:06 | 227:13020 | SHORT RURAL | Animal | Animal impact | 9 | 114 | 0.00456 | 0.004 | N
25/03/2017 | 05:48 | ZN14144:PA4 | URBAN | Animal | Animal impact | 53 | 77 | 0.00281 | 0.0036493 | N
28/03/2017 | 21:42 | 243:80078 | SHORT RURAL | Animal | Animal impact | 95 | 98 | 0.041321 | 0.042165 | N
30/03/2017 | 15:42 | 807:74184 | SHORT RURAL | Animal | Animal impact | 2 | 88 | 0.00078067 | 0.00088712 | N
30/03/2017 | 19:54 | 801:74121 | LONG RURAL | Animal | Animal impact | 1 | 51 | 0.018208 | 0.035702 | N
01/04/2017 | 01:02 | 242:81539 | URBAN | Animal | Animal impact | 1,568 | 60 | 0.064817 | 0.10788 | N
02/04/2017 | 21:46 | ZN12570:PA22 | SHORT RURAL | Animal | Animal impact | 680 | 94 | 0.28464 | 0.30281 | N
04/04/2017 | 20:20 | ZN3154:PA23 | URBAN | Animal | Animal impact | 466 | 103 | 0.033026 | 0.032064 | N
05/04/2017 | 11:48 | 810:74062 | SHORT RURAL | Animal | Animal impact | 7 | 87 | 0.0027119 | 0.0031172 | N
06/04/2017 | 13:43 | ZN15006:PA13 | URBAN | Animal | Animal impact | 1,320 | 106 | 0.096045 | 0.090825 | N
11/04/2017 | 18:12 | ZN15012:PA2 | URBAN | Animal | Animal impact | 1 | 415 | 0.00028552 | 6.878e-05 | N
11/04/2017 | 20:49 | 221:11898 | URBAN | Animal | Animal impact | 31 | 106 | 0.0022601 | 0.0021322 | N
13/04/2017 | 00:20 | ZN2400:PA18 | SHORT RURAL | Animal | Animal impact | 44 | 74 | 0.014545 | 0.019599 | N
19/04/2017 | 13:51 | 233:82815 | SHORT RURAL | Animal | Animal impact | 22 | 113 | 0.011107 | 0.0097963 | N
20/04/2017 | 02:45 | ZN15015:PA15 | SHORT RURAL | Animal | Animal impact | 1 | 595 | 0.0026426 | 0.00044413 | N
22/04/2017 | 07:13 | 526:34639 | SHORT RURAL | Animal | Animal impact | 254 | 334 | 0.37703 | 0.11277 | N
28/04/2017 | 00:52 | ZN965:PA22 | URBAN | Animal | Animal impact | 564 | 55 | 0.02133 | 0.038781 | N
30/04/2017 | 03:04 | ZN15006:PA8 | URBAN | Animal | Animal impact | 1,910 | 209 | 0.27438 | 0.13134 | N
02/05/2017 | 20:09 | ZN10995:PA1 | URBAN | Animal | Animal impact | 84 | 81 | 0.0046787 | 0.0057762 | N
12/05/2017 | 04:50 | ZN3425:PA33 | URBAN | Animal | Animal impact | 237 | 39 | 0.006357 | 0.0163 | N
16/05/2017 | 22:46 | ZN9252:PA24 | URBAN | Animal | Animal impact | 1,948 | 59 | 0.078999 | 0.1339 | N
16/05/2017 | 22:46 | ZN9252:PA31 | URBAN | Animal | Animal impact | 1 | 59 | 4.0554e-05 | 6.8736e-05 | N
20/05/2017 | 21:15 | ZN9035:PA7 | URBAN | Animal | Animal impact | 2 | 104 | 0.0001432 | 0.00013745 | N
24/05/2017 | 18:13 | ZN9037:PA4 | URBAN | Animal | Animal impact | 1 | 227 | 0.000156 | 6.8723e-05 | N
24/05/2017 | 18:13 | ZN9700:PA11 | URBAN | Animal | Animal impact | 46 | 53 | 0.0016755 | 0.0031612 | N
24/05/2017 | 18:13 | ZN9700:PA15 | URBAN | Animal | Animal impact | 1,238 | 52 | 0.044241 | 0.085079 | N
24/05/2017 | 18:13 | ZN9700:PA16 | URBAN | Animal | Animal impact | 20 | 221 | 0.003032 | 0.0013745 | N
24/05/2017 | 18:13 | ZN9700:PA17 | URBAN | Animal | Animal impact | 2,253 | 52 | 0.080513 | 0.15483 | N
24/05/2017 | 18:13 | ZN9700:PA19 | URBAN | Animal | Animal impact | 904 | 52 | 0.032305 | 0.062125 | N
24/05/2017 | 18:13 | ZN9700:PA20 | URBAN | Animal | Animal impact | 1,810 | 53 | 0.065926 | 0.12439 | N
24/05/2017 | 18:13 | ZN9700:PA21 | URBAN | Animal | Animal impact | 482 | 53 | 0.017556 | 0.033124 | N
24/05/2017 | 18:13 | ZN9700:PA22 | URBAN | Animal | Animal impact | 248 | 53 | 0.0090329 | 0.017043 | N
24/05/2017 | 18:13 | ZN9700:PA23 | URBAN | Animal | Animal impact | 1,641 | 108 | 0.12176 | 0.11277 | N
26/05/2017 | 08:18 | ZN129:PA38 | URBAN | Animal | Animal impact | 1,218 | 102 | 0.085601 | 0.083704 | Y
26/05/2017 | 16:30 | 526:34636 | SHORT RURAL | Animal | Animal impact | 1 | 1,115 | 0.0049908 | 0.00044761 | Y
27/05/2017 | 23:54 | 217:33611 | URBAN | Animal | Animal impact | 493 | 41 | 0.013891 | 0.03388 | N
02/06/2017 | 06:45 | 523:33501 | SHORT RURAL | Animal | Animal impact | 3 | 105 | 0.00141 | 0.0013428 | N
05/06/2017 | 11:34 | 813:89062 | SHORT RURAL | Animal | Animal impact | 1 | 141 | 0.00063112 | 0.0004476 | N
07/06/2017 | 07:56 | ZN14144:PA5 | SHORT RURAL | Animal | Animal impact | 1 | 199 | 0.00088916 | 0.0004476 | N
08/06/2017 | 04:46 | ZN12620:PA11 | SHORT RURAL | Animal | Animal impact | 16 | 245 | 0.017531 | 0.0071617 | N
17/06/2017 | 18:32 | 508:82574 | SHORT RURAL | Animal | Animal impact | 191 | 75 | 0.06424 | 0.085492 | N
18/06/2017 | 08:19 | 223:14398 | URBAN | Animal | Animal impact | 52 | 111 | 0.0039666 | 0.0035735 | N
21/06/2017 | 19:16 | 232:33409 | SHORT RURAL | Animal | Animal impact | 3,382 | 18 | 0.27401 | 1.5138 | N
27/06/2017 | 09:41 | 807:74179 | SHORT RURAL | Animal | Animal impact | 1 | 117 | 0.00052161 | 0.0004476 | N
27/06/2017 | 19:20 | ZN965:PA33 | URBAN | Animal | Animal impact | 49 | 69 | 0.0023363 | 0.0033635 | N
28/06/2017 | 05:35 | 813:89065 | URBAN | Animal | Animal impact | 1 | 474 | 0.00032502 | 6.8642e-05 | N
06/07/2016 | 12:05 | ZN12610:PA2 | URBAN | Weather |  | 115 | 155 | 0.012331 | 0.0079648 | N
13/07/2016 | 12:48 | ZN188:PA1 | URBAN | Weather |  | 109 | 156 | 0.011811 | 0.0075487 | N
13/07/2016 | 12:48 | ZN188:PA21 | URBAN | Weather |  | 100 | 157 | 0.010873 | 0.0069254 | N
13/07/2016 | 13:53 | ZN3155:PA15 | URBAN | Weather |  | 60 | 126 | 0.0052384 | 0.0041552 | N
15/07/2016 | 12:04 | ZN9252:PA22 | URBAN | Weather |  | 38 | 146 | 0.0038322 | 0.0026317 | N
23/07/2016 | 06:50 | ZN12640:PA15 | URBAN | Weather |  | 74 | 83 | 0.0042345 | 0.0051234 | N
23/07/2016 | 08:16 | ZN15002:PA8 | URBAN | Weather |  | 52 | 199 | 0.0071644 | 0.0036002 | N
23/07/2016 | 08:19 | 256:80653 | URBAN | Weather |  | 70 | 111 | 0.0053569 | 0.0048465 | N
23/07/2016 | 10:03 | ZN12640:PA15 | URBAN | Weather |  | 47 | 127 | 0.0041326 | 0.003254 | N
23/07/2016 | 10:51 | ZN3154:PA16 | URBAN | Weather |  | 41 | 124 | 0.0035199 | 0.0028386 | N
23/07/2016 | 11:07 | ZN3425:PA30 | URBAN | Weather |  | 42 | 203 | 0.0058943 | 0.0029079 | N
21/07/2016 | 09:00 | ZN9245:PA41 | URBAN | Weather |  | 18 | 300 | 0.0037384 | 0.0012461 | N
03/08/2016 | 15:03 | ZN12660:PA14 | SHORT RURAL | Weather |  | 6 | 1,562 | 0.042521 | 0.0027222 | N
20/08/2016 | 07:22 | ZN4545:PA26 | URBAN | Weather |  | 9 | 84 | 0.00052451 | 0.00062442 | N
25/08/2016 | 15:16 | ZN15001:PA10 | URBAN | Weather |  | 25 | 334 | 0.005761 | 0.0017274 | N
03/09/2016 | 13:27 | 238:34141 | SHORT RURAL | Weather |  | 31 | 83 | 0.011745 | 0.014151 | N
03/09/2016 | 15:56 | 230:81440 | SHORT RURAL | Weather |  | 1 | 377 | 0.0017227 | 0.00045648 | N
03/09/2016 | 16:52 | ZN36200:PA11 | SHORT RURAL | Weather |  | 1 | 352 | 0.0016076 | 0.00045648 | N
04/09/2016 | 08:18 | ZN80:PA25 | URBAN | Weather |  | 29 | 89 | 0.001782 | 0.0020022 | N
19/09/2016 | 09:58 | ZN10994:PA1 | URBAN | Weather |  | 18 | 104 | 0.0012929 | 0.0012432 | N
27/09/2016 | 17:32 | 813:89063 | SHORT RURAL | Weather |  | 1 | 87 | 0.00039639 | 0.00045388 | N
30/09/2016 | 09:42 | 516:48066 | SHORT RURAL | Weather |  | 5 | 153 | 0.0034713 | 0.0022688 | N
01/10/2016 | 16:33 | 801:74121 | LONG RURAL | Weather |  | 1 | 77 | 0.02748 | 0.035689 | N
04/10/2016 | 10:39 | ZN1673:PA2 | URBAN | Weather |  | 1 | 291 | 0.00020063 | 6.9059e-05 | N
05/11/2016 | 15:09 | 513:48056 | SHORT RURAL | Weather |  | 90 | 68 | 0.027477 | 0.040499 | N
05/11/2016 | 15:50 | 265:81641 | URBAN | Weather |  | 1 | 115 | 7.9381e-05 | 6.9027e-05 | N
08/11/2016 | 12:20 | ZN2635:PA43 | URBAN | Weather |  | 1 | 100 | 6.8684e-05 | 6.9029e-05 | N
09/11/2016 | 18:32 | ZN12650:PA1 | SHORT RURAL | Weather |  | 3 | 118 | 0.001593 | 0.00135 | N
13/11/2016 | 15:00 | ZN690:PA4 | URBAN | Weather |  | 38 | 1,154 | 0.030266 | 0.0026224 | N
23/11/2016 | 16:09 | ZN847:PA2 | URBAN | Weather |  | 1 | 380 | 0.00026247 | 6.8998e-05 | N
23/11/2016 | 17:35 | 240:34849 | SHORT RURAL | Weather |  | 152 | 99 | 0.067709 | 0.068347 | N
30/11/2016 | 16:41 | 810:74058 | SHORT RURAL | Weather |  | 1 | 380 | 0.0017062 | 0.00044945 | N
01/12/2016 | 08:00 | 520:48172 | SHORT RURAL | Weather |  | 1 | 209 | 0.00093852 | 0.00044927 | N
02/12/2016 | 21:25 | ZN10999:PA39 | URBAN | Weather |  | 1 | 196 | 0.00013556 | 6.9009e-05 | N
05/12/2016 | 15:08 | 528:83020 | SHORT RURAL | Weather |  | 520 | 145 | 0.33812 | 0.23362 | N
05/12/2016 | 16:06 | 508:82574 | SHORT RURAL | Weather |  | 1 | 294 | 0.0013209 | 0.00044927 | N
05/12/2016 | 16:50 | 523:33501 | SHORT RURAL | Weather |  | 3 | 1,120 | 0.015096 | 0.0013478 | N
06/12/2016 | 14:27 | 811:74234 | SHORT RURAL | Weather |  | 1 | 253 | 0.0011358 | 0.00044927 | N
20/12/2016 | 12:00 | 504:48033 | SHORT RURAL | Weather |  | 1 | 329 | 0.0014785 | 0.00044908 | N
22/12/2016 | 12:21 | ZN12640:PA13 | SHORT RURAL | Weather |  | 1 | 189 | 0.00084852 | 0.00044895 | N
24/12/2016 | 17:48 | 512:48049 | SHORT RURAL | Weather |  | 3 | 877 | 0.011812 | 0.0013469 | N
24/12/2016 | 17:53 | 511:29878 | SHORT RURAL | Weather |  | 1 | 360 | 0.0016163 | 0.00044897 | N
24/12/2016 | 18:38 | 511:29878 | SHORT RURAL | Weather |  | 1 | 442 | 0.0019829 | 0.00044897 | N
24/12/2016 | 20:46 | 508:82579 | SHORT RURAL | Weather |  | 2 | 99 | 0.00088896 | 0.00089794 | N
25/12/2016 | 01:52 | 520:48172 | SHORT RURAL | Weather |  | 3 | 53 | 0.00071386 | 0.0013469 | N
25/12/2016 | 06:38 | 801:74121 | LONG RURAL | Weather |  | 1 | 352 | 0.1254 | 0.035625 | N
26/12/2016 | 07:46 | 511:29878 | SHORT RURAL | Weather |  | 1 | 153 | 0.00068872 | 0.00044897 | N
11/01/2017 | 17:43 | ZN9035:PA1 | URBAN | Weather |  | 458 | 37 | 0.011675 | 0.031553 | N
11/01/2017 | 17:43 | ZN9035:PA10 | URBAN | Weather |  | 527 | 38 | 0.013797 | 0.036307 | N
11/01/2017 | 17:43 | ZN9035:PA11 | URBAN | Weather |  | 130 | 38 | 0.0034034 | 0.0089562 | N
11/01/2017 | 17:43 | ZN9035:PA2 | URBAN | Weather |  | 738 | 37 | 0.018812 | 0.050844 | N
11/01/2017 | 17:43 | ZN9035:PA4 | URBAN | Weather |  | 1,895 | 38 | 0.049611 | 0.13055 | N
11/01/2017 | 17:43 | ZN9035:PA5 | URBAN | Weather |  | 317 | 37 | 0.0080806 | 0.021839 | N
11/01/2017 | 17:43 | ZN9035:PA7 | URBAN | Weather |  | 1,119 | 38 | 0.029295 | 0.077092 | N
11/01/2017 | 17:43 | ZN9035:PA8 | URBAN | Weather |  | 115 | 38 | 0.0030107 | 0.0079228 | N
12/01/2017 | 10:28 | ZN15014:PA20 | URBAN | Weather |  | 62 | 72 | 0.003075 | 0.0042708 | N
17/01/2017 | 17:36 | 812:19071 | SHORT RURAL | Weather |  | 1 | 72 | 0.00032213 | 0.00044885 | N
18/01/2017 | 19:35 | 813:89061 | LONG RURAL | Weather |  | 1 | 48 | 0.017082 | 0.035625 | N
23/01/2017 | 16:23 | ZN35700:PA1 | URBAN | Weather |  | 92 | 112 | 0.0070733 | 0.0063371 | N
24/01/2017 | 21:41 | 813:89061 | LONG RURAL | Weather |  | 12 | 69 | 0.29508 | 0.42766 | N
29/01/2017 | 16:21 | 814:82283 | SHORT RURAL | Weather |  | 20 | 298 | 0.026734 | 0.0089652 | N
29/01/2017 | 17:06 | 813:89062 | SHORT RURAL | Weather |  | 83 | 380 | 0.14152 | 0.037205 | N
29/01/2017 | 23:39 | 813:89062 | SHORT RURAL | Weather |  | 83 | 214 | 0.079508 | 0.037205 | N
30/01/2017 | 12:50 | 813:89062 | SHORT RURAL | Weather |  | 1 | 190 | 0.00085139 | 0.00044826 | N
04/02/2017 | 17:04 | 813:89061 | LONG RURAL | Weather |  | 110 | 11 | 0.43091 | 3.9174 | N
04/02/2017 | 17:38 | 813:89063 | SHORT RURAL | Weather |  | 1 | 1,808 | 0.0081016 | 0.0004482 | N
12/02/2017 | 00:54 | 264:81244 | SHORT RURAL | Weather |  | 31 | 106 | 0.014704 | 0.013872 | N
17/02/2017 | 15:00 | 801:74121 | LONG RURAL | Weather |  | 1 | 30 | 0.010684 | 0.035613 | Y
17/02/2017 | 15:55 | ZN3922:PA10 | URBAN | Weather |  | 1 | 212 | 0.00014587 | 6.889e-05 | Y
17/02/2017 | 16:18 | ZN14143:PA17 | SHORT RURAL | Weather |  | 2 | 2,952 | 0.026367 | 0.0008932 | Y
17/02/2017 | 16:32 | ZN12630:PA1 | SHORT RURAL | Weather |  | 566 | 148 | 0.37411 | 0.25277 | Y
17/02/2017 | 16:32 | ZN12630:PA10 | SHORT RURAL | Weather |  | 320 | 148 | 0.21151 | 0.14291 | Y
17/02/2017 | 16:32 | ZN12630:PA11 | SHORT RURAL | Weather |  | 238 | 148 | 0.15731 | 0.10629 | Y
17/02/2017 | 16:32 | ZN12630:PA13 | SHORT RURAL | Weather |  | 94 | 148 | 0.062131 | 0.04198 | Y
17/02/2017 | 16:32 | ZN12630:PA3 | SHORT RURAL | Weather |  | 415 | 148 | 0.2743 | 0.18534 | Y
17/02/2017 | 16:32 | ZN12630:PA6 | SHORT RURAL | Weather |  | 7 | 148 | 0.0046268 | 0.0031262 | Y
17/02/2017 | 16:32 | ZN12630:PA8 | SHORT RURAL | Weather |  | 372 | 148 | 0.24588 | 0.16613 | Y
17/02/2017 | 16:39 | ZN15010:PA1 | URBAN | Weather |  | 1 | 1,118 | 0.00077012 | 6.889e-05 | Y
17/02/2017 | 16:37 | ZN12640:PA1 | SHORT RURAL | Weather |  | 639 | 130 | 0.37099 | 0.28538 | Y
17/02/2017 | 16:37 | ZN12640:PA10 | URBAN | Weather |  | 1,674 | 130 | 0.14992 | 0.11532 | Y
17/02/2017 | 16:37 | ZN12640:PA13 | SHORT RURAL | Weather |  | 2,039 | 130 | 1.1838 | 0.91061 | Y
17/02/2017 | 16:37 | ZN12640:PA15 | URBAN | Weather |  | 1,068 | 130 | 0.095647 | 0.073575 | Y
17/02/2017 | 16:37 | ZN12640:PA16 | URBAN | Weather |  | 800 | 130 | 0.071646 | 0.055112 | Y
17/02/2017 | 16:37 | ZN12640:PA18 | SHORT RURAL | Weather |  | 841 | 130 | 0.48827 | 0.37559 | Y
17/02/2017 | 16:37 | ZN12640:PA19 | URBAN | Weather |  | 1,794 | 130 | 0.16067 | 0.12359 | Y
17/02/2017 | 16:37 | ZN12640:PA2 | URBAN | Weather |  | 2,003 | 130 | 0.17938 | 0.13799 | Y
17/02/2017 | 16:37 | ZN12640:PA6 | URBAN | Weather |  | 1,250 | 130 | 0.11195 | 0.086113 | Y
17/02/2017 | 16:37 | ZN12640:PA7 | URBAN | Weather |  | 1,660 | 130 | 0.14866 | 0.11436 | Y
17/02/2017 | 16:37 | ZN12640:PA8 | URBAN | Weather |  | 911 | 130 | 0.081586 | 0.062759 | Y
17/02/2017 | 16:37 | ZN12660:PA10 | URBAN | Weather |  | 1,765 | 85 | 0.10335 | 0.12159 | Y
17/02/2017 | 16:37 | ZN12660:PA11 | URBAN | Weather |  | 719 | 85 | 0.042102 | 0.049532 | Y
17/02/2017 | 16:37 | ZN12660:PA13 | URBAN | Weather |  | 611 | 85 | 0.035778 | 0.042092 | Y
17/02/2017 | 16:37 | ZN12660:PA14 | SHORT RURAL | Weather |  | 1,243 | 85 | 0.47185 | 0.55512 | Y
17/02/2017 | 16:37 | ZN12660:PA16 | URBAN | Weather |  | 260 | 85 | 0.015225 | 0.017911 | Y
17/02/2017 | 16:37 | ZN12660:PA17 | URBAN | Weather |  | 1,248 | 85 | 0.073079 | 0.085975 | Y
17/02/2017 | 16:37 | ZN12660:PA5 | SHORT RURAL | Weather |  | 279 | 85 | 0.10591 | 0.1246 | Y
17/02/2017 | 16:37 | ZN12660:PA6 | SHORT RURAL | Weather |  | 491 | 85 | 0.18639 | 0.21928 | Y
17/02/2017 | 16:37 | ZN12660:PA8 | URBAN | Weather |  | 1,323 | 85 | 0.07747 | 0.091142 | Y
17/02/2017 | 16:37 | ZN36200:PA1 | URBAN | Weather |  | 1,351 | 60 | 0.055842 | 0.09307 | Y
17/02/2017 | 16:37 | ZN36200:PA11 | SHORT RURAL | Weather |  | 1,300 | 60 | 0.34835 | 0.58058 | Y
17/02/2017 | 16:37 | ZN36200:PA4 | SHORT RURAL | Weather |  | 920 | 60 | 0.24652 | 0.41087 | Y
17/02/2017 | 16:37 | ZN36200:PA8 | SHORT RURAL | Weather |  | 1,369 | 60 | 0.36684 | 0.61139 | Y
17/02/2017 | 17:50 | ZN15010:PA9 | SHORT RURAL | Weather |  | 76 | 1,084 | 0.36793 | 0.033941 | Y
18/02/2017 | 08:20 | ZN15014:PA12 | SHORT RURAL | Weather |  | 166 | 3,429 | 2.5421 | 0.074137 | N
17/02/2017 | 17:36 | ZN12690:PA16 | SHORT RURAL | Weather |  | 1 | 2,663 | 0.011893 | 0.0004466 | Y
17/02/2017 | 17:46 | ZN15004:PA3 | URBAN | Weather |  | 43 | 903 | 0.026754 | 0.0029623 | Y
17/02/2017 | 18:05 | 523:33501 | SHORT RURAL | Weather |  | 1 | 390 | 0.0017398 | 0.0004466 | Y
17/02/2017 | 18:27 | ZN15004:PA5 | URBAN | Weather |  | 1 | 1,746 | 0.0012026 | 6.889e-05 | Y
17/02/2017 | 18:52 | ZN12610:PA7 | URBAN | Weather |  | 1 | 2,227 | 0.0015342 | 6.889e-05 | Y
17/02/2017 | 19:15 | ZN15014:PA12 | SHORT RURAL | Weather |  | 1 | 3,104 | 0.013863 | 0.0004466 | Y
17/02/2017 | 20:30 | ZN116:PA76 | URBAN | Weather |  | 30 | 784 | 0.016205 | 0.0020667 | Y
17/02/2017 | 17:17 | ZN12620:PA10 | SHORT RURAL | Weather |  | 1 | 2,503 | 0.011178 | 0.0004466 | Y
17/02/2017 | 20:27 | 807:74184 | SHORT RURAL | Weather |  | 1 | 934 | 0.0041697 | 0.0004466 | Y
17/02/2017 | 21:40 | ZN12580:PA12 | SHORT RURAL | Weather |  | 1 | 2,659 | 0.011877 | 0.0004466 | Y
18/02/2017 | 08:01 | ZN15004:PA5 | URBAN | Weather |  | 47 | 1,418 | 0.045917 | 0.0032378 | N
18/02/2017 | 08:47 | 238:34148 | SHORT RURAL | Weather |  | 1 | 519 | 0.0023168 | 0.00044661 | N
18/02/2017 | 11:06 | 802:82225 | SHORT RURAL | Weather |  | 2 | 181 | 0.0016167 | 0.00089321 | N
18/02/2017 | 09:20 | ZN12640:PA2 | URBAN | Weather |  | 1 | 399 | 0.00027503 | 6.889e-05 | N
18/02/2017 | 10:33 | ZN15010:PA9 | SHORT RURAL | Weather |  | 1 | 1,401 | 0.0062576 | 0.00044661 | N
18/02/2017 | 12:40 | 516:48067 | SHORT RURAL | Weather |  | 1 | 129 | 0.00057642 | 0.00044661 | N
18/02/2017 | 15:31 | ZN14891:PA5 | SHORT RURAL | Weather |  | 1 | 1,079 | 0.0048182 | 0.00044661 | N
18/02/2017 | 17:38 | ZN12650:PA1 | SHORT RURAL | Weather |  | 1 | 1,026 | 0.0045843 | 0.00044661 | N
18/02/2017 | 20:05 | 801:74121 | LONG RURAL | Weather |  | 1 | 27 | 0.0094789 | 0.035613 | N
19/02/2017 | 09:27 | ZN12690:PA16 | SHORT RURAL | Weather |  | 1 | 303 | 0.0013521 | 0.00044661 | N
19/02/2017 | 13:22 | ZN12610:PA16 | SHORT RURAL | Weather |  | 1 | 202 | 0.00090259 | 0.00044661 | N
20/02/2017 | 08:41 | ZN15004:PA9 | URBAN | Weather |  | 1 | 159 | 0.00010948 | 6.889e-05 | N
20/02/2017 | 19:22 | ZN15010:PA1 | URBAN | Weather |  | 1 | 1,118 | 0.00077004 | 6.889e-05 | N
21/02/2017 | 10:19 | ZN15014:PA12 | SHORT RURAL | Weather |  | 1 | 1,540 | 0.0068794 | 0.00044663 | N
21/02/2017 | 18:14 | ZN15014:PA12 | SHORT RURAL | Weather |  | 1 | 1,066 | 0.0047593 | 0.00044663 | N
21/02/2017 | 18:14 | ZN15014:PA12 | SHORT RURAL | Weather |  | 1 | 1,065 | 0.0047576 | 0.00044663 | N
22/02/2017 | 12:02 | ZN15010:PA1 | URBAN | Weather |  | 1 | 582 | 0.0004012 | 6.8893e-05 | N
24/02/2017 | 10:00 | 813:89055 | SHORT RURAL | Weather |  | 1 | 198 | 0.00088201 | 0.00044648 | N
05/03/2017 | 17:36 | 810:74054 | LONG RURAL | Weather |  | 1 | 71 | 0.02543 | 0.0356 | N
07/03/2017 | 10:21 | ZN15006:PA16 | URBAN | Weather |  | 1 | 504 | 0.00034682 | 6.8879e-05 | N
08/03/2017 | 18:55 | ZN15014:PA12 | SHORT RURAL | Weather |  | 1 | 784 | 0.0034991 | 0.00044617 | N
14/03/2017 | 14:55 | ZN12610:PA11 | URBAN | Weather |  | 1 | 94 | 6.5023e-05 | 6.8892e-05 | N
17/03/2017 | 23:14 | ZN2602:PA4 | URBAN | Weather |  | 63 | 259 | 0.011234 | 0.0043393 | N
18/03/2017 | 04:36 | ZN10994:PA10 | URBAN | Weather |  | 52 | 734 | 0.026286 | 0.0035817 | N
18/03/2017 | 15:52 | ZN2310:PA53 | URBAN | Weather |  | 1 | 88 | 6.0337e-05 | 6.8878e-05 | N
19/03/2017 | 00:19 | 228:7491 | URBAN | Weather |  | 1 | 626 | 0.00043105 | 6.8879e-05 | N
19/03/2017 | 08:45 | ZN15005:PA2 | URBAN | Weather |  | 1 | 1,068 | 0.00073586 | 6.8879e-05 | N
21/03/2017 | 17:40 | ZN3672:PA36 | URBAN | Weather |  | 86 | 77 | 0.0045612 | 0.0059236 | N
21/03/2017 | 18:38 | ZN2400:PA21 | URBAN | Weather |  | 1,234 | 187 | 0.15877 | 0.084997 | N
21/03/2017 | 19:11 | ZN14143:PA17 | SHORT RURAL | Weather |  | 27 | 834 | 0.10008 | 0.012 | N
22/03/2017 | 18:11 | ZN12660:PA16 | URBAN | Weather |  | 1 | 1,159 | 0.00079798 | 6.8881e-05 | N
22/03/2017 | 18:01 | ZN12640:PA16 | URBAN | Weather |  | 1 | 973 | 0.0006703 | 6.8881e-05 | N
21/03/2017 | 19:11 | ZN14143:PA17 | SHORT RURAL | Weather |  | 4 | 899 | 0.015983 | 0.0017778 | N
29/03/2017 | 08:40 | 812:19072 | SHORT RURAL | Weather |  | 1 | 106 | 0.00047048 | 0.00044384 | N
04/04/2017 | 19:04 | ZN15014:PA12 | SHORT RURAL | Weather |  | 1 | 977 | 0.0043489 | 0.00044531 | N
11/04/2017 | 13:55 | 240:34835 | SHORT RURAL | Weather |  | 37 | 45 | 0.007415 | 0.016478 | N
26/04/2017 | 16:20 | 507:80914 | SHORT RURAL | Weather |  | 18 | 283 | 0.022634 | 0.0079919 | N
26/04/2017 | 14:50 | ZN9550:PA4 | URBAN | Weather |  | 59 | 240 | 0.0097367 | 0.0040578 | N
21/05/2017 | 12:59 | ZN10999:PA10 | URBAN | Weather |  | 1,847 | 110 | 0.13962 | 0.12693 | N
21/05/2017 | 12:59 | ZN10999:PA32 | URBAN | Weather |  | 1 | 110 | 7.5595e-05 | 6.8723e-05 | N
24/05/2017 | 11:29 | 206:34432 | URBAN | Weather |  | 1 | 268 | 0.00018443 | 6.8723e-05 | N
07/06/2017 | 06:12 | ZN9700:PA19 | URBAN | Weather |  | 63 | 203 | 0.0087888 | 0.0043295 | N
07/06/2017 | 16:59 | ZN965:PA11 | URBAN | Weather |  | 910 | 85 | 0.053156 | 0.062537 | N
07/06/2017 | 16:59 | ZN965:PA12 | URBAN | Weather |  | 621 | 280 | 0.11932 | 0.042676 | N
07/06/2017 | 16:59 | ZN965:PA13 | URBAN | Weather |  | 1 | 2,286 | 0.001571 | 6.8722e-05 | N
07/06/2017 | 16:59 | ZN965:PA15 | URBAN | Weather |  | 1,161 | 211 | 0.16834 | 0.079786 | N
07/06/2017 | 16:59 | ZN965:PA2 | URBAN | Weather |  | 532 | 227 | 0.082991 | 0.03656 | N
07/06/2017 | 16:59 | ZN965:PA20 | URBAN | Weather |  | 57 | 85 | 0.0033296 | 0.0039171 | N
07/06/2017 | 16:59 | ZN965:PA3 | URBAN | Weather |  | 1,145 | 246 | 0.19371 | 0.078686 | N
07/06/2017 | 16:59 | ZN965:PA37 | URBAN | Weather |  | 461 | 85 | 0.026929 | 0.031681 | N
07/06/2017 | 16:59 | ZN965:PA38 | URBAN | Weather |  | 979 | 85 | 0.057187 | 0.067279 | N
07/06/2017 | 16:59 | ZN965:PA4 | URBAN | Weather |  | 1,106 | 131 | 0.099568 | 0.076006 | N
07/06/2017 | 16:59 | ZN965:PA42 | URBAN | Weather |  | 1,097 | 85 | 0.06408 | 0.075388 | N
07/06/2017 | 16:59 | ZN965:PA43 | URBAN | Weather |  | 1,019 | 85 | 0.059523 | 0.070027 | N
07/06/2017 | 16:59 | ZN965:PA6 | URBAN | Weather |  | 1,070 | 169 | 0.12427 | 0.073532 | N
07/06/2017 | 16:59 | ZN965:PA8 | URBAN | Weather |  | 1,191 | 254 | 0.20751 | 0.081848 | N
01/07/2016 | 08:05 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 51 | 70 | 0.0024725 | 0.0035321 | N
01/07/2016 | 21:48 | ZN9252:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,271 | 0.00088045 | 6.9257e-05 | N
05/07/2016 | 01:02 | ZN12620:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,097 | 82 | 0.40958 | 0.49949 | N
05/07/2016 | 13:58 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 241 | 0.0010993 | 0.00045532 | N
06/07/2016 | 13:40 | ZN3154:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 10 | 0.00027704 | 0.0027704 | N
06/07/2016 | 19:17 | 213:33771 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 83 | 5.7462e-05 | 6.9259e-05 | N
07/07/2016 | 10:27 | ZN15004:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 118 | 8.1386e-05 | 6.9245e-05 | N
07/07/2016 | 20:29 | ZN15015:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,640 | 164 | 0.18619 | 0.11356 | N
08/07/2016 | 02:42 | ZN15013:PA6 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 377 | 0.0017167 | 0.00045525 | N
08/07/2016 | 02:59 | ZN12600:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 421 | 0.00029153 | 6.9246e-05 | N
08/07/2016 | 04:23 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 69 | 543 | 0.17071 | 0.031412 | N
08/07/2016 | 19:26 | ZN2635:PA52 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 174 | 0.0039761 | 0.0022851 | N
09/07/2016 | 02:50 | ZN3154:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 35 | 120 | 0.0029085 | 0.0024238 | N
11/07/2016 | 14:26 | ZN1287:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 134 | 0.0039897 | 0.0029778 | N
12/07/2016 | 10:59 | ZN36200:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2 | 151 | 0.00020914 | 0.0001385 | N
12/07/2016 | 13:00 | 227:13019 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 85 | 0.00038696 | 0.00045525 | N
12/07/2016 | 14:21 | ZN10993:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 339 | 0.00023457 | 6.9252e-05 | N
12/07/2016 | 16:47 | ZN2310:PA53 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 284 | 0.00019633 | 6.9252e-05 | N
12/07/2016 | 19:25 | ZN13000:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 158 | 0.00072028 | 0.00045525 | N
13/07/2016 | 06:55 | ZN12570:PA22 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 275 | 0.0012509 | 0.00045526 | N
13/07/2016 | 07:54 | ZN1193:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 175 | 0.00012138 | 6.9254e-05 | N
13/07/2016 | 10:30 | ZN965:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 240 | 0.00016621 | 6.9254e-05 | N
13/07/2016 | 10:30 | ZN965:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 169 | 0.00011704 | 6.9254e-05 | N
13/07/2016 | 10:30 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 949 | 172 | 0.11314 | 0.065722 | N
13/07/2016 | 10:49 | ZN9118:PA3 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 76 | 171 | 0.059038 | 0.0346 | N
13/07/2016 | 10:51 | ZN35500:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 8 | 5.5749e-06 | 6.9254e-05 | N
13/07/2016 | 11:13 | ZN15014:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 78 | 0.00035563 | 0.00045526 | N
13/07/2016 | 11:20 | ZN12640:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 74 | 129 | 0.0066289 | 0.0051248 | N
13/07/2016 | 11:45 | 257:81999 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 38 | 2.6443e-05 | 6.9254e-05 | N
13/07/2016 | 12:08 | 257:81999 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 15 | 1.0088e-05 | 6.9254e-05 | N
13/07/2016 | 12:11 | ZN12640:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 47 | 189 | 0.0061442 | 0.0032549 | N
13/07/2016 | 12:30 | ZN1673:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 149 | 0.00010341 | 6.9254e-05 | N
13/07/2016 | 13:23 | ZN690:PA33 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 347 | 0.0091301 | 0.0026317 | N
13/07/2016 | 13:36 | ZN9245:PA45 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 21 | 102 | 0.0014834 | 0.0014543 | N
13/07/2016 | 13:50 | ZN12630:PA23 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 59 | 0.00026891 | 0.00045526 | N
15/07/2016 | 00:13 | ZN36100:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 47 | 87 | 0.0028167 | 0.003255 | N
17/07/2016 | 22:56 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 123 | 8.4995e-05 | 6.9243e-05 | N
19/07/2016 | 12:17 | ZN35600:PA1 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 47 | 3.2706e-05 | 6.9244e-05 | N
19/07/2016 | 15:51 | ZN4545:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 22 | 128 | 0.0019542 | 0.0015234 | N
19/07/2016 | 16:08 | ZN3425:PA44 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 27 | 337 | 0.0063005 | 0.0018696 | N
20/07/2016 | 02:54 | 227:13020 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 15 | 266 | 0.018113 | 0.0068095 | N
20/07/2016 | 09:41 | ZN15005:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,287 | 0.00089111 | 6.9227e-05 | N
20/07/2016 | 15:35 | ZN12600:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 16 | 105 | 0.0076267 | 0.0072635 | N
20/07/2016 | 20:23 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 127 | 0.00057503 | 0.00045397 | N
20/07/2016 | 22:18 | 205:12205 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 816 | 0.0037045 | 0.00045397 | N
21/07/2016 | 14:29 | ZN12640:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 39 | 55 | 0.0014913 | 0.0026999 | N
21/07/2016 | 14:40 | ZN12690:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 199 | 0.00013778 | 6.9229e-05 | N
21/07/2016 | 15:10 | ZN15014:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 152 | 0.00010541 | 6.9229e-05 | N
22/07/2016 | 06:23 | ZN35500:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 39 | 158 | 0.0042667 | 0.0027002 | N
22/07/2016 | 10:50 | ZN14892:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 70 | 4.828e-05 | 6.9235e-05 | N
22/07/2016 | 12:15 | ZN15004:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 134 | 9.289e-05 | 6.9235e-05 | N
23/07/2016 | 01:50 | 513:48051 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 821 | 118 | 0.067011 | 0.056842 | N
23/07/2016 | 02:26 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 13 | 324 | 0.019119 | 0.0059008 | N
23/07/2016 | 04:11 | ZN3154:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 32 | 54 | 0.0011964 | 0.0022155 | N
22/07/2016 | 23:15 | 243:80083 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 15 | 575 | 0.039153 | 0.0068093 | N
23/07/2016 | 08:35 | ZN36200:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 925 | 78 | 0.32851 | 0.41986 | N
23/07/2016 | 10:38 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 390 | 0.0017693 | 0.00045391 | N
23/07/2016 | 11:42 | 229:34995 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 392 | 0.0017778 | 0.00045391 | N
23/07/2016 | 13:08 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 6 | 577 | 0.015714 | 0.0027234 | N
23/07/2016 | 13:24 | 230:81432 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 659 | 71 | 0.21238 | 0.29913 | N
23/07/2016 | 15:14 | ZN187:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 36 | 0.0010638 | 0.0029771 | N
23/07/2016 | 15:00 | ZN35500:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 41 | 20 | 0.00056773 | 0.0028386 | N
23/07/2016 | 14:22 | ZN12610:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 37 | 148 | 0.0037913 | 0.0025617 | N
23/07/2016 | 15:50 | 229:34995 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 408 | 0.0018512 | 0.00045391 | N
23/07/2016 | 16:01 | ZN3154:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,000 | 55 | 0.038079 | 0.069235 | N
23/07/2016 | 16:09 | ZN690:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 346 | 0.00023925 | 6.9235e-05 | N
23/07/2016 | 16:37 | ZN12630:PA23 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 5 | 183 | 0.0041533 | 0.0022695 | N
23/07/2016 | 16:53 | ZN12600:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 420 | 0.0019079 | 0.00045391 | N
23/07/2016 | 17:26 | ZN36200:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,054 | 0.0047824 | 0.00045391 | N
23/07/2016 | 20:51 | ZN15010:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 18 | 1,405 | 0.01751 | 0.0012462 | N
24/07/2016 | 07:33 | ZN12610:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 387 | 0.00026778 | 6.9235e-05 | N
24/07/2016 | 14:08 | ZN35370:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 281 | 106 | 0.13489 | 0.12755 | N
25/07/2016 | 08:38 | 502:48008 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 181 | 0.00012559 | 6.9235e-05 | N
25/07/2016 | 10:03 | 504:48031 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 226 | 0.0010274 | 0.00045391 | N
25/07/2016 | 11:28 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 14 | 452 | 0.0043799 | 0.00096929 | N
25/07/2016 | 13:47 | 227:13019 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 673 | 0.0030548 | 0.00045391 | N
25/07/2016 | 13:40 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 4 | 115 | 0.00031848 | 0.00027694 | N
25/07/2016 | 14:00 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 26 | 170 | 0.0030602 | 0.0018001 | N
26/07/2016 | 06:06 | ZN15006:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 8 | 169 | 0.00093744 | 0.00055388 | N
27/07/2016 | 08:11 | ZN10994:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 168 | 0.00011638 | 6.9237e-05 | N
27/07/2016 | 15:05 | 264:81241 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 105 | 0.00047503 | 0.00045393 | N
17/07/2016 | 19:30 | ZN2635:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 31 | 10 | 0.00021465 | 0.0021465 | N
01/08/2016 | 12:33 | 239:82136 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 122 | 0.00055306 | 0.0004537 | N
01/08/2016 | 13:19 | ZN1193:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 36 | 41 | 0.0010218 | 0.0024923 | N
01/08/2016 | 13:37 | ZN12630:PA25 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 2,873 | 0.013032 | 0.0004537 | N
01/08/2016 | 15:56 | ZN3922:PA29 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 381 | 0.00026343 | 6.923e-05 | N
02/08/2016 | 12:53 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 19 | 26 | 0.1763 | 0.67809 | N
02/08/2016 | 17:17 | ZN1850:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 98 | 0.0027027 | 0.0027692 | N
03/08/2016 | 07:30 | 232:33407 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 119 | 0.00053999 | 0.00045371 | N
03/08/2016 | 15:58 | ZN9118:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 35 | 542 | 0.013132 | 0.0024231 | N
03/08/2016 | 16:18 | ZN2400:PA15 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 246 | 0.0011157 | 0.00045371 | N
04/08/2016 | 02:57 | ZN187:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 392 | 0.00027148 | 6.9177e-05 | N
04/08/2016 | 15:23 | ZN2568:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 69 | 162 | 0.0077326 | 0.0047732 | N
08/08/2016 | 12:05 | ZN12630:PA25 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 6 | 36 | 0.00097291 | 0.0027278 | N
08/08/2016 | 13:37 | ZN3472:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 45 | 3.0923e-05 | 6.9178e-05 | N
10/08/2016 | 16:54 | ZN35800:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 52 | 3.5962e-05 | 6.9179e-05 | N
14/08/2016 | 13:57 | ZN14144:PA7 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 2 | 243 | 0.0022162 | 0.00091203 | N
15/08/2016 | 17:04 | ZN3472:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 41 | 2.8193e-05 | 6.9157e-05 | N
16/08/2016 | 14:44 | ZN15004:PA9 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 391 | 0.00027021 | 6.9157e-05 | N
18/08/2016 | 12:27 | 232:11454 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 2 | 208 | 0.0019283 | 0.00092706 | N
20/08/2016 | 14:30 | ZN847:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 235 | 0.00016303 | 6.938e-05 | N
20/08/2016 | 14:52 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 34 | 78 | 0.0018399 | 0.0023589 | N
22/08/2016 | 23:56 | ZN9037:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 64 | 84 | 0.0037217 | 0.0044403 | N
23/08/2016 | 16:06 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 72 | 4.9629e-05 | 6.909e-05 | N
24/08/2016 | 21:40 | ZN10995:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 229 | 0.0076101 | 0.0033164 | N
25/08/2016 | 09:06 | ZN1193:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 203 | 0.00014037 | 6.9094e-05 | N
26/08/2016 | 13:34 | 217:33612 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 206 | 0.00014217 | 6.9094e-05 | N
27/08/2016 | 09:41 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 131 | 0.0038901 | 0.0029696 | N
28/08/2016 | 06:24 | 504:48031 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 222 | 0.0010119 | 0.00045662 | N
28/08/2016 | 16:37 | ZN12600:PA9 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,121 | 94 | 0.48319 | 0.51187 | N
28/08/2016 | 17:30 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 56 | 595 | 0.023011 | 0.0038674 | N
29/08/2016 | 05:21 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 56 | 249 | 0.0096168 | 0.0038674 | N
30/08/2016 | 10:56 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 47 | 98 | 0.0031885 | 0.0032459 | N
30/08/2016 | 10:58 | ZN2400:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 88 | 269 | 0.10794 | 0.040182 | N
30/08/2016 | 18:17 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 3 | 267 | 0.00055318 | 0.00020718 | N
31/08/2016 | 11:17 | ZN35500:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 193 | 0.00013311 | 6.9039e-05 | N
01/09/2016 | 02:01 | ZN195:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 72 | 188 | 0.0093501 | 0.0049708 | N
01/09/2016 | 15:05 | ZN14144:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,044 | 0.0047661 | 0.00045647 | N
02/09/2016 | 09:31 | ZN12630:PA23 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 255 | 138 | 0.16039 | 0.1164 | N
02/09/2016 | 12:08 | ZN15006:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 54 | 32 | 0.0011781 | 0.0037281 | N
01/09/2016 | 14:07 | ZN3425:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 29 | 48 | 0.00096103 | 0.0020021 | N
02/09/2016 | 18:30 | 233:82819 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 43 | 180 | 0.035331 | 0.019628 | N
03/09/2016 | 06:40 | 514:18137 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 94 | 0.00042924 | 0.00045648 | N
03/09/2016 | 08:52 | ZN195:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 23 | 398 | 0.00632 | 0.0015879 | N
03/09/2016 | 09:31 | ZN180:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 102 | 189 | 0.013344 | 0.0070421 | N
03/09/2016 | 09:59 | ZN2635:PA38 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 52 | 156 | 0.0056006 | 0.0035901 | N
03/09/2016 | 09:58 | ZN195:PA30 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 38 | 301 | 0.052221 | 0.017346 | N
03/09/2016 | 10:07 | 515:35197 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 100 | 187 | 6.6854 | 3.5663 | N
03/09/2016 | 10:33 | ZN2310:PA61 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 77 | 5.3345e-05 | 6.9041e-05 | N
03/09/2016 | 10:33 | ZN2400:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 223 | 0.00015388 | 6.9041e-05 | N
03/09/2016 | 10:36 | ZN9035:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 57 | 364 | 0.014325 | 0.0039353 | N
03/09/2016 | 10:47 | ZN9035:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 369 | 0.00025451 | 6.9041e-05 | N
03/09/2016 | 10:51 | 528:83014 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 338 | 0.0015441 | 0.00045648 | N
03/09/2016 | 10:59 | ZN14891:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 366 | 96 | 0.16075 | 0.16707 | N
03/09/2016 | 11:00 | ZN9037:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 540 | 0.014167 | 0.0026235 | N
03/09/2016 | 11:43 | ZN3154:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 611 | 72 | 0.030372 | 0.042184 | N
03/09/2016 | 11:56 | ZN847:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 273 | 0.00018858 | 6.9041e-05 | N
03/09/2016 | 11:57 | 532:83309 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 33 | 0.00014866 | 0.00045648 | N
03/09/2016 | 12:05 | 504:48033 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 178 | 75 | 0.06094 | 0.081253 | N
03/09/2016 | 09:24 | ZN2400:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 672 | 284 | 0.87074 | 0.30675 | N
03/09/2016 | 12:51 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 23 | 154 | 0.016168 | 0.010499 | N
03/09/2016 | 12:49 | ZN9037:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 60 | 295 | 0.012212 | 0.0041424 | N
03/09/2016 | 13:15 | 238:34150 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 225 | 0.0010258 | 0.00045648 | N
03/09/2016 | 13:24 | 532:83298 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 262 | 128 | 0.023108 | 0.018089 | N
03/09/2016 | 14:34 | 230:81440 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 295 | 0.001348 | 0.00045648 | N
03/09/2016 | 14:37 | ZN12570:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 143 | 9.8728e-05 | 6.9041e-05 | N
03/09/2016 | 16:54 | ZN195:PA30 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 311 | 0.0014206 | 0.00045648 | N
05/09/2016 | 12:42 | ZN847:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 288 | 0.00019851 | 6.9042e-05 | N
07/09/2016 | 09:13 | ZN1193:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 257 | 0.00017722 | 6.9043e-05 | N
03/09/2016 | 09:10 | ZN12630:PA22 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 3 | 30 | 0.00041083 | 0.0013694 | N
08/09/2016 | 13:38 | 224:80340 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 20 | 76 | 0.00691 | 0.0090902 | N
09/09/2016 | 16:12 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 108 | 221 | 0.10868 | 0.049087 | N
09/09/2016 | 16:22 | ZN2310:PA72 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 36 | 2.5137e-05 | 6.9058e-05 | N
09/09/2016 | 19:02 | 235:2124 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 180 | 0.00081902 | 0.00045451 | N
10/09/2016 | 07:37 | ZN12630:PA25 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 237 | 124 | 0.13364 | 0.10772 | N
10/09/2016 | 10:59 | ZN36100:PA12 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 388 | 0.00026761 | 6.9061e-05 | N
12/09/2016 | 09:03 | 232:33407 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 176 | 0.00080137 | 0.0004545 | N
13/09/2016 | 09:18 | 532:83293 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 36 | 2.4644e-05 | 6.9064e-05 | N
13/09/2016 | 11:51 | ZN15009:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 69 | 4.7355e-05 | 6.9064e-05 | N
13/09/2016 | 03:30 | ZN195:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 22 | 120 | 0.0018233 | 0.0015194 | N
14/09/2016 | 08:05 | ZN398:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 294 | 0.00020308 | 6.9066e-05 | N
14/09/2016 | 17:57 | ZN35370:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 2 | 73 | 0.00066358 | 0.00090902 | N
15/09/2016 | 10:14 | ZN72:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 80 | 5.5541e-05 | 6.9052e-05 | N
15/09/2016 | 10:25 | ZN965:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 14 | 145 | 0.0014018 | 0.00096673 | N
15/09/2016 | 12:42 | 511:29878 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 89 | 104 | 0.04195 | 0.040437 | N
15/09/2016 | 14:28 | ZN129:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 257 | 0.00017735 | 6.9052e-05 | N
15/09/2016 | 15:03 | ZN1290:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,136 | 205 | 0.16081 | 0.078443 | N
15/09/2016 | 15:03 | ZN1290:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 37 | 205 | 0.0052376 | 0.0025549 | N
15/09/2016 | 15:03 | ZN1290:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,180 | 205 | 0.16704 | 0.081481 | N
15/09/2016 | 15:03 | ZN1290:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,053 | 205 | 0.14906 | 0.072712 | N
15/09/2016 | 15:03 | ZN1290:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 161 | 205 | 0.022791 | 0.011117 | N
15/09/2016 | 15:03 | ZN1290:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 26 | 205 | 0.0036805 | 0.0017954 | N
15/09/2016 | 15:03 | ZN1290:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 205 | 0.0067947 | 0.0033145 | N
15/09/2016 | 15:03 | ZN1290:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 657 | 205 | 0.093003 | 0.045367 | N
15/09/2016 | 15:03 | ZN1290:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 10 | 205 | 0.0014156 | 0.00069052 | N
15/09/2016 | 15:03 | ZN1290:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 75 | 205 | 0.010617 | 0.0051789 | N
15/09/2016 | 15:03 | ZN3472:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 205 | 0.00014156 | 6.9052e-05 | N
15/09/2016 | 21:27 | ZN847:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 167 | 0.00011541 | 6.9052e-05 | N
15/09/2016 | 17:30 | ZN12690:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 110 | 7.5957e-05 | 6.9052e-05 | N
16/09/2016 | 11:37 | ZN9252:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 29 | 58 | 0.0011531 | 0.0020025 | N
15/09/2016 | 15:27 | 264:81241 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 18 | 8.1782e-05 | 0.00045435 | N
20/09/2016 | 09:14 | ZN35800:PA22 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 245 | 0.000169 | 6.9065e-05 | N
21/09/2016 | 08:39 | ZN965:PA46 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 200 | 0.00013831 | 6.9066e-05 | N
21/09/2016 | 09:45 | ZN15010:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 62 | 4.2821e-05 | 6.9066e-05 | N
21/09/2016 | 10:25 | ZN10999:PA32 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 48 | 3.3348e-05 | 6.9066e-05 | N
22/09/2016 | 09:41 | ZN12630:PA24 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 319 | 0.0014479 | 0.00045391 | N
23/09/2016 | 02:09 | ZN15011:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 36 | 181 | 0.004499 | 0.0024856 | N
22/09/2016 | 16:43 | ZN1850:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 19 | 77 | 0.0010095 | 0.0013119 | N
23/09/2016 | 06:41 | ZN15011:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 36 | 198 | 0.0049224 | 0.0024856 | N
23/09/2016 | 17:07 | ZN2196:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 55 | 308 | 0.011696 | 0.0037975 | N
26/09/2016 | 14:03 | 232:33409 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 126 | 0.0005705 | 0.00045392 | N
27/09/2016 | 11:56 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 692 | 90 | 0.28149 | 0.31409 | N
27/09/2016 | 12:46 | ZN3154:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 478 | 0.00033021 | 6.9047e-05 | N
27/09/2016 | 13:02 | ZN3472:PA28 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 147 | 0.00010172 | 6.9047e-05 | N
27/09/2016 | 14:04 | ZN262:PA30 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 58 | 3.9702e-05 | 6.9047e-05 | N
27/09/2016 | 14:42 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 41 | 249 | 0.0070526 | 0.0028309 | N
28/09/2016 | 04:47 | ZN847:PA39 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 373 | 0.00025721 | 6.9049e-05 | N
28/09/2016 | 12:20 | ZN36300:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 31 | 15 | 0.00032108 | 0.0021405 | N
28/09/2016 | 14:00 | ZN15011:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 52 | 3.5905e-05 | 6.9049e-05 | N
29/09/2016 | 15:19 | ZN12630:PA25 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 221 | 0.0010006 | 0.00045377 | N
29/09/2016 | 16:42 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 16 | 38 | 0.0027589 | 0.0072603 | N
30/09/2016 | 15:00 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 25 | 365 | 0.041406 | 0.011344 | N
30/09/2016 | 13:19 | ZN4545:PA42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 73 | 371 | 0.018695 | 0.005039 | N
03/10/2016 | 13:50 | ZN12690:PA7 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 3 | 140 | 0.0019013 | 0.001358 | N
30/09/2016 | 14:30 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 399 | 0.0077141 | 0.0019328 | N
30/09/2016 | 14:53 | 224:80337 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 60 | 187 | 0.050908 | 0.027226 | N
30/09/2016 | 16:33 | ZN12640:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 32 | 123 | 0.01786 | 0.014521 | N
01/10/2016 | 10:09 | ZN690:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 44 | 45 | 0.0013724 | 0.0030386 | N
01/10/2016 | 11:07 | ZN2635:PA57 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,233 | 97 | 0.082595 | 0.085149 | N
01/10/2016 | 11:12 | ZN80:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 73 | 153 | 0.0077132 | 0.0050413 | N
01/10/2016 | 11:12 | ZN80:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 82 | 178 | 0.01008 | 0.0056628 | N
01/10/2016 | 11:33 | ZN35500:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 78 | 57 | 0.0030524 | 0.0053866 | N
01/10/2016 | 11:36 | ZN9700:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 593 | 0.00040953 | 6.9059e-05 | N
01/10/2016 | 12:11 | ZN15012:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 367 | 0.00025325 | 6.9059e-05 | N
01/10/2016 | 15:15 | ZN12570:PA24 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,621 | 6 | 0.044028 | 0.7338 | N
01/10/2016 | 15:57 | ZN5868:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 48 | 3.2883e-05 | 6.9059e-05 | N
01/10/2016 | 16:44 | 238:34137 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 196 | 0.00088726 | 0.00045268 | N
01/10/2016 | 21:32 | ZN10994:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 893 | 0.00061649 | 6.9059e-05 | N
02/10/2016 | 10:55 | 524:33572 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 2 | 95 | 0.00086009 | 0.00090536 | N
02/10/2016 | 12:23 | ZN15011:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 218 | 0.00015066 | 6.9059e-05 | N
03/10/2016 | 10:15 | 813:89063 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 153 | 0.00069479 | 0.00045268 | N
03/10/2016 | 12:20 | 524:33578 | URBAN | Vegetation | Grow-in - NSP responsibility | 29 | 25 | 0.00050068 | 0.0020027 | N
03/10/2016 | 11:34 | 243:80084 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 221 | 0.00099846 | 0.00045268 | N
03/10/2016 | 15:46 | ZN3154:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 119 | 0.0031242 | 0.0026243 | N
03/10/2016 | 21:44 | ZN10999:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2,724 | 44 | 0.082772 | 0.18812 | N
04/10/2016 | 06:00 | ZN36200:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 209 | 0.00094625 | 0.00045268 | N
04/10/2016 | 12:00 | ZN12580:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 19 | 80 | 0.0068808 | 0.0086009 | N
04/10/2016 | 13:09 | ZN12690:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 406 | 41 | 0.011608 | 0.028038 | N
04/10/2016 | 14:58 | ZN187:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 6 | 271 | 0.0011233 | 0.00041436 | N
04/10/2016 | 17:48 | ZN180:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 335 | 0.00023104 | 6.9059e-05 | N
04/10/2016 | 21:38 | ZN3425:PA33 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 27 | 143 | 0.0026664 | 0.0018646 | N
04/10/2016 | 21:43 | ZN2635:PA43 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 87 | 197 | 0.011836 | 0.0060082 | N
06/10/2016 | 09:12 | ZN1648:PA21 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 21 | 1.4687e-05 | 6.9062e-05 | N
08/10/2016 | 10:46 | ZN10993:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 344 | 0.00023734 | 6.9085e-05 | N
08/10/2016 | 11:45 | ZN1285:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 210 | 0.00014477 | 6.9085e-05 | N
08/10/2016 | 14:29 | ZN180:PA41 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 120 | 8.3133e-05 | 6.9085e-05 | N
09/10/2016 | 11:37 | ZN15010:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 107 | 7.3669e-05 | 6.9086e-05 | N
10/10/2016 | 10:49 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 23 | 31 | 0.0032266 | 0.010408 | N
10/10/2016 | 15:55 | ZN35800:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 15 | 100 | 0.0010363 | 0.0010363 | N
10/10/2016 | 15:55 | ZN35800:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 15 | 100 | 0.0010363 | 0.0010363 | N
10/10/2016 | 23:00 | ZN10994:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 735 | 75 | 0.038084 | 0.050778 | N
11/10/2016 | 01:43 | ZN12650:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 30 | 187 | 0.025366 | 0.013565 | N
11/10/2016 | 16:21 | ZN4545:PA40 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 129 | 8.8748e-05 | 6.9046e-05 | N
12/10/2016 | 10:04 | ZN9245:PA42 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 94 | 6.5193e-05 | 6.9048e-05 | N
12/10/2016 | 12:27 | ZN9252:PA22 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 43 | 2.9656e-05 | 6.9048e-05 | N
12/10/2016 | 15:32 | ZN2196:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,754 | 87 | 0.10537 | 0.12111 | N
13/10/2016 | 06:35 | ZN12610:PA20 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 1 | 174 | 0.00078699 | 0.00045199 | N
13/10/2016 | 22:30 | ZN12640:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 794 | 0.0035908 | 0.00045199 | N
14/10/2016 | 15:51 | ZN12650:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 399 | 0.001803 | 0.00045199 | N
16/10/2016 | 19:51 | ZN195:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 42 | 254 | 0.0073611 | 0.0029009 | N
17/10/2016 | 11:35 | ZN15001:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 474 | 0.00032769 | 6.9069e-05 | N
17/10/2016 | 11:36 | ZN2635:PA38 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 53 | 149 | 0.0054373 | 0.0036607 | N
17/10/2016 | 12:21 | 504:48033 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 3 | 414 | 0.0055941 | 0.0013512 | N
19/10/2016 | 12:43 | ZN690:PA18 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 71 | 4.9319e-05 | 6.9075e-05 | N
21/10/2016 | 18:17 | ZN15010:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 45 | 525 | 0.016397 | 0.0031239 | N
22/10/2016 | 05:48 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 57 | 78 | 0.020017 | 0.025663 | N
22/10/2016 | 11:45 | 232:33407 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 3 | 55 | 0.00074287 | 0.0013507 | N
23/10/2016 | 18:53 | ZN12690:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 187 | 0.00012898 | 6.9058e-05 | N
20/10/2016 | 11:10 | ZN35370:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 39 | 30 | 0.0052699 | 0.017566 | N
25/10/2016 | 09:06 | 235:2123 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 81 | 5.5926e-05 | 6.9059e-05 | N
25/10/2016 | 13:41 | ZN3472:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 229 | 0.0001581 | 6.9059e-05 | N
26/10/2016 | 21:27 | ZN12630:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 8 | 743 | 0.026762 | 0.0036019 | N
27/10/2016 | 09:15 | 224:80332 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 75 | 5.1467e-05 | 6.9037e-05 | N
27/10/2016 | 21:10 | ZN35370:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 186 | 104 | 0.08707 | 0.083722 | N
28/10/2016 | 12:18 | ZN180:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 22 | 162 | 0.0024569 | 0.0015188 | N
28/10/2016 | 22:21 | ZN35500:PA27 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 324 | 0.00022356 | 6.9037e-05 | N
29/10/2016 | 15:57 | ZN3154:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 94 | 138 | 0.0089556 | 0.0064896 | N
29/10/2016 | 19:42 | ZN384:PA33 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 16 | 214 | 0.0023639 | 0.0011046 | N
29/10/2016 | 21:51 | ZN187:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 83 | 73 | 0.0042098 | 0.0057302 | N
30/10/2016 | 21:00 | ZN12690:PA7 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 14 | 80 | 0.0050192 | 0.0063016 | N
31/10/2016 | 05:26 | ZN15005:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 79 | 92 | 0.0050377 | 0.005454 | N
31/10/2016 | 05:54 | ZN3155:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 156 | 0.00010754 | 6.9038e-05 | N
31/10/2016 | 05:55 | ZN3472:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 274 | 0.00018948 | 6.9038e-05 | N
31/10/2016 | 07:32 | 239:82132 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 507 | 0.00035028 | 6.9038e-05 | N
31/10/2016 | 11:24 | ZN15004:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 395 | 0.00027286 | 6.9038e-05 | N
31/10/2016 | 12:55 | ZN3155:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 365 | 0.00025177 | 6.9038e-05 | N
28/10/2016 | 14:00 | ZN35370:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 18 | 30 | 0.0024306 | 0.0081021 | N
27/10/2016 | 21:00 | ZN80:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 145 | 0.0038039 | 0.0026234 | N
29/10/2016 | 20:49 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 30 | 96 | 0.0019883 | 0.0020711 | N
01/11/2016 | 19:48 | ZN80:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 307 | 0.00021226 | 6.9041e-05 | N
02/11/2016 | 18:21 | ZN9245:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 52 | 98 | 0.0035328 | 0.0035903 | N
05/11/2016 | 10:59 | ZN9118:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 240 | 0.00016572 | 6.9027e-05 | N
05/11/2016 | 11:33 | ZN3922:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 44 | 298 | 0.059003 | 0.0198 | N
05/11/2016 | 11:46 | ZN690:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 409 | 0.00028214 | 6.9027e-05 | N
05/11/2016 | 14:58 | ZN4545:PA40 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 50 | 432 | 0.01491 | 0.0034514 | N
05/11/2016 | 12:12 | ZN690:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 384 | 0.00026475 | 6.9027e-05 | N
05/11/2016 | 12:19 | ZN10991:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 59 | 226 | 0.0092041 | 0.0040726 | N
05/11/2016 | 14:37 | ZN9700:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 49 | 118 | 0.0039911 | 0.0033823 | N
05/11/2016 | 16:13 | ZN690:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 141 | 9.7639e-05 | 6.9027e-05 | N
05/11/2016 | 23:36 | ZN965:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 20 | 659 | 0.0090913 | 0.0013805 | N
06/11/2016 | 08:10 | 504:48031 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 559 | 121 | 0.30389 | 0.25155 | N
06/11/2016 | 13:13 | ZN12620:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 377 | 0.0016965 | 0.00044999 | N
06/11/2016 | 18:23 | ZN1673:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 448 | 0.00030895 | 6.9028e-05 | N
07/11/2016 | 14:37 | ZN14144:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 142 | 9.8192e-05 | 6.9028e-05 | N
07/11/2016 | 17:49 | ZN15014:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 170 | 0.00011759 | 6.9028e-05 | N
08/11/2016 | 09:17 | ZN9550:PA36 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 147 | 0.00010157 | 6.9029e-05 | N
08/11/2016 | 18:50 | ZN2310:PA71 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 437 | 0.00030193 | 6.9029e-05 | N
08/11/2016 | 19:01 | ZN2310:PA71 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 426 | 0.00029401 | 6.9029e-05 | N
09/11/2016 | 12:46 | ZN13000:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 253 | 0.001139 | 0.00045 | N
09/11/2016 | 15:29 | ZN4545:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 81 | 5.5892e-05 | 6.9031e-05 | N
10/11/2016 | 09:13 | ZN4545:PA40 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 79 | 5.4846e-05 | 6.9033e-05 | N
10/11/2016 | 12:49 | 524:33578 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 55 | 3.7979e-05 | 6.9033e-05 | N
11/11/2016 | 08:57 | ZN1193:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 152 | 0.00010501 | 6.9033e-05 | N
11/11/2016 | 20:02 | ZN12630:PA22 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 185 | 235 | 0.19526 | 0.083252 | N
12/11/2016 | 04:12 | ZN35370:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 719 | 74 | 0.2393 | 0.32338 | N
12/11/2016 | 07:12 | 243:80074 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,795 | 10 | 0.084309 | 0.80733 | N
12/11/2016 | 14:42 | ZN15010:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 345 | 0.000238 | 6.9011e-05 | N
12/11/2016 | 18:02 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 59 | 113 | 0.0045888 | 0.0040717 | N
12/11/2016 | 18:16 | ZN195:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 89 | 0.002334 | 0.0026224 | N
12/11/2016 | 20:16 | ZN3154:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 44 | 83 | 0.0025304 | 0.0030365 | N
13/11/2016 | 08:26 | ZN12660:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,819 | 0.008181 | 0.00044977 | N
13/11/2016 | 12:10 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 4 | 206 | 0.0037061 | 0.0017991 | N
13/11/2016 | 13:46 | ZN14891:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 395 | 0.0017756 | 0.00044977 | N
13/11/2016 | 16:10 | ZN847:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 440 | 0.0019784 | 0.00044977 | N
13/11/2016 | 16:12 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 6 | 253 | 0.0068275 | 0.0026986 | N
13/11/2016 | 16:42 | ZN1673:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 347 | 0.00023964 | 6.9011e-05 | N
14/11/2016 | 00:24 | ZN847:PA47 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 55 | 51 | 0.012616 | 0.024737 | N
13/11/2016 | 21:23 | ZN13000:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 265 | 0.0011935 | 0.00044977 | N
14/11/2016 | 05:59 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 70 | 0.0013549 | 0.0019323 | N
14/11/2016 | 07:36 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 404 | 0.00027863 | 6.9011e-05 | N
14/11/2016 | 10:10 | ZN847:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 739 | 0.00051029 | 6.9011e-05 | N
14/11/2016 | 15:01 | ZN4545:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 89 | 241 | 0.014778 | 0.006142 | N
14/11/2016 | 16:25 | 227:13015 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 9 | 55 | 0.0022264 | 0.0040479 | N
14/11/2016 | 18:32 | ZN2400:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 695 | 8 | 0.025007 | 0.31259 | N
14/11/2016 | 19:08 | ZN12640:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,311 | 0.0058974 | 0.00044977 | N
15/11/2016 | 09:35 | 224:80340 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,086 | 94 | 0.45841 | 0.48845 | N
15/11/2016 | 12:25 | ZN3154:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 19 | 14 | 0.00018597 | 0.0013112 | N
15/11/2016 | 14:34 | ZN12630:PA23 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 205 | 0.00092399 | 0.00044977 | N
15/11/2016 | 15:12 | ZN15006:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 198 | 0.00013655 | 6.9011e-05 | N
16/11/2016 | 12:07 | ZN9700:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 112 | 7.7443e-05 | 6.9012e-05 | N
16/11/2016 | 14:32 | 513:48059 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 148 | 0.0006638 | 0.00044978 | N
17/11/2016 | 15:27 | ZN14144:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 173 | 0.0033419 | 0.0019317 | N
17/11/2016 | 23:54 | ZN129:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 486 | 0.00033518 | 6.8991e-05 | N
18/11/2016 | 15:47 | ZN15002:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 988 | 73 | 0.049759 | 0.068163 | N
19/11/2016 | 01:02 | ZN1193:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 839 | 81 | 0.046887 | 0.057885 | N
19/11/2016 | 19:35 | ZN965:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 35 | 25 | 0.00060369 | 0.0024148 | N
21/11/2016 | 02:55 | ZN965:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 35 | 125 | 0.0030185 | 0.0024148 | N
21/11/2016 | 02:55 | ZN965:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 83 | 803 | 0.045991 | 0.0057266 | N
21/11/2016 | 08:14 | 223:14394 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 56 | 3.8534e-05 | 6.8995e-05 | N
21/11/2016 | 11:25 | ZN12570:PA37 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 61 | 0.00027601 | 0.00044965 | N
21/11/2016 | 16:01 | ZN2635:PA52 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 224 | 0.00015434 | 6.8995e-05 | N
21/11/2016 | 18:41 | ZN1193:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 178 | 0.00012298 | 6.8995e-05 | N
22/11/2016 | 06:53 | ZN35370:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 6 | 2.8028e-05 | 0.00044965 | N
22/11/2016 | 15:24 | ZN4545:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 365 | 0.00025189 | 6.8996e-05 | N
22/11/2016 | 16:47 | ZN2400:PA15 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 24 | 148 | 0.015972 | 0.010792 | N
22/11/2016 | 16:48 | ZN195:PA30 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 342 | 0.0015356 | 0.00044965 | N
22/11/2016 | 16:57 | 526:34636 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 1 | 374 | 0.0016837 | 0.00044965 | N
22/11/2016 | 17:48 | ZN1673:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 20 | 90 | 0.0012419 | 0.0013799 | N
23/11/2016 | 13:57 | 223:14393 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 67 | 4.6562e-05 | 6.8998e-05 | N
23/11/2016 | 18:14 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 45 | 162 | 0.0050346 | 0.0031049 | N
24/11/2016 | 11:07 | ZN9118:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 233 | 0.00016071 | 6.8978e-05 | N
24/11/2016 | 20:42 | ZN36300:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 481 | 0.00033176 | 6.8978e-05 | N
24/11/2016 | 15:47 | ZN3154:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 111 | 0.0030502 | 0.0027591 | N
26/11/2016 | 10:48 | 504:48026 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,275 | 76 | 0.43582 | 0.57305 | N
26/11/2016 | 18:59 | ZN15005:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 39 | 61 | 0.0016422 | 0.0026921 | N
27/11/2016 | 03:51 | ZN2310:PA54 | URBAN | Vegetation | Grow-in - NSP responsibility | 58 | 254 | 0.010169 | 0.0040036 | N
27/11/2016 | 19:28 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 26 | 52 | 0.00093326 | 0.0017947 | N
28/11/2016 | 10:04 | ZN35370:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 220 | 0.00099037 | 0.00044945 | N
28/11/2016 | 10:46 | ZN15014:PA19 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 1,248 | 0.00086169 | 6.9028e-05 | N
27/11/2016 | 03:51 | ZN2310:PA54 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 76 | 254 | 0.013325 | 0.0052462 | N
29/11/2016 | 05:21 | ZN9700:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 549 | 0.00037862 | 6.9028e-05 | N
29/11/2016 | 14:24 | ZN15006:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 371 | 0.00025588 | 6.9028e-05 | N
30/11/2016 | 08:58 | ZN3155:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 52 | 3.5676e-05 | 6.9028e-05 | N
01/12/2016 | 20:57 | ZN80:PA39 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 93 | 0.0025616 | 0.0027603 | N
02/12/2016 | 19:12 | ZN2196:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 97 | 0.0026812 | 0.0027603 | N
03/12/2016 | 08:23 | ZN15006:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 236 | 0.0001627 | 6.8959e-05 | N
04/12/2016 | 19:24 | ZN3425:PA43 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 21 | 1.4366e-05 | 6.8959e-05 | N
05/12/2016 | 06:29 | ZN1193:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,479 | 80 | 0.081471 | 0.10199 | N
05/12/2016 | 06:33 | ZN4545:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 39 | 105 | 0.0028239 | 0.0026894 | N
05/12/2016 | 14:55 | ZN2635:PA52 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 90 | 0.0026687 | 0.0029652 | N
05/12/2016 | 15:05 | ZN15009:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 380 | 0.00026237 | 6.8959e-05 | N
05/12/2016 | 15:18 | 238:34140 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 71 | 4.9018e-05 | 6.8959e-05 | N
05/12/2016 | 16:02 | ZN9900:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 208 | 0.0001434 | 6.8959e-05 | N
05/12/2016 | 16:28 | ZN14144:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 572 | 0.0025685 | 0.00044927 | N
05/12/2016 | 17:34 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 24 | 1,151 | 0.1241 | 0.010783 | N
05/12/2016 | 17:01 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,439 | 0.0064636 | 0.00044927 | N
05/12/2016 | 17:01 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 10 | 1,048 | 0.0072269 | 0.00068959 | N
05/12/2016 | 17:35 | ZN15014:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,012 | 132 | 0.092054 | 0.069787 | N
05/12/2016 | 17:35 | ZN15014:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 325 | 0.00022412 | 6.8959e-05 | N
06/12/2016 | 12:00 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 83 | 170 | 0.063393 | 0.03729 | N
05/12/2016 | 17:40 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 8 | 1,310 | 0.047068 | 0.0035942 | N
05/12/2016 | 17:44 | ZN15013:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,096 | 0.0049237 | 0.00044927 | N
05/12/2016 | 22:22 | ZN10995:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 181 | 0.00012484 | 6.8959e-05 | N
05/12/2016 | 22:39 | ZN9037:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 41 | 46 | 0.0013006 | 0.0028273 | N
06/12/2016 | 08:38 | ZN15014:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 66 | 4.5284e-05 | 6.8961e-05 | N
06/12/2016 | 13:24 | ZN15014:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 216 | 0.00014889 | 6.8961e-05 | N
06/12/2016 | 21:17 | ZN965:PA47 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 147 | 0.0033457 | 0.0022757 | N
07/12/2016 | 04:52 | ZN15002:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 47 | 247 | 0.008016 | 0.0032412 | N
07/12/2016 | 08:03 | ZN15014:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 325 | 127 | 0.18544 | 0.14602 | N
07/12/2016 | 09:22 | 508:82580 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 308 | 0.0013827 | 0.00044928 | N
07/12/2016 | 13:23 | ZN12570:PA24 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 53 | 56 | 0.013343 | 0.023812 | N
07/12/2016 | 13:00 | ZN36100:PA19 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 37 | 2.5757e-05 | 6.8962e-05 | N
08/12/2016 | 09:37 | ZN1673:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 36 | 152 | 0.0037738 | 0.0024817 | N
09/12/2016 | 07:05 | ZN80:PA37 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 235 | 0.00016184 | 6.8938e-05 | N
09/12/2016 | 09:26 | ZN1673:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 224 | 0.00015424 | 6.8938e-05 | N
09/12/2016 | 10:43 | ZN3672:PA35 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 376 | 0.0016916 | 0.00044934 | N
09/12/2016 | 13:02 | ZN36800:PA42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 53 | 3.6434e-05 | 6.8938e-05 | N
09/12/2016 | 15:15 | ZN9534:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 314 | 0.0014113 | 0.00044934 | N
09/12/2016 | 16:13 | ZN15013:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 306 | 0.0013759 | 0.00044934 | N
09/12/2016 | 18:22 | ZN35600:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 188 | 0.00012945 | 6.8938e-05 | N
09/12/2016 | 23:18 | ZN398:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 345 | 0.00023802 | 6.8938e-05 | N
10/12/2016 | 14:01 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 26 | 194 | 0.0034758 | 0.0017924 | N
10/12/2016 | 14:14 | ZN10994:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 32 | 191 | 0.0042136 | 0.0022061 | N
10/12/2016 | 14:27 | ZN1673:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 14 | 148 | 0.0014284 | 0.00096515 | N
10/12/2016 | 16:51 | ZN965:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 266 | 0.0001835 | 6.8939e-05 | N
10/12/2016 | 20:57 | ZN1673:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 16 | 148 | 0.0016314 | 0.001103 | N
11/12/2016 | 03:43 | ZN36800:PA40 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 737 | 0.0005081 | 6.8941e-05 | N
12/12/2016 | 07:59 | ZN14144:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 72 | 4.9753e-05 | 6.8941e-05 | N
12/12/2016 | 13:49 | 205:12213 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 58 | 0.00026145 | 0.00044935 | N
12/12/2016 | 16:37 | 220:8687 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 103 | 7.0837e-05 | 6.8941e-05 | N
13/12/2016 | 13:45 | ZN80:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,484 | 53 | 0.054224 | 0.10231 | N
13/12/2016 | 17:37 | ZN12660:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 239 | 0.0010723 | 0.00044935 | N
14/12/2016 | 14:47 | ZN36200:PA1 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 342 | 0.00023587 | 6.8943e-05 | N
14/12/2016 | 16:01 | ZN2835:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 104 | 203 | 0.014588 | 0.0071701 | N
14/12/2016 | 23:11 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 693 | 0.00047796 | 6.8943e-05 | N
15/12/2016 | 00:31 | ZN847:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 614 | 0.00042292 | 6.8924e-05 | N
15/12/2016 | 01:03 | ZN15010:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 50 | 392 | 0.013509 | 0.0034462 | N
15/12/2016 | 08:57 | ZN36100:PA13 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 992 | 0.00068399 | 6.8924e-05 | N
15/12/2016 | 12:14 | 523:33503 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 88 | 6.0596e-05 | 6.8924e-05 | N
15/12/2016 | 13:39 | ZN3922:PA2 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 186 | 0.00012785 | 6.8924e-05 | N
15/12/2016 | 16:06 | ZN12570:PA29 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 483 | 0.002171 | 0.00044909 | N
15/12/2016 | 17:22 | ZN847:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 277 | 0.00019106 | 6.8924e-05 | N
15/12/2016 | 18:57 | ZN12600:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 2 | 36 | 0.00032334 | 0.00089818 | N
16/12/2016 | 10:24 | ZN195:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 32 | 281 | 0.0061978 | 0.0022056 | N
16/12/2016 | 08:23 | 206:34440 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 15 | 112 | 0.001158 | 0.0010339 | N
16/12/2016 | 17:30 | ZN342:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 144 | 171 | 0.016987 | 0.0099253 | N
17/12/2016 | 06:01 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 458 | 0.00031557 | 6.8927e-05 | N
17/12/2016 | 13:01 | 229:34995 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 246 | 0.0011035 | 0.00044909 | N
17/12/2016 | 04:10 | ZN2635:PA58 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 800 | 0.00055118 | 6.8927e-05 | N
17/12/2016 | 22:26 | ZN35400:PA81 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,263 | 0.00087061 | 6.8927e-05 | N
18/12/2016 | 07:29 | 227:13015 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 182 | 0.00081747 | 0.00044908 | N
18/12/2016 | 23:24 | ZN12690:PA24 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 6 | 51 | 0.0013742 | 0.0026945 | N
19/12/2016 | 09:25 | ZN9700:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 65 | 0.0012545 | 0.00193 | N
19/12/2016 | 09:57 | 507:80925 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 57 | 0.00025605 | 0.00044908 | N
19/12/2016 | 11:43 | ZN15010:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,175 | 0.0008098 | 6.8927e-05 | N
19/12/2016 | 18:08 | ZN3154:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 20 | 192 | 0.0026468 | 0.0013785 | N
19/12/2016 | 21:40 | ZN80:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 84 | 5 | 0.00028949 | 0.0057899 | N
20/12/2016 | 15:57 | ZN3472:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 94 | 28 | 0.0018142 | 0.0064792 | N
20/12/2016 | 17:19 | ZN9245:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2 | 941 | 0.0012972 | 0.00013785 | N
20/12/2016 | 17:47 | ZN14892:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 103 | 0.0034078 | 0.0033085 | N
20/12/2016 | 19:23 | ZN847:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 62 | 99 | 0.0042443 | 0.0042735 | N
21/12/2016 | 10:44 | ZN3154:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,147 | 68 | 0.053857 | 0.07906 | N
21/12/2016 | 17:15 | ZN847:PA36 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 78 | 5.3833e-05 | 6.8928e-05 | N
21/12/2016 | 18:30 | ZN847:PA36 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 56 | 250 | 0.0096499 | 0.00386 | N
23/12/2016 | 14:32 | 504:48033 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 52 | 0.00023496 | 0.00044896 | N
23/12/2016 | 17:53 | ZN12600:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,744 | 58 | 0.069666 | 0.12018 | N
23/12/2016 | 19:54 | ZN847:PA46 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 125 | 8.6331e-05 | 6.8908e-05 | N
24/12/2016 | 17:01 | 520:48172 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,438 | 0.0064567 | 0.00044897 | N
24/12/2016 | 19:05 | ZN35900:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 64 | 120 | 0.034481 | 0.028734 | N
25/12/2016 | 11:32 | ZN9700:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 49 | 103 | 0.0034722 | 0.0033765 | N
25/12/2016 | 14:39 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 56 | 558 | 0.14035 | 0.025142 | N
25/12/2016 | 20:35 | ZN10994:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 205 | 0.00014103 | 6.8909e-05 | N
27/12/2016 | 02:18 | ZN12640:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 12 | 96 | 0.00079686 | 0.00082691 | N
26/12/2016 | 20:31 | ZN14891:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 43 | 189 | 0.036488 | 0.019306 | N
27/12/2016 | 10:29 | ZN2400:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 36 | 433 | 0.069942 | 0.016163 | N
27/12/2016 | 12:46 | ZN3922:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 243 | 0.00016777 | 6.8909e-05 | N
28/12/2016 | 15:10 | ZN14891:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 53 | 0.00023586 | 0.00044897 | N
28/12/2016 | 17:11 | 242:81541 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 309 | 0.00021316 | 6.8909e-05 | N
28/12/2016 | 17:12 | ZN15004:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,751 | 91 | 0.1098 | 0.12066 | N
28/12/2016 | 18:16 | ZN2310:PA72 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 224 | 0.00015443 | 6.8909e-05 | N
29/12/2016 | 04:10 | ZN1287:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 379 | 0.00026127 | 6.891e-05 | N
29/12/2016 | 08:30 | ZN965:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 74 | 240 | 0.012238 | 0.0050993 | N
29/12/2016 | 11:19 | 223:14394 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 250 | 0.00017239 | 6.891e-05 | N
29/12/2016 | 12:27 | 526:34639 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 2 | 68 | 0.0006106 | 0.00089795 | N
29/12/2016 | 18:45 | ZN3472:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 87 | 45 | 0.0026978 | 0.0059951 | N
29/12/2016 | 17:39 | ZN847:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 21 | 242 | 0.003502 | 0.0014471 | N
29/12/2016 | 18:20 | 239:82127 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 869 | 95 | 0.36888 | 0.39016 | N
29/12/2016 | 18:39 | ZN9037:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 41 | 180 | 0.0050916 | 0.0028253 | N
30/12/2016 | 19:31 | 232:11454 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 205 | 0.00092198 | 0.00044898 | N
30/12/2016 | 19:34 | ZN4545:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 75 | 136 | 0.0070289 | 0.0051683 | N
30/12/2016 | 19:34 | ZN4545:PA42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 80 | 136 | 0.0074974 | 0.0055128 | N
31/12/2016 | 12:04 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 392 | 0.0017581 | 0.00044898 | N
31/12/2016 | 14:04 | ZN1287:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 25 | 56 | 0.00096476 | 0.0017228 | N
01/01/2017 | 03:03 | ZN12690:PA7 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 427 | 0.0019178 | 0.00044898 | N
01/01/2017 | 10:22 | ZN1673:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 482 | 52 | 0.017341 | 0.033215 | N
02/01/2017 | 04:40 | ZN180:PA30 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 593 | 0.00040886 | 6.8911e-05 | N
02/01/2017 | 05:52 | ZN2835:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 89 | 107 | 0.0065788 | 0.0061331 | N
02/01/2017 | 09:02 | 243:80081 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 394 | 0.0017694 | 0.00044898 | N
02/01/2017 | 09:50 | ZN2835:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 89 | 384 | 0.023551 | 0.0061331 | N
02/01/2017 | 12:15 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 135 | 235 | 0.021852 | 0.009303 | N
03/01/2017 | 11:51 | ZN3154:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 428 | 0.00029513 | 6.8911e-05 | N
03/01/2017 | 13:35 | ZN3154:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,414 | 0.00097456 | 6.8911e-05 | N
03/01/2017 | 14:20 | ZN1290:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 45 | 3.1079e-05 | 6.8911e-05 | N
03/01/2017 | 19:32 | ZN3154:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 620 | 64 | 0.17816 | 0.27837 | N
04/01/2017 | 16:42 | 227:13015 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 321 | 51 | 0.073503 | 0.14412 | N
05/01/2017 | 14:06 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 112 | 7.7355e-05 | 6.8913e-05 | N
05/01/2017 | 19:23 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 249 | 0.00017132 | 6.8913e-05 | N
05/01/2017 | 20:14 | ZN12600:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 282 | 138 | 0.17517 | 0.12661 | N
06/01/2017 | 17:53 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 73 | 172 | 0.056376 | 0.032777 | N
07/01/2017 | 05:40 | ZN12600:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 470 | 0.0021071 | 0.00044881 | N
07/01/2017 | 10:58 | ZN12650:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 76 | 5.229e-05 | 6.8893e-05 | N
07/01/2017 | 13:59 | ZN36200:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 62 | 0.00027699 | 0.00044881 | N
07/01/2017 | 14:17 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 446 | 0.0020002 | 0.00044881 | N
08/01/2017 | 10:27 | ZN13000:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 272 | 0.0012214 | 0.00044881 | N
09/01/2017 | 10:21 | ZN1788:PA1 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 81 | 5.5481e-05 | 6.8892e-05 | N
09/01/2017 | 11:28 | ZN188:PA22 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 1,411 | 0.00097239 | 6.8892e-05 | N
09/01/2017 | 12:17 | ZN12690:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 102 | 0.00045801 | 0.00044881 | N
09/01/2017 | 13:44 | ZN9118:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 97 | 6.6516e-05 | 6.8892e-05 | N
09/01/2017 | 22:22 | ZN9700:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 55 | 112 | 0.0042608 | 0.0037891 | N
10/01/2017 | 09:44 | ZN3672:PA36 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 150 | 0.0001035 | 6.8893e-05 | N
10/01/2017 | 13:53 | ZN1290:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 132 | 9.126e-05 | 6.8893e-05 | N
10/01/2017 | 15:56 | ZN398:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 93 | 6.4323e-05 | 6.8893e-05 | N
10/01/2017 | 17:14 | ZN2635:PA38 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 707 | 46 | 0.022596 | 0.048707 | N
10/01/2017 | 17:14 | ZN2635:PA52 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 296 | 78 | 0.015906 | 0.020392 | N
10/01/2017 | 17:25 | ZN15001:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 238 | 0.00016397 | 6.8893e-05 | N
10/01/2017 | 17:59 | ZN195:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 34 | 36 | 0.00084325 | 0.0023424 | N
10/01/2017 | 17:59 | ZN195:PA30 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 36 | 0.00016157 | 0.00044881 | N
11/01/2017 | 11:42 | 264:81236 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 35 | 0.00015746 | 0.00044882 | N
11/01/2017 | 14:59 | ZN3154:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 551 | 0.016323 | 0.0029624 | N
11/01/2017 | 17:27 | 243:80075 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 30 | 147 | 0.019768 | 0.013465 | N
11/01/2017 | 17:33 | ZN965:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 327 | 0.00022505 | 6.8894e-05 | N
11/01/2017 | 18:02 | ZN35500:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 236 | 31 | 0.0050403 | 0.016259 | N
11/01/2017 | 18:08 | ZN15006:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 821 | 90 | 0.050906 | 0.056562 | N
11/01/2017 | 18:14 | ZN847:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 270 | 0.00018616 | 6.8894e-05 | N
11/01/2017 | 18:20 | ZN3154:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 399 | 0.011834 | 0.0029624 | N
11/01/2017 | 18:23 | ZN4545:PA40 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 246 | 0.00016953 | 6.8894e-05 | N
11/01/2017 | 18:51 | ZN1850:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 344 | 0.0094766 | 0.0027558 | N
11/01/2017 | 19:04 | ZN9900:PA19 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 374 | 0.00025796 | 6.8894e-05 | N
11/01/2017 | 19:44 | 261:81885 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 136 | 9.3638e-05 | 6.8894e-05 | N
11/01/2017 | 21:05 | 261:81865 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 84 | 5.817e-05 | 6.8894e-05 | N
12/01/2017 | 06:44 | ZN965:PA42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 29 | 91 | 0.0018142 | 0.0019976 | N
12/01/2017 | 07:08 | ZN9037:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 124 | 8.5175e-05 | 6.8884e-05 | N
12/01/2017 | 08:46 | ZN72:PA26 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 111 | 7.6278e-05 | 6.8884e-05 | N
11/01/2017 | 19:00 | ZN9700:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 85 | 5.856e-05 | 6.8894e-05 | N
12/01/2017 | 13:29 | ZN15005:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 210 | 0.00014491 | 6.8884e-05 | N
12/01/2017 | 15:55 | ZN12650:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 155 | 0.00010651 | 6.8884e-05 | N
12/01/2017 | 20:03 | ZN195:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 266 | 0.0011959 | 0.00044885 | N
13/01/2017 | 02:37 | ZN965:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 41 | 293 | 0.0082639 | 0.0028243 | N
13/01/2017 | 13:20 | ZN12570:PA24 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,763 | 51 | 0.40358 | 0.79134 | N
13/01/2017 | 15:02 | ZN1673:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 628 | 0.00043228 | 6.8886e-05 | N
13/01/2017 | 15:51 | ZN1673:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 14 | 169 | 0.0016269 | 0.0009644 | N
13/01/2017 | 17:29 | ZN9900:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 345 | 0.00023798 | 6.8886e-05 | N
14/01/2017 | 00:03 | ZN9118:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 34 | 417 | 0.0097666 | 0.0023421 | N
14/01/2017 | 14:59 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 7 | 450 | 0.014144 | 0.003142 | N
14/01/2017 | 23:23 | ZN965:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 665 | 0.00045817 | 6.8886e-05 | N
15/01/2017 | 01:35 | ZN195:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 25 | 345 | 0.0059414 | 0.0017221 | N
15/01/2017 | 11:46 | ZN3672:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 256 | 0.0001765 | 6.8886e-05 | N
15/01/2017 | 12:30 | ZN2635:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 24 | 30 | 0.00049598 | 0.0016533 | N
15/01/2017 | 16:33 | ZN1193:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2 | 338 | 0.00046556 | 0.00013777 | N
15/01/2017 | 17:03 | 243:80083 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 58 | 0.00026011 | 0.00044885 | N
16/01/2017 | 13:16 | ZN901:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 193 | 0.00013296 | 6.8886e-05 | N
16/01/2017 | 13:46 | ZN901:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 163 | 0.00011253 | 6.8886e-05 | N
16/01/2017 | 15:52 | ZN80:PA39 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 24 | 0.00065258 | 0.0027554 | N
16/01/2017 | 17:48 | ZN2400:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 282 | 0.00019422 | 6.8886e-05 | N
16/01/2017 | 18:03 | ZN15005:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 157 | 0.003569 | 0.0022732 | N
17/01/2017 | 14:26 | 203:8086 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 48 | 3.2962e-05 | 6.8887e-05 | N
17/01/2017 | 15:06 | ZN9035:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 204 | 0.00014034 | 6.8887e-05 | N
17/01/2017 | 15:54 | ZN847:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 119 | 164 | 0.013475 | 0.0081975 | N
17/01/2017 | 17:01 | 205:12213 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 66 | 124 | 0.036734 | 0.029624 | N
17/01/2017 | 17:39 | ZN1673:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 25 | 111 | 0.0019113 | 0.0017222 | N
17/01/2017 | 21:05 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 227 | 0.00015633 | 6.8887e-05 | N
17/01/2017 | 21:33 | ZN2635:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 188 | 0.00012961 | 6.8887e-05 | N
17/01/2017 | 23:12 | 205:12205 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 360 | 0.0016167 | 0.00044885 | N
18/01/2017 | 08:32 | 256:80632 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 147 | 0.00010148 | 6.8887e-05 | N
18/01/2017 | 12:20 | ZN1673:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 50 | 0.0011366 | 0.0022733 | N
18/01/2017 | 10:58 | ZN3154:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 202 | 0.00013893 | 6.8887e-05 | N
18/01/2017 | 11:01 | ZN3922:PA5 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 119 | 8.1941e-05 | 6.8887e-05 | N
18/01/2017 | 11:06 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 204 | 0.00014053 | 6.8887e-05 | N
18/01/2017 | 14:45 | ZN9252:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 166 | 0.0054762 | 0.0033066 | N
12/01/2017 | 08:38 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 22 | 0.00060618 | 0.0027554 | N
18/01/2017 | 15:25 | ZN3154:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 215 | 0.00014783 | 6.8887e-05 | N
18/01/2017 | 15:49 | ZN2835:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 39 | 84 | 0.0022567 | 0.0026866 | N
18/01/2017 | 16:37 | ZN10994:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 202 | 0.0055757 | 0.0027555 | N
18/01/2017 | 17:22 | ZN12580:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 3 | 168 | 0.00034719 | 0.00020666 | N
18/01/2017 | 17:41 | 508:82578 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 234 | 0.001051 | 0.00044885 | N
18/01/2017 | 17:49 | ZN10995:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 550 | 0.00037903 | 6.8887e-05 | N
18/01/2017 | 17:51 | 810:74050 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 17 | 43 | 0.0032811 | 0.0076305 | N
18/01/2017 | 17:55 | ZN965:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 214 | 0.00014773 | 6.8887e-05 | N
18/01/2017 | 18:45 | ZN12580:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 104 | 7.1574e-05 | 6.8887e-05 | N
18/01/2017 | 23:15 | ZN3155:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 78 | 574 | 0.030842 | 0.0053732 | N
19/01/2017 | 11:25 | ZN13000:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 139 | 0.00062469 | 0.00044882 | N
16/01/2017 | 21:21 | ZN35370:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 186 | 9 | 0.0075138 | 0.083486 | N
16/01/2017 | 21:21 | ZN35370:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 77 | 9 | 0.0031105 | 0.034562 | N
19/01/2017 | 17:52 | 225:13446 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 367 | 0.00025254 | 6.8881e-05 | N
19/01/2017 | 21:24 | ZN965:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 242 | 0.0001667 | 6.8881e-05 | N
20/01/2017 | 03:44 | ZN3154:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 236 | 0.0045517 | 0.0019287 | N
20/01/2017 | 10:56 | 261:81879 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 270 | 0.00018618 | 6.8882e-05 | N
20/01/2017 | 12:17 | ZN36200:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 372 | 0.001671 | 0.00044881 | N
20/01/2017 | 17:22 | ZN12600:PA2 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 1 | 247 | 0.0011107 | 0.00044881 | N
20/01/2017 | 23:15 | ZN36300:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 30 | 0.00088858 | 0.0029619 | N
20/01/2017 | 22:02 | ZN3425:PA43 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,107 | 0.00076271 | 6.8882e-05 | N
20/01/2017 | 23:10 | ZN9252:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 169 | 0.00011669 | 6.8882e-05 | N
20/01/2017 | 23:20 | 221:11900 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,195 | 64 | 0.34445 | 0.53633 | N
21/01/2017 | 20:10 | 801:74118 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 161 | 0.00011107 | 6.8883e-05 | N
22/01/2017 | 08:38 | ZN2635:PA38 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 232 | 0.00015953 | 6.8883e-05 | N
23/01/2017 | 08:24 | ZN3425:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,221 | 134 | 0.11264 | 0.084105 | N
23/01/2017 | 08:24 | ZN1193:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 170 | 261 | 0.030563 | 0.01171 | N
23/01/2017 | 11:21 | ZN187:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 819 | 0.00056382 | 6.8882e-05 | N
23/01/2017 | 14:04 | ZN13000:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 51 | 0.00022727 | 0.00044886 | N
23/01/2017 | 17:42 | ZN1673:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 236 | 0.00016281 | 6.8882e-05 | N
23/01/2017 | 18:06 | ZN5868:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 682 | 0.00046945 | 6.8882e-05 | N
24/01/2017 | 10:48 | ZN690:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 61 | 101 | 0.0042621 | 0.0042019 | N
24/01/2017 | 13:09 | ZN12570:PA37 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,515 | 51 | 0.34682 | 0.68003 | N
24/01/2017 | 16:41 | ZN931:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 87 | 199 | 0.011926 | 0.0059929 | N
24/01/2017 | 17:00 | ZN15012:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 36 | 50 | 0.0012399 | 0.0024798 | N
24/01/2017 | 17:00 | ZN35500:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 103 | 70 | 0.0049665 | 0.007095 | N
24/01/2017 | 17:16 | ZN9118:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 313 | 0.00021534 | 6.8884e-05 | N
24/01/2017 | 17:22 | ZN80:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 34 | 73 | 0.0017097 | 0.002342 | N
24/01/2017 | 17:22 | 508:82578 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 316 | 229 | 0.32527 | 0.14184 | N
24/01/2017 | 17:53 | ZN15004:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 522 | 0.00035951 | 6.8884e-05 | N
24/01/2017 | 17:33 | ZN10990:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,107 | 0.00076254 | 6.8884e-05 | N
24/01/2017 | 18:05 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 504 | 0.0022626 | 0.00044887 | N
24/01/2017 | 18:24 | 243:80080 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 35 | 0.00015882 | 0.00044887 | N
24/01/2017 | 18:24 | 227:13019 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 116 | 170 | 0.088745 | 0.052068 | N
24/01/2017 | 18:40 | ZN12640:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 25 | 105 | 0.011783 | 0.011222 | N
24/01/2017 | 20:10 | ZN14144:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 165 | 73 | 0.054337 | 0.074063 | N
24/01/2017 | 10:00 | 514:18137 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 8 | 180 | 0.0064637 | 0.0035909 | N
25/01/2017 | 08:35 | ZN36200:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 265 | 0.0011879 | 0.00044889 | N
26/01/2017 | 12:37 | ZN1673:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 263 | 0.00018097 | 6.888e-05 | N
25/01/2017 | 16:27 | ZN15010:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 30 | 208 | 0.0042984 | 0.0020665 | N
26/01/2017 | 04:55 | ZN3425:PA39 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 95 | 145 | 0.0094883 | 0.0065436 | N
20/01/2017 | 14:30 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 3 | 40 | 0.00053858 | 0.0013464 | N
27/01/2017 | 10:57 | 504:48028 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 156 | 0.00010765 | 6.8874e-05 | N
27/01/2017 | 11:29 | ZN3155:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 316 | 0.00021747 | 6.8874e-05 | N
28/01/2017 | 09:21 | ZN9245:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 249 | 0.00017115 | 6.8875e-05 | N
28/01/2017 | 16:40 | ZN965:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 109 | 0.002858 | 0.0026173 | N
29/01/2017 | 00:27 | ZN9252:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 52 | 62 | 0.0022366 | 0.0035815 | N
29/01/2017 | 02:24 | ZN15008:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2,310 | 144 | 0.22884 | 0.1591 | N
29/01/2017 | 14:17 | ZN9118:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 387 | 0.00026672 | 6.8875e-05 | N
29/01/2017 | 14:17 | ZN9118:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 387 | 0.00026658 | 6.8875e-05 | N
29/01/2017 | 19:59 | ZN12630:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 102 | 289 | 0.13227 | 0.045722 | N
30/01/2017 | 02:08 | ZN9118:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 577 | 0.00039723 | 6.8875e-05 | N
30/01/2017 | 07:30 | ZN965:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 90 | 6.193e-05 | 6.8875e-05 | N
30/01/2017 | 07:38 | 813:89062 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 149 | 0.00066708 | 0.00044826 | N
30/01/2017 | 15:25 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 705 | 413 | 103.8717 | 25.1247 | N
30/01/2017 | 18:21 | ZN965:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 189 | 0.0036449 | 0.0019285 | N
30/01/2017 | 19:03 | ZN35600:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 207 | 0.00014227 | 6.8875e-05 | N
30/01/2017 | 22:45 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 11 | 20 | 0.078403 | 0.39202 | N
31/01/2017 | 11:05 | ZN12640:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 219 | 0.00098371 | 0.00044826 | N
31/01/2017 | 11:24 | ZN35370:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 43 | 156 | 0.030047 | 0.019275 | N
31/01/2017 | 12:21 | ZN35370:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 186 | 81 | 0.067632 | 0.083377 | N
28/01/2017 | 16:23 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 44 | 56 | 0.011135 | 0.019723 | N
31/01/2017 | 20:23 | ZN4545:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 58 | 51 | 0.0020447 | 0.0039948 | N
31/01/2017 | 15:10 | ZN15002:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 200 | 0.00013747 | 6.8876e-05 | N
31/01/2017 | 16:16 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 69 | 4.741e-05 | 6.8876e-05 | N
31/01/2017 | 17:05 | ZN1673:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 22 | 230 | 0.0034851 | 0.0015153 | N
31/01/2017 | 18:42 | 227:13020 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 33 | 203 | 0.030022 | 0.014793 | N
31/01/2017 | 21:45 | ZN36200:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 184 | 0.00082293 | 0.00044826 | N
01/02/2017 | 06:21 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 471 | 0.0090796 | 0.0019285 | N
31/01/2017 | 14:00 | ZN10994:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 25 | 20 | 0.00034438 | 0.0017219 | N
01/02/2017 | 08:25 | ZN847:PA46 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 109 | 7.5121e-05 | 6.8877e-05 | N
01/02/2017 | 09:06 | ZN3154:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 25 | 164 | 0.0028239 | 0.0017219 | N
01/02/2017 | 16:37 | 811:74234 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 11 | 32 | 0.0015828 | 0.0049309 | N
02/02/2017 | 08:20 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 370 | 0.0002546 | 6.8866e-05 | N
02/02/2017 | 10:30 | ZN874:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 212 | 0.00014595 | 6.8866e-05 | N
27/01/2017 | 11:50 | ZN9118:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 22 | 50 | 0.00075762 | 0.0015152 | N
02/02/2017 | 10:49 | ZN262:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 61 | 56 | 0.0023518 | 0.0042008 | N
02/02/2017 | 13:36 | ZN12570:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 484 | 0.00033335 | 6.8866e-05 | N
02/02/2017 | 15:42 | ZN1287:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 296 | 0.00020404 | 6.8866e-05 | N
02/02/2017 | 19:18 | ZN965:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 77 | 62 | 0.0032868 | 0.0053027 | N
02/02/2017 | 19:45 | ZN15008:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 180 | 0.00012384 | 6.8866e-05 | N
03/02/2017 | 12:42 | 221:11899 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 47 | 0.00020849 | 0.0004482 | N
04/02/2017 | 08:50 | ZN15006:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 151 | 94 | 0.0097562 | 0.010399 | N
04/02/2017 | 15:10 | 810:74054 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 40 | 194 | 2.7618 | 1.4245 | N
04/02/2017 | 15:24 | 810:74054 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 185 | 232 | 15.2778 | 6.5883 | N
04/02/2017 | 18:18 | 508:82579 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 2,893 | 0.012965 | 0.0004482 | N
05/02/2017 | 13:30 | ZN15012:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 63 | 30 | 0.0013017 | 0.004339 | N
05/02/2017 | 08:30 | ZN3154:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 29 | 245 | 0.0048935 | 0.0019973 | N
05/02/2017 | 17:02 | ZN15002:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 377 | 0.00025932 | 6.8873e-05 | N
05/02/2017 | 17:08 | ZN14891:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 93 | 0.00041548 | 0.00044811 | N
05/02/2017 | 17:07 | ZN14143:PA17 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 490 | 61 | 0.13303 | 0.21958 | N
05/02/2017 | 20:31 | ZN195:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 267 | 0.00018389 | 6.8873e-05 | N
06/02/2017 | 09:34 | ZN12640:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 116 | 0.00051779 | 0.00044811 | N
06/02/2017 | 12:44 | ZN14891:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 525 | 0.0023543 | 0.00044811 | N
06/02/2017 | 12:47 | ZN35800:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 79 | 173 | 0.0093984 | 0.005441 | N
06/02/2017 | 13:18 | 504:48031 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 252 | 0.0011273 | 0.00044811 | N
06/02/2017 | 14:08 | ZN10995:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 351 | 0.00024206 | 6.8873e-05 | N
06/02/2017 | 14:14 | ZN10995:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 345 | 0.0066545 | 0.0019285 | N
06/02/2017 | 14:18 | ZN10995:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 342 | 0.0002354 | 6.8873e-05 | N
06/02/2017 | 15:34 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 226 | 0.080484 | 0.035613 | N
06/02/2017 | 19:08 | ZN1673:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 26 | 255 | 0.0045663 | 0.0017907 | N
06/02/2017 | 23:20 | ZN80:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 66 | 215 | 0.0097731 | 0.0045456 | N
06/02/2017 | 20:21 | ZN15012:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,014 | 0.00069808 | 6.8873e-05 | N
07/02/2017 | 01:21 | ZN965:PA42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 29 | 88 | 0.0017597 | 0.0019974 | N
07/02/2017 | 08:00 | ZN12660:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 285 | 0.0012762 | 0.00044812 | N
07/02/2017 | 09:00 | ZN188:PA45 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 239 | 0.0010726 | 0.00044812 | N
07/02/2017 | 11:55 | ZN15002:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 494 | 0.00034025 | 6.8875e-05 | N
07/02/2017 | 12:15 | ZN847:PA45 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 244 | 102 | 0.11099 | 0.10934 | N
07/02/2017 | 12:37 | ZN80:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,484 | 92 | 0.094034 | 0.10221 | N
07/02/2017 | 12:37 | ZN80:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 92 | 0.0024079 | 0.0026172 | N
07/02/2017 | 13:17 | ZN36200:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 8 | 218 | 0.0078151 | 0.0035849 | N
07/02/2017 | 14:36 | ZN2635:PA58 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 94 | 6.4524e-05 | 6.8875e-05 | N
07/02/2017 | 17:23 | 513:48059 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 42 | 245 | 0.046084 | 0.018821 | N
08/02/2017 | 05:09 | ZN12570:PA22 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,608 | 63 | 0.45396 | 0.72058 | N
08/02/2017 | 12:44 | ZN3154:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 61 | 4.1968e-05 | 6.8876e-05 | N
08/02/2017 | 12:53 | 232:33413 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 127 | 8.7208e-05 | 6.8876e-05 | N
08/02/2017 | 13:12 | ZN3922:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 73 | 5.0233e-05 | 6.8876e-05 | N
08/02/2017 | 14:14 | ZN3154:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 31 | 0.00069324 | 0.0022729 | N
09/02/2017 | 11:54 | ZN1673:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 185 | 0.0001275 | 6.8876e-05 | N
09/02/2017 | 20:09 | ZN195:PA30 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 201 | 0.00089884 | 0.00044748 | N
09/02/2017 | 22:35 | ZN4545:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 265 | 0.00018246 | 6.8876e-05 | N
10/02/2017 | 03:45 | ZN5868:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 42 | 10 | 0.00028931 | 0.0028931 | N
10/02/2017 | 10:52 | ZN1287:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 75 | 5.1513e-05 | 6.8883e-05 | N
10/02/2017 | 16:36 | ZN1673:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 279 | 0.00019192 | 6.8883e-05 | N
10/02/2017 | 18:39 | ZN12620:PA10 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 1 | 127 | 0.00056755 | 0.00044747 | N
10/02/2017 | 19:38 | 504:48033 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 45 | 82 | 0.016512 | 0.020136 | N
10/02/2017 | 20:57 | 504:48031 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 42 | 214 | 0.040268 | 0.018794 | N
10/02/2017 | 21:01 | ZN965:PA33 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 34 | 318 | 0.007455 | 0.002342 | N
10/02/2017 | 21:41 | ZN12570:PA40 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 28 | 659 | 0.082568 | 0.012529 | N
11/02/2017 | 07:55 | ZN847:PA46 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 645 | 0.0004441 | 6.8883e-05 | N
11/02/2017 | 18:24 | ZN187:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 335 | 0.00023045 | 6.8883e-05 | N
11/02/2017 | 20:46 | ZN116:PA74 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 19 | 299 | 0.0039132 | 0.0013088 | N
11/02/2017 | 20:36 | ZN10995:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 60 | 94 | 0.0038813 | 0.004133 | N
11/02/2017 | 22:11 | ZN965:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 234 | 0.00016139 | 6.8883e-05 | N
11/02/2017 | 23:08 | ZN10994:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 277 | 0.0076442 | 0.0027553 | N
12/02/2017 | 00:05 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 467 | 126 | 0.26365 | 0.20897 | N
12/02/2017 | 01:50 | ZN12570:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2,221 | 73 | 0.11168 | 0.15299 | N
12/02/2017 | 03:03 | 264:81232 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 127 | 177 | 0.015483 | 0.0087481 | N
12/02/2017 | 07:16 | ZN2602:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 88 | 49 | 0.0029702 | 0.0060617 | N
12/02/2017 | 09:55 | ZN14892:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,324 | 0.00091234 | 6.8883e-05 | N
12/02/2017 | 11:55 | 504:48033 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 236 | 0.001058 | 0.00044747 | N
12/02/2017 | 13:25 | 515:35197 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 98 | 393 | 13.7037 | 3.49 | N
12/02/2017 | 15:10 | ZN4545:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 85 | 5.8619e-05 | 6.8883e-05 | N
12/02/2017 | 17:14 | ZN847:PA45 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 244 | 156 | 0.17055 | 0.10918 | N
12/02/2017 | 17:32 | 210:8682 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 117 | 8.0915e-05 | 6.8883e-05 | N
12/02/2017 | 17:42 | ZN35500:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 60 | 141 | 0.0058275 | 0.004133 | N
12/02/2017 | 20:53 | ZN965:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 60 | 4.1353e-05 | 6.8883e-05 | N
13/02/2017 | 00:02 | ZN9252:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 175 | 0.00012087 | 6.8883e-05 | N
13/02/2017 | 09:19 | ZN4545:PA39 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 6 | 78 | 0.00032237 | 0.0004133 | N
13/02/2017 | 07:14 | ZN4545:PA39 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 211 | 0.00014514 | 6.8883e-05 | N
13/02/2017 | 09:35 | ZN690:PA34 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 45 | 3.0917e-05 | 6.8883e-05 | N
13/02/2017 | 15:38 | ZN14891:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 77 | 115 | 0.039543 | 0.034455 | N
13/02/2017 | 11:52 | 225:33670 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 87 | 5.9767e-05 | 6.8883e-05 | N
13/02/2017 | 12:06 | 203:8086 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 62 | 4.2811e-05 | 6.8883e-05 | N
13/02/2017 | 22:36 | ZN3154:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 24 | 0.00069705 | 0.002962 | N
13/02/2017 | 17:48 | ZN129:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 107 | 7.3934e-05 | 6.8883e-05 | N
14/02/2017 | 08:29 | ZN965:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 32 | 91 | 0.0020081 | 0.0022067 | N
14/02/2017 | 10:34 | ZN10994:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 235 | 0.00016184 | 6.896e-05 | N
14/02/2017 | 11:00 | ZN10991:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 106 | 7.296e-05 | 6.896e-05 | N
14/02/2017 | 11:06 | ZN690:PA33 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 161 | 0.00011121 | 6.896e-05 | N
14/02/2017 | 11:36 | ZN1673:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 174 | 0.00011965 | 6.896e-05 | N
14/02/2017 | 13:58 | ZN14144:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,022 | 38 | 0.17333 | 0.45612 | N
15/02/2017 | 15:46 | ZN14892:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 21 | 1.4332e-05 | 6.8905e-05 | N
15/02/2017 | 19:10 | 220:8689 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 84 | 5.8133e-05 | 6.8905e-05 | N
16/02/2017 | 10:56 | ZN4545:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 12 | 19 | 0.00015541 | 0.00082666 | N
17/02/2017 | 06:55 | ZN14892:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 124 | 8.5447e-05 | 6.889e-05 | Y
17/02/2017 | 07:13 | 256:80638 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 111 | 7.6778e-05 | 6.889e-05 | Y
16/02/2017 | 13:36 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 839 | 3 | 0.0017339 | 0.057797 | N
17/02/2017 | 15:20 | ZN12610:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 78 | 5.3769e-05 | 6.889e-05 | Y
17/02/2017 | 15:35 | ZN35370:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 371 | 66 | 0.10935 | 0.16569 | Y
17/02/2017 | 16:51 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 51 | 383 | 0.013459 | 0.0035134 | Y
17/02/2017 | 16:20 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 74 | 430 | 0.021921 | 0.0050979 | Y
17/02/2017 | 15:56 | ZN15014:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 325 | 277 | 0.40205 | 0.14514 | Y
17/02/2017 | 16:01 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 268 | 0.00018483 | 6.889e-05 | Y
17/02/2017 | 16:02 | ZN3922:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 72 | 168 | 0.0083329 | 0.0049601 | Y
17/02/2017 | 16:05 | ZN3922:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 37 | 575 | 0.014656 | 0.0025489 | Y
17/02/2017 | 18:18 | ZN3922:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 52 | 181 | 0.0064923 | 0.0035823 | Y
17/02/2017 | 16:05 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 114 | 7.8845e-05 | 6.889e-05 | Y
17/02/2017 | 16:33 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 82 | 1,361 | 0.076885 | 0.005649 | Y
17/02/2017 | 16:20 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 54 | 430 | 0.015982 | 0.0037201 | Y
17/02/2017 | 20:15 | ZN3922:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 80 | 140 | 0.0077157 | 0.0055112 | Y
17/02/2017 | 16:14 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 76 | 5.2012e-05 | 6.889e-05 | Y
17/02/2017 | 16:05 | ZN3922:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 74 | 625 | 0.031862 | 0.0050979 | Y
17/02/2017 | 16:18 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 431 | 0.00029713 | 6.889e-05 | Y
17/02/2017 | 16:28 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 61 | 546 | 0.022928 | 0.0042023 | Y
17/02/2017 | 17:58 | ZN15010:PA9 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 64 | 1,757 | 0.50219 | 0.028582 | Y
17/02/2017 | 16:18 | ZN14143:PA17 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 538 | 1,441 | 3.4623 | 0.24027 | Y
17/02/2017 | 16:34 | ZN116:PA87 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 116 | 7.9614e-05 | 6.889e-05 | Y
17/02/2017 | 17:44 | ZN15010:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 113 | 1,351 | 0.10517 | 0.0077846 | Y
17/02/2017 | 16:36 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 114 | 7.8489e-05 | 6.889e-05 | Y
17/02/2017 | 18:04 | ZN15010:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 95 | 2,816 | 0.18429 | 0.0065446 | Y
17/02/2017 | 16:37 | ZN15004:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 4,066 | 0.0028011 | 6.889e-05 | Y
17/02/2017 | 16:39 | ZN15010:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,403 | 0.00096622 | 6.889e-05 | Y
18/02/2017 | 01:00 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 1,470 | 0.028355 | 0.0019289 | N
17/02/2017 | 16:49 | ZN15010:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 88 | 326 | 0.019736 | 0.0060623 | Y
17/02/2017 | 16:45 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,325 | 0.0059177 | 0.0004466 | Y
17/02/2017 | 16:46 | ZN12690:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 966 | 684 | 0.45523 | 0.066548 | Y
17/02/2017 | 16:50 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 276 | 0.00019035 | 6.889e-05 | Y
17/02/2017 | 16:53 | ZN3922:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 337 | 0.00023206 | 6.889e-05 | Y
17/02/2017 | 16:54 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 215 | 0.00014844 | 6.889e-05 | Y
17/02/2017 | 16:55 | ZN12690:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2 | 2,765 | 0.0038095 | 0.00013778 | Y
17/02/2017 | 16:57 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 7,467 | 0.03335 | 0.0004466 | Y
17/02/2017 | 16:49 | 515:35192 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 179 | 288 | 0.23053 | 0.079941 | Y
17/02/2017 | 16:59 | ZN12610:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,050 | 0.0007236 | 6.889e-05 | Y
17/02/2017 | 18:00 | ZN15010:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 87 | 2,480 | 0.14862 | 0.0059934 | Y
19/02/2017 | 18:18 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 355 | 1,647 | 2.6113 | 0.15855 | N
17/02/2017 | 17:03 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 478 | 0.00032925 | 6.889e-05 | Y
17/02/2017 | 17:04 | ZN15013:PA6 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 226 | 390 | 0.39363 | 0.10093 | Y
17/02/2017 | 16:55 | 516:48067 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 209 | 295 | 0.27505 | 0.093339 | Y
17/02/2017 | 17:09 | ZN12690:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,311 | 0.00090286 | 6.889e-05 | Y
17/02/2017 | 17:14 | ZN12690:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 826 | 0.00056899 | 6.889e-05 | Y
17/02/2017 | 17:17 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,422 | 0.0063508 | 0.0004466 | Y
17/02/2017 | 17:21 | ZN12610:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 625 | 0.00043088 | 6.889e-05 | Y
17/02/2017 | 17:23 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 5,616 | 0.0038691 | 6.889e-05 | Y
17/02/2017 | 17:23 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 2,676 | 0.011951 | 0.0004466 | Y
17/02/2017 | 17:46 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 144 | 1,830 | 0.18149 | 0.0099202 | Y
17/02/2017 | 17:25 | ZN12610:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,115 | 0.000768 | 6.889e-05 | Y
17/02/2017 | 17:26 | ZN12610:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,114 | 0.00076723 | 6.889e-05 | Y
17/02/2017 | 17:31 | 524:33576 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 253 | 0.0011304 | 0.0004466 | Y
17/02/2017 | 17:35 | 243:80075 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 165 | 0.00073584 | 0.0004466 | Y
17/02/2017 | 17:36 | ZN15010:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 929 | 0.00063995 | 6.889e-05 | Y
17/02/2017 | 17:58 | 513:48052 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 781 | 0.00053776 | 6.889e-05 | Y
17/02/2017 | 17:54 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 486 | 0.00033481 | 6.889e-05 | Y
17/02/2017 | 17:56 | 508:82578 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 381 | 0.0017003 | 0.0004466 | Y
17/02/2017 | 16:11 | ZN3922:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 73 | 454 | 0.022809 | 0.005029 | Y
17/02/2017 | 17:59 | 230:81432 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 879 | 697 | 2.7369 | 0.39256 | Y
17/02/2017 | 18:06 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 2,529 | 0.011294 | 0.0004466 | Y
17/02/2017 | 21:11 | ZN12640:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 107 | 2,629 | 1.2563 | 0.047786 | Y
17/02/2017 | 16:54 | 516:48065 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 34 | 348 | 0.052841 | 0.015184 | Y
17/02/2017 | 18:13 | 233:82819 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,727 | 0.0077127 | 0.0004466 | Y
17/02/2017 | 19:55 | 504:48028 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 229 | 0.0001578 | 6.889e-05 | Y
17/02/2017 | 18:16 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 74 | 5.0738e-05 | 6.889e-05 | Y
17/02/2017 | 18:16 | 515:35197 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,513 | 0.53886 | 0.035613 | Y
17/02/2017 | 18:21 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 68 | 4.7121e-05 | 6.889e-05 | Y
17/02/2017 | 18:38 | ZN12610:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 26 | 210 | 0.0037614 | 0.0017911 | Y
17/02/2017 | 23:15 | ZN15014:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 101 | 1,688 | 0.76119 | 0.045106 | Y
17/02/2017 | 19:24 | 264:81244 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 288 | 0.0012874 | 0.0004466 | Y
17/02/2017 | 19:49 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 47 | 1,281 | 0.041477 | 0.0032378 | Y
17/02/2017 | 19:55 | ZN36200:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 8 | 885 | 0.0048774 | 0.00055112 | Y
17/02/2017 | 19:56 | ZN116:PA87 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,278 | 0.00088059 | 6.889e-05 | Y
17/02/2017 | 16:22 | ZN12630:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 566 | 1,693 | 4.2794 | 0.25277 | Y
17/02/2017 | 20:07 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 2,338 | 0.0016108 | 6.889e-05 | Y
17/02/2017 | 16:09 | ZN3922:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 57 | 565 | 0.022193 | 0.0039267 | Y
17/02/2017 | 17:51 | ZN3922:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 72 | 293 | 0.014555 | 0.0049601 | Y
17/02/2017 | 20:45 | ZN116:PA76 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 14 | 9.9431e-06 | 6.889e-05 | Y
17/02/2017 | 21:02 | ZN3922:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 252 | 0.00017369 | 6.889e-05 | Y
17/02/2017 | 16:29 | ZN3922:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 116 | 206 | 0.016462 | 0.0079912 | Y
17/02/2017 | 16:21 | ZN3922:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 25 | 539 | 0.0092829 | 0.0017223 | Y
17/02/2017 | 16:21 | ZN3922:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 117 | 319 | 0.025689 | 0.0080601 | Y
17/02/2017 | 21:30 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 300 | 0.00020658 | 6.889e-05 | Y
17/02/2017 | 22:38 | ZN15013:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 696 | 0.00047934 | 6.889e-05 | Y
17/02/2017 | 18:11 | ZN3922:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 418 | 0.013811 | 0.0033067 | Y
18/02/2017 | 00:47 | ZN12690:PA3 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,933 | 0.0086319 | 0.00044661 | N
18/02/2017 | 08:54 | ZN12600:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,656 | 0.0011408 | 6.889e-05 | N
18/02/2017 | 07:02 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,467 | 0.0065535 | 0.00044661 | N
18/02/2017 | 07:59 | ZN12610:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 26 | 1,811 | 0.032438 | 0.0017911 | N
18/02/2017 | 09:26 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 4,337 | 0.0029877 | 6.889e-05 | N
18/02/2017 | 09:41 | ZN3922:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 319 | 0.00021961 | 6.889e-05 | N
18/02/2017 | 11:11 | ZN15004:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,341 | 0.00092396 | 6.889e-05 | N
18/02/2017 | 12:10 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,610 | 0.0071901 | 0.00044661 | N
18/02/2017 | 12:50 | ZN15010:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,576 | 0.0010855 | 6.889e-05 | N
18/02/2017 | 12:55 | ZN116:PA74 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 137 | 115 | 0.010836 | 0.0094379 | N
18/02/2017 | 13:21 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,306 | 0.00089951 | 6.889e-05 | N
18/02/2017 | 13:39 | ZN15010:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,582 | 0.0010896 | 6.889e-05 | N
18/02/2017 | 12:26 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,384 | 0.00095333 | 6.889e-05 | N
18/02/2017 | 16:55 | ZN3922:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 64 | 4.4262e-05 | 6.889e-05 | N
18/02/2017 | 17:31 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 625 | 0.0004304 | 6.889e-05 | N
18/02/2017 | 17:52 | ZN847:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,207 | 0.0008316 | 6.889e-05 | N
18/02/2017 | 18:14 | 233:82812 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 247 | 45 | 0.04964 | 0.11031 | N
18/02/2017 | 18:46 | 232:11454 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,855 | 106 | 0.8745 | 0.82845 | N
18/02/2017 | 19:22 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 727 | 0.0032479 | 0.00044661 | N
18/02/2017 | 20:07 | ZN12570:PA40 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 262 | 0.0011711 | 0.00044661 | N
18/02/2017 | 20:09 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 965 | 0.0043105 | 0.00044661 | N
18/02/2017 | 20:47 | 515:35193 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 734 | 0.0032771 | 0.00044661 | N
18/02/2017 | 22:12 | 239:82129 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 18 | 168 | 0.013505 | 0.0080389 | N
19/02/2017 | 07:35 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,579 | 0.001088 | 6.889e-05 | N
19/02/2017 | 09:16 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 931 | 0.0041572 | 0.00044661 | N
19/02/2017 | 13:05 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,424 | 0.00098122 | 6.889e-05 | N
19/02/2017 | 14:42 | ZN12690:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 152 | 0.00010485 | 6.889e-05 | N
19/02/2017 | 17:51 | ZN15004:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 455 | 0.00031315 | 6.889e-05 | N
19/02/2017 | 18:01 | ZN1193:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 209 | 0.00014382 | 6.889e-05 | N
20/02/2017 | 09:51 | ZN15014:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 345 | 99 | 0.023529 | 0.023767 | N
20/02/2017 | 09:52 | ZN12690:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 278 | 0.00019124 | 6.889e-05 | N
20/02/2017 | 10:20 | ZN12690:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 91 | 6.2724e-05 | 6.889e-05 | N
20/02/2017 | 12:05 | ZN3154:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 125 | 0.0041334 | 0.0033067 | N
20/02/2017 | 14:53 | ZN15010:PA5 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 1,147 | 0.00078989 | 6.889e-05 | N
20/02/2017 | 17:21 | ZN3672:PA46 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 79 | 5.4653e-05 | 6.889e-05 | N
20/02/2017 | 18:12 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 228 | 0.00015693 | 6.889e-05 | N
21/02/2017 | 09:41 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,458 | 0.0065128 | 0.00044663 | N
21/02/2017 | 16:20 | ZN15010:PA9 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 48 | 65 | 0.013935 | 0.021438 | N
21/02/2017 | 17:27 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 333 | 0.0014874 | 0.00044663 | N
21/02/2017 | 18:00 | ZN9700:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 120 | 8.2509e-05 | 6.8892e-05 | N
22/02/2017 | 10:27 | ZN15006:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 39 | 32 | 0.00086068 | 0.0026868 | N
22/02/2017 | 15:08 | ZN13000:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 693 | 81 | 0.038672 | 0.047743 | N
22/02/2017 | 15:31 | ZN36300:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 129 | 0.0042515 | 0.0033068 | N
22/02/2017 | 16:14 | ZN80:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 294 | 0.0002025 | 6.8893e-05 | N
22/02/2017 | 17:29 | ZN12630:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 318 | 145 | 0.20584 | 0.14203 | N
22/02/2017 | 17:54 | ZN12600:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,742 | 124 | 0.14871 | 0.12001 | N
22/02/2017 | 20:31 | ZN12640:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 2,039 | 90 | 0.81544 | 0.91069 | N
23/02/2017 | 06:39 | ZN4545:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 190 | 0.00432 | 0.0022731 | N
23/02/2017 | 12:55 | ZN15009:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,273 | 0.00087675 | 6.8883e-05 | N
23/02/2017 | 17:14 | 242:81539 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 183 | 0.00012637 | 6.8883e-05 | N
23/02/2017 | 20:05 | ZN80:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 272 | 4 | 0.00074945 | 0.018736 | N
24/02/2017 | 10:39 | ZN13000:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 251 | 0.0011207 | 0.00044648 | N
25/02/2017 | 03:46 | ZN9118:PA3 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 217 | 114 | 0.11048 | 0.096916 | N
25/02/2017 | 04:25 | ZN80:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 781 | 56 | 0.030125 | 0.053794 | N
25/02/2017 | 11:45 | ZN36300:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 65 | 225 | 0.010074 | 0.0044771 | N
25/02/2017 | 11:48 | ZN15004:PA5 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 565 | 0.0003895 | 6.8879e-05 | N
26/02/2017 | 06:05 | ZN35800:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 406 | 158 | 0.044102 | 0.027965 | N
26/02/2017 | 06:05 | ZN35800:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 111 | 7.6455e-05 | 6.8879e-05 | N
26/02/2017 | 07:29 | ZN12690:PA16 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 27 | 65 | 0.0078381 | 0.012059 | N
26/02/2017 | 07:42 | ZN180:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 294 | 0.00020226 | 6.8879e-05 | N
26/02/2017 | 08:39 | ZN10999:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 480 | 0.00033063 | 6.8879e-05 | N
26/02/2017 | 12:13 | ZN2196:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 64 | 198 | 0.0087357 | 0.0044082 | N
27/02/2017 | 06:50 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 135 | 0.0044633 | 0.0033062 | N
27/02/2017 | 12:12 | ZN2635:PA52 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 86 | 163 | 0.0096554 | 0.0059236 | N
27/02/2017 | 10:20 | ZN180:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 27 | 70 | 0.0013018 | 0.0018597 | N
27/02/2017 | 10:37 | ZN398:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 562 | 0.00038714 | 6.8879e-05 | N
27/02/2017 | 15:16 | ZN10995:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,123 | 0.00077358 | 6.8879e-05 | N
27/02/2017 | 23:26 | ZN12580:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 21 | 919 | 0.086192 | 0.0093789 | N
28/02/2017 | 09:42 | ZN195:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 267 | 0.00018409 | 6.8879e-05 | N
28/02/2017 | 09:57 | ZN80:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 112 | 7.7478e-05 | 6.8879e-05 | N
28/02/2017 | 10:35 | ZN2400:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 58 | 357 | 0.092348 | 0.025904 | N
01/03/2017 | 07:23 | 265:81648 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 247 | 0.001103 | 0.00044662 | N
01/03/2017 | 10:55 | ZN2635:PA44 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 20 | 0.00045461 | 0.002273 | N
01/03/2017 | 08:30 | 508:82579 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 39 | 44 | 0.0076461 | 0.017418 | N
01/03/2017 | 13:18 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 212 | 0.00094669 | 0.00044662 | N
01/03/2017 | 18:25 | 508:82580 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 360 | 0.0016084 | 0.00044662 | N
02/03/2017 | 00:39 | ZN12650:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 66 | 0.0019548 | 0.0029619 | N
02/03/2017 | 01:14 | ZN35500:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 78 | 176 | 0.0094559 | 0.0053727 | N
02/03/2017 | 05:16 | ZN3154:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 399 | 0.0017821 | 0.00044663 | N
02/03/2017 | 09:59 | ZN1673:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 151 | 0.00010384 | 6.8881e-05 | N
02/03/2017 | 14:14 | ZN965:PA47 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 511 | 0.00035182 | 6.8881e-05 | N
02/03/2017 | 14:15 | ZN965:PA47 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 510 | 0.00035116 | 6.8881e-05 | N
03/03/2017 | 01:45 | ZN3154:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 19 | 35 | 0.00045794 | 0.0013084 | N
03/03/2017 | 01:36 | ZN3154:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 27 | 358 | 0.043193 | 0.01206 | N
03/03/2017 | 06:38 | 243:80075 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 4 | 252 | 0.0045022 | 0.0017866 | N
03/03/2017 | 11:52 | ZN15001:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 67 | 4.6196e-05 | 6.8863e-05 | N
03/03/2017 | 15:52 | ZN3155:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 44 | 253 | 0.0076658 | 0.00303 | N
04/03/2017 | 00:30 | ZN1673:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 32 | 50 | 0.001102 | 0.002204 | N
04/03/2017 | 02:47 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 973 | 0.004351 | 0.00044728 | N
04/03/2017 | 06:32 | ZN12600:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 886 | 270 | 0.16478 | 0.061024 | N
04/03/2017 | 08:25 | ZN2602:PA41 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 335 | 0.00023068 | 6.8876e-05 | N
04/03/2017 | 09:52 | ZN12610:PA20 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 458 | 0.0020484 | 0.00044728 | N
04/03/2017 | 12:06 | ZN36200:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,394 | 0.0062329 | 0.00044728 | N
04/03/2017 | 13:48 | ZN2602:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,632 | 0.0011238 | 6.8876e-05 | N
04/03/2017 | 14:09 | ZN1673:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 36 | 355 | 0.0088122 | 0.0024795 | N
04/03/2017 | 15:00 | ZN195:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 29 | 180 | 0.023348 | 0.012971 | N
04/03/2017 | 15:41 | ZN36200:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 51 | 446 | 0.10174 | 0.022811 | N
18/03/2017 | 11:25 | ZN35370:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 187 | 177 | 0.14749 | 0.083112 | N
04/03/2017 | 16:02 | ZN9118:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 277 | 0.00019107 | 6.8876e-05 | N
05/03/2017 | 16:50 | ZN12630:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 22 | 110 | 0.010824 | 0.0098398 | N
05/03/2017 | 10:33 | ZN2400:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 507 | 0.0022673 | 0.00044727 | N
06/03/2017 | 04:03 | ZN12570:PA37 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 642 | 0.0028711 | 0.00044727 | N
06/03/2017 | 11:32 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 56 | 200 | 0.050152 | 0.025047 | N
06/03/2017 | 12:29 | ZN12570:PA22 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,208 | 43 | 0.23411 | 0.5403 | N
06/03/2017 | 12:29 | ZN12570:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,056 | 38 | 0.027639 | 0.072734 | N
06/03/2017 | 16:41 | ZN12640:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 199 | 0.00013704 | 6.8877e-05 | N
06/03/2017 | 16:47 | ZN12570:PA24 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 60 | 0.00026784 | 0.00044727 | N
06/03/2017 | 17:50 | 261:81876 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 15 | 100 | 0.0010332 | 0.0010332 | N
06/03/2017 | 17:58 | 229:34995 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 1 | 202 | 0.00090407 | 0.00044727 | N
06/03/2017 | 17:02 | 206:34440 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 15 | 198 | 0.0020456 | 0.0010332 | N
06/03/2017 | 18:46 | ZN129:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 66 | 63 | 0.0028609 | 0.0045459 | N
06/03/2017 | 21:33 | ZN15004:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 31 | 126 | 0.0026974 | 0.0021352 | N
07/03/2017 | 02:24 | ZN2400:PA11 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 58 | 360 | 0.093082 | 0.025877 | N
07/03/2017 | 08:26 | 230:81432 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 663 | 116 | 0.34353 | 0.2958 | N
07/03/2017 | 10:27 | ZN9700:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 161 | 0.00011055 | 6.8879e-05 | N
07/03/2017 | 10:52 | ZN9118:PA3 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 102 | 0.0004559 | 0.00044616 | N
07/03/2017 | 11:31 | 214:8665 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 70 | 4.8008e-05 | 6.8879e-05 | N
07/03/2017 | 11:49 | 261:81882 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 310 | 0.00021381 | 6.8879e-05 | N
07/03/2017 | 17:08 | ZN3922:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 72 | 157 | 0.007786 | 0.0049593 | N
07/03/2017 | 17:19 | ZN13000:PA2 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 1 | 130 | 0.00058157 | 0.00044616 | N
07/03/2017 | 23:17 | 202:34254 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 96 | 6.6169e-05 | 6.8879e-05 | N
07/03/2017 | 20:52 | ZN3922:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 9 | 299 | 0.0018535 | 0.00061991 | N
08/03/2017 | 14:24 | 243:80081 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 201 | 0.00089561 | 0.00044617 | N
09/03/2017 | 10:47 | ZN12640:PA10 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 202 | 0.00013945 | 6.8889e-05 | N
09/03/2017 | 11:13 | ZN9700:PA17 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 337 | 0.000232 | 6.8889e-05 | N
09/03/2017 | 13:11 | ZN3154:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 56 | 3.8635e-05 | 6.8889e-05 | N
09/03/2017 | 18:05 | ZN9252:PA27 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 220 | 0.00015146 | 6.8889e-05 | N
10/03/2017 | 10:51 | ZN80:PA31 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 181 | 0.00012466 | 6.8891e-05 | N
10/03/2017 | 15:09 | ZN9245:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 20 | 141 | 0.0019427 | 0.0013778 | N
11/03/2017 | 05:36 | ZN8000:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 43 | 234 | 0.0069318 | 0.0029623 | N
12/03/2017 | 16:04 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 655 | 45 | 0.13222 | 0.29124 | N
12/03/2017 | 16:37 | ZN10996:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 322 | 0.00022211 | 6.8892e-05 | N
12/03/2017 | 18:02 | ZN9700:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 325 | 0.0002236 | 6.8892e-05 | N
12/03/2017 | 18:32 | ZN10996:PA9 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 208 | 0.00014305 | 6.8892e-05 | N
13/03/2017 | 09:24 | ZN15013:PA6 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 17 | 216 | 0.016327 | 0.0075589 | N
13/03/2017 | 15:24 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 46 | 162 | 0.033135 | 0.020454 | N
13/03/2017 | 17:24 | ZN15004:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 303 | 0.00020872 | 6.8892e-05 | N
14/03/2017 | 06:20 | ZN1193:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 19 | 140 | 0.0018303 | 0.0013089 | N
14/03/2017 | 06:20 | ZN195:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 76 | 138 | 0.0072212 | 0.0052358 | N
14/03/2017 | 02:08 | ZN35370:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 279 | 86 | 0.10669 | 0.12406 | N
14/03/2017 | 02:37 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 97 | 768 | 0.051322 | 0.0066825 | N
14/03/2017 | 09:38 | ZN12610:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 202 | 0.00013912 | 6.8892e-05 | N
14/03/2017 | 09:57 | ZN2400:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 658 | 61 | 0.027754 | 0.045331 | N
14/03/2017 | 12:21 | ZN14144:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 670 | 26 | 0.077457 | 0.29791 | N
14/03/2017 | 20:40 | ZN965:PA43 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 254 | 0.00017486 | 6.8892e-05 | N
15/03/2017 | 03:01 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,089 | 93 | 0.069772 | 0.075024 | N
15/03/2017 | 04:40 | ZN965:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 353 | 0.0068019 | 0.001929 | N
15/03/2017 | 10:13 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 346 | 0.0015406 | 0.00044465 | N
15/03/2017 | 11:58 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 31 | 498 | 0.068634 | 0.013784 | N
15/03/2017 | 21:46 | ZN3154:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 198 | 0.00088196 | 0.00044465 | N
15/03/2017 | 22:37 | ZN2568:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 127 | 293 | 0.025636 | 0.0087493 | N
16/03/2017 | 04:57 | ZN12630:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 374 | 134 | 0.22202 | 0.16625 | N
16/03/2017 | 05:52 | ZN12630:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 530 | 258 | 0.6076 | 0.23559 | N
16/03/2017 | 08:25 | ZN14144:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 20 | 177 | 0.0024382 | 0.0013775 | N
16/03/2017 | 12:30 | ZN35370:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 187 | 59 | 0.049043 | 0.083124 | N
16/03/2017 | 16:36 | 513:48051 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 93 | 48 | 0.0030907 | 0.0064055 | N
16/03/2017 | 18:51 | 243:80075 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 66 | 0.00029367 | 0.00044451 | N
16/03/2017 | 19:57 | ZN12640:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 92 | 6.3126e-05 | 6.8877e-05 | N
16/03/2017 | 22:44 | ZN12640:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 32 | 136 | 0.019345 | 0.014224 | N
16/03/2017 | 22:54 | ZN15014:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 626 | 0.00043112 | 6.8877e-05 | N
17/03/2017 | 07:11 | ZN2400:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 109 | 0.0004826 | 0.00044445 | N
17/03/2017 | 08:02 | ZN9118:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 148 | 0.00010187 | 6.8877e-05 | N
17/03/2017 | 08:25 | ZN14144:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 27 | 165 | 0.0198 | 0.012 | N
17/03/2017 | 09:17 | ZN9118:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 39 | 72 | 0.0019444 | 0.0026862 | N
17/03/2017 | 11:32 | ZN15002:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 148 | 0.00010188 | 6.8877e-05 | N
17/03/2017 | 11:38 | ZN12610:PA20 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 223 | 39 | 0.038654 | 0.099112 | N
17/03/2017 | 12:10 | ZN12620:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 100 | 0.00044341 | 0.00044445 | N
17/03/2017 | 12:23 | ZN12650:PA1 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 1 | 276 | 0.0012274 | 0.00044445 | N
17/03/2017 | 12:25 | ZN35500:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 42 | 25 | 0.00072321 | 0.0028928 | N
17/03/2017 | 14:57 | ZN13000:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 78 | 107 | 0.037111 | 0.034667 | N
17/03/2017 | 15:48 | ZN10994:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 147 | 0.00010125 | 6.8877e-05 | N
17/03/2017 | 15:49 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 130 | 8.9667e-05 | 6.8877e-05 | N
18/03/2017 | 04:16 | ZN965:PA33 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 50 | 41 | 0.001412 | 0.0034439 | N
17/03/2017 | 16:36 | 202:34231 37 42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 261 | 0.00017991 | 6.8877e-05 | N
17/03/2017 | 18:14 | 202:34231 37 42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2 | 166 | 0.00022837 | 0.00013775 | N
17/03/2017 | 19:09 | 202:34231 37 42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 111 | 7.6419e-05 | 6.8877e-05 | N
17/03/2017 | 19:50 | ZN12630:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,535 | 0.0068223 | 0.00044445 | N
17/03/2017 | 20:37 | ZN15011:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,500 | 0.0010335 | 6.8877e-05 | N
17/03/2017 | 21:04 | ZN9700:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,021 | 0.0007029 | 6.8877e-05 | N
17/03/2017 | 22:07 | ZN12630:PA3 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 70 | 792 | 0.2463 | 0.031111 | N
17/03/2017 | 22:15 | ZN3155:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 405 | 0.00027887 | 6.8877e-05 | N
17/03/2017 | 22:16 | ZN3155:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 404 | 0.00027805 | 6.8877e-05 | N
17/03/2017 | 22:50 | ZN129:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,579 | 118 | 0.12887 | 0.10876 | N
18/03/2017 | 02:16 | ZN80:PA25 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 62 | 49 | 0.0020925 | 0.0042705 | N
18/03/2017 | 00:10 | ZN9700:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,100 | 0.00075742 | 6.8878e-05 | N
18/03/2017 | 00:29 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 49 | 875 | 0.029541 | 0.003375 | N
18/03/2017 | 00:53 | ZN262:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 999 | 0.0006883 | 6.8878e-05 | N
18/03/2017 | 07:30 | ZN1193:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 40 | 122 | 0.0033613 | 0.0027551 | N
18/03/2017 | 00:51 | ZN3425:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 1,004 | 0.019363 | 0.0019286 | N
18/03/2017 | 01:19 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,610 | 184 | 1.3152 | 0.71557 | N
18/03/2017 | 09:41 | ZN9700:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 55 | 263 | 0.0099626 | 0.0037883 | N
18/03/2017 | 01:36 | ZN9035:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 649 | 0.00044681 | 6.8878e-05 | N
18/03/2017 | 02:42 | ZN9700:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 684 | 0.00047107 | 6.8878e-05 | N
18/03/2017 | 04:03 | ZN15010:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 53 | 920 | 0.033576 | 0.0036506 | N
18/03/2017 | 05:40 | ZN9245:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 500 | 0.0022236 | 0.00044445 | N
18/03/2017 | 07:44 | ZN2400:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 2,296 | 0.0015814 | 6.8878e-05 | N
18/03/2017 | 07:57 | ZN14144:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 6 | 268 | 0.0071414 | 0.0026667 | N
18/03/2017 | 08:17 | ZN15010:PA9 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 3,283 | 0.014591 | 0.00044445 | N
18/03/2017 | 08:37 | ZN690:PA34 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 548 | 0.00037774 | 6.8878e-05 | N
18/03/2017 | 09:34 | ZN10999:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 516 | 0.00035546 | 6.8878e-05 | N
18/03/2017 | 09:48 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 25 | 201 | 0.003464 | 0.001722 | N
18/03/2017 | 10:22 | ZN690:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 19 | 381 | 0.0049798 | 0.0013087 | N
18/03/2017 | 11:10 | 220:8689 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 242 | 0.00016674 | 6.8878e-05 | N
18/03/2017 | 14:03 | ZN10994:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 297 | 0.00020438 | 6.8878e-05 | N
18/03/2017 | 16:14 | ZN12620:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 405 | 0.0018011 | 0.00044445 | N
18/03/2017 | 02:56 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 934 | 0.00064331 | 6.8878e-05 | N
18/03/2017 | 20:54 | 811:74234 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 8 | 935 | 0.03325 | 0.0035556 | N
19/03/2017 | 00:12 | 225:13446 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 128 | 8.8084e-05 | 6.8879e-05 | N
19/03/2017 | 02:17 | ZN35800:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 907 | 123 | 0.076963 | 0.062473 | N
19/03/2017 | 05:54 | ZN3154:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 15 | 306 | 0.0031607 | 0.0010332 | N
19/03/2017 | 05:54 | ZN3154:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 30 | 546 | 0.011282 | 0.0020664 | N
19/03/2017 | 07:45 | 513:48059 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 144 | 0.00064023 | 0.00044445 | N
19/03/2017 | 07:56 | ZN12570:PA22 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 234 | 0.0010405 | 0.00044445 | N
19/03/2017 | 14:26 | 225:33670 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 32 | 63 | 0.0013959 | 0.0022041 | N
19/03/2017 | 13:00 | ZN35800:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 92 | 280 | 0.017743 | 0.0063368 | N
19/03/2017 | 16:53 | ZN80:PA40 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 27 | 116 | 0.0021576 | 0.0018597 | N
19/03/2017 | 12:22 | ZN35800:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 16 | 163 | 0.0017964 | 0.0011021 | N
20/03/2017 | 01:08 | ZN15008:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 55 | 26 | 0.00098812 | 0.0037883 | N
19/03/2017 | 16:03 | ZN2635:PA38 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 36 | 13 | 0.00033434 | 0.0024796 | N
19/03/2017 | 21:45 | ZN195:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 27 | 15 | 0.0018 | 0.012 | N
18/03/2017 | 19:40 | ZN1673:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 23 | 90 | 0.0014258 | 0.0015842 | N
20/03/2017 | 17:18 | ZN14144:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 34 | 76 | 0.0017896 | 0.0023419 | N
20/03/2017 | 20:35 | ZN965:PA42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 29 | 203 | 0.0040549 | 0.0019975 | N
18/03/2017 | 04:00 | ZN15010:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 30 | 190 | 0.0039261 | 0.0020663 | N
21/03/2017 | 08:47 | 230:81434 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 83 | 5.6894e-05 | 6.8879e-05 | N
21/03/2017 | 11:55 | 801:74121 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 253 | 113 | 10.2094 | 9.026 | N
21/03/2017 | 15:08 | ZN847:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 292 | 0.0012972 | 0.00044446 | N
21/03/2017 | 15:37 | ZN12630:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 81 | 517 | 0.18624 | 0.036001 | N
21/03/2017 | 18:56 | ZN2310:PA62 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 44 | 79 | 0.0023821 | 0.0030307 | N
21/03/2017 | 18:39 | ZN12650:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,071 | 0.00073743 | 6.8879e-05 | N
21/03/2017 | 18:57 | ZN12640:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 381 | 163 | 0.27638 | 0.16934 | N
21/03/2017 | 20:59 | ZN9245:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 271 | 0.0012025 | 0.00044446 | N
21/03/2017 | 21:06 | ZN9245:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 264 | 0.001173 | 0.00044446 | N
21/03/2017 | 21:25 | ZN10994:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 244 | 0.00016817 | 6.8879e-05 | N
21/03/2017 | 22:09 | ZN10994:PA13 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 201 | 0.00013834 | 6.8879e-05 | N
21/03/2017 | 22:37 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 129 | 8.9026e-05 | 6.8879e-05 | N
22/03/2017 | 00:29 | ZN35500:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 64 | 4.39e-05 | 6.8881e-05 | N
22/03/2017 | 15:31 | 242:81539 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 391 | 0.00026915 | 6.8881e-05 | N
22/03/2017 | 16:24 | ZN9252:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 318 | 0.00021919 | 6.8881e-05 | N
22/03/2017 | 18:43 | ZN2400:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 39 | 962 | 0.16668 | 0.017334 | N
22/03/2017 | 17:09 | ZN12660:PA6 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 491 | 240 | 0.52376 | 0.21823 | N
22/03/2017 | 17:12 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,764 | 246 | 0.29904 | 0.12151 | N
22/03/2017 | 17:23 | ZN12660:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,176 | 0.0052285 | 0.00044447 | N
22/03/2017 | 07:48 | ZN12660:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 28 | 937 | 0.018072 | 0.0019287 | N
22/03/2017 | 07:48 | ZN12660:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 57 | 937 | 0.036789 | 0.0039262 | N
22/03/2017 | 17:29 | ZN12640:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,101 | 0.00075854 | 6.8881e-05 | N
22/03/2017 | 17:31 | ZN847:PA44 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,109 | 0.00076389 | 6.8881e-05 | N
22/03/2017 | 17:31 | ZN12660:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,168 | 0.0051915 | 0.00044447 | N
22/03/2017 | 17:34 | ZN15014:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 68 | 661 | 0.030961 | 0.0046839 | N
22/03/2017 | 17:35 | ZN2400:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 369 | 0.0016417 | 0.00044447 | N
22/03/2017 | 17:37 | ZN12660:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,162 | 0.0051663 | 0.00044447 | N
22/03/2017 | 17:40 | ZN12580:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,340 | 0.00092281 | 6.8881e-05 | N
22/03/2017 | 17:40 | ZN14891:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 381 | 78 | 0.13285 | 0.16934 | N
22/03/2017 | 17:54 | ZN12580:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,236 | 0.00085114 | 6.8881e-05 | N
22/03/2017 | 17:57 | ZN12660:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,142 | 0.0050772 | 0.00044447 | N
22/03/2017 | 18:28 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 62 | 4.2603e-05 | 6.8881e-05 | N
22/03/2017 | 17:34 | ZN12660:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 986 | 0.0043821 | 0.00044447 | N
22/03/2017 | 18:56 | ZN12580:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 12 | 169 | 0.0013969 | 0.00082657 | N
22/03/2017 | 20:32 | ZN36200:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 848 | 0.00058383 | 6.8881e-05 | N
22/03/2017 | 19:40 | ZN2400:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 79 | 589 | 0.032076 | 0.0054416 | N
22/03/2017 | 19:52 | ZN12660:PA14 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,028 | 0.0045686 | 0.00044447 | N
22/03/2017 | 22:01 | ZN12640:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 629 | 0.00043297 | 6.8881e-05 | N
23/03/2017 | 00:53 | ZN195:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 39 | 87 | 0.0023252 | 0.0026855 | N
22/03/2017 | 21:33 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,764 | 67 | 0.081349 | 0.12151 | N
23/03/2017 | 07:28 | ZN35900:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 121 | 8.3341e-05 | 6.8858e-05 | N
20/03/2017 | 11:40 | ZN847:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 21 | 35 | 0.00050626 | 0.0014465 | N
20/03/2017 | 09:40 | ZN2400:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 29 | 45 | 0.0058001 | 0.012889 | N
23/03/2017 | 16:14 | ZN3154:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 331 | 0.00022791 | 6.8858e-05 | N
24/03/2017 | 07:58 | 232:11454 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 182 | 0.00080711 | 0.00044461 | N
24/03/2017 | 13:20 | ZN2568:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 179 | 0.00012328 | 6.8859e-05 | N
24/03/2017 | 14:11 | ZN2568:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 57 | 38 | 0.0015091 | 0.0039249 | N
24/03/2017 | 15:04 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 6 | 236 | 0.0062956 | 0.0026676 | N
24/03/2017 | 17:37 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 122 | 0.002777 | 0.0022723 | N
25/03/2017 | 00:17 | ZN3425:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 92 | 583 | 0.036929 | 0.0063347 | N
25/03/2017 | 12:14 | ZN12640:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 136 | 0.00060298 | 0.00044462 | N
25/03/2017 | 18:08 | ZN36200:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 52 | 3.5942e-05 | 6.8855e-05 | N
26/03/2017 | 11:27 | ZN15010:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 501 | 0.00034493 | 6.8857e-05 | N
26/03/2017 | 16:53 | ZN965:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 577 | 0.00039723 | 6.8857e-05 | N
27/03/2017 | 09:24 | ZN15012:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 4 | 199 | 0.00054879 | 0.00027543 | N
22/03/2017 | 22:42 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 54 | 728 | 0.027078 | 0.0037196 | N
22/03/2017 | 22:37 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 19 | 763 | 0.0099857 | 0.0013087 | N
22/03/2017 | 22:37 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 17 | 143 | 0.0016745 | 0.001171 | N
23/03/2017 | 23:35 | ZN12660:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 82 | 5 | 0.00028232 | 0.0056463 | N
27/03/2017 | 14:37 | ZN9118:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 425 | 0.00029233 | 6.8857e-05 | N
27/03/2017 | 18:30 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 11 | 95 | 0.37295 | 0.39258 | N
27/03/2017 | 20:12 | 264:81236 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 179 | 0.00079321 | 0.00044384 | N
28/03/2017 | 05:45 | ZN1673:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 31 | 149 | 0.0031852 | 0.0021346 | N
28/03/2017 | 08:57 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 393 | 0.0017424 | 0.00044384 | N
28/03/2017 | 11:16 | ZN2835:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 30 | 94 | 0.0019377 | 0.0020657 | N
30/03/2017 | 14:47 | ZN72:PA34 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 423 | 0.00029106 | 6.8836e-05 | N
30/03/2017 | 14:52 | ZN72:PA34 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 417 | 0.0002873 | 6.8836e-05 | N
30/03/2017 | 15:25 | ZN3425:PA44 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 406 | 0.00027915 | 6.8836e-05 | N
30/03/2017 | 16:19 | ZN3154:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 23 | 126 | 0.012854 | 0.010202 | N
30/03/2017 | 19:07 | ZN12570:PA33 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 6 | 98 | 0.0026064 | 0.0026614 | N
30/03/2017 | 19:13 | ZN12690:PA19 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 107 | 7.3494e-05 | 6.8836e-05 | N
30/03/2017 | 19:36 | ZN847:PA46 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 189 | 0.00012991 | 6.8836e-05 | N
30/03/2017 | 20:04 | 801:74123 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 166 | 132 | 0.097082 | 0.073631 | N
30/03/2017 | 20:39 | ZN3672:PA37 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 75 | 171 | 0.0088162 | 0.0051627 | N
30/03/2017 | 20:54 | 232:33407 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 260 | 0.0011524 | 0.00044356 | N
31/03/2017 | 00:02 | 504:48033 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 142 | 0.00062875 | 0.00044356 | N
31/03/2017 | 09:54 | 229:34995 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 126 | 0.00055807 | 0.00044356 | N
31/03/2017 | 11:18 | 532:83314 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 37 | 2.5379e-05 | 6.884e-05 | N
31/03/2017 | 11:43 | 243:80084 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 162 | 0.00071672 | 0.00044356 | N
31/03/2017 | 13:12 | ZN12660:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 79 | 471 | 0.025637 | 0.0054383 | N
31/03/2017 | 12:26 | ZN180:PA43 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 101 | 6.9689e-05 | 6.884e-05 | N
31/03/2017 | 17:18 | ZN15002:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 42 | 157 | 0.0045325 | 0.0028913 | N
31/03/2017 | 13:26 | 239:82129 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,429 | 55 | 0.34862 | 0.63385 | N
31/03/2017 | 14:14 | ZN9118:PA3 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 226 | 0.0010011 | 0.00044356 | N
31/03/2017 | 15:21 | ZN1673:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 339 | 0.00023313 | 6.884e-05 | N
02/04/2017 | 14:43 | ZN72:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 105 | 67 | 0.0048237 | 0.0072247 | N
02/04/2017 | 16:00 | ZN9118:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 240 | 0.00016509 | 6.8806e-05 | N
31/03/2017 | 13:30 | ZN12600:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 16 | 105 | 0.0074518 | 0.007097 | N
03/04/2017 | 16:32 | ZN1287:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 309 | 0.00021269 | 6.8806e-05 | N
03/04/2017 | 21:24 | ZN12580:PA14 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,023 | 108 | 0.07603 | 0.070389 | N
04/04/2017 | 04:13 | ZN1285:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 286 | 0.00019701 | 6.8807e-05 | N
04/04/2017 | 17:45 | ZN14144:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 31 | 110 | 0.015185 | 0.013805 | N
04/04/2017 | 12:20 | ZN2835:PA36 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 369 | 0.00025416 | 6.8807e-05 | N
04/04/2017 | 15:51 | 509:33399 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 278 | 0.00124 | 0.00044531 | N
05/04/2017 | 18:50 | ZN15014:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 99 | 84 | 0.0057435 | 0.0068119 | N
06/04/2017 | 09:22 | ZN2835:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 57 | 3.8956e-05 | 6.8807e-05 | N
04/04/2017 | 18:07 | ZN14144:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 13 | 55 | 0.003184 | 0.005789 | N
07/04/2017 | 09:02 | ZN12570:PA24 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 178 | 0.00079122 | 0.00044534 | N
08/04/2017 | 00:01 | ZN1193:PA28 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 54 | 209 | 0.0077626 | 0.0037141 | N
09/04/2017 | 11:35 | 264:81236 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 63 | 85 | 0.023848 | 0.028057 | N
09/04/2017 | 12:41 | ZN80:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 198 | 0.00013633 | 6.878e-05 | N
09/04/2017 | 17:04 | ZN847:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,292 | 0.00088829 | 6.878e-05 | N
09/04/2017 | 17:29 | ZN15005:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 1,015 | 0.00069813 | 6.878e-05 | N
09/04/2017 | 17:49 | ZN2196:PA3 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 947 | 68 | 0.28678 | 0.42174 | N
09/04/2017 | 18:18 | ZN35900:PA4 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 192 | 0.00085298 | 0.00044534 | N
09/04/2017 | 18:22 | ZN1287:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 556 | 0.0003822 | 6.878e-05 | N
09/04/2017 | 18:25 | ZN2835:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 62 | 505 | 0.021535 | 0.0042644 | N
09/04/2017 | 18:34 | ZN847:PA10 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 505 | 0.0003474 | 6.878e-05 | N
09/04/2017 | 18:41 | ZN9700:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 79 | 5.4279e-05 | 6.878e-05 | N
09/04/2017 | 19:09 | ZN12650:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 186 | 0.00012778 | 6.878e-05 | N
09/04/2017 | 19:24 | ZN12610:PA2 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1,039 | 53 | 0.038075 | 0.071463 | N
09/04/2017 | 21:40 | ZN14891:PA8 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 9 | 219 | 0.0087955 | 0.0040081 | N
09/04/2017 | 20:09 | ZN1673:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 57 | 244 | 0.0095652 | 0.0039205 | N
10/04/2017 | 11:03 | 532:83293 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 95 | 6.5593e-05 | 6.878e-05 | N
10/04/2017 | 11:59 | ZN3155:PA44 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 15 | 285 | 0.0029403 | 0.0010317 | N
10/04/2017 | 16:25 | ZN14891:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 12 | 15 | 0.00080162 | 0.0053441 | N
11/04/2017 | 09:18 | ZN847:PA26 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 11 | 32 | 0.00024211 | 0.00075658 | N
12/04/2017 | 06:42 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 51 | 88 | 0.0030871 | 0.0035081 | N
13/04/2017 | 10:27 | ZN14891:PA20 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 14 | 92 | 0.0057433 | 0.0062359 | N
13/04/2017 | 15:04 | ZN129:PA9 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 389 | 0.00026781 | 6.8788e-05 | N
14/04/2017 | 14:40 | ZN14144:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 435 | 0.0019366 | 0.00044527 | N
16/04/2017 | 07:01 | ZN12630:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 531 | 138 | 0.32705 | 0.23644 | N
17/04/2017 | 00:01 | ZN1193:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 751 | 0.00051618 | 6.8766e-05 | N
17/04/2017 | 11:53 | ZN195:PA29 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 35 | 14 | 0.00033695 | 0.0024068 | N
19/04/2017 | 16:19 | ZN15005:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 26 | 176 | 0.0031469 | 0.001788 | N
21/04/2017 | 17:25 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 278 | 0.099143 | 0.035702 | N
21/04/2017 | 18:44 | ZN14891:PA20 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 298 | 0.0013248 | 0.00044414 | N
22/04/2017 | 14:24 | ZN15010:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 504 | 0.0003468 | 6.8775e-05 | N
23/04/2017 | 02:55 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 48 | 650 | 0.021461 | 0.0033012 | N
23/04/2017 | 03:10 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 60 | 189 | 0.0078115 | 0.0041265 | N
23/04/2017 | 02:55 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 47 | 1,065 | 0.034426 | 0.0032325 | N
24/04/2017 | 08:52 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 46 | 167 | 2.7434 | 1.6423 | N
24/04/2017 | 12:29 | ZN129:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 72 | 4.9816e-05 | 6.8776e-05 | N
24/04/2017 | 13:22 | 228:7487 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 56 | 3.8468e-05 | 6.8776e-05 | N
26/04/2017 | 09:16 | 205:12206 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 64 | 4.373e-05 | 6.8776e-05 | N
26/04/2017 | 12:01 | ZN2602:PA9 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 659 | 0.0004532 | 6.8776e-05 | N
26/04/2017 | 14:30 | ZN35800:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 907 | 59 | 0.036804 | 0.06238 | N
26/04/2017 | 14:30 | ZN35800:PA3 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 2 | 59 | 8.1156e-05 | 0.00013755 | N
26/04/2017 | 14:42 | ZN12620:PA7 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 62 | 4.232e-05 | 6.8776e-05 | N
26/04/2017 | 14:47 | ZN12650:PA1 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 342 | 0.0015196 | 0.00044399 | N
26/04/2017 | 15:26 | ZN9252:PA22 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 75 | 1,044 | 0.053854 | 0.0051582 | N
26/04/2017 | 14:55 | ZN2466:PA45 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 89 | 115 | 0.0070393 | 0.0061211 | N
26/04/2017 | 15:37 | ZN35800:PA1 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 663 | 0.00045602 | 6.8776e-05 | N
26/04/2017 | 15:59 | 532:83301 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 210 | 0.00014425 | 6.8776e-05 | N
26/04/2017 | 16:22 | ZN15004:PA5 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 1,138 | 0.00078238 | 6.8776e-05 | N
26/04/2017 | 16:44 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 10 | 1,306 | 4.6618 | 0.35702 | N
26/04/2017 | 17:15 | ZN9037:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 77 | 334 | 0.017694 | 0.0052958 | N
27/04/2017 | 08:34 | 511:29878 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 127 | 0.0005617 | 0.00044391 | N
27/04/2017 | 09:36 | ZN15014:PA12 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 103 | 0.00045871 | 0.00044391 | N
29/04/2017 | 12:09 | 511:29877 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 258 | 0.0011466 | 0.00044389 | N
03/05/2017 | 04:40 | ZN9252:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 289 | 0.00019885 | 6.8767e-05 | N
03/05/2017 | 07:51 | ZN9252:PA27 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 99 | 6.7873e-05 | 6.8767e-05 | N
03/05/2017 | 12:17 | 206:34432 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 81 | 5.585e-05 | 6.8767e-05 | N
04/05/2017 | 10:34 | ZN398:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 119 | 8.1552e-05 | 6.8752e-05 | N
04/05/2017 | 17:11 | 230:81440 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 68 | 0.00030261 | 0.00044382 | N
06/05/2017 | 20:36 | ZN2400:PA18 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 11 | 954 | 0.046574 | 0.004882 | N
07/05/2017 | 16:10 | 508:82579 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 112 | 0.00049586 | 0.00044458 | N
08/05/2017 | 12:23 | ZN12610:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 66 | 4.5453e-05 | 6.8747e-05 | N
09/05/2017 | 14:31 | ZN3154:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 119 | 8.1834e-05 | 6.8749e-05 | N
10/05/2017 | 10:20 | ZN15014:PA22 | URBAN | Vegetation | Grow-in - NSP responsibility | 1 | 300 | 0.00020604 | 6.875e-05 | N
19/05/2017 | 04:08 | ZN15005:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 157 | 0.0041 | 0.0026115 | N
19/05/2017 | 12:53 | ZN2602:PA20 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 46 | 212 | 0.0067018 | 0.0031612 | N
19/05/2017 | 17:29 | 227:13015 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,901 | 115 | 0.98038 | 0.8509 | N
20/05/2017 | 08:30 | ZN4545:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 210 | 0.00014416 | 6.8723e-05 | N
21/05/2017 | 07:22 | ZN180:PA42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 52 | 182 | 0.0065075 | 0.0035736 | N
21/05/2017 | 12:35 | ZN12600:PA9 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,124 | 158 | 0.7951 | 0.50311 | N
21/05/2017 | 09:45 | ZN180:PA42 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 8 | 40 | 0.00021991 | 0.00054978 | N
23/05/2017 | 10:14 | ZN12600:PA12 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 85 | 5.8517e-05 | 6.8723e-05 | N
24/05/2017 | 09:03 | ZN15004:PA5 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 72 | 4.9366e-05 | 6.8723e-05 | N
24/05/2017 | 16:45 | ZN2196:PA17 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 116 | 7.9684e-05 | 6.8723e-05 | N
25/05/2017 | 01:24 | ZN10994:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 434 | 0.00029802 | 6.8723e-05 | N
26/05/2017 | 09:43 | ZN1673:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 186 | 0.0048647 | 0.0026115 | Y
28/05/2017 | 20:23 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 655 | 57 | 0.16711 | 0.29318 | N
30/05/2017 | 07:20 | ZN1287:PA15 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 250 | 0.00017153 | 6.8722e-05 | N
31/05/2017 | 10:11 | ZN12570:PA22 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 681 | 40 | 0.12193 | 0.30482 | N
31/05/2017 | 10:44 | ZN12600:PA9 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1,503 | 41 | 0.27583 | 0.67275 | N
02/06/2017 | 12:48 | ZN80:PA32 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 66 | 4.5448e-05 | 6.8722e-05 | N
02/06/2017 | 14:43 | ZN35500:PA24 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 376 | 0.00025843 | 6.8722e-05 | N
06/06/2017 | 18:33 | ZN15005:PA8 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 257 | 0.00017647 | 6.8722e-05 | N
07/06/2017 | 06:25 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 70 | 58 | 0.018173 | 0.031332 | N
07/06/2017 | 07:40 | ZN15010:PA9 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 379 | 0.0016985 | 0.0004476 | N
07/06/2017 | 09:24 | ZN12600:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 857 | 89 | 0.34041 | 0.3836 | N
07/06/2017 | 18:45 | ZN12650:PA13 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 935 | 69 | 0.29058 | 0.41851 | N
08/06/2017 | 14:13 | ZN3922:PA13 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 1 | 286 | 0.0012808 | 0.0004476 | N
09/06/2017 | 13:12 | ZN14144:PA10 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 258 | 0.001153 | 0.0004476 | N
09/06/2017 | 18:40 | ZN8000:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 320 | 0.00021984 | 6.8722e-05 | N
09/06/2017 | 19:16 | ZN180:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 149 | 0.00010238 | 6.8722e-05 | N
09/06/2017 | 23:26 | ZN15013:PA4 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 123 | 68 | 0.0057479 | 0.0084528 | N
09/06/2017 | 23:29 | ZN847:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 33 | 152 | 0.0034553 | 0.0022678 | N
10/06/2017 | 01:40 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 319 | 0.00021928 | 6.8722e-05 | N
11/06/2017 | 03:47 | ZN12580:PA1 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 342 | 0.00023507 | 6.8722e-05 | N
11/06/2017 | 20:15 | ZN195:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 32 | 89 | 0.001966 | 0.0021991 | N
11/06/2017 | 19:11 | ZN1673:PA18 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 46 | 279 | 0.0088197 | 0.0031612 | N
11/06/2017 | 22:51 | ZN965:PA35 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 137 | 300 | 0.028219 | 0.0094149 | N
13/06/2017 | 13:03 | ZN12570:PA21 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 44 | 3.0238e-05 | 6.8722e-05 | N
13/06/2017 | 13:03 | ZN12580:PA16 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 996 | 36 | 0.024641 | 0.068447 | N
15/06/2017 | 05:59 | ZN14891:PA5 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 9 | 533 | 0.021458 | 0.0040284 | N
16/06/2017 | 09:05 | 220:8688 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 37 | 2.5083e-05 | 6.8722e-05 | N
16/06/2017 | 14:10 | 258:80781 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 53 | 3.6182e-05 | 6.8722e-05 | N
17/06/2017 | 13:22 | ZN12570:PA33 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 57 | 0.00025551 | 0.0004476 | N
17/06/2017 | 17:12 | ZN9700:PA23 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 198 | 0.00013599 | 6.8722e-05 | N
18/06/2017 | 13:12 | ZN80:PA30 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 80 | 218 | 0.011969 | 0.0054977 | N
20/06/2017 | 10:49 | 532:83309 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 66 | 0.00029512 | 0.0004476 | N
21/06/2017 | 03:23 | 509:33395 | LONG RURAL | Vegetation | Blow/Fall In - NSP responsibility | 45 | 365 | 5.8638 | 1.6054 | N
24/06/2017 | 17:00 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 38 | 10 | 0.00026084 | 0.0026084 | N
24/06/2017 | 18:00 | ZN1673:PA11 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 51 | 15 | 0.00052511 | 0.0035008 | N
24/06/2017 | 18:00 | ZN1673:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 17 | 60 | 0.00070015 | 0.0011669 | N
25/06/2017 | 23:42 | ZN12570:PA34 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 850 | 35 | 0.13316 | 0.38046 | N
30/06/2017 | 13:09 | ZN12600:PA2 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 291 | 0.0013014 | 0.0004476 | N
30/06/2017 | 13:25 | 512:48046 | SHORT RURAL | Vegetation | Blow/Fall In - NSP responsibility | 1 | 199 | 0.0008917 | 0.0004476 | N
30/06/2017 | 16:22 | ZN10990:PA6 | URBAN | Vegetation | Blow/Fall In - NSP responsibility | 1 | 290 | 0.00019886 | 6.8642e-05 | N
02/07/2016 | 11:31 | ZN5868:PA17 | URBAN | Third Party | Other | 1 | 119 | 8.2418e-05 | 6.9259e-05 | N
03/07/2016 | 22:40 | 265:81651 | SHORT RURAL | Third Party | Vehicle impact | 20 | 969 | 0.08823 | 0.0091053 | N
04/07/2016 | 09:53 | 222:33601 | SHORT RURAL | Third Party | Unauthorised access | 6 | 372 | 0.010161 | 0.0027316 | N
04/07/2016 | 15:22 | 524:33572 | SHORT RURAL | Third Party | Unauthorised access | 1 | 128 | 0.00058274 | 0.00045526 | N
05/07/2016 | 02:47 | 814:82285 | SHORT RURAL | Third Party | Vehicle impact | 156 | 139 | 0.098977 | 0.07103 | N
05/07/2016 | 08:32 | 265:81651 | SHORT RURAL | Third Party | Vehicle impact | 157 | 130 | 0.092617 | 0.071485 | N
07/07/2016 | 12:46 | ZN15004:PA3 | URBAN | Third Party | Vehicle impact | 29 | 139 | 0.0027842 | 0.0020081 | N
07/07/2016 | 16:06 | 235:2124 | SHORT RURAL | Third Party | Vehicle impact | 7 | 286 | 0.0091141 | 0.0031867 | N
08/07/2016 | 00:41 | ZN195:PA9 | URBAN | Third Party | Vehicle impact | 1 | 880 | 0.0006092 | 6.9246e-05 | N
08/07/2016 | 12:08 | ZN690:PA25 | URBAN | Third Party | Other | 87 | 81 | 0.0049059 | 0.0060244 | N
08/07/2016 | 12:55 | ZN14892:PA6 | SHORT RURAL | Third Party | Vehicle impact | 50 | 265 | 0.060226 | 0.022763 | N
08/07/2016 | 13:15 | ZN14892:PA6 | SHORT RURAL | Third Party | Vehicle impact | 11 | 30 | 0.0015023 | 0.0050078 | N
10/07/2016 | 13:15 | ZN262:PA19 | URBAN | Third Party | Vehicle impact | 1 | 344 | 0.00023852 | 6.925e-05 | N
10/07/2016 | 13:46 | ZN10996:PA4 | URBAN | Third Party | Vehicle impact | 1 | 239 | 0.00016551 | 6.925e-05 | N
10/07/2016 | 19:39 | ZN4545:PA31 | URBAN | Third Party | Vehicle impact | 1 | 192 | 0.00013271 | 6.925e-05 | N
11/07/2016 | 00:27 | 224:80341 | URBAN | Third Party | Vehicle impact | 1 | 418 | 0.00028965 | 6.925e-05 | N
11/07/2016 | 21:32 | ZN35800:PA16 | URBAN | Third Party | Vehicle impact | 29 | 138 | 0.0027714 | 0.0020083 | N
12/07/2016 | 09:04 | ZN15011:PA2 | URBAN | Third Party | Vehicle impact | 46 | 81 | 0.0025798 | 0.0031856 | N
12/07/2016 | 13:35 | ZN35500:PA23 | URBAN | Third Party | Other | 377 | 76 | 0.019911 | 0.026108 | N
13/07/2016 | 08:55 | ZN36300:PA5 | URBAN | Third Party | Vehicle impact | 86 | 64 | 0.0038237 | 0.0059558 | N
13/07/2016 | 13:59 | ZN36300:PA5 | URBAN | Third Party | Vehicle impact | 86 | 180 | 0.010746 | 0.0059558 | N
14/07/2016 | 07:40 | ZN35500:PA24 | URBAN | Third Party | Vehicle impact | 1 | 140 | 9.6657e-05 | 6.9255e-05 | N
14/07/2016 | 09:19 | ZN14892:PA19 | URBAN | Third Party | Vehicle impact | 22 | 81 | 0.0012341 | 0.0015236 | N
14/07/2016 | 11:07 | ZN4545:PA36 | URBAN | Third Party | Vehicle impact | 1 | 259 | 0.00017914 | 6.9255e-05 | N
14/07/2016 | 11:43 | ZN15002:PA4 | URBAN | Third Party | Vehicle impact | 1 | 197 | 0.00013633 | 6.9255e-05 | N
14/07/2016 | 19:11 | ZN965:PA43 | URBAN | Third Party | Vehicle impact | 38 | 94 | 0.0024738 | 0.0026317 | N
15/07/2016 | 08:15 | 238:34141 | SHORT RURAL | Third Party | Vehicle impact | 23 | 105 | 0.010995 | 0.010471 | N
15/07/2016 | 12:04 | ZN15014:PA19 | URBAN | Third Party | Vehicle impact | 50 | 141 | 0.0048825 | 0.0034628 | N
15/07/2016 | 15:02 | ZN195:PA25 | URBAN | Third Party | Dig-in | 1 | 372 | 0.00025776 | 6.9256e-05 | N
15/07/2016 | 19:26 | 239:82132 | URBAN | Third Party | Vehicle impact | 214 | 273 | 0.040461 | 0.014821 | N
16/07/2016 | 05:53 | ZN2310:PA65 | URBAN | Third Party | Vehicle impact | 1 | 293 | 0.0002027 | 6.9243e-05 | N
16/07/2016 | 08:38 | ZN14144:PA10 | SHORT RURAL | Third Party | Other | 5 | 97 | 0.0022023 | 0.0022704 | N
18/07/2016 | 15:46 | 512:48048 | SHORT RURAL | Third Party | Vehicle impact | 3 | 154 | 0.0020978 | 0.0013622 | N
19/07/2016 | 07:43 | ZN15008:PA1 | URBAN | Third Party | Other | 1 | 77 | 5.3018e-05 | 6.9244e-05 | N
22/07/2016 | 02:02 | ZN1290:PA16 | URBAN | Third Party | Vehicle impact | 3 | 718 | 0.0014913 | 0.0002077 | N
22/07/2016 | 09:33 | ZN4545:PA25 | URBAN | Third Party | Vehicle impact | 1 | 147 | 0.00010167 | 6.9235e-05 | N
22/07/2016 | 09:49 | ZN167:PA21 | URBAN | Third Party | Vehicle impact | 1 | 341 | 0.00023607 | 6.9235e-05 | N
22/07/2016 | 10:33 | ZN15006:PA15 | URBAN | Third Party | Vehicle impact | 1 | 87 | 5.9946e-05 | 6.9235e-05 | N
22/07/2016 | 17:36 | ZN3922:PA26 | URBAN | Third Party | Vehicle impact | 16 | 331 | 0.0036667 | 0.0011078 | N
23/07/2016 | 00:30 | ZN12600:PA2 | SHORT RURAL | Third Party | Vehicle impact | 15 | 245 | 0.016681 | 0.0068086 | N
23/07/2016 | 10:10 | 242:81541 | URBAN | Third Party | Vehicle impact | 1 | 328 | 0.00022737 | 6.9235e-05 | N
24/07/2016 | 08:15 | ZN3425:PA30 | URBAN | Third Party | Vehicle impact | 37 | 500 | 0.012805 | 0.0025617 | N
24/07/2016 | 16:36 | ZN12610:PA13 | URBAN | Third Party | Vehicle impact | 1 | 1,164 | 0.00080588 | 6.9235e-05 | N
25/07/2016 | 16:15 | ZN14143:PA17 | SHORT RURAL | Third Party | Vehicle impact | 4 | 195 | 0.0035405 | 0.0018156 | N
27/07/2016 | 17:16 | ZN36800:PA57 | URBAN | Third Party | Dig-in | 69 | 480 | 0.022942 | 0.0047773 | N
29/07/2016 | 09:30 | 261:81879 | URBAN | Third Party | Vehicle impact | 1 | 269 | 0.00018626 | 6.9228e-05 | N
29/07/2016 | 13:30 | ZN690:PA28 | URBAN | Third Party | Vehicle impact | 1 | 419 | 0.00029033 | 6.9228e-05 | N
30/07/2016 | 13:15 | ZN4545:PA26 | URBAN | Third Party | Vehicle impact | 19 | 250 | 0.0032883 | 0.0013153 | N
30/07/2016 | 14:00 | ZN4545:PA26 | URBAN | Third Party | Vehicle impact | 51 | 330 | 0.011651 | 0.0035306 | N
30/07/2016 | 14:55 | ZN2466:PA27 | URBAN | Third Party | Vehicle impact | 3 | 120 | 0.00024922 | 0.00020769 | N
30/07/2016 | 18:19 | ZN9900:PA21 | URBAN | Third Party | Vehicle impact | 44 | 140 | 0.0042761 | 0.003046 | N
30/07/2016 | 21:21 | ZN9900:PA21 | URBAN | Third Party | Vehicle impact | 44 | 729 | 0.022206 | 0.003046 | N
01/08/2016 | 10:32 | ZN9252:PA21 | URBAN | Third Party | Vehicle impact | 1 | 238 | 0.00016467 | 6.923e-05 | N
01/08/2016 | 11:10 | 202:34259 | URBAN | Third Party | Other | 374 | 48 | 0.012428 | 0.025892 | N
01/08/2016 | 11:13 | ZN2835:PA16 | URBAN | Third Party | Vehicle impact | 28 | 137 | 0.0026556 | 0.0019384 | N
03/08/2016 | 11:32 | ZN2835:PA10 | URBAN | Third Party | Vehicle impact | 1 | 267 | 0.0001849 | 6.9231e-05 | N
03/08/2016 | 12:48 | ZN180:PA7 | URBAN | Third Party | Dig-in | 43 | 79 | 0.0023548 | 0.0029769 | N
03/08/2016 | 20:41 | ZN690:PA35 | URBAN | Third Party | Vehicle impact | 1 | 282 | 0.00019521 | 6.9231e-05 | N
04/08/2016 | 23:14 | ZN14143:PA17 | SHORT RURAL | Third Party | Vehicle impact | 1 | 246 | 0.0011171 | 0.00045463 | N
05/08/2016 | 14:02 | ZN35500:PA22 | URBAN | Third Party | Vehicle impact | 61 | 63 | 0.0026585 | 0.0042198 | N
05/08/2016 | 15:01 | ZN35600:PA4 | URBAN | Third Party | Vehicle impact | 284 | 446 | 0.087714 | 0.019646 | N
05/08/2016 | 15:01 | ZN35600:PA9 | URBAN | Third Party | Vehicle impact | 1 | 569 | 0.00039362 | 6.9177e-05 | N
05/08/2016 | 15:17 | ZN15008:PA9 | URBAN | Third Party | Vehicle impact | 1 | 162 | 0.00011214 | 6.9177e-05 | N
05/08/2016 | 15:23 | ZN1285:PA33 | URBAN | Third Party | Vehicle impact | 1 | 546 | 0.00037741 | 6.9177e-05 | N
05/08/2016 | 22:41 | ZN15008:PA5 | URBAN | Third Party | Other | 1 | 797 | 0.00055126 | 6.9177e-05 | N
06/08/2016 | 07:50 | ZN10996:PA12 | URBAN | Third Party | Vehicle impact | 49 | 70 | 0.0023666 | 0.0033897 | N
09/08/2016 | 08:55 | ZN15001:PA2 | URBAN | Third Party | Vehicle impact | 100 | 185 | 0.012798 | 0.0069177 | N
11/08/2016 | 09:16 | ZN9245:PA42 | URBAN | Third Party | Other | 53 | 148 | 0.00543 | 0.0036652 | N
12/08/2016 | 08:15 | 232:11454 | SHORT RURAL | Third Party | Dig-in | 33 | 214 | 0.032221 | 0.015048 | N
12/08/2016 | 12:18 | 264:81240 | SHORT RURAL | Third Party | Other | 1 | 49 | 0.0002242 | 0.00045601 | N
13/08/2016 | 10:15 | ZN10990:PA6 | URBAN | Third Party | Vehicle impact | 1 | 254 | 0.00017569 | 6.9157e-05 | N
15/08/2016 | 14:44 | ZN690:PA18 | URBAN | Third Party | Vehicle impact | 76 | 209 | 0.010985 | 0.0052559 | N
16/08/2016 | 12:12 | ZN1673:PA7 | URBAN | Third Party | Other | 20 | 72 | 0.00099586 | 0.0013831 | N
16/08/2016 | 16:29 | ZN2568:PA30 | URBAN | Third Party | Vehicle impact | 70 | 386 | 0.018686 | 0.004841 | N
17/08/2016 | 12:45 | ZN14144:PA1 | URBAN | Third Party | Vehicle impact | 54 | 365 | 0.013631 | 0.0037346 | N
18/08/2016 | 08:27 | ZN10996:PA10 | URBAN | Third Party | Other | 1 | 153 | 0.0001061 | 6.9379e-05 | N
18/08/2016 | 12:30 | ZN80:PA21 | URBAN | Third Party | Vehicle impact | 44 | 360 | 0.01099 | 0.0030527 | N
18/08/2016 | 16:52 | ZN690:PA18 | URBAN | Third Party | Vehicle impact | 1 | 410 | 0.00028427 | 6.9379e-05 | N
19/08/2016 | 13:30 | ZN35370:PA10 | SHORT RURAL | Third Party | Dig-in | 102 | 166 | 0.078522 | 0.04728 | N
19/08/2016 | 19:48 | ZN35800:PA3 | URBAN | Third Party | Vehicle impact | 3 | 187 | 0.00038922 | 0.00020814 | N
22/08/2016 | 06:38 | ZN9252:PA24 | URBAN | Third Party | Vehicle impact | 1 | 111 | 7.7289e-05 | 6.938e-05 | N
22/08/2016 | 14:13 | ZN129:PA28 | URBAN | Third Party | Vehicle impact | 1 | 242 | 0.00016786 | 6.938e-05 | N
24/08/2016 | 14:07 | ZN15006:PA12 | URBAN | Third Party | Vehicle impact | 1 | 83 | 5.7243e-05 | 6.9092e-05 | N
24/08/2016 | 15:12 | ZN2473:PA31 | URBAN | Third Party | Vehicle impact | 1 | 37 | 2.5875e-05 | 6.9092e-05 | N
24/08/2016 | 15:58 | ZN3155:PA16 | URBAN | Third Party | Vehicle impact | 40 | 283 | 0.0078208 | 0.0027637 | N
27/08/2016 | 11:23 | ZN3922:PA21 | URBAN | Third Party | Other | 73 | 116 | 0.0058698 | 0.0050413 | N
29/08/2016 | 08:00 | 806:82662 | SHORT RURAL | Third Party | Vehicle impact | 15 | 256 | 0.017534 | 0.0068493 | N
29/08/2016 | 08:35 | ZN195:PA28 | URBAN | Third Party | Dig-in | 905 | 84 | 0.052213 | 0.062499 | N
29/08/2016 | 14:30 | ZN80:PA25 | URBAN | Third Party | Vehicle impact | 61 | 99 | 0.0041832 | 0.0042127 | N
30/08/2016 | 08:45 | 523:33503 | URBAN | Third Party | Vehicle impact | 2 | 174 | 0.00024055 | 0.00013812 | N
30/08/2016 | 10:40 | ZN3472:PA8 | URBAN | Third Party | Vehicle impact | 42 | 125 | 0.0036151 | 0.0029006 | N
30/08/2016 | 15:21 | ZN3472:PA34 | URBAN | Third Party | Vehicle impact | 4 | 344 | 0.00095028 | 0.00027625 | N
31/08/2016 | 08:37 | ZN12650:PA16 | URBAN | Third Party | Other | 1 | 202 | 0.00013967 | 6.9039e-05 | N
31/08/2016 | 13:46 | ZN35800:PA7 | URBAN | Third Party | Vehicle impact | 1 | 194 | 0.00013388 | 6.9039e-05 | N
31/08/2016 | 17:30 | ZN14892:PA19 | URBAN | Third Party | Vehicle impact | 56 | 90 | 0.0034796 | 0.0038662 | N
01/09/2016 | 01:35 | ZN9700:PA19 | URBAN | Third Party | Vehicle impact | 1 | 325 | 0.00022434 | 6.904e-05 | N
01/09/2016 | 14:43 | ZN874:PA26 | URBAN | Third Party | Vehicle impact | 1 | 1,097 | 0.00075717 | 6.904e-05 | N
01/09/2016 | 21:01 | ZN3472:PA8 | URBAN | Third Party | Vehicle impact | 63 | 169 | 0.0073376 | 0.0043495 | N
01/09/2016 | 21:40 | 528:83020 | SHORT RURAL | Third Party | Vehicle impact | 10 | 80 | 0.0036518 | 0.0045647 | N
02/09/2016 | 11:40 | ZN195:PA11 | URBAN | Third Party | Vehicle impact | 1 | 170 | 0.00011706 | 6.904e-05 | N
02/09/2016 | 14:06 | ZN35800:PA2 | SHORT RURAL | Third Party | Vehicle impact | 1 | 330 | 0.0015077 | 0.00045647 | N
03/09/2016 | 15:25 | ZN2466:PA20 | URBAN | Third Party | Dig-in | 6 | 1,935 | 0.0080156 | 0.00041424 | N
02/09/2016 | 18:32 | ZN340:PA27 | URBAN | Third Party | Dig-in | 37 | 52 | 0.0013377 | 0.0025545 | N
02/09/2016 | 23:05 | ZN340:PA27 | URBAN | Third Party | Dig-in | 37 | 895 | 0.022862 | 0.0025545 | N
03/09/2016 | 00:46 | ZN12620:PA10 | SHORT RURAL | Third Party | Vehicle impact | 1 | 655 | 0.0029898 | 0.00045648 | N
03/09/2016 | 02:52 | 507:80925 | SHORT RURAL | Third Party | Vehicle impact | 1 | 502 | 0.0022924 | 0.00045648 | N
03/09/2016 | 08:05 | 528:83019 | SHORT RURAL | Third Party | Unauthorised access | 1 | 115 | 0.00052282 | 0.00045648 | N
04/09/2016 | 17:06 | ZN398:PA20 | URBAN | Third Party | Vehicle impact | 45 | 99 | 0.0030758 | 0.0031069 | N
05/09/2016 | 12:50 | ZN3672:PA44 | URBAN | Third Party | Vehicle impact | 89 | 219 | 0.013462 | 0.0061447 | N
05/09/2016 | 17:26 | ZN1290:PA1 | URBAN | Third Party | Vehicle impact | 1 | 192 | 0.00013288 | 6.9042e-05 | N
05/09/2016 | 21:27 | ZN3672:PA44 | URBAN | Third Party | Vehicle impact | 1 | 693 | 0.00047826 | 6.9042e-05 | N
06/09/2016 | 09:10 | ZN3472:PA12 | URBAN | Third Party | Vehicle impact | 1 | 155 | 0.00010677 | 6.9042e-05 | N
06/09/2016 | 10:27 | ZN1068:PA26 | URBAN | Third Party | Vehicle impact | 119 | 68 | 0.0055869 | 0.008216 | N
06/09/2016 | 10:21 | ZN12610:PA16 | SHORT RURAL | Third Party | Vehicle impact | 1 | 159 | 0.00072359 | 0.00045648 | N
07/09/2016 | 04:43 | ZN3472:PA30 | URBAN | Third Party | Vehicle impact | 63 | 256 | 0.011137 | 0.0043497 | N
07/09/2016 | 10:58 | ZN2635:PA38 | URBAN | Third Party | Vehicle impact | 1 | 272 | 0.00018753 | 6.9043e-05 | N
07/09/2016 | 11:22 | ZN9245:PA41 | URBAN | Third Party | Other | 1 | 114 | 7.8709e-05 | 6.9043e-05 | N
07/09/2016 | 11:23 | ZN2635:PA58 | URBAN | Third Party | Vehicle impact | 1 | 37 | 2.5488e-05 | 6.9043e-05 | N
07/09/2016 | 14:14 | ZN3154:PA12 | URBAN | Third Party | Vehicle impact | 1 | 345 | 0.00023826 | 6.9043e-05 | N
08/09/2016 | 21:24 | 224:80332 | URBAN | Third Party | Vehicle impact | 1 | 145 | 0.00010043 | 6.9058e-05 | N
10/09/2016 | 15:59 | ZN1850:PA3 | URBAN | Third Party | Vehicle impact | 49 | 81 | 0.002741 | 0.003384 | N
11/09/2016 | 02:27 | ZN10993:PA33 | URBAN | Third Party | Vehicle impact | 699 | 98 | 0.047309 | 0.048274 | N
11/09/2016 | 02:27 | ZN10993:PA35 | URBAN | Third Party | Vehicle impact | 17 | 623 | 0.0073143 | 0.0011741 | N
11/09/2016 | 07:26 | ZN180:PA31 | URBAN | Third Party | Vehicle impact | 93 | 194 | 0.012439 | 0.0064228 | N
12/09/2016 | 12:29 | ZN80:PA25 | URBAN | Third Party | Vehicle impact | 1,348 | 75 | 0.07009 | 0.093095 | N
12/09/2016 | 12:29 | ZN80:PA32 | URBAN | Third Party | Vehicle impact | 63 | 75 | 0.0032632 | 0.0043509 | N
13/09/2016 | 11:57 | ZN167:PA20 | URBAN | Third Party | Vehicle impact | 116 | 67 | 0.0053797 | 0.0080114 | N
13/09/2016 | 12:32 | ZN72:PA14 | URBAN | Third Party | Vehicle impact | 1 | 418 | 0.00028868 | 6.9064e-05 | N
14/09/2016 | 06:54 | ZN4545:PA41 | SHORT RURAL | Third Party | Vehicle impact | 131 | 152 | 0.090293 | 0.059541 | N
14/09/2016 | 12:07 | ZN14891:PA5 | SHORT RURAL | Third Party | Vehicle impact | 81 | 142 | 0.052437 | 0.036815 | N
14/09/2016 | 13:22 | 532:83309 | SHORT RURAL | Third Party | Vehicle impact | 1 | 245 | 0.001112 | 0.00045451 | N
16/09/2016 | 12:17 | ZN3472:PA15 | URBAN | Third Party | Vehicle impact | 1 | 193 | 0.00013326 | 6.9052e-05 | N
18/09/2016 | 04:10 | 508:82575 | SHORT RURAL | Third Party | Vehicle impact | 16 | 660 | 0.047946 | 0.0072645 | N
19/09/2016 | 15:14 | ZN1285:PA27 | URBAN | Third Party | Vehicle impact | 1 | 374 | 0.00025819 | 6.9064e-05 | N
20/09/2016 | 09:18 | 264:81244 | SHORT RURAL | Third Party | Vehicle impact | 1 | 672 | 0.0030503 | 0.00045403 | N
21/09/2016 | 18:50 | ZN14143:PA6 | URBAN | Third Party | Vehicle impact | 2 | 225 | 0.0003108 | 0.00013813 | N
21/09/2016 | 16:35 | ZN690:PA17 | URBAN | Third Party | Vehicle impact | 136 | 651 | 0.061113 | 0.009393 | N
23/09/2016 | 16:12 | ZN13000:PA7 | SHORT RURAL | Third Party | Vehicle impact | 1 | 197 | 0.00089489 | 0.00045391 | N
24/09/2016 | 00:13 | ZN1193:PA28 | URBAN | Third Party | Vehicle impact | 22 | 421 | 0.006397 | 0.001519 | N
24/09/2016 | 19:37 | ZN167:PA20 | URBAN | Third Party | Unauthorised access | 6 | 143 | 0.00059241 | 0.00041427 | N
25/09/2016 | 04:02 | ZN14892:PA19 | URBAN | Third Party | Vehicle impact | 1 | 74 | 5.0922e-05 | 6.9046e-05 | N
25/09/2016 | 05:15 | ZN10996:PA10 | URBAN | Third Party | Vehicle impact | 84 | 377 | 0.021843 | 0.0057999 | N
26/09/2016 | 10:36 | ZN3425:PA32 | URBAN | Third Party | Vehicle impact | 23 | 59 | 0.00093696 | 0.0015881 | N
26/09/2016 | 14:20 | ZN14892:PA16 | URBAN | Third Party | Other | 1 | 448 | 0.00030936 | 6.9046e-05 | N
27/09/2016 | 13:15 | ZN36300:PA3 | URBAN | Third Party | Other | 1 | 164 | 0.00011334 | 6.9047e-05 | N
27/09/2016 | 15:21 | 239:82127 | SHORT RURAL | Third Party | Dig-in | 21 | 478 | 0.045569 | 0.0095315 | N
28/09/2016 | 13:00 | ZN15011:PA8 | URBAN | Third Party | Vehicle impact | 35 | 239 | 0.0057795 | 0.0024167 | N
29/09/2016 | 09:35 | ZN690:PA18 | URBAN | Third Party | Vehicle impact | 1 | 235 | 0.00016216 | 6.9028e-05 | N
29/09/2016 | 10:10 | 239:82127 | SHORT RURAL | Third Party | Dig-in | 11 | 250 | 0.012479 | 0.0049914 | N
29/09/2016 | 16:51 | ZN15013:PA6 | SHORT RURAL | Third Party | Vehicle impact | 1 | 221 | 0.0010043 | 0.00045377 | N
30/09/2016 | 10:06 | ZN1193:PA15 | URBAN | Third Party | Vehicle impact | 62 | 69 | 0.002953 | 0.0042797 | N
30/09/2016 | 13:13 | 229:34995 | SHORT RURAL | Third Party | Other | 1 | 177 | 0.00080105 | 0.00045377 | N
01/10/2016 | 08:52 | ZN10996:PA10 | URBAN | Third Party | Vehicle impact | 1 | 128 | 8.8395e-05 | 6.9059e-05 | N
01/10/2016 | 08:52 | ZN10996:PA8 | URBAN | Third Party | Vehicle impact | 24 | 128 | 0.0021215 | 0.0016574 | N
04/10/2016 | 11:07 | ZN2635:PA31 | URBAN | Third Party | Dig-in | 1,594 | 79 | 0.087245 | 0.11008 | N
04/10/2016 | 20:41 | ZN10995:PA12 | URBAN | Third Party | Vehicle impact | 1 | 1,038 | 0.00071686 | 6.9059e-05 | N
05/10/2016 | 08:13 | ZN180:PA33 | URBAN | Third Party | Vehicle impact | 1 | 287 | 0.00019817 | 6.9061e-05 | N
05/10/2016 | 19:05 | ZN7900:PA14 | URBAN | Third Party | Other | 1 | 45 | 3.1077e-05 | 6.9061e-05 | N
06/10/2016 | 10:07 | ZN2635:PA31 | URBAN | Third Party | Other | 1 | 363 | 0.00025056 | 6.9062e-05 | N
06/10/2016 | 21:07 | 216:10724 | URBAN | Third Party | Unauthorised access | 3 | 158 | 0.00032735 | 0.00020719 | N
07/10/2016 | 12:15 | ZN14892:PA13 | URBAN | Third Party | Vehicle impact | 958 | 41 | 0.02701 | 0.066135 | N
07/10/2016 | 13:59 | ZN10994:PA3 | URBAN | Third Party | Vehicle impact | 57 | 91 | 0.0035808 | 0.003935 | N
07/10/2016 | 14:27 | ZN7900:PA23 | URBAN | Third Party | Dig-in | 8 | 363 | 0.0020048 | 0.00055227 | N
07/10/2016 | 14:27 | ZN901:PA24 | URBAN | Third Party | Dig-in | 1 | 362 | 0.00025 | 6.9034e-05 | N
08/10/2016 | 22:43 | 203:8085 | URBAN | Third Party | Unauthorised access | 44 | 62 | 0.0018846 | 0.0030398 | N
08/10/2016 | 09:09 | ZN15006:PA8 | URBAN | Third Party | Vehicle impact | 1 | 255 | 0.00017635 | 6.9085e-05 | N
09/10/2016 | 21:16 | ZN12640:PA1 | SHORT RURAL | Third Party | Vehicle impact | 678 | 121 | 0.37178 | 0.30682 | N
10/10/2016 | 15:14 | ZN15009:PA1 | URBAN | Third Party | Vehicle impact | 1,044 | 135 | 0.09737 | 0.072126 | N
10/10/2016 | 15:14 | ZN15009:PA7 | URBAN | Third Party | Vehicle impact | 1,589 | 174 | 0.19077 | 0.10978 | N
11/10/2016 | 05:05 | 813:89061 | LONG RURAL | Third Party | Vehicle impact | 1 | 139 | 0.04975 | 0.035689 | N
11/10/2016 | 16:05 | ZN72:PA24 | SHORT RURAL | Third Party | Other | 44 | 95 | 0.018837 | 0.019895 | N
12/10/2016 | 15:26 | ZN4545:PA21 | URBAN | Third Party | Vehicle impact | 1 | 273 | 0.00018863 | 6.9048e-05 | N
13/10/2016 | 10:26 | ZN5868:PA30 | URBAN | Third Party | Vehicle impact | 44 | 222 | 0.0067425 | 0.0030422 | N
14/10/2016 | 15:28 | ZN15004:PA5 | URBAN | Third Party | Vehicle impact | 1 | 289 | 0.00020002 | 6.914e-05 | N
17/10/2016 | 15:30 | 225:13444 | SHORT RURAL | Third Party | Vehicle impact | 189 | 82 | 0.069805 | 0.085128 | N
17/10/2016 | 15:30 | 225:13446 | URBAN | Third Party | Vehicle impact | 1,565 | 82 | 0.088637 | 0.10809 | N
17/10/2016 | 15:30 | 225:33670 | URBAN | Third Party | Vehicle impact | 815 | 82 | 0.046159 | 0.056291 | N
17/10/2016 | 15:30 | 225:33676 | URBAN | Third Party | Vehicle impact | 1,203 | 82 | 0.068134 | 0.08309 | N
17/10/2016 | 15:30 | 225:33679 | URBAN | Third Party | Vehicle impact | 654 | 82 | 0.03704 | 0.045171 | N
18/10/2016 | 09:13 | ZN1287:PA12 | URBAN | Third Party | Other | 66 | 122 | 0.0055451 | 0.0045588 | N
18/10/2016 | 08:15 | ZN12620:PA2 | SHORT RURAL | Third Party | Unauthorised access | 81 | 315 | 0.11492 | 0.036483 | N
18/10/2016 | 12:40 | ZN398:PA19 | URBAN | Third Party | Other | 73 | 140 | 0.0070593 | 0.0050423 | N
19/10/2016 | 08:33 | ZN35800:PA14 | URBAN | Third Party | Vehicle impact | 79 | 116 | 0.0063373 | 0.0054569 | N
19/10/2016 | 10:03 | ZN1285:PA27 | URBAN | Third Party | Vehicle impact | 1 | 26 | 1.8029e-05 | 6.9075e-05 | N
19/10/2016 | 17:10 | 221:11899 | SHORT RURAL | Third Party | Vehicle impact | 1 | 129 | 0.00058223 | 0.00045041 | N
20/10/2016 | 12:24 | ZN15005:PA2 | URBAN | Third Party | Other | 1 | 1,309 | 0.00090455 | 6.9078e-05 | N
21/10/2016 | 12:23 | ZN36300:PA8 | URBAN | Third Party | Vehicle impact | 1 | 67 | 4.6303e-05 | 6.942e-05 | N
21/10/2016 | 15:12 | ZN874:PA17 | URBAN | Third Party | Dig-in | 1 | 406 | 0.00028174 | 6.942e-05 | N
22/10/2016 | 18:38 | 532:83301 | URBAN | Third Party | Vehicle impact | 1 | 232 | 0.00016017 | 6.9057e-05 | N
24/10/2016 | 11:36 | 258:80793 | URBAN | Third Party | Vehicle impact | 58 | 29 | 0.0011616 | 0.0040054 | N
24/10/2016 | 15:02 | ZN36300:PA8 | URBAN | Third Party | Vehicle impact | 1 | 322 | 0.00022238 | 6.9058e-05 | N
25/10/2016 | 21:37 | 507:80925 | SHORT RURAL | Third Party | Vehicle impact | 41 | 72 | 0.013322 | 0.01846 | N
25/10/2016 | 10:00 | 807:74180 | SHORT RURAL | Third Party | Unauthorised access | 1 | 60 | 0.00027014 | 0.00045024 | N
28/10/2016 | 08:05 | ZN9118:PA20 | URBAN | Third Party | Vehicle impact | 1 | 114 | 7.9013e-05 | 6.9037e-05 | N
28/10/2016 | 10:45 | ZN847:PA10 | URBAN | Third Party | Dig-in | 15 | 899 | 0.0093096 | 0.0010356 | N
28/10/2016 | 14:32 | ZN874:PA18 | URBAN | Third Party | Dig-in | 1,212 | 93 | 0.077816 | 0.083673 | N
28/10/2016 | 14:32 | ZN874:PA4 | URBAN | Third Party | Dig-in | 1,789 | 96 | 0.11914 | 0.12351 | N
28/10/2016 | 14:32 | ZN874:PA7 | URBAN | Third Party | Dig-in | 528 | 93 | 0.0339 | 0.036452 | N
30/10/2016 | 16:36 | 205:12205 | SHORT RURAL | Third Party | Vehicle impact | 1,672 | 60 | 0.44833 | 0.75259 | N
31/10/2016 | 09:13 | ZN262:PA31 | URBAN | Third Party | Vehicle impact | 1 | 166 | 0.00011482 | 6.9038e-05 | N
31/10/2016 | 19:10 | ZN36800:PA57 | URBAN | Third Party | Other | 93 | 70 | 0.0044944 | 0.0064206 | N
01/11/2016 | 11:35 | ZN12570:PA37 | SHORT RURAL | Third Party | Other | 28 | 85 | 0.010714 | 0.012604 | N
01/11/2016 | 12:17 | ZN35600:PA9 | URBAN | Third Party | Vehicle impact | 1 | 137 | 9.4678e-05 | 6.9041e-05 | N
01/11/2016 | 14:42 | ZN116:PA43 | URBAN | Third Party | Vehicle impact | 1 | 257 | 0.00017767 | 6.9041e-05 | N
01/11/2016 | 15:21 | ZN35600:PA9 | URBAN | Third Party | Vehicle impact | 1 | 368 | 0.00025429 | 6.9041e-05 | N
01/11/2016 | 15:20 | ZN1193:PA28 | URBAN | Third Party | Vehicle impact | 27 | 100 | 0.0018641 | 0.0018641 | N
01/11/2016 | 15:20 | ZN80:PA31 | URBAN | Third Party | Vehicle impact | 58 | 90 | 0.0036039 | 0.0040044 | N
01/11/2016 | 15:41 | 507:80925 | SHORT RURAL | Third Party | Vehicle impact | 12 | 90 | 0.0048617 | 0.0054019 | N
01/11/2016 | 15:41 | 524:33570 | SHORT RURAL | Third Party | Vehicle impact | 1,304 | 103 | 0.60624 | 0.587 | N
02/11/2016 | 09:08 | ZN1193:PA28 | URBAN | Third Party | Other | 1 | 381 | 0.00026337 | 6.9044e-05 | N
02/11/2016 | 12:22 | ZN2835:PA10 | URBAN | Third Party | Vehicle impact | 1 | 187 | 0.00012941 | 6.9044e-05 | N
05/11/2016 | 04:46 | ZN262:PA15 | URBAN | Third Party | Vehicle impact | 1 | 448 | 0.0003094 | 6.9027e-05 | N
05/11/2016 | 10:40 | ZN630:PA3 | URBAN | Third Party | Vehicle impact | 1 | 260 | 0.0001793 | 6.9027e-05 | N
05/11/2016 | 11:31 | ZN3154:PA17 | URBAN | Third Party | Other | 1 | 148 | 0.00010236 | 6.9027e-05 | N
05/11/2016 | 12:06 | ZN9037:PA7 | URBAN | Third Party | Other | 494 | 165 | 0.056264 | 0.034099 | N
05/11/2016 | 12:06 | ZN9252:PA27 | URBAN | Third Party | Other | 702 | 165 | 0.079954 | 0.048457 | N
07/11/2016 | 10:47 | ZN690:PA30 | URBAN | Third Party | Vehicle impact | 1 | 192 | 0.0001326 | 6.9028e-05 | N
07/11/2016 | 10:52 | ZN5868:PA17 | URBAN | Third Party | Vehicle impact | 1 | 58 | 4.0025e-05 | 6.9028e-05 | N
07/11/2016 | 10:57 | ZN15006:PA16 | URBAN | Third Party | Vehicle impact | 31 | 202 | 0.0043247 | 0.0021399 | N
07/11/2016 | 17:39 | 243:80074 | SHORT RURAL | Third Party | Vehicle impact | 1 | 231 | 0.0010374 | 0.00044999 | N
08/11/2016 | 05:27 | ZN3472:PA28 | URBAN | Third Party | Vehicle impact | 1,501 | 155 | 0.16096 | 0.10361 | N
08/11/2016 | 11:31 | ZN3472:PA17 | URBAN | Third Party | Vehicle impact | 3 | 89 | 0.00018431 | 0.00020709 | N
09/11/2016 | 05:13 | ZN14892:PA6 | SHORT RURAL | Third Party | Vehicle impact | 1 | 16 | 7.2375e-05 | 0.00045 | N
09/11/2016 | 07:45 | 528:83011 | SHORT RURAL | Third Party | Vehicle impact | 42 | 230 | 0.04347 | 0.0189 | N
07/11/2016 | 10:52 | ZN5868:PA2 | URBAN | Third Party | Vehicle impact | 1 | 83 | 5.7293e-05 | 6.9028e-05 | N
09/11/2016 | 11:59 | ZN4545:PA35 | URBAN | Third Party | Vehicle impact | 69 | 96 | 0.0045726 | 0.0047631 | N
10/11/2016 | 03:15 | 243:80075 | SHORT RURAL | Third Party | Vehicle impact | 3 | 735 | 0.0099227 | 0.00135 | N
10/11/2016 | 13:46 | ZN12690:PA7 | SHORT RURAL | Third Party | Dig-in | 8 | 154 | 0.0055441 | 0.0036001 | N
10/11/2016 | 13:50 | ZN2310:PA65 | URBAN | Third Party | Vehicle impact | 1 | 160 | 0.00011013 | 6.9033e-05 | N
10/11/2016 | 14:18 | ZN1648:PA4 | URBAN | Third Party | Vehicle impact | 1 | 191 | 0.00013214 | 6.9033e-05 | N
10/11/2016 | 23:45 | 202:34249 | URBAN | Third Party | Vehicle impact | 1 | 295 | 0.00020365 | 6.9033e-05 | N
10/11/2016 | 23:45 | 202:34254 | URBAN | Third Party | Vehicle impact | 6 | 295 | 0.0012219 | 0.0004142 | N
11/11/2016 | 22:15 | ZN180:PA41 | URBAN | Third Party | Vehicle impact | 1 | 258 | 0.00017786 | 6.9033e-05 | N
12/11/2016 | 10:37 | 238:34141 | SHORT RURAL | Third Party | Vehicle impact | 15 | 335 | 0.022601 | 0.0067465 | N
12/11/2016 | 18:24 | ZN10999:PA25 | URBAN | Third Party | Vehicle impact | 51 | 426 | 0.014993 | 0.0035196 | N
12/11/2016 | 18:35 | ZN10999:PA2 | URBAN | Third Party | Vehicle impact | 39 | 145 | 0.0039021 | 0.0026914 | N
12/11/2016 | 21:05 | ZN10999:PA22 | URBAN | Third Party | Vehicle impact | 1 | 800 | 0.00055205 | 6.9011e-05 | N
14/11/2016 | 11:41 | ZN1285:PA33 | URBAN | Third Party | Other | 1 | 229 | 0.00015776 | 6.9011e-05 | N
14/11/2016 | 16:32 | ZN12650:PA10 | URBAN | Third Party | Vehicle impact | 57 | 1,148 | 0.045158 | 0.0039336 | N
14/11/2016 | 16:32 | ZN12650:PA14 | URBAN | Third Party | Vehicle impact | 669 | 128 | 0.059171 | 0.046168 | N
14/11/2016 | 21:43 | ZN12580:PA16 | URBAN | Third Party | Vehicle impact | 1 | 856 | 0.00059081 | 6.9011e-05 | N
15/11/2016 | 09:58 | ZN2310:PA67 | URBAN | Third Party | Vehicle impact | 49 | 332 | 0.011218 | 0.0033816 | N
15/11/2016 | 19:15 | 513:48056 | SHORT RURAL | Third Party | Vehicle impact | 17 | 95 | 0.0072638 | 0.0076462 | N
16/11/2016 | 08:34 | 526:34637 | SHORT RURAL | Third Party | Vehicle impact | 1 | 405 | 0.0018237 | 0.00044978 | N
17/11/2016 | 13:54 | ZN3472:PA11 | URBAN | Third Party | Vehicle impact | 7 | 146 | 0.00070509 | 0.00048294 | N
18/11/2016 | 11:45 | ZN14891:PA21 | SHORT RURAL | Third Party | Vehicle impact | 14 | 75 | 0.0047213 | 0.006295 | N
18/11/2016 | 11:45 | ZN14891:PA21 | SHORT RURAL | Third Party | Vehicle impact | 15 | 75 | 0.0050585 | 0.0067447 | N
18/11/2016 | 11:50 | 258:80775 | URBAN | Third Party | Other | 19 | 90 | 0.0011797 | 0.0013108 | N
18/11/2016 | 15:12 | ZN262:PA27 | URBAN | Third Party | Vehicle impact | 1 | 227 | 0.00015675 | 6.8991e-05 | N
18/11/2016 | 20:49 | ZN15006:PA12 | URBAN | Third Party | Vehicle impact | 63 | 76 | 0.0032939 | 0.0043464 | N
19/11/2016 | 10:52 | ZN12660:PA14 | SHORT RURAL | Third Party | Vehicle impact | 1,245 | 63 | 0.35107 | 0.55981 | N
19/11/2016 | 17:40 | ZN14891:PA1 | SHORT RURAL | Third Party | Vehicle impact | 1 | 225 | 0.0010107 | 0.00044964 | N
21/11/2016 | 08:16 | ZN10999:PA14 | URBAN | Third Party | Other | 192 | 95 | 0.012524 | 0.013247 | N
21/11/2016 | 14:49 | ZN180:PA41 | URBAN | Third Party | Other | 1 | 178 | 0.00012308 | 6.8995e-05 | N
21/11/2016 | 15:51 | ZN8700:PA61 62GHJ | CBD | Third Party | Dig-in | 5 | 609 | 0.098064 | 0.016103 | N
21/11/2016 | 17:50 | ZN1648:PA19 | URBAN | Third Party | Vehicle impact | 1 | 282 | 0.00019453 | 6.8995e-05 | N
21/11/2016 | 19:56 | ZN2635:PA58 | URBAN | Third Party | Other | 43 | 209 | 0.0061981 | 0.0029668 | N
23/11/2016 | 10:58 | ZN3425:PA16 | URBAN | Third Party | Vehicle impact | 1 | 182 | 0.00012554 | 6.8998e-05 | N
23/11/2016 | 11:45 | ZN3922:PA3 | URBAN | Third Party | Other | 60 | 75 | 0.0030897 | 0.0041399 | N
23/11/2016 | 21:55 | ZN12650:PA3 | URBAN | Third Party | Vehicle impact | 84 | 146 | 0.0084619 | 0.0057958 | N
24/11/2016 | 10:29 | ZN398:PA19 | URBAN | Third Party | Vehicle impact | 1 | 121 | 8.3198e-05 | 6.8978e-05 | N
24/11/2016 | 15:54 | ZN1600:PA21DEF | CBD | Third Party | Dig-in | 1 | 1,830 | 0.058918 | 0.0032196 | N
24/11/2016 | 16:33 | 532:83312 | URBAN | Third Party | Dig-in | 27 | 157 | 0.0029236 | 0.0018624 | N
25/11/2016 | 09:27 | ZN35800:PA22 | URBAN | Third Party | Vehicle impact | 65 | 218 | 0.0097637 | 0.0044835 | N
26/11/2016 | 09:06 | ZN262:PA16 | URBAN | Third Party | Vehicle impact | 1 | 343 | 0.00023664 | 6.9028e-05 | N
26/11/2016 | 21:30 | 524:33578 | URBAN | Third Party | Vehicle impact | 1 | 310 | 0.00021385 | 6.9028e-05 | N
27/11/2016 | 14:01 | ZN1068:PA18 | URBAN | Third Party | Vehicle impact | 36 | 224 | 0.0055665 | 0.002485 | N
28/11/2016 | 09:40 | ZN2466:PA25 | URBAN | Third Party | Vehicle impact | 73 | 50 | 0.0025195 | 0.0050391 | N
28/11/2016 | 09:35 | ZN1068:PA18 | URBAN | Third Party | Vehicle impact | 1 | 134 | 9.2199e-05 | 6.9028e-05 | N
28/11/2016 | 10:35 | ZN2635:PA46 | URBAN | Third Party | Dig-in | 18 | 145 | 0.0018016 | 0.0012425 | N
28/11/2016 | 13:05 | ZN15014:PA5 | URBAN | Third Party | Other | 1 | 115 | 7.9176e-05 | 6.9028e-05 | N
30/11/2016 | 03:41 | ZN7481:PA17 | URBAN | Third Party | Vehicle impact | 1 | 588 | 0.000406 | 6.9028e-05 | N
30/11/2016 | 08:15 | ZN1193:PA12 | URBAN | Third Party | Vehicle impact | 1 | 179 | 0.0001236 | 6.9028e-05 | N
30/11/2016 | 12:03 | ZN3425:PA23 | URBAN | Third Party | Vehicle impact | 1 | 176 | 0.00012156 | 6.9028e-05 | N
01/12/2016 | 16:10 | ZN690:PA25 | URBAN | Third Party | Vehicle impact | 75 | 140 | 0.0072218 | 0.0051757 | N
01/12/2016 | 16:39 | ZN12660:PA10 | URBAN | Third Party | Vehicle impact | 1 | 290 | 0.00020024 | 6.9009e-05 | N
02/12/2016 | 09:17 | ZN690:PA33 | URBAN | Third Party | Vehicle impact | 1 | 223 | 0.00015364 | 6.9009e-05 | N
02/12/2016 | 10:46 | 258:80776 | URBAN | Third Party | Vehicle impact | 1 | 223 | 0.00015421 | 6.9009e-05 | N
01/12/2016 | 12:30 | 513:48059 | SHORT RURAL | Third Party | Dig-in | 3 | 60 | 0.00080868 | 0.0013478 | N
03/12/2016 | 09:23 | 257:81987 | URBAN | Third Party | Vehicle impact | 1 | 174 | 0.00011993 | 6.8959e-05 | N
03/12/2016 | 16:52 | ZN1850:PA4 | URBAN | Third Party | Vehicle impact | 1 | 238 | 0.00016446 | 6.8959e-05 | N
05/12/2016 | 09:34 | ZN35500:PA24 | URBAN | Third Party | Vehicle impact | 47 | 91 | 0.002944 | 0.0032411 | N
05/12/2016 | 14:09 | ZN10991:PA8 | URBAN | Third Party | Vehicle impact | 1 | 680 | 0.00046923 | 6.8959e-05 | N
05/12/2016 | 14:44 | ZN15009:PA5 | URBAN | Third Party | Other | 1 | 1,009 | 0.00069587 | 6.8959e-05 | N
05/12/2016 | 15:05 | ZN14891:PA12 | SHORT RURAL | Third Party | Vehicle impact | 705 | 194 | 0.61343 | 0.31674 | N
05/12/2016 | 15:25 | ZN15009:PA5 | URBAN | Third Party | Dig-in | 1 | 371 | 0.00025599 | 6.8959e-05 | N
05/12/2016 | 16:59 | ZN965:PA3 | URBAN | Third Party | Vehicle impact | 51 | 78 | 0.0027349 | 0.0035169 | N
05/12/2016 | 18:03 | ZN10991:PA8 | URBAN | Third Party | Vehicle impact | 1 | 447 | 0.00030824 | 6.8959e-05 | N
05/12/2016 | 18:03 | ZN10991:PA8 | URBAN | Third Party | Vehicle impact | 1 | 447 | 0.00030804 | 6.8959e-05 | N
06/12/2016 | 06:31 | 233:82815 | SHORT RURAL | Third Party | Vehicle impact | 42 | 89 | 0.016794 | 0.01887 | N
06/12/2016 | 08:52 | 509:33399 | SHORT RURAL | Third Party | Vehicle impact | 1 | 458 | 0.0020569 | 0.00044927 | N
06/12/2016 | 09:38 | 233:82815 | SHORT RURAL | Third Party | Vehicle impact | 43 | 537 | 0.10374 | 0.019319 | N
06/12/2016 | 20:43 | ZN14892:PA16 | URBAN | Third Party | Vehicle impact | 1 | 268 | 0.00018469 | 6.8961e-05 | N
07/12/2016 | 16:07 | ZN10994:PA1 | URBAN | Third Party | Vehicle impact | 1 | 534 | 0.00036834 | 6.8962e-05 | N
09/12/2016 | 02:04 | ZN10994:PA3 | URBAN | Third Party | Vehicle impact | 1 | 595 | 0.00041025 | 6.8938e-05 | N
09/12/2016 | 17:26 | 812:19071 | SHORT RURAL | Third Party | Vehicle impact | 96 | 94 | 0.040548 | 0.043137 | N
09/12/2016 | 23:03 | 264:81236 | SHORT RURAL | Third Party | Vehicle impact | 21 | 55 | 0.0051899 | 0.0094361 | N
10/12/2016 | 08:15 | ZN1287:PA3 | URBAN | Third Party | Other | 1,540 | 125 | 0.13239 | 0.10617 | N
10/12/2016 | 10:15 | ZN1610:PA23 | URBAN | Third Party | Vehicle impact | 12 | 445 | 0.0036814 | 0.00082727 | N
10/12/2016 | 13:16 | ZN35600:PA3 | URBAN | Third Party | Vehicle impact | 71 | 349 | 0.01708 | 0.0048947 | N
13/12/2016 | 15:21 | ZN12640:PA7 | URBAN | Third Party | Vehicle impact | 1 | 218 | 0.00015059 | 6.8942e-05 | N
13/12/2016 | 21:10 | 511:29878 | SHORT RURAL | Third Party | Vehicle impact | 8 | 140 | 0.0050328 | 0.0035948 | N
14/12/2016 | 06:02 | ZN1285:PA23 | URBAN | Third Party | Vehicle impact | 51 | 203 | 0.0071377 | 0.0035161 | N
14/12/2016 | 08:17 | ZN35500:PA24 | URBAN | Third Party | Dig-in | 69 | 113 | 0.0053755 | 0.0047571 | N
14/12/2016 | 14:40 | 507:80932 | SHORT RURAL | Third Party | Vehicle impact | 1 | 410 | 0.0018424 | 0.00044936 | N
14/12/2016 | 14:40 | 525:34580 | SHORT RURAL | Third Party | Vehicle impact | 2 | 239 | 0.0021479 | 0.00089872 | N
14/12/2016 | 14:40 | 525:34586 | SHORT RURAL | Third Party | Vehicle impact | 2 | 239 | 0.0021479 | 0.00089872 | N
14/12/2016 | 14:40 | 525:34589 | URBAN | Third Party | Vehicle impact | 1 | 239 | 0.00016477 | 6.8943e-05 | N
15/12/2016 | 19:21 | ZN3472:PA30 | URBAN | Third Party | Vehicle impact | 80 | 114 | 0.0062831 | 0.0055139 | N
16/12/2016 | 20:34 | ZN2602:PA41 | URBAN | Third Party | Vehicle impact | 1 | 176 | 0.000121 | 6.8926e-05 | N
17/12/2016 | 13:29 | ZN9118:PA3 | SHORT RURAL | Third Party | Vehicle impact | 487 | 87 | 0.19027 | 0.21871 | N
18/12/2016 | 03:28 | ZN1290:PA10 | URBAN | Third Party | Vehicle impact | 35 | 382 | 0.0092154 | 0.0024124 | N
18/12/2016 | 03:28 | ZN1290:PA11 | URBAN | Third Party | Vehicle impact | 1,180 | 382 | 0.31069 | 0.081333 | N
18/12/2016 | 03:28 | ZN1290:PA12 | URBAN | Third Party | Vehicle impact | 1,045 | 382 | 0.27515 | 0.072028 | N
18/12/2016 | 03:28 | ZN1290:PA13 | URBAN | Third Party | Vehicle impact | 160 | 382 | 0.042128 | 0.011028 | N
18/12/2016 | 03:28 | ZN1290:PA16 | URBAN | Third Party | Vehicle impact | 22 | 382 | 0.0057926 | 0.0015164 | N
18/12/2016 | 03:28 | ZN1290:PA17 | URBAN | Third Party | Vehicle impact | 48 | 382 | 0.012638 | 0.0033085 | N
18/12/2016 | 03:28 | ZN1290:PA8 | URBAN | Third Party | Vehicle impact | 719 | 382 | 0.18931 | 0.049558 | N
18/12/2016 | 03:28 | ZN1290:PA9 | URBAN | Third Party | Vehicle impact | 1,223 | 382 | 0.32201 | 0.084297 | N
18/12/2016 | 13:52 | ZN4545:PA44 | URBAN | Third Party | Other | 84 | 83 | 0.0048046 | 0.0057898 | N
19/12/2016 | 16:07 | ZN1287:PA21 | URBAN | Third Party | Vehicle impact | 86 | 339 | 0.020095 | 0.0059277 | N
19/12/2016 | 17:57 | ZN3425:PA33 | URBAN | Third Party | Vehicle impact | 237 | 194 | 0.031664 | 0.016336 | N
20/12/2016 | 18:00 | 813:89061 | LONG RURAL | Third Party | Vehicle impact | 37 | 70 | 0.92236 | 1.3177 | N
20/12/2016 | 14:51 | ZN10990:PA12 | URBAN | Third Party | Vehicle impact | 1 | 278 | 0.0001918 | 6.8927e-05 | N
21/12/2016 | 02:11 | ZN10991:PA13 | URBAN | Third Party | Vehicle impact | 1 | 498 | 0.0003434 | 6.8928e-05 | N
21/12/2016 | 07:42 | 227:13018 | URBAN | Third Party | Vehicle impact | 1 | 398 | 0.00027413 | 6.8928e-05 | N
21/12/2016 | 09:41 | ZN10990:PA6 | URBAN | Third Party | Vehicle impact | 1 | 139 | 9.5787e-05 | 6.8928e-05 | N
21/12/2016 | 11:57 | ZN9118:PA15 | URBAN | Third Party | Vehicle impact | 1 | 183 | 0.00012579 | 6.8928e-05 | N
22/12/2016 | 20:41 | ZN35800:PA15 | URBAN | Third Party | Vehicle impact | 1 | 129 | 8.8603e-05 | 6.8907e-05 | N
23/12/2016 | 11:19 | ZN1285:PA27 | URBAN | Third Party | Vehicle impact | 14 | 131 | 0.0012638 | 0.00096472 | N
23/12/2016 | 14:29 | ZN10991:PA13 | URBAN | Third Party | Vehicle impact | 1 | 239 | 0.00016448 | 6.8908e-05 | N
24/12/2016 | 20:13 | ZN2602:PA29 | URBAN | Third Party | Vehicle impact | 33 | 52 | 0.0011825 | 0.002274 | N
26/12/2016 | 15:12 | ZN9700:PA20 | URBAN | Third Party | Vehicle impact | 35 | 227 | 0.0054768 | 0.0024118 | N
26/12/2016 | 17:02 | ZN12600:PA3 | URBAN | Third Party | Vehicle impact | 1,744 | 49 | 0.059406 | 0.12018 | N
28/12/2016 | 04:38 | ZN35900:PA6 | URBAN | Third Party | Vehicle impact | 1 | 103 | 7.0666e-05 | 6.8909e-05 | N
28/12/2016 | 09:06 | ZN9037:PA3 | URBAN | Third Party | Vehicle impact | 1 | 174 | 0.00011957 | 6.8909e-05 | N
30/12/2016 | 09:22 | ZN12620:PA3 | URBAN | Third Party | Other | 1 | 397 | 0.0002736 | 6.891e-05 | N
31/12/2016 | 16:33 | ZN3472:PA27 | URBAN | Third Party | Vehicle impact | 1 | 308 | 0.00021254 | 6.8911e-05 | N
03/01/2017 | 11:22 | ZN2635:PA32 | URBAN | Third Party | Other | 1 | 227 | 0.00015623 | 6.8911e-05 | N
04/01/2017 | 09:37 | ZN630:PA34 | URBAN | Third Party | Vehicle impact | 1 | 112 | 7.7457e-05 | 6.8912e-05 | N
04/01/2017 | 09:51 | ZN847:PA2 | URBAN | Third Party | Other | 1 | 99 | 6.7936e-05 | 6.8912e-05 | N
05/01/2017 | 16:39 | 256:80632 | URBAN | Third Party | Vehicle impact | 44 | 371 | 0.011249 | 0.0030322 | N
06/01/2017 | 14:12 | ZN3155:PA34 | URBAN | Third Party | Vehicle impact | 1 | 288 | 0.00019831 | 6.8915e-05 | N
07/01/2017 | 04:00 | ZN2196:PA9 | URBAN | Third Party | Vehicle impact | 1 | 550 | 0.00037914 | 6.8893e-05 | N
11/01/2017 | 01:05 | ZN2568:PA25 | URBAN | Third Party | Vehicle impact | 1 | 220 | 0.00015177 | 6.8894e-05 | N
11/01/2017 | 11:14 | ZN80:PA40 | URBAN | Third Party | Vehicle impact | 134 | 106 | 0.0097816 | 0.0092318 | N
11/01/2017 | 19:28 | 243:80080 | SHORT RURAL | Third Party | Vehicle impact | 6 | 360 | 0.0096941 | 0.0026929 | N
12/01/2017 | 09:42 | ZN12640:PA7 | URBAN | Third Party | Vehicle impact | 1 | 138 | 9.4969e-05 | 6.8884e-05 | N
12/01/2017 | 09:46 | ZN80:PA40 | URBAN | Third Party | Other | 1 | 314 | 0.00021615 | 6.8884e-05 | N
12/01/2017 | 22:00 | ZN1193:PA11 | URBAN | Third Party | Vehicle impact | 30 | 105 | 0.0021699 | 0.0020665 | N
13/01/2017 | 18:30 | ZN72:PA16 | URBAN | Third Party | Vehicle impact | 17 | 100 | 0.0011711 | 0.0011711 | N
16/01/2017 | 08:22 | ZN4545:PA4 | URBAN | Third Party | Unauthorised access | 6 | 470 | 0.0019426 | 0.00041332 | N
16/01/2017 | 16:21 | ZN35800:PA1 | URBAN | Third Party | Vehicle impact | 1 | 377 | 0.00025984 | 6.8886e-05 | N
17/01/2017 | 08:56 | ZN15002:PA6 | URBAN | Third Party | Other | 1,681 | 119 | 0.13783 | 0.1158 | N
17/01/2017 | 13:35 | ZN187:PA30 | URBAN | Third Party | Vehicle impact | 39 | 5 | 0.00013433 | 0.0026866 | N
18/01/2017 | 08:12 | ZN10996:PA10 | URBAN | Third Party | Other | 77 | 153 | 0.0081156 | 0.0053043 | N
18/01/2017 | 10:37 | ZN35900:PA23 | SHORT RURAL | Third Party | Other | 54 | 97 | 0.023555 | 0.024238 | N
19/01/2017 | 10:49 | ZN35600:PA19 | URBAN | Third Party | Vehicle impact | 1 | 190 | 0.00013093 | 6.8881e-05 | N
19/01/2017 | 10:55 | ZN35600:PA19 | URBAN | Third Party | Vehicle impact | 1 | 184 | 0.00012698 | 6.8881e-05 | N
20/01/2017 | 09:26 | ZN3425:PA39 | URBAN | Third Party | Other | 1 | 124 | 8.5345e-05 | 6.8882e-05 | N
20/01/2017 | 14:08 | ZN12610:PA7 | URBAN | Third Party | Vehicle impact | 72 | 517 | 0.025625 | 0.0049595 | N
21/01/2017 | 09:00 | ZN1193:PA15 | URBAN | Third Party | Vehicle impact | 108 | 372 | 0.027674 | 0.0074393 | N
22/01/2017 | 17:35 | ZN2400:PA11 | SHORT RURAL | Third Party | Vehicle impact | 1 | 265 | 0.0011885 | 0.00044881 | N
23/01/2017 | 10:58 | ZN10997:PA8 | URBAN | Third Party | Vehicle impact | 1 | 91 | 6.2763e-05 | 6.8882e-05 | N
23/01/2017 | 13:02 | ZN10994:PA4 | URBAN | Third Party | Vehicle impact | 1 | 88 | 6.0513e-05 | 6.8882e-05 | N
23/01/2017 | 18:08 | ZN3425:PA22 | URBAN | Third Party | Vehicle impact | 1 | 854 | 0.00058802 | 6.8882e-05 | N
24/01/2017 | 09:48 | 243:80081 | SHORT RURAL | Third Party | Vehicle impact | 1 | 236 | 0.001061 | 0.00044887 | N
27/01/2017 | 09:15 | ZN180:PA34 | URBAN | Third Party | Other | 700 | 72 | 0.034557 | 0.048212 | N
27/01/2017 | 12:55 | ZN15008:PA1 | URBAN | Third Party | Vehicle impact | 12 | 590 | 0.0048763 | 0.00082649 | N
28/01/2017 | 16:48 | ZN847:PA39 | URBAN | Third Party | Vehicle impact | 22 | 42 | 0.00063641 | 0.0015153 | N
30/01/2017 | 03:50 | ZN9550:PA28 | URBAN | Third Party | Vehicle impact | 51 | 55 | 0.0019144 | 0.0035126 | N
25/01/2017 | 09:05 | 526:34633 | SHORT RURAL | Third Party | Vehicle impact | 2 | 495 | 0.004444 | 0.00089779 | N
30/01/2017 | 16:32 | ZN35370:PA10 | SHORT RURAL | Third Party | Vehicle impact | 186 | 342 | 0.28552 | 0.083376 | N
31/01/2017 | 01:02 | ZN2835:PA23 | URBAN | Third Party | Vehicle impact | 1 | 447 | 0.000308 | 6.8876e-05 | N
31/01/2017 | 10:15 | ZN690:PA17 | URBAN | Third Party | Vehicle impact | 1 | 225 | 0.0001548 | 6.8876e-05 | N
31/01/2017 | 13:10 | ZN3155:PA22 | URBAN | Third Party | Dig-in | 23 | 410 | 0.006495 | 0.0015842 | N
02/02/2017 | 00:02 | ZN15006:PA16 | URBAN | Third Party | Other | 1 | 656 | 0.0004519 | 6.8866e-05 | N
02/02/2017 | 07:57 | ZN180:PA20 | URBAN | Third Party | Other | 1 | 92 | 6.354e-05 | 6.8866e-05 | N
03/02/2017 | 11:17 | ZN3288:PA43 44KLM | CBD | Third Party | Dig-in | 7 | 263 | 0.05922 | 0.022547 | N
04/02/2017 | 00:52 | ZN630:PA27 | URBAN | Third Party | Vehicle impact | 6 | 108 | 0.00044627 | 0.00041321 | N
06/02/2017 | 12:26 | 801:74121 | LONG RURAL | Third Party | Vehicle impact | 1 | 83 | 0.029606 | 0.035613 | N
06/02/2017 | 15:21 | ZN1850:PA9 | URBAN | Third Party | Other | 1 | 200 | 0.00013806 | 6.8873e-05 | N
07/02/2017 | 09:38 | ZN36800:PA32 | URBAN | Third Party | Dig-in | 83 | 261 | 0.014937 | 0.0057166 | N
07/02/2017 | 16:00 | ZN9550:PA36 | URBAN | Third Party | Vehicle impact | 1 | 329 | 0.00022667 | 6.8875e-05 | N
08/02/2017 | 08:53 | ZN195:PA28 | URBAN | Third Party | Dig-in | 1 | 306 | 0.00021087 | 6.8876e-05 | N
10/02/2017 | 10:04 | 813:89063 | SHORT RURAL | Third Party | Vehicle impact | 1 | 106 | 0.00047313 | 0.00044747 | N
10/02/2017 | 14:21 | ZN15015:PA15 | SHORT RURAL | Third Party | Other | 1 | 150 | 0.00066905 | 0.00044747 | N
10/02/2017 | 16:58 | ZN35800:PA22 | URBAN | Third Party | Vehicle impact | 15 | 142 | 0.0014672 | 0.0010332 | N
11/02/2017 | 11:13 | ZN630:PA3 | URBAN | Third Party | Vehicle impact | 3 | 207 | 0.00042776 | 0.00020665 | N
12/02/2017 | 07:38 | ZN2466:PA45 | URBAN | Third Party | Vehicle impact | 6 | 712 | 0.0029427 | 0.0004133 | N
12/02/2017 | 07:38 | ZN2835:PA15 | URBAN | Third Party | Vehicle impact | 51 | 712 | 0.025013 | 0.003513 | N
14/02/2017 | 10:50 | ZN2568:PA30 | URBAN | Third Party | Vehicle impact | 1 | 99 | 6.8455e-05 | 6.896e-05 | N
14/02/2017 | 11:11 | ZN2568:PA30 | URBAN | Third Party | Vehicle impact | 1 | 78 | 5.4065e-05 | 6.896e-05 | N
14/02/2017 | 11:51 | ZN2635:PA31 | URBAN | Third Party | Vehicle impact | 34 | 169 | 0.0039625 | 0.0023447 | N
15/02/2017 | 08:23 | ZN10997:PA12 | URBAN | Third Party | Other | 1 | 127 | 8.7418e-05 | 6.8905e-05 | N
16/02/2017 | 01:49 | ZN2568:PA17 | URBAN | Third Party | Vehicle impact | 47 | 1,076 | 0.034838 | 0.0032378 | N
16/02/2017 | 12:57 | ZN690:PA11 | URBAN | Third Party | Vehicle impact | 57 | 108 | 0.0042408 | 0.0039266 | N
16/02/2017 | 13:19 | ZN2602:PA36 | URBAN | Third Party | Vehicle impact | 24 | 65 | 0.001081 | 0.0016533 | N
16/02/2017 | 15:31 | ZN12660:PA6 | SHORT RURAL | Third Party | Vehicle impact | 1 | 438 | 0.0019577 | 0.0004466 | N
16/02/2017 | 15:41 | 516:48067 | SHORT RURAL | Third Party | Vehicle impact | 13 | 49 | 0.0028448 | 0.0058058 | N
17/02/2017 | 13:46 | ZN12650:PA17 | URBAN | Third Party | Other | 1 | 2,833 | 0.001952 | 6.889e-05 | Y
17/02/2017 | 16:17 | ZN15004:PA3 | URBAN | Third Party | Other | 1 | 660 | 0.00045443 | 6.889e-05 | Y
18/02/2017 | 16:49 | ZN35800:PA2 | SHORT RURAL | Third Party | Vehicle impact | 1 | 251 | 0.0011207 | 0.00044661 | N
19/02/2017 | 16:54 | ZN9245:PA3 | URBAN | Third Party | Vehicle impact | 4 | 536 | 0.001477 | 0.00027556 | N
20/02/2017 | 16:03 | ZN129:PA28 | URBAN | Third Party | Vehicle impact | 97 | 222 | 0.014835 | 0.0066823 | N
20/02/2017 | 16:06 | ZN15012:PA4 | URBAN | Third Party | Vehicle impact | 40 | 214 | 0.0058873 | 0.0027556 | N
21/02/2017 | 11:30 | ZN2568:PA32 | URBAN | Third Party | Vehicle impact | 1 | 359 | 0.00024733 | 6.8892e-05 | N
21/02/2017 | 13:57 | ZN35370:PA10 | SHORT RURAL | Third Party | Vehicle impact | 1 | 363 | 0.0016213 | 0.00044663 | N
22/02/2017 | 08:00 | ZN2635:PA52 | URBAN | Third Party | Vehicle impact | 1 | 779 | 0.00053689 | 6.8893e-05 | N
22/02/2017 | 11:22 | ZN9118:PA6 | URBAN | Third Party | Other | 1 | 187 | 0.00012897 | 6.8893e-05 | N
22/02/2017 | 13:23 | ZN2602:PA29 | URBAN | Third Party | Vehicle impact | 74 | 107 | 0.0054549 | 0.0050981 | N
22/02/2017 | 23:45 | ZN10997:PA12 | URBAN | Third Party | Vehicle impact | 35 | 320 | 0.007716 | 0.0024112 | N
23/02/2017 | 13:54 | ZN1673:PA19 | URBAN | Third Party | Dig-in | 482 | 60 | 0.019825 | 0.033202 | N
23/02/2017 | 14:01 | ZN187:PA26 | URBAN | Third Party | Dig-in | 2 | 149 | 0.00020527 | 0.00013777 | N
23/02/2017 | 14:01 | ZN187:PA30 | URBAN | Third Party | Dig-in | 2 | 149 | 0.00020527 | 0.00013777 | N
23/02/2017 | 14:01 | ZN187:PA7 | URBAN | Third Party | Dig-in | 1 | 149 | 0.00010264 | 6.8883e-05 | N
23/02/2017 | 14:01 | ZN5868:PA27 | URBAN | Third Party | Dig-in | 738 | 143 | 0.07272 | 0.050836 | N
23/02/2017 | 14:01 | ZN5868:PA30 | URBAN | Third Party | Dig-in | 11 | 137 | 0.0010381 | 0.00075772 | N
23/02/2017 | 14:01 | ZN5868:PA7 | URBAN | Third Party | Dig-in | 63 | 136 | 0.0059019 | 0.0043396 | N
24/02/2017 | 10:42 | ZN2602:PA30 | URBAN | Third Party | Vehicle impact | 1 | 198 | 0.00013627 | 6.8881e-05 | N
24/02/2017 | 23:09 | ZN690:PA36 | URBAN | Third Party | Vehicle impact | 1 | 283 | 0.00019473 | 6.8881e-05 | N
25/02/2017 | 14:28 | ZN1287:PA11 | URBAN | Third Party | Other | 23 | 97 | 0.0015304 | 0.0015842 | N
27/02/2017 | 04:16 | ZN129:PA24 | URBAN | Third Party | Vehicle impact | 16 | 254 | 0.0027992 | 0.0011021 | N
27/02/2017 | 11:51 | ZN2310:PA59 | URBAN | Third Party | Vehicle impact | 1 | 218 | 0.00015035 | 6.8879e-05 | N
01/03/2017 | 15:35 | ZN1285:PA24 | URBAN | Third Party | Dig-in | 1 | 412 | 0.00028411 | 6.888e-05 | N
01/03/2017 | 15:37 | ZN15010:PA1 | URBAN | Third Party | Other | 1 | 219 | 0.00015054 | 6.888e-05 | N
02/03/2017 | 01:24 | ZN3472:PA12 | URBAN | Third Party | Vehicle impact | 1 | 575 | 0.00039621 | 6.8881e-05 | N
02/03/2017 | 09:21 | ZN3472:PA12 | URBAN | Third Party | Vehicle impact | 1 | 99 | 6.7847e-05 | 6.8881e-05 | N
02/03/2017 | 13:34 | ZN3155:PA44 | URBAN | Third Party | Dig-in | 162 | 459 | 0.051243 | 0.011159 | N
02/03/2017 | 14:17 | 524:33570 | SHORT RURAL | Third Party | Vehicle impact | 120 | 128 | 0.068477 | 0.053596 | N
04/03/2017 | 16:55 | ZN8000:PA19 | URBAN | Third Party | Dig-in | 28 | 415 | 0.0080033 | 0.0019285 | N
05/03/2017 | 23:17 | ZN15004:PA5 | URBAN | Third Party | Other | 1 | 664 | 0.00045708 | 6.8877e-05 | N
06/03/2017 | 23:27 | ZN2466:PA5 | URBAN | Third Party | Vehicle impact | 82 | 723 | 0.040834 | 0.0056479 | N
07/03/2017 | 07:06 | ZN35800:PA18 | URBAN | Third Party | Vehicle impact | 9 | 99 | 0.00061371 | 0.00061991 | N
09/03/2017 | 08:40 | ZN2310:PA54 | URBAN | Third Party | Vehicle impact | 1 | 350 | 0.00024101 | 6.8889e-05 | N
09/03/2017 | 16:18 | 801:74118 | URBAN | Third Party | Other | 1 | 261 | 0.00017954 | 6.8889e-05 | N
10/03/2017 | 07:48 | ZN2635:PA46 | URBAN | Third Party | Vehicle impact | 27 | 412 | 0.0076634 | 0.0018601 | N
10/03/2017 | 10:25 | ZN167:PA20 | URBAN | Third Party | Vehicle impact | 17 | 145 | 0.0016982 | 0.0011711 | N
10/03/2017 | 10:25 | ZN167:PA1 | URBAN | Third Party | Vehicle impact | 4 | 205 | 0.00056491 | 0.00027556 | N
10/03/2017 | 11:00 | ZN35500:PA18 | SHORT RURAL | Third Party | Vehicle impact | 62 | 225 | 0.062028 | 0.027568 | N
10/03/2017 | 17:06 | ZN15008:PA7 | URBAN | Third Party | Vehicle impact | 1 | 27 | 1.8819e-05 | 6.8891e-05 | N
12/03/2017 | 04:11 | ZN2466:PA11 | URBAN | Third Party | Unauthorised access | 1 | 479 | 0.00032999 | 6.8892e-05 | N
12/03/2017 | 13:23 | ZN12630:PA1 | SHORT RURAL | Third Party | Other | 31 | 156 | 0.021521 | 0.013784 | N
14/03/2017 | 16:30 | ZN7900:PA23 | URBAN | Third Party | Dig-in | 34 | 440 | 0.010306 | 0.0023423 | N
15/03/2017 | 10:47 | ZN14892:PA6 | SHORT RURAL | Third Party | Other | 1 | 203 | 0.00090049 | 0.00044465 | N
15/03/2017 | 12:03 | ZN690:PA26 | URBAN | Third Party | Vehicle impact | 1 | 326 | 0.00022472 | 6.8892e-05 | N
15/03/2017 | 12:23 | ZN167:PA20 | URBAN | Third Party | Vehicle impact | 8 | 145 | 0.00079915 | 0.00055114 | N
15/03/2017 | 22:42 | ZN12620:PA7 | URBAN | Third Party | Vehicle impact | 1 | 257 | 0.00017706 | 6.8892e-05 | N
17/03/2017 | 09:53 | ZN7900:PA11 | URBAN | Third Party | Dig-in | 40 | 260 | 0.0071683 | 0.0027551 | N
17/03/2017 | 15:55 | ZN3472:PA17 | URBAN | Third Party | Vehicle impact | 1 | 270 | 0.00018573 | 6.8877e-05 | N
20/03/2017 | 11:59 | ZN3154:PA10 | URBAN | Third Party | Other | 36 | 101 | 0.0024978 | 0.0024796 | N
21/03/2017 | 16:49 | ZN1068:PA21 | URBAN | Third Party | Vehicle impact | 1 | 276 | 0.00018991 | 6.8879e-05 | N
21/03/2017 | 07:47 | ZN2568:PA29 | URBAN | Third Party | Vehicle impact | 1 | 237 | 0.0001633 | 6.8879e-05 | N
21/03/2017 | 07:50 | ZN2568:PA27 | URBAN | Third Party | Vehicle impact | 261 | 221 | 0.039668 | 0.017977 | N
21/03/2017 | 19:30 | 528:83013 | URBAN | Third Party | Other | 1,204 | 4 | 0.003291 | 0.082931 | N
23/03/2017 | 08:02 | ZN3472:PA27 | URBAN | Third Party | Vehicle impact | 1 | 237 | 0.00016335 | 6.8858e-05 | N
24/03/2017 | 04:51 | ZN1788:PA29 | SHORT RURAL | Third Party | Vehicle impact | 4 | 44 | 0.00078251 | 0.0017784 | N
24/03/2017 | 11:20 | ZN12650:PA2 | URBAN | Third Party | Vehicle impact | 1 | 279 | 0.00019245 | 6.8859e-05 | N
24/03/2017 | 13:01 | ZN9035:PA7 | URBAN | Third Party | Vehicle impact | 42 | 109 | 0.0031523 | 0.0028921 | N
24/03/2017 | 15:24 | ZN10990:PA12 | URBAN | Third Party | Vehicle impact | 871 | 108 | 0.064933 | 0.059976 | N
25/03/2017 | 15:37 | 222:33596 | URBAN | Third Party | Vehicle impact | 1 | 757 | 0.00052127 | 6.8855e-05 | N
27/03/2017 | 12:09 | ZN12610:PA6 | URBAN | Third Party | Vehicle impact | 1 | 501 | 0.00034478 | 6.8857e-05 | N
27/03/2017 | 14:05 | 801:74122 | URBAN | Third Party | Other | 18 | 25 | 0.00030986 | 0.0012394 | N
28/03/2017 | 05:40 | ZN8000:PA38 | URBAN | Third Party | Vehicle impact | 3 | 172 | 0.00035531 | 0.00020657 | N
28/03/2017 | 12:20 | ZN3672:PA42 | URBAN | Third Party | Other | 1 | 384 | 0.00026435 | 6.8858e-05 | N
31/03/2017 | 11:00 | ZN167:PA20 | URBAN | Third Party | Vehicle impact | 1 | 413 | 0.00028431 | 6.884e-05 | N
31/03/2017 | 11:00 | ZN167:PA21 | URBAN | Third Party | Vehicle impact | 10 | 360 | 0.0024782 | 0.0006884 | N
04/04/2017 | 03:05 | ZN1648:PA21 | URBAN | Third Party | Vehicle impact | 38 | 512 | 0.013387 | 0.0026147 | N
03/04/2017 | 13:30 | ZN180:PA24 | URBAN | Third Party | Vehicle impact | 30 | 90 | 0.0018578 | 0.0020642 | N
04/04/2017 | 17:14 | ZN10994:PA20 | URBAN | Third Party | Vehicle impact | 52 | 181 | 0.0064761 | 0.003578 | N
05/04/2017 | 09:33 | ZN3472:PA34 | URBAN | Third Party | Other | 65 | 122 | 0.0054534 | 0.0044724 | N
05/04/2017 | 12:11 | ZN2466:PA22 | URBAN | Third Party | Other | 2 | 1,544 | 0.0021248 | 0.00013761 | N
05/04/2017 | 16:00 | ZN36200:PA1 | URBAN | Third Party | Vehicle impact | 1 | 333 | 0.0002294 | 6.8807e-05 | N
06/04/2017 | 08:27 | ZN1287:PA17 | URBAN | Third Party | Vehicle impact | 1 | 152 | 0.00010464 | 6.8807e-05 | N
06/04/2017 | 14:15 | ZN342:PA22 | URBAN | Third Party | Vehicle impact | 1 | 225 | 0.00015467 | 6.8807e-05 | N
06/04/2017 | 14:16 | ZN342:PA22 | URBAN | Third Party | Vehicle impact | 1 | 223 | 0.00015368 | 6.8807e-05 | N
07/04/2017 | 22:54 | ZN874:PA4 | URBAN | Third Party | Vehicle impact | 21 | 226 | 0.0032707 | 0.0014472 | N
08/04/2017 | 10:52 | 235:2120 | SHORT RURAL | Third Party | Other | 1 | 268 | 0.0011917 | 0.00044534 | N
08/04/2017 | 12:10 | 232:11454 | SHORT RURAL | Third Party | Other | 1 | 380 | 0.0016912 | 0.00044534 | N
09/04/2017 | 04:40 | 222:33602 | URBAN | Third Party | Vehicle impact | 114 | 604 | 0.047324 | 0.0078409 | N
09/04/2017 | 12:16 | ZN1068:PA27 | URBAN | Third Party | Vehicle impact | 1 | 318 | 0.00021904 | 6.878e-05 | N
09/04/2017 | 18:07 | ZN10994:PA1 | URBAN | Third Party | Other | 1 | 413 | 0.00028405 | 6.878e-05 | N
09/04/2017 | 21:05 | ZN9245:PA19 | URBAN | Third Party | Other | 1 | 355 | 0.00024403 | 6.878e-05 | N
09/04/2017 | 22:04 | ZN12660:PA11 | URBAN | Third Party | Vehicle impact | 1 | 271 | 0.00018673 | 6.878e-05 | N
10/04/2017 | 12:28 | ZN180:PA23 | URBAN | Third Party | Vehicle impact | 1 | 425 | 0.00029201 | 6.878e-05 | N
11/04/2017 | 14:52 | ZN15002:PA8 | URBAN | Third Party | Vehicle impact | 1 | 346 | 0.00023813 | 6.878e-05 | N
12/04/2017 | 07:37 | ZN167:PA21 | URBAN | Third Party | Other | 10 | 278 | 0.0019123 | 0.00068787 | N
12/04/2017 | 09:51 | ZN10993:PA22 | URBAN | Third Party | Vehicle impact | 1 | 113 | 7.7878e-05 | 6.8787e-05 | N
12/04/2017 | 15:03 | ZN195:PA10 | SHORT RURAL | Third Party | Vehicle impact | 28 | 96 | 0.011935 | 0.012471 | N
13/04/2017 | 14:05 | ZN35800:PA15 | URBAN | Third Party | Vehicle impact | 1 | 84 | 5.7931e-05 | 6.8788e-05 | N
13/04/2017 | 13:53 | ZN35800:PA15 | URBAN | Third Party | Vehicle impact | 1 | 232 | 0.00015927 | 6.8788e-05 | N
15/04/2017 | 15:38 | 217:33611 | URBAN | Third Party | Vehicle impact | 23 | 29 | 0.00045867 | 0.0015816 | N
15/04/2017 | 23:30 | ZN35800:PA15 | URBAN | Third Party | Vehicle impact | 89 | 70 | 0.0042841 | 0.0061201 | N
16/04/2017 | 00:13 | 210:83465 | URBAN | Third Party | Vehicle impact | 700 | 144 | 0.069142 | 0.048136 | N
19/04/2017 | 08:57 | ZN12600:PA13 | SHORT RURAL | Third Party | Vehicle impact | 9 | 368 | 0.014748 | 0.0040076 | N
19/04/2017 | 10:28 | ZN847:PA15 | URBAN | Third Party | Vehicle impact | 18 | 107 | 0.0013245 | 0.0012379 | N
19/04/2017 | 09:15 | 243:80083 | SHORT RURAL | Third Party | Unauthorised access | 4 | 569 | 0.010135 | 0.0017811 | N
22/04/2017 | 05:42 | 256:80653 | URBAN | Third Party | Vehicle impact | 1 | 423 | 0.00029079 | 6.8775e-05 | N
24/04/2017 | 12:37 | ZN901:PA18 | URBAN | Third Party | Other | 1 | 202 | 0.00013918 | 6.8776e-05 | N
26/04/2017 | 09:23 | ZN80:PA32 | URBAN | Third Party | Vehicle impact | 2 | 247 | 0.0003395 | 0.00013755 | N
27/04/2017 | 02:50 | ZN1850:PA11 | URBAN | Third Party | Vehicle impact | 3 | 105 | 0.00021659 | 0.00020628 | N
27/04/2017 | 02:50 | ZN1850:PA11 | URBAN | Third Party | Vehicle impact | 1 | 105 | 7.2198e-05 | 6.876e-05 | N
27/04/2017 | 15:02 | ZN9700:PA11 | URBAN | Third Party | Dig-in | 1,948 | 89 | 0.119 | 0.13394 | N
27/04/2017 | 16:07 | ZN12570:PA34 | SHORT RURAL | Third Party | Other | 33 | 203 | 0.029738 | 0.014649 | N
27/04/2017 | 16:31 | ZN12580:PA12 | SHORT RURAL | Third Party | Vehicle impact | 1 | 29 | 0.00012807 | 0.00044391 | N
01/05/2017 | 10:35 | ZN10997:PA1 | URBAN | Third Party | Other | 1 | 272 | 0.0001869 | 6.8762e-05 | N
30/04/2017 | 23:58 | ZN10990:PA12 | URBAN | Third Party | Vehicle impact | 52 | 467 | 0.016698 | 0.0035756 | N
30/04/2017 | 23:58 | ZN10990:PA8 | URBAN | Third Party | Vehicle impact | 20 | 812 | 0.011167 | 0.0013752 | N
30/04/2017 | 23:58 | ZN10996:PA12 | URBAN | Third Party | Vehicle impact | 202 | 98 | 0.013597 | 0.01389 | N
01/05/2017 | 13:53 | ZN1788:PA14 | URBAN | Third Party | Vehicle impact | 1 | 171 | 0.00011776 | 6.8762e-05 | N
02/05/2017 | 06:16 | ZN3472:PA28 | URBAN | Third Party | Other | 75 | 79 | 0.0040743 | 0.0051573 | N
02/05/2017 | 09:27 | ZN195:PA30 | SHORT RURAL | Third Party | Dig-in | 38 | 204 | 0.034402 | 0.016868 | N
02/05/2017 | 10:01 | ZN1648:PA11 | URBAN | Third Party | Vehicle impact | 1 | 309 | 0.0002122 | 6.8765e-05 | N
02/05/2017 | 10:34 | ZN2602:PA27 | URBAN | Third Party | Dig-in | 1 | 26 | 1.7776e-05 | 6.8765e-05 | N
02/05/2017 | 11:22 | 202:34245 | URBAN | Third Party | Vehicle impact | 1 | 167 | 0.00011512 | 6.8765e-05 | N
02/05/2017 | 11:44 | ZN15001:PA3 | URBAN | Third Party | Vehicle impact | 47 | 51 | 0.0016483 | 0.0032319 | N
02/05/2017 | 18:55 | ZN35900:PA20 | URBAN | Third Party | Vehicle impact | 9 | 35 | 0.00021661 | 0.00061888 | N
03/05/2017 | 17:31 | ZN80:PA21 | URBAN | Third Party | Other | 1 | 246 | 0.00016894 | 6.8767e-05 | N
04/05/2017 | 12:47 | 507:80932 | SHORT RURAL | Third Party | Other | 110 | 93 | 0.045438 | 0.04882 | N
04/05/2017 | 15:12 | ZN3425:PA24 | URBAN | Third Party | Vehicle impact | 53 | 93 | 0.0033888 | 0.0036439 | N
05/05/2017 | 03:06 | ZN35400:PA56 | URBAN | Third Party | Other | 3 | 534 | 0.0011029 | 0.00020653 | N
06/05/2017 | 11:47 | ZN2310:PA71 | URBAN | Third Party | Vehicle impact | 17 | 173 | 0.0020222 | 0.0011689 | N
07/05/2017 | 09:50 | ZN15008:PA10 | URBAN | Third Party | Vehicle impact | 41 | 100 | 0.0028186 | 0.0028186 | N
07/05/2017 | 17:56 | ZN12630:PA8 | SHORT RURAL | Third Party | Vehicle impact | 19 | 174 | 0.014698 | 0.008447 | N
08/05/2017 | 13:51 | ZN262:PA34 | URBAN | Third Party | Vehicle impact | 6 | 133 | 0.00055025 | 0.00041248 | N
09/05/2017 | 06:06 | ZN129:PA28 | URBAN | Third Party | Vehicle impact | 106 | 454 | 0.033072 | 0.0072874 | N
09/05/2017 | 07:46 | ZN12570:PA37 | SHORT RURAL | Third Party | Other | 59 | 379 | 0.099413 | 0.02623 | N
10/05/2017 | 13:43 | 224:80331 | URBAN | Third Party | Vehicle impact | 1 | 615 | 0.00042282 | 6.875e-05 | N
10/05/2017 | 22:44 | ZN1290:PA11 | URBAN | Third Party | Other | 1 | 105 | 7.2405e-05 | 6.875e-05 | N
11/05/2017 | 12:58 | ZN15004:PA9 | URBAN | Third Party | Vehicle impact | 1 | 91 | 6.2713e-05 | 6.8802e-05 | N
11/05/2017 | 14:21 | ZN3155:PA23 | URBAN | Third Party | Dig-in | 1 | 128 | 8.817e-05 | 6.8802e-05 | N
13/05/2017 | 03:30 | ZN1673:PA21 | SHORT RURAL | Third Party | Vehicle impact | 26 | 150 | 0.01733 | 0.011554 | N
13/05/2017 | 14:43 | ZN167:PA1 | URBAN | Third Party | Vehicle impact | 43 | 267 | 0.0078915 | 0.0029556 | N
15/05/2017 | 10:15 | ZN10996:PA10 | URBAN | Third Party | Vehicle impact | 1 | 240 | 0.0001647 | 6.8735e-05 | N
16/05/2017 | 14:15 | ZN15004:PA3 | URBAN | Third Party | Vehicle impact | 64 | 73 | 0.0032113 | 0.0043991 | N
16/05/2017 | 14:02 | ZN12620:PA10 | SHORT RURAL | Third Party | Vehicle impact | 2 | 231 | 0.0020532 | 0.00088881 | N
16/05/2017 | 14:43 | ZN1193:PA12 | URBAN | Third Party | Vehicle impact | 1 | 77 | 5.2823e-05 | 6.8736e-05 | N
17/05/2017 | 10:59 | ZN35600:PA16 | URBAN | Third Party | Vehicle impact | 2 | 181 | 0.00024821 | 0.00013747 | N
18/05/2017 | 13:45 | 202:34232 | URBAN | Third Party | Vehicle impact | 2 | 10 | 1.3743e-05 | 0.00013743 | N
20/05/2017 | 00:38 | 264:81236 | SHORT RURAL | Third Party | Vehicle impact | 1 | 681 | 0.0030498 | 0.00044761 | N
20/05/2017 | 12:36 | ZN965:PA29 | URBAN | Third Party | Vehicle impact | 30 | 244 | 0.0050298 | 0.0020617 | N
20/05/2017 | 15:30 | 238:34151 | URBAN | Third Party | Vehicle impact | 12 | 125 | 0.0010308 | 0.00082467 | N
21/05/2017 | 15:20 | 258:80773 | URBAN | Third Party | Vehicle impact | 43 | 55 | 0.0016253 | 0.0029551 | N
22/05/2017 | 09:16 | ZN15001:PA6 | URBAN | Third Party | Vehicle impact | 17 | 444 | 0.0051872 | 0.0011683 | N
22/05/2017 | 13:11 | ZN36300:PA17 | URBAN | Third Party | Vehicle impact | 1 | 358 | 0.00024631 | 6.8723e-05 | N
22/05/2017 | 13:20 | ZN36300:PA17 | URBAN | Third Party | Vehicle impact | 1 | 349 | 0.00024012 | 6.8723e-05 | N
22/05/2017 | 13:53 | ZN36300:PA17 | URBAN | Third Party | Vehicle impact | 1 | 307 | 0.00021074 | 6.8723e-05 | N
22/05/2017 | 14:44 | ZN3155:PA34 | URBAN | Third Party | Dig-in | 41 | 136 | 0.0038315 | 0.0028176 | N
22/05/2017 | 16:18 | ZN36300:PA17 | URBAN | Third Party | Vehicle impact | 1 | 172 | 0.00011788 | 6.8723e-05 | N
23/05/2017 | 08:24 | ZN72:PA30 | URBAN | Third Party | Vehicle impact | 1 | 171 | 0.00011724 | 6.8723e-05 | N
23/05/2017 | 08:36 | 507:80922 | SHORT RURAL | Third Party | Other | 1 | 413 | 0.0018497 | 0.00044761 | N
23/05/2017 | 12:10 | ZN965:PA42 | URBAN | Third Party | Dig-in | 1 | 679 | 0.00046688 | 6.8723e-05 | N
24/05/2017 | 13:16 | ZN15014:PA14 | SHORT RURAL | Third Party | Other | 1 | 253 | 0.001133 | 0.00044761 | N
25/05/2017 | 09:31 | 256:80640 | URBAN | Third Party | Vehicle impact | 35 | 70 | 0.0016753 | 0.0024053 | N
25/05/2017 | 10:49 | ZN2196:PA25 | URBAN | Third Party | Vehicle impact | 1 | 491 | 0.00033726 | 6.8723e-05 | N
26/05/2017 | 04:16 | ZN2568:PA25 | URBAN | Third Party | Vehicle impact | 1 | 369 | 0.00025359 | 6.8723e-05 | Y
27/05/2017 | 22:05 | 524:33570 | SHORT RURAL | Third Party | Vehicle impact | 82 | 215 | 0.078913 | 0.036704 | N
29/05/2017 | 10:52 | ZN12630:PA8 | SHORT RURAL | Third Party | Dig-in | 1 | 488 | 0.0021831 | 0.00044761 | N
29/05/2017 | 15:35 | 532:83301 | URBAN | Third Party | Vehicle impact | 1 | 204 | 0.00014018 | 6.8723e-05 | N
31/05/2017 | 13:48 | 232:11454 | SHORT RURAL | Third Party | Vehicle impact | 1 | 161 | 0.00072273 | 0.0004476 | N
02/06/2017 | 11:32 | 511:29878 | SHORT RURAL | Third Party | Dig-in | 1 | 208 | 0.00093057 | 0.0004476 | N
02/06/2017 | 12:19 | ZN630:PA41 | URBAN | Third Party | Vehicle impact | 3 | 311 | 0.00064117 | 0.00020617 | N
03/06/2017 | 09:10 | ZN3154:PA19 | URBAN | Third Party | Vehicle impact | 9 | 276 | 0.001707 | 0.0006185 | N
05/06/2017 | 19:34 | ZN35800:PA9 | URBAN | Third Party | Vehicle impact | 119 | 170 | 0.01393 | 0.0081779 | N
05/06/2017 | 20:49 | ZN35800:PA2 | SHORT RURAL | Third Party | Vehicle impact | 172 | 95 | 0.073203 | 0.076988 | N
07/06/2017 | 03:50 | ZN2602:PA42 | URBAN | Third Party | Vehicle impact | 63 | 40 | 0.0017318 | 0.0043295 | N
07/06/2017 | 11:14 | ZN72:PA26 | URBAN | Third Party | Vehicle impact | 88 | 106 | 0.0064104 | 0.0060475 | N
07/06/2017 | 12:18 | ZN1068:PA22 | URBAN | Third Party | Vehicle impact | 1 | 161 | 0.0001108 | 6.8722e-05 | N
07/06/2017 | 13:57 | ZN2310:PA59 | URBAN | Third Party | Vehicle impact | 1 | 123 | 8.4264e-05 | 6.8722e-05 | N
07/06/2017 | 17:57 | ZN9035:PA4 | URBAN | Third Party | Vehicle impact | 1 | 316 | 0.00021726 | 6.8722e-05 | N
08/06/2017 | 02:27 | ZN1068:PA16 | URBAN | Third Party | Vehicle impact | 6 | 123 | 0.00050717 | 0.00041233 | N
11/06/2017 | 13:29 | ZN690:PA5 | URBAN | Third Party | Vehicle impact | 1 | 270 | 0.00018556 | 6.8722e-05 | N
14/06/2017 | 16:28 | ZN2568:PA40 | URBAN | Third Party | Other | 73 | 79 | 0.0039782 | 0.0050167 | N
16/06/2017 | 08:17 | ZN262:PA42 | URBAN | Third Party | Vehicle impact | 1 | 133 | 9.1388e-05 | 6.8722e-05 | N
23/06/2017 | 05:16 | ZN15006:PA12 | URBAN | Third Party | Vehicle impact | 27 | 171 | 0.0031738 | 0.0018533 | N
19/06/2017 | 08:23 | ZN9700:PA11 | URBAN | Third Party | Vehicle impact | 10 | 192 | 0.0013195 | 0.00068722 | N
20/06/2017 | 11:01 | ZN690:PA17 | URBAN | Third Party | Vehicle impact | 22 | 144 | 0.0021771 | 0.0015119 | N
20/06/2017 | 11:01 | ZN690:PA34 | URBAN | Third Party | Vehicle impact | 64 | 194 | 0.0085325 | 0.0043982 | N
20/06/2017 | 13:40 | ZN690:PA35 | URBAN | Third Party | Vehicle impact | 1 | 409 | 0.00028123 | 6.8722e-05 | N
22/06/2017 | 09:52 | ZN1673:PA6 | URBAN | Third Party | Vehicle impact | 37 | 87 | 0.0022126 | 0.0025427 | N
22/06/2017 | 14:24 | ZN12610:PA18 | URBAN | Third Party | Vehicle impact | 1 | 479 | 0.00032922 | 6.8722e-05 | N
22/06/2017 | 15:00 | ZN3155:PA22 | URBAN | Third Party | Dig-in | 23 | 315 | 0.0049789 | 0.0015806 | N
22/06/2017 | 23:02 | ZN2635:PA59 | URBAN | Third Party | Other | 1 | 48 | 3.2986e-05 | 6.8722e-05 | N
23/06/2017 | 14:02 | ZN1788:PA8 | URBAN | Third Party | Other | 1 | 148 | 0.00010145 | 6.8642e-05 | N
23/06/2017 | 14:48 | ZN630:PA14 | URBAN | Third Party | Other | 1 | 162 | 0.00011087 | 6.8642e-05 | N
24/06/2017 | 09:12 | 220:8687 | URBAN | Third Party | Vehicle impact | 1 | 240 | 0.0001646 | 6.8642e-05 | N
25/06/2017 | 03:39 | ZN1648:PA10 | URBAN | Third Party | Vehicle impact | 48 | 528 | 0.017397 | 0.0032948 | N
25/06/2017 | 11:13 | 508:82578 | SHORT RURAL | Third Party | Vehicle impact | 4 | 37 | 0.00066245 | 0.0017904 | N
25/06/2017 | 17:19 | ZN2568:PA14 | URBAN | Third Party | Other | 1 | 520 | 0.00035726 | 6.8642e-05 | N
26/06/2017 | 10:12 | ZN9245:PA10 | URBAN | Third Party | Vehicle impact | 64 | 128 | 0.0056188 | 0.0043931 | N
23/06/2017 | 17:00 | ZN262:PA7 | URBAN | Third Party | Dig-in | 1 | 50 | 3.4321e-05 | 6.8642e-05 | N
28/06/2017 | 11:12 | ZN2635:PA52 | URBAN | Third Party | Vehicle impact | 1 | 197 | 0.00013525 | 6.8642e-05 | N
29/06/2017 | 04:30 | 230:81434 | URBAN | Third Party | Vehicle impact | 66 | 255 | 0.011553 | 0.0045304 | N
29/06/2017 | 18:53 | 232:11454 | SHORT RURAL | Third Party | Vehicle impact | 3 | 267 | 0.0035853 | 0.0013428 | N
30/06/2017 | 14:50 | ZN14891:PA16 | SHORT RURAL | Third Party | Other | 139 | 150 | 0.093325 | 0.062217 | N
01/07/2016 | 12:59 | ZN262:PA17 | URBAN | Network business | Network error | 69 | 422 | 0.020166 | 0.0047788 | N
02/07/2016 | 07:19 | ZN195:PA25 | URBAN | Network business | Network error | 52 | 491 | 0.017683 | 0.0036015 | N
03/07/2016 | 18:18 | ZN10991:PA1 | URBAN | Network business | Network error | 22 | 152 | 0.002316 | 0.0015237 | N
03/07/2016 | 18:30 | ZN3154:PA10 | URBAN | Network business | Network error | 43 | 235 | 0.0069987 | 0.0029782 | N
04/07/2016 | 18:29 | ZN2196:PA25 | URBAN | Network business | Network error | 202 | 269 | 0.037587 | 0.01399 | N
04/07/2016 | 19:57 | ZN4545:PA28 | URBAN | Network business | Network error | 210 | 45 | 0.0065363 | 0.014545 | N
04/07/2016 | 20:59 | ZN35800:PA16 | URBAN | Network business | Network error | 62 | 391 | 0.016768 | 0.0042941 | N
03/07/2016 | 18:18 | ZN10991:PA1 | URBAN | Network business | Network error | 34 | 152 | 0.0035793 | 0.0023548 | N
05/07/2016 | 19:15 | ZN35800:PA6 | URBAN | Network business | Network error | 202 | 85 | 0.011919 | 0.01399 | N
06/07/2016 | 20:06 | ZN3155:PA20 | URBAN | Network business | Network error | 175 | 39 | 0.0047269 | 0.01212 | N
06/07/2016 | 20:06 | ZN3155:PA21 | URBAN | Network business | Network error | 107 | 39 | 0.0028902 | 0.0074107 | N
06/07/2016 | 20:06 | ZN3155:PA34 | URBAN | Network business | Network error | 164 | 39 | 0.0044298 | 0.011359 | N
11/07/2016 | 10:58 | ZN36300:PA9 | URBAN | Network business | Network error | 55 | 103 | 0.003923 | 0.0038088 | N
12/07/2016 | 21:01 | ZN35500:PA23 | URBAN | Network business | Network error | 1 | 520 | 0.00035999 | 6.9252e-05 | N
13/07/2016 | 13:50 | ZN9118:PA24 | URBAN | Network business | Network error | 14 | 20 | 0.00019391 | 0.00096956 | N
15/07/2016 | 18:46 | ZN9252:PA27 | URBAN | Network business | Network error | 40 | 1,019 | 0.028229 | 0.0027702 | N
16/07/2016 | 09:16 | ZN10991:PA1 | URBAN | Network business | Network error | 32 | 554 | 0.012275 | 0.0022158 | N
18/07/2016 | 19:40 | ZN2635:PA46 | URBAN | Network business | Network error | 45 | 147 | 0.0045804 | 0.0031159 | N
18/07/2016 | 20:00 | ZN8000:PA25 | URBAN | Network business | Network error | 17 | 95 | 0.0011183 | 0.0011771 | N
21/07/2016 | 11:23 | ZN10999:PA4 | URBAN | Network business | Network error | 39 | 63 | 0.0017131 | 0.0026999 | N
23/07/2016 | 16:25 | ZN3154:PA23 | URBAN | Network business | Network error | 27 | 31 | 0.00057202 | 0.0018693 | N
24/07/2016 | 18:40 | ZN35500:PA24 | URBAN | Network business | Network error | 24 | 110 | 0.0018278 | 0.0016616 | N
24/07/2016 | 18:40 | ZN4545:PA4 | URBAN | Network business | Network error | 40 | 212 | 0.005872 | 0.0027694 | N
25/07/2016 | 10:49 | ZN2568:PA30 | URBAN | Network business | Network error | 3 | 276 | 0.00057327 | 0.0002077 | N
25/07/2016 | 10:49 | ZN630:PA40 | URBAN | Network business | Network error | 16 | 266 | 0.0029431 | 0.0011078 | N
25/07/2016 | 18:46 | ZN1193:PA27 | URBAN | Network business | Network error | 65 | 257 | 0.011552 | 0.0045003 | N
26/07/2016 | 18:54 | ZN9118:PA7 | URBAN | Network business | Network error | 68 | 276 | 0.012994 | 0.004708 | N
26/07/2016 | 19:39 | ZN36100:PA15 | URBAN | Network business | Network error | 71 | 111 | 0.0054564 | 0.0049157 | N
26/07/2016 | 19:39 | ZN36100:PA7 | URBAN | Network business | Network error | 125 | 111 | 0.0096064 | 0.0086544 | N
27/07/2016 | 12:43 | ZN15008:PA9 | URBAN | Network business | Network error | 79 | 62 | 0.0033912 | 0.0054697 | N
29/07/2016 | 09:00 | 265:81651 | SHORT RURAL | Network business | Network error | 10 | 12 | 0.00054444 | 0.004537 | N
01/08/2016 | 10:28 | 502:48010 | SHORT RURAL | Network business | Network error | 861 | 2 | 0.0078126 | 0.39063 | N
09/08/2016 | 08:30 | 264:81244 | SHORT RURAL | Network business | Network error | 56 | 120 | 0.030651 | 0.025542 | N
09/08/2016 | 18:15 | ZN3155:PA24 | URBAN | Network business | Network error | 9 | 195 | 0.0012141 | 0.00062259 | N
10/08/2016 | 19:27 | ZN965:PA29 | URBAN | Network business | Network error | 28 | 117 | 0.0022724 | 0.001937 | N
17/08/2016 | 09:18 | 240:34835 | SHORT RURAL | Network business | Network error | 84 | 20 | 0.0074952 | 0.038306 | N
17/08/2016 | 21:09 | ZN35600:PA16 | URBAN | Network business | Network error | 166 | 156 | 0.01791 | 0.011481 | N
18/08/2016 | 17:34 | ZN10994:PA12 | URBAN | Network business | Network error | 50 | 271 | 0.0094008 | 0.0034689 | N
18/08/2016 | 17:34 | ZN10994:PA2 | URBAN | Network business | Network error | 1 | 271 | 0.00018787 | 6.9379e-05 | N
19/08/2016 | 17:21 | 813:89061 | LONG RURAL | Network business | Switching and protection error | 6 | 79 | 0.16904 | 0.21398 | N
21/08/2016 | 18:58 | ZN10991:PA8 | URBAN | Network business | Network error | 83 | 162 | 0.0093288 | 0.0057585 | N
24/08/2016 | 15:40 | ZN14891:PA14 | URBAN | Network business | Network error | 24 | 30 | 0.00049746 | 0.0016582 | N
25/08/2016 | 10:44 | ZN1193:PA17 | URBAN | Network business | Network error | 66 | 221 | 0.010078 | 0.0045602 | N
25/08/2016 | 10:44 | ZN1193:PA28 | URBAN | Network business | Network error | 44 | 221 | 0.0067187 | 0.0030402 | N
26/08/2016 | 11:31 | ZN690:PA14 | URBAN | Network business | Network error | 1 | 270 | 0.00018635 | 6.9094e-05 | N
27/08/2016 | 09:30 | ZN965:PA38 | URBAN | Network business | Network error | 99 | 175 | 0.011965 | 0.0068369 | N
30/08/2016 | 18:09 | ZN690:PA30 | URBAN | Network business | Network error | 29 | 279 | 0.0055878 | 0.0020028 | N
31/08/2016 | 06:36 | ZN847:PA46 | URBAN | Network business | Network error | 85 | 189 | 0.011091 | 0.0058683 | N
04/09/2016 | 19:37 | ZN9037:PA9 | URBAN | Network business | Network error | 25 | 243 | 0.0041943 | 0.001726 | N
06/09/2016 | 12:10 | ZN3155:PA20 | URBAN | Network business | Network error | 77 | 80 | 0.004253 | 0.0053163 | N
03/09/2016 | 12:14 | ZN180:PA27 | URBAN | Network business | Network error | 47 | 211 | 0.0068468 | 0.0032449 | N
12/09/2016 | 10:35 | ZN10993:PA33 | URBAN | Network business | Switching and protection error | 74 | 70 | 0.0035774 | 0.0051106 | N
12/09/2016 | 11:12 | ZN10993:PA23 | URBAN | Network business | Switching and protection error | 25 | 33 | 0.0005689 | 0.0017265 | N
25/09/2016 | 10:45 | ZN262:PA39 | URBAN | Network business | Network error | 42 | 890 | 0.025809 | 0.0028999 | N
30/09/2016 | 08:45 | 813:89065 | URBAN | Network business | Switching and protection error | 29 | 20 | 0.00040036 | 0.0020018 | N
10/10/2016 | 01:18 | ZN1287:PA12 | URBAN | Network business | Network error | 41 | 50 | 0.0014163 | 0.0028325 | N
10/10/2016 | 01:24 | ZN1287:PA4 | URBAN | Network business | Network error | 41 | 51 | 0.0014446 | 0.0028325 | N
11/10/2016 | 12:45 | ZN35500:PA28 | URBAN | Network business | Network error | 38 | 165 | 0.0043292 | 0.0026238 | N
13/10/2016 | 13:39 | 806:82662 | SHORT RURAL | Network business | Network error | 1 | 200 | 0.00090421 | 0.00045199 | N
18/10/2016 | 09:58 | ZN2835:PA22 | URBAN | Network business | Network error | 12 | 97 | 0.00080277 | 0.00082888 | N
17/10/2016 | 21:00 | 239:82127 | SHORT RURAL | Network business | Network error | 7 | 708 | 0.022322 | 0.0031529 | N
18/10/2016 | 08:00 | 528:83019 | SHORT RURAL | Network business | Switching and protection error | 3 | 590 | 0.0079722 | 0.0013512 | N
20/10/2016 | 20:35 | ZN35500:PA27 | URBAN | Network business | Network error | 1 | 539 | 0.000372 | 6.9078e-05 | N
20/10/2016 | 22:35 | 532:83307 | SHORT RURAL | Network business | Switching and protection error | 77 | 40 | 0.013873 | 0.034682 | N
24/10/2016 | 03:32 | ZN9035:PA7 | URBAN | Network business | Network error | 43 | 508 | 0.015085 | 0.0029695 | N
24/10/2016 | 03:32 | ZN9118:PA13 | URBAN | Network business | Network error | 97 | 508 | 0.034029 | 0.0066986 | N
24/10/2016 | 06:45 | ZN12630:PA13 | SHORT RURAL | Network business | Switching and protection error | 466 | 6 | 0.012588 | 0.20981 | N
24/10/2016 | 06:45 | ZN12630:PA22 | SHORT RURAL | Network business | Switching and protection error | 565 | 6 | 0.015263 | 0.25438 | N
24/10/2016 | 06:45 | ZN12630:PA23 | SHORT RURAL | Network business | Switching and protection error | 414 | 6 | 0.011184 | 0.1864 | N
24/10/2016 | 06:45 | ZN12630:PA24 | SHORT RURAL | Network business | Switching and protection error | 322 | 6 | 0.0086985 | 0.14497 | N
24/10/2016 | 06:45 | ZN12630:PA25 | SHORT RURAL | Network business | Switching and protection error | 244 | 6 | 0.0065914 | 0.10986 | N
27/10/2016 | 14:01 | 507:80932 | SHORT RURAL | Network business | Switching and protection error | 4 | 74 | 0.0013323 | 0.0018005 | N
31/10/2016 | 08:45 | ZN2310:PA53 | URBAN | Network business | Switching and protection error | 30 | 58 | 0.0012013 | 0.0020712 | N
28/10/2016 | 06:19 | ZN12630:PA13 | SHORT RURAL | Network business | Switching and protection error | 466 | 3 | 0.0062926 | 0.20975 | N
28/10/2016 | 06:19 | ZN12630:PA22 | SHORT RURAL | Network business | Switching and protection error | 564 | 3 | 0.007616 | 0.25387 | N
28/10/2016 | 06:19 | ZN12630:PA23 | SHORT RURAL | Network business | Switching and protection error | 414 | 3 | 0.0055904 | 0.18635 | N
28/10/2016 | 06:19 | ZN12630:PA24 | SHORT RURAL | Network business | Switching and protection error | 322 | 3 | 0.0043481 | 0.14494 | N
28/10/2016 | 06:19 | ZN12630:PA25 | SHORT RURAL | Network business | Switching and protection error | 244 | 3 | 0.0032948 | 0.10983 | N
04/11/2016 | 09:30 | 264:81240 | SHORT RURAL | Network business | Switching and protection error | 10 | 530 | 0.023849 | 0.0044998 | N
09/11/2016 | 05:20 | 261:81882 | URBAN | Network business | Switching and protection error | 68 | 100 | 0.0046792 | 0.0046941 | N
11/11/2016 | 14:15 | 513:48052 | URBAN | Network business | Network error | 16 | 5 | 5.5226e-05 | 0.0011045 | N
17/11/2016 | 13:03 | ZN1068:PA21 | URBAN | Network business | Network error | 74 | 46 | 0.0023519 | 0.0051053 | N
18/11/2016 | 14:42 | 528:83019 | SHORT RURAL | Network business | Switching and protection error | 21 | 123 | 0.011614 | 0.0094426 | N
19/11/2016 | 23:19 | ZN3922:PA13 | SHORT RURAL | Network business | Network error | 4 | 134 | 0.0024101 | 0.0017986 | N
19/11/2016 | 23:19 | ZN3922:PA29 | URBAN | Network business | Network error | 81 | 134 | 0.0074783 | 0.0055884 | N
21/11/2016 | 00:19 | ZN342:PA33 | URBAN | Network business | Network error | 579 | 66 | 0.026366 | 0.039948 | N
18/11/2016 | 11:34 | ZN14891:PA16 | SHORT RURAL | Network business | Switching and protection error | 1,777 | 3 | 0.023971 | 0.79902 | N
18/11/2016 | 11:34 | ZN14891:PA21 | SHORT RURAL | Network business | Switching and protection error | 311 | 3 | 0.0041952 | 0.13984 | N
21/11/2016 | 16:18 | ZN2602:PA35 | URBAN | Network business | Network error | 18 | 177 | 0.0021982 | 0.0012419 | N
21/11/2016 | 16:50 | ZN3472:PA30 | URBAN | Network business | Network error | 252 | 153 | 0.026563 | 0.017387 | N
21/11/2016 | 16:50 | ZN35900:PA17 | URBAN | Network business | Network error | 97 | 105 | 0.0070271 | 0.0066925 | N
22/11/2016 | 07:46 | ZN3472:PA22 | URBAN | Network business | Network error | 899 | 4 | 0.0024811 | 0.062027 | N
22/11/2016 | 07:46 | ZN3472:PA29 | URBAN | Network business | Network error | 690 | 4 | 0.0019043 | 0.047607 | N
23/11/2016 | 09:33 | ZN9037:PA2 | URBAN | Network business | Switching and protection error | 35 | 36 | 0.00087662 | 0.0024149 | N
23/11/2016 | 09:50 | ZN14892:PA9 | URBAN | Network business | Switching and protection error | 700 | 32 | 0.015455 | 0.048298 | N
23/11/2016 | 12:50 | ZN15001:PA2 | URBAN | Network business | Network error | 24 | 227 | 0.003759 | 0.0016559 | N
24/11/2016 | 13:35 | ZN9118:PA3 | SHORT RURAL | Network business | Network error | 77 | 164 | 0.056884 | 0.034608 | N
26/11/2016 | 12:22 | ZN10990:PA11 | URBAN | Network business | Network error | 53 | 68 | 0.0024878 | 0.0036585 | N
28/11/2016 | 19:00 | 528:83022 | URBAN | Network business | Switching and protection error | 22 | 300 | 0.0045559 | 0.0015186 | N
05/12/2016 | 09:26 | 806:82662 | SHORT RURAL | Network business | Switching and protection error | 227 | 5 | 0.0050992 | 0.10198 | N
05/12/2016 | 09:26 | 806:82667 | SHORT RURAL | Network business | Switching and protection error | 40 | 5 | 0.00089855 | 0.017971 | N
05/12/2016 | 17:55 | ZN35900:PA4 | SHORT RURAL | Network business | Switching and protection error | 1 | 170 | 0.00076376 | 0.00044927 | N
05/12/2016 | 17:17 | ZN129:PA28 | URBAN | Network business | Network error | 100 | 353 | 0.024343 | 0.0068959 | N
13/12/2016 | 18:46 | ZN2466:PA20 | URBAN | Network business | Switching and protection error | 10 | 10 | 6.8942e-05 | 0.00068942 | N
13/12/2016 | 18:05 | ZN4545:PA17 | URBAN | Network business | Network error | 33 | 130 | 0.0029576 | 0.0022751 | N
13/12/2016 | 18:05 | ZN4545:PA19 | URBAN | Network business | Network error | 154 | 99 | 0.010511 | 0.010617 | N
13/12/2016 | 18:05 | ZN4545:PA21 | URBAN | Network business | Network error | 35 | 99 | 0.0023888 | 0.002413 | N
13/12/2016 | 18:05 | ZN129:PA16 | URBAN | Network business | Network error | 143 | 205 | 0.02021 | 0.0098587 | N
13/12/2016 | 18:05 | ZN129:PA3 | URBAN | Network business | Network error | 2 | 205 | 0.00028266 | 0.00013788 | N
13/12/2016 | 18:05 | ZN129:PA8 | URBAN | Network business | Network error | 66 | 205 | 0.0093127 | 0.0045502 | N
13/12/2016 | 19:04 | ZN9252:PA27 | URBAN | Network business | Network error | 31 | 245 | 0.0052362 | 0.0021372 | N
13/12/2016 | 19:24 | ZN9037:PA2 | URBAN | Network business | Network error | 36 | 306 | 0.0075947 | 0.0024819 | N
13/12/2016 | 20:54 | ZN874:PA18 | URBAN | Network business | Network error | 77 | 206 | 0.010936 | 0.0053085 | N
14/12/2016 | 16:37 | ZN35900:PA23 | SHORT RURAL | Network business | Network error | 47 | 323 | 0.068218 | 0.02112 | N
14/12/2016 | 17:05 | ZN195:PA11 | URBAN | Network business | Network error | 1 | 170 | 0.00011742 | 6.8943e-05 | N
14/12/2016 | 20:20 | ZN9550:PA4 | URBAN | Network business | Network error | 162 | 172 | 0.019221 | 0.011169 | N
17/12/2016 | 13:10 | ZN35400:PA110 | URBAN | Network business | Network error | 95 | 490 | 0.032085 | 0.006548 | N
17/12/2016 | 13:10 | ZN35400:PA73 | URBAN | Network business | Network error | 2 | 491 | 0.00067624 | 0.00013785 | N
17/12/2016 | 13:10 | ZN35400:PA97 | URBAN | Network business | Network error | 1 | 491 | 0.00033812 | 6.8927e-05 | N
18/12/2016 | 10:59 | ZN116:PA84 | URBAN | Network business | Network error | 4 | 312 | 0.0008602 | 0.00027571 | N
18/12/2016 | 10:40 | ZN116:PA87 | URBAN | Network business | Network error | 6 | 330 | 0.0013647 | 0.00041356 | N
19/12/2016 | 16:07 | ZN1287:PA21 | URBAN | Network business | Network error | 65 | 42 | 0.0018817 | 0.0044803 | N
14/12/2016 | 16:37 | ZN35900:PA24 | URBAN | Network business | Network error | 71 | 323 | 0.015811 | 0.004895 | N
24/12/2016 | 10:23 | ZN384:PA22 | URBAN | Network business | Network error | 143 | 72 | 0.0070832 | 0.0098538 | N
24/12/2016 | 10:23 | ZN711:PA21 | URBAN | Network business | Network error | 143 | 72 | 0.0070947 | 0.0098538 | N
29/12/2016 | 14:26 | ZN2196:PA25 | URBAN | Network business | Network error | 39 | 214 | 0.0057512 | 0.0026875 | N
30/12/2016 | 09:14 | ZN1850:PA8 | URBAN | Network business | Network error | 1 | 416 | 0.00028635 | 6.891e-05 | N
30/12/2016 | 12:02 | 242:81541 | URBAN | Network business | Network error | 65 | 623 | 0.027905 | 0.0044792 | N
03/01/2017 | 09:24 | ZN1193:PA15 | URBAN | Network business | Network error | 50 | 60 | 0.0020708 | 0.0034456 | N
03/01/2017 | 19:32 | ZN1673:PA7 | URBAN | Network business | Network error | 28 | 64 | 0.0012349 | 0.0019295 | N
03/01/2017 | 19:32 | ZN1673:PA7 | URBAN | Network business | Network error | 34 | 64 | 0.0014995 | 0.002343 | N
10/01/2017 | 21:19 | ZN116:PA83 | URBAN | Network business | Network error | 86 | 826 | 0.048939 | 0.0059248 | N
11/01/2017 | 09:53 | ZN1287:PA4 | URBAN | Network business | Network error | 50 | 521 | 0.017947 | 0.0034447 | N
11/01/2017 | 11:23 | ZN35500:PA27 | URBAN | Network business | Network error | 1 | 561 | 0.00038631 | 6.8894e-05 | N
11/01/2017 | 13:07 | ZN2635:PA52 | URBAN | Network business | Network error | 54 | 376 | 0.013988 | 0.0037203 | N
11/01/2017 | 13:13 | ZN167:PA12 | URBAN | Network business | Network error | 57 | 187 | 0.0073434 | 0.003927 | N
11/01/2017 | 13:13 | ZN167:PA20 | URBAN | Network business | Network error | 6 | 187 | 0.00077182 | 0.00041336 | N
11/01/2017 | 22:24 | ZN129:PA9 | URBAN | Network business | Network error | 105 | 50 | 0.0036447 | 0.0072339 | N
12/01/2017 | 08:59 | ZN2196:PA18 | URBAN | Network business | Network error | 1 | 685 | 0.00047217 | 6.8884e-05 | N
12/01/2017 | 11:20 | ZN2835:PA16 | URBAN | Network business | Network error | 130 | 445 | 0.03985 | 0.008955 | N
12/01/2017 | 11:20 | ZN2835:PA28 | URBAN | Network business | Network error | 103 | 190 | 0.013481 | 0.0070951 | N
12/01/2017 | 11:20 | ZN2835:PA36 | URBAN | Network business | Network error | 25 | 150 | 0.0025832 | 0.0017221 | N
12/01/2017 | 15:37 | ZN10999:PA16 | URBAN | Network business | Network error | 1,409 | 9 | 0.0087352 | 0.097058 | N
12/01/2017 | 15:37 | ZN10999:PA39 | URBAN | Network business | Network error | 846 | 10 | 0.0058276 | 0.058276 | N
13/01/2017 | 15:44 | ZN35500:PA32 | URBAN | Network business | Network error | 143 | 128 | 0.012599 | 0.0098507 | N
13/01/2017 | 18:39 | ZN10994:PA7 | URBAN | Network business | Network error | 34 | 322 | 0.0075416 | 0.0023421 | N
13/01/2017 | 19:22 | ZN129:PA18 | URBAN | Network business | Network error | 51 | 23 | 0.0007969 | 0.0035132 | N
13/01/2017 | 19:22 | ZN129:PA4 | URBAN | Network business | Network error | 66 | 63 | 0.0028643 | 0.0045465 | N
13/01/2017 | 19:45 | ZN2635:PA58 | URBAN | Network business | Network error | 128 | 215 | 0.018954 | 0.0088174 | N
13/01/2017 | 20:14 | ZN2635:PA31 | URBAN | Network business | Network error | 78 | 171 | 0.0091827 | 0.0053731 | N
14/01/2017 | 15:34 | ZN195:PA11 | URBAN | Network business | Network error | 46 | 161 | 0.0051017 | 0.0031687 | N
13/01/2017 | 22:15 | ZN10991:PA13 | URBAN | Network business | Network error | 84 | 45 | 0.0026039 | 0.0057864 | N
11/01/2017 | 22:24 | ZN129:PA9 | URBAN | Network business | Network error | 25 | 51 | 0.0008784 | 0.0017224 | N
11/01/2017 | 22:24 | ZN129:PA9 | URBAN | Network business | Network error | 63 | 51 | 0.0022136 | 0.0043403 | N
13/01/2017 | 19:13 | ZN2635:PA52 | URBAN | Network business | Network error | 46 | 317 | 0.010045 | 0.0031687 | N
17/01/2017 | 17:31 | ZN10991:PA12 | URBAN | Network business | Network error | 93 | 404 | 0.025876 | 0.0064064 | N
17/01/2017 | 17:50 | ZN35500:PA23 | URBAN | Network business | Network error | 71 | 1,067 | 0.052186 | 0.0048909 | N
17/01/2017 | 18:14 | ZN15005:PA12 | URBAN | Network business | Network error | 47 | 181 | 0.0058602 | 0.0032377 | N
17/01/2017 | 18:14 | ZN15005:PA8 | URBAN | Network business | Network error | 52 | 166 | 0.0059308 | 0.0035821 | N
17/01/2017 | 18:18 | ZN35800:PA15 | URBAN | Network business | Network error | 55 | 522 | 0.019777 | 0.0037888 | N
17/01/2017 | 19:05 | ZN2196:PA9 | URBAN | Network business | Network error | 165 | 360 | 0.040917 | 0.011366 | N
17/01/2017 | 20:37 | ZN874:PA2 | URBAN | Network business | Network error | 47 | 222 | 0.0071768 | 0.0032377 | N
17/01/2017 | 20:37 | ZN874:PA8 | URBAN | Network business | Network error | 62 | 246 | 0.010508 | 0.004271 | N
18/01/2017 | 06:56 | ZN7481:PA17 | URBAN | Network business | Network error | 112 | 64 | 0.0049378 | 0.0077153 | N
18/01/2017 | 07:13 | ZN7481:PA1 | URBAN | Network business | Network error | 82 | 37 | 0.00209 | 0.0056487 | N
18/01/2017 | 20:39 | 513:48052 | URBAN | Network business | Network error | 1 | 747 | 0.00051445 | 6.8887e-05 | N
19/01/2017 | 08:57 | ZN180:PA21 | URBAN | Network business | Network error | 12 | 87 | 0.00071912 | 0.00082658 | N
20/01/2017 | 15:07 | ZN180:PA20 | URBAN | Network business | Network error | 73 | 112 | 0.0056469 | 0.0050284 | N
20/01/2017 | 15:07 | ZN180:PA33 | URBAN | Network business | Network error | 33 | 113 | 0.0025686 | 0.0022731 | N
20/01/2017 | 15:07 | ZN180:PA35 | URBAN | Network business | Network error | 103 | 53 | 0.0037603 | 0.0070949 | N
23/01/2017 | 12:29 | 233:82819 | SHORT RURAL | Network business | Switching and protection error | 1 | 31 | 0.00013915 | 0.00044886 | N
24/01/2017 | 14:55 | ZN1287:PA17 | URBAN | Network business | Network error | 138 | 72 | 0.0068438 | 0.0095059 | N
28/01/2017 | 15:56 | ZN847:PA44 | URBAN | Network business | Network error | 76 | 214 | 0.011202 | 0.0052345 | N
30/01/2017 | 13:25 | ZN9245:PA21 | URBAN | Network business | Network error | 60 | 335 | 0.013844 | 0.0041325 | N
30/01/2017 | 14:28 | ZN35800:PA16 | URBAN | Network business | Network error | 59 | 328 | 0.013329 | 0.0040636 | N
30/01/2017 | 16:40 | ZN129:PA27 | URBAN | Network business | Network error | 56 | 230 | 0.0088711 | 0.003857 | N
30/01/2017 | 16:40 | ZN129:PA28 | URBAN | Network business | Network error | 93 | 140 | 0.0089675 | 0.0064054 | N
30/01/2017 | 16:40 | ZN129:PA9 | URBAN | Network business | Network error | 50 | 200 | 0.0068875 | 0.0034438 | N
30/01/2017 | 17:55 | ZN1285:PA31 | URBAN | Network business | Network error | 54 | 545 | 0.02027 | 0.0037193 | N
30/01/2017 | 18:14 | ZN35500:PA23 | URBAN | Network business | Network error | 90 | 278 | 0.017229 | 0.0061988 | N
30/01/2017 | 18:14 | ZN35500:PA31 | URBAN | Network business | Network error | 52 | 266 | 0.0095268 | 0.0035815 | N
30/01/2017 | 18:46 | ZN9245:PA3 | URBAN | Network business | Network error | 66 | 64 | 0.0029093 | 0.0045458 | N
30/01/2017 | 18:46 | ZN9245:PA9 | URBAN | Network business | Network error | 53 | 64 | 0.002335 | 0.0036504 | N
30/01/2017 | 20:40 | ZN35900:PA20 | URBAN | Network business | Network error | 50 | 320 | 0.01102 | 0.0034438 | N
30/01/2017 | 19:43 | ZN2635:PA58 | URBAN | Network business | Network error | 70 | 61 | 0.0029506 | 0.0048213 | N
30/01/2017 | 20:40 | ZN35900:PA1 | URBAN | Network business | Network error | 75 | 320 | 0.016521 | 0.0051656 | N
30/01/2017 | 21:37 | ZN8000:PA4 | URBAN | Network business | Network error | 184 | 187 | 0.023677 | 0.012673 | N
30/01/2017 | 20:40 | ZN35900:PA20 | URBAN | Network business | Network error | 49 | 320 | 0.0108 | 0.0033749 | N
30/01/2017 | 22:29 | ZN35900:PA20 | URBAN | Network business | Network error | 76 | 224 | 0.01171 | 0.0052345 | N
01/02/2017 | 06:37 | ZN965:PA2 | URBAN | Network business | Network error | 33 | 128 | 0.0029052 | 0.0022729 | N
01/02/2017 | 08:30 | ZN12640:PA10 | URBAN | Network business | Switching and protection error | 169 | 45 | 0.0052381 | 0.01164 | N
02/02/2017 | 13:49 | ZN180:PA29 | URBAN | Network business | Switching and protection error | 1,189 | 2 | 0.0016376 | 0.081881 | N
04/02/2017 | 13:44 | ZN3154:PA18 | URBAN | Network business | Network error | 37 | 276 | 0.0070329 | 0.0025482 | N
04/02/2017 | 16:51 | ZN15005:PA4 | URBAN | Network business | Network error | 112 | 109 | 0.0084075 | 0.0077133 | N
04/02/2017 | 18:27 | ZN1068:PA17 | URBAN | Network business | Network error | 74 | 368 | 0.018754 | 0.0050963 | N
04/02/2017 | 18:34 | ZN1068:PA26 | URBAN | Network business | Network error | 96 | 96 | 0.0063249 | 0.0066114 | N
04/02/2017 | 18:39 | ZN1068:PA26 | URBAN | Network business | Network error | 69 | 166 | 0.0078859 | 0.004752 | N
04/02/2017 | 18:39 | ZN1068:PA22 | URBAN | Network business | Switching and protection error | 81 | 166 | 0.0092601 | 0.0055784 | N
05/02/2017 | 12:21 | ZN1068:PA26 | URBAN | Network business | Network error | 69 | 238 | 0.011327 | 0.0047523 | N
05/02/2017 | 12:52 | ZN1068:PA26 | URBAN | Network business | Network error | 96 | 208 | 0.013738 | 0.0066119 | N
05/02/2017 | 16:50 | ZN35800:PA15 | URBAN | Network business | Network error | 68 | 961 | 0.045011 | 0.0046834 | N
05/02/2017 | 16:54 | ZN2835:PA27 | URBAN | Network business | Network error | 153 | 1,026 | 0.10812 | 0.010538 | N
05/02/2017 | 16:54 | ZN874:PA18 | URBAN | Network business | Network error | 1 | 1,026 | 0.00070664 | 6.8873e-05 | N
05/02/2017 | 17:28 | ZN35900:PA1 | URBAN | Network business | Network error | 148 | 452 | 0.046074 | 0.010193 | N
05/02/2017 | 17:28 | ZN35900:PA20 | URBAN | Network business | Network error | 99 | 452 | 0.030819 | 0.0068185 | N
05/02/2017 | 17:48 | ZN129:PA24 | URBAN | Network business | Network error | 82 | 142 | 0.0080196 | 0.0056476 | N
05/02/2017 | 18:26 | ZN1287:PA16 | URBAN | Network business | Network error | 66 | 488 | 0.022193 | 0.0045456 | N
05/02/2017 | 18:36 | ZN35900:PA4 | SHORT RURAL | Network business | Network error | 52 | 413 | 0.096287 | 0.023302 | N
05/02/2017 | 18:41 | ZN1287:PA16 | URBAN | Network business | Network error | 33 | 469 | 0.010649 | 0.0022728 | N
05/02/2017 | 20:17 | ZN2196:PA25 | URBAN | Network business | Network error | 55 | 132 | 0.0050002 | 0.003788 | N
05/02/2017 | 19:05 | ZN129:PA28 | URBAN | Network business | Network error | 40 | 1,295 | 0.035676 | 0.0027549 | N
05/02/2017 | 19:18 | ZN10995:PA7 | URBAN | Network business | Network error | 143 | 542 | 0.053359 | 0.0098489 | N
05/02/2017 | 19:53 | ZN4545:PA36 | URBAN | Network business | Network error | 50 | 107 | 0.0036824 | 0.0034437 | N
05/02/2017 | 20:43 | ZN10999:PA22 | URBAN | Network business | Network error | 138 | 322 | 0.030591 | 0.0095045 | N
05/02/2017 | 20:43 | ZN10999:PA22 | URBAN | Network business | Network error | 62 | 346 | 0.014784 | 0.0042702 | N
05/02/2017 | 20:46 | ZN1610:PA19 | URBAN | Network business | Network error | 104 | 914 | 0.065468 | 0.0071628 | N
05/02/2017 | 21:08 | ZN10999:PA10 | URBAN | Network business | Network error | 58 | 271 | 0.010838 | 0.0039947 | N
05/02/2017 | 21:09 | ZN3472:PA33 | URBAN | Network business | Network error | 53 | 231 | 0.0084322 | 0.0036503 | N
05/02/2017 | 21:09 | ZN3472:PA8 | URBAN | Network business | Network error | 101 | 231 | 0.016062 | 0.0069562 | N
05/02/2017 | 21:09 | ZN2196:PA9 | URBAN | Network business | Network error | 66 | 91 | 0.0041365 | 0.0045456 | N
05/02/2017 | 21:36 | ZN10999:PA22 | URBAN | Network business | Network error | 62 | 244 | 0.010411 | 0.0042702 | N
05/02/2017 | 21:39 | ZN2835:PA10 | URBAN | Network business | Network error | 64 | 815 | 0.035924 | 0.0044079 | N
05/02/2017 | 23:21 | ZN965:PA11 | URBAN | Network business | Network error | 58 | 139 | 0.0055526 | 0.0039947 | N
05/02/2017 | 23:21 | ZN965:PA47 | URBAN | Network business | Network error | 12 | 139 | 0.0011488 | 0.00082648 | N
05/02/2017 | 20:48 | ZN1610:PA19 | URBAN | Network business | Network error | 19 | 912 | 0.011934 | 0.0013086 | N
05/02/2017 | 20:46 | ZN1610:PA19 | URBAN | Network business | Network error | 210 | 913 | 0.13208 | 0.014463 | N
06/02/2017 | 11:40 | ZN129:PA24 | URBAN | Network business | Network error | 60 | 450 | 0.018596 | 0.0041324 | N
06/02/2017 | 13:33 | ZN2466:PA2 | URBAN | Network business | Network error | 3 | 567 | 0.0011715 | 0.00020662 | N
03/02/2017 | 10:50 | ZN12640:PA13 | SHORT RURAL | Network business | Network error | 17 | 90 | 0.0068574 | 0.0076194 | N
06/02/2017 | 17:39 | ZN1193:PA12 | URBAN | Network business | Network error | 40 | 66 | 0.0018155 | 0.0027549 | N
06/02/2017 | 17:39 | ZN1193:PA28 | URBAN | Network business | Network error | 15 | 66 | 0.00068185 | 0.0010331 | N
06/02/2017 | 18:35 | ZN262:PA30 | URBAN | Network business | Network error | 81 | 96 | 0.0053798 | 0.0055788 | N
04/02/2017 | 18:27 | ZN1068:PA17 | URBAN | Network business | Network error | 42 | 378 | 0.010934 | 0.0028925 | N
04/02/2017 | 18:27 | ZN1068:PA17 | URBAN | Network business | Network error | 45 | 383 | 0.01187 | 0.0030991 | N
05/02/2017 | 21:11 | ZN2196:PA9 | URBAN | Network business | Network error | 65 | 169 | 0.0075658 | 0.0044768 | N
06/02/2017 | 08:07 | ZN1287:PA16 | URBAN | Network business | Network error | 84 | 88 | 0.0050911 | 0.0057854 | N
09/02/2017 | 17:02 | ZN874:PA18 | URBAN | Network business | Network error | 72 | 263 | 0.013042 | 0.004959 | N
09/02/2017 | 21:11 | ZN15006:PA12 | URBAN | Network business | Switching and protection error | 478 | 9 | 0.002963 | 0.032923 | N
09/02/2017 | 21:11 | ZN15006:PA15 | URBAN | Network business | Switching and protection error | 2,017 | 9 | 0.012503 | 0.13892 | N
09/02/2017 | 21:11 | ZN15006:PA6 | URBAN | Network business | Switching and protection error | 327 | 9 | 0.002027 | 0.022522 | N
10/02/2017 | 14:24 | ZN690:PA18 | URBAN | Network business | Network error | 49 | 205 | 0.006921 | 0.0033753 | N
10/02/2017 | 14:24 | ZN690:PA33 | URBAN | Network business | Network error | 1 | 206 | 0.0001419 | 6.8883e-05 | N
10/02/2017 | 14:30 | ZN10999:PA16 | URBAN | Network business | Network error | 19 | 145 | 0.0018977 | 0.0013088 | N
10/02/2017 | 17:55 | ZN10995:PA1 | URBAN | Network business | Network error | 66 | 45 | 0.002039 | 0.0045463 | N
10/02/2017 | 17:58 | ZN35800:PA1 | URBAN | Network business | Switching and protection error | 2,517 | 7 | 0.012395 | 0.17338 | N
10/02/2017 | 18:06 | ZN10999:PA38 | URBAN | Network business | Network error | 136 | 129 | 0.012085 | 0.0093681 | N
10/02/2017 | 18:17 | ZN35900:PA20 | URBAN | Network business | Network error | 76 | 127 | 0.0066556 | 0.0052351 | N
10/02/2017 | 18:20 | ZN2835:PA10 | URBAN | Network business | Switching and protection error | 1,504 | 24 | 0.025168 | 0.1036 | N
10/02/2017 | 18:37 | ZN35900:PA1 | URBAN | Network business | Network error | 144 | 213 | 0.021128 | 0.0099192 | N
10/02/2017 | 18:37 | ZN35900:PA4 | SHORT RURAL | Network business | Network error | 1 | 213 | 0.00095312 | 0.00044747 | N
10/02/2017 | 18:49 | ZN35900:PA20 | URBAN | Network business | Network error | 49 | 191 | 0.0064468 | 0.0033753 | N
10/02/2017 | 18:57 | ZN15014:PA7 | URBAN | Network business | Network error | 62 | 163 | 0.0069613 | 0.0042707 | N
10/02/2017 | 19:51 | ZN965:PA42 | URBAN | Network business | Network error | 45 | 279 | 0.0086364 | 0.0030997 | N
10/02/2017 | 20:12 | ZN965:PA12 | URBAN | Network business | Network error | 89 | 122 | 0.0075079 | 0.0061306 | N
10/02/2017 | 20:14 | ZN10993:PA22 | URBAN | Network business | Network error | 54 | 706 | 0.026261 | 0.0037197 | N
11/02/2017 | 00:10 | ZN2835:PA27 | URBAN | Network business | Network error | 60 | 1,415 | 0.058482 | 0.004133 | N
10/02/2017 | 21:00 | ZN965:PA28 | URBAN | Network business | Network error | 28 | 74 | 0.0014343 | 0.0019287 | N
10/02/2017 | 22:06 | ZN1285:PA24 | URBAN | Network business | Network error | 80 | 124 | 0.0068176 | 0.0055106 | N
10/02/2017 | 22:08 | ZN1285:PA24 | URBAN | Network business | Network error | 49 | 197 | 0.0066639 | 0.0033753 | N
11/02/2017 | 08:18 | ZN35500:PA23 | URBAN | Network business | Network error | 51 | 232 | 0.0081467 | 0.003513 | N
11/02/2017 | 08:58 | ZN35900:PA4 | SHORT RURAL | Network business | Network error | 52 | 241 | 0.056167 | 0.023269 | N
11/02/2017 | 08:58 | ZN35900:PA20 | URBAN | Network business | Network error | 76 | 204 | 0.01068 | 0.0052351 | N
11/02/2017 | 10:57 | ZN690:PA18 | URBAN | Network business | Network error | 49 | 183 | 0.0061621 | 0.0033753 | N
11/02/2017 | 11:34 | ZN4545:PA4 | URBAN | Network business | Network error | 135 | 131 | 0.012182 | 0.0092992 | N
11/02/2017 | 14:01 | ZN35800:PA15 | URBAN | Network business | Network error | 248 | 642 | 0.10969 | 0.017083 | N
11/02/2017 | 15:03 | ZN2835:PA29 | URBAN | Network business | Network error | 128 | 487 | 0.042934 | 0.008817 | N
11/02/2017 | 15:18 | ZN35900:PA1 | URBAN | Network business | Network error | 73 | 127 | 0.0063786 | 0.0050285 | N
11/02/2017 | 16:53 | ZN1648:PA21 | URBAN | Network business | Network error | 150 | 277 | 0.028621 | 0.010332 | N
11/02/2017 | 17:26 | ZN1285:PA27 | URBAN | Network business | Network error | 71 | 213 | 0.010418 | 0.0048907 | N
11/02/2017 | 18:22 | ZN35500:PA23 | URBAN | Network business | Network error | 51 | 384 | 0.013497 | 0.003513 | N
11/02/2017 | 18:37 | ZN10993:PA22 | URBAN | Network business | Network error | 49 | 173 | 0.0058392 | 0.0033753 | N
11/02/2017 | 18:40 | ZN10995:PA1 | URBAN | Network business | Network error | 66 | 139 | 0.0063307 | 0.0045463 | N
11/02/2017 | 18:57 | ZN36300:PA11 | URBAN | Network business | Network error | 36 | 140 | 0.0034601 | 0.0024798 | N
11/02/2017 | 18:57 | ZN36300:PA5 | URBAN | Network business | Network error | 45 | 135 | 0.004197 | 0.0030997 | N
11/02/2017 | 19:36 | ZN847:PA44 | URBAN | Network business | Network error | 76 | 269 | 0.014057 | 0.0052351 | N
11/02/2017 | 20:27 | ZN35500:PA19 | SHORT RURAL | Network business | Network error | 50 | 288 | 0.064369 | 0.022374 | N
12/02/2017 | 01:34 | ZN35500:PA28 | URBAN | Network business | Network error | 315 | 159 | 0.034524 | 0.021698 | N
12/02/2017 | 06:11 | ZN35500:PA23 | URBAN | Network business | Network error | 51 | 123 | 0.0043374 | 0.003513 | N
12/02/2017 | 10:16 | ZN1285:PA33 | URBAN | Network business | Network error | 30 | 344 | 0.0071087 | 0.0020665 | N
12/02/2017 | 12:46 | ZN1285:PA31 | URBAN | Network business | Network error | 75 | 255 | 0.013174 | 0.0051662 | N
12/02/2017 | 16:47 | ZN3288:PA41 42KLM | CBD | Network business | Switching and protection error | 36 | 32 | 0.037106 | 0.11596 | N
10/02/2017 | 21:09 | ZN12650:PA13 | SHORT RURAL | Network business | Switching and protection error | 936 | 4 | 0.016753 | 0.41884 | N
11/02/2017 | 17:46 | ZN4545:PA4 | URBAN | Network business | Network error | 135 | 89 | 0.0082763 | 0.0092992 | N
10/02/2017 | 16:59 | ZN2835:PA29 | URBAN | Network business | Network error | 133 | 291 | 0.026705 | 0.0091614 | N
11/02/2017 | 15:18 | ZN35900:PA1 | URBAN | Network business | Network error | 76 | 127 | 0.0066486 | 0.0052351 | N
17/02/2017 | 17:52 | ZN15010:PA9 | SHORT RURAL | Network business | Network error | 74 | 488 | 0.16128 | 0.033048 | Y
17/02/2017 | 17:16 | ZN7481:PA6 | URBAN | Network business | Network error | 14 | 179 | 0.0017216 | 0.00096446 | Y
17/02/2017 | 17:25 | ZN15010:PA1 | URBAN | Network business | Network error | 99 | 515 | 0.035124 | 0.0068201 | Y
17/02/2017 | 17:42 | ZN15010:PA1 | URBAN | Network business | Network error | 64 | 498 | 0.021957 | 0.004409 | Y
18/02/2017 | 12:28 | 238:34148 | SHORT RURAL | Network business | Switching and protection error | 8 | 117 | 0.0041802 | 0.0035728 | N
11/02/2017 | 19:21 | ZN1285:PA27 | URBAN | Network business | Network error | 72 | 929 | 0.046074 | 0.0049596 | N
12/02/2017 | 10:16 | ZN1285:PA33 | URBAN | Network business | Network error | 44 | 314 | 0.0095169 | 0.0030309 | N
10/02/2017 | 18:17 | ZN35900:PA20 | URBAN | Network business | Network error | 61 | 123 | 0.0051683 | 0.0042019 | N
10/02/2017 | 18:37 | ZN35900:PA20 | URBAN | Network business | Network error | 51 | 228 | 0.0080097 | 0.003513 | N
20/02/2017 | 16:49 | ZN10994:PA2 | URBAN | Network business | Network error | 69 | 80 | 0.0038249 | 0.0047534 | N
20/02/2017 | 16:49 | ZN10994:PA4 | URBAN | Network business | Network error | 30 | 96 | 0.001984 | 0.0020667 | N
21/02/2017 | 14:01 | ZN2196:PA9 | URBAN | Network business | Switching and protection error | 34 | 109 | 0.0025492 | 0.0023423 | N
11/02/2017 | 14:01 | ZN35800:PA15 | URBAN | Network business | Network error | 98 | 631 | 0.042596 | 0.0067505 | N
22/02/2017 | 12:17 | ZN180:PA35 | URBAN | Network business | Network error | 103 | 63 | 0.0044704 | 0.0070959 | N
22/02/2017 | 12:32 | ZN180:PA33 | URBAN | Network business | Network error | 31 | 48 | 0.0010251 | 0.0021357 | N
24/02/2017 | 20:23 | ZN2835:PA24 | URBAN | Network business | Network error | 56 | 242 | 0.0093277 | 0.0038574 | N
26/02/2017 | 06:05 | ZN2196:PA25 | URBAN | Network business | Network error | 79 | 535 | 0.029112 | 0.0054414 | N
28/02/2017 | 17:58 | ZN2602:PA29 | URBAN | Network business | Network error | 34 | 62 | 0.00145 | 0.0023419 | N
27/02/2017 | 10:29 | ZN14891:PA12 | SHORT RURAL | Network business | Switching and protection error | 381 | 2 | 0.0034032 | 0.17016 | N
02/03/2017 | 05:16 | ZN3154:PA13 | SHORT RURAL | Network business | Network error | 31 | 399 | 0.055244 | 0.013846 | N
02/03/2017 | 10:13 | ZN187:PA30 | URBAN | Network business | Network error | 2 | 116 | 0.0001598 | 0.00013776 | N
03/03/2017 | 13:28 | ZN931:PA22 | URBAN | Network business | Switching and protection error | 33 | 62 | 0.0014089 | 0.0022725 | N
03/03/2017 | 13:28 | ZN931:PA25 | URBAN | Network business | Switching and protection error | 130 | 62 | 0.0055296 | 0.0089522 | N
06/03/2017 | 10:17 | ZN10999:PA39 | URBAN | Network business | Network error | 20 | 82 | 0.0011353 | 0.0013775 | N
06/03/2017 | 14:43 | ZN3425:PA23 | URBAN | Network business | Network error | 12 | 342 | 0.0028267 | 0.00082652 | N
09/03/2017 | 15:35 | ZN3154:PA12 | URBAN | Network business | Network error | 28 | 125 | 0.0024111 | 0.0019289 | N
09/03/2017 | 16:19 | ZN3154:PA11 | URBAN | Network business | Network error | 4 | 215 | 0.0005913 | 0.00027556 | N
09/03/2017 | 16:33 | ZN2400:PA11 | SHORT RURAL | Network business | Network error | 209 | 372 | 0.3457 | 0.092931 | N
09/03/2017 | 18:26 | ZN3154:PA12 | URBAN | Network business | Network error | 16 | 274 | 0.0030201 | 0.0011022 | N
13/03/2017 | 21:31 | 508:82580 | SHORT RURAL | Network business | Switching and protection error | 15 | 29 | 0.0019253 | 0.0066697 | N
13/03/2017 | 07:30 | 511:29878 | SHORT RURAL | Network business | Network error | 6 | 115 | 0.003068 | 0.0026679 | N
16/03/2017 | 15:22 | ZN80:PA22 | URBAN | Network business | Network error | 2 | 116 | 0.00015979 | 0.00013775 | N
16/03/2017 | 15:22 | ZN80:PA31 | URBAN | Network business | Network error | 31 | 116 | 0.0024768 | 0.0021352 | N
16/03/2017 | 15:22 | ZN80:PA40 | URBAN | Network business | Network error | 31 | 116 | 0.0024768 | 0.0021352 | N
17/03/2017 | 11:50 | ZN80:PA40 | URBAN | Network business | Network error | 2 | 190 | 0.00026173 | 0.00013775 | N
21/03/2017 | 18:38 | ZN2400:PA26 | URBAN | Network business | Network error | 57 | 153 | 0.006007 | 0.0039261 | N
22/03/2017 | 17:29 | ZN129:PA9 | URBAN | Network business | Network error | 59 | 120 | 0.0048768 | 0.004064 | N
24/03/2017 | 15:41 | ZN1193:PA15 | URBAN | Network business | Network error | 158 | 129 | 0.014035 | 0.01088 | N
28/03/2017 | 09:10 | ZN9245:PA1 | URBAN | Network business | Network error | 40 | 12 | 0.00033052 | 0.0027543 | N
30/03/2017 | 15:14 | ZN847:PA1 | URBAN | Network business | Network error | 56 | 270 | 0.010426 | 0.0038548 | N
02/04/2017 | 19:30 | ZN188:PA17 | URBAN | Network business | Switching and protection error | 1 | 37 | 2.5458e-05 | 6.8806e-05 | N
02/04/2017 | 19:30 | ZN8100:PA2 | URBAN | Network business | Switching and protection error | 2 | 39 | 5.3669e-05 | 0.00013761 | N
02/04/2017 | 19:30 | ZN8100:PA20 | URBAN | Network business | Switching and protection error | 617 | 37 | 0.015708 | 0.042454 | N
06/04/2017 | 11:34 | 801:74123 | SHORT RURAL | Network business | Switching and protection error | 3 | 4 | 5.3437e-05 | 0.0013359 | N
07/04/2017 | 23:28 | ZN35800:PA1 | URBAN | Network business | Network error | 21 | 112 | 0.0016209 | 0.0014472 | N
07/04/2017 | 23:28 | ZN35800:PA14 | URBAN | Network business | Network error | 78 | 112 | 0.0060204 | 0.0053753 | N
07/04/2017 | 23:23 | ZN35800:PA14 | URBAN | Network business | Network error | 73 | 126 | 0.0063555 | 0.0050307 | N
10/04/2017 | 17:08 | ZN10997:PA5 | URBAN | Network business | Network error | 1 | 261 | 0.00017957 | 6.878e-05 | N
09/04/2017 | 13:28 | ZN262:PA39 | URBAN | Network business | Switching and protection error | 50 | 2 | 6.878e-05 | 0.003439 | N
17/04/2017 | 18:02 | ZN10991:PA5 | URBAN | Network business | Switching and protection error | 104 | 221 | 0.015805 | 0.0071517 | N
17/04/2017 | 18:09 | ZN10991:PA5 | URBAN | Network business | Switching and protection error | 45 | 213 | 0.0065928 | 0.0030945 | N
27/04/2017 | 10:39 | ZN3154:PA5 | URBAN | Network business | Network error | 17 | 236 | 0.0027587 | 0.0011689 | N
28/04/2017 | 11:40 | ZN35800:PA3 | URBAN | Network business | Network error | 25 | 209 | 0.0035976 | 0.001719 | N
28/04/2017 | 11:47 | ZN35800:PA16 | URBAN | Network business | Network error | 14 | 203 | 0.0019511 | 0.00096266 | N
28/04/2017 | 11:50 | ZN35800:PA7 | URBAN | Network business | Network error | 15 | 200 | 0.0020616 | 0.0010314 | N
28/04/2017 | 11:40 | ZN35800:PA3 | URBAN | Network business | Network error | 13 | 210 | 0.0018772 | 0.00089389 | N
28/04/2017 | 18:14 | ZN12570:PA24 | SHORT RURAL | Network business | Network error | 15 | 36 | 0.0023704 | 0.0066586 | N
01/05/2017 | 12:06 | ZN10990:PA12 | URBAN | Network business | Network error | 52 | 112 | 0.0040047 | 0.0035756 | N
27/04/2017 | 08:00 | ZN2835:PA9 | URBAN | Network business | Network error | 26 | 60 | 0.0010727 | 0.0017878 | N
02/05/2017 | 07:45 | ZN72:PA16 | URBAN | Network business | Network error | 87 | 232 | 0.013881 | 0.0059825 | N
07/05/2017 | 11:45 | ZN262:PA6 | URBAN | Network business | Switching and protection error | 78 | 175 | 0.0093839 | 0.0053622 | N
07/05/2017 | 07:41 | ZN15014:PA18 | URBAN | Network business | Network error | 68 | 108 | 0.0050503 | 0.0046748 | N
07/05/2017 | 23:12 | ZN1193:PA25 | URBAN | Network business | Network error | 1 | 269 | 0.00018483 | 6.8747e-05 | N
08/05/2017 | 19:14 | ZN3155:PA15 | URBAN | Network business | Network error | 62 | 230 | 0.0098033 | 0.0042623 | N
08/05/2017 | 19:14 | ZN3155:PA23 | URBAN | Network business | Network error | 36 | 86 | 0.0021284 | 0.0024749 | N
08/05/2017 | 19:14 | ZN3155:PA24 | URBAN | Network business | Network error | 717 | 49 | 0.024153 | 0.049291 | N
08/05/2017 | 19:14 | ZN3155:PA27 | URBAN | Network business | Network error | 115 | 206 | 0.016286 | 0.0079059 | N
09/05/2017 | 11:26 | ZN10994:PA13 | URBAN | Network business | Network error | 164 | 49 | 0.0055247 | 0.011275 | N
08/05/2017 | 19:52 | ZN10993:PA22 | URBAN | Network business | Network error | 49 | 143 | 0.0048171 | 0.0033686 | N
11/05/2017 | 04:07 | ZN15011:PA4 | URBAN | Network business | Network error | 21 | 64 | 0.00092471 | 0.0014449 | N
12/05/2017 | 17:01 | ZN3672:PA13 | URBAN | Network business | Switching and protection error | 1,802 | 12 | 0.014872 | 0.12393 | N
12/05/2017 | 17:01 | ZN3672:PA21 | URBAN | Network business | Switching and protection error | 121 | 12 | 0.00099863 | 0.0083219 | N
12/05/2017 | 17:01 | ZN3672:PA23 | URBAN | Network business | Switching and protection error | 148 | 12 | 0.0012215 | 0.010179 | N
12/05/2017 | 17:01 | ZN3672:PA26 | URBAN | Network business | Switching and protection error | 187 | 12 | 0.0015433 | 0.012861 | N
12/05/2017 | 17:01 | ZN3672:PA29 | URBAN | Network business | Switching and protection error | 176 | 12 | 0.0014525 | 0.012105 | N
12/05/2017 | 17:01 | ZN3672:PA32 | URBAN | Network business | Switching and protection error | 144 | 13 | 0.0012538 | 0.0099037 | N
12/05/2017 | 17:01 | ZN3672:PA34 | URBAN | Network business | Switching and protection error | 99 | 13 | 0.00088515 | 0.0068088 | N
12/05/2017 | 17:01 | ZN3672:PA35 | SHORT RURAL | Network business | Switching and protection error | 638 | 13 | 0.036859 | 0.28353 | N
12/05/2017 | 17:01 | ZN3672:PA36 | URBAN | Network business | Switching and protection error | 1,848 | 13 | 0.016523 | 0.1271 | N
12/05/2017 | 17:01 | ZN3672:PA37 | URBAN | Network business | Switching and protection error | 1,811 | 13 | 0.016192 | 0.12455 | N
12/05/2017 | 17:01 | ZN3672:PA4 | URBAN | Network business | Switching and protection error | 112 | 13 | 0.0010014 | 0.0077029 | N
12/05/2017 | 17:01 | ZN3672:PA42 | URBAN | Network business | Switching and protection error | 346 | 13 | 0.0030935 | 0.023796 | N
12/05/2017 | 17:01 | ZN3672:PA43 | URBAN | Network business | Switching and protection error | 1,954 | 13 | 0.01747 | 0.13439 | N
12/05/2017 | 17:01 | ZN3672:PA44 | URBAN | Network business | Switching and protection error | 1,926 | 13 | 0.01722 | 0.13246 | N
12/05/2017 | 17:01 | ZN3672:PA46 | URBAN | Network business | Switching and protection error | 1,619 | 13 | 0.014475 | 0.11135 | N
12/05/2017 | 17:01 | ZN3672:PA6 | URBAN | Network business | Switching and protection error | 1,255 | 13 | 0.011221 | 0.086314 | N
12/05/2017 | 17:01 | ZN3672:PA9 | URBAN | Network business | Switching and protection error | 1,311 | 12 | 0.01082 | 0.090165 | N
14/05/2017 | 19:20 | ZN1285:PA31 | URBAN | Network business | Switching and protection error | 55 | 65 | 0.0024573 | 0.0037804 | N
11/05/2017 | 08:16 | ZN15002:PA6 | URBAN | Network business | Switching and protection error | 742 | 6 | 0.0030631 | 0.051051 | N
22/05/2017 | 10:36 | ZN15012:PA8 | URBAN | Network business | Network error | 1 | 129 | 8.8538e-05 | 6.8723e-05 | N
24/05/2017 | 06:06 | 202:34253 | URBAN | Network business | Network error | 33 | 73 | 0.0016555 | 0.0022678 | N
25/05/2017 | 11:58 | ZN2400:PA23 | URBAN | Network business | Network error | 39 | 207 | 0.005548 | 0.0026802 | N
27/05/2017 | 08:22 | ZN690:PA18 | URBAN | Network business | Network error | 50 | 258 | 0.0088652 | 0.0034361 | N
29/05/2017 | 09:29 | ZN690:PA35 | URBAN | Network business | Network error | 16 | 102 | 0.0011216 | 0.0010996 | N
29/05/2017 | 18:56 | 504:48031 | SHORT RURAL | Network business | Switching and protection error | 1 | 80 | 0.00035719 | 0.00044761 | N
02/06/2017 | 10:45 | ZN15002:PA6 | URBAN | Network business | Network error | 16 | 190 | 0.0020891 | 0.0010995 | N
02/06/2017 | 19:38 | ZN167:PA21 | URBAN | Network business | Network error | 82 | 112 | 0.0063114 | 0.0056352 | N
02/06/2017 | 19:38 | ZN167:PA10 | URBAN | Network business | Network error | 68 | 111 | 0.0052058 | 0.0046731 | N
03/06/2017 | 12:59 | ZN35900:PA1 | URBAN | Network business | Network error | 69 | 161 | 0.0076343 | 0.0047418 | N
06/06/2017 | 21:14 | ZN116:PA81 | URBAN | Network business | Network error | 148 | 107 | 0.010905 | 0.010171 | N
06/06/2017 | 21:14 | ZN116:PA83 | URBAN | Network business | Network error | 87 | 115 | 0.0068915 | 0.0059788 | N
07/06/2017 | 23:55 | ZN80:PA21 | URBAN | Network business | Network error | 188 | 725 | 0.093668 | 0.01292 | N
07/06/2017 | 23:55 | ZN80:PA22 | URBAN | Network business | Network error | 40 | 725 | 0.019929 | 0.0027489 | N
07/06/2017 | 23:55 | ZN80:PA40 | URBAN | Network business | Network error | 2 | 725 | 0.00099646 | 0.00013744 | N
14/06/2017 | 18:55 | ZN1788:PA14 | URBAN | Network business | Network error | 65 | 200 | 0.0089338 | 0.0044669 | N
15/06/2017 | 10:32 | 508:82579 | SHORT RURAL | Network business | Network error | 3 | 417 | 0.0055995 | 0.0013428 | N
16/06/2017 | 14:37 | ZN129:PA39 | URBAN | Network business | Network error | 107 | 235 | 0.01728 | 0.0073532 | N
16/06/2017 | 19:01 | ZN10991:PA7 | URBAN | Network business | Network error | 92 | 159 | 0.010053 | 0.0063224 | N
22/06/2017 | 15:28 | ZN14891:PA9 | URBAN | Network business | Switching and protection error | 1,299 | 3 | 0.0026781 | 0.089269 | N
23/06/2017 | 18:25 | ZN2602:PA28 | URBAN | Network business | Switching and protection error | 1 | 5 | 3.4321e-06 | 6.8642e-05 | N
23/06/2017 | 18:25 | ZN2602:PA29 | URBAN | Network business | Switching and protection error | 2,184 | 5 | 0.0074957 | 0.14991 | N
23/06/2017 | 18:25 | ZN2602:PA30 | URBAN | Network business | Switching and protection error | 2 | 5 | 6.8642e-06 | 0.00013728 | N
23/06/2017 | 18:25 | ZN2602:PA32 | URBAN | Network business | Switching and protection error | 1,012 | 5 | 0.0034733 | 0.069466 | N
23/06/2017 | 18:25 | ZN2602:PA34 | URBAN | Network business | Switching and protection error | 1,234 | 5 | 0.0042352 | 0.084705 | N
23/06/2017 | 18:25 | ZN2602:PA35 | URBAN | Network business | Switching and protection error | 1,045 | 5 | 0.0035866 | 0.071731 | N
23/06/2017 | 18:25 | ZN2602:PA36 | URBAN | Network business | Switching and protection error | 1,316 | 5 | 0.0045167 | 0.090333 | N
23/06/2017 | 18:25 | ZN2602:PA41 | URBAN | Network business | Switching and protection error | 1,387 | 5 | 0.0047603 | 0.095207 | N
25/06/2017 | 21:00 | ZN36300:PA8 | URBAN | Network business | Network error | 146 | 89 | 0.0089511 | 0.010022 | N
25/06/2017 | 21:01 | ZN36300:PA13 | URBAN | Network business | Network error | 129 | 89 | 0.0078513 | 0.0088549 | N
25/06/2017 | 23:16 | ZN14144:PA8 | URBAN | Network business | Switching and protection error | 419 | 2 | 0.00057522 | 0.028761 | N
26/06/2017 | 17:00 | ZN72:PA31 | URBAN | Network business | Network error | 62 | 245 | 0.010427 | 0.0042558 | N
28/06/2017 | 09:30 | ZN72:PA10 | URBAN | Network business | Network error | 37 | 90 | 0.0022858 | 0.0025398 | N
28/06/2017 | 09:30 | ZN72:PA31 | URBAN | Network business | Network error | 95 | 134 | 0.0087107 | 0.006521 | N
28/06/2017 | 17:24 | ZN9037:PA4 | URBAN | Network business | Network error | 59 | 116 | 0.0046979 | 0.0040499 | N
29/06/2017 | 11:52 | ZN9118:PA11 | URBAN | Network business | Network error | 2 | 68 | 9.3354e-05 | 0.00013728 | N
29/06/2017 | 11:52 | ZN9118:PA20 | URBAN | Network business | Network error | 30 | 67 | 0.0013845 | 0.0020593 | N
29/06/2017 | 17:13 | ZN5868:PA30 | URBAN | Network business | Network error | 54 | 76 | 0.0028301 | 0.0037067 | N
30/06/2017 | 12:37 | ZN9900:PA19 | URBAN | Network business | Network error | 1 | 188 | 0.00012905 | 6.8642e-05 | N
30/06/2017 | 12:37 | ZN9900:PA2 | URBAN | Network business | Network error | 3 | 353 | 0.00072692 | 0.00020593 | N
03/07/2016 | 18:28 | 813:89061 | LONG RURAL | Overloads |  | 2 | 137 | 0.097718 | 0.071327 | N
01/08/2016 | 08:17 | ZN35600:PA22 | URBAN | Overloads |  | 2 | 163 | 0.00022516 | 0.00013846 | N
10/08/2016 | 13:00 | ZN2602:PA33 | URBAN | Overloads |  | 1 | 269 | 0.00018638 | 6.9179e-05 | N
30/08/2016 | 13:34 | ZN2602:PA22 | URBAN | Overloads |  | 1 | 145 | 0.00010021 | 6.9061e-05 | N
01/09/2016 | 18:21 | ZN3155:PA20 | URBAN | Overloads |  | 77 | 1,713 | 0.091086 | 0.005316 | N
01/09/2016 | 18:21 | ZN3155:PA23 | URBAN | Overloads |  | 28 | 399 | 0.0077131 | 0.0019331 | N
01/09/2016 | 18:21 | ZN3155:PA34 | URBAN | Overloads |  | 369 | 399 | 0.10163 | 0.025476 | N
29/09/2016 | 23:52 | ZN3472:PA20 | URBAN | Overloads |  | 95 | 79 | 0.0051904 | 0.0065577 | N
24/10/2016 | 10:29 | 807:74179 | SHORT RURAL | Overloads |  | 1 | 181 | 0.00081312 | 0.00045023 | N
03/11/2016 | 18:40 | 229:34995 | SHORT RURAL | Overloads |  | 167 | 35 | 0.026301 | 0.075146 | N
23/11/2016 | 11:29 | ZN9035:PA1 | URBAN | Overloads |  | 457 | 32 | 0.01009 | 0.031532 | N
23/11/2016 | 11:29 | ZN9035:PA10 | URBAN | Overloads |  | 526 | 32 | 0.011614 | 0.036293 | N
23/11/2016 | 11:29 | ZN9035:PA11 | URBAN | Overloads |  | 1,944 | 32 | 0.042922 | 0.13413 | N
23/11/2016 | 11:29 | ZN9035:PA2 | URBAN | Overloads |  | 846 | 32 | 0.018679 | 0.058372 | N
23/11/2016 | 11:29 | ZN9035:PA4 | URBAN | Overloads |  | 1,890 | 32 | 0.04173 | 0.13041 | N
23/11/2016 | 11:29 | ZN9035:PA5 | URBAN | Overloads |  | 318 | 32 | 0.0070212 | 0.021941 | N
23/11/2016 | 11:29 | ZN9035:PA7 | URBAN | Overloads |  | 1,118 | 32 | 0.024685 | 0.077139 | N
23/11/2016 | 11:29 | ZN9035:PA8 | URBAN | Overloads |  | 117 | 32 | 0.0025695 | 0.0080727 | N
23/11/2016 | 11:29 | ZN9118:PA7 | URBAN | Overloads |  | 977 | 32 | 0.021571 | 0.067411 | N
23/11/2016 | 17:02 | ZN9118:PA26 | URBAN | Overloads |  | 1 | 213 | 0.00014726 | 6.8998e-05 | N
02/12/2016 | 13:47 | 515:35197 | LONG RURAL | Overloads |  | 1 | 193 | 0.068708 | 0.0356 | N
06/12/2016 | 13:49 | 513:48058 | URBAN | Overloads |  | 15 | 40 | 0.00041566 | 0.0010344 | N
13/12/2016 | 20:06 | ZN9900:PA21 | URBAN | Overloads |  | 41 | 58 | 0.0016475 | 0.0028266 | N
14/12/2016 | 09:50 | ZN2310:PA70 | URBAN | Overloads |  | 37 | 110 | 0.0027937 | 0.0025509 | N
18/12/2016 | 01:35 | 202:34254 | URBAN | Overloads |  | 7 | 35 | 0.00016887 | 0.00048248 | N
09/01/2017 | 22:51 | 513:48057 | URBAN | Overloads |  | 1 | 608 | 0.00041903 | 6.8892e-05 | N
11/01/2017 | 18:45 | 232:11457 | SHORT RURAL | Overloads |  | 150 | 115 | 0.077422 | 0.067323 | N
11/01/2017 | 18:51 | 205:12206 | URBAN | Overloads |  | 73 | 113 | 0.0056898 | 0.0050293 | N
17/01/2017 | 15:41 | ZN35800:PA15 | URBAN | Overloads |  | 2,995 | 113 | 0.23361 | 0.20632 | N
17/01/2017 | 15:41 | ZN35800:PA16 | URBAN | Overloads |  | 629 | 105 | 0.045496 | 0.04333 | N
18/01/2017 | 10:54 | 225:13446 | URBAN | Overloads |  | 116 | 78 | 0.0062329 | 0.0079909 | N
18/01/2017 | 11:11 | ZN187:PA26 | URBAN | Overloads |  | 58 | 159 | 0.0063528 | 0.0039954 | N
24/01/2017 | 11:36 | ZN10997:PA7 | URBAN | Overloads |  | 92 | 124 | 0.0078355 | 0.0063373 | N
30/01/2017 | 13:44 | ZN72:PA30 | URBAN | Overloads |  | 50 | 140 | 0.0048304 | 0.0034438 | N
04/02/2017 | 19:23 | ZN7900:PA16 | URBAN | Overloads |  | 22 | 88 | 0.0013404 | 0.0015151 | N
05/02/2017 | 23:41 | 520:48172 | SHORT RURAL | Overloads |  | 1 | 619 | 0.0027734 | 0.00044811 | N
06/02/2017 | 17:25 | ZN35800:PA15 | URBAN | Overloads |  | 59 | 54 | 0.0022045 | 0.0040635 | N
06/02/2017 | 17:52 | ZN874:PA4 | URBAN | Overloads |  | 75 | 63 | 0.00325 | 0.0051655 | N
06/02/2017 | 19:15 | ZN1287:PA21 | URBAN | Overloads |  | 82 | 89 | 0.0050537 | 0.0056476 | N
08/02/2017 | 12:30 | ZN12570:PA26 | URBAN | Overloads |  | 5 | 30 | 0.00010331 | 0.00034438 | N
10/02/2017 | 15:18 | ZN72:PA30 | URBAN | Overloads |  | 50 | 197 | 0.0067798 | 0.0034442 | N
10/02/2017 | 16:37 | ZN2835:PA20 | URBAN | Overloads |  | 104 | 22 | 0.001576 | 0.0071638 | N
10/02/2017 | 16:37 | ZN2835:PA27 | URBAN | Overloads |  | 907 | 22 | 0.013745 | 0.062477 | N
10/02/2017 | 16:37 | ZN2835:PA29 | URBAN | Overloads |  | 831 | 22 | 0.012593 | 0.057242 | N
10/02/2017 | 16:37 | ZN2835:PA30 | URBAN | Overloads |  | 1,835 | 22 | 0.027808 | 0.1264 | N
10/02/2017 | 16:37 | ZN2835:PA31 | URBAN | Overloads |  | 1,388 | 22 | 0.021034 | 0.09561 | N
10/02/2017 | 16:37 | ZN2835:PA32 | URBAN | Overloads |  | 912 | 22 | 0.013821 | 0.062821 | N
10/02/2017 | 16:37 | ZN2835:PA33 | URBAN | Overloads |  | 592 | 22 | 0.0089713 | 0.040779 | N
10/02/2017 | 16:37 | ZN2835:PA34 | URBAN | Overloads |  | 1 | 22 | 1.5154e-05 | 6.8883e-05 | N
10/02/2017 | 16:37 | ZN2835:PA35 | URBAN | Overloads |  | 773 | 256 | 0.13631 | 0.053247 | N
10/02/2017 | 16:37 | ZN2835:PA36 | URBAN | Overloads |  | 768 | 22 | 0.011638 | 0.052902 | N
10/02/2017 | 16:37 | ZN2835:PA41 | URBAN | Overloads |  | 1,246 | 22 | 0.018882 | 0.085828 | N
10/02/2017 | 16:37 | ZN2835:PA42 | URBAN | Overloads |  | 94 | 24 | 0.001554 | 0.006475 | N
10/02/2017 | 16:37 | ZN2835:PA43 | URBAN | Overloads |  | 163 | 25 | 0.002807 | 0.011228 | N
10/02/2017 | 16:47 | ZN35800:PA15 | URBAN | Overloads |  | 59 | 123 | 0.0050063 | 0.0040641 | N
10/02/2017 | 17:45 | ZN1285:PA31 | URBAN | Overloads |  | 78 | 206 | 0.011082 | 0.0053729 | N
10/02/2017 | 18:00 | ZN10991:PA1 | URBAN | Overloads |  | 81 | 155 | 0.0086241 | 0.0055795 | N
10/02/2017 | 18:25 | 238:34148 | SHORT RURAL | Overloads |  | 340 | 6 | 0.0091285 | 0.15214 | N
10/02/2017 | 18:25 | 532:83309 | SHORT RURAL | Overloads |  | 204 | 6 | 0.0054771 | 0.091285 | N
10/02/2017 | 18:38 | ZN690:PA5 | URBAN | Overloads |  | 114 | 72 | 0.0056199 | 0.0078527 | N
10/02/2017 | 18:49 | ZN14892:PA10 | URBAN | Overloads |  | 57 | 85 | 0.0033393 | 0.0039263 | N
11/02/2017 | 07:00 | ZN2835:PA24 | URBAN | Overloads |  | 12 | 289 | 0.00239 | 0.0008266 | N
11/02/2017 | 14:47 | ZN180:PA19 | URBAN | Overloads |  | 92 | 93 | 0.0059021 | 0.0063372 | N
11/02/2017 | 16:29 | 224:80340 | SHORT RURAL | Overloads |  | 60 | 101 | 0.027117 | 0.026848 | N
11/02/2017 | 17:03 | ZN10991:PA1 | URBAN | Overloads |  | 81 | 206 | 0.011514 | 0.0055795 | N
11/02/2017 | 17:24 | ZN7900:PA16 | URBAN | Overloads |  | 22 | 140 | 0.0021246 | 0.0015154 | N
11/02/2017 | 17:40 | 224:80326 | SHORT RURAL | Overloads |  | 95 | 75 | 0.031882 | 0.04251 | N
11/02/2017 | 17:47 | ZN690:PA5 | URBAN | Overloads |  | 114 | 217 | 0.017076 | 0.0078527 | N
11/02/2017 | 18:22 | 225:33676 | URBAN | Overloads |  | 70 | 68 | 0.0032788 | 0.0048218 | N
11/02/2017 | 19:23 | ZN1610:PA19 | URBAN | Overloads |  | 175 | 147 | 0.017678 | 0.012055 | N
11/02/2017 | 19:44 | ZN690:PA14 | URBAN | Overloads |  | 61 | 376 | 0.015799 | 0.0042019 | N
10/02/2017 | 18:25 | 532:83309 | SHORT RURAL | Overloads |  | 2,299 | 7 | 0.072012 | 1.0287 | N
11/02/2017 | 15:03 | ZN2835:PA35 | URBAN | Overloads |  | 56 | 508 | 0.019596 | 0.0038574 | N
22/02/2017 | 09:15 | 523:33503 | URBAN | Overloads |  | 1 | 59 | 4.036e-05 | 6.8893e-05 | N
24/02/2017 | 20:46 | ZN15014:PA12 | SHORT RURAL | Overloads |  | 34 | 169 | 0.025655 | 0.01518 | N
01/03/2017 | 19:11 | ZN15014:PA12 | SHORT RURAL | Overloads |  | 34 | 1,329 | 0.20181 | 0.015185 | N
01/03/2017 | 19:58 | ZN15014:PA12 | SHORT RURAL | Overloads |  | 16 | 1,282 | 0.091611 | 0.0071459 | N
06/03/2017 | 19:48 | ZN36100:PA12 | URBAN | Overloads |  | 1 | 1,482 | 0.0010207 | 6.8877e-05 | N
15/03/2017 | 12:01 | ZN3154:PA22 | SHORT RURAL | Overloads |  | 26 | 151 | 0.017463 | 0.011561 | N
22/03/2017 | 01:38 | ZN965:PA38 | URBAN | Overloads |  | 1 | 951 | 0.00065507 | 6.8881e-05 | N
22/03/2017 | 15:15 | ZN14891:PA14 | URBAN | Overloads |  | 88 | 22 | 0.0013335 | 0.0060615 | N
22/03/2017 | 15:15 | ZN14891:PA8 | SHORT RURAL | Overloads |  | 1,332 | 23 | 0.13329 | 0.59203 | N
05/04/2017 | 14:04 | ZN2602:PA28 | URBAN | Overloads |  | 1 | 386 | 0.00026531 | 6.8807e-05 | N
06/05/2017 | 14:01 | 812:19072 | SHORT RURAL | Overloads |  | 1 | 161 | 0.00071432 | 0.00044382 | N
11/05/2017 | 13:58 | 802:82220 | SHORT RURAL | Overloads |  | 1 | 222 | 0.00098582 | 0.00044443 | N
28/05/2017 | 18:15 | ZN3155:PA33 | URBAN | Overloads |  | 83 | 79 | 0.0045147 | 0.005704 | N
01/06/2017 | 18:55 | 513:48056 | SHORT RURAL | Overloads |  | 15 | 97 | 0.0065339 | 0.0067141 | N
05/06/2017 | 18:33 | 513:48058 | URBAN | Overloads |  | 1 | 93 | 6.4152e-05 | 6.8722e-05 | N
07/06/2017 | 18:24 | ZN965:PA42 | URBAN | Overloads |  | 45 | 208 | 0.0064323 | 0.0030925 | N
26/06/2017 | 11:14 | ZN10994:PA8 | URBAN | Overloads |  | 1 | 165 | 0.00011343 | 6.8642e-05 | N
07/07/2016 | 17:49 | ZN690:PA35 | URBAN | Third Party | Other | 1 | 301 | 0.00020832 | 6.9245e-05 | N
03/09/2016 | 15:35 | ZN3672:PA44 | URBAN | Third Party | Other | 2 | 379 | 0.00052278 | 0.00013808 | N
09/10/2016 | 09:43 | ZN12600:PA11 | URBAN | Third Party | Other | 1 | 51 | 3.5061e-05 | 6.9086e-05 | N
24/12/2016 | 21:08 | ZN3472:PA30 | URBAN | Third Party | Other | 1 | 334 | 0.00022997 | 6.8908e-05 | N
12/02/2017 | 11:39 | ZN3672:PA13 | URBAN | Third Party | Other | 1 | 350 | 0.00024111 | 6.8883e-05 | N
12/02/2017 | 17:00 | ZN36100:PA15 | URBAN | Third Party | Other | 1 | 180 | 0.00012374 | 6.8883e-05 | N
12/02/2017 | 17:19 | 528:83014 | SHORT RURAL | Third Party | Other | 1 | 176 | 0.00078584 | 0.00044747 | N
15/02/2017 | 06:49 | ZN262:PA40 | URBAN | Third Party | Other | 1 | 161 | 0.0001106 | 6.8905e-05 | N
01/03/2017 | 04:03 | 812:19071 | SHORT RURAL | Third Party | Other | 1 | 331 | 0.0014761 | 0.00044662 | N
30/05/2017 | 23:42 | ZN35600:PA9 | URBAN | Third Party | Other | 1 | 542 | 0.0003728 | 6.8722e-05 | N
01/07/2016 | 11:40 | ZN9118:PA12 | URBAN | Asset Failure | HV | 1,259 | 189 | 0.16446 | 0.087195 | N
01/07/2016 | 11:40 | ZN9118:PA21 | URBAN | Asset Failure | HV | 2 | 170 | 0.00023548 | 0.00013851 | N
02/07/2016 | 16:16 | 507:80932 | SHORT RURAL | Asset Failure | HV | 1,176 | 107 | 0.57396 | 0.53539 | N
03/07/2016 | 02:00 | 813:89061 | LONG RURAL | Asset Failure | HV | 159 | 512 | 29.046 | 5.6705 | N
03/07/2016 | 19:48 | ZN4545:PA28 | URBAN | Asset Failure | HV | 332 | 42 | 0.0096576 | 0.022994 | N
04/07/2016 | 14:30 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 44 | 6 | 0.0012019 | 0.020032 | N
04/07/2016 | 20:46 | 243:80075 | SHORT RURAL | Asset Failure | HV | 842 | 77 | 0.29502 | 0.38333 | N
05/07/2016 | 06:30 | 227:13015 | SHORT RURAL | Asset Failure | HV | 644 | 93 | 0.27124 | 0.29323 | N
06/07/2016 | 05:07 | ZN965:PA33 | URBAN | Asset Failure | HV | 317 | 110 | 0.024151 | 0.021955 | N
06/07/2016 | 05:07 | ZN965:PA43 | URBAN | Asset Failure | HV | 1,021 | 107 | 0.075486 | 0.070714 | N
06/07/2016 | 10:19 | ZN3425:PA39 | URBAN | Asset Failure | HV | 673 | 18 | 0.0085133 | 0.046611 | N
06/07/2016 | 12:10 | 223:14398 | URBAN | Asset Failure | HV | 741 | 82 | 0.041846 | 0.051321 | N
06/07/2016 | 15:10 | ZN2568:PA33 | URBAN | Asset Failure | HV | 29 | 43 | 0.00086366 | 0.0020085 | N
06/07/2016 | 15:10 | ZN2568:PA43 | URBAN | Asset Failure | HV | 17 | 120 | 0.0014129 | 0.0011774 | N
06/07/2016 | 15:10 | ZN630:PA40 | URBAN | Asset Failure | HV | 79 | 120 | 0.0065658 | 0.0054715 | N
07/07/2016 | 01:21 | ZN711:PA22 | URBAN | Asset Failure | HV | 546 | 116 | 0.043832 | 0.037808 | N
06/07/2016 | 21:56 | 515:35193 | SHORT RURAL | Asset Failure | HV | 1 | 844 | 0.0038429 | 0.00045533 | N
06/07/2016 | 11:34 | ZN2568:PA39 | URBAN | Asset Failure | HV | 1,054 | 2 | 0.00146 | 0.072999 | N
06/07/2016 | 11:34 | ZN2568:PA43 | URBAN | Asset Failure | HV | 271 | 2 | 0.00037538 | 0.018769 | N
07/07/2016 | 14:22 | ZN2635:PA58 | URBAN | Asset Failure | HV | 2,493 | 126 | 0.21832 | 0.17263 | N
08/07/2016 | 06:49 | ZN12610:PA18 | URBAN | Asset Failure | HV | 558 | 122 | 0.047134 | 0.038639 | N
08/07/2016 | 13:00 | 509:33395 | LONG RURAL | Asset Failure | HV | 18 | 260 | 1.669 | 0.64194 | N
08/07/2016 | 17:15 | 520:48172 | SHORT RURAL | Asset Failure | HV | 37 | 120 | 0.020213 | 0.016844 | N
08/07/2016 | 15:04 | ZN12650:PA3 | URBAN | Asset Failure | HV | 1,256 | 90 | 0.077901 | 0.086973 | N
08/07/2016 | 17:02 | ZN1287:PA15 | URBAN | Asset Failure | HV | 96 | 258 | 0.017161 | 0.0066476 | N
08/07/2016 | 20:49 | ZN36300:PA11 | URBAN | Asset Failure | HV | 2,965 | 113 | 0.23147 | 0.20531 | N
08/07/2016 | 20:49 | ZN36300:PA19 | URBAN | Asset Failure | HV | 738 | 96 | 0.04906 | 0.051104 | N
10/07/2016 | 13:55 | ZN12570:PA33 | SHORT RURAL | Asset Failure | HV | 34 | 225 | 0.034826 | 0.015478 | N
10/07/2016 | 14:10 | ZN3154:PA19 | URBAN | Asset Failure | HV | 1,014 | 200 | 0.1403 | 0.07022 | N
13/07/2016 | 08:55 | ZN180:PA22 | URBAN | Asset Failure | HV | 15 | 333 | 0.0034592 | 0.0010388 | N
12/07/2016 | 16:52 | 507:80932 | SHORT RURAL | Asset Failure | HV | 109 | 69 | 0.034285 | 0.049622 | N
12/07/2016 | 16:31 | ZN690:PA5 | URBAN | Asset Failure | HV | 530 | 102 | 0.037463 | 0.036704 | N
12/07/2016 | 18:36 | ZN14143:PA6 | URBAN | Asset Failure | HV | 5 | 234 | 0.00081025 | 0.00034626 | N
13/07/2016 | 15:16 | 507:80914 | SHORT RURAL | Asset Failure | HV | 3 | 424 | 0.0057909 | 0.0013658 | N
13/07/2016 | 11:25 | 242:81541 | URBAN | Asset Failure | HV | 1 | 133 | 9.2108e-05 | 6.9254e-05 | N
15/07/2016 | 11:29 | ZN9037:PA7 | URBAN | Asset Failure | HV | 653 | 74 | 0.033642 | 0.045224 | N
15/07/2016 | 11:29 | ZN9252:PA27 | URBAN | Asset Failure | HV | 308 | 72 | 0.015358 | 0.021331 | N
16/07/2016 | 22:41 | ZN15008:PA5 | URBAN | Asset Failure | HV | 1,133 | 89 | 0.069646 | 0.078452 | N
17/07/2016 | 03:45 | ZN12600:PA2 | SHORT RURAL | Asset Failure | HV | 129 | 84 | 0.049494 | 0.058576 | N
17/07/2016 | 17:49 | ZN398:PA24 | URBAN | Asset Failure | HV | 2,025 | 67 | 0.094199 | 0.14022 | N
18/07/2016 | 19:25 | ZN35500:PA23 | URBAN | Asset Failure | HV | 52 | 140 | 0.0050409 | 0.0036006 | N
18/07/2016 | 19:25 | ZN35500:PA28 | URBAN | Asset Failure | HV | 3,149 | 133 | 0.29015 | 0.21804 | N
18/07/2016 | 23:27 | ZN931:PA24 | URBAN | Asset Failure | HV | 160 | 1,085 | 0.12019 | 0.011079 | N
19/07/2016 | 11:26 | ZN9037:PA2 | URBAN | Asset Failure | HV | 1,044 | 91 | 0.065498 | 0.072291 | N
19/07/2016 | 11:30 | ZN12630:PA22 | SHORT RURAL | Asset Failure | HV | 3 | 171 | 0.0023307 | 0.001363 | N
19/07/2016 | 11:30 | ZN12630:PA23 | SHORT RURAL | Asset Failure | HV | 421 | 171 | 0.32708 | 0.19127 | N
20/07/2016 | 05:15 | ZN1193:PA16 | URBAN | Asset Failure | HV | 887 | 159 | 0.097739 | 0.061404 | N
20/07/2016 | 13:13 | 235:2120 | SHORT RURAL | Asset Failure | HV | 22 | 67 | 0.0066915 | 0.0099873 | N
20/07/2016 | 18:03 | 524:33576 | SHORT RURAL | Asset Failure | HV | 17 | 467 | 0.03604 | 0.0077175 | N
21/07/2016 | 09:20 | ZN12630:PA23 | SHORT RURAL | Asset Failure | HV | 5 | 120 | 0.0027239 | 0.0022699 | N
21/07/2016 | 15:46 | 230:81440 | SHORT RURAL | Asset Failure | HV | 895 | 113 | 0.45778 | 0.40631 | N
21/07/2016 | 19:14 | 508:82579 | SHORT RURAL | Asset Failure | HV | 2 | 719 | 0.0065236 | 0.00090795 | N
21/07/2016 | 21:44 | ZN8000:PA1 | URBAN | Asset Failure | HV | 591 | 101 | 0.041323 | 0.040914 | N
22/07/2016 | 14:18 | 532:83300 | URBAN | Asset Failure | HV | 513 | 57 | 0.020245 | 0.035517 | N
22/07/2016 | 20:01 | 813:89061 | LONG RURAL | Asset Failure | HV | 29 | 211 | 2.179 | 1.0342 | N
22/07/2016 | 20:26 | 523:33507 | URBAN | Asset Failure | HV | 372 | 63 | 0.016236 | 0.025755 | N
23/07/2016 | 03:34 | 801:74118 | URBAN | Asset Failure | HV | 792 | 76 | 0.041809 | 0.054834 | N
23/07/2016 | 03:34 | 801:74120 | URBAN | Asset Failure | HV | 614 | 76 | 0.032308 | 0.04251 | N
23/07/2016 | 07:19 | ZN9700:PA19 | URBAN | Asset Failure | HV | 910 | 75 | 0.047069 | 0.063004 | N
23/07/2016 | 08:28 | 526:34640 | SHORT RURAL | Asset Failure | HV | 7 | 262 | 0.0083247 | 0.0031774 | N
23/07/2016 | 13:41 | 520:48172 | SHORT RURAL | Asset Failure | HV | 2 | 149 | 0.0013526 | 0.00090782 | N
23/07/2016 | 16:28 | ZN9118:PA11 | URBAN | Asset Failure | HV | 256 | 90 | 0.015952 | 0.017724 | N
23/07/2016 | 16:44 | 520:48172 | SHORT RURAL | Asset Failure | HV | 1 | 196 | 0.00088966 | 0.00045391 | N
24/07/2016 | 18:15 | ZN12650:PA13 | SHORT RURAL | Asset Failure | HV | 1,794 | 102 | 0.82657 | 0.81431 | N
25/07/2016 | 17:17 | 509:33399 | SHORT RURAL | Asset Failure | HV | 19 | 140 | 0.012074 | 0.0086243 | N
25/07/2016 | 23:40 | ZN9118:PA22 | URBAN | Asset Failure | HV | 1,442 | 111 | 0.11038 | 0.099837 | N
26/07/2016 | 00:57 | ZN965:PA33 | URBAN | Asset Failure | HV | 1,286 | 72 | 0.064357 | 0.089036 | N
28/07/2016 | 11:39 | 227:13015 | SHORT RURAL | Asset Failure | HV | 3 | 405 | 0.0055129 | 0.0013612 | N
28/07/2016 | 14:00 | ZN9035:PA2 | URBAN | Asset Failure | HV | 292 | 20 | 0.003984 | 0.020214 | N
31/07/2016 | 01:50 | ZN12630:PA22 | SHORT RURAL | Asset Failure | HV | 115 | 455 | 0.2374 | 0.052175 | N
31/07/2016 | 11:26 | ZN12570:PA25 | SHORT RURAL | Asset Failure | HV | 60 | 59 | 0.016061 | 0.027222 | N
01/08/2016 | 15:57 | ZN10991:PA1 | URBAN | Asset Failure | HV | 1,338 | 64 | 0.059283 | 0.092629 | N
02/08/2016 | 00:11 | ZN12610:PA18 | URBAN | Asset Failure | HV | 1,172 | 130 | 0.10537 | 0.081138 | N
02/08/2016 | 03:18 | ZN12650:PA17 | URBAN | Asset Failure | HV | 2,145 | 103 | 0.1528 | 0.1485 | N
02/08/2016 | 03:18 | ZN12650:PA9 | URBAN | Asset Failure | HV | 1 | 95 | 6.5769e-05 | 6.923e-05 | N
02/08/2016 | 21:24 | 502:48010 | SHORT RURAL | Asset Failure | HV | 154 | 121 | 0.084543 | 0.06987 | N
02/08/2016 | 21:24 | 532:83307 | SHORT RURAL | Asset Failure | HV | 1,157 | 120 | 0.62975 | 0.52494 | N
04/08/2016 | 02:07 | ZN10991:PA8 | URBAN | Asset Failure | HV | 1,818 | 130 | 0.16306 | 0.12576 | N
06/08/2016 | 08:26 | ZN12570:PA24 | SHORT RURAL | Asset Failure | HV | 119 | 89 | 0.04815 | 0.054101 | N
04/08/2016 | 15:39 | 526:34639 | SHORT RURAL | Asset Failure | HV | 1 | 156 | 0.00070923 | 0.00045463 | N
08/08/2016 | 18:29 | 217:33610 | URBAN | Asset Failure | HV | 1,915 | 66 | 0.086801 | 0.13248 | N
08/08/2016 | 22:19 | 508:82579 | SHORT RURAL | Asset Failure | HV | 376 | 350 | 0.59766 | 0.17094 | N
09/08/2016 | 06:55 | 232:11455 | SHORT RURAL | Asset Failure | HV | 102 | 195 | 0.090721 | 0.046524 | N
10/08/2016 | 16:55 | 813:89062 | SHORT RURAL | Asset Failure | HV | 26 | 80 | 0.0094873 | 0.011859 | N
11/08/2016 | 11:45 | ZN9700:PA18 | URBAN | Asset Failure | HV | 1,305 | 133 | 0.11973 | 0.090247 | N
17/08/2016 | 14:59 | ZN10991:PA7 | URBAN | Asset Failure | HV | 116 | 196 | 0.015724 | 0.0080225 | N
17/08/2016 | 14:59 | ZN10991:PA8 | URBAN | Asset Failure | HV | 84 | 196 | 0.011386 | 0.0058094 | N
17/08/2016 | 14:59 | ZN10994:PA12 | URBAN | Asset Failure | HV | 63 | 211 | 0.0091934 | 0.0043571 | N
17/08/2016 | 14:59 | ZN10994:PA2 | URBAN | Asset Failure | HV | 1,672 | 85 | 0.098413 | 0.11563 | N
19/08/2016 | 12:30 | 813:89055 | SHORT RURAL | Asset Failure | HV | 17 | 105 | 0.008274 | 0.00788 | N
19/08/2016 | 19:22 | ZN3155:PA19 | URBAN | Asset Failure | HV | 972 | 66 | 0.044653 | 0.067436 | N
19/08/2016 | 19:22 | ZN3155:PA20 | URBAN | Asset Failure | HV | 1,195 | 66 | 0.054719 | 0.082908 | N
21/08/2016 | 07:39 | ZN690:PA5 | URBAN | Asset Failure | HV | 530 | 84 | 0.030965 | 0.036771 | N
22/08/2016 | 11:22 | ZN12650:PA12 | URBAN | Asset Failure | HV | 1,124 | 53 | 0.041331 | 0.077983 | N
24/08/2016 | 20:45 | ZN690:PA30 | URBAN | Asset Failure | HV | 1,235 | 64 | 0.05432 | 0.085329 | N
24/08/2016 | 20:45 | ZN690:PA4 | URBAN | Asset Failure | HV | 73 | 873 | 0.044032 | 0.0050437 | N
25/08/2016 | 08:42 | ZN180:PA10 | URBAN | Asset Failure | HV | 7 | 106 | 0.00051268 | 0.00048366 | N
25/08/2016 | 08:42 | ZN180:PA18 | URBAN | Asset Failure | HV | 3 | 106 | 0.00021972 | 0.00020728 | N
25/08/2016 | 08:42 | ZN180:PA20 | URBAN | Asset Failure | HV | 1,291 | 75 | 0.06679 | 0.089201 | N
25/08/2016 | 08:42 | ZN180:PA21 | URBAN | Asset Failure | HV | 1 | 106 | 7.324e-05 | 6.9094e-05 | N
25/08/2016 | 08:42 | ZN180:PA27 | URBAN | Asset Failure | HV | 114 | 693 | 0.054571 | 0.0078768 | N
25/08/2016 | 08:42 | ZN180:PA28 | URBAN | Asset Failure | HV | 3 | 106 | 0.00021972 | 0.00020728 | N
26/08/2016 | 14:21 | 240:34846 | URBAN | Asset Failure | HV | 836 | 36 | 0.020842 | 0.057763 | N
26/08/2016 | 18:21 | 515:35197 | LONG RURAL | Asset Failure | HV | 3 | 151 | 0.16155 | 0.10699 | N
26/08/2016 | 20:39 | ZN195:PA9 | URBAN | Asset Failure | HV | 1,324 | 77 | 0.070672 | 0.091481 | N
28/08/2016 | 04:03 | 504:48032 | URBAN | Asset Failure | HV | 341 | 99 | 0.023314 | 0.023549 | N
28/08/2016 | 08:49 | ZN15004:PA1 | URBAN | Asset Failure | HV | 1 | 127 | 8.7706e-05 | 6.906e-05 | N
28/08/2016 | 08:49 | ZN15004:PA9 | URBAN | Asset Failure | HV | 1,935 | 125 | 0.16639 | 0.13363 | N
29/08/2016 | 09:15 | 814:82283 | SHORT RURAL | Asset Failure | HV | 1 | 735 | 0.0033561 | 0.00045662 | N
30/08/2016 | 06:52 | ZN35370:PA8 | SHORT RURAL | Asset Failure | HV | 2 | 263 | 0.0024018 | 0.00091323 | N
30/08/2016 | 10:14 | ZN342:PA26 | URBAN | Asset Failure | HV | 2,838 | 53 | 0.10445 | 0.196 | N
30/08/2016 | 11:45 | ZN2602:PA3 | URBAN | Asset Failure | HV | 1,537 | 47 | 0.050168 | 0.10615 | N
31/08/2016 | 02:40 | 812:19065 | SHORT RURAL | Asset Failure | HV | 140 | 77 | 0.049413 | 0.063905 | N
31/08/2016 | 09:00 | 807:74181 | SHORT RURAL | Asset Failure | HV | 461 | 80 | 0.16834 | 0.21043 | N
31/08/2016 | 18:19 | ZN1610:PA2 | URBAN | Asset Failure | HV | 1,526 | 55 | 0.058289 | 0.10535 | N
01/09/2016 | 10:50 | 520:48172 | SHORT RURAL | Asset Failure | HV | 5 | 90 | 0.0020541 | 0.0022824 | N
01/09/2016 | 22:07 | ZN15006:PA15 | URBAN | Asset Failure | HV | 2,050 | 68 | 0.096929 | 0.14153 | N
02/09/2016 | 04:30 | 807:74184 | SHORT RURAL | Asset Failure | HV | 57 | 200 | 0.051969 | 0.026019 | N
02/09/2016 | 13:10 | 801:74118 | URBAN | Asset Failure | HV | 135 | 19 | 0.0017819 | 0.0093203 | N
03/09/2016 | 11:42 | 807:74179 | SHORT RURAL | Asset Failure | HV | 51 | 160 | 0.037334 | 0.02328 | N
03/09/2016 | 12:17 | 512:48048 | SHORT RURAL | Asset Failure | HV | 7 | 213 | 0.0068061 | 0.0031953 | N
04/09/2016 | 10:29 | 511:29880 | URBAN | Asset Failure | HV | 15 | 91 | 0.00094242 | 0.0010356 | N
04/09/2016 | 11:35 | 515:35193 | SHORT RURAL | Asset Failure | HV | 5 | 95 | 0.0021683 | 0.0022824 | N
06/09/2016 | 18:58 | ZN901:PA18 | URBAN | Asset Failure | HV | 1,492 | 81 | 0.083484 | 0.10301 | N
06/09/2016 | 18:58 | ZN901:PA20 | URBAN | Asset Failure | HV | 1 | 75 | 5.1782e-05 | 6.9042e-05 | N
08/09/2016 | 01:51 | ZN630:PA24 | URBAN | Asset Failure | HV | 1,091 | 53 | 0.039712 | 0.075342 | N
08/09/2016 | 07:08 | 242:81538 | URBAN | Asset Failure | HV | 72 | 126 | 0.0062881 | 0.0049722 | N
08/09/2016 | 13:45 | 532:83309 | SHORT RURAL | Asset Failure | HV | 2 | 22 | 0.00019998 | 0.00090902 | N
10/09/2016 | 11:15 | ZN931:PA22 | URBAN | Asset Failure | HV | 526 | 120 | 0.043591 | 0.036326 | N
10/09/2016 | 12:52 | 513:48059 | SHORT RURAL | Asset Failure | HV | 3 | 188 | 0.0025634 | 0.0013635 | N
10/09/2016 | 16:59 | ZN10997:PA11 | URBAN | Asset Failure | HV | 706 | 70 | 0.034231 | 0.048757 | N
11/09/2016 | 09:07 | 516:48067 | SHORT RURAL | Asset Failure | HV | 1 | 133 | 0.00060449 | 0.0004545 | N
11/09/2016 | 16:03 | ZN1648:PA20 | URBAN | Asset Failure | HV | 1 | 90 | 6.2156e-05 | 6.9062e-05 | N
11/09/2016 | 16:03 | ZN398:PA16 | URBAN | Asset Failure | HV | 2,289 | 93 | 0.1463 | 0.15808 | N
11/09/2016 | 16:03 | ZN398:PA9 | URBAN | Asset Failure | HV | 186 | 90 | 0.011561 | 0.012846 | N
11/09/2016 | 19:01 | 526:34639 | SHORT RURAL | Asset Failure | HV | 1 | 207 | 0.00094082 | 0.0004545 | N
12/09/2016 | 11:06 | 235:2120 | SHORT RURAL | Asset Failure | HV | 3 | 409 | 0.0055768 | 0.0013635 | N
12/09/2016 | 16:05 | 235:2120 | SHORT RURAL | Asset Failure | HV | 18 | 110 | 0.0089992 | 0.0081811 | N
13/09/2016 | 20:01 | ZN1788:PA7 | URBAN | Asset Failure | HV | 77 | 51 | 0.0027273 | 0.0053179 | N
15/09/2016 | 10:03 | ZN1068:PA27 | URBAN | Asset Failure | HV | 758 | 100 | 0.052542 | 0.052341 | N
15/09/2016 | 16:38 | 526:34639 | SHORT RURAL | Asset Failure | HV | 4 | 237 | 0.0043072 | 0.0018174 | N
18/09/2016 | 17:11 | 511:29876 | SHORT RURAL | Asset Failure | HV | 1,355 | 72 | 0.44307 | 0.61522 | N
20/09/2016 | 04:31 | ZN12610:PA16 | SHORT RURAL | Asset Failure | HV | 1,383 | 100 | 0.62793 | 0.62793 | N
20/09/2016 | 04:31 | ZN12610:PA6 | URBAN | Asset Failure | HV | 1,721 | 100 | 0.11886 | 0.11886 | N
21/09/2016 | 03:53 | ZN3472:PA8 | URBAN | Asset Failure | HV | 1,144 | 121 | 0.09593 | 0.079012 | N
21/09/2016 | 14:12 | ZN2835:PA33 | URBAN | Asset Failure | HV | 530 | 82 | 0.030021 | 0.036605 | N
20/09/2016 | 06:11 | ZN12610:PA16 | SHORT RURAL | Asset Failure | HV | 1,154 | 3 | 0.015719 | 0.52395 | N
20/09/2016 | 06:11 | ZN12610:PA22 | URBAN | Asset Failure | HV | 1,229 | 2 | 0.0016976 | 0.084881 | N
20/09/2016 | 06:11 | ZN12610:PA6 | URBAN | Asset Failure | HV | 1,721 | 8 | 0.009203 | 0.11886 | N
22/09/2016 | 17:55 | ZN342:PA35 | URBAN | Asset Failure | HV | 704 | 72 | 0.034998 | 0.048608 | N
23/09/2016 | 14:42 | ZN12690:PA19 | URBAN | Asset Failure | HV | 51 | 103 | 0.003627 | 0.0035213 | N
23/09/2016 | 19:31 | ZN15013:PA8 | URBAN | Asset Failure | HV | 99 | 89 | 0.0060836 | 0.0068355 | N
26/09/2016 | 10:58 | 810:74050 | SHORT RURAL | Asset Failure | HV | 47 | 249 | 0.053122 | 0.021334 | N
27/09/2016 | 15:02 | 513:48059 | SHORT RURAL | Asset Failure | HV | 5 | 113 | 0.0025644 | 0.0022694 | N
27/09/2016 | 17:41 | 516:48066 | SHORT RURAL | Asset Failure | HV | 4 | 254 | 0.0046114 | 0.0018155 | N
29/09/2016 | 14:31 | ZN931:PA10 | URBAN | Asset Failure | HV | 1,812 | 95 | 0.11928 | 0.12508 | N
02/10/2016 | 17:30 | 239:82129 | SHORT RURAL | Asset Failure | HV | 104 | 45 | 0.021185 | 0.047079 | N
02/10/2016 | 21:34 | ZN1287:PA12 | URBAN | Asset Failure | HV | 904 | 99 | 0.062098 | 0.06243 | N
03/10/2016 | 17:12 | ZN2196:PA5 | URBAN | Asset Failure | HV | 1,580 | 152 | 0.16634 | 0.10911 | N
04/10/2016 | 12:42 | 512:48049 | SHORT RURAL | Asset Failure | HV | 1 | 128 | 0.00057943 | 0.00045268 | N
04/10/2016 | 17:20 | ZN10991:PA1 | URBAN | Asset Failure | HV | 240 | 35 | 0.005801 | 0.016574 | N
04/10/2016 | 18:00 | 507:80932 | SHORT RURAL | Asset Failure | HV | 16 | 175 | 0.012675 | 0.0072429 | N
04/10/2016 | 18:20 | ZN10990:PA12 | URBAN | Asset Failure | HV | 422 | 105 | 0.0306 | 0.029143 | N
04/10/2016 | 19:46 | 511:29878 | SHORT RURAL | Asset Failure | HV | 1 | 414 | 0.0018741 | 0.00045268 | N
05/10/2016 | 08:09 | 242:81539 | URBAN | Asset Failure | HV | 1,565 | 59 | 0.063308 | 0.10808 | N
05/10/2016 | 21:05 | ZN5868:PA2 | URBAN | Asset Failure | HV | 300 | 52 | 0.010743 | 0.020718 | N
06/10/2016 | 11:47 | ZN188:PA4 | URBAN | Asset Failure | HV | 956 | 66 | 0.043836 | 0.066023 | N
07/10/2016 | 02:23 | ZN847:PA14 | URBAN | Asset Failure | HV | 388 | 73 | 0.019553 | 0.026785 | N
07/10/2016 | 15:00 | ZN384:PA70 | URBAN | Asset Failure | HV | 2 | 89 | 0.00012288 | 0.00013807 | N
07/10/2016 | 15:00 | ZN7481:PA17 | URBAN | Asset Failure | HV | 4,211 | 66 | 0.19123 | 0.2907 | N
08/10/2016 | 03:53 | ZN2602:PA17 | URBAN | Asset Failure | HV | 1,547 | 90 | 0.095894 | 0.10687 | N
08/10/2016 | 09:19 | 512:48049 | SHORT RURAL | Asset Failure | HV | 11 | 123 | 0.0061228 | 0.0049779 | N
09/10/2016 | 15:54 | ZN15014:PA16 | URBAN | Asset Failure | HV | 386 | 78 | 0.020705 | 0.026667 | N
10/10/2016 | 07:45 | ZN10990:PA6 | URBAN | Asset Failure | HV | 744 | 42 | 0.021392 | 0.0514 | N
10/10/2016 | 07:45 | ZN10990:PA8 | URBAN | Asset Failure | HV | 1,885 | 41 | 0.053393 | 0.13023 | N
10/10/2016 | 14:03 | ZN15009:PA5 | URBAN | Asset Failure | HV | 1,615 | 81 | 0.090021 | 0.11157 | N
10/10/2016 | 19:39 | 513:48059 | SHORT RURAL | Asset Failure | HV | 2 | 135 | 0.0012219 | 0.00090508 | N
10/10/2016 | 22:02 | 813:89055 | SHORT RURAL | Asset Failure | HV | 7 | 266 | 0.0084217 | 0.0031678 | N
11/10/2016 | 03:47 | 507:80925 | SHORT RURAL | Asset Failure | HV | 34 | 261 | 0.040139 | 0.015374 | N
11/10/2016 | 06:42 | 509:33395 | LONG RURAL | Asset Failure | HV | 1 | 783 | 0.27944 | 0.035689 | N
11/10/2016 | 15:38 | 515:35193 | SHORT RURAL | Asset Failure | HV | 4 | 195 | 0.0035269 | 0.0018087 | N
11/10/2016 | 17:26 | ZN874:PA18 | URBAN | Asset Failure | HV | 1,996 | 173 | 0.23811 | 0.13782 | N
13/10/2016 | 11:11 | ZN10990:PA11 | URBAN | Asset Failure | HV | 549 | 94 | 0.035681 | 0.037958 | N
13/10/2016 | 20:15 | 509:33395 | LONG RURAL | Asset Failure | HV | 1 | 25 | 0.0089222 | 0.035689 | N
14/10/2016 | 02:20 | 520:48172 | SHORT RURAL | Asset Failure | HV | 2 | 415 | 0.0037515 | 0.00090398 | N
14/10/2016 | 04:56 | ZN965:PA22 | URBAN | Asset Failure | HV | 561 | 58 | 0.022505 | 0.038788 | N
14/10/2016 | 21:08 | ZN180:PA18 | URBAN | Asset Failure | HV | 2,352 | 103 | 0.16672 | 0.16262 | N
15/10/2016 | 19:48 | ZN12690:PA7 | SHORT RURAL | Asset Failure | HV | 24 | 27 | 0.0028718 | 0.01081 | N
20/10/2016 | 13:06 | 509:33395 | LONG RURAL | Asset Failure | HV | 2 | 339 | 0.24197 | 0.071378 | N
21/10/2016 | 17:24 | 509:33397 | SHORT RURAL | Asset Failure | HV | 33 | 73 | 0.010917 | 0.014955 | N
22/10/2016 | 08:26 | ZN14143:PA17 | SHORT RURAL | Asset Failure | HV | 7 | 524 | 0.016514 | 0.0031516 | N
23/10/2016 | 11:09 | ZN2196:PA22 | URBAN | Asset Failure | HV | 25 | 44 | 0.00075964 | 0.0017265 | N
25/10/2016 | 23:42 | ZN847:PA39 | URBAN | Asset Failure | HV | 1,579 | 145 | 0.15759 | 0.10904 | N
28/10/2016 | 03:04 | ZN15006:PA12 | URBAN | Asset Failure | HV | 8 | 1,166 | 0.0064398 | 0.0005523 | N
29/10/2016 | 03:04 | ZN195:PA29 | URBAN | Asset Failure | HV | 1,108 | 96 | 0.073648 | 0.076494 | N
29/10/2016 | 09:13 | ZN80:PA30 | URBAN | Asset Failure | HV | 1,170 | 73 | 0.059208 | 0.080775 | N
30/10/2016 | 18:04 | 810:74062 | SHORT RURAL | Asset Failure | HV | 52 | 261 | 0.06109 | 0.023406 | N
30/10/2016 | 21:19 | 232:11457 | SHORT RURAL | Asset Failure | HV | 1,991 | 58 | 0.51959 | 0.89618 | N
01/11/2016 | 03:02 | ZN14891:PA20 | SHORT RURAL | Asset Failure | HV | 10 | 565 | 0.02542 | 0.0045016 | N
01/11/2016 | 04:48 | ZN1648:PA13 | URBAN | Asset Failure | HV | 66 | 83 | 0.0037904 | 0.0045567 | N
01/11/2016 | 09:02 | 515:35197 | LONG RURAL | Asset Failure | HV | 1 | 518 | 0.18467 | 0.035651 | N
02/11/2016 | 07:09 | 528:83019 | SHORT RURAL | Asset Failure | HV | 4 | 248 | 0.0044656 | 0.0018007 | N
03/11/2016 | 00:07 | ZN901:PA18 | URBAN | Asset Failure | HV | 1,479 | 111 | 0.11299 | 0.10209 | N
03/11/2016 | 15:42 | ZN2635:PA52 | URBAN | Asset Failure | HV | 1,042 | 66 | 0.047565 | 0.071922 | N
03/11/2016 | 16:11 | ZN262:PA16 | URBAN | Asset Failure | HV | 228 | 180 | 0.028327 | 0.015737 | N
05/11/2016 | 12:58 | ZN12630:PA23 | SHORT RURAL | Asset Failure | HV | 6 | 472 | 0.012741 | 0.0027 | N
05/11/2016 | 22:36 | ZN4545:PA4 | URBAN | Asset Failure | HV | 1,244 | 77 | 0.06583 | 0.08587 | N
06/11/2016 | 12:21 | 807:74184 | SHORT RURAL | Asset Failure | HV | 476 | 23 | 0.049846 | 0.2142 | N
06/11/2016 | 15:58 | ZN35800:PA16 | URBAN | Asset Failure | HV | 900 | 76 | 0.047413 | 0.062125 | N
07/11/2016 | 01:10 | ZN931:PA24 | URBAN | Asset Failure | HV | 309 | 70 | 0.014931 | 0.02133 | N
07/11/2016 | 08:03 | 802:82215 | SHORT RURAL | Asset Failure | HV | 5 | 257 | 0.0057809 | 0.00225 | N
08/11/2016 | 10:05 | ZN2635:PA33 | URBAN | Asset Failure | HV | 19 | 66 | 0.00087046 | 0.0013116 | N
08/11/2016 | 14:53 | 814:82289 | SHORT RURAL | Asset Failure | HV | 9 | 187 | 0.0075735 | 0.00405 | N
08/11/2016 | 18:42 | ZN15012:PA4 | URBAN | Asset Failure | HV | 1,180 | 90 | 0.073309 | 0.081455 | N
08/11/2016 | 18:42 | ZN15012:PA8 | URBAN | Asset Failure | HV | 832 | 94 | 0.054181 | 0.057432 | N
08/11/2016 | 19:10 | ZN2400:PA11 | SHORT RURAL | Asset Failure | HV | 669 | 192 | 0.57794 | 0.30105 | N
08/11/2016 | 19:49 | ZN9700:PA20 | URBAN | Asset Failure | HV | 3 | 1,322 | 0.0027384 | 0.00020709 | N
09/11/2016 | 20:43 | ZN15014:PA16 | URBAN | Asset Failure | HV | 382 | 109 | 0.028614 | 0.02637 | N
09/11/2016 | 20:43 | ZN15014:PA19 | URBAN | Asset Failure | HV | 1,893 | 93 | 0.12128 | 0.13068 | N
10/11/2016 | 14:15 | 235:2120 | SHORT RURAL | Asset Failure | HV | 21 | 15 | 0.0014175 | 0.0094502 | N
10/11/2016 | 22:08 | 509:33395 | LONG RURAL | Asset Failure | HV | 791 | 3 | 0.84539 | 28.1796 | N
10/11/2016 | 18:40 | ZN874:PA9 | URBAN | Asset Failure | HV | 370 | 72 | 0.018283 | 0.025542 | N
11/11/2016 | 10:07 | 801:74121 | LONG RURAL | Asset Failure | HV | 10 | 214 | 0.76238 | 0.35625 | N
11/11/2016 | 10:07 | 807:74180 | SHORT RURAL | Asset Failure | HV | 3 | 214 | 0.0028891 | 0.00135 | N
12/11/2016 | 03:56 | 513:48050 | SHORT RURAL | Asset Failure | HV | 200 | 189 | 0.17041 | 0.089954 | N
12/11/2016 | 05:02 | 807:74181 | SHORT RURAL | Asset Failure | HV | 705 | 123 | 0.38976 | 0.31709 | N
12/11/2016 | 08:52 | 807:74180 | SHORT RURAL | Asset Failure | HV | 2 | 218 | 0.001961 | 0.00089954 | N
12/11/2016 | 17:54 | 243:80075 | SHORT RURAL | Asset Failure | HV | 152 | 132 | 0.090502 | 0.068365 | N
12/11/2016 | 22:37 | ZN2196:PA11 | URBAN | Asset Failure | HV | 24 | 163 | 0.0026997 | 0.0016563 | N
13/11/2016 | 01:54 | ZN9245:PA3 | URBAN | Asset Failure | HV | 1,184 | 176 | 0.14366 | 0.081709 | N
13/11/2016 | 08:38 | ZN14892:PA14 | SHORT RURAL | Asset Failure | HV | 873 | 91 | 0.35709 | 0.39265 | N
13/11/2016 | 12:57 | 509:33399 | SHORT RURAL | Asset Failure | HV | 1 | 583 | 0.0026221 | 0.00044977 | N
13/11/2016 | 13:48 | 504:48031 | SHORT RURAL | Asset Failure | HV | 559 | 66 | 0.16478 | 0.25142 | N
13/11/2016 | 15:50 | 217:33612 | URBAN | Asset Failure | HV | 1,067 | 110 | 0.080992 | 0.073635 | N
14/11/2016 | 05:31 | ZN342:PA18 | URBAN | Asset Failure | HV | 756 | 206 | 0.10736 | 0.052172 | N
14/11/2016 | 09:43 | 528:83014 | SHORT RURAL | Asset Failure | HV | 73 | 107 | 0.035131 | 0.032833 | N
14/11/2016 | 18:31 | 507:80914 | SHORT RURAL | Asset Failure | HV | 7 | 129 | 0.0040614 | 0.0031484 | N
15/11/2016 | 03:50 | 504:48031 | SHORT RURAL | Asset Failure | HV | 92 | 165 | 0.06815 | 0.041379 | N
15/11/2016 | 03:50 | 507:80932 | SHORT RURAL | Asset Failure | HV | 17 | 65 | 0.00497 | 0.0076462 | N
15/11/2016 | 15:13 | ZN1285:PA10 | URBAN | Asset Failure | HV | 824 | 110 | 0.062625 | 0.056865 | N
16/11/2016 | 03:04 | ZN3472:PA22 | URBAN | Asset Failure | HV | 279 | 574 | 0.11049 | 0.019254 | N
16/11/2016 | 03:04 | ZN3472:PA29 | URBAN | Asset Failure | HV | 2 | 431 | 0.00059488 | 0.00013802 | N
16/11/2016 | 11:35 | 526:34640 | SHORT RURAL | Asset Failure | HV | 7 | 65 | 0.0020465 | 0.0031484 | N
16/11/2016 | 19:26 | 507:80932 | SHORT RURAL | Asset Failure | HV | 25 | 39 | 0.0043853 | 0.011244 | N
17/11/2016 | 02:31 | ZN35600:PA1 | URBAN | Asset Failure | HV | 2,728 | 103 | 0.19314 | 0.18821 | N
18/11/2016 | 21:15 | ZN180:PA35 | URBAN | Asset Failure | HV | 1,426 | 76 | 0.07477 | 0.098381 | N
19/11/2016 | 18:09 | 810:74054 | LONG RURAL | Asset Failure | HV | 1 | 381 | 0.13568 | 0.035613 | N
20/11/2016 | 07:51 | ZN2466:PA6 | URBAN | Asset Failure | HV | 23 | 119 | 0.0018815 | 0.0015869 | N
20/11/2016 | 09:37 | 515:35192 | SHORT RURAL | Asset Failure | HV | 10 | 133 | 0.0059593 | 0.0044965 | N
20/11/2016 | 11:08 | 528:83020 | SHORT RURAL | Asset Failure | HV | 6 | 27 | 0.00072843 | 0.0026979 | N
21/11/2016 | 17:42 | ZN2835:PA17 | URBAN | Asset Failure | HV | 307 | 107 | 0.022712 | 0.021181 | N
22/11/2016 | 11:55 | ZN4545:PA17 | URBAN | Asset Failure | HV | 48 | 120 | 0.0039742 | 0.0033118 | N
22/11/2016 | 11:55 | ZN4545:PA19 | URBAN | Asset Failure | HV | 500 | 69 | 0.0239 | 0.034498 | N
22/11/2016 | 13:48 | ZN931:PA3 | URBAN | Asset Failure | HV | 499 | 56 | 0.019296 | 0.034429 | N
22/11/2016 | 16:21 | ZN12660:PA6 | SHORT RURAL | Asset Failure | HV | 492 | 76 | 0.16813 | 0.22123 | N
22/11/2016 | 16:52 | ZN10995:PA12 | URBAN | Asset Failure | HV | 3 | 79 | 0.00016352 | 0.00020699 | N
22/11/2016 | 16:52 | ZN10995:PA5 | URBAN | Asset Failure | HV | 1,448 | 79 | 0.078926 | 0.099906 | N
22/11/2016 | 16:52 | ZN35800:PA10 | URBAN | Asset Failure | HV | 2 | 79 | 0.00010901 | 0.00013799 | N
23/11/2016 | 12:03 | ZN630:PA32 | URBAN | Asset Failure | HV | 327 | 51 | 0.011444 | 0.022562 | N
23/11/2016 | 12:52 | ZN35370:PA10 | SHORT RURAL | Asset Failure | HV | 513 | 136 | 0.31469 | 0.23067 | N
23/11/2016 | 23:00 | ZN180:PA33 | URBAN | Asset Failure | HV | 899 | 76 | 0.046853 | 0.062029 | N
24/11/2016 | 06:31 | 806:82662 | SHORT RURAL | Asset Failure | HV | 1 | 279 | 0.001254 | 0.00044945 | N
24/11/2016 | 06:55 | ZN35900:PA17 | URBAN | Asset Failure | HV | 1,787 | 119 | 0.14667 | 0.12326 | N
25/11/2016 | 11:40 | 509:33395 | LONG RURAL | Asset Failure | HV | 7 | 80 | 0.19936 | 0.2492 | N
25/11/2016 | 18:50 | 810:74058 | SHORT RURAL | Asset Failure | HV | 1 | 70 | 0.00031462 | 0.00044945 | N
28/11/2016 | 09:18 | ZN1068:PA17 | URBAN | Asset Failure | HV | 869 | 91 | 0.05468 | 0.059986 | N
28/11/2016 | 09:18 | ZN1068:PA26 | URBAN | Asset Failure | HV | 77 | 94 | 0.0049963 | 0.0053152 | N
28/11/2016 | 09:18 | ZN1068:PA27 | URBAN | Asset Failure | HV | 710 | 94 | 0.04607 | 0.04901 | N
25/11/2016 | 17:19 | ZN1287:PA12 | URBAN | Asset Failure | HV | 57 | 3 | 0.00011795 | 0.0039317 | N
25/11/2016 | 17:19 | ZN1287:PA4 | URBAN | Asset Failure | HV | 985 | 3 | 0.0020383 | 0.067943 | N
28/11/2016 | 14:43 | ZN2400:PA11 | SHORT RURAL | Asset Failure | HV | 613 | 274 | 0.75491 | 0.27552 | N
29/11/2016 | 03:17 | ZN36300:PA17 | URBAN | Asset Failure | HV | 768 | 124 | 0.065976 | 0.053014 | N
30/11/2016 | 00:51 | ZN195:PA22 | URBAN | Asset Failure | HV | 81 | 1,149 | 0.064244 | 0.0055913 | N
30/11/2016 | 11:14 | ZN14891:PA8 | SHORT RURAL | Asset Failure | HV | 1,363 | 112 | 0.68918 | 0.61261 | N
30/11/2016 | 16:33 | 807:74181 | SHORT RURAL | Asset Failure | HV | 456 | 68 | 0.14001 | 0.20495 | N
30/11/2016 | 16:33 | 807:74183 | SHORT RURAL | Asset Failure | HV | 86 | 107 | 0.041372 | 0.038653 | N
30/11/2016 | 16:33 | 801:74121 | LONG RURAL | Asset Failure | HV | 246 | 76 | 6.6362 | 8.7576 | N
01/12/2016 | 05:55 | 807:74184 | SHORT RURAL | Asset Failure | HV | 1 | 340 | 0.0015275 | 0.00044927 | N
01/12/2016 | 14:38 | 220:8688 | URBAN | Asset Failure | HV | 453 | 90 | 0.028205 | 0.031261 | N
01/12/2016 | 15:21 | 502:48010 | SHORT RURAL | Asset Failure | HV | 3,585 | 61 | 0.98176 | 1.6106 | N
01/12/2016 | 15:45 | 508:82579 | SHORT RURAL | Asset Failure | HV | 382 | 380 | 0.6513 | 0.17162 | N
02/12/2016 | 02:38 | 225:13446 | URBAN | Asset Failure | HV | 1,559 | 92 | 0.099297 | 0.10758 | N
02/12/2016 | 21:10 | ZN12690:PA7 | SHORT RURAL | Asset Failure | HV | 828 | 99 | 0.36721 | 0.37199 | N
02/12/2016 | 23:52 | ZN188:PA15 | URBAN | Asset Failure | HV | 2 | 447 | 0.00061694 | 0.00013802 | N
02/12/2016 | 23:52 | ZN8100:PA28 | URBAN | Asset Failure | HV | 388 | 87 | 0.023373 | 0.026775 | N
03/12/2016 | 00:25 | ZN262:PA27 | URBAN | Asset Failure | HV | 1,091 | 60 | 0.045255 | 0.075234 | N
04/12/2016 | 01:12 | ZN262:PA30 | URBAN | Asset Failure | HV | 2,053 | 97 | 0.13775 | 0.14157 | N
05/12/2016 | 01:45 | ZN3672:PA13 | URBAN | Asset Failure | HV | 726 | 36 | 0.018023 | 0.050064 | N
01/12/2016 | 10:32 | 807:74179 | SHORT RURAL | Asset Failure | HV | 1 | 453 | 0.0020352 | 0.00044927 | N
05/12/2016 | 12:44 | ZN9035:PA11 | URBAN | Asset Failure | HV | 1,944 | 60 | 0.079892 | 0.13406 | N
05/12/2016 | 13:12 | ZN2466:PA19 | URBAN | Asset Failure | HV | 24 | 88 | 0.0014488 | 0.001655 | N
05/12/2016 | 15:14 | 511:29878 | SHORT RURAL | Asset Failure | HV | 8 | 656 | 0.023578 | 0.0035942 | N
05/12/2016 | 15:40 | 238:34141 | SHORT RURAL | Asset Failure | HV | 15 | 634 | 0.042729 | 0.0067391 | N
05/12/2016 | 15:35 | 813:89062 | SHORT RURAL | Asset Failure | HV | 3 | 550 | 0.007413 | 0.0013478 | N
05/12/2016 | 15:59 | ZN35500:PA27 | URBAN | Asset Failure | HV | 1,731 | 110 | 0.13186 | 0.11937 | N
05/12/2016 | 16:34 | ZN2400:PA18 | SHORT RURAL | Asset Failure | HV | 1,342 | 129 | 0.77746 | 0.60292 | N
05/12/2016 | 16:33 | ZN35370:PA8 | SHORT RURAL | Asset Failure | HV | 98 | 342 | 0.15058 | 0.044029 | N
05/12/2016 | 20:15 | 511:29878 | SHORT RURAL | Asset Failure | HV | 4 | 476 | 0.0085586 | 0.0017971 | N
06/12/2016 | 08:28 | ZN129:PA28 | URBAN | Asset Failure | HV | 939 | 96 | 0.061893 | 0.064754 | N
06/12/2016 | 08:50 | 528:83013 | URBAN | Asset Failure | HV | 1,204 | 108 | 0.089793 | 0.083029 | N
06/12/2016 | 16:42 | ZN10995:PA1 | URBAN | Asset Failure | HV | 81 | 151 | 0.0084346 | 0.0055858 | N
06/12/2016 | 18:46 | 238:34148 | SHORT RURAL | Asset Failure | HV | 628 | 83 | 0.23491 | 0.28214 | N
07/12/2016 | 00:24 | ZN14144:PA10 | SHORT RURAL | Asset Failure | HV | 668 | 60 | 0.17934 | 0.30012 | N
07/12/2016 | 01:03 | ZN847:PA14 | URBAN | Asset Failure | HV | 387 | 51 | 0.013611 | 0.026688 | N
07/12/2016 | 03:07 | 812:19072 | SHORT RURAL | Asset Failure | HV | 203 | 142 | 0.12942 | 0.091204 | N
08/12/2016 | 02:56 | ZN12690:PA7 | SHORT RURAL | Asset Failure | HV | 292 | 87 | 0.1144 | 0.13121 | N
08/12/2016 | 13:46 | 504:48028 | URBAN | Asset Failure | HV | 41 | 124 | 0.0035047 | 0.0028263 | N
09/12/2016 | 01:09 | ZN12620:PA1 | SHORT RURAL | Asset Failure | HV | 37 | 446 | 0.07415 | 0.016626 | N
09/12/2016 | 02:51 | ZN2635:PA33 | URBAN | Asset Failure | HV | 19 | 57 | 0.0007466 | 0.0013098 | N
09/12/2016 | 09:37 | 512:48049 | SHORT RURAL | Asset Failure | HV | 7 | 249 | 0.007832 | 0.0031454 | N
09/12/2016 | 12:14 | ZN14143:PA14 | URBAN | Asset Failure | HV | 66 | 47 | 0.002144 | 0.0045499 | N
09/12/2016 | 18:25 | ZN1850:PA9 | URBAN | Asset Failure | HV | 110 | 89 | 0.006749 | 0.0075832 | N
10/12/2016 | 02:12 | ZN7481:PA9 | URBAN | Asset Failure | HV | 1,675 | 87 | 0.10007 | 0.11547 | N
11/12/2016 | 17:45 | ZN36200:PA8 | SHORT RURAL | Asset Failure | HV | 481 | 95 | 0.20533 | 0.21614 | N
11/12/2016 | 19:25 | 514:18137 | SHORT RURAL | Asset Failure | HV | 55 | 161 | 0.039696 | 0.024714 | N
12/12/2016 | 20:15 | 235:2120 | SHORT RURAL | Asset Failure | HV | 2 | 179 | 0.0016088 | 0.00089871 | N
13/12/2016 | 10:49 | ZN901:PA20 | URBAN | Asset Failure | HV | 832 | 112 | 0.06416 | 0.05736 | N
13/12/2016 | 13:26 | ZN12580:PA8 | URBAN | Asset Failure | HV | 306 | 66 | 0.013853 | 0.021096 | N
13/12/2016 | 16:00 | ZN1610:PA12 | URBAN | Asset Failure | HV | 451 | 58 | 0.018034 | 0.031093 | N
13/12/2016 | 17:33 | ZN12570:PA21 | URBAN | Asset Failure | HV | 2,217 | 119 | 0.18165 | 0.15284 | N
13/12/2016 | 17:33 | ZN12580:PA2 | URBAN | Asset Failure | HV | 288 | 138 | 0.0274 | 0.019855 | N
13/12/2016 | 22:22 | ZN3922:PA5 | URBAN | Asset Failure | HV | 2,430 | 160 | 0.26744 | 0.16753 | N
14/12/2016 | 12:23 | 813:89061 | LONG RURAL | Asset Failure | HV | 57 | 22 | 0.44101 | 2.0292 | N
14/12/2016 | 12:34 | ZN12640:PA13 | SHORT RURAL | Asset Failure | HV | 381 | 776 | 1.3286 | 0.17121 | N
14/12/2016 | 18:15 | ZN12620:PA11 | SHORT RURAL | Asset Failure | HV | 538 | 89 | 0.21516 | 0.24176 | N
14/12/2016 | 19:02 | ZN1610:PA10 | URBAN | Asset Failure | HV | 51 | 70 | 0.0024558 | 0.0035161 | N
15/12/2016 | 04:30 | ZN1610:PA12 | URBAN | Asset Failure | HV | 450 | 85 | 0.026405 | 0.031016 | N
15/12/2016 | 05:59 | ZN965:PA33 | URBAN | Asset Failure | HV | 43 | 101 | 0.0029934 | 0.0029637 | N
15/12/2016 | 06:34 | ZN12580:PA14 | URBAN | Asset Failure | HV | 57 | 55 | 0.0021641 | 0.0039287 | N
15/12/2016 | 14:59 | 243:80074 | SHORT RURAL | Asset Failure | HV | 1,821 | 43 | 0.35301 | 0.81779 | N
15/12/2016 | 15:35 | 502:48010 | SHORT RURAL | Asset Failure | HV | 18 | 30 | 0.0024251 | 0.0080836 | N
15/12/2016 | 23:44 | 513:48059 | SHORT RURAL | Asset Failure | HV | 141 | 85 | 0.054111 | 0.063322 | N
16/12/2016 | 13:30 | 812:19072 | SHORT RURAL | Asset Failure | HV | 1 | 45 | 0.00020209 | 0.00044908 | N
17/12/2016 | 07:11 | ZN1610:PA12 | URBAN | Asset Failure | HV | 445 | 24 | 0.0074868 | 0.030672 | N
17/12/2016 | 07:36 | ZN15006:PA12 | URBAN | Asset Failure | HV | 86 | 117 | 0.0069206 | 0.0059277 | N
17/12/2016 | 10:07 | ZN35400:PA110 | URBAN | Asset Failure | HV | 1,885 | 138 | 0.17966 | 0.12993 | N
17/12/2016 | 22:33 | ZN847:PA46 | URBAN | Asset Failure | HV | 998 | 99 | 0.068101 | 0.068789 | N
17/12/2016 | 23:07 | ZN80:PA24 | URBAN | Asset Failure | HV | 1,633 | 60 | 0.067359 | 0.11256 | N
18/12/2016 | 01:19 | ZN9700:PA16 | URBAN | Asset Failure | HV | 119 | 71 | 0.0058236 | 0.0082022 | N
18/12/2016 | 02:07 | ZN3922:PA17 | SHORT RURAL | Asset Failure | HV | 1,016 | 82 | 0.37503 | 0.45626 | N
18/12/2016 | 07:28 | 238:34141 | SHORT RURAL | Asset Failure | HV | 8 | 202 | 0.0072571 | 0.0035926 | N
20/12/2016 | 00:23 | ZN13000:PA7 | SHORT RURAL | Asset Failure | HV | 45 | 127 | 0.025665 | 0.020209 | N
21/12/2016 | 15:16 | 513:48050 | SHORT RURAL | Asset Failure | HV | 200 | 123 | 0.11037 | 0.08982 | N
21/12/2016 | 16:43 | 513:48056 | SHORT RURAL | Asset Failure | HV | 410 | 31 | 0.057619 | 0.18413 | N
22/12/2016 | 15:27 | ZN342:PA17 | URBAN | Asset Failure | HV | 1,439 | 131 | 0.1299 | 0.099158 | N
22/12/2016 | 15:27 | ZN342:PA23 | URBAN | Asset Failure | HV | 653 | 126 | 0.056886 | 0.044996 | N
23/12/2016 | 19:42 | 221:11894 | URBAN | Asset Failure | HV | 57 | 68 | 0.0026709 | 0.0039278 | N
24/12/2016 | 08:39 | 228:7491 | URBAN | Asset Failure | HV | 105 | 6 | 0.00043412 | 0.0072353 | N
24/12/2016 | 11:03 | 512:48046 | SHORT RURAL | Asset Failure | HV | 6 | 137 | 0.0036906 | 0.0026938 | N
24/12/2016 | 17:44 | 520:48172 | SHORT RURAL | Asset Failure | HV | 116 | 488 | 0.2539 | 0.052081 | N
24/12/2016 | 20:03 | ZN1850:PA11 | URBAN | Asset Failure | HV | 289 | 102 | 0.020313 | 0.019914 | N
25/12/2016 | 07:35 | 813:89061 | LONG RURAL | Asset Failure | HV | 24 | 183 | 1.5622 | 0.85501 | N
26/12/2016 | 12:20 | 812:19072 | SHORT RURAL | Asset Failure | HV | 5 | 70 | 0.0015714 | 0.0022448 | N
26/12/2016 | 09:48 | 513:48050 | SHORT RURAL | Asset Failure | HV | 7 | 117 | 0.0036744 | 0.0031428 | N
26/12/2016 | 17:48 | ZN3922:PA22 | URBAN | Asset Failure | HV | 916 | 84 | 0.053021 | 0.063121 | N
27/12/2016 | 19:17 | ZN874:PA2 | URBAN | Asset Failure | HV | 218 | 69 | 0.010344 | 0.015022 | N
27/12/2016 | 19:17 | ZN874:PA9 | URBAN | Asset Failure | HV | 292 | 72 | 0.014487 | 0.020121 | N
28/12/2016 | 03:40 | ZN12580:PA10 | URBAN | Asset Failure | HV | 1,598 | 74 | 0.081597 | 0.11012 | N
28/12/2016 | 08:34 | 202:34260 | URBAN | Asset Failure | HV | 119 | 86 | 0.0070317 | 0.0082002 | N
28/12/2016 | 14:10 | 515:35197 | LONG RURAL | Asset Failure | HV | 2 | 40 | 0.0285 | 0.07125 | N
28/12/2016 | 12:03 | 807:74184 | SHORT RURAL | Asset Failure | HV | 2 | 186 | 0.0016702 | 0.00089794 | N
28/12/2016 | 16:57 | ZN4545:PA29 | URBAN | Asset Failure | HV | 75 | 183 | 0.0094578 | 0.0051682 | N
28/12/2016 | 22:04 | ZN901:PA9 | URBAN | Asset Failure | HV | 28 | 32 | 0.00061743 | 0.0019295 | N
29/12/2016 | 08:33 | ZN342:PA17 | URBAN | Asset Failure | HV | 1,439 | 60 | 0.059576 | 0.099161 | N
29/12/2016 | 08:33 | ZN342:PA23 | URBAN | Asset Failure | HV | 592 | 65 | 0.026516 | 0.040794 | N
29/12/2016 | 08:44 | 812:19072 | SHORT RURAL | Asset Failure | HV | 2 | 294 | 0.00264 | 0.00089795 | N
29/12/2016 | 16:30 | 228:7490 | SHORT RURAL | Asset Failure | HV | 1,555 | 59 | 0.4129 | 0.69815 | N
29/12/2016 | 16:54 | ZN1850:PA11 | URBAN | Asset Failure | HV | 289 | 59 | 0.011719 | 0.019915 | N
29/12/2016 | 17:30 | ZN12690:PA7 | SHORT RURAL | Asset Failure | HV | 832 | 104 | 0.38829 | 0.37355 | N
29/12/2016 | 17:40 | ZN9037:PA17 | URBAN | Asset Failure | HV | 35 | 54 | 0.0013024 | 0.0024118 | N
29/12/2016 | 17:49 | ZN14892:PA5 | URBAN | Asset Failure | HV | 1 | 1,336 | 0.00092063 | 6.891e-05 | N
29/12/2016 | 19:08 | ZN2635:PA52 | URBAN | Asset Failure | HV | 1,048 | 125 | 0.090254 | 0.072217 | N
29/12/2016 | 19:16 | 227:13015 | SHORT RURAL | Asset Failure | HV | 29 | 76 | 0.009846 | 0.01302 | N
30/12/2016 | 02:40 | ZN12570:PA21 | URBAN | Asset Failure | HV | 1,069 | 66 | 0.048571 | 0.073665 | N
30/12/2016 | 02:40 | ZN12580:PA2 | URBAN | Asset Failure | HV | 289 | 75 | 0.014936 | 0.019915 | N
30/12/2016 | 05:46 | ZN2466:PA30 | URBAN | Asset Failure | HV | 1,851 | 101 | 0.12844 | 0.12755 | N
30/12/2016 | 13:08 | ZN9037:PA17 | URBAN | Asset Failure | HV | 35 | 195 | 0.0046942 | 0.0024119 | N
30/12/2016 | 13:29 | 511:29878 | SHORT RURAL | Asset Failure | HV | 4 | 136 | 0.0024425 | 0.0017959 | N
30/12/2016 | 23:30 | 232:11454 | SHORT RURAL | Asset Failure | HV | 82 | 20 | 0.0073633 | 0.036817 | N
31/12/2016 | 00:11 | ZN15006:PA12 | URBAN | Asset Failure | HV | 821 | 74 | 0.041866 | 0.056576 | N
31/12/2016 | 00:56 | ZN14892:PA6 | SHORT RURAL | Asset Failure | HV | 1,676 | 109 | 0.81955 | 0.75249 | N
31/12/2016 | 11:49 | ZN15006:PA6 | URBAN | Asset Failure | HV | 327 | 61 | 0.013746 | 0.022534 | N
31/12/2016 | 17:56 | 516:48067 | SHORT RURAL | Asset Failure | HV | 2 | 74 | 0.00066449 | 0.00089796 | N
25/12/2016 | 10:45 | 813:89061 | LONG RURAL | Asset Failure | HV | 24 | 86 | 0.7321 | 0.85501 | N
04/01/2017 | 12:02 | ZN14143:PA17 | SHORT RURAL | Asset Failure | HV | 14 | 272 | 0.017097 | 0.0062858 | N
04/01/2017 | 14:20 | 523:33501 | SHORT RURAL | Asset Failure | HV | 48 | 50 | 0.010689 | 0.021551 | N
05/01/2017 | 11:40 | 810:74054 | LONG RURAL | Asset Failure | HV | 3 | 275 | 0.29391 | 0.10688 | N
05/01/2017 | 12:11 | ZN9035:PA11 | URBAN | Asset Failure | HV | 1 | 13 | 8.9587e-06 | 6.8913e-05 | N
05/01/2017 | 12:11 | ZN9037:PA10 | URBAN | Asset Failure | HV | 892 | 13 | 0.0079912 | 0.061471 | N
05/01/2017 | 12:11 | ZN9037:PA16 | URBAN | Asset Failure | HV | 397 | 14 | 0.0039425 | 0.027359 | N
06/01/2017 | 11:08 | 812:19071 | SHORT RURAL | Asset Failure | HV | 812 | 33 | 0.11887 | 0.36458 | N
06/01/2017 | 12:12 | ZN2310:PA72 | URBAN | Asset Failure | HV | 688 | 130 | 0.061757 | 0.047413 | N
06/01/2017 | 12:12 | ZN35800:PA22 | URBAN | Asset Failure | HV | 2 | 139 | 0.00019158 | 0.00013783 | N
06/01/2017 | 23:38 | 232:11454 | SHORT RURAL | Asset Failure | HV | 753 | 83 | 0.27901 | 0.33809 | N
07/01/2017 | 02:13 | 261:81882 | URBAN | Asset Failure | HV | 68 | 73 | 0.0034198 | 0.0046847 | N
07/01/2017 | 22:25 | ZN15006:PA12 | URBAN | Asset Failure | HV | 564 | 126 | 0.048975 | 0.038856 | N
07/01/2017 | 23:35 | ZN14892:PA17 | URBAN | Asset Failure | HV | 510 | 61 | 0.021448 | 0.035135 | N
08/01/2017 | 08:28 | ZN180:PA10 | URBAN | Asset Failure | HV | 1 | 139 | 9.5761e-05 | 6.8892e-05 | N
08/01/2017 | 08:28 | ZN2635:PA44 | URBAN | Asset Failure | HV | 997 | 73 | 0.049927 | 0.068686 | N
08/01/2017 | 18:31 | ZN340:PA10 | URBAN | Asset Failure | HV | 125 | 55 | 0.0047384 | 0.0086116 | N
08/01/2017 | 18:31 | ZN630:PA14 | URBAN | Asset Failure | HV | 1 | 58 | 3.9958e-05 | 6.8892e-05 | N
09/01/2017 | 16:36 | ZN2602:PA15 | URBAN | Asset Failure | HV | 2 | 64 | 8.8182e-05 | 0.00013778 | N
09/01/2017 | 16:36 | ZN2602:PA4 | URBAN | Asset Failure | HV | 1,774 | 62 | 0.075617 | 0.12222 | N
09/01/2017 | 17:52 | ZN10994:PA12 | URBAN | Asset Failure | HV | 2,076 | 51 | 0.072432 | 0.14302 | N
09/01/2017 | 17:52 | ZN10994:PA7 | URBAN | Asset Failure | HV | 1 | 112 | 7.716e-05 | 6.8892e-05 | N
10/01/2017 | 06:36 | 523:33503 | URBAN | Asset Failure | HV | 772 | 84 | 0.044676 | 0.053185 | N
11/01/2017 | 14:16 | ZN15002:PA2 | URBAN | Asset Failure | HV | 9 | 234 | 0.0014509 | 0.00062005 | N
11/01/2017 | 14:55 | ZN35335:PA16 | URBAN | Asset Failure | HV | 199 | 69 | 0.0094633 | 0.01371 | N
11/01/2017 | 15:14 | ZN195:PA11 | URBAN | Asset Failure | HV | 1,271 | 113 | 0.098948 | 0.087564 | N
11/01/2017 | 15:25 | ZN1285:PA24 | URBAN | Asset Failure | HV | 57 | 289 | 0.011349 | 0.003927 | N
11/01/2017 | 15:25 | ZN35800:PA15 | URBAN | Asset Failure | HV | 3,054 | 222 | 0.46783 | 0.2104 | N
11/01/2017 | 15:25 | ZN35800:PA16 | URBAN | Asset Failure | HV | 629 | 226 | 0.097936 | 0.043334 | N
11/01/2017 | 15:25 | ZN35800:PA7 | URBAN | Asset Failure | HV | 1 | 226 | 0.0001557 | 6.8894e-05 | N
11/01/2017 | 15:43 | ZN187:PA30 | URBAN | Asset Failure | HV | 1,893 | 81 | 0.10568 | 0.13042 | N
11/01/2017 | 15:54 | ZN12580:PA10 | URBAN | Asset Failure | HV | 1,588 | 195 | 0.21351 | 0.1094 | N
11/01/2017 | 17:30 | 528:83019 | SHORT RURAL | Asset Failure | HV | 4 | 273 | 0.0049011 | 0.0017953 | N
11/01/2017 | 17:47 | ZN14892:PA14 | SHORT RURAL | Asset Failure | HV | 878 | 161 | 0.63532 | 0.39406 | N
11/01/2017 | 17:47 | ZN14892:PA16 | URBAN | Asset Failure | HV | 1 | 158 | 0.00010885 | 6.8894e-05 | N
11/01/2017 | 17:54 | ZN12650:PA13 | SHORT RURAL | Asset Failure | HV | 1,815 | 115 | 0.93384 | 0.81461 | N
11/01/2017 | 17:59 | 227:13015 | SHORT RURAL | Asset Failure | HV | 1,860 | 66 | 0.54728 | 0.83481 | N
11/01/2017 | 18:55 | ZN15006:PA8 | URBAN | Asset Failure | HV | 1,910 | 89 | 0.11698 | 0.13159 | N
12/01/2017 | 00:48 | 220:8689 | URBAN | Asset Failure | HV | 86 | 182 | 0.010774 | 0.0059241 | N
13/01/2017 | 14:24 | ZN1285:PA32 | URBAN | Asset Failure | HV | 47 | 96 | 0.0031081 | 0.0032376 | N
13/01/2017 | 14:24 | ZN1285:PA35 | URBAN | Asset Failure | HV | 381 | 88 | 0.023049 | 0.026245 | N
13/01/2017 | 15:13 | ZN36300:PA19 | URBAN | Asset Failure | HV | 1,377 | 100 | 0.0953 | 0.094856 | N
13/01/2017 | 18:10 | ZN36300:PA19 | URBAN | Asset Failure | HV | 523 | 42 | 0.015131 | 0.036027 | N
14/01/2017 | 01:11 | ZN965:PA6 | URBAN | Asset Failure | HV | 1,072 | 119 | 0.087827 | 0.073846 | N
15/01/2017 | 06:39 | ZN35370:PA8 | SHORT RURAL | Asset Failure | HV | 512 | 112 | 0.25776 | 0.22981 | N
16/01/2017 | 08:19 | ZN12650:PA5 | URBAN | Asset Failure | HV | 114 | 49 | 0.0038741 | 0.007853 | N
16/01/2017 | 15:09 | ZN1850:PA9 | URBAN | Asset Failure | HV | 449 | 143 | 0.04423 | 0.03093 | N
16/01/2017 | 15:51 | ZN5868:PA24 | URBAN | Asset Failure | HV | 69 | 62 | 0.00296 | 0.0047531 | N
16/01/2017 | 21:09 | ZN1068:PA17 | URBAN | Asset Failure | HV | 355 | 175 | 0.042678 | 0.024454 | N
16/01/2017 | 21:09 | ZN1068:PA26 | URBAN | Asset Failure | HV | 2,901 | 101 | 0.20143 | 0.19984 | N
16/01/2017 | 21:09 | ZN3472:PA33 | URBAN | Asset Failure | HV | 66 | 191 | 0.0086837 | 0.0045465 | N
17/01/2017 | 03:52 | ZN2635:PA57 | URBAN | Asset Failure | HV | 1,242 | 61 | 0.052162 | 0.085557 | N
17/01/2017 | 18:14 | ZN1850:PA10 | URBAN | Asset Failure | HV | 912 | 328 | 0.20619 | 0.062824 | N
17/01/2017 | 18:14 | ZN1850:PA8 | URBAN | Asset Failure | HV | 2 | 1,211 | 0.0016684 | 0.00013777 | N
17/01/2017 | 18:14 | ZN3472:PA28 | URBAN | Asset Failure | HV | 479 | 367 | 0.12103 | 0.032997 | N
18/01/2017 | 12:29 | ZN2466:PA7 | URBAN | Asset Failure | HV | 275 | 108 | 0.020413 | 0.018944 | N
18/01/2017 | 12:43 | 528:83019 | SHORT RURAL | Asset Failure | HV | 2 | 101 | 0.00090668 | 0.00089771 | N
06/01/2017 | 12:48 | 232:11454 | SHORT RURAL | Asset Failure | HV | 1,853 | 138 | 1.1492 | 0.83199 | N
18/01/2017 | 14:41 | 230:81434 | URBAN | Asset Failure | HV | 683 | 92 | 0.043235 | 0.04705 | N
18/01/2017 | 17:56 | 813:89061 | LONG RURAL | Asset Failure | HV | 110 | 81 | 3.1585 | 3.9188 | N
18/01/2017 | 21:34 | 202:34245 | URBAN | Asset Failure | HV | 149 | 56 | 0.0057479 | 0.010264 | N
18/01/2017 | 21:27 | ZN7481:PA19 | URBAN | Asset Failure | HV | 139 | 48 | 0.0045934 | 0.0095753 | N
19/01/2017 | 08:29 | ZN180:PA15 | URBAN | Asset Failure | HV | 1 | 115 | 7.9214e-05 | 6.8881e-05 | N
19/01/2017 | 08:29 | ZN180:PA17 | URBAN | Asset Failure | HV | 22 | 115 | 0.0017427 | 0.0015154 | N
19/01/2017 | 08:29 | ZN180:PA7 | URBAN | Asset Failure | HV | 1,477 | 112 | 0.11401 | 0.10174 | N
19/01/2017 | 13:20 | 810:74054 | LONG RURAL | Asset Failure | HV | 3 | 60 | 0.064148 | 0.10691 | N
19/01/2017 | 12:00 | 813:89062 | SHORT RURAL | Asset Failure | HV | 1 | 90 | 0.00040394 | 0.00044882 | N
19/01/2017 | 10:59 | ZN4545:PA31 | URBAN | Asset Failure | HV | 2,991 | 94 | 0.19374 | 0.20602 | N
20/01/2017 | 15:29 | 807:74184 | SHORT RURAL | Asset Failure | HV | 9 | 96 | 0.0038778 | 0.0040393 | N
20/01/2017 | 18:34 | ZN14144:PA10 | SHORT RURAL | Asset Failure | HV | 4 | 176 | 0.0031597 | 0.0017953 | N
20/01/2017 | 20:12 | 239:82133 | URBAN | Asset Failure | HV | 89 | 58 | 0.0035557 | 0.0061305 | N
20/01/2017 | 20:58 | ZN12690:PA24 | SHORT RURAL | Asset Failure | HV | 5 | 722 | 0.016202 | 0.0022441 | N
20/01/2017 | 22:19 | 507:80925 | SHORT RURAL | Asset Failure | HV | 7 | 431 | 0.013541 | 0.0031417 | N
21/01/2017 | 00:27 | 512:48049 | SHORT RURAL | Asset Failure | HV | 11 | 48 | 0.0023697 | 0.004937 | N
21/01/2017 | 13:37 | ZN12630:PA1 | SHORT RURAL | Asset Failure | HV | 3 | 223 | 0.0029983 | 0.0013464 | N
21/01/2017 | 21:35 | 814:82283 | SHORT RURAL | Asset Failure | HV | 14 | 30 | 0.001885 | 0.0062834 | N
21/01/2017 | 17:40 | 813:89055 | SHORT RURAL | Asset Failure | HV | 584 | 96 | 0.25146 | 0.26211 | N
22/01/2017 | 21:02 | 513:48059 | SHORT RURAL | Asset Failure | HV | 4 | 158 | 0.0028365 | 0.0017953 | N
24/01/2017 | 01:27 | 520:48172 | SHORT RURAL | Asset Failure | HV | 60 | 273 | 0.073484 | 0.026932 | N
23/01/2017 | 08:55 | 515:35197 | LONG RURAL | Asset Failure | HV | 2 | 80 | 0.057021 | 0.071276 | N
24/01/2017 | 11:29 | 511:29878 | SHORT RURAL | Asset Failure | HV | 2 | 171 | 0.0015351 | 0.00089773 | N
24/01/2017 | 17:37 | ZN1610:PA11 | URBAN | Asset Failure | HV | 271 | 134 | 0.025007 | 0.018667 | N
24/01/2017 | 17:37 | ZN2835:PA15 | URBAN | Asset Failure | HV | 1 | 136 | 9.3682e-05 | 6.8884e-05 | N
24/01/2017 | 20:42 | ZN15008:PA5 | URBAN | Asset Failure | HV | 1,992 | 142 | 0.19434 | 0.13722 | N
25/01/2017 | 12:06 | ZN2568:PA8 | URBAN | Asset Failure | HV | 6 | 51 | 0.00021079 | 0.00041331 | N
26/01/2017 | 03:06 | ZN2310:PA65 | URBAN | Asset Failure | HV | 2,232 | 67 | 0.1033 | 0.15374 | N
26/01/2017 | 22:19 | ZN12580:PA4 | URBAN | Asset Failure | HV | 2,112 | 60 | 0.08761 | 0.14548 | N
29/01/2017 | 17:03 | 509:33395 | LONG RURAL | Asset Failure | HV | 4 | 162 | 0.23093 | 0.14255 | N
29/01/2017 | 16:21 | 813:89061 | LONG RURAL | Asset Failure | HV | 607 | 320 | 69.2969 | 21.6322 | N
29/01/2017 | 16:21 | 813:89065 | URBAN | Asset Failure | HV | 688 | 353 | 0.16725 | 0.047386 | N
29/01/2017 | 17:50 | 813:89055 | SHORT RURAL | Asset Failure | HV | 1 | 250 | 0.0011206 | 0.00044826 | N
29/01/2017 | 18:35 | 813:89055 | SHORT RURAL | Asset Failure | HV | 30 | 445 | 0.059842 | 0.013448 | N
30/01/2017 | 07:37 | 813:89062 | SHORT RURAL | Asset Failure | HV | 5 | 446 | 0.0099961 | 0.0022413 | N
30/01/2017 | 13:21 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 18 | 173 | 0.013981 | 0.0080686 | N
30/01/2017 | 17:45 | ZN35370:PA10 | SHORT RURAL | Asset Failure | HV | 319 | 78 | 0.11143 | 0.14299 | N
30/01/2017 | 17:12 | ZN2400:PA18 | SHORT RURAL | Asset Failure | HV | 49 | 183 | 0.040195 | 0.021965 | N
31/01/2017 | 08:25 | ZN14143:PA6 | URBAN | Asset Failure | HV | 1 | 110 | 7.5764e-05 | 6.8876e-05 | N
31/01/2017 | 14:08 | ZN874:PA17 | URBAN | Asset Failure | HV | 849 | 126 | 0.073695 | 0.058476 | N
01/02/2017 | 00:36 | ZN180:PA27 | URBAN | Asset Failure | HV | 987 | 142 | 0.096364 | 0.067981 | N
01/02/2017 | 00:36 | ZN180:PA32 | URBAN | Asset Failure | HV | 2,521 | 183 | 0.31694 | 0.17364 | N
01/02/2017 | 00:36 | ZN180:PA34 | URBAN | Asset Failure | HV | 172 | 176 | 0.02085 | 0.011847 | N
01/02/2017 | 06:53 | 511:29878 | SHORT RURAL | Asset Failure | HV | 5 | 347 | 0.0077774 | 0.0022413 | N
01/02/2017 | 09:28 | ZN12630:PA8 | SHORT RURAL | Asset Failure | HV | 3 | 127 | 0.0017079 | 0.0013448 | N
01/02/2017 | 11:13 | ZN180:PA29 | URBAN | Asset Failure | HV | 1,190 | 79 | 0.064853 | 0.081963 | N
03/02/2017 | 06:45 | ZN14891:PA5 | SHORT RURAL | Asset Failure | HV | 6 | 225 | 0.0060507 | 0.0026892 | N
04/02/2017 | 02:45 | 257:81994 | URBAN | Asset Failure | HV | 745 | 68 | 0.03499 | 0.051308 | N
04/02/2017 | 14:29 | 509:33395 | LONG RURAL | Asset Failure | HV | 185 | 632 | 41.6143 | 6.5883 | N
04/02/2017 | 20:00 | 812:19071 | SHORT RURAL | Asset Failure | HV | 1 | 970 | 0.0043475 | 0.0004482 | N
04/02/2017 | 17:14 | 813:89061 | LONG RURAL | Asset Failure | HV | 173 | 49 | 2.9986 | 6.161 | N
04/02/2017 | 17:14 | 813:89065 | URBAN | Asset Failure | HV | 687 | 202 | 0.09573 | 0.047313 | N
04/02/2017 | 17:04 | 526:34636 | SHORT RURAL | Asset Failure | HV | 126 | 174 | 0.098366 | 0.056473 | N
04/02/2017 | 17:15 | 813:89061 | LONG RURAL | Asset Failure | HV | 636 | 325 | 73.5132 | 22.6496 | N
04/02/2017 | 18:21 | 524:33580 | SHORT RURAL | Asset Failure | HV | 21 | 509 | 0.047908 | 0.0094121 | N
04/02/2017 | 18:16 | 509:33395 | LONG RURAL | Asset Failure | HV | 46 | 1,072 | 17.5634 | 1.6382 | N
04/02/2017 | 19:58 | 511:29876 | SHORT RURAL | Asset Failure | HV | 6 | 1,247 | 0.033534 | 0.0026892 | N
04/02/2017 | 20:29 | 526:34639 | SHORT RURAL | Asset Failure | HV | 2 | 486 | 0.0043565 | 0.00089639 | N
04/02/2017 | 20:30 | 214:8667 | URBAN | Asset Failure | HV | 864 | 144 | 0.085467 | 0.059503 | N
05/02/2017 | 09:08 | 511:29876 | SHORT RURAL | Asset Failure | HV | 3 | 478 | 0.0064259 | 0.0013443 | N
05/02/2017 | 07:02 | 508:82579 | SHORT RURAL | Asset Failure | HV | 1 | 517 | 0.0023168 | 0.00044811 | N
05/02/2017 | 10:46 | 810:74050 | SHORT RURAL | Asset Failure | HV | 1 | 299 | 0.0013399 | 0.00044811 | N
05/02/2017 | 13:28 | ZN10995:PA7 | URBAN | Asset Failure | HV | 2,074 | 109 | 0.15553 | 0.14284 | N
05/02/2017 | 16:45 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 14 | 80 | 0.0050189 | 0.0062736 | N
05/02/2017 | 18:01 | ZN2196:PA25 | URBAN | Asset Failure | HV | 2,162 | 138 | 0.20522 | 0.1489 | N
05/02/2017 | 22:49 | 214:8666 | URBAN | Asset Failure | HV | 35 | 90 | 0.0021759 | 0.0024106 | N
06/02/2017 | 08:21 | 507:80914 | SHORT RURAL | Asset Failure | HV | 1 | 369 | 0.0016535 | 0.00044811 | N
06/02/2017 | 09:34 | 229:34995 | SHORT RURAL | Asset Failure | HV | 2 | 186 | 0.001667 | 0.00089623 | N
06/02/2017 | 12:18 | 509:33395 | LONG RURAL | Asset Failure | HV | 2 | 331 | 0.23609 | 0.071225 | N
06/02/2017 | 18:26 | ZN262:PA5 | URBAN | Asset Failure | HV | 1,419 | 77 | 0.074815 | 0.097731 | N
06/02/2017 | 18:40 | 513:48059 | SHORT RURAL | Asset Failure | HV | 22 | 210 | 0.020703 | 0.0098585 | N
06/02/2017 | 19:26 | 216:10726 | URBAN | Asset Failure | HV | 77 | 94 | 0.0049851 | 0.0053033 | N
07/02/2017 | 11:54 | ZN711:PA15 | URBAN | Asset Failure | HV | 22 | 88 | 0.0013334 | 0.0015152 | N
07/02/2017 | 11:54 | ZN711:PA21 | URBAN | Asset Failure | HV | 752 | 88 | 0.045579 | 0.051794 | N
07/02/2017 | 19:51 | ZN12630:PA13 | SHORT RURAL | Asset Failure | HV | 58 | 67 | 0.01736 | 0.025991 | N
08/02/2017 | 02:01 | ZN9252:PA31 | URBAN | Asset Failure | HV | 582 | 180 | 0.072032 | 0.040086 | N
08/02/2017 | 02:01 | ZN9252:PA24 | URBAN | Asset Failure | HV | 865 | 172 | 0.10271 | 0.059578 | N
09/02/2017 | 10:30 | ZN167:PA11 | URBAN | Asset Failure | HV | 133 | 90 | 0.0082664 | 0.0091604 | N
09/02/2017 | 16:38 | ZN2400:PA18 | SHORT RURAL | Asset Failure | HV | 49 | 21 | 0.0046046 | 0.021927 | N
09/02/2017 | 16:38 | ZN35370:PA4 | SHORT RURAL | Asset Failure | HV | 306 | 21 | 0.028755 | 0.13693 | N
09/02/2017 | 16:38 | ZN35370:PA8 | SHORT RURAL | Asset Failure | HV | 703 | 21 | 0.066062 | 0.31458 | N
10/02/2017 | 11:37 | 516:48065 | SHORT RURAL | Asset Failure | HV | 34 | 77 | 0.011715 | 0.015214 | N
10/02/2017 | 11:59 | ZN15014:PA9 | URBAN | Asset Failure | HV | 1,015 | 71 | 0.049791 | 0.069916 | N
10/02/2017 | 16:24 | ZN12620:PA1 | SHORT RURAL | Asset Failure | HV | 974 | 56 | 0.24487 | 0.43584 | N
10/02/2017 | 16:24 | ZN12620:PA11 | SHORT RURAL | Asset Failure | HV | 1 | 59 | 0.00026401 | 0.00044747 | N
10/02/2017 | 17:53 | 504:48027 | URBAN | Asset Failure | HV | 134 | 11 | 0.0010236 | 0.0092303 | N
10/02/2017 | 17:04 | ZN14891:PA20 | SHORT RURAL | Asset Failure | HV | 5 | 164 | 0.0036693 | 0.0022374 | N
10/02/2017 | 16:58 | ZN12650:PA6 | URBAN | Asset Failure | HV | 1,273 | 215 | 0.18863 | 0.087688 | N
10/02/2017 | 17:30 | ZN3154:PA14 | URBAN | Asset Failure | HV | 425 | 7 | 0.0020493 | 0.029275 | N
10/02/2017 | 17:30 | ZN3154:PA5 | URBAN | Asset Failure | HV | 1,147 | 97 | 0.076548 | 0.079009 | N
10/02/2017 | 18:08 | 528:83020 | SHORT RURAL | Asset Failure | HV | 6 | 92 | 0.0024701 | 0.0026848 | N
10/02/2017 | 18:14 | ZN35900:PA2 | URBAN | Asset Failure | HV | 1,552 | 134 | 0.14324 | 0.10691 | N
10/02/2017 | 19:34 | 532:83301 | URBAN | Asset Failure | HV | 1,022 | 124 | 0.087322 | 0.070398 | N
10/02/2017 | 19:05 | ZN965:PA26 | URBAN | Asset Failure | HV | 68 | 175 | 0.0081971 | 0.004684 | N
10/02/2017 | 19:20 | ZN847:PA47 | SHORT RURAL | Asset Failure | HV | 1,067 | 96 | 0.4563 | 0.47745 | N
11/02/2017 | 07:46 | ZN35500:PA28 | URBAN | Asset Failure | HV | 3,617 | 125 | 0.31251 | 0.24915 | N
11/02/2017 | 17:41 | ZN35500:PA28 | URBAN | Asset Failure | HV | 3,346 | 195 | 0.45036 | 0.23048 | N
11/02/2017 | 17:41 | ZN4545:PA36 | URBAN | Asset Failure | HV | 275 | 394 | 0.074587 | 0.018943 | N
11/02/2017 | 17:03 | ZN1285:PA27 | URBAN | Asset Failure | HV | 134 | 62 | 0.0057228 | 0.0092303 | N
11/02/2017 | 17:03 | ZN1285:PA31 | URBAN | Asset Failure | HV | 1,900 | 260 | 0.3402 | 0.13088 | N
11/02/2017 | 17:23 | 532:83295 | URBAN | Asset Failure | HV | 647 | 41 | 0.01805 | 0.044567 | N
11/02/2017 | 18:52 | ZN847:PA26 | URBAN | Asset Failure | HV | 175 | 184 | 0.02218 | 0.012055 | N
11/02/2017 | 18:52 | ZN847:PA46 | URBAN | Asset Failure | HV | 1,070 | 189 | 0.13943 | 0.073705 | N
11/02/2017 | 19:33 | 524:33570 | SHORT RURAL | Asset Failure | HV | 1,313 | 69 | 0.40808 | 0.58753 | N
11/02/2017 | 19:54 | ZN4545:PA6 | URBAN | Asset Failure | HV | 154 | 126 | 0.013317 | 0.010608 | N
12/02/2017 | 10:46 | ZN35500:PA27 | URBAN | Asset Failure | HV | 750 | 108 | 0.055795 | 0.051662 | N
12/02/2017 | 11:03 | 807:74184 | SHORT RURAL | Asset Failure | HV | 3 | 267 | 0.0035843 | 0.0013424 | N
12/02/2017 | 14:41 | 513:48059 | SHORT RURAL | Asset Failure | HV | 197 | 30 | 0.026414 | 0.088152 | N
12/02/2017 | 15:56 | ZN14143:PA17 | SHORT RURAL | Asset Failure | HV | 730 | 52 | 0.17121 | 0.32666 | N
12/02/2017 | 17:53 | 526:34639 | SHORT RURAL | Asset Failure | HV | 2 | 252 | 0.0022553 | 0.00089495 | N
12/02/2017 | 18:27 | ZN12610:PA6 | URBAN | Asset Failure | HV | 767 | 71 | 0.037728 | 0.052833 | N
13/02/2017 | 08:05 | 520:48172 | SHORT RURAL | Asset Failure | HV | 1 | 210 | 0.00093969 | 0.00044747 | N
13/02/2017 | 12:28 | 507:80914 | SHORT RURAL | Asset Failure | HV | 1 | 377 | 0.001687 | 0.00044747 | N
13/02/2017 | 16:25 | ZN12630:PA8 | SHORT RURAL | Asset Failure | HV | 2 | 150 | 0.0013424 | 0.00089495 | N
09/02/2017 | 12:11 | 810:74054 | LONG RURAL | Asset Failure | HV | 1 | 209 | 0.07443 | 0.035613 | N
09/02/2017 | 13:28 | 810:74054 | LONG RURAL | Asset Failure | HV | 15 | 32 | 0.17094 | 0.53419 | N
14/02/2017 | 20:00 | ZN9700:PA20 | URBAN | Asset Failure | HV | 4 | 130 | 0.00035859 | 0.00027584 | N
14/02/2017 | 22:51 | ZN12690:PA24 | SHORT RURAL | Asset Failure | HV | 113 | 297 | 0.14958 | 0.050432 | N
15/02/2017 | 17:21 | ZN3155:PA23 | URBAN | Asset Failure | HV | 2,167 | 81 | 0.12096 | 0.14932 | N
16/02/2017 | 13:25 | 516:48067 | SHORT RURAL | Asset Failure | HV | 175 | 57 | 0.044548 | 0.078155 | N
16/02/2017 | 13:50 | ZN5868:PA14 | URBAN | Asset Failure | HV | 1 | 86 | 5.9244e-05 | 6.8888e-05 | N
16/02/2017 | 13:50 | ZN80:PA24 | URBAN | Asset Failure | HV | 1,635 | 75 | 0.084605 | 0.11263 | N
16/02/2017 | 13:50 | ZN80:PA37 | URBAN | Asset Failure | HV | 1 | 241 | 0.00016585 | 6.8888e-05 | N
17/02/2017 | 15:02 | ZN2400:PA21 | URBAN | Asset Failure | HV | 242 | 268 | 0.044679 | 0.016671 | Y
17/02/2017 | 15:50 | 802:82225 | SHORT RURAL | Asset Failure | HV | 6 | 113 | 0.0030145 | 0.0026796 | Y
17/02/2017 | 15:53 | ZN3154:PA12 | URBAN | Asset Failure | HV | 1,297 | 111 | 0.099117 | 0.08935 | Y
17/02/2017 | 15:51 | 514:18146 | SHORT RURAL | Asset Failure | HV | 5 | 24 | 0.00053592 | 0.002233 | Y
17/02/2017 | 16:15 | 514:18141 | SHORT RURAL | Asset Failure | HV | 7 | 43 | 0.0013443 | 0.0031262 | Y
17/02/2017 | 16:15 | 514:18146 | SHORT RURAL | Asset Failure | HV | 5 | 1,303 | 0.029096 | 0.002233 | Y
17/02/2017 | 16:26 | ZN12580:PA4 | URBAN | Asset Failure | HV | 2,111 | 287 | 0.4171 | 0.14543 | Y
17/02/2017 | 16:36 | 807:74184 | SHORT RURAL | Asset Failure | HV | 80 | 168 | 0.059938 | 0.035728 | Y
17/02/2017 | 16:44 | ZN12690:PA19 | URBAN | Asset Failure | HV | 1,216 | 472 | 0.39541 | 0.08377 | Y
17/02/2017 | 16:50 | 516:48067 | SHORT RURAL | Asset Failure | HV | 68 | 300 | 0.091106 | 0.030369 | Y
17/02/2017 | 16:42 | ZN12690:PA24 | SHORT RURAL | Asset Failure | HV | 784 | 737 | 2.5789 | 0.35013 | Y
17/02/2017 | 16:49 | ZN14891:PA12 | SHORT RURAL | Asset Failure | HV | 467 | 983 | 2.0502 | 0.20856 | Y
17/02/2017 | 16:58 | 807:74184 | SHORT RURAL | Asset Failure | HV | 1 | 1,072 | 0.0047875 | 0.0004466 | Y
17/02/2017 | 16:45 | ZN12570:PA26 | URBAN | Asset Failure | HV | 1,124 | 460 | 0.35603 | 0.077432 | Y
23/02/2017 | 17:30 | ZN12570:PA22 | SHORT RURAL | Asset Failure | HV | 1,208 | 40 | 0.21575 | 0.53937 | N
17/02/2017 | 16:37 | ZN12600:PA13 | SHORT RURAL | Asset Failure | HV | 855 | 905 | 3.4571 | 0.38184 | Y
17/02/2017 | 17:10 | 807:74184 | SHORT RURAL | Asset Failure | HV | 191 | 81 | 0.069254 | 0.0853 | Y
17/02/2017 | 18:13 | 514:18137 | SHORT RURAL | Asset Failure | HV | 45 | 508 | 0.10209 | 0.020097 | Y
17/02/2017 | 16:39 | ZN14891:PA8 | SHORT RURAL | Asset Failure | HV | 76 | 1,319 | 0.44752 | 0.033941 | Y
17/02/2017 | 19:48 | 232:11453 | SHORT RURAL | Asset Failure | HV | 1,337 | 227 | 1.3542 | 0.5971 | Y
17/02/2017 | 22:04 | 213:33771 | URBAN | Asset Failure | HV | 506 | 86 | 0.029978 | 0.034858 | Y
17/02/2017 | 20:16 | ZN12630:PA13 | SHORT RURAL | Asset Failure | HV | 7 | 1,322 | 0.04133 | 0.0031262 | Y
18/02/2017 | 15:05 | 502:48010 | SHORT RURAL | Asset Failure | HV | 1 | 90 | 0.00040195 | 0.00044661 | N
18/02/2017 | 18:23 | 265:81651 | SHORT RURAL | Asset Failure | HV | 151 | 91 | 0.061064 | 0.067438 | N
18/02/2017 | 19:01 | 801:74121 | LONG RURAL | Asset Failure | HV | 177 | 113 | 7.1343 | 6.3034 | N
18/02/2017 | 19:15 | ZN15013:PA4 | URBAN | Asset Failure | HV | 110 | 106 | 0.0079967 | 0.0075779 | N
18/02/2017 | 20:43 | 811:74234 | SHORT RURAL | Asset Failure | HV | 8 | 1,182 | 0.042231 | 0.0035728 | N
18/02/2017 | 21:27 | 813:89062 | SHORT RURAL | Asset Failure | HV | 54 | 160 | 0.038694 | 0.024117 | N
18/02/2017 | 22:03 | ZN14143:PA12 | SHORT RURAL | Asset Failure | HV | 1,327 | 278 | 1.6464 | 0.59265 | N
19/02/2017 | 19:29 | 807:74184 | SHORT RURAL | Asset Failure | HV | 61 | 107 | 0.029043 | 0.027243 | N
19/02/2017 | 20:55 | ZN36100:PA27 | URBAN | Asset Failure | HV | 269 | 328 | 0.060768 | 0.018531 | N
19/02/2017 | 21:11 | 813:89055 | SHORT RURAL | Asset Failure | HV | 1 | 224 | 0.0010004 | 0.00044661 | N
20/02/2017 | 18:32 | 528:83011 | SHORT RURAL | Asset Failure | HV | 20 | 122 | 0.010897 | 0.0089321 | N
20/02/2017 | 19:54 | ZN7481:PA9 | URBAN | Asset Failure | HV | 1,679 | 47 | 0.054604 | 0.11567 | N
20/02/2017 | 23:40 | 516:48065 | SHORT RURAL | Asset Failure | HV | 2 | 180 | 0.0016078 | 0.00089321 | N
18/02/2017 | 10:37 | 807:74184 | SHORT RURAL | Asset Failure | HV | 161 | 189 | 0.1359 | 0.071904 | N
22/02/2017 | 21:00 | ZN35900:PA6 | URBAN | Asset Failure | HV | 5 | 90 | 0.00031002 | 0.00034446 | N
23/02/2017 | 10:30 | 509:33395 | LONG RURAL | Asset Failure | HV | 7 | 255 | 0.63568 | 0.24929 | N
23/02/2017 | 13:56 | 507:80917 | URBAN | Asset Failure | HV | 16 | 59 | 0.00065026 | 0.0011021 | N
23/02/2017 | 15:55 | 227:13015 | SHORT RURAL | Asset Failure | HV | 2 | 265 | 0.0023664 | 0.00089299 | N
24/02/2017 | 13:43 | 814:82283 | SHORT RURAL | Asset Failure | HV | 1 | 132 | 0.00058935 | 0.00044648 | N
24/02/2017 | 18:00 | 230:81432 | SHORT RURAL | Asset Failure | HV | 50 | 172 | 0.038375 | 0.022324 | N
25/02/2017 | 05:44 | ZN342:PA17 | URBAN | Asset Failure | HV | 1,749 | 67 | 0.080264 | 0.12047 | N
25/02/2017 | 07:36 | ZN2466:PA21 | URBAN | Asset Failure | HV | 1 | 47 | 3.2373e-05 | 6.8879e-05 | N
25/02/2017 | 07:36 | ZN2466:PA22 | URBAN | Asset Failure | HV | 9 | 45 | 0.00028034 | 0.00061991 | N
25/02/2017 | 07:36 | ZN2466:PA27 | URBAN | Asset Failure | HV | 83 | 47 | 0.002687 | 0.005717 | N
25/02/2017 | 09:01 | ZN10996:PA12 | URBAN | Asset Failure | HV | 2 | 115 | 0.00015842 | 0.00013776 | N
25/02/2017 | 09:01 | ZN10996:PA19 | URBAN | Asset Failure | HV | 10 | 115 | 0.00079211 | 0.00068879 | N
25/02/2017 | 09:01 | ZN10996:PA9 | URBAN | Asset Failure | HV | 1,042 | 114 | 0.081766 | 0.071772 | N
25/02/2017 | 10:38 | ZN12570:PA33 | SHORT RURAL | Asset Failure | HV | 655 | 165 | 0.4834 | 0.29253 | N
25/02/2017 | 17:45 | ZN14144:PA2 | SHORT RURAL | Asset Failure | HV | 1,023 | 211 | 0.96241 | 0.45689 | N
26/02/2017 | 16:40 | 507:80932 | SHORT RURAL | Asset Failure | HV | 48 | 310 | 0.066456 | 0.021437 | N
27/02/2017 | 12:57 | ZN12640:PA13 | SHORT RURAL | Asset Failure | HV | 1 | 103 | 0.00046001 | 0.00044661 | N
28/02/2017 | 10:45 | 203:8082 | URBAN | Asset Failure | HV | 13 | 103 | 0.00091954 | 0.00089543 | N
28/02/2017 | 08:20 | ZN1610:PA1 | URBAN | Asset Failure | HV | 2 | 83 | 0.00011434 | 0.00013776 | N
28/02/2017 | 08:42 | ZN12640:PA13 | SHORT RURAL | Asset Failure | HV | 381 | 368 | 0.62574 | 0.17016 | N
28/02/2017 | 17:21 | 526:34637 | SHORT RURAL | Asset Failure | HV | 3 | 439 | 0.005882 | 0.0013399 | N
01/03/2017 | 10:09 | ZN8000:PA10 | URBAN | Asset Failure | HV | 31 | 72 | 0.0015422 | 0.0021353 | N
01/03/2017 | 15:32 | ZN3922:PA17 | SHORT RURAL | Asset Failure | HV | 1,077 | 91 | 0.43632 | 0.48101 | N
02/03/2017 | 04:34 | ZN1673:PA13 | URBAN | Asset Failure | HV | 841 | 98 | 0.056975 | 0.057929 | N
02/03/2017 | 06:24 | 801:74121 | LONG RURAL | Asset Failure | HV | 1 | 111 | 0.039516 | 0.0356 | N
03/03/2017 | 15:05 | ZN2835:PA27 | URBAN | Asset Failure | HV | 905 | 59 | 0.036689 | 0.062321 | N
03/03/2017 | 15:05 | ZN2835:PA30 | URBAN | Asset Failure | HV | 1 | 60 | 4.1318e-05 | 6.8863e-05 | N
03/03/2017 | 15:04 | ZN711:PA22 | URBAN | Asset Failure | HV | 381 | 65 | 0.017095 | 0.026237 | N
03/03/2017 | 20:21 | 528:83013 | URBAN | Asset Failure | HV | 1,205 | 57 | 0.047434 | 0.08298 | N
04/03/2017 | 12:19 | ZN187:PA13 | URBAN | Asset Failure | HV | 108 | 66 | 0.0049094 | 0.0074386 | N
04/03/2017 | 12:19 | ZN187:PA17 | URBAN | Asset Failure | HV | 1,300 | 66 | 0.059095 | 0.089538 | N
04/03/2017 | 14:45 | ZN15014:PA16 | URBAN | Asset Failure | HV | 384 | 81 | 0.021438 | 0.026448 | N
05/03/2017 | 08:09 | 507:80932 | SHORT RURAL | Asset Failure | HV | 30 | 351 | 0.047097 | 0.013418 | N
05/03/2017 | 19:58 | 810:74054 | LONG RURAL | Asset Failure | HV | 1 | 47 | 0.016732 | 0.0356 | N
06/03/2017 | 09:26 | ZN1610:PA5 | URBAN | Asset Failure | HV | 7 | 53 | 0.00025553 | 0.00048214 | N
06/03/2017 | 15:30 | ZN3472:PA34 | URBAN | Asset Failure | HV | 542 | 67 | 0.025012 | 0.037331 | N
06/03/2017 | 15:30 | ZN3472:PA35 | URBAN | Asset Failure | HV | 414 | 101 | 0.028927 | 0.028515 | N
06/03/2017 | 15:30 | ZN3472:PA8 | URBAN | Asset Failure | HV | 151 | 417 | 0.043376 | 0.0104 | N
07/03/2017 | 12:17 | ZN10997:PA11 | URBAN | Asset Failure | HV | 710 | 49 | 0.024093 | 0.048904 | N
07/03/2017 | 12:44 | ZN36300:PA17 | URBAN | Asset Failure | HV | 131 | 61 | 0.0055041 | 0.0090231 | N
07/03/2017 | 12:44 | ZN36300:PA8 | URBAN | Asset Failure | HV | 1,569 | 34 | 0.036744 | 0.10807 | N
07/03/2017 | 23:33 | ZN12650:PA17 | URBAN | Asset Failure | HV | 2,199 | 98 | 0.14769 | 0.15146 | N
07/03/2017 | 23:33 | ZN12650:PA9 | URBAN | Asset Failure | HV | 1 | 97 | 6.6812e-05 | 6.8879e-05 | N
08/03/2017 | 01:15 | ZN14891:PA20 | SHORT RURAL | Asset Failure | HV | 8 | 420 | 0.014991 | 0.0035693 | N
08/03/2017 | 13:55 | ZN3154:PA12 | URBAN | Asset Failure | HV | 604 | 58 | 0.024044 | 0.041603 | N
11/03/2017 | 09:14 | 516:48067 | SHORT RURAL | Asset Failure | HV | 1 | 131 | 0.00058248 | 0.00044464 | N
11/03/2017 | 15:55 | 511:29878 | SHORT RURAL | Asset Failure | HV | 1,064 | 75 | 0.35256 | 0.4731 | N
12/03/2017 | 12:43 | ZN36100:PA15 | URBAN | Asset Failure | HV | 753 | 154 | 0.079976 | 0.051875 | N
12/03/2017 | 13:41 | ZN3154:PA19 | URBAN | Asset Failure | HV | 1,012 | 149 | 0.10419 | 0.069718 | N
12/03/2017 | 16:12 | ZN7900:PA6 | URBAN | Asset Failure | HV | 980 | 48 | 0.032407 | 0.067514 | N
13/03/2017 | 16:22 | ZN14143:PA12 | SHORT RURAL | Asset Failure | HV | 1,327 | 134 | 0.79259 | 0.59004 | N
13/03/2017 | 16:40 | ZN2400:PA11 | SHORT RURAL | Asset Failure | HV | 696 | 129 | 0.39922 | 0.30947 | N
13/03/2017 | 16:40 | ZN2400:PA21 | URBAN | Asset Failure | HV | 242 | 143 | 0.023761 | 0.016672 | N
13/03/2017 | 22:43 | ZN12630:PA13 | SHORT RURAL | Asset Failure | HV | 2 | 937 | 0.0083326 | 0.00088929 | N
14/03/2017 | 08:21 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 57 | 82 | 0.020898 | 0.025345 | N
14/03/2017 | 09:23 | ZN12610:PA11 | URBAN | Asset Failure | HV | 1 | 252 | 0.00017361 | 6.8892e-05 | N
14/03/2017 | 09:23 | ZN12610:PA17 | URBAN | Asset Failure | HV | 1,054 | 81 | 0.058487 | 0.072612 | N
14/03/2017 | 11:46 | 504:48034 | URBAN | Asset Failure | HV | 192 | 89 | 0.011772 | 0.013227 | N
14/03/2017 | 11:27 | 227:13015 | SHORT RURAL | Asset Failure | HV | 322 | 173 | 0.2484 | 0.14318 | N
14/03/2017 | 17:59 | 217:33610 | URBAN | Asset Failure | HV | 981 | 77 | 0.05196 | 0.067583 | N
14/03/2017 | 18:16 | 810:74054 | LONG RURAL | Asset Failure | HV | 2 | 34 | 0.024217 | 0.071225 | N
15/03/2017 | 09:21 | ZN15013:PA8 | URBAN | Asset Failure | HV | 1 | 1,619 | 0.0011154 | 6.8892e-05 | N
16/03/2017 | 10:35 | 807:74179 | SHORT RURAL | Asset Failure | HV | 52 | 210 | 0.04851 | 0.023115 | N
16/03/2017 | 14:48 | 509:33395 | LONG RURAL | Asset Failure | HV | 1 | 262 | 0.093338 | 0.035625 | N
16/03/2017 | 15:22 | ZN80:PA32 | URBAN | Asset Failure | HV | 3,652 | 128 | 0.32281 | 0.25154 | N
16/03/2017 | 15:22 | ZN80:PA37 | URBAN | Asset Failure | HV | 559 | 207 | 0.07983 | 0.038502 | N
16/03/2017 | 15:22 | ZN80:PA40 | URBAN | Asset Failure | HV | 152 | 238 | 0.024917 | 0.010469 | N
18/03/2017 | 09:05 | 512:48048 | SHORT RURAL | Asset Failure | HV | 12 | 285 | 0.0152 | 0.0053334 | N
14/03/2017 | 18:25 | 810:74054 | LONG RURAL | Asset Failure | HV | 92 | 187 | 6.1314 | 3.2764 | N
17/03/2017 | 23:59 | 507:80914 | SHORT RURAL | Asset Failure | HV | 28 | 131 | 0.016276 | 0.012445 | N
18/03/2017 | 00:32 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 107 | 514 | 0.24425 | 0.047556 | N
18/03/2017 | 03:19 | ZN9900:PA13 | URBAN | Asset Failure | HV | 830 | 148 | 0.08461 | 0.057169 | N
18/03/2017 | 03:19 | ZN9900:PA2 | URBAN | Asset Failure | HV | 21 | 148 | 0.0021407 | 0.0014464 | N
18/03/2017 | 03:19 | ZN9900:PA19 | URBAN | Asset Failure | HV | 705 | 194 | 0.094333 | 0.048559 | N
18/03/2017 | 03:26 | 528:83024 | URBAN | Asset Failure | HV | 43 | 263 | 0.0077756 | 0.0029618 | N
18/03/2017 | 04:54 | ZN690:PA35 | URBAN | Asset Failure | HV | 2,680 | 165 | 0.3046 | 0.18459 | N
18/03/2017 | 07:16 | 812:19065 | SHORT RURAL | Asset Failure | HV | 5 | 402 | 0.0089335 | 0.0022223 | N
18/03/2017 | 09:04 | ZN14143:PA17 | SHORT RURAL | Asset Failure | HV | 164 | 326 | 0.23762 | 0.07289 | N
19/03/2017 | 04:27 | ZN187:PA14 | URBAN | Asset Failure | HV | 666 | 76 | 0.034863 | 0.045873 | N
20/03/2017 | 08:20 | 512:48049 | SHORT RURAL | Asset Failure | HV | 3 | 265 | 0.0035334 | 0.0013334 | N
20/03/2017 | 14:00 | ZN1850:PA11 | URBAN | Asset Failure | HV | 290 | 64 | 0.012732 | 0.019975 | N
21/03/2017 | 00:53 | ZN847:PA47 | SHORT RURAL | Asset Failure | HV | 1,069 | 158 | 0.75018 | 0.47512 | N
21/03/2017 | 08:02 | 507:80914 | SHORT RURAL | Asset Failure | HV | 1 | 339 | 0.0015066 | 0.00044446 | N
21/03/2017 | 13:08 | 256:80647 | URBAN | Asset Failure | HV | 597 | 34 | 0.014029 | 0.041121 | N
21/03/2017 | 18:19 | ZN965:PA4 | URBAN | Asset Failure | HV | 1,108 | 195 | 0.14894 | 0.076318 | N
21/03/2017 | 18:19 | ZN965:PA46 | URBAN | Asset Failure | HV | 23 | 191 | 0.0030259 | 0.0015842 | N
21/03/2017 | 20:05 | ZN3154:PA18 | URBAN | Asset Failure | HV | 1,156 | 44 | 0.0354 | 0.079624 | N
22/03/2017 | 12:13 | 516:48067 | SHORT RURAL | Asset Failure | HV | 3 | 142 | 0.0018934 | 0.0013334 | N
22/03/2017 | 15:00 | 810:74054 | LONG RURAL | Asset Failure | HV | 1 | 125 | 0.044611 | 0.035689 | N
22/03/2017 | 15:48 | ZN2835:PA41 | URBAN | Asset Failure | HV | 1 | 317 | 0.00021835 | 6.8881e-05 | N
22/03/2017 | 16:10 | ZN847:PA45 | SHORT RURAL | Asset Failure | HV | 51 | 176 | 0.039989 | 0.022668 | N
22/03/2017 | 16:16 | ZN129:PA51 | URBAN | Asset Failure | HV | 206 | 160 | 0.022718 | 0.014189 | N
22/03/2017 | 16:28 | ZN15013:PA10 | SHORT RURAL | Asset Failure | HV | 119 | 210 | 0.11132 | 0.052892 | N
22/03/2017 | 18:09 | ZN12650:PA17 | URBAN | Asset Failure | HV | 70 | 1,251 | 0.060319 | 0.0048217 | N
22/03/2017 | 19:07 | ZN12640:PA1 | SHORT RURAL | Asset Failure | HV | 55 | 293 | 0.071626 | 0.024446 | N
22/03/2017 | 18:35 | 807:74180 | SHORT RURAL | Asset Failure | HV | 3 | 389 | 0.005187 | 0.0013334 | N
23/03/2017 | 11:19 | 513:48056 | SHORT RURAL | Asset Failure | HV | 1 | 176 | 0.0007825 | 0.0004446 | N
23/03/2017 | 12:02 | ZN10999:PA16 | URBAN | Asset Failure | HV | 166 | 158 | 0.01806 | 0.01143 | N
23/03/2017 | 12:12 | ZN12640:PA13 | SHORT RURAL | Asset Failure | HV | 2 | 228 | 0.0020274 | 0.00088921 | N
23/03/2017 | 14:32 | 801:74121 | LONG RURAL | Asset Failure | HV | 254 | 143 | 12.9222 | 9.065 | N
23/03/2017 | 22:13 | 513:48056 | SHORT RURAL | Asset Failure | HV | 121 | 235 | 0.12637 | 0.053797 | N
24/03/2017 | 16:24 | 812:19072 | SHORT RURAL | Asset Failure | HV | 1 | 106 | 0.00047128 | 0.00044461 | N
25/03/2017 | 15:43 | 513:48056 | SHORT RURAL | Asset Failure | HV | 47 | 73 | 0.01526 | 0.020897 | N
26/03/2017 | 09:57 | 511:29878 | SHORT RURAL | Asset Failure | HV | 2 | 308 | 0.002734 | 0.00088767 | N
26/03/2017 | 13:34 | ZN195:PA25 | URBAN | Asset Failure | HV | 763 | 126 | 0.066198 | 0.052538 | N
26/03/2017 | 13:34 | ZN195:PA29 | URBAN | Asset Failure | HV | 481 | 357 | 0.1184 | 0.03312 | N
26/03/2017 | 13:34 | ZN195:PA4 | URBAN | Asset Failure | HV | 5 | 126 | 0.0004338 | 0.00034429 | N
26/03/2017 | 15:15 | 802:82225 | SHORT RURAL | Asset Failure | HV | 1 | 330 | 0.0014647 | 0.00044384 | N
26/03/2017 | 18:07 | 802:82225 | SHORT RURAL | Asset Failure | HV | 11 | 7 | 0.00034175 | 0.0048822 | N
28/03/2017 | 11:09 | 232:11455 | SHORT RURAL | Asset Failure | HV | 126 | 51 | 0.028521 | 0.055924 | N
28/03/2017 | 14:11 | ZN2466:PA20 | URBAN | Asset Failure | HV | 1,129 | 103 | 0.079998 | 0.077741 | N
28/03/2017 | 22:12 | 238:34148 | SHORT RURAL | Asset Failure | HV | 8 | 568 | 0.020168 | 0.0035507 | N
29/03/2017 | 18:00 | 243:80078 | SHORT RURAL | Asset Failure | HV | 74 | 300 | 0.098534 | 0.032845 | N
29/03/2017 | 22:27 | ZN3425:PA22 | URBAN | Asset Failure | HV | 1,078 | 75 | 0.055835 | 0.074231 | N
30/03/2017 | 12:53 | ZN187:PA10 | URBAN | Asset Failure | HV | 27 | 317 | 0.005883 | 0.0018586 | N
30/03/2017 | 12:53 | ZN187:PA20 | URBAN | Asset Failure | HV | 2,050 | 53 | 0.075286 | 0.14111 | N
30/03/2017 | 12:53 | ZN187:PA8 | URBAN | Asset Failure | HV | 449 | 51 | 0.015763 | 0.030907 | N
30/03/2017 | 14:15 | 807:74184 | SHORT RURAL | Asset Failure | HV | 37 | 50 | 0.0082059 | 0.016412 | N
30/03/2017 | 18:11 | 265:81648 | SHORT RURAL | Asset Failure | HV | 182 | 53 | 0.042586 | 0.080728 | N
29/03/2017 | 22:58 | ZN14891:PA5 | SHORT RURAL | Asset Failure | HV | 79 | 298 | 0.10455 | 0.035064 | N
03/04/2017 | 11:27 | 523:33501 | SHORT RURAL | Asset Failure | HV | 1 | 208 | 0.00092625 | 0.00044531 | N
03/04/2017 | 12:08 | 515:35197 | LONG RURAL | Asset Failure | HV | 9 | 156 | 0.50143 | 0.32143 | N
03/04/2017 | 17:30 | ZN14891:PA1 | SHORT RURAL | Asset Failure | HV | 2 | 70 | 0.00062344 | 0.00089062 | N
03/04/2017 | 17:30 | ZN14891:PA16 | SHORT RURAL | Asset Failure | HV | 103 | 70 | 0.032023 | 0.045867 | N
04/04/2017 | 12:30 | 509:33395 | LONG RURAL | Asset Failure | HV | 49 | 150 | 2.625 | 1.75 | N
05/04/2017 | 12:48 | 509:33395 | LONG RURAL | Asset Failure | HV | 15 | 480 | 2.5736 | 0.53571 | N
05/04/2017 | 15:46 | ZN15013:PA10 | SHORT RURAL | Asset Failure | HV | 1 | 434 | 0.0019327 | 0.00044531 | N
06/04/2017 | 23:08 | 258:80775 | URBAN | Asset Failure | HV | 125 | 27 | 0.0023222 | 0.0086008 | N
07/04/2017 | 23:04 | ZN35800:PA21 | URBAN | Asset Failure | HV | 289 | 66 | 0.013141 | 0.019916 | N
08/04/2017 | 15:03 | ZN342:PA28 | URBAN | Asset Failure | HV | 1,197 | 53 | 0.043307 | 0.08233 | N
09/04/2017 | 09:40 | 243:80080 | SHORT RURAL | Asset Failure | HV | 640 | 139 | 0.39485 | 0.28502 | N
09/04/2017 | 11:39 | 513:48056 | SHORT RURAL | Asset Failure | HV | 90 | 205 | 0.082095 | 0.040081 | N
09/04/2017 | 12:07 | 507:80932 | SHORT RURAL | Asset Failure | HV | 3 | 133 | 0.0017769 | 0.001336 | N
09/04/2017 | 15:53 | 515:35197 | LONG RURAL | Asset Failure | HV | 98 | 319 | 11.1696 | 3.4988 | N
10/04/2017 | 03:38 | ZN10994:PA10 | URBAN | Asset Failure | HV | 1,104 | 71 | 0.054121 | 0.075933 | N
10/04/2017 | 03:38 | ZN10994:PA21 | URBAN | Asset Failure | HV | 228 | 80 | 0.012545 | 0.015682 | N
10/04/2017 | 14:38 | 238:34141 | SHORT RURAL | Asset Failure | HV | 5 | 381 | 0.0084868 | 0.0022267 | N
11/04/2017 | 19:54 | 801:74123 | SHORT RURAL | Asset Failure | HV | 230 | 286 | 0.29295 | 0.10243 | N
13/04/2017 | 22:37 | ZN1287:PA6 | URBAN | Asset Failure | HV | 859 | 124 | 0.073465 | 0.059089 | N
14/04/2017 | 23:00 | ZN4545:PA9 | URBAN | Asset Failure | HV | 26 | 117 | 0.0020932 | 0.001789 | N
16/04/2017 | 02:03 | ZN15014:PA9 | URBAN | Asset Failure | HV | 1,015 | 77 | 0.053871 | 0.069797 | N
18/04/2017 | 10:10 | 807:74184 | SHORT RURAL | Asset Failure | HV | 1 | 210 | 0.00093509 | 0.00044528 | N
18/04/2017 | 18:20 | 512:48048 | SHORT RURAL | Asset Failure | HV | 8 | 100 | 0.0035623 | 0.0035623 | N
19/04/2017 | 10:40 | ZN2602:PA30 | URBAN | Asset Failure | HV | 1,907 | 72 | 0.094863 | 0.13114 | N
21/04/2017 | 03:16 | ZN12620:PA11 | SHORT RURAL | Asset Failure | HV | 1,630 | 108 | 0.78163 | 0.72395 | N
21/04/2017 | 14:39 | ZN188:PA22 | URBAN | Asset Failure | HV | 68 | 82 | 0.0038246 | 0.0046784 | N
22/04/2017 | 04:06 | ZN1290:PA12 | URBAN | Asset Failure | HV | 1,030 | 114 | 0.081058 | 0.070838 | N
24/04/2017 | 06:34 | ZN3472:PA30 | URBAN | Asset Failure | HV | 2,098 | 108 | 0.15583 | 0.14429 | N
24/04/2017 | 06:34 | ZN35900:PA17 | URBAN | Asset Failure | HV | 54 | 108 | 0.004011 | 0.0037139 | N
25/04/2017 | 03:05 | ZN180:PA33 | URBAN | Asset Failure | HV | 899 | 53 | 0.032709 | 0.06183 | N
25/04/2017 | 18:09 | 812:19072 | SHORT RURAL | Asset Failure | HV | 224 | 111 | 0.11053 | 0.099454 | N
26/04/2017 | 10:14 | 511:29876 | SHORT RURAL | Asset Failure | HV | 98 | 66 | 0.028717 | 0.043511 | N
26/04/2017 | 15:38 | 504:48034 | URBAN | Asset Failure | HV | 1,414 | 100 | 0.097616 | 0.09725 | N
26/04/2017 | 15:39 | 512:48049 | SHORT RURAL | Asset Failure | HV | 404 | 182 | 0.3258 | 0.17937 | N
26/04/2017 | 16:56 | 513:48059 | SHORT RURAL | Asset Failure | HV | 1 | 119 | 0.00052835 | 0.00044399 | N
26/04/2017 | 17:19 | 813:89062 | SHORT RURAL | Asset Failure | HV | 14 | 316 | 0.019642 | 0.0062159 | N
26/04/2017 | 15:39 | ZN10994:PA1 | URBAN | Asset Failure | HV | 133 | 301 | 0.027533 | 0.0091473 | N
27/04/2017 | 12:30 | 515:35197 | LONG RURAL | Asset Failure | HV | 6 | 40 | 0.085684 | 0.21421 | N
27/04/2017 | 17:10 | 526:34637 | SHORT RURAL | Asset Failure | HV | 3 | 255 | 0.0033959 | 0.0013317 | N
27/04/2017 | 23:10 | 228:7490 | SHORT RURAL | Asset Failure | HV | 32 | 83 | 0.011786 | 0.014205 | N
28/04/2017 | 10:30 | 514:18137 | SHORT RURAL | Asset Failure | HV | 4 | 70 | 0.0012429 | 0.0017756 | N
29/04/2017 | 12:51 | 520:48172 | SHORT RURAL | Asset Failure | HV | 6 | 24 | 0.0006392 | 0.0026634 | N
02/05/2017 | 09:26 | ZN398:PA4 | URBAN | Asset Failure | HV | 1 | 364 | 0.0002503 | 6.8765e-05 | N
02/05/2017 | 09:26 | ZN690:PA12 | URBAN | Asset Failure | HV | 1,380 | 237 | 0.22475 | 0.094895 | N
02/05/2017 | 09:26 | ZN690:PA14 | URBAN | Asset Failure | HV | 155 | 280 | 0.029871 | 0.010659 | N
02/05/2017 | 09:26 | ZN690:PA24 | SHORT RURAL | Asset Failure | HV | 10 | 362 | 0.016069 | 0.0044389 | N
02/05/2017 | 09:26 | ZN690:PA30 | URBAN | Asset Failure | HV | 1,213 | 125 | 0.10435 | 0.083411 | N
02/05/2017 | 19:25 | ZN9118:PA11 | URBAN | Asset Failure | HV | 1,846 | 77 | 0.09778 | 0.12694 | N
02/05/2017 | 19:25 | ZN9118:PA20 | URBAN | Asset Failure | HV | 1 | 71 | 4.8823e-05 | 6.8765e-05 | N
03/05/2017 | 07:59 | 511:29876 | SHORT RURAL | Asset Failure | HV | 12 | 140 | 0.0074717 | 0.0053268 | N
03/05/2017 | 10:15 | 509:33395 | LONG RURAL | Asset Failure | HV | 114 | 248 | 10.0935 | 4.07 | N
03/05/2017 | 21:04 | 229:34995 | SHORT RURAL | Asset Failure | HV | 3 | 31 | 0.00041282 | 0.0013317 | N
05/05/2017 | 18:01 | 227:13020 | SHORT RURAL | Asset Failure | HV | 827 | 90 | 0.32864 | 0.36704 | N
06/05/2017 | 15:50 | 227:13020 | SHORT RURAL | Asset Failure | HV | 91 | 25 | 0.010097 | 0.040387 | N
06/05/2017 | 17:40 | 520:48172 | SHORT RURAL | Asset Failure | HV | 39 | 157 | 0.027219 | 0.017309 | N
08/05/2017 | 04:11 | ZN10994:PA10 | URBAN | Asset Failure | HV | 598 | 133 | 0.054677 | 0.041111 | N
08/05/2017 | 04:11 | ZN10994:PA19 | URBAN | Asset Failure | HV | 903 | 131 | 0.081337 | 0.062078 | N
08/05/2017 | 04:11 | ZN10994:PA21 | URBAN | Asset Failure | HV | 228 | 133 | 0.020847 | 0.015674 | N
08/05/2017 | 14:45 | 233:82812 | SHORT RURAL | Asset Failure | HV | 25 | 80 | 0.0088916 | 0.011115 | N
09/05/2017 | 01:00 | ZN263:PA33 34GHJ | CBD | Asset Failure | HV | 561 | 435 | 7.843 | 1.8041 | N
13/05/2017 | 03:58 | 265:81645 | URBAN | Asset Failure | HV | 40 | 48 | 0.0013197 | 0.0027494 | N
13/05/2017 | 03:58 | 265:81648 | SHORT RURAL | Asset Failure | HV | 163 | 94 | 0.068362 | 0.072437 | N
15/05/2017 | 05:38 | ZN15012:PA6 | URBAN | Asset Failure | HV | 1,445 | 114 | 0.11362 | 0.099322 | N
16/05/2017 | 18:26 | 202:34260 | URBAN | Asset Failure | HV | 1,486 | 55 | 0.056178 | 0.10214 | N
18/05/2017 | 10:20 | ZN3922:PA17 | SHORT RURAL | Asset Failure | HV | 1,074 | 62 | 0.29583 | 0.47714 | N
18/05/2017 | 10:20 | ZN3922:PA29 | URBAN | Asset Failure | HV | 67 | 62 | 0.0028545 | 0.004604 | N
19/05/2017 | 18:10 | ZN10997:PA1 | URBAN | Asset Failure | HV | 80 | 136 | 0.0074789 | 0.0054978 | N
19/05/2017 | 18:10 | ZN10997:PA2 | URBAN | Asset Failure | HV | 2 | 137 | 0.0001883 | 0.00013745 | N
19/05/2017 | 22:14 | ZN2310:PA54 | URBAN | Asset Failure | HV | 1,097 | 96 | 0.072502 | 0.075389 | N
20/05/2017 | 03:28 | 526:34639 | SHORT RURAL | Asset Failure | HV | 129 | 269 | 0.15541 | 0.057741 | N
20/05/2017 | 14:45 | 232:33407 | SHORT RURAL | Asset Failure | HV | 39 | 25 | 0.0043642 | 0.017457 | N
22/05/2017 | 10:00 | 813:89061 | LONG RURAL | Asset Failure | HV | 2 | 120 | 0.085623 | 0.071352 | N
24/05/2017 | 05:17 | 206:34440 | URBAN | Asset Failure | HV | 1,623 | 171 | 0.19033 | 0.11154 | N
24/05/2017 | 06:06 | 202:34260 | URBAN | Asset Failure | HV | 2,463 | 81 | 0.13788 | 0.16926 | N
24/05/2017 | 15:42 | ZN2196:PA3 | SHORT RURAL | Asset Failure | HV | 679 | 120 | 0.36446 | 0.30392 | N
24/05/2017 | 17:08 | ZN15013:PA2 | URBAN | Asset Failure | HV | 66 | 114 | 0.0051707 | 0.0045357 | N
24/05/2017 | 17:08 | ZN15013:PA4 | URBAN | Asset Failure | HV | 823 | 113 | 0.063911 | 0.056559 | N
24/05/2017 | 17:08 | ZN15013:PA6 | SHORT RURAL | Asset Failure | HV | 226 | 114 | 0.11532 | 0.10116 | N
25/05/2017 | 14:11 | ZN690:PA15 | URBAN | Asset Failure | HV | 41 | 113 | 0.0031919 | 0.0028176 | N
25/05/2017 | 21:58 | ZN12610:PA10 | URBAN | Asset Failure | HV | 1,955 | 92 | 0.12346 | 0.13435 | N
26/05/2017 | 17:36 | ZN384:PA22 | URBAN | Asset Failure | HV | 143 | 454 | 0.044616 | 0.0098273 | Y
26/05/2017 | 17:36 | ZN711:PA15 | URBAN | Asset Failure | HV | 1 | 454 | 0.000312 | 6.8723e-05 | Y
26/05/2017 | 17:36 | ZN711:PA21 | URBAN | Asset Failure | HV | 162 | 454 | 0.050544 | 0.011133 | Y
27/05/2017 | 05:43 | 812:19071 | SHORT RURAL | Asset Failure | HV | 13 | 297 | 0.017282 | 0.0058189 | N
27/05/2017 | 20:53 | ZN12570:PA37 | SHORT RURAL | Asset Failure | HV | 432 | 83 | 0.16049 | 0.19337 | N
28/05/2017 | 18:50 | 528:83019 | SHORT RURAL | Asset Failure | HV | 1 | 130 | 0.00058189 | 0.00044761 | N
30/05/2017 | 03:07 | ZN12690:PA24 | SHORT RURAL | Asset Failure | HV | 78 | 95 | 0.033279 | 0.034913 | N
30/05/2017 | 09:14 | ZN2196:PA13 | URBAN | Asset Failure | HV | 31 | 79 | 0.0016754 | 0.0021304 | N
30/05/2017 | 14:30 | 508:82578 | SHORT RURAL | Asset Failure | HV | 90 | 110 | 0.044286 | 0.040284 | N
30/05/2017 | 18:15 | ZN15006:PA13 | URBAN | Asset Failure | HV | 225 | 237 | 0.036704 | 0.015462 | N
30/05/2017 | 20:25 | 264:81236 | SHORT RURAL | Asset Failure | HV | 29 | 5 | 0.00064903 | 0.012981 | N
30/05/2017 | 23:48 | 222:33597 | SHORT RURAL | Asset Failure | HV | 105 | 47 | 0.022089 | 0.046998 | N
31/05/2017 | 12:37 | 511:29878 | SHORT RURAL | Asset Failure | HV | 2 | 353 | 0.0031601 | 0.00089521 | N
31/05/2017 | 19:19 | ZN12580:PA7 | URBAN | Asset Failure | HV | 172 | 85 | 0.01005 | 0.01182 | N
01/06/2017 | 00:08 | 515:35197 | LONG RURAL | Asset Failure | HV | 512 | 89 | 16.2954 | 18.2661 | N
02/06/2017 | 11:45 | 520:48172 | SHORT RURAL | Asset Failure | HV | 18 | 90 | 0.0072512 | 0.0080569 | N
04/06/2017 | 16:29 | ZN1193:PA12 | URBAN | Asset Failure | HV | 1,299 | 76 | 0.068127 | 0.089269 | N
04/06/2017 | 20:18 | ZN965:PA11 | URBAN | Asset Failure | HV | 1,160 | 86 | 0.068839 | 0.079717 | N
05/06/2017 | 09:17 | ZN14143:PA17 | SHORT RURAL | Asset Failure | HV | 9 | 808 | 0.03255 | 0.0040284 | N
07/06/2017 | 06:11 | 225:13446 | URBAN | Asset Failure | HV | 59 | 138 | 0.0056136 | 0.0040546 | N
07/06/2017 | 13:22 | ZN12580:PA7 | URBAN | Asset Failure | HV | 172 | 73 | 0.008593 | 0.01182 | N
07/06/2017 | 21:16 | ZN12690:PA24 | SHORT RURAL | Asset Failure | HV | 7 | 144 | 0.0045118 | 0.0031332 | N
08/06/2017 | 09:00 | ZN12580:PA1 | URBAN | Asset Failure | HV | 3 | 90 | 0.00018555 | 0.00020617 | N
08/06/2017 | 09:29 | 206:34432 | URBAN | Asset Failure | HV | 1,157 | 62 | 0.048992 | 0.079511 | N
08/06/2017 | 15:50 | 813:89055 | SHORT RURAL | Asset Failure | HV | 1 | 184 | 0.00082359 | 0.0004476 | N
09/06/2017 | 07:18 | 509:33395 | LONG RURAL | Asset Failure | HV | 2 | 127 | 0.090522 | 0.071352 | N
09/06/2017 | 10:47 | 220:8691 | URBAN | Asset Failure | HV | 1 | 1,493 | 0.001026 | 6.8722e-05 | N
09/06/2017 | 18:18 | 528:83024 | URBAN | Asset Failure | HV | 730 | 112 | 0.056388 | 0.050167 | N
09/06/2017 | 21:22 | ZN12610:PA11 | URBAN | Asset Failure | HV | 1,117 | 74 | 0.056804 | 0.076762 | N
10/06/2017 | 01:39 | ZN80:PA25 | URBAN | Asset Failure | HV | 1,489 | 352 | 0.35971 | 0.10233 | N
10/06/2017 | 20:56 | ZN129:PA38 | URBAN | Asset Failure | HV | 1,219 | 96 | 0.080714 | 0.083772 | N
11/06/2017 | 02:41 | 238:34151 | URBAN | Asset Failure | HV | 1,236 | 95 | 0.080693 | 0.08494 | N
12/06/2017 | 14:46 | ZN3672:PA44 | URBAN | Asset Failure | HV | 1,925 | 240 | 0.31696 | 0.13229 | N
12/06/2017 | 14:35 | ZN1788:PA14 | URBAN | Asset Failure | HV | 2 | 245 | 0.00033674 | 0.00013744 | N
12/06/2017 | 14:35 | ZN1788:PA30 | URBAN | Asset Failure | HV | 1,305 | 260 | 0.23335 | 0.089682 | N
12/06/2017 | 17:50 | ZN36800:PA46 | URBAN | Asset Failure | HV | 1,086 | 73 | 0.054543 | 0.074632 | N
13/06/2017 | 09:37 | 240:34835 | SHORT RURAL | Asset Failure | HV | 459 | 39 | 0.080085 | 0.20545 | N
14/06/2017 | 08:03 | ZN35500:PA27 | URBAN | Asset Failure | HV | 445 | 157 | 0.048012 | 0.030581 | N
14/06/2017 | 18:26 | ZN12610:PA16 | SHORT RURAL | Asset Failure | HV | 1,147 | 24 | 0.12322 | 0.5134 | N
14/06/2017 | 18:26 | ZN12610:PA6 | URBAN | Asset Failure | HV | 1,756 | 39 | 0.04667 | 0.12068 | N
15/06/2017 | 22:41 | ZN10991:PA7 | URBAN | Asset Failure | HV | 1,606 | 68 | 0.075494 | 0.11037 | N
17/06/2017 | 06:21 | ZN14892:PA9 | URBAN | Asset Failure | HV | 702 | 86 | 0.041709 | 0.048243 | N
17/06/2017 | 09:18 | 232:33407 | SHORT RURAL | Asset Failure | HV | 1 | 207 | 0.00092654 | 0.0004476 | N
18/06/2017 | 06:08 | 232:11455 | SHORT RURAL | Asset Failure | HV | 2,520 | 45 | 0.5125 | 1.128 | N
18/06/2017 | 09:21 | 514:18137 | SHORT RURAL | Asset Failure | HV | 1 | 99 | 0.00044313 | 0.0004476 | N
18/06/2017 | 17:57 | 511:29878 | SHORT RURAL | Asset Failure | HV | 3 | 152 | 0.0020422 | 0.0013428 | N
18/06/2017 | 18:45 | ZN12580:PA1 | URBAN | Asset Failure | HV | 1,193 | 94 | 0.077431 | 0.081985 | N
19/06/2017 | 10:21 | 261:81886 | URBAN | Asset Failure | HV | 97 | 49 | 0.0032663 | 0.006666 | N
20/06/2017 | 03:19 | ZN1648:PA19 | URBAN | Asset Failure | HV | 805 | 80 | 0.04441 | 0.055321 | N
20/06/2017 | 07:16 | 504:48031 | SHORT RURAL | Asset Failure | HV | 3 | 284 | 0.0038136 | 0.0013428 | N
21/06/2017 | 04:42 | ZN1610:PA3 | SHORT RURAL | Asset Failure | HV | 465 | 63 | 0.13014 | 0.20814 | N
21/06/2017 | 10:49 | 238:34141 | SHORT RURAL | Asset Failure | HV | 4 | 156 | 0.002793 | 0.0017904 | N
21/06/2017 | 16:41 | ZN12600:PA2 | SHORT RURAL | Asset Failure | HV | 41 | 64 | 0.011745 | 0.018352 | N
21/06/2017 | 22:12 | 807:74179 | SHORT RURAL | Asset Failure | HV | 50 | 328 | 0.073407 | 0.02238 | N
22/06/2017 | 18:13 | ZN931:PA11 | URBAN | Asset Failure | HV | 228 | 64 | 0.010028 | 0.015669 | N
22/06/2017 | 18:13 | ZN931:PA12 | URBAN | Asset Failure | HV | 1 | 64 | 4.3982e-05 | 6.8722e-05 | N
22/06/2017 | 18:13 | ZN931:PA13 | URBAN | Asset Failure | HV | 2 | 64 | 8.7964e-05 | 0.00013744 | N
23/06/2017 | 22:43 | ZN10994:PA10 | URBAN | Asset Failure | HV | 599 | 143 | 0.05893 | 0.041117 | N
23/06/2017 | 22:43 | ZN10994:PA19 | URBAN | Asset Failure | HV | 905 | 143 | 0.088946 | 0.062121 | N
24/06/2017 | 06:46 | ZN167:PA21 | URBAN | Asset Failure | HV | 974 | 45 | 0.030329 | 0.066858 | N
26/06/2017 | 14:27 | ZN72:PA10 | URBAN | Asset Failure | HV | 2 | 398 | 0.00054639 | 0.00013728 | N
26/06/2017 | 14:27 | ZN72:PA14 | URBAN | Asset Failure | HV | 17 | 398 | 0.0046443 | 0.0011669 | N
26/06/2017 | 14:27 | ZN72:PA26 | URBAN | Asset Failure | HV | 1 | 398 | 0.0002732 | 6.8642e-05 | N
26/06/2017 | 14:27 | ZN72:PA31 | URBAN | Asset Failure | HV | 1,664 | 211 | 0.24083 | 0.11422 | N
26/06/2017 | 14:27 | ZN72:PA35 | URBAN | Asset Failure | HV | 26 | 398 | 0.0071031 | 0.0017847 | N
27/06/2017 | 16:39 | 515:35192 | SHORT RURAL | Asset Failure | HV | 4 | 171 | 0.0030616 | 0.0017904 | N
27/06/2017 | 19:34 | ZN12570:PA35 | URBAN | Asset Failure | HV | 1,055 | 51 | 0.036933 | 0.072418 | N
28/06/2017 | 19:26 | ZN847:PA47 | SHORT RURAL | Asset Failure | HV | 1,068 | 66 | 0.31728 | 0.47804 | N
29/06/2017 | 18:29 | ZN35500:PA23 | URBAN | Asset Failure | HV | 52 | 101 | 0.0036051 | 0.0035694 | N
29/06/2017 | 18:29 | ZN35500:PA28 | URBAN | Asset Failure | HV | 583 | 100 | 0.040132 | 0.040018 | N
29/06/2017 | 18:35 | 807:74179 | SHORT RURAL | Asset Failure | HV | 50 | 16 | 0.0036524 | 0.02238 | N
29/06/2017 | 19:07 | ZN340:PA1 | SHORT RURAL | Asset Failure | HV | 110 | 148 | 0.07287 | 0.049236 | N
29/06/2017 | 19:07 | ZN340:PA14 | URBAN | Asset Failure | HV | 1 | 70 | 4.805e-05 | 6.8642e-05 | N
29/06/2017 | 19:07 | ZN340:PA20 | URBAN | Asset Failure | HV | 1,043 | 70 | 0.050081 | 0.071594 | N
30/06/2017 | 16:55 | 807:74179 | SHORT RURAL | Asset Failure | HV | 50 | 208 | 0.046558 | 0.02238 | N
30/06/2017 | 18:57 | 221:11894 | URBAN | Asset Failure | HV | 99 | 79 | 0.0053685 | 0.0067956 | N
01/07/2016 | 05:42 | ZN80:PA37 | URBAN | Asset Failure | LV | 35 | 168 | 0.0040711 | 0.002424 | N
02/07/2016 | 08:46 | ZN12570:PA24 | SHORT RURAL | Asset Failure | LV | 1 | 704 | 0.0032046 | 0.00045526 | N
02/07/2016 | 11:22 | ZN12570:PA24 | SHORT RURAL | Asset Failure | LV | 1 | 547 | 0.0024905 | 0.00045526 | N
03/07/2016 | 18:00 | ZN12650:PA13 | SHORT RURAL | Asset Failure | LV | 41 | 1,235 | 0.23052 | 0.018666 | N
05/07/2016 | 05:51 | ZN965:PA24 | URBAN | Asset Failure | LV | 22 | 638 | 0.0097155 | 0.0015237 | N
05/07/2016 | 18:39 | 228:7487 | URBAN | Asset Failure | LV | 122 | 57 | 0.0048077 | 0.0084495 | N
05/07/2016 | 19:42 | ZN35600:PA25 | URBAN | Asset Failure | LV | 172 | 123 | 0.014609 | 0.011912 | N
05/07/2016 | 20:19 | ZN4545:PA28 | URBAN | Asset Failure | LV | 136 | 41 | 0.0038257 | 0.0094191 | N
06/07/2016 | 09:24 | ZN35900:PA24 | URBAN | Asset Failure | LV | 48 | 145 | 0.004826 | 0.0033244 | N
06/07/2016 | 11:40 | ZN2568:PA39 | URBAN | Asset Failure | LV | 1 | 80 | 5.5384e-05 | 6.9259e-05 | N
06/07/2016 | 17:29 | ZN3155:PA21 | URBAN | Asset Failure | LV | 7 | 1,491 | 0.0072286 | 0.00048481 | N
06/07/2016 | 18:54 | ZN187:PA16 | URBAN | Asset Failure | LV | 82 | 645 | 0.036643 | 0.0056793 | N
06/07/2016 | 21:23 | ZN35600:PA19 | URBAN | Asset Failure | LV | 113 | 82 | 0.0064176 | 0.0078263 | N
06/07/2016 | 23:16 | ZN340:PA2 | URBAN | Asset Failure | LV | 1 | 2,784 | 0.0019282 | 6.9259e-05 | N
08/07/2016 | 06:01 | ZN9035:PA1 | URBAN | Asset Failure | LV | 9 | 239 | 0.0014895 | 0.00062322 | N
08/07/2016 | 19:49 | ZN4545:PA4 | URBAN | Asset Failure | LV | 40 | 81 | 0.0022353 | 0.0027698 | N
09/07/2016 | 16:05 | 258:80793 | URBAN | Asset Failure | LV | 124 | 51 | 0.0043794 | 0.008587 | N
10/07/2016 | 10:23 | ZN15010:PA1 | URBAN | Asset Failure | LV | 1 | 686 | 0.00047524 | 6.925e-05 | N
09/07/2016 | 20:46 | ZN72:PA22 | URBAN | Asset Failure | LV | 30 | 86 | 0.0017804 | 0.0020775 | N
10/07/2016 | 07:30 | ZN9900:PA19 | URBAN | Asset Failure | LV | 23 | 89 | 0.0014194 | 0.0015928 | N
10/07/2016 | 15:38 | 520:48172 | SHORT RURAL | Asset Failure | LV | 1 | 202 | 0.00091958 | 0.00045524 | N
11/07/2016 | 04:34 | ZN847:PA5 | URBAN | Asset Failure | LV | 53 | 251 | 0.0092123 | 0.0036703 | N
11/07/2016 | 13:08 | ZN690:PA24 | SHORT RURAL | Asset Failure | LV | 13 | 558 | 0.033023 | 0.0059181 | N
10/07/2016 | 19:25 | ZN7481:PA17 | URBAN | Asset Failure | LV | 95 | 5 | 0.00032894 | 0.0065788 | N
11/07/2016 | 22:18 | 811:74234 | SHORT RURAL | Asset Failure | LV | 1 | 117 | 0.00053263 | 0.00045524 | N
12/07/2016 | 12:05 | ZN4545:PA4 | URBAN | Asset Failure | LV | 40 | 547 | 0.015152 | 0.0027701 | N
12/07/2016 | 17:54 | ZN3472:PA30 | URBAN | Asset Failure | LV | 31 | 155 | 0.0033351 | 0.0021468 | N
13/07/2016 | 07:34 | ZN2466:PA7 | URBAN | Asset Failure | LV | 1 | 176 | 0.00012181 | 6.9254e-05 | N
13/07/2016 | 11:06 | ZN35500:PA32 | URBAN | Asset Failure | LV | 73 | 109 | 0.0054895 | 0.0050555 | N
13/07/2016 | 12:10 | ZN15005:PA8 | URBAN | Asset Failure | LV | 36 | 223 | 0.0055489 | 0.0024931 | N
13/07/2016 | 14:40 | ZN9037:PA8 | URBAN | Asset Failure | LV | 37 | 548 | 0.014038 | 0.0025624 | N
13/07/2016 | 15:40 | ZN9037:PA4 | URBAN | Asset Failure | LV | 47 | 175 | 0.0056961 | 0.0032549 | N
13/07/2016 | 15:40 | ZN9700:PA23 | URBAN | Asset Failure | LV | 22 | 175 | 0.0026663 | 0.0015236 | N
15/07/2016 | 06:57 | ZN36100:PA12 | URBAN | Asset Failure | LV | 14 | 1,580 | 0.015319 | 0.00096958 | N
15/07/2016 | 13:17 | 203:8084 | URBAN | Asset Failure | LV | 18 | 53 | 0.00065634 | 0.0012466 | N
15/07/2016 | 18:52 | 228:7487 | URBAN | Asset Failure | LV | 57 | 422 | 0.016641 | 0.0039476 | N
16/07/2016 | 11:33 | ZN690:PA36 | URBAN | Asset Failure | LV | 19 | 337 | 0.004431 | 0.0013156 | N
17/07/2016 | 01:53 | ZN4545:PA4 | URBAN | Asset Failure | LV | 46 | 222 | 0.0070634 | 0.0031852 | N
17/07/2016 | 21:40 | ZN4545:PA4 | URBAN | Asset Failure | LV | 45 | 315 | 0.0098151 | 0.0031159 | N
18/07/2016 | 09:31 | ZN4545:PA4 | URBAN | Asset Failure | LV | 45 | 553 | 0.017232 | 0.0031159 | N
19/07/2016 | 21:56 | ZN12570:PA40 | SHORT RURAL | Asset Failure | LV | 83 | 189 | 0.071195 | 0.037709 | N
20/07/2016 | 19:20 | ZN4545:PA29 | URBAN | Asset Failure | LV | 39 | 80 | 0.0021599 | 0.0026998 | N
21/07/2016 | 03:05 | ZN1287:PA11 | URBAN | Asset Failure | LV | 81 | 84 | 0.0047262 | 0.0056075 | N
21/07/2016 | 06:33 | ZN1287:PA11 | URBAN | Asset Failure | LV | 81 | 156 | 0.0087608 | 0.0056075 | N
21/07/2016 | 17:12 | ZN12570:PA24 | SHORT RURAL | Asset Failure | LV | 24 | 351 | 0.038243 | 0.010895 | N
22/07/2016 | 15:26 | ZN263:PA33 34KLM | CBD | Asset Failure | LV | 7 | 2,844 | 0.6417 | 0.022563 | N
22/07/2016 | 16:49 | ZN12630:PA23 | SHORT RURAL | Asset Failure | LV | 1 | 169 | 0.00076529 | 0.00045395 | N
23/07/2016 | 06:50 | 523:33508 | SHORT RURAL | Asset Failure | LV | 1 | 140 | 0.00063547 | 0.00045391 | N
23/07/2016 | 11:02 | 511:29873 | URBAN | Asset Failure | LV | 1 | 368 | 0.0002548 | 6.9235e-05 | N
23/07/2016 | 17:00 | ZN15006:PA12 | URBAN | Asset Failure | LV | 52 | 100 | 0.0036002 | 0.0036002 | N
23/07/2016 | 18:52 | 214:8666 | URBAN | Asset Failure | LV | 54 | 43 | 0.0016076 | 0.0037387 | N
23/07/2016 | 19:02 | ZN15008:PA5 | URBAN | Asset Failure | LV | 108 | 118 | 0.0087984 | 0.0074774 | N
23/07/2016 | 19:02 | ZN15008:PA7 | URBAN | Asset Failure | LV | 1 | 118 | 8.1697e-05 | 6.9235e-05 | N
24/07/2016 | 08:54 | ZN12610:PA10 | URBAN | Asset Failure | LV | 1 | 341 | 0.0002364 | 6.9235e-05 | N
24/07/2016 | 11:38 | ZN5868:PA5 | SHORT RURAL | Asset Failure | LV | 90 | 262 | 0.10687 | 0.040852 | N
24/07/2016 | 14:51 | ZN965:PA38 | URBAN | Asset Failure | LV | 42 | 169 | 0.0049124 | 0.0029079 | N
24/07/2016 | 18:33 | ZN2602:PA31 | URBAN | Asset Failure | LV | 89 | 236 | 0.014559 | 0.0061619 | N
24/07/2016 | 19:51 | ZN965:PA38 | URBAN | Asset Failure | LV | 42 | 308 | 0.0089582 | 0.0029079 | N
25/07/2016 | 10:07 | ZN8700:PA61 62GHJ | CBD | Asset Failure | LV | 1 | 412 | 0.013291 | 0.0032234 | N
25/07/2016 | 10:22 | 801:74121 | LONG RURAL | Asset Failure | LV | 1 | 175 | 0.062433 | 0.035676 | N
23/07/2016 | 09:11 | ZN12600:PA2 | SHORT RURAL | Asset Failure | LV | 4 | 169 | 0.0030684 | 0.0018156 | N
26/07/2016 | 10:34 | ZN10996:PA4 | URBAN | Asset Failure | LV | 180 | 48 | 0.0059279 | 0.012462 | N
25/07/2016 | 18:36 | ZN9118:PA20 | URBAN | Asset Failure | LV | 47 | 125 | 0.0040681 | 0.003254 | N
25/07/2016 | 21:53 | ZN2466:PA40 | URBAN | Asset Failure | LV | 118 | 67 | 0.0054356 | 0.0081697 | N
26/07/2016 | 12:09 | ZN965:PA8 | URBAN | Asset Failure | LV | 12 | 131 | 0.001088 | 0.00083082 | N
27/07/2016 | 11:07 | ZN15001:PA10 | URBAN | Asset Failure | LV | 1 | 233 | 0.00016107 | 6.9237e-05 | N
27/07/2016 | 12:40 | ZN36800:PA57 | URBAN | Asset Failure | LV | 48 | 185 | 0.0061482 | 0.0033234 | N
27/07/2016 | 17:42 | 227:13015 | SHORT RURAL | Asset Failure | LV | 1 | 143 | 0.00064753 | 0.00045393 | N
27/07/2016 | 20:23 | ZN690:PA11 | URBAN | Asset Failure | LV | 1 | 116 | 8.0315e-05 | 6.9237e-05 | N
27/07/2016 | 20:23 | ZN690:PA5 | URBAN | Asset Failure | LV | 96 | 116 | 0.0077102 | 0.0066467 | N
28/07/2016 | 13:41 | 261:81879 | URBAN | Asset Failure | LV | 1 | 71 | 4.899e-05 | 6.9227e-05 | N
28/07/2016 | 20:17 | ZN9252:PA27 | URBAN | Asset Failure | LV | 46 | 108 | 0.0034249 | 0.0031844 | N
28/07/2016 | 23:35 | ZN116:PA33 | URBAN | Asset Failure | LV | 74 | 283 | 0.014516 | 0.0051228 | N
13/07/2016 | 10:32 | ZN2635:PA31 | URBAN | Asset Failure | LV | 46 | 221 | 0.0070404 | 0.0031857 | N
29/07/2016 | 17:02 | ZN1673:PA7 | URBAN | Asset Failure | LV | 23 | 857 | 0.01365 | 0.0015922 | N
29/07/2016 | 19:20 | ZN15008:PA7 | URBAN | Asset Failure | LV | 44 | 34 | 0.0010458 | 0.003046 | N
30/07/2016 | 11:24 | ZN180:PA10 | URBAN | Asset Failure | LV | 3 | 181 | 0.00037591 | 0.00020769 | N
30/07/2016 | 11:24 | ZN180:PA30 | URBAN | Asset Failure | LV | 36 | 181 | 0.0045109 | 0.0024922 | N
30/07/2016 | 11:24 | ZN180:PA9 | URBAN | Asset Failure | LV | 85 | 181 | 0.010631 | 0.0058844 | N
31/07/2016 | 09:04 | ZN9118:PA26 | URBAN | Asset Failure | LV | 8 | 216 | 0.0011963 | 0.00055384 | N
31/07/2016 | 09:08 | 223:14397 | URBAN | Asset Failure | LV | 13 | 652 | 0.005867 | 0.00089998 | N
01/08/2016 | 07:19 | ZN3155:PA16 | URBAN | Asset Failure | LV | 93 | 671 | 0.043198 | 0.0064384 | N
01/08/2016 | 08:09 | ZN4545:PA36 | URBAN | Asset Failure | LV | 48 | 306 | 0.010152 | 0.003323 | N
02/08/2016 | 17:36 | ZN9118:PA7 | URBAN | Asset Failure | LV | 1 | 257 | 0.00017823 | 6.923e-05 | N
03/08/2016 | 10:59 | ZN35800:PA16 | URBAN | Asset Failure | LV | 1 | 71 | 4.9154e-05 | 6.9231e-05 | N
03/08/2016 | 16:43 | ZN10999:PA12 | URBAN | Asset Failure | LV | 44 | 172 | 0.005237 | 0.0030462 | N
04/08/2016 | 11:54 | ZN180:PA7 | URBAN | Asset Failure | LV | 43 | 376 | 0.011171 | 0.0029746 | N
04/08/2016 | 16:30 | ZN10999:PA12 | URBAN | Asset Failure | LV | 55 | 185 | 0.0070387 | 0.0038047 | N
04/08/2016 | 18:35 | ZN15012:PA6 | URBAN | Asset Failure | LV | 79 | 55 | 0.0029948 | 0.0054649 | N
05/08/2016 | 06:42 | ZN35500:PA28 | URBAN | Asset Failure | LV | 38 | 163 | 0.0042848 | 0.0026287 | N
05/08/2016 | 06:42 | ZN8000:PA25 | URBAN | Asset Failure | LV | 17 | 163 | 0.0019169 | 0.001176 | N
06/08/2016 | 12:14 | ZN35500:PA28 | URBAN | Asset Failure | LV | 38 | 286 | 0.0075183 | 0.0026288 | N
06/08/2016 | 12:14 | ZN8000:PA25 | URBAN | Asset Failure | LV | 17 | 286 | 0.0033634 | 0.001176 | N
06/08/2016 | 18:24 | ZN2602:PA34 | URBAN | Asset Failure | LV | 125 | 60 | 0.0052128 | 0.0086472 | N
07/08/2016 | 06:59 | ZN15006:PA15 | URBAN | Asset Failure | LV | 60 | 121 | 0.0050223 | 0.0041507 | N
07/08/2016 | 18:28 | ZN9118:PA20 | URBAN | Asset Failure | LV | 171 | 192 | 0.022713 | 0.011829 | N
07/08/2016 | 18:42 | 243:80083 | SHORT RURAL | Asset Failure | LV | 1 | 37 | 0.00016943 | 0.00045463 | N
08/08/2016 | 07:42 | ZN9252:PA30 | URBAN | Asset Failure | LV | 37 | 263 | 0.0067223 | 0.0025596 | N
08/08/2016 | 08:53 | ZN35400:PA110 | URBAN | Asset Failure | LV | 54 | 261 | 0.009763 | 0.0037356 | N
08/08/2016 | 10:48 | ZN180:PA22 | URBAN | Asset Failure | LV | 59 | 62 | 0.0025305 | 0.0040815 | N
08/08/2016 | 10:55 | ZN965:PA29 | URBAN | Asset Failure | LV | 69 | 404 | 0.019293 | 0.0047733 | N
08/08/2016 | 19:08 | 507:80932 | SHORT RURAL | Asset Failure | LV | 7 | 217 | 0.0069059 | 0.0031824 | N
09/08/2016 | 18:06 | ZN7481:PA20 | URBAN | Asset Failure | LV | 49 | 79 | 0.002662 | 0.0033897 | N
10/08/2016 | 16:08 | ZN3155:PA29 | URBAN | Asset Failure | LV | 33 | 652 | 0.014887 | 0.0022829 | N
10/08/2016 | 16:08 | ZN3155:PA44 | URBAN | Asset Failure | LV | 137 | 662 | 0.062741 | 0.0094775 | N
10/08/2016 | 18:13 | ZN12570:PA25 | SHORT RURAL | Asset Failure | LV | 30 | 91 | 0.012505 | 0.013684 | N
11/08/2016 | 00:23 | ZN35500:PA32 | URBAN | Asset Failure | LV | 70 | 307 | 0.014877 | 0.0048408 | N
11/08/2016 | 06:15 | 513:48056 | SHORT RURAL | Asset Failure | LV | 1 | 193 | 0.00087848 | 0.000456 | N
11/08/2016 | 07:20 | ZN15005:PA2 | URBAN | Asset Failure | LV | 57 | 175 | 0.0068982 | 0.0039418 | N
11/08/2016 | 08:32 | ZN14891:PA16 | SHORT RURAL | Asset Failure | LV | 1 | 267 | 0.0012179 | 0.000456 | N
11/08/2016 | 08:40 | 806:82662 | SHORT RURAL | Asset Failure | LV | 1 | 184 | 0.00083874 | 0.000456 | N
11/08/2016 | 17:17 | ZN35370:PA8 | SHORT RURAL | Asset Failure | LV | 13 | 116 | 0.0068785 | 0.005928 | N
13/08/2016 | 00:53 | ZN398:PA9 | URBAN | Asset Failure | LV | 63 | 187 | 0.0081474 | 0.0043569 | N
13/08/2016 | 07:11 | 507:80914 | SHORT RURAL | Asset Failure | LV | 1 | 167 | 0.00076155 | 0.00045602 | N
14/08/2016 | 05:37 | ZN180:PA34 | URBAN | Asset Failure | LV | 27 | 717 | 0.013379 | 0.0018672 | N
14/08/2016 | 18:10 | ZN1193:PA15 | URBAN | Asset Failure | LV | 41 | 20 | 0.00056709 | 0.0028354 | N
14/08/2016 | 19:58 | ZN398:PA19 | URBAN | Asset Failure | LV | 43 | 201 | 0.0059837 | 0.0029738 | N
14/08/2016 | 19:59 | 514:18137 | SHORT RURAL | Asset Failure | LV | 3 | 76 | 0.0010397 | 0.001368 | N
15/08/2016 | 07:36 | ZN2568:PA32 | URBAN | Asset Failure | LV | 33 | 193 | 0.0044103 | 0.0022822 | N
16/08/2016 | 07:47 | 813:89061 | LONG RURAL | Asset Failure | LV | 1 | 430 | 0.15323 | 0.035676 | N
16/08/2016 | 08:26 | ZN12630:PA24 | SHORT RURAL | Asset Failure | LV | 1 | 363 | 0.0016573 | 0.00045602 | N
16/08/2016 | 15:29 | ZN1287:PA24 | URBAN | Asset Failure | LV | 16 | 181 | 0.0020028 | 0.0011065 | N
16/08/2016 | 15:59 | 528:83014 | SHORT RURAL | Asset Failure | LV | 27 | 306 | 0.037676 | 0.012312 | N
17/08/2016 | 07:09 | ZN1287:PA12 | URBAN | Asset Failure | LV | 57 | 186 | 0.0073277 | 0.0039421 | N
18/08/2016 | 09:28 | ZN3472:PA29 | URBAN | Asset Failure | LV | 42 | 202 | 0.0058856 | 0.0029139 | N
19/08/2016 | 05:50 | ZN10991:PA8 | URBAN | Asset Failure | LV | 1 | 439 | 0.00030487 | 6.9379e-05 | N
19/08/2016 | 12:11 | ZN9900:PA13 | URBAN | Asset Failure | LV | 35 | 84 | 0.0020349 | 0.0024283 | N
19/08/2016 | 13:44 | ZN2635:PA31 | URBAN | Asset Failure | LV | 39 | 97 | 0.0026327 | 0.0027058 | N
20/08/2016 | 17:53 | 256:80650 | URBAN | Asset Failure | LV | 13 | 226 | 0.0020384 | 0.00090194 | N
21/08/2016 | 17:51 | ZN180:PA17 | URBAN | Asset Failure | LV | 34 | 159 | 0.0037429 | 0.0023589 | N
23/08/2016 | 09:50 | ZN1287:PA23 | URBAN | Asset Failure | LV | 39 | 100 | 0.0026945 | 0.0026945 | N
23/08/2016 | 18:52 | 511:29876 | SHORT RURAL | Asset Failure | LV | 27 | 233 | 0.028739 | 0.012334 | N
23/08/2016 | 20:51 | ZN262:PA42 | URBAN | Asset Failure | LV | 98 | 74 | 0.0049889 | 0.0067708 | N
24/08/2016 | 09:35 | ZN9245:PA42 | URBAN | Asset Failure | LV | 54 | 105 | 0.0039175 | 0.003731 | N
24/08/2016 | 22:35 | ZN965:PA2 | URBAN | Asset Failure | LV | 60 | 249 | 0.01034 | 0.0041455 | N
25/08/2016 | 06:47 | ZN9035:PA1 | URBAN | Asset Failure | LV | 9 | 282 | 0.0017537 | 0.00062185 | N
25/08/2016 | 18:27 | ZN36800:PA57 | URBAN | Asset Failure | LV | 164 | 1,847 | 0.2093 | 0.011331 | N
25/08/2016 | 21:00 | ZN35400:PA72 | URBAN | Asset Failure | LV | 66 | 915 | 0.041726 | 0.0045602 | N
25/08/2016 | 22:06 | ZN965:PA8 | URBAN | Asset Failure | LV | 30 | 73 | 0.0015156 | 0.0020728 | N
25/08/2016 | 15:05 | ZN10991:PA13 | URBAN | Asset Failure | LV | 1 | 1,435 | 0.00099127 | 6.9094e-05 | N
26/08/2016 | 11:25 | ZN35500:PA32 | URBAN | Asset Failure | LV | 18 | 130 | 0.0016168 | 0.0012437 | N
26/08/2016 | 15:08 | 504:48032 | URBAN | Asset Failure | LV | 1 | 57 | 3.9384e-05 | 6.9094e-05 | N
26/08/2016 | 16:55 | ZN35500:PA23 | URBAN | Asset Failure | LV | 18 | 140 | 0.0017412 | 0.0012437 | N
26/08/2016 | 20:18 | ZN3672:PA13 | URBAN | Asset Failure | LV | 1 | 342 | 0.0002363 | 6.9094e-05 | N
26/08/2016 | 20:18 | ZN3672:PA9 | URBAN | Asset Failure | LV | 56 | 341 | 0.013197 | 0.0038693 | N
27/08/2016 | 01:30 | ZN965:PA38 | URBAN | Asset Failure | LV | 25 | 870 | 0.015015 | 0.0017265 | N
28/08/2016 | 05:00 | ZN2602:PA17 | URBAN | Asset Failure | LV | 42 | 75 | 0.0021754 | 0.0029005 | N
28/08/2016 | 06:39 | ZN965:PA24 | URBAN | Asset Failure | LV | 17 | 391 | 0.0045904 | 0.001174 | N
28/08/2016 | 20:00 | 512:48049 | SHORT RURAL | Asset Failure | LV | 5 | 180 | 0.0041096 | 0.0022831 | N
29/08/2016 | 20:24 | ZN3154:PA16 | URBAN | Asset Failure | LV | 30 | 330 | 0.006837 | 0.0020718 | N
30/08/2016 | 00:14 | ZN9700:PA16 | URBAN | Asset Failure | LV | 40 | 455 | 0.012576 | 0.0027625 | N
30/08/2016 | 12:50 | ZN2568:PA16 | URBAN | Asset Failure | LV | 45 | 120 | 0.0037293 | 0.0031078 | N
30/08/2016 | 13:09 | ZN35600:PA19 | URBAN | Asset Failure | LV | 44 | 291 | 0.0088279 | 0.0030387 | N
31/08/2016 | 00:05 | ZN9550:PA6 | URBAN | Asset Failure | LV | 45 | 415 | 0.012886 | 0.0031068 | N
31/08/2016 | 09:32 | ZN180:PA18 | URBAN | Asset Failure | LV | 31 | 258 | 0.0055218 | 0.0021402 | N
31/08/2016 | 09:32 | ZN180:PA20 | URBAN | Asset Failure | LV | 34 | 258 | 0.0060553 | 0.0023473 | N
01/09/2016 | 07:17 | 213:33774 | URBAN | Asset Failure | LV | 61 | 73 | 0.0030743 | 0.0042114 | N
02/09/2016 | 08:16 | ZN15004:PA9 | URBAN | Asset Failure | LV | 59 | 201 | 0.0081874 | 0.0040733 | N
02/09/2016 | 16:50 | ZN12570:PA26 | URBAN | Asset Failure | LV | 14 | 55 | 0.0005316 | 0.00096655 | N
02/09/2016 | 14:30 | ZN12570:PA37 | SHORT RURAL | Asset Failure | LV | 31 | 134 | 0.019009 | 0.014151 | N
02/09/2016 | 18:24 | 802:82220 | SHORT RURAL | Asset Failure | LV | 1 | 846 | 0.0038618 | 0.00045647 | N
02/09/2016 | 23:36 | ZN965:PA20 | URBAN | Asset Failure | LV | 38 | 343 | 0.0090004 | 0.0026235 | N
03/09/2016 | 03:20 | ZN965:PA42 | URBAN | Asset Failure | LV | 35 | 120 | 0.0028997 | 0.0024164 | N
03/09/2016 | 15:30 | ZN965:PA35 | URBAN | Asset Failure | LV | 34 | 40 | 0.00093895 | 0.0023474 | N
03/09/2016 | 16:39 | 232:11457 | SHORT RURAL | Asset Failure | LV | 11 | 251 | 0.012603 | 0.0050212 | N
05/09/2016 | 12:03 | ZN9900:PA1 | URBAN | Asset Failure | LV | 40 | 15 | 0.00041425 | 0.0027617 | N
05/09/2016 | 12:03 | ZN9900:PA8 | URBAN | Asset Failure | LV | 31 | 327 | 0.0069955 | 0.0021403 | N
05/09/2016 | 23:00 | ZN3922:PA29 | URBAN | Asset Failure | LV | 58 | 1,279 | 0.051223 | 0.0040044 | N
06/09/2016 | 09:14 | ZN2568:PA40 | URBAN | Asset Failure | LV | 1 | 705 | 0.00048678 | 6.9042e-05 | N
06/09/2016 | 09:54 | ZN3154:PA23 | URBAN | Asset Failure | LV | 11 | 525 | 0.0039872 | 0.00075946 | N
06/09/2016 | 10:05 | 235:2120 | SHORT RURAL | Asset Failure | LV | 4 | 125 | 0.0022824 | 0.0018259 | N
06/09/2016 | 14:07 | ZN10994:PA20 | URBAN | Asset Failure | LV | 53 | 218 | 0.0079771 | 0.0036592 | N
08/09/2016 | 09:01 | ZN3154:PA14 | URBAN | Asset Failure | LV | 48 | 109 | 0.0036131 | 0.0033148 | N
08/09/2016 | 15:50 | ZN35370:PA2 | SHORT RURAL | Asset Failure | LV | 12 | 87 | 0.0047451 | 0.0054541 | N
09/09/2016 | 05:24 | ZN9035:PA11 | URBAN | Asset Failure | LV | 41 | 195 | 0.0055316 | 0.0028314 | N
10/09/2016 | 06:15 | ZN3472:PA22 | URBAN | Asset Failure | LV | 42 | 420 | 0.012182 | 0.0029006 | N
10/09/2016 | 06:28 | ZN1193:PA10 | URBAN | Asset Failure | LV | 39 | 117 | 0.0031512 | 0.0026934 | N
12/09/2016 | 09:26 | 807:74184 | SHORT RURAL | Asset Failure | LV | 1 | 94 | 0.00042723 | 0.0004545 | N
12/09/2016 | 16:27 | ZN9245:PA33 | URBAN | Asset Failure | LV | 10 | 1,613 | 0.01114 | 0.00069062 | N
13/09/2016 | 10:27 | ZN188:PA17 | URBAN | Asset Failure | LV | 84 | 213 | 0.012357 | 0.0058014 | N
13/09/2016 | 18:21 | ZN3672:PA13 | URBAN | Asset Failure | LV | 55 | 205 | 0.0078034 | 0.0037985 | N
13/09/2016 | 20:49 | 258:80775 | URBAN | Asset Failure | LV | 1 | 82 | 5.6575e-05 | 6.9064e-05 | N
14/09/2016 | 09:14 | ZN12570:PA33 | SHORT RURAL | Asset Failure | LV | 21 | 211 | 0.020139 | 0.0095447 | N
16/09/2016 | 05:51 | ZN9900:PA5 | URBAN | Asset Failure | LV | 26 | 84 | 0.001503 | 0.0017954 | N
16/09/2016 | 16:57 | 228:7490 | SHORT RURAL | Asset Failure | LV | 12 | 98 | 0.0053322 | 0.0054521 | N
17/09/2016 | 05:10 | 228:7490 | SHORT RURAL | Asset Failure | LV | 12 | 600 | 0.032669 | 0.0054484 | N
18/09/2016 | 04:27 | ZN187:PA13 | URBAN | Asset Failure | LV | 48 | 314 | 0.010409 | 0.0033151 | N
18/09/2016 | 10:51 | 807:74179 | SHORT RURAL | Asset Failure | LV | 1 | 99 | 0.00044949 | 0.00045403 | N
18/09/2016 | 14:45 | ZN2635:PA38 | URBAN | Asset Failure | LV | 83 | 1,083 | 0.0621 | 0.0057323 | N
18/09/2016 | 14:45 | ZN2635:PA57 | URBAN | Asset Failure | LV | 54 | 330 | 0.012307 | 0.0037295 | N
18/09/2016 | 21:44 | ZN35500:PA24 | URBAN | Asset Failure | LV | 38 | 106 | 0.0027819 | 0.0026244 | N
19/09/2016 | 13:41 | ZN12630:PA24 | SHORT RURAL | Asset Failure | LV | 1 | 459 | 0.0020844 | 0.00045403 | N
19/09/2016 | 19:12 | 520:48172 | SHORT RURAL | Asset Failure | LV | 1 | 207 | 0.00093985 | 0.00045403 | N
21/09/2016 | 06:40 | ZN12690:PA7 | SHORT RURAL | Asset Failure | LV | 1 | 200 | 0.00090634 | 0.00045404 | N
22/09/2016 | 09:24 | ZN180:PA30 | URBAN | Asset Failure | LV | 43 | 171 | 0.0050725 | 0.002969 | N
22/09/2016 | 13:26 | ZN12570:PA24 | SHORT RURAL | Asset Failure | LV | 45 | 624 | 0.12737 | 0.020426 | N
23/09/2016 | 08:56 | 812:19072 | SHORT RURAL | Asset Failure | LV | 1 | 164 | 0.00074442 | 0.00045391 | N
24/09/2016 | 17:07 | ZN2602:PA29 | URBAN | Asset Failure | LV | 19 | 1,619 | 0.021239 | 0.0013119 | N
27/09/2016 | 15:35 | ZN2310:PA61 | URBAN | Asset Failure | LV | 1 | 194 | 0.00013404 | 6.9047e-05 | N
28/09/2016 | 15:11 | ZN15006:PA2 | URBAN | Asset Failure | LV | 65 | 39 | 0.0017504 | 0.0044882 | N
28/09/2016 | 20:27 | ZN7900:PA7 | URBAN | Asset Failure | LV | 52 | 58 | 0.0020723 | 0.0035905 | N
29/09/2016 | 21:15 | ZN188:PA26 | URBAN | Asset Failure | LV | 29 | 1,155 | 0.023121 | 0.0020018 | N
30/09/2016 | 15:15 | ZN36300:PA3 | URBAN | Asset Failure | LV | 58 | 292 | 0.011681 | 0.0040036 | N
01/10/2016 | 04:36 | ZN9245:PA33 | URBAN | Asset Failure | LV | 64 | 158 | 0.0069876 | 0.0044198 | N
01/10/2016 | 06:02 | 264:81240 | SHORT RURAL | Asset Failure | LV | 2 | 238 | 0.0021548 | 0.00090536 | N
01/10/2016 | 11:31 | ZN188:PA31 | URBAN | Asset Failure | LV | 27 | 49 | 0.00091023 | 0.0018646 | N
01/10/2016 | 12:10 | ZN10994:PA7 | URBAN | Asset Failure | LV | 39 | 185 | 0.0049826 | 0.0026933 | N
01/10/2016 | 15:14 | ZN1610:PA11 | URBAN | Asset Failure | LV | 112 | 36 | 0.0027844 | 0.0077346 | N
02/10/2016 | 11:07 | 256:80650 | URBAN | Asset Failure | LV | 72 | 97 | 0.0048281 | 0.0049723 | N
03/10/2016 | 14:42 | 811:74234 | SHORT RURAL | Asset Failure | LV | 13 | 48 | 0.0028247 | 0.0058849 | N
03/10/2016 | 22:17 | ZN10991:PA7 | URBAN | Asset Failure | LV | 104 | 58 | 0.0041657 | 0.0071822 | N
04/10/2016 | 07:23 | 256:80650 | URBAN | Asset Failure | LV | 26 | 149 | 0.002683 | 0.0017955 | N
04/10/2016 | 07:51 | ZN9037:PA2 | URBAN | Asset Failure | LV | 1 | 169 | 0.00011671 | 6.9059e-05 | N
04/10/2016 | 07:51 | ZN9550:PA43 | URBAN | Asset Failure | LV | 29 | 169 | 0.0033846 | 0.0020027 | N
04/10/2016 | 10:10 | ZN12610:PA10 | URBAN | Asset Failure | LV | 19 | 65 | 0.00085288 | 0.0013121 | N
29/09/2016 | 21:15 | ZN188:PA26 | URBAN | Asset Failure | LV | 33 | 1,155 | 0.02631 | 0.0022779 | N
04/10/2016 | 18:33 | 511:29878 | SHORT RURAL | Asset Failure | LV | 1 | 367 | 0.0016613 | 0.00045268 | N
05/10/2016 | 06:57 | ZN9118:PA8 | URBAN | Asset Failure | LV | 14 | 258 | 0.0024945 | 0.00096685 | N
05/10/2016 | 16:52 | 221:11893 | URBAN | Asset Failure | LV | 92 | 53 | 0.00336 | 0.0063536 | N
07/10/2016 | 16:15 | ZN35400:PA110 | URBAN | Asset Failure | LV | 10 | 347 | 0.0023955 | 0.00069034 | N
07/10/2016 | 17:02 | ZN14143:PA12 | SHORT RURAL | Asset Failure | LV | 43 | 148 | 0.0288 | 0.01946 | N
07/10/2016 | 20:48 | ZN36300:PA9 | URBAN | Asset Failure | LV | 97 | 172 | 0.011504 | 0.0066963 | N
07/10/2016 | 20:50 | ZN36300:PA11 | URBAN | Asset Failure | LV | 101 | 419 | 0.0292 | 0.0069725 | N
07/10/2016 | 20:50 | ZN36300:PA7 | URBAN | Asset Failure | LV | 69 | 195 | 0.0092886 | 0.0047634 | N
09/10/2016 | 08:30 | ZN2835:PA28 | URBAN | Asset Failure | LV | 34 | 270 | 0.0063421 | 0.0023489 | N
09/10/2016 | 08:30 | ZN2835:PA36 | URBAN | Asset Failure | LV | 78 | 270 | 0.014529 | 0.0053887 | N
09/10/2016 | 14:31 | ZN15012:PA6 | URBAN | Asset Failure | LV | 56 | 98 | 0.0037992 | 0.0038688 | N
09/10/2016 | 19:21 | ZN3155:PA24 | URBAN | Asset Failure | LV | 62 | 308 | 0.013206 | 0.0042833 | N
09/10/2016 | 23:11 | ZN188:PA21 | URBAN | Asset Failure | LV | 87 | 145 | 0.0087152 | 0.0060105 | N
10/10/2016 | 02:11 | ZN188:PA21 | URBAN | Asset Failure | LV | 87 | 79 | 0.0047483 | 0.0060105 | N
10/10/2016 | 10:40 | ZN12640:PA7 | URBAN | Asset Failure | LV | 1 | 560 | 0.00038657 | 6.9086e-05 | N
13/10/2016 | 12:47 | ZN36800:PA43 | URBAN | Asset Failure | LV | 2 | 437 | 0.00060403 | 0.00013828 | N
13/10/2016 | 13:58 | 242:81541 | URBAN | Asset Failure | LV | 88 | 22 | 0.0013386 | 0.0060844 | N
13/10/2016 | 14:17 | ZN9252:PA25 | URBAN | Asset Failure | LV | 40 | 298 | 0.008236 | 0.0027656 | N
13/10/2016 | 20:45 | ZN35500:PA28 | URBAN | Asset Failure | LV | 38 | 60 | 0.0015764 | 0.0026273 | N
14/10/2016 | 13:17 | ZN116:PA43 | URBAN | Asset Failure | LV | 93 | 148 | 0.0094972 | 0.0064301 | N
14/10/2016 | 16:29 | ZN35500:PA28 | URBAN | Asset Failure | LV | 38 | 53 | 0.0013857 | 0.0026273 | N
15/10/2016 | 10:10 | ZN1788:PA37 | URBAN | Asset Failure | LV | 6 | 300 | 0.0012432 | 0.00041442 | N
15/10/2016 | 17:34 | ZN9700:PA17 | URBAN | Asset Failure | LV | 9 | 71 | 0.00044135 | 0.00062162 | N
16/10/2016 | 16:02 | ZN15005:PA6 | URBAN | Asset Failure | LV | 38 | 76 | 0.0019943 | 0.0026246 | N
17/10/2016 | 11:00 | 526:34637 | SHORT RURAL | Asset Failure | LV | 2 | 100 | 0.00090082 | 0.00090082 | N
17/10/2016 | 17:42 | ZN965:PA15 | URBAN | Asset Failure | LV | 32 | 64 | 0.0014145 | 0.0022102 | N
18/10/2016 | 08:11 | ZN9245:PA15 | URBAN | Asset Failure | LV | 10 | 588 | 0.0040629 | 0.00069073 | N
18/10/2016 | 08:58 | 513:48059 | SHORT RURAL | Asset Failure | LV | 1 | 134 | 0.00060159 | 0.00045041 | N
19/10/2016 | 09:23 | ZN35500:PA34 | URBAN | Asset Failure | LV | 96 | 96 | 0.0063847 | 0.0066312 | N
19/10/2016 | 15:53 | 256:80650 | URBAN | Asset Failure | LV | 2 | 163 | 0.00022512 | 0.00013815 | N
20/10/2016 | 13:47 | ZN2196:PA9 | URBAN | Asset Failure | LV | 34 | 182 | 0.0042835 | 0.0023486 | N
21/10/2016 | 01:51 | ZN9245:PA42 | URBAN | Asset Failure | LV | 38 | 429 | 0.011317 | 0.002638 | N
21/10/2016 | 08:36 | ZN1610:PA11 | URBAN | Asset Failure | LV | 57 | 207 | 0.0081909 | 0.003957 | N
21/10/2016 | 13:42 | ZN9245:PA1 | URBAN | Asset Failure | LV | 52 | 183 | 0.0065976 | 0.0036099 | N
22/10/2016 | 16:55 | ZN15006:PA12 | URBAN | Asset Failure | LV | 72 | 79 | 0.0039503 | 0.0049721 | N
23/10/2016 | 21:06 | ZN195:PA29 | URBAN | Asset Failure | LV | 59 | 143 | 0.0058325 | 0.0040744 | N
24/10/2016 | 12:30 | ZN14892:PA19 | URBAN | Asset Failure | LV | 1 | 389 | 0.00026871 | 6.9058e-05 | N
24/10/2016 | 13:13 | ZN9245:PA6 | URBAN | Asset Failure | LV | 1 | 166 | 0.00011496 | 6.9058e-05 | N
24/10/2016 | 13:16 | ZN9035:PA7 | URBAN | Asset Failure | LV | 32 | 104 | 0.0022983 | 0.0022099 | N
25/10/2016 | 08:58 | ZN2835:PA15 | URBAN | Asset Failure | LV | 47 | 212 | 0.006881 | 0.0032458 | N
25/10/2016 | 14:30 | ZN35500:PA28 | URBAN | Asset Failure | LV | 38 | 16 | 0.00041988 | 0.0026242 | N
24/10/2016 | 17:20 | ZN14892:PA19 | URBAN | Asset Failure | LV | 29 | 75 | 0.001502 | 0.0020027 | N
26/10/2016 | 14:25 | ZN129:PA5 | URBAN | Asset Failure | LV | 57 | 253 | 0.009957 | 0.0039364 | N
26/10/2016 | 18:49 | 513:48056 | SHORT RURAL | Asset Failure | LV | 3 | 155 | 0.0020936 | 0.0013507 | N
27/10/2016 | 21:14 | 513:48059 | SHORT RURAL | Asset Failure | LV | 2 | 126 | 0.0011343 | 0.00090023 | N
01/11/2016 | 09:24 | ZN15011:PA6 | URBAN | Asset Failure | LV | 1 | 260 | 0.00017983 | 6.9041e-05 | N
01/11/2016 | 12:18 | ZN10990:PA11 | URBAN | Asset Failure | LV | 59 | 622 | 0.025341 | 0.0040734 | N
02/11/2016 | 12:40 | ZN72:PA25 | URBAN | Asset Failure | LV | 10 | 75 | 0.00051783 | 0.00069044 | N
03/11/2016 | 02:36 | ZN1850:PA9 | URBAN | Asset Failure | LV | 4 | 414 | 0.001143 | 0.00027609 | N
04/11/2016 | 18:15 | 807:74180 | SHORT RURAL | Asset Failure | LV | 1 | 195 | 0.00087746 | 0.00044998 | N
05/11/2016 | 16:02 | 813:89061 | LONG RURAL | Asset Failure | LV | 7 | 77 | 0.19264 | 0.24938 | N
05/11/2016 | 18:18 | ZN2635:PA38 | URBAN | Asset Failure | LV | 73 | 97 | 0.0048626 | 0.005039 | N
06/11/2016 | 05:42 | ZN2635:PA58 | URBAN | Asset Failure | LV | 23 | 568 | 0.0090178 | 0.0015876 | N
08/11/2016 | 13:25 | 264:81232 | URBAN | Asset Failure | LV | 20 | 99 | 0.0013725 | 0.0013806 | N
08/11/2016 | 21:01 | ZN36300:PA9 | URBAN | Asset Failure | LV | 97 | 88 | 0.0059247 | 0.0066958 | N
09/11/2016 | 15:20 | ZN2466:PA16 | URBAN | Asset Failure | LV | 2 | 110 | 0.00015187 | 0.00013806 | N
10/11/2016 | 18:55 | ZN8700:PA61 62KLM | CBD | Asset Failure | LV | 23 | 260 | 0.19272 | 0.074122 | N
11/11/2016 | 14:38 | ZN36800:PA33 | URBAN | Asset Failure | LV | 127 | 1,019 | 0.08934 | 0.0087671 | N
11/11/2016 | 15:21 | ZN3672:PA34 | URBAN | Asset Failure | LV | 11 | 259 | 0.0019667 | 0.00075936 | N
11/11/2016 | 17:21 | ZN9245:PA4 | SHORT RURAL | Asset Failure | LV | 26 | 179 | 0.020895 | 0.0117 | N
12/11/2016 | 14:47 | 528:83019 | SHORT RURAL | Asset Failure | LV | 21 | 382 | 0.03608 | 0.0094451 | N
13/11/2016 | 03:03 | ZN965:PA42 | URBAN | Asset Failure | LV | 71 | 71 | 0.0035025 | 0.0048998 | N
13/11/2016 | 18:43 | ZN7900:PA11 | URBAN | Asset Failure | LV | 86 | 157 | 0.009308 | 0.0059349 | N
13/11/2016 | 21:36 | ZN7900:PA11 | URBAN | Asset Failure | LV | 86 | 704 | 0.041782 | 0.0059349 | N
14/11/2016 | 06:15 | ZN36100:PA5 | URBAN | Asset Failure | LV | 1 | 464 | 0.00032049 | 6.9011e-05 | N
14/11/2016 | 18:57 | ZN15002:PA2 | URBAN | Asset Failure | LV | 180 | 63 | 0.0078258 | 0.012422 | N
15/11/2016 | 08:36 | 812:19072 | SHORT RURAL | Asset Failure | LV | 1 | 194 | 0.00087256 | 0.00044977 | N
15/11/2016 | 14:48 | ZN35900:PA25 | SHORT RURAL | Asset Failure | LV | 22 | 203 | 0.020087 | 0.009895 | N
16/11/2016 | 10:07 | 807:74184 | SHORT RURAL | Asset Failure | LV | 1 | 290 | 0.0013044 | 0.00044978 | N
16/11/2016 | 15:59 | ZN3425:PA43 | URBAN | Asset Failure | LV | 65 | 161 | 0.0072139 | 0.0044858 | N
16/11/2016 | 18:33 | ZN1193:PA28 | URBAN | Asset Failure | LV | 54 | 197 | 0.0073415 | 0.0037266 | N
16/11/2016 | 10:15 | 813:89055 | SHORT RURAL | Asset Failure | LV | 1 | 420 | 0.0018891 | 0.00044978 | N
17/11/2016 | 20:44 | ZN4545:PA41 | SHORT RURAL | Asset Failure | LV | 52 | 136 | 0.031764 | 0.023382 | N
15/11/2016 | 11:30 | ZN14892:PA10 | URBAN | Asset Failure | LV | 15 | 10 | 0.00010352 | 0.0010352 | N
18/11/2016 | 18:25 | 217:33611 | URBAN | Asset Failure | LV | 14 | 334 | 0.0032236 | 0.00096587 | N
18/11/2016 | 23:36 | ZN4545:PA17 | URBAN | Asset Failure | LV | 2 | 39 | 5.3813e-05 | 0.00013798 | N
22/11/2016 | 18:16 | 224:80340 | SHORT RURAL | Asset Failure | LV | 61 | 84 | 0.02304 | 0.027429 | N
22/11/2016 | 17:49 | ZN690:PA4 | URBAN | Asset Failure | LV | 1 | 332 | 0.00022926 | 6.8996e-05 | N
22/11/2016 | 18:49 | ZN9037:PA2 | URBAN | Asset Failure | LV | 36 | 101 | 0.0025087 | 0.0024839 | N
22/11/2016 | 19:47 | ZN9037:PA2 | URBAN | Asset Failure | LV | 21 | 823 | 0.011919 | 0.0014489 | N
23/11/2016 | 20:15 | ZN180:PA19 | URBAN | Asset Failure | LV | 97 | 285 | 0.019074 | 0.0066928 | N
23/11/2016 | 20:15 | ZN180:PA21 | URBAN | Asset Failure | LV | 39 | 35 | 0.00094182 | 0.0026909 | N
23/11/2016 | 20:50 | ZN180:PA21 | URBAN | Asset Failure | LV | 114 | 270 | 0.021237 | 0.0078657 | N
24/11/2016 | 07:57 | ZN8100:PA4 | URBAN | Asset Failure | LV | 2 | 92 | 0.00012738 | 0.00013796 | N
25/11/2016 | 16:49 | ZN35500:PA24 | URBAN | Asset Failure | LV | 1 | 325 | 0.00022445 | 6.8978e-05 | N
25/11/2016 | 19:10 | ZN4545:PA36 | URBAN | Asset Failure | LV | 1 | 408 | 0.0002815 | 6.8978e-05 | N
25/11/2016 | 22:25 | ZN4545:PA36 | URBAN | Asset Failure | LV | 59 | 50 | 0.0020294 | 0.0040697 | N
27/11/2016 | 08:44 | ZN4545:PA28 | URBAN | Asset Failure | LV | 134 | 226 | 0.020883 | 0.0092498 | N
27/11/2016 | 08:50 | ZN180:PA35 | URBAN | Asset Failure | LV | 1 | 144 | 9.9527e-05 | 6.9028e-05 | N
27/11/2016 | 21:20 | 810:74062 | SHORT RURAL | Asset Failure | LV | 3 | 25 | 0.00033709 | 0.0013484 | N
28/11/2016 | 11:32 | ZN2835:PA15 | URBAN | Asset Failure | LV | 44 | 68 | 0.0020506 | 0.0030372 | N
28/11/2016 | 11:43 | ZN2835:PA15 | URBAN | Asset Failure | LV | 1 | 57 | 3.9082e-05 | 6.9028e-05 | N
28/11/2016 | 12:30 | 203:8085 | URBAN | Asset Failure | LV | 46 | 180 | 0.0057108 | 0.0031753 | N
29/11/2016 | 07:38 | ZN15009:PA5 | URBAN | Asset Failure | LV | 124 | 156 | 0.013384 | 0.0085595 | N
29/11/2016 | 08:06 | ZN711:PA31 | URBAN | Asset Failure | LV | 3 | 240 | 0.000497 | 0.00020709 | N
29/11/2016 | 17:25 | ZN1285:PA27 | URBAN | Asset Failure | LV | 14 | 380 | 0.0036688 | 0.0009664 | N
30/11/2016 | 00:39 | ZN4545:PA31 | URBAN | Asset Failure | LV | 71 | 651 | 0.031906 | 0.004901 | N
30/11/2016 | 16:36 | ZN1673:PA1 | URBAN | Asset Failure | LV | 16 | 504 | 0.0055665 | 0.0011045 | N
30/11/2016 | 16:36 | ZN1673:PA7 | URBAN | Asset Failure | LV | 32 | 323 | 0.0071436 | 0.0022089 | N
01/12/2016 | 11:19 | ZN15013:PA10 | SHORT RURAL | Asset Failure | LV | 28 | 71 | 0.0089314 | 0.012579 | N
01/12/2016 | 13:57 | ZN10995:PA12 | URBAN | Asset Failure | LV | 65 | 243 | 0.010883 | 0.0044856 | N
02/12/2016 | 10:04 | 232:11457 | SHORT RURAL | Asset Failure | LV | 29 | 156 | 0.020325 | 0.013029 | N
02/12/2016 | 11:57 | 508:82579 | SHORT RURAL | Asset Failure | LV | 2 | 146 | 0.0013119 | 0.00089853 | N
02/12/2016 | 14:45 | ZN12640:PA7 | URBAN | Asset Failure | LV | 17 | 258 | 0.0030267 | 0.0011731 | N
02/12/2016 | 15:35 | ZN72:PA31 | URBAN | Asset Failure | LV | 1 | 154 | 0.00010656 | 6.9009e-05 | N
02/12/2016 | 17:15 | 232:33413 | URBAN | Asset Failure | LV | 2 | 95 | 0.00013112 | 0.00013802 | N
02/12/2016 | 22:37 | ZN13000:PA11 | SHORT RURAL | Asset Failure | LV | 2 | 88 | 0.00079071 | 0.00089853 | N
03/12/2016 | 07:01 | ZN12630:PA8 | SHORT RURAL | Asset Failure | LV | 8 | 189 | 0.006793 | 0.0035942 | N
04/12/2016 | 05:33 | ZN15006:PA8 | URBAN | Asset Failure | LV | 41 | 207 | 0.0058526 | 0.0028273 | N
05/12/2016 | 12:37 | ZN398:PA16 | URBAN | Asset Failure | LV | 80 | 93 | 0.0051306 | 0.0055167 | N
05/12/2016 | 12:37 | ZN398:PA20 | URBAN | Asset Failure | LV | 249 | 93 | 0.015969 | 0.017171 | N
05/12/2016 | 15:13 | 813:89055 | SHORT RURAL | Asset Failure | LV | 7 | 302 | 0.0094976 | 0.0031449 | N
05/12/2016 | 20:30 | ZN15004:PA9 | URBAN | Asset Failure | LV | 114 | 34 | 0.0026825 | 0.0078613 | N
05/12/2016 | 17:01 | ZN15014:PA12 | SHORT RURAL | Asset Failure | LV | 56 | 419 | 0.10532 | 0.025159 | N
06/12/2016 | 09:10 | 524:33578 | URBAN | Asset Failure | LV | 11 | 289 | 0.0021939 | 0.00075857 | N
06/12/2016 | 20:55 | ZN874:PA22 | URBAN | Asset Failure | LV | 59 | 80 | 0.003255 | 0.0040687 | N
07/12/2016 | 13:03 | ZN36800:PA32 | URBAN | Asset Failure | LV | 83 | 2,102 | 0.1203 | 0.0057238 | N
07/12/2016 | 23:15 | ZN10993:PA27 | URBAN | Asset Failure | LV | 77 | 1,200 | 0.063721 | 0.0053101 | N
08/12/2016 | 01:00 | ZN9252:PA28 | URBAN | Asset Failure | LV | 36 | 90 | 0.002224 | 0.0024817 | N
07/12/2016 | 13:40 | 814:82285 | SHORT RURAL | Asset Failure | LV | 2 | 105 | 0.00094349 | 0.00089856 | N
08/12/2016 | 12:40 | ZN15013:PA1 | URBAN | Asset Failure | LV | 5 | 250 | 0.00086169 | 0.00034468 | N
08/12/2016 | 19:14 | ZN1287:PA17 | URBAN | Asset Failure | LV | 45 | 146 | 0.0045264 | 0.0031021 | N
10/12/2016 | 23:00 | ZN36100:PA2 | URBAN | Asset Failure | LV | 28 | 825 | 0.015925 | 0.0019303 | N
11/12/2016 | 05:45 | ZN901:PA20 | URBAN | Asset Failure | LV | 84 | 209 | 0.012117 | 0.0057911 | N
11/12/2016 | 07:27 | ZN2400:PA21 | URBAN | Asset Failure | LV | 55 | 123 | 0.0046639 | 0.0037918 | N
11/12/2016 | 09:38 | ZN901:PA20 | URBAN | Asset Failure | LV | 105 | 1,057 | 0.076515 | 0.0072389 | N
12/12/2016 | 07:05 | ZN5868:PA25 | URBAN | Asset Failure | LV | 8 | 190 | 0.0010475 | 0.00055153 | N
13/12/2016 | 06:39 | ZN263:PA31 32KLM | CBD | Asset Failure | LV | 26 | 896 | 0.75006 | 0.083712 | N
13/12/2016 | 12:46 | ZN398:PA11 | URBAN | Asset Failure | LV | 6 | 843 | 0.0034857 | 0.00041365 | N
13/12/2016 | 19:09 | 206:34438 | URBAN | Asset Failure | LV | 51 | 155 | 0.0054505 | 0.003516 | N
13/12/2016 | 19:11 | ZN180:PA21 | URBAN | Asset Failure | LV | 30 | 419 | 0.008666 | 0.0020683 | N
13/12/2016 | 20:21 | ZN2835:PA31 | URBAN | Asset Failure | LV | 54 | 279 | 0.010373 | 0.0037229 | N
14/12/2016 | 08:26 | ZN10997:PA2 | URBAN | Asset Failure | LV | 103 | 147 | 0.010469 | 0.0071011 | N
14/12/2016 | 14:14 | ZN12650:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 349 | 0.0015677 | 0.00044936 | N
15/12/2016 | 22:33 | ZN72:PA31 | URBAN | Asset Failure | LV | 43 | 207 | 0.006134 | 0.0029637 | N
16/12/2016 | 11:16 | ZN15014:PA18 | URBAN | Asset Failure | LV | 1 | 161 | 0.00011098 | 6.8926e-05 | N
16/12/2016 | 15:15 | ZN630:PA40 | URBAN | Asset Failure | LV | 19 | 304 | 0.0039875 | 0.0013096 | N
16/12/2016 | 23:28 | ZN690:PA34 | URBAN | Asset Failure | LV | 91 | 242 | 0.015179 | 0.0062722 | N
17/12/2016 | 08:15 | ZN3154:PA23 | URBAN | Asset Failure | LV | 48 | 114 | 0.0037744 | 0.0033085 | N
17/12/2016 | 10:11 | ZN3155:PA18 | URBAN | Asset Failure | LV | 36 | 1,779 | 0.044143 | 0.0024814 | N
17/12/2016 | 14:19 | ZN1287:PA23 | URBAN | Asset Failure | LV | 78 | 220 | 0.011847 | 0.0053763 | N
17/12/2016 | 15:04 | ZN2310:PA67 | URBAN | Asset Failure | LV | 49 | 140 | 0.0047419 | 0.0033774 | N
17/12/2016 | 19:06 | ZN12650:PA1 | SHORT RURAL | Asset Failure | LV | 5 | 329 | 0.0073875 | 0.0022454 | N
18/12/2016 | 11:41 | ZN3472:PA34 | URBAN | Asset Failure | LV | 4 | 289 | 0.00079679 | 0.00027571 | N
18/12/2016 | 14:04 | ZN180:PA27 | URBAN | Asset Failure | LV | 47 | 161 | 0.0052157 | 0.0032395 | N
19/12/2016 | 17:42 | ZN2196:PA21 | URBAN | Asset Failure | LV | 88 | 145 | 0.0088113 | 0.0060656 | N
19/12/2016 | 20:54 | ZN4545:PA32 | URBAN | Asset Failure | LV | 20 | 240 | 0.0033085 | 0.0013785 | N
20/12/2016 | 07:54 | 238:34143 | URBAN | Asset Failure | LV | 34 | 420 | 0.0098464 | 0.0023435 | N
20/12/2016 | 12:48 | ZN72:PA15 | URBAN | Asset Failure | LV | 31 | 131 | 0.0027991 | 0.0021368 | N
21/12/2016 | 04:19 | ZN10999:PA12 | URBAN | Asset Failure | LV | 66 | 223 | 0.010124 | 0.0045492 | N
19/12/2016 | 00:56 | ZN180:PA27 | URBAN | Asset Failure | LV | 47 | 559 | 0.018109 | 0.0032396 | N
21/12/2016 | 22:34 | ZN9900:PA12 | URBAN | Asset Failure | LV | 55 | 596 | 0.022595 | 0.003791 | N
23/12/2016 | 06:06 | ZN180:PA30 | URBAN | Asset Failure | LV | 36 | 125 | 0.0031009 | 0.0024807 | N
23/12/2016 | 17:40 | 217:33612 | URBAN | Asset Failure | LV | 29 | 125 | 0.0024906 | 0.0019983 | N
24/12/2016 | 18:09 | 502:48010 | SHORT RURAL | Asset Failure | LV | 22 | 344 | 0.033978 | 0.0098774 | N
25/12/2016 | 05:30 | ZN2310:PA60 | URBAN | Asset Failure | LV | 27 | 190 | 0.0035279 | 0.0018605 | N
25/12/2016 | 11:24 | 227:13020 | SHORT RURAL | Asset Failure | LV | 45 | 225 | 0.045489 | 0.020204 | N
25/12/2016 | 22:45 | ZN187:PA30 | URBAN | Asset Failure | LV | 63 | 80 | 0.0034622 | 0.0043413 | N
26/12/2016 | 14:39 | ZN12600:PA9 | SHORT RURAL | Asset Failure | LV | 4 | 119 | 0.0021281 | 0.0017959 | N
27/12/2016 | 02:44 | ZN12640:PA6 | URBAN | Asset Failure | LV | 103 | 241 | 0.017105 | 0.0070976 | N
27/12/2016 | 21:12 | ZN2568:PA19 | URBAN | Asset Failure | LV | 1 | 138 | 9.4865e-05 | 6.8909e-05 | N
28/12/2016 | 12:40 | ZN965:PA38 | URBAN | Asset Failure | LV | 14 | 380 | 0.003664 | 0.00096473 | N
28/12/2016 | 19:28 | ZN3154:PA17 | URBAN | Asset Failure | LV | 35 | 34 | 0.00081881 | 0.0024118 | N
28/12/2016 | 21:14 | ZN4545:PA19 | URBAN | Asset Failure | LV | 51 | 226 | 0.0079389 | 0.0035144 | N
29/12/2016 | 00:05 | ZN36800:PA33 | URBAN | Asset Failure | LV | 1 | 624 | 0.00043006 | 6.891e-05 | N
29/12/2016 | 06:05 | ZN15002:PA8 | URBAN | Asset Failure | LV | 29 | 389 | 0.0077777 | 0.0019984 | N
29/12/2016 | 09:08 | ZN12570:PA26 | URBAN | Asset Failure | LV | 2 | 112 | 0.00015417 | 0.00013782 | N
29/12/2016 | 13:55 | ZN35500:PA34 | URBAN | Asset Failure | LV | 57 | 184 | 0.0072423 | 0.0039278 | N
29/12/2016 | 13:59 | 511:29872 | URBAN | Asset Failure | LV | 3 | 321 | 0.00066405 | 0.00020673 | N
29/12/2016 | 19:34 | 512:48049 | SHORT RURAL | Asset Failure | LV | 2 | 146 | 0.001311 | 0.00089795 | N
29/12/2016 | 21:45 | 511:29872 | URBAN | Asset Failure | LV | 3 | 115 | 0.00023774 | 0.00020673 | N
29/12/2016 | 22:15 | ZN10996:PA8 | URBAN | Asset Failure | LV | 43 | 180 | 0.0053336 | 0.0029631 | N
30/12/2016 | 12:26 | ZN3155:PA22 | URBAN | Asset Failure | LV | 23 | 1,879 | 0.029775 | 0.0015849 | N
30/12/2016 | 15:29 | 264:81244 | SHORT RURAL | Asset Failure | LV | 1 | 247 | 0.001109 | 0.00044898 | N
30/12/2016 | 17:50 | ZN2310:PA53 | URBAN | Asset Failure | LV | 36 | 45 | 0.0011163 | 0.0024808 | N
30/12/2016 | 18:03 | ZN9900:PA21 | URBAN | Asset Failure | LV | 41 | 157 | 0.0044329 | 0.0028253 | N
01/01/2017 | 11:09 | 203:8085 | URBAN | Asset Failure | LV | 26 | 50 | 0.00089614 | 0.0017917 | N
30/12/2016 | 20:50 | ZN2310:PA53 | URBAN | Asset Failure | LV | 36 | 138 | 0.0034235 | 0.0024808 | N
03/01/2017 | 17:10 | ZN15006:PA16 | URBAN | Asset Failure | LV | 85 | 365 | 0.02138 | 0.0058574 | N
03/01/2017 | 07:24 | ZN2602:PA36 | URBAN | Asset Failure | LV | 72 | 83 | 0.0041112 | 0.0049616 | N
04/01/2017 | 20:00 | ZN9245:PA1 | URBAN | Asset Failure | LV | 17 | 150 | 0.0017537 | 0.0011715 | N
04/01/2017 | 08:15 | ZN36800:PA33 | URBAN | Asset Failure | LV | 104 | 55 | 0.0039114 | 0.0071668 | N
06/01/2017 | 19:40 | 242:81541 | URBAN | Asset Failure | LV | 99 | 324 | 0.022122 | 0.0068225 | N
07/01/2017 | 05:35 | ZN9900:PA21 | URBAN | Asset Failure | LV | 41 | 798 | 0.022545 | 0.0028246 | N
07/01/2017 | 14:10 | ZN9700:PA17 | URBAN | Asset Failure | LV | 9 | 49 | 0.00030444 | 0.00062004 | N
07/01/2017 | 20:24 | ZN4545:PA9 | URBAN | Asset Failure | LV | 4 | 696 | 0.001918 | 0.00027557 | N
08/01/2017 | 15:38 | ZN3472:PA20 | URBAN | Asset Failure | LV | 37 | 190 | 0.0048431 | 0.002549 | N
09/01/2017 | 20:31 | ZN2635:PA35 | URBAN | Asset Failure | LV | 26 | 279 | 0.0049975 | 0.0017912 | N
09/01/2017 | 20:31 | ZN2635:PA44 | URBAN | Asset Failure | LV | 68 | 278 | 0.013046 | 0.0046847 | N
09/01/2017 | 20:33 | ZN1648:PA16 | URBAN | Asset Failure | LV | 32 | 293 | 0.0064649 | 0.0022046 | N
10/01/2017 | 00:45 | ZN2635:PA44 | URBAN | Asset Failure | LV | 1 | 41 | 2.8258e-05 | 6.8893e-05 | N
10/01/2017 | 11:57 | ZN342:PA35 | URBAN | Asset Failure | LV | 145 | 92 | 0.0091937 | 0.0099895 | N
10/01/2017 | 18:48 | 814:82285 | SHORT RURAL | Asset Failure | LV | 3 | 192 | 0.0025852 | 0.0013464 | N
10/01/2017 | 19:29 | ZN15005:PA6 | URBAN | Asset Failure | LV | 38 | 310 | 0.00812 | 0.0026179 | N
11/01/2017 | 08:42 | ZN12570:PA26 | URBAN | Asset Failure | LV | 1 | 77 | 5.3244e-05 | 6.8894e-05 | N
11/01/2017 | 08:45 | ZN263:PA31 32DEF | CBD | Asset Failure | LV | 27 | 140 | 0.12166 | 0.086901 | N
11/01/2017 | 09:01 | ZN15011:PA4 | URBAN | Asset Failure | LV | 1 | 118 | 8.1559e-05 | 6.8894e-05 | N
11/01/2017 | 18:00 | ZN1193:PA21 | URBAN | Asset Failure | LV | 79 | 45 | 0.0024386 | 0.0054426 | N
11/01/2017 | 15:10 | ZN12600:PA11 | URBAN | Asset Failure | LV | 21 | 190 | 0.0027489 | 0.0014468 | N
11/01/2017 | 17:25 | ZN12640:PA18 | SHORT RURAL | Asset Failure | LV | 59 | 244 | 0.064709 | 0.02648 | N
11/01/2017 | 17:58 | ZN4545:PA40 | URBAN | Asset Failure | LV | 38 | 62 | 0.0016162 | 0.002618 | N
11/01/2017 | 17:56 | ZN15005:PA6 | URBAN | Asset Failure | LV | 38 | 281 | 0.0073565 | 0.002618 | N
12/01/2017 | 07:02 | ZN4990:PA55 56DEF | CBD | Asset Failure | LV | 113 | 58 | 0.21088 | 0.36359 | N
12/01/2017 | 08:10 | ZN188:PA9 | URBAN | Asset Failure | LV | 6 | 1,145 | 0.0047319 | 0.00041331 | N
12/01/2017 | 09:43 | ZN10999:PA7 | URBAN | Asset Failure | LV | 86 | 172 | 0.010169 | 0.0059241 | N
12/01/2017 | 10:08 | 812:19072 | SHORT RURAL | Asset Failure | LV | 3 | 152 | 0.0020468 | 0.0013466 | N
12/01/2017 | 15:23 | 814:82289 | SHORT RURAL | Asset Failure | LV | 1 | 210 | 0.00094476 | 0.00044885 | N
12/01/2017 | 16:03 | 811:74234 | SHORT RURAL | Asset Failure | LV | 1 | 147 | 0.00065944 | 0.00044885 | N
12/01/2017 | 20:45 | 812:19072 | SHORT RURAL | Asset Failure | LV | 1 | 130 | 0.0005853 | 0.00044885 | N
13/01/2017 | 14:27 | ZN9245:PA15 | URBAN | Asset Failure | LV | 26 | 143 | 0.0025612 | 0.001791 | N
13/01/2017 | 20:48 | ZN965:PA15 | URBAN | Asset Failure | LV | 34 | 842 | 0.019721 | 0.0023421 | N
13/01/2017 | 22:10 | ZN10990:PA2 | URBAN | Asset Failure | LV | 58 | 95 | 0.003777 | 0.0039954 | N
14/01/2017 | 15:44 | ZN12600:PA11 | URBAN | Asset Failure | LV | 61 | 196 | 0.008225 | 0.004202 | N
15/01/2017 | 10:06 | ZN965:PA38 | URBAN | Asset Failure | LV | 45 | 894 | 0.027705 | 0.0030999 | N
15/01/2017 | 21:04 | ZN129:PA5 | URBAN | Asset Failure | LV | 40 | 36 | 0.00098461 | 0.0027554 | N
16/01/2017 | 01:16 | ZN36300:PA19 | URBAN | Asset Failure | LV | 47 | 182 | 0.0058925 | 0.0032376 | N
16/01/2017 | 16:23 | ZN15014:PA12 | SHORT RURAL | Asset Failure | LV | 1 | 147 | 0.00066108 | 0.00044885 | N
16/01/2017 | 19:49 | ZN2466:PA15 | URBAN | Asset Failure | LV | 22 | 855 | 0.01296 | 0.0015155 | N
17/01/2017 | 04:44 | ZN129:PA5 | URBAN | Asset Failure | LV | 40 | 220 | 0.0060698 | 0.0027555 | N
17/01/2017 | 09:03 | ZN15014:PA22 | URBAN | Asset Failure | LV | 61 | 285 | 0.011989 | 0.0042021 | N
17/01/2017 | 09:29 | 516:48067 | SHORT RURAL | Asset Failure | LV | 1 | 202 | 0.00090548 | 0.00044885 | N
17/01/2017 | 10:37 | ZN129:PA5 | URBAN | Asset Failure | LV | 40 | 1,883 | 0.051885 | 0.0027555 | N
17/01/2017 | 12:44 | ZN4545:PA17 | URBAN | Asset Failure | LV | 48 | 436 | 0.014417 | 0.0033066 | N
17/01/2017 | 12:44 | ZN4545:PA19 | URBAN | Asset Failure | LV | 117 | 436 | 0.035118 | 0.0080597 | N
17/01/2017 | 13:00 | ZN965:PA38 | URBAN | Asset Failure | LV | 58 | 741 | 0.029618 | 0.0039954 | N
17/01/2017 | 14:43 | ZN2635:PA31 | URBAN | Asset Failure | LV | 46 | 137 | 0.0043412 | 0.0031688 | N
17/01/2017 | 14:43 | ZN2635:PA43 | URBAN | Asset Failure | LV | 31 | 227 | 0.0048475 | 0.0021355 | N
17/01/2017 | 14:43 | ZN2635:PA57 | URBAN | Asset Failure | LV | 194 | 252 | 0.033677 | 0.013364 | N
17/01/2017 | 16:28 | ZN129:PA16 | URBAN | Asset Failure | LV | 143 | 472 | 0.046496 | 0.0098508 | N
17/01/2017 | 16:28 | ZN129:PA8 | URBAN | Asset Failure | LV | 66 | 472 | 0.021449 | 0.0045465 | N
17/01/2017 | 17:43 | ZN1287:PA15 | URBAN | Asset Failure | LV | 45 | 597 | 0.018498 | 0.0030999 | N
17/01/2017 | 18:54 | 225:33676 | URBAN | Asset Failure | LV | 70 | 56 | 0.0026955 | 0.0048221 | N
17/01/2017 | 20:23 | ZN15002:PA6 | URBAN | Asset Failure | LV | 41 | 119 | 0.0033492 | 0.0028243 | N
18/01/2017 | 01:41 | ZN965:PA38 | URBAN | Asset Failure | LV | 57 | 754 | 0.029594 | 0.0039266 | N
18/01/2017 | 05:54 | ZN187:PA30 | URBAN | Asset Failure | LV | 42 | 76 | 0.0021989 | 0.0028933 | N
18/01/2017 | 10:01 | ZN12600:PA11 | URBAN | Asset Failure | LV | 30 | 631 | 0.01304 | 0.0020666 | N
18/01/2017 | 11:03 | 214:8669 | URBAN | Asset Failure | LV | 37 | 37 | 0.00094306 | 0.0025488 | N
18/01/2017 | 11:44 | ZN12570:PA35 | URBAN | Asset Failure | LV | 25 | 197 | 0.0033927 | 0.0017222 | N
18/01/2017 | 17:22 | 801:74121 | LONG RURAL | Asset Failure | LV | 4 | 118 | 0.16815 | 0.1425 | N
19/01/2017 | 03:06 | 232:11454 | SHORT RURAL | Asset Failure | LV | 137 | 314 | 0.19308 | 0.061489 | N
19/01/2017 | 13:04 | ZN3155:PA19 | URBAN | Asset Failure | LV | 1 | 506 | 0.00034825 | 6.8881e-05 | N
17/01/2017 | 07:35 | ZN2466:PA20 | URBAN | Asset Failure | LV | 1 | 550 | 0.00037888 | 6.8887e-05 | N
19/01/2017 | 23:03 | ZN12600:PA3 | URBAN | Asset Failure | LV | 20 | 761 | 0.010486 | 0.0013776 | N
20/01/2017 | 10:22 | 511:29876 | SHORT RURAL | Asset Failure | LV | 18 | 597 | 0.04823 | 0.0080787 | N
20/01/2017 | 12:15 | ZN72:PA26 | URBAN | Asset Failure | LV | 18 | 480 | 0.0059514 | 0.0012399 | N
20/01/2017 | 19:26 | 508:82574 | SHORT RURAL | Asset Failure | LV | 4 | 179 | 0.0032135 | 0.0017953 | N
21/01/2017 | 00:33 | 224:80346 | URBAN | Asset Failure | LV | 9 | 67 | 0.00041536 | 0.00061994 | N
22/01/2017 | 09:43 | ZN931:PA9 | URBAN | Asset Failure | LV | 86 | 56 | 0.003345 | 0.0059239 | N
21/01/2017 | 06:30 | 232:11454 | SHORT RURAL | Asset Failure | LV | 1 | 65 | 0.00029173 | 0.00044881 | N
23/01/2017 | 11:35 | 801:74121 | LONG RURAL | Asset Failure | LV | 1 | 268 | 0.095539 | 0.035638 | N
20/01/2017 | 21:52 | ZN10990:PA1 | URBAN | Asset Failure | LV | 51 | 102 | 0.0035833 | 0.003513 | N
23/01/2017 | 19:52 | ZN80:PA37 | URBAN | Asset Failure | LV | 24 | 193 | 0.00319 | 0.0016532 | N
24/01/2017 | 06:52 | 520:48172 | SHORT RURAL | Asset Failure | LV | 1 | 144 | 0.00064637 | 0.00044887 | N
22/01/2017 | 12:29 | ZN931:PA9 | URBAN | Asset Failure | LV | 86 | 1,091 | 0.06463 | 0.0059239 | N
24/01/2017 | 12:59 | ZN8000:PA4 | URBAN | Asset Failure | LV | 16 | 116 | 0.0012785 | 0.0011021 | N
24/01/2017 | 15:15 | ZN36800:PA58 | URBAN | Asset Failure | LV | 121 | 44 | 0.0037029 | 0.0083349 | N
24/01/2017 | 16:10 | ZN2635:PA43 | URBAN | Asset Failure | LV | 69 | 60 | 0.0028518 | 0.004753 | N
24/01/2017 | 18:01 | ZN2602:PA42 | URBAN | Asset Failure | LV | 31 | 264 | 0.0056374 | 0.0021354 | N
25/01/2017 | 00:45 | ZN36100:PA27 | URBAN | Asset Failure | LV | 23 | 120 | 0.0019012 | 0.0015844 | N
25/01/2017 | 08:30 | 213:33775 | URBAN | Asset Failure | LV | 61 | 152 | 0.006387 | 0.004202 | N
20/01/2017 | 09:40 | ZN14891:PA8 | SHORT RURAL | Asset Failure | LV | 6 | 120 | 0.0032315 | 0.0026929 | N
25/01/2017 | 15:52 | 502:48008 | URBAN | Asset Failure | LV | 43 | 33 | 0.00096316 | 0.0029621 | N
25/01/2017 | 17:06 | ZN36800:PA40 | URBAN | Asset Failure | LV | 103 | 94 | 0.006647 | 0.0070951 | N
26/01/2017 | 12:47 | 512:48049 | SHORT RURAL | Asset Failure | LV | 3 | 108 | 0.0014524 | 0.0013448 | N
27/01/2017 | 12:56 | ZN80:PA22 | URBAN | Asset Failure | LV | 1 | 304 | 0.00020938 | 6.8874e-05 | N
27/01/2017 | 12:56 | ZN80:PA31 | URBAN | Asset Failure | LV | 31 | 124 | 0.0026475 | 0.0021351 | N
29/01/2017 | 01:28 | ZN12600:PA3 | URBAN | Asset Failure | LV | 1 | 519 | 0.00035755 | 6.8875e-05 | N
29/01/2017 | 22:09 | ZN3922:PA18 | URBAN | Asset Failure | LV | 29 | 449 | 0.0089682 | 0.0019974 | N
30/01/2017 | 06:55 | ZN9550:PA9 | URBAN | Asset Failure | LV | 34 | 154 | 0.0036086 | 0.0023418 | N
30/01/2017 | 12:32 | ZN10999:PA11 | URBAN | Asset Failure | LV | 99 | 118 | 0.008046 | 0.0068186 | N
30/01/2017 | 14:07 | ZN4545:PA39 | URBAN | Asset Failure | LV | 9 | 83 | 0.0005145 | 0.00061988 | N
28/01/2017 | 02:28 | ZN1285:PA10 | URBAN | Asset Failure | LV | 22 | 277 | 0.0041972 | 0.0015153 | N
30/01/2017 | 14:52 | ZN1673:PA7 | URBAN | Asset Failure | LV | 22 | 92 | 0.0013948 | 0.0015153 | N
30/01/2017 | 18:54 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 189 | 0.067439 | 0.035638 | N
30/01/2017 | 19:15 | 523:33507 | URBAN | Asset Failure | LV | 1 | 60 | 4.1245e-05 | 6.8875e-05 | N
30/01/2017 | 20:42 | ZN2568:PA29 | URBAN | Asset Failure | LV | 84 | 128 | 0.0073997 | 0.0057855 | N
30/01/2017 | 22:23 | ZN10994:PA11 | URBAN | Asset Failure | LV | 59 | 76 | 0.0030978 | 0.0040636 | N
31/01/2017 | 08:08 | ZN384:PA22 | URBAN | Asset Failure | LV | 143 | 22 | 0.0021652 | 0.0098493 | N
31/01/2017 | 11:07 | ZN35800:PA16 | URBAN | Asset Failure | LV | 4 | 68 | 0.00018734 | 0.0002755 | N
31/01/2017 | 11:07 | ZN35800:PA7 | URBAN | Asset Failure | LV | 64 | 67 | 0.0029571 | 0.0044081 | N
31/01/2017 | 12:33 | ZN180:PA32 | URBAN | Asset Failure | LV | 21 | 312 | 0.0045128 | 0.0014464 | N
31/01/2017 | 12:00 | ZN10994:PA1 | URBAN | Asset Failure | LV | 1 | 150 | 0.00010325 | 6.8876e-05 | N
31/01/2017 | 12:11 | 232:11455 | SHORT RURAL | Asset Failure | LV | 11 | 153 | 0.0075566 | 0.0049309 | N
31/01/2017 | 15:41 | 232:11457 | SHORT RURAL | Asset Failure | LV | 150 | 59 | 0.039671 | 0.067239 | N
31/01/2017 | 17:24 | 515:35198 | SHORT RURAL | Asset Failure | LV | 4 | 71 | 0.0012731 | 0.001793 | N
31/01/2017 | 18:40 | 813:89061 | LONG RURAL | Asset Failure | LV | 1 | 433 | 0.15428 | 0.035638 | N
31/01/2017 | 18:55 | 814:82283 | SHORT RURAL | Asset Failure | LV | 1 | 176 | 0.00078984 | 0.00044826 | N
31/01/2017 | 19:09 | 516:48067 | SHORT RURAL | Asset Failure | LV | 12 | 96 | 0.005164 | 0.0053791 | N
01/02/2017 | 12:09 | 523:33505 | URBAN | Asset Failure | LV | 1 | 170 | 0.0001174 | 6.8877e-05 | N
01/02/2017 | 19:00 | ZN14891:PA8 | SHORT RURAL | Asset Failure | LV | 46 | 85 | 0.017527 | 0.02062 | N
02/02/2017 | 08:45 | ZN10999:PA22 | URBAN | Asset Failure | LV | 1 | 75 | 5.1649e-05 | 6.8866e-05 | N
02/02/2017 | 08:45 | ZN10999:PA7 | URBAN | Asset Failure | LV | 86 | 74 | 0.0043955 | 0.0059225 | N
02/02/2017 | 11:23 | ZN35800:PA16 | URBAN | Asset Failure | LV | 14 | 157 | 0.0015137 | 0.00096412 | N
03/02/2017 | 16:20 | ZN187:PA10 | URBAN | Asset Failure | LV | 12 | 90 | 0.00074101 | 0.00082641 | N
03/02/2017 | 19:06 | ZN187:PA10 | URBAN | Asset Failure | LV | 12 | 74 | 0.00061099 | 0.00082641 | N
04/02/2017 | 00:09 | ZN187:PA10 | URBAN | Asset Failure | LV | 12 | 96 | 0.00079337 | 0.00082643 | N
04/02/2017 | 13:35 | 217:33610 | URBAN | Asset Failure | LV | 74 | 149 | 0.0075952 | 0.0050963 | N
04/02/2017 | 21:24 | ZN10999:PA29 | URBAN | Asset Failure | LV | 37 | 215 | 0.005487 | 0.0025482 | N
04/02/2017 | 21:27 | 227:13020 | SHORT RURAL | Asset Failure | LV | 42 | 899 | 0.16918 | 0.018824 | N
05/02/2017 | 18:45 | ZN15005:PA12 | URBAN | Asset Failure | LV | 83 | 195 | 0.011147 | 0.0057165 | N
05/02/2017 | 17:30 | ZN14892:PA16 | URBAN | Asset Failure | LV | 80 | 149 | 0.008207 | 0.0055099 | N
05/02/2017 | 18:24 | ZN1285:PA24 | URBAN | Asset Failure | LV | 130 | 866 | 0.077512 | 0.0089536 | N
05/02/2017 | 18:24 | ZN1285:PA33 | URBAN | Asset Failure | LV | 2 | 866 | 0.0011929 | 0.00013775 | N
05/02/2017 | 20:30 | ZN1285:PA33 | URBAN | Asset Failure | LV | 53 | 885 | 0.032289 | 0.0036503 | N
05/02/2017 | 21:10 | ZN1285:PA31 | URBAN | Asset Failure | LV | 78 | 565 | 0.030332 | 0.0053721 | N
05/02/2017 | 22:54 | ZN4545:PA19 | URBAN | Asset Failure | LV | 69 | 164 | 0.0077876 | 0.0047523 | N
06/02/2017 | 08:15 | 221:11893 | URBAN | Asset Failure | LV | 11 | 944 | 0.0071489 | 0.00075761 | N
05/02/2017 | 18:24 | ZN1285:PA24 | URBAN | Asset Failure | LV | 103 | 981 | 0.069592 | 0.007094 | N
05/02/2017 | 18:24 | ZN1285:PA33 | URBAN | Asset Failure | LV | 41 | 981 | 0.027702 | 0.0028238 | N
05/02/2017 | 18:24 | ZN1285:PA8 | URBAN | Asset Failure | LV | 1 | 981 | 0.00067565 | 6.8873e-05 | N
06/02/2017 | 14:28 | ZN9118:PA20 | URBAN | Asset Failure | LV | 49 | 231 | 0.0077997 | 0.0033748 | N
07/02/2017 | 04:12 | ZN187:PA10 | URBAN | Asset Failure | LV | 20 | 618 | 0.0085105 | 0.0013775 | N
07/02/2017 | 06:49 | ZN180:PA10 | URBAN | Asset Failure | LV | 7 | 301 | 0.0014511 | 0.00048212 | N
07/02/2017 | 11:04 | ZN7900:PA11 | URBAN | Asset Failure | LV | 30 | 456 | 0.0094138 | 0.0020662 | N
07/02/2017 | 12:06 | ZN167:PA20 | URBAN | Asset Failure | LV | 1 | 204 | 0.00014046 | 6.8875e-05 | N
07/02/2017 | 18:30 | ZN14144:PA4 | URBAN | Asset Failure | LV | 83 | 87 | 0.0049858 | 0.0057166 | N
07/02/2017 | 19:29 | ZN1850:PA4 | URBAN | Asset Failure | LV | 33 | 110 | 0.0025055 | 0.0022729 | N
07/02/2017 | 09:55 | 221:11893 | URBAN | Asset Failure | LV | 11 | 60 | 0.00045457 | 0.00075762 | N
08/02/2017 | 07:14 | ZN3155:PA23 | URBAN | Asset Failure | LV | 95 | 206 | 0.013448 | 0.0065432 | N
08/02/2017 | 09:03 | ZN14144:PA8 | URBAN | Asset Failure | LV | 1 | 267 | 0.00018355 | 6.8876e-05 | N
09/02/2017 | 05:58 | ZN965:PA38 | URBAN | Asset Failure | LV | 61 | 352 | 0.014789 | 0.0042014 | N
08/02/2017 | 16:30 | 801:74118 | URBAN | Asset Failure | LV | 21 | 49 | 0.00070942 | 0.0014464 | N
09/02/2017 | 10:36 | ZN9550:PA1 | URBAN | Asset Failure | LV | 9 | 143 | 0.00088736 | 0.00061988 | N
09/02/2017 | 11:24 | ZN187:PA30 | URBAN | Asset Failure | LV | 46 | 226 | 0.0071603 | 0.0031683 | N
09/02/2017 | 19:00 | 221:11894 | URBAN | Asset Failure | LV | 14 | 55 | 0.00053034 | 0.00096426 | N
10/02/2017 | 12:27 | ZN7900:PA16 | URBAN | Asset Failure | LV | 22 | 38 | 0.00057258 | 0.0015154 | N
10/02/2017 | 15:55 | ZN690:PA33 | URBAN | Asset Failure | LV | 1 | 149 | 0.00010241 | 6.8883e-05 | N
10/02/2017 | 16:19 | 513:48052 | URBAN | Asset Failure | LV | 72 | 41 | 0.0020334 | 0.0049596 | N
10/02/2017 | 17:41 | ZN1285:PA27 | URBAN | Asset Failure | LV | 59 | 233 | 0.0094734 | 0.0040641 | N
10/02/2017 | 22:06 | ZN1285:PA27 | URBAN | Asset Failure | LV | 59 | 179 | 0.0072747 | 0.0040641 | N
11/02/2017 | 15:23 | ZN2196:PA9 | URBAN | Asset Failure | LV | 45 | 637 | 0.019739 | 0.0030997 | N
11/02/2017 | 17:17 | ZN1068:PA22 | URBAN | Asset Failure | LV | 81 | 1,168 | 0.065142 | 0.0055795 | N
11/02/2017 | 18:34 | 502:48002 | URBAN | Asset Failure | LV | 20 | 305 | 0.0042019 | 0.0013777 | N
11/02/2017 | 18:44 | ZN1287:PA11 | URBAN | Asset Failure | LV | 83 | 465 | 0.026609 | 0.0057173 | N
11/02/2017 | 19:25 | ZN129:PA18 | URBAN | Asset Failure | LV | 90 | 153 | 0.0094801 | 0.0061995 | N
11/02/2017 | 20:29 | ZN3922:PA22 | URBAN | Asset Failure | LV | 48 | 221 | 0.0073044 | 0.0033064 | N
11/02/2017 | 21:30 | ZN965:PA4 | URBAN | Asset Failure | LV | 23 | 165 | 0.0026099 | 0.0015843 | N
12/02/2017 | 01:45 | ZN35500:PA28 | URBAN | Asset Failure | LV | 92 | 335 | 0.02123 | 0.0063372 | N
12/02/2017 | 17:42 | ZN9550:PA28 | URBAN | Asset Failure | LV | 83 | 112 | 0.0064081 | 0.0057173 | N
13/02/2017 | 12:18 | ZN15015:PA5 | URBAN | Asset Failure | LV | 48 | 54 | 0.0018009 | 0.0033064 | N
13/02/2017 | 09:25 | ZN690:PA24 | SHORT RURAL | Asset Failure | LV | 13 | 200 | 0.011634 | 0.0058172 | N
13/02/2017 | 14:23 | 810:74062 | SHORT RURAL | Asset Failure | LV | 1 | 246 | 0.0011021 | 0.00044747 | N
13/02/2017 | 11:38 | ZN14891:PA5 | SHORT RURAL | Asset Failure | LV | 2 | 139 | 0.001244 | 0.00089495 | N
13/02/2017 | 16:12 | 512:48049 | SHORT RURAL | Asset Failure | LV | 3 | 158 | 0.002121 | 0.0013424 | N
14/02/2017 | 06:17 | ZN10997:PA12 | URBAN | Asset Failure | LV | 82 | 298 | 0.016851 | 0.0056548 | N
14/02/2017 | 10:57 | ZN36200:PA4 | SHORT RURAL | Asset Failure | LV | 23 | 193 | 0.019811 | 0.010265 | N
14/02/2017 | 15:48 | 801:74120 | URBAN | Asset Failure | LV | 43 | 86 | 0.0025576 | 0.0029653 | N
14/02/2017 | 20:13 | 801:74123 | SHORT RURAL | Asset Failure | LV | 8 | 114 | 0.0040703 | 0.0035704 | N
14/02/2017 | 22:42 | ZN965:PA20 | URBAN | Asset Failure | LV | 39 | 1,351 | 0.036348 | 0.0026895 | N
06/02/2017 | 18:05 | ZN36100:PA13 | URBAN | Asset Failure | LV | 8 | 75 | 0.00041324 | 0.00055099 | N
15/02/2017 | 10:20 | 504:48028 | URBAN | Asset Failure | LV | 1 | 220 | 0.00015156 | 6.8905e-05 | N
15/02/2017 | 14:45 | ZN36800:PA33 | URBAN | Asset Failure | LV | 37 | 825 | 0.021033 | 0.0025495 | N
17/02/2017 | 00:40 | ZN2635:PA59 | URBAN | Asset Failure | LV | 7 | 85 | 0.0004099 | 0.00048223 | Y
17/02/2017 | 18:17 | ZN9252:PA30 | URBAN | Asset Failure | LV | 61 | 238 | 0.010001 | 0.0042023 | Y
17/02/2017 | 17:10 | ZN15010:PA11 | URBAN | Asset Failure | LV | 1 | 1,536 | 0.0010583 | 6.889e-05 | Y
17/02/2017 | 22:00 | ZN12690:PA19 | URBAN | Asset Failure | LV | 30 | 1,455 | 0.03007 | 0.0020667 | Y
18/02/2017 | 09:15 | ZN3155:PA23 | URBAN | Asset Failure | LV | 112 | 83 | 0.0063899 | 0.0077157 | N
18/02/2017 | 22:06 | ZN12610:PA16 | SHORT RURAL | Asset Failure | LV | 71 | 933 | 0.29595 | 0.031709 | N
19/02/2017 | 07:45 | ZN180:PA32 | URBAN | Asset Failure | LV | 6 | 1,050 | 0.0043388 | 0.00041334 | N
19/02/2017 | 13:48 | ZN36200:PA4 | SHORT RURAL | Asset Failure | LV | 28 | 151 | 0.018903 | 0.012505 | N
20/02/2017 | 19:10 | ZN2568:PA26 | URBAN | Asset Failure | LV | 50 | 70 | 0.0023974 | 0.0034445 | N
21/02/2017 | 15:17 | ZN2635:PA43 | URBAN | Asset Failure | LV | 26 | 173 | 0.0030946 | 0.0017912 | N
21/02/2017 | 17:01 | ZN14144:PA7 | SHORT RURAL | Asset Failure | LV | 65 | 39 | 0.01124 | 0.029031 | N
22/02/2017 | 18:07 | ZN12650:PA1 | SHORT RURAL | Asset Failure | LV | 50 | 350 | 0.078161 | 0.022332 | N
22/02/2017 | 18:06 | ZN12580:PA4 | URBAN | Asset Failure | LV | 7 | 266 | 0.0012828 | 0.00048225 | N
24/02/2017 | 20:12 | ZN2835:PA29 | URBAN | Asset Failure | LV | 92 | 288 | 0.018251 | 0.0063371 | N
25/02/2017 | 10:24 | ZN12660:PA8 | URBAN | Asset Failure | LV | 53 | 479 | 0.017486 | 0.0036506 | N
25/02/2017 | 10:34 | ZN10996:PA12 | URBAN | Asset Failure | LV | 55 | 210 | 0.0079694 | 0.0037883 | N
25/02/2017 | 10:34 | ZN10996:PA14 | URBAN | Asset Failure | LV | 1 | 211 | 0.00014533 | 6.8879e-05 | N
25/02/2017 | 10:56 | ZN3425:PA7 | URBAN | Asset Failure | LV | 6 | 874 | 0.003612 | 0.00041327 | N
25/02/2017 | 10:56 | ZN80:PA37 | URBAN | Asset Failure | LV | 20 | 864 | 0.011902 | 0.0013776 | N
25/02/2017 | 19:31 | ZN2568:PA38 | URBAN | Asset Failure | LV | 72 | 49 | 0.0024193 | 0.0049593 | N
27/02/2017 | 04:39 | 814:82289 | SHORT RURAL | Asset Failure | LV | 4 | 216 | 0.0038587 | 0.0017865 | N
27/02/2017 | 07:22 | 202:34260 | URBAN | Asset Failure | LV | 7 | 638 | 0.003074 | 0.00048215 | N
27/02/2017 | 10:31 | ZN36200:PA8 | SHORT RURAL | Asset Failure | LV | 1 | 253 | 0.0011307 | 0.00044661 | N
27/02/2017 | 18:48 | ZN12630:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 251 | 0.0011232 | 0.00044661 | N
27/02/2017 | 14:47 | ZN12690:PA24 | SHORT RURAL | Asset Failure | LV | 9 | 188 | 0.0075567 | 0.0040195 | N
27/02/2017 | 22:55 | ZN4990:PA53 54KLM | CBD | Asset Failure | LV | 13 | 320 | 0.13402 | 0.041881 | N
28/02/2017 | 04:50 | ZN180:PA30 | URBAN | Asset Failure | LV | 46 | 422 | 0.013385 | 0.0031685 | N
28/02/2017 | 08:13 | ZN342:PA28 | URBAN | Asset Failure | LV | 50 | 1,097 | 0.03778 | 0.003444 | N
28/02/2017 | 08:13 | ZN931:PA11 | URBAN | Asset Failure | LV | 101 | 1,096 | 0.076254 | 0.0069568 | N
28/02/2017 | 17:26 | 228:7490 | SHORT RURAL | Asset Failure | LV | 2 | 84 | 0.00075032 | 0.00089324 | N
28/02/2017 | 21:27 | 801:74118 | URBAN | Asset Failure | LV | 1 | 267 | 0.00018413 | 6.8879e-05 | N
01/03/2017 | 07:31 | ZN36800:PA57 | URBAN | Asset Failure | LV | 103 | 108 | 0.0076894 | 0.0070946 | N
01/03/2017 | 10:32 | ZN3425:PA30 | URBAN | Asset Failure | LV | 57 | 455 | 0.017883 | 0.0039262 | N
01/03/2017 | 14:20 | ZN965:PA4 | URBAN | Asset Failure | LV | 43 | 581 | 0.017208 | 0.0029618 | N
02/03/2017 | 06:38 | ZN874:PA26 | URBAN | Asset Failure | LV | 38 | 217 | 0.0056751 | 0.0026175 | N
02/03/2017 | 09:49 | ZN3155:PA23 | URBAN | Asset Failure | LV | 29 | 168 | 0.0033582 | 0.0019975 | N
02/03/2017 | 14:37 | 526:34640 | SHORT RURAL | Asset Failure | LV | 2 | 153 | 0.0013667 | 0.00089326 | N
02/03/2017 | 14:55 | ZN1673:PA13 | URBAN | Asset Failure | LV | 25 | 30 | 0.00051086 | 0.001722 | N
02/03/2017 | 16:37 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 173 | 0.061588 | 0.0356 | N
02/03/2017 | 16:30 | 239:82131 | SHORT RURAL | Asset Failure | LV | 6 | 155 | 0.0041537 | 0.0026798 | N
02/03/2017 | 23:13 | ZN3155:PA44 | URBAN | Asset Failure | LV | 104 | 1,307 | 0.093628 | 0.0071636 | N
03/03/2017 | 14:40 | ZN3425:PA28 | URBAN | Asset Failure | LV | 25 | 315 | 0.0054164 | 0.0017216 | N
03/03/2017 | 19:30 | ZN2602:PA36 | URBAN | Asset Failure | LV | 74 | 120 | 0.006115 | 0.0050959 | N
05/03/2017 | 16:00 | ZN36300:PA8 | URBAN | Asset Failure | LV | 11 | 35 | 0.00026518 | 0.00075765 | N
04/03/2017 | 15:25 | ZN3154:PA12 | URBAN | Asset Failure | LV | 21 | 125 | 0.001808 | 0.0014464 | N
04/03/2017 | 15:59 | 807:74184 | SHORT RURAL | Asset Failure | LV | 5 | 141 | 0.0031533 | 0.0022364 | N
04/03/2017 | 19:02 | ZN965:PA6 | URBAN | Asset Failure | LV | 16 | 237 | 0.0026147 | 0.001102 | N
04/03/2017 | 23:39 | ZN2635:PA58 | URBAN | Asset Failure | LV | 37 | 766 | 0.019519 | 0.0025484 | N
08/03/2017 | 06:12 | ZN12660:PA10 | URBAN | Asset Failure | LV | 15 | 110 | 0.0011365 | 0.0010332 | N
08/03/2017 | 00:05 | ZN931:PA24 | URBAN | Asset Failure | LV | 5 | 95 | 0.00032718 | 0.0003444 | N
08/03/2017 | 10:13 | ZN14143:PA17 | SHORT RURAL | Asset Failure | LV | 1 | 226 | 0.0010087 | 0.00044617 | N
08/03/2017 | 10:14 | ZN262:PA7 | URBAN | Asset Failure | LV | 37 | 76 | 0.0019297 | 0.0025486 | N
08/03/2017 | 13:13 | ZN15008:PA7 | URBAN | Asset Failure | LV | 53 | 377 | 0.013759 | 0.0036506 | N
08/03/2017 | 13:25 | ZN80:PA22 | URBAN | Asset Failure | LV | 89 | 304 | 0.018636 | 0.0061303 | N
08/03/2017 | 18:45 | ZN3288:PA45 46DEF | CBD | Asset Failure | LV | 22 | 385 | 0.27264 | 0.07086 | N
09/03/2017 | 08:43 | 512:48049 | SHORT RURAL | Asset Failure | LV | 1 | 164 | 0.00072788 | 0.00044464 | N
09/03/2017 | 13:58 | ZN15001:PA10 | URBAN | Asset Failure | LV | 13 | 86 | 0.00077347 | 0.00089556 | N
10/03/2017 | 17:53 | ZN3155:PA34 | URBAN | Asset Failure | LV | 22 | 67 | 0.0010155 | 0.0015156 | N
11/03/2017 | 09:37 | ZN2400:PA11 | SHORT RURAL | Asset Failure | LV | 1 | 480 | 0.0021364 | 0.00044464 | N
11/03/2017 | 13:07 | 509:33395 | LONG RURAL | Asset Failure | LV | 4 | 158 | 0.22507 | 0.14245 | N
11/03/2017 | 18:24 | 802:82225 | SHORT RURAL | Asset Failure | LV | 1 | 153 | 0.00067845 | 0.00044464 | N
12/03/2017 | 00:35 | ZN690:PA35 | URBAN | Asset Failure | LV | 90 | 81 | 0.0050501 | 0.0062003 | N
12/03/2017 | 13:32 | ZN36100:PA7 | URBAN | Asset Failure | LV | 44 | 598 | 0.018116 | 0.0030312 | N
13/03/2017 | 08:39 | ZN3425:PA27 | URBAN | Asset Failure | LV | 75 | 216 | 0.011143 | 0.0051669 | N
13/03/2017 | 11:24 | ZN2635:PA46 | URBAN | Asset Failure | LV | 64 | 104 | 0.0045803 | 0.0044091 | N
13/03/2017 | 11:33 | ZN3922:PA7 | URBAN | Asset Failure | LV | 63 | 147 | 0.0063801 | 0.0043402 | N
13/03/2017 | 13:21 | ZN2635:PA46 | URBAN | Asset Failure | LV | 64 | 89 | 0.0039241 | 0.0044091 | N
14/03/2017 | 15:51 | ZN195:PA8 | URBAN | Asset Failure | LV | 9 | 353 | 0.0021894 | 0.00062003 | N
15/03/2017 | 13:43 | ZN195:PA11 | URBAN | Asset Failure | LV | 45 | 152 | 0.0047024 | 0.0031002 | N
16/03/2017 | 14:58 | ZN2635:PA46 | URBAN | Asset Failure | LV | 45 | 71 | 0.002213 | 0.0030995 | N
16/03/2017 | 15:50 | ZN965:PA6 | URBAN | Asset Failure | LV | 16 | 295 | 0.003251 | 0.001102 | N
16/03/2017 | 18:50 | ZN2602:PA42 | URBAN | Asset Failure | LV | 19 | 330 | 0.0043186 | 0.0013087 | N
16/03/2017 | 19:21 | ZN14144:PA1 | URBAN | Asset Failure | LV | 51 | 63 | 0.0022195 | 0.0035127 | N
16/03/2017 | 20:36 | 243:80083 | SHORT RURAL | Asset Failure | LV | 4 | 104 | 0.0018492 | 0.001778 | N
17/03/2017 | 14:47 | ZN15004:PA9 | URBAN | Asset Failure | LV | 61 | 433 | 0.018186 | 0.0042015 | N
17/03/2017 | 16:35 | ZN3425:PA15 | URBAN | Asset Failure | LV | 29 | 391 | 0.0078133 | 0.0019974 | N
17/03/2017 | 19:01 | ZN180:PA21 | URBAN | Asset Failure | LV | 3 | 1,649 | 0.0034074 | 0.00020663 | N
18/03/2017 | 00:18 | ZN9037:PA10 | URBAN | Asset Failure | LV | 1 | 119 | 8.1701e-05 | 6.8878e-05 | N
18/03/2017 | 07:33 | ZN2602:PA27 | URBAN | Asset Failure | LV | 253 | 867 | 0.15109 | 0.017426 | N
18/03/2017 | 10:12 | ZN15012:PA2 | URBAN | Asset Failure | LV | 1 | 557 | 0.00038373 | 6.8878e-05 | N
18/03/2017 | 10:42 | ZN847:PA47 | SHORT RURAL | Asset Failure | LV | 25 | 107 | 0.011921 | 0.011111 | N
18/03/2017 | 11:45 | ZN4545:PA19 | URBAN | Asset Failure | LV | 116 | 225 | 0.017977 | 0.0079899 | N
18/03/2017 | 14:50 | ZN180:PA21 | URBAN | Asset Failure | LV | 77 | 460 | 0.024397 | 0.0053036 | N
18/03/2017 | 16:26 | 222:33596 | URBAN | Asset Failure | LV | 1 | 232 | 0.00015961 | 6.8878e-05 | N
18/03/2017 | 21:01 | ZN15005:PA2 | URBAN | Asset Failure | LV | 5 | 218 | 0.00075077 | 0.00034439 | N
19/03/2017 | 01:50 | ZN35600:PA1 | URBAN | Asset Failure | LV | 79 | 95 | 0.0051693 | 0.0054414 | N
19/03/2017 | 01:50 | ZN35600:PA9 | URBAN | Asset Failure | LV | 31 | 79 | 0.0016883 | 0.0021352 | N
19/03/2017 | 06:27 | ZN14143:PA12 | SHORT RURAL | Asset Failure | LV | 43 | 948 | 0.18112 | 0.019111 | N
19/03/2017 | 11:52 | ZN4990:PA55 56DEF | CBD | Asset Failure | LV | 85 | 225 | 0.61541 | 0.27351 | N
19/03/2017 | 15:45 | ZN14891:PA8 | SHORT RURAL | Asset Failure | LV | 54 | 59 | 0.014176 | 0.024 | N
20/03/2017 | 06:51 | ZN2196:PA18 | URBAN | Asset Failure | LV | 1 | 114 | 7.8418e-05 | 6.8879e-05 | N
20/03/2017 | 11:33 | ZN15001:PA6 | URBAN | Asset Failure | LV | 1 | 176 | 0.00012134 | 6.8879e-05 | N
21/03/2017 | 09:32 | ZN9900:PA21 | URBAN | Asset Failure | LV | 36 | 57 | 0.0014184 | 0.0024797 | N
31/03/2017 | 11:34 | ZN36300:PA11 | URBAN | Asset Failure | LV | 28 | 776 | 0.014957 | 0.0019275 | N
22/03/2017 | 06:37 | ZN12600:PA13 | SHORT RURAL | Asset Failure | LV | 6 | 337 | 0.0089956 | 0.0026668 | N
22/03/2017 | 07:03 | ZN4990:PA55 56KLM | CBD | Asset Failure | LV | 93 | 1,187 | 3.5524 | 0.29928 | N
22/03/2017 | 11:28 | ZN14143:PA10 | SHORT RURAL | Asset Failure | LV | 15 | 212 | 0.014129 | 0.0066671 | N
22/03/2017 | 14:39 | 508:82575 | SHORT RURAL | Asset Failure | LV | 1 | 300 | 0.0013329 | 0.00044447 | N
22/03/2017 | 14:56 | ZN340:PA11 | URBAN | Asset Failure | LV | 52 | 54 | 0.0019455 | 0.0035818 | N
22/03/2017 | 19:10 | ZN2400:PA18 | SHORT RURAL | Asset Failure | LV | 44 | 85 | 0.016623 | 0.019557 | N
23/03/2017 | 08:24 | ZN847:PA44 | URBAN | Asset Failure | LV | 21 | 156 | 0.0022531 | 0.001446 | N
23/03/2017 | 16:53 | ZN129:PA4 | URBAN | Asset Failure | LV | 31 | 196 | 0.0041874 | 0.0021346 | N
24/03/2017 | 10:32 | ZN14143:PA12 | SHORT RURAL | Asset Failure | LV | 42 | 447 | 0.08352 | 0.018673 | N
24/03/2017 | 14:08 | ZN965:PA6 | URBAN | Asset Failure | LV | 1 | 211 | 0.00014549 | 6.8859e-05 | N
24/03/2017 | 14:52 | 258:80778 | URBAN | Asset Failure | LV | 68 | 58 | 0.002708 | 0.0046824 | N
24/03/2017 | 15:41 | ZN3425:PA30 | URBAN | Asset Failure | LV | 92 | 129 | 0.0081574 | 0.006335 | N
24/03/2017 | 18:44 | ZN1193:PA15 | URBAN | Asset Failure | LV | 158 | 121 | 0.013164 | 0.01088 | N
24/03/2017 | 18:44 | ZN3425:PA30 | URBAN | Asset Failure | LV | 92 | 121 | 0.0076653 | 0.006335 | N
24/03/2017 | 21:02 | ZN2835:PA9 | URBAN | Asset Failure | LV | 137 | 171 | 0.016101 | 0.0094336 | N
24/03/2017 | 21:44 | ZN1193:PA15 | URBAN | Asset Failure | LV | 158 | 63 | 0.0068542 | 0.01088 | N
24/03/2017 | 21:44 | ZN3425:PA30 | URBAN | Asset Failure | LV | 92 | 63 | 0.0039752 | 0.006335 | N
26/03/2017 | 07:02 | 243:80081 | SHORT RURAL | Asset Failure | LV | 59 | 285 | 0.074583 | 0.026186 | N
26/03/2017 | 07:06 | 242:81538 | URBAN | Asset Failure | LV | 36 | 370 | 0.0091608 | 0.0024789 | N
26/03/2017 | 11:05 | ZN847:PA5 | URBAN | Asset Failure | LV | 16 | 2,040 | 0.022475 | 0.0011017 | N
28/03/2017 | 14:05 | ZN7900:PA6 | URBAN | Asset Failure | LV | 102 | 20 | 0.0014047 | 0.0070235 | N
28/03/2017 | 20:02 | 813:89055 | SHORT RURAL | Asset Failure | LV | 1 | 83 | 0.00036668 | 0.00044384 | N
28/03/2017 | 12:00 | ZN35900:PA6 | URBAN | Asset Failure | LV | 1 | 165 | 0.00011362 | 6.8858e-05 | N
29/03/2017 | 13:46 | ZN931:PA9 | URBAN | Asset Failure | LV | 43 | 313 | 0.0092713 | 0.002961 | N
30/03/2017 | 11:27 | ZN12580:PA16 | URBAN | Asset Failure | LV | 19 | 85 | 0.0011117 | 0.0013079 | N
31/03/2017 | 04:17 | ZN262:PA14 | URBAN | Asset Failure | LV | 2 | 63 | 8.6715e-05 | 0.00013768 | N
31/03/2017 | 09:59 | 814:82283 | SHORT RURAL | Asset Failure | LV | 1 | 136 | 0.00060154 | 0.00044356 | N
31/03/2017 | 13:04 | ZN10999:PA36 | URBAN | Asset Failure | LV | 44 | 328 | 0.0099432 | 0.0030289 | N
31/03/2017 | 15:02 | ZN10999:PA36 | URBAN | Asset Failure | LV | 1 | 297 | 0.00020473 | 6.884e-05 | N
31/03/2017 | 15:13 | ZN847:PA44 | URBAN | Asset Failure | LV | 21 | 362 | 0.0052269 | 0.0014456 | N
01/04/2017 | 19:57 | ZN901:PA10 | URBAN | Asset Failure | LV | 56 | 507 | 0.019517 | 0.0038527 | N
02/04/2017 | 05:14 | ZN262:PA6 | URBAN | Asset Failure | LV | 55 | 365 | 0.013824 | 0.0037844 | N
02/04/2017 | 07:06 | ZN116:PA84 | URBAN | Asset Failure | LV | 52 | 319 | 0.011414 | 0.0035779 | N
03/04/2017 | 02:48 | ZN901:PA11 | URBAN | Asset Failure | LV | 58 | 464 | 0.018527 | 0.0039908 | N
03/04/2017 | 10:15 | ZN3155:PA21 | URBAN | Asset Failure | LV | 51 | 1,044 | 0.036641 | 0.0035091 | N
30/03/2017 | 11:35 | ZN12580:PA16 | URBAN | Asset Failure | LV | 4 | 85 | 0.00023404 | 0.00027534 | N
04/04/2017 | 18:24 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 96 | 0.034286 | 0.035714 | N
04/04/2017 | 22:29 | ZN3425:PA27 | URBAN | Asset Failure | LV | 40 | 841 | 0.023147 | 0.0027523 | N
05/04/2017 | 08:19 | ZN15001:PA8 | URBAN | Asset Failure | LV | 1 | 761 | 0.00052361 | 6.8807e-05 | N
05/04/2017 | 12:24 | 813:89065 | URBAN | Asset Failure | LV | 1 | 221 | 0.00015186 | 6.8807e-05 | N
06/04/2017 | 18:49 | ZN901:PA19 | URBAN | Asset Failure | LV | 58 | 615 | 0.024535 | 0.0039908 | N
06/04/2017 | 20:32 | ZN15006:PA13 | URBAN | Asset Failure | LV | 82 | 68 | 0.0038254 | 0.0056422 | N
07/04/2017 | 08:31 | 523:33508 | SHORT RURAL | Asset Failure | LV | 7 | 115 | 0.0035782 | 0.0031174 | N
08/04/2017 | 14:36 | ZN2602:PA8 | URBAN | Asset Failure | LV | 54 | 354 | 0.013131 | 0.0037141 | N
09/04/2017 | 08:17 | ZN262:PA39 | URBAN | Asset Failure | LV | 36 | 313 | 0.0077427 | 0.0024761 | N
09/04/2017 | 06:28 | ZN965:PA24 | URBAN | Asset Failure | LV | 17 | 719 | 0.0084048 | 0.0011693 | N
09/04/2017 | 15:28 | ZN12570:PA35 | URBAN | Asset Failure | LV | 9 | 10 | 6.1902e-05 | 0.00061902 | N
09/04/2017 | 12:01 | 814:82283 | SHORT RURAL | Asset Failure | LV | 1 | 169 | 0.00075441 | 0.00044534 | N
09/04/2017 | 16:03 | ZN262:PA19 | URBAN | Asset Failure | LV | 46 | 267 | 0.0084365 | 0.0031639 | N
09/04/2017 | 18:39 | ZN36100:PA13 | URBAN | Asset Failure | LV | 19 | 271 | 0.003535 | 0.0013068 | N
10/04/2017 | 08:31 | ZN35400:PA64 | URBAN | Asset Failure | LV | 40 | 148 | 0.004081 | 0.0027512 | N
10/04/2017 | 02:49 | ZN3154:PA23 | URBAN | Asset Failure | LV | 20 | 941 | 0.012944 | 0.0013756 | N
10/04/2017 | 10:22 | ZN1673:PA1 | URBAN | Asset Failure | LV | 22 | 491 | 0.0074296 | 0.0015132 | N
10/04/2017 | 10:22 | ZN1673:PA14 | URBAN | Asset Failure | LV | 2 | 491 | 0.00067542 | 0.00013756 | N
10/04/2017 | 10:46 | 222:33601 | SHORT RURAL | Asset Failure | LV | 67 | 104 | 0.031032 | 0.029838 | N
10/04/2017 | 16:39 | ZN2400:PA18 | SHORT RURAL | Asset Failure | LV | 44 | 359 | 0.070386 | 0.019595 | N
11/04/2017 | 07:07 | ZN9534:PA18 | URBAN | Asset Failure | LV | 4 | 173 | 0.00047596 | 0.00027512 | N
09/04/2017 | 21:43 | ZN1287:PA21 | URBAN | Asset Failure | LV | 65 | 102 | 0.0045601 | 0.0044707 | N
11/04/2017 | 11:27 | ZN1287:PA24 | URBAN | Asset Failure | LV | 72 | 113 | 0.0055803 | 0.0049522 | N
11/04/2017 | 19:54 | 810:74050 | SHORT RURAL | Asset Failure | LV | 1 | 1,116 | 0.00497 | 0.00044534 | N
12/04/2017 | 15:08 | ZN15001:PA8 | URBAN | Asset Failure | LV | 7 | 381 | 0.0018337 | 0.00048151 | N
14/04/2017 | 20:03 | ZN15005:PA6 | URBAN | Asset Failure | LV | 36 | 81 | 0.0020176 | 0.0024771 | N
14/04/2017 | 23:35 | ZN15006:PA2 | URBAN | Asset Failure | LV | 66 | 80 | 0.0036331 | 0.0045414 | N
14/04/2017 | 23:45 | ZN15006:PA2 | URBAN | Asset Failure | LV | 59 | 75 | 0.0030448 | 0.0040597 | N
16/04/2017 | 03:14 | ZN2602:PA3 | URBAN | Asset Failure | LV | 48 | 341 | 0.011256 | 0.0033008 | N
17/04/2017 | 12:37 | 507:80932 | SHORT RURAL | Asset Failure | LV | 4 | 263 | 0.0046844 | 0.0017811 | N
17/04/2017 | 18:41 | ZN1068:PA21 | URBAN | Asset Failure | LV | 23 | 725 | 0.011473 | 0.0015816 | N
17/04/2017 | 18:57 | ZN180:PA34 | URBAN | Asset Failure | LV | 71 | 37 | 0.0018146 | 0.0048824 | N
18/04/2017 | 16:56 | 810:74062 | SHORT RURAL | Asset Failure | LV | 1 | 150 | 0.00066859 | 0.00044528 | N
19/04/2017 | 05:46 | ZN711:PA32 | URBAN | Asset Failure | LV | 7 | 809 | 0.0038925 | 0.00048139 | N
19/04/2017 | 07:00 | ZN2400:PA21 | URBAN | Asset Failure | LV | 59 | 158 | 0.0063918 | 0.0040574 | N
19/04/2017 | 17:17 | 512:48049 | SHORT RURAL | Asset Failure | LV | 1 | 97 | 0.0004323 | 0.00044529 | N
20/04/2017 | 02:46 | 810:74062 | SHORT RURAL | Asset Failure | LV | 1 | 145 | 0.00064406 | 0.00044413 | N
20/04/2017 | 18:55 | 507:80932 | SHORT RURAL | Asset Failure | LV | 2 | 145 | 0.001288 | 0.00088826 | N
21/04/2017 | 01:37 | ZN965:PA8 | URBAN | Asset Failure | LV | 22 | 572 | 0.008651 | 0.0015136 | N
21/04/2017 | 18:09 | ZN12630:PA8 | SHORT RURAL | Asset Failure | LV | 4 | 96 | 0.0017055 | 0.0017766 | N
22/04/2017 | 10:36 | 232:11453 | SHORT RURAL | Asset Failure | LV | 37 | 204 | 0.033444 | 0.016428 | N
23/04/2017 | 11:32 | ZN9550:PA6 | URBAN | Asset Failure | LV | 41 | 87 | 0.0024654 | 0.0028198 | N
23/04/2017 | 17:58 | ZN15014:PA9 | URBAN | Asset Failure | LV | 40 | 1,068 | 0.029368 | 0.002751 | N
24/04/2017 | 11:14 | ZN10997:PA2 | URBAN | Asset Failure | LV | 54 | 104 | 0.0038624 | 0.0037139 | N
25/04/2017 | 18:15 | 502:48010 | SHORT RURAL | Asset Failure | LV | 5 | 80 | 0.001776 | 0.00222 | N
26/04/2017 | 10:16 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 133 | 0.047614 | 0.035702 | N
27/04/2017 | 12:50 | ZN342:PA17 | URBAN | Asset Failure | LV | 31 | 95 | 0.0020236 | 0.0021316 | N
27/04/2017 | 17:14 | ZN12630:PA8 | SHORT RURAL | Asset Failure | LV | 4 | 171 | 0.0030364 | 0.0017757 | N
27/04/2017 | 17:41 | ZN342:PA17 | URBAN | Asset Failure | LV | 31 | 78 | 0.001663 | 0.0021316 | N
27/04/2017 | 17:41 | ZN342:PA23 | URBAN | Asset Failure | LV | 1 | 79 | 5.432e-05 | 6.876e-05 | N
29/04/2017 | 01:26 | ZN10995:PA5 | URBAN | Asset Failure | LV | 57 | 424 | 0.016619 | 0.0039195 | N
29/04/2017 | 19:01 | ZN342:PA17 | URBAN | Asset Failure | LV | 12 | 329 | 0.0027148 | 0.00082515 | N
30/04/2017 | 12:23 | ZN3155:PA23 | URBAN | Asset Failure | LV | 16 | 1,882 | 0.020704 | 0.0011002 | N
01/05/2017 | 14:39 | ZN630:PA24 | URBAN | Asset Failure | LV | 2 | 366 | 0.00050334 | 0.00013752 | N
01/05/2017 | 14:39 | ZN630:PA3 | URBAN | Asset Failure | LV | 10 | 366 | 0.0025167 | 0.00068762 | N
01/05/2017 | 18:43 | ZN690:PA14 | URBAN | Asset Failure | LV | 1 | 267 | 0.00018387 | 6.8762e-05 | N
02/05/2017 | 07:44 | ZN15014:PA12 | SHORT RURAL | Asset Failure | LV | 24 | 166 | 0.017637 | 0.010653 | N
03/05/2017 | 06:27 | ZN10991:PA5 | URBAN | Asset Failure | LV | 74 | 317 | 0.016136 | 0.0050888 | N
03/05/2017 | 06:30 | ZN12610:PA22 | URBAN | Asset Failure | LV | 38 | 580 | 0.015156 | 0.0026131 | N
02/05/2017 | 17:17 | ZN2602:PA29 | URBAN | Asset Failure | LV | 87 | 73 | 0.0043672 | 0.0059825 | N
03/05/2017 | 11:27 | ZN1850:PA4 | URBAN | Asset Failure | LV | 31 | 163 | 0.0034748 | 0.0021318 | N
03/05/2017 | 13:47 | ZN262:PA6 | URBAN | Asset Failure | LV | 1 | 372 | 0.00025583 | 6.8767e-05 | N
03/05/2017 | 14:45 | ZN262:PA30 | URBAN | Asset Failure | LV | 47 | 277 | 0.0089452 | 0.0032321 | N
03/05/2017 | 16:11 | 526:34637 | SHORT RURAL | Asset Failure | LV | 1 | 94 | 0.00041726 | 0.0004439 | N
03/05/2017 | 18:24 | 812:19066 | SHORT RURAL | Asset Failure | LV | 1 | 201 | 0.00089349 | 0.0004439 | N
03/05/2017 | 10:30 | ZN10991:PA6 | URBAN | Asset Failure | LV | 79 | 30 | 0.0016298 | 0.0054326 | N
04/05/2017 | 08:36 | ZN180:PA34 | URBAN | Asset Failure | LV | 69 | 160 | 0.0075728 | 0.0047439 | N
04/05/2017 | 13:56 | ZN690:PA26 | URBAN | Asset Failure | LV | 75 | 63 | 0.0032571 | 0.0051564 | N
04/05/2017 | 14:01 | 229:34989 | SHORT RURAL | Asset Failure | LV | 1 | 329 | 0.001459 | 0.00044382 | N
04/05/2017 | 15:45 | ZN180:PA10 | URBAN | Asset Failure | LV | 90 | 345 | 0.021348 | 0.0061877 | N
04/05/2017 | 15:45 | ZN180:PA32 | URBAN | Asset Failure | LV | 99 | 345 | 0.023482 | 0.0068065 | N
05/05/2017 | 01:58 | ZN12620:PA11 | SHORT RURAL | Asset Failure | LV | 17 | 212 | 0.015995 | 0.0075449 | N
05/05/2017 | 06:35 | ZN9118:PA11 | URBAN | Asset Failure | LV | 75 | 159 | 0.0082232 | 0.0051632 | N
05/05/2017 | 07:14 | ZN2568:PA27 | URBAN | Asset Failure | LV | 5 | 166 | 0.00057139 | 0.00034421 | N
05/05/2017 | 13:44 | 502:48004 | URBAN | Asset Failure | LV | 19 | 305 | 0.0039944 | 0.001308 | N
08/05/2017 | 12:15 | ZN10996:PA10 | URBAN | Asset Failure | LV | 3 | 1,543 | 0.0031823 | 0.00020624 | N
08/05/2017 | 13:13 | 807:74183 | SHORT RURAL | Asset Failure | LV | 1 | 227 | 0.0010092 | 0.00044458 | N
08/05/2017 | 15:27 | 801:74121 | LONG RURAL | Asset Failure | LV | 6 | 238 | 0.50982 | 0.21421 | N
08/05/2017 | 13:13 | 807:74183 | SHORT RURAL | Asset Failure | LV | 2 | 182 | 0.0016183 | 0.00088916 | N
08/05/2017 | 17:56 | ZN35500:PA28 | URBAN | Asset Failure | LV | 14 | 1,534 | 0.014764 | 0.00096245 | N
09/05/2017 | 14:55 | 807:74183 | SHORT RURAL | Asset Failure | LV | 2 | 30 | 0.00026675 | 0.00088917 | N
09/05/2017 | 18:31 | ZN180:PA10 | URBAN | Asset Failure | LV | 54 | 139 | 0.0051603 | 0.0037124 | N
10/05/2017 | 11:27 | 509:33395 | LONG RURAL | Asset Failure | LV | 1 | 483 | 0.17244 | 0.035702 | N
11/05/2017 | 08:18 | 813:89063 | SHORT RURAL | Asset Failure | LV | 1 | 132 | 0.00058591 | 0.00044443 | N
11/05/2017 | 12:27 | ZN9700:PA17 | URBAN | Asset Failure | LV | 9 | 63 | 0.00038763 | 0.00061922 | N
13/05/2017 | 10:48 | 814:82285 | SHORT RURAL | Asset Failure | LV | 1 | 132 | 0.0005866 | 0.0004444 | N
13/05/2017 | 20:00 | ZN3922:PA13 | SHORT RURAL | Asset Failure | LV | 51 | 284 | 0.064476 | 0.022664 | N
15/05/2017 | 14:23 | ZN9900:PA13 | URBAN | Asset Failure | LV | 1 | 1,137 | 0.00078143 | 6.8735e-05 | N
15/05/2017 | 20:30 | ZN36100:PA1 | URBAN | Asset Failure | LV | 155 | 1,167 | 0.12436 | 0.010654 | N
16/05/2017 | 18:19 | 801:74119 | URBAN | Asset Failure | LV | 13 | 11 | 9.8292e-05 | 0.00089356 | N
16/05/2017 | 19:06 | 238:34148 | SHORT RURAL | Asset Failure | LV | 42 | 106 | 0.019813 | 0.018665 | N
16/05/2017 | 20:57 | ZN965:PA35 | URBAN | Asset Failure | LV | 49 | 767 | 0.025848 | 0.003368 | N
18/05/2017 | 11:27 | ZN1285:PA33 | URBAN | Asset Failure | LV | 71 | 142 | 0.0069488 | 0.0048789 | N
18/05/2017 | 14:23 | ZN9900:PA5 | URBAN | Asset Failure | LV | 35 | 121 | 0.002917 | 0.0024051 | N
18/05/2017 | 21:04 | ZN36800:PA32 | URBAN | Asset Failure | LV | 88 | 10 | 0.00061378 | 0.0060471 | N
18/05/2017 | 19:47 | ZN36100:PA20 | URBAN | Asset Failure | LV | 139 | 247 | 0.02364 | 0.0095517 | N
19/05/2017 | 09:21 | 222:33596 | URBAN | Asset Failure | LV | 8 | 104 | 0.00057177 | 0.00054978 | N
20/05/2017 | 14:18 | ZN8100:PA2 | URBAN | Asset Failure | LV | 3 | 382 | 0.00078756 | 0.00020617 | N
20/05/2017 | 18:31 | ZN15010:PA7 | URBAN | Asset Failure | LV | 86 | 78 | 0.0046336 | 0.0059101 | N
20/05/2017 | 22:47 | 801:74121 | LONG RURAL | Asset Failure | LV | 4 | 120 | 0.17125 | 0.1427 | N
21/05/2017 | 19:43 | ZN180:PA7 | URBAN | Asset Failure | LV | 62 | 59 | 0.0025196 | 0.0042608 | N
22/05/2017 | 18:18 | 233:82821 | SHORT RURAL | Asset Failure | LV | 41 | 362 | 0.066434 | 0.018352 | N
23/05/2017 | 18:06 | ZN180:PA32 | URBAN | Asset Failure | LV | 83 | 157 | 0.0089552 | 0.005704 | N
24/05/2017 | 18:03 | ZN12610:PA11 | URBAN | Asset Failure | LV | 1 | 102 | 6.9983e-05 | 6.8723e-05 | N
25/05/2017 | 09:10 | ZN4990:PA53 54KLM | CBD | Asset Failure | LV | 9 | 505 | 0.14526 | 0.028778 | N
25/05/2017 | 17:22 | ZN3672:PA46 | URBAN | Asset Failure | LV | 101 | 183 | 0.012686 | 0.006941 | N
26/05/2017 | 03:21 | ZN9118:PA2 | URBAN | Asset Failure | LV | 33 | 101 | 0.0022905 | 0.0022678 | Y
26/05/2017 | 03:21 | ZN9550:PA6 | URBAN | Asset Failure | LV | 46 | 338 | 0.010694 | 0.0031612 | Y
26/05/2017 | 14:35 | 807:74183 | SHORT RURAL | Asset Failure | LV | 1 | 186 | 0.00083165 | 0.00044761 | Y
27/05/2017 | 06:55 | ZN12610:PA10 | URBAN | Asset Failure | LV | 29 | 65 | 0.0012954 | 0.001993 | N
27/05/2017 | 12:30 | ZN263:PA35 37DEF | CBD | Asset Failure | LV | 8 | 180 | 0.046045 | 0.02558 | N
27/05/2017 | 12:30 | ZN263:PA35 37DEF | CBD | Asset Failure | LV | 6 | 181 | 0.034709 | 0.019185 | N
28/05/2017 | 12:02 | 222:33601 | SHORT RURAL | Asset Failure | LV | 1 | 297 | 0.0013315 | 0.00044761 | N
28/05/2017 | 19:45 | 242:81541 | URBAN | Asset Failure | LV | 50 | 210 | 0.0072159 | 0.0034361 | N
29/05/2017 | 17:30 | ZN1850:PA10 | URBAN | Asset Failure | LV | 33 | 129 | 0.0029244 | 0.0022678 | N
30/05/2017 | 16:34 | ZN195:PA30 | SHORT RURAL | Asset Failure | LV | 38 | 206 | 0.035038 | 0.017009 | N
31/05/2017 | 00:17 | ZN35370:PA8 | SHORT RURAL | Asset Failure | LV | 8 | 123 | 0.0044044 | 0.0035808 | N
31/05/2017 | 19:10 | ZN10995:PA1 | URBAN | Asset Failure | LV | 210 | 83 | 0.011946 | 0.014432 | N
01/06/2017 | 06:56 | ZN3155:PA12 | URBAN | Asset Failure | LV | 110 | 394 | 0.029784 | 0.0075594 | N
01/06/2017 | 06:56 | ZN3155:PA29 | URBAN | Asset Failure | LV | 2 | 394 | 0.00054153 | 0.00013744 | N
23/05/2017 | 19:40 | 507:80922 | SHORT RURAL | Asset Failure | LV | 13 | 70 | 0.0040732 | 0.0058189 | N
02/06/2017 | 11:20 | ZN10994:PA12 | URBAN | Asset Failure | LV | 1 | 634 | 0.00043545 | 6.8722e-05 | N
02/06/2017 | 11:26 | ZN262:PA30 | URBAN | Asset Failure | LV | 71 | 69 | 0.0033667 | 0.0048792 | N
02/06/2017 | 15:09 | ZN10994:PA12 | URBAN | Asset Failure | LV | 1 | 405 | 0.00027811 | 6.8722e-05 | N
02/06/2017 | 21:40 | ZN10990:PA11 | URBAN | Asset Failure | LV | 141 | 65 | 0.0062983 | 0.0096898 | N
03/06/2017 | 09:46 | ZN36300:PA3 | URBAN | Asset Failure | LV | 1 | 671 | 0.00046117 | 6.8722e-05 | N
03/06/2017 | 09:50 | ZN3155:PA23 | URBAN | Asset Failure | LV | 71 | 1,969 | 0.096087 | 0.0048792 | N
04/06/2017 | 00:26 | ZN10990:PA7 | URBAN | Asset Failure | LV | 59 | 123 | 0.0050067 | 0.0040546 | N
05/06/2017 | 18:36 | ZN129:PA35 | URBAN | Asset Failure | LV | 42 | 158 | 0.0045647 | 0.0028863 | N
06/06/2017 | 10:59 | ZN3288:PA41 42KLM | CBD | Asset Failure | LV | 28 | 466 | 0.41715 | 0.089517 | N
02/06/2017 | 09:35 | ZN12630:PA11 | SHORT RURAL | Asset Failure | LV | 9 | 40 | 0.0016114 | 0.0040284 | N
06/06/2017 | 18:48 | ZN3155:PA33 | URBAN | Asset Failure | LV | 83 | 92 | 0.0052476 | 0.0057039 | N
06/06/2017 | 23:14 | 232:11455 | SHORT RURAL | Asset Failure | LV | 94 | 178 | 0.074802 | 0.042075 | N
07/06/2017 | 02:10 | ZN3155:PA33 | URBAN | Asset Failure | LV | 86 | 170 | 0.010047 | 0.0059101 | N
07/06/2017 | 05:38 | ZN10994:PA1 | URBAN | Asset Failure | LV | 23 | 176 | 0.0027845 | 0.0015806 | N
07/06/2017 | 06:15 | ZN3155:PA33 | URBAN | Asset Failure | LV | 84 | 1,145 | 0.066082 | 0.0057726 | N
07/06/2017 | 10:55 | 232:11455 | SHORT RURAL | Asset Failure | LV | 94 | 240 | 0.10098 | 0.042075 | N
07/06/2017 | 13:25 | 202:34260 | URBAN | Asset Failure | LV | 5 | 365 | 0.0012542 | 0.00034361 | N
07/06/2017 | 16:59 | ZN965:PA28 | URBAN | Asset Failure | LV | 46 | 276 | 0.0087249 | 0.0031612 | N
07/06/2017 | 18:27 | ZN2400:PA26 | URBAN | Asset Failure | LV | 79 | 468 | 0.025408 | 0.005429 | N
08/06/2017 | 07:33 | ZN901:PA2 | URBAN | Asset Failure | LV | 1 | 266 | 0.00018299 | 6.8722e-05 | N
08/06/2017 | 08:26 | ZN4545:PA24 | URBAN | Asset Failure | LV | 50 | 214 | 0.0073429 | 0.0034361 | N
08/06/2017 | 15:48 | ZN195:PA29 | URBAN | Asset Failure | LV | 61 | 101 | 0.0042395 | 0.004192 | N
08/06/2017 | 16:48 | ZN167:PA10 | URBAN | Asset Failure | LV | 69 | 1,696 | 0.080429 | 0.0047418 | N
08/06/2017 | 18:26 | ZN901:PA2 | URBAN | Asset Failure | LV | 5 | 2,314 | 0.0079501 | 0.00034361 | N
08/06/2017 | 20:13 | ZN129:PA41 | URBAN | Asset Failure | LV | 20 | 72 | 0.00098822 | 0.0013744 | N
09/06/2017 | 07:32 | ZN4545:PA2 | URBAN | Asset Failure | LV | 7 | 153 | 0.00073521 | 0.00048105 | N
09/06/2017 | 10:51 | 512:48046 | SHORT RURAL | Asset Failure | LV | 5 | 89 | 0.0019918 | 0.002238 | N
09/06/2017 | 16:32 | ZN847:PA10 | URBAN | Asset Failure | LV | 1 | 98 | 6.7347e-05 | 6.8722e-05 | N
11/06/2017 | 05:30 | ZN2602:PA17 | URBAN | Asset Failure | LV | 58 | 219 | 0.0087304 | 0.0039859 | N
11/06/2017 | 15:57 | ZN3425:PA44 | URBAN | Asset Failure | LV | 37 | 68 | 0.0017282 | 0.0025427 | N
12/06/2017 | 13:05 | 508:82580 | SHORT RURAL | Asset Failure | LV | 10 | 70 | 0.0031332 | 0.004476 | N
12/06/2017 | 23:02 | ZN965:PA22 | URBAN | Asset Failure | LV | 28 | 197 | 0.0037952 | 0.0019242 | N
13/06/2017 | 08:05 | ZN2835:PA15 | URBAN | Asset Failure | LV | 1 | 295 | 0.00020257 | 6.8722e-05 | N
13/06/2017 | 18:21 | ZN14144:PA5 | SHORT RURAL | Asset Failure | LV | 55 | 79 | 0.019448 | 0.024618 | N
14/06/2017 | 12:30 | 526:34640 | SHORT RURAL | Asset Failure | LV | 1 | 460 | 0.002059 | 0.0004476 | N
14/06/2017 | 16:32 | ZN36300:PA5 | URBAN | Asset Failure | LV | 2 | 820 | 0.001127 | 0.00013744 | N
14/06/2017 | 18:01 | ZN2635:PA57 | URBAN | Asset Failure | LV | 71 | 404 | 0.019702 | 0.0048792 | N
14/06/2017 | 20:04 | ZN4545:PA2 | URBAN | Asset Failure | LV | 45 | 96 | 0.0029683 | 0.0030925 | N
15/06/2017 | 12:43 | ZN965:PA38 | URBAN | Asset Failure | LV | 10 | 47 | 0.00032299 | 0.00068722 | N
15/06/2017 | 14:52 | ZN2835:PA24 | URBAN | Asset Failure | LV | 16 | 78 | 0.00085398 | 0.0010995 | N
15/06/2017 | 16:02 | 508:82579 | SHORT RURAL | Asset Failure | LV | 1 | 267 | 0.0011954 | 0.0004476 | N
16/06/2017 | 12:35 | ZN14144:PA10 | SHORT RURAL | Asset Failure | LV | 7 | 145 | 0.0045432 | 0.0031332 | N
16/06/2017 | 18:10 | 214:8665 | URBAN | Asset Failure | LV | 91 | 42 | 0.0026114 | 0.0062537 | N
17/06/2017 | 09:19 | 242:81535 | URBAN | Asset Failure | LV | 74 | 191 | 0.0096996 | 0.0050854 | N
18/06/2017 | 20:55 | 221:11897 | URBAN | Asset Failure | LV | 44 | 55 | 0.0016631 | 0.0030238 | N
19/06/2017 | 12:09 | ZN15006:PA16 | URBAN | Asset Failure | LV | 1 | 170 | 0.0001171 | 6.8722e-05 | N
16/06/2017 | 08:20 | ZN4545:PA2 | URBAN | Asset Failure | LV | 45 | 340 | 0.010514 | 0.0030925 | N
19/06/2017 | 19:13 | ZN2835:PA41 | URBAN | Asset Failure | LV | 12 | 122 | 0.0010032 | 0.00082466 | N
20/06/2017 | 13:17 | 206:34440 | URBAN | Asset Failure | LV | 31 | 47 | 0.0010052 | 0.0021304 | N
20/06/2017 | 15:40 | 206:34440 | URBAN | Asset Failure | LV | 31 | 135 | 0.0028668 | 0.0021304 | N
20/06/2017 | 22:24 | ZN36100:PA27 | URBAN | Asset Failure | LV | 54 | 291 | 0.010795 | 0.003711 | N
21/06/2017 | 10:44 | ZN262:PA41 | URBAN | Asset Failure | LV | 8 | 191 | 0.0010501 | 0.00054977 | N
21/06/2017 | 19:01 | 213:33775 | URBAN | Asset Failure | LV | 24 | 96 | 0.0015751 | 0.0016493 | N
22/06/2017 | 19:42 | ZN15005:PA8 | URBAN | Asset Failure | LV | 44 | 827 | 0.025012 | 0.0030238 | N
23/06/2017 | 10:43 | ZN12610:PA18 | URBAN | Asset Failure | LV | 2 | 547 | 0.00075095 | 0.00013728 | N
23/06/2017 | 09:35 | ZN15006:PA12 | URBAN | Asset Failure | LV | 1 | 1,705 | 0.0011704 | 6.8642e-05 | N
23/06/2017 | 23:40 | ZN1788:PA36 | URBAN | Asset Failure | LV | 84 | 208 | 0.011993 | 0.005766 | N
23/06/2017 | 15:57 | 240:34835 | SHORT RURAL | Asset Failure | LV | 1 | 183 | 0.00081874 | 0.0004476 | N
24/06/2017 | 20:29 | ZN3425:PA28 | URBAN | Asset Failure | LV | 25 | 76 | 0.0012985 | 0.0017161 | N
25/06/2017 | 23:16 | ZN14144:PA8 | URBAN | Asset Failure | LV | 56 | 169 | 0.0064963 | 0.003844 | N
26/06/2017 | 15:09 | ZN14891:PA5 | SHORT RURAL | Asset Failure | LV | 1 | 86 | 0.00038494 | 0.0004476 | N
26/06/2017 | 20:47 | ZN690:PA5 | URBAN | Asset Failure | LV | 112 | 72 | 0.0055635 | 0.0076879 | N
23/06/2017 | 20:20 | ZN1788:PA36 | URBAN | Asset Failure | LV | 19 | 200 | 0.0026084 | 0.0013042 | N
27/06/2017 | 19:02 | ZN12610:PA22 | URBAN | Asset Failure | LV | 75 | 47 | 0.0024274 | 0.0051482 | N
28/06/2017 | 11:38 | ZN262:PA42 | URBAN | Asset Failure | LV | 1 | 412 | 0.00028255 | 6.8642e-05 | N
29/06/2017 | 03:21 | ZN188:PA4 | URBAN | Asset Failure | LV | 8 | 220 | 0.0012081 | 0.00054914 | N
29/06/2017 | 03:21 | ZN342:PA33 | URBAN | Asset Failure | LV | 47 | 349 | 0.011259 | 0.0032262 | N
29/06/2017 | 08:27 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 488 | 0.1741 | 0.035676 | N
30/06/2017 | 10:53 | ZN15012:PA6 | URBAN | Asset Failure | LV | 56 | 537 | 0.020633 | 0.003844 | N
30/06/2017 | 20:43 | ZN15004:PA3 | URBAN | Asset Failure | LV | 64 | 51 | 0.002239 | 0.0043931 | N
01/07/2016 | 10:33 | 513:48057 | URBAN | Asset Failure | LV | 1 | 139 | 9.6476e-05 | 6.9257e-05 | N
01/07/2016 | 13:16 | 235:2124 | SHORT RURAL | Asset Failure | LV | 1 | 133 | 0.00060633 | 0.00045526 | N
03/07/2016 | 08:28 | ZN180:PA18 | URBAN | Asset Failure | LV | 46 | 156 | 0.0049605 | 0.0031859 | N
03/07/2016 | 08:45 | ZN9252:PA28 | URBAN | Asset Failure | LV | 1 | 344 | 0.00023854 | 6.926e-05 | N
03/07/2016 | 14:05 | ZN1285:PA33 | URBAN | Asset Failure | LV | 1 | 310 | 0.00021436 | 6.926e-05 | N
04/07/2016 | 09:15 | ZN9118:PA13 | URBAN | Asset Failure | LV | 1 | 495 | 0.00034258 | 6.926e-05 | N
05/07/2016 | 09:19 | ZN15015:PA5 | URBAN | Asset Failure | LV | 1 | 101 | 6.9696e-05 | 6.9258e-05 | N
06/07/2016 | 10:17 | 508:82575 | SHORT RURAL | Asset Failure | LV | 1 | 770 | 0.0035058 | 0.00045533 | N
06/07/2016 | 12:45 | 512:48046 | SHORT RURAL | Asset Failure | LV | 1 | 121 | 0.00055132 | 0.00045533 | N
06/07/2016 | 13:47 | 202:34260 | URBAN | Asset Failure | LV | 1 | 222 | 0.00015407 | 6.9259e-05 | N
06/07/2016 | 15:13 | 256:80638 | URBAN | Asset Failure | LV | 1 | 240 | 0.00016591 | 6.9259e-05 | N
06/07/2016 | 17:57 | 528:83014 | SHORT RURAL | Asset Failure | LV | 1 | 311 | 0.0014139 | 0.00045533 | N
07/07/2016 | 08:36 | ZN2310:PA62 | URBAN | Asset Failure | LV | 5 | 204 | 0.0007063 | 0.00034623 | N
08/07/2016 | 09:26 | ZN1193:PA16 | URBAN | Asset Failure | LV | 1 | 663 | 0.00045919 | 6.9246e-05 | N
08/07/2016 | 08:50 | ZN1673:PA13 | URBAN | Asset Failure | LV | 21 | 205 | 0.0029803 | 0.0014542 | N
09/07/2016 | 17:51 | ZN9700:PA15 | URBAN | Asset Failure | LV | 2 | 438 | 0.00060596 | 0.0001385 | N
11/07/2016 | 16:15 | ZN262:PA41 | URBAN | Asset Failure | LV | 1 | 224 | 0.00015515 | 6.925e-05 | N
11/07/2016 | 16:36 | ZN10993:PA23 | URBAN | Asset Failure | LV | 1 | 113 | 7.8426e-05 | 6.925e-05 | N
11/07/2016 | 17:41 | ZN10993:PA22 | URBAN | Asset Failure | LV | 1 | 48 | 3.3367e-05 | 6.925e-05 | N
11/07/2016 | 18:15 | ZN2466:PA16 | URBAN | Asset Failure | LV | 3 | 180 | 0.00037395 | 0.00020775 | N
12/07/2016 | 12:27 | ZN12640:PA2 | URBAN | Asset Failure | LV | 1 | 352 | 0.00024379 | 6.9252e-05 | N
12/07/2016 | 13:20 | 258:80778 | URBAN | Asset Failure | LV | 1 | 80 | 5.5102e-05 | 6.9252e-05 | N
12/07/2016 | 13:42 | 232:11455 | SHORT RURAL | Asset Failure | LV | 2 | 665 | 0.0060548 | 0.0009105 | N
12/07/2016 | 16:59 | 258:80775 | URBAN | Asset Failure | LV | 3 | 131 | 0.00027216 | 0.00020776 | N
12/07/2016 | 22:20 | 261:81864 | URBAN | Asset Failure | LV | 1 | 90 | 6.235e-05 | 6.9252e-05 | N
13/07/2016 | 08:58 | ZN1850:PA13 | URBAN | Asset Failure | LV | 1 | 181 | 0.00012542 | 6.9254e-05 | N
13/07/2016 | 14:22 | ZN1788:PA37 | URBAN | Asset Failure | LV | 1 | 187 | 0.00012971 | 6.9254e-05 | N
13/07/2016 | 15:19 | ZN15008:PA9 | URBAN | Asset Failure | LV | 1 | 281 | 0.00019427 | 6.9254e-05 | N
14/07/2016 | 14:58 | 528:83024 | URBAN | Asset Failure | LV | 1 | 218 | 0.00015103 | 6.9255e-05 | N
14/07/2016 | 18:54 | ZN15011:PA6 | URBAN | Asset Failure | LV | 1 | 228 | 0.00015818 | 6.9255e-05 | N
18/07/2016 | 15:15 | ZN15012:PA4 | URBAN | Asset Failure | LV | 1 | 240 | 0.00016584 | 6.9243e-05 | N
20/07/2016 | 12:47 | ZN1290:PA12 | URBAN | Asset Failure | LV | 1 | 252 | 0.00017473 | 6.9227e-05 | N
20/07/2016 | 12:57 | ZN12630:PA21 | SHORT RURAL | Asset Failure | LV | 1 | 303 | 0.0013745 | 0.00045397 | N
20/07/2016 | 14:27 | ZN15008:PA7 | URBAN | Asset Failure | LV | 9 | 1,011 | 0.0062989 | 0.00062304 | N
20/07/2016 | 14:37 | ZN36300:PA11 | URBAN | Asset Failure | LV | 1 | 185 | 0.00012815 | 6.9227e-05 | N
20/07/2016 | 14:57 | ZN690:PA11 | URBAN | Asset Failure | LV | 1 | 182 | 0.0001263 | 6.9227e-05 | N
21/07/2016 | 08:18 | ZN12630:PA21 | SHORT RURAL | Asset Failure | LV | 1 | 884 | 0.0040145 | 0.00045398 | N
21/07/2016 | 16:03 | ZN15008:PA5 | URBAN | Asset Failure | LV | 1 | 215 | 0.00014913 | 6.9229e-05 | N
21/07/2016 | 16:03 | 504:48034 | URBAN | Asset Failure | LV | 2 | 223 | 0.00030876 | 0.00013846 | N
23/07/2016 | 15:30 | 264:81240 | SHORT RURAL | Asset Failure | LV | 1 | 496 | 0.0022524 | 0.00045391 | N
23/07/2016 | 15:26 | 235:2857 | SHORT RURAL | Asset Failure | LV | 1 | 500 | 0.0022715 | 0.00045391 | N
23/07/2016 | 23:16 | 232:11457 | SHORT RURAL | Asset Failure | LV | 1 | 113 | 0.00051481 | 0.00045391 | N
23/07/2016 | 23:54 | 238:34137 | SHORT RURAL | Asset Failure | LV | 2 | 451 | 0.0040905 | 0.00090782 | N
24/07/2016 | 17:24 | ZN36300:PA5 | URBAN | Asset Failure | LV | 1 | 305 | 0.00021143 | 6.9235e-05 | N
25/07/2016 | 15:00 | 232:11457 | SHORT RURAL | Asset Failure | LV | 1 | 597 | 0.0027098 | 0.00045391 | N
27/07/2016 | 07:58 | ZN180:PA34 | URBAN | Asset Failure | LV | 1 | 172 | 0.00011874 | 6.9237e-05 | N
28/07/2016 | 07:59 | ZN3288:PA45 46GHJ | CBD | Asset Failure | LV | 1 | 310 | 0.0099793 | 0.0032226 | N
28/07/2016 | 10:10 | ZN12610:PA13 | URBAN | Asset Failure | LV | 1 | 249 | 0.00017239 | 6.9227e-05 | N
29/07/2016 | 17:15 | ZN15005:PA8 | URBAN | Asset Failure | LV | 1 | 219 | 0.00015177 | 6.9228e-05 | N
31/07/2016 | 03:16 | 222:33601 | SHORT RURAL | Asset Failure | LV | 1 | 261 | 0.0011848 | 0.0004537 | N
31/07/2016 | 09:44 | 202:34260 | URBAN | Asset Failure | LV | 1 | 303 | 0.00020957 | 6.923e-05 | N
02/08/2016 | 14:14 | 225:13446 | URBAN | Asset Failure | LV | 1 | 225 | 0.00015602 | 6.923e-05 | N
02/08/2016 | 22:25 | ZN2602:PA15 | URBAN | Asset Failure | LV | 1 | 134 | 9.3091e-05 | 6.923e-05 | N
03/08/2016 | 08:58 | 513:48056 | SHORT RURAL | Asset Failure | LV | 1 | 55 | 0.00024727 | 0.00045371 | N
03/08/2016 | 09:33 | ZN10997:PA5 | URBAN | Asset Failure | LV | 1 | 326 | 0.00022595 | 6.9231e-05 | N
03/08/2016 | 10:04 | ZN9900:PA8 | URBAN | Asset Failure | LV | 1 | 567 | 0.00039235 | 6.9231e-05 | N
03/08/2016 | 11:25 | ZN2835:PA18 | URBAN | Asset Failure | LV | 1 | 588 | 0.00040717 | 6.9231e-05 | N
03/08/2016 | 11:27 | ZN15014:PA12 | SHORT RURAL | Asset Failure | LV | 1 | 1,292 | 0.0058621 | 0.00045371 | N
03/08/2016 | 15:40 | ZN9900:PA8 | URBAN | Asset Failure | LV | 1 | 231 | 0.00015966 | 6.9231e-05 | N
03/08/2016 | 16:05 | ZN1648:PA11 | URBAN | Asset Failure | LV | 7 | 264 | 0.0012794 | 0.00048462 | N
03/08/2016 | 20:13 | 210:8682 | URBAN | Asset Failure | LV | 2 | 827 | 0.0011447 | 0.00013846 | N
04/08/2016 | 06:46 | ZN2602:PA15 | URBAN | Asset Failure | LV | 1 | 554 | 0.00038311 | 6.9177e-05 | N
04/08/2016 | 07:59 | ZN10999:PA36 | URBAN | Asset Failure | LV | 1 | 91 | 6.2974e-05 | 6.9177e-05 | N
04/08/2016 | 17:17 | 232:33407 | SHORT RURAL | Asset Failure | LV | 1 | 98 | 0.00044516 | 0.00045463 | N
04/08/2016 | 19:01 | 233:82812 | SHORT RURAL | Asset Failure | LV | 1 | 200 | 0.00090949 | 0.00045463 | N
05/08/2016 | 08:20 | 238:34141 | SHORT RURAL | Asset Failure | LV | 1 | 115 | 0.00052229 | 0.00045463 | N
05/08/2016 | 08:49 | ZN263:PA33 34KLM | CBD | Asset Failure | LV | 1 | 630 | 0.02031 | 0.0032224 | N
05/08/2016 | 14:33 | ZN4545:PA29 | URBAN | Asset Failure | LV | 1 | 48 | 3.2905e-05 | 6.9177e-05 | N
05/08/2016 | 19:32 | ZN129:PA5 | URBAN | Asset Failure | LV | 1 | 386 | 0.00026733 | 6.9177e-05 | N
05/08/2016 | 20:15 | ZN15002:PA6 | URBAN | Asset Failure | LV | 1 | 943 | 0.00065226 | 6.9177e-05 | N
06/08/2016 | 09:06 | ZN847:PA44 | URBAN | Asset Failure | LV | 1 | 414 | 0.0002864 | 6.9178e-05 | N
06/08/2016 | 19:37 | 526:34636 | SHORT RURAL | Asset Failure | LV | 1 | 199 | 0.00090472 | 0.00045463 | N
07/08/2016 | 09:07 | ZN12610:PA18 | URBAN | Asset Failure | LV | 1 | 332 | 0.00022976 | 6.9178e-05 | N
07/08/2016 | 16:09 | ZN3425:PA28 | URBAN | Asset Failure | LV | 1 | 300 | 0.0002076 | 6.9178e-05 | N
08/08/2016 | 11:23 | 220:8687 | URBAN | Asset Failure | LV | 2 | 157 | 0.00021722 | 0.00013836 | N
08/08/2016 | 15:40 | 257:82000 | SHORT RURAL | Asset Failure | LV | 1 | 169 | 0.00076848 | 0.00045463 | N
09/08/2016 | 08:40 | ZN12620:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 222 | 0.0010136 | 0.00045611 | N
09/08/2016 | 09:19 | ZN12650:PA12 | URBAN | Asset Failure | LV | 1 | 131 | 9.0461e-05 | 6.9177e-05 | N
09/08/2016 | 12:04 | 507:80931 | URBAN | Asset Failure | LV | 1 | 265 | 0.00018363 | 6.9177e-05 | N
10/08/2016 | 09:21 | ZN15002:PA6 | URBAN | Asset Failure | LV | 1 | 219 | 0.0001512 | 6.9179e-05 | N
10/08/2016 | 12:11 | ZN14891:PA14 | URBAN | Asset Failure | LV | 1 | 259 | 0.00017898 | 6.9179e-05 | N
12/08/2016 | 07:23 | ZN15013:PA4 | URBAN | Asset Failure | LV | 1 | 156 | 0.00010807 | 6.9156e-05 | N
12/08/2016 | 09:54 | 504:48026 | SHORT RURAL | Asset Failure | LV | 1 | 115 | 0.00052464 | 0.00045601 | N
13/08/2016 | 11:56 | ZN12630:PA22 | SHORT RURAL | Asset Failure | LV | 1 | 304 | 0.0013846 | 0.00045602 | N
13/08/2016 | 16:36 | ZN12640:PA7 | URBAN | Asset Failure | LV | 2 | 144 | 0.00019917 | 0.00013831 | N
15/08/2016 | 17:15 | ZN9700:PA17 | URBAN | Asset Failure | LV | 1 | 163 | 0.00011305 | 6.9157e-05 | N
17/08/2016 | 17:04 | ZN2310:PA61 | URBAN | Asset Failure | LV | 1 | 322 | 0.00022298 | 6.916e-05 | N
18/08/2016 | 15:35 | ZN3155:PA23 | URBAN | Asset Failure | LV | 1 | 235 | 0.00016274 | 6.9379e-05 | N
22/08/2016 | 11:00 | 504:48033 | SHORT RURAL | Asset Failure | LV | 1 | 389 | 0.0018034 | 0.00046353 | N
22/08/2016 | 14:16 | ZN14143:PA17 | SHORT RURAL | Asset Failure | LV | 1 | 1,094 | 0.0050697 | 0.00046353 | N
22/08/2016 | 14:44 | ZN9252:PA27 | URBAN | Asset Failure | LV | 1 | 166 | 0.00011502 | 6.938e-05 | N
24/08/2016 | 11:22 | ZN2196:PA3 | SHORT RURAL | Asset Failure | LV | 1 | 37 | 0.00016971 | 0.00045683 | N
25/08/2016 | 07:14 | 513:48059 | SHORT RURAL | Asset Failure | LV | 1 | 190 | 0.00086982 | 0.00045684 | N
25/08/2016 | 07:19 | ZN9245:PA34 | URBAN | Asset Failure | LV | 2 | 431 | 0.00059502 | 0.00013819 | N
25/08/2016 | 08:59 | ZN180:PA27 | URBAN | Asset Failure | LV | 55 | 181 | 0.0068783 | 0.0038002 | N
26/08/2016 | 09:39 | 523:33508 | SHORT RURAL | Asset Failure | LV | 1 | 84 | 0.00038313 | 0.00045684 | N
27/08/2016 | 09:45 | 261:81886 | URBAN | Asset Failure | LV | 1 | 429 | 0.00029651 | 6.9059e-05 | N
29/08/2016 | 17:30 | ZN9245:PA44 | URBAN | Asset Failure | LV | 54 | 316 | 0.011774 | 0.0037292 | N
29/08/2016 | 19:59 | ZN180:PA18 | URBAN | Asset Failure | LV | 88 | 156 | 0.0094684 | 0.0060773 | N
30/08/2016 | 14:27 | ZN36200:PA8 | SHORT RURAL | Asset Failure | LV | 1 | 243 | 0.0011074 | 0.00045662 | N
31/08/2016 | 13:43 | 232:11454 | SHORT RURAL | Asset Failure | LV | 1 | 296 | 0.0013531 | 0.00045647 | N
01/09/2016 | 15:13 | 509:33397 | SHORT RURAL | Asset Failure | LV | 1 | 152 | 0.00069346 | 0.00045647 | N
02/09/2016 | 14:36 | ZN3425:PA12 | URBAN | Asset Failure | LV | 1 | 164 | 0.00011316 | 6.904e-05 | N
03/09/2016 | 12:52 | ZN35800:PA9 | URBAN | Asset Failure | LV | 1 | 427 | 0.00029449 | 6.9041e-05 | N
03/09/2016 | 13:04 | ZN12660:PA6 | SHORT RURAL | Asset Failure | LV | 1 | 284 | 0.0012946 | 0.00045648 | N
03/09/2016 | 14:47 | 206:34440 | URBAN | Asset Failure | LV | 1 | 479 | 0.0003309 | 6.9041e-05 | N
03/09/2016 | 15:49 | 230:81434 | URBAN | Asset Failure | LV | 1 | 250 | 0.00017274 | 6.9041e-05 | N
03/09/2016 | 17:50 | 264:81240 | SHORT RURAL | Asset Failure | LV | 1 | 249 | 0.0011379 | 0.00045648 | N
03/09/2016 | 17:54 | 224:80332 | URBAN | Asset Failure | LV | 1 | 297 | 0.00020492 | 6.9041e-05 | N
03/09/2016 | 21:16 | 256:80650 | URBAN | Asset Failure | LV | 1 | 850 | 0.00058713 | 6.9041e-05 | N
05/09/2016 | 15:01 | 813:89061 | LONG RURAL | Asset Failure | LV | 1 | 132 | 0.047076 | 0.035663 | N
06/09/2016 | 20:51 | 511:29877 | SHORT RURAL | Asset Failure | LV | 1 | 243 | 0.0011114 | 0.00045648 | N
07/09/2016 | 05:39 | ZN180:PA22 | URBAN | Asset Failure | LV | 2 | 292 | 0.00040363 | 0.00013809 | N
07/09/2016 | 13:17 | ZN9252:PA28 | URBAN | Asset Failure | LV | 1 | 90 | 6.2288e-05 | 6.9043e-05 | N
19/09/2016 | 11:54 | ZN3288:PA43 44KLM | CBD | Asset Failure | LV | 1 | 185 | 0.0059674 | 0.0032233 | N
08/09/2016 | 10:25 | 216:10727 | SHORT RURAL | Asset Failure | LV | 1 | 85 | 0.00038497 | 0.00045451 | N
08/09/2016 | 12:40 | 512:48046 | SHORT RURAL | Asset Failure | LV | 1 | 349 | 0.0015871 | 0.00045451 | N
09/09/2016 | 14:36 | 511:29880 | URBAN | Asset Failure | LV | 1 | 180 | 0.00012449 | 6.9058e-05 | N
10/09/2016 | 10:17 | ZN15006:PA13 | URBAN | Asset Failure | LV | 1 | 192 | 0.00013265 | 6.9061e-05 | N
10/09/2016 | 15:24 | ZN9118:PA15 | URBAN | Asset Failure | LV | 1 | 267 | 0.00018425 | 6.9061e-05 | N
10/09/2016 | 17:09 | ZN12640:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 211 | 0.00095885 | 0.0004545 | N
11/09/2016 | 16:20 | ZN2835:PA32 | URBAN | Asset Failure | LV | 1 | 96 | 6.6196e-05 | 6.9062e-05 | N
11/09/2016 | 16:45 | ZN72:PA23 | URBAN | Asset Failure | LV | 1 | 71 | 4.8723e-05 | 6.9062e-05 | N
11/09/2016 | 17:00 | ZN72:PA31 | URBAN | Asset Failure | LV | 1 | 56 | 3.8916e-05 | 6.9062e-05 | N
12/09/2016 | 19:10 | ZN931:PA26 | URBAN | Asset Failure | LV | 1 | 829 | 0.0005726 | 6.9062e-05 | N
13/09/2016 | 16:20 | ZN15014:PA11 | URBAN | Asset Failure | LV | 38 | 265 | 0.0069504 | 0.0026244 | N
14/09/2016 | 05:49 | ZN2835:PA30 | URBAN | Asset Failure | LV | 1 | 191 | 0.0001316 | 6.9066e-05 | N
15/09/2016 | 15:57 | 513:48052 | URBAN | Asset Failure | LV | 1 | 110 | 7.5796e-05 | 6.9052e-05 | N
15/09/2016 | 17:01 | ZN9534:PA17 | URBAN | Asset Failure | LV | 1 | 252 | 0.00017433 | 6.9052e-05 | N
16/09/2016 | 07:17 | ZN12640:PA18 | SHORT RURAL | Asset Failure | LV | 1 | 312 | 0.0014191 | 0.00045435 | N
16/09/2016 | 15:56 | ZN14143:PA5 | URBAN | Asset Failure | LV | 1 | 316 | 0.00021803 | 6.9052e-05 | N
19/09/2016 | 12:16 | ZN262:PA31 | URBAN | Asset Failure | LV | 16 | 223 | 0.0024651 | 0.001105 | N
20/09/2016 | 18:06 | 813:89065 | URBAN | Asset Failure | LV | 1 | 105 | 7.2852e-05 | 6.9065e-05 | N
21/09/2016 | 13:26 | ZN10995:PA1 | URBAN | Asset Failure | LV | 1 | 85 | 5.8672e-05 | 6.9066e-05 | N
21/09/2016 | 16:26 | ZN12570:PA37 | SHORT RURAL | Asset Failure | LV | 1 | 1,180 | 0.0053558 | 0.00045404 | N
22/09/2016 | 08:20 | ZN3922:PA7 | URBAN | Asset Failure | LV | 7 | 430 | 0.0020783 | 0.00048332 | N
22/09/2016 | 15:27 | ZN15008:PA10 | URBAN | Asset Failure | LV | 1 | 97 | 6.7204e-05 | 6.9045e-05 | N
23/09/2016 | 16:22 | 203:8086 | URBAN | Asset Failure | LV | 1 | 195 | 0.00013485 | 6.9045e-05 | N
24/09/2016 | 17:11 | ZN188:PA44 | URBAN | Asset Failure | LV | 1 | 346 | 0.00023904 | 6.9046e-05 | N
25/09/2016 | 10:37 | ZN15006:PA4 | URBAN | Asset Failure | LV | 1 | 386 | 0.00026642 | 6.9046e-05 | N
26/09/2016 | 09:53 | ZN9037:PA16 | URBAN | Asset Failure | LV | 2 | 335 | 0.00046245 | 0.00013809 | N
27/09/2016 | 17:57 | ZN15005:PA4 | URBAN | Asset Failure | LV | 1 | 172 | 0.00011901 | 6.9047e-05 | N
28/09/2016 | 06:35 | ZN2602:PA10 | URBAN | Asset Failure | LV | 1 | 204 | 0.00014107 | 6.9049e-05 | N
29/09/2016 | 06:44 | ZN15008:PA9 | URBAN | Asset Failure | LV | 1 | 315 | 0.00021746 | 6.9028e-05 | N
30/09/2016 | 20:00 | ZN12580:PA1 | URBAN | Asset Failure | LV | 1 | 206 | 0.00014217 | 6.9028e-05 | N
01/10/2016 | 11:45 | ZN35800:PA22 | URBAN | Asset Failure | LV | 1 | 550 | 0.00037957 | 6.9059e-05 | N
01/10/2016 | 14:47 | 810:74062 | SHORT RURAL | Asset Failure | LV | 1 | 161 | 0.00073017 | 0.00045268 | N
03/10/2016 | 09:41 | 227:13020 | SHORT RURAL | Asset Failure | LV | 1 | 169 | 0.00076503 | 0.00045268 | N
04/10/2016 | 06:41 | ZN35600:PA7 | URBAN | Asset Failure | LV | 1 | 228 | 0.00015767 | 6.9059e-05 | N
04/10/2016 | 12:46 | 502:48010 | SHORT RURAL | Asset Failure | LV | 1 | 314 | 0.0014207 | 0.00045268 | N
04/10/2016 | 13:57 | ZN12620:PA7 | URBAN | Asset Failure | LV | 1 | 353 | 0.00024361 | 6.9059e-05 | N
04/10/2016 | 18:00 | 504:48031 | SHORT RURAL | Asset Failure | LV | 1 | 453 | 0.0020524 | 0.00045268 | N
04/10/2016 | 18:43 | ZN3155:PA19 | URBAN | Asset Failure | LV | 1 | 197 | 0.00013594 | 6.9059e-05 | N
05/10/2016 | 08:11 | ZN15002:PA2 | URBAN | Asset Failure | LV | 1 | 1,432 | 0.0009886 | 6.9061e-05 | N
05/10/2016 | 14:46 | ZN1068:PA22 | URBAN | Asset Failure | LV | 1 | 163 | 0.00011281 | 6.9061e-05 | N
05/10/2016 | 15:52 | ZN12650:PA2 | URBAN | Asset Failure | LV | 1 | 1,328 | 0.00091701 | 6.9061e-05 | N
06/10/2016 | 13:33 | ZN12650:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 237 | 0.0010719 | 0.00045269 | N
07/10/2016 | 13:16 | ZN384:PA70 | URBAN | Asset Failure | LV | 1 | 333 | 0.00022998 | 6.9034e-05 | N
08/10/2016 | 08:59 | ZN14144:PA1 | URBAN | Asset Failure | LV | 1 | 257 | 0.0001774 | 6.9085e-05 | N
11/10/2016 | 12:03 | ZN4545:PA31 | URBAN | Asset Failure | LV | 1 | 57 | 3.9161e-05 | 6.9046e-05 | N
11/10/2016 | 12:26 | ZN10999:PA32 | URBAN | Asset Failure | LV | 1 | 1,284 | 0.00088666 | 6.9046e-05 | N
11/10/2016 | 18:38 | 216:10729 | URBAN | Asset Failure | LV | 1 | 86 | 5.9553e-05 | 6.9046e-05 | N
12/10/2016 | 10:41 | ZN2602:PA30 | URBAN | Asset Failure | LV | 1 | 258 | 0.00017827 | 6.9048e-05 | N
14/10/2016 | 13:55 | ZN15014:PA12 | SHORT RURAL | Asset Failure | LV | 1 | 382 | 0.0017252 | 0.00045199 | N
14/10/2016 | 15:23 | 202:34260 | URBAN | Asset Failure | LV | 1 | 188 | 0.00012994 | 6.914e-05 | N
17/10/2016 | 11:43 | ZN35900:PA24 | URBAN | Asset Failure | LV | 1 | 587 | 0.0004051 | 6.9069e-05 | N
17/10/2016 | 12:43 | 203:8085 | URBAN | Asset Failure | LV | 1 | 167 | 0.000115 | 6.9069e-05 | N
17/10/2016 | 17:08 | ZN3472:PA20 | URBAN | Asset Failure | LV | 1 | 289 | 0.00019984 | 6.9069e-05 | N
17/10/2016 | 18:37 | ZN4545:PA40 | URBAN | Asset Failure | LV | 1 | 259 | 0.00017909 | 6.9069e-05 | N
18/10/2016 | 11:47 | ZN1290:PA13 | URBAN | Asset Failure | LV | 1 | 151 | 0.00010398 | 6.9073e-05 | N
18/10/2016 | 13:59 | ZN15013:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 196 | 0.00088205 | 0.00045041 | N
18/10/2016 | 15:02 | ZN187:PA26 | URBAN | Asset Failure | LV | 1 | 1,108 | 0.00076518 | 6.9073e-05 | N
19/10/2016 | 08:42 | ZN1285:PA31 | URBAN | Asset Failure | LV | 1 | 107 | 7.4071e-05 | 6.9075e-05 | N
19/10/2016 | 12:10 | ZN2835:PA30 | URBAN | Asset Failure | LV | 1 | 200 | 0.00013806 | 6.9075e-05 | N
19/10/2016 | 18:16 | ZN2835:PA33 | URBAN | Asset Failure | LV | 1 | 269 | 0.0001859 | 6.9075e-05 | N
20/10/2016 | 18:05 | 205:12210 | URBAN | Asset Failure | LV | 1 | 116 | 8.0349e-05 | 6.9078e-05 | N
21/10/2016 | 12:37 | ZN12600:PA3 | URBAN | Asset Failure | LV | 1 | 382 | 0.00026527 | 6.942e-05 | N
21/10/2016 | 22:44 | ZN35600:PA1 | URBAN | Asset Failure | LV | 1 | 669 | 0.00046436 | 6.942e-05 | N
22/10/2016 | 08:55 | 528:83019 | SHORT RURAL | Asset Failure | LV | 1 | 281 | 0.0012668 | 0.00045023 | N
22/10/2016 | 18:38 | ZN1068:PA18 | URBAN | Asset Failure | LV | 1 | 1,218 | 0.00084095 | 6.9057e-05 | N
24/10/2016 | 10:42 | ZN384:PA43 | URBAN | Asset Failure | LV | 1 | 408 | 0.00028152 | 6.9058e-05 | N
24/10/2016 | 17:29 | ZN35400:PA95 | URBAN | Asset Failure | LV | 1 | 327 | 0.0002257 | 6.9058e-05 | N
24/10/2016 | 18:53 | 507:80914 | SHORT RURAL | Asset Failure | LV | 1 | 36 | 0.00016126 | 0.00045023 | N
24/10/2016 | 19:53 | ZN12640:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 187 | 0.00084058 | 0.00045023 | N
25/10/2016 | 11:59 | ZN3155:PA29 | URBAN | Asset Failure | LV | 1 | 1,260 | 0.00087037 | 6.9059e-05 | N
29/10/2016 | 16:29 | ZN129:PA3 | URBAN | Asset Failure | LV | 1 | 273 | 0.00018823 | 6.9038e-05 | N
31/10/2016 | 09:00 | ZN15012:PA2 | URBAN | Asset Failure | LV | 1 | 90 | 6.1962e-05 | 6.9038e-05 | N
31/10/2016 | 14:56 | 224:80341 | URBAN | Asset Failure | LV | 1 | 322 | 0.00022261 | 6.9038e-05 | N
02/11/2016 | 15:16 | ZN2310:PA65 | URBAN | Asset Failure | LV | 1 | 464 | 0.00032066 | 6.9044e-05 | N
02/11/2016 | 15:17 | ZN2310:PA62 | URBAN | Asset Failure | LV | 1 | 464 | 0.0003204 | 6.9044e-05 | N
02/11/2016 | 15:20 | ZN2310:PA65 | URBAN | Asset Failure | LV | 1 | 461 | 0.00031819 | 6.9044e-05 | N
05/11/2016 | 12:13 | ZN1285:PA33 | URBAN | Asset Failure | LV | 1 | 1,091 | 0.00075305 | 6.9027e-05 | N
06/11/2016 | 12:07 | ZN1285:PA33 | URBAN | Asset Failure | LV | 1 | 218 | 0.00015079 | 6.9028e-05 | N
07/11/2016 | 13:32 | ZN10994:PA11 | URBAN | Asset Failure | LV | 3 | 498 | 0.001031 | 0.00020708 | N
08/11/2016 | 14:19 | ZN3672:PA13 | URBAN | Asset Failure | LV | 1 | 1,001 | 0.00069071 | 6.9029e-05 | N
09/11/2016 | 00:41 | ZN36100:PA20 | URBAN | Asset Failure | LV | 1 | 829 | 0.00057209 | 6.9031e-05 | N
09/11/2016 | 10:21 | ZN9900:PA1 | URBAN | Asset Failure | LV | 1 | 338 | 0.00023349 | 6.9031e-05 | N
09/11/2016 | 13:16 | ZN3672:PA44 | URBAN | Asset Failure | LV | 1 | 223 | 0.00015395 | 6.9031e-05 | N
09/11/2016 | 15:04 | ZN15009:PA5 | URBAN | Asset Failure | LV | 1 | 985 | 0.00068026 | 6.9031e-05 | N
10/11/2016 | 08:12 | 513:48059 | SHORT RURAL | Asset Failure | LV | 1 | 108 | 0.00048384 | 0.00045001 | N
13/11/2016 | 12:16 | 217:33612 | URBAN | Asset Failure | LV | 1 | 138 | 9.5143e-05 | 6.9011e-05 | N
13/11/2016 | 14:16 | 227:13015 | SHORT RURAL | Asset Failure | LV | 1 | 463 | 0.0020829 | 0.00044977 | N
13/11/2016 | 19:00 | ZN4545:PA27 | URBAN | Asset Failure | LV | 9 | 180 | 0.0011151 | 0.0006211 | N
13/11/2016 | 19:04 | 206:34440 | URBAN | Asset Failure | LV | 1 | 161 | 0.00011105 | 6.9011e-05 | N
14/11/2016 | 09:12 | ZN398:PA9 | URBAN | Asset Failure | LV | 1 | 198 | 0.00013633 | 6.9011e-05 | N
14/11/2016 | 13:57 | ZN262:PA19 | URBAN | Asset Failure | LV | 1 | 345 | 0.00023809 | 6.9011e-05 | N
14/11/2016 | 18:07 | ZN7900:PA11 | URBAN | Asset Failure | LV | 2 | 138 | 0.00018978 | 0.00013802 | N
14/11/2016 | 19:00 | ZN9700:PA24 | URBAN | Asset Failure | LV | 1 | 209 | 0.00014452 | 6.9011e-05 | N
15/11/2016 | 14:48 | ZN35900:PA25 | SHORT RURAL | Asset Failure | LV | 1 | 300 | 0.0013486 | 0.00044977 | N
17/11/2016 | 08:50 | ZN1610:PA26 | URBAN | Asset Failure | LV | 1 | 340 | 0.0002345 | 6.8991e-05 | N
17/11/2016 | 12:23 | ZN2835:PA32 | URBAN | Asset Failure | LV | 1 | 187 | 0.00012882 | 6.8991e-05 | N
19/11/2016 | 11:08 | ZN35600:PA20 | URBAN | Asset Failure | LV | 1 | 321 | 0.00022179 | 6.8993e-05 | N
20/11/2016 | 17:47 | ZN15006:PA16 | URBAN | Asset Failure | LV | 1 | 216 | 0.0001489 | 6.8995e-05 | N
20/11/2016 | 18:12 | ZN12610:PA24 | URBAN | Asset Failure | LV | 1 | 289 | 0.00019923 | 6.8995e-05 | N
21/11/2016 | 12:53 | ZN9900:PA8 | URBAN | Asset Failure | LV | 1 | 1,207 | 0.00083246 | 6.8995e-05 | N
21/11/2016 | 16:34 | ZN874:PA17 | URBAN | Asset Failure | LV | 1 | 146 | 0.00010047 | 6.8995e-05 | N
23/11/2016 | 06:53 | ZN10994:PA1 | URBAN | Asset Failure | LV | 1 | 456 | 0.00031464 | 6.8998e-05 | N
23/11/2016 | 09:58 | ZN12610:PA13 | URBAN | Asset Failure | LV | 1 | 122 | 8.4085e-05 | 6.8998e-05 | N
23/11/2016 | 12:13 | 504:48034 | URBAN | Asset Failure | LV | 1 | 76 | 5.2668e-05 | 6.8998e-05 | N
23/11/2016 | 14:27 | ZN12570:PA33 | SHORT RURAL | Asset Failure | LV | 1 | 243 | 0.0010908 | 0.00044965 | N
23/11/2016 | 15:15 | ZN9118:PA13 | URBAN | Asset Failure | LV | 1 | 195 | 0.0001342 | 6.8998e-05 | N
25/11/2016 | 11:16 | ZN2602:PA31 | URBAN | Asset Failure | LV | 1 | 523 | 0.00036097 | 6.8978e-05 | N
25/11/2016 | 14:33 | ZN2602:PA31 | URBAN | Asset Failure | LV | 1 | 327 | 0.00022523 | 6.8978e-05 | N
26/11/2016 | 06:53 | ZN10995:PA7 | URBAN | Asset Failure | LV | 1 | 217 | 0.00014945 | 6.9028e-05 | N
26/11/2016 | 15:42 | ZN15010:PA7 | URBAN | Asset Failure | LV | 1 | 241 | 0.00016621 | 6.9028e-05 | N
28/11/2016 | 02:43 | ZN180:PA33 | URBAN | Asset Failure | LV | 1 | 752 | 0.00051891 | 6.9028e-05 | N
28/11/2016 | 14:19 | ZN35600:PA19 | URBAN | Asset Failure | LV | 1 | 190 | 0.00013123 | 6.9028e-05 | N
30/11/2016 | 03:57 | ZN9035:PA7 | URBAN | Asset Failure | LV | 1 | 242 | 0.00016722 | 6.9028e-05 | N
30/11/2016 | 23:27 | 524:33574 | SHORT RURAL | Asset Failure | LV | 1 | 1,207 | 0.0054263 | 0.00044945 | N
01/12/2016 | 11:34 | ZN12570:PA35 | URBAN | Asset Failure | LV | 1 | 173 | 0.0001192 | 6.9009e-05 | N
01/12/2016 | 19:06 | 507:80914 | SHORT RURAL | Asset Failure | LV | 1 | 147 | 0.0006584 | 0.00044927 | N
02/12/2016 | 06:02 | 523:33508 | SHORT RURAL | Asset Failure | LV | 1 | 73 | 0.00032767 | 0.00044927 | N
02/12/2016 | 07:36 | ZN3472:PA30 | URBAN | Asset Failure | LV | 1 | 413 | 0.00028524 | 6.9009e-05 | N
02/12/2016 | 14:10 | ZN1610:PA23 | URBAN | Asset Failure | LV | 1 | 1,170 | 0.00080764 | 6.9009e-05 | N
02/12/2016 | 17:13 | ZN9700:PA24 | URBAN | Asset Failure | LV | 1 | 551 | 0.00038032 | 6.9009e-05 | N
02/12/2016 | 17:56 | 217:33611 | URBAN | Asset Failure | LV | 1 | 379 | 0.00026127 | 6.9009e-05 | N
05/12/2016 | 08:53 | ZN15009:PA11 | URBAN | Asset Failure | LV | 1 | 342 | 0.00023583 | 6.8959e-05 | N
05/12/2016 | 16:04 | ZN12640:PA15 | URBAN | Asset Failure | LV | 1 | 206 | 0.00014201 | 6.8959e-05 | N
05/12/2016 | 16:53 | ZN15014:PA12 | SHORT RURAL | Asset Failure | LV | 1 | 382 | 0.0017164 | 0.00044927 | N
05/12/2016 | 22:41 | ZN180:PA9 | URBAN | Asset Failure | LV | 1 | 889 | 0.0006129 | 6.8959e-05 | N
06/12/2016 | 09:52 | ZN847:PA47 | SHORT RURAL | Asset Failure | LV | 1 | 97 | 0.00043759 | 0.00044927 | N
06/12/2016 | 10:05 | 213:33770 | URBAN | Asset Failure | LV | 1 | 208 | 0.00014311 | 6.8961e-05 | N
06/12/2016 | 16:05 | 217:33611 | URBAN | Asset Failure | LV | 1 | 404 | 0.00027876 | 6.8961e-05 | N
07/12/2016 | 12:12 | ZN180:PA7 | URBAN | Asset Failure | LV | 1 | 167 | 0.00011537 | 6.8962e-05 | N
07/12/2016 | 15:44 | 512:48049 | SHORT RURAL | Asset Failure | LV | 1 | 111 | 0.00049788 | 0.00044928 | N
08/12/2016 | 15:41 | ZN15006:PA16 | URBAN | Asset Failure | LV | 1 | 300 | 0.00020654 | 6.8935e-05 | N
09/12/2016 | 13:41 | 233:82821 | SHORT RURAL | Asset Failure | LV | 1 | 573 | 0.0025758 | 0.00044934 | N
09/12/2016 | 16:59 | ZN15005:PA2 | URBAN | Asset Failure | LV | 1 | 259 | 0.00017888 | 6.8938e-05 | N
09/12/2016 | 20:54 | ZN3472:PA22 | URBAN | Asset Failure | LV | 1 | 266 | 0.00018316 | 6.8938e-05 | N
10/12/2016 | 08:43 | ZN4545:PA27 | URBAN | Asset Failure | LV | 2 | 977 | 0.0013471 | 0.00013788 | N
10/12/2016 | 08:56 | 813:89061 | LONG RURAL | Asset Failure | LV | 1 | 77 | 0.027376 | 0.0356 | N
10/12/2016 | 18:28 | ZN9245:PA13 | URBAN | Asset Failure | LV | 1 | 266 | 0.00018354 | 6.8939e-05 | N
12/12/2016 | 18:33 | ZN12620:PA3 | URBAN | Asset Failure | LV | 1 | 237 | 0.00016366 | 6.8941e-05 | N
13/12/2016 | 09:08 | ZN12640:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 406 | 0.001825 | 0.00044935 | N
13/12/2016 | 12:23 | 243:80080 | SHORT RURAL | Asset Failure | LV | 1 | 89 | 0.00039805 | 0.00044935 | N
13/12/2016 | 18:15 | ZN35500:PA27 | URBAN | Asset Failure | LV | 1 | 241 | 0.00016618 | 6.8942e-05 | N
14/12/2016 | 10:09 | ZN340:PA23 | URBAN | Asset Failure | LV | 1 | 440 | 0.00030364 | 6.8943e-05 | N
14/12/2016 | 12:38 | ZN12620:PA7 | URBAN | Asset Failure | LV | 1 | 552 | 0.00038032 | 6.8943e-05 | N
14/12/2016 | 13:43 | ZN1788:PA30 | URBAN | Asset Failure | LV | 1 | 167 | 0.00011503 | 6.8943e-05 | N
14/12/2016 | 15:14 | 220:8691 | URBAN | Asset Failure | LV | 1 | 150 | 0.00010351 | 6.8943e-05 | N
14/12/2016 | 15:43 | ZN15006:PA8 | URBAN | Asset Failure | LV | 1 | 293 | 0.00020196 | 6.8943e-05 | N
14/12/2016 | 18:02 | ZN14144:PA2 | SHORT RURAL | Asset Failure | LV | 1 | 328 | 0.0014721 | 0.00044936 | N
14/12/2016 | 20:30 | ZN180:PA41 | URBAN | Asset Failure | LV | 1 | 167 | 0.00011515 | 6.8943e-05 | N
15/12/2016 | 07:11 | ZN3425:PA43 | URBAN | Asset Failure | LV | 1 | 108 | 7.4473e-05 | 6.8924e-05 | N
15/12/2016 | 09:08 | ZN1850:PA4 | URBAN | Asset Failure | LV | 1 | 292 | 0.00020109 | 6.8924e-05 | N
15/12/2016 | 12:20 | ZN1193:PA21 | URBAN | Asset Failure | LV | 1 | 130 | 8.9291e-05 | 6.8924e-05 | N
15/12/2016 | 18:22 | ZN9035:PA4 | URBAN | Asset Failure | LV | 1 | 98 | 6.7442e-05 | 6.8924e-05 | N
16/12/2016 | 13:43 | ZN690:PA18 | URBAN | Asset Failure | LV | 2 | 527 | 0.00072595 | 0.00013785 | N
16/12/2016 | 22:18 | 221:11893 | URBAN | Asset Failure | LV | 1 | 163 | 0.00011218 | 6.8926e-05 | N
17/12/2016 | 12:05 | 214:8670 | URBAN | Asset Failure | LV | 1 | 453 | 0.00031227 | 6.8927e-05 | N
17/12/2016 | 12:07 | 807:74181 | SHORT RURAL | Asset Failure | LV | 1 | 170 | 0.0007648 | 0.00044909 | N
17/12/2016 | 15:48 | 507:80923 | SHORT RURAL | Asset Failure | LV | 1 | 197 | 0.0008835 | 0.00044909 | N
18/12/2016 | 09:28 | ZN2835:PA15 | URBAN | Asset Failure | LV | 1 | 1,211 | 0.00083486 | 6.8926e-05 | N
18/12/2016 | 12:40 | ZN9900:PA17 | URBAN | Asset Failure | LV | 1 | 1,148 | 0.00079119 | 6.8926e-05 | N
18/12/2016 | 13:41 | ZN4545:PA32 | URBAN | Asset Failure | LV | 1 | 195 | 0.00013452 | 6.8926e-05 | N
19/12/2016 | 11:57 | ZN12610:PA11 | URBAN | Asset Failure | LV | 1 | 93 | 6.3964e-05 | 6.8927e-05 | N
19/12/2016 | 13:53 | ZN36300:PA1 | URBAN | Asset Failure | LV | 1 | 386 | 0.00026623 | 6.8927e-05 | N
20/12/2016 | 07:18 | ZN15001:PA15 | URBAN | Asset Failure | LV | 1 | 311 | 0.00021444 | 6.8927e-05 | N
20/12/2016 | 10:20 | ZN15014:PA12 | SHORT RURAL | Asset Failure | LV | 1 | 249 | 0.0011196 | 0.00044908 | N
21/12/2016 | 08:50 | ZN4545:PA41 | SHORT RURAL | Asset Failure | LV | 1 | 235 | 0.0010546 | 0.0004491 | N
21/12/2016 | 11:23 | 205:12205 | SHORT RURAL | Asset Failure | LV | 1 | 667 | 0.002997 | 0.0004491 | N
23/12/2016 | 09:34 | ZN2466:PA41 | URBAN | Asset Failure | LV | 1 | 595 | 0.00040995 | 6.8908e-05 | N
23/12/2016 | 15:59 | ZN2466:PA41 | URBAN | Asset Failure | LV | 1 | 209 | 0.00014428 | 6.8908e-05 | N
24/12/2016 | 10:26 | 811:74234 | SHORT RURAL | Asset Failure | LV | 1 | 220 | 0.00098968 | 0.00044897 | N
24/12/2016 | 18:44 | ZN3425:PA35 | URBAN | Asset Failure | LV | 1 | 435 | 0.00030002 | 6.8908e-05 | N
24/12/2016 | 19:18 | ZN187:PA8 | URBAN | Asset Failure | LV | 1 | 671 | 0.0004624 | 6.8908e-05 | N
24/12/2016 | 20:10 | ZN2568:PA22 | URBAN | Asset Failure | LV | 1 | 288 | 0.00019871 | 6.8908e-05 | N
26/12/2016 | 11:40 | 807:74184 | SHORT RURAL | Asset Failure | LV | 1 | 224 | 0.0010038 | 0.00044897 | N
26/12/2016 | 14:09 | ZN2400:PA21 | URBAN | Asset Failure | LV | 1 | 1,404 | 0.00096748 | 6.8909e-05 | N
27/12/2016 | 21:06 | ZN901:PA19 | URBAN | Asset Failure | LV | 1 | 743 | 0.00051219 | 6.8909e-05 | N
29/12/2016 | 20:32 | ZN14892:PA8 | SHORT RURAL | Asset Failure | LV | 1 | 1,048 | 0.0047033 | 0.00044897 | N
30/12/2016 | 15:55 | ZN15011:PA4 | URBAN | Asset Failure | LV | 1 | 1,019 | 0.00070201 | 6.891e-05 | N
30/12/2016 | 16:09 | 239:82133 | URBAN | Asset Failure | LV | 1 | 200 | 0.00013802 | 6.891e-05 | N
31/12/2016 | 07:32 | ZN2400:PA15 | SHORT RURAL | Asset Failure | LV | 1 | 379 | 0.0017037 | 0.00044898 | N
31/12/2016 | 13:03 | 216:10728 | SHORT RURAL | Asset Failure | LV | 1 | 208 | 0.00093171 | 0.00044898 | N
31/12/2016 | 13:19 | 513:48059 | SHORT RURAL | Asset Failure | LV | 1 | 129 | 0.00058083 | 0.00044898 | N
01/01/2017 | 05:41 | ZN129:PA9 | URBAN | Asset Failure | LV | 1 | 39 | 2.6703e-05 | 6.8911e-05 | N
01/01/2017 | 16:48 | ZN9118:PA6 | URBAN | Asset Failure | LV | 1 | 161 | 0.00011114 | 6.8911e-05 | N
01/01/2017 | 19:07 | ZN9118:PA6 | URBAN | Asset Failure | LV | 1 | 139 | 9.5752e-05 | 6.8911e-05 | N
01/01/2017 | 21:16 | ZN9534:PA17 | URBAN | Asset Failure | LV | 1 | 1,483 | 0.001022 | 6.8911e-05 | N
03/01/2017 | 09:32 | ZN10997:PA8 | URBAN | Asset Failure | LV | 1 | 219 | 0.00015125 | 6.8911e-05 | N
03/01/2017 | 09:33 | ZN10997:PA8 | URBAN | Asset Failure | LV | 1 | 218 | 0.00015024 | 6.8911e-05 | N
03/01/2017 | 09:36 | ZN35800:PA10 | URBAN | Asset Failure | LV | 1 | 1,014 | 0.00069848 | 6.8911e-05 | N
03/01/2017 | 16:07 | ZN2602:PA42 | URBAN | Asset Failure | LV | 1 | 345 | 0.00023764 | 6.8911e-05 | N
04/01/2017 | 09:15 | ZN262:PA7 | URBAN | Asset Failure | LV | 1 | 348 | 0.00023999 | 6.8912e-05 | N
04/01/2017 | 19:00 | ZN15006:PA2 | URBAN | Asset Failure | LV | 1 | 134 | 9.2422e-05 | 6.8912e-05 | N
04/01/2017 | 22:15 | ZN9118:PA17 | URBAN | Asset Failure | LV | 1 | 433 | 0.00029861 | 6.8912e-05 | N
05/01/2017 | 08:02 | ZN15006:PA8 | URBAN | Asset Failure | LV | 19 | 327 | 0.0042864 | 0.0013094 | N
05/01/2017 | 08:46 | ZN10994:PA20 | URBAN | Asset Failure | LV | 1 | 190 | 0.00013059 | 6.8913e-05 | N
05/01/2017 | 11:07 | ZN965:PA33 | URBAN | Asset Failure | LV | 1 | 232 | 0.00016009 | 6.8913e-05 | N
06/01/2017 | 10:02 | ZN2568:PA9 | URBAN | Asset Failure | LV | 1 | 148 | 0.00010196 | 6.8915e-05 | N
06/01/2017 | 13:15 | 801:74120 | URBAN | Asset Failure | LV | 1 | 125 | 8.6384e-05 | 6.8915e-05 | N
07/01/2017 | 16:27 | ZN2400:PA15 | SHORT RURAL | Asset Failure | LV | 1 | 573 | 0.0025701 | 0.00044881 | N
08/01/2017 | 19:24 | 221:11900 | SHORT RURAL | Asset Failure | LV | 1 | 164 | 0.0007338 | 0.00044881 | N
09/01/2017 | 13:22 | ZN711:PA23 | URBAN | Asset Failure | LV | 1 | 457 | 0.00031513 | 6.8892e-05 | N
09/01/2017 | 20:19 | ZN12600:PA3 | URBAN | Asset Failure | LV | 1 | 312 | 0.00021474 | 6.8892e-05 | N
10/01/2017 | 10:34 | ZN2602:PA9 | URBAN | Asset Failure | LV | 1 | 205 | 0.00014124 | 6.8893e-05 | N
10/01/2017 | 11:24 | ZN12570:PA26 | URBAN | Asset Failure | LV | 1 | 185 | 0.00012768 | 6.8893e-05 | N
10/01/2017 | 12:58 | ZN12640:PA10 | URBAN | Asset Failure | LV | 1 | 362 | 0.0002493 | 6.8893e-05 | N
11/01/2017 | 18:09 | ZN14892:PA6 | SHORT RURAL | Asset Failure | LV | 1 | 155 | 0.00069747 | 0.00044882 | N
11/01/2017 | 18:23 | ZN398:PA24 | URBAN | Asset Failure | LV | 1 | 282 | 0.00019461 | 6.8894e-05 | N
12/01/2017 | 10:12 | 238:34143 | URBAN | Asset Failure | LV | 1 | 155 | 0.00010671 | 6.8884e-05 | N
13/01/2017 | 13:50 | ZN195:PA11 | URBAN | Asset Failure | LV | 1 | 252 | 0.00017372 | 6.8886e-05 | N
13/01/2017 | 14:05 | 523:33508 | SHORT RURAL | Asset Failure | LV | 1 | 127 | 0.00056863 | 0.00044886 | N
14/01/2017 | 09:07 | ZN2835:PA16 | URBAN | Asset Failure | LV | 1 | 285 | 0.00019601 | 6.8886e-05 | N
14/01/2017 | 13:31 | 526:34637 | SHORT RURAL | Asset Failure | LV | 1 | 131 | 0.00058801 | 0.00044886 | N
15/01/2017 | 05:49 | ZN12580:PA10 | URBAN | Asset Failure | LV | 44 | 954 | 0.028903 | 0.003031 | N
15/01/2017 | 12:10 | ZN35800:PA1 | URBAN | Asset Failure | LV | 1 | 177 | 0.00012226 | 6.8886e-05 | N
16/01/2017 | 06:47 | ZN15010:PA11 | URBAN | Asset Failure | LV | 1 | 313 | 0.00021558 | 6.8886e-05 | N
16/01/2017 | 14:27 | ZN180:PA30 | URBAN | Asset Failure | LV | 1 | 264 | 0.00018196 | 6.8886e-05 | N
16/01/2017 | 16:04 | ZN5868:PA6 | URBAN | Asset Failure | LV | 293 | 124 | 0.025061 | 0.020184 | N
16/01/2017 | 17:40 | ZN36800:PA36 | URBAN | Asset Failure | LV | 1 | 890 | 0.00061287 | 6.8886e-05 | N
16/01/2017 | 20:41 | ZN10994:PA12 | URBAN | Asset Failure | LV | 1 | 138 | 9.5246e-05 | 6.8886e-05 | N
17/01/2017 | 17:20 | 813:89063 | SHORT RURAL | Asset Failure | LV | 1 | 281 | 0.001261 | 0.00044885 | N
18/01/2017 | 11:37 | ZN12610:PA23 | URBAN | Asset Failure | LV | 1 | 353 | 0.00024302 | 6.8887e-05 | N
18/01/2017 | 13:59 | ZN12610:PA23 | URBAN | Asset Failure | LV | 1 | 210 | 0.00014474 | 6.8887e-05 | N
18/01/2017 | 23:43 | 242:81541 | URBAN | Asset Failure | LV | 1 | 166 | 0.00011458 | 6.8887e-05 | N
19/01/2017 | 10:15 | ZN1193:PA10 | URBAN | Asset Failure | LV | 1 | 464 | 0.00031962 | 6.8881e-05 | N
19/01/2017 | 15:49 | 205:12213 | SHORT RURAL | Asset Failure | LV | 1 | 974 | 0.0043713 | 0.00044882 | N
19/01/2017 | 16:56 | ZN3425:PA43 | URBAN | Asset Failure | LV | 1 | 245 | 0.00016886 | 6.8881e-05 | N
20/01/2017 | 07:14 | ZN180:PA30 | URBAN | Asset Failure | LV | 1 | 285 | 0.00019634 | 6.8882e-05 | N
20/01/2017 | 13:18 | 243:80080 | SHORT RURAL | Asset Failure | LV | 1 | 71 | 0.00031993 | 0.00044881 | N
20/01/2017 | 13:35 | 227:13020 | SHORT RURAL | Asset Failure | LV | 1 | 125 | 0.000559 | 0.00044881 | N
20/01/2017 | 13:44 | 515:35193 | SHORT RURAL | Asset Failure | LV | 1 | 97 | 0.00043752 | 0.00044881 | N
20/01/2017 | 19:32 | ZN36300:PA11 | URBAN | Asset Failure | LV | 1 | 345 | 0.00023791 | 6.8882e-05 | N
20/01/2017 | 22:31 | ZN2602:PA17 | URBAN | Asset Failure | LV | 1 | 899 | 0.00061921 | 6.8882e-05 | N
22/01/2017 | 14:47 | ZN15005:PA6 | URBAN | Asset Failure | LV | 19 | 346 | 0.0045281 | 0.0013088 | N
23/01/2017 | 08:00 | ZN15009:PA1 | URBAN | Asset Failure | LV | 1 | 120 | 8.2635e-05 | 6.8882e-05 | N
23/01/2017 | 12:14 | ZN36100:PA27 | URBAN | Asset Failure | LV | 1 | 1,425 | 0.00098175 | 6.8882e-05 | N
23/01/2017 | 15:13 | 225:33676 | URBAN | Asset Failure | LV | 1 | 346 | 0.0002385 | 6.8882e-05 | N
25/01/2017 | 08:06 | ZN15006:PA15 | URBAN | Asset Failure | LV | 1 | 414 | 0.0002851 | 6.8885e-05 | N
25/01/2017 | 10:59 | ZN36300:PA3 | URBAN | Asset Failure | LV | 1 | 301 | 0.00020706 | 6.8885e-05 | N
25/01/2017 | 19:13 | ZN10999:PA4 | URBAN | Asset Failure | LV | 1 | 226 | 0.00015581 | 6.8885e-05 | N
26/01/2017 | 19:51 | ZN4545:PA40 | URBAN | Asset Failure | LV | 1 | 199 | 0.00013699 | 6.888e-05 | N
28/01/2017 | 08:55 | ZN12640:PA7 | URBAN | Asset Failure | LV | 1 | 297 | 0.00020438 | 6.8875e-05 | N
28/01/2017 | 22:34 | ZN10994:PA7 | URBAN | Asset Failure | LV | 1 | 746 | 0.00051377 | 6.8875e-05 | N
28/01/2017 | 22:42 | ZN10994:PA7 | URBAN | Asset Failure | LV | 1 | 737 | 0.00050768 | 6.8875e-05 | N
29/01/2017 | 07:56 | 812:19066 | SHORT RURAL | Asset Failure | LV | 1 | 143 | 0.00064235 | 0.00044826 | N
31/01/2017 | 18:26 | 507:80914 | SHORT RURAL | Asset Failure | LV | 1 | 82 | 0.00036548 | 0.00044826 | N
31/01/2017 | 17:50 | ZN1193:PA27 | URBAN | Asset Failure | LV | 1 | 399 | 0.00027514 | 6.8876e-05 | N
31/01/2017 | 19:58 | 516:48067 | SHORT RURAL | Asset Failure | LV | 1 | 68 | 0.00030684 | 0.00044826 | N
31/01/2017 | 22:10 | ZN965:PA8 | URBAN | Asset Failure | LV | 1 | 244 | 0.0001682 | 6.8876e-05 | N
01/02/2017 | 08:04 | 516:48067 | SHORT RURAL | Asset Failure | LV | 1 | 107 | 0.00047793 | 0.00044827 | N
01/02/2017 | 16:59 | 814:82285 | SHORT RURAL | Asset Failure | LV | 1 | 217 | 0.00097244 | 0.00044827 | N
01/02/2017 | 22:47 | ZN3154:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 347 | 0.0015554 | 0.00044827 | N
02/02/2017 | 00:56 | ZN15004:PA5 | URBAN | Asset Failure | LV | 1 | 813 | 0.00056001 | 6.8866e-05 | N
02/02/2017 | 09:19 | ZN15014:PA20 | URBAN | Asset Failure | LV | 1 | 1,424 | 0.00098084 | 6.8866e-05 | N
02/02/2017 | 13:51 | ZN9900:PA12 | URBAN | Asset Failure | LV | 1 | 98 | 6.75e-05 | 6.8866e-05 | N
03/02/2017 | 17:18 | ZN35500:PA31 | URBAN | Asset Failure | LV | 1 | 207 | 0.00014241 | 6.8867e-05 | N
04/02/2017 | 17:58 | 520:48172 | SHORT RURAL | Asset Failure | LV | 1 | 205 | 0.0009203 | 0.0004482 | N
04/02/2017 | 19:07 | 220:8689 | URBAN | Asset Failure | LV | 1 | 138 | 9.4959e-05 | 6.8869e-05 | N
06/02/2017 | 08:34 | ZN384:PA43 | URBAN | Asset Failure | LV | 1 | 955 | 0.0006578 | 6.8873e-05 | N
06/02/2017 | 09:23 | ZN9118:PA11 | URBAN | Asset Failure | LV | 1 | 517 | 0.000356 | 6.8873e-05 | N
07/02/2017 | 09:03 | ZN340:PA19 | URBAN | Asset Failure | LV | 1 | 72 | 4.9475e-05 | 6.8875e-05 | N
07/02/2017 | 11:13 | ZN10990:PA2 | URBAN | Asset Failure | LV | 1 | 134 | 9.2602e-05 | 6.8875e-05 | N
07/02/2017 | 11:39 | ZN847:PA46 | URBAN | Asset Failure | LV | 1 | 560 | 0.0003858 | 6.8875e-05 | N
07/02/2017 | 11:52 | ZN9118:PA20 | URBAN | Asset Failure | LV | 1 | 487 | 0.00033562 | 6.8875e-05 | N
07/02/2017 | 11:56 | ZN9700:PA21 | URBAN | Asset Failure | LV | 1 | 94 | 6.4513e-05 | 6.8875e-05 | N
08/02/2017 | 11:39 | 261:81882 | URBAN | Asset Failure | LV | 1 | 336 | 0.00023139 | 6.8876e-05 | N
08/02/2017 | 16:20 | ZN14891:PA20 | SHORT RURAL | Asset Failure | LV | 1 | 183 | 0.00081849 | 0.00044812 | N
09/02/2017 | 07:41 | ZN12620:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 139 | 0.00062148 | 0.00044748 | N
09/02/2017 | 08:17 | ZN2602:PA15 | URBAN | Asset Failure | LV | 1 | 407 | 0.00028028 | 6.8876e-05 | N
09/02/2017 | 15:29 | 524:33578 | URBAN | Asset Failure | LV | 1 | 209 | 0.00014379 | 6.8876e-05 | N
09/02/2017 | 16:04 | ZN15009:PA5 | URBAN | Asset Failure | LV | 1 | 224 | 0.00015445 | 6.8876e-05 | N
09/02/2017 | 18:13 | 223:14397 | URBAN | Asset Failure | LV | 1 | 242 | 0.00016655 | 6.8876e-05 | N
09/02/2017 | 18:31 | ZN15008:PA1 | URBAN | Asset Failure | LV | 1 | 329 | 0.0002266 | 6.8876e-05 | N
10/02/2017 | 08:01 | ZN1788:PA7 | URBAN | Asset Failure | LV | 1 | 179 | 0.00012305 | 6.8883e-05 | N
10/02/2017 | 14:27 | ZN10997:PA11 | URBAN | Asset Failure | LV | 1 | 393 | 0.00027055 | 6.8883e-05 | N
12/02/2017 | 11:31 | ZN8000:PA25 | URBAN | Asset Failure | LV | 1 | 68 | 4.6565e-05 | 6.8883e-05 | N
12/02/2017 | 13:18 | 523:33501 | SHORT RURAL | Asset Failure | LV | 1 | 77 | 0.00034552 | 0.00044747 | N
15/02/2017 | 14:09 | ZN12690:PA24 | SHORT RURAL | Asset Failure | LV | 1 | 504 | 0.0022504 | 0.00044631 | N
16/02/2017 | 14:01 | ZN7481:PA1 | URBAN | Asset Failure | LV | 1 | 539 | 0.00037114 | 6.8888e-05 | N
17/02/2017 | 07:53 | ZN12620:PA8 | SHORT RURAL | Asset Failure | LV | 1 | 127 | 0.00056711 | 0.0004466 | Y
17/02/2017 | 17:24 | ZN12690:PA6 | URBAN | Asset Failure | LV | 1 | 815 | 0.00056173 | 6.889e-05 | Y
17/02/2017 | 17:40 | ZN116:PA76 | URBAN | Asset Failure | LV | 1 | 110 | 7.5607e-05 | 6.889e-05 | Y
17/02/2017 | 18:44 | 511:29878 | SHORT RURAL | Asset Failure | LV | 1 | 375 | 0.0016759 | 0.0004466 | Y
18/02/2017 | 05:45 | ZN12690:PA16 | SHORT RURAL | Asset Failure | LV | 1 | 675 | 0.0030142 | 0.00044661 | N
18/02/2017 | 05:53 | ZN2602:PA15 | URBAN | Asset Failure | LV | 4 | 802 | 0.002209 | 0.00027556 | N
19/02/2017 | 21:01 | ZN847:PA5 | URBAN | Asset Failure | LV | 1 | 284 | 0.00019558 | 6.889e-05 | N
21/02/2017 | 07:50 | ZN195:PA9 | URBAN | Asset Failure | LV | 1 | 249 | 0.00017183 | 6.8892e-05 | N
21/02/2017 | 14:46 | ZN12660:PA10 | URBAN | Asset Failure | LV | 1 | 390 | 0.00026869 | 6.8892e-05 | N
24/02/2017 | 14:06 | ZN14892:PA13 | URBAN | Asset Failure | LV | 1 | 127 | 8.7353e-05 | 6.8881e-05 | N
24/02/2017 | 16:50 | ZN847:PA39 | URBAN | Asset Failure | LV | 1 | 188 | 0.00012926 | 6.8881e-05 | N
25/02/2017 | 13:37 | ZN3154:PA18 | URBAN | Asset Failure | LV | 1 | 66 | 4.5334e-05 | 6.8879e-05 | N
25/02/2017 | 19:27 | ZN10999:PA29 | URBAN | Asset Failure | LV | 1 | 272 | 0.00018726 | 6.8879e-05 | N
26/02/2017 | 10:02 | ZN12610:PA10 | URBAN | Asset Failure | LV | 1 | 1,678 | 0.0011556 | 6.8879e-05 | N
27/02/2017 | 15:02 | ZN72:PA23 | URBAN | Asset Failure | LV | 1 | 688 | 0.00047407 | 6.8879e-05 | N
27/02/2017 | 15:20 | ZN12600:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 1,359 | 0.0060699 | 0.00044661 | N
28/02/2017 | 18:16 | 813:89061 | LONG RURAL | Asset Failure | LV | 1 | 194 | 0.069064 | 0.0356 | N
28/02/2017 | 21:19 | ZN180:PA7 | URBAN | Asset Failure | LV | 1 | 1,776 | 0.0012232 | 6.8879e-05 | N
01/03/2017 | 11:26 | ZN965:PA38 | URBAN | Asset Failure | LV | 1 | 153 | 0.00010547 | 6.888e-05 | N
01/03/2017 | 18:16 | ZN35500:PA34 | URBAN | Asset Failure | LV | 1 | 234 | 0.00016102 | 6.888e-05 | N
05/03/2017 | 11:37 | ZN9700:PA23 | URBAN | Asset Failure | LV | 1 | 540 | 0.00037216 | 6.8877e-05 | N
05/03/2017 | 11:41 | ZN9700:PA23 | URBAN | Asset Failure | LV | 1 | 536 | 0.00036926 | 6.8877e-05 | N
06/03/2017 | 07:03 | ZN9118:PA15 | URBAN | Asset Failure | LV | 1 | 416 | 0.0002866 | 6.8877e-05 | N
06/03/2017 | 07:37 | ZN15008:PA5 | URBAN | Asset Failure | LV | 1 | 202 | 0.00013941 | 6.8877e-05 | N
06/03/2017 | 09:36 | 216:10729 | URBAN | Asset Failure | LV | 1 | 113 | 7.8037e-05 | 6.8877e-05 | N
06/03/2017 | 10:10 | 228:7491 | URBAN | Asset Failure | LV | 1 | 200 | 0.00013762 | 6.8877e-05 | N
06/03/2017 | 16:53 | ZN3472:PA29 | URBAN | Asset Failure | LV | 1 | 336 | 0.00023167 | 6.8877e-05 | N
07/03/2017 | 12:57 | ZN10993:PA22 | URBAN | Asset Failure | LV | 1 | 632 | 0.00043555 | 6.8879e-05 | N
07/03/2017 | 15:38 | ZN35800:PA15 | URBAN | Asset Failure | LV | 1 | 331 | 0.0002278 | 6.8879e-05 | N
08/03/2017 | 08:15 | ZN1287:PA3 | URBAN | Asset Failure | LV | 1 | 345 | 0.00023734 | 6.888e-05 | N
08/03/2017 | 08:33 | ZN7900:PA2 | URBAN | Asset Failure | LV | 1 | 626 | 0.00043128 | 6.888e-05 | N
09/03/2017 | 10:31 | 504:48034 | URBAN | Asset Failure | LV | 1 | 383 | 0.00026391 | 6.8889e-05 | N
10/03/2017 | 08:23 | ZN15004:PA9 | URBAN | Asset Failure | LV | 1 | 845 | 0.00058216 | 6.8891e-05 | N
11/03/2017 | 15:25 | ZN1788:PA30 | URBAN | Asset Failure | LV | 1 | 266 | 0.00018319 | 6.8891e-05 | N
12/03/2017 | 20:32 | ZN2602:PA42 | URBAN | Asset Failure | LV | 1 | 262 | 0.00018021 | 6.8892e-05 | N
13/03/2017 | 19:08 | ZN262:PA16 | URBAN | Asset Failure | LV | 1 | 201 | 0.00013866 | 6.8892e-05 | N
13/03/2017 | 19:16 | ZN12630:PA11 | SHORT RURAL | Asset Failure | LV | 1 | 1,154 | 0.0051301 | 0.00044464 | N
13/03/2017 | 19:22 | ZN9245:PA3 | URBAN | Asset Failure | LV | 1 | 922 | 0.00063537 | 6.8892e-05 | N
14/03/2017 | 07:40 | ZN12610:PA13 | URBAN | Asset Failure | LV | 1 | 349 | 0.00024054 | 6.8892e-05 | N
14/03/2017 | 13:09 | ZN15006:PA4 | URBAN | Asset Failure | LV | 1 | 111 | 7.6286e-05 | 6.8892e-05 | N
14/03/2017 | 18:35 | 813:89061 | LONG RURAL | Asset Failure | LV | 1 | 199 | 0.070804 | 0.035613 | N
15/03/2017 | 10:21 | ZN9118:PA6 | URBAN | Asset Failure | LV | 9 | 549 | 0.0034047 | 0.00062003 | N
15/03/2017 | 11:14 | 220:8689 | URBAN | Asset Failure | LV | 1 | 155 | 0.0001071 | 6.8892e-05 | N
15/03/2017 | 12:24 | ZN14892:PA16 | URBAN | Asset Failure | LV | 1 | 105 | 7.236e-05 | 6.8892e-05 | N
16/03/2017 | 08:03 | ZN2568:PA16 | URBAN | Asset Failure | LV | 1 | 237 | 0.00016297 | 6.8877e-05 | N
16/03/2017 | 09:31 | 224:80332 | URBAN | Asset Failure | LV | 1 | 154 | 0.00010629 | 6.8877e-05 | N
17/03/2017 | 12:10 | 508:82575 | SHORT RURAL | Asset Failure | LV | 1 | 289 | 0.0012855 | 0.00044445 | N
17/03/2017 | 13:00 | ZN9245:PA1 | URBAN | Asset Failure | LV | 1 | 570 | 0.00039247 | 6.8877e-05 | N
17/03/2017 | 14:10 | ZN80:PA31 | URBAN | Asset Failure | LV | 1 | 179 | 0.00012351 | 6.8877e-05 | N
17/03/2017 | 17:36 | ZN14144:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 1,523 | 0.0067707 | 0.00044445 | N
17/03/2017 | 20:12 | 222:33597 | SHORT RURAL | Asset Failure | LV | 1 | 800 | 0.003554 | 0.00044445 | N
17/03/2017 | 20:59 | ZN10995:PA2 | URBAN | Asset Failure | LV | 1 | 317 | 0.00021846 | 6.8877e-05 | N
18/03/2017 | 02:07 | ZN15009:PA5 | URBAN | Asset Failure | LV | 105 | 607 | 0.043913 | 0.0072322 | N
18/03/2017 | 07:56 | ZN15014:PA19 | URBAN | Asset Failure | LV | 1 | 873 | 0.00060147 | 6.8878e-05 | N
18/03/2017 | 08:28 | ZN1610:PA19 | URBAN | Asset Failure | LV | 1 | 2,500 | 0.0017221 | 6.8878e-05 | N
18/03/2017 | 14:09 | ZN14144:PA7 | SHORT RURAL | Asset Failure | LV | 1 | 215 | 0.00095646 | 0.00044445 | N
18/03/2017 | 19:20 | ZN3472:PA17 | URBAN | Asset Failure | LV | 1 | 294 | 0.0002028 | 6.8878e-05 | N
18/03/2017 | 23:31 | ZN12640:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 854 | 0.0037964 | 0.00044445 | N
19/03/2017 | 01:28 | ZN12610:PA24 | URBAN | Asset Failure | LV | 1 | 714 | 0.00049205 | 6.8879e-05 | N
19/03/2017 | 10:26 | ZN340:PA14 | URBAN | Asset Failure | LV | 1 | 204 | 0.00014023 | 6.8879e-05 | N
19/03/2017 | 12:14 | ZN36200:PA4 | SHORT RURAL | Asset Failure | LV | 1 | 472 | 0.0020985 | 0.00044445 | N
19/03/2017 | 19:33 | ZN2635:PA38 | URBAN | Asset Failure | LV | 1 | 222 | 0.00015288 | 6.8879e-05 | N
20/03/2017 | 13:10 | ZN4545:PA2 | URBAN | Asset Failure | LV | 1 | 735 | 0.00050614 | 6.8879e-05 | N
20/03/2017 | 15:27 | ZN15006:PA1 | URBAN | Asset Failure | LV | 1 | 440 | 0.00030274 | 6.8879e-05 | N
20/03/2017 | 17:19 | ZN12580:PA1 | URBAN | Asset Failure | LV | 1 | 1,241 | 0.00085447 | 6.8879e-05 | N
20/03/2017 | 17:36 | ZN10994:PA10 | URBAN | Asset Failure | LV | 1 | 414 | 0.00028508 | 6.8879e-05 | N
20/03/2017 | 17:36 | 228:7490 | SHORT RURAL | Asset Failure | LV | 1 | 308 | 0.0013702 | 0.00044445 | N
20/03/2017 | 19:23 | ZN12610:PA6 | URBAN | Asset Failure | LV | 2 | 997 | 0.0013734 | 0.00013776 | N
21/03/2017 | 06:21 | ZN15012:PA6 | URBAN | Asset Failure | LV | 1 | 353 | 0.00024336 | 6.8879e-05 | N
22/03/2017 | 19:08 | ZN901:PA13 | URBAN | Asset Failure | LV | 53 | 351 | 0.012829 | 0.0036507 | N
23/03/2017 | 06:49 | ZN3425:PA30 | URBAN | Asset Failure | LV | 7 | 791 | 0.0038108 | 0.00048201 | N
23/03/2017 | 07:10 | ZN874:PA22 | URBAN | Asset Failure | LV | 1 | 319 | 0.00021978 | 6.8858e-05 | N
24/03/2017 | 09:06 | ZN262:PA29 | URBAN | Asset Failure | LV | 1 | 253 | 0.00017432 | 6.8859e-05 | N
25/03/2017 | 07:55 | ZN12620:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 214 | 0.00095231 | 0.00044462 | N
26/03/2017 | 11:11 | ZN9900:PA13 | URBAN | Asset Failure | LV | 1 | 461 | 0.00031719 | 6.8857e-05 | N
26/03/2017 | 14:57 | ZN35400:PA53 | SHORT RURAL | Asset Failure | LV | 1 | 415 | 0.0018399 | 0.00044384 | N
27/03/2017 | 09:36 | 532:83307 | SHORT RURAL | Asset Failure | LV | 1 | 234 | 0.0010371 | 0.00044384 | N
27/03/2017 | 11:32 | 202:34256 | URBAN | Asset Failure | LV | 1 | 212 | 0.00014616 | 6.8857e-05 | N
30/03/2017 | 06:55 | 523:33501 | SHORT RURAL | Asset Failure | LV | 1 | 304 | 0.0013491 | 0.00044356 | N
30/03/2017 | 08:55 | ZN5868:PA17 | URBAN | Asset Failure | LV | 1 | 184 | 0.00012692 | 6.8836e-05 | N
30/03/2017 | 12:57 | ZN36100:PA23 | URBAN | Asset Failure | LV | 1 | 138 | 9.4994e-05 | 6.8836e-05 | N
30/03/2017 | 16:10 | ZN5868:PA27 | URBAN | Asset Failure | LV | 1 | 1,249 | 0.0008598 | 6.8836e-05 | N
30/03/2017 | 17:53 | ZN80:PA31 | URBAN | Asset Failure | LV | 1 | 503 | 0.00034656 | 6.8836e-05 | N
30/03/2017 | 18:45 | ZN4545:PA29 | URBAN | Asset Failure | LV | 1 | 535 | 0.00036829 | 6.8836e-05 | N
31/03/2017 | 13:37 | ZN4545:PA21 | URBAN | Asset Failure | LV | 1 | 612 | 0.00042144 | 6.884e-05 | N
31/03/2017 | 14:39 | ZN4545:PA27 | URBAN | Asset Failure | LV | 1 | 611 | 0.00042031 | 6.884e-05 | N
31/03/2017 | 20:15 | 214:8669 | URBAN | Asset Failure | LV | 1 | 135 | 9.2888e-05 | 6.884e-05 | N
01/04/2017 | 01:10 | ZN35600:PA19 | URBAN | Asset Failure | LV | 1 | 874 | 0.00060156 | 6.8798e-05 | N
02/04/2017 | 09:46 | ZN4545:PA36 | URBAN | Asset Failure | LV | 1 | 133 | 9.1845e-05 | 6.8806e-05 | N
02/04/2017 | 13:36 | ZN690:PA11 | URBAN | Asset Failure | LV | 1 | 503 | 0.00034642 | 6.8806e-05 | N
02/04/2017 | 18:24 | ZN12570:PA24 | SHORT RURAL | Asset Failure | LV | 1 | 179 | 0.00079859 | 0.00044531 | N
02/04/2017 | 20:29 | ZN3155:PA23 | URBAN | Asset Failure | LV | 1 | 900 | 0.00061928 | 6.8806e-05 | N
02/04/2017 | 22:15 | ZN36100:PA20 | URBAN | Asset Failure | LV | 1 | 315 | 0.00021652 | 6.8806e-05 | N
03/04/2017 | 06:39 | ZN1788:PA6 | URBAN | Asset Failure | LV | 1 | 275 | 0.00018954 | 6.8806e-05 | N
03/04/2017 | 19:48 | 202:34231 37 42 | URBAN | Asset Failure | LV | 1 | 557 | 0.00038295 | 6.8806e-05 | N
04/04/2017 | 06:23 | 221:11897 | URBAN | Asset Failure | LV | 1 | 276 | 0.0001902 | 6.8807e-05 | N
04/04/2017 | 12:01 | 220:8689 | URBAN | Asset Failure | LV | 1 | 155 | 0.00010651 | 6.8807e-05 | N
07/04/2017 | 18:20 | ZN1788:PA11 | URBAN | Asset Failure | LV | 1 | 250 | 0.00017218 | 6.8914e-05 | N
08/04/2017 | 08:45 | ZN340:PA2 | URBAN | Asset Failure | LV | 1 | 344 | 0.00023662 | 6.8781e-05 | N
08/04/2017 | 09:22 | ZN10993:PA35 | URBAN | Asset Failure | LV | 1 | 466 | 0.00032065 | 6.8781e-05 | N
09/04/2017 | 18:43 | ZN1648:PA4 | URBAN | Asset Failure | LV | 1 | 421 | 0.00028987 | 6.878e-05 | N
10/04/2017 | 18:21 | ZN1287:PA17 | URBAN | Asset Failure | LV | 1 | 252 | 0.00017346 | 6.878e-05 | N
11/04/2017 | 17:38 | ZN2568:PA14 | URBAN | Asset Failure | LV | 1 | 412 | 0.00028316 | 6.878e-05 | N
13/04/2017 | 09:25 | ZN1788:PA8 | URBAN | Asset Failure | LV | 1 | 305 | 0.00020962 | 6.8788e-05 | N
13/04/2017 | 18:47 | ZN1068:PA17 | URBAN | Asset Failure | LV | 1 | 194 | 0.00013341 | 6.8788e-05 | N
17/04/2017 | 10:44 | 814:82291 | SHORT RURAL | Asset Failure | LV | 1 | 75 | 0.00033582 | 0.00044528 | N
17/04/2017 | 18:29 | ZN12570:PA39 | URBAN | Asset Failure | LV | 1 | 320 | 0.0002201 | 6.8766e-05 | N
18/04/2017 | 09:56 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 132 | 0.047144 | 0.035702 | N
18/04/2017 | 12:04 | ZN9118:PA3 | SHORT RURAL | Asset Failure | LV | 1 | 446 | 0.0019843 | 0.00044528 | N
18/04/2017 | 16:52 | ZN9900:PA8 | URBAN | Asset Failure | LV | 1 | 1,143 | 0.00078602 | 6.8766e-05 | N
19/04/2017 | 12:07 | ZN129:PA47 | URBAN | Asset Failure | LV | 1 | 413 | 0.000284 | 6.877e-05 | N
19/04/2017 | 14:58 | ZN1285:PA33 | URBAN | Asset Failure | LV | 1 | 247 | 0.00017 | 6.877e-05 | N
20/04/2017 | 15:58 | ZN14144:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 392 | 0.0017402 | 0.00044413 | N
24/04/2017 | 14:02 | ZN12640:PA7 | URBAN | Asset Failure | LV | 2 | 586 | 0.00080543 | 0.00013755 | N
26/04/2017 | 14:49 | ZN384:PA70 | URBAN | Asset Failure | LV | 1 | 160 | 0.00011024 | 6.8776e-05 | N
26/04/2017 | 17:21 | 232:11454 | SHORT RURAL | Asset Failure | LV | 1 | 232 | 0.0010308 | 0.00044399 | N
27/04/2017 | 16:08 | ZN15006:PA2 | URBAN | Asset Failure | LV | 1 | 277 | 0.00019076 | 6.876e-05 | N
27/04/2017 | 17:27 | ZN9252:PA24 | URBAN | Asset Failure | LV | 1 | 235 | 0.00016169 | 6.876e-05 | N
29/04/2017 | 09:09 | ZN1648:PA21 | URBAN | Asset Failure | LV | 1 | 276 | 0.00018966 | 6.8763e-05 | N
01/05/2017 | 17:14 | ZN36100:PA8 | URBAN | Asset Failure | LV | 1 | 436 | 0.00029947 | 6.8762e-05 | N
02/05/2017 | 15:24 | 239:82131 | SHORT RURAL | Asset Failure | LV | 1 | 193 | 0.0008579 | 0.00044389 | N
03/05/2017 | 10:28 | ZN12610:PA23 | URBAN | Asset Failure | LV | 1 | 59 | 4.0699e-05 | 6.8767e-05 | N
03/05/2017 | 10:40 | ZN12610:PA23 | URBAN | Asset Failure | LV | 1 | 47 | 3.2378e-05 | 6.8767e-05 | N
03/05/2017 | 16:29 | ZN72:PA16 | URBAN | Asset Failure | LV | 1 | 278 | 0.00019086 | 6.8767e-05 | N
04/05/2017 | 09:32 | ZN36100:PA5 | URBAN | Asset Failure | LV | 1 | 177 | 0.00012186 | 6.8752e-05 | N
04/05/2017 | 15:11 | ZN72:PA16 | URBAN | Asset Failure | LV | 1 | 434 | 0.00029841 | 6.8752e-05 | N
06/05/2017 | 17:58 | ZN12650:PA17 | URBAN | Asset Failure | LV | 1 | 285 | 0.00019596 | 6.8759e-05 | N
08/05/2017 | 12:08 | ZN690:PA25 | URBAN | Asset Failure | LV | 1 | 201 | 0.00013847 | 6.8747e-05 | N
08/05/2017 | 16:55 | ZN9700:PA17 | URBAN | Asset Failure | LV | 1 | 1,025 | 0.00070444 | 6.8747e-05 | N
11/05/2017 | 09:24 | ZN1673:PA21 | SHORT RURAL | Asset Failure | LV | 1 | 608 | 0.0027039 | 0.00044443 | N
11/05/2017 | 20:50 | ZN180:PA34 | URBAN | Asset Failure | LV | 1 | 789 | 0.00054308 | 6.8802e-05 | N
12/05/2017 | 00:35 | ZN15002:PA6 | URBAN | Asset Failure | LV | 1 | 534 | 0.0003675 | 6.8776e-05 | N
12/05/2017 | 10:30 | ZN12580:PA4 | URBAN | Asset Failure | LV | 1 | 419 | 0.0002884 | 6.8776e-05 | N
13/05/2017 | 09:58 | 202:34240 | URBAN | Asset Failure | LV | 1 | 122 | 8.3524e-05 | 6.8735e-05 | N
14/05/2017 | 11:11 | 511:29876 | SHORT RURAL | Asset Failure | LV | 1 | 439 | 0.0019504 | 0.0004444 | N
14/05/2017 | 12:42 | 801:74119 | URBAN | Asset Failure | LV | 1 | 150 | 0.00010317 | 6.8735e-05 | N
14/05/2017 | 12:57 | ZN2635:PA31 | URBAN | Asset Failure | LV | 1 | 273 | 0.00018734 | 6.8735e-05 | N
15/05/2017 | 07:43 | ZN2568:PA38 | URBAN | Asset Failure | LV | 1 | 226 | 0.00015558 | 6.8735e-05 | N
15/05/2017 | 09:26 | ZN9118:PA17 | URBAN | Asset Failure | LV | 1 | 363 | 0.00024982 | 6.8735e-05 | N
15/05/2017 | 10:10 | ZN36100:PA12 | URBAN | Asset Failure | LV | 1 | 455 | 0.00031267 | 6.8735e-05 | N
19/05/2017 | 13:24 | ZN10995:PA7 | URBAN | Asset Failure | LV | 1 | 546 | 0.000375 | 6.8723e-05 | N
20/05/2017 | 13:12 | 511:29873 | URBAN | Asset Failure | LV | 1 | 150 | 0.00010282 | 6.8723e-05 | N
22/05/2017 | 09:29 | ZN9118:PA11 | URBAN | Asset Failure | LV | 1 | 224 | 0.00015363 | 6.8723e-05 | N
23/05/2017 | 14:20 | ZN36300:PA5 | URBAN | Asset Failure | LV | 1 | 306 | 0.00021009 | 6.8723e-05 | N
23/05/2017 | 21:28 | ZN262:PA31 | URBAN | Asset Failure | LV | 1 | 782 | 0.00053716 | 6.8723e-05 | N
25/05/2017 | 05:08 | ZN10996:PA12 | URBAN | Asset Failure | LV | 1 | 304 | 0.00020899 | 6.8723e-05 | N
25/05/2017 | 16:43 | ZN116:PA76 | URBAN | Asset Failure | LV | 1 | 532 | 0.00036542 | 6.8723e-05 | N
26/05/2017 | 18:16 | 513:48056 | SHORT RURAL | Asset Failure | LV | 2 | 87 | 0.00077794 | 0.00089521 | Y
27/05/2017 | 12:30 | 258:80787 | URBAN | Asset Failure | LV | 1 | 140 | 9.6154e-05 | 6.8723e-05 | N
28/05/2017 | 11:52 | 504:48026 | SHORT RURAL | Asset Failure | LV | 1 | 321 | 0.0014385 | 0.00044761 | N
29/05/2017 | 11:22 | ZN3922:PA12 | URBAN | Asset Failure | LV | 1 | 36 | 2.4717e-05 | 6.8723e-05 | N
29/05/2017 | 12:23 | ZN35800:PA15 | URBAN | Asset Failure | LV | 1 | 337 | 0.00023142 | 6.8723e-05 | N
31/05/2017 | 11:06 | ZN2568:PA26 | URBAN | Asset Failure | LV | 1 | 358 | 0.00024608 | 6.8722e-05 | N
31/05/2017 | 12:24 | ZN129:PA38 | URBAN | Asset Failure | LV | 1 | 395 | 0.00027157 | 6.8722e-05 | N
31/05/2017 | 14:04 | 532:83301 | URBAN | Asset Failure | LV | 1 | 329 | 0.00022629 | 6.8722e-05 | N
31/05/2017 | 14:52 | ZN15001:PA2 | URBAN | Asset Failure | LV | 1 | 319 | 0.00021911 | 6.8722e-05 | N
31/05/2017 | 18:19 | ZN12650:PA10 | URBAN | Asset Failure | LV | 1 | 130 | 8.9579e-05 | 6.8722e-05 | N
03/06/2017 | 08:15 | ZN188:PA22 | URBAN | Asset Failure | LV | 1 | 464 | 0.00031894 | 6.8722e-05 | N
03/06/2017 | 19:10 | 225:13446 | URBAN | Asset Failure | LV | 1 | 138 | 9.5076e-05 | 6.8722e-05 | N
04/06/2017 | 14:47 | ZN15011:PA10 | URBAN | Asset Failure | LV | 1 | 191 | 0.00013097 | 6.8722e-05 | N
04/06/2017 | 18:36 | 214:8667 | URBAN | Asset Failure | LV | 1 | 149 | 0.00010229 | 6.8722e-05 | N
06/06/2017 | 14:19 | ZN10999:PA15 | URBAN | Asset Failure | LV | 1 | 112 | 7.7048e-05 | 6.8722e-05 | N
06/06/2017 | 21:26 | ZN15012:PA8 | URBAN | Asset Failure | LV | 1 | 634 | 0.00043568 | 6.8722e-05 | N
07/06/2017 | 07:28 | ZN10994:PA19 | URBAN | Asset Failure | LV | 1 | 286 | 0.00019683 | 6.8722e-05 | N
07/06/2017 | 11:41 | ZN36100:PA16 | URBAN | Asset Failure | LV | 2 | 498 | 0.00068495 | 0.00013744 | N
07/06/2017 | 12:08 | ZN2466:PA7 | URBAN | Asset Failure | LV | 1 | 112 | 7.6716e-05 | 6.8722e-05 | N
11/06/2017 | 13:39 | 812:19066 | SHORT RURAL | Asset Failure | LV | 1 | 82 | 0.00036808 | 0.0004476 | N
11/06/2017 | 13:56 | ZN12690:PA3 | SHORT RURAL | Asset Failure | LV | 1 | 1,808 | 0.0080916 | 0.0004476 | N
12/06/2017 | 13:32 | ZN2602:PA30 | URBAN | Asset Failure | LV | 1 | 148 | 0.0001014 | 6.8722e-05 | N
12/06/2017 | 16:37 | ZN12580:PA10 | URBAN | Asset Failure | LV | 1 | 1,102 | 0.0007574 | 6.8722e-05 | N
13/06/2017 | 06:35 | ZN4545:PA40 | URBAN | Asset Failure | LV | 1 | 385 | 0.00026456 | 6.8722e-05 | N
14/06/2017 | 07:06 | ZN9900:PA17 | URBAN | Asset Failure | LV | 1 | 254 | 0.00017436 | 6.8722e-05 | N
14/06/2017 | 10:36 | ZN10994:PA3 | URBAN | Asset Failure | LV | 1 | 444 | 0.00030502 | 6.8722e-05 | N
15/06/2017 | 04:33 | ZN340:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 296 | 0.0013257 | 0.0004476 | N
15/06/2017 | 17:46 | ZN80:PA25 | URBAN | Asset Failure | LV | 1 | 232 | 0.00015959 | 6.8722e-05 | N
18/06/2017 | 21:21 | ZN15006:PA9 | URBAN | Asset Failure | LV | 1 | 668 | 0.00045918 | 6.8722e-05 | N
21/06/2017 | 14:55 | ZN35500:PA23 | URBAN | Asset Failure | LV | 1 | 65 | 4.4577e-05 | 6.8722e-05 | N
23/06/2017 | 15:05 | ZN14144:PA2 | SHORT RURAL | Asset Failure | LV | 1 | 479 | 0.0021424 | 0.0004476 | N
24/06/2017 | 14:19 | ZN36200:PA1 | URBAN | Asset Failure | LV | 1 | 205 | 0.00014091 | 6.8642e-05 | N
25/06/2017 | 15:17 | 814:82291 | SHORT RURAL | Asset Failure | LV | 1 | 128 | 0.00057077 | 0.0004476 | N
26/06/2017 | 15:25 | 813:89065 | URBAN | Asset Failure | LV | 1 | 54 | 3.6735e-05 | 6.8642e-05 | N
26/06/2017 | 20:46 | ZN15013:PA4 | URBAN | Asset Failure | LV | 1 | 249 | 0.00017062 | 6.8642e-05 | N
27/06/2017 | 19:23 | ZN10995:PA2 | URBAN | Asset Failure | LV | 1 | 967 | 0.0006637 | 6.8642e-05 | N
28/06/2017 | 07:52 | 507:80922 | SHORT RURAL | Asset Failure | LV | 1 | 188 | 0.0008409 | 0.0004476 | N
28/06/2017 | 17:27 | 216:10727 | SHORT RURAL | Asset Failure | LV | 1 | 78 | 0.00034786 | 0.0004476 | N
28/06/2017 | 18:43 | 801:74117 | SHORT RURAL | Asset Failure | LV | 1 | 257 | 0.0011486 | 0.0004476 | N
29/06/2017 | 07:56 | ZN180:PA22 | URBAN | Asset Failure | LV | 1 | 383 | 0.00026322 | 6.8642e-05 | N
30/06/2017 | 06:45 | ZN2602:PA15 | URBAN | Asset Failure | LV | 1 | 374 | 0.00025684 | 6.8642e-05 | N
30/06/2017 | 08:53 | 221:11894 | URBAN | Asset Failure | LV | 1 | 126 | 8.6821e-05 | 6.8642e-05 | N
01/07/2016 | 01:09 | ZN35800:PA15 | URBAN | Asset Failure | Distribution substation | 102 | 200 | 0.014149 | 0.0070643 | N
07/07/2016 | 05:33 | ZN12570:PA24 | SHORT RURAL | Asset Failure | Distribution substation | 62 | 146 | 0.041322 | 0.028225 | N
06/07/2016 | 11:40 | 514:18137 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 110 | 0.00050086 | 0.00045533 | N
12/07/2016 | 17:06 | 504:48033 | SHORT RURAL | Asset Failure | Distribution substation | 33 | 94 | 0.014102 | 0.015023 | N
13/07/2016 | 07:43 | 532:83309 | SHORT RURAL | Asset Failure | Distribution substation | 15 | 262 | 0.017892 | 0.0068289 | N
12/07/2016 | 19:53 | 526:34639 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 77 | 0.0010516 | 0.0013657 | N
12/07/2016 | 09:00 | 801:74121 | LONG RURAL | Asset Failure | Distribution substation | 3 | 105 | 0.11234 | 0.10699 | N
13/07/2016 | 14:25 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 199 | 0.071131 | 0.035663 | N
23/07/2016 | 20:02 | 801:74123 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 267 | 0.0012137 | 0.00045391 | N
25/07/2016 | 15:37 | 235:2124 | SHORT RURAL | Asset Failure | Distribution substation | 53 | 43 | 0.010304 | 0.024057 | N
28/07/2016 | 14:58 | ZN14892:PA19 | URBAN | Asset Failure | Distribution substation | 69 | 46 | 0.002214 | 0.0047767 | N
03/08/2016 | 05:50 | ZN15006:PA8 | URBAN | Asset Failure | Distribution substation | 112 | 119 | 0.0092426 | 0.0077539 | N
03/08/2016 | 19:24 | ZN12660:PA17 | URBAN | Asset Failure | Distribution substation | 91 | 53 | 0.0033495 | 0.0063 | N
04/08/2016 | 04:42 | 511:29878 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 398 | 0.0018076 | 0.00045463 | N
04/08/2016 | 16:31 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 304 | 0.10831 | 0.035676 | N
08/08/2016 | 12:20 | 810:74050 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 80 | 0.00036371 | 0.00045463 | N
18/08/2016 | 21:32 | ZN35600:PA16 | URBAN | Asset Failure | Distribution substation | 166 | 399 | 0.045995 | 0.011517 | N
19/08/2016 | 17:27 | ZN12660:PA11 | URBAN | Asset Failure | Distribution substation | 99 | 78 | 0.0053322 | 0.0068685 | N
21/08/2016 | 21:14 | ZN13000:PA2 | SHORT RURAL | Asset Failure | Distribution substation | 74 | 106 | 0.036314 | 0.034301 | N
24/08/2016 | 17:34 | ZN12620:PA2 | SHORT RURAL | Asset Failure | Distribution substation | 44 | 55 | 0.011146 | 0.020101 | N
26/08/2016 | 05:00 | 243:80074 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 75 | 0.0003424 | 0.00045684 | N
28/08/2016 | 10:19 | ZN12620:PA2 | SHORT RURAL | Asset Failure | Distribution substation | 44 | 136 | 0.027324 | 0.020091 | N
31/08/2016 | 19:54 | 217:33610 | URBAN | Asset Failure | Distribution substation | 101 | 38 | 0.0026637 | 0.006973 | N
03/09/2016 | 16:30 | 264:81240 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 30 | 0.00013664 | 0.00045648 | N
05/09/2016 | 12:00 | 512:48049 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 20 | 9.0002e-05 | 0.00045648 | N
05/09/2016 | 14:14 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 131 | 0.00059844 | 0.00045648 | N
05/09/2016 | 17:17 | 511:29876 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 143 | 0.00065292 | 0.00045648 | N
03/09/2016 | 19:10 | ZN12650:PA13 | SHORT RURAL | Asset Failure | Distribution substation | 17 | 270 | 0.020952 | 0.0077601 | N
09/09/2016 | 12:55 | 802:82225 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 254 | 0.0011561 | 0.00045451 | N
10/09/2016 | 06:55 | ZN36100:PA5 | URBAN | Asset Failure | Distribution substation | 76 | 139 | 0.0073148 | 0.0052486 | N
15/09/2016 | 11:49 | 507:80917 | URBAN | Asset Failure | Distribution substation | 71 | 115 | 0.0056602 | 0.0049027 | N
19/09/2016 | 09:09 | ZN15001:PA17 | URBAN | Asset Failure | Distribution substation | 8 | 45 | 0.00024863 | 0.00055251 | N
19/09/2016 | 15:48 | ZN14143:PA6 | URBAN | Asset Failure | Distribution substation | 1 | 1,462 | 0.0010096 | 6.9064e-05 | N
25/09/2016 | 09:59 | 224:80337 | SHORT RURAL | Asset Failure | Distribution substation | 123 | 60 | 0.033574 | 0.055832 | N
27/09/2016 | 06:22 | 813:89061 | LONG RURAL | Asset Failure | Distribution substation | 1 | 47 | 0.016857 | 0.035676 | N
27/09/2016 | 16:41 | 515:35192 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 184 | 0.00083401 | 0.00045388 | N
29/09/2016 | 13:00 | 516:48066 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 1,484 | 0.01347 | 0.00090754 | N
03/10/2016 | 12:54 | 257:81999 | URBAN | Asset Failure | Distribution substation | 104 | 66 | 0.0047139 | 0.0071822 | N
05/10/2016 | 08:14 | 511:29878 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 309 | 0.001398 | 0.00045268 | N
06/10/2016 | 17:00 | 261:81879 | URBAN | Asset Failure | Distribution substation | 111 | 75 | 0.0057188 | 0.0076659 | N
06/10/2016 | 19:48 | 242:81535 | URBAN | Asset Failure | Distribution substation | 75 | 93 | 0.0048076 | 0.0051797 | N
11/10/2016 | 04:15 | 229:34983 | SHORT RURAL | Asset Failure | Distribution substation | 17 | 101 | 0.0077777 | 0.0076868 | N
15/10/2016 | 23:25 | ZN847:PA1 | URBAN | Asset Failure | Distribution substation | 55 | 149 | 0.0056602 | 0.0037988 | N
16/10/2016 | 18:33 | 507:80922 | SHORT RURAL | Asset Failure | Distribution substation | 83 | 86 | 0.032281 | 0.037384 | N
14/10/2016 | 10:40 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 55 | 0.019629 | 0.035689 | N
21/10/2016 | 13:33 | 512:48046 | SHORT RURAL | Asset Failure | Distribution substation | 78 | 207 | 0.073104 | 0.035347 | N
22/10/2016 | 00:12 | ZN10994:PA7 | URBAN | Asset Failure | Distribution substation | 117 | 97 | 0.0078507 | 0.0080797 | N
22/10/2016 | 13:10 | ZN14143:PA17 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 250 | 0.0011256 | 0.00045023 | N
24/10/2016 | 13:50 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 629 | 0.22449 | 0.035689 | N
27/10/2016 | 19:15 | 258:80785 | URBAN | Asset Failure | Distribution substation | 1 | 105 | 7.2489e-05 | 6.9037e-05 | N
28/10/2016 | 07:05 | 806:82662 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 184 | 0.00083024 | 0.00045012 | N
27/10/2016 | 14:00 | 528:83019 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 115 | 0.00051763 | 0.00045012 | N
02/11/2016 | 10:57 | 526:34636 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 563 | 0.0025344 | 0.00045016 | N
04/11/2016 | 14:48 | ZN8000:PA28 | URBAN | Asset Failure | Distribution substation | 7 | 201 | 0.0009714 | 0.00048316 | N
07/11/2016 | 11:32 | 528:83014 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 178 | 0.00080016 | 0.00044999 | N
07/11/2016 | 17:36 | 232:11457 | SHORT RURAL | Asset Failure | Distribution substation | 47 | 80 | 0.016952 | 0.02115 | N
12/11/2016 | 10:07 | 512:48046 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 257 | 0.001157 | 0.00044977 | N
12/11/2016 | 20:10 | 807:74184 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 889 | 0.0039993 | 0.00044977 | N
13/11/2016 | 08:38 | ZN14892:PA16 | URBAN | Asset Failure | Distribution substation | 45 | 132 | 0.0040992 | 0.0031055 | N
13/11/2016 | 17:12 | 507:80932 | SHORT RURAL | Asset Failure | Distribution substation | 70 | 138 | 0.043364 | 0.031484 | N
20/11/2016 | 21:16 | ZN4545:PA31 | URBAN | Asset Failure | Distribution substation | 107 | 112 | 0.0082536 | 0.0073825 | N
17/11/2016 | 10:21 | 512:48048 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 284 | 0.002554 | 0.00089929 | N
02/12/2016 | 08:29 | 812:19072 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 171 | 0.00076765 | 0.00044927 | N
02/12/2016 | 16:17 | ZN3155:PA44 | URBAN | Asset Failure | Distribution substation | 151 | 703 | 0.073241 | 0.01042 | N
02/12/2016 | 12:55 | 813:89055 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 75 | 0.00033695 | 0.00044927 | N
05/12/2016 | 15:43 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 466 | 0.0041914 | 0.00089855 | N
06/12/2016 | 14:19 | 813:89065 | URBAN | Asset Failure | Distribution substation | 29 | 56 | 0.0011169 | 0.0019999 | N
06/12/2016 | 15:30 | 801:74121 | LONG RURAL | Asset Failure | Distribution substation | 1 | 66 | 0.023496 | 0.0356 | N
07/12/2016 | 18:02 | ZN15014:PA19 | URBAN | Asset Failure | Distribution substation | 103 | 73 | 0.0051698 | 0.0071031 | N
08/12/2016 | 01:21 | 238:34148 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 799 | 0.0035904 | 0.00044936 | N
09/12/2016 | 08:18 | 524:33572 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 252 | 0.0022629 | 0.00089868 | N
09/12/2016 | 14:10 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 280 | 0.099668 | 0.0356 | N
09/12/2016 | 14:18 | 511:29878 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 174 | 0.00078193 | 0.00044934 | N
10/12/2016 | 20:55 | 807:74180 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 126 | 0.00056812 | 0.00044934 | N
11/12/2016 | 15:34 | ZN14143:PA17 | SHORT RURAL | Asset Failure | Distribution substation | 9 | 535 | 0.021645 | 0.0040442 | N
13/12/2016 | 10:03 | 507:80926 | URBAN | Asset Failure | Distribution substation | 1 | 147 | 0.00010133 | 6.8942e-05 | N
13/12/2016 | 21:33 | ZN35370:PA10 | SHORT RURAL | Asset Failure | Distribution substation | 11 | 83 | 0.0040779 | 0.0049429 | N
13/12/2016 | 17:10 | 812:19072 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 20 | 8.9871e-05 | 0.00044935 | N
14/12/2016 | 17:54 | 507:80925 | SHORT RURAL | Asset Failure | Distribution substation | 72 | 386 | 0.12487 | 0.032354 | N
14/12/2016 | 21:21 | ZN12570:PA33 | SHORT RURAL | Asset Failure | Distribution substation | 108 | 184 | 0.089483 | 0.048531 | N
19/12/2016 | 22:48 | 210:8681 | URBAN | Asset Failure | Distribution substation | 101 | 87 | 0.0060462 | 0.0069616 | N
24/12/2016 | 11:21 | ZN12630:PA10 | SHORT RURAL | Asset Failure | Distribution substation | 12 | 209 | 0.011243 | 0.0053877 | N
25/12/2016 | 13:11 | 526:34639 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 648 | 0.002908 | 0.00044897 | N
29/12/2016 | 09:03 | 238:34137 | SHORT RURAL | Asset Failure | Distribution substation | 20 | 224 | 0.020077 | 0.0089795 | N
29/12/2016 | 16:17 | 217:33610 | URBAN | Asset Failure | Distribution substation | 124 | 40 | 0.0034435 | 0.0085448 | N
29/12/2016 | 21:36 | ZN12610:PA9 | URBAN | Asset Failure | Distribution substation | 31 | 174 | 0.003717 | 0.0021362 | N
30/12/2016 | 13:56 | ZN3154:PA5 | URBAN | Asset Failure | Distribution substation | 83 | 159 | 0.0090884 | 0.0057196 | N
30/12/2016 | 14:46 | ZN711:PA34 | URBAN | Asset Failure | Distribution substation | 359 | 107 | 0.026458 | 0.024739 | N
31/12/2016 | 19:21 | 523:33501 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 59 | 0.00026452 | 0.00044898 | N
01/01/2017 | 11:56 | 801:74121 | LONG RURAL | Asset Failure | Distribution substation | 4 | 154 | 0.21945 | 0.1425 | N
02/01/2017 | 04:36 | 812:19072 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 283 | 0.0012721 | 0.00044898 | N
05/01/2017 | 04:25 | ZN10991:PA12 | URBAN | Asset Failure | Distribution substation | 56 | 219 | 0.0084676 | 0.0038591 | N
08/01/2017 | 08:55 | 814:82285 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 134 | 0.00060342 | 0.00044881 | N
10/01/2017 | 22:45 | 504:48027 | URBAN | Asset Failure | Distribution substation | 15 | 554 | 0.0057298 | 0.0010334 | N
11/01/2017 | 13:01 | ZN1287:PA5 | URBAN | Asset Failure | Distribution substation | 127 | 223 | 0.019523 | 0.0087495 | N
11/01/2017 | 14:18 | ZN10995:PA6 | URBAN | Asset Failure | Distribution substation | 90 | 147 | 0.0090847 | 0.0062005 | N
11/01/2017 | 19:31 | 233:82812 | SHORT RURAL | Asset Failure | Distribution substation | 28 | 69 | 0.0086147 | 0.012567 | N
11/01/2017 | 15:50 | 811:74234 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 90 | 0.00040394 | 0.00044882 | N
13/01/2017 | 15:13 | ZN9252:PA27 | URBAN | Asset Failure | Distribution substation | 57 | 91 | 0.0035711 | 0.0039265 | N
14/01/2017 | 17:07 | 802:82225 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 182 | 0.00081872 | 0.00044886 | N
16/01/2017 | 11:48 | 512:48049 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 137 | 0.00061433 | 0.00044885 | N
17/01/2017 | 15:56 | ZN14891:PA12 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 14 | 6.1493e-05 | 0.00044885 | N
18/01/2017 | 06:50 | 256:80632 | URBAN | Asset Failure | Distribution substation | 2 | 90 | 0.000124 | 0.00013777 | N
18/01/2017 | 13:10 | ZN965:PA46 | URBAN | Asset Failure | Distribution substation | 37 | 110 | 0.0028037 | 0.0025488 | N
19/01/2017 | 10:00 | 513:48056 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 150 | 0.00067324 | 0.00044882 | N
22/01/2017 | 21:43 | 813:89055 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 264 | 0.0023733 | 0.00089763 | N
24/01/2017 | 10:28 | ZN10999:PA15 | URBAN | Asset Failure | Distribution substation | 78 | 166 | 0.0089038 | 0.0053729 | N
29/01/2017 | 09:23 | 511:29878 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 102 | 0.00045722 | 0.00044826 | N
31/01/2017 | 11:28 | ZN12660:PA10 | URBAN | Asset Failure | Distribution substation | 40 | 141 | 0.0038901 | 0.002755 | N
31/01/2017 | 12:20 | 813:89061 | LONG RURAL | Asset Failure | Distribution substation | 1 | 55 | 0.019536 | 0.035638 | N
02/02/2017 | 15:28 | 813:89062 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 206 | 0.00185 | 0.00089638 | N
04/02/2017 | 19:19 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 1,166 | 0.41524 | 0.035613 | N
05/02/2017 | 13:04 | 813:89061 | LONG RURAL | Asset Failure | Distribution substation | 1 | 306 | 0.10894 | 0.035613 | N
05/02/2017 | 15:43 | ZN9037:PA2 | URBAN | Asset Failure | Distribution substation | 80 | 282 | 0.015525 | 0.0055099 | N
05/02/2017 | 13:00 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 2 | 1,530 | 1.0897 | 0.071225 | N
07/02/2017 | 02:41 | 225:13444 | SHORT RURAL | Asset Failure | Distribution substation | 47 | 58 | 0.012254 | 0.021061 | N
04/02/2017 | 20:30 | 526:34640 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 535 | 0.0071936 | 0.0013446 | N
07/02/2017 | 08:16 | 508:82580 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 374 | 0.0016754 | 0.00044812 | N
06/02/2017 | 18:00 | ZN14891:PA6 | URBAN | Asset Failure | Distribution substation | 1 | 105 | 7.2317e-05 | 6.8873e-05 | N
09/02/2017 | 05:00 | ZN180:PA15 | URBAN | Asset Failure | Distribution substation | 60 | 349 | 0.014424 | 0.0041325 | N
10/02/2017 | 14:20 | 812:19071 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 139 | 0.000624 | 0.00044747 | N
10/02/2017 | 18:06 | 813:89061 | LONG RURAL | Asset Failure | Distribution substation | 1 | 179 | 0.063687 | 0.035613 | N
10/02/2017 | 18:41 | 243:80081 | SHORT RURAL | Asset Failure | Distribution substation | 116 | 86 | 0.044458 | 0.051907 | N
11/02/2017 | 11:26 | 220:8689 | URBAN | Asset Failure | Distribution substation | 34 | 71 | 0.0016722 | 0.002342 | N
11/02/2017 | 18:26 | 513:48056 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 296 | 0.0013245 | 0.00044747 | N
13/02/2017 | 21:25 | 509:33399 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 235 | 0.0010495 | 0.00044747 | N
14/02/2017 | 10:47 | ZN931:PA11 | URBAN | Asset Failure | Distribution substation | 228 | 118 | 0.018553 | 0.015723 | N
17/02/2017 | 17:35 | 810:74054 | LONG RURAL | Asset Failure | Distribution substation | 1 | 220 | 0.078348 | 0.035613 | Y
17/02/2017 | 18:06 | ZN15010:PA7 | URBAN | Asset Failure | Distribution substation | 105 | 3,045 | 0.22024 | 0.0072335 | Y
18/02/2017 | 04:35 | 514:18137 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 823 | 0.0036746 | 0.00044661 | N
18/02/2017 | 20:13 | ZN12630:PA8 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 1,051 | 0.014084 | 0.0013398 | N
18/02/2017 | 21:13 | 807:74179 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 157 | 0.0007011 | 0.00044661 | N
18/02/2017 | 21:22 | 507:80932 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 336 | 0.0030003 | 0.00089321 | N
21/02/2017 | 14:50 | 801:74121 | LONG RURAL | Asset Failure | Distribution substation | 1 | 40 | 0.014245 | 0.035613 | N
18/02/2017 | 00:00 | 807:74184 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 690 | 0.0061632 | 0.00089321 | N
18/02/2017 | 21:58 | 806:82662 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 242 | 0.0010808 | 0.00044661 | N
23/02/2017 | 06:16 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 123 | 0.00054978 | 0.00044649 | N
23/02/2017 | 07:38 | 807:74179 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 351 | 0.0015673 | 0.00044649 | N
26/02/2017 | 15:03 | 806:82662 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 176 | 0.00078738 | 0.00044661 | N
11/02/2017 | 20:05 | ZN12650:PA13 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 1,140 | 0.0051012 | 0.00044747 | N
01/03/2017 | 09:58 | 239:82131 | SHORT RURAL | Asset Failure | Distribution substation | 6 | 227 | 0.006083 | 0.0026797 | N
02/03/2017 | 10:47 | ZN15013:PA8 | URBAN | Asset Failure | Distribution substation | 1 | 673 | 0.00046353 | 6.8881e-05 | N
05/03/2017 | 10:00 | 528:83013 | URBAN | Asset Failure | Distribution substation | 8 | 105 | 0.00057857 | 0.00055101 | N
11/03/2017 | 13:08 | ZN14891:PA5 | SHORT RURAL | Asset Failure | Distribution substation | 7 | 266 | 0.0082933 | 0.0031125 | N
11/03/2017 | 20:51 | ZN14891:PA5 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 843 | 0.0037498 | 0.00044464 | N
14/03/2017 | 08:12 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 273 | 0.0012129 | 0.00044464 | N
18/03/2017 | 13:10 | ZN12610:PA5 | URBAN | Asset Failure | Distribution substation | 4 | 100 | 0.00027551 | 0.00027551 | N
17/03/2017 | 10:05 | 801:74121 | LONG RURAL | Asset Failure | Distribution substation | 1 | 70 | 0.024938 | 0.035625 | N
16/03/2017 | 19:15 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 5,505 | 1.9612 | 0.035625 | N
17/03/2017 | 11:15 | 243:80083 | SHORT RURAL | Asset Failure | Distribution substation | 4 | 15 | 0.00026667 | 0.0017778 | N
22/03/2017 | 05:41 | ZN12630:PA8 | SHORT RURAL | Asset Failure | Distribution substation | 8 | 124 | 0.0043985 | 0.0035558 | N
22/03/2017 | 13:49 | ZN1285:PA17 | URBAN | Asset Failure | Distribution substation | 72 | 65 | 0.0032236 | 0.0049594 | N
23/03/2017 | 20:22 | ZN12690:PA6 | URBAN | Asset Failure | Distribution substation | 44 | 32 | 0.00097558 | 0.0030297 | N
25/03/2017 | 17:58 | 238:34148 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 261 | 0.0011615 | 0.00044462 | N
28/03/2017 | 06:55 | ZN36200:PA1 | URBAN | Asset Failure | Distribution substation | 63 | 70 | 0.0030193 | 0.004338 | N
28/03/2017 | 15:32 | ZN15005:PA2 | URBAN | Asset Failure | Distribution substation | 111 | 97 | 0.0074496 | 0.0076432 | N
30/03/2017 | 11:54 | ZN9252:PA28 | URBAN | Asset Failure | Distribution substation | 118 | 79 | 0.0064196 | 0.0081227 | N
31/03/2017 | 10:00 | 515:35192 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 95 | 0.00042138 | 0.00044356 | N
31/03/2017 | 10:18 | 812:19072 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 321 | 0.0014252 | 0.00044356 | N
01/04/2017 | 08:02 | 524:33572 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 283 | 0.0025205 | 0.00089062 | N
03/04/2017 | 17:13 | ZN4545:PA36 | URBAN | Asset Failure | Distribution substation | 100 | 157 | 0.010771 | 0.0068806 | N
04/04/2017 | 21:15 | 230:81440 | SHORT RURAL | Asset Failure | Distribution substation | 70 | 69 | 0.021618 | 0.031172 | N
04/04/2017 | 14:23 | 516:48065 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 21 | 0.00028055 | 0.0013359 | N
05/04/2017 | 20:50 | ZN36200:PA4 | SHORT RURAL | Asset Failure | Distribution substation | 17 | 69 | 0.0052563 | 0.0075703 | N
08/04/2017 | 13:37 | 235:2124 | SHORT RURAL | Asset Failure | Distribution substation | 87 | 33 | 0.012786 | 0.038745 | N
10/04/2017 | 12:58 | 507:80914 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 131 | 0.0005837 | 0.00044534 | N
10/04/2017 | 13:03 | 235:2857 | SHORT RURAL | Asset Failure | Distribution substation | 46 | 72 | 0.014668 | 0.020486 | N
13/04/2017 | 06:09 | 261:81876 | URBAN | Asset Failure | Distribution substation | 63 | 46 | 0.0019899 | 0.0043336 | N
14/04/2017 | 10:10 | 232:33407 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 280 | 0.0037381 | 0.0013358 | N
15/04/2017 | 13:53 | 230:81434 | URBAN | Asset Failure | Distribution substation | 49 | 81 | 0.0027383 | 0.0033695 | N
04/05/2017 | 14:08 | ZN180:PA32 | URBAN | Asset Failure | Distribution substation | 277 | 82 | 0.015616 | 0.019044 | N
05/05/2017 | 17:07 | ZN14891:PA5 | SHORT RURAL | Asset Failure | Distribution substation | 6 | 73 | 0.0019395 | 0.0026629 | N
10/05/2017 | 19:48 | 243:80083 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 57 | 0.00025194 | 0.00044459 | N
11/05/2017 | 17:16 | ZN15005:PA8 | URBAN | Asset Failure | Distribution substation | 102 | 133 | 0.0093583 | 0.0070179 | N
26/05/2017 | 09:09 | 228:7486 | URBAN | Asset Failure | Distribution substation | 2 | 371 | 0.00050992 | 0.00013745 | Y
27/05/2017 | 17:16 | ZN167:PA11 | URBAN | Asset Failure | Distribution substation | 110 | 2 | 0.00015119 | 0.0075595 | N
29/05/2017 | 20:45 | ZN12640:PA13 | SHORT RURAL | Asset Failure | Distribution substation | 105 | 59 | 0.027933 | 0.046999 | N
29/05/2017 | 20:45 | ZN12640:PA13 | SHORT RURAL | Asset Failure | Distribution substation | 115 | 60 | 0.030885 | 0.051475 | N
31/05/2017 | 01:05 | 264:81236 | SHORT RURAL | Asset Failure | Distribution substation | 29 | 5 | 0.00064903 | 0.012981 | N
07/06/2017 | 06:46 | ZN12640:PA19 | URBAN | Asset Failure | Distribution substation | 72 | 69 | 0.00341 | 0.004948 | N
08/06/2017 | 04:28 | ZN12570:PA34 | SHORT RURAL | Asset Failure | Distribution substation | 53 | 71 | 0.016954 | 0.023723 | N
08/06/2017 | 16:49 | ZN965:PA12 | URBAN | Asset Failure | Distribution substation | 62 | 49 | 0.0020686 | 0.0042607 | N
09/06/2017 | 08:10 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 5 | 2.238e-05 | 0.0004476 | N
13/06/2017 | 09:19 | ZN965:PA47 | URBAN | Asset Failure | Distribution substation | 52 | 176 | 0.0062894 | 0.0035735 | N
23/06/2017 | 12:35 | ZN12660:PA11 | URBAN | Asset Failure | Distribution substation | 64 | 144 | 0.0063319 | 0.0043931 | N
25/06/2017 | 23:30 | ZN14144:PA8 | URBAN | Asset Failure | Distribution substation | 38 | 150 | 0.0039126 | 0.0026084 | N
27/07/2016 | 09:32 | ZN15001:PA10 | URBAN | Asset Failure | Subtransmission | 318 | 71 | 0.015632 | 0.022017 | N
27/07/2016 | 09:32 | ZN15001:PA11 | URBAN | Asset Failure | Subtransmission | 892 | 71 | 0.043849 | 0.061759 | N
27/07/2016 | 09:32 | ZN15001:PA2 | URBAN | Asset Failure | Subtransmission | 2,291 | 69 | 0.10945 | 0.15862 | N
27/07/2016 | 09:32 | ZN15001:PA3 | URBAN | Asset Failure | Subtransmission | 407 | 69 | 0.019444 | 0.028179 | N
27/07/2016 | 09:32 | ZN15001:PA4 | URBAN | Asset Failure | Subtransmission | 403 | 72 | 0.02009 | 0.027902 | N
27/07/2016 | 09:32 | ZN15001:PA6 | URBAN | Asset Failure | Subtransmission | 1,238 | 109 | 0.093736 | 0.085715 | N
27/07/2016 | 09:32 | ZN15001:PA8 | URBAN | Asset Failure | Subtransmission | 687 | 90 | 0.042809 | 0.047566 | N
27/07/2016 | 09:32 | ZN15008:PA7 | URBAN | Asset Failure | Subtransmission | 962 | 90 | 0.059945 | 0.066606 | N
14/11/2016 | 09:40 | 802:82215 | SHORT RURAL | Asset Failure | Subtransmission | 36 | 44 | 0.0071243 | 0.016192 | N
14/11/2016 | 09:40 | 802:82220 | SHORT RURAL | Asset Failure | Subtransmission | 63 | 44 | 0.012468 | 0.028335 | N
14/11/2016 | 09:40 | 802:82225 | SHORT RURAL | Asset Failure | Subtransmission | 106 | 44 | 0.020977 | 0.047675 | N
14/11/2016 | 09:40 | 810:74050 | SHORT RURAL | Asset Failure | Subtransmission | 137 | 44 | 0.027112 | 0.061618 | N
14/11/2016 | 09:40 | 810:74054 | LONG RURAL | Asset Failure | Subtransmission | 321 | 44 | 5.0299 | 11.4316 | N
14/11/2016 | 09:40 | 810:74058 | SHORT RURAL | Asset Failure | Subtransmission | 197 | 44 | 0.038986 | 0.088604 | N
14/11/2016 | 09:40 | 810:74062 | SHORT RURAL | Asset Failure | Subtransmission | 565 | 44 | 0.11181 | 0.25412 | N
25/11/2016 | 16:43 | ZN4545:PA11 | URBAN | Asset Failure | Subtransmission | 525 | 145 | 0.052509 | 0.036213 | N
25/11/2016 | 16:43 | ZN4545:PA13 | URBAN | Asset Failure | Subtransmission | 289 | 144 | 0.0287 | 0.019934 | N
25/11/2016 | 16:43 | ZN4545:PA17 | URBAN | Asset Failure | Subtransmission | 1,187 | 148 | 0.12118 | 0.081876 | N
25/11/2016 | 16:43 | ZN4545:PA19 | URBAN | Asset Failure | Subtransmission | 500 | 148 | 0.051043 | 0.034489 | N
25/11/2016 | 16:43 | ZN4545:PA2 | URBAN | Asset Failure | Subtransmission | 1,681 | 147 | 0.17045 | 0.11595 | N
25/11/2016 | 16:43 | ZN4545:PA21 | URBAN | Asset Failure | Subtransmission | 714 | 148 | 0.07289 | 0.04925 | N
25/11/2016 | 16:43 | ZN4545:PA24 | URBAN | Asset Failure | Subtransmission | 1,669 | 142 | 0.16348 | 0.11512 | N
25/11/2016 | 16:43 | ZN4545:PA25 | URBAN | Asset Failure | Subtransmission | 1,069 | 142 | 0.10471 | 0.073737 | N
25/11/2016 | 16:43 | ZN4545:PA26 | URBAN | Asset Failure | Subtransmission | 1,246 | 142 | 0.12204 | 0.085946 | N
25/11/2016 | 16:43 | ZN4545:PA27 | URBAN | Asset Failure | Subtransmission | 1,078 | 142 | 0.10559 | 0.074358 | N
25/11/2016 | 16:43 | ZN4545:PA28 | URBAN | Asset Failure | Subtransmission | 1,094 | 142 | 0.10716 | 0.075461 | N
25/11/2016 | 16:43 | ZN4545:PA29 | URBAN | Asset Failure | Subtransmission | 1,673 | 148 | 0.17079 | 0.1154 | N
25/11/2016 | 16:43 | ZN4545:PA3 | URBAN | Asset Failure | Subtransmission | 623 | 147 | 0.06317 | 0.042973 | N
25/11/2016 | 16:43 | ZN4545:PA31 | URBAN | Asset Failure | Subtransmission | 2,990 | 146 | 0.30111 | 0.20624 | N
25/11/2016 | 16:43 | ZN4545:PA32 | URBAN | Asset Failure | Subtransmission | 811 | 147 | 0.082233 | 0.055941 | N
25/11/2016 | 16:43 | ZN4545:PA33 | URBAN | Asset Failure | Subtransmission | 2,664 | 147 | 0.27012 | 0.18376 | N
25/11/2016 | 16:43 | ZN4545:PA35 | URBAN | Asset Failure | Subtransmission | 1,365 | 147 | 0.13841 | 0.094154 | N
25/11/2016 | 16:43 | ZN4545:PA36 | URBAN | Asset Failure | Subtransmission | 1,224 | 147 | 0.12411 | 0.084428 | N
25/11/2016 | 16:43 | ZN4545:PA39 | URBAN | Asset Failure | Subtransmission | 1,141 | 146 | 0.11491 | 0.078703 | N
25/11/2016 | 16:43 | ZN4545:PA4 | URBAN | Asset Failure | Subtransmission | 1,075 | 147 | 0.109 | 0.074151 | N
25/11/2016 | 16:43 | ZN4545:PA40 | URBAN | Asset Failure | Subtransmission | 1,771 | 146 | 0.17835 | 0.12216 | N
25/11/2016 | 16:43 | ZN4545:PA41 | SHORT RURAL | Asset Failure | Subtransmission | 1,052 | 146 | 0.69033 | 0.47283 | N
25/11/2016 | 16:43 | ZN4545:PA42 | URBAN | Asset Failure | Subtransmission | 1,112 | 146 | 0.11199 | 0.076703 | N
25/11/2016 | 16:43 | ZN4545:PA44 | URBAN | Asset Failure | Subtransmission | 1,192 | 147 | 0.12087 | 0.082221 | N
25/11/2016 | 16:43 | ZN4545:PA6 | URBAN | Asset Failure | Subtransmission | 726 | 147 | 0.073614 | 0.050078 | N
25/11/2016 | 16:43 | ZN4545:PA9 | URBAN | Asset Failure | Subtransmission | 26 | 145 | 0.0026005 | 0.0017934 | N
11/12/2016 | 03:20 | ZN630:PA26 | URBAN | Asset Failure | Subtransmission | 551 | 33 | 0.012536 | 0.037987 | N
11/12/2016 | 03:20 | ZN630:PA27 | URBAN | Asset Failure | Subtransmission | 337 | 33 | 0.007667 | 0.023233 | N
11/12/2016 | 03:20 | ZN630:PA30 | URBAN | Asset Failure | Subtransmission | 1 | 33 | 2.2751e-05 | 6.8941e-05 | N
11/12/2016 | 03:20 | ZN630:PA31 | URBAN | Asset Failure | Subtransmission | 320 | 33 | 0.0072802 | 0.022061 | N
11/12/2016 | 03:20 | ZN630:PA32 | URBAN | Asset Failure | Subtransmission | 326 | 33 | 0.0074167 | 0.022475 | N
11/12/2016 | 03:20 | ZN630:PA33 | URBAN | Asset Failure | Subtransmission | 117 | 33 | 0.0026618 | 0.0080662 | N
09/01/2017 | 21:55 | ZN12570:PA21 | URBAN | Asset Failure | Subtransmission | 2,221 | 69 | 0.10558 | 0.15301 | N
09/01/2017 | 21:55 | ZN12570:PA22 | SHORT RURAL | Asset Failure | Subtransmission | 1,607 | 69 | 0.49765 | 0.72124 | N
09/01/2017 | 21:55 | ZN12570:PA24 | SHORT RURAL | Asset Failure | Subtransmission | 1,763 | 69 | 0.54596 | 0.79125 | N
09/01/2017 | 21:55 | ZN12570:PA25 | SHORT RURAL | Asset Failure | Subtransmission | 1,048 | 69 | 0.32454 | 0.47035 | N
09/01/2017 | 21:55 | ZN12570:PA26 | URBAN | Asset Failure | Subtransmission | 1,127 | 69 | 0.053573 | 0.077642 | N
09/01/2017 | 21:55 | ZN12570:PA29 | SHORT RURAL | Asset Failure | Subtransmission | 740 | 69 | 0.22916 | 0.33212 | N
09/01/2017 | 21:55 | ZN12570:PA33 | SHORT RURAL | Asset Failure | Subtransmission | 1,562 | 69 | 0.48372 | 0.70104 | N
09/01/2017 | 21:55 | ZN12570:PA34 | SHORT RURAL | Asset Failure | Subtransmission | 852 | 69 | 0.26385 | 0.38239 | N
09/01/2017 | 21:55 | ZN12570:PA35 | URBAN | Asset Failure | Subtransmission | 1,056 | 69 | 0.050198 | 0.07275 | N
09/01/2017 | 21:55 | ZN12570:PA37 | SHORT RURAL | Asset Failure | Subtransmission | 1,515 | 69 | 0.46916 | 0.67995 | N
09/01/2017 | 21:55 | ZN12570:PA39 | URBAN | Asset Failure | Subtransmission | 1,431 | 69 | 0.068024 | 0.098585 | N
09/01/2017 | 21:55 | ZN12570:PA40 | SHORT RURAL | Asset Failure | Subtransmission | 1,171 | 69 | 0.36263 | 0.52556 | N
09/01/2017 | 21:55 | ZN12570:PA41 | URBAN | Asset Failure | Subtransmission | 807 | 69 | 0.038361 | 0.055596 | N
09/01/2017 | 21:55 | ZN12580:PA1 | URBAN | Asset Failure | Subtransmission | 1,193 | 69 | 0.05671 | 0.082189 | N
09/01/2017 | 21:55 | ZN12580:PA10 | URBAN | Asset Failure | Subtransmission | 1,599 | 69 | 0.07601 | 0.11016 | N
09/01/2017 | 21:55 | ZN12580:PA12 | SHORT RURAL | Asset Failure | Subtransmission | 343 | 69 | 0.10622 | 0.15394 | N
09/01/2017 | 21:55 | ZN12580:PA13 | URBAN | Asset Failure | Subtransmission | 93 | 69 | 0.0044208 | 0.006407 | N
09/01/2017 | 21:55 | ZN12580:PA14 | URBAN | Asset Failure | Subtransmission | 1,834 | 69 | 0.087181 | 0.12635 | N
09/01/2017 | 21:55 | ZN12580:PA16 | URBAN | Asset Failure | Subtransmission | 1,299 | 69 | 0.061749 | 0.089491 | N
09/01/2017 | 21:55 | ZN12580:PA2 | URBAN | Asset Failure | Subtransmission | 378 | 69 | 0.017969 | 0.026041 | N
09/01/2017 | 21:55 | ZN12580:PA4 | URBAN | Asset Failure | Subtransmission | 2,112 | 69 | 0.1004 | 0.1455 | N
09/01/2017 | 21:55 | ZN12580:PA7 | URBAN | Asset Failure | Subtransmission | 174 | 69 | 0.0082712 | 0.011987 | N
09/01/2017 | 21:55 | ZN12580:PA8 | URBAN | Asset Failure | Subtransmission | 306 | 69 | 0.014546 | 0.021081 | N
06/02/2017 | 16:12 | ZN340:PA14 | URBAN | Asset Failure | Subtransmission | 70 | 192 | 0.0092359 | 0.0048211 | N
06/02/2017 | 16:12 | ZN630:PA25 | URBAN | Asset Failure | Subtransmission | 1 | 106 | 7.3006e-05 | 6.8873e-05 | N
06/02/2017 | 16:12 | ZN630:PA34 | URBAN | Asset Failure | Subtransmission | 180 | 36 | 0.004463 | 0.012397 | N
06/02/2017 | 16:12 | ZN630:PA35 | URBAN | Asset Failure | Subtransmission | 561 | 36 | 0.01391 | 0.038638 | N
06/02/2017 | 16:12 | ZN630:PA38 | URBAN | Asset Failure | Subtransmission | 1,728 | 89 | 0.1058 | 0.11901 | N
06/02/2017 | 16:12 | ZN630:PA40 | URBAN | Asset Failure | Subtransmission | 80 | 77 | 0.0042426 | 0.0055099 | N
06/02/2017 | 16:12 | ZN630:PA41 | URBAN | Asset Failure | Subtransmission | 457 | 108 | 0.03387 | 0.031475 | N
03/03/2017 | 23:19 | ZN15004:PA1 | URBAN | Asset Failure | Subtransmission | 1,718 | 229 | 0.27092 | 0.11831 | N
03/03/2017 | 23:19 | ZN15004:PA3 | URBAN | Asset Failure | Subtransmission | 895 | 229 | 0.14114 | 0.061632 | N
03/03/2017 | 23:19 | ZN15004:PA5 | URBAN | Asset Failure | Subtransmission | 1,729 | 229 | 0.27266 | 0.11906 | N
03/03/2017 | 23:19 | ZN15004:PA9 | URBAN | Asset Failure | Subtransmission | 1,968 | 229 | 0.31035 | 0.13552 | N
03/03/2017 | 23:19 | ZN15010:PA1 | URBAN | Asset Failure | Subtransmission | 1,393 | 230 | 0.22063 | 0.095926 | N
03/03/2017 | 23:19 | ZN15010:PA11 | URBAN | Asset Failure | Subtransmission | 473 | 230 | 0.074916 | 0.032572 | N
03/03/2017 | 23:19 | ZN15010:PA12 | URBAN | Asset Failure | Subtransmission | 79 | 230 | 0.012512 | 0.0054402 | N
03/03/2017 | 23:19 | ZN15010:PA5 | URBAN | Asset Failure | Subtransmission | 908 | 230 | 0.14381 | 0.062528 | N
03/03/2017 | 23:19 | ZN15010:PA7 | URBAN | Asset Failure | Subtransmission | 1,812 | 230 | 0.28699 | 0.12478 | N
03/03/2017 | 23:19 | ZN15010:PA9 | SHORT RURAL | Asset Failure | Subtransmission | 1,122 | 230 | 1.1526 | 0.50114 | N
18/03/2017 | 13:25 | ZN3154:PA16 | URBAN | Asset Failure | Subtransmission | 1,000 | 8 | 0.0055103 | 0.068878 | N
18/03/2017 | 13:25 | ZN3154:PA17 | URBAN | Asset Failure | Subtransmission | 933 | 8 | 0.0051411 | 0.064263 | N
18/03/2017 | 13:25 | ZN3154:PA18 | URBAN | Asset Failure | Subtransmission | 1,156 | 8 | 0.0063699 | 0.079623 | N
18/03/2017 | 13:25 | ZN3154:PA19 | URBAN | Asset Failure | Subtransmission | 1,012 | 8 | 0.0055764 | 0.069705 | N
18/03/2017 | 13:25 | ZN3154:PA22 | SHORT RURAL | Asset Failure | Subtransmission | 723 | 8 | 0.025707 | 0.32134 | N
18/03/2017 | 13:25 | ZN3154:PA23 | URBAN | Asset Failure | Subtransmission | 466 | 8 | 0.0025678 | 0.032097 | N
18/03/2017 | 13:25 | ZN3154:PA24 | URBAN | Asset Failure | Subtransmission | 1,021 | 8 | 0.005626 | 0.070325 | N
18/03/2017 | 13:25 | ZN3154:PA25 | URBAN | Asset Failure | Subtransmission | 565 | 8 | 0.0031133 | 0.038916 | N
14/04/2017 | 12:27 | ZN262:PA15 | URBAN | Asset Failure | Subtransmission | 175 | 39 | 0.0046962 | 0.012042 | N
14/04/2017 | 12:27 | ZN398:PA10 | URBAN | Asset Failure | Subtransmission | 591 | 39 | 0.01586 | 0.040666 | N
14/04/2017 | 12:27 | ZN398:PA11 | URBAN | Asset Failure | Subtransmission | 1,036 | 39 | 0.027801 | 0.071286 | N
14/04/2017 | 12:27 | ZN398:PA15 | URBAN | Asset Failure | Subtransmission | 2 | 39 | 5.3671e-05 | 0.00013762 | N
14/04/2017 | 12:27 | ZN398:PA2 | URBAN | Asset Failure | Subtransmission | 2,890 | 39 | 0.077554 | 0.19886 | N
14/04/2017 | 12:27 | ZN398:PA3 | URBAN | Asset Failure | Subtransmission | 1,926 | 39 | 0.051685 | 0.13253 | N
14/04/2017 | 12:27 | ZN398:PA31 | URBAN | Asset Failure | Subtransmission | 1 | 39 | 2.6835e-05 | 6.8809e-05 | N
14/04/2017 | 12:27 | ZN398:PA4 | URBAN | Asset Failure | Subtransmission | 2,003 | 39 | 0.053751 | 0.13782 | N
14/04/2017 | 12:27 | ZN398:PA9 | URBAN | Asset Failure | Subtransmission | 838 | 39 | 0.022488 | 0.057662 | N
26/05/2017 | 15:53 | ZN1285:PA27 | URBAN | Asset Failure | Subtransmission | 1 | 132 | 9.0714e-05 | 6.8723e-05 | Y
26/05/2017 | 15:53 | ZN1648:PA1 | URBAN | Asset Failure | Subtransmission | 284 | 133 | 0.025958 | 0.019517 | Y
26/05/2017 | 15:53 | ZN1648:PA10 | URBAN | Asset Failure | Subtransmission | 468 | 133 | 0.042776 | 0.032162 | Y
26/05/2017 | 15:53 | ZN1648:PA11 | URBAN | Asset Failure | Subtransmission | 542 | 133 | 0.049539 | 0.037248 | Y
26/05/2017 | 15:53 | ZN1648:PA13 | URBAN | Asset Failure | Subtransmission | 67 | 132 | 0.0060778 | 0.0046044 | Y
26/05/2017 | 15:53 | ZN1648:PA15 | URBAN | Asset Failure | Subtransmission | 1,117 | 132 | 0.10133 | 0.076763 | Y
26/05/2017 | 15:53 | ZN1648:PA16 | URBAN | Asset Failure | Subtransmission | 656 | 132 | 0.059508 | 0.045082 | Y
26/05/2017 | 15:53 | ZN1648:PA19 | URBAN | Asset Failure | Subtransmission | 806 | 132 | 0.073115 | 0.05539 | Y
26/05/2017 | 15:53 | ZN1648:PA2 | URBAN | Asset Failure | Subtransmission | 393 | 133 | 0.035921 | 0.027008 | Y
26/05/2017 | 15:53 | ZN1648:PA20 | URBAN | Asset Failure | Subtransmission | 1,027 | 132 | 0.093163 | 0.070578 | Y
26/05/2017 | 15:53 | ZN1648:PA21 | URBAN | Asset Failure | Subtransmission | 357 | 132 | 0.032385 | 0.024534 | Y
26/05/2017 | 15:53 | ZN1648:PA4 | URBAN | Asset Failure | Subtransmission | 595 | 133 | 0.054384 | 0.04089 | Y
26/05/2017 | 15:53 | ZN1648:PA8 | SHORT RURAL | Asset Failure | Subtransmission | 851 | 133 | 0.50661 | 0.38091 | Y
26/05/2017 | 15:53 | ZN262:PA15 | URBAN | Asset Failure | Subtransmission | 174 | 130 | 0.015545 | 0.011958 | Y
26/05/2017 | 15:53 | ZN398:PA10 | URBAN | Asset Failure | Subtransmission | 593 | 130 | 0.052978 | 0.040753 | Y
26/05/2017 | 15:53 | ZN398:PA11 | URBAN | Asset Failure | Subtransmission | 1,034 | 130 | 0.092377 | 0.071059 | Y
26/05/2017 | 15:53 | ZN398:PA15 | URBAN | Asset Failure | Subtransmission | 1,607 | 138 | 0.1524 | 0.11044 | Y
26/05/2017 | 15:53 | ZN398:PA16 | URBAN | Asset Failure | Subtransmission | 2,278 | 138 | 0.21604 | 0.15655 | Y
26/05/2017 | 15:53 | ZN398:PA19 | URBAN | Asset Failure | Subtransmission | 874 | 138 | 0.082888 | 0.060064 | Y
26/05/2017 | 15:53 | ZN398:PA2 | URBAN | Asset Failure | Subtransmission | 2,893 | 130 | 0.25846 | 0.19881 | Y
26/05/2017 | 15:53 | ZN398:PA20 | URBAN | Asset Failure | Subtransmission | 1,454 | 138 | 0.13789 | 0.099923 | Y
26/05/2017 | 15:53 | ZN398:PA22 | URBAN | Asset Failure | Subtransmission | 81 | 138 | 0.0076818 | 0.0055665 | Y
26/05/2017 | 15:53 | ZN398:PA24 | URBAN | Asset Failure | Subtransmission | 2,017 | 142 | 0.19683 | 0.13861 | Y
26/05/2017 | 15:53 | ZN398:PA25 | URBAN | Asset Failure | Subtransmission | 865 | 142 | 0.084412 | 0.059445 | Y
26/05/2017 | 15:53 | ZN398:PA26 | URBAN | Asset Failure | Subtransmission | 1,082 | 142 | 0.10559 | 0.074358 | Y
26/05/2017 | 15:53 | ZN398:PA29 | URBAN | Asset Failure | Subtransmission | 901 | 142 | 0.087925 | 0.061919 | Y
26/05/2017 | 15:53 | ZN398:PA3 | URBAN | Asset Failure | Subtransmission | 1,924 | 130 | 0.17189 | 0.13222 | Y
26/05/2017 | 15:53 | ZN398:PA30 | URBAN | Asset Failure | Subtransmission | 1,373 | 142 | 0.13399 | 0.094356 | Y
26/05/2017 | 15:53 | ZN398:PA31 | URBAN | Asset Failure | Subtransmission | 915 | 142 | 0.089291 | 0.062881 | Y
26/05/2017 | 15:53 | ZN398:PA4 | URBAN | Asset Failure | Subtransmission | 2,002 | 130 | 0.17886 | 0.13758 | Y
26/05/2017 | 15:53 | ZN398:PA9 | URBAN | Asset Failure | Subtransmission | 836 | 130 | 0.074688 | 0.057452 | Y
26/05/2017 | 15:53 | ZN690:PA10 | URBAN | Asset Failure | Subtransmission | 1,222 | 99 | 0.083139 | 0.083979 | Y
26/05/2017 | 15:53 | ZN690:PA11 | URBAN | Asset Failure | Subtransmission | 1,778 | 99 | 0.12097 | 0.12219 | Y
26/05/2017 | 15:53 | ZN690:PA12 | URBAN | Asset Failure | Subtransmission | 2,006 | 99 | 0.13648 | 0.13786 | Y
26/05/2017 | 15:53 | ZN690:PA14 | URBAN | Asset Failure | Subtransmission | 2,105 | 99 | 0.14321 | 0.14466 | Y
26/05/2017 | 15:53 | ZN690:PA15 | URBAN | Asset Failure | Subtransmission | 545 | 101 | 0.037981 | 0.037454 | Y
26/05/2017 | 15:53 | ZN690:PA17 | URBAN | Asset Failure | Subtransmission | 1,775 | 98 | 0.11954 | 0.12198 | Y
26/05/2017 | 15:53 | ZN690:PA18 | URBAN | Asset Failure | Subtransmission | 1,434 | 98 | 0.096577 | 0.098548 | Y
26/05/2017 | 15:53 | ZN690:PA24 | SHORT RURAL | Asset Failure | Subtransmission | 923 | 98 | 0.40488 | 0.41314 | Y
26/05/2017 | 15:53 | ZN690:PA25 | URBAN | Asset Failure | Subtransmission | 2,312 | 98 | 0.15571 | 0.15889 | Y
26/05/2017 | 15:53 | ZN690:PA26 | URBAN | Asset Failure | Subtransmission | 1,864 | 98 | 0.12554 | 0.1281 | Y
26/05/2017 | 15:53 | ZN690:PA27 | SHORT RURAL | Asset Failure | Subtransmission | 198 | 131 | 0.1161 | 0.088626 | Y
26/05/2017 | 15:53 | ZN690:PA28 | URBAN | Asset Failure | Subtransmission | 1,622 | 131 | 0.14602 | 0.11147 | Y
26/05/2017 | 15:53 | ZN690:PA29 | URBAN | Asset Failure | Subtransmission | 1 | 131 | 9.0027e-05 | 6.8723e-05 | Y
26/05/2017 | 15:53 | ZN690:PA3 | URBAN | Asset Failure | Subtransmission | 507 | 99 | 0.034494 | 0.034842 | Y
26/05/2017 | 15:53 | ZN690:PA30 | URBAN | Asset Failure | Subtransmission | 1,214 | 131 | 0.10929 | 0.083429 | Y
26/05/2017 | 15:53 | ZN690:PA33 | URBAN | Asset Failure | Subtransmission | 1,243 | 131 | 0.1119 | 0.085422 | Y
26/05/2017 | 15:53 | ZN690:PA34 | URBAN | Asset Failure | Subtransmission | 2,170 | 131 | 0.19536 | 0.14913 | Y
26/05/2017 | 15:53 | ZN690:PA35 | URBAN | Asset Failure | Subtransmission | 2,683 | 131 | 0.24154 | 0.18438 | Y
26/05/2017 | 15:53 | ZN690:PA36 | URBAN | Asset Failure | Subtransmission | 1,297 | 131 | 0.11676 | 0.089133 | Y
26/05/2017 | 15:53 | ZN690:PA4 | URBAN | Asset Failure | Subtransmission | 1,365 | 99 | 0.092868 | 0.093806 | Y
26/05/2017 | 15:53 | ZN690:PA5 | URBAN | Asset Failure | Subtransmission | 683 | 99 | 0.046468 | 0.046938 | Y
26/05/2017 | 15:53 | ZN690:PA6 | URBAN | Asset Failure | Subtransmission | 816 | 99 | 0.055517 | 0.056078 | Y
04/10/2016 | 06:38 | ZN711:PA10 | URBAN | Asset Failure | Zone substation | 2 | 93 | 0.00012845 | 0.00013812 | N
04/10/2016 | 06:38 | ZN711:PA11 | URBAN | Asset Failure | Zone substation | 406 | 83 | 0.023272 | 0.028038 | N
04/10/2016 | 06:38 | ZN711:PA12 | URBAN | Asset Failure | Zone substation | 307 | 84 | 0.017809 | 0.021201 | N
04/10/2016 | 06:38 | ZN711:PA13 | URBAN | Asset Failure | Zone substation | 32 | 84 | 0.0018563 | 0.0022099 | N
04/10/2016 | 06:38 | ZN711:PA14 | URBAN | Asset Failure | Zone substation | 639 | 90 | 0.039716 | 0.044129 | N
04/10/2016 | 06:38 | ZN711:PA3 | URBAN | Asset Failure | Zone substation | 345 | 79 | 0.018822 | 0.023825 | N
04/10/2016 | 06:38 | ZN711:PA9 | URBAN | Asset Failure | Zone substation | 92 | 82 | 0.0052098 | 0.0063535 | N
19/10/2016 | 18:19 | 807:74179 | SHORT RURAL | Asset Failure | Zone substation | 136 | 108 | 0.066156 | 0.061256 | N
19/10/2016 | 18:19 | 807:74180 | SHORT RURAL | Asset Failure | Zone substation | 111 | 108 | 0.053995 | 0.049995 | N
19/10/2016 | 18:19 | 807:74181 | SHORT RURAL | Asset Failure | Zone substation | 711 | 108 | 0.34586 | 0.32024 | N
19/10/2016 | 18:19 | 807:74183 | SHORT RURAL | Asset Failure | Zone substation | 88 | 108 | 0.042807 | 0.039636 | N
19/10/2016 | 18:19 | 807:74184 | SHORT RURAL | Asset Failure | Zone substation | 499 | 108 | 0.24273 | 0.22475 | N
24/02/2017 | 20:30 | ZN2466:PA25 | URBAN | Asset Failure | Zone substation | 1,204 | 7 | 0.0058053 | 0.082933 | N
24/02/2017 | 20:30 | ZN2466:PA26 | URBAN | Asset Failure | Zone substation | 25 | 7 | 0.00012054 | 0.001722 | N
24/02/2017 | 20:30 | ZN2466:PA27 | URBAN | Asset Failure | Zone substation | 83 | 7 | 0.0004002 | 0.0057172 | N
24/02/2017 | 20:30 | ZN2466:PA28 | SHORT RURAL | Asset Failure | Zone substation | 533 | 7 | 0.016658 | 0.23797 | N
24/02/2017 | 20:30 | ZN2466:PA29 | URBAN | Asset Failure | Zone substation | 9 | 7 | 4.3395e-05 | 0.00061993 | N
24/02/2017 | 20:30 | ZN2466:PA30 | URBAN | Asset Failure | Zone substation | 1,850 | 7 | 0.0089201 | 0.12743 | N
24/02/2017 | 20:30 | ZN2466:PA31 | URBAN | Asset Failure | Zone substation | 5 | 7 | 2.4108e-05 | 0.00034441 | N
24/02/2017 | 20:30 | ZN2466:PA32 | URBAN | Asset Failure | Zone substation | 37 | 7 | 0.0001784 | 0.0025486 | N
24/02/2017 | 20:30 | ZN2466:PA39 | URBAN | Asset Failure | Zone substation | 5 | 7 | 2.4108e-05 | 0.00034441 | N
24/02/2017 | 20:30 | ZN2466:PA40 | URBAN | Asset Failure | Zone substation | 840 | 7 | 0.0040502 | 0.05786 | N
24/02/2017 | 20:30 | ZN2466:PA41 | URBAN | Asset Failure | Zone substation | 1,162 | 7 | 0.0056028 | 0.08004 | N
24/02/2017 | 20:30 | ZN2466:PA44 | URBAN | Asset Failure | Zone substation | 21 | 7 | 0.00010126 | 0.0014465 | N
24/02/2017 | 20:30 | ZN2466:PA45 | URBAN | Asset Failure | Zone substation | 1,999 | 7 | 0.0096386 | 0.13769 | N
26/04/2017 | 11:40 | ZN340:PA1 | SHORT RURAL | Asset Failure | Zone substation | 966 | 2 | 0.0085779 | 0.4289 | N
26/04/2017 | 11:40 | ZN340:PA10 | URBAN | Asset Failure | Zone substation | 125 | 2 | 0.00017194 | 0.0085971 | N
26/04/2017 | 11:40 | ZN340:PA11 | URBAN | Asset Failure | Zone substation | 308 | 2 | 0.00042366 | 0.021183 | N
26/04/2017 | 11:40 | ZN340:PA2 | URBAN | Asset Failure | Zone substation | 631 | 2 | 0.00086796 | 0.043398 | N
26/04/2017 | 11:40 | ZN340:PA3 | URBAN | Asset Failure | Zone substation | 1,049 | 2 | 0.0014429 | 0.072146 | N
26/04/2017 | 11:40 | ZN340:PA4 | URBAN | Asset Failure | Zone substation | 231 | 2 | 0.00031775 | 0.015887 | N
26/04/2017 | 11:40 | ZN340:PA8 | URBAN | Asset Failure | Zone substation | 670 | 2 | 0.0009216 | 0.04608 | N
11/06/2017 | 09:43 | ZN12580:PA10 | URBAN | Asset Failure | Zone substation | 1,611 | 88 | 0.097425 | 0.11071 | N
11/06/2017 | 09:43 | ZN12580:PA8 | URBAN | Asset Failure | Zone substation | 308 | 86 | 0.018203 | 0.021166 | N
18/06/2017 | 18:45 | ZN12580:PA10 | URBAN | Asset Failure | Zone substation | 1,611 | 22 | 0.024356 | 0.11071 | N
18/06/2017 | 18:45 | ZN12580:PA8 | URBAN | Asset Failure | Zone substation | 307 | 22 | 0.0046415 | 0.021098 | N
18/06/2017 | 19:51 | ZN12580:PA10 | URBAN | Asset Failure | Zone substation | 1,611 | 11 | 0.012178 | 0.11071 | N
18/06/2017 | 19:51 | ZN12580:PA8 | URBAN | Asset Failure | Zone substation | 307 | 11 | 0.0023207 | 0.021098 | N
25/06/2017 | 07:57 | ZN15013:PA1 | URBAN | Asset Failure | Zone substation | 274 | 56 | 0.010532 | 0.018808 | N
25/06/2017 | 07:57 | ZN15013:PA10 | SHORT RURAL | Asset Failure | Zone substation | 442 | 56 | 0.11079 | 0.19784 | N
25/06/2017 | 07:57 | ZN15013:PA12 | URBAN | Asset Failure | Zone substation | 101 | 56 | 0.0038824 | 0.0069329 | N
25/06/2017 | 07:57 | ZN15013:PA2 | URBAN | Asset Failure | Zone substation | 66 | 56 | 0.002537 | 0.0045304 | N
25/06/2017 | 07:57 | ZN15013:PA4 | URBAN | Asset Failure | Zone substation | 824 | 56 | 0.031674 | 0.056561 | N
25/06/2017 | 07:57 | ZN15013:PA6 | SHORT RURAL | Asset Failure | Zone substation | 228 | 56 | 0.05715 | 0.10205 | N
25/06/2017 | 07:57 | ZN15013:PA8 | URBAN | Asset Failure | Zone substation | 131 | 56 | 0.0050356 | 0.0089921 | N
01/07/2016 | 06:48 | 240:34849 | SHORT RURAL | Other | Other | 1 | 131 | 0.00059677 | 0.00045526 | N
01/07/2016 | 09:11 | 216:10729 | URBAN | Other | Other | 1 | 93 | 6.4167e-05 | 6.9257e-05 | N
01/07/2016 | 12:30 | 528:83011 | SHORT RURAL | Other | Other | 1 | 229 | 0.0010441 | 0.00045526 | N
02/07/2016 | 10:50 | ZN12610:PA6 | URBAN | Other | Other | 1 | 85 | 5.8732e-05 | 6.9259e-05 | N
03/07/2016 | 06:07 | 216:10727 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 58 | 0.00079216 | 0.0013658 | N
03/07/2016 | 08:28 | 261:81882 | URBAN | Other | Other | 1 | 87 | 6.0187e-05 | 6.926e-05 | N
03/07/2016 | 14:07 | 222:33602 | URBAN | Other | Other | 1 | 73 | 5.0467e-05 | 6.926e-05 | N
03/07/2016 | 20:03 | ZN10996:PA9 | URBAN | Other | Other - Arcing | 1 | 221 | 0.00015311 | 6.926e-05 | N
01/07/2016 | 07:00 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 110 | 0.0020031 | 0.001821 | N
04/07/2016 | 13:36 | ZN2196:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 44 | 131 | 0.026148 | 0.020032 | N
04/07/2016 | 15:25 | 528:83013 | URBAN | Other | Other | 1 | 99 | 6.8752e-05 | 6.926e-05 | N
04/07/2016 | 19:18 | ZN10990:PA2 | URBAN | Other | Other - Self Clearing Trigger | 64 | 86 | 0.0038283 | 0.0044326 | N
04/07/2016 | 20:00 | 230:81432 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 850 | 0.019345 | 0.0022763 | N
04/07/2016 | 20:59 | ZN35800:PA7 | URBAN | Other | Other - Self Clearing Trigger | 64 | 181 | 0.008023 | 0.0044326 | N
05/07/2016 | 07:39 | ZN35800:PA1 | URBAN | Other | Other - Arcing | 7 | 261 | 0.0012653 | 0.0004848 | N
05/07/2016 | 07:46 | 528:83014 | SHORT RURAL | Other | Other - Self Clearing Trigger | 73 | 134 | 0.044539 | 0.033238 | N
05/07/2016 | 10:17 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 103 | 0.00046807 | 0.00045532 | N
05/07/2016 | 12:02 | ZN15005:PA4 | URBAN | Other | Other - Arcing | 1 | 148 | 0.00010242 | 6.9258e-05 | N
05/07/2016 | 14:34 | 205:12206 | URBAN | Other | Other | 7 | 80 | 0.00038881 | 0.0004848 | N
05/07/2016 | 14:46 | 220:8687 | URBAN | Other | Other | 1 | 110 | 7.5987e-05 | 6.9258e-05 | N
05/07/2016 | 18:48 | 228:7491 | URBAN | Other | Other | 1 | 101 | 6.9962e-05 | 6.9258e-05 | N
05/07/2016 | 21:59 | 502:48010 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,519 | 60 | 0.41394 | 0.69163 | N
06/07/2016 | 10:06 | ZN15005:PA4 | URBAN | Other | Other | 1 | 69 | 4.802e-05 | 6.9259e-05 | N
06/07/2016 | 11:23 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 117 | 0.00053273 | 0.00045533 | N
06/07/2016 | 12:39 | 532:83314 | URBAN | Other | Other | 1 | 51 | 3.5149e-05 | 6.9259e-05 | N
06/07/2016 | 16:42 | 213:33771 | URBAN | Other | Other | 1 | 148 | 0.00010239 | 6.9259e-05 | N
06/07/2016 | 17:30 | 235:2857 | SHORT RURAL | Other | Other | 1 | 254 | 0.0011554 | 0.00045533 | N
06/07/2016 | 23:47 | ZN12620:PA7 | URBAN | Other | Other - Self Clearing Trigger | 1 | 379 | 0.00026277 | 6.9259e-05 | N
06/07/2016 | 23:58 | ZN12620:PA7 | URBAN | Other | Other - Arcing | 1 | 631 | 0.00043728 | 6.9259e-05 | N
07/07/2016 | 05:35 | ZN1287:PA15 | URBAN | Other | Other - Arcing | 1 | 264 | 0.00018289 | 6.9245e-05 | N
07/07/2016 | 06:18 | ZN1788:PA8 | URBAN | Other | Other | 1 | 82 | 5.6966e-05 | 6.9245e-05 | N
07/07/2016 | 13:30 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,215 | 0.0055313 | 0.00045525 | N
07/07/2016 | 13:52 | ZN690:PA36 | URBAN | Other | Other - Arcing | 1 | 488 | 0.00033762 | 6.9245e-05 | N
07/07/2016 | 16:21 | 504:48026 | SHORT RURAL | Other | Other | 1 | 318 | 0.0014484 | 0.00045525 | N
07/07/2016 | 22:50 | 261:81886 | URBAN | Other | Other - Self Clearing Trigger | 16 | 55 | 0.00060936 | 0.0011079 | N
07/07/2016 | 18:55 | 220:8691 | URBAN | Other | Other - Arcing | 1 | 95 | 6.5621e-05 | 6.9245e-05 | N
08/07/2016 | 02:08 | ZN1673:PA18 | URBAN | Other | Other - Arcing | 1 | 801 | 0.00055473 | 6.9246e-05 | N
08/07/2016 | 13:34 | ZN9534:PA17 | URBAN | Other | Other - Arcing | 1 | 446 | 0.00030849 | 6.9246e-05 | N
08/07/2016 | 14:00 | 258:80793 | URBAN | Other | Other - Self Clearing Trigger | 124 | 260 | 0.022325 | 0.0085865 | N
08/07/2016 | 23:55 | ZN3154:PA18 | URBAN | Other | Other | 1 | 127 | 8.7896e-05 | 6.9246e-05 | N
09/07/2016 | 01:54 | 258:80793 | URBAN | Other | Other | 1 | 383 | 0.00026508 | 6.925e-05 | N
09/07/2016 | 10:08 | 217:33611 | URBAN | Other | Other | 1 | 170 | 0.00011755 | 6.925e-05 | N
09/07/2016 | 16:30 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 160 | 0.057061 | 0.035663 | N
09/07/2016 | 18:11 | ZN2602:PA9 | URBAN | Other | Other - Arcing | 1 | 185 | 0.00012779 | 6.925e-05 | N
09/07/2016 | 19:19 | 232:11455 | SHORT RURAL | Other | Other - Self Clearing Trigger | 54 | 121 | 0.029717 | 0.024583 | N
10/07/2016 | 01:49 | 224:80337 | SHORT RURAL | Other | Other - Arcing | 1 | 202 | 0.00092133 | 0.00045524 | N
10/07/2016 | 10:18 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 192 | 0.0069925 | 0.0036419 | N
11/07/2016 | 08:33 | ZN2196:PA11 | URBAN | Other | Other - Self Clearing Trigger | 3 | 212 | 0.00044043 | 0.00020775 | N
11/07/2016 | 09:16 | ZN167:PA1 | URBAN | Other | Other - Arcing | 1 | 104 | 7.1847e-05 | 6.925e-05 | N
11/07/2016 | 10:21 | ZN847:PA19 | URBAN | Other | Other - Self Clearing Trigger | 31 | 89 | 0.0019106 | 0.0021468 | N
11/07/2016 | 14:48 | ZN35800:PA16 | URBAN | Other | Other - Self Clearing Trigger | 17 | 72 | 0.00084664 | 0.0011773 | N
11/07/2016 | 19:45 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 110 | 0.0020031 | 0.001821 | N
11/07/2016 | 20:25 | ZN4545:PA4 | URBAN | Other | Other - Self Clearing Trigger | 45 | 54 | 0.0016916 | 0.0031163 | N
12/07/2016 | 07:03 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 31 | 147 | 0.020746 | 0.014113 | N
12/07/2016 | 08:49 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 141 | 0.0006419 | 0.00045525 | N
12/07/2016 | 09:32 | 528:83019 | SHORT RURAL | Other | Other | 1 | 17 | 7.8379e-05 | 0.00045525 | N
12/07/2016 | 10:13 | 532:83293 | URBAN | Other | Other | 1 | 47 | 3.2249e-05 | 6.9252e-05 | N
12/07/2016 | 14:03 | 512:48048 | SHORT RURAL | Other | Other | 1 | 346 | 0.0015753 | 0.00045525 | N
12/07/2016 | 16:14 | 512:48046 | SHORT RURAL | Other | Other | 1 | 247 | 0.0011254 | 0.00045525 | N
12/07/2016 | 17:44 | 507:80932 | SHORT RURAL | Other | Other | 1 | 89 | 0.00040343 | 0.00045525 | N
12/07/2016 | 17:48 | 526:34639 | SHORT RURAL | Other | Other | 1 | 121 | 0.00055115 | 0.00045525 | N
12/07/2016 | 18:19 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 176 | 0.1883 | 0.10699 | N
12/07/2016 | 18:35 | ZN3472:PA28 | URBAN | Other | Other - Self Clearing Trigger | 48 | 115 | 0.0038172 | 0.0033241 | N
12/07/2016 | 19:53 | 526:34639 | SHORT RURAL | Other | Other | 1 | 91 | 0.00041344 | 0.00045525 | N
12/07/2016 | 23:54 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 461 | 115 | 0.24207 | 0.20987 | N
13/07/2016 | 05:17 | 261:81886 | URBAN | Other | Other - Arcing | 1 | 193 | 0.00013333 | 6.9254e-05 | N
13/07/2016 | 08:25 | ZN12570:PA22 | SHORT RURAL | Other | Other | 1 | 35 | 0.00015737 | 0.00045526 | N
13/07/2016 | 09:10 | ZN2635:PA57 | URBAN | Other | Other - Self Clearing Trigger | 81 | 140 | 0.0078534 | 0.0056096 | N
12/07/2016 | 11:25 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,440 | 0.0065556 | 0.00045525 | N
13/07/2016 | 10:55 | ZN3425:PA30 | URBAN | Other | Other - Arcing | 1 | 155 | 0.00010714 | 6.9254e-05 | N
13/07/2016 | 12:36 | ZN12640:PA6 | URBAN | Other | Other - Self Clearing Trigger | 15 | 194 | 0.0020153 | 0.0010388 | N
13/07/2016 | 12:51 | ZN12640:PA15 | URBAN | Other | Other - Self Clearing Trigger | 1 | 117 | 8.1316e-05 | 6.9254e-05 | N
13/07/2016 | 13:54 | ZN847:PA22 | URBAN | Other | Other - Self Clearing Trigger | 80 | 150 | 0.0082855 | 0.0055403 | N
13/07/2016 | 14:11 | 221:11899 | SHORT RURAL | Other | Other | 1 | 23 | 0.000106 | 0.00045526 | N
13/07/2016 | 16:50 | ZN12640:PA1 | SHORT RURAL | Other | Other | 1 | 35 | 0.00016116 | 0.00045526 | N
13/07/2016 | 17:36 | 227:13015 | SHORT RURAL | Other | Other - Self Clearing Trigger | 56 | 92 | 0.023455 | 0.025494 | N
13/07/2016 | 17:39 | ZN2835:PA18 | URBAN | Other | Other - Arcing | 1 | 368 | 0.00025454 | 6.9254e-05 | N
14/07/2016 | 06:19 | ZN9245:PA40 | URBAN | Other | Other - Self Clearing Trigger | 53 | 110 | 0.0040406 | 0.0036705 | N
14/07/2016 | 08:17 | ZN12640:PA19 | URBAN | Other | Other - Arcing | 1 | 192 | 0.0001332 | 6.9255e-05 | N
14/07/2016 | 10:12 | ZN4545:PA6 | URBAN | Other | Other | 1 | 109 | 7.5141e-05 | 6.9255e-05 | N
14/07/2016 | 11:45 | 213:33771 | URBAN | Other | Other | 1 | 125 | 8.6315e-05 | 6.9255e-05 | N
14/07/2016 | 15:33 | ZN2310:PA53 | URBAN | Other | Other | 1 | 282 | 0.00019533 | 6.9255e-05 | N
14/07/2016 | 15:45 | ZN36100:PA12 | URBAN | Other | Other - Self Clearing Trigger | 47 | 79 | 0.0025872 | 0.003255 | N
14/07/2016 | 15:45 | ZN36100:PA5 | URBAN | Other | Other - Self Clearing Trigger | 1 | 80 | 5.5404e-05 | 6.9255e-05 | N
15/07/2016 | 09:56 | ZN14892:PA19 | URBAN | Other | Other - Arcing | 1 | 94 | 6.51e-05 | 6.9256e-05 | N
16/07/2016 | 03:00 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 119 | 0.042455 | 0.035676 | N
16/07/2016 | 07:20 | ZN690:PA36 | URBAN | Other | Other - Self Clearing Trigger | 19 | 220 | 0.0028893 | 0.0013156 | N
16/07/2016 | 08:11 | ZN2635:PA35 | URBAN | Other | Other - Self Clearing Trigger | 53 | 78 | 0.0028753 | 0.0036699 | N
16/07/2016 | 09:19 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 36 | 75 | 0.012323 | 0.016347 | N
16/07/2016 | 11:04 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 56 | 0.019979 | 0.035676 | N
16/07/2016 | 14:12 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 93 | 0.00042229 | 0.00045407 | N
16/07/2016 | 17:54 | 228:7490 | SHORT RURAL | Other | Other | 2 | 170 | 0.0015454 | 0.00090815 | N
17/07/2016 | 16:33 | ZN36300:PA11 | URBAN | Other | Other - Arcing | 1 | 231 | 0.00015994 | 6.9243e-05 | N
18/07/2016 | 12:33 | ZN262:PA20 | URBAN | Other | Other - Arcing | 41 | 484 | 0.013737 | 0.0028389 | N
19/07/2016 | 10:14 | ZN10993:PA33 | URBAN | Other | Other - Self Clearing Trigger | 700 | 84 | 0.040511 | 0.048471 | N
19/07/2016 | 10:14 | ZN10993:PA35 | URBAN | Other | Other - Self Clearing Trigger | 1 | 83 | 5.7473e-05 | 6.9244e-05 | N
19/07/2016 | 10:45 | 223:14394 | URBAN | Other | Other - Self Clearing Trigger | 189 | 67 | 0.0087509 | 0.013087 | N
19/07/2016 | 11:01 | ZN15011:PA10 | URBAN | Other | Other | 1 | 107 | 7.4345e-05 | 6.9244e-05 | N
19/07/2016 | 12:39 | 205:12213 | SHORT RURAL | Other | Other | 1 | 59 | 0.00026942 | 0.00045433 | N
19/07/2016 | 13:21 | 214:8666 | URBAN | Other | Other | 1 | 54 | 3.768e-05 | 6.9244e-05 | N
19/07/2016 | 14:09 | ZN2635:PA32 | URBAN | Other | Other - Self Clearing Trigger | 19 | 101 | 0.0013288 | 0.0013156 | N
19/07/2016 | 14:43 | ZN36300:PA5 | URBAN | Other | Other | 1 | 42 | 2.9336e-05 | 6.9244e-05 | N
19/07/2016 | 15:35 | ZN36300:PA8 | URBAN | Other | Other | 1 | 53 | 3.7034e-05 | 6.9244e-05 | N
19/07/2016 | 23:30 | ZN10993:PA23 | URBAN | Other | Other - Arcing | 1 | 718 | 0.0004973 | 6.9244e-05 | N
20/07/2016 | 09:51 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 6 | 129 | 0.27603 | 0.21398 | N
20/07/2016 | 10:25 | ZN9550:PA9 | URBAN | Other | Other - Self Clearing Trigger | 153 | 86 | 0.0091089 | 0.010592 | N
20/07/2016 | 10:38 | ZN129:PA8 | URBAN | Other | Other - Arcing | 1 | 202 | 0.00013968 | 6.9227e-05 | N
20/07/2016 | 16:20 | ZN195:PA11 | URBAN | Other | Other | 1 | 76 | 5.2405e-05 | 6.9227e-05 | N
20/07/2016 | 16:27 | 228:7487 | URBAN | Other | Other | 1 | 77 | 5.342e-05 | 6.9227e-05 | N
20/07/2016 | 17:47 | ZN35900:PA16 | URBAN | Other | Other - Self Clearing Trigger | 12 | 103 | 0.00085564 | 0.00083072 | N
21/07/2016 | 08:49 | ZN12600:PA3 | URBAN | Other | Other | 1 | 368 | 0.00025467 | 6.9229e-05 | N
21/07/2016 | 09:08 | ZN15002:PA2 | URBAN | Other | Other | 1 | 211 | 0.0001464 | 6.9229e-05 | N
21/07/2016 | 09:53 | ZN15011:PA6 | URBAN | Other | Other - Arcing | 1 | 279 | 0.00019293 | 6.9229e-05 | N
21/07/2016 | 11:10 | ZN15004:PA1 | URBAN | Other | Other | 1 | 150 | 0.00010362 | 6.9229e-05 | N
22/07/2016 | 08:00 | ZN14891:PA20 | SHORT RURAL | Other | Other - Arcing | 1 | 120 | 0.00054353 | 0.00045395 | N
22/07/2016 | 08:55 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 185 | 0.00083845 | 0.00045395 | N
22/07/2016 | 09:37 | 221:11895 | URBAN | Other | Other | 1 | 307 | 0.00021261 | 6.9235e-05 | N
22/07/2016 | 19:43 | ZN4545:PA41 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,054 | 97 | 0.46411 | 0.47847 | N
22/07/2016 | 19:47 | 802:82220 | SHORT RURAL | Other | Other - Self Clearing Trigger | 28 | 237 | 0.030183 | 0.012711 | N
23/07/2016 | 04:48 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 10 | 952 | 3.3964 | 0.35676 | N
23/07/2016 | 06:57 | ZN15006:PA8 | URBAN | Other | Other - Arcing | 1 | 415 | 0.00028751 | 6.9235e-05 | N
23/07/2016 | 07:01 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 892 | 115 | 0.4638 | 0.40489 | N
23/07/2016 | 08:37 | 532:83293 | URBAN | Other | Other | 1 | 123 | 8.4951e-05 | 6.9235e-05 | N
23/07/2016 | 11:15 | ZN35370:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 20 | 0.0009986 | 0.004993 | N
23/07/2016 | 14:15 | ZN3922:PA10 | URBAN | Other | Other | 1 | 84 | 5.8238e-05 | 6.9235e-05 | N
24/07/2016 | 07:06 | 223:14394 | URBAN | Other | Other | 1 | 213 | 0.00014754 | 6.9235e-05 | N
24/07/2016 | 08:22 | 258:80778 | URBAN | Other | Other | 1 | 37 | 2.5871e-05 | 6.9235e-05 | N
24/07/2016 | 13:53 | 507:80932 | SHORT RURAL | Other | Other | 1 | 51 | 0.00023172 | 0.00045391 | N
25/07/2016 | 08:48 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 191 | 0.00086764 | 0.00045391 | N
25/07/2016 | 12:00 | ZN15008:PA5 | URBAN | Other | Other - Self Clearing Trigger | 108 | 75 | 0.0055918 | 0.0074774 | N
25/07/2016 | 14:42 | ZN15001:PA15 | URBAN | Other | Other | 1 | 127 | 8.8263e-05 | 6.9235e-05 | N
25/07/2016 | 15:20 | ZN15010:PA11 | URBAN | Other | Other | 1 | 161 | 0.00011112 | 6.9235e-05 | N
25/07/2016 | 16:27 | ZN3154:PA22 | SHORT RURAL | Other | Other - Self Clearing Trigger | 24 | 152 | 0.016577 | 0.010894 | N
25/07/2016 | 19:52 | 524:33578 | URBAN | Other | Other | 1 | 62 | 4.3226e-05 | 6.9235e-05 | N
26/07/2016 | 07:15 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 80 | 0.0010894 | 0.0013617 | N
26/07/2016 | 09:02 | 202:34254 | URBAN | Other | Other | 1 | 133 | 9.2163e-05 | 6.9235e-05 | N
26/07/2016 | 11:14 | ZN12690:PA7 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 171 | 0.0062095 | 0.0036313 | N
26/07/2016 | 16:20 | ZN15013:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 150 | 0.0013617 | 0.00090782 | N
26/07/2016 | 19:00 | ZN12610:PA23 | URBAN | Other | Other | 1 | 74 | 5.1245e-05 | 6.9235e-05 | N
27/07/2016 | 06:45 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 325 | 0.039779 | 0.012256 | N
27/07/2016 | 12:10 | 230:81438 | SHORT RURAL | Other | Other - Arcing | 1 | 290 | 0.0013141 | 0.00045393 | N
27/07/2016 | 16:10 | 221:11900 | SHORT RURAL | Other | Other | 1 | 51 | 0.00023082 | 0.00045393 | N
27/07/2016 | 22:31 | ZN12650:PA1 | SHORT RURAL | Other | Other - Arcing | 44 | 54 | 0.010785 | 0.019973 | N
28/07/2016 | 09:38 | ZN35600:PA4 | URBAN | Other | Other - Arcing | 1 | 141 | 9.7876e-05 | 6.9227e-05 | N
28/07/2016 | 10:27 | 206:34432 | URBAN | Other | Other | 1 | 132 | 9.1576e-05 | 6.9227e-05 | N
28/07/2016 | 10:42 | ZN1285:PA27 | URBAN | Other | Other | 1 | 137 | 9.5014e-05 | 6.9227e-05 | N
28/07/2016 | 12:23 | 227:13015 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 221 | 0.0010028 | 0.00045373 | N
28/07/2016 | 15:42 | ZN2635:PA43 | URBAN | Other | Other - Self Clearing Trigger | 67 | 83 | 0.0038281 | 0.0046382 | N
28/07/2016 | 15:42 | ZN2635:PA58 | URBAN | Other | Other - Self Clearing Trigger | 54 | 68 | 0.002542 | 0.0037383 | N
28/07/2016 | 19:01 | ZN10996:PA19 | URBAN | Other | Other - Arcing | 982 | 92 | 0.06277 | 0.067981 | N
28/07/2016 | 19:01 | ZN10999:PA11 | URBAN | Other | Other - Arcing | 2,059 | 136 | 0.19388 | 0.14254 | N
29/07/2016 | 19:33 | ZN398:PA20 | URBAN | Other | Other - Arcing | 7 | 237 | 0.0011485 | 0.00048459 | N
30/07/2016 | 09:25 | ZN9118:PA26 | URBAN | Other | Other - Self Clearing Trigger | 10 | 225 | 0.0015576 | 0.00069228 | N
30/07/2016 | 15:56 | ZN14144:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 25 | 58 | 0.006624 | 0.011342 | N
30/07/2016 | 20:17 | ZN12650:PA9 | URBAN | Other | Other | 1 | 141 | 9.7439e-05 | 6.9228e-05 | N
31/07/2016 | 03:06 | ZN12580:PA4 | URBAN | Other | Other - Self Clearing Trigger | 153 | 202 | 0.021368 | 0.010592 | N
31/07/2016 | 12:00 | ZN15005:PA12 | URBAN | Other | Other | 1 | 69 | 4.7999e-05 | 6.923e-05 | N
31/07/2016 | 21:03 | 502:48008 | URBAN | Other | Other | 1 | 72 | 4.9557e-05 | 6.923e-05 | N
31/07/2016 | 02:40 | ZN9900:PA21 | URBAN | Other | Other - Self Clearing Trigger | 41 | 280 | 0.0079476 | 0.0028384 | N
02/08/2016 | 10:35 | ZN4545:PA36 | URBAN | Other | Other - Arcing | 1 | 255 | 0.00017647 | 6.923e-05 | N
02/08/2016 | 15:19 | ZN2310:PA53 | URBAN | Other | Other - Arcing | 1 | 916 | 0.00063444 | 6.923e-05 | N
02/08/2016 | 23:47 | ZN15013:PA8 | URBAN | Other | Other - Self Clearing Trigger | 1 | 372 | 0.00025749 | 6.923e-05 | N
02/08/2016 | 23:48 | ZN15004:PA9 | URBAN | Other | Other - Self Clearing Trigger | 1 | 372 | 0.00025736 | 6.923e-05 | N
03/08/2016 | 07:22 | ZN847:PA36 | URBAN | Other | Other - Arcing | 1 | 37 | 2.5765e-05 | 6.9231e-05 | N
03/08/2016 | 07:38 | ZN3154:PA17 | URBAN | Other | Other - Arcing | 1 | 81 | 5.6285e-05 | 6.9231e-05 | N
03/08/2016 | 17:42 | ZN10999:PA36 | URBAN | Other | Other - Arcing | 1 | 347 | 0.0002403 | 6.9231e-05 | N
03/08/2016 | 19:53 | 224:80346 | URBAN | Other | Other | 1 | 122 | 8.4254e-05 | 6.9231e-05 | N
03/08/2016 | 20:54 | ZN1068:PA26 | URBAN | Other | Other - Arcing | 1 | 270 | 0.00018682 | 6.9231e-05 | N
04/08/2016 | 06:10 | ZN187:PA14 | URBAN | Other | Other - Self Clearing Trigger | 95 | 140 | 0.0091786 | 0.0065718 | N
04/08/2016 | 07:37 | ZN15011:PA2 | URBAN | Other | Other - Self Clearing Trigger | 7 | 149 | 0.00072377 | 0.00048424 | N
04/08/2016 | 08:20 | ZN3425:PA27 | URBAN | Other | Other - Arcing | 4 | 500 | 0.0013835 | 0.00027671 | N
04/08/2016 | 10:32 | ZN2602:PA36 | URBAN | Other | Other - Arcing | 1 | 207 | 0.00014333 | 6.9177e-05 | N
04/08/2016 | 10:59 | ZN14892:PA19 | URBAN | Other | Other | 1 | 198 | 0.00013665 | 6.9177e-05 | N
04/08/2016 | 13:11 | ZN3155:PA35 | URBAN | Other | Other - Self Clearing Trigger | 26 | 109 | 0.0019578 | 0.0017986 | N
04/08/2016 | 14:12 | 203:8084 | URBAN | Other | Other - Arcing | 1 | 137 | 9.4783e-05 | 6.9177e-05 | N
04/08/2016 | 16:47 | ZN35900:PA2 | URBAN | Other | Other | 1 | 173 | 0.00011955 | 6.9177e-05 | N
04/08/2016 | 17:23 | ZN12610:PA24 | URBAN | Other | Other - Arcing | 1 | 972 | 0.00067212 | 6.9177e-05 | N
05/08/2016 | 03:39 | ZN35800:PA14 | URBAN | Other | Other - Arcing | 1 | 410 | 0.00028379 | 6.9177e-05 | N
05/08/2016 | 06:16 | ZN3672:PA46 | URBAN | Other | Other - Arcing | 5 | 254 | 0.00087855 | 0.00034588 | N
05/08/2016 | 07:54 | ZN262:PA42 | URBAN | Other | Other - Self Clearing Trigger | 98 | 90 | 0.0061025 | 0.0067793 | N
05/08/2016 | 09:01 | ZN129:PA5 | URBAN | Other | Other - Self Clearing Trigger | 8 | 134 | 0.00074158 | 0.00055342 | N
05/08/2016 | 10:08 | 240:34849 | SHORT RURAL | Other | Other | 1 | 202 | 0.0009176 | 0.00045463 | N
05/08/2016 | 11:49 | ZN36300:PA11 | URBAN | Other | Other - Arcing | 1 | 131 | 9.0576e-05 | 6.9177e-05 | N
06/08/2016 | 21:21 | ZN12610:PA13 | URBAN | Other | Other - Arcing | 1 | 198 | 0.00013728 | 6.9178e-05 | N
07/08/2016 | 08:32 | ZN35500:PA24 | URBAN | Other | Other - Self Clearing Trigger | 38 | 107 | 0.0028163 | 0.0026288 | N
07/08/2016 | 08:32 | ZN2400:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 672 | 53 | 0.16192 | 0.30551 | N
07/08/2016 | 12:13 | ZN15002:PA2 | URBAN | Other | Other - Arcing | 1 | 256 | 0.00017675 | 6.9178e-05 | N
07/08/2016 | 14:33 | 206:34441 | URBAN | Other | Other - Arcing | 1 | 128 | 8.8686e-05 | 6.9178e-05 | N
07/08/2016 | 14:35 | 202:34231 37 42 | URBAN | Other | Other - Arcing | 100 | 205 | 0.014178 | 0.0069178 | N
07/08/2016 | 16:23 | 504:48033 | SHORT RURAL | Other | Other | 1 | 66 | 0.00029922 | 0.00045463 | N
07/08/2016 | 19:51 | 224:80341 | URBAN | Other | Other - Arcing | 1 | 129 | 8.9113e-05 | 6.9178e-05 | N
08/08/2016 | 12:15 | ZN14891:PA9 | URBAN | Other | Other | 1 | 334 | 0.00023101 | 6.9178e-05 | N
09/08/2016 | 10:10 | ZN14891:PA16 | SHORT RURAL | Other | Other | 1 | 405 | 0.001849 | 0.00045611 | N
09/08/2016 | 11:17 | 507:80932 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 93 | 0.00084837 | 0.00091223 | N
09/08/2016 | 16:15 | ZN10999:PA24 | URBAN | Other | Other - Self Clearing Trigger | 109 | 65 | 0.0048886 | 0.0075403 | N
09/08/2016 | 17:22 | ZN35600:PA16 | URBAN | Other | Other - Arcing | 1 | 158 | 0.00010918 | 6.9177e-05 | N
10/08/2016 | 10:36 | 258:80785 | URBAN | Other | Other | 1 | 127 | 8.7707e-05 | 6.9179e-05 | N
10/08/2016 | 13:15 | 239:82136 | SHORT RURAL | Other | Other | 1 | 61 | 0.00027816 | 0.00045612 | N
11/08/2016 | 08:49 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 136 | 0.00062016 | 0.000456 | N
11/08/2016 | 09:00 | 230:81438 | SHORT RURAL | Other | Other | 1 | 144 | 0.00065611 | 0.000456 | N
11/08/2016 | 09:26 | 230:81438 | SHORT RURAL | Other | Other | 1 | 134 | 0.00061051 | 0.000456 | N
11/08/2016 | 10:59 | ZN12650:PA17 | URBAN | Other | Other | 1 | 251 | 0.00017345 | 6.9155e-05 | N
12/08/2016 | 08:41 | 528:83019 | SHORT RURAL | Other | Other | 1 | 31 | 0.00014288 | 0.00045601 | N
12/08/2016 | 08:45 | 528:83024 | URBAN | Other | Other | 1 | 74 | 5.1475e-05 | 6.9156e-05 | N
12/08/2016 | 08:48 | 528:83013 | URBAN | Other | Other | 1 | 170 | 0.00011788 | 6.9156e-05 | N
12/08/2016 | 08:50 | 528:83014 | SHORT RURAL | Other | Other | 1 | 27 | 0.00012137 | 0.00045601 | N
12/08/2016 | 13:32 | ZN35600:PA9 | URBAN | Other | Other | 1 | 118 | 8.1281e-05 | 6.9156e-05 | N
12/08/2016 | 13:56 | ZN262:PA42 | URBAN | Other | Other - Self Clearing Trigger | 98 | 143 | 0.0096994 | 0.0067773 | N
12/08/2016 | 16:22 | ZN12570:PA25 | SHORT RURAL | Other | Other | 1 | 490 | 0.0022354 | 0.00045601 | N
12/08/2016 | 20:25 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 60 | 0.00027193 | 0.00045601 | N
13/08/2016 | 01:54 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 51 | 0.00046514 | 0.00091203 | N
13/08/2016 | 07:16 | ZN36100:PA15 | URBAN | Other | Other - Arcing | 1 | 284 | 0.00019611 | 6.9157e-05 | N
13/08/2016 | 08:49 | 224:80340 | SHORT RURAL | Other | Other | 1 | 84 | 0.00038412 | 0.00045602 | N
13/08/2016 | 10:51 | 507:80932 | SHORT RURAL | Other | Other | 1 | 284 | 0.0012959 | 0.00045602 | N
13/08/2016 | 16:35 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 130 | 63 | 0.037111 | 0.059282 | N
13/08/2016 | 22:35 | ZN180:PA34 | URBAN | Other | Other - Self Clearing Trigger | 15 | 70 | 0.00072615 | 0.0010374 | N
13/08/2016 | 22:40 | 261:81879 | URBAN | Other | Other - Self Clearing Trigger | 109 | 44 | 0.0033168 | 0.0075381 | N
14/08/2016 | 10:05 | 504:48031 | SHORT RURAL | Other | Other | 1 | 86 | 0.00039118 | 0.00045602 | N
14/08/2016 | 11:28 | ZN2196:PA12 | URBAN | Other | Other - Self Clearing Trigger | 3 | 1,202 | 0.0024938 | 0.00020747 | N
14/08/2016 | 15:16 | 258:80793 | URBAN | Other | Other | 1 | 42 | 2.8977e-05 | 6.9157e-05 | N
15/08/2016 | 11:26 | 228:7490 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 183 | 0.010015 | 0.0054722 | N
16/08/2016 | 06:39 | ZN3154:PA19 | URBAN | Other | Other - Arcing | 1 | 140 | 9.7016e-05 | 6.9157e-05 | N
16/08/2016 | 08:29 | ZN1285:PA24 | URBAN | Other | Other - Arcing | 1 | 211 | 0.00014569 | 6.9157e-05 | N
16/08/2016 | 13:48 | ZN3472:PA33 | URBAN | Other | Other | 1 | 370 | 0.00025559 | 6.9157e-05 | N
16/08/2016 | 15:24 | 221:11893 | URBAN | Other | Other | 1 | 41 | 2.8251e-05 | 6.9157e-05 | N
17/08/2016 | 12:36 | 512:48046 | SHORT RURAL | Other | Other | 1 | 98 | 0.00044865 | 0.00045602 | N
17/08/2016 | 14:11 | ZN10990:PA2 | URBAN | Other | Other - Arcing | 1 | 288 | 0.00019919 | 6.916e-05 | N
17/08/2016 | 19:43 | 513:48059 | SHORT RURAL | Other | Other - Arcing | 1 | 1,156 | 0.0052728 | 0.00045602 | N
18/08/2016 | 12:30 | 512:48048 | SHORT RURAL | Other | Other | 1 | 65 | 0.00030323 | 0.00046353 | N
19/08/2016 | 08:41 | 214:8669 | URBAN | Other | Other | 1 | 54 | 3.7129e-05 | 6.9379e-05 | N
19/08/2016 | 14:36 | ZN15011:PA6 | URBAN | Other | Other - Self Clearing Trigger | 57 | 171 | 0.0067558 | 0.0039546 | N
19/08/2016 | 23:09 | 205:12206 | URBAN | Other | Other | 1 | 490 | 0.00034018 | 6.9379e-05 | N
20/08/2016 | 00:18 | ZN690:PA34 | URBAN | Other | Other - Arcing | 1 | 988 | 0.00068548 | 6.938e-05 | N
20/08/2016 | 00:35 | ZN398:PA15 | URBAN | Other | Other - Arcing | 3 | 693 | 0.0014424 | 0.00020814 | N
20/08/2016 | 07:22 | ZN188:PA21 | URBAN | Other | Other - Arcing | 1 | 423 | 0.00029381 | 6.938e-05 | N
20/08/2016 | 08:05 | ZN129:PA3 | URBAN | Other | Other - Self Clearing Trigger | 84 | 224 | 0.013068 | 0.0058279 | N
20/08/2016 | 08:43 | ZN188:PA21 | URBAN | Other | Other - Arcing | 1 | 342 | 0.00023752 | 6.938e-05 | N
20/08/2016 | 11:04 | ZN15014:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 296 | 0.0013717 | 0.00046353 | N
20/08/2016 | 18:00 | 504:48026 | SHORT RURAL | Other | Other | 1 | 89 | 0.00041417 | 0.00046353 | N
20/08/2016 | 20:00 | 512:48046 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 80 | 0.00074165 | 0.00092706 | N
21/08/2016 | 10:29 | 227:13020 | SHORT RURAL | Other | Other | 1 | 51 | 0.0002354 | 0.00046353 | N
21/08/2016 | 13:04 | 239:82136 | SHORT RURAL | Other | Other | 1 | 56 | 0.00025919 | 0.00046353 | N
22/08/2016 | 00:20 | ZN10996:PA10 | URBAN | Other | Other | 1 | 44 | 3.0411e-05 | 6.938e-05 | N
22/08/2016 | 07:34 | ZN12650:PA10 | URBAN | Other | Other | 1 | 60 | 4.1847e-05 | 6.938e-05 | N
22/08/2016 | 09:11 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 224 | 0.0020766 | 0.00092706 | N
22/08/2016 | 11:28 | ZN9035:PA1 | URBAN | Other | Other - Self Clearing Trigger | 9 | 242 | 0.0015111 | 0.00062442 | N
22/08/2016 | 14:59 | ZN129:PA11 | URBAN | Other | Other - Self Clearing Trigger | 183 | 69 | 0.0087606 | 0.012696 | N
22/08/2016 | 15:49 | ZN36800:PA40 | URBAN | Other | Other - Arcing | 2 | 331 | 0.00045895 | 0.00013876 | N
22/08/2016 | 18:30 | ZN15012:PA4 | URBAN | Other | Other - Arcing | 1 | 146 | 0.00010112 | 6.938e-05 | N
22/08/2016 | 19:59 | ZN3472:PA20 | URBAN | Other | Other - Arcing | 1 | 229 | 0.00015915 | 6.938e-05 | N
23/08/2016 | 07:46 | ZN2196:PA26 | URBAN | Other | Other - Self Clearing Trigger | 1 | 310 | 0.00021436 | 6.909e-05 | N
23/08/2016 | 12:54 | ZN10993:PA33 | URBAN | Other | Other | 1 | 79 | 5.4765e-05 | 6.909e-05 | N
23/08/2016 | 15:11 | 528:83019 | SHORT RURAL | Other | Other | 1 | 63 | 0.0002891 | 0.00045683 | N
23/08/2016 | 17:15 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 38 | 134 | 1.8194 | 1.3552 | N
24/08/2016 | 10:55 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 200 | 0.071327 | 0.035663 | N
24/08/2016 | 16:32 | ZN1285:PA20 | URBAN | Other | Other - Arcing | 44 | 375 | 0.0114 | 0.0030401 | N
24/08/2016 | 18:32 | ZN35600:PA19 | URBAN | Other | Other - Arcing | 10 | 388 | 0.0026808 | 0.00069092 | N
25/08/2016 | 07:55 | ZN12580:PA12 | SHORT RURAL | Other | Other | 1 | 146 | 0.00066523 | 0.00045684 | N
25/08/2016 | 05:11 | ZN35400:PA110 | URBAN | Other | Other - Self Clearing Trigger | 122 | 354 | 0.02984 | 0.0084295 | N
26/08/2016 | 09:49 | ZN35370:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 565 | 0.0025823 | 0.00045684 | N
26/08/2016 | 13:04 | ZN3425:PA22 | URBAN | Other | Other - Arcing | 1 | 265 | 0.00018317 | 6.9094e-05 | N
26/08/2016 | 16:30 | ZN12690:PA19 | URBAN | Other | Other | 1 | 72 | 4.9656e-05 | 6.9094e-05 | N
26/08/2016 | 16:50 | ZN12690:PA19 | URBAN | Other | Other | 1 | 193 | 0.00013331 | 6.9094e-05 | N
27/08/2016 | 11:59 | ZN15014:PA22 | URBAN | Other | Other - Self Clearing Trigger | 19 | 176 | 0.002305 | 0.0013121 | N
28/08/2016 | 08:18 | ZN1673:PA1 | URBAN | Other | Other - Self Clearing Trigger | 40 | 56 | 0.0015511 | 0.0027624 | N
28/08/2016 | 09:21 | ZN14891:PA5 | SHORT RURAL | Other | Other - Arcing | 1 | 158 | 0.0007232 | 0.00045662 | N
29/08/2016 | 12:53 | 504:48034 | URBAN | Other | Other | 1 | 87 | 5.991e-05 | 6.906e-05 | N
29/08/2016 | 13:07 | ZN14891:PA16 | SHORT RURAL | Other | Other | 1 | 308 | 0.0014085 | 0.00045662 | N
29/08/2016 | 00:01 | ZN3288:PA45 46GHJ | CBD | Other | Other - Self Clearing Trigger | 1 | 835 | 0.026896 | 0.0032211 | N
30/08/2016 | 14:52 | 504:48026 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 93 | 0.0021233 | 0.0022831 | N
30/08/2016 | 15:31 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 94 | 0.00042922 | 0.00045662 | N
30/08/2016 | 16:00 | 228:7491 | URBAN | Other | Other | 1 | 60 | 4.1425e-05 | 6.9061e-05 | N
30/08/2016 | 18:52 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 64 | 0.00029399 | 0.00045662 | N
31/08/2016 | 09:40 | 504:48028 | URBAN | Other | Other - Self Clearing Trigger | 1 | 140 | 9.6655e-05 | 6.9039e-05 | N
31/08/2016 | 14:00 | ZN35800:PA16 | URBAN | Other | Other - Self Clearing Trigger | 16 | 110 | 0.0012131 | 0.0011046 | N
31/08/2016 | 17:31 | 221:11899 | SHORT RURAL | Other | Other | 1 | 86 | 0.00039043 | 0.00045647 | N
01/09/2016 | 17:37 | 210:8682 | URBAN | Other | Other | 1 | 143 | 9.8646e-05 | 6.904e-05 | N
01/09/2016 | 18:27 | ZN12610:PA10 | URBAN | Other | Other | 1 | 46 | 3.1954e-05 | 6.904e-05 | N
02/09/2016 | 00:21 | ZN2602:PA9 | URBAN | Other | Other - Arcing | 1 | 659 | 0.00045475 | 6.904e-05 | N
02/09/2016 | 03:37 | ZN15015:PA5 | URBAN | Other | Other - Arcing | 1 | 418 | 0.00028849 | 6.904e-05 | N
02/09/2016 | 10:42 | ZN9035:PA7 | URBAN | Other | Other - Arcing | 1 | 198 | 0.00013657 | 6.904e-05 | N
02/09/2016 | 14:23 | 217:33610 | URBAN | Other | Other | 1 | 117 | 8.0477e-05 | 6.904e-05 | N
02/09/2016 | 19:24 | 507:80917 | URBAN | Other | Other | 1 | 95 | 6.5634e-05 | 6.904e-05 | N
02/09/2016 | 21:08 | ZN3288:PA45 46GHJ | CBD | Other | Other - Self Clearing Trigger | 4 | 212 | 0.027334 | 0.012893 | N
03/09/2016 | 10:01 | 224:80337 | SHORT RURAL | Other | Other | 1 | 34 | 0.0001571 | 0.00045648 | N
03/09/2016 | 10:51 | 224:80332 | URBAN | Other | Other | 1 | 46 | 3.1874e-05 | 6.9041e-05 | N
03/09/2016 | 11:41 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 199 | 0.0027252 | 0.0013694 | N
03/09/2016 | 12:57 | 508:82578 | SHORT RURAL | Other | Other - Self Clearing Trigger | 92 | 131 | 0.054978 | 0.041996 | N
03/09/2016 | 13:05 | 264:81244 | SHORT RURAL | Other | Other - Self Clearing Trigger | 84 | 325 | 0.12459 | 0.038344 | N
03/09/2016 | 14:40 | ZN129:PA28 | URBAN | Other | Other - Arcing | 1 | 379 | 0.00026174 | 6.9041e-05 | N
03/09/2016 | 13:41 | 217:33612 | URBAN | Other | Other | 1 | 112 | 7.7245e-05 | 6.9041e-05 | N
03/09/2016 | 17:25 | 222:33601 | SHORT RURAL | Other | Other - Arcing | 1 | 320 | 0.001462 | 0.00045648 | N
03/09/2016 | 20:52 | ZN188:PA1 | URBAN | Other | Other - Arcing | 1 | 968 | 0.00066807 | 6.9041e-05 | N
04/09/2016 | 08:22 | ZN36100:PA27 | URBAN | Other | Other - Arcing | 1 | 392 | 0.00027084 | 6.9042e-05 | N
04/09/2016 | 09:56 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 214 | 0.0039075 | 0.0018259 | N
04/09/2016 | 12:00 | ZN195:PA25 | URBAN | Other | Other | 1 | 1,190 | 0.00082138 | 6.9042e-05 | N
04/09/2016 | 17:57 | 228:7490 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 62 | 0.0034081 | 0.0054778 | N
05/09/2016 | 07:28 | 230:81432 | SHORT RURAL | Other | Other | 1 | 91 | 0.00041327 | 0.00045648 | N
05/09/2016 | 10:33 | ZN14891:PA5 | SHORT RURAL | Other | Other | 1 | 213 | 0.00097314 | 0.00045648 | N
03/09/2016 | 12:29 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 79 | 200 | 0.07211 | 0.036062 | N
05/09/2016 | 14:05 | 227:13016 | SHORT RURAL | Other | Other | 1 | 58 | 0.00026308 | 0.00045648 | N
05/09/2016 | 15:13 | ZN12620:PA3 | URBAN | Other | Other | 1 | 61 | 4.2046e-05 | 6.9042e-05 | N
06/09/2016 | 02:50 | ZN12650:PA17 | URBAN | Other | Other - Self Clearing Trigger | 41 | 130 | 0.00368 | 0.0028307 | N
06/09/2016 | 06:16 | ZN1193:PA10 | URBAN | Other | Other | 1 | 93 | 6.4175e-05 | 6.9042e-05 | N
06/09/2016 | 07:00 | 502:48010 | SHORT RURAL | Other | Other | 1 | 61 | 0.00027952 | 0.00045648 | N
05/09/2016 | 09:00 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 265 | 0.094508 | 0.035663 | N
07/09/2016 | 06:40 | ZN10999:PA24 | URBAN | Other | Other | 1 | 167 | 0.00011505 | 6.9043e-05 | N
07/09/2016 | 08:42 | 206:34441 | URBAN | Other | Other | 1 | 77 | 5.3485e-05 | 6.9043e-05 | N
07/09/2016 | 12:00 | 233:82812 | SHORT RURAL | Other | Other | 1 | 119 | 0.00054458 | 0.00045648 | N
07/09/2016 | 15:06 | ZN14144:PA7 | SHORT RURAL | Other | Other | 1 | 36 | 0.00016494 | 0.00045648 | N
07/09/2016 | 15:38 | ZN12610:PA11 | URBAN | Other | Other | 1 | 80 | 5.5211e-05 | 6.9043e-05 | N
07/09/2016 | 23:41 | ZN35500:PA24 | URBAN | Other | Other - Self Clearing Trigger | 38 | 118 | 0.0030968 | 0.0026236 | N
08/09/2016 | 08:29 | ZN9900:PA21 | URBAN | Other | Other - Self Clearing Trigger | 34 | 140 | 0.0032887 | 0.002348 | N
08/09/2016 | 17:00 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 105 | 0.00095447 | 0.00090902 | N
08/09/2016 | 21:27 | 508:82574 | SHORT RURAL | Other | Other - Self Clearing Trigger | 58 | 108 | 0.028356 | 0.026361 | N
09/09/2016 | 11:31 | 230:81438 | SHORT RURAL | Other | Other | 1 | 118 | 0.00053715 | 0.00045451 | N
10/09/2016 | 16:48 | 532:83314 | URBAN | Other | Other | 1 | 181 | 0.00012465 | 6.9061e-05 | N
13/09/2016 | 04:58 | ZN12620:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 175 | 150 | 0.11931 | 0.079539 | N
13/09/2016 | 04:58 | ZN14892:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 940 | 149 | 0.63658 | 0.42724 | N
13/09/2016 | 04:58 | ZN14892:PA10 | URBAN | Other | Other - Self Clearing Trigger | 972 | 149 | 0.10002 | 0.06713 | N
13/09/2016 | 04:58 | ZN14892:PA12 | URBAN | Other | Other - Self Clearing Trigger | 218 | 150 | 0.022584 | 0.015056 | N
13/09/2016 | 04:58 | ZN14892:PA13 | URBAN | Other | Other - Self Clearing Trigger | 1,102 | 150 | 0.11416 | 0.076108 | N
13/09/2016 | 04:58 | ZN14892:PA14 | SHORT RURAL | Other | Other - Self Clearing Trigger | 869 | 150 | 0.59245 | 0.39497 | N
13/09/2016 | 04:58 | ZN14892:PA16 | URBAN | Other | Other - Self Clearing Trigger | 2,245 | 150 | 0.23257 | 0.15505 | N
13/09/2016 | 04:58 | ZN14892:PA17 | URBAN | Other | Other - Self Clearing Trigger | 513 | 141 | 0.050055 | 0.03543 | N
13/09/2016 | 04:58 | ZN14892:PA19 | URBAN | Other | Other - Self Clearing Trigger | 1,761 | 150 | 0.18243 | 0.12162 | N
13/09/2016 | 04:58 | ZN14892:PA20 | URBAN | Other | Other - Self Clearing Trigger | 13 | 150 | 0.0013467 | 0.00089783 | N
13/09/2016 | 04:58 | ZN14892:PA21 | URBAN | Other | Other - Self Clearing Trigger | 1,072 | 150 | 0.11105 | 0.074037 | N
13/09/2016 | 04:58 | ZN14892:PA3 | URBAN | Other | Other - Self Clearing Trigger | 1,218 | 149 | 0.12534 | 0.08412 | N
13/09/2016 | 04:58 | ZN14892:PA5 | URBAN | Other | Other - Self Clearing Trigger | 296 | 149 | 0.03046 | 0.020443 | N
13/09/2016 | 04:58 | ZN14892:PA6 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,674 | 149 | 1.1337 | 0.76085 | N
13/09/2016 | 04:58 | ZN14892:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 882 | 149 | 0.59731 | 0.40088 | N
13/09/2016 | 04:58 | ZN14892:PA9 | URBAN | Other | Other - Self Clearing Trigger | 697 | 149 | 0.071725 | 0.048138 | N
13/09/2016 | 08:18 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 102 | 0.036403 | 0.035689 | N
13/09/2016 | 10:32 | 532:83293 | URBAN | Other | Other | 1 | 41 | 2.8247e-05 | 6.9064e-05 | N
13/09/2016 | 11:56 | 224:80332 | URBAN | Other | Other | 1 | 128 | 8.839e-05 | 6.9064e-05 | N
13/09/2016 | 18:59 | 238:34141 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 66 | 0.00029998 | 0.00045451 | N
14/09/2016 | 06:11 | ZN342:PA17 | URBAN | Other | Other - Arcing | 1 | 288 | 0.00019919 | 6.9066e-05 | N
14/09/2016 | 08:51 | ZN965:PA33 | URBAN | Other | Other - Self Clearing Trigger | 57 | 94 | 0.0036946 | 0.0039367 | N
14/09/2016 | 09:23 | 232:11455 | SHORT RURAL | Other | Other - Arcing | 1 | 397 | 0.0018032 | 0.00045451 | N
14/09/2016 | 10:35 | ZN10999:PA36 | URBAN | Other | Other - Self Clearing Trigger | 44 | 130 | 0.0039505 | 0.0030389 | N
14/09/2016 | 11:59 | 228:7490 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 96 | 0.0052359 | 0.0054541 | N
15/09/2016 | 09:07 | 224:80326 | SHORT RURAL | Other | Other | 1 | 122 | 0.00055635 | 0.00045435 | N
15/09/2016 | 11:12 | ZN8000:PA19 | URBAN | Other | Other - Self Clearing Trigger | 75 | 278 | 0.014397 | 0.0051789 | N
15/09/2016 | 11:33 | 257:81991 | URBAN | Other | Other - Self Clearing Trigger | 416 | 42 | 0.012065 | 0.028726 | N
15/09/2016 | 13:02 | ZN2400:PA21 | URBAN | Other | Other - Self Clearing Trigger | 237 | 130 | 0.021275 | 0.016365 | N
15/09/2016 | 14:44 | 507:80925 | SHORT RURAL | Other | Other | 1 | 91 | 0.00041239 | 0.00045435 | N
15/09/2016 | 16:35 | 528:83020 | SHORT RURAL | Other | Other | 1 | 86 | 0.00038983 | 0.00045435 | N
15/09/2016 | 20:19 | ZN9245:PA44 | URBAN | Other | Other - Self Clearing Trigger | 17 | 71 | 0.00083013 | 0.0011739 | N
16/09/2016 | 04:48 | 228:7490 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 111 | 0.0060646 | 0.0054521 | N
16/09/2016 | 11:10 | 256:80632 | URBAN | Other | Other | 1 | 60 | 4.1121e-05 | 6.9052e-05 | N
16/09/2016 | 11:17 | ZN9245:PA42 | URBAN | Other | Other | 1 | 166 | 0.00011463 | 6.9052e-05 | N
16/09/2016 | 16:12 | ZN14891:PA12 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 98 | 0.00044526 | 0.00045435 | N
16/09/2016 | 19:24 | ZN3425:PA33 | URBAN | Other | Other - Arcing | 1 | 931 | 0.0006429 | 6.9052e-05 | N
18/09/2016 | 03:28 | ZN12650:PA17 | URBAN | Other | Other - Self Clearing Trigger | 7 | 865 | 0.0041818 | 0.00048345 | N
18/09/2016 | 14:01 | 243:80084 | SHORT RURAL | Other | Other | 1 | 78 | 0.00035543 | 0.00045403 | N
18/09/2016 | 18:50 | ZN72:PA31 | URBAN | Other | Other - Arcing | 1 | 346 | 0.00023922 | 6.9064e-05 | N
19/09/2016 | 00:10 | 801:74120 | URBAN | Other | Other - Self Clearing Trigger | 614 | 103 | 0.043616 | 0.042406 | N
19/09/2016 | 10:44 | ZN129:PA27 | URBAN | Other | Other - Arcing | 1 | 495 | 0.0003421 | 6.9064e-05 | N
20/09/2016 | 09:36 | ZN15004:PA5 | URBAN | Other | Other - Self Clearing Trigger | 47 | 97 | 0.0031395 | 0.0032461 | N
20/09/2016 | 12:32 | 235:2124 | SHORT RURAL | Other | Other | 1 | 38 | 0.00017087 | 0.00045403 | N
20/09/2016 | 13:08 | ZN9118:PA8 | URBAN | Other | Other - Self Clearing Trigger | 40 | 331 | 0.0091548 | 0.0027626 | N
20/09/2016 | 13:17 | 235:2124 | SHORT RURAL | Other | Other | 1 | 8 | 3.5112e-05 | 0.00045403 | N
20/09/2016 | 14:46 | ZN36300:PA7 | URBAN | Other | Other | 1 | 174 | 0.0001202 | 6.9065e-05 | N
20/09/2016 | 14:47 | ZN4545:PA21 | URBAN | Other | Other | 1 | 63 | 4.32e-05 | 6.9065e-05 | N
20/09/2016 | 15:18 | ZN12580:PA4 | URBAN | Other | Other | 1 | 94 | 6.5037e-05 | 6.9065e-05 | N
20/09/2016 | 18:55 | ZN1788:PA15 | URBAN | Other | Other | 1 | 123 | 8.4709e-05 | 6.9065e-05 | N
21/09/2016 | 12:58 | 509:33397 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 122 | 0.0011079 | 0.00090808 | N
22/09/2016 | 10:24 | ZN384:PA33 | URBAN | Other | Other - Arcing | 1 | 216 | 0.00014886 | 6.9045e-05 | N
22/09/2016 | 12:19 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 146 | 0.052087 | 0.035676 | N
23/09/2016 | 06:33 | ZN12640:PA10 | URBAN | Other | Other | 1 | 58 | 4.0127e-05 | 6.9045e-05 | N
22/09/2016 | 08:30 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 14 | 400 | 0.025419 | 0.0063548 | N
23/09/2016 | 12:49 | ZN262:PA15 | URBAN | Other | Other | 1 | 36 | 2.4983e-05 | 6.9045e-05 | N
23/09/2016 | 14:13 | ZN14144:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 277 | 69 | 0.086756 | 0.12573 | N
23/09/2016 | 15:09 | ZN35900:PA23 | SHORT RURAL | Other | Other | 1 | 83 | 0.00037531 | 0.00045391 | N
23/09/2016 | 15:26 | ZN167:PA1 | URBAN | Other | Other | 1 | 136 | 9.3614e-05 | 6.9045e-05 | N
23/09/2016 | 16:31 | ZN12610:PA18 | URBAN | Other | Other | 1 | 87 | 6.0403e-05 | 6.9045e-05 | N
23/09/2016 | 17:23 | 224:80326 | SHORT RURAL | Other | Other | 1 | 77 | 0.00034913 | 0.00045391 | N
24/09/2016 | 23:16 | ZN1287:PA24 | URBAN | Other | Other - Arcing | 1,165 | 88 | 0.070686 | 0.080438 | N
25/09/2016 | 08:52 | 222:33600 | URBAN | Other | Other - Arcing | 1 | 159 | 0.00010993 | 6.9046e-05 | N
25/09/2016 | 15:50 | ZN15004:PA9 | URBAN | Other | Other - Arcing | 1 | 248 | 0.00017135 | 6.9046e-05 | N
27/09/2016 | 09:57 | ZN13000:PA7 | SHORT RURAL | Other | Other | 1 | 76 | 0.00034518 | 0.00045388 | N
27/09/2016 | 11:23 | ZN12570:PA34 | SHORT RURAL | Other | Other - Arcing | 1 | 156 | 0.00070957 | 0.00045388 | N
27/09/2016 | 16:40 | ZN4545:PA26 | URBAN | Other | Other - Self Clearing Trigger | 9 | 175 | 0.0010855 | 0.00062142 | N
27/09/2016 | 17:52 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 428 | 0.30539 | 0.071352 | N
27/09/2016 | 18:52 | ZN12660:PA6 | SHORT RURAL | Other | Other | 1 | 87 | 0.00039351 | 0.00045388 | N
28/09/2016 | 08:23 | 242:81539 | URBAN | Other | Other | 1 | 104 | 7.15e-05 | 6.9049e-05 | N
28/09/2016 | 08:52 | ZN3922:PA27 | URBAN | Other | Other | 1 | 98 | 6.7322e-05 | 6.9049e-05 | N
29/09/2016 | 14:32 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 93 | 19 | 0.0078547 | 0.0422 | N
29/09/2016 | 20:14 | 807:74181 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 96 | 0.00087123 | 0.00090754 | N
30/09/2016 | 09:55 | 257:81987 | URBAN | Other | Other - Arcing | 1 | 155 | 0.00010667 | 6.9028e-05 | N
30/09/2016 | 11:53 | ZN15004:PA9 | URBAN | Other | Other - Arcing | 1 | 696 | 0.00048056 | 6.9028e-05 | N
30/09/2016 | 12:25 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 55 | 0.00024957 | 0.00045377 | N
30/09/2016 | 14:14 | 507:80923 | SHORT RURAL | Other | Other | 1 | 95 | 0.00043289 | 0.00045377 | N
30/09/2016 | 16:28 | ZN12610:PA16 | SHORT RURAL | Other | Other - Arcing | 1 | 332 | 0.0015059 | 0.00045377 | N
01/10/2016 | 10:27 | ZN14892:PA19 | URBAN | Other | Other | 1 | 59 | 4.0411e-05 | 6.9059e-05 | N
01/10/2016 | 14:18 | 512:48048 | SHORT RURAL | Other | Other | 1 | 85 | 0.00038606 | 0.00045268 | N
01/10/2016 | 15:14 | ZN35800:PA6 | URBAN | Other | Other - Arcing | 1 | 958 | 0.00066186 | 6.9059e-05 | N
01/10/2016 | 19:37 | ZN690:PA34 | URBAN | Other | Other - Self Clearing Trigger | 90 | 72 | 0.004503 | 0.0062153 | N
02/10/2016 | 10:31 | 220:8689 | URBAN | Other | Other | 1 | 112 | 7.7116e-05 | 6.9059e-05 | N
03/10/2016 | 13:01 | 238:34140 | URBAN | Other | Other | 1 | 78 | 5.405e-05 | 6.9059e-05 | N
03/10/2016 | 13:10 | 507:80931 | URBAN | Other | Other | 1 | 164 | 0.00011306 | 6.9059e-05 | N
03/10/2016 | 16:44 | ZN35370:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 750 | 131 | 0.44447 | 0.33951 | N
03/10/2016 | 17:34 | ZN1788:PA15 | URBAN | Other | Other - Arcing | 1 | 205 | 0.00014188 | 6.9059e-05 | N
03/10/2016 | 22:17 | ZN36300:PA17 | URBAN | Other | Other - Self Clearing Trigger | 54 | 102 | 0.0038175 | 0.0037292 | N
04/10/2016 | 10:27 | ZN36300:PA3 | URBAN | Other | Other - Self Clearing Trigger | 58 | 203 | 0.0081297 | 0.0040054 | N
04/10/2016 | 15:38 | 258:80787 | URBAN | Other | Other | 1 | 77 | 5.3268e-05 | 6.9059e-05 | N
04/10/2016 | 17:33 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 932 | 0.016876 | 0.0018107 | N
04/10/2016 | 18:09 | 224:80337 | SHORT RURAL | Other | Other - Arcing | 1 | 1,267 | 0.0057368 | 0.00045268 | N
05/10/2016 | 07:17 | ZN35500:PA31 | URBAN | Other | Other | 1 | 48 | 3.3034e-05 | 6.9061e-05 | N
05/10/2016 | 11:25 | 257:81999 | URBAN | Other | Other | 1 | 85 | 5.8471e-05 | 6.9061e-05 | N
06/10/2016 | 09:58 | ZN195:PA4 | URBAN | Other | Other | 1 | 90 | 6.2098e-05 | 6.9062e-05 | N
06/10/2016 | 11:16 | 230:81440 | SHORT RURAL | Other | Other | 1 | 113 | 0.00051343 | 0.00045269 | N
06/10/2016 | 12:00 | ZN187:PA10 | URBAN | Other | Other | 1 | 158 | 0.0001092 | 6.9062e-05 | N
06/10/2016 | 12:29 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 81 | 0.00036668 | 0.00045269 | N
06/10/2016 | 14:13 | ZN1673:PA19 | URBAN | Other | Other - Self Clearing Trigger | 15 | 126 | 0.0013073 | 0.0010359 | N
07/10/2016 | 06:29 | 258:80778 | URBAN | Other | Other - Self Clearing Trigger | 83 | 90 | 0.0051769 | 0.0057298 | N
07/10/2016 | 07:22 | 258:80790 | URBAN | Other | Other | 1 | 60 | 4.1409e-05 | 6.9034e-05 | N
07/10/2016 | 08:43 | 523:33503 | URBAN | Other | Other - Arcing | 1 | 406 | 0.00028059 | 6.9034e-05 | N
07/10/2016 | 13:15 | 261:81886 | URBAN | Other | Other | 1 | 62 | 4.2836e-05 | 6.9034e-05 | N
07/10/2016 | 16:45 | 205:12203 | URBAN | Other | Other | 1 | 71 | 4.8968e-05 | 6.9034e-05 | N
07/10/2016 | 17:11 | ZN187:PA16 | URBAN | Other | Other - Self Clearing Trigger | 50 | 78 | 0.0027056 | 0.0034517 | N
08/10/2016 | 08:03 | ZN9245:PA33 | URBAN | Other | Other - Self Clearing Trigger | 10 | 332 | 0.0022936 | 0.00069085 | N
08/10/2016 | 09:40 | 261:81885 | URBAN | Other | Other | 1 | 42 | 2.8797e-05 | 6.9085e-05 | N
08/10/2016 | 10:11 | ZN15011:PA10 | URBAN | Other | Other | 1 | 67 | 4.661e-05 | 6.9085e-05 | N
08/10/2016 | 11:37 | 504:48033 | SHORT RURAL | Other | Other | 1 | 123 | 0.00055466 | 0.00045254 | N
08/10/2016 | 18:42 | ZN15002:PA6 | URBAN | Other | Other | 1 | 136 | 9.4209e-05 | 6.9085e-05 | N
09/10/2016 | 19:09 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 35 | 0.0001596 | 0.00045254 | N
10/10/2016 | 10:27 | ZN2466:PA16 | URBAN | Other | Other - Self Clearing Trigger | 21 | 82 | 0.0011953 | 0.0014508 | N
10/10/2016 | 11:13 | ZN180:PA30 | URBAN | Other | Other | 1 | 67 | 4.6115e-05 | 6.9086e-05 | N
10/10/2016 | 20:50 | ZN35500:PA28 | URBAN | Other | Other - Self Clearing Trigger | 23 | 55 | 0.00087394 | 0.001589 | N
10/10/2016 | 21:13 | 229:34983 | SHORT RURAL | Other | Other - Self Clearing Trigger | 31 | 121 | 0.016975 | 0.014029 | N
10/10/2016 | 22:37 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 202 | 0.0018319 | 0.00090508 | N
11/10/2016 | 07:59 | ZN1673:PA19 | URBAN | Other | Other - Arcing | 1 | 150 | 0.00010386 | 6.9046e-05 | N
11/10/2016 | 09:08 | ZN8700:PA63 64DEF | CBD | Other | Other - Self Clearing Trigger | 7 | 157 | 0.03543 | 0.022567 | N
11/10/2016 | 12:27 | ZN12570:PA40 | SHORT RURAL | Other | Other | 1 | 69 | 0.00031237 | 0.00045216 | N
11/10/2016 | 14:04 | ZN2635:PA57 | URBAN | Other | Other | 1 | 48 | 3.3246e-05 | 6.9046e-05 | N
11/10/2016 | 14:51 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 189 | 0.00085459 | 0.00045216 | N
11/10/2016 | 22:45 | ZN167:PA21 | URBAN | Other | Other - Self Clearing Trigger | 3 | 85 | 0.00017607 | 0.00020714 | N
12/10/2016 | 08:30 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 90 | 0.0012209 | 0.0013565 | N
12/10/2016 | 07:00 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 200 | 0.0018087 | 0.00090433 | N
12/10/2016 | 10:18 | 203:8085 | URBAN | Other | Other | 1 | 51 | 3.5261e-05 | 6.9048e-05 | N
12/10/2016 | 14:28 | ZN35370:PA4 | SHORT RURAL | Other | Other - Arcing | 1 | 227 | 0.0010256 | 0.00045217 | N
13/10/2016 | 02:31 | ZN15006:PA16 | URBAN | Other | Other - Arcing | 1 | 449 | 0.00031011 | 6.914e-05 | N
13/10/2016 | 04:08 | 222:33600 | URBAN | Other | Other - Arcing | 1 | 156 | 0.00010801 | 6.914e-05 | N
13/10/2016 | 08:30 | 233:82819 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 211 | 0.0047685 | 0.0022599 | N
13/10/2016 | 14:27 | ZN12690:PA3 | SHORT RURAL | Other | Other | 1 | 106 | 0.00048084 | 0.00045199 | N
13/10/2016 | 15:11 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 1 | 198 | 0.00013715 | 6.914e-05 | N
13/10/2016 | 19:53 | 230:81440 | SHORT RURAL | Other | Other | 1 | 66 | 0.00029884 | 0.00045199 | N
14/10/2016 | 08:39 | ZN2310:PA71 | URBAN | Other | Other - Self Clearing Trigger | 81 | 116 | 0.0064964 | 0.0056004 | N
14/10/2016 | 12:50 | ZN1788:PA14 | URBAN | Other | Other | 1 | 29 | 2.0189e-05 | 6.914e-05 | N
14/10/2016 | 16:39 | ZN14144:PA2 | SHORT RURAL | Other | Other | 1 | 40 | 0.00018117 | 0.00045199 | N
14/10/2016 | 18:20 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 59 | 0.021068 | 0.035689 | N
14/10/2016 | 21:18 | ZN180:PA20 | URBAN | Other | Other - Self Clearing Trigger | 1 | 171 | 0.00011824 | 6.914e-05 | N
14/10/2016 | 21:26 | ZN180:PA20 | URBAN | Other | Other - Self Clearing Trigger | 34 | 124 | 0.002915 | 0.0023508 | N
14/10/2016 | 23:19 | 239:82136 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 101 | 0.001826 | 0.001808 | N
15/10/2016 | 08:39 | 238:34147 | SHORT RURAL | Other | Other | 1 | 51 | 0.00022888 | 0.00045041 | N
15/10/2016 | 12:55 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 50 | 0.035689 | 0.071378 | N
15/10/2016 | 16:54 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 71 | 0.00063958 | 0.00090081 | N
16/10/2016 | 09:01 | ZN9245:PA15 | URBAN | Other | Other - Self Clearing Trigger | 10 | 163 | 0.0011258 | 0.00069069 | N
16/10/2016 | 09:46 | ZN1850:PA10 | URBAN | Other | Other - Arcing | 1 | 315 | 0.00021742 | 6.9069e-05 | N
16/10/2016 | 10:09 | 217:33610 | URBAN | Other | Other | 1 | 56 | 3.8426e-05 | 6.9069e-05 | N
16/10/2016 | 10:39 | ZN3154:PA11 | URBAN | Other | Other - Self Clearing Trigger | 22 | 144 | 0.0021881 | 0.0015195 | N
16/10/2016 | 10:56 | 513:48059 | SHORT RURAL | Other | Other - Arcing | 1 | 171 | 0.00076968 | 0.00045041 | N
16/10/2016 | 15:01 | ZN3672:PA37 | URBAN | Other | Other - Arcing | 84 | 349 | 0.020248 | 0.0058018 | N
17/10/2016 | 08:46 | 504:48029 | URBAN | Other | Other | 1 | 115 | 7.9706e-05 | 6.9069e-05 | N
17/10/2016 | 12:22 | ZN35800:PA9 | URBAN | Other | Other - Arcing | 1 | 127 | 8.7914e-05 | 6.9069e-05 | N
17/10/2016 | 13:15 | ZN9700:PA11 | URBAN | Other | Other - Arcing | 2 | 93 | 0.00012907 | 0.00013814 | N
17/10/2016 | 13:16 | ZN9118:PA26 | URBAN | Other | Other - Arcing | 1 | 73 | 5.0674e-05 | 6.9069e-05 | N
17/10/2016 | 15:01 | ZN3922:PA27 | URBAN | Other | Other - Arcing | 1 | 417 | 0.00028786 | 6.9069e-05 | N
17/10/2016 | 17:38 | 225:33679 | URBAN | Other | Other | 1 | 86 | 5.9699e-05 | 6.9069e-05 | N
17/10/2016 | 20:29 | ZN12660:PA6 | SHORT RURAL | Other | Other | 1 | 85 | 0.00038247 | 0.00045041 | N
17/10/2016 | 21:31 | ZN14891:PA5 | SHORT RURAL | Other | Other - Arcing | 1 | 119 | 0.00053479 | 0.00045041 | N
18/10/2016 | 06:33 | ZN36200:PA1 | URBAN | Other | Other - Self Clearing Trigger | 64 | 86 | 0.0038173 | 0.0044207 | N
18/10/2016 | 13:44 | 507:80932 | SHORT RURAL | Other | Other | 1 | 85 | 0.00038427 | 0.00045041 | N
18/10/2016 | 14:03 | ZN1285:PA24 | URBAN | Other | Other - Arcing | 1 | 384 | 0.00026549 | 6.9073e-05 | N
18/10/2016 | 20:23 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 77 | 0.0013873 | 0.0018016 | N
19/10/2016 | 09:55 | 261:81870 | URBAN | Other | Other | 1 | 43 | 2.9909e-05 | 6.9075e-05 | N
19/10/2016 | 16:31 | 257:81999 | URBAN | Other | Other | 1 | 58 | 4.0271e-05 | 6.9075e-05 | N
19/10/2016 | 21:23 | ZN10999:PA4 | URBAN | Other | Other | 1 | 143 | 9.865e-05 | 6.9075e-05 | N
20/10/2016 | 05:52 | ZN4545:PA17 | URBAN | Other | Other - Self Clearing Trigger | 1,191 | 145 | 0.11911 | 0.082272 | N
19/10/2016 | 14:43 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 107 | 0.00096388 | 0.00090082 | N
20/10/2016 | 08:32 | ZN2310:PA66 | URBAN | Other | Other - Self Clearing Trigger | 37 | 148 | 0.0037729 | 0.0025559 | N
20/10/2016 | 17:28 | ZN80:PA32 | URBAN | Other | Other | 1 | 55 | 3.7786e-05 | 6.9078e-05 | N
20/10/2016 | 21:13 | ZN12690:PA7 | SHORT RURAL | Other | Other - Self Clearing Trigger | 821 | 72 | 0.26517 | 0.36979 | N
21/10/2016 | 11:41 | 258:80784 | URBAN | Other | Other | 1 | 66 | 4.5771e-05 | 6.942e-05 | N
21/10/2016 | 15:30 | 516:48066 | SHORT RURAL | Other | Other - Arcing | 1 | 103 | 0.0004648 | 0.00045317 | N
21/10/2016 | 21:29 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 16 | 326 | 1.8974 | 0.58203 | N
21/10/2016 | 22:54 | ZN630:PA35 | URBAN | Other | Other - Arcing | 1 | 845 | 0.00058674 | 6.942e-05 | N
21/10/2016 | 21:29 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 756 | 0.27501 | 0.036377 | N
22/10/2016 | 08:28 | ZN2602:PA10 | URBAN | Other | Other - Arcing | 1 | 182 | 0.00012552 | 6.9057e-05 | N
21/10/2016 | 21:29 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 696 | 0.50637 | 0.072754 | N
22/10/2016 | 11:40 | ZN12630:PA22 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 371 | 0.0016708 | 0.00045023 | N
22/10/2016 | 13:06 | ZN10995:PA7 | URBAN | Other | Other - Arcing | 1 | 359 | 0.00024757 | 6.9057e-05 | N
22/10/2016 | 13:16 | ZN690:PA6 | URBAN | Other | Other - Arcing | 1 | 348 | 0.00024039 | 6.9057e-05 | N
22/10/2016 | 13:59 | 214:8666 | URBAN | Other | Other | 1 | 40 | 2.7404e-05 | 6.9057e-05 | N
23/10/2016 | 08:49 | 220:8689 | URBAN | Other | Other - Arcing | 1 | 235 | 0.0001624 | 6.9058e-05 | N
24/10/2016 | 12:57 | ZN2835:PA15 | URBAN | Other | Other - Self Clearing Trigger | 30 | 123 | 0.0025482 | 0.0020717 | N
23/10/2016 | 22:40 | ZN9252:PA31 | URBAN | Other | Other - Arcing | 1 | 240 | 0.00016541 | 6.9058e-05 | N
23/10/2016 | 22:44 | ZN9252:PA31 | URBAN | Other | Other - Arcing | 1 | 236 | 0.0001629 | 6.9058e-05 | N
24/10/2016 | 01:35 | ZN9035:PA1 | URBAN | Other | Other - Self Clearing Trigger | 459 | 116 | 0.036769 | 0.031698 | N
24/10/2016 | 01:35 | ZN9035:PA10 | URBAN | Other | Other - Self Clearing Trigger | 526 | 116 | 0.042136 | 0.036325 | N
24/10/2016 | 01:35 | ZN9035:PA11 | URBAN | Other | Other - Self Clearing Trigger | 1,941 | 116 | 0.15549 | 0.13404 | N
24/10/2016 | 01:35 | ZN9035:PA2 | URBAN | Other | Other - Self Clearing Trigger | 560 | 116 | 0.04486 | 0.038673 | N
24/10/2016 | 01:35 | ZN9035:PA4 | URBAN | Other | Other - Self Clearing Trigger | 1,887 | 116 | 0.15116 | 0.13031 | N
24/10/2016 | 01:35 | ZN9035:PA5 | URBAN | Other | Other - Self Clearing Trigger | 318 | 116 | 0.025474 | 0.02196 | N
24/10/2016 | 01:35 | ZN9035:PA7 | URBAN | Other | Other - Self Clearing Trigger | 1,119 | 116 | 0.08964 | 0.077276 | N
24/10/2016 | 01:35 | ZN9035:PA8 | URBAN | Other | Other - Self Clearing Trigger | 116 | 112 | 0.0090003 | 0.0080107 | N
24/10/2016 | 09:40 | 512:48048 | SHORT RURAL | Other | Other | 1 | 77 | 0.00034855 | 0.00045023 | N
24/10/2016 | 10:08 | ZN35600:PA16 | URBAN | Other | Other - Arcing | 1 | 276 | 0.00019067 | 6.9058e-05 | N
24/10/2016 | 11:31 | ZN3425:PA12 | URBAN | Other | Other - Arcing | 1 | 4 | 2.6472e-06 | 6.9058e-05 | N
24/10/2016 | 12:53 | 528:83013 | URBAN | Other | Other | 1 | 163 | 0.00011282 | 6.9058e-05 | N
24/10/2016 | 23:04 | ZN3155:PA29 | URBAN | Other | Other - Self Clearing Trigger | 35 | 250 | 0.0060426 | 0.002417 | N
25/10/2016 | 10:23 | 504:48026 | SHORT RURAL | Other | Other | 1 | 126 | 0.00056887 | 0.00045024 | N
25/10/2016 | 18:10 | ZN12610:PA9 | URBAN | Other | Other | 1 | 78 | 5.4004e-05 | 6.9059e-05 | N
25/10/2016 | 20:17 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 83 | 0.00037355 | 0.00045024 | N
26/10/2016 | 07:08 | ZN12600:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 616 | 42 | 0.11648 | 0.27735 | N
26/10/2016 | 07:08 | ZN12600:PA11 | URBAN | Other | Other - Self Clearing Trigger | 887 | 43 | 0.02634 | 0.061255 | N
26/10/2016 | 07:08 | ZN12600:PA12 | URBAN | Other | Other - Self Clearing Trigger | 280 | 43 | 0.0083147 | 0.019336 | N
26/10/2016 | 07:08 | ZN12600:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 856 | 43 | 0.16572 | 0.3854 | N
26/10/2016 | 07:08 | ZN12600:PA2 | SHORT RURAL | Other | Other - Self Clearing Trigger | 778 | 42 | 0.14712 | 0.35028 | N
26/10/2016 | 07:08 | ZN12600:PA3 | URBAN | Other | Other - Self Clearing Trigger | 1,745 | 42 | 0.050613 | 0.12051 | N
26/10/2016 | 07:08 | ZN12600:PA5 | URBAN | Other | Other - Self Clearing Trigger | 82 | 42 | 0.0023784 | 0.0056628 | N
26/10/2016 | 07:08 | ZN12600:PA9 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,495 | 43 | 0.28943 | 0.6731 | N
26/10/2016 | 20:38 | ZN2602:PA41 | URBAN | Other | Other - Self Clearing Trigger | 62 | 48 | 0.002073 | 0.0042816 | N
27/10/2016 | 06:44 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 201 | 0.071658 | 0.035651 | N
27/10/2016 | 06:45 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 290 | 0.0013053 | 0.00045012 | N
27/10/2016 | 08:39 | ZN1285:PA20 | URBAN | Other | Other - Self Clearing Trigger | 62 | 56 | 0.002397 | 0.0042803 | N
27/10/2016 | 14:11 | ZN15010:PA9 | SHORT RURAL | Other | Other | 1 | 39 | 0.0001757 | 0.00045012 | N
27/10/2016 | 17:59 | ZN15012:PA8 | URBAN | Other | Other - Arcing | 1 | 151 | 0.00010402 | 6.9037e-05 | N
27/10/2016 | 18:44 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 465 | 11 | 1.8446 | 16.5775 | N
27/10/2016 | 18:55 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 100 | 0.035651 | 0.035651 | N
27/10/2016 | 19:14 | ZN15010:PA7 | URBAN | Other | Other - Arcing | 1 | 286 | 0.00019724 | 6.9037e-05 | N
27/10/2016 | 19:27 | ZN9700:PA16 | URBAN | Other | Other - Arcing | 1 | 183 | 0.00012627 | 6.9037e-05 | N
27/10/2016 | 22:04 | ZN3922:PA29 | URBAN | Other | Other - Arcing | 1 | 715 | 0.00049391 | 6.9037e-05 | N
27/10/2016 | 22:20 | ZN262:PA20 | URBAN | Other | Other - Arcing | 1 | 310 | 0.00021386 | 6.9037e-05 | N
28/10/2016 | 05:21 | ZN874:PA4 | URBAN | Other | Other - Arcing | 1 | 249 | 0.00017156 | 6.9037e-05 | N
28/10/2016 | 09:24 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 106 | 0.075579 | 0.071301 | N
28/10/2016 | 10:11 | ZN15014:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 1,408 | 0.0063357 | 0.00045012 | N
28/10/2016 | 20:33 | ZN10991:PA12 | URBAN | Other | Other - Arcing | 1 | 177 | 0.00012216 | 6.9037e-05 | N
28/10/2016 | 21:42 | ZN1788:PA8 | URBAN | Other | Other - Arcing | 1 | 371 | 0.00025613 | 6.9037e-05 | N
28/10/2016 | 21:59 | ZN2568:PA28 | URBAN | Other | Other - Arcing | 1 | 277 | 0.00019092 | 6.9037e-05 | N
28/10/2016 | 22:14 | ZN901:PA11 | URBAN | Other | Other - Arcing | 1 | 340 | 0.00023445 | 6.9037e-05 | N
28/10/2016 | 22:16 | ZN262:PA20 | URBAN | Other | Other - Arcing | 1 | 260 | 0.00017945 | 6.9037e-05 | N
29/10/2016 | 00:17 | ZN3472:PA30 | URBAN | Other | Other - Arcing | 1 | 559 | 0.00038582 | 6.9038e-05 | N
29/10/2016 | 01:27 | ZN2310:PA65 | URBAN | Other | Other - Arcing | 1 | 594 | 0.00041014 | 6.9038e-05 | N
29/10/2016 | 01:33 | ZN9252:PA27 | URBAN | Other | Other - Arcing | 1 | 767 | 0.00052937 | 6.9038e-05 | N
29/10/2016 | 01:58 | ZN3472:PA17 | URBAN | Other | Other - Arcing | 1 | 457 | 0.00031564 | 6.9038e-05 | N
29/10/2016 | 02:26 | ZN1290:PA12 | URBAN | Other | Other - Arcing | 1 | 678 | 0.00046785 | 6.9038e-05 | N
29/10/2016 | 05:58 | ZN10991:PA13 | URBAN | Other | Other - Arcing | 1 | 501 | 0.00034565 | 6.9038e-05 | N
29/10/2016 | 08:33 | ZN15008:PA1 | URBAN | Other | Other - Arcing | 1 | 205 | 0.00014146 | 6.9038e-05 | N
29/10/2016 | 15:34 | ZN35500:PA28 | URBAN | Other | Other - Self Clearing Trigger | 15 | 64 | 0.00065793 | 0.0010356 | N
29/10/2016 | 21:56 | ZN1287:PA12 | URBAN | Other | Other - Arcing | 1 | 238 | 0.00016416 | 6.9038e-05 | N
30/10/2016 | 02:49 | ZN2602:PA31 | URBAN | Other | Other - Arcing | 1 | 569 | 0.00039302 | 6.9038e-05 | N
30/10/2016 | 12:51 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 94 | 0.00084622 | 0.00090023 | N
30/10/2016 | 17:11 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 14 | 214 | 0.013485 | 0.0063016 | N
30/10/2016 | 17:24 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 80 | 0.0065168 | 0.0081021 | N
30/10/2016 | 19:33 | 205:12205 | SHORT RURAL | Other | Other | 1 | 56 | 0.00025282 | 0.00045012 | N
30/10/2016 | 19:52 | 205:12205 | SHORT RURAL | Other | Other | 1 | 37 | 0.00016737 | 0.00045012 | N
30/10/2016 | 20:51 | ZN1068:PA27 | URBAN | Other | Other - Arcing | 1 | 144 | 9.9082e-05 | 6.9038e-05 | N
30/10/2016 | 22:13 | ZN9550:PA43 | URBAN | Other | Other - Self Clearing Trigger | 1,043 | 106 | 0.076484 | 0.072007 | N
31/10/2016 | 00:46 | ZN12640:PA15 | URBAN | Other | Other - Self Clearing Trigger | 124 | 110 | 0.0094168 | 0.0085608 | N
31/10/2016 | 08:42 | ZN12570:PA37 | SHORT RURAL | Other | Other | 1 | 38 | 0.00017134 | 0.00045012 | N
31/10/2016 | 08:59 | ZN35335:PA14 | URBAN | Other | Other - Self Clearing Trigger | 23 | 151 | 0.0023977 | 0.0015879 | N
31/10/2016 | 09:40 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 2 | 260 | 0.00035836 | 0.00013808 | N
31/10/2016 | 09:41 | ZN12570:PA37 | SHORT RURAL | Other | Other | 1 | 95 | 0.00042536 | 0.00045012 | N
31/10/2016 | 16:39 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 110 | 0.0004961 | 0.00045012 | N
31/10/2016 | 16:45 | ZN9037:PA9 | URBAN | Other | Other - Self Clearing Trigger | 44 | 134 | 0.0040801 | 0.0030377 | N
31/10/2016 | 20:35 | ZN901:PA8 | URBAN | Other | Other - Self Clearing Trigger | 12 | 29 | 0.00024329 | 0.00082846 | N
01/11/2016 | 03:25 | 217:33611 | URBAN | Other | Other - Self Clearing Trigger | 493 | 74 | 0.025188 | 0.034037 | N
31/10/2016 | 13:30 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 72 | 0.00032408 | 0.00045012 | N
01/11/2016 | 09:23 | ZN7900:PA1 | URBAN | Other | Other - Self Clearing Trigger | 18 | 192 | 0.0023861 | 0.0012427 | N
01/11/2016 | 12:48 | ZN9118:PA12 | URBAN | Other | Other - Self Clearing Trigger | 45 | 52 | 0.0016011 | 0.0031068 | N
01/11/2016 | 19:21 | ZN72:PA24 | SHORT RURAL | Other | Other - Arcing | 1 | 198 | 0.00089206 | 0.00045016 | N
02/11/2016 | 20:52 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 32 | 67 | 0.0096659 | 0.014405 | N
02/11/2016 | 21:29 | ZN35500:PA34 | URBAN | Other | Other - Self Clearing Trigger | 4 | 201 | 0.00055511 | 0.00027617 | N
02/11/2016 | 20:27 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 33 | 0.00014855 | 0.00045016 | N
03/11/2016 | 13:17 | 507:80917 | URBAN | Other | Other | 1 | 71 | 4.9053e-05 | 6.9023e-05 | N
03/11/2016 | 21:45 | ZN847:PA1 | URBAN | Other | Other - Self Clearing Trigger | 37 | 35 | 0.00089385 | 0.0025539 | N
04/11/2016 | 09:58 | ZN36100:PA13 | URBAN | Other | Other - Arcing | 1 | 482 | 0.00033264 | 6.9023e-05 | N
04/11/2016 | 13:14 | ZN1193:PA12 | URBAN | Other | Other | 1 | 106 | 7.2981e-05 | 6.9023e-05 | N
04/11/2016 | 16:10 | ZN10997:PA12 | URBAN | Other | Other - Self Clearing Trigger | 25 | 49 | 0.00084985 | 0.0017256 | N
04/11/2016 | 19:32 | ZN35600:PA1 | URBAN | Other | Other - Arcing | 1 | 223 | 0.00015398 | 6.9023e-05 | N
04/11/2016 | 23:22 | ZN9245:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 26 | 83 | 0.0097105 | 0.011699 | N
05/11/2016 | 09:44 | ZN10995:PA1 | URBAN | Other | Other - Arcing | 1 | 599 | 0.00041355 | 6.9027e-05 | N
05/11/2016 | 14:14 | ZN690:PA10 | URBAN | Other | Other - Self Clearing Trigger | 1 | 192 | 0.0001325 | 6.9027e-05 | N
05/11/2016 | 14:14 | ZN690:PA5 | URBAN | Other | Other - Self Clearing Trigger | 1 | 262 | 0.00018062 | 6.9027e-05 | N
05/11/2016 | 16:26 | 512:48048 | SHORT RURAL | Other | Other | 1 | 68 | 0.00030674 | 0.00044999 | N
05/11/2016 | 22:28 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 602 | 0.013545 | 0.00225 | N
07/11/2016 | 12:23 | ZN3425:PA35 | URBAN | Other | Other - Arcing | 47 | 156 | 0.0050644 | 0.0032443 | N
07/11/2016 | 12:51 | ZN13000:PA10 | SHORT RURAL | Other | Other | 1 | 53 | 0.00023812 | 0.00044999 | N
08/11/2016 | 06:55 | ZN35900:PA17 | URBAN | Other | Other - Arcing | 1 | 514 | 0.00035514 | 6.9029e-05 | N
08/11/2016 | 09:43 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 227 | 0.0010205 | 0.00045 | N
08/11/2016 | 12:45 | ZN15010:PA11 | URBAN | Other | Other | 1 | 79 | 5.4349e-05 | 6.9029e-05 | N
08/11/2016 | 17:18 | 225:33670 | URBAN | Other | Other | 1 | 47 | 3.2329e-05 | 6.9029e-05 | N
08/11/2016 | 18:06 | ZN3472:PA12 | URBAN | Other | Other - Arcing | 1 | 270 | 0.00018607 | 6.9029e-05 | N
08/11/2016 | 18:24 | ZN3472:PA12 | URBAN | Other | Other - Arcing | 1 | 252 | 0.00017388 | 6.9029e-05 | N
08/11/2016 | 18:25 | ZN3472:PA12 | URBAN | Other | Other - Arcing | 1 | 252 | 0.00017371 | 6.9029e-05 | N
08/11/2016 | 18:37 | ZN2400:PA26 | URBAN | Other | Other - Self Clearing Trigger | 27 | 173 | 0.0032234 | 0.0018638 | N
08/11/2016 | 18:38 | ZN2568:PA29 | URBAN | Other | Other - Arcing | 1 | 81 | 5.596e-05 | 6.9029e-05 | N
08/11/2016 | 18:54 | ZN262:PA19 | URBAN | Other | Other - Arcing | 1 | 220 | 0.00015172 | 6.9029e-05 | N
08/11/2016 | 18:54 | ZN262:PA19 | URBAN | Other | Other - Arcing | 1 | 306 | 0.00021097 | 6.9029e-05 | N
08/11/2016 | 19:04 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 7 | 181 | 0.45137 | 0.24938 | N
08/11/2016 | 20:08 | ZN3155:PA30 | URBAN | Other | Other - Self Clearing Trigger | 8 | 182 | 0.0010051 | 0.00055223 | N
08/11/2016 | 23:00 | ZN15010:PA7 | URBAN | Other | Other - Arcing | 1 | 367 | 0.00025318 | 6.9029e-05 | N
09/11/2016 | 01:36 | 221:11897 | URBAN | Other | Other - Self Clearing Trigger | 64 | 84 | 0.0036978 | 0.004418 | N
09/11/2016 | 06:40 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 135 | 0.001215 | 0.0009 | N
09/11/2016 | 08:28 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 355 | 0.003195 | 0.0009 | N
09/11/2016 | 10:00 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 135 | 0.0018225 | 0.00135 | N
09/11/2016 | 20:31 | ZN2310:PA72 | URBAN | Other | Other - Arcing | 1 | 839 | 0.00057905 | 6.9031e-05 | N
10/11/2016 | 09:38 | ZN931:PA10 | URBAN | Other | Other | 1 | 311 | 0.00021489 | 6.9033e-05 | N
10/11/2016 | 10:26 | 228:7491 | URBAN | Other | Other | 1 | 153 | 0.0001058 | 6.9033e-05 | N
11/11/2016 | 08:44 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 102 | 0.00045901 | 0.00045001 | N
11/11/2016 | 10:27 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 78 | 0.001404 | 0.0018 | N
11/11/2016 | 10:38 | 509:33399 | SHORT RURAL | Other | Other | 1 | 95 | 0.00042729 | 0.00045001 | N
12/11/2016 | 04:17 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 178 | 0.016009 | 0.0089954 | N
12/11/2016 | 06:00 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 5 | 310 | 0.55125 | 0.17806 | N
12/11/2016 | 06:14 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 16 | 216 | 1.2308 | 0.5698 | N
12/11/2016 | 06:23 | ZN12630:PA23 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 94 | 0.00042076 | 0.00044977 | N
12/11/2016 | 06:58 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 302 | 0.0027166 | 0.00089954 | N
12/11/2016 | 07:32 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 78 | 0.055556 | 0.071225 | N
12/11/2016 | 08:01 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 279 | 0.0012549 | 0.00044977 | N
12/11/2016 | 08:33 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 146 | 0.052024 | 0.035613 | N
12/11/2016 | 09:02 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 227 | 0.080983 | 0.035613 | N
12/11/2016 | 09:03 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 131 | 0.00058995 | 0.00044977 | N
12/11/2016 | 10:02 | ZN2310:PA67 | URBAN | Other | Other - Arcing | 1 | 278 | 0.00019178 | 6.9011e-05 | N
12/11/2016 | 10:24 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 95 | 0.033986 | 0.035613 | N
12/11/2016 | 13:29 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 91 | 0.0012279 | 0.0013493 | N
12/11/2016 | 17:32 | 225:33670 | URBAN | Other | Other | 1 | 133 | 9.1681e-05 | 6.9011e-05 | N
12/11/2016 | 19:18 | ZN2635:PA51 | URBAN | Other | Other - Arcing | 1 | 282 | 0.00019471 | 6.9011e-05 | N
13/11/2016 | 00:38 | 202:34254 | URBAN | Other | Other - Self Clearing Trigger | 7 | 65 | 0.000314 | 0.00048308 | N
13/11/2016 | 01:50 | 528:83014 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 335 | 0.01356 | 0.0040479 | N
13/11/2016 | 08:54 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 66 | 0.0011874 | 0.0017991 | N
13/11/2016 | 15:39 | ZN9550:PA3 | URBAN | Other | Other - Self Clearing Trigger | 54 | 185 | 0.006896 | 0.0037266 | N
13/11/2016 | 17:30 | ZN12610:PA16 | SHORT RURAL | Other | Other | 1 | 988 | 0.0044447 | 0.00044977 | N
13/11/2016 | 21:20 | 227:13015 | SHORT RURAL | Other | Other | 1 | 79 | 0.00035577 | 0.00044977 | N
13/11/2016 | 21:31 | ZN36100:PA5 | URBAN | Other | Other - Self Clearing Trigger | 50 | 108 | 0.0037312 | 0.0034505 | N
14/11/2016 | 08:20 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 154 | 0.00069362 | 0.00044977 | N
14/11/2016 | 08:46 | ZN3154:PA17 | URBAN | Other | Other | 1 | 187 | 0.0001293 | 6.9011e-05 | N
14/11/2016 | 11:47 | 258:80785 | URBAN | Other | Other | 1 | 50 | 3.4781e-05 | 6.9011e-05 | N
14/11/2016 | 12:07 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 62 | 0.00028066 | 0.00044977 | N
14/11/2016 | 17:02 | ZN3154:PA17 | URBAN | Other | Other | 1 | 181 | 0.00012497 | 6.9011e-05 | N
15/11/2016 | 09:33 | 206:34441 | URBAN | Other | Other | 1 | 56 | 3.8876e-05 | 6.9011e-05 | N
15/11/2016 | 11:49 | ZN12600:PA9 | SHORT RURAL | Other | Other | 1 | 66 | 0.00029603 | 0.00044977 | N
15/11/2016 | 13:05 | 230:81440 | SHORT RURAL | Other | Other | 1 | 95 | 0.00042556 | 0.00044977 | N
15/11/2016 | 13:20 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 100 | 0.00044925 | 0.00044977 | N
15/11/2016 | 20:20 | 507:80914 | SHORT RURAL | Other | Other | 1 | 110 | 0.0004961 | 0.00044977 | N
15/11/2016 | 21:35 | ZN10997:PA12 | URBAN | Other | Other - Arcing | 1 | 805 | 0.00055537 | 6.9011e-05 | N
16/11/2016 | 00:49 | ZN3472:PA22 | URBAN | Other | Other - Self Clearing Trigger | 899 | 39 | 0.024196 | 0.062042 | N
12/11/2016 | 03:37 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 236 | 0.0010615 | 0.00044977 | N
16/11/2016 | 09:13 | 507:80922 | SHORT RURAL | Other | Other | 1 | 187 | 0.00083914 | 0.00044978 | N
12/11/2016 | 10:00 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.032051 | 0.035613 | N
17/11/2016 | 06:10 | 242:81539 | URBAN | Other | Other - Self Clearing Trigger | 44 | 144 | 0.0043733 | 0.0030356 | N
17/11/2016 | 08:31 | ZN12690:PA24 | SHORT RURAL | Other | Other | 1 | 9 | 3.8745e-05 | 0.00044965 | N
17/11/2016 | 08:40 | 230:81438 | SHORT RURAL | Other | Other | 1 | 56 | 0.00025278 | 0.00044965 | N
17/11/2016 | 12:51 | ZN15004:PA3 | URBAN | Other | Other | 1 | 61 | 4.1993e-05 | 6.8991e-05 | N
17/11/2016 | 14:39 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 201 | 0.00090379 | 0.00044965 | N
17/11/2016 | 20:37 | ZN15014:PA11 | URBAN | Other | Other - Self Clearing Trigger | 1,013 | 131 | 0.091553 | 0.069888 | N
17/11/2016 | 20:37 | ZN15014:PA20 | URBAN | Other | Other - Self Clearing Trigger | 1 | 131 | 9.0378e-05 | 6.8991e-05 | N
18/11/2016 | 09:32 | 242:81539 | URBAN | Other | Other | 1 | 87 | 6.0114e-05 | 6.8991e-05 | N
18/11/2016 | 10:45 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 45 | 0.00020234 | 0.00044965 | N
18/11/2016 | 14:21 | ZN1673:PA18 | URBAN | Other | Other | 1 | 109 | 7.5005e-05 | 6.8991e-05 | N
19/11/2016 | 12:51 | ZN1673:PA9 | URBAN | Other | Other | 1 | 13 | 9.1186e-06 | 6.8993e-05 | N
20/11/2016 | 08:38 | ZN2568:PA9 | URBAN | Other | Other - Self Clearing Trigger | 35 | 62 | 0.0014972 | 0.0024148 | N
20/11/2016 | 21:48 | ZN72:PA10 | URBAN | Other | Other - Self Clearing Trigger | 102 | 71 | 0.0050177 | 0.0070375 | N
21/11/2016 | 05:25 | ZN2568:PA42 | URBAN | Other | Other - Arcing | 1 | 395 | 0.00027242 | 6.8995e-05 | N
21/11/2016 | 07:18 | 261:81885 | URBAN | Other | Other | 1 | 81 | 5.5886e-05 | 6.8995e-05 | N
21/11/2016 | 13:43 | ZN15008:PA7 | URBAN | Other | Other | 1 | 131 | 9.036e-05 | 6.8995e-05 | N
21/11/2016 | 14:49 | ZN9700:PA20 | URBAN | Other | Other - Arcing | 3 | 226 | 0.00046779 | 0.00020698 | N
21/11/2016 | 15:35 | 508:82574 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 63 | 0.0011331 | 0.0017986 | N
21/11/2016 | 17:04 | ZN2568:PA27 | URBAN | Other | Other - Self Clearing Trigger | 101 | 100 | 0.006972 | 0.0069685 | N
21/11/2016 | 17:54 | 528:83014 | SHORT RURAL | Other | Other - Self Clearing Trigger | 73 | 56 | 0.018228 | 0.032824 | N
21/11/2016 | 20:23 | ZN2835:PA41 | URBAN | Other | Other - Self Clearing Trigger | 1 | 112 | 7.7274e-05 | 6.8995e-05 | N
21/11/2016 | 22:25 | ZN116:PA53 | URBAN | Other | Other - Arcing | 1 | 214 | 0.00014798 | 6.8995e-05 | N
21/11/2016 | 22:29 | ZN116:PA53 | URBAN | Other | Other - Arcing | 1 | 31 | 2.1204e-05 | 6.8995e-05 | N
21/11/2016 | 22:31 | ZN116:PA53 | URBAN | Other | Other - Arcing | 1 | 28 | 1.9388e-05 | 6.8995e-05 | N
21/11/2016 | 22:34 | ZN10990:PA6 | URBAN | Other | Other - Arcing | 1 | 145 | 0.00010017 | 6.8995e-05 | N
21/11/2016 | 22:42 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 93 | 0.03312 | 0.035613 | N
21/11/2016 | 15:02 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 68 | 0.00030576 | 0.00044965 | N
22/11/2016 | 09:23 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 207 | 0.14744 | 0.071225 | N
22/11/2016 | 17:07 | 213:33777 | SHORT RURAL | Other | Other | 1 | 67 | 0.00030216 | 0.00044965 | N
22/11/2016 | 17:40 | 224:80346 | URBAN | Other | Other - Self Clearing Trigger | 53 | 40 | 0.0014603 | 0.0036568 | N
22/11/2016 | 18:53 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 82 | 0.00036871 | 0.00044965 | N
23/11/2016 | 15:09 | ZN195:PA28 | URBAN | Other | Other - Self Clearing Trigger | 17 | 136 | 0.0015952 | 0.001173 | N
22/11/2016 | 19:32 | ZN3154:PA11 | URBAN | Other | Other - Arcing | 1 | 687 | 0.00047411 | 6.8996e-05 | N
23/11/2016 | 06:28 | 801:74118 | URBAN | Other | Other - Self Clearing Trigger | 8 | 66 | 0.00036624 | 0.00055198 | N
23/11/2016 | 07:09 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 70 | 0.00031476 | 0.00044965 | N
23/11/2016 | 07:22 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 97 | 0.00043818 | 0.00044965 | N
23/11/2016 | 08:36 | 224:80329 | SHORT RURAL | Other | Other | 1 | 114 | 0.00051223 | 0.00044965 | N
23/11/2016 | 17:00 | ZN15008:PA7 | URBAN | Other | Other - Arcing | 1 | 170 | 0.00011745 | 6.8998e-05 | N
24/11/2016 | 08:22 | 526:34641 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 107 | 0.00048301 | 0.00044945 | N
24/11/2016 | 09:54 | 507:80925 | SHORT RURAL | Other | Other | 1 | 66 | 0.00029567 | 0.00044945 | N
24/11/2016 | 17:17 | 243:80084 | SHORT RURAL | Other | Other | 1 | 37 | 0.00016825 | 0.00044945 | N
24/11/2016 | 20:21 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 49 | 0.00088093 | 0.0017978 | N
25/11/2016 | 04:22 | ZN15008:PA9 | URBAN | Other | Other - Self Clearing Trigger | 1,193 | 85 | 0.069965 | 0.08229 | N
25/11/2016 | 04:22 | ZN15011:PA2 | URBAN | Other | Other - Self Clearing Trigger | 566 | 111 | 0.043336 | 0.039041 | N
25/11/2016 | 14:14 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 60 | 0.021479 | 0.0356 | N
27/11/2016 | 18:54 | ZN847:PA39 | URBAN | Other | Other | 1 | 98 | 6.7901e-05 | 6.9028e-05 | N
28/11/2016 | 02:48 | ZN180:PA33 | URBAN | Other | Other | 1 | 36 | 2.4563e-05 | 6.9028e-05 | N
28/11/2016 | 14:36 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 103 | 0.00046399 | 0.00044945 | N
28/11/2016 | 15:25 | 257:81988 | URBAN | Other | Other | 1 | 98 | 6.797e-05 | 6.9028e-05 | N
29/11/2016 | 08:08 | 504:48033 | SHORT RURAL | Other | Other | 1 | 97 | 0.00043417 | 0.00044945 | N
29/11/2016 | 10:47 | ZN180:PA27 | URBAN | Other | Other - Self Clearing Trigger | 113 | 112 | 0.008757 | 0.0078002 | N
29/11/2016 | 15:51 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 69 | 0.024564 | 0.0356 | N
29/11/2016 | 15:57 | 210:8682 | URBAN | Other | Other | 1 | 37 | 2.5851e-05 | 6.9028e-05 | N
29/11/2016 | 17:54 | 222:33600 | URBAN | Other | Other - Arcing | 1 | 155 | 0.00010706 | 6.9028e-05 | N
29/11/2016 | 18:53 | ZN129:PA28 | URBAN | Other | Other - Self Clearing Trigger | 65 | 62 | 0.0027818 | 0.0044868 | N
29/11/2016 | 19:45 | ZN15008:PA7 | URBAN | Other | Other - Arcing | 1 | 207 | 0.00014269 | 6.9028e-05 | N
29/11/2016 | 19:53 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 847 | 0.0038069 | 0.00044945 | N
29/11/2016 | 20:11 | 242:81539 | URBAN | Other | Other - Arcing | 1 | 165 | 0.00011366 | 6.9028e-05 | N
30/11/2016 | 08:04 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 101 | 0.071912 | 0.0712 | N
30/11/2016 | 16:06 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 44 | 236 | 0.046572 | 0.019776 | N
30/11/2016 | 16:38 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 277 | 0.001245 | 0.00044945 | N
30/11/2016 | 17:12 | ZN9118:PA21 | URBAN | Other | Other | 1 | 219 | 0.00015106 | 6.9028e-05 | N
30/11/2016 | 18:00 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 155 | 0.00209 | 0.0013484 | N
30/11/2016 | 18:05 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 284 | 0.0012774 | 0.00044945 | N
30/11/2016 | 18:07 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 153 | 0.0048137 | 0.0031462 | N
30/11/2016 | 18:09 | ZN10999:PA36 | URBAN | Other | Other - Arcing | 1 | 205 | 0.00014184 | 6.9028e-05 | N
30/11/2016 | 18:16 | ZN10999:PA36 | URBAN | Other | Other - Arcing | 1 | 198 | 0.00013693 | 6.9028e-05 | N
30/11/2016 | 18:30 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 170 | 0.00076407 | 0.00044945 | N
30/11/2016 | 19:32 | 220:8692 | URBAN | Other | Other - Arcing | 1 | 99 | 6.8338e-05 | 6.9028e-05 | N
30/11/2016 | 21:07 | 224:80346 | URBAN | Other | Other - Arcing | 1 | 127 | 8.7954e-05 | 6.9028e-05 | N
30/11/2016 | 21:11 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 694 | 0.024954 | 0.0035956 | N
01/12/2016 | 09:00 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 380 | 0.13528 | 0.0356 | N
01/12/2016 | 07:47 | ZN36200:PA4 | SHORT RURAL | Other | Other - Arcing | 9 | 168 | 0.0067929 | 0.0040434 | N
01/12/2016 | 06:01 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 189 | 0.0016982 | 0.00089853 | N
01/12/2016 | 06:05 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 215 | 0.0028978 | 0.0013478 | N
01/12/2016 | 06:03 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 149 | 146 | 0.097531 | 0.066941 | N
01/12/2016 | 07:05 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 65 | 0.00058405 | 0.00089853 | N
01/12/2016 | 08:06 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 84 | 0.00037738 | 0.00044927 | N
01/12/2016 | 09:01 | 202:34254 | URBAN | Other | Other | 1 | 89 | 6.1291e-05 | 6.9009e-05 | N
30/11/2016 | 20:28 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 112 | 0.0010068 | 0.00089891 | N
01/12/2016 | 21:23 | ZN15010:PA5 | URBAN | Other | Other - Arcing | 1 | 142 | 9.7659e-05 | 6.9009e-05 | N
01/12/2016 | 21:50 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 75 | 0.00033695 | 0.00044927 | N
02/12/2016 | 02:12 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 63 | 0.0016982 | 0.0026956 | N
02/12/2016 | 04:08 | ZN14892:PA17 | URBAN | Other | Other - Arcing | 28 | 272 | 0.0052538 | 0.0019322 | N
02/12/2016 | 05:39 | 233:82812 | SHORT RURAL | Other | Other - Self Clearing Trigger | 28 | 201 | 0.025285 | 0.012579 | N
02/12/2016 | 06:10 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 130 | 0.0017521 | 0.0013478 | N
02/12/2016 | 07:00 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 100 | 0.00089853 | 0.00089853 | N
02/12/2016 | 08:10 | ZN14144:PA2 | SHORT RURAL | Other | Other | 1 | 95 | 0.00042598 | 0.00044927 | N
02/12/2016 | 08:19 | ZN3472:PA30 | URBAN | Other | Other - Arcing | 1 | 340 | 0.00023483 | 6.9009e-05 | N
01/12/2016 | 05:15 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 410 | 0.14596 | 0.0356 | N
01/12/2016 | 08:43 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 97 | 0.00043579 | 0.00044927 | N
01/12/2016 | 09:52 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 28 | 0.00012579 | 0.00044927 | N
01/12/2016 | 11:00 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 50 | 0.0178 | 0.0356 | N
02/12/2016 | 23:30 | ZN10995:PA5 | URBAN | Other | Other - Arcing | 1,449 | 110 | 0.11043 | 0.099994 | N
02/12/2016 | 23:30 | ZN10995:PA7 | URBAN | Other | Other - Arcing | 2,138 | 110 | 0.16269 | 0.14754 | N
03/12/2016 | 02:38 | ZN180:PA7 | URBAN | Other | Other - Self Clearing Trigger | 67 | 102 | 0.0047127 | 0.0046203 | N
03/12/2016 | 07:31 | 225:33676 | URBAN | Other | Other | 1 | 72 | 4.9363e-05 | 6.8959e-05 | N
03/12/2016 | 07:34 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 221 | 0.078676 | 0.0356 | N
03/12/2016 | 09:02 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 358 | 0.0032168 | 0.00089854 | N
03/12/2016 | 15:19 | 225:33670 | URBAN | Other | Other | 1 | 89 | 6.1534e-05 | 6.8959e-05 | N
03/12/2016 | 20:13 | ZN15008:PA10 | URBAN | Other | Other - Arcing | 1 | 214 | 0.00014789 | 6.8959e-05 | N
04/12/2016 | 21:57 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 82 | 0.00036998 | 0.00044927 | N
05/12/2016 | 05:54 | ZN2466:PA5 | URBAN | Other | Other - Arcing | 1 | 365 | 0.00025176 | 6.8959e-05 | N
05/12/2016 | 06:21 | ZN2635:PA52 | URBAN | Other | Other | 1 | 109 | 7.5108e-05 | 6.8959e-05 | N
05/12/2016 | 06:23 | ZN2635:PA52 | URBAN | Other | Other - Arcing | 1 | 277 | 0.00019068 | 6.8959e-05 | N
05/12/2016 | 14:16 | 514:18146 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 321 | 0.0072108 | 0.0022464 | N
05/12/2016 | 14:48 | 814:82291 | SHORT RURAL | Other | Other - Self Clearing Trigger | 45 | 142 | 0.028648 | 0.020217 | N
05/12/2016 | 15:02 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 26 | 148 | 0.01727 | 0.011681 | N
05/12/2016 | 15:00 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 120 | 0.00053913 | 0.00044927 | N
05/12/2016 | 15:32 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 418 | 0.001878 | 0.00044927 | N
05/12/2016 | 16:04 | ZN847:PA2 | URBAN | Other | Other - Self Clearing Trigger | 20 | 265 | 0.0036551 | 0.0013792 | N
05/12/2016 | 16:11 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 109 | 0.0014691 | 0.0013478 | N
05/12/2016 | 16:41 | ZN12630:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 565 | 90 | 0.22846 | 0.25384 | N
05/12/2016 | 16:41 | ZN12630:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 322 | 90 | 0.1302 | 0.14467 | N
05/12/2016 | 16:41 | ZN12630:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 238 | 90 | 0.096234 | 0.10693 | N
05/12/2016 | 16:41 | ZN12630:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 94 | 90 | 0.038008 | 0.042232 | N
05/12/2016 | 16:41 | ZN12630:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 414 | 90 | 0.1674 | 0.186 | N
05/12/2016 | 16:41 | ZN12630:PA6 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 90 | 0.0028304 | 0.0031449 | N
05/12/2016 | 16:41 | ZN12630:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 373 | 90 | 0.15082 | 0.16758 | N
05/12/2016 | 16:59 | ZN36100:PA23 | URBAN | Other | Other - Arcing | 1 | 270 | 0.00018628 | 6.8959e-05 | N
05/12/2016 | 17:02 | ZN12690:PA24 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 137 | 0.0074067 | 0.0053913 | N
05/12/2016 | 17:20 | ZN1850:PA10 | URBAN | Other | Other - Arcing | 1 | 294 | 0.00020274 | 6.8959e-05 | N
05/12/2016 | 17:34 | ZN13000:PA5 | SHORT RURAL | Other | Other | 1 | 9 | 4.1932e-05 | 0.00044927 | N
05/12/2016 | 16:44 | ZN2400:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 396 | 0.01957 | 0.004942 | N
05/12/2016 | 18:25 | ZN12630:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 46 | 0.00020614 | 0.00044927 | N
05/12/2016 | 20:17 | 812:19071 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 53 | 0.00023632 | 0.00044927 | N
05/12/2016 | 20:35 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 740 | 0.0066492 | 0.00089855 | N
05/12/2016 | 21:14 | 526:34640 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 751 | 0.010119 | 0.0013478 | N
05/12/2016 | 21:58 | ZN12660:PA14 | SHORT RURAL | Other | Other - Arcing | 1 | 182 | 0.0008176 | 0.00044927 | N
05/12/2016 | 22:21 | ZN4545:PA31 | URBAN | Other | Other - Self Clearing Trigger | 2,991 | 213 | 0.4397 | 0.20626 | N
06/12/2016 | 05:49 | ZN35900:PA2 | URBAN | Other | Other - Arcing | 1 | 221 | 0.00015228 | 6.8961e-05 | N
06/12/2016 | 07:15 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 75 | 0.00033696 | 0.00044927 | N
06/12/2016 | 07:22 | 508:82574 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 253 | 0.0011358 | 0.00044927 | N
06/12/2016 | 13:10 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 298 | 2 | 0.0026777 | 0.13388 | N
05/12/2016 | 22:27 | 238:34141 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 658 | 0.0088686 | 0.0013478 | N
06/12/2016 | 09:33 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 121 | 0.043094 | 0.0356 | N
06/12/2016 | 09:30 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 235 | 0.0010558 | 0.00044927 | N
06/12/2016 | 09:45 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 160 | 0.0014377 | 0.00089855 | N
06/12/2016 | 10:21 | 812:19071 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 119 | 0.0016039 | 0.0013478 | N
05/12/2016 | 15:00 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 150 | 0.00067391 | 0.00044927 | N
06/12/2016 | 11:12 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 88 | 0.0019768 | 0.0022464 | N
05/12/2016 | 15:32 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 403 | 0.0018106 | 0.00044927 | N
06/12/2016 | 11:59 | ZN15004:PA9 | URBAN | Other | Other | 1 | 366 | 0.0002527 | 6.8961e-05 | N
06/12/2016 | 12:17 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 178 | 0.0031988 | 0.0017971 | N
06/12/2016 | 12:38 | 526:34640 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 140 | 0.0037739 | 0.0026956 | N
06/12/2016 | 13:27 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 86 | 0.0077275 | 0.0089855 | N
06/12/2016 | 14:17 | ZN2602:PA28 | URBAN | Other | Other - Arcing | 1 | 163 | 0.00011241 | 6.8961e-05 | N
06/12/2016 | 14:31 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 154 | 0.0062269 | 0.0040435 | N
06/12/2016 | 14:38 | ZN3155:PA19 | URBAN | Other | Other - Arcing | 1 | 232 | 0.00015964 | 6.8961e-05 | N
06/12/2016 | 14:42 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 43 | 0.00057956 | 0.0013478 | N
06/12/2016 | 14:55 | ZN10996:PA10 | URBAN | Other | Other - Arcing | 1 | 455 | 0.00031354 | 6.8961e-05 | N
06/12/2016 | 15:55 | ZN12640:PA16 | URBAN | Other | Other | 1 | 96 | 6.6019e-05 | 6.8961e-05 | N
06/12/2016 | 17:51 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 34 | 0.011973 | 0.0356 | N
06/12/2016 | 18:05 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 115 | 0.00051667 | 0.00044927 | N
06/12/2016 | 19:30 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 57 | 0.0012804 | 0.0022464 | N
06/12/2016 | 19:41 | 232:33407 | SHORT RURAL | Other | Other - Arcing | 1 | 259 | 0.0011635 | 0.00044927 | N
06/12/2016 | 22:51 | ZN2310:PA65 | URBAN | Other | Other - Arcing | 1 | 326 | 0.00022447 | 6.8961e-05 | N
07/12/2016 | 03:40 | ZN3472:PA8 | URBAN | Other | Other - Arcing | 1 | 319 | 0.00022015 | 6.8962e-05 | N
07/12/2016 | 05:53 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 194 | 0.0034858 | 0.0017971 | N
07/12/2016 | 06:44 | ZN15006:PA6 | URBAN | Other | Other - Arcing | 1 | 496 | 0.00034182 | 6.8962e-05 | N
07/12/2016 | 08:21 | ZN36200:PA4 | SHORT RURAL | Other | Other | 1 | 64 | 0.00028851 | 0.00044928 | N
07/12/2016 | 09:52 | ZN180:PA10 | URBAN | Other | Other - Arcing | 1 | 278 | 0.00019152 | 6.8962e-05 | N
07/12/2016 | 09:57 | ZN3154:PA4 | URBAN | Other | Other | 1 | 180 | 0.00012427 | 6.8962e-05 | N
07/12/2016 | 10:54 | ZN12650:PA6 | URBAN | Other | Other - Arcing | 1 | 726 | 0.00050035 | 6.8962e-05 | N
07/12/2016 | 15:48 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 102 | 0.00045826 | 0.00044928 | N
07/12/2016 | 16:47 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 73 | 0.00065595 | 0.00089856 | N
07/12/2016 | 17:32 | ZN2835:PA17 | URBAN | Other | Other - Self Clearing Trigger | 71 | 373 | 0.018263 | 0.0048963 | N
07/12/2016 | 17:32 | ZN2835:PA35 | URBAN | Other | Other - Self Clearing Trigger | 62 | 373 | 0.015948 | 0.0042756 | N
07/12/2016 | 22:19 | 205:12206 | URBAN | Other | Other - Self Clearing Trigger | 24 | 195 | 0.0032304 | 0.0016551 | N
07/12/2016 | 13:00 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 109 | 0.00048971 | 0.00044928 | N
08/12/2016 | 10:26 | ZN12620:PA1 | SHORT RURAL | Other | Other | 1 | 77 | 0.00034608 | 0.00044936 | N
08/12/2016 | 21:29 | ZN36100:PA13 | URBAN | Other | Other - Arcing | 18 | 295 | 0.0036652 | 0.0012408 | N
08/12/2016 | 23:29 | 264:81244 | SHORT RURAL | Other | Other - Self Clearing Trigger | 83 | 104 | 0.038618 | 0.037297 | N
09/12/2016 | 04:17 | 224:80341 | URBAN | Other | Other - Self Clearing Trigger | 93 | 67 | 0.0042987 | 0.0064112 | N
09/12/2016 | 12:34 | ZN12610:PA23 | URBAN | Other | Other | 1 | 122 | 8.4207e-05 | 6.8938e-05 | N
09/12/2016 | 13:06 | ZN12570:PA37 | SHORT RURAL | Other | Other - Arcing | 1 | 49 | 0.0002189 | 0.00044934 | N
09/12/2016 | 15:14 | ZN1068:PA22 | URBAN | Other | Other - Arcing | 1 | 439 | 0.00030236 | 6.8938e-05 | N
09/12/2016 | 17:33 | ZN12600:PA3 | URBAN | Other | Other - Arcing | 1 | 206 | 0.00014218 | 6.8938e-05 | N
10/12/2016 | 12:14 | 806:82667 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 136 | 0.00061043 | 0.00044934 | N
10/12/2016 | 13:50 | 261:81879 | URBAN | Other | Other | 1 | 64 | 4.4247e-05 | 6.8939e-05 | N
10/12/2016 | 14:05 | ZN1287:PA3 | URBAN | Other | Other - Self Clearing Trigger | 66 | 40 | 0.0017988 | 0.00455 | N
11/12/2016 | 06:45 | ZN12610:PA13 | URBAN | Other | Other | 1 | 94 | 6.4713e-05 | 6.8941e-05 | N
11/12/2016 | 07:57 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 68 | 0.00030526 | 0.00044935 | N
11/12/2016 | 11:18 | ZN965:PA15 | URBAN | Other | Other | 1 | 76 | 5.2062e-05 | 6.8941e-05 | N
11/12/2016 | 11:48 | ZN80:PA32 | URBAN | Other | Other | 1 | 63 | 4.3537e-05 | 6.8941e-05 | N
11/12/2016 | 14:13 | 224:80326 | SHORT RURAL | Other | Other | 1 | 51 | 0.00023127 | 0.00044935 | N
11/12/2016 | 20:24 | ZN263:PA31 32KLM | CBD | Other | Other - Self Clearing Trigger | 26 | 144 | 0.12054 | 0.083706 | N
11/12/2016 | 20:33 | ZN12640:PA8 | URBAN | Other | Other - Self Clearing Trigger | 58 | 76 | 0.0030449 | 0.0039986 | N
12/12/2016 | 09:32 | 202:34260 | URBAN | Other | Other | 1 | 148 | 0.00010172 | 6.8941e-05 | N
09/12/2016 | 11:00 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 80 | 0.00071894 | 0.00089868 | N
12/12/2016 | 11:27 | 261:81865 | URBAN | Other | Other | 1 | 80 | 5.5084e-05 | 6.8941e-05 | N
12/12/2016 | 11:42 | 258:80793 | URBAN | Other | Other | 1 | 114 | 7.826e-05 | 6.8941e-05 | N
12/12/2016 | 12:49 | 514:18141 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 121 | 0.00054372 | 0.00044935 | N
12/12/2016 | 13:26 | 223:14394 | URBAN | Other | Other | 1 | 63 | 4.3169e-05 | 6.8941e-05 | N
12/12/2016 | 15:01 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 94 | 0.00042239 | 0.00044935 | N
12/12/2016 | 15:34 | ZN12610:PA16 | SHORT RURAL | Other | Other | 1 | 60 | 0.00026841 | 0.00044935 | N
12/12/2016 | 17:38 | ZN12610:PA16 | SHORT RURAL | Other | Other - Arcing | 1 | 231 | 0.0010402 | 0.00044935 | N
12/12/2016 | 18:43 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 142 | 0.0012762 | 0.00089871 | N
13/12/2016 | 03:56 | 227:13018 | URBAN | Other | Other | 1 | 79 | 5.4384e-05 | 6.8942e-05 | N
13/12/2016 | 04:49 | ZN15006:PA12 | URBAN | Other | Other - Self Clearing Trigger | 821 | 46 | 0.026037 | 0.056601 | N
13/12/2016 | 08:29 | 232:11460 | URBAN | Other | Other | 1 | 87 | 6.0198e-05 | 6.8942e-05 | N
13/12/2016 | 10:24 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 121 | 0.0010874 | 0.00089871 | N
13/12/2016 | 12:05 | 238:34140 | URBAN | Other | Other | 1 | 94 | 6.507e-05 | 6.8942e-05 | N
13/12/2016 | 13:13 | 214:8665 | URBAN | Other | Other | 1 | 124 | 8.5339e-05 | 6.8942e-05 | N
13/12/2016 | 13:17 | 214:8665 | URBAN | Other | Other | 1 | 119 | 8.2282e-05 | 6.8942e-05 | N
13/12/2016 | 14:05 | ZN12650:PA20 | URBAN | Other | Other - Arcing | 1,532 | 35 | 0.036606 | 0.10562 | N
13/12/2016 | 14:25 | ZN630:PA41 | URBAN | Other | Other - Self Clearing Trigger | 6 | 121 | 0.00050142 | 0.00041365 | N
13/12/2016 | 15:00 | ZN262:PA42 | URBAN | Other | Other - Self Clearing Trigger | 1 | 1,110 | 0.00076518 | 6.8942e-05 | N
13/12/2016 | 15:05 | ZN10999:PA22 | URBAN | Other | Other - Self Clearing Trigger | 128 | 114 | 0.010087 | 0.0088246 | N
13/12/2016 | 18:03 | 528:83011 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 137 | 0.011081 | 0.0080884 | N
13/12/2016 | 20:44 | 528:83011 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 31 | 0.0025074 | 0.0080884 | N
13/12/2016 | 22:31 | ZN3922:PA29 | URBAN | Other | Other - Self Clearing Trigger | 75 | 170 | 0.0088065 | 0.0051707 | N
14/12/2016 | 06:11 | ZN10997:PA2 | URBAN | Other | Other - Self Clearing Trigger | 103 | 86 | 0.0060916 | 0.0071011 | N
14/12/2016 | 09:08 | ZN35600:PA14 | URBAN | Other | Other | 1 | 177 | 0.00012175 | 6.8943e-05 | N
14/12/2016 | 20:03 | ZN35500:PA34 | URBAN | Other | Other - Arcing | 1 | 206 | 0.0001423 | 6.8943e-05 | N
14/12/2016 | 20:23 | ZN15006:PA2 | URBAN | Other | Other - Arcing | 1 | 174 | 0.00011966 | 6.8943e-05 | N
14/12/2016 | 20:29 | ZN711:PA15 | URBAN | Other | Other - Arcing | 1 | 180 | 0.00012414 | 6.8943e-05 | N
14/12/2016 | 21:08 | ZN15012:PA4 | URBAN | Other | Other - Arcing | 1 | 243 | 0.0001678 | 6.8943e-05 | N
14/12/2016 | 23:05 | ZN12660:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 24 | 165 | 0.017789 | 0.010785 | N
15/12/2016 | 00:34 | ZN4545:PA25 | URBAN | Other | Other - Arcing | 1 | 445 | 0.00030702 | 6.8924e-05 | N
15/12/2016 | 00:40 | ZN129:PA16 | URBAN | Other | Other - Arcing | 1 | 529 | 0.00036491 | 6.8924e-05 | N
15/12/2016 | 00:58 | ZN36200:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,213 | 173 | 0.9437 | 0.54474 | N
15/12/2016 | 01:12 | ZN35400:PA81 | URBAN | Other | Other - Arcing | 1 | 467 | 0.0003222 | 6.8924e-05 | N
15/12/2016 | 01:44 | ZN15014:PA19 | URBAN | Other | Other - Arcing | 1 | 1,035 | 0.00071339 | 6.8924e-05 | N
15/12/2016 | 02:18 | ZN15004:PA9 | URBAN | Other | Other - Arcing | 1 | 582 | 0.00040109 | 6.8924e-05 | N
15/12/2016 | 02:41 | ZN15012:PA8 | URBAN | Other | Other - Arcing | 1 | 484 | 0.00033351 | 6.8924e-05 | N
15/12/2016 | 04:08 | ZN398:PA20 | URBAN | Other | Other - Arcing | 1 | 472 | 0.00032524 | 6.8924e-05 | N
15/12/2016 | 04:10 | ZN36300:PA1 | URBAN | Other | Other - Arcing | 1 | 454 | 0.00031322 | 6.8924e-05 | N
15/12/2016 | 05:48 | ZN10996:PA9 | URBAN | Other | Other - Arcing | 1 | 222 | 0.00015287 | 6.8924e-05 | N
15/12/2016 | 06:19 | ZN12650:PA10 | URBAN | Other | Other - Arcing | 1 | 190 | 0.00013117 | 6.8924e-05 | N
15/12/2016 | 06:35 | ZN398:PA2 | URBAN | Other | Other - Arcing | 1 | 174 | 0.00012005 | 6.8924e-05 | N
15/12/2016 | 06:54 | ZN10999:PA29 | URBAN | Other | Other - Arcing | 1 | 156 | 0.00010738 | 6.8924e-05 | N
15/12/2016 | 07:19 | ZN12580:PA16 | URBAN | Other | Other - Arcing | 1 | 190 | 0.00013106 | 6.8924e-05 | N
15/12/2016 | 07:26 | ZN3155:PA16 | URBAN | Other | Other - Self Clearing Trigger | 27 | 123 | 0.002289 | 0.001861 | N
15/12/2016 | 07:26 | ZN3155:PA20 | URBAN | Other | Other - Self Clearing Trigger | 1 | 122 | 8.4088e-05 | 6.8924e-05 | N
15/12/2016 | 07:35 | ZN3154:PA22 | SHORT RURAL | Other | Other - Arcing | 1 | 415 | 0.001862 | 0.00044909 | N
15/12/2016 | 07:54 | 502:48002 | URBAN | Other | Other - Arcing | 1 | 246 | 0.00016953 | 6.8924e-05 | N
15/12/2016 | 08:08 | ZN3425:PA33 | URBAN | Other | Other - Arcing | 1 | 22 | 1.5324e-05 | 6.8924e-05 | N
15/12/2016 | 08:37 | ZN80:PA31 | URBAN | Other | Other - Arcing | 1 | 82 | 5.6736e-05 | 6.8924e-05 | N
15/12/2016 | 08:53 | ZN4545:PA36 | URBAN | Other | Other - Arcing | 1 | 187 | 0.00012854 | 6.8924e-05 | N
15/12/2016 | 09:12 | ZN2835:PA30 | URBAN | Other | Other - Arcing | 1 | 108 | 7.4209e-05 | 6.8924e-05 | N
15/12/2016 | 09:26 | ZN2835:PA30 | URBAN | Other | Other - Arcing | 1 | 93 | 6.4157e-05 | 6.8924e-05 | N
15/12/2016 | 11:24 | ZN1673:PA2 | URBAN | Other | Other - Arcing | 1 | 396 | 0.00027292 | 6.8924e-05 | N
15/12/2016 | 14:33 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 4 | 111 | 0.15806 | 0.1424 | N
15/12/2016 | 16:08 | 213:33775 | URBAN | Other | Other - Self Clearing Trigger | 60 | 122 | 0.0050453 | 0.0041355 | N
15/12/2016 | 17:10 | ZN3472:PA12 | URBAN | Other | Other - Arcing | 1 | 427 | 0.00029416 | 6.8924e-05 | N
15/12/2016 | 19:51 | ZN14144:PA2 | SHORT RURAL | Other | Other | 1 | 136 | 0.00061121 | 0.00044909 | N
16/12/2016 | 04:39 | ZN180:PA18 | URBAN | Other | Other - Self Clearing Trigger | 62 | 176 | 0.0075148 | 0.0042734 | N
16/12/2016 | 06:23 | ZN15006:PA2 | URBAN | Other | Other - Self Clearing Trigger | 156 | 106 | 0.011424 | 0.010752 | N
16/12/2016 | 08:40 | ZN342:PA16 | URBAN | Other | Other - Arcing | 1 | 379 | 0.00026131 | 6.8926e-05 | N
16/12/2016 | 09:27 | ZN35900:PA3 | URBAN | Other | Other - Arcing | 1 | 152 | 0.00010489 | 6.8926e-05 | N
16/12/2016 | 10:42 | ZN1287:PA5 | URBAN | Other | Other - Arcing | 1 | 287 | 0.00019801 | 6.8926e-05 | N
16/12/2016 | 10:55 | ZN12580:PA4 | URBAN | Other | Other | 1 | 141 | 9.7415e-05 | 6.8926e-05 | N
16/12/2016 | 12:34 | 213:33775 | URBAN | Other | Other - Self Clearing Trigger | 60 | 89 | 0.0036806 | 0.0041355 | N
16/12/2016 | 13:08 | 511:29877 | SHORT RURAL | Other | Other - Arcing | 1 | 341 | 0.0015316 | 0.00044908 | N
16/12/2016 | 13:21 | ZN35900:PA23 | SHORT RURAL | Other | Other - Arcing | 1 | 278 | 0.0012501 | 0.00044908 | N
16/12/2016 | 14:19 | ZN10991:PA12 | URBAN | Other | Other - Arcing | 1 | 400 | 0.00027576 | 6.8926e-05 | N
16/12/2016 | 14:34 | 210:8682 | URBAN | Other | Other - Self Clearing Trigger | 30 | 91 | 0.0018727 | 0.0020678 | N
16/12/2016 | 16:51 | ZN35370:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 84 | 0.00037551 | 0.00044908 | N
16/12/2016 | 17:36 | ZN398:PA4 | URBAN | Other | Other | 1 | 87 | 5.969e-05 | 6.8926e-05 | N
16/12/2016 | 22:42 | ZN2310:PA60 | URBAN | Other | Other - Self Clearing Trigger | 29 | 673 | 0.013452 | 0.0019988 | N
22/12/2016 | 01:46 | ZN129:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 66 | 36 | 0.010667 | 0.029631 | N
22/12/2016 | 01:46 | ZN35500:PA24 | URBAN | Other | Other - Self Clearing Trigger | 614 | 36 | 0.015231 | 0.042309 | N
17/12/2016 | 16:23 | 507:80923 | SHORT RURAL | Other | Other | 1 | 61 | 0.00027447 | 0.00044909 | N
17/12/2016 | 16:46 | 507:80923 | SHORT RURAL | Other | Other | 1 | 39 | 0.00017477 | 0.00044909 | N
17/12/2016 | 18:14 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 270 | 0.0024272 | 0.00089817 | N
17/12/2016 | 19:58 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 43 | 0.00019183 | 0.00044909 | N
17/12/2016 | 21:50 | ZN10990:PA1 | URBAN | Other | Other - Self Clearing Trigger | 51 | 75 | 0.0026364 | 0.0035153 | N
17/12/2016 | 22:21 | ZN690:PA35 | URBAN | Other | Other - Self Clearing Trigger | 101 | 194 | 0.013503 | 0.0069616 | N
17/12/2016 | 23:18 | ZN3672:PA44 | URBAN | Other | Other - Self Clearing Trigger | 89 | 852 | 0.052251 | 0.0061345 | N
18/12/2016 | 00:29 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 121 | 0.00054241 | 0.00044908 | N
18/12/2016 | 01:03 | ZN13000:PA7 | SHORT RURAL | Other | Other | 1 | 75 | 0.00033591 | 0.00044908 | N
18/12/2016 | 02:33 | 508:82578 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 302 | 0.0054248 | 0.0017963 | N
18/12/2016 | 05:47 | ZN7481:PA17 | URBAN | Other | Other - Self Clearing Trigger | 66 | 223 | 0.010159 | 0.0045491 | N
18/12/2016 | 07:03 | 239:82129 | SHORT RURAL | Other | Other | 1 | 85 | 0.00038172 | 0.00044908 | N
18/12/2016 | 07:48 | ZN12640:PA13 | SHORT RURAL | Other | Other - Arcing | 1 | 287 | 0.0012886 | 0.00044908 | N
18/12/2016 | 08:31 | ZN1788:PA11 | URBAN | Other | Other - Arcing | 1 | 479 | 0.00033009 | 6.8926e-05 | N
18/12/2016 | 11:38 | ZN12610:PA16 | SHORT RURAL | Other | Other | 1 | 66 | 0.00029549 | 0.00044908 | N
18/12/2016 | 12:30 | 258:80787 | URBAN | Other | Other | 1 | 59 | 4.0919e-05 | 6.8926e-05 | N
18/12/2016 | 17:40 | ZN1610:PA19 | URBAN | Other | Other - Arcing | 1 | 236 | 0.0001624 | 6.8926e-05 | N
18/12/2016 | 17:57 | ZN14891:PA1 | SHORT RURAL | Other | Other | 1 | 140 | 0.00062908 | 0.00044908 | N
18/12/2016 | 18:32 | ZN14891:PA9 | URBAN | Other | Other | 1 | 55 | 3.7921e-05 | 6.8926e-05 | N
18/12/2016 | 18:36 | ZN3472:PA33 | URBAN | Other | Other - Arcing | 1 | 414 | 0.00028506 | 6.8926e-05 | N
18/12/2016 | 21:49 | ZN12650:PA12 | URBAN | Other | Other - Arcing | 1 | 671 | 0.00046235 | 6.8926e-05 | N
18/12/2016 | 22:45 | ZN12690:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 554 | 0.0024893 | 0.00044908 | N
19/12/2016 | 00:53 | ZN12690:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 284 | 0.0012748 | 0.00044908 | N
19/12/2016 | 05:50 | ZN1193:PA21 | URBAN | Other | Other - Arcing | 1 | 250 | 0.00017215 | 6.8927e-05 | N
19/12/2016 | 06:56 | ZN2635:PA58 | URBAN | Other | Other - Arcing | 1 | 3 | 2.1138e-06 | 6.8927e-05 | N
19/12/2016 | 10:30 | ZN3155:PA12 | URBAN | Other | Other - Arcing | 1 | 150 | 0.00010324 | 6.8927e-05 | N
19/12/2016 | 16:00 | ZN35400:PA52 | URBAN | Other | Other - Arcing | 1 | 1,050 | 0.00072366 | 6.8927e-05 | N
19/12/2016 | 21:10 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 74 | 0.0089888 | 0.012125 | N
20/12/2016 | 07:00 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 435 | 0.0058605 | 0.0013472 | N
20/12/2016 | 07:24 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 260 | 0.0011695 | 0.00044908 | N
20/12/2016 | 07:40 | 210:8682 | URBAN | Other | Other | 1 | 40 | 2.7548e-05 | 6.8927e-05 | N
20/12/2016 | 07:57 | ZN2466:PA20 | URBAN | Other | Other - Self Clearing Trigger | 1 | 168 | 0.0001158 | 6.8927e-05 | N
20/12/2016 | 08:07 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 113 | 0.00050746 | 0.00044908 | N
20/12/2016 | 08:55 | ZN4545:PA29 | URBAN | Other | Other - Arcing | 1 | 155 | 0.0001067 | 6.8927e-05 | N
20/12/2016 | 09:05 | ZN15014:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 324 | 0.0014572 | 0.00044908 | N
20/12/2016 | 15:25 | 216:10728 | SHORT RURAL | Other | Other | 1 | 136 | 0.00061277 | 0.00044908 | N
20/12/2016 | 19:19 | ZN8000:PA1 | URBAN | Other | Other - Arcing | 1 | 206 | 0.00014191 | 6.8927e-05 | N
18/12/2016 | 17:40 | ZN1610:PA19 | URBAN | Other | Other - Arcing | 2 | 220 | 0.00030328 | 0.00013785 | N
21/12/2016 | 10:29 | 813:89063 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 121 | 0.0010868 | 0.0008982 | N
21/12/2016 | 12:11 | ZN188:PA27 | URBAN | Other | Other - Arcing | 1 | 288 | 0.00019852 | 6.8928e-05 | N
21/12/2016 | 20:14 | 227:13015 | SHORT RURAL | Other | Other | 1 | 216 | 0.00096983 | 0.0004491 | N
21/12/2016 | 20:58 | ZN3425:PA22 | URBAN | Other | Other - Arcing | 1 | 145 | 9.9934e-05 | 6.8928e-05 | N
21/12/2016 | 21:01 | ZN1673:PA9 | URBAN | Other | Other | 1 | 177 | 0.00012214 | 6.8928e-05 | N
22/12/2016 | 09:50 | ZN10995:PA7 | URBAN | Other | Other - Arcing | 1 | 249 | 0.00017172 | 6.8907e-05 | N
22/12/2016 | 11:50 | ZN14891:PA16 | SHORT RURAL | Other | Other | 1 | 347 | 0.0015585 | 0.00044895 | N
21/12/2016 | 14:20 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 30 | 0.010684 | 0.035613 | N
22/12/2016 | 20:04 | ZN14891:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 79 | 0.00035654 | 0.00044895 | N
23/12/2016 | 14:10 | ZN116:PA84 | URBAN | Other | Other - Arcing | 1 | 258 | 0.00017747 | 6.8908e-05 | N
23/12/2016 | 16:42 | 214:8669 | URBAN | Other | Other | 1 | 32 | 2.2211e-05 | 6.8908e-05 | N
23/12/2016 | 18:30 | 261:81870 | URBAN | Other | Other | 1 | 67 | 4.6157e-05 | 6.8908e-05 | N
23/12/2016 | 19:13 | ZN874:PA12 | URBAN | Other | Other - Arcing | 1 | 183 | 0.00012606 | 6.8908e-05 | N
24/12/2016 | 08:13 | ZN2400:PA15 | SHORT RURAL | Other | Other - Arcing | 1 | 285 | 0.0012788 | 0.00044897 | N
24/12/2016 | 08:15 | 221:11900 | SHORT RURAL | Other | Other | 1 | 58 | 0.00026257 | 0.00044897 | N
24/12/2016 | 12:20 | 233:82815 | SHORT RURAL | Other | Other | 1 | 159 | 0.0007117 | 0.00044897 | N
24/12/2016 | 12:29 | 233:82815 | SHORT RURAL | Other | Other | 1 | 151 | 0.00067623 | 0.00044897 | N
24/12/2016 | 16:13 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 255 | 75 | 6.8133 | 9.0844 | N
24/12/2016 | 16:36 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 279 | 0.012526 | 0.0044897 | N
24/12/2016 | 16:42 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 468 | 0.0021012 | 0.00044897 | N
24/12/2016 | 16:49 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 541 | 0.019432 | 0.0035918 | N
24/12/2016 | 17:01 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 199 | 0.070894 | 0.035625 | N
24/12/2016 | 17:57 | 508:82574 | SHORT RURAL | Other | Other - Self Clearing Trigger | 57 | 76 | 0.019373 | 0.025591 | N
24/12/2016 | 18:00 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 376 | 166 | 0.28015 | 0.16881 | N
24/12/2016 | 18:00 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 1,705 | 0.60741 | 0.035625 | N
24/12/2016 | 18:07 | 504:48026 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,276 | 48 | 0.27499 | 0.57289 | N
24/12/2016 | 18:07 | 504:48027 | URBAN | Other | Other - Self Clearing Trigger | 133 | 48 | 0.0043991 | 0.0091647 | N
24/12/2016 | 18:07 | 504:48028 | URBAN | Other | Other - Self Clearing Trigger | 1,266 | 48 | 0.041874 | 0.087237 | N
24/12/2016 | 18:07 | 504:48029 | URBAN | Other | Other - Self Clearing Trigger | 255 | 48 | 0.0084343 | 0.017571 | N
24/12/2016 | 18:07 | 504:48031 | SHORT RURAL | Other | Other - Self Clearing Trigger | 561 | 48 | 0.1209 | 0.25187 | N
24/12/2016 | 18:07 | 504:48032 | URBAN | Other | Other - Self Clearing Trigger | 336 | 48 | 0.011113 | 0.023153 | N
24/12/2016 | 18:07 | 504:48033 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,167 | 48 | 0.2515 | 0.52395 | N
24/12/2016 | 18:07 | 504:48034 | URBAN | Other | Other - Self Clearing Trigger | 1,414 | 48 | 0.046769 | 0.097435 | N
24/12/2016 | 18:07 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 814 | 50 | 14.4995 | 28.9989 | N
24/12/2016 | 18:07 | 509:33397 | SHORT RURAL | Other | Other - Self Clearing Trigger | 398 | 50 | 0.089345 | 0.17869 | N
24/12/2016 | 18:07 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 907 | 50 | 0.20361 | 0.40722 | N
24/12/2016 | 18:07 | 525:34580 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 144 | 0.001293 | 0.00089794 | N
24/12/2016 | 18:07 | 525:34586 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 144 | 0.001293 | 0.00089794 | N
24/12/2016 | 18:07 | 525:34589 | URBAN | Other | Other - Self Clearing Trigger | 1 | 144 | 9.9227e-05 | 6.8908e-05 | N
24/12/2016 | 18:26 | 261:81870 | URBAN | Other | Other | 1 | 78 | 5.3472e-05 | 6.8908e-05 | N
24/12/2016 | 19:29 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 211 | 0.0047367 | 0.0022449 | N
24/12/2016 | 18:43 | ZN847:PA46 | URBAN | Other | Other - Arcing | 1 | 301 | 0.00020752 | 6.8908e-05 | N
24/12/2016 | 18:52 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 174 | 0.00078308 | 0.00044897 | N
24/12/2016 | 18:54 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 26 | 0.018525 | 0.07125 | N
24/12/2016 | 18:56 | ZN12600:PA3 | URBAN | Other | Other | 1 | 61 | 4.208e-05 | 6.8908e-05 | N
24/12/2016 | 19:03 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 232 | 0.082651 | 0.035625 | N
24/12/2016 | 19:50 | ZN187:PA17 | URBAN | Other | Other - Arcing | 1 | 490 | 0.00033757 | 6.8908e-05 | N
24/12/2016 | 19:39 | 223:14394 | URBAN | Other | Other - Arcing | 1 | 129 | 8.9086e-05 | 6.8908e-05 | N
24/12/2016 | 19:53 | 508:82575 | SHORT RURAL | Other | Other - Arcing | 1 | 327 | 0.0014676 | 0.00044897 | N
24/12/2016 | 20:13 | ZN116:PA73 | URBAN | Other | Other - Arcing | 1 | 322 | 0.0002222 | 6.8908e-05 | N
24/12/2016 | 20:45 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 75 | 0.026719 | 0.035625 | N
24/12/2016 | 21:04 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 746 | 0.53153 | 0.07125 | N
24/12/2016 | 22:04 | 227:13015 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,026 | 0.0046065 | 0.00044897 | N
24/12/2016 | 23:50 | ZN2310:PA60 | URBAN | Other | Other - Self Clearing Trigger | 28 | 135 | 0.0026047 | 0.0019294 | N
25/12/2016 | 00:01 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 719 | 0.0096842 | 0.0013469 | N
25/12/2016 | 06:06 | ZN9550:PA9 | URBAN | Other | Other - Self Clearing Trigger | 34 | 144 | 0.0033679 | 0.0023429 | N
25/12/2016 | 06:38 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 362 | 0.0032505 | 0.00089794 | N
25/12/2016 | 07:49 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 176 | 0.062605 | 0.035625 | N
26/12/2016 | 16:40 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 106 | 0.00047404 | 0.00044897 | N
26/12/2016 | 19:20 | ZN1287:PA4 | URBAN | Other | Other - Arcing | 1 | 245 | 0.00016871 | 6.8909e-05 | N
26/12/2016 | 21:09 | ZN10990:PA11 | URBAN | Other | Other - Arcing | 1 | 281 | 0.00019392 | 6.8909e-05 | N
27/12/2016 | 08:15 | ZN12600:PA9 | SHORT RURAL | Other | Other | 1 | 84 | 0.00037878 | 0.00044897 | N
27/12/2016 | 09:32 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 98 | 0.00043991 | 0.00044897 | N
27/12/2016 | 09:34 | ZN12600:PA3 | URBAN | Other | Other | 1 | 41 | 2.8241e-05 | 6.8909e-05 | N
27/12/2016 | 10:06 | ZN4545:PA41 | SHORT RURAL | Other | Other | 1 | 73 | 0.00032849 | 0.00044897 | N
27/12/2016 | 16:49 | 812:19071 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 81 | 0.00036366 | 0.00044897 | N
28/12/2016 | 08:30 | 224:80340 | SHORT RURAL | Other | Other | 1 | 65 | 0.00029303 | 0.00044897 | N
24/12/2016 | 16:44 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 177 | 11 | 0.0087415 | 0.079468 | N
28/12/2016 | 12:23 | ZN7481:PA17 | URBAN | Other | Other - Self Clearing Trigger | 66 | 131 | 0.0059594 | 0.004548 | N
28/12/2016 | 13:13 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 47 | 0.0012661 | 0.0026938 | N
29/12/2016 | 06:10 | ZN36200:PA11 | SHORT RURAL | Other | Other | 1 | 75 | 0.00033456 | 0.00044897 | N
28/12/2016 | 12:00 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.00040407 | 0.00044897 | N
29/12/2016 | 08:59 | 256:80638 | URBAN | Other | Other | 1 | 36 | 2.4739e-05 | 6.891e-05 | N
29/12/2016 | 12:28 | 526:34639 | SHORT RURAL | Other | Other | 1 | 89 | 0.00040161 | 0.00044897 | N
29/12/2016 | 19:26 | ZN262:PA39 | URBAN | Other | Other - Arcing | 1 | 213 | 0.00014679 | 6.891e-05 | N
30/12/2016 | 05:40 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 95 | 148 | 0.062935 | 0.042653 | N
30/12/2016 | 11:00 | ZN5868:PA30 | URBAN | Other | Other | 1 | 168 | 0.00011576 | 6.891e-05 | N
30/12/2016 | 17:04 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 46 | 0.016388 | 0.035625 | N
30/12/2016 | 17:53 | 258:80785 | URBAN | Other | Other | 1 | 152 | 0.00010453 | 6.891e-05 | N
30/12/2016 | 22:52 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 52 | 0.00023355 | 0.00044898 | N
30/12/2016 | 23:35 | ZN9700:PA23 | URBAN | Other | Other - Arcing | 1 | 205 | 0.00014101 | 6.891e-05 | N
30/12/2016 | 23:55 | ZN9118:PA26 | URBAN | Other | Other - Arcing | 1 | 245 | 0.00016878 | 6.891e-05 | N
31/12/2016 | 08:02 | ZN15002:PA8 | URBAN | Other | Other | 1 | 122 | 8.4003e-05 | 6.8911e-05 | N
31/12/2016 | 14:44 | ZN15004:PA9 | URBAN | Other | Other - Arcing | 1 | 417 | 0.00028762 | 6.8911e-05 | N
31/12/2016 | 11:34 | ZN15002:PA6 | URBAN | Other | Other - Arcing | 1 | 260 | 0.00017913 | 6.8911e-05 | N
01/01/2017 | 04:54 | ZN129:PA24 | URBAN | Other | Other - Self Clearing Trigger | 1,573 | 83 | 0.08997 | 0.1084 | N
01/01/2017 | 04:54 | ZN129:PA28 | URBAN | Other | Other - Self Clearing Trigger | 386 | 83 | 0.022078 | 0.0266 | N
01/01/2017 | 04:54 | ZN129:PA9 | URBAN | Other | Other - Self Clearing Trigger | 1 | 83 | 5.7196e-05 | 6.8911e-05 | N
01/01/2017 | 05:31 | ZN129:PA28 | URBAN | Other | Other - Self Clearing Trigger | 1 | 49 | 3.4054e-05 | 6.8911e-05 | N
01/01/2017 | 08:17 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 88 | 0.0015804 | 0.0017959 | N
01/01/2017 | 09:09 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 96 | 0.00043102 | 0.00044898 | N
01/01/2017 | 09:18 | ZN12610:PA10 | URBAN | Other | Other - Arcing | 1 | 183 | 0.00012635 | 6.8911e-05 | N
01/01/2017 | 15:50 | ZN12610:PA18 | URBAN | Other | Other - Arcing | 1 | 265 | 0.00018251 | 6.8911e-05 | N
01/01/2017 | 16:03 | ZN12610:PA10 | URBAN | Other | Other | 1 | 41 | 2.8541e-05 | 6.8911e-05 | N
01/01/2017 | 16:22 | 225:33670 | URBAN | Other | Other | 1 | 63 | 4.3288e-05 | 6.8911e-05 | N
01/01/2017 | 17:24 | ZN35600:PA19 | URBAN | Other | Other - Arcing | 1 | 212 | 0.00014637 | 6.8911e-05 | N
01/01/2017 | 19:13 | ZN2310:PA54 | URBAN | Other | Other - Arcing | 1 | 293 | 0.00020207 | 6.8911e-05 | N
01/01/2017 | 19:23 | ZN35600:PA25 | URBAN | Other | Other - Arcing | 1 | 425 | 0.00029309 | 6.8911e-05 | N
01/01/2017 | 19:50 | 222:33602 | URBAN | Other | Other | 1 | 85 | 5.8322e-05 | 6.8911e-05 | N
01/01/2017 | 20:04 | 213:33771 | URBAN | Other | Other - Arcing | 1 | 181 | 0.00012503 | 6.8911e-05 | N
01/01/2017 | 20:14 | ZN36100:PA15 | URBAN | Other | Other - Arcing | 1 | 151 | 0.00010429 | 6.8911e-05 | N
01/01/2017 | 20:31 | ZN15006:PA2 | URBAN | Other | Other - Arcing | 1 | 68 | 4.6802e-05 | 6.8911e-05 | N
01/01/2017 | 20:44 | ZN15001:PA18 | URBAN | Other | Other - Arcing | 1 | 190 | 0.00013063 | 6.8911e-05 | N
01/01/2017 | 20:53 | ZN15008:PA9 | URBAN | Other | Other - Arcing | 1 | 379 | 0.000261 | 6.8911e-05 | N
01/01/2017 | 20:57 | ZN36100:PA27 | URBAN | Other | Other - Arcing | 1 | 108 | 7.4378e-05 | 6.8911e-05 | N
01/01/2017 | 21:03 | ZN36100:PA8 | URBAN | Other | Other - Arcing | 1 | 344 | 0.00023692 | 6.8911e-05 | N
01/01/2017 | 21:08 | ZN187:PA14 | URBAN | Other | Other - Arcing | 1 | 347 | 0.000239 | 6.8911e-05 | N
01/01/2017 | 21:17 | ZN398:PA4 | URBAN | Other | Other - Arcing | 1 | 382 | 0.0002634 | 6.8911e-05 | N
01/01/2017 | 21:20 | ZN931:PA31 | URBAN | Other | Other - Arcing | 1 | 193 | 0.00013326 | 6.8911e-05 | N
01/01/2017 | 21:23 | ZN9118:PA22 | URBAN | Other | Other - Arcing | 1 | 216 | 0.00014887 | 6.8911e-05 | N
01/01/2017 | 21:28 | ZN72:PA23 | URBAN | Other | Other - Arcing | 1 | 159 | 0.00010949 | 6.8911e-05 | N
01/01/2017 | 21:30 | ZN9534:PA17 | URBAN | Other | Other - Arcing | 1 | 180 | 0.00012379 | 6.8911e-05 | N
01/01/2017 | 21:34 | 222:33600 | URBAN | Other | Other - Arcing | 1 | 206 | 0.0001417 | 6.8911e-05 | N
01/01/2017 | 21:57 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 4 | 73 | 0.10403 | 0.1425 | N
01/01/2017 | 21:58 | ZN9534:PA17 | URBAN | Other | Other - Arcing | 1 | 152 | 0.00010458 | 6.8911e-05 | N
01/01/2017 | 22:09 | ZN931:PA31 | URBAN | Other | Other - Arcing | 1 | 308 | 0.00021195 | 6.8911e-05 | N
01/01/2017 | 23:16 | 256:80644 | URBAN | Other | Other - Arcing | 1 | 84 | 5.8172e-05 | 6.8911e-05 | N
01/01/2017 | 23:49 | ZN2835:PA29 | URBAN | Other | Other - Arcing | 1 | 207 | 0.00014262 | 6.8911e-05 | N
02/01/2017 | 00:42 | ZN9118:PA22 | URBAN | Other | Other - Arcing | 1 | 18 | 1.2105e-05 | 6.8911e-05 | N
02/01/2017 | 01:23 | 221:11895 | URBAN | Other | Other - Arcing | 1 | 77 | 5.2786e-05 | 6.8911e-05 | N
02/01/2017 | 06:24 | ZN35600:PA16 | URBAN | Other | Other - Arcing | 1 | 882 | 0.00060806 | 6.8911e-05 | N
02/01/2017 | 06:56 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 49 | 0.0011 | 0.0022449 | N
02/01/2017 | 08:09 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 120 | 0.00053997 | 0.00044898 | N
02/01/2017 | 08:50 | ZN116:PA73 | URBAN | Other | Other | 1 | 58 | 4.0152e-05 | 6.8911e-05 | N
02/01/2017 | 09:02 | 511:29873 | URBAN | Other | Other | 1 | 93 | 6.4076e-05 | 6.8911e-05 | N
02/01/2017 | 10:33 | 220:8691 | URBAN | Other | Other | 1 | 41 | 2.838e-05 | 6.8911e-05 | N
02/01/2017 | 10:56 | ZN12580:PA16 | URBAN | Other | Other - Arcing | 1 | 405 | 0.00027931 | 6.8911e-05 | N
02/01/2017 | 11:46 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 111 | 0.039645 | 0.035625 | N
02/01/2017 | 11:57 | ZN15002:PA6 | URBAN | Other | Other | 1 | 81 | 5.5761e-05 | 6.8911e-05 | N
02/01/2017 | 12:20 | ZN7900:PA2 | URBAN | Other | Other - Arcing | 1 | 689 | 0.00047488 | 6.8911e-05 | N
02/01/2017 | 15:19 | 507:80932 | SHORT RURAL | Other | Other | 1 | 89 | 0.00039982 | 0.00044898 | N
02/01/2017 | 15:39 | ZN12650:PA6 | URBAN | Other | Other | 1 | 67 | 4.5987e-05 | 6.8911e-05 | N
02/01/2017 | 18:27 | ZN15006:PA8 | URBAN | Other | Other - Arcing | 1 | 189 | 0.00013053 | 6.8911e-05 | N
02/01/2017 | 19:47 | ZN3425:PA15 | URBAN | Other | Other - Arcing | 1 | 1,002 | 0.00069065 | 6.8911e-05 | N
02/01/2017 | 21:19 | ZN9245:PA21 | URBAN | Other | Other - Arcing | 1 | 414 | 0.00028544 | 6.8911e-05 | N
02/01/2017 | 21:30 | ZN690:PA35 | URBAN | Other | Other - Arcing | 1 | 150 | 0.00010329 | 6.8911e-05 | N
02/01/2017 | 21:34 | ZN10990:PA1 | URBAN | Other | Other - Arcing | 1 | 185 | 0.0001275 | 6.8911e-05 | N
02/01/2017 | 23:34 | ZN188:PA44 | URBAN | Other | Other - Arcing | 1 | 1,315 | 0.00090632 | 6.8911e-05 | N
03/01/2017 | 01:59 | ZN36300:PA3 | URBAN | Other | Other - Arcing | 1 | 480 | 0.00033101 | 6.8911e-05 | N
03/01/2017 | 02:10 | ZN35600:PA1 | URBAN | Other | Other - Arcing | 1 | 199 | 0.00013719 | 6.8911e-05 | N
03/01/2017 | 02:27 | ZN188:PA44 | URBAN | Other | Other - Arcing | 1 | 1,142 | 0.00078721 | 6.8911e-05 | N
03/01/2017 | 02:33 | ZN10997:PA8 | URBAN | Other | Other - Arcing | 1 | 566 | 0.00039009 | 6.8911e-05 | N
03/01/2017 | 02:39 | ZN5868:PA30 | URBAN | Other | Other - Arcing | 1 | 380 | 0.00026213 | 6.8911e-05 | N
03/01/2017 | 02:49 | ZN15010:PA5 | URBAN | Other | Other - Arcing | 1 | 640 | 0.00044116 | 6.8911e-05 | N
03/01/2017 | 03:02 | ZN342:PA23 | URBAN | Other | Other - Arcing | 1 | 417 | 0.00028766 | 6.8911e-05 | N
03/01/2017 | 03:24 | ZN36100:PA19 | URBAN | Other | Other - Arcing | 9 | 516 | 0.0032002 | 0.0006202 | N
03/01/2017 | 04:43 | ZN1788:PA1 | URBAN | Other | Other - Arcing | 1 | 257 | 0.00017695 | 6.8911e-05 | N
03/01/2017 | 05:25 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 80 | 0.00071837 | 0.00089796 | N
03/01/2017 | 06:41 | ZN35600:PA4 | URBAN | Other | Other - Arcing | 1 | 258 | 0.00017788 | 6.8911e-05 | N
03/01/2017 | 07:15 | ZN3672:PA36 | URBAN | Other | Other - Arcing | 1 | 434 | 0.0002993 | 6.8911e-05 | N
03/01/2017 | 07:39 | ZN3155:PA20 | URBAN | Other | Other - Arcing | 1 | 410 | 0.00028283 | 6.8911e-05 | N
03/01/2017 | 07:58 | 513:48050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 197 | 0.00088225 | 0.00044898 | N
03/01/2017 | 08:44 | ZN3155:PA12 | URBAN | Other | Other - Self Clearing Trigger | 35 | 170 | 0.0041002 | 0.0024119 | N
02/01/2017 | 10:53 | 227:13020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 149 | 0.00066898 | 0.00044898 | N
03/01/2017 | 10:13 | ZN4545:PA32 | URBAN | Other | Other - Arcing | 1 | 293 | 0.00020199 | 6.8911e-05 | N
03/01/2017 | 13:01 | ZN188:PA44 | URBAN | Other | Other - Arcing | 1 | 509 | 0.00035047 | 6.8911e-05 | N
03/01/2017 | 14:03 | ZN9118:PA22 | URBAN | Other | Other - Arcing | 1 | 278 | 0.00019139 | 6.8911e-05 | N
03/01/2017 | 15:19 | ZN9700:PA24 | URBAN | Other | Other - Arcing | 1 | 161 | 0.00011088 | 6.8911e-05 | N
03/01/2017 | 19:12 | ZN2602:PA28 | URBAN | Other | Other - Arcing | 1 | 227 | 0.00015672 | 6.8911e-05 | N
03/01/2017 | 21:39 | ZN80:PA25 | URBAN | Other | Other - Arcing | 1 | 200 | 0.00013812 | 6.8911e-05 | N
03/01/2017 | 22:08 | ZN12650:PA17 | URBAN | Other | Other - Arcing | 1 | 832 | 0.00057313 | 6.8911e-05 | N
03/01/2017 | 22:18 | ZN9700:PA24 | URBAN | Other | Other - Arcing | 1 | 702 | 0.00048348 | 6.8911e-05 | N
03/01/2017 | 23:01 | ZN3672:PA9 | URBAN | Other | Other - Arcing | 1 | 118 | 8.1602e-05 | 6.8911e-05 | N
04/01/2017 | 02:29 | ZN12570:PA22 | SHORT RURAL | Other | Other - Arcing | 1 | 690 | 0.0031002 | 0.00044898 | N
04/01/2017 | 06:25 | ZN14144:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 334 | 0.0015015 | 0.00044898 | N
04/01/2017 | 07:10 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 185 | 0.00083055 | 0.00044898 | N
04/01/2017 | 07:25 | ZN180:PA24 | URBAN | Other | Other - Arcing | 1 | 95 | 6.5306e-05 | 6.8912e-05 | N
04/01/2017 | 09:18 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 117 | 0.0015759 | 0.001347 | N
04/01/2017 | 14:46 | ZN35370:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 98 | 137 | 0.060215 | 0.044 | N
04/01/2017 | 16:13 | 210:8676 | URBAN | Other | Other | 1 | 56 | 3.8637e-05 | 6.8912e-05 | N
04/01/2017 | 19:01 | 235:2124 | SHORT RURAL | Other | Other | 1 | 58 | 0.00026078 | 0.00044898 | N
04/01/2017 | 21:21 | ZN9118:PA22 | URBAN | Other | Other - Arcing | 1 | 819 | 0.00056427 | 6.8912e-05 | N
04/01/2017 | 21:49 | ZN9700:PA11 | URBAN | Other | Other - Arcing | 1 | 970 | 0.00066873 | 6.8912e-05 | N
04/01/2017 | 21:57 | ZN9118:PA17 | URBAN | Other | Other - Arcing | 1 | 362 | 0.00024973 | 6.8912e-05 | N
04/01/2017 | 22:44 | ZN3425:PA12 | URBAN | Other | Other - Arcing | 1 | 675 | 0.00046521 | 6.8912e-05 | N
05/01/2017 | 03:13 | ZN36200:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 646 | 0.0029022 | 0.00044899 | N
05/01/2017 | 08:27 | ZN180:PA43 | URBAN | Other | Other - Arcing | 1 | 273 | 0.00018798 | 6.8913e-05 | N
05/01/2017 | 09:04 | ZN690:PA12 | URBAN | Other | Other - Arcing | 1 | 326 | 0.00022466 | 6.8913e-05 | N
05/01/2017 | 09:04 | ZN12610:PA11 | URBAN | Other | Other - Arcing | 1 | 235 | 0.00016221 | 6.8913e-05 | N
05/01/2017 | 09:08 | ZN690:PA12 | URBAN | Other | Other - Arcing | 1 | 322 | 0.00022189 | 6.8913e-05 | N
05/01/2017 | 09:27 | ZN10994:PA12 | URBAN | Other | Other - Arcing | 1 | 63 | 4.3163e-05 | 6.8913e-05 | N
05/01/2017 | 09:46 | ZN15004:PA5 | URBAN | Other | Other - Arcing | 1 | 1,290 | 0.00088871 | 6.8913e-05 | N
05/01/2017 | 10:13 | ZN9035:PA2 | URBAN | Other | Other - Arcing | 1 | 305 | 0.00021051 | 6.8913e-05 | N
05/01/2017 | 10:49 | 240:34849 | SHORT RURAL | Other | Other - Arcing | 1 | 190 | 0.00085338 | 0.00044899 | N
05/01/2017 | 11:29 | ZN10997:PA1 | URBAN | Other | Other - Arcing | 1 | 121 | 8.3132e-05 | 6.8913e-05 | N
05/01/2017 | 12:16 | ZN195:PA30 | SHORT RURAL | Other | Other | 1 | 75 | 0.00033532 | 0.00044899 | N
05/01/2017 | 12:55 | ZN1068:PA22 | URBAN | Other | Other - Arcing | 1 | 458 | 0.00031562 | 6.8913e-05 | N
05/01/2017 | 16:36 | ZN10999:PA22 | URBAN | Other | Other - Arcing | 1 | 237 | 0.00016331 | 6.8913e-05 | N
05/01/2017 | 21:29 | ZN10997:PA2 | URBAN | Other | Other | 1 | 71 | 4.894e-05 | 6.8913e-05 | N
05/01/2017 | 21:49 | ZN15002:PA4 | URBAN | Other | Other - Arcing | 1 | 771 | 0.00053115 | 6.8913e-05 | N
05/01/2017 | 23:26 | ZN36100:PA2 | URBAN | Other | Other - Arcing | 1 | 664 | 0.00045725 | 6.8913e-05 | N
06/01/2017 | 07:14 | 807:74183 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 116 | 0.0036458 | 0.003143 | N
06/01/2017 | 08:18 | ZN10994:PA7 | URBAN | Other | Other - Arcing | 2 | 162 | 0.00022295 | 0.00013783 | N
06/01/2017 | 10:07 | 813:89063 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 103 | 0.00092493 | 0.00089799 | N
06/01/2017 | 10:17 | ZN12610:PA11 | URBAN | Other | Other - Arcing | 1 | 162 | 0.00011193 | 6.8915e-05 | N
06/01/2017 | 10:27 | 258:80785 | URBAN | Other | Other | 1 | 63 | 4.3347e-05 | 6.8915e-05 | N
06/01/2017 | 13:06 | 504:48031 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 159 | 0.0007139 | 0.000449 | N
06/01/2017 | 13:43 | 228:7487 | URBAN | Other | Other | 1 | 66 | 4.5507e-05 | 6.8915e-05 | N
06/01/2017 | 13:54 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 410 | 49 | 0.090069 | 0.18409 | N
07/01/2017 | 08:53 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 102 | 0.00091557 | 0.00089761 | N
07/01/2017 | 09:44 | ZN9550:PA6 | URBAN | Other | Other - Arcing | 1 | 331 | 0.00022827 | 6.8893e-05 | N
07/01/2017 | 10:46 | ZN2602:PA28 | URBAN | Other | Other - Arcing | 1 | 449 | 0.00030903 | 6.8893e-05 | N
07/01/2017 | 15:00 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 135 | 0.096188 | 0.07125 | N
08/01/2017 | 23:03 | ZN36800:PA49 | URBAN | Other | Other - Self Clearing Trigger | 73 | 44 | 0.0022329 | 0.0050292 | N
09/01/2017 | 08:11 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 6 | 289 | 0.61774 | 0.21375 | N
09/01/2017 | 08:23 | ZN35900:PA3 | URBAN | Other | Other - Arcing | 1 | 126 | 8.6908e-05 | 6.8892e-05 | N
09/01/2017 | 12:49 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 96 | 0.1026 | 0.10688 | N
09/01/2017 | 16:07 | 507:80922 | SHORT RURAL | Other | Other | 1 | 92 | 0.00041507 | 0.00044881 | N
09/01/2017 | 16:30 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 46 | 0.016388 | 0.035625 | N
10/01/2017 | 08:29 | 512:48048 | SHORT RURAL | Other | Other | 1 | 66 | 0.00029427 | 0.00044881 | N
10/01/2017 | 14:50 | 511:29877 | SHORT RURAL | Other | Other - Self Clearing Trigger | 145 | 152 | 0.098622 | 0.065078 | N
10/01/2017 | 17:24 | ZN9035:PA4 | URBAN | Other | Other - Self Clearing Trigger | 39 | 86 | 0.0022999 | 0.0026868 | N
10/01/2017 | 17:47 | 504:48027 | URBAN | Other | Other - Self Clearing Trigger | 15 | 236 | 0.0024388 | 0.0010334 | N
10/01/2017 | 22:34 | ZN12570:PA22 | SHORT RURAL | Other | Other - Arcing | 1 | 685 | 0.0030753 | 0.00044881 | N
11/01/2017 | 02:24 | ZN3155:PA19 | URBAN | Other | Other - Self Clearing Trigger | 78 | 279 | 0.014993 | 0.0053737 | N
11/01/2017 | 07:06 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 144 | 0.0006463 | 0.00044882 | N
11/01/2017 | 09:05 | ZN2635:PA57 | URBAN | Other | Other - Self Clearing Trigger | 40 | 98 | 0.0027066 | 0.0027558 | N
11/01/2017 | 10:03 | ZN36300:PA19 | URBAN | Other | Other - Self Clearing Trigger | 12 | 123 | 0.0010169 | 0.00082673 | N
11/01/2017 | 10:26 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 199 | 0.21268 | 0.10688 | N
11/01/2017 | 15:09 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 91 | 0.00081685 | 0.00089764 | N
11/01/2017 | 15:23 | 225:13446 | URBAN | Other | Other - Self Clearing Trigger | 116 | 77 | 0.0061536 | 0.0079917 | N
11/01/2017 | 16:24 | 507:80931 | URBAN | Other | Other | 1 | 130 | 8.9597e-05 | 6.8894e-05 | N
11/01/2017 | 17:16 | 258:80779 | URBAN | Other | Other - Self Clearing Trigger | 77 | 44 | 0.0023341 | 0.0053048 | N
11/01/2017 | 17:31 | ZN4545:PA44 | URBAN | Other | Other - Self Clearing Trigger | 42 | 219 | 0.0063354 | 0.0028935 | N
11/01/2017 | 17:52 | ZN14892:PA6 | SHORT RURAL | Other | Other - Self Clearing Trigger | 40 | 182 | 0.032674 | 0.017953 | N
11/01/2017 | 22:11 | 258:80779 | URBAN | Other | Other - Self Clearing Trigger | 77 | 97 | 0.0051457 | 0.0053048 | N
12/01/2017 | 03:57 | ZN3155:PA19 | URBAN | Other | Other - Self Clearing Trigger | 78 | 68 | 0.0036536 | 0.005373 | N
12/01/2017 | 04:13 | ZN15001:PA6 | URBAN | Other | Other - Arcing | 1 | 78 | 5.3764e-05 | 6.8884e-05 | N
12/01/2017 | 06:32 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 208 | 0.1482 | 0.07125 | N
12/01/2017 | 07:44 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 121 | 0.086213 | 0.07125 | N
12/01/2017 | 18:55 | ZN15014:PA5 | URBAN | Other | Other - Self Clearing Trigger | 6 | 125 | 0.00051663 | 0.00041331 | N
13/01/2017 | 05:14 | ZN965:PA21 | URBAN | Other | Other - Self Clearing Trigger | 32 | 510 | 0.011244 | 0.0022043 | N
13/01/2017 | 08:07 | ZN965:PA21 | URBAN | Other | Other - Self Clearing Trigger | 22 | 228 | 0.0034553 | 0.0015155 | N
13/01/2017 | 09:46 | ZN15013:PA10 | SHORT RURAL | Other | Other | 1 | 406 | 0.0018208 | 0.00044886 | N
13/01/2017 | 12:38 | ZN15014:PA14 | SHORT RURAL | Other | Other - Self Clearing Trigger | 325 | 48 | 0.070022 | 0.14588 | N
13/01/2017 | 16:00 | 504:48033 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 144 | 0.0077769 | 0.0053863 | N
13/01/2017 | 16:41 | 504:48026 | SHORT RURAL | Other | Other - Self Clearing Trigger | 32 | 169 | 0.024202 | 0.014363 | N
13/01/2017 | 16:52 | 512:48048 | SHORT RURAL | Other | Other - Self Clearing Trigger | 45 | 43 | 0.0085878 | 0.020199 | N
13/01/2017 | 17:38 | 528:83011 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 272 | 0.0048836 | 0.0017954 | N
13/01/2017 | 18:18 | 239:82136 | SHORT RURAL | Other | Other - Self Clearing Trigger | 60 | 97 | 0.026123 | 0.026931 | N
13/01/2017 | 18:42 | 225:33676 | URBAN | Other | Other - Self Clearing Trigger | 70 | 108 | 0.0052078 | 0.004822 | N
13/01/2017 | 18:56 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 109 | 0.0014678 | 0.0013466 | N
13/01/2017 | 19:00 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 100 | 0.0049374 | 0.0049374 | N
13/01/2017 | 19:19 | 203:8084 | URBAN | Other | Other - Self Clearing Trigger | 238 | 141 | 0.023117 | 0.016395 | N
13/01/2017 | 19:35 | 258:80779 | URBAN | Other | Other - Self Clearing Trigger | 77 | 24 | 0.0012898 | 0.0053042 | N
13/01/2017 | 19:53 | 224:80332 | URBAN | Other | Other - Self Clearing Trigger | 67 | 64 | 0.0029538 | 0.0046153 | N
13/01/2017 | 20:49 | 507:80917 | URBAN | Other | Other - Self Clearing Trigger | 94 | 40 | 0.002616 | 0.0064753 | N
13/01/2017 | 20:26 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 769 | 0.02071 | 0.0026931 | N
13/01/2017 | 21:50 | 508:82576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 110 | 0.0039499 | 0.0035909 | N
13/01/2017 | 22:44 | 507:80917 | URBAN | Other | Other - Self Clearing Trigger | 80 | 136 | 0.0074948 | 0.0055109 | N
14/01/2017 | 08:58 | ZN14892:PA17 | URBAN | Other | Other | 1 | 91 | 6.2583e-05 | 6.8886e-05 | N
14/01/2017 | 14:36 | ZN14891:PA12 | SHORT RURAL | Other | Other - Self Clearing Trigger | 39 | 124 | 0.021752 | 0.017506 | N
14/01/2017 | 17:01 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 149 | 0.0026752 | 0.0017954 | N
14/01/2017 | 17:25 | 257:81994 | URBAN | Other | Other - Arcing | 84 | 187 | 0.0108 | 0.0057864 | N
14/01/2017 | 22:44 | ZN3155:PA19 | URBAN | Other | Other - Arcing | 63 | 60 | 0.0026198 | 0.0043398 | N
15/01/2017 | 00:02 | 523:33501 | SHORT RURAL | Other | Other - Arcing | 1 | 110 | 0.00049329 | 0.00044885 | N
15/01/2017 | 02:54 | ZN12600:PA11 | URBAN | Other | Other - Self Clearing Trigger | 29 | 126 | 0.0025171 | 0.0019977 | N
15/01/2017 | 07:18 | 238:34141 | SHORT RURAL | Other | Other - Arcing | 1 | 192 | 0.0008597 | 0.00044885 | N
15/01/2017 | 07:38 | ZN931:PA11 | URBAN | Other | Other - Self Clearing Trigger | 141 | 51 | 0.0049698 | 0.0097129 | N
15/01/2017 | 09:44 | ZN129:PA5 | URBAN | Other | Other - Self Clearing Trigger | 40 | 81 | 0.0022195 | 0.0027554 | N
16/01/2017 | 01:06 | ZN36300:PA11 | URBAN | Other | Other - Self Clearing Trigger | 2,960 | 158 | 0.32217 | 0.2039 | N
16/01/2017 | 01:06 | ZN36300:PA19 | URBAN | Other | Other - Self Clearing Trigger | 287 | 158 | 0.031237 | 0.01977 | N
13/01/2017 | 15:23 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 125 | 0.00056107 | 0.00044886 | N
16/01/2017 | 09:30 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 70 | 0.0003142 | 0.00044885 | N
16/01/2017 | 10:04 | ZN187:PA17 | URBAN | Other | Other - Self Clearing Trigger | 21 | 8 | 0.00011583 | 0.0014466 | N
16/01/2017 | 10:04 | ZN187:PA19 | URBAN | Other | Other - Self Clearing Trigger | 80 | 3 | 0.00015751 | 0.0055109 | N
16/01/2017 | 10:04 | ZN187:PA6 | URBAN | Other | Other - Self Clearing Trigger | 182 | 39 | 0.0048923 | 0.012537 | N
16/01/2017 | 10:04 | ZN35400:PA53 | SHORT RURAL | Other | Other - Self Clearing Trigger | 153 | 29 | 0.019916 | 0.068674 | N
16/01/2017 | 12:21 | ZN1648:PA19 | URBAN | Other | Other - Arcing | 1 | 99 | 6.7956e-05 | 6.8886e-05 | N
16/01/2017 | 13:56 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 153 | 0.00068674 | 0.00044885 | N
16/01/2017 | 17:23 | 256:80646 | URBAN | Other | Other | 1 | 67 | 4.5855e-05 | 6.8886e-05 | N
16/01/2017 | 22:05 | ZN2400:PA23 | URBAN | Other | Other - Arcing | 1 | 835 | 0.00057506 | 6.8886e-05 | N
17/01/2017 | 01:28 | ZN12690:PA19 | URBAN | Other | Other - Self Clearing Trigger | 1,215 | 72 | 0.060037 | 0.083697 | N
17/01/2017 | 05:15 | 524:33580 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 130 | 0.0017505 | 0.0013466 | N
17/01/2017 | 09:36 | ZN12610:PA20 | SHORT RURAL | Other | Other | 1 | 82 | 0.00036731 | 0.00044885 | N
17/01/2017 | 12:29 | ZN630:PA41 | URBAN | Other | Other - Self Clearing Trigger | 6 | 76 | 0.00031412 | 0.00041332 | N
17/01/2017 | 16:12 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 138 | 0.098326 | 0.07125 | N
17/01/2017 | 16:53 | ZN35800:PA7 | URBAN | Other | Other - Self Clearing Trigger | 68 | 116 | 0.0054392 | 0.0046843 | N
17/01/2017 | 18:01 | ZN72:PA35 | URBAN | Other | Other - Arcing | 58 | 278 | 0.011123 | 0.0039954 | N
17/01/2017 | 19:20 | 258:80779 | URBAN | Other | Other - Self Clearing Trigger | 89 | 50 | 0.0030654 | 0.0061309 | N
17/01/2017 | 19:23 | 507:80917 | URBAN | Other | Other - Self Clearing Trigger | 94 | 102 | 0.0065822 | 0.0064753 | N
17/01/2017 | 21:19 | 243:80083 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 101 | 0.00045334 | 0.00044885 | N
18/01/2017 | 06:02 | 239:82127 | SHORT RURAL | Other | Other | 1 | 54 | 0.00024268 | 0.00044885 | N
18/01/2017 | 07:54 | 256:80632 | URBAN | Other | Other | 1 | 134 | 9.2182e-05 | 6.8887e-05 | N
18/01/2017 | 11:42 | ZN1285:PA20 | URBAN | Other | Other - Arcing | 1 | 943 | 0.00064978 | 6.8887e-05 | N
18/01/2017 | 12:35 | 240:34835 | SHORT RURAL | Other | Other | 1 | 175 | 0.0007843 | 0.00044885 | N
18/01/2017 | 12:38 | ZN35500:PA27 | URBAN | Other | Other - Self Clearing Trigger | 68 | 61 | 0.0028699 | 0.0046843 | N
18/01/2017 | 12:40 | ZN14891:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 269 | 0.0012083 | 0.00044885 | N
18/01/2017 | 13:13 | 240:34835 | SHORT RURAL | Other | Other | 1 | 167 | 0.00074891 | 0.00044885 | N
18/01/2017 | 16:43 | ZN2835:PA32 | URBAN | Other | Other - Self Clearing Trigger | 58 | 67 | 0.002657 | 0.0039954 | N
18/01/2017 | 17:08 | 233:82819 | SHORT RURAL | Other | Other | 1 | 262 | 0.0011746 | 0.00044885 | N
18/01/2017 | 18:05 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 7 | 250 | 0.62344 | 0.24938 | N
18/01/2017 | 18:09 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 92 | 291 | 9.5376 | 3.2775 | N
18/01/2017 | 18:12 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 308 | 0.02761 | 0.0089771 | N
18/01/2017 | 19:33 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 307 | 0.0013772 | 0.00044885 | N
18/01/2017 | 20:13 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 182 | 0.0016338 | 0.00089771 | N
18/01/2017 | 22:58 | ZN195:PA28 | URBAN | Other | Other - Arcing | 1 | 841 | 0.00057948 | 6.8887e-05 | N
18/01/2017 | 23:33 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 497 | 0.17706 | 0.035625 | N
19/01/2017 | 00:31 | ZN3472:PA12 | URBAN | Other | Other - Arcing | 1 | 173 | 0.00011931 | 6.8881e-05 | N
19/01/2017 | 01:27 | ZN12650:PA20 | URBAN | Other | Other - Arcing | 1 | 603 | 0.0004151 | 6.8881e-05 | N
19/01/2017 | 02:20 | 508:82575 | SHORT RURAL | Other | Other - Arcing | 1 | 579 | 0.0025988 | 0.00044882 | N
19/01/2017 | 02:23 | 508:82575 | SHORT RURAL | Other | Other | 1 | 56 | 0.00024955 | 0.00044882 | N
19/01/2017 | 07:01 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 1 | 148 | 0.00010225 | 6.8881e-05 | N
19/01/2017 | 07:46 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 351 | 0.0015764 | 0.00044882 | N
19/01/2017 | 08:03 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 332 | 0.0089406 | 0.0026929 | N
19/01/2017 | 08:42 | 206:34441 | URBAN | Other | Other | 1 | 104 | 7.1855e-05 | 6.8881e-05 | N
19/01/2017 | 09:52 | ZN1673:PA6 | URBAN | Other | Other | 1 | 148 | 0.00010171 | 6.8881e-05 | N
19/01/2017 | 10:03 | ZN195:PA3 | URBAN | Other | Other - Arcing | 1 | 296 | 0.000204 | 6.8881e-05 | N
19/01/2017 | 10:34 | 213:33771 | URBAN | Other | Other - Arcing | 1 | 191 | 0.00013143 | 6.8881e-05 | N
19/01/2017 | 10:36 | ZN1673:PA6 | URBAN | Other | Other | 1 | 105 | 7.2084e-05 | 6.8881e-05 | N
19/01/2017 | 10:51 | ZN180:PA7 | URBAN | Other | Other | 1 | 137 | 9.454e-05 | 6.8881e-05 | N
19/01/2017 | 11:10 | 257:81987 | URBAN | Other | Other - Arcing | 1 | 199 | 0.00013741 | 6.8881e-05 | N
19/01/2017 | 11:19 | ZN3288:PA41 42KLM | CBD | Other | Other - Self Clearing Trigger | 28 | 100 | 0.090201 | 0.090096 | N
19/01/2017 | 11:30 | ZN14891:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 270 | 0.00121 | 0.00044882 | N
19/01/2017 | 11:40 | ZN180:PA7 | URBAN | Other | Other | 1 | 88 | 6.0535e-05 | 6.8881e-05 | N
19/01/2017 | 11:44 | ZN36200:PA11 | SHORT RURAL | Other | Other | 1 | 93 | 0.00041763 | 0.00044882 | N
19/01/2017 | 11:59 | ZN2196:PA5 | URBAN | Other | Other - Arcing | 1 | 120 | 8.2945e-05 | 6.8881e-05 | N
19/01/2017 | 18:42 | ZN180:PA24 | URBAN | Other | Other - Arcing | 1 | 157 | 0.00010832 | 6.8881e-05 | N
19/01/2017 | 19:50 | ZN1673:PA9 | URBAN | Other | Other | 1 | 55 | 3.7758e-05 | 6.8881e-05 | N
19/01/2017 | 21:55 | ZN965:PA20 | URBAN | Other | Other - Self Clearing Trigger | 56 | 160 | 0.0061621 | 0.0038574 | N
19/01/2017 | 21:55 | ZN965:PA3 | URBAN | Other | Other - Self Clearing Trigger | 28 | 160 | 0.0030859 | 0.0019287 | N
19/01/2017 | 23:40 | 502:48010 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 485 | 0.0065304 | 0.0013465 | N
20/01/2017 | 00:17 | ZN4545:PA27 | URBAN | Other | Other - Arcing | 1 | 931 | 0.00064111 | 6.8882e-05 | N
20/01/2017 | 00:17 | ZN4545:PA40 | URBAN | Other | Other - Arcing | 1 | 931 | 0.00064129 | 6.8882e-05 | N
20/01/2017 | 05:59 | ZN8100:PA30 | URBAN | Other | Other - Arcing | 1 | 750 | 0.00051665 | 6.8882e-05 | N
20/01/2017 | 06:21 | ZN15008:PA9 | URBAN | Other | Other - Arcing | 1 | 399 | 0.00027451 | 6.8882e-05 | N
20/01/2017 | 06:58 | ZN3425:PA24 | URBAN | Other | Other - Arcing | 1 | 172 | 0.00011826 | 6.8882e-05 | N
20/01/2017 | 08:12 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 48 | 0.00043086 | 0.00089763 | N
20/01/2017 | 09:42 | 220:8689 | URBAN | Other | Other - Self Clearing Trigger | 14 | 168 | 0.0016201 | 0.00096435 | N
20/01/2017 | 11:19 | 516:48066 | SHORT RURAL | Other | Other - Arcing | 1 | 185 | 0.00082919 | 0.00044881 | N
20/01/2017 | 11:41 | ZN874:PA22 | URBAN | Other | Other - Arcing | 1 | 318 | 0.00021936 | 6.8882e-05 | N
20/01/2017 | 11:43 | ZN35500:PA19 | SHORT RURAL | Other | Other - Arcing | 1 | 476 | 0.0021382 | 0.00044881 | N
20/01/2017 | 11:44 | ZN72:PA15 | URBAN | Other | Other | 1 | 244 | 0.00016791 | 6.8882e-05 | N
20/01/2017 | 11:47 | ZN2196:PA21 | URBAN | Other | Other - Arcing | 1 | 103 | 7.0845e-05 | 6.8882e-05 | N
20/01/2017 | 11:47 | ZN2196:PA21 | URBAN | Other | Other - Arcing | 1 | 102 | 7.0375e-05 | 6.8882e-05 | N
20/01/2017 | 11:51 | ZN72:PA15 | URBAN | Other | Other - Arcing | 1 | 429 | 0.00029521 | 6.8882e-05 | N
20/01/2017 | 11:53 | ZN36800:PA46 | URBAN | Other | Other - Arcing | 1 | 186 | 0.00012814 | 6.8882e-05 | N
20/01/2017 | 11:54 | 238:34150 | SHORT RURAL | Other | Other - Arcing | 1 | 167 | 0.00075004 | 0.00044881 | N
20/01/2017 | 12:37 | ZN12650:PA6 | URBAN | Other | Other - Arcing | 1 | 82 | 5.6782e-05 | 6.8882e-05 | N
20/01/2017 | 12:42 | ZN10991:PA12 | URBAN | Other | Other - Arcing | 1 | 617 | 0.00042519 | 6.8882e-05 | N
20/01/2017 | 13:15 | ZN12610:PA6 | URBAN | Other | Other - Arcing | 1 | 560 | 0.00038558 | 6.8882e-05 | N
20/01/2017 | 13:15 | ZN12650:PA6 | URBAN | Other | Other - Arcing | 1 | 89 | 6.1604e-05 | 6.8882e-05 | N
20/01/2017 | 13:32 | ZN15006:PA8 | URBAN | Other | Other - Arcing | 1 | 507 | 0.00034928 | 6.8882e-05 | N
20/01/2017 | 13:34 | ZN35500:PA22 | URBAN | Other | Other - Arcing | 1 | 195 | 0.00013447 | 6.8882e-05 | N
20/01/2017 | 13:40 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 60 | 0.0032315 | 0.0053858 | N
20/01/2017 | 13:42 | ZN12690:PA16 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 228 | 0.0020466 | 0.00089763 | N
20/01/2017 | 14:09 | 526:34640 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 471 | 0.0042278 | 0.00089763 | N
20/01/2017 | 14:11 | ZN167:PA21 | URBAN | Other | Other - Arcing | 1 | 198 | 0.00013644 | 6.8882e-05 | N
20/01/2017 | 15:16 | 213:33775 | URBAN | Other | Other - Self Clearing Trigger | 61 | 94 | 0.0039497 | 0.0042018 | N
20/01/2017 | 15:25 | ZN15010:PA11 | URBAN | Other | Other - Arcing | 1 | 210 | 0.00014487 | 6.8882e-05 | N
20/01/2017 | 15:27 | ZN167:PA21 | URBAN | Other | Other - Arcing | 1 | 122 | 8.4105e-05 | 6.8882e-05 | N
20/01/2017 | 17:21 | ZN12610:PA16 | SHORT RURAL | Other | Other - Arcing | 1 | 444 | 0.0019921 | 0.00044881 | N
20/01/2017 | 17:28 | 238:34150 | SHORT RURAL | Other | Other - Arcing | 1 | 121 | 0.00054441 | 0.00044881 | N
20/01/2017 | 18:17 | ZN72:PA15 | URBAN | Other | Other - Arcing | 1 | 1,115 | 0.00076814 | 6.8882e-05 | N
20/01/2017 | 18:45 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 125 | 0.13364 | 0.10691 | N
20/01/2017 | 19:05 | 528:83019 | SHORT RURAL | Other | Other | 1 | 107 | 0.00048173 | 0.00044881 | N
20/01/2017 | 20:38 | ZN15004:PA1 | URBAN | Other | Other - Arcing | 1 | 1,351 | 0.00093069 | 6.8882e-05 | N
20/01/2017 | 20:43 | ZN12650:PA17 | URBAN | Other | Other - Arcing | 1 | 316 | 0.0002179 | 6.8882e-05 | N
20/01/2017 | 21:20 | ZN12650:PA12 | URBAN | Other | Other - Arcing | 1 | 309 | 0.0002129 | 6.8882e-05 | N
20/01/2017 | 22:32 | ZN15006:PA16 | URBAN | Other | Other - Arcing | 1 | 1,078 | 0.00074276 | 6.8882e-05 | N
21/01/2017 | 00:12 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 463 | 0.006234 | 0.0013464 | N
21/01/2017 | 06:17 | ZN3425:PA39 | URBAN | Other | Other - Arcing | 1 | 522 | 0.00035961 | 6.8883e-05 | N
21/01/2017 | 09:33 | ZN14144:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 396 | 0.0017769 | 0.00044881 | N
21/01/2017 | 17:57 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 48 | 0.00064629 | 0.0013464 | N
21/01/2017 | 19:25 | 513:48056 | SHORT RURAL | Other | Other - Arcing | 1 | 107 | 0.00048046 | 0.00044881 | N
22/01/2017 | 11:04 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 106 | 0.001903 | 0.0017953 | N
23/01/2017 | 06:32 | ZN1850:PA8 | URBAN | Other | Other - Arcing | 1 | 147 | 0.0001013 | 6.8882e-05 | N
23/01/2017 | 10:13 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 22 | 92 | 0.71935 | 0.78403 | N
23/01/2017 | 20:37 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 93 | 0.00041744 | 0.00044886 | N
23/01/2017 | 22:56 | 526:34640 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 124 | 0.0016697 | 0.0013466 | N
24/01/2017 | 09:28 | ZN3155:PA19 | URBAN | Other | Other - Arcing | 1 | 272 | 0.0001872 | 6.8884e-05 | N
24/01/2017 | 10:51 | 513:48051 | URBAN | Other | Other - Arcing | 51 | 55 | 0.0019462 | 0.0035131 | N
24/01/2017 | 12:00 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 69 | 0.00030994 | 0.00044887 | N
24/01/2017 | 12:37 | 512:48049 | SHORT RURAL | Other | Other | 1 | 82 | 0.00036762 | 0.00044887 | N
24/01/2017 | 14:00 | ZN2310:PA70 | URBAN | Other | Other - Self Clearing Trigger | 37 | 60 | 0.0015292 | 0.0025487 | N
24/01/2017 | 14:39 | 217:33612 | URBAN | Other | Other | 1 | 39 | 2.6681e-05 | 6.8884e-05 | N
24/01/2017 | 17:57 | ZN1648:PA16 | URBAN | Other | Other - Arcing | 1 | 272 | 0.00018731 | 6.8884e-05 | N
24/01/2017 | 18:02 | ZN12610:PA22 | URBAN | Other | Other - Arcing | 1 | 1,093 | 0.00075289 | 6.8884e-05 | N
24/01/2017 | 18:21 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 1 | 175 | 0.00012081 | 6.8884e-05 | N
24/01/2017 | 19:14 | 528:83020 | SHORT RURAL | Other | Other - Arcing | 1 | 226 | 0.0010162 | 0.00044887 | N
25/01/2017 | 06:55 | ZN12570:PA35 | URBAN | Other | Other - Arcing | 1 | 215 | 0.00014795 | 6.8885e-05 | N
25/01/2017 | 06:58 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 132 | 0.00059254 | 0.00044889 | N
25/01/2017 | 07:44 | ZN12640:PA16 | URBAN | Other | Other | 1 | 77 | 5.2995e-05 | 6.8885e-05 | N
25/01/2017 | 09:02 | 235:2123 | URBAN | Other | Other | 1 | 9 | 6.3833e-06 | 6.8885e-05 | N
25/01/2017 | 09:31 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 29 | 0.01027 | 0.035638 | N
25/01/2017 | 09:54 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 170 | 0.00076342 | 0.00044889 | N
25/01/2017 | 10:14 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 141 | 0.00063294 | 0.00044889 | N
25/01/2017 | 12:30 | ZN12610:PA2 | URBAN | Other | Other | 1 | 177 | 0.0001217 | 6.8885e-05 | N
25/01/2017 | 14:22 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 423 | 0.0018988 | 0.00044889 | N
25/01/2017 | 16:19 | ZN10999:PA7 | URBAN | Other | Other - Arcing | 1 | 251 | 0.00017258 | 6.8885e-05 | N
26/01/2017 | 20:54 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 121 | 0.002712 | 0.0022413 | N
25/01/2017 | 23:31 | ZN262:PA39 | URBAN | Other | Other - Arcing | 1 | 748 | 0.00051557 | 6.8885e-05 | N
26/01/2017 | 08:57 | ZN12620:PA3 | URBAN | Other | Other | 1 | 174 | 0.00011979 | 6.888e-05 | N
26/01/2017 | 11:39 | 264:81232 | URBAN | Other | Other - Self Clearing Trigger | 800 | 76 | 0.041728 | 0.055104 | N
26/01/2017 | 12:24 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 66 | 0.00059172 | 0.00089654 | N
27/01/2017 | 11:20 | ZN12610:PA24 | URBAN | Other | Other | 1 | 179 | 0.00012349 | 6.8874e-05 | N
27/01/2017 | 12:24 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 38 | 102 | 0.017355 | 0.017034 | N
27/01/2017 | 14:52 | ZN80:PA40 | URBAN | Other | Other | 1 | 67 | 4.6284e-05 | 6.8874e-05 | N
27/01/2017 | 15:09 | 239:82127 | SHORT RURAL | Other | Other | 1 | 73 | 0.0003267 | 0.00044826 | N
27/01/2017 | 15:39 | ZN12630:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 238 | 156 | 0.16618 | 0.10668 | N
27/01/2017 | 20:25 | ZN12580:PA1 | URBAN | Other | Other - Arcing | 1 | 729 | 0.00050235 | 6.8874e-05 | N
28/01/2017 | 02:00 | ZN12650:PA16 | URBAN | Other | Other - Arcing | 1 | 599 | 0.0004126 | 6.8875e-05 | N
28/01/2017 | 09:17 | ZN1285:PA10 | URBAN | Other | Other - Self Clearing Trigger | 22 | 57 | 0.00086773 | 0.0015153 | N
28/01/2017 | 05:59 | 202:34254 | URBAN | Other | Other - Arcing | 92 | 197 | 0.012454 | 0.0063365 | N
28/01/2017 | 16:31 | ZN10999:PA29 | URBAN | Other | Other - Self Clearing Trigger | 37 | 58 | 0.0014789 | 0.0025484 | N
28/01/2017 | 17:41 | ZN3472:PA22 | URBAN | Other | Other - Arcing | 1 | 244 | 0.00016771 | 6.8875e-05 | N
29/01/2017 | 11:06 | 256:80647 | URBAN | Other | Other - Arcing | 1 | 194 | 0.00013328 | 6.8875e-05 | N
29/01/2017 | 15:42 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 18 | 292 | 1.8744 | 0.64148 | N
29/01/2017 | 16:11 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 37 | 73 | 0.96478 | 1.3186 | N
29/01/2017 | 16:58 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 202 | 0.21597 | 0.10691 | N
29/01/2017 | 17:03 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 228 | 188 | 0.19214 | 0.1022 | N
29/01/2017 | 17:03 | 806:82667 | SHORT RURAL | Other | Other - Self Clearing Trigger | 40 | 188 | 0.033709 | 0.01793 | N
29/01/2017 | 17:03 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 254 | 115 | 0.13094 | 0.11386 | N
29/01/2017 | 17:25 | 216:10727 | SHORT RURAL | Other | Other | 1 | 49 | 0.00022136 | 0.00044826 | N
29/01/2017 | 17:55 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 37 | 118 | 1.5575 | 1.3186 | N
29/01/2017 | 18:55 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 295 | 0.0026447 | 0.00089652 | N
29/01/2017 | 19:04 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 286 | 0.02564 | 0.0089652 | N
29/01/2017 | 19:24 | 813:89063 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 236 | 0.019042 | 0.0080686 | N
29/01/2017 | 19:55 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 140 | 0.099786 | 0.071276 | N
30/01/2017 | 06:29 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 146 | 0.00065311 | 0.00044826 | N
30/01/2017 | 06:52 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 132 | 0.047167 | 0.035638 | N
30/01/2017 | 07:48 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 157 | 0.014075 | 0.0089652 | N
29/01/2017 | 01:15 | 202:34254 | URBAN | Other | Other - Self Clearing Trigger | 8 | 32 | 0.00017632 | 0.000551 | N
30/01/2017 | 08:31 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 99 | 0.035282 | 0.035638 | N
30/01/2017 | 09:10 | ZN13000:PA5 | SHORT RURAL | Other | Other | 1 | 65 | 0.00029137 | 0.00044826 | N
30/01/2017 | 09:12 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 98 | 0.0017572 | 0.001793 | N
30/01/2017 | 09:53 | 242:81535 | URBAN | Other | Other | 1 | 76 | 5.2598e-05 | 6.8875e-05 | N
30/01/2017 | 09:55 | 512:48046 | SHORT RURAL | Other | Other - Self Clearing Trigger | 63 | 74 | 0.020907 | 0.02824 | N
30/01/2017 | 13:10 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 100 | 0.0031378 | 0.0031378 | N
30/01/2017 | 14:13 | ZN35800:PA7 | URBAN | Other | Other - Self Clearing Trigger | 1,157 | 102 | 0.081254 | 0.079688 | N
30/01/2017 | 15:03 | ZN9035:PA11 | URBAN | Other | Other | 1 | 182 | 0.00012557 | 6.8875e-05 | N
30/01/2017 | 15:15 | ZN15006:PA6 | URBAN | Other | Other - Arcing | 1 | 297 | 0.00020428 | 6.8875e-05 | N
30/01/2017 | 15:36 | 511:29876 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 54 | 0.0021785 | 0.0040343 | N
30/01/2017 | 16:23 | 261:81864 | URBAN | Other | Other | 1 | 86 | 5.8911e-05 | 6.8875e-05 | N
30/01/2017 | 17:26 | ZN35800:PA7 | URBAN | Other | Other - Self Clearing Trigger | 1,157 | 118 | 0.094036 | 0.079688 | N
30/01/2017 | 18:41 | 214:8666 | URBAN | Other | Other - Self Clearing Trigger | 64 | 58 | 0.002561 | 0.004408 | N
30/01/2017 | 19:06 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 74 | 0.0016586 | 0.0022413 | N
30/01/2017 | 19:15 | ZN965:PA33 | URBAN | Other | Other - Self Clearing Trigger | 62 | 135 | 0.0057648 | 0.0042703 | N
30/01/2017 | 23:16 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 64 | 684 | 15.6009 | 2.2808 | N
31/01/2017 | 07:23 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 122 | 0.00054546 | 0.00044826 | N
31/01/2017 | 07:30 | 264:81241 | SHORT RURAL | Other | Other | 1 | 239 | 0.0010732 | 0.00044826 | N
31/01/2017 | 08:13 | ZN1673:PA21 | SHORT RURAL | Other | Other - Arcing | 1 | 16 | 7.217e-05 | 0.00044826 | N
30/01/2017 | 11:51 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 49 | 5 | 0.0010982 | 0.021965 | N
30/01/2017 | 09:12 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 93 | 0.0012506 | 0.0013448 | N
31/01/2017 | 10:44 | 528:83014 | SHORT RURAL | Other | Other | 1 | 96 | 0.00043033 | 0.00044826 | N
31/01/2017 | 13:03 | 813:89065 | URBAN | Other | Other | 1 | 107 | 7.3353e-05 | 6.8876e-05 | N
31/01/2017 | 13:33 | 801:74123 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 77 | 0.00034516 | 0.00044826 | N
31/01/2017 | 14:21 | 238:34144 | URBAN | Other | Other - Arcing | 1 | 243 | 0.00016727 | 6.8876e-05 | N
31/01/2017 | 15:45 | ZN80:PA22 | URBAN | Other | Other - Self Clearing Trigger | 33 | 119 | 0.0027101 | 0.0022729 | N
01/02/2017 | 09:44 | ZN15004:PA3 | URBAN | Other | Other - Arcing | 1 | 136 | 9.3419e-05 | 6.8877e-05 | N
31/01/2017 | 18:03 | ZN4545:PA21 | URBAN | Other | Other | 1 | 335 | 0.00023101 | 6.8876e-05 | N
31/01/2017 | 18:16 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 69 | 0.0037116 | 0.0053791 | N
31/01/2017 | 19:03 | ZN1673:PA19 | URBAN | Other | Other - Arcing | 1 | 267 | 0.00018372 | 6.8876e-05 | N
31/01/2017 | 22:09 | ZN14143:PA5 | URBAN | Other | Other - Self Clearing Trigger | 1,023 | 127 | 0.089477 | 0.07046 | N
31/01/2017 | 23:39 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 1 | 21 | 1.412e-05 | 6.8876e-05 | N
01/02/2017 | 02:07 | ZN15004:PA3 | URBAN | Other | Other - Arcing | 1 | 288 | 0.00019855 | 6.8877e-05 | N
01/02/2017 | 02:58 | ZN15009:PA7 | URBAN | Other | Other - Self Clearing Trigger | 48 | 307 | 0.01015 | 0.0033061 | N
01/02/2017 | 04:07 | ZN3425:PA12 | URBAN | Other | Other - Arcing | 1 | 493 | 0.00033934 | 6.8877e-05 | N
01/02/2017 | 05:16 | ZN4545:PA31 | URBAN | Other | Other - Arcing | 1 | 403 | 0.00027772 | 6.8877e-05 | N
01/02/2017 | 05:47 | ZN15014:PA22 | URBAN | Other | Other - Arcing | 1 | 312 | 0.00021514 | 6.8877e-05 | N
01/02/2017 | 05:49 | ZN35800:PA21 | URBAN | Other | Other - Arcing | 1 | 411 | 0.00028277 | 6.8877e-05 | N
01/02/2017 | 05:53 | ZN12660:PA14 | SHORT RURAL | Other | Other - Arcing | 1 | 126 | 0.00056519 | 0.00044827 | N
01/02/2017 | 07:12 | ZN15014:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 707 | 0.0031711 | 0.00044827 | N
01/02/2017 | 09:02 | ZN15014:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 292 | 0.0013095 | 0.00044827 | N
01/02/2017 | 07:15 | ZN15013:PA4 | URBAN | Other | Other | 1 | 420 | 0.00028924 | 6.8877e-05 | N
01/02/2017 | 07:32 | ZN36100:PA5 | URBAN | Other | Other - Arcing | 1 | 208 | 0.000143 | 6.8877e-05 | N
31/01/2017 | 07:00 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 80 | 0.00035861 | 0.00044826 | N
01/02/2017 | 09:08 | ZN12610:PA20 | SHORT RURAL | Other | Other - Arcing | 1 | 472 | 0.0021141 | 0.00044827 | N
01/02/2017 | 16:01 | ZN15002:PA2 | URBAN | Other | Other - Arcing | 1 | 337 | 0.00023223 | 6.8877e-05 | N
01/02/2017 | 11:09 | ZN2602:PA29 | URBAN | Other | Other - Arcing | 1 | 170 | 0.00011731 | 6.8877e-05 | N
01/02/2017 | 12:43 | 508:82578 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 77 | 0.00034517 | 0.00044827 | N
01/02/2017 | 16:04 | ZN15009:PA7 | URBAN | Other | Other - Arcing | 1 | 802 | 0.00055263 | 6.8877e-05 | N
01/02/2017 | 19:23 | ZN15013:PA4 | URBAN | Other | Other - Arcing | 1 | 217 | 0.00014931 | 6.8877e-05 | N
01/02/2017 | 19:50 | ZN3922:PA29 | URBAN | Other | Other - Arcing | 1 | 167 | 0.00011491 | 6.8877e-05 | N
01/02/2017 | 20:01 | ZN35800:PA1 | URBAN | Other | Other - Arcing | 1 | 155 | 0.0001068 | 6.8877e-05 | N
01/02/2017 | 20:20 | ZN15002:PA2 | URBAN | Other | Other - Arcing | 1 | 547 | 0.00037678 | 6.8877e-05 | N
01/02/2017 | 20:04 | ZN4545:PA21 | URBAN | Other | Other - Arcing | 1 | 176 | 0.0001209 | 6.8877e-05 | N
01/02/2017 | 21:32 | ZN15014:PA19 | URBAN | Other | Other - Arcing | 1 | 475 | 0.00032685 | 6.8877e-05 | N
01/02/2017 | 21:54 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 44 | 57 | 0.89986 | 1.5681 | N
01/02/2017 | 23:04 | ZN3425:PA44 | URBAN | Other | Other - Arcing | 1 | 79 | 5.4286e-05 | 6.8877e-05 | N
01/02/2017 | 23:20 | ZN965:PA21 | URBAN | Other | Other - Arcing | 1 | 670 | 0.00046115 | 6.8877e-05 | N
01/02/2017 | 23:23 | ZN3472:PA33 | URBAN | Other | Other - Arcing | 1 | 200 | 0.00013758 | 6.8877e-05 | N
01/02/2017 | 23:33 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 1 | 237 | 0.00016324 | 6.8877e-05 | N
02/02/2017 | 00:08 | ZN10994:PA4 | URBAN | Other | Other - Arcing | 1 | 232 | 0.00015963 | 6.8866e-05 | N
02/02/2017 | 00:25 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 1 | 184 | 0.00012672 | 6.8866e-05 | N
02/02/2017 | 00:26 | ZN965:PA3 | URBAN | Other | Other - Arcing | 1 | 693 | 0.00047725 | 6.8866e-05 | N
02/02/2017 | 03:20 | ZN965:PA15 | URBAN | Other | Other - Arcing | 1 | 685 | 0.00047146 | 6.8866e-05 | N
02/02/2017 | 07:31 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 169 | 0.0030298 | 0.0017928 | N
02/02/2017 | 07:53 | ZN14891:PA16 | SHORT RURAL | Other | Other | 1 | 71 | 0.00031717 | 0.00044819 | N
01/02/2017 | 10:00 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 150 | 0.053457 | 0.035638 | N
02/02/2017 | 09:32 | 243:80081 | SHORT RURAL | Other | Other | 1 | 89 | 0.00039732 | 0.00044819 | N
02/02/2017 | 22:30 | ZN1287:PA22 | URBAN | Other | Other - Self Clearing Trigger | 951 | 57 | 0.03733 | 0.065491 | N
03/02/2017 | 06:38 | 205:12213 | SHORT RURAL | Other | Other | 1 | 112 | 0.00050026 | 0.0004482 | N
03/02/2017 | 10:56 | ZN3154:PA18 | URBAN | Other | Other - Self Clearing Trigger | 19 | 79 | 0.0010337 | 0.0013085 | N
03/02/2017 | 12:36 | 532:83293 | URBAN | Other | Other | 1 | 63 | 4.3099e-05 | 6.8867e-05 | N
03/02/2017 | 15:18 | ZN15011:PA2 | URBAN | Other | Other | 1 | 76 | 5.2087e-05 | 6.8867e-05 | N
03/02/2017 | 17:13 | ZN3154:PA18 | URBAN | Other | Other | 1 | 68 | 4.7059e-05 | 6.8867e-05 | N
03/02/2017 | 17:26 | ZN35500:PA27 | URBAN | Other | Other - Arcing | 1 | 169 | 0.00011627 | 6.8867e-05 | N
04/02/2017 | 07:58 | ZN12640:PA16 | URBAN | Other | Other - Arcing | 1 | 301 | 0.00020746 | 6.8869e-05 | N
04/02/2017 | 08:05 | ZN12640:PA2 | URBAN | Other | Other | 1 | 56 | 3.8429e-05 | 6.8869e-05 | N
04/02/2017 | 09:00 | ZN14892:PA13 | URBAN | Other | Other - Arcing | 1 | 139 | 9.574e-05 | 6.8869e-05 | N
04/02/2017 | 10:49 | 524:33572 | SHORT RURAL | Other | Other | 1 | 111 | 0.00049742 | 0.0004482 | N
04/02/2017 | 11:32 | 202:34262 | URBAN | Other | Other - Self Clearing Trigger | 65 | 323 | 0.014459 | 0.0044765 | N
04/02/2017 | 13:22 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 73 | 0.0065392 | 0.0089639 | N
04/02/2017 | 14:29 | 224:80332 | URBAN | Other | Other - Self Clearing Trigger | 138 | 45 | 0.0042831 | 0.0095039 | N
04/02/2017 | 16:43 | 264:81232 | URBAN | Other | Other | 1 | 82 | 5.6622e-05 | 6.8869e-05 | N
04/02/2017 | 16:55 | 264:81232 | URBAN | Other | Other | 1 | 71 | 4.8633e-05 | 6.8869e-05 | N
04/02/2017 | 17:35 | ZN1287:PA3 | URBAN | Other | Other - Self Clearing Trigger | 67 | 59 | 0.0027247 | 0.0046142 | N
04/02/2017 | 17:43 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 617 | 0.0055308 | 0.00089639 | N
04/02/2017 | 18:13 | 502:48010 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 118 | 0.00052887 | 0.0004482 | N
04/02/2017 | 18:17 | 511:29876 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 238 | 0.0096004 | 0.0040338 | N
04/02/2017 | 18:23 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 5 | 627 | 1.1165 | 0.17806 | N
04/02/2017 | 18:45 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 5 | 1,040 | 1.8519 | 0.17806 | N
04/02/2017 | 18:51 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 394 | 0.0017637 | 0.0004482 | N
04/02/2017 | 19:08 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 4 | 532 | 0.75783 | 0.14245 | N
04/02/2017 | 19:25 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 94 | 0.00042272 | 0.0004482 | N
04/02/2017 | 19:33 | 264:81240 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 312 | 0.0083871 | 0.0026892 | N
04/02/2017 | 19:34 | 507:80925 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 156 | 0.00069747 | 0.0004482 | N
04/02/2017 | 19:41 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 39 | 0.00052439 | 0.0013446 | N
04/02/2017 | 19:42 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 363 | 0.019523 | 0.0053784 | N
04/02/2017 | 18:51 | 233:82812 | SHORT RURAL | Other | Other - Self Clearing Trigger | 16 | 379 | 0.027179 | 0.0071712 | N
04/02/2017 | 20:40 | 224:80346 | URBAN | Other | Other - Self Clearing Trigger | 53 | 175 | 0.0063876 | 0.0036501 | N
04/02/2017 | 20:44 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 10 | 1,076 | 3.8319 | 0.35613 | N
04/02/2017 | 21:20 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 915 | 0.016404 | 0.0017928 | N
04/02/2017 | 21:57 | 238:34148 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 661 | 0.0059252 | 0.00089639 | N
04/02/2017 | 23:24 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 741 | 0.0066423 | 0.00089639 | N
05/02/2017 | 07:00 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 615 | 0.43803 | 0.071225 | N
05/02/2017 | 09:02 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 4 | 118 | 0.16809 | 0.14245 | N
05/02/2017 | 09:06 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 379 | 0.0016983 | 0.00044811 | N
05/02/2017 | 09:13 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 427 | 0.0019134 | 0.00044811 | N
05/02/2017 | 09:19 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 286 | 0.0012816 | 0.00044811 | N
05/02/2017 | 09:51 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 166 | 0.0022316 | 0.0013443 | N
05/02/2017 | 11:18 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 207 | 0.00092625 | 0.00044811 | N
05/02/2017 | 12:22 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 158 | 0.056268 | 0.035613 | N
05/02/2017 | 12:22 | 532:83309 | SHORT RURAL | Other | Other - Self Clearing Trigger | 50 | 158 | 0.035315 | 0.022406 | N
05/02/2017 | 13:17 | 508:82580 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 123 | 0.0011024 | 0.00089623 | N
05/02/2017 | 16:12 | ZN15014:PA20 | URBAN | Other | Other | 1 | 141 | 9.7226e-05 | 6.8873e-05 | N
05/02/2017 | 09:30 | 504:48031 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 475 | 0.0021285 | 0.00044811 | N
05/02/2017 | 16:50 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 120 | 0.00053699 | 0.00044811 | N
05/02/2017 | 16:51 | ZN12610:PA10 | URBAN | Other | Other | 1 | 168 | 0.00011589 | 6.8873e-05 | N
05/02/2017 | 17:31 | ZN15005:PA8 | URBAN | Other | Other - Self Clearing Trigger | 39 | 111 | 0.0029813 | 0.0026861 | N
05/02/2017 | 17:37 | ZN80:PA25 | URBAN | Other | Other - Self Clearing Trigger | 62 | 53 | 0.0022447 | 0.0042702 | N
05/02/2017 | 18:48 | ZN1287:PA11 | URBAN | Other | Other - Self Clearing Trigger | 2 | 359 | 0.00049451 | 0.00013775 | N
05/02/2017 | 18:48 | ZN1287:PA4 | URBAN | Other | Other - Self Clearing Trigger | 90 | 371 | 0.023013 | 0.0061986 | N
05/02/2017 | 19:25 | ZN874:PA4 | URBAN | Other | Other - Self Clearing Trigger | 75 | 540 | 0.027892 | 0.0051655 | N
05/02/2017 | 19:27 | ZN4545:PA44 | URBAN | Other | Other - Self Clearing Trigger | 85 | 93 | 0.0054405 | 0.0058542 | N
05/02/2017 | 19:32 | ZN690:PA11 | URBAN | Other | Other - Self Clearing Trigger | 1 | 673 | 0.00046352 | 6.8873e-05 | N
05/02/2017 | 19:32 | ZN690:PA5 | URBAN | Other | Other - Self Clearing Trigger | 115 | 672 | 0.05324 | 0.0079204 | N
05/02/2017 | 19:39 | ZN3425:PA30 | URBAN | Other | Other - Self Clearing Trigger | 60 | 110 | 0.0045629 | 0.0041324 | N
05/02/2017 | 19:49 | 239:82129 | SHORT RURAL | Other | Other | 1 | 186 | 0.00083185 | 0.00044811 | N
05/02/2017 | 20:10 | 512:48046 | SHORT RURAL | Other | Other - Self Clearing Trigger | 60 | 100 | 0.026887 | 0.026887 | N
05/02/2017 | 20:37 | 504:48031 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 148 | 0.0026528 | 0.0017925 | N
05/02/2017 | 20:46 | ZN10994:PA7 | URBAN | Other | Other - Self Clearing Trigger | 51 | 659 | 0.023137 | 0.0035125 | N
05/02/2017 | 21:23 | ZN10991:PA1 | URBAN | Other | Other - Self Clearing Trigger | 81 | 177 | 0.0098642 | 0.0055788 | N
05/02/2017 | 21:44 | ZN35800:PA15 | URBAN | Other | Other - Self Clearing Trigger | 59 | 400 | 0.016264 | 0.0040635 | N
05/02/2017 | 22:19 | ZN15004:PA5 | URBAN | Other | Other - Arcing | 1 | 201 | 0.00013813 | 6.8873e-05 | N
06/02/2017 | 09:05 | 229:34986 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 114 | 0.0092141 | 0.008066 | N
06/02/2017 | 10:31 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 48 | 0.00021719 | 0.00044811 | N
06/02/2017 | 11:50 | ZN180:PA32 | URBAN | Other | Other - Self Clearing Trigger | 46 | 119 | 0.0037833 | 0.0031682 | N
06/02/2017 | 13:04 | ZN15002:PA4 | URBAN | Other | Other | 1 | 84 | 5.7842e-05 | 6.8873e-05 | N
04/02/2017 | 18:17 | 511:29876 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 283 | 0.0025368 | 0.00089639 | N
04/02/2017 | 19:14 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 236 | 0.0010577 | 0.0004482 | N
04/02/2017 | 19:14 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 121 | 0.0010846 | 0.00089639 | N
06/02/2017 | 14:51 | 528:83020 | SHORT RURAL | Other | Other | 1 | 187 | 0.00083745 | 0.00044811 | N
04/02/2017 | 19:20 | 526:34640 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 60 | 0.00080676 | 0.0013446 | N
06/02/2017 | 16:38 | ZN1068:PA16 | URBAN | Other | Other - Arcing | 1 | 268 | 0.00018474 | 6.8873e-05 | N
06/02/2017 | 18:18 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 161 | 0.057461 | 0.035613 | N
06/02/2017 | 20:36 | ZN12640:PA7 | URBAN | Other | Other - Arcing | 1 | 294 | 0.00020236 | 6.8873e-05 | N
06/02/2017 | 21:31 | ZN340:PA11 | URBAN | Other | Other - Self Clearing Trigger | 52 | 99 | 0.0035396 | 0.0035814 | N
06/02/2017 | 22:50 | ZN72:PA16 | URBAN | Other | Other - Arcing | 1 | 879 | 0.00060544 | 6.8873e-05 | N
07/02/2017 | 00:30 | ZN4545:PA31 | URBAN | Other | Other - Self Clearing Trigger | 2,989 | 102 | 0.21082 | 0.20587 | N
07/02/2017 | 02:46 | ZN3472:PA28 | URBAN | Other | Other - Arcing | 1 | 524 | 0.00036061 | 6.8875e-05 | N
07/02/2017 | 03:39 | ZN630:PA38 | URBAN | Other | Other - Arcing | 1 | 290 | 0.00019979 | 6.8875e-05 | N
07/02/2017 | 04:01 | ZN35500:PA31 | URBAN | Other | Other - Arcing | 1 | 298 | 0.00020555 | 6.8875e-05 | N
07/02/2017 | 04:44 | ZN12610:PA23 | URBAN | Other | Other - Self Clearing Trigger | 31 | 95 | 0.0020376 | 0.0021351 | N
07/02/2017 | 06:05 | ZN384:PA70 | URBAN | Other | Other - Arcing | 1 | 174 | 0.00011987 | 6.8875e-05 | N
07/02/2017 | 06:52 | ZN2568:PA32 | URBAN | Other | Other - Arcing | 1 | 158 | 0.00010852 | 6.8875e-05 | N
07/02/2017 | 07:08 | ZN72:PA31 | URBAN | Other | Other - Arcing | 1 | 277 | 0.00019049 | 6.8875e-05 | N
07/02/2017 | 07:12 | ZN630:PA38 | URBAN | Other | Other - Arcing | 1 | 287 | 0.00019791 | 6.8875e-05 | N
07/02/2017 | 07:17 | ZN262:PA5 | URBAN | Other | Other - Arcing | 1 | 203 | 0.00013949 | 6.8875e-05 | N
04/02/2017 | 23:24 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 741 | 0.0033211 | 0.0004482 | N
05/02/2017 | 00:45 | 233:82812 | SHORT RURAL | Other | Other - Self Clearing Trigger | 231 | 2 | 0.0020703 | 0.10351 | N
07/02/2017 | 08:36 | ZN12690:PA19 | URBAN | Other | Other | 1 | 50 | 3.4139e-05 | 6.8875e-05 | N
07/02/2017 | 08:57 | ZN2602:PA29 | URBAN | Other | Other - Arcing | 1 | 152 | 0.00010502 | 6.8875e-05 | N
05/02/2017 | 16:44 | 264:81232 | URBAN | Other | Other - Self Clearing Trigger | 8 | 60 | 0.00033059 | 0.00055099 | N
05/02/2017 | 18:30 | 511:29876 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 325 | 0.0029127 | 0.00089623 | N
07/02/2017 | 10:31 | ZN262:PA5 | URBAN | Other | Other - Arcing | 1 | 149 | 0.00010229 | 6.8875e-05 | N
07/02/2017 | 10:35 | ZN36800:PA46 | URBAN | Other | Other - Arcing | 33 | 594 | 0.013511 | 0.0022729 | N
07/02/2017 | 10:50 | ZN1285:PA17 | URBAN | Other | Other - Arcing | 1 | 190 | 0.00013072 | 6.8875e-05 | N
07/02/2017 | 11:10 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 60 | 0.00080661 | 0.0013443 | N
07/02/2017 | 11:33 | ZN35500:PA24 | URBAN | Other | Other - Self Clearing Trigger | 38 | 98 | 0.0025523 | 0.0026172 | N
07/02/2017 | 12:01 | ZN9118:PA20 | URBAN | Other | Other - Arcing | 1 | 419 | 0.00028825 | 6.8875e-05 | N
07/02/2017 | 11:54 | ZN9118:PA20 | URBAN | Other | Other - Arcing | 1 | 486 | 0.0003345 | 6.8875e-05 | N
07/02/2017 | 13:11 | ZN15002:PA8 | URBAN | Other | Other - Arcing | 1 | 1,395 | 0.00096074 | 6.8875e-05 | N
07/02/2017 | 12:22 | ZN10995:PA6 | URBAN | Other | Other - Arcing | 1 | 67 | 4.6295e-05 | 6.8875e-05 | N
07/02/2017 | 12:29 | ZN342:PA26 | URBAN | Other | Other | 1 | 199 | 0.00013708 | 6.8875e-05 | N
07/02/2017 | 14:44 | ZN180:PA23 | URBAN | Other | Other - Arcing | 34 | 11 | 0.00024705 | 0.0023417 | N
07/02/2017 | 15:02 | ZN965:PA4 | URBAN | Other | Other - Self Clearing Trigger | 68 | 118 | 0.0055265 | 0.0046835 | N
07/02/2017 | 15:44 | ZN15004:PA1 | URBAN | Other | Other - Arcing | 1 | 152 | 0.0001049 | 6.8875e-05 | N
07/02/2017 | 18:59 | ZN15004:PA5 | URBAN | Other | Other - Arcing | 1 | 273 | 0.00018771 | 6.8875e-05 | N
07/02/2017 | 18:10 | 513:48050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 70 | 0.00062736 | 0.00089623 | N
07/02/2017 | 18:59 | ZN14144:PA4 | URBAN | Other | Other | 1 | 42 | 2.8721e-05 | 6.8875e-05 | N
07/02/2017 | 20:38 | 256:80647 | URBAN | Other | Other | 1 | 45 | 3.1327e-05 | 6.8875e-05 | N
07/02/2017 | 20:42 | ZN262:PA7 | URBAN | Other | Other - Arcing | 1 | 1,039 | 0.0007154 | 6.8875e-05 | N
07/02/2017 | 22:47 | 801:74123 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 72 | 0.00032264 | 0.00044812 | N
08/02/2017 | 07:01 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 123 | 0.00055163 | 0.00044812 | N
08/02/2017 | 07:07 | 504:48033 | SHORT RURAL | Other | Other - Arcing | 1 | 262 | 0.0011748 | 0.00044812 | N
08/02/2017 | 08:18 | ZN1068:PA17 | URBAN | Other | Other - Arcing | 1 | 432 | 0.00029742 | 6.8876e-05 | N
08/02/2017 | 09:51 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 156 | 0.00070048 | 0.00044812 | N
08/02/2017 | 10:00 | 507:80922 | SHORT RURAL | Other | Other - Self Clearing Trigger | 103 | 76 | 0.035086 | 0.046156 | N
08/02/2017 | 15:03 | ZN15002:PA8 | URBAN | Other | Other - Arcing | 1 | 403 | 0.00027764 | 6.8876e-05 | N
08/02/2017 | 18:36 | ZN3155:PA29 | URBAN | Other | Other - Arcing | 1 | 204 | 0.00014019 | 6.8876e-05 | N
08/02/2017 | 19:16 | ZN9245:PA13 | URBAN | Other | Other - Arcing | 1 | 403 | 0.00027766 | 6.8876e-05 | N
08/02/2017 | 19:30 | ZN12610:PA13 | URBAN | Other | Other | 1 | 63 | 4.3552e-05 | 6.8876e-05 | N
08/02/2017 | 19:33 | ZN965:PA2 | URBAN | Other | Other - Arcing | 1 | 116 | 8.0137e-05 | 6.8876e-05 | N
08/02/2017 | 22:46 | 507:80917 | URBAN | Other | Other | 1 | 502 | 0.00034572 | 6.8876e-05 | N
09/02/2017 | 08:30 | ZN12620:PA7 | URBAN | Other | Other | 1 | 293 | 0.00020213 | 6.8876e-05 | N
09/02/2017 | 15:11 | ZN180:PA31 | URBAN | Other | Other | 1 | 199 | 0.00013687 | 6.8876e-05 | N
09/02/2017 | 15:39 | 235:8685 | URBAN | Other | Other | 1 | 1,031 | 0.0007101 | 6.8876e-05 | N
09/02/2017 | 20:57 | ZN35900:PA1 | URBAN | Other | Other - Arcing | 1 | 114 | 7.8323e-05 | 6.8876e-05 | N
09/02/2017 | 21:20 | ZN15006:PA13 | URBAN | Other | Other - Self Clearing Trigger | 1 | 93 | 6.3882e-05 | 6.8876e-05 | N
10/02/2017 | 00:39 | ZN35370:PA2 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 345 | 0.015453 | 0.0044747 | N
09/02/2017 | 08:12 | 511:29877 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 338 | 0.0090749 | 0.0026849 | N
04/02/2017 | 19:06 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 44 | 0.0015777 | 0.0035856 | N
10/02/2017 | 17:51 | ZN15011:PA10 | URBAN | Other | Other - Arcing | 53 | 264 | 0.0096235 | 0.0036508 | N
10/02/2017 | 18:14 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 96 | 0.034188 | 0.035613 | N
10/02/2017 | 18:43 | 513:48052 | URBAN | Other | Other - Arcing | 1 | 140 | 9.6585e-05 | 6.8883e-05 | N
10/02/2017 | 19:54 | 512:48046 | SHORT RURAL | Other | Other - Self Clearing Trigger | 60 | 106 | 0.028459 | 0.026848 | N
10/02/2017 | 21:13 | ZN965:PA33 | URBAN | Other | Other | 1 | 592 | 0.00040758 | 6.8883e-05 | N
11/02/2017 | 07:26 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 144 | 0.0025774 | 0.0017899 | N
11/02/2017 | 10:40 | 508:82580 | SHORT RURAL | Other | Other | 1 | 95 | 0.00042428 | 0.00044747 | N
11/02/2017 | 11:24 | 205:12210 | URBAN | Other | Other - Self Clearing Trigger | 114 | 40 | 0.0031699 | 0.0078527 | N
11/02/2017 | 13:45 | 217:33612 | URBAN | Other | Other - Self Clearing Trigger | 16 | 99 | 0.0010913 | 0.0011021 | N
11/02/2017 | 14:09 | 258:80775 | URBAN | Other | Other | 1 | 131 | 9.0076e-05 | 6.8883e-05 | N
11/02/2017 | 15:09 | 504:48028 | URBAN | Other | Other | 1 | 267 | 0.00018384 | 6.8883e-05 | N
11/02/2017 | 16:15 | 224:80341 | URBAN | Other | Other - Self Clearing Trigger | 75 | 60 | 0.0030842 | 0.0051662 | N
11/02/2017 | 16:28 | ZN129:PA8 | URBAN | Other | Other - Self Clearing Trigger | 53 | 62 | 0.0022507 | 0.0036508 | N
11/02/2017 | 16:41 | 507:80917 | URBAN | Other | Other - Self Clearing Trigger | 94 | 34 | 0.0021896 | 0.006475 | N
11/02/2017 | 17:13 | 233:82819 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 237 | 0.0084841 | 0.0035798 | N
11/02/2017 | 17:45 | ZN1285:PA27 | URBAN | Other | Other - Self Clearing Trigger | 61 | 215 | 0.0090277 | 0.0042019 | N
11/02/2017 | 18:42 | ZN13000:PA11 | SHORT RURAL | Other | Other | 1 | 94 | 0.0004201 | 0.00044747 | N
11/02/2017 | 18:44 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 194 | 95 | 0.082514 | 0.08681 | N
11/02/2017 | 19:01 | ZN965:PA38 | URBAN | Other | Other - Self Clearing Trigger | 48 | 168 | 0.0055685 | 0.0033064 | N
11/02/2017 | 19:30 | ZN35400:PA52 | URBAN | Other | Other | 1 | 1,078 | 0.00074226 | 6.8883e-05 | N
11/02/2017 | 19:35 | ZN10997:PA5 | URBAN | Other | Other - Self Clearing Trigger | 56 | 185 | 0.0071241 | 0.0038574 | N
11/02/2017 | 19:46 | 507:80917 | URBAN | Other | Other - Self Clearing Trigger | 174 | 64 | 0.0076269 | 0.011986 | N
11/02/2017 | 20:36 | ZN2400:PA21 | URBAN | Other | Other - Self Clearing Trigger | 51 | 134 | 0.004694 | 0.003513 | N
11/02/2017 | 20:54 | ZN180:PA34 | URBAN | Other | Other - Arcing | 1 | 413 | 0.00028456 | 6.8883e-05 | N
11/02/2017 | 21:15 | ZN847:PA21 | URBAN | Other | Other | 1 | 578 | 0.0003978 | 6.8883e-05 | N
11/02/2017 | 21:48 | ZN965:PA22 | URBAN | Other | Other - Self Clearing Trigger | 27 | 582 | 0.010824 | 0.0018598 | N
12/02/2017 | 10:12 | ZN15012:PA2 | URBAN | Other | Other - Arcing | 1 | 227 | 0.00015657 | 6.8883e-05 | N
12/02/2017 | 13:31 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 17 | 374 | 2.2617 | 0.60541 | N
12/02/2017 | 15:55 | ZN35370:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 279 | 128 | 0.15943 | 0.12485 | N
12/02/2017 | 17:23 | 224:80332 | URBAN | Other | Other | 1 | 31 | 2.1514e-05 | 6.8883e-05 | N
12/02/2017 | 21:18 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 992 | 0.0088779 | 0.00089495 | N
10/02/2017 | 09:50 | 524:33576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 58 | 0.00025953 | 0.00044747 | N
13/02/2017 | 08:11 | 228:7487 | URBAN | Other | Other | 1 | 119 | 8.1879e-05 | 6.8883e-05 | N
13/02/2017 | 09:31 | ZN847:PA2 | URBAN | Other | Other - Self Clearing Trigger | 41 | 178 | 0.0050407 | 0.0028242 | N
13/02/2017 | 10:09 | 524:33578 | URBAN | Other | Other - Self Clearing Trigger | 95 | 51 | 0.0033374 | 0.0065439 | N
13/02/2017 | 10:24 | ZN14892:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 1,625 | 0.007272 | 0.00044747 | N
13/02/2017 | 11:42 | ZN12570:PA33 | SHORT RURAL | Other | Other - Arcing | 1 | 62 | 0.00027937 | 0.00044747 | N
13/02/2017 | 11:57 | ZN965:PA24 | URBAN | Other | Other - Self Clearing Trigger | 32 | 92 | 0.0020371 | 0.0022043 | N
13/02/2017 | 12:28 | ZN10999:PA4 | URBAN | Other | Other | 1 | 77 | 5.2925e-05 | 6.8883e-05 | N
13/02/2017 | 18:09 | ZN129:PA27 | URBAN | Other | Other - Self Clearing Trigger | 206 | 76 | 0.010784 | 0.01419 | N
13/02/2017 | 18:45 | ZN72:PA26 | URBAN | Other | Other - Arcing | 1 | 396 | 0.00027266 | 6.8883e-05 | N
14/02/2017 | 07:24 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 56 | 0.00024993 | 0.00044631 | N
14/02/2017 | 07:35 | 239:82129 | SHORT RURAL | Other | Other | 1 | 115 | 0.0005131 | 0.00044631 | N
14/02/2017 | 07:38 | ZN847:PA1 | URBAN | Other | Other - Arcing | 527 | 50 | 0.018171 | 0.036342 | N
14/02/2017 | 09:35 | ZN9118:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 217 | 71 | 0.068762 | 0.096848 | N
14/02/2017 | 09:59 | ZN129:PA9 | URBAN | Other | Other - Self Clearing Trigger | 48 | 155 | 0.0051141 | 0.0033101 | N
14/02/2017 | 15:54 | 504:48026 | SHORT RURAL | Other | Other | 1 | 126 | 0.00056391 | 0.00044631 | N
14/02/2017 | 19:13 | ZN931:PA11 | URBAN | Other | Other - Self Clearing Trigger | 101 | 67 | 0.0046526 | 0.006965 | N
14/02/2017 | 20:23 | ZN12600:PA3 | URBAN | Other | Other - Arcing | 1 | 408 | 0.00028132 | 6.896e-05 | N
14/02/2017 | 23:27 | ZN12600:PA12 | URBAN | Other | Other - Self Clearing Trigger | 14 | 70 | 0.00067581 | 0.00096545 | N
14/02/2017 | 23:57 | ZN398:PA19 | URBAN | Other | Other - Arcing | 1 | 289 | 0.00019903 | 6.896e-05 | N
15/02/2017 | 08:40 | ZN15015:PA5 | URBAN | Other | Other - Arcing | 1 | 290 | 0.00019983 | 6.8905e-05 | N
15/02/2017 | 08:59 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 301 | 0.0013434 | 0.00044631 | N
16/02/2017 | 06:54 | 221:11897 | URBAN | Other | Other | 1 | 59 | 4.0587e-05 | 6.8888e-05 | N
16/02/2017 | 09:38 | ZN965:PA20 | URBAN | Other | Other - Arcing | 1 | 262 | 0.00018046 | 6.8888e-05 | N
12/02/2017 | 00:05 | ZN14891:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 77 | 5 | 0.0017228 | 0.034455 | N
16/02/2017 | 14:16 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 26 | 72 | 0.0083623 | 0.011612 | N
16/02/2017 | 14:25 | ZN35370:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 394 | 0.0017617 | 0.0004466 | N
16/02/2017 | 14:43 | 511:29877 | SHORT RURAL | Other | Other | 1 | 35 | 0.00015586 | 0.0004466 | N
16/02/2017 | 16:21 | ZN35370:PA8 | SHORT RURAL | Other | Other | 1 | 103 | 0.00045821 | 0.0004466 | N
16/02/2017 | 18:40 | ZN874:PA18 | URBAN | Other | Other - Self Clearing Trigger | 38 | 309 | 0.0080889 | 0.0026178 | N
16/02/2017 | 20:40 | 206:34441 | URBAN | Other | Other - Self Clearing Trigger | 1 | 39 | 2.7085e-05 | 6.8888e-05 | N
16/02/2017 | 21:29 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 31 | 0.01104 | 0.035613 | N
17/02/2017 | 05:31 | 217:33610 | URBAN | Other | Other - Self Clearing Trigger | 86 | 26 | 0.0015404 | 0.0059245 | Y
17/02/2017 | 08:33 | 507:80923 | SHORT RURAL | Other | Other | 1 | 108 | 0.000483 | 0.0004466 | Y
17/02/2017 | 09:15 | 232:11454 | SHORT RURAL | Other | Other | 1 | 188 | 0.00083759 | 0.0004466 | Y
17/02/2017 | 10:40 | 224:80326 | SHORT RURAL | Other | Other - Self Clearing Trigger | 24 | 40 | 0.0042873 | 0.010718 | Y
17/02/2017 | 10:49 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 146 | 0.051905 | 0.035613 | Y
17/02/2017 | 11:29 | ZN195:PA22 | URBAN | Other | Other - Arcing | 1 | 180 | 0.00012417 | 6.889e-05 | Y
17/02/2017 | 13:35 | 264:81240 | SHORT RURAL | Other | Other | 1 | 91 | 0.00040633 | 0.0004466 | Y
17/02/2017 | 13:44 | 258:80793 | URBAN | Other | Other - Self Clearing Trigger | 133 | 61 | 0.005589 | 0.0091624 | Y
17/02/2017 | 15:43 | 528:83019 | SHORT RURAL | Other | Other | 1 | 86 | 0.00038445 | 0.0004466 | Y
17/02/2017 | 15:45 | ZN35600:PA3 | URBAN | Other | Other - Arcing | 1 | 284 | 0.00019595 | 6.889e-05 | Y
17/02/2017 | 15:50 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 87 | 0.03103 | 0.035613 | Y
17/02/2017 | 16:32 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 131 | 313 | 0.18312 | 0.058504 | Y
17/02/2017 | 16:41 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 107 | 234 | 0.11173 | 0.047786 | Y
17/02/2017 | 16:41 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 32 | 278 | 0.039729 | 0.014291 | Y
17/02/2017 | 16:53 | ZN12690:PA10 | URBAN | Other | Other | 1 | 228 | 0.00015681 | 6.889e-05 | Y
17/02/2017 | 17:04 | ZN12690:PA26 | URBAN | Other | Other - Self Clearing Trigger | 296 | 379 | 0.077317 | 0.020391 | Y
18/02/2017 | 08:19 | ZN14891:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 401 | 0.0017909 | 0.00044661 | N
17/02/2017 | 17:16 | 507:80923 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 614 | 0.0054842 | 0.0008932 | Y
17/02/2017 | 17:16 | ZN12600:PA2 | SHORT RURAL | Other | Other - Self Clearing Trigger | 17 | 1,314 | 0.099761 | 0.0075922 | Y
17/02/2017 | 17:44 | ZN12690:PA16 | SHORT RURAL | Other | Other - Arcing | 1 | 1,336 | 0.0059645 | 0.0004466 | Y
17/02/2017 | 17:46 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 64 | 0.00028582 | 0.0004466 | Y
17/02/2017 | 17:46 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 707 | 191 | 0.60334 | 0.31574 | Y
17/02/2017 | 17:48 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 112 | 0.00050019 | 0.0004466 | Y
17/02/2017 | 17:57 | 235:2120 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 168 | 0.0014966 | 0.0008932 | Y
17/02/2017 | 17:58 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 163 | 293 | 17.0082 | 5.8048 | Y
17/02/2017 | 16:54 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 86 | 336 | 0.12905 | 0.038407 | Y
17/02/2017 | 18:13 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 117 | 0.0036576 | 0.0031262 | Y
17/02/2017 | 16:43 | ZN15004:PA9 | URBAN | Other | Other - Arcing | 1 | 4,217 | 0.0029048 | 6.889e-05 | Y
17/02/2017 | 18:34 | 511:29878 | SHORT RURAL | Other | Other | 1 | 186 | 0.00083 | 0.0004466 | Y
17/02/2017 | 18:35 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 273 | 0.0012209 | 0.0004466 | Y
17/02/2017 | 18:06 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,119 | 0.0049974 | 0.0004466 | Y
17/02/2017 | 18:55 | 264:81240 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 886 | 0.023741 | 0.0026796 | Y
17/02/2017 | 17:44 | ZN12570:PA33 | SHORT RURAL | Other | Other - Self Clearing Trigger | 772 | 846 | 2.9183 | 0.34477 | Y
17/02/2017 | 19:08 | ZN14143:PA17 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,477 | 0.0065963 | 0.0004466 | Y
17/02/2017 | 19:10 | ZN12610:PA23 | URBAN | Other | Other - Self Clearing Trigger | 22 | 1,583 | 0.023997 | 0.0015156 | Y
17/02/2017 | 19:21 | 232:33407 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 314 | 0.0028046 | 0.0008932 | Y
17/02/2017 | 19:28 | ZN12610:PA9 | URBAN | Other | Other - Self Clearing Trigger | 60 | 1,471 | 0.060813 | 0.0041334 | Y
18/02/2017 | 07:41 | 264:81240 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 89 | 0.0011924 | 0.0013398 | N
17/02/2017 | 20:07 | 524:33576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 813 | 0.0072617 | 0.0008932 | Y
17/02/2017 | 20:13 | 265:81651 | SHORT RURAL | Other | Other | 1 | 81 | 0.00035966 | 0.0004466 | Y
17/02/2017 | 20:46 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 120 | 0.000538 | 0.0004466 | Y
17/02/2017 | 22:01 | ZN12610:PA20 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 1,416 | 0.037943 | 0.0026796 | Y
17/02/2017 | 23:00 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 740 | 0.029743 | 0.0040194 | Y
18/02/2017 | 00:52 | ZN12690:PA26 | URBAN | Other | Other - Self Clearing Trigger | 58 | 898 | 0.035868 | 0.0039956 | N
18/02/2017 | 05:19 | ZN3922:PA1 | URBAN | Other | Other | 1 | 161 | 0.00011105 | 6.889e-05 | N
18/02/2017 | 08:19 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 186 | 0.0016614 | 0.00089321 | N
18/02/2017 | 06:14 | ZN847:PA2 | URBAN | Other | Other - Self Clearing Trigger | 41 | 270 | 0.0076355 | 0.0028245 | N
18/02/2017 | 06:37 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 167 | 0.0037292 | 0.002233 | N
18/02/2017 | 06:30 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 232 | 0.0010361 | 0.00044661 | N
18/02/2017 | 07:19 | ZN12610:PA23 | URBAN | Other | Other - Self Clearing Trigger | 32 | 859 | 0.018936 | 0.0022045 | N
18/02/2017 | 07:24 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 308 | 0.0068777 | 0.002233 | N
18/02/2017 | 07:35 | ZN12650:PA17 | URBAN | Other | Other - Self Clearing Trigger | 50 | 567 | 0.019547 | 0.0034445 | N
18/02/2017 | 08:05 | ZN2400:PA21 | URBAN | Other | Other | 1 | 174 | 0.00011997 | 6.889e-05 | N
18/02/2017 | 08:13 | ZN35370:PA8 | SHORT RURAL | Other | Other | 1 | 178 | 0.00079652 | 0.00044661 | N
18/02/2017 | 08:50 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 296 | 0.001322 | 0.00044661 | N
18/02/2017 | 09:14 | ZN12610:PA16 | SHORT RURAL | Other | Other - Self Clearing Trigger | 80 | 749 | 0.26761 | 0.035728 | N
18/02/2017 | 10:04 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 146 | 0.0013041 | 0.00089321 | N
18/02/2017 | 11:08 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 57 | 0.0007637 | 0.0013398 | N
18/02/2017 | 16:40 | ZN12660:PA14 | SHORT RURAL | Other | Other - Self Clearing Trigger | 55 | 69 | 0.017006 | 0.024563 | N
18/02/2017 | 16:19 | ZN14143:PA17 | SHORT RURAL | Other | Other - Self Clearing Trigger | 164 | 1,770 | 1.2964 | 0.073243 | N
18/02/2017 | 16:49 | ZN12660:PA14 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 76 | 0.00067884 | 0.00089321 | N
18/02/2017 | 17:04 | ZN2635:PA39 | URBAN | Other | Other - Self Clearing Trigger | 67 | 395 | 0.018242 | 0.0046156 | N
18/02/2017 | 17:06 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 14 | 40 | 0.002501 | 0.0062525 | N
18/02/2017 | 17:25 | ZN12690:PA24 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 285 | 0.011455 | 0.0040195 | N
18/02/2017 | 17:37 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 463 | 0.32977 | 0.071225 | N
18/02/2017 | 17:37 | ZN1193:PA21 | URBAN | Other | Other - Self Clearing Trigger | 39 | 97 | 0.0026128 | 0.0026867 | N
18/02/2017 | 17:43 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 107 | 0.038105 | 0.035613 | N
18/02/2017 | 17:59 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 188 | 0.0016792 | 0.00089321 | N
18/02/2017 | 17:59 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 260 | 0.010455 | 0.0040195 | N
18/02/2017 | 18:12 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 53 | 67 | 1.2731 | 1.8875 | N
18/02/2017 | 18:52 | 504:48031 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 63 | 0.00084409 | 0.0013398 | N
18/02/2017 | 19:36 | ZN35500:PA24 | URBAN | Other | Other - Self Clearing Trigger | 38 | 893 | 0.023389 | 0.0026178 | N
18/02/2017 | 20:13 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 67 | 0.0029923 | 0.0044661 | N
18/02/2017 | 21:48 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 732 | 0.003268 | 0.00044661 | N
18/02/2017 | 21:58 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 212 | 0.0009468 | 0.00044661 | N
18/02/2017 | 23:49 | ZN12570:PA33 | SHORT RURAL | Other | Other - Self Clearing Trigger | 772 | 161 | 0.55467 | 0.34478 | N
19/02/2017 | 07:20 | ZN3922:PA1 | URBAN | Other | Other | 1 | 89 | 6.0979e-05 | 6.889e-05 | N
19/02/2017 | 08:57 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 68 | 0.00030161 | 0.00044661 | N
19/02/2017 | 09:52 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 98 | 0.0349 | 0.035613 | N
19/02/2017 | 11:07 | ZN12640:PA16 | URBAN | Other | Other | 1 | 132 | 9.0923e-05 | 6.889e-05 | N
19/02/2017 | 11:10 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 125 | 0.00055684 | 0.00044661 | N
19/02/2017 | 11:30 | 229:34995 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 160 | 0.0021437 | 0.0013398 | N
19/02/2017 | 12:31 | ZN12570:PA39 | URBAN | Other | Other | 1 | 196 | 0.0001347 | 6.889e-05 | N
19/02/2017 | 12:33 | ZN12570:PA33 | SHORT RURAL | Other | Other - Self Clearing Trigger | 772 | 149 | 0.51539 | 0.34478 | N
19/02/2017 | 14:30 | ZN12650:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 280 | 0.007503 | 0.0026796 | N
19/02/2017 | 14:42 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 178 | 0.06339 | 0.035613 | N
19/02/2017 | 15:08 | ZN12630:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 332 | 0.0088964 | 0.0026796 | N
19/02/2017 | 16:15 | ZN12610:PA17 | URBAN | Other | Other | 1 | 55 | 3.7602e-05 | 6.889e-05 | N
19/02/2017 | 20:26 | ZN342:PA22 | URBAN | Other | Other - Self Clearing Trigger | 73 | 69 | 0.0034566 | 0.005029 | N
19/02/2017 | 20:28 | ZN12570:PA33 | SHORT RURAL | Other | Other - Self Clearing Trigger | 772 | 107 | 0.36831 | 0.34478 | N
17/02/2017 | 10:32 | 224:80326 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,008 | 8 | 0.036014 | 0.45017 | Y
17/02/2017 | 10:32 | 224:80328 | SHORT RURAL | Other | Other - Self Clearing Trigger | 56 | 8 | 0.0020008 | 0.025009 | Y
17/02/2017 | 10:32 | 224:80329 | SHORT RURAL | Other | Other - Self Clearing Trigger | 410 | 8 | 0.014648 | 0.18311 | Y
17/02/2017 | 10:32 | 224:80337 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,864 | 8 | 0.066597 | 0.83246 | Y
17/02/2017 | 10:32 | 224:80340 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,085 | 8 | 0.038765 | 0.48456 | Y
17/02/2017 | 10:32 | 224:80341 | URBAN | Other | Other - Self Clearing Trigger | 1,376 | 8 | 0.0075834 | 0.094793 | Y
20/02/2017 | 08:46 | 223:14394 | URBAN | Other | Other | 1 | 89 | 6.1392e-05 | 6.889e-05 | N
20/02/2017 | 11:01 | 216:10728 | SHORT RURAL | Other | Other | 1 | 198 | 0.00088532 | 0.00044661 | N
17/02/2017 | 21:40 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 10 | 4.466e-05 | 0.0004466 | Y
20/02/2017 | 14:08 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 172 | 0.061254 | 0.035613 | N
18/02/2017 | 12:00 | 230:81432 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 390 | 0.0017418 | 0.00044661 | N
21/02/2017 | 02:56 | ZN10993:PA22 | URBAN | Other | Other - Arcing | 1 | 274 | 0.0001888 | 6.8892e-05 | N
21/02/2017 | 06:52 | ZN9118:PA6 | URBAN | Other | Other - Arcing | 1 | 188 | 0.0001292 | 6.8892e-05 | N
18/02/2017 | 21:00 | 504:48031 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 70 | 0.00031262 | 0.00044661 | N
16/02/2017 | 13:25 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 250 | 0.0011165 | 0.0004466 | N
21/02/2017 | 10:30 | 524:33572 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 260 | 0.01275 | 0.0049129 | N
17/02/2017 | 13:00 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 88 | 0.00039301 | 0.0004466 | Y
21/02/2017 | 13:46 | ZN35600:PA16 | URBAN | Other | Other - Self Clearing Trigger | 49 | 114 | 0.0038483 | 0.0033757 | N
17/02/2017 | 17:12 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 1,158 | 0.010343 | 0.0008932 | Y
17/02/2017 | 17:35 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 235 | 0.083689 | 0.035613 | Y
22/02/2017 | 03:36 | ZN80:PA32 | URBAN | Other | Other - Arcing | 71 | 234 | 0.011456 | 0.0048914 | N
22/02/2017 | 03:42 | 238:34141 | SHORT RURAL | Other | Other - Self Clearing Trigger | 24 | 47 | 0.0050898 | 0.010719 | N
18/02/2017 | 11:06 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 114 | 0.00050913 | 0.00044661 | N
18/02/2017 | 12:00 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 180 | 0.00080389 | 0.00044661 | N
18/02/2017 | 10:37 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 228 | 0.0010183 | 0.00044661 | N
22/02/2017 | 08:53 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 322 | 0.0014382 | 0.00044663 | N
22/02/2017 | 10:06 | 258:80775 | URBAN | Other | Other | 1 | 64 | 4.3908e-05 | 6.8893e-05 | N
18/02/2017 | 21:58 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 257 | 0.0011478 | 0.00044661 | N
19/02/2017 | 06:00 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 218 | 0.0009736 | 0.00044661 | N
19/02/2017 | 14:42 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 18 | 0.0064103 | 0.035613 | N
19/02/2017 | 19:00 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 120 | 0.042735 | 0.035613 | N
22/02/2017 | 12:05 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 185 | 0.0016525 | 0.00089327 | N
22/02/2017 | 12:19 | 258:80785 | URBAN | Other | Other | 1 | 234 | 0.00016111 | 6.8893e-05 | N
22/02/2017 | 12:38 | ZN180:PA20 | URBAN | Other | Other - Self Clearing Trigger | 38 | 122 | 0.0031939 | 0.0026179 | N
22/02/2017 | 16:58 | 224:80337 | SHORT RURAL | Other | Other | 1 | 64 | 0.00028406 | 0.00044663 | N
22/02/2017 | 18:20 | 256:80647 | URBAN | Other | Other | 1 | 70 | 4.7892e-05 | 6.8893e-05 | N
22/02/2017 | 09:58 | ZN8100:PA28 | URBAN | Other | Other - Self Clearing Trigger | 2 | 27 | 3.7202e-05 | 0.00013779 | N
24/02/2017 | 10:13 | ZN9700:PA17 | URBAN | Other | Other | 1 | 88 | 6.042e-05 | 6.8881e-05 | N
24/02/2017 | 12:16 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 102 | 0.00045392 | 0.00044648 | N
24/02/2017 | 20:04 | 243:80081 | SHORT RURAL | Other | Other | 1 | 56 | 0.00024794 | 0.00044648 | N
24/02/2017 | 23:13 | ZN35600:PA22 | URBAN | Other | Other - Arcing | 1 | 676 | 0.00046571 | 6.8881e-05 | N
25/02/2017 | 10:01 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 128 | 0.045675 | 0.0356 | N
25/02/2017 | 12:02 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 43 | 0.00019205 | 0.00044662 | N
25/02/2017 | 15:44 | ZN4545:PA2 | URBAN | Other | Other - Arcing | 1 | 299 | 0.00020578 | 6.8879e-05 | N
25/02/2017 | 16:18 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 92 | 0.00082178 | 0.00089324 | N
25/02/2017 | 17:42 | ZN1287:PA11 | URBAN | Other | Other | 1 | 44 | 3.0272e-05 | 6.8879e-05 | N
25/02/2017 | 21:06 | 221:11897 | URBAN | Other | Other | 1 | 78 | 5.3932e-05 | 6.8879e-05 | N
25/02/2017 | 23:45 | ZN9550:PA33 | URBAN | Other | Other - Arcing | 1 | 329 | 0.00022665 | 6.8879e-05 | N
26/02/2017 | 00:34 | ZN10993:PA23 | URBAN | Other | Other - Arcing | 1 | 776 | 0.00053422 | 6.8879e-05 | N
26/02/2017 | 03:27 | 238:34141 | SHORT RURAL | Other | Other - Self Clearing Trigger | 24 | 282 | 0.030246 | 0.010719 | N
26/02/2017 | 06:46 | 206:34440 | URBAN | Other | Other | 1 | 37 | 2.5497e-05 | 6.8879e-05 | N
26/02/2017 | 09:19 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 51 | 0.00022584 | 0.00044661 | N
26/02/2017 | 09:48 | ZN12660:PA17 | URBAN | Other | Other | 1 | 87 | 5.9603e-05 | 6.8879e-05 | N
26/02/2017 | 17:55 | 508:82575 | SHORT RURAL | Other | Other - Arcing | 1 | 322 | 0.0014385 | 0.00044661 | N
26/02/2017 | 18:42 | ZN15014:PA19 | URBAN | Other | Other - Arcing | 33 | 232 | 0.0052787 | 0.002273 | N
26/02/2017 | 21:40 | ZN12690:PA24 | SHORT RURAL | Other | Other - Self Clearing Trigger | 784 | 82 | 0.28742 | 0.35015 | N
27/02/2017 | 01:51 | 217:33611 | URBAN | Other | Other - Self Clearing Trigger | 31 | 324 | 0.0069128 | 0.0021352 | N
27/02/2017 | 07:20 | ZN35800:PA3 | URBAN | Other | Other - Arcing | 1 | 309 | 0.00021294 | 6.8879e-05 | N
27/02/2017 | 07:40 | ZN36100:PA13 | URBAN | Other | Other - Arcing | 1 | 470 | 0.00032342 | 6.8879e-05 | N
27/02/2017 | 08:20 | 203:8086 | URBAN | Other | Other | 1 | 69 | 4.7228e-05 | 6.8879e-05 | N
27/02/2017 | 09:17 | ZN36100:PA15 | URBAN | Other | Other - Arcing | 1 | 447 | 0.00030822 | 6.8879e-05 | N
27/02/2017 | 13:43 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 51 | 0.00022829 | 0.00044661 | N
27/02/2017 | 13:59 | ZN36100:PA7 | URBAN | Other | Other - Arcing | 1 | 1,425 | 0.00098176 | 6.8879e-05 | N
27/02/2017 | 14:55 | 232:11454 | SHORT RURAL | Other | Other | 1 | 98 | 0.00043828 | 0.00044661 | N
27/02/2017 | 18:06 | ZN931:PA13 | URBAN | Other | Other - Arcing | 1 | 144 | 9.9139e-05 | 6.8879e-05 | N
27/02/2017 | 20:39 | ZN1788:PA8 | URBAN | Other | Other - Arcing | 1 | 81 | 5.5677e-05 | 6.8879e-05 | N
28/02/2017 | 04:49 | 202:34245 | URBAN | Other | Other | 1 | 444 | 0.00030586 | 6.8879e-05 | N
28/02/2017 | 06:23 | 507:80917 | URBAN | Other | Other - Self Clearing Trigger | 16 | 176 | 0.0019413 | 0.0011021 | N
28/02/2017 | 09:13 | ZN10999:PA24 | URBAN | Other | Other - Arcing | 1 | 67 | 4.5885e-05 | 6.8879e-05 | N
28/02/2017 | 09:25 | ZN1610:PA2 | URBAN | Other | Other - Self Clearing Trigger | 1 | 79 | 5.4564e-05 | 6.8879e-05 | N
28/02/2017 | 09:40 | ZN2602:PA27 | URBAN | Other | Other - Arcing | 1 | 289 | 0.00019936 | 6.8879e-05 | N
28/02/2017 | 11:03 | ZN2400:PA15 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,223 | 133 | 0.7269 | 0.54622 | N
06/02/2017 | 08:00 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 3,205 | 0.014362 | 0.00044811 | N
28/02/2017 | 13:38 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 92 | 0.00041044 | 0.00044662 | N
28/02/2017 | 16:49 | ZN72:PA16 | URBAN | Other | Other - Self Clearing Trigger | 105 | 50 | 0.003621 | 0.0072323 | N
28/02/2017 | 17:03 | ZN3472:PA22 | URBAN | Other | Other - Arcing | 1 | 538 | 0.00037057 | 6.8879e-05 | N
01/03/2017 | 00:05 | ZN12620:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 309 | 0.0013791 | 0.00044662 | N
01/03/2017 | 05:05 | 221:11895 | URBAN | Other | Other | 1 | 85 | 5.8376e-05 | 6.888e-05 | N
01/03/2017 | 09:31 | ZN35800:PA2 | SHORT RURAL | Other | Other | 1 | 111 | 0.00049627 | 0.00044662 | N
01/03/2017 | 09:33 | ZN12610:PA11 | URBAN | Other | Other | 1 | 73 | 5.0236e-05 | 6.888e-05 | N
01/03/2017 | 09:36 | ZN35400:PA52 | URBAN | Other | Other | 1 | 58 | 3.9675e-05 | 6.888e-05 | N
01/03/2017 | 10:17 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 283 | 0.10075 | 0.0356 | N
01/03/2017 | 11:43 | ZN3425:PA28 | URBAN | Other | Other - Self Clearing Trigger | 25 | 132 | 0.002271 | 0.001722 | N
01/03/2017 | 16:39 | 515:35200 | URBAN | Other | Other - Self Clearing Trigger | 1 | 81 | 5.5448e-05 | 6.888e-05 | N
02/03/2017 | 04:24 | ZN10997:PA1 | URBAN | Other | Other - Self Clearing Trigger | 40 | 216 | 0.0059481 | 0.0027552 | N
02/03/2017 | 05:11 | ZN3425:PA28 | URBAN | Other | Other - Self Clearing Trigger | 25 | 163 | 0.0028109 | 0.001722 | N
02/03/2017 | 07:10 | 239:82129 | SHORT RURAL | Other | Other | 1 | 85 | 0.00038165 | 0.00044663 | N
02/03/2017 | 13:21 | ZN2835:PA10 | URBAN | Other | Other - Self Clearing Trigger | 222 | 100 | 0.015291 | 0.015291 | N
02/03/2017 | 13:21 | ZN2835:PA31 | URBAN | Other | Other - Self Clearing Trigger | 1,002 | 102 | 0.070425 | 0.069018 | N
02/03/2017 | 18:49 | 225:13446 | URBAN | Other | Other - Arcing | 1 | 143 | 9.8201e-05 | 6.8881e-05 | N
02/03/2017 | 22:57 | ZN15012:PA6 | URBAN | Other | Other | 1 | 624 | 0.00043003 | 6.8881e-05 | N
03/03/2017 | 03:22 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 68 | 0.00030194 | 0.00044665 | N
03/03/2017 | 06:07 | ZN15008:PA5 | URBAN | Other | Other - Arcing | 1 | 142 | 9.8061e-05 | 6.8863e-05 | N
03/03/2017 | 08:46 | ZN12650:PA13 | SHORT RURAL | Other | Other | 1 | 70 | 0.00031117 | 0.00044665 | N
03/03/2017 | 10:17 | 213:33771 | URBAN | Other | Other | 1 | 81 | 5.5446e-05 | 6.8863e-05 | N
03/03/2017 | 10:46 | ZN72:PA10 | URBAN | Other | Other - Arcing | 1 | 193 | 0.00013304 | 6.8863e-05 | N
03/03/2017 | 11:48 | ZN10999:PA36 | URBAN | Other | Other - Self Clearing Trigger | 44 | 321 | 0.0097408 | 0.00303 | N
03/03/2017 | 12:02 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 1 | 207 | 0.00014284 | 6.8863e-05 | N
03/03/2017 | 12:13 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 1 | 196 | 0.0001352 | 6.8863e-05 | N
03/03/2017 | 12:20 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 1 | 189 | 0.00013032 | 6.8863e-05 | N
03/03/2017 | 18:20 | ZN14891:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 1,303 | 0.15714 | 0.01206 | N
04/03/2017 | 00:46 | ZN35500:PA28 | URBAN | Other | Other - Self Clearing Trigger | 38 | 429 | 0.011228 | 0.0026173 | N
04/03/2017 | 04:58 | ZN2196:PA25 | URBAN | Other | Other - Arcing | 1 | 246 | 0.00016923 | 6.8876e-05 | N
04/03/2017 | 05:02 | ZN2196:PA25 | URBAN | Other | Other - Arcing | 1 | 242 | 0.00016695 | 6.8876e-05 | N
04/03/2017 | 06:55 | ZN15014:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 481 | 0.0021509 | 0.00044728 | N
04/03/2017 | 07:30 | ZN15010:PA1 | URBAN | Other | Other - Arcing | 1 | 445 | 0.00030646 | 6.8876e-05 | N
04/03/2017 | 10:18 | ZN35500:PA28 | URBAN | Other | Other - Self Clearing Trigger | 38 | 91 | 0.0023826 | 0.0026173 | N
04/03/2017 | 11:21 | ZN35800:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 415 | 0.0018545 | 0.00044728 | N
04/03/2017 | 11:44 | 225:13446 | URBAN | Other | Other - Self Clearing Trigger | 1 | 56 | 3.857e-05 | 6.8876e-05 | N
04/03/2017 | 12:20 | 507:80922 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 40 | 0.0012524 | 0.003131 | N
04/03/2017 | 12:35 | ZN2835:PA27 | URBAN | Other | Other - Arcing | 1 | 235 | 0.00016154 | 6.8876e-05 | N
04/03/2017 | 15:15 | ZN965:PA6 | URBAN | Other | Other - Self Clearing Trigger | 16 | 159 | 0.0017575 | 0.001102 | N
04/03/2017 | 17:27 | ZN8000:PA19 | URBAN | Other | Other | 1 | 45 | 3.1201e-05 | 6.8876e-05 | N
04/03/2017 | 22:35 | ZN2602:PA8 | URBAN | Other | Other - Arcing | 1 | 357 | 0.00024617 | 6.8876e-05 | N
05/03/2017 | 06:48 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 97 | 0.00086769 | 0.00089453 | N
05/03/2017 | 08:32 | ZN3155:PA16 | URBAN | Other | Other - Arcing | 1 | 413 | 0.00028416 | 6.8877e-05 | N
06/03/2017 | 10:03 | ZN180:PA18 | URBAN | Other | Other - Self Clearing Trigger | 57 | 96 | 0.0037755 | 0.003926 | N
06/03/2017 | 10:17 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 37 | 0.00016698 | 0.00044727 | N
06/03/2017 | 10:17 | ZN15004:PA5 | URBAN | Other | Other | 1 | 313 | 0.0002156 | 6.8877e-05 | N
06/03/2017 | 12:21 | ZN3155:PA32 | URBAN | Other | Other - Arcing | 1 | 128 | 8.8403e-05 | 6.8877e-05 | N
06/03/2017 | 13:04 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 198 | 0.070488 | 0.0356 | N
06/03/2017 | 15:49 | ZN931:PA24 | URBAN | Other | Other - Self Clearing Trigger | 5 | 469 | 0.0016152 | 0.00034438 | N
07/03/2017 | 06:24 | ZN3154:PA5 | URBAN | Other | Other | 1 | 49 | 3.3636e-05 | 6.8879e-05 | N
07/03/2017 | 07:36 | ZN15002:PA8 | URBAN | Other | Other - Self Clearing Trigger | 1 | 124 | 8.541e-05 | 6.8879e-05 | N
07/03/2017 | 07:44 | 235:2121 | URBAN | Other | Other - Self Clearing Trigger | 1 | 70 | 4.8353e-05 | 6.8879e-05 | N
07/03/2017 | 08:39 | ZN1673:PA9 | URBAN | Other | Other - Arcing | 1 | 251 | 0.00017287 | 6.8879e-05 | N
07/03/2017 | 09:17 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 128 | 0.00057108 | 0.00044616 | N
07/03/2017 | 10:08 | ZN262:PA20 | URBAN | Other | Other - Arcing | 1 | 112 | 7.6892e-05 | 6.8879e-05 | N
07/03/2017 | 10:44 | ZN1673:PA9 | URBAN | Other | Other - Arcing | 1 | 185 | 0.00012776 | 6.8879e-05 | N
07/03/2017 | 10:47 | ZN15012:PA2 | URBAN | Other | Other | 1 | 38 | 2.6472e-05 | 6.8879e-05 | N
07/03/2017 | 11:00 | ZN3288:PA45 46DEF | CBD | Other | Other - Self Clearing Trigger | 22 | 320 | 0.22675 | 0.070858 | N
07/03/2017 | 13:44 | 524:33572 | SHORT RURAL | Other | Other - Arcing | 1 | 446 | 0.0019899 | 0.00044616 | N
07/03/2017 | 13:47 | 230:81432 | SHORT RURAL | Other | Other | 1 | 55 | 0.00024516 | 0.00044616 | N
07/03/2017 | 14:36 | ZN12620:PA7 | URBAN | Other | Other | 1 | 117 | 8.0841e-05 | 6.8879e-05 | N
07/03/2017 | 14:45 | 205:12210 | URBAN | Other | Other - Arcing | 1 | 219 | 0.0001506 | 6.8879e-05 | N
07/03/2017 | 21:37 | ZN35600:PA12 | URBAN | Other | Other - Arcing | 1 | 353 | 0.000243 | 6.8879e-05 | N
07/03/2017 | 21:48 | ZN1850:PA10 | URBAN | Other | Other - Arcing | 1 | 237 | 0.00016309 | 6.8879e-05 | N
08/03/2017 | 03:48 | ZN36100:PA21 | URBAN | Other | Other - Arcing | 1 | 312 | 0.00021473 | 6.888e-05 | N
08/03/2017 | 11:10 | ZN15004:PA9 | URBAN | Other | Other - Arcing | 1 | 609 | 0.00041978 | 6.888e-05 | N
08/03/2017 | 12:28 | 224:80340 | SHORT RURAL | Other | Other | 1 | 31 | 0.00013839 | 0.00044617 | N
08/03/2017 | 15:36 | ZN2635:PA35 | URBAN | Other | Other | 1 | 34 | 2.3327e-05 | 6.888e-05 | N
08/03/2017 | 16:27 | 230:81440 | SHORT RURAL | Other | Other | 1 | 102 | 0.00045717 | 0.00044617 | N
08/03/2017 | 17:43 | ZN15001:PA18 | URBAN | Other | Other - Arcing | 1 | 298 | 0.00020551 | 6.888e-05 | N
08/03/2017 | 19:54 | ZN36100:PA5 | URBAN | Other | Other - Arcing | 1 | 306 | 0.00021066 | 6.888e-05 | N
08/03/2017 | 20:43 | ZN12570:PA26 | URBAN | Other | Other | 1 | 60 | 4.1569e-05 | 6.888e-05 | N
08/03/2017 | 20:54 | ZN12570:PA26 | URBAN | Other | Other - Arcing | 1 | 156 | 0.00010725 | 6.888e-05 | N
09/03/2017 | 18:46 | 520:48172 | SHORT RURAL | Other | Other - Arcing | 1 | 725 | 0.0032237 | 0.00044464 | N
09/03/2017 | 19:51 | 256:80647 | URBAN | Other | Other | 1 | 79 | 5.4308e-05 | 6.8889e-05 | N
09/03/2017 | 20:29 | 214:8670 | URBAN | Other | Other | 1 | 51 | 3.4846e-05 | 6.8889e-05 | N
09/03/2017 | 23:47 | ZN10999:PA10 | URBAN | Other | Other - Arcing | 1 | 733 | 0.00050474 | 6.8889e-05 | N
10/03/2017 | 04:19 | ZN2635:PA31 | URBAN | Other | Other - Self Clearing Trigger | 1,548 | 133 | 0.14184 | 0.10664 | N
10/03/2017 | 04:19 | ZN2635:PA32 | URBAN | Other | Other - Self Clearing Trigger | 495 | 133 | 0.045354 | 0.034101 | N
10/03/2017 | 04:19 | ZN2635:PA33 | URBAN | Other | Other - Self Clearing Trigger | 19 | 133 | 0.0017409 | 0.0013089 | N
10/03/2017 | 04:19 | ZN2635:PA35 | URBAN | Other | Other - Self Clearing Trigger | 1,539 | 133 | 0.14101 | 0.10602 | N
10/03/2017 | 04:19 | ZN2635:PA38 | URBAN | Other | Other - Self Clearing Trigger | 1,016 | 133 | 0.093091 | 0.069993 | N
10/03/2017 | 04:19 | ZN2635:PA39 | URBAN | Other | Other - Self Clearing Trigger | 597 | 133 | 0.0547 | 0.041128 | N
10/03/2017 | 04:19 | ZN2635:PA40 | URBAN | Other | Other - Self Clearing Trigger | 499 | 133 | 0.045721 | 0.034377 | N
10/03/2017 | 04:19 | ZN2635:PA41 | URBAN | Other | Other - Self Clearing Trigger | 427 | 133 | 0.039124 | 0.029416 | N
10/03/2017 | 04:19 | ZN2635:PA43 | URBAN | Other | Other - Self Clearing Trigger | 945 | 133 | 0.086586 | 0.065102 | N
10/03/2017 | 04:19 | ZN2635:PA44 | URBAN | Other | Other - Self Clearing Trigger | 997 | 133 | 0.09135 | 0.068684 | N
10/03/2017 | 04:19 | ZN2635:PA46 | URBAN | Other | Other - Self Clearing Trigger | 496 | 133 | 0.045446 | 0.03417 | N
10/03/2017 | 04:19 | ZN2635:PA47 | URBAN | Other | Other - Self Clearing Trigger | 27 | 133 | 0.0024739 | 0.0018601 | N
10/03/2017 | 04:19 | ZN2635:PA50 | URBAN | Other | Other - Self Clearing Trigger | 775 | 133 | 0.071009 | 0.053391 | N
10/03/2017 | 04:19 | ZN2635:PA51 | URBAN | Other | Other - Self Clearing Trigger | 407 | 133 | 0.037291 | 0.028039 | N
10/03/2017 | 04:19 | ZN2635:PA52 | URBAN | Other | Other - Self Clearing Trigger | 1,345 | 133 | 0.12324 | 0.092658 | N
10/03/2017 | 04:19 | ZN2635:PA53 | URBAN | Other | Other - Self Clearing Trigger | 1 | 133 | 9.1625e-05 | 6.8891e-05 | N
10/03/2017 | 04:19 | ZN2635:PA55 | URBAN | Other | Other - Self Clearing Trigger | 987 | 133 | 0.090434 | 0.067995 | N
10/03/2017 | 04:19 | ZN2635:PA57 | URBAN | Other | Other - Self Clearing Trigger | 1,271 | 133 | 0.11646 | 0.087561 | N
10/03/2017 | 04:19 | ZN2635:PA58 | URBAN | Other | Other - Self Clearing Trigger | 2,219 | 133 | 0.20332 | 0.15287 | N
10/03/2017 | 04:19 | ZN2635:PA59 | URBAN | Other | Other - Self Clearing Trigger | 145 | 133 | 0.013286 | 0.0099892 | N
10/03/2017 | 04:19 | ZN2635:PA62 | URBAN | Other | Other - Self Clearing Trigger | 69 | 133 | 0.0063221 | 0.0047535 | N
10/03/2017 | 04:19 | ZN2635:PA64 | URBAN | Other | Other - Self Clearing Trigger | 244 | 133 | 0.022357 | 0.016809 | N
10/03/2017 | 04:19 | ZN2635:PA65 | URBAN | Other | Other - Self Clearing Trigger | 6 | 133 | 0.00054975 | 0.00041335 | N
10/03/2017 | 06:23 | ZN2602:PA3 | URBAN | Other | Other - Self Clearing Trigger | 48 | 232 | 0.0076667 | 0.0033068 | N
10/03/2017 | 14:57 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 92 | 0.00040915 | 0.00044464 | N
10/03/2017 | 17:35 | 221:11899 | SHORT RURAL | Other | Other | 1 | 70 | 0.00030999 | 0.00044464 | N
10/03/2017 | 23:13 | ZN12630:PA1 | SHORT RURAL | Other | Other - Arcing | 1 | 1,172 | 0.0052115 | 0.00044464 | N
11/03/2017 | 13:43 | ZN14892:PA16 | URBAN | Other | Other | 1 | 69 | 4.7569e-05 | 6.8891e-05 | N
11/03/2017 | 13:53 | 217:33610 | URBAN | Other | Other | 1 | 37 | 2.5306e-05 | 6.8891e-05 | N
11/03/2017 | 14:41 | ZN15013:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 174 | 0.0069631 | 0.0040018 | N
11/03/2017 | 16:20 | 511:29872 | URBAN | Other | Other | 1 | 69 | 4.7776e-05 | 6.8891e-05 | N
12/03/2017 | 07:23 | ZN965:PA21 | URBAN | Other | Other - Self Clearing Trigger | 32 | 192 | 0.0042298 | 0.0022045 | N
12/03/2017 | 08:36 | ZN15014:PA11 | URBAN | Other | Other - Arcing | 1 | 284 | 0.0001959 | 6.8892e-05 | N
12/03/2017 | 09:52 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 73 | 0.00032363 | 0.00044464 | N
12/03/2017 | 16:48 | 512:48048 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 127 | 0.0016941 | 0.0013339 | N
12/03/2017 | 17:18 | ZN36200:PA11 | SHORT RURAL | Other | Other | 1 | 88 | 0.00039121 | 0.00044464 | N
12/03/2017 | 18:56 | ZN3154:PA11 | URBAN | Other | Other - Self Clearing Trigger | 30 | 108 | 0.0022366 | 0.0020668 | N
13/03/2017 | 07:00 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 75 | 0.00066697 | 0.00088929 | N
13/03/2017 | 07:20 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 115 | 0.0035794 | 0.0031125 | N
13/03/2017 | 07:41 | 512:48048 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 439 | 0.003904 | 0.00088929 | N
13/03/2017 | 13:38 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 172 | 0.12251 | 0.071225 | N
13/03/2017 | 14:35 | ZN12610:PA6 | URBAN | Other | Other | 1 | 55 | 3.7603e-05 | 6.8892e-05 | N
13/03/2017 | 15:47 | ZN931:PA31 | URBAN | Other | Other - Arcing | 1 | 192 | 0.00013252 | 6.8892e-05 | N
13/03/2017 | 15:49 | ZN931:PA31 | URBAN | Other | Other - Arcing | 1 | 191 | 0.00013142 | 6.8892e-05 | N
13/03/2017 | 15:50 | ZN931:PA31 | URBAN | Other | Other - Arcing | 1 | 190 | 0.00013079 | 6.8892e-05 | N
13/03/2017 | 16:29 | ZN12690:PA19 | URBAN | Other | Other - Self Clearing Trigger | 1,216 | 60 | 0.050404 | 0.083772 | N
13/03/2017 | 16:29 | ZN12690:PA24 | SHORT RURAL | Other | Other - Self Clearing Trigger | 784 | 165 | 0.57652 | 0.3486 | N
13/03/2017 | 17:22 | ZN12630:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 188 | 0.0058515 | 0.0031125 | N
13/03/2017 | 17:57 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 41 | 0.00036461 | 0.00088929 | N
13/03/2017 | 18:39 | 513:48057 | URBAN | Other | Other - Self Clearing Trigger | 18 | 31 | 0.00038442 | 0.0012401 | N
14/03/2017 | 08:24 | ZN12630:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 238 | 204 | 0.21589 | 0.10583 | N
14/03/2017 | 10:02 | ZN35400:PA81 | URBAN | Other | Other - Arcing | 1 | 147 | 0.00010148 | 6.8892e-05 | N
14/03/2017 | 10:14 | ZN10994:PA11 | URBAN | Other | Other - Arcing | 1 | 645 | 0.00044449 | 6.8892e-05 | N
14/03/2017 | 11:32 | ZN15013:PA8 | URBAN | Other | Other - Self Clearing Trigger | 1 | 127 | 8.7493e-05 | 6.8892e-05 | N
14/03/2017 | 16:00 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 90 | 0.0020009 | 0.0022232 | N
14/03/2017 | 16:05 | ZN9037:PA4 | URBAN | Other | Other - Arcing | 1 | 145 | 9.9583e-05 | 6.8892e-05 | N
14/03/2017 | 17:43 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 87 | 0.0011605 | 0.0013339 | N
14/03/2017 | 17:54 | 239:82127 | SHORT RURAL | Other | Other | 1 | 70 | 0.00031155 | 0.00044464 | N
14/03/2017 | 18:20 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 37 | 70 | 0.91687 | 1.3177 | N
14/03/2017 | 18:38 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 577 | 0.20548 | 0.035613 | N
14/03/2017 | 19:13 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 397 | 0.14134 | 0.035613 | N
14/03/2017 | 17:00 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 64 | 291 | 6.6343 | 2.2792 | N
14/03/2017 | 20:05 | ZN1648:PA21 | URBAN | Other | Other - Arcing | 1 | 181 | 0.00012457 | 6.8892e-05 | N
15/03/2017 | 01:00 | ZN2602:PA4 | URBAN | Other | Other - Arcing | 1 | 359 | 0.00024762 | 6.8892e-05 | N
15/03/2017 | 06:43 | ZN2635:PA35 | URBAN | Other | Other - Self Clearing Trigger | 45 | 154 | 0.0047603 | 0.0031002 | N
15/03/2017 | 06:44 | ZN2602:PA27 | URBAN | Other | Other - Arcing | 1 | 196 | 0.00013487 | 6.8892e-05 | N
14/03/2017 | 17:43 | 238:34151 | URBAN | Other | Other - Self Clearing Trigger | 1 | 87 | 5.9936e-05 | 6.8892e-05 | N
15/03/2017 | 12:04 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 221 | 0.002948 | 0.0013339 | N
15/03/2017 | 13:29 | 512:48048 | SHORT RURAL | Other | Other | 1 | 63 | 0.00027872 | 0.00044465 | N
15/03/2017 | 13:35 | ZN2635:PA46 | URBAN | Other | Other - Self Clearing Trigger | 64 | 85 | 0.0037477 | 0.0044091 | N
15/03/2017 | 17:09 | ZN14892:PA19 | URBAN | Other | Other | 1 | 244 | 0.00016779 | 6.8892e-05 | N
16/03/2017 | 05:22 | ZN12620:PA7 | URBAN | Other | Other - Arcing | 1 | 457 | 0.0003149 | 6.8877e-05 | N
16/03/2017 | 05:58 | 239:82136 | SHORT RURAL | Other | Other | 1 | 96 | 0.00042769 | 0.00044451 | N
16/03/2017 | 06:39 | ZN9118:PA11 | URBAN | Other | Other - Arcing | 1 | 200 | 0.00013797 | 6.8877e-05 | N
15/03/2017 | 07:55 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 55 | 0.039174 | 0.071225 | N
16/03/2017 | 07:29 | 524:33570 | SHORT RURAL | Other | Other | 1 | 60 | 0.00026737 | 0.00044451 | N
16/03/2017 | 07:45 | ZN342:PA16 | URBAN | Other | Other - Arcing | 1 | 105 | 7.2321e-05 | 6.8877e-05 | N
16/03/2017 | 07:45 | ZN342:PA16 | URBAN | Other | Other - Arcing | 1 | 104 | 7.1861e-05 | 6.8877e-05 | N
16/03/2017 | 08:01 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 229 | 0.0010179 | 0.00044451 | N
16/03/2017 | 08:46 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 96 | 0.0004251 | 0.00044451 | N
16/03/2017 | 08:50 | ZN10996:PA9 | URBAN | Other | Other - Arcing | 1 | 235 | 0.0001616 | 6.8877e-05 | N
16/03/2017 | 10:11 | ZN7900:PA11 | URBAN | Other | Other - Self Clearing Trigger | 42 | 59 | 0.0017068 | 0.0028928 | N
16/03/2017 | 11:42 | ZN12620:PA1 | SHORT RURAL | Other | Other - Arcing | 1 | 498 | 0.0022127 | 0.00044451 | N
16/03/2017 | 11:57 | 264:81238 | SHORT RURAL | Other | Other - Arcing | 1 | 333 | 0.0014797 | 0.00044451 | N
16/03/2017 | 12:37 | ZN12610:PA13 | URBAN | Other | Other - Arcing | 1 | 1,372 | 0.00094531 | 6.8877e-05 | N
16/03/2017 | 13:20 | 233:82819 | SHORT RURAL | Other | Other | 1 | 97 | 0.00042999 | 0.00044451 | N
16/03/2017 | 13:27 | ZN12620:PA1 | SHORT RURAL | Other | Other - Arcing | 1 | 392 | 0.0017433 | 0.00044451 | N
16/03/2017 | 15:19 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 140 | 0.016745 | 0.012002 | N
16/03/2017 | 16:06 | ZN9037:PA4 | URBAN | Other | Other - Arcing | 1 | 382 | 0.00026312 | 6.8877e-05 | N
16/03/2017 | 22:01 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 74 | 0.026339 | 0.035625 | N
16/03/2017 | 23:52 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 177 | 21 | 1.3168 | 6.3057 | N
17/03/2017 | 08:45 | ZN12620:PA2 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 330 | 0.010267 | 0.0031111 | N
17/03/2017 | 08:50 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 125 | 0.014968 | 0.012 | N
17/03/2017 | 09:39 | 220:8689 | URBAN | Other | Other | 1 | 91 | 6.2529e-05 | 6.8877e-05 | N
17/03/2017 | 09:40 | ZN14892:PA16 | URBAN | Other | Other - Arcing | 1 | 305 | 0.00020998 | 6.8877e-05 | N
17/03/2017 | 14:22 | ZN180:PA41 | URBAN | Other | Other - Arcing | 1 | 689 | 0.00047428 | 6.8877e-05 | N
17/03/2017 | 14:52 | ZN9252:PA24 | URBAN | Other | Other - Arcing | 1 | 548 | 0.00037739 | 6.8877e-05 | N
17/03/2017 | 14:58 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 47 | 0.016744 | 0.035625 | N
17/03/2017 | 18:39 | ZN3154:PA5 | URBAN | Other | Other | 1 | 1,018 | 0.00070135 | 6.8877e-05 | N
17/03/2017 | 19:55 | ZN14892:PA19 | URBAN | Other | Other - Arcing | 1 | 1,099 | 0.00075712 | 6.8877e-05 | N
17/03/2017 | 20:52 | ZN3425:PA43 | URBAN | Other | Other - Arcing | 1 | 298 | 0.00020528 | 6.8877e-05 | N
17/03/2017 | 21:05 | ZN15008:PA7 | URBAN | Other | Other - Arcing | 1 | 439 | 0.00030257 | 6.8877e-05 | N
17/03/2017 | 23:19 | ZN2196:PA2 | URBAN | Other | Other - Arcing | 1 | 176 | 0.00012127 | 6.8877e-05 | N
17/03/2017 | 23:22 | 235:2124 | SHORT RURAL | Other | Other | 1 | 66 | 0.00029148 | 0.00044445 | N
18/03/2017 | 03:02 | ZN262:PA15 | URBAN | Other | Other - Arcing | 107 | 967 | 0.071295 | 0.00737 | N
18/03/2017 | 03:02 | ZN262:PA31 | URBAN | Other | Other - Arcing | 1 | 968 | 0.00066674 | 6.8878e-05 | N
18/03/2017 | 04:25 | ZN847:PA15 | URBAN | Other | Other - Arcing | 15 | 2,255 | 0.023294 | 0.0010332 | N
18/03/2017 | 05:26 | ZN12650:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 61 | 159 | 0.043107 | 0.027111 | N
18/03/2017 | 08:08 | ZN262:PA17 | URBAN | Other | Other - Arcing | 1 | 986 | 0.00067905 | 6.8878e-05 | N
18/03/2017 | 09:04 | 504:48031 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 496 | 0.0022041 | 0.00044445 | N
18/03/2017 | 09:28 | 233:82819 | SHORT RURAL | Other | Other | 1 | 151 | 0.00067245 | 0.00044445 | N
18/03/2017 | 09:29 | 232:11454 | SHORT RURAL | Other | Other - Arcing | 1 | 527 | 0.0023401 | 0.00044445 | N
18/03/2017 | 11:18 | ZN12630:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 16 | 66 | 0.0046934 | 0.0071112 | N
18/03/2017 | 11:18 | ZN12650:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 224 | 314 | 0.31237 | 0.099557 | N
18/03/2017 | 11:28 | ZN847:PA48 | URBAN | Other | Other - Self Clearing Trigger | 3 | 392 | 0.00081001 | 0.00020663 | N
18/03/2017 | 18:08 | 217:33611 | URBAN | Other | Other | 1 | 152 | 0.0001044 | 6.8878e-05 | N
18/03/2017 | 19:37 | ZN4545:PA2 | URBAN | Other | Other - Self Clearing Trigger | 45 | 227 | 0.0070468 | 0.0030995 | N
18/03/2017 | 20:51 | 256:80641 | URBAN | Other | Other | 1 | 213 | 0.00014654 | 6.8878e-05 | N
18/03/2017 | 21:48 | 203:8086 | URBAN | Other | Other | 1 | 116 | 8.0197e-05 | 6.8878e-05 | N
18/03/2017 | 22:00 | ZN15012:PA2 | URBAN | Other | Other - Arcing | 1 | 119 | 8.1942e-05 | 6.8878e-05 | N
18/03/2017 | 22:23 | ZN9245:PA13 | URBAN | Other | Other | 1 | 801 | 0.00055152 | 6.8878e-05 | N
18/03/2017 | 23:49 | ZN180:PA32 | URBAN | Other | Other - Arcing | 1 | 190 | 0.00013108 | 6.8878e-05 | N
19/03/2017 | 04:09 | ZN14892:PA16 | URBAN | Other | Other - Arcing | 1 | 380 | 0.00026197 | 6.8879e-05 | N
19/03/2017 | 07:09 | 224:80346 | URBAN | Other | Other | 1 | 100 | 6.9131e-05 | 6.8879e-05 | N
19/03/2017 | 10:42 | 202:34260 | URBAN | Other | Other - Arcing | 1 | 482 | 0.00033205 | 6.8879e-05 | N
19/03/2017 | 13:15 | ZN2400:PA18 | SHORT RURAL | Other | Other - Self Clearing Trigger | 98 | 206 | 0.089726 | 0.043556 | N
19/03/2017 | 13:30 | ZN12640:PA13 | SHORT RURAL | Other | Other | 1 | 97 | 0.00043104 | 0.00044445 | N
19/03/2017 | 17:02 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 48 | 0.0171 | 0.035625 | N
19/03/2017 | 17:59 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 31 | 0.010901 | 0.035625 | N
19/03/2017 | 18:04 | 512:48048 | SHORT RURAL | Other | Other | 1 | 66 | 0.00029304 | 0.00044445 | N
19/03/2017 | 18:31 | ZN12610:PA10 | URBAN | Other | Other - Arcing | 1 | 839 | 0.00057765 | 6.8879e-05 | N
16/03/2017 | 02:00 | 227:13020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 576 | 0.0025604 | 0.00044451 | N
20/03/2017 | 08:37 | 213:33771 | URBAN | Other | Other | 1 | 192 | 0.00013253 | 6.8879e-05 | N
20/03/2017 | 10:02 | ZN12610:PA22 | URBAN | Other | Other | 1 | 218 | 0.00015028 | 6.8879e-05 | N
20/03/2017 | 10:30 | ZN14891:PA10 | SHORT RURAL | Other | Other | 1 | 96 | 0.00042749 | 0.00044445 | N
16/03/2017 | 10:55 | 813:89055 | SHORT RURAL | Other | Other - Arcing | 3 | 80 | 0.0010668 | 0.0013335 | N
20/03/2017 | 13:19 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 86 | 0.00076446 | 0.0008889 | N
20/03/2017 | 18:48 | ZN10999:PA15 | URBAN | Other | Other - Arcing | 1 | 191 | 0.00013189 | 6.8879e-05 | N
20/03/2017 | 19:16 | ZN12600:PA11 | URBAN | Other | Other | 1 | 44 | 3.0111e-05 | 6.8879e-05 | N
21/03/2017 | 09:34 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 116 | 0.0015467 | 0.0013334 | N
21/03/2017 | 09:35 | 504:48028 | URBAN | Other | Other | 1 | 69 | 4.7791e-05 | 6.8879e-05 | N
21/03/2017 | 09:57 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 1 | 153 | 0.00010526 | 6.8879e-05 | N
21/03/2017 | 12:35 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 115 | 0.041016 | 0.035676 | N
21/03/2017 | 15:50 | 528:83014 | SHORT RURAL | Other | Other | 1 | 204 | 0.00090839 | 0.00044446 | N
21/03/2017 | 19:47 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 93 | 0.0037394 | 0.0040001 | N
21/03/2017 | 20:24 | 516:48065 | SHORT RURAL | Other | Other - Self Clearing Trigger | 34 | 167 | 0.02521 | 0.015112 | N
22/03/2017 | 00:18 | ZN9900:PA13 | URBAN | Other | Other - Self Clearing Trigger | 43 | 112 | 0.0033079 | 0.0029619 | N
22/03/2017 | 06:49 | ZN35400:PA79 | URBAN | Other | Other - Self Clearing Trigger | 20 | 331 | 0.0045599 | 0.0013776 | N
22/03/2017 | 06:56 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 59 | 0.0015734 | 0.0026668 | N
21/03/2017 | 07:00 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 308 | 0.0013689 | 0.00044446 | N
22/03/2017 | 08:55 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 55 | 0.0029335 | 0.0053336 | N
22/03/2017 | 10:05 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 220 | 0.00097783 | 0.00044447 | N
22/03/2017 | 10:19 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 131 | 0.0029113 | 0.0022224 | N
22/03/2017 | 14:50 | ZN2835:PA9 | URBAN | Other | Other - Self Clearing Trigger | 137 | 190 | 0.017894 | 0.0094367 | N
22/03/2017 | 14:02 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 112 | 0.0099754 | 0.0088894 | N
22/03/2017 | 14:49 | 258:80779 | URBAN | Other | Other | 1 | 100 | 6.8904e-05 | 6.8881e-05 | N
22/03/2017 | 16:01 | ZN12690:PA16 | SHORT RURAL | Other | Other | 1 | 84 | 0.00037454 | 0.00044447 | N
22/03/2017 | 16:27 | ZN2400:PA21 | URBAN | Other | Other - Self Clearing Trigger | 658 | 158 | 0.071611 | 0.045324 | N
22/03/2017 | 16:35 | ZN129:PA28 | URBAN | Other | Other - Self Clearing Trigger | 32 | 174 | 0.0038353 | 0.0022042 | N
22/03/2017 | 16:16 | ZN129:PA39 | URBAN | Other | Other - Self Clearing Trigger | 40 | 193 | 0.0053176 | 0.0027552 | N
22/03/2017 | 16:54 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 24 | 55 | 0.47181 | 0.85653 | N
22/03/2017 | 17:25 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 65 | 0.00028728 | 0.00044447 | N
22/03/2017 | 17:30 | ZN7481:PA1 | URBAN | Other | Other - Self Clearing Trigger | 43 | 199 | 0.0058966 | 0.0029619 | N
22/03/2017 | 17:28 | ZN12630:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 566 | 9 | 0.022641 | 0.25157 | N
22/03/2017 | 17:28 | ZN12630:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 322 | 9 | 0.012881 | 0.14312 | N
22/03/2017 | 17:28 | ZN12630:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 238 | 9 | 0.0095206 | 0.10578 | N
22/03/2017 | 17:28 | ZN12630:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 94 | 9 | 0.0037602 | 0.04178 | N
22/03/2017 | 17:28 | ZN12630:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 415 | 9 | 0.016601 | 0.18446 | N
22/03/2017 | 17:28 | ZN12630:PA6 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 9 | 0.00028002 | 0.0031113 | N
22/03/2017 | 17:28 | ZN12630:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 374 | 9 | 0.014961 | 0.16623 | N
22/03/2017 | 21:02 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 43 | 0.046039 | 0.10707 | N
22/03/2017 | 23:04 | ZN3425:PA30 | URBAN | Other | Other - Self Clearing Trigger | 92 | 76 | 0.0048077 | 0.006337 | N
23/03/2017 | 05:44 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 131 | 0.004077 | 0.0031122 | N
23/03/2017 | 06:48 | ZN12660:PA14 | SHORT RURAL | Other | Other | 1 | 127 | 0.00056591 | 0.0004446 | N
23/03/2017 | 12:57 | ZN2400:PA21 | URBAN | Other | Other | 1 | 363 | 0.00024975 | 6.8858e-05 | N
21/03/2017 | 19:00 | ZN35370:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 30 | 0.00066668 | 0.0022223 | N
23/03/2017 | 16:40 | ZN10996:PA19 | URBAN | Other | Other - Arcing | 1 | 170 | 0.00011694 | 6.8858e-05 | N
23/03/2017 | 18:44 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 109 | 0.00048462 | 0.0004446 | N
23/03/2017 | 21:57 | ZN12600:PA2 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 58 | 0.00051248 | 0.00088921 | N
24/03/2017 | 03:40 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 255 | 0.0011337 | 0.00044461 | N
24/03/2017 | 04:09 | ZN9550:PA42 | URBAN | Other | Other - Self Clearing Trigger | 1,015 | 68 | 0.047833 | 0.069892 | N
24/03/2017 | 08:17 | 224:80332 | URBAN | Other | Other | 1 | 320 | 0.00022044 | 6.8859e-05 | N
24/03/2017 | 09:20 | 528:83022 | URBAN | Other | Other - Arcing | 15 | 189 | 0.0019523 | 0.0010329 | N
24/03/2017 | 10:14 | ZN2835:PA9 | URBAN | Other | Other - Self Clearing Trigger | 90 | 114 | 0.0070641 | 0.0061973 | N
24/03/2017 | 14:19 | ZN1850:PA10 | URBAN | Other | Other - Arcing | 1 | 71 | 4.8718e-05 | 6.8859e-05 | N
25/03/2017 | 15:30 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 49 | 0.00021794 | 0.00044462 | N
25/03/2017 | 18:18 | 224:80337 | SHORT RURAL | Other | Other | 1 | 56 | 0.00025025 | 0.00044462 | N
25/03/2017 | 18:48 | ZN15006:PA13 | URBAN | Other | Other | 1 | 112 | 7.7405e-05 | 6.8855e-05 | N
26/03/2017 | 05:52 | ZN9900:PA13 | URBAN | Other | Other - Self Clearing Trigger | 22 | 117 | 0.0017757 | 0.0015149 | N
26/03/2017 | 19:56 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 124 | 0.0011007 | 0.00088767 | N
27/03/2017 | 06:28 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 102 | 0.0049798 | 0.0048822 | N
27/03/2017 | 08:36 | ZN12580:PA4 | URBAN | Other | Other | 1 | 20 | 1.3829e-05 | 6.8857e-05 | N
27/03/2017 | 08:47 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 97 | 0.034672 | 0.035689 | N
22/03/2017 | 10:05 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 205 | 0.0018223 | 0.00088894 | N
28/03/2017 | 11:27 | ZN3922:PA22 | URBAN | Other | Other - Self Clearing Trigger | 68 | 193 | 0.0090346 | 0.0046823 | N
28/03/2017 | 19:02 | ZN7900:PA23 | URBAN | Other | Other - Self Clearing Trigger | 7 | 153 | 0.00073747 | 0.00048201 | N
28/03/2017 | 19:02 | ZN901:PA17 | URBAN | Other | Other - Self Clearing Trigger | 2 | 153 | 0.00021022 | 0.00013772 | N
28/03/2017 | 23:16 | ZN35600:PA3 | URBAN | Other | Other | 1 | 13 | 9.1466e-06 | 6.8858e-05 | N
29/03/2017 | 14:00 | 502:48004 | URBAN | Other | Other - Arcing | 1 | 295 | 0.00020303 | 6.886e-05 | N
29/03/2017 | 15:48 | ZN9900:PA8 | URBAN | Other | Other | 1 | 62 | 4.2521e-05 | 6.886e-05 | N
29/03/2017 | 15:51 | ZN72:PA16 | URBAN | Other | Other - Self Clearing Trigger | 51 | 49 | 0.0017073 | 0.0035118 | N
29/03/2017 | 19:24 | ZN35800:PA6 | URBAN | Other | Other - Self Clearing Trigger | 136 | 126 | 0.0118 | 0.0093649 | N
29/03/2017 | 20:11 | ZN14891:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,415 | 124 | 0.78028 | 0.62804 | N
29/03/2017 | 23:00 | 238:34148 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 120 | 0.0042609 | 0.0035508 | N
30/03/2017 | 08:59 | ZN965:PA6 | URBAN | Other | Other - Arcing | 1 | 336 | 0.00023098 | 6.8836e-05 | N
30/03/2017 | 09:22 | ZN80:PA31 | URBAN | Other | Other - Arcing | 1 | 218 | 0.00014979 | 6.8836e-05 | N
30/03/2017 | 09:43 | ZN15004:PA9 | URBAN | Other | Other - Arcing | 1 | 197 | 0.00013549 | 6.8836e-05 | N
30/03/2017 | 11:13 | 223:14395 | SHORT RURAL | Other | Other | 1 | 51 | 0.00022681 | 0.00044356 | N
30/03/2017 | 11:39 | ZN12690:PA8 | SHORT RURAL | Other | Other | 1 | 82 | 0.00036409 | 0.00044356 | N
30/03/2017 | 11:47 | ZN12690:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 162 | 0.0007202 | 0.00044356 | N
30/03/2017 | 11:50 | ZN12690:PA8 | SHORT RURAL | Other | Other | 1 | 72 | 0.00031936 | 0.00044356 | N
30/03/2017 | 11:54 | ZN12690:PA8 | SHORT RURAL | Other | Other | 1 | 68 | 0.00030073 | 0.00044356 | N
30/03/2017 | 12:34 | ZN1287:PA21 | URBAN | Other | Other - Arcing | 1 | 447 | 0.000308 | 6.8836e-05 | N
30/03/2017 | 17:51 | ZN36100:PA12 | URBAN | Other | Other - Arcing | 2 | 398 | 0.00054812 | 0.00013767 | N
30/03/2017 | 20:12 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 1 | 348 | 0.00023955 | 6.8836e-05 | N
30/03/2017 | 23:06 | 261:81885 | URBAN | Other | Other - Arcing | 1 | 234 | 0.00016103 | 6.8836e-05 | N
31/03/2017 | 02:23 | ZN9245:PA1 | URBAN | Other | Other - Self Clearing Trigger | 1,081 | 113 | 0.08396 | 0.074416 | N
31/03/2017 | 06:30 | 258:80791 | URBAN | Other | Other | 1 | 154 | 0.000106 | 6.884e-05 | N
31/03/2017 | 12:31 | 261:81879 | URBAN | Other | Other | 1 | 231 | 0.00015869 | 6.884e-05 | N
31/03/2017 | 12:56 | 524:33572 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 46 | 0.00040808 | 0.00088712 | N
31/03/2017 | 20:08 | 205:12205 | SHORT RURAL | Other | Other - Arcing | 1 | 230 | 0.0010223 | 0.00044356 | N
31/03/2017 | 23:53 | ZN262:PA6 | URBAN | Other | Other - Arcing | 1 | 636 | 0.00043799 | 6.884e-05 | N
01/04/2017 | 14:27 | 242:81541 | URBAN | Other | Other | 1 | 153 | 0.00010499 | 6.8798e-05 | N
01/04/2017 | 17:09 | ZN2602:PA3 | URBAN | Other | Other - Self Clearing Trigger | 48 | 141 | 0.0046431 | 0.0033023 | N
02/04/2017 | 06:51 | 261:81870 | URBAN | Other | Other - Arcing | 1 | 189 | 0.00012998 | 6.8806e-05 | N
02/04/2017 | 09:22 | ZN12640:PA13 | SHORT RURAL | Other | Other - Arcing | 1 | 292 | 0.0013011 | 0.00044531 | N
02/04/2017 | 10:22 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 98 | 0.035 | 0.035714 | N
02/04/2017 | 12:16 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 59 | 0.021071 | 0.035714 | N
02/04/2017 | 16:48 | ZN1287:PA11 | URBAN | Other | Other - Arcing | 1 | 1,122 | 0.00077193 | 6.8806e-05 | N
03/04/2017 | 07:17 | ZN167:PA11 | URBAN | Other | Other - Self Clearing Trigger | 3 | 191 | 0.00039426 | 0.00020642 | N
03/04/2017 | 07:50 | ZN12640:PA8 | URBAN | Other | Other - Arcing | 1 | 249 | 0.00017151 | 6.8806e-05 | N
03/04/2017 | 09:23 | ZN12610:PA10 | URBAN | Other | Other | 1 | 50 | 3.4128e-05 | 6.8806e-05 | N
31/03/2017 | 13:45 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 70 | 0.00062099 | 0.00088712 | N
03/04/2017 | 14:50 | ZN12640:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 13 | 170 | 0.0098414 | 0.005789 | N
03/04/2017 | 15:21 | 532:83307 | SHORT RURAL | Other | Other | 1 | 80 | 0.00035669 | 0.00044531 | N
03/04/2017 | 17:51 | ZN14891:PA16 | SHORT RURAL | Other | Other | 1 | 53 | 0.00023498 | 0.00044531 | N
03/04/2017 | 12:00 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 110 | 0.00097968 | 0.00089062 | N
04/04/2017 | 08:32 | 222:33601 | SHORT RURAL | Other | Other | 1 | 182 | 0.00081151 | 0.00044531 | N
04/04/2017 | 11:13 | ZN12610:PA6 | URBAN | Other | Other | 1 | 65 | 4.4759e-05 | 6.8807e-05 | N
04/04/2017 | 13:43 | ZN2568:PA27 | URBAN | Other | Other - Arcing | 1 | 106 | 7.3027e-05 | 6.8807e-05 | N
04/04/2017 | 16:16 | 511:29878 | SHORT RURAL | Other | Other | 1 | 74 | 0.00032938 | 0.00044531 | N
04/04/2017 | 19:40 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 279 | 0.0012442 | 0.00044531 | N
05/04/2017 | 05:00 | ZN9900:PA5 | URBAN | Other | Other - Self Clearing Trigger | 35 | 269 | 0.0064822 | 0.0024082 | N
05/04/2017 | 06:18 | ZN2196:PA25 | URBAN | Other | Other - Arcing | 1 | 192 | 0.0001321 | 6.8807e-05 | N
05/04/2017 | 11:52 | ZN15006:PA13 | URBAN | Other | Other - Self Clearing Trigger | 34 | 113 | 0.0026525 | 0.0023394 | N
05/04/2017 | 20:32 | ZN12620:PA13 | SHORT RURAL | Other | Other | 1 | 62 | 0.00027632 | 0.00044531 | N
05/04/2017 | 21:14 | 223:14397 | URBAN | Other | Other - Self Clearing Trigger | 54 | 56 | 0.0020807 | 0.0037156 | N
06/04/2017 | 11:21 | 508:82575 | SHORT RURAL | Other | Other | 1 | 78 | 0.00034571 | 0.00044531 | N
06/04/2017 | 11:42 | 222:33600 | URBAN | Other | Other | 1 | 43 | 2.938e-05 | 6.8807e-05 | N
06/04/2017 | 14:41 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 88 | 0.0003938 | 0.00044531 | N
06/04/2017 | 16:55 | ZN12610:PA16 | SHORT RURAL | Other | Other | 1 | 110 | 0.00048843 | 0.00044531 | N
06/04/2017 | 13:28 | ZN9534:PA18 | URBAN | Other | Other - Self Clearing Trigger | 4 | 73 | 0.00020092 | 0.00027523 | N
07/04/2017 | 08:48 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 107 | 0.00047651 | 0.00044534 | N
07/04/2017 | 14:12 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 407 | 0.0018128 | 0.00044534 | N
08/04/2017 | 17:21 | 232:11457 | SHORT RURAL | Other | Other - Self Clearing Trigger | 109 | 87 | 0.04228 | 0.048542 | N
08/04/2017 | 23:03 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 141 | 0.011288 | 0.0080161 | N
09/04/2017 | 10:58 | ZN1290:PA12 | URBAN | Other | Other - Arcing | 1 | 420 | 0.00028864 | 6.878e-05 | N
09/04/2017 | 11:36 | ZN12630:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 68 | 130 | 0.039448 | 0.030283 | N
09/04/2017 | 12:02 | ZN12630:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 13 | 22 | 0.0012603 | 0.0057895 | N
09/04/2017 | 18:08 | ZN10999:PA11 | URBAN | Other | Other - Self Clearing Trigger | 43 | 182 | 0.0053697 | 0.0029575 | N
09/04/2017 | 18:09 | ZN4545:PA44 | URBAN | Other | Other | 1 | 146 | 0.0001005 | 6.878e-05 | N
09/04/2017 | 18:55 | ZN690:PA33 | URBAN | Other | Other - Self Clearing Trigger | 37 | 315 | 0.0080163 | 0.0025449 | N
09/04/2017 | 19:49 | ZN72:PA26 | URBAN | Other | Other - Arcing | 1 | 851 | 0.0005852 | 6.878e-05 | N
09/04/2017 | 22:19 | ZN2400:PA21 | URBAN | Other | Other - Self Clearing Trigger | 1 | 126 | 8.6663e-05 | 6.878e-05 | N
10/04/2017 | 16:23 | ZN12620:PA1 | SHORT RURAL | Other | Other - Arcing | 1 | 157 | 0.00069889 | 0.00044534 | N
10/04/2017 | 19:52 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 98 | 0.00087287 | 0.00089069 | N
11/04/2017 | 11:09 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 137 | 0.00061153 | 0.00044534 | N
11/04/2017 | 12:04 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 82 | 0.00036696 | 0.00044534 | N
11/04/2017 | 12:43 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 67 | 0.00029719 | 0.00044534 | N
11/04/2017 | 15:25 | 240:34835 | SHORT RURAL | Other | Other | 1 | 176 | 0.00078514 | 0.00044534 | N
11/04/2017 | 21:21 | ZN15004:PA3 | URBAN | Other | Other - Arcing | 1 | 139 | 9.549e-05 | 6.878e-05 | N
11/04/2017 | 22:18 | ZN5868:PA27 | URBAN | Other | Other - Self Clearing Trigger | 62 | 136 | 0.0058074 | 0.0042644 | N
12/04/2017 | 08:23 | 224:80341 | URBAN | Other | Other | 1 | 102 | 6.983e-05 | 6.8787e-05 | N
12/04/2017 | 21:05 | ZN1673:PA18 | URBAN | Other | Other - Arcing | 1 | 175 | 0.00012022 | 6.8787e-05 | N
12/04/2017 | 22:46 | ZN10999:PA25 | URBAN | Other | Other - Arcing | 2 | 858 | 0.0011803 | 0.00013757 | N
13/04/2017 | 00:07 | ZN35800:PA15 | URBAN | Other | Other - Arcing | 1 | 251 | 0.00017269 | 6.8788e-05 | N
13/04/2017 | 03:42 | ZN9245:PA21 | URBAN | Other | Other - Arcing | 1 | 437 | 0.00030072 | 6.8788e-05 | N
13/04/2017 | 11:48 | ZN129:PA9 | URBAN | Other | Other | 1 | 89 | 6.1095e-05 | 6.8788e-05 | N
14/04/2017 | 13:33 | 214:8665 | URBAN | Other | Other | 1 | 67 | 4.5964e-05 | 6.8809e-05 | N
14/04/2017 | 13:56 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 74 | 0.052838 | 0.071403 | N
14/04/2017 | 14:07 | ZN35370:PA2 | SHORT RURAL | Other | Other - Self Clearing Trigger | 19 | 133 | 0.011252 | 0.0084602 | N
14/04/2017 | 16:08 | 229:34995 | SHORT RURAL | Other | Other | 1 | 87 | 0.00038687 | 0.00044527 | N
14/04/2017 | 21:24 | ZN15002:PA6 | URBAN | Other | Other - Self Clearing Trigger | 43 | 95 | 0.0028168 | 0.0029588 | N
15/04/2017 | 10:01 | ZN12580:PA16 | URBAN | Other | Other | 1 | 108 | 7.4427e-05 | 6.8765e-05 | N
15/04/2017 | 20:00 | ZN2400:PA26 | URBAN | Other | Other - Arcing | 1 | 110 | 7.5837e-05 | 6.8765e-05 | N
16/04/2017 | 10:28 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 47 | 0.016762 | 0.035702 | N
16/04/2017 | 12:33 | ZN1290:PA8 | URBAN | Other | Other | 1 | 115 | 7.9001e-05 | 6.8766e-05 | N
17/04/2017 | 07:00 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 65 | 0.0011577 | 0.0017811 | N
17/04/2017 | 11:54 | 240:34849 | SHORT RURAL | Other | Other | 1 | 43 | 0.0001914 | 0.00044528 | N
17/04/2017 | 13:18 | ZN36200:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 17 | 172 | 0.01302 | 0.0075698 | N
13/04/2017 | 12:00 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 70 | 0.049982 | 0.071403 | N
18/04/2017 | 08:51 | ZN195:PA29 | URBAN | Other | Other - Arcing | 61 | 162 | 0.0067801 | 0.0041947 | N
18/04/2017 | 14:47 | 232:11457 | SHORT RURAL | Other | Other | 1 | 130 | 0.00057909 | 0.00044528 | N
15/03/2017 | 12:04 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 221 | 0.00098268 | 0.00044465 | N
19/04/2017 | 07:21 | ZN965:PA8 | URBAN | Other | Other - Self Clearing Trigger | 22 | 60 | 0.0009113 | 0.0015129 | N
19/04/2017 | 08:31 | ZN14892:PA8 | SHORT RURAL | Other | Other | 1 | 76 | 0.00033975 | 0.00044529 | N
19/04/2017 | 08:53 | ZN12690:PA16 | SHORT RURAL | Other | Other | 1 | 106 | 0.00047237 | 0.00044529 | N
19/04/2017 | 11:35 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 49 | 0.00043638 | 0.00089057 | N
19/04/2017 | 13:36 | ZN9118:PA11 | URBAN | Other | Other - Self Clearing Trigger | 75 | 69 | 0.0035494 | 0.0051578 | N
19/04/2017 | 20:07 | ZN8000:PA4 | URBAN | Other | Other | 1 | 63 | 4.3279e-05 | 6.877e-05 | N
20/04/2017 | 06:51 | 203:8088 | URBAN | Other | Other | 1 | 93 | 6.3995e-05 | 6.8799e-05 | N
20/04/2017 | 07:12 | 203:8088 | URBAN | Other | Other | 1 | 73 | 5.0189e-05 | 6.8799e-05 | N
20/04/2017 | 19:43 | 507:80932 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 177 | 0.0015701 | 0.00088826 | N
20/04/2017 | 20:28 | ZN2196:PA5 | URBAN | Other | Other - Arcing | 1 | 901 | 0.00062016 | 6.8799e-05 | N
21/04/2017 | 08:22 | 214:8671 | URBAN | Other | Other | 1 | 98 | 6.7138e-05 | 6.88e-05 | N
21/04/2017 | 10:15 | 258:80785 | URBAN | Other | Other | 1 | 89 | 6.1427e-05 | 6.88e-05 | N
21/04/2017 | 15:43 | 220:8689 | URBAN | Other | Other | 1 | 100 | 6.8686e-05 | 6.88e-05 | N
22/04/2017 | 01:05 | ZN9118:PA11 | URBAN | Other | Other - Self Clearing Trigger | 75 | 58 | 0.0029831 | 0.0051581 | N
22/04/2017 | 03:04 | 265:81648 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 122 | 0.00054345 | 0.00044399 | N
22/04/2017 | 06:51 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 84 | 0.00037295 | 0.00044399 | N
22/04/2017 | 19:48 | 222:33600 | URBAN | Other | Other | 1 | 72 | 4.9392e-05 | 6.8775e-05 | N
22/04/2017 | 22:12 | ZN35800:PA14 | URBAN | Other | Other - Arcing | 1 | 915 | 0.0006291 | 6.8775e-05 | N
23/04/2017 | 08:47 | ZN2400:PA21 | URBAN | Other | Other - Arcing | 11 | 367 | 0.0027771 | 0.00075653 | N
23/04/2017 | 11:48 | 224:80329 | SHORT RURAL | Other | Other | 1 | 86 | 0.00038331 | 0.00044399 | N
23/04/2017 | 14:45 | ZN847:PA18 | SHORT RURAL | Other | Other - Arcing | 1 | 82 | 0.000364 | 0.00044399 | N
24/04/2017 | 12:49 | ZN15006:PA6 | URBAN | Other | Other - Arcing | 1 | 71 | 4.8521e-05 | 6.8776e-05 | N
24/04/2017 | 21:07 | ZN12610:PA17 | URBAN | Other | Other - Arcing | 1 | 160 | 0.00011034 | 6.8776e-05 | N
24/04/2017 | 21:22 | 224:80346 | URBAN | Other | Other - Arcing | 1 | 183 | 0.00012561 | 6.8776e-05 | N
24/04/2017 | 23:44 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 66 | 0.00029303 | 0.00044399 | N
25/04/2017 | 06:17 | 216:10728 | SHORT RURAL | Other | Other - Self Clearing Trigger | 56 | 62 | 0.015531 | 0.024864 | N
25/04/2017 | 07:03 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 66 | 0.00029511 | 0.00044399 | N
25/04/2017 | 13:25 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 60 | 35 | 0.0093061 | 0.02664 | N
25/04/2017 | 15:17 | ZN2602:PA4 | URBAN | Other | Other - Arcing | 1 | 282 | 0.0001942 | 6.8776e-05 | N
25/04/2017 | 17:49 | ZN3155:PA23 | URBAN | Other | Other - Arcing | 1 | 490 | 0.00033713 | 6.8776e-05 | N
25/04/2017 | 18:06 | ZN965:PA4 | URBAN | Other | Other - Arcing | 1 | 218 | 0.00015005 | 6.8776e-05 | N
25/04/2017 | 18:15 | ZN3425:PA39 | URBAN | Other | Other - Arcing | 1 | 250 | 0.00017227 | 6.8776e-05 | N
25/04/2017 | 19:53 | ZN1850:PA3 | URBAN | Other | Other - Arcing | 1 | 218 | 0.00015022 | 6.8776e-05 | N
26/04/2017 | 10:31 | ZN3154:PA11 | URBAN | Other | Other | 1 | 131 | 9.0212e-05 | 6.8776e-05 | N
26/04/2017 | 10:46 | ZN14143:PA17 | SHORT RURAL | Other | Other - Self Clearing Trigger | 38 | 156 | 0.0264 | 0.016872 | N
26/04/2017 | 14:52 | ZN690:PA33 | URBAN | Other | Other - Self Clearing Trigger | 37 | 112 | 0.0028603 | 0.0025447 | N
26/04/2017 | 16:02 | ZN35800:PA14 | URBAN | Other | Other - Self Clearing Trigger | 85 | 73 | 0.0042676 | 0.005846 | N
26/04/2017 | 16:03 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 317 | 0.025329 | 0.0079919 | N
26/04/2017 | 18:02 | 526:34641 | SHORT RURAL | Other | Other | 1 | 268 | 0.0011884 | 0.00044399 | N
26/04/2017 | 19:19 | ZN901:PA11 | URBAN | Other | Other - Self Clearing Trigger | 104 | 60 | 0.0043226 | 0.0071528 | N
26/04/2017 | 19:32 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 203 | 0.0081117 | 0.0039959 | N
27/04/2017 | 02:19 | 813:89063 | SHORT RURAL | Other | Other - Self Clearing Trigger | 34 | 285 | 0.04305 | 0.015093 | N
27/04/2017 | 07:48 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 242 | 0.0010743 | 0.00044391 | N
26/04/2017 | 19:00 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 110 | 0.00048839 | 0.00044399 | N
27/04/2017 | 10:54 | ZN12640:PA18 | SHORT RURAL | Other | Other | 1 | 83 | 0.00036837 | 0.00044391 | N
27/04/2017 | 16:03 | 216:10724 | URBAN | Other | Other | 1 | 52 | 3.5698e-05 | 6.876e-05 | N
27/04/2017 | 16:03 | 213:33775 | URBAN | Other | Other | 1 | 51 | 3.5377e-05 | 6.876e-05 | N
27/04/2017 | 20:03 | 210:83465 | URBAN | Other | Other - Self Clearing Trigger | 30 | 46 | 0.00095061 | 0.0020628 | N
29/04/2017 | 13:04 | ZN10995:PA8 | URBAN | Other | Other - Arcing | 1 | 476 | 0.00032712 | 6.8763e-05 | N
30/04/2017 | 07:33 | 261:81879 | URBAN | Other | Other | 1 | 54 | 3.7063e-05 | 6.8762e-05 | N
30/04/2017 | 09:23 | 210:83466 | URBAN | Other | Other | 1 | 36 | 2.5029e-05 | 6.8762e-05 | N
30/04/2017 | 09:29 | 507:80925 | SHORT RURAL | Other | Other | 1 | 116 | 0.00051417 | 0.00044389 | N
01/05/2017 | 08:26 | ZN195:PA29 | URBAN | Other | Other - Arcing | 1 | 354 | 0.00024333 | 6.8762e-05 | N
01/05/2017 | 10:06 | 813:89058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 64 | 0.00028409 | 0.00044389 | N
01/05/2017 | 12:56 | 813:89065 | URBAN | Other | Other - Self Clearing Trigger | 22 | 94 | 0.0014172 | 0.0015128 | N
01/05/2017 | 14:47 | 511:29874 | URBAN | Other | Other | 1 | 121 | 8.3122e-05 | 6.8762e-05 | N
01/05/2017 | 08:15 | 257:82006 | URBAN | Other | Other - Self Clearing Trigger | 135 | 505 | 0.046879 | 0.0092829 | N
02/05/2017 | 10:24 | 239:82133 | URBAN | Other | Other | 1 | 91 | 6.2392e-05 | 6.8765e-05 | N
02/05/2017 | 20:17 | ZN630:PA38 | URBAN | Other | Other | 1 | 163 | 0.00011201 | 6.8765e-05 | N
03/05/2017 | 02:06 | ZN3672:PA29 | URBAN | Other | Other - Arcing | 1 | 234 | 0.0001607 | 6.8767e-05 | N
03/05/2017 | 08:38 | 217:33612 | URBAN | Other | Other - Arcing | 1 | 181 | 0.0001245 | 6.8767e-05 | N
03/05/2017 | 12:28 | ZN2400:PA26 | URBAN | Other | Other - Self Clearing Trigger | 57 | 138 | 0.0054125 | 0.0039197 | N
03/05/2017 | 13:42 | ZN262:PA15 | URBAN | Other | Other - Arcing | 1 | 317 | 0.0002182 | 6.8767e-05 | N
03/05/2017 | 14:52 | ZN9252:PA27 | URBAN | Other | Other - Arcing | 1 | 277 | 0.00019074 | 6.8767e-05 | N
03/05/2017 | 14:52 | ZN10991:PA5 | URBAN | Other | Other | 1 | 125 | 8.62e-05 | 6.8767e-05 | N
03/05/2017 | 15:15 | ZN2196:PA21 | URBAN | Other | Other - Arcing | 1 | 352 | 0.00024203 | 6.8767e-05 | N
03/05/2017 | 15:24 | ZN4545:PA27 | URBAN | Other | Other - Arcing | 1 | 156 | 0.00010715 | 6.8767e-05 | N
03/05/2017 | 18:03 | 812:19071 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 224 | 0.00099514 | 0.0004439 | N
03/05/2017 | 18:22 | ZN14144:PA5 | SHORT RURAL | Other | Other | 1 | 111 | 0.00049065 | 0.0004439 | N
03/05/2017 | 20:33 | ZN10999:PA12 | URBAN | Other | Other - Arcing | 1 | 147 | 0.00010093 | 6.8767e-05 | N
04/05/2017 | 06:25 | ZN9118:PA11 | URBAN | Other | Other - Self Clearing Trigger | 75 | 79 | 0.0040985 | 0.0051564 | N
05/05/2017 | 11:42 | ZN3425:PA22 | URBAN | Other | Other - Self Clearing Trigger | 38 | 38 | 0.00099365 | 0.002616 | N
05/05/2017 | 13:06 | ZN12610:PA23 | URBAN | Other | Other - Self Clearing Trigger | 30 | 109 | 0.0022474 | 0.0020653 | N
05/05/2017 | 20:26 | ZN10999:PA29 | URBAN | Other | Other - Arcing | 1 | 93 | 6.4287e-05 | 6.8843e-05 | N
05/05/2017 | 23:45 | 511:29876 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 109 | 0.0058051 | 0.0053258 | N
06/05/2017 | 08:17 | 220:8689 | URBAN | Other | Other | 1 | 72 | 4.9644e-05 | 6.8759e-05 | N
06/05/2017 | 09:35 | 801:74123 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 132 | 0.0017575 | 0.0013314 | N
06/05/2017 | 12:53 | ZN3155:PA16 | URBAN | Other | Other - Self Clearing Trigger | 29 | 141 | 0.0028136 | 0.001994 | N
06/05/2017 | 23:57 | ZN12640:PA7 | URBAN | Other | Other - Self Clearing Trigger | 51 | 63 | 0.0022092 | 0.0035067 | N
07/05/2017 | 05:21 | 206:34437 | SHORT RURAL | Other | Other - Self Clearing Trigger | 14 | 169 | 0.010519 | 0.0062241 | N
07/05/2017 | 11:14 | ZN398:PA11 | URBAN | Other | Other - Arcing | 1 | 106 | 7.2837e-05 | 6.8747e-05 | N
07/05/2017 | 16:18 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 77 | 0.00068465 | 0.00088916 | N
08/05/2017 | 12:53 | 258:80784 | URBAN | Other | Other | 1 | 44 | 3.0134e-05 | 6.8747e-05 | N
08/05/2017 | 17:26 | 509:33399 | SHORT RURAL | Other | Other | 1 | 69 | 0.00030743 | 0.00044458 | N
09/05/2017 | 08:45 | 214:8669 | URBAN | Other | Other | 1 | 43 | 2.9413e-05 | 6.8749e-05 | N
09/05/2017 | 11:10 | 258:80779 | URBAN | Other | Other | 1 | 54 | 3.7262e-05 | 6.8749e-05 | N
09/05/2017 | 11:45 | 243:80080 | SHORT RURAL | Other | Other | 1 | 72 | 0.00032032 | 0.00044458 | N
10/05/2017 | 06:30 | ZN9037:PA10 | URBAN | Other | Other - Arcing | 1 | 329 | 0.00022642 | 6.875e-05 | N
10/05/2017 | 09:48 | ZN3154:PA4 | URBAN | Other | Other - Self Clearing Trigger | 14 | 314 | 0.0030223 | 0.0009625 | N
10/05/2017 | 10:55 | 504:48031 | SHORT RURAL | Other | Other | 1 | 384 | 0.0017087 | 0.00044459 | N
10/05/2017 | 10:57 | 532:83309 | SHORT RURAL | Other | Other - Arcing | 1 | 195 | 0.00086903 | 0.00044459 | N
11/05/2017 | 00:13 | ZN15001:PA13 | URBAN | Other | Other - Self Clearing Trigger | 91 | 32 | 0.0020035 | 0.006261 | N
11/05/2017 | 00:13 | ZN15001:PA15 | URBAN | Other | Other - Self Clearing Trigger | 2,854 | 32 | 0.062836 | 0.19636 | N
11/05/2017 | 00:13 | ZN15001:PA16 | URBAN | Other | Other - Self Clearing Trigger | 538 | 32 | 0.011845 | 0.037016 | N
11/05/2017 | 00:13 | ZN15001:PA17 | URBAN | Other | Other - Self Clearing Trigger | 2 | 32 | 4.4034e-05 | 0.0001376 | N
11/05/2017 | 00:13 | ZN15001:PA18 | URBAN | Other | Other - Self Clearing Trigger | 2,356 | 32 | 0.051872 | 0.1621 | N
11/05/2017 | 13:57 | 206:34434 | URBAN | Other | Other | 1 | 62 | 4.2887e-05 | 6.8802e-05 | N
11/05/2017 | 15:12 | ZN12630:PA3 | SHORT RURAL | Other | Other | 1 | 109 | 0.00048628 | 0.00044443 | N
12/05/2017 | 18:37 | 270:83590 | URBAN | Other | Other | 1 | 58 | 3.9649e-05 | 6.8776e-05 | N
13/05/2017 | 10:40 | 238:34141 | SHORT RURAL | Other | Other | 1 | 148 | 0.00065934 | 0.0004444 | N
13/05/2017 | 16:03 | ZN12640:PA2 | URBAN | Other | Other | 1 | 115 | 7.8942e-05 | 6.8735e-05 | N
13/05/2017 | 21:46 | ZN15008:PA10 | URBAN | Other | Other - Self Clearing Trigger | 89 | 104 | 0.0063519 | 0.0061174 | N
14/05/2017 | 11:18 | ZN15005:PA6 | URBAN | Other | Other - Arcing | 1 | 169 | 0.00011582 | 6.8735e-05 | N
14/05/2017 | 12:44 | 507:80922 | SHORT RURAL | Other | Other | 1 | 92 | 0.00040759 | 0.0004444 | N
14/05/2017 | 17:19 | ZN35800:PA15 | URBAN | Other | Other - Arcing | 1 | 307 | 0.00021116 | 6.8735e-05 | N
14/05/2017 | 20:33 | 532:83309 | SHORT RURAL | Other | Other - Arcing | 1 | 305 | 0.0013545 | 0.0004444 | N
14/05/2017 | 22:36 | 224:80326 | SHORT RURAL | Other | Other - Arcing | 1 | 173 | 0.00076992 | 0.0004444 | N
15/05/2017 | 17:25 | ZN4545:PA36 | URBAN | Other | Other - Arcing | 1 | 229 | 0.00015771 | 6.8735e-05 | N
15/05/2017 | 20:25 | ZN36300:PA11 | URBAN | Other | Other - Self Clearing Trigger | 43 | 49 | 0.0014502 | 0.0029556 | N
16/05/2017 | 09:55 | ZN12640:PA8 | URBAN | Other | Other | 1 | 60 | 4.1562e-05 | 6.8736e-05 | N
16/05/2017 | 11:34 | 233:82815 | SHORT RURAL | Other | Other | 1 | 36 | 0.00015999 | 0.0004444 | N
16/05/2017 | 14:07 | 802:82220 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 111 | 0.00049329 | 0.0004444 | N
16/05/2017 | 14:15 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 185 | 0.0016443 | 0.00088881 | N
16/05/2017 | 14:47 | ZN9900:PA5 | URBAN | Other | Other - Self Clearing Trigger | 35 | 202 | 0.0048676 | 0.0024057 | N
16/05/2017 | 22:09 | ZN4545:PA31 | URBAN | Other | Other - Self Clearing Trigger | 64 | 41 | 0.0018036 | 0.0043991 | N
17/05/2017 | 07:37 | ZN2568:PA9 | URBAN | Other | Other | 1 | 146 | 0.00010038 | 6.8736e-05 | N
17/05/2017 | 09:38 | ZN12570:PA24 | SHORT RURAL | Other | Other | 1 | 52 | 0.00023198 | 0.00044441 | N
17/05/2017 | 10:33 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 101 | 0.0361 | 0.035702 | N
17/05/2017 | 15:27 | ZN14144:PA8 | URBAN | Other | Other | 1 | 52 | 3.5766e-05 | 6.8736e-05 | N
17/05/2017 | 16:45 | ZN1285:PA8 | URBAN | Other | Other | 1 | 69 | 4.7497e-05 | 6.8736e-05 | N
17/05/2017 | 16:46 | ZN36800:PA40 | URBAN | Other | Other | 1 | 96 | 6.57e-05 | 6.8736e-05 | N
18/05/2017 | 04:53 | ZN262:PA34 | URBAN | Other | Other - Self Clearing Trigger | 12 | 112 | 0.00092356 | 0.00082461 | N
18/05/2017 | 09:38 | 227:13015 | SHORT RURAL | Other | Other | 1 | 121 | 0.00053808 | 0.00044427 | N
18/05/2017 | 11:41 | 202:34249 | URBAN | Other | Other | 1 | 94 | 6.4766e-05 | 6.8717e-05 | N
18/05/2017 | 13:02 | ZN12630:PA3 | SHORT RURAL | Other | Other | 1 | 84 | 0.00037444 | 0.00044427 | N
18/05/2017 | 16:18 | 224:80346 | URBAN | Other | Other | 1 | 131 | 9.0191e-05 | 6.8717e-05 | N
18/05/2017 | 16:35 | 230:81440 | SHORT RURAL | Other | Other | 1 | 24 | 0.00010744 | 0.00044427 | N
19/05/2017 | 08:00 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 115 | 0.041027 | 0.035676 | N
19/05/2017 | 09:04 | ZN2568:PA22 | URBAN | Other | Other - Arcing | 1 | 145 | 9.9739e-05 | 6.8723e-05 | N
19/05/2017 | 10:38 | 507:80922 | SHORT RURAL | Other | Other | 1 | 188 | 0.00084329 | 0.00044761 | N
19/05/2017 | 14:18 | 814:82283 | SHORT RURAL | Other | Other - Arcing | 1 | 269 | 0.0012032 | 0.00044761 | N
19/05/2017 | 14:29 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 73 | 229 | 5.9761 | 2.6044 | N
19/05/2017 | 16:08 | ZN690:PA10 | URBAN | Other | Other - Arcing | 1 | 285 | 0.00019588 | 6.8723e-05 | N
19/05/2017 | 16:59 | ZN4545:PA17 | URBAN | Other | Other - Arcing | 1 | 91 | 6.248e-05 | 6.8723e-05 | N
19/05/2017 | 20:21 | ZN14891:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 339 | 0.0015151 | 0.00044761 | N
19/05/2017 | 22:52 | ZN4545:PA17 | URBAN | Other | Other - Arcing | 1 | 308 | 0.00021138 | 6.8723e-05 | N
19/05/2017 | 23:07 | ZN1285:PA24 | URBAN | Other | Other - Arcing | 1 | 148 | 0.00010142 | 6.8723e-05 | N
20/05/2017 | 06:07 | ZN847:PA45 | SHORT RURAL | Other | Other - Arcing | 1 | 314 | 0.0014067 | 0.00044761 | N
20/05/2017 | 10:36 | ZN2835:PA30 | URBAN | Other | Other - Self Clearing Trigger | 42 | 73 | 0.0021171 | 0.0028863 | N
20/05/2017 | 11:38 | ZN10997:PA1 | URBAN | Other | Other - Arcing | 1 | 341 | 0.00023416 | 6.8723e-05 | N
20/05/2017 | 14:55 | ZN12600:PA3 | URBAN | Other | Other - Self Clearing Trigger | 29 | 84 | 0.0016831 | 0.001993 | N
20/05/2017 | 16:31 | ZN3155:PA34 | URBAN | Other | Other | 1 | 186 | 0.00012764 | 6.8723e-05 | N
21/05/2017 | 09:24 | ZN12640:PA16 | URBAN | Other | Other - Arcing | 1 | 215 | 0.00014778 | 6.8723e-05 | N
21/05/2017 | 15:23 | ZN8100:PA2 | URBAN | Other | Other | 1 | 180 | 0.00012379 | 6.8723e-05 | N
21/05/2017 | 17:48 | ZN12640:PA7 | URBAN | Other | Other | 1 | 149 | 0.00010222 | 6.8723e-05 | N
22/05/2017 | 04:51 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 89 | 0.00079674 | 0.00089521 | N
22/05/2017 | 09:05 | 210:83465 | URBAN | Other | Other | 1 | 155 | 0.00010637 | 6.8723e-05 | N
22/05/2017 | 22:13 | ZN3472:PA29 | URBAN | Other | Other - Arcing | 1 | 646 | 0.00044411 | 6.8723e-05 | N
23/05/2017 | 08:07 | 508:82574 | SHORT RURAL | Other | Other | 1 | 128 | 0.00057271 | 0.00044761 | N
23/05/2017 | 09:10 | ZN3155:PA44 | URBAN | Other | Other | 1 | 310 | 0.00021329 | 6.8723e-05 | N
23/05/2017 | 16:00 | 507:80922 | SHORT RURAL | Other | Other | 1 | 129 | 0.00057786 | 0.00044761 | N
23/05/2017 | 23:20 | ZN2835:PA10 | URBAN | Other | Other - Self Clearing Trigger | 47 | 30 | 0.00096899 | 0.00323 | N
24/05/2017 | 05:55 | 504:48033 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 120 | 0.0048341 | 0.0040284 | N
24/05/2017 | 05:55 | 504:48033 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 160 | 0.0021485 | 0.0013428 | N
24/05/2017 | 08:02 | 504:48033 | SHORT RURAL | Other | Other | 1 | 55 | 0.0002482 | 0.00044761 | N
24/05/2017 | 08:46 | ZN12620:PA7 | URBAN | Other | Other | 1 | 79 | 5.4039e-05 | 6.8723e-05 | N
24/05/2017 | 12:05 | ZN3672:PA36 | URBAN | Other | Other | 1 | 70 | 4.8278e-05 | 6.8723e-05 | N
24/05/2017 | 12:33 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 446 | 58 | 0.11503 | 0.19963 | N
25/05/2017 | 08:43 | 511:29878 | SHORT RURAL | Other | Other | 1 | 125 | 0.000561 | 0.00044761 | N
25/05/2017 | 08:51 | ZN12620:PA1 | SHORT RURAL | Other | Other | 1 | 58 | 0.00026125 | 0.00044761 | N
25/05/2017 | 10:38 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 287 | 0.0064231 | 0.002238 | N
25/05/2017 | 13:18 | ZN2310:PA53 | URBAN | Other | Other - Arcing | 1 | 251 | 0.00017272 | 6.8723e-05 | N
26/05/2017 | 04:23 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 177 | 0.003169 | 0.0017904 | Y
26/05/2017 | 08:12 | ZN3672:PA46 | URBAN | Other | Other - Arcing | 2 | 318 | 0.0004365 | 0.00013745 | Y
26/05/2017 | 08:18 | 240:34846 | URBAN | Other | Other - Arcing | 1 | 221 | 0.00015175 | 6.8723e-05 | Y
26/05/2017 | 14:02 | ZN116:PA76 | URBAN | Other | Other | 1 | 92 | 6.3534e-05 | 6.8723e-05 | Y
26/05/2017 | 16:38 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 122 | 0.00054503 | 0.00044761 | Y
26/05/2017 | 22:15 | 243:80075 | SHORT RURAL | Other | Other | 1 | 589 | 0.0026375 | 0.00044761 | Y
27/05/2017 | 09:12 | ZN2466:PA16 | URBAN | Other | Other - Self Clearing Trigger | 28 | 48 | 0.00092267 | 0.0019242 | N
27/05/2017 | 14:40 | 807:74183 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 160 | 0.0021485 | 0.0013428 | N
28/05/2017 | 21:25 | ZN10997:PA5 | URBAN | Other | Other - Arcing | 1 | 465 | 0.00031962 | 6.8723e-05 | N
29/05/2017 | 10:23 | ZN3154:PA4 | URBAN | Other | Other | 1 | 164 | 0.00011269 | 6.8723e-05 | N
29/05/2017 | 11:02 | 524:33578 | URBAN | Other | Other | 1 | 97 | 6.673e-05 | 6.8723e-05 | N
29/05/2017 | 16:20 | ZN9700:PA20 | URBAN | Other | Other - Arcing | 1 | 1,119 | 0.00076902 | 6.8723e-05 | N
29/05/2017 | 17:51 | 261:81870 | URBAN | Other | Other | 1 | 109 | 7.4701e-05 | 6.8723e-05 | N
30/05/2017 | 08:45 | 813:89063 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 167 | 0.001495 | 0.00089521 | N
30/05/2017 | 10:40 | 239:82132 | URBAN | Other | Other | 1 | 98 | 6.7508e-05 | 6.8722e-05 | N
30/05/2017 | 16:13 | 214:8665 | URBAN | Other | Other | 1 | 59 | 4.0317e-05 | 6.8722e-05 | N
30/05/2017 | 17:00 | 238:34148 | SHORT RURAL | Other | Other | 1 | 887 | 0.0039717 | 0.0004476 | N
30/05/2017 | 23:17 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 198 | 0.0017725 | 0.00089521 | N
30/05/2017 | 23:46 | 243:80083 | SHORT RURAL | Other | Other | 1 | 200 | 0.00089707 | 0.0004476 | N
31/05/2017 | 06:14 | 801:74123 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 120 | 0.00053712 | 0.0004476 | N
31/05/2017 | 08:41 | ZN2835:PA30 | URBAN | Other | Other - Self Clearing Trigger | 42 | 213 | 0.0061498 | 0.0028863 | N
31/05/2017 | 13:30 | ZN965:PA20 | URBAN | Other | Other - Self Clearing Trigger | 91 | 62 | 0.0039033 | 0.0062537 | N
31/05/2017 | 17:29 | ZN180:PA7 | URBAN | Other | Other | 1 | 211 | 0.0001448 | 6.8722e-05 | N
31/05/2017 | 17:31 | 221:11895 | URBAN | Other | Other | 1 | 104 | 7.1471e-05 | 6.8722e-05 | N
31/05/2017 | 19:29 | ZN12580:PA16 | URBAN | Other | Other | 1 | 35 | 2.4133e-05 | 6.8722e-05 | N
01/06/2017 | 11:16 | ZN9550:PA42 | URBAN | Other | Other - Self Clearing Trigger | 44 | 124 | 0.0037384 | 0.0030238 | N
01/06/2017 | 12:12 | ZN965:PA15 | URBAN | Other | Other - Self Clearing Trigger | 33 | 108 | 0.0024432 | 0.0022678 | N
01/06/2017 | 14:29 | 235:2857 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 51 | 0.00045656 | 0.00089521 | N
01/06/2017 | 16:04 | ZN188:PA32 | URBAN | Other | Other - Self Clearing Trigger | 59 | 241 | 0.0097715 | 0.0040546 | N
02/06/2017 | 09:55 | 227:13020 | SHORT RURAL | Other | Other | 1 | 114 | 0.00051086 | 0.0004476 | N
02/06/2017 | 17:18 | ZN3155:PA33 | URBAN | Other | Other - Self Clearing Trigger | 83 | 126 | 0.0071612 | 0.0057039 | N
02/06/2017 | 18:34 | 511:29876 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 116 | 0.0020769 | 0.0017904 | N
02/06/2017 | 19:17 | 210:83474 | URBAN | Other | Other | 1 | 63 | 4.2962e-05 | 6.8722e-05 | N
03/06/2017 | 01:45 | 217:33612 | URBAN | Other | Other | 1 | 74 | 5.1026e-05 | 6.8722e-05 | N
03/06/2017 | 09:13 | ZN12660:PA10 | URBAN | Other | Other | 1 | 87 | 5.9788e-05 | 6.8722e-05 | N
03/06/2017 | 09:58 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 62 | 0.00027751 | 0.0004476 | N
03/06/2017 | 14:29 | ZN12610:PA11 | URBAN | Other | Other - Arcing | 1 | 221 | 0.00015185 | 6.8722e-05 | N
03/06/2017 | 15:50 | ZN35500:PA34 | URBAN | Other | Other - Self Clearing Trigger | 95 | 44 | 0.0028791 | 0.0065286 | N
04/06/2017 | 10:05 | ZN12640:PA15 | URBAN | Other | Other | 1 | 91 | 6.2628e-05 | 6.8722e-05 | N
04/06/2017 | 13:45 | ZN10991:PA6 | URBAN | Other | Other - Self Clearing Trigger | 67 | 54 | 0.0024984 | 0.0046044 | N
05/06/2017 | 08:37 | 239:82131 | SHORT RURAL | Other | Other | 1 | 58 | 0.00025909 | 0.0004476 | N
05/06/2017 | 09:37 | ZN2400:PA18 | SHORT RURAL | Other | Other | 1 | 136 | 0.00060822 | 0.0004476 | N
05/06/2017 | 15:05 | ZN1068:PA26 | URBAN | Other | Other | 1 | 130 | 8.9315e-05 | 6.8722e-05 | N
05/06/2017 | 16:19 | ZN15006:PA13 | URBAN | Other | Other - Arcing | 1 | 175 | 0.00012031 | 6.8722e-05 | N
05/06/2017 | 21:28 | ZN3155:PA33 | URBAN | Other | Other - Self Clearing Trigger | 83 | 42 | 0.0023956 | 0.0057039 | N
05/06/2017 | 23:56 | ZN2602:PA36 | URBAN | Other | Other - Arcing | 1 | 244 | 0.00016767 | 6.8722e-05 | N
06/06/2017 | 07:40 | 508:82574 | SHORT RURAL | Other | Other | 1 | 159 | 0.00070997 | 0.0004476 | N
06/06/2017 | 11:15 | ZN3472:PA34 | URBAN | Other | Other | 1 | 57 | 3.8885e-05 | 6.8722e-05 | N
06/06/2017 | 22:59 | ZN15005:PA6 | URBAN | Other | Other - Self Clearing Trigger | 849 | 95 | 0.055427 | 0.058345 | N
07/06/2017 | 00:31 | ZN384:PA2 | URBAN | Other | Other - Arcing | 1 | 689 | 0.00047323 | 6.8722e-05 | N
07/06/2017 | 06:53 | ZN9037:PA8 | URBAN | Other | Other - Arcing | 1 | 306 | 0.00021037 | 6.8722e-05 | N
07/06/2017 | 09:25 | 232:33413 | URBAN | Other | Other - Arcing | 1 | 155 | 0.00010661 | 6.8722e-05 | N
07/06/2017 | 09:13 | ZN2400:PA18 | SHORT RURAL | Other | Other - Self Clearing Trigger | 44 | 124 | 0.024415 | 0.019695 | N
07/06/2017 | 10:07 | ZN2602:PA10 | URBAN | Other | Other - Arcing | 1 | 143 | 9.81e-05 | 6.8722e-05 | N
07/06/2017 | 12:40 | 232:33413 | URBAN | Other | Other - Self Clearing Trigger | 56 | 80 | 0.0030787 | 0.0038484 | N
07/06/2017 | 12:58 | ZN3672:PA13 | URBAN | Other | Other - Arcing | 1 | 556 | 0.00038212 | 6.8722e-05 | N
07/06/2017 | 13:36 | 228:7491 | URBAN | Other | Other | 1 | 63 | 4.3398e-05 | 6.8722e-05 | N
07/06/2017 | 13:36 | ZN12580:PA16 | URBAN | Other | Other - Self Clearing Trigger | 1 | 78 | 5.3374e-05 | 6.8722e-05 | N
07/06/2017 | 13:50 | ZN12580:PA16 | URBAN | Other | Other - Self Clearing Trigger | 1 | 64 | 4.3787e-05 | 6.8722e-05 | N
07/06/2017 | 16:19 | 232:11453 | SHORT RURAL | Other | Other - Self Clearing Trigger | 19 | 86 | 0.0073138 | 0.0085045 | N
07/06/2017 | 19:40 | ZN167:PA10 | URBAN | Other | Other - Self Clearing Trigger | 69 | 60 | 0.0028364 | 0.0047418 | N
07/06/2017 | 23:47 | ZN965:PA20 | URBAN | Other | Other - Self Clearing Trigger | 91 | 622 | 0.038903 | 0.0062537 | N
08/06/2017 | 02:06 | ZN8000:PA4 | URBAN | Other | Other - Self Clearing Trigger | 808 | 240 | 0.13309 | 0.055527 | N
08/06/2017 | 07:26 | ZN1850:PA3 | URBAN | Other | Other - Arcing | 1 | 1,436 | 0.00098667 | 6.8722e-05 | N
08/06/2017 | 07:27 | ZN35500:PA28 | URBAN | Other | Other - Arcing | 1 | 228 | 0.00015641 | 6.8722e-05 | N
08/06/2017 | 08:30 | ZN847:PA2 | URBAN | Other | Other - Self Clearing Trigger | 42 | 151 | 0.0043503 | 0.0028863 | N
08/06/2017 | 10:54 | ZN14144:PA5 | SHORT RURAL | Other | Other - Arcing | 1 | 724 | 0.0032409 | 0.0004476 | N
08/06/2017 | 15:36 | ZN14891:PA14 | URBAN | Other | Other - Arcing | 7 | 241 | 0.0011606 | 0.00048105 | N
08/06/2017 | 15:46 | ZN965:PA20 | URBAN | Other | Other - Self Clearing Trigger | 91 | 58 | 0.0036459 | 0.0062537 | N
08/06/2017 | 16:49 | ZN12630:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,318 | 0.0058994 | 0.0004476 | N
08/06/2017 | 16:49 | ZN12630:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 416 | 165 | 0.30765 | 0.1862 | N
09/06/2017 | 00:38 | 222:33601 | SHORT RURAL | Other | Other - Self Clearing Trigger | 56 | 74 | 0.018553 | 0.025066 | N
09/06/2017 | 13:55 | ZN3472:PA27 | URBAN | Other | Other - Arcing | 1 | 95 | 6.4953e-05 | 6.8722e-05 | N
09/06/2017 | 19:49 | ZN2466:PA16 | URBAN | Other | Other - Self Clearing Trigger | 28 | 245 | 0.0047162 | 0.0019242 | N
09/06/2017 | 22:07 | ZN2602:PA9 | URBAN | Other | Other | 1 | 118 | 8.1424e-05 | 6.8722e-05 | N
10/06/2017 | 08:35 | 526:34640 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 184 | 0.00082359 | 0.0004476 | N
10/06/2017 | 14:39 | 508:82578 | SHORT RURAL | Other | Other | 1 | 239 | 0.0010697 | 0.0004476 | N
10/06/2017 | 18:22 | ZN630:PA26 | URBAN | Other | Other - Self Clearing Trigger | 21 | 1,153 | 0.01664 | 0.0014432 | N
11/06/2017 | 00:02 | ZN4545:PA21 | URBAN | Other | Other - Arcing | 1 | 238 | 0.00016335 | 6.8722e-05 | N
11/06/2017 | 13:39 | ZN2466:PA16 | URBAN | Other | Other - Self Clearing Trigger | 28 | 166 | 0.0031942 | 0.0019242 | N
11/06/2017 | 14:33 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 77 | 0.00034465 | 0.0004476 | N
11/06/2017 | 15:21 | 258:80778 | URBAN | Other | Other | 1 | 55 | 3.7545e-05 | 6.8722e-05 | N
12/06/2017 | 03:02 | ZN129:PA41 | URBAN | Other | Other - Arcing | 1 | 1,827 | 0.0012558 | 6.8722e-05 | N
12/06/2017 | 09:54 | ZN965:PA35 | URBAN | Other | Other | 1 | 26 | 1.7581e-05 | 6.8722e-05 | N
12/06/2017 | 16:32 | ZN1290:PA9 | URBAN | Other | Other | 1 | 43 | 2.9321e-05 | 6.8722e-05 | N
13/06/2017 | 12:29 | ZN3155:PA34 | URBAN | Other | Other - Self Clearing Trigger | 66 | 50 | 0.0022746 | 0.0045356 | N
13/06/2017 | 13:22 | ZN12690:PA3 | SHORT RURAL | Other | Other | 1 | 78 | 0.00035114 | 0.0004476 | N
13/06/2017 | 15:28 | 507:80922 | SHORT RURAL | Other | Other | 1 | 1,191 | 0.0053322 | 0.0004476 | N
13/06/2017 | 18:04 | ZN36100:PA8 | URBAN | Other | Other | 1 | 163 | 0.00011226 | 6.8722e-05 | N
14/06/2017 | 00:57 | ZN9900:PA17 | URBAN | Other | Other - Self Clearing Trigger | 29 | 58 | 0.0011559 | 0.0019929 | N
14/06/2017 | 08:53 | 526:34640 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 167 | 0.0007475 | 0.0004476 | N
14/06/2017 | 11:59 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 71 | 0.0003178 | 0.0004476 | N
14/06/2017 | 12:34 | ZN3425:PA44 | URBAN | Other | Other - Arcing | 1 | 145 | 9.9887e-05 | 6.8722e-05 | N
14/06/2017 | 13:57 | ZN2635:PA57 | URBAN | Other | Other - Self Clearing Trigger | 71 | 53 | 0.0025852 | 0.0048792 | N
14/06/2017 | 18:50 | ZN12600:PA11 | URBAN | Other | Other | 1 | 65 | 4.4463e-05 | 6.8722e-05 | N
15/06/2017 | 10:44 | 221:11899 | SHORT RURAL | Other | Other | 1 | 88 | 0.00039337 | 0.0004476 | N
15/06/2017 | 15:57 | ZN129:PA35 | URBAN | Other | Other | 1 | 33 | 2.2415e-05 | 6.8722e-05 | N
15/06/2017 | 15:59 | ZN129:PA47 | URBAN | Other | Other | 1 | 48 | 3.3181e-05 | 6.8722e-05 | N
15/06/2017 | 22:19 | ZN2602:PA32 | URBAN | Other | Other - Arcing | 47 | 237 | 0.0076651 | 0.0032299 | N
15/06/2017 | 16:30 | 502:48009 | URBAN | Other | Other - Self Clearing Trigger | 1 | 10 | 6.8722e-06 | 6.8722e-05 | N
16/06/2017 | 11:20 | ZN847:PA39 | URBAN | Other | Other - Arcing | 1 | 220 | 0.00015096 | 6.8722e-05 | N
16/06/2017 | 12:34 | ZN12610:PA18 | URBAN | Other | Other - Arcing | 1 | 326 | 0.00022402 | 6.8722e-05 | N
16/06/2017 | 19:42 | 257:81987 | URBAN | Other | Other | 1 | 67 | 4.6273e-05 | 6.8722e-05 | N
17/06/2017 | 00:40 | 813:89059 | URBAN | Other | Other - Self Clearing Trigger | 274 | 60 | 0.011298 | 0.01883 | N
17/06/2017 | 09:18 | 205:12205 | SHORT RURAL | Other | Other - Self Clearing Trigger | 59 | 49 | 0.01294 | 0.026409 | N
17/06/2017 | 13:31 | ZN12620:PA1 | SHORT RURAL | Other | Other | 1 | 143 | 0.00064089 | 0.0004476 | N
17/06/2017 | 15:12 | 502:48010 | SHORT RURAL | Other | Other | 1 | 32 | 0.00014435 | 0.0004476 | N
18/06/2017 | 07:52 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 449 | 0.0060292 | 0.0013428 | N
18/06/2017 | 10:11 | 807:74180 | SHORT RURAL | Other | Other | 1 | 286 | 0.0012804 | 0.0004476 | N
18/06/2017 | 23:08 | ZN80:PA32 | URBAN | Other | Other - Arcing | 1 | 951 | 0.00065376 | 6.8722e-05 | N
19/06/2017 | 07:46 | ZN15005:PA8 | URBAN | Other | Other - Arcing | 1 | 305 | 0.00020981 | 6.8722e-05 | N
16/06/2017 | 13:47 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 12 | 138 | 0.5908 | 0.42811 | N
19/06/2017 | 17:31 | ZN2835:PA41 | URBAN | Other | Other - Self Clearing Trigger | 12 | 83 | 0.00068474 | 0.00082466 | N
19/06/2017 | 21:19 | ZN3154:PA18 | URBAN | Other | Other - Arcing | 37 | 871 | 0.022147 | 0.0025427 | N
19/06/2017 | 22:14 | ZN9900:PA17 | URBAN | Other | Other | 1 | 91 | 6.2663e-05 | 6.8722e-05 | N
20/06/2017 | 06:19 | 802:82220 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 334 | 0.001495 | 0.0004476 | N
20/06/2017 | 09:29 | ZN1850:PA3 | URBAN | Other | Other | 1 | 286 | 0.00019641 | 6.8722e-05 | N
20/06/2017 | 11:16 | ZN690:PA36 | URBAN | Other | Other - Arcing | 1 | 254 | 0.00017424 | 6.8722e-05 | N
20/06/2017 | 17:07 | ZN35500:PA18 | SHORT RURAL | Other | Other | 1 | 130 | 0.00058144 | 0.0004476 | N
21/06/2017 | 07:24 | 524:33570 | SHORT RURAL | Other | Other - Arcing | 1 | 246 | 0.001101 | 0.0004476 | N
21/06/2017 | 15:59 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 131 | 0.015822 | 0.012085 | N
21/06/2017 | 18:00 | 243:80081 | SHORT RURAL | Other | Other - Self Clearing Trigger | 132 | 75 | 0.044313 | 0.059084 | N
22/06/2017 | 06:21 | ZN15013:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 64 | 0.0025782 | 0.0040284 | N
22/06/2017 | 14:08 | 223:14393 | URBAN | Other | Other | 1 | 77 | 5.2629e-05 | 6.8722e-05 | N
23/06/2017 | 07:22 | 202:34254 | URBAN | Other | Other - Arcing | 1 | 198 | 0.00013582 | 6.8642e-05 | N
23/06/2017 | 16:29 | 802:82220 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 187 | 0.00083702 | 0.0004476 | N
23/06/2017 | 17:22 | ZN12610:PA11 | URBAN | Other | Other - Arcing | 1 | 277 | 0.00019033 | 6.8642e-05 | N
23/06/2017 | 18:31 | ZN2602:PA30 | URBAN | Other | Other - Arcing | 1 | 178 | 0.0001223 | 6.8642e-05 | N
23/06/2017 | 18:35 | ZN2602:PA30 | URBAN | Other | Other - Arcing | 1 | 174 | 0.00011953 | 6.8642e-05 | N
23/06/2017 | 20:12 | 235:2123 | URBAN | Other | Other | 1 | 72 | 4.964e-05 | 6.8642e-05 | N
24/06/2017 | 10:15 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 140 | 0.049946 | 0.035676 | N
24/06/2017 | 17:01 | 504:48026 | SHORT RURAL | Other | Other | 1 | 118 | 0.00052989 | 0.0004476 | N
25/06/2017 | 13:23 | 507:80917 | URBAN | Other | Other | 1 | 57 | 3.8863e-05 | 6.8642e-05 | N
25/06/2017 | 14:35 | 270:83586 | URBAN | Other | Other | 1 | 159 | 0.00010936 | 6.8642e-05 | N
26/06/2017 | 09:48 | 206:34432 | URBAN | Other | Other | 1 | 101 | 6.9409e-05 | 6.8642e-05 | N
26/06/2017 | 14:29 | 222:33602 | URBAN | Other | Other | 1 | 215 | 0.00014762 | 6.8642e-05 | N
26/06/2017 | 15:59 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 91 | 0.032465 | 0.035676 | N
26/06/2017 | 19:08 | ZN3672:PA9 | URBAN | Other | Other - Arcing | 2 | 262 | 0.00035946 | 0.00013728 | N
27/06/2017 | 12:30 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 166 | 0.00074332 | 0.0004476 | N
27/06/2017 | 14:25 | 233:82812 | SHORT RURAL | Other | Other | 1 | 100 | 0.00044551 | 0.0004476 | N
27/06/2017 | 15:23 | ZN262:PA15 | URBAN | Other | Other | 1 | 188 | 0.00012872 | 6.8642e-05 | N
27/06/2017 | 16:29 | ZN72:PA10 | URBAN | Other | Other - Self Clearing Trigger | 55 | 990 | 0.037387 | 0.0037753 | N
28/06/2017 | 05:13 | 243:80083 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 157 | 0.002811 | 0.0017904 | N
28/06/2017 | 10:15 | ZN4545:PA19 | URBAN | Other | Other - Self Clearing Trigger | 39 | 69 | 0.0018476 | 0.0026771 | N
28/06/2017 | 10:22 | ZN12580:PA12 | SHORT RURAL | Other | Other | 1 | 53 | 0.00023507 | 0.0004476 | N
28/06/2017 | 10:36 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 114 | 0.00051027 | 0.0004476 | N
28/06/2017 | 13:11 | 813:89061 | LONG RURAL | Other | Other - Arcing | 1 | 1,549 | 0.55262 | 0.035676 | N
28/06/2017 | 09:30 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 105 | 0.00046998 | 0.0004476 | N
28/06/2017 | 13:42 | ZN2602:PA30 | URBAN | Other | Other - Arcing | 1 | 497 | 0.0003412 | 6.8642e-05 | N
29/06/2017 | 08:44 | 528:83020 | SHORT RURAL | Other | Other | 1 | 84 | 0.00037435 | 0.0004476 | N
29/06/2017 | 13:06 | 524:33570 | SHORT RURAL | Other | Other - Arcing | 1 | 253 | 0.0011344 | 0.0004476 | N
29/06/2017 | 15:20 | 507:80932 | SHORT RURAL | Other | Other | 1 | 47 | 0.00021134 | 0.0004476 | N
29/06/2017 | 16:07 | ZN9245:PA13 | URBAN | Other | Other - Arcing | 1 | 173 | 0.00011867 | 6.8642e-05 | N
30/06/2017 | 10:49 | ZN35500:PA28 | URBAN | Other | Other | 1 | 78 | 5.3816e-05 | 6.8642e-05 | N
30/06/2017 | 14:37 | ZN262:PA41 | URBAN | Other | Other - Arcing | 1 | 4,012 | 0.0027542 | 6.8642e-05 | N
30/06/2017 | 15:27 | ZN847:PA26 | URBAN | Other | Other - Self Clearing Trigger | 175 | 94 | 0.011292 | 0.012012 | N
30/06/2017 | 15:27 | ZN847:PA46 | URBAN | Other | Other - Self Clearing Trigger | 1,089 | 111 | 0.082923 | 0.074751 | N
05/11/2016 | 18:53 | 504:48031 | SHORT RURAL | Other |  | 550 | 7 | 0.017325 | 0.2475 | N
06/11/2016 | 15:21 | 509:33395 | LONG RURAL | Other |  | 812 | 738 | 213.4863 | 28.9277 | N
06/11/2016 | 15:21 | 509:33397 | SHORT RURAL | Other |  | 395 | 738 | 1.3118 | 0.17775 | N
06/11/2016 | 15:21 | 509:33399 | SHORT RURAL | Other |  | 899 | 42 | 0.16991 | 0.40454 | N
13/12/2016 | 15:36 | 507:80925 | SHORT RURAL | Other |  | 1,517 | 78 | 0.53041 | 0.68167 | N
14/12/2016 | 20:02 | 504:48026 | SHORT RURAL | Other |  | 1,276 | 53 | 0.30389 | 0.57339 | N
14/12/2016 | 20:02 | 504:48027 | URBAN | Other |  | 134 | 53 | 0.0048963 | 0.0092384 | N
14/12/2016 | 20:02 | 504:48028 | URBAN | Other |  | 1,266 | 53 | 0.046259 | 0.087282 | N
14/12/2016 | 20:02 | 504:48029 | URBAN | Other |  | 256 | 53 | 0.0093542 | 0.017649 | N
14/12/2016 | 20:02 | 504:48031 | SHORT RURAL | Other |  | 560 | 53 | 0.13337 | 0.25164 | N
14/12/2016 | 20:02 | 504:48032 | URBAN | Other |  | 336 | 53 | 0.012277 | 0.023165 | N
14/12/2016 | 20:02 | 504:48033 | SHORT RURAL | Other |  | 1,167 | 53 | 0.27793 | 0.5244 | N
14/12/2016 | 20:02 | 504:48034 | URBAN | Other |  | 1,413 | 53 | 0.051631 | 0.097416 | N
14/12/2016 | 20:02 | 509:33395 | LONG RURAL | Other |  | 813 | 53 | 15.3396 | 28.9427 | N
14/12/2016 | 20:02 | 509:33397 | SHORT RURAL | Other |  | 399 | 53 | 0.095026 | 0.1793 | N
14/12/2016 | 20:02 | 509:33399 | SHORT RURAL | Other |  | 905 | 53 | 0.21554 | 0.40667 | N
14/12/2016 | 20:02 | 525:34580 | SHORT RURAL | Other |  | 2 | 53 | 0.00047632 | 0.00089872 | N
14/12/2016 | 20:02 | 525:34586 | SHORT RURAL | Other |  | 2 | 53 | 0.00047632 | 0.00089872 | N
14/12/2016 | 20:02 | 525:34589 | URBAN | Other |  | 1 | 53 | 3.654e-05 | 6.8943e-05 | N
09/02/2017 | 02:01 | 810:74050 | SHORT RURAL | Other |  | 1 | 195 | 0.00087296 | 0.00044748 | N
01/07/2016 | 14:45 | ZN10991:PA1 | URBAN | Other |  | 1,527 | 90 | 0.095181 | 0.10576 | N
06/07/2016 | 12:11 | ZN2400:PA21 | URBAN | Other |  | 1 | 138 | 9.5716e-05 | 6.9259e-05 | N
06/07/2016 | 23:28 | ZN12570:PA24 | SHORT RURAL | Other |  | 740 | 297 | 1.0007 | 0.33694 | N
07/07/2016 | 09:39 | 513:48056 | SHORT RURAL | Other |  | 1 | 340 | 0.0015465 | 0.00045525 | N
10/07/2016 | 15:23 | ZN2196:PA18 | URBAN | Other |  | 1 | 306 | 0.00021218 | 6.925e-05 | N
13/07/2016 | 07:06 | ZN36300:PA5 | URBAN | Other |  | 40 | 344 | 0.0095293 | 0.0027702 | N
13/07/2016 | 12:44 | ZN9700:PA17 | URBAN | Other |  | 9 | 43 | 0.00026791 | 0.00062329 | N
12/07/2016 | 18:14 | ZN690:PA3 | URBAN | Other |  | 497 | 2 | 0.00068837 | 0.034418 | N
14/07/2016 | 11:38 | ZN35800:PA15 | URBAN | Other |  | 1 | 142 | 9.8203e-05 | 6.9255e-05 | N
14/07/2016 | 18:15 | ZN1850:PA10 | URBAN | Other |  | 33 | 237 | 0.0054191 | 0.0022854 | N
15/07/2016 | 18:34 | ZN35400:PA110 | URBAN | Other |  | 1 | 64 | 4.4185e-05 | 6.9256e-05 | N
16/07/2016 | 07:14 | ZN2310:PA65 | URBAN | Other |  | 1 | 37 | 2.5643e-05 | 6.9243e-05 | N
18/07/2016 | 19:19 | ZN3922:PA29 | URBAN | Other |  | 58 | 31 | 0.001245 | 0.0040161 | N
21/07/2016 | 07:42 | 813:89061 | LONG RURAL | Other |  | 1 | 246 | 0.08788 | 0.035663 | N
26/07/2016 | 08:08 | 812:19071 | SHORT RURAL | Other |  | 1 | 89 | 0.00040368 | 0.00045391 | N
27/07/2016 | 11:23 | ZN15006:PA9 | URBAN | Other |  | 1 | 165 | 0.00011446 | 6.9237e-05 | N
27/07/2016 | 20:59 | 513:48051 | URBAN | Other |  | 1 | 34 | 2.3656e-05 | 6.9237e-05 | N
28/07/2016 | 13:38 | ZN10999:PA16 | URBAN | Other |  | 1 | 429 | 0.00029702 | 6.9227e-05 | N
28/07/2016 | 19:28 | ZN15010:PA11 | URBAN | Other |  | 1 | 902 | 0.0006246 | 6.9227e-05 | N
01/08/2016 | 10:20 | ZN3154:PA19 | URBAN | Other |  | 35 | 23 | 0.0005573 | 0.002423 | N
04/08/2016 | 23:17 | ZN36800:PA43 | URBAN | Other |  | 1 | 822 | 0.00056865 | 6.9177e-05 | N
08/08/2016 | 08:02 | ZN15010:PA5 | URBAN | Other |  | 1 | 188 | 0.00012973 | 6.9178e-05 | N
10/08/2016 | 07:15 | 812:19072 | SHORT RURAL | Other |  | 1 | 89 | 0.00040686 | 0.00045612 | N
12/08/2016 | 20:40 | ZN4545:PA29 | URBAN | Other |  | 1 | 979 | 0.00067733 | 6.9156e-05 | N
12/08/2016 | 11:59 | 520:48172 | SHORT RURAL | Other |  | 262 | 13 | 0.015532 | 0.11947 | N
15/08/2016 | 17:27 | 807:74181 | SHORT RURAL | Other |  | 4 | 215 | 0.0039217 | 0.0018241 | N
16/08/2016 | 08:34 | 807:74181 | SHORT RURAL | Other |  | 1 | 322 | 0.0014687 | 0.00045602 | N
16/08/2016 | 10:20 | 812:19071 | SHORT RURAL | Other |  | 1 | 283 | 0.0012903 | 0.00045602 | N
16/08/2016 | 17:20 | 812:19066 | SHORT RURAL | Other |  | 1 | 1,002 | 0.0045693 | 0.00045602 | N
17/08/2016 | 07:11 | ZN15008:PA9 | URBAN | Other |  | 1 | 408 | 0.00028237 | 6.916e-05 | N
17/08/2016 | 09:50 | 811:74234 | SHORT RURAL | Other |  | 1 | 313 | 0.0014289 | 0.00045602 | N
18/08/2016 | 16:42 | ZN188:PA17 | URBAN | Other |  | 1 | 77 | 5.348e-05 | 6.9379e-05 | N
22/08/2016 | 10:35 | 513:48059 | SHORT RURAL | Other |  | 1 | 95 | 0.00043997 | 0.00046353 | N
22/08/2016 | 15:52 | ZN14891:PA5 | SHORT RURAL | Other |  | 1 | 430 | 0.0019913 | 0.00046353 | N
22/08/2016 | 19:30 | ZN180:PA23 | URBAN | Other |  | 1,087 | 12 | 0.0090499 | 0.075416 | N
22/08/2016 | 19:30 | ZN180:PA30 | URBAN | Other |  | 903 | 12 | 0.007518 | 0.06265 | N
22/08/2016 | 19:30 | ZN180:PA34 | URBAN | Other |  | 1,273 | 13 | 0.011426 | 0.08832 | N
24/08/2016 | 13:00 | 513:48056 | SHORT RURAL | Other |  | 1 | 92 | 0.00041869 | 0.00045683 | N
25/08/2016 | 04:42 | ZN1068:PA27 | URBAN | Other |  | 757 | 89 | 0.046476 | 0.052304 | N
25/08/2016 | 11:11 | ZN1285:PA8 | URBAN | Other |  | 1 | 109 | 7.5278e-05 | 6.9094e-05 | N
28/08/2016 | 01:06 | 814:82291 | SHORT RURAL | Other |  | 1 | 454 | 0.0020714 | 0.00045662 | N
01/09/2016 | 13:35 | ZN10991:PA8 | URBAN | Other |  | 75 | 250 | 0.012926 | 0.005178 | N
03/09/2016 | 02:23 | 523:33500 | URBAN | Other |  | 1 | 532 | 0.00036741 | 6.9041e-05 | N
03/09/2016 | 18:31 | ZN195:PA11 | URBAN | Other |  | 1 | 126 | 8.7302e-05 | 6.9041e-05 | N
03/09/2016 | 16:41 | 508:82575 | SHORT RURAL | Other |  | 3 | 1,274 | 0.017447 | 0.0013694 | N
04/09/2016 | 23:56 | 512:48046 | SHORT RURAL | Other |  | 1 | 124 | 0.00056756 | 0.00045648 | N
06/09/2016 | 09:04 | 523:33503 | URBAN | Other |  | 1 | 163 | 0.00011268 | 6.9042e-05 | N
07/09/2016 | 10:17 | 814:82289 | SHORT RURAL | Other |  | 1 | 108 | 0.00049422 | 0.00045648 | N
11/09/2016 | 20:55 | ZN15014:PA19 | URBAN | Other |  | 1 | 980 | 0.00067658 | 6.9062e-05 | N
14/09/2016 | 14:00 | 807:74179 | SHORT RURAL | Other |  | 1 | 1,167 | 0.0053031 | 0.00045451 | N
16/09/2016 | 13:10 | ZN35800:PA7 | URBAN | Other |  | 54 | 170 | 0.006339 | 0.0037288 | N
19/09/2016 | 00:18 | 801:74118 | URBAN | Other |  | 1 | 544 | 0.00037547 | 6.9064e-05 | N
20/09/2016 | 00:56 | 813:89061 | LONG RURAL | Other |  | 1 | 193 | 0.068998 | 0.035676 | N
20/09/2016 | 11:22 | 812:19071 | SHORT RURAL | Other |  | 1 | 49 | 0.00022248 | 0.00045403 | N
25/09/2016 | 17:41 | ZN2835:PA16 | URBAN | Other |  | 1 | 245 | 0.00016927 | 6.9046e-05 | N
26/09/2016 | 06:35 | 810:74062 | SHORT RURAL | Other |  | 1 | 174 | 0.00079073 | 0.00045392 | N
27/09/2016 | 12:54 | ZN3472:PA27 | URBAN | Other |  | 1 | 156 | 0.00010758 | 6.9047e-05 | N
27/09/2016 | 16:07 | ZN10994:PA7 | URBAN | Other |  | 46 | 158 | 0.0050183 | 0.0031762 | N
28/09/2016 | 10:31 | 807:74181 | SHORT RURAL | Other |  | 1 | 103 | 0.00046788 | 0.00045388 | N
29/09/2016 | 16:16 | 807:74181 | SHORT RURAL | Other |  | 1 | 393 | 0.0017812 | 0.00045377 | N
29/09/2016 | 18:04 | 813:89063 | SHORT RURAL | Other |  | 1 | 90 | 0.00041043 | 0.00045377 | N
30/09/2016 | 07:44 | 801:74121 | LONG RURAL | Other |  | 1 | 389 | 0.13895 | 0.035689 | N
30/09/2016 | 09:49 | 801:74121 | LONG RURAL | Other |  | 1 | 263 | 0.094016 | 0.035689 | N
30/09/2016 | 10:13 | 807:74184 | SHORT RURAL | Other |  | 1 | 242 | 0.0010975 | 0.00045377 | N
01/10/2016 | 11:36 | 508:82579 | SHORT RURAL | Other |  | 7 | 144 | 0.004563 | 0.0031688 | N
04/10/2016 | 16:08 | 814:82285 | SHORT RURAL | Other |  | 1 | 1,042 | 0.004717 | 0.00045268 | N
06/10/2016 | 11:06 | 801:74120 | URBAN | Other |  | 1 | 243 | 0.00016766 | 6.9062e-05 | N
10/10/2016 | 09:14 | 509:33397 | SHORT RURAL | Other |  | 1 | 255 | 0.0011545 | 0.00045254 | N
10/10/2016 | 12:06 | 814:82283 | SHORT RURAL | Other |  | 1 | 152 | 0.0006868 | 0.00045254 | N
10/10/2016 | 16:35 | ZN36300:PA3 | URBAN | Other |  | 1 | 560 | 0.00038655 | 6.9086e-05 | N
11/10/2016 | 00:32 | ZN167:PA21 | URBAN | Other |  | 1 | 674 | 0.00046504 | 6.9046e-05 | N
11/10/2016 | 12:22 | ZN1648:PA13 | URBAN | Other |  | 1 | 127 | 8.7827e-05 | 6.9046e-05 | N
12/10/2016 | 11:25 | ZN10994:PA21 | URBAN | Other |  | 1 | 185 | 0.00012764 | 6.9048e-05 | N
13/10/2016 | 09:47 | ZN2466:PA27 | URBAN | Other |  | 6 | 98 | 0.00040655 | 0.00041484 | N
14/10/2016 | 14:11 | ZN3154:PA10 | URBAN | Other |  | 31 | 129 | 0.0027553 | 0.0021434 | N
15/10/2016 | 22:22 | 801:74119 | URBAN | Other |  | 1 | 638 | 0.00044041 | 6.9069e-05 | N
17/10/2016 | 16:07 | ZN35370:PA4 | SHORT RURAL | Other |  | 1 | 409 | 0.0018435 | 0.00045041 | N
18/10/2016 | 07:31 | 512:48049 | SHORT RURAL | Other |  | 1 | 507 | 0.0022832 | 0.00045041 | N
18/10/2016 | 14:49 | ZN72:PA30 | URBAN | Other |  | 29 | 116 | 0.0023236 | 0.0020031 | N
19/10/2016 | 09:02 | 261:81870 | URBAN | Other |  | 1 | 118 | 8.1451e-05 | 6.9075e-05 | N
19/10/2016 | 09:13 | 513:48052 | URBAN | Other |  | 1 | 311 | 0.000215 | 6.9075e-05 | N
21/10/2016 | 21:53 | 801:74123 | SHORT RURAL | Other |  | 1 | 178 | 0.00080733 | 0.00045317 | N
23/10/2016 | 11:50 | ZN1193:PA15 | URBAN | Other |  | 1 | 55 | 3.7763e-05 | 6.9058e-05 | N
27/10/2016 | 12:35 | ZN2835:PA29 | URBAN | Other |  | 39 | 60 | 0.0016155 | 0.0026924 | N
27/10/2016 | 12:33 | 504:48033 | SHORT RURAL | Other |  | 1 | 87 | 0.0003913 | 0.00045012 | N
28/10/2016 | 09:49 | ZN340:PA19 | URBAN | Other |  | 1 | 235 | 0.00016237 | 6.9037e-05 | N
31/10/2016 | 17:10 | 232:11457 | SHORT RURAL | Other |  | 56 | 5 | 0.0012603 | 0.025206 | N
01/11/2016 | 11:00 | 507:80925 | SHORT RURAL | Other |  | 19 | 105 | 0.0089806 | 0.008553 | N
02/11/2016 | 10:59 | 526:34636 | SHORT RURAL | Other |  | 1 | 111 | 0.00049758 | 0.00045016 | N
02/11/2016 | 15:11 | 512:48046 | SHORT RURAL | Other |  | 1 | 92 | 0.0004143 | 0.00045016 | N
02/11/2016 | 19:44 | 807:74184 | SHORT RURAL | Other |  | 1 | 115 | 0.00051581 | 0.00045016 | N
03/11/2016 | 11:38 | 813:89063 | SHORT RURAL | Other |  | 1 | 182 | 0.00081671 | 0.00044998 | N
05/11/2016 | 13:41 | ZN14891:PA8 | SHORT RURAL | Other |  | 1 | 219 | 0.00098473 | 0.00044999 | N
06/11/2016 | 08:38 | 810:74062 | SHORT RURAL | Other |  | 1 | 159 | 0.00071444 | 0.00044999 | N
07/11/2016 | 06:59 | 814:82289 | SHORT RURAL | Other |  | 1 | 481 | 0.0021629 | 0.00044999 | N
10/11/2016 | 19:59 | ZN1193:PA27 | URBAN | Other |  | 1 | 214 | 0.00014753 | 6.9033e-05 | N
13/11/2016 | 08:53 | 812:19072 | SHORT RURAL | Other |  | 1 | 68 | 0.00030487 | 0.00044977 | N
13/11/2016 | 15:33 | ZN4545:PA31 | URBAN | Other |  | 1 | 476 | 0.0003286 | 6.9011e-05 | N
14/11/2016 | 08:56 | ZN4545:PA40 | URBAN | Other |  | 1 | 124 | 8.5412e-05 | 6.9011e-05 | N
14/11/2016 | 09:55 | 513:48051 | URBAN | Other |  | 9 | 69 | 0.00043063 | 0.0006211 | N
15/11/2016 | 09:42 | 513:48052 | URBAN | Other |  | 1 | 40 | 2.7444e-05 | 6.9011e-05 | N
11/11/2016 | 09:45 | 513:48052 | URBAN | Other |  | 16 | 5 | 5.5226e-05 | 0.0011045 | N
15/11/2016 | 16:41 | ZN15014:PA14 | SHORT RURAL | Other |  | 1 | 371 | 0.0016684 | 0.00044977 | N
16/11/2016 | 12:28 | ZN129:PA3 | URBAN | Other |  | 1 | 152 | 0.00010481 | 6.9012e-05 | N
16/11/2016 | 21:29 | 813:89062 | SHORT RURAL | Other |  | 1 | 706 | 0.0031757 | 0.00044978 | N
17/11/2016 | 08:57 | ZN2568:PA32 | URBAN | Other |  | 1 | 212 | 0.00014644 | 6.8991e-05 | N
18/11/2016 | 09:11 | 813:89063 | SHORT RURAL | Other |  | 1 | 106 | 0.0004746 | 0.00044965 | N
18/11/2016 | 21:27 | ZN180:PA21 | URBAN | Other |  | 1 | 125 | 8.617e-05 | 6.8991e-05 | N
18/11/2016 | 21:30 | ZN180:PA18 | URBAN | Other |  | 1 | 121 | 8.3514e-05 | 6.8991e-05 | N
19/11/2016 | 11:45 | ZN965:PA15 | URBAN | Other |  | 9 | 22 | 0.00013661 | 0.00062094 | N
23/11/2016 | 14:43 | 810:74054 | LONG RURAL | Other |  | 1 | 107 | 0.037927 | 0.035613 | N
23/11/2016 | 15:44 | ZN12620:PA10 | SHORT RURAL | Other |  | 1 | 226 | 0.0010141 | 0.00044965 | N
23/11/2016 | 17:16 | 513:48051 | URBAN | Other |  | 1 | 103 | 7.1171e-05 | 6.8998e-05 | N
26/11/2016 | 12:33 | 806:82662 | SHORT RURAL | Other |  | 1 | 149 | 0.00066916 | 0.00044945 | N
02/12/2016 | 14:13 | ZN10999:PA4 | URBAN | Other |  | 1 | 347 | 0.00023923 | 6.9009e-05 | N
05/12/2016 | 16:44 | ZN3922:PA10 | URBAN | Other |  | 81 | 231 | 0.012875 | 0.0055857 | N
05/12/2016 | 16:43 | ZN15014:PA20 | URBAN | Other |  | 912 | 121 | 0.076098 | 0.062891 | N
05/12/2016 | 19:54 | ZN9118:PA26 | URBAN | Other |  | 1 | 1,162 | 0.00080157 | 6.8959e-05 | N
06/12/2016 | 09:26 | ZN15014:PA20 | URBAN | Other |  | 53 | 494 | 0.01805 | 0.0036549 | N
07/12/2016 | 14:11 | ZN35600:PA14 | URBAN | Other |  | 1 | 318 | 0.00021959 | 6.8962e-05 | N
12/12/2016 | 19:02 | ZN10993:PA35 | URBAN | Other |  | 90 | 178 | 0.01102 | 0.0062047 | N
12/12/2016 | 19:02 | ZN10995:PA2 | URBAN | Other |  | 1 | 178 | 0.00012272 | 6.8941e-05 | N
12/12/2016 | 14:20 | ZN15013:PA4 | URBAN | Other |  | 18 | 15 | 0.00018614 | 0.0012409 | N
13/12/2016 | 14:36 | ZN14143:PA17 | SHORT RURAL | Other |  | 503 | 41 | 0.09267 | 0.22602 | N
13/12/2016 | 19:31 | ZN9900:PA6 | URBAN | Other |  | 37 | 49 | 0.0012499 | 0.0025509 | N
13/12/2016 | 20:11 | 256:80644 | URBAN | Other |  | 1 | 753 | 0.00051939 | 6.8942e-05 | N
14/12/2016 | 17:34 | 801:74122 | URBAN | Other |  | 1 | 206 | 0.00014209 | 6.8943e-05 | N
15/12/2016 | 09:54 | ZN398:PA24 | URBAN | Other |  | 1 | 246 | 0.0001694 | 6.8924e-05 | N
15/12/2016 | 21:09 | 807:74181 | SHORT RURAL | Other |  | 1 | 744 | 0.0033411 | 0.00044909 | N
16/12/2016 | 00:11 | ZN9550:PA11 | URBAN | Other |  | 1 | 1,249 | 0.00086059 | 6.8926e-05 | N
16/12/2016 | 04:35 | 807:74183 | SHORT RURAL | Other |  | 1 | 596 | 0.0026783 | 0.00044908 | N
16/12/2016 | 07:21 | 523:33503 | URBAN | Other |  | 1 | 114 | 7.8736e-05 | 6.8926e-05 | N
16/12/2016 | 11:00 | 514:18137 | SHORT RURAL | Other |  | 1 | 118 | 0.00052992 | 0.00044908 | N
16/12/2016 | 16:34 | ZN2602:PA15 | URBAN | Other |  | 1 | 296 | 0.0002038 | 6.8926e-05 | N
17/12/2016 | 15:33 | ZN35400:PA79 | URBAN | Other |  | 119 | 347 | 0.028429 | 0.0082023 | N
20/12/2016 | 05:40 | ZN965:PA33 | URBAN | Other |  | 1 | 289 | 0.00019946 | 6.8927e-05 | N
18/12/2016 | 03:39 | ZN116:PA84 | URBAN | Other |  | 2,130 | 2 | 0.0029363 | 0.14681 | N
19/12/2016 | 22:50 | ZN35400:PA110 | URBAN | Other |  | 19 | 20 | 0.00026192 | 0.0013096 | N
24/12/2016 | 23:31 | 224:80332 | URBAN | Other |  | 1 | 658 | 0.00045311 | 6.8908e-05 | N
28/12/2016 | 06:44 | 812:19072 | SHORT RURAL | Other |  | 1 | 101 | 0.00045136 | 0.00044897 | N
28/12/2016 | 09:35 | 801:74121 | LONG RURAL | Other |  | 1 | 334 | 0.11911 | 0.035625 | N
28/12/2016 | 09:50 | ZN3154:PA13 | SHORT RURAL | Other |  | 1 | 69 | 0.00031099 | 0.00044897 | N
28/12/2016 | 18:40 | 523:33501 | SHORT RURAL | Other |  | 1 | 112 | 0.00050427 | 0.00044897 | N
29/12/2016 | 10:25 | 812:19071 | SHORT RURAL | Other |  | 1 | 237 | 0.0010647 | 0.00044897 | N
29/12/2016 | 21:40 | ZN9245:PA1 | URBAN | Other |  | 1 | 1,016 | 0.00070035 | 6.891e-05 | N
30/12/2016 | 12:10 | ZN10995:PA2 | URBAN | Other |  | 1 | 264 | 0.00018224 | 6.891e-05 | N
02/01/2017 | 08:22 | 801:74121 | LONG RURAL | Other |  | 1 | 147 | 0.052541 | 0.035625 | N
02/01/2017 | 09:46 | 814:82283 | SHORT RURAL | Other |  | 1 | 137 | 0.00061473 | 0.00044898 | N
03/01/2017 | 09:22 | 801:74121 | LONG RURAL | Other |  | 1 | 194 | 0.069285 | 0.035625 | N
03/01/2017 | 11:44 | ZN15010:PA5 | URBAN | Other |  | 1 | 1,179 | 0.00081251 | 6.8911e-05 | N
03/01/2017 | 12:27 | 807:74181 | SHORT RURAL | Other |  | 1 | 215 | 0.00096418 | 0.00044898 | N
06/01/2017 | 06:06 | ZN35500:PA27 | URBAN | Other |  | 1 | 255 | 0.00017569 | 6.8915e-05 | N
06/01/2017 | 12:27 | ZN690:PA12 | URBAN | Other |  | 1 | 333 | 0.00022926 | 6.8915e-05 | N
10/01/2017 | 19:42 | 801:74120 | URBAN | Other |  | 1 | 701 | 0.00048272 | 6.8893e-05 | N
10/01/2017 | 19:54 | 812:19071 | SHORT RURAL | Other |  | 1 | 748 | 0.0033588 | 0.00044881 | N
11/01/2017 | 17:37 | ZN4545:PA31 | URBAN | Other |  | 1 | 308 | 0.00021241 | 6.8894e-05 | N
11/01/2017 | 19:20 | ZN3922:PA12 | URBAN | Other |  | 1 | 789 | 0.00054359 | 6.8894e-05 | N
12/01/2017 | 08:53 | ZN35370:PA10 | SHORT RURAL | Other |  | 1 | 196 | 0.00087848 | 0.00044885 | N
12/01/2017 | 09:39 | 801:74122 | URBAN | Other |  | 1 | 90 | 6.1824e-05 | 6.8884e-05 | N
12/01/2017 | 12:31 | 265:81648 | SHORT RURAL | Other |  | 1 | 179 | 0.00080127 | 0.00044885 | N
13/01/2017 | 22:37 | ZN12610:PA13 | URBAN | Other |  | 1 | 378 | 0.00026011 | 6.8886e-05 | N
16/01/2017 | 08:28 | 256:80646 | URBAN | Other |  | 1 | 241 | 0.00016624 | 6.8886e-05 | N
16/01/2017 | 10:27 | ZN187:PA8 | URBAN | Other |  | 1 | 135 | 9.2881e-05 | 6.8886e-05 | N
16/01/2017 | 21:58 | 515:35197 | LONG RURAL | Other |  | 1 | 144 | 0.051366 | 0.035625 | N
18/01/2017 | 11:46 | 523:33511 | URBAN | Other |  | 1 | 55 | 3.814e-05 | 6.8887e-05 | N
18/01/2017 | 12:21 | ZN965:PA47 | URBAN | Other |  | 1 | 83 | 5.6843e-05 | 6.8887e-05 | N
18/01/2017 | 12:37 | 801:74118 | URBAN | Other |  | 1 | 58 | 3.9897e-05 | 6.8887e-05 | N
18/01/2017 | 14:58 | ZN4545:PA40 | URBAN | Other |  | 38 | 197 | 0.0051512 | 0.0026177 | N
19/01/2017 | 08:11 | 523:33507 | URBAN | Other |  | 1 | 124 | 8.5654e-05 | 6.8881e-05 | N
19/01/2017 | 08:58 | ZN180:PA21 | URBAN | Other |  | 88 | 177 | 0.010729 | 0.0060616 | N
19/01/2017 | 13:01 | ZN847:PA22 | URBAN | Other |  | 74 | 117 | 0.0059451 | 0.0050972 | N
20/01/2017 | 12:04 | ZN8000:PA25 | URBAN | Other |  | 1 | 145 | 0.00010019 | 6.8882e-05 | N
20/01/2017 | 12:36 | ZN2835:PA19 | URBAN | Other |  | 1 | 293 | 0.00020199 | 6.8882e-05 | N
23/01/2017 | 08:46 | ZN1193:PA16 | URBAN | Other |  | 27 | 80 | 0.001482 | 0.0018598 | N
24/01/2017 | 20:37 | 807:74179 | SHORT RURAL | Other |  | 1 | 100 | 0.00045014 | 0.00044887 | N
26/01/2017 | 04:52 | 807:74184 | SHORT RURAL | Other |  | 1 | 212 | 0.00094899 | 0.00044827 | N
26/01/2017 | 12:17 | 801:74118 | URBAN | Other |  | 1 | 39 | 2.6668e-05 | 6.888e-05 | N
27/01/2017 | 10:46 | 812:19072 | SHORT RURAL | Other |  | 1 | 94 | 0.00041942 | 0.00044826 | N
30/01/2017 | 14:57 | ZN2835:PA27 | URBAN | Other |  | 93 | 513 | 0.03286 | 0.0064054 | N
30/01/2017 | 19:44 | ZN2835:PA15 | URBAN | Other |  | 2 | 1,186 | 0.0016337 | 0.00013775 | N
31/01/2017 | 10:42 | ZN2835:PA15 | URBAN | Other |  | 1 | 287 | 0.00019772 | 6.8876e-05 | N
01/02/2017 | 06:46 | ZN847:PA39 | URBAN | Other |  | 1 | 194 | 0.00013332 | 6.8877e-05 | N
01/02/2017 | 18:04 | 509:33395 | LONG RURAL | Other |  | 1 | 138 | 0.049109 | 0.035638 | N
01/02/2017 | 18:36 | 513:48056 | SHORT RURAL | Other |  | 1 | 137 | 0.00061278 | 0.00044827 | N
04/02/2017 | 17:55 | ZN4545:PA27 | URBAN | Other |  | 16 | 95 | 0.0010468 | 0.0011019 | N
08/02/2017 | 05:15 | ZN3155:PA17 | URBAN | Other |  | 34 | 1,115 | 0.026105 | 0.0023418 | N
08/02/2017 | 10:10 | ZN36300:PA19 | URBAN | Other |  | 71 | 266 | 0.012997 | 0.0048902 | N
08/02/2017 | 23:30 | ZN3155:PA34 | URBAN | Other |  | 32 | 80 | 0.0017529 | 0.002204 | N
10/02/2017 | 09:32 | ZN9118:PA20 | URBAN | Other |  | 2 | 252 | 0.00034765 | 0.00013777 | N
10/02/2017 | 10:42 | ZN9118:PA26 | URBAN | Other |  | 1 | 528 | 0.00036352 | 6.8883e-05 | N
10/02/2017 | 16:57 | ZN1285:PA31 | URBAN | Other |  | 1 | 222 | 0.00015295 | 6.8883e-05 | N
11/02/2017 | 09:49 | 528:83014 | SHORT RURAL | Other |  | 1 | 627 | 0.002806 | 0.00044747 | N
11/02/2017 | 16:59 | 813:89065 | URBAN | Other |  | 1 | 106 | 7.2775e-05 | 6.8883e-05 | N
12/02/2017 | 16:25 | ZN10999:PA4 | URBAN | Other |  | 1 | 412 | 0.00028405 | 6.8883e-05 | N
13/02/2017 | 01:40 | 233:82812 | SHORT RURAL | Other |  | 1 | 660 | 0.0029513 | 0.00044747 | N
13/02/2017 | 05:55 | 233:82812 | SHORT RURAL | Other |  | 1 | 404 | 0.0018099 | 0.00044747 | N
13/02/2017 | 11:15 | ZN12650:PA1 | SHORT RURAL | Other |  | 1 | 104 | 0.00046679 | 0.00044747 | N
13/02/2017 | 14:34 | 801:74122 | URBAN | Other |  | 1 | 237 | 0.00016334 | 6.8883e-05 | N
11/02/2017 | 17:35 | ZN35500:PA28 | URBAN | Other |  | 271 | 25 | 0.0046668 | 0.018667 | N
16/02/2017 | 12:52 | 814:82285 | SHORT RURAL | Other |  | 1 | 119 | 0.00053071 | 0.0004466 | N
16/02/2017 | 16:54 | 513:48056 | SHORT RURAL | Other |  | 1 | 1,007 | 0.0044978 | 0.0004466 | N
17/02/2017 | 10:32 | 813:89061 | LONG RURAL | Other |  | 1 | 68 | 0.024038 | 0.035613 | Y
17/02/2017 | 15:45 | ZN35370:PA10 | SHORT RURAL | Other |  | 187 | 135 | 0.11274 | 0.083514 | Y
17/02/2017 | 16:21 | ZN3922:PA10 | URBAN | Other |  | 1 | 179 | 0.000123 | 6.889e-05 | Y
17/02/2017 | 16:54 | ZN12610:PA11 | URBAN | Other |  | 1 | 845 | 0.00058219 | 6.889e-05 | Y
17/02/2017 | 17:26 | ZN12690:PA8 | SHORT RURAL | Other |  | 1 | 1,113 | 0.004972 | 0.0004466 | Y
17/02/2017 | 17:40 | ZN12690:PA19 | URBAN | Other |  | 1 | 1,279 | 0.00088141 | 6.889e-05 | Y
17/02/2017 | 17:44 | ZN12690:PA8 | SHORT RURAL | Other |  | 1 | 856 | 0.0038221 | 0.0004466 | Y
17/02/2017 | 18:38 | ZN15004:PA9 | URBAN | Other |  | 1 | 658 | 0.00045335 | 6.889e-05 | Y
17/02/2017 | 17:05 | ZN15010:PA1 | URBAN | Other |  | 1 | 1,566 | 0.001079 | 6.889e-05 | Y
17/02/2017 | 19:36 | ZN12650:PA1 | SHORT RURAL | Other |  | 1 | 623 | 0.002784 | 0.0004466 | Y
17/02/2017 | 20:30 | ZN12690:PA8 | SHORT RURAL | Other |  | 1 | 929 | 0.0041508 | 0.0004466 | Y
17/02/2017 | 21:04 | ZN12650:PA1 | SHORT RURAL | Other |  | 1 | 535 | 0.0023912 | 0.0004466 | Y
17/02/2017 | 21:09 | 523:33508 | SHORT RURAL | Other |  | 2 | 960 | 0.0085789 | 0.0008932 | Y
18/02/2017 | 08:05 | ZN15010:PA9 | SHORT RURAL | Other |  | 1 | 663 | 0.0029617 | 0.00044661 | N
18/02/2017 | 09:04 | ZN12650:PA1 | SHORT RURAL | Other |  | 1 | 32 | 0.000145 | 0.00044661 | N
18/02/2017 | 10:19 | ZN116:PA76 | URBAN | Other |  | 1 | 281 | 0.00019351 | 6.889e-05 | N
18/02/2017 | 17:08 | ZN15010:PA9 | SHORT RURAL | Other |  | 1 | 5 | 2.2107e-05 | 0.00044661 | N
18/02/2017 | 20:39 | ZN12650:PA1 | SHORT RURAL | Other |  | 1 | 50 | 0.00022345 | 0.00044661 | N
20/02/2017 | 06:49 | 812:19065 | SHORT RURAL | Other |  | 1 | 261 | 0.0011655 | 0.00044661 | N
20/02/2017 | 09:55 | ZN1648:PA21 | URBAN | Other |  | 1 | 275 | 0.00018913 | 6.889e-05 | N
20/02/2017 | 19:47 | ZN195:PA9 | URBAN | Other |  | 1 | 972 | 0.00066979 | 6.889e-05 | N
20/02/2017 | 22:28 | ZN15011:PA2 | URBAN | Other |  | 1 | 793 | 0.00054604 | 6.889e-05 | N
21/02/2017 | 07:10 | 812:19065 | SHORT RURAL | Other |  | 1 | 226 | 0.0010074 | 0.00044663 | N
23/02/2017 | 13:44 | ZN4545:PA24 | URBAN | Other |  | 1 | 286 | 0.00019688 | 6.8883e-05 | N
23/02/2017 | 19:10 | 227:13015 | SHORT RURAL | Other |  | 52 | 70 | 0.016252 | 0.023218 | N
25/02/2017 | 10:29 | ZN15010:PA7 | URBAN | Other |  | 1 | 646 | 0.00044516 | 6.8879e-05 | N
27/02/2017 | 09:29 | 807:74181 | SHORT RURAL | Other |  | 1 | 329 | 0.0014679 | 0.00044661 | N
28/02/2017 | 06:21 | ZN35800:PA16 | URBAN | Other |  | 6 | 327 | 0.0013514 | 0.00041328 | N
28/02/2017 | 07:12 | 813:89055 | SHORT RURAL | Other |  | 1 | 162 | 0.0007236 | 0.00044662 | N
02/03/2017 | 07:04 | ZN1673:PA1 | URBAN | Other |  | 1 | 130 | 8.9591e-05 | 6.8881e-05 | N
03/03/2017 | 15:21 | ZN2835:PA30 | URBAN | Other |  | 1 | 59 | 4.0939e-05 | 6.8863e-05 | N
03/03/2017 | 16:26 | ZN965:PA11 | URBAN | Other |  | 1 | 361 | 0.00024861 | 6.8863e-05 | N
06/03/2017 | 11:43 | 807:74181 | SHORT RURAL | Other |  | 1 | 194 | 0.00086762 | 0.00044727 | N
09/03/2017 | 08:32 | ZN262:PA15 | URBAN | Other |  | 1 | 208 | 0.00014314 | 6.8889e-05 | N
09/03/2017 | 22:10 | 206:34441 | URBAN | Other |  | 1 | 620 | 0.00042677 | 6.8889e-05 | N
10/03/2017 | 08:02 | ZN35500:PA18 | SHORT RURAL | Other |  | 1 | 178 | 0.00078961 | 0.00044464 | N
10/03/2017 | 08:15 | ZN2635:PA47 | URBAN | Other |  | 3 | 223 | 0.00046088 | 0.00020667 | N
10/03/2017 | 17:33 | 257:82000 | SHORT RURAL | Other |  | 1 | 385 | 0.0017138 | 0.00044464 | N
11/03/2017 | 12:47 | 216:10728 | SHORT RURAL | Other |  | 1 | 145 | 0.00064444 | 0.00044464 | N
11/03/2017 | 15:23 | 216:10728 | SHORT RURAL | Other |  | 1 | 13 | 5.6099e-05 | 0.00044464 | N
12/03/2017 | 00:43 | 239:82131 | SHORT RURAL | Other |  | 186 | 102 | 0.084358 | 0.082704 | N
15/03/2017 | 12:00 | ZN690:PA26 | URBAN | Other |  | 1 | 329 | 0.00022677 | 6.8892e-05 | N
17/03/2017 | 11:17 | ZN9252:PA30 | URBAN | Other |  | 1 | 187 | 0.00012881 | 6.8877e-05 | N
17/03/2017 | 18:18 | ZN2602:PA15 | URBAN | Other |  | 1 | 734 | 0.00050558 | 6.8877e-05 | N
18/03/2017 | 01:00 | ZN35800:PA2 | SHORT RURAL | Other |  | 106 | 400 | 0.18845 | 0.047112 | N
18/03/2017 | 06:10 | ZN35800:PA22 | URBAN | Other |  | 6 | 319 | 0.0013187 | 0.00041327 | N
18/03/2017 | 09:27 | 507:80914 | SHORT RURAL | Other |  | 1 | 299 | 0.0013279 | 0.00044445 | N
18/03/2017 | 13:09 | ZN4545:PA19 | URBAN | Other |  | 1 | 184 | 0.00012639 | 6.8878e-05 | N
18/03/2017 | 16:30 | ZN1285:PA33 | URBAN | Other |  | 39 | 247 | 0.006635 | 0.0026863 | N
19/03/2017 | 10:26 | 258:80785 | URBAN | Other |  | 1 | 273 | 0.00018837 | 6.8879e-05 | N
19/03/2017 | 10:29 | ZN2635:PA38 | URBAN | Other |  | 43 | 347 | 0.010277 | 0.0029618 | N
19/03/2017 | 12:11 | ZN14891:PA16 | SHORT RURAL | Other |  | 1 | 274 | 0.0012175 | 0.00044445 | N
20/03/2017 | 07:45 | 213:33771 | URBAN | Other |  | 1 | 184 | 0.00012698 | 6.8879e-05 | N
20/03/2017 | 17:03 | 532:83295 | URBAN | Other |  | 24 | 269 | 0.0044479 | 0.0016531 | N
21/03/2017 | 09:07 | 814:82291 | SHORT RURAL | Other |  | 1 | 205 | 0.00091173 | 0.00044446 | N
22/03/2017 | 18:40 | ZN12640:PA19 | URBAN | Other |  | 1 | 1,205 | 0.00082983 | 6.8881e-05 | N
22/03/2017 | 19:34 | ZN12570:PA40 | SHORT RURAL | Other |  | 1 | 1,024 | 0.0045506 | 0.00044447 | N
23/03/2017 | 08:14 | ZN1068:PA29 | URBAN | Other |  | 1 | 1,096 | 0.00075434 | 6.8858e-05 | N
23/03/2017 | 09:57 | 813:89065 | URBAN | Other |  | 1 | 91 | 6.2798e-05 | 6.8858e-05 | N
23/03/2017 | 12:16 | 812:19065 | SHORT RURAL | Other |  | 1 | 82 | 0.00036509 | 0.0004446 | N
22/03/2017 | 11:12 | ZN2400:PA21 | URBAN | Other |  | 41 | 11 | 0.00031065 | 0.0028241 | N
24/03/2017 | 13:04 | ZN10999:PA11 | URBAN | Other |  | 24 | 517 | 0.0085517 | 0.0016526 | N
25/03/2017 | 21:12 | ZN4545:PA2 | URBAN | Other |  | 1 | 348 | 0.00023952 | 6.8855e-05 | N
26/03/2017 | 15:02 | 507:80922 | SHORT RURAL | Other |  | 1 | 1,097 | 0.0048691 | 0.00044384 | N
27/03/2017 | 04:29 | ZN80:PA21 | URBAN | Other |  | 851 | 122 | 0.071489 | 0.058598 | N
27/03/2017 | 04:29 | ZN80:PA32 | URBAN | Other |  | 1,271 | 130 | 0.11402 | 0.087518 | N
29/03/2017 | 15:14 | ZN384:PA70 | URBAN | Other |  | 1 | 311 | 0.00021444 | 6.886e-05 | N
29/03/2017 | 16:43 | ZN5868:PA17 | URBAN | Other |  | 23 | 337 | 0.0053318 | 0.0015838 | N
29/03/2017 | 18:18 | 239:82132 | URBAN | Other |  | 52 | 281 | 0.010075 | 0.0035807 | N
30/03/2017 | 13:26 | ZN965:PA26 | URBAN | Other |  | 909 | 176 | 0.11003 | 0.062572 | N
30/03/2017 | 21:47 | 523:33507 | URBAN | Other |  | 1 | 136 | 9.3376e-05 | 6.8836e-05 | N
31/03/2017 | 03:33 | 523:33507 | URBAN | Other |  | 1 | 374 | 0.00025738 | 6.884e-05 | N
03/04/2017 | 17:07 | ZN1287:PA3 | URBAN | Other |  | 1 | 275 | 0.00018891 | 6.8806e-05 | N
04/04/2017 | 08:48 | 814:82285 | SHORT RURAL | Other |  | 1 | 35 | 0.00015512 | 0.00044531 | N
04/04/2017 | 17:10 | 807:74184 | SHORT RURAL | Other |  | 4 | 100 | 0.0017812 | 0.0017812 | N
05/04/2017 | 09:19 | 813:89065 | URBAN | Other |  | 1 | 301 | 0.00020733 | 6.8807e-05 | N
08/04/2017 | 08:22 | ZN35370:PA10 | SHORT RURAL | Other |  | 1 | 368 | 0.0016377 | 0.00044534 | N
10/04/2017 | 07:39 | 813:89061 | LONG RURAL | Other |  | 1 | 450 | 0.1607 | 0.035702 | N
10/04/2017 | 08:25 | 258:80779 | URBAN | Other |  | 1 | 215 | 0.0001476 | 6.878e-05 | N
10/04/2017 | 08:55 | 258:80784 | URBAN | Other |  | 1 | 184 | 0.00012659 | 6.878e-05 | N
10/04/2017 | 12:02 | ZN965:PA21 | URBAN | Other |  | 1 | 597 | 0.00041065 | 6.878e-05 | N
10/04/2017 | 17:07 | ZN10999:PA7 | URBAN | Other |  | 1 | 143 | 9.8252e-05 | 6.878e-05 | N
19/04/2017 | 09:58 | ZN9118:PA2 | URBAN | Other |  | 1 | 212 | 0.00014556 | 6.877e-05 | N
20/04/2017 | 19:57 | ZN10997:PA5 | URBAN | Other |  | 1 | 63 | 4.3068e-05 | 6.8799e-05 | N
26/04/2017 | 15:54 | ZN15008:PA10 | URBAN | Other |  | 1 | 373 | 0.00025634 | 6.8776e-05 | N
27/04/2017 | 06:43 | ZN1285:PA17 | URBAN | Other |  | 1 | 437 | 0.00030047 | 6.876e-05 | N
27/04/2017 | 14:10 | ZN15009:PA11 | URBAN | Other |  | 2 | 320 | 0.00043965 | 0.00013752 | N
01/05/2017 | 01:29 | ZN9700:PA11 | URBAN | Other |  | 805 | 49 | 0.027345 | 0.055354 | N
01/05/2017 | 11:00 | 801:74119 | URBAN | Other |  | 1 | 240 | 0.00016493 | 6.8762e-05 | N
02/05/2017 | 16:53 | 507:80925 | SHORT RURAL | Other |  | 1 | 216 | 0.00095718 | 0.00044389 | N
02/05/2017 | 19:35 | ZN2635:PA40 | URBAN | Other |  | 53 | 1,290 | 0.047011 | 0.0036445 | N
04/05/2017 | 13:35 | ZN72:PA16 | URBAN | Other |  | 1 | 510 | 0.00035035 | 6.8752e-05 | N
03/05/2017 | 10:50 | ZN15013:PA10 | SHORT RURAL | Other |  | 8 | 5 | 0.00017756 | 0.0035512 | N
03/05/2017 | 10:50 | ZN15013:PA10 | SHORT RURAL | Other |  | 16 | 5 | 0.00035512 | 0.0071023 | N
10/05/2017 | 09:15 | ZN180:PA24 | URBAN | Other |  | 32 | 145 | 0.00319 | 0.0022 | N
10/05/2017 | 10:32 | 801:74121 | LONG RURAL | Other |  | 1 | 70 | 0.02511 | 0.035702 | N
13/05/2017 | 19:47 | 802:82225 | SHORT RURAL | Other |  | 1 | 147 | 0.00065223 | 0.0004444 | N
14/05/2017 | 11:59 | 813:89055 | SHORT RURAL | Other |  | 1 | 99 | 0.00043885 | 0.0004444 | N
16/05/2017 | 13:26 | 801:74119 | URBAN | Other |  | 1 | 334 | 0.00022958 | 6.8736e-05 | N
19/05/2017 | 00:08 | 807:74184 | SHORT RURAL | Other |  | 1 | 547 | 0.0024466 | 0.00044761 | N
24/05/2017 | 16:30 | 507:80922 | SHORT RURAL | Other |  | 13 | 90 | 0.005237 | 0.0058189 | N
23/05/2017 | 15:09 | ZN10999:PA15 | URBAN | Other |  | 1 | 290 | 0.00019938 | 6.8723e-05 | N
23/05/2017 | 07:50 | ZN8000:PA4 | URBAN | Other |  | 56 | 160 | 0.0061575 | 0.0038485 | N
26/05/2017 | 21:36 | ZN9700:PA11 | URBAN | Other |  | 595 | 8 | 0.0032712 | 0.04089 | Y
27/05/2017 | 00:54 | ZN9037:PA8 | URBAN | Other |  | 2 | 67 | 9.2088e-05 | 0.00013745 | N
28/05/2017 | 12:23 | 801:74120 | URBAN | Other |  | 1 | 77 | 5.2859e-05 | 6.8723e-05 | N
02/06/2017 | 14:34 | ZN847:PA2 | URBAN | Other |  | 1 | 474 | 0.00032549 | 6.8722e-05 | N
06/06/2017 | 12:23 | 814:82285 | SHORT RURAL | Other |  | 1 | 109 | 0.00048796 | 0.0004476 | N
07/06/2017 | 08:59 | ZN1285:PA17 | URBAN | Other |  | 1 | 90 | 6.193e-05 | 6.8722e-05 | N
07/06/2017 | 11:49 | ZN15005:PA6 | URBAN | Other |  | 30 | 693 | 0.014287 | 0.0020617 | N
08/06/2017 | 10:12 | 810:74054 | LONG RURAL | Other |  | 1 | 218 | 0.077863 | 0.035676 | N
08/06/2017 | 10:38 | ZN15002:PA2 | URBAN | Other |  | 1 | 186 | 0.00012763 | 6.8722e-05 | N
08/06/2017 | 18:26 | ZN15005:PA2 | URBAN | Other |  | 1 | 214 | 0.0001468 | 6.8722e-05 | N
09/06/2017 | 18:20 | 220:8689 | URBAN | Other |  | 63 | 145 | 0.0062777 | 0.0043295 | N
10/06/2017 | 21:22 | ZN129:PA46 | URBAN | Other |  | 1 | 263 | 0.00018058 | 6.8722e-05 | N
10/06/2017 | 21:40 | ZN129:PA46 | URBAN | Other |  | 1 | 244 | 0.00016783 | 6.8722e-05 | N
10/06/2017 | 22:09 | ZN129:PA46 | URBAN | Other |  | 1 | 215 | 0.00014808 | 6.8722e-05 | N
13/06/2017 | 09:06 | ZN1290:PA11 | URBAN | Other |  | 1 | 263 | 0.00018078 | 6.8722e-05 | N
13/06/2017 | 11:10 | ZN630:PA15 | URBAN | Other |  | 51 | 38 | 0.0013318 | 0.0035048 | N
14/06/2017 | 17:44 | ZN15005:PA12 | URBAN | Other |  | 1 | 50 | 3.4292e-05 | 6.8722e-05 | N
29/06/2017 | 07:23 | ZN15014:PA12 | SHORT RURAL | Other |  | 1 | 181 | 0.00080845 | 0.0004476 | N
29/06/2017 | 19:55 | 807:74181 | SHORT RURAL | Other |  | 1 | 159 | 0.00071087 | 0.0004476 | N
30/06/2017 | 12:37 | 810:74062 | SHORT RURAL | Other |  | 1 | 128 | 0.00057226 | 0.0004476 | N
29/06/2017 | 17:57 | ZN9900:PA13 | URBAN | Other |  | 829 | 4 | 0.0022762 | 0.056904 | N
29/06/2017 | 17:57 | ZN9900:PA2 | URBAN | Other |  | 655 | 4 | 0.0017984 | 0.044961 | N
04/07/2016 | 07:10 | 801:74118 | URBAN | Third Party | Fire | 15 | 35 | 0.00036361 | 0.0010389 | N
19/07/2016 | 15:09 | 520:48172 | SHORT RURAL | Third Party | Fire | 1 | 81 | 0.00036801 | 0.00045433 | N
11/08/2016 | 02:40 | ZN1287:PA11 | URBAN | Third Party | Fire | 58 | 125 | 0.0050137 | 0.004011 | N
20/08/2016 | 07:21 | ZN9550:PA3 | URBAN | Third Party | Fire | 55 | 64 | 0.0024422 | 0.0038159 | N
30/09/2016 | 11:48 | 264:81236 | SHORT RURAL | Third Party | Fire | 1 | 87 | 0.00039463 | 0.00045377 | N
12/10/2016 | 09:56 | ZN1285:PA23 | URBAN | Third Party | Fire | 1 | 123 | 8.5136e-05 | 6.9048e-05 | N
20/10/2016 | 02:57 | ZN10999:PA11 | URBAN | Third Party | Fire | 117 | 78 | 0.006304 | 0.0080821 | N
05/11/2016 | 19:51 | 264:81244 | SHORT RURAL | Third Party | Fire | 83 | 493 | 0.18412 | 0.037349 | N
07/11/2016 | 17:31 | 504:48033 | SHORT RURAL | Third Party | Fire | 231 | 591 | 0.61434 | 0.10395 | N
25/12/2016 | 22:20 | 813:89062 | SHORT RURAL | Third Party | Fire | 2 | 190 | 0.0017061 | 0.00089794 | N
26/12/2016 | 15:28 | 812:19071 | SHORT RURAL | Third Party | Fire | 1 | 56 | 0.00024925 | 0.00044897 | N
27/12/2016 | 11:36 | ZN630:PA3 | URBAN | Third Party | Fire | 1 | 233 | 0.00016074 | 6.8909e-05 | N
29/12/2016 | 09:33 | ZN711:PA33 | URBAN | Third Party | Fire | 1 | 837 | 0.0005766 | 6.891e-05 | N
03/01/2017 | 02:54 | ZN3425:PA34 | URBAN | Third Party | Fire | 18 | 651 | 0.008075 | 0.0012404 | N
14/01/2017 | 09:36 | 265:81649 | URBAN | Third Party | Fire | 1 | 177 | 0.00012173 | 6.8886e-05 | N
18/01/2017 | 16:51 | 507:80923 | SHORT RURAL | Third Party | Fire | 847 | 38 | 0.14308 | 0.38018 | N
20/01/2017 | 04:04 | ZN9700:PA24 | URBAN | Third Party | Fire | 1 | 295 | 0.00020327 | 6.8882e-05 | N
18/01/2017 | 23:11 | 507:80923 | SHORT RURAL | Third Party | Fire | 2 | 29 | 0.00026033 | 0.00089771 | N
05/02/2017 | 08:34 | 507:80922 | SHORT RURAL | Third Party | Fire | 13 | 156 | 0.0090877 | 0.0058255 | N
09/02/2017 | 09:05 | 810:74050 | SHORT RURAL | Third Party | Fire | 27 | 160 | 0.019331 | 0.012082 | N
11/02/2017 | 00:38 | ZN12650:PA17 | URBAN | Third Party | Fire | 12 | 605 | 0.0050009 | 0.0008266 | N
23/02/2017 | 11:05 | ZN35900:PA22 | URBAN | Third Party | Fire | 3 | 425 | 0.00087826 | 0.00020665 | N
25/02/2017 | 03:51 | 509:33395 | LONG RURAL | Third Party | Fire | 2 | 169 | 0.12033 | 0.0712 | N
06/03/2017 | 14:06 | 230:81440 | SHORT RURAL | Third Party | Fire | 2 | 324 | 0.0028983 | 0.00089453 | N
15/04/2017 | 02:08 | 520:48172 | SHORT RURAL | Third Party | Fire | 1 | 86 | 0.00038256 | 0.00044527 | N
30/05/2017 | 18:09 | ZN13000:PA5 | SHORT RURAL | Third Party | Fire | 39 | 150 | 0.026194 | 0.017457 | N
01/07/2016 | 10:14 | ZN12630:PA23 | SHORT RURAL | Third Party | Other | 1 | 436 | 0.0019838 | 0.00045526 | N
06/07/2016 | 15:01 | 258:80787 | URBAN | Third Party | Other | 12 | 330 | 0.0027453 | 0.00083111 | N
07/07/2016 | 20:30 | ZN1193:PA17 | URBAN | Third Party | Other | 1 | 150 | 0.00010381 | 6.9245e-05 | N
08/07/2016 | 20:54 | 258:80793 | URBAN | Third Party | Other | 124 | 46 | 0.0039498 | 0.0085865 | N
13/07/2016 | 13:01 | ZN72:PA35 | URBAN | Third Party | Other | 12 | 76 | 0.0006316 | 0.00083105 | N
17/07/2016 | 18:37 | 202:34250 | URBAN | Third Party | Other | 1 | 127 | 8.818e-05 | 6.9243e-05 | N
20/07/2016 | 11:45 | ZN15008:PA5 | URBAN | Third Party | Other | 123 | 25 | 0.002146 | 0.0085149 | N
20/07/2016 | 13:44 | 801:74118 | URBAN | Third Party | Other | 1 | 136 | 9.4091e-05 | 6.9227e-05 | N
23/07/2016 | 04:20 | 264:81240 | SHORT RURAL | Third Party | Other | 1 | 74 | 0.00033385 | 0.00045391 | N
23/07/2016 | 09:47 | 202:34260 | URBAN | Third Party | Other | 1 | 96 | 6.6143e-05 | 6.9235e-05 | N
23/07/2016 | 09:54 | 813:89065 | URBAN | Third Party | Other | 1 | 107 | 7.3955e-05 | 6.9235e-05 | N
05/08/2016 | 10:40 | ZN9900:PA8 | URBAN | Third Party | Other | 1 | 170 | 0.00011743 | 6.9177e-05 | N
06/08/2016 | 18:00 | ZN7900:PA6 | URBAN | Third Party | Other | 102 | 162 | 0.011456 | 0.0070562 | N
25/08/2016 | 10:32 | ZN9700:PA12 | URBAN | Third Party | Other | 1 | 478 | 0.00033021 | 6.9094e-05 | N
03/09/2016 | 13:19 | 256:80646 | URBAN | Third Party | Other | 1 | 105 | 7.2355e-05 | 6.9041e-05 | N
07/09/2016 | 14:32 | ZN15001:PA16 | URBAN | Third Party | Other | 1 | 37 | 2.5695e-05 | 6.9043e-05 | N
09/09/2016 | 13:45 | ZN9245:PA3 | URBAN | Third Party | Other | 1 | 495 | 0.00034179 | 6.9058e-05 | N
20/09/2016 | 16:06 | 801:74118 | URBAN | Third Party | Other | 2 | 242 | 0.00033474 | 0.00013813 | N
27/09/2016 | 14:38 | 203:8084 | URBAN | Third Party | Other | 1 | 257 | 0.00017732 | 6.9047e-05 | N
06/10/2016 | 05:14 | 224:80344 | URBAN | Third Party | Other | 1 | 96 | 6.63e-05 | 6.9062e-05 | N
23/10/2016 | 11:09 | 511:29878 | SHORT RURAL | Third Party | Other | 9 | 121 | 0.0048915 | 0.0040521 | N
27/10/2016 | 11:22 | ZN1068:PA16 | URBAN | Third Party | Other | 1 | 67 | 4.6485e-05 | 6.9037e-05 | N
04/11/2016 | 17:16 | 812:19071 | SHORT RURAL | Third Party | Other | 1 | 289 | 0.0013024 | 0.00044998 | N
06/11/2016 | 21:00 | 264:81244 | SHORT RURAL | Third Party | Other | 1 | 151 | 0.00067844 | 0.00044999 | N
09/11/2016 | 13:02 | 801:74121 | LONG RURAL | Third Party | Other | 1 | 128 | 0.045588 | 0.035625 | N
09/11/2016 | 16:57 | ZN15001:PA18 | URBAN | Third Party | Other | 1 | 214 | 0.00014801 | 6.9031e-05 | N
09/11/2016 | 17:46 | ZN14891:PA12 | SHORT RURAL | Third Party | Other | 1 | 193 | 0.00087008 | 0.00045 | N
14/11/2016 | 08:16 | ZN14891:PA12 | SHORT RURAL | Third Party | Other | 6 | 913 | 0.02465 | 0.0026986 | N
14/11/2016 | 17:10 | ZN195:PA11 | URBAN | Third Party | Other | 33 | 281 | 0.0063906 | 0.0022774 | N
23/11/2016 | 19:44 | ZN3472:PA30 | URBAN | Third Party | Other | 1 | 209 | 0.00014404 | 6.8998e-05 | N
24/11/2016 | 16:06 | 801:74121 | LONG RURAL | Third Party | Other | 1 | 134 | 0.047704 | 0.0356 | N
28/11/2016 | 07:05 | 810:74058 | SHORT RURAL | Third Party | Other | 1 | 45 | 0.00020225 | 0.00044945 | N
01/12/2016 | 18:17 | 239:82129 | SHORT RURAL | Third Party | Other | 1 | 88 | 0.00039535 | 0.00044927 | N
02/12/2016 | 09:33 | ZN15001:PA16 | URBAN | Third Party | Other | 1 | 87 | 5.9773e-05 | 6.9009e-05 | N
07/12/2016 | 09:54 | ZN15014:PA12 | SHORT RURAL | Third Party | Other | 1 | 214 | 0.00095988 | 0.00044928 | N
08/12/2016 | 11:20 | ZN1600:PA23ABC | CBD | Third Party | Other | 1 | 625 | 0.02012 | 0.0032193 | N
12/12/2016 | 14:29 | 514:18137 | SHORT RURAL | Third Party | Other | 1 | 27 | 0.00012222 | 0.00044935 | N
13/12/2016 | 19:20 | 528:83011 | SHORT RURAL | Third Party | Other | 1 | 70 | 0.00031372 | 0.00044935 | N
14/12/2016 | 21:12 | ZN14144:PA2 | SHORT RURAL | Third Party | Other | 1 | 78 | 0.00034885 | 0.00044936 | N
15/12/2016 | 13:42 | ZN2400:PA21 | URBAN | Third Party | Other | 27 | 206 | 0.0038336 | 0.001861 | N
16/12/2016 | 10:31 | ZN12570:PA24 | SHORT RURAL | Third Party | Other | 1 | 88 | 0.00039677 | 0.00044908 | N
17/12/2016 | 11:00 | 515:35193 | SHORT RURAL | Third Party | Other | 1 | 147 | 0.00066016 | 0.00044909 | N
17/12/2016 | 13:10 | ZN35400:PA97 | URBAN | Third Party | Other | 9 | 490 | 0.0030403 | 0.00062034 | N
18/12/2016 | 11:49 | ZN15014:PA20 | URBAN | Third Party | Other | 1 | 562 | 0.00038723 | 6.8926e-05 | N
20/12/2016 | 15:10 | ZN12610:PA2 | URBAN | Third Party | Other | 1 | 200 | 0.00013775 | 6.8927e-05 | N
23/12/2016 | 12:15 | ZN5868:PA5 | SHORT RURAL | Third Party | Other | 1 | 35 | 0.00015714 | 0.00044896 | N
23/12/2016 | 23:52 | ZN12610:PA2 | URBAN | Third Party | Other | 115 | 163 | 0.012904 | 0.0079245 | N
26/12/2016 | 15:39 | ZN931:PA9 | URBAN | Third Party | Other | 20 | 76 | 0.0010493 | 0.0013782 | N
27/12/2016 | 01:18 | 523:33505 | URBAN | Third Party | Other | 1 | 548 | 0.00037762 | 6.8909e-05 | N
28/12/2016 | 20:31 | ZN15004:PA5 | URBAN | Third Party | Other | 1 | 749 | 0.00051578 | 6.8909e-05 | N
29/12/2016 | 17:27 | 508:82580 | SHORT RURAL | Third Party | Other | 1 | 965 | 0.0043334 | 0.00044897 | N
30/12/2016 | 14:29 | ZN180:PA27 | URBAN | Third Party | Other | 47 | 164 | 0.0052976 | 0.0032388 | N
30/12/2016 | 14:29 | ZN180:PA28 | URBAN | Third Party | Other | 73 | 165 | 0.0082818 | 0.0050305 | N
30/12/2016 | 14:39 | 511:29873 | URBAN | Third Party | Other | 1 | 38 | 2.5864e-05 | 6.891e-05 | N
30/12/2016 | 18:16 | ZN15014:PA20 | URBAN | Third Party | Other | 1 | 1,297 | 0.00089404 | 6.891e-05 | N
01/01/2017 | 23:34 | ZN3472:PA30 | URBAN | Third Party | Other | 48 | 76 | 0.0025067 | 0.0033077 | N
03/01/2017 | 10:07 | 227:13020 | SHORT RURAL | Third Party | Other | 1 | 68 | 0.00030531 | 0.00044898 | N
04/01/2017 | 12:39 | ZN15014:PA12 | SHORT RURAL | Third Party | Other | 1 | 20 | 9.1817e-05 | 0.00044898 | N
05/01/2017 | 12:22 | ZN10990:PA11 | URBAN | Third Party | Other | 1 | 158 | 0.00010855 | 6.8913e-05 | N
05/01/2017 | 18:51 | ZN12640:PA2 | URBAN | Third Party | Other | 1 | 98 | 6.7857e-05 | 6.8913e-05 | N
09/01/2017 | 08:17 | 227:13015 | SHORT RURAL | Third Party | Other | 4 | 153 | 0.0027467 | 0.0017952 | N
16/01/2017 | 09:53 | ZN9550:PA27 | URBAN | Third Party | Other | 13 | 172 | 0.0015403 | 0.00089552 | N
16/01/2017 | 11:46 | ZN12610:PA23 | URBAN | Third Party | Other | 1 | 118 | 8.1354e-05 | 6.8886e-05 | N
16/01/2017 | 16:42 | 238:34141 | SHORT RURAL | Third Party | Other | 11 | 266 | 0.013142 | 0.0049374 | N
17/01/2017 | 08:49 | ZN15010:PA1 | URBAN | Third Party | Other | 1 | 304 | 0.00020963 | 6.8887e-05 | N
19/01/2017 | 19:30 | 507:80926 | URBAN | Third Party | Other | 1 | 210 | 0.00014465 | 6.8881e-05 | N
22/01/2017 | 18:59 | ZN847:PA44 | URBAN | Third Party | Other | 1 | 91 | 6.2683e-05 | 6.8883e-05 | N
23/01/2017 | 15:59 | ZN12630:PA3 | SHORT RURAL | Third Party | Other | 1 | 426 | 0.00191 | 0.00044886 | N
28/01/2017 | 13:12 | ZN9118:PA20 | URBAN | Third Party | Other | 2 | 258 | 0.00035489 | 0.00013775 | N
29/01/2017 | 16:55 | 813:89063 | SHORT RURAL | Third Party | Other | 1 | 254 | 0.0011407 | 0.00044826 | N
30/01/2017 | 16:18 | 513:48051 | URBAN | Third Party | Other | 1 | 123 | 8.4739e-05 | 6.8875e-05 | N
31/01/2017 | 10:09 | ZN35900:PA20 | URBAN | Third Party | Other | 1 | 470 | 0.00032386 | 6.8876e-05 | N
31/01/2017 | 10:17 | ZN129:PA18 | URBAN | Third Party | Other | 1 | 119 | 8.2284e-05 | 6.8876e-05 | N
03/02/2017 | 08:10 | ZN15014:PA5 | URBAN | Third Party | Other | 1 | 380 | 0.00026153 | 6.8867e-05 | N
08/02/2017 | 18:57 | ZN3922:PA29 | URBAN | Third Party | Other | 1 | 325 | 0.00022355 | 6.8876e-05 | N
09/02/2017 | 06:44 | 243:80083 | SHORT RURAL | Third Party | Other | 5 | 478 | 0.010695 | 0.0022374 | N
10/02/2017 | 15:33 | ZN630:PA41 | URBAN | Third Party | Other | 10 | 257 | 0.0017703 | 0.00068883 | N
11/02/2017 | 08:21 | 520:48172 | SHORT RURAL | Third Party | Other | 1 | 108 | 0.0004826 | 0.00044747 | N
11/02/2017 | 13:06 | ZN15006:PA13 | URBAN | Third Party | Other | 1 | 599 | 0.00041239 | 6.8883e-05 | N
11/02/2017 | 20:00 | 232:33413 | URBAN | Third Party | Other | 92 | 28 | 0.0017744 | 0.0063372 | N
15/02/2017 | 13:33 | ZN14891:PA5 | SHORT RURAL | Third Party | Other | 1 | 267 | 0.0011901 | 0.00044631 | N
17/02/2017 | 16:51 | 807:74181 | SHORT RURAL | Third Party | Other | 1 | 73 | 0.00032527 | 0.0004466 | Y
17/02/2017 | 17:36 | 807:74181 | SHORT RURAL | Third Party | Other | 1 | 27 | 0.00011887 | 0.0004466 | Y
17/02/2017 | 23:37 | 523:33508 | SHORT RURAL | Third Party | Other | 1 | 136 | 0.00060715 | 0.0004466 | Y
18/02/2017 | 12:17 | 807:74181 | SHORT RURAL | Third Party | Other | 1 | 367 | 0.0016397 | 0.00044661 | N
18/02/2017 | 15:54 | ZN9118:PA17 | URBAN | Third Party | Other | 1 | 354 | 0.0002442 | 6.889e-05 | N
22/02/2017 | 17:07 | ZN874:PA2 | URBAN | Third Party | Other | 1 | 341 | 0.00023469 | 6.8893e-05 | N
23/02/2017 | 10:53 | 206:34438 | URBAN | Third Party | Other | 1 | 1,391 | 0.00095834 | 6.8883e-05 | N
23/02/2017 | 18:09 | ZN10999:PA29 | URBAN | Third Party | Other | 1 | 1,255 | 0.00086475 | 6.8883e-05 | N
02/03/2017 | 11:26 | 261:81865 | URBAN | Third Party | Other | 1 | 1,259 | 0.00086701 | 6.8881e-05 | N
04/03/2017 | 07:16 | 813:89062 | SHORT RURAL | Third Party | Other | 1 | 167 | 0.00074733 | 0.00044728 | N
08/03/2017 | 10:30 | ZN2635:PA44 | URBAN | Third Party | Other | 1 | 420 | 0.0002893 | 6.888e-05 | N
08/03/2017 | 09:52 | 812:19072 | SHORT RURAL | Third Party | Other | 1 | 118 | 0.00052648 | 0.00044617 | N
16/03/2017 | 20:46 | 801:74121 | LONG RURAL | Third Party | Other | 1 | 107 | 0.038273 | 0.035625 | N
17/03/2017 | 10:15 | ZN10999:PA4 | URBAN | Third Party | Other | 1 | 434 | 0.00029903 | 6.8877e-05 | N
17/03/2017 | 17:21 | ZN5868:PA30 | URBAN | Third Party | Other | 1 | 85 | 5.8396e-05 | 6.8877e-05 | N
18/03/2017 | 03:50 | 502:48010 | SHORT RURAL | Third Party | Other | 5 | 270 | 0.0060001 | 0.0022223 | N
18/03/2017 | 21:24 | 520:48172 | SHORT RURAL | Third Party | Other | 1 | 298 | 0.0013262 | 0.00044445 | N
19/03/2017 | 00:01 | ZN9700:PA20 | URBAN | Third Party | Other | 1 | 1,171 | 0.00080645 | 6.8879e-05 | N
22/03/2017 | 17:25 | 511:29880 | URBAN | Third Party | Other | 1 | 405 | 0.00027911 | 6.8881e-05 | N
22/03/2017 | 17:36 | ZN12630:PA1 | SHORT RURAL | Third Party | Other | 1 | 863 | 0.0038378 | 0.00044447 | N
27/03/2017 | 08:06 | 802:82220 | SHORT RURAL | Third Party | Other | 1 | 294 | 0.0013049 | 0.00044384 | N
30/03/2017 | 07:48 | 238:34148 | SHORT RURAL | Third Party | Other | 7 | 107 | 0.0033223 | 0.0031049 | N
30/03/2017 | 17:17 | 228:7490 | SHORT RURAL | Third Party | Other | 1 | 6 | 2.861e-05 | 0.00044356 | N
30/03/2017 | 21:09 | 520:48172 | SHORT RURAL | Third Party | Other | 1 | 106 | 0.00047017 | 0.00044356 | N
02/04/2017 | 08:51 | 513:48056 | SHORT RURAL | Third Party | Other | 3 | 96 | 0.0012778 | 0.0013359 | N
02/04/2017 | 14:50 | 801:74121 | LONG RURAL | Third Party | Other | 1 | 130 | 0.046429 | 0.035714 | N
04/04/2017 | 11:56 | ZN36800:PA57 | URBAN | Third Party | Other | 110 | 184 | 0.013926 | 0.0075687 | N
08/04/2017 | 10:48 | ZN3922:PA22 | URBAN | Third Party | Other | 68 | 611 | 0.028578 | 0.0046771 | N
09/04/2017 | 19:49 | 807:74179 | SHORT RURAL | Third Party | Other | 1 | 226 | 0.0010065 | 0.00044534 | N
09/04/2017 | 20:18 | ZN15015:PA15 | SHORT RURAL | Third Party | Other | 1 | 592 | 0.0026364 | 0.00044534 | N
13/04/2017 | 13:29 | ZN1673:PA2 | URBAN | Third Party | Other | 1 | 330 | 0.00022722 | 6.8788e-05 | N
14/04/2017 | 15:08 | ZN1673:PA14 | URBAN | Third Party | Other | 34 | 74 | 0.0017215 | 0.0023395 | N
17/04/2017 | 12:44 | 504:48033 | SHORT RURAL | Third Party | Other | 1 | 363 | 0.0016171 | 0.00044528 | N
26/04/2017 | 13:29 | 257:81987 | URBAN | Third Party | Other | 1 | 62 | 4.2825e-05 | 6.8776e-05 | N
03/05/2017 | 18:40 | 812:19066 | SHORT RURAL | Third Party | Other | 1 | 184 | 0.00081566 | 0.0004439 | N
05/05/2017 | 10:38 | ZN36200:PA8 | SHORT RURAL | Third Party | Other | 1 | 411 | 0.0018242 | 0.00044382 | N
16/05/2017 | 09:30 | ZN3154:PA5 | URBAN | Third Party | Other | 1 | 600 | 0.00041227 | 6.8736e-05 | N
16/05/2017 | 22:59 | 515:35197 | LONG RURAL | Third Party | Other | 1 | 60 | 0.021296 | 0.035702 | N
26/05/2017 | 12:25 | 228:7486 | URBAN | Third Party | Other | 1 | 190 | 0.00013057 | 6.8723e-05 | Y
30/05/2017 | 09:03 | 202:34250 | URBAN | Third Party | Other | 1 | 45 | 3.1074e-05 | 6.8722e-05 | N
02/06/2017 | 04:00 | ZN398:PA2 | URBAN | Third Party | Other | 1 | 179 | 0.00012334 | 6.8722e-05 | N
06/06/2017 | 14:36 | ZN12630:PA8 | SHORT RURAL | Third Party | Other | 1 | 203 | 0.00090968 | 0.0004476 | N
08/06/2017 | 17:43 | 243:80081 | SHORT RURAL | Third Party | Other | 1 | 292 | 0.0013051 | 0.0004476 | N
09/06/2017 | 14:15 | ZN35400:PA52 | URBAN | Third Party | Other | 1 | 198 | 0.00013624 | 6.8722e-05 | N
10/06/2017 | 10:28 | ZN690:PA15 | URBAN | Third Party | Other | 1 | 2,092 | 0.0014377 | 6.8722e-05 | N
13/06/2017 | 09:59 | ZN1673:PA14 | URBAN | Third Party | Other | 1 | 741 | 0.00050955 | 6.8722e-05 | N
15/06/2017 | 08:22 | 516:48067 | SHORT RURAL | Third Party | Other | 3 | 118 | 0.0015845 | 0.0013428 | N
20/06/2017 | 11:32 | ZN116:PA76 | URBAN | Third Party | Other | 1 | 387 | 0.00026619 | 6.8722e-05 | N
22/06/2017 | 15:23 | ZN398:PA29 | URBAN | Third Party | Other | 1 | 395 | 0.00027143 | 6.8722e-05 | N
23/06/2017 | 16:18 | ZN3472:PA8 | URBAN | Third Party | Other | 1 | 191 | 0.00013089 | 6.8642e-05 | N
23/06/2017 | 16:29 | 507:80923 | SHORT RURAL | Third Party | Other | 1 | 203 | 0.00090677 | 0.0004476 | N
23/06/2017 | 18:58 | ZN847:PA39 | URBAN | Third Party | Other | 36 | 159 | 0.003927 | 0.0024711 | N
25/06/2017 | 11:43 | 243:80075 | SHORT RURAL | Third Party | Other | 1 | 230 | 0.0010296 | 0.0004476 | N
26/06/2017 | 11:45 | ZN9037:PA7 | URBAN | Third Party | Other | 1 | 81 | 5.56e-05 | 6.8642e-05 | N
26/06/2017 | 21:04 | 232:33413 | URBAN | Third Party | Other | 11 | 76 | 0.00057385 | 0.00075507 | N
28/06/2017 | 14:44 | ZN15001:PA18 | URBAN | Third Party | Other | 11 | 323 | 0.0024389 | 0.00075507 | N
30/06/2017 | 12:39 | 810:74062 | SHORT RURAL | Third Party | Other | 1 | 131 | 0.00058621 | 0.0004476 | N
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## Amendments
This sheet may be used to identify amendments made to data resubmitted to the AER.
NSP data amendments
Worksheet | Table | Comments
Contents
Instructions