## Instructions
Electricity Distribution Network Service Provider
Annual Reporting RIN
This template is to be used by Ausgrid to fulfil its reporting obligations to the AER.
INSTRUCTIONS
GENERAL | Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting.
CONFIDENTIAL INFORMATION | Please use the macro at the top of each worksheet to identify confidential information in the confidential workbook.
-Do this by selecting the cell or cells that contain confidential information and then run the Mark selection as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential. -To reverse this, select the cell or cells and run the Return selection to NON-CONFIDENTIAL macro.
RESPONSES | Please return four (4) files to the AER: 1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 2. An actual and an estimate version with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response. Use the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public.
AMENDMENTS | If an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. NSPs must identify the reason for the amendments in the Amendment Reason box on the Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. .
NSP may use Amended Data macro to highlight cells that contain amended data. NB: if data is also CONFIDENTIAL, re-apply the Confidentiality macro after applying the Amended macro
Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER
UNITS OF MEASURE | All amounts are to be unrounded and reported on a one for one basis: that is 1000 is to be entered as '1000'. Applicable units of measure may be identified in the table column headings or row descriptors.
INPUT / NON-INPUT CELLS
Yellow = Input cell (mandatory)
Darker yellow = input cell (mandatory)
Orange = input cell (if data available)
Grey = Not applicable/No inputs required
PLEASE DO NOT ENTER TEXT into cells that are to contain numeric data.
NAVIGATION | Many tables in the worksheets have been "grouped" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin (for Row groupings) or above the columns (for column groupings).

## Business & other details
CATEGORY ANALYSIS
Ausgrid
2018-19
BUSINESS & OTHER DETAILS
INSTRUCTIONS
Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells.
SUBMISSION PARTICULARS INPUT SHEET
ENTITY DETAILS
Business Name
| Short name |  |  | Ausgrid
| ACN/ABN |  |  | 67505337385
| Business Address | [7 empty] | Postal Address
| Address 1 |  |  | 24-28 Campbell St. |  |  |  | Address 1 | GPO Box 4009
| Address 2 | [6 empty] | Address 2
| Suburb |  |  | SYDNEY |  |  |  | Suburb | SYDNEY
| State |  |  | NSW | Post code | 2000 |  | State | NSW | Post code | 2001
`
Contact Names
Name
Phone
Email
REGULATORY CONTROL PERIODS
|  |  | Commencing year | 2018-19
ANNUAL RINS
|  |  | Final year | 2020-21
SUBMISSION DETAILS
|  |  | RIN type | Category Analysis
|  |  | Source | Reporting
|  | THIS FILE | Data Quality | Consolidated
|  |  | Confidentiality Status | Public
|  |  | Amended RIN Amendment Reason | .20191129 - 6.3 amended (D19/188405) 20220207 - 2.6 amended to update costs #13526897 21/05/2024 - #16,723,124 - 2.1.1 and 2.1.2 DFA correction
|  |  | Submission Date | dd/mm/yy
Contents
Instructions

## Contents
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
CONTENTS
| 1. Business details | 2. Expenditure
| 4. Alternative control services | 5. Network information | 6. Service & quality
Business & other details
2.1 Expenditure summary & reconciliation
2.3 Augex project data
2.5 Connections
2.2 Repex
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency response
2.10 Overheads
2.6 Non-network
4.3 Ancillary services - Fee-based services
4.4 Ancillary services - Quoted services
4.1 Public lighting
4.2 Metering
5.4 Maximum demand & utilisation - Spatial
5.2 Asset age profile
5.3 Maximum demand - network level
6.3 Sustained interruptions
2.11 Labour
2.12 Input tables
2.3 (b) Augex data
2.1 Expenditure summary & reconciliation
2.3 (a) Augex project data
2.5 Connections
2.2 Repex
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency response
2.6 Non-network
2.3 (b) Augex data

## 2.1 Expenditure summary
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.1 EXPENDITURE SUMMARY & RECONCILIATION
There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.1.1 - STANDARD CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2018-19
Replacement expenditure | 427236927
Connections | 11257355
Augmentation Expenditure | 19033052
Non-network | 241242767
Capitalised network overheads | 117479732
Capitalised corporate overheads | 8001454
Metering
Public Lighting
balancing item | 116821247
capcons (included in the above) | 116821247
TOTAL GROSS CAPEX (including capcons) | 941072534
2.1.2 - STANDARD CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2018-19
Vegetation management | 38067701
Maintenance | 28608014
Emergency response | 24396719
Non-network | 114066524
Network overheads | 104839610
Corporate overheads | 111509305
Metering | 0
Public Lighting
balancing item
TOTAL OPEX | 421487873
2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2018-19
Connections | 0
Capitalised network overheads | 9076348
Capitalised corporate overheads | 1214148
Metering | 3333175
Public lighting | 27769010
Fee and quoted | 20580675
balancing item | -10290496
TOTAL CAPEX | 51682860
2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2018-19
Connections | 0
Network overheads | 26249903
Corporate overheads | 14800979
Metering | 23451708
Public lighting | 14439850
Fee and quoted | 50557350
0
balancing item | -41050882
TOTAL OPEX | 88448908
2.1.5 - DUAL FUNCTION ASSETS CAPEX
EXPENDITURE ($0's)
2018-19
Replacement expenditure | 38116613
Connections | 322212
Augmentation Expenditure | 6789199
Non-network | 18998051
Capitalised network overheads | 8362679
Capitalised corporate overheads | 672606
balancing item
capcons (included in the above)
TOTAL GROSS CAPEX (including capcons) | 73261360
2.1.6 - DUAL FUNCTION ASSETS OPEX
EXPENDITURE ($0's)
2018-19
Vegetation management | 2191352
Maintenance | 1646809
Emergency response | 1404387
Non-network | 6566194
Network overheads | 6035050
Corporate overheads | 6418989
balancing item
TOTAL OPEX | 24262781
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.2 Repex
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.2 REPEX
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY
|  |  | EXPENDITURE ($0's) | ASSET REPLACEMENTS (0's) | ASSET FAILURES (0's)
ASSET GROUP | ASSET CATEGORY |  | 2018-19 | 2018-19 | 2018-19
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole |  | 528544.91 | 536 | 0
| ˂ = 1 kV; Wood |  | 15348380.52 | 1537.75 | 317
| > 1 kV & < = 11 kV; Wood |  | 7968080.08 | 772.09 | 67
| ˃ 11 kV & < = 22 kV; Wood |  | 35921.31 | 3.89 | 1
| > 22 kV & < = 66 kV; Wood |  | 1304928.4 | 74.85 | 19
| > 66 kV & < = 132 kV; Wood |  | 288360.4 | 14.83 | 1
| > 132 kV; Wood |  | 0 | 0 | 0
| ˂ = 1 kV; Concrete |  | 30719.21 | 3.17 | 0
| > 1 kV & < = 11 kV; Concrete |  | 15228.57 | 1.57 | 0
| ˃ 11 kV & < = 22 kV; Concrete |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; Concrete |  | 230637.61 | 11.86 | 0
| > 66 kV & < = 132 kV; Concrete |  | 169667.08 | 8.73 | 0
| > 132 kV; Concrete |  | 0 | 0 | 0
| ˂ = 1 kV; Steel |  | 390575.29 | 40.26 | 7
| > 1 kV & < = 11 kV; Steel |  | 2310.86 | 0.24 | 0
| ˃ 11 kV & < = 22 kV; Steel |  | 420.16 | 0.04 | 0
| > 22 kV & < = 66 kV; Steel |  | 15116.11 | 0.78 | 0
| > 66 kV & < = 132 kV; Steel |  | 949169.92 | 3.92 | 0
| > 132 kV; Steel |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
POLE TOP STRUCTURES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 1670964.82 | 659.1 | 338
| > 1 kV & < = 11 kV |  | 796921.32 | 314.34 | 162
| ˃ 11 kV & < = 22 kV |  | 102828.15 | 40.56 | 0
| > 22 kV & < = 66 kV |  | 785827.48 | 59 | 32
| > 66 kV & < = 132 kV |  | 203773.01 | 17 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 346256.14 | 62 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV |  | 4060102 | 101.2 | 1140
| > 1 kV & < = 11 kV |  | 7702662 | 196.14 | 335
| ˃ 11 kV & < = 22 kV ; SWER |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Single-Phase |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase |  | 0 | 0 | 1
| > 22 kV & < = 66 kV |  | 824663 | 7.23 | 55
| > 66 kV & < = 132 kV |  | 6 | 0 | 5
| > 132 kV |  | 0 | 0 | 0
| Other |  | 1599429 | 229.43 | 46
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 37447243 | 110.68 | 292
| > 1 kV & < = 11 kV |  | 12845981.93 | 31.16 | 255
| > 11 kV & < = 22 kV |  | 0 | 0 | 0
| > 22 kV & < = 33 kV |  | 33841782.8 | 41.69 | 14
| > 33 kV & < = 66 kV |  | 0 | 0 | 0
| > 66 kV & < = 132 kV |  | 51450961.13 | 23.84 | 1
| > 132 kV |  | 0 | 0 | 0
| Other |  | 7972108.7 | 204 | 281
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type |  | 9731363 | 10546.63 | 5889
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type |  | 698822 | 757.37 | 0
| ˂ = 11 kV ; Residential ; Complex Type |  | 122974 | 26 | 98
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type |  | 0 | 0 | 0
| ˂ = 11 kV ; Subdivision ; Complex Type |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision |  | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 132 kV ; Subdivision |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 166351.71 | 4.65 | 12
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 34144.17 | 0.62 | 1
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 299433.99 | 8.37 | 29
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 956040.28 | 17.36 | 57
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 795644.73 | 8.12 | 17
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 95578.56 | 0.88 | 4
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 893086.89 | 5.76 | 7
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase |  | 1553646.27 | 20.24 | 23
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA |  | 931554.12 | 1.3 | 2
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA |  | 12615285.08 | 17.75 | 42
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA |  | 170566.42 | 0.24 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA |  | 498577.98 | 0.69 | 3
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA |  | 19013979.7 | 11.26 | 27
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA |  | 6179606.5 | 4.04 | 18
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA |  | 209163.88 | 0.02 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA |  | 0 | 0 | 0
| Other |  | 2790375.02 | 106.25 | 19
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; FUSE |  | 5202531.98 | 2021 | 218
| ˂ = 11 kV ; Switch |  | 11631619.28 | 403 | 372
| ˂ = 11 kV ; Circuit Breaker |  | 19338849.89 | 297.12 | 143
| > 11 kV & < = 22 kV ; Switch |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker |  | 0 | 0 | 1
| > 22 kV & < = 33 kV ; Switch |  | 1564313.37 | 25 | 9
| > 22 kV & < = 33 kV ; Circuit Breaker |  | 8978789.87 | 39.72 | 35
| > 33 kV & < = 66 kV ; Switch |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker |  | 278485.88 | 1.18 | 1
| > 66 kV & < = 132 kV ; Switch |  | 1301964.5 | 12 | 9
| > 66 kV & < = 132 kV ; Circuit Breaker |  | 4285968.96 | 7.23 | 17
| > 132 kV ; Switch |  | 0 | 0 | 0
| > 132 kV ; Circuit Breaker |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road |  | 0 | 0 | 0
| Luminaires ; Minor Road |  | 0 | 0 | 0
| Brackets ; Major Road |  | 0 | 0 | 0
| Brackets ; Minor Road |  | 0 | 0 | 0
| Lamps ; Major Road |  | 0 | 0 | 0
| Lamps ; Minor Road |  | 0 | 0 | 0
| Poles / Columns ; Major Road |  | 0 | 0 | 0
| Poles / Columns ; Minor Road |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices |  | 25790571.43 | 1645.32 | 280
| Local Network Wiring Assets |  | 0 | 0 | 0
| Communications Network Assets |  | 2886971.44 | 5.26 | 77
| Master Station Assets |  | 0 | 0 | 0
| Communications Site Infrastructure |  | 0 | 0 | 44
| Communications Linear Assets |  | 420219.95 | 0 | 107
| AFLC |  | 2877300.22 | 12.17 | 84
| Other |  | 34516282 | 0 | 11
OTHER BY: DNSP DEFINED | DISTRIBUTION SUBSTATIONS - OTHER |  | 6194655.75 | 802 | 112
| DISTRIBUTION VOLTAGE REGULATION |  | 0 | 0 | 8
| OVERHEAD CONDUCTORS - OTHER |  | 7235046.33 | 242.8 | 0
| TOWERS - > = 33 KV ; REFURBISHMENT |  | 2675826.65 | 24 | 1
| TRANSFORMERS - OTHER |  | 1878792.05 | 38 | 0
| UNDERGROUND CABLES - OTHER |  | 1102505.47 | 92 | 0
| ZONE & SUBTRANSMISSION SUBSTATIONS - OTHER |  | 16722502.88 | 142.27 | 42
| DISTRIBUTION SUBSTATIONS - NOT AGE RELATED |  | 4969193.7 | 345 | 0
| OVERHEAD CONDUCTORS - NOT AGE RELATED |  | 4209807.53 | 281.23 | 0
| ZONE & SUBTRANSMISSION SUBSTATIONS - NOT AGE RELATED |  | 15606952.14 | 268 | 0
| FIELD DEVICES - NOT AGE RELATED |  | 694895.99 | 43 | 0
| UNDERGROUND CABLES - NOT AGE RELATED |  | 4725046.72 | 18 | 0
| SWITCHGEAR - NOT AGE RELATED |  | 0 | 0 | 0
| TRANSFORMERS - NOT AGE RELATED |  | 0 | 0 | 0
| LAND (I.E. STRATEGIC SYSTEM PROPERTY) |  | 7659075.14 | 0 | 0
| SUBSTATION BUILDINGS |  | 23314669.63 | 33.05 | 0
| SUPPORT COSTS (I.E. GIS DATA CAPTURE AND SWITCHING) |  | 0 | 0 | 0
| BALANCING ITEM (I.E. MULTI-NODE DISCREPANCY) |  | 0 | 0 | 0
| Switchgear - < = 11 KV ; CIRCUIT BREAKER REFURBISHMENT |  | 2604936.06 | 105 | 0
| 0 |  | 0 | 0 | 0
2.2.2 - SELECTED ASSET CHARACTERISTICS
|  |  | ASSET VOLUMES CURRENTLY IN COMMISSION | ASSET REPLACEMENTS (0's)
ASSET GROUP | METRIC | UNITS | 2018-19 | 2018-19
TOTAL POLES BY: FEEDER TYPE | Total CBD poles | Number | 55 | 0
| Total urban poles | Number | 271536 | 1704
| Total rural long poles | Number | 8912 | 56
| Total rural short poles | Number | 113834 | 714
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH BY FEEDER TYPE | Conductors CBD | KM | 2.0204 | 0.03
| Conductors urban | KM | 11807.166 | 157.18
| Conductors rural long | KM | 1251.036 | 16.65
| Conductors rural short | KM | 9816.2502 | 130.67
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH MATERIAL TYPE | OH conductor LV ABC | KM | 1490.4748 | 12.68
| OH conductor steel | KM | 479.6369 | 117.85
| OH conductor ACSR | KM | 5087.4095 | 61.47
| OH conductor AAAC | KM | 808.2675 | 1.25
| OH conductor AAC | KM | 9382.2599 | 51.66
| OH conductor HDBC | KM | 7893.4607 | 53.48
| Other | KM | 790.9379 | 6.15
UNDERGROUND CABLES BY: CABLE LENGTH BY FEEDER TYPE | Cable CBD | KM | 424.3861 | 6
| Cable urban | KM | 11341.0587 | 159
| Cable rural long | KM | 20.627 | 0
| Cable rural short | KM | 2981.7146 | 42
TRANSFORMERS BY: TOTAL MVA | Total MVA replaced | MVA | 38047.79 | 138.307
| Total MVA disposed of | MVA | 0 | 99.739
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(a) Augex
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.3 AUGEX PROJECT DATA
There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped. See the Instructions sheet on how to group or ungroup tables.
2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
SUBSTATION ID | SUBSTATION TYPE (drop down) | PROJECT ID | PROJECT TYPE (drop down) | PROJECT TRIGGER (drop down) | VOLTAGE (KV) | SUBSTATION RATING NORMAL CYCLIC (MVA) |  | SUBSTATION RATING N-1 EMERGENCY (MVA) |  | TRANSFORMERS |  |  | SWITCHGEAR |  | CAPACITORS |  |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | PRE | POST | PRE | POST | UNITS ADDED | MVA ADDED | EXPENDITURE ($0's) | UNITS ADDED | EXPENDITURE ($0's) | MVAR ADDED | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
NEW ROCKDALE 132/11KV ZN (SJ-05993) | Zone substation | ARA_04.1.0008 | New substation establishment | Other | 132/11 | 58 | 75 | 27.1 | 65 | 2 | 75 | 2255238.44 | 37 | 3169625.97 | 0 | $- |  |  | 2998603.29 | 34348.72 | 2995365.91 | 8140645.71 | 1180868.63 | 20740347.95 | 2010-2020 | 0 | 0 | 0 | 1541377 | 0
ENGADINE ZN 132KV CONVERSION (SJ-04726 & SJ-05749) | Zone substation | ARA_04.2.0015 | Substation upgrade - capacity | Other | 132/11 | 48 | 75 | 31.7 | 60.1 | 2 | 75 | 1216085 | 6 | 1717765 | 0 | $- |  |  | 2364899 | 30546.78 | 3146135.67 | 12610825 | 3057994 | 24113703.67 | 2009-2019 | 0 | 0 | 0 | 0 | 0
CROWS NEST ZN 132KV CONVERSION (SJ-05651) | Zone substation | ARA_05.1.0006 | Substation upgrade - capacity | Other | 132/11 | 94.5 | 114.3 | 50.8 | 57.1 | 2 | 114.3 | 1151215 | 6 | 3992573 | 12 | 573844 |  |  | 3813080 | 35747.28 | 3947387.7 | 2350267.85 | 418904 | 16247271.55 | 2009-2020 | 0 | 0 | 0 | 6319600 | 0
NEW MACQUARIE 132/33KV STS (SJ-00297) | Subtransmission substation | ARA_05.3.0035U | New substation establishment | Demand growth | 132/33 | 0 | 280 | 0 | 140 | 2 | 280 | 3748309.06 | 24 | 2793669.29 | 0 | $- |  |  | 1615567.5 | 42855.05 | 3745136.95 | 7820448.85 | 253400.48 | 19976532.12 | 2018-2023 | 0 | 0 | 0 | 0 | 0
NEW KOORAGANG 132/33KV STS (SJ-04087 & SJ-05642) | Subtransmission substation | ARA_07.2.0007C | New substation establishment | Demand growth | 132/33 | 0 | 285.8 | 0 | 142.9 | 2 | 285.8 | 3857136 | 26 | 1337699 | 0 | $- |  |  | 11195561 | 139507.06 | 9085495.87 | 13452790 | 1392345 | 40321026.87 | 2008-2019 | 0 | 0 | 0 | 2247799 | 0
NEW RATHMINES 132/11KV ZN (SJ-03278 & SJ-00039) | Zone substation | ARA_07.4.0010 | New substation establishment | Demand growth | 132/11 | 37.5 | 76.2 | 0 | 38.1 | 2 | 76.2 | 2133339 | 20 | 1097124 | 0 | $- |  |  | 4843867 | 78496.02 | 7383315.88 | 8859847 | 1870469 | 26187961.88 | 2008-2019 | 0 | 0 | 0 | 412244 | 491970
NEW CHARLESTOWN 132/11KV ZN (SJ-05319 & SJ-06071) | Zone substation | ARA_07.5.0005 | New substation establishment | Other | 132/11 | 75 | 113 | 36.1 | 60.2 | 2 | 113 | 3363772 | 28 | 4634442 | 12 | 589227 |  |  | 3393630 | 57082.31 | 5997193.76 | 8468800 | 1042346 | 27489410.76 | 2008-2019 | 0 | 0 | 0 | 1216740 | 0
NEW ABERDEEN 66/11KV ZN (SJ-05634 & SJ-06031) | Zone substation | ARA_08.2.0014 | New substation establishment | Other | 66/11 | 12.5 | 46.4 | 6.3 | 25.5 | 2 | 46.4 | 2550397 | 9 | 2390186 | 0 | $- |  |  | 1475788.33 | 57052.63 | 5960988 | 5147367.86 | 491100 | 18015827.19 | 2008-2019 | 0 | 0 | 0 | 1158497 | 0
|  | Non material projects - [actual] | [21 empty] | 2121160.1 |  |  |  |  | 0 | 0
AUG232_1 | AUG232_2 | AUG232_3 | AUG232_4 | AUG232_5 | AUG232_6 | ED_AUG232_00001 | ED_AUG232_00002 | ED_AUG232_00003 | ED_AUG232_00004 | ED_AUG232_00005 | ED_AUG232_00006 | ED_AUG232_00007 | ED_AUG232_00008 | ED_AUG232_00009 | ED_AUG232_00010 | ED_AUG232_00011 | ED_AUG232_00012 | ED_AUG232_00013 | ED_AUG232_00014 | ED_AUG232_00015 | ED_AUG232_00016 | ED_AUG232_00017 | ED_AUG232_00018 | ED_AUG232_00019 | ED_AUG232_00020 | ED_AUG232_00021
2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
LINE ID | PROJECT ID | PROJECT TYPE | PROJECT TRIGGER |  | VOLTAGE (KV) | ROUTE LINE LENGTH ADDED |  |  |  | POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS) |  |  | OVERHEAD LINES |  |  | UNDERGROUND CABLES |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | KM ADDED |  |  |  | POLES/TOWERS ADDED | POLES/TOWERS UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
NEW ROCKDALE 132KV CONNECTION WORKS (SJ-06161) | ARA_04.1.0008 | New line on new route - dual circuit | Other |  | 132 | 0.1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 425575.25 | 0 | 1545.65 | 140915.98 | 549896.73 | 0 | 1116387.96 | 2017-2020 | 0 | 0 | 0 | 0 | 0 | New line on new route - single circuit
CROWS NEST ZN 132KV CONNECTION WORKS (SJ-05651) | ARA_05.1.0006 | Other | Other |  | 132 | 0.1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2281851 | 0 | 6561.96 | 669023.44 | 1997.17 | 0 | 2952871.61 | 2009-2020 | 0 | 0 | 0 | 0 | 0 | New line on new route - dual circuit
NEW MACQUARIE STS 132KV CONNECTIONS (SJ-00298) | ARA_05.3.0035U | New line on new route - single circuit | Demand growth |  | 132 | 1.465 |  |  |  | 18 | 0 | 271828.26 | 1.24 | 0 | 96640.12 | 0.225 | 0 | 373830.13 | 0 | 8288.3 | 724321.39 | 3915899.41 | 96137.06 | 5478656.36 | 2021-2023 | 0 | 0 | 0 | 0 | 1655020 | New line on new route - other
NEW KOORAGANG STS 132KV FEEDERS 96X & 97M (SJ-04087) | ARA_07.2.0007C | New line on new route - single circuit | Demand growth |  | 132 | 16 |  |  |  | 150 | 0 | 1587 | 16 | 0 | 1587 | 0 | 0 | 25947.12 | 155328 | 140231.44 | 1107718.57 | 445217.62 | 22759 | 1760144.3 | 2008-2019 | 0 | 0 | 0 | 0 | 154 | Line rebuild over existing route - single circuit
NEW MEDOWIE ZN 33KV FEEDERS TM13, TM4, 81401(3) (SJ-00166) | ARA_07.8.0032A | New line on new route - single circuit | Demand growth |  | Other | 12 |  |  |  | 130 | 0 | 407054 | 12 | 0 | 407054 | 0 | 0 | 36542 | 1664689.98 | 60487.01 | 4004376.53 | 3066973.44 | 400100 | 9986789.95 | 2010-2020 | 0 | 0 | 0 | 0 | 46915 | Line rebuild over existing route - dual circuit
NEW ABERDEEN ZN 66KV FEEDERS 82257 & 82244 (SJ-05634) | ARA_08.2.0014 | Line rebuild over existing route - single circuit | Other |  | 66 | 30.8 |  |  |  | 10 | 191 | 184123 | 1 | 31 | 184190 | 0 | 0 | 0 | 0 | 2404.8 | 273915 | 290239.54 | 0 | 932467.54 | 2008-2019 | 0 | 0 | 0 | 0 | 0 | Reconductor - Single circuit
NEW 132KV FEEDER 90Y BEACONSFIELD-BELMORE PARK (SJ-00167) | ARA_01.1.0035A | New line on new route - single circuit | Other |  | 132 | 5.4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1380157.92 | 0 | 15308.44 | 1477600.3 | 10112658.43 | 19591.03 | 12990007.68 | 2015-2020 | 0 | 0 | 0 | 0 | 0 | Reconductor - Dual circuit
Reconductor - Other
Line upgrade - raising/retensoring
Line upgrade - voltage upgrade
Line upgrade - capacity
String spare circuit
Other
| Non material projects - [actual] | [22 empty] | 45215.02
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(b) Augex
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.3 AUGEX DATA
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS.
DESCRIPTOR METRICS
PROJECT TYPE |  | UNITS ADDED (0's) | UNITS UPGRADED (0's)
| UNITS | 2018-19 | 2018-19
HV Feeder Augmentations - Overhead Lines | Circuit line length in km | 0.012 | 4.325
HV Feeder Augmentations - Underground Cables | Circuit line length in km | 1.553 | 0
LV Feeder Augmentations - Overhead Lines | Circuit line length in km | 0.409 | 1.351
LV Feeder Augmentations - Underground Cables | Circuit line length in km | 0.015 | 0.075
Distribution Substation Augmentations - Pole Mounted | Number | 1 | 0
Distribution Substation Augmentations - Ground Mounted | Number | 0 | 1
Distribution Substation Augmentations - Indoor | Number | 0 | 0
COST METRICS
TOTAL DIRECT EXPENDITURE - Project Type |  | EXPENDITURE ($0's)
2018-19
HV Feeder Augmentations - Overhead Lines |  | 3724552
HV Feeder Augmentations - Underground Cables |  | 5513011
HV Feeder Non-Material Projects |  | 626655
LV Feeder Augmentations - Overhead Lines |  | 3803013
LV Feeder Augmentations - Underground Cables |  | 1157258
LV Feeder Non-Material Projects |  | 1346489
Distribution Substation Augmentations - Pole Mounted |  | 506893
Distribution Substation Augmentations - Ground Mounted |  | 38910
Distribution Substation Augmentations - Indoor |  | 511903
2.3.4 - AUGEX DATA - TOTAL EXPENDITURE
AUGMENTATION CAPEX (As incurred) |  | EXPENDITURE ($0's)
2018-19
Subtransmission Substations, Switching Stations, Zone Substations |  | 7664952
Subtransmission Lines |  | 927117
HV Feeders |  | 9864218
HV Feeders - Land Purchases and Easements |  | 0
Distribution Substations |  | 1057706
Distribution Substations - Land Purchases And Easements |  | 0
LV Feeders |  | 6306760
LV Feeders - Land Purchases And Easements |  | 0
Other Assets |  | 1498
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.5 Connections
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.5 CONNECTIONS
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.5.1 - DESCRIPTOR METRICS
<<<GROUP-ROW>>>
VOLUMES AND EXPENDITURE
CONNECTION SUBCATEGORY | DESCRIPTOR METRIC | UNITS | 2018-19
RESIDENTIAL | Underground connections | 0's | 8
| Overhead connections | 0's | 2
| Distribution substation installed | MVA added | 0
| Distribution substations installed | 0's | 0
| Distribution substation installed | total spend $0s | 145290
| Augmentation HV | net circuit km added | 1.037
| Augmentation HV | total spend $0s | -5060
| Augmentation LV | net circuit km added | 0
| Augmentation LV | total spend $0s | 0
| Mean days to connect residential customer with LV single phase connection | 0's | 0
| Volume of GSL breaches for residential customers | 0's | 0
| Volume of customer complaints relating to connection services | 0's | 0
| GSL payments | $0s | 0
COMMERCIAL/INDUSTRIAL | Underground connections | 0's | 391
| Overhead connections | 0's | 106
| Distribution substation installed | MVA added | 0
| Distribution substations installed | 0's | 0
| Distribution substation installed | total spend $0s | 1419306
| Augmentation HV | net circuit km added | 0.09
| Augmentation HV | total spend $0s | 7148008
| Augmentation LV | net circuit km added | 0.022
| Augmentation LV | total spend $0s | 2857575
SUBDIVISION | Underground connections | 0's | 1
| Overhead connections | 0's | 0
| Distribution substation installed | MVA added | 0
| Distribution substations installed | 0's | 0
| Distribution substation installed | total spend $0s | 0
| Augmentation HV | net circuit km added | 0.591
| Augmentation HV | total spend $0s | 10822
| Augmentation LV | net circuit km added | 0
| Augmentation LV | total spend $0s | 0
| Cost per lot ($) | $0s | 0
EMBEDDED GENERATION | Underground connections | 0's | 0
| Overhead connections | 0's | 0
| Distribution substation installed | MVA added | 0
| Distribution substations installed | 0's | 0
| Distribution substation installed | total spend $0s | 0
| Augmentation HV | net circuit km added | 0
| Augmentation HV | total spend $0s | 3625
| Augmentation LV | net circuit km added | 0
| Augmentation LV | total spend $0s | 0
2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION
|  | EXPENDITURE ($0's) | VOLUMES (0's)
CONNECTION SUBCATEGORY | CONNECTION CLASSIFICATION | 2018-19 | 2018-19
RESIDENTIAL | Simple connection LV | 0 | 0
| Complex connection LV | 0 | 0
| Complex connection HV | 140230 | 10
COMMERCIAL/INDUSTRIAL | Simple connection LV | 2639961 | 370
| Complex connection HV (customer connected at LV, minor HV works) | 383665 | 103
| Complex connection HV (customer connected at LV, upstream asset works) | 1253255 | 16
| Complex connection HV (customer connected at HV) | 689423 | 2
| Complex connection sub-transmission | 6458586 | 6
SUBDIVISION | Complex connection LV | 0 | 0
| Complex connection HV (no upstream asset works) | 0 | 0
| Complex connection HV (with upstream asset works) | 10822 | 1
EMBEDDED GENERATION | Simple connection LV | 3625 | 0
| Complex connection HV (small capacity) | 0 | 0
| Complex connection HV (large capacity) | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.6 Non-network
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.6 NON NETWORK EXPENDITURE
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.6.1 - NON-NETWORK EXPENDITURE
EXPENDITURE ($0's)
SERVICE SUBCATEGORY | ASSET CATEGORY |  |  | 2018-19
OPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 1974015.59
| Recurrent expenditure |  |  | 53621887.53
| Non-recurrent expenditure |  |  | 2181533.64
MOTOR VEHICLES | Car |  |  | 1296111.79
| Light commercial vehicle |  |  | 5949850.76
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 3614374
| Heavy commercial vehicle |  |  | 2354730.25
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 47852185
OTHER | Other expenditure
OTHER - DNSP nominated | Motor vehicles - Cable handling equipment |  |  | 175186.39
| Motor vehicles - Crane borer (HCV) |  |  | 790183.13
| Motor vehicles - Material handling |  |  | 312088.67
| Motor vehicles - Vehicle loading cranes |  |  | 127184.96
| Motor vehicles - Other plant |  |  | 383386.05
CAPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 7876467.15
| Recurrent expenditure |  |  | 28292855.86
| Non-recurrent expenditure |  |  | 58171879.38
MOTOR VEHICLES | Car |  |  | 1279374.33
| Light commercial vehicle |  |  | 8914739.08
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 1105205.88
| Heavy commercial vehicle |  |  | 2178436.81
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 143256455
OTHER | Other expenditure |  |  | 4912881
OTHER - DNSP nominated | Motor vehicles - Cable handling equipment |  |  | 0
| Motor vehicles - Crane borer (HCV) |  |  | 526729.62
| Motor vehicles - Material handling |  |  | 394222.84
| Motor vehicles - Vehicle loading cranes |  |  | 777500.78
| Motor vehicles - Other plant |  |  | 182
| Motor vehicles - BlueWorx Project |  |  | 0
| Fleet - Telematics |  |  | 2553887.66
2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE
VOLUMES (0's)
NON-NETWORK CATEGORY | DESCRIPTOR METRIC |  |  | 2018-19
IT & COMMUNICATIONS | Employee numbers |  |  | 2853
| User numbers |  |  | 3479
| Number of devices |  |  | 9820
2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES
VOLUMES / %
NON-NETWORK CATEGORY | ASSET CATEGORY | DESCRIPTOR METRIC | UNITS | 2018-19
MOTOR VEHICLES | CAR | Average kilometres travelled | 0's | 12522
|  | Number purchased | 0's | 50
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 216.7333
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 95.9%
| LIGHT COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 12843
|  | Number purchased | 0's | 206
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 1036.6759
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 95.9%
| ELEVATED WORK PLATFORM (LCV) | Average kilometres travelled | 0's
|  | Number purchased | 0's
|  | Number leased | 0's
|  | Number in fleet | 0's
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent)
| ELEVATED WORK PLATFORM (HCV) | Average kilometres travelled | 0's | 8251
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 184.1274
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 95.9%
| HEAVY COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 6682
|  | Number purchased | 0's | 14
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 301.1251
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 95.9%
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.7 Vegetation management
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.7 VEGETATION MANAGEMENT
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Please enter a description for each Zone in table 2.7.1 - Urban and CBD. The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2.
` | 2.7.1 - DESCRIPTOR METRICS BY ZONE
URBAN AND CBD
2018-19
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km | 9875
|  | Number of maintenance spans | 0's | 887963
|  | Total length of maintenance spans | km | 9875
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's | 0.57797
|  | Average frequency of cutting cycle | years | 1
| ZONE 2 | Route line length within zone | km | 0
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km | 0
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
RURAL
2018-19
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km | 9473
|  | Number of maintenance spans | 0's | 254319
|  | Total length of maintenance spans | km | 9473
|  | Length of vegetation corridors | km | 2101
|  | Average number of trees per maintenance span | 0's | 2.1592
|  | Average frequency of cutting cycle | years | 1
| ZONE 2 | Route line length within zone | km | 0
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km | 0
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
2.7.2 - EXPENDITURE METRICS BY ZONE
EXPENDITURE ($0's)
| ZONES | SERVICE SUBCATEGORY |  | 2018-19
| ZONE 1 | Tree trimming (excluding hazard trees) |  | 34447910
|  | Hazard tree cutting |  | 269880
|  | Ground clearance |  | 369338
|  | Vegetation corridor clearance |  | 369338
|  | Inspection |  | 2380433
|  | Audit |  | 969054
|  | Contractor liaison expenditure |  | 646036
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 807064
| ZONE 2 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 3 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 4 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 5 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 6 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 7 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 8 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 9 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 10 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 11 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 12 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 13 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 14 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 15 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 16 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 17 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
| ZONE 18 | Tree trimming (excluding hazard trees) |  | 0
|  | Hazard tree cutting |  | 0
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 0
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 0
2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS
VOLUMES (0's)
| DESCRIPTOR METRIC |  |  | 2018-19
| Number of fire starts caused by vegetation grow-ins (NSP responsibility) |  |  | 0
| Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility) |  |  | 7
| Number of fire starts caused by vegetation grow-ins (other party responsibility) |  |  | 0
| Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility) |  |  | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.8 Maintenance
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.8 MAINTENANCE
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
|  |  |  | ASSET QUANTITY (0's) |  | AVERAGE AGE OF ASSET GROUP | INSPECTION CYCLE (YEARS) | MAINTENANCE CYCLE (YEARS)
|  |  |  | AT YEAR END | INSPECTED / MAINTAINED
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2018-19 | 2018-19 | 2018-19
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 506390 | 1350 | 36 | 5 | 0
| Service lines | Number of customers | Number | 716079 | 0 | 29 | 0 | 0
Pole inspection and treatment | All poles | Number of poles | Number | 511647 | 106787 | 36 | 5 | 0
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 21969 | 4585 | 41 | 5 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 14989 | 13447 | 31 | 0 | 0
| 33 KV and above | Length (KM) | KM | 1000 | 356 | 35 | 5 | 0
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 402 | 346.95 | 40 | 0 | 0
| Non-CBD | Length (KM) | KM | 15586 | 13456.05 | 31 | 0 | 0
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 34059 | 0 | 26 | 0 | 0
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 22757 | 1875 | 25 | 12 | 30
| Distribution substation - other equipment | Earth mat | Number | 32301 | 9293 | 29 | 12 | 0
| Distribution substation - property | Number of distribution substation properties maintained | Number | 2968 | 6930 | 36 | 0 | 0
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 487 | 1223 | 26 | 0.5 | 6
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 31 | 0 | 43 | 12 | 0
| Transformers - HV | Number of HV transformers | Number | 0 | 0 | 0 | 0 | 0
| Zone substation - other equipment | Number of zone substations maintained | Number | 203 | 22023 | 38 | 0.5 | 0
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 203 | 11530 | 38 | 0.08 | 0
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 194925 | 18071 | 11 | 4 | 4
| Major roads | Number of public lights maintained | Number | 55354 | 8122 | 18 | 4 | 4
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 890 | 0 | 28 | 0 | 0
Protection systems maintenance | Protection systems | Number of systems | Number | 23930 | 0 | 30 | 0 | 0
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets | Length (KM) | Number | 894.77 | 6970 | 34.85 | 5 | 0
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 0 | 0 | 0 | 0 | 0
Ground clearance - access tracks | Access tracks | Number | Number | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
EXPENDITURE ($0'S)
|  |  |  | ROUTINE MAINTENANCE | NON-ROUTINE MAINTENANCE
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2018-19 | 2018-19
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 2308750 | 2196420
| Service lines | Number of customers | Number | 11624 | 42138
Pole inspection and treatment | All poles | Number of poles | Number | 4738472 | 159449
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 1421508 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 320304 | 392691
| 33 KV and above | Length (KM) | KM | 523759 | 999783
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 21216 | 35001
| Non-CBD | Length (KM) | KM | 822846 | 1357472
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 20925 | 495335
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 1218252 | 309971
| Distribution substation - other equipment | Earth mat | Number | 2018504 | 865736
| Distribution substation - property | Number of distribution substation properties maintained | Number | 259493 | 229973
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 689613 | 382272
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 0 | 0
| Transformers - HV | Number of HV transformers | Number | 0 | 0
| Zone substation - other equipment | Number of zone substations maintained | Number | 3857335 | 1118194
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 2053918 | 755792
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 1766533 | 65707
| Major roads | Number of public lights maintained | Number | 793930 | 29530
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 146535 | 13382
Protection systems maintenance | Protection systems | Number of systems | Number | 261562 | 283701
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets | Length (KM) | Number | 1353377 | 806055
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 0 | 0
Ground clearance - access tracks | Access tracks | Number | Number | 0 | 0
Other | 0 | 0 |  | 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.9 Emergency Response
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.9 EMERGENCY RESPONSE
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)
EXPENDITURE ($0's)
2018-19
(A) TOTAL EMERGENCY RESPONSE EXPENDITURE
Total Expenditure | 25801105.58
(B) MAJOR EVENTS O&M EXPENDITURE
(C) MAJOR EVENT DAYS O&M EXPENDITURE
20 October 2018 | 150207.79
15-16 December 2018 | 921458.83
20 December 2019 | 756935.55
5 January 2019 | 663624.98
31 January 2019 | 304659.41
13 February 2019 | 326880.35
14 March 2019 | 177565.17
19 Match 2019 | 341070.52
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10 Overheads
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.10 OVERHEADS
Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. Ausgrid is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If Ausgrid is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. Ausgrid is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN. |  | Choose Response drop down selection
Worksheet 2.10A
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Instructions Please enter a description for each expenditure category as currently reported under Ausgrid's annual RIN.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2018-19
NETWORK OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED NETWORK OVERHEADS
Standard Control Services
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2018-19
CORPORATE OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED CORPORATE OVERHEADS
Standard Control Services
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10(A) Overheads
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.10(A) OVERHEADS
This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options.
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2018-19
OPEX
Standard Control Services | Total | 110874660
Alternative Control Services | Total | 26249903
CAPEX
Standard Control Services | Total | 125842411
Alternative Control Services | Total | 9076348
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total
Unregulated Services | Total | 395531
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2018-19
OPEX
Standard Control Services | Total | 117928294
Alternative Control Services | Total | 14800979
CAPEX
Standard Control Services | Total | 8674060
Alternative Control Services | Total | 1214148
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total
Unregulated Services | Total | 2987095
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.11 Labour
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.11 LABOUR
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.11.1 - COST METRICS PER ANNUM
|  | ASL (0's) | TOTAL LABOUR EXPENDITURE ($0's) | AVERAGE PRODUCTIVE WORK HOURS PER ASL (0's) | STAND-DOWN OCCURENCES PER ASL (0's)
|  | 2018-19 | 2018-19 | 2018-19 | 2018-19
INTERNAL LABOUR EXPENDITURE
CORPORATE OVERHEADS | Executive manager | 5 | 4885674 | 1648
| Senior manager | 14 | 6063725 | 1625
| Manager | 106 | 25783698 | 1531
| Professional | 314 | 65665399 | 1569
| Semi professional | 115 | 20589288 | 1467
| Support staff | 177 | 23945165 | 1512
| Intern, junior staff, apprentice | 4 | 308497 | 1624
NETWORK OVERHEADS | Executive manager | 4 | 3177291 | 1642
| Senior manager | 13 | 4721281 | 1534
| Manager | 255 | 54130049 | 1576 | 1
| Professional | 444 | 89456849 | 1538
| Semi professional | 343 | 66325174 | 1567
| Support staff | 142 | 19942039 | 1560
| Intern, junior staff, apprentice | 1 | 115346 | 1470
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker | 1001 | 164064044 | 1668 | 3
| Skilled non electical worker | 29 | 4151683 | 1599
| Apprentice | 8 | 590665 | 1699
| Unskilled worker | 138 | 17644653 | 1633 | 4
2.11.2 - DESCRIPTOR METRICS
|  | ORDINARY TIME (0's) |  | OVERTIME (0's)
|  | PER ASL | HOURLY RATE PER ASL | PER ASL | HOURLY RATE PER ASL
|  | 2018-19 | 2018-19 | 2018-19 | 2018-19
AVERAGE PRODUCTIVE WORK HOURS PER ASL
CORPORATE OVERHEADS | Executive manager | 1648 | 463
| Senior manager | 1625 | 219
| Manager | 1529 | 130 | 2 | 114
| Professional | 1555 | 98 | 14 | 117
| Semi professional | 1459 | 99 | 8 | 107
| Support staff | 1494 | 76 | 18 | 84
| Intern, junior staff, apprentice | 1620 | 42 | 5 | 50
NETWORK OVERHEADS | Executive manager | 1642 | 364
| Senior manager | 1534 | 200
| Manager | 1493 | 111 | 84 | 114
| Professional | 1493 | 103 | 45 | 139
| Semi professional | 1504 | 101 | 63 | 114
| Support staff | 1498 | 75 | 63 | 86
| Intern, junior staff, apprentice | 1418 | 81 | 52 | 117
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker | 1484 | 78 | 184 | 92
| Skilled non electical worker | 1498 | 72 | 101 | 82
| Apprentice | 1681 | 37 | 18 | 49
| Unskilled worker | 1469 | 61 | 165 | 74
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.12 Input tables
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
2.12 INPUT TABLES
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.12.1 - INPUT TABLES
|  | DIRECT MATERIAL EXPENDITURE | DIRECT LABOUR EXPENDITURE | CONTRACT EXPENDITURE | OTHER EXPENDITURE | RELATED PARTY CONTRACT EXPENDITURE | RELATED PARTY CONTRACT MARGIN EXPENDITURE
EXPENDITURE ($0's)
|  | 2018-19 | 2018-19 | 2018-19 | 2018-19 | 2018-19 | 2018-19
VEGETATION MANAGEMENT | ZONE 1 | 5617.98 | 2400236.94 | 37836898.69 | 16300
| ZONE 2 | 0 | 0 | 0 | 0
| ZONE 3 | 0 | 0 | 0 | 0
| ZONE 4 | 0 | 0 | 0 | 0
| ZONE 5 | 0 | 0 | 0 | 0
| ZONE 6 | 0 | 0 | 0 | 0
| ZONE 7 | 0 | 0 | 0 | 0
| ZONE 8 | 0 | 0 | 0 | 0
| ZONE 9 | 0 | 0 | 0 | 0
| ZONE 10 | 0 | 0 | 0 | 0
| ZONE 11 | 0 | 0 | 0 | 0
| ZONE 12 | 0 | 0 | 0 | 0
| ZONE 13 | 0 | 0 | 0 | 0
| ZONE 14 | 0 | 0 | 0 | 0
| ZONE 15 | 0 | 0 | 0 | 0
| ZONE 16 | 0 | 0 | 0 | 0
| ZONE 17 | 0 | 0 | 0 | 0
| ZONE 18 | 0 | 0 | 0 | 0
ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 10344.47 | 664333.26 | 1639797.3 | 5898.32
| Pole inspection and treatment | 66376.27 | 403029.28 | 4269066.62 | 0
| Overhead asset inspection | 0 | 1384565.48 | 27807.98 | 9135
| Network underground cable maintenance | 5480.4 | 707715.41 | 129204.87 | 1662.11
| Distribution substation equipment & property maintenance | 15592.4 | 2546928.14 | 952326.4 | 2327.44
| Zone substation equipment maintenance | 84805.4 | 2881249.09 | 1573781.89 | 4687.42
| Zone substation property maintenance | 17970.95 | 602855.63 | 1428855.86 | 3055.74
| Public lighting maintenance | 175274.57 | 183457.43 | 2201730.74 | 0
| Scada & network control maintenance | 490.35 | 22565.4 | 116479.03 | 7000
| Protection systems maintenance | 820.09 | 260665.4 | 0 | 76.61
| Subtransmission asset maintenance - for dnsps with dual function assets | 19075.51 | 922292.15 | 406331.56 | 5677.38
| Other | 0 | 0 | 0 | 0
NON-ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 17284.42 | 1784086.07 | 429167.03 | 8019.99
| Pole inspection and treatment | 5286.66 | 12622.26 | 141540.43 | 0
| Overhead asset inspection | 0 | 0 | 0 | 0
| Network underground cable maintenance | 236019.53 | 791159.1 | 359674.88 | 5620.09
| Distribution substation equipment & property maintenance | 104325.02 | 1520337.21 | 260707.58 | 15287.79
| Zone substation equipment maintenance | 246273.89 | 812521.07 | 412621.36 | 3932.83
| Zone substation property maintenance | 5491.49 | 112830.79 | 591414.07 | 971.02
| Public lighting maintenance | 7294.87 | 61481.7 | 25220.28 | 0
| SCADA & network control maintenance | 0 | 8743.3 | 2176.3 | 1830.9
| Protection systems maintenance | 24718.52 | 258508.77 | 419.57 | 54.41
| Subtransmission asset maintenance - for DNSP with dual function assets | 81252.06 | 415116.05 | 268982.94 | 20142.2
| Other | 0 | 0 | 0 | 0
OVERHEADS | Network overheads | 18982669 | 128171620 | 85295422 | 32766295
| Corporate overheads | 3786566 | 92926264 | 18200461 | 27699796
AUGMENTATION | Subtransmission substations, switching stations, zone substations | 1190485 | 2495236 | 2878368 | 1091014
| Subtransmission lines | 26876 | 473503 | 270440 | 156293
| HV feeders | 1286427 | 3921455 | 2698595 | 1957741
| Distribution substations | 114523 | 555241 | 196597 | 191345
| LV feeders | 446259 | 4003285 | 853333 | 1003882
| Other assets | 969 | 310 | 6 | 213
CONNECTIONS | Simple and complex customer connections | 496154 | 7064910 | 2799817 | 1050585
EMERGENCY RESPONSE | Major storms | 51003 | 1685605 | 908442 | 24743
| Major event days | 37872 | 798480 | 119523 | 9062
PUBLIC LIGHTING | All public lighting services | 10821739 | 13144468 | 10481196 | 7723524
METERING | All metering services | 758685 | 3383609 | 1661670 | 400045
FEE-BASED SERVICES | All fee-based services | 4959 | 13333985 | 343300 | 2816013
QUOTED SERVICES | All quoted services | 117193 | 18671282 | 6911 | 22624559
REPLACEMENT | Poles | 2173540 | 11813909 | 12977091 | 313520
| Pole top structures | 469501 | 2814481 | 566084 | 56506
| Overhead conductors | 1735910 | 10262472 | 1962487 | 37472
| Underground cables | 9952438 | 35729063 | 94004402 | 3630180
| Service lines | 1782384 | 6870447 | 1331129 | 6319
| Transformers | 17236566 | 15160460 | 13746937 | 772420
| Switchgear | 14635008 | 24640953 | 15226214 | 460399
| Public lighting | 0 | 0 | 0 | 0
| SCADA network control and protection systems | 7016412 | 15189243 | 40184108 | 3701989
| Other | 12336890 | 27294078 | 48439720 | 8858249
NON-NETWORK EXPENDITURE | IT and communications | 1523454 | 23711819 | 74296003 | 51583243
| Motor vehicles | 18351654 | 2484658 | 1042307 | 10847965
| Buildings and property | 680598 | 5920963 | 138243297 | 45836887
| Other | 1820503 | 15164 | 2842978 | 233243
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.1 Public lighting
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
4.1 PUBLIC LIGHTING
There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.1.1 - DESCRIPTOR METRICS OVER YEAR
VOLUME (0's)
| LIGHT TYPE |  | 2018-19
POPULATION OF LIGHTS | 1*17W LED |  | 13384
| 1*22W LED |  | 15146
| 1*25W LED GE |  | 4374
| 1*29W LED |  | 15315
| 1*40W TF |  | 252
| 1*80W TF |  | 99
| 1000W MBF |  | 5
| 1000W SON |  | 40
| 1000W SON FLOODLIGHT |  | 8
| 1000W/1500W MBI FLOODLIG |  | 8
| 100W LED ALD |  | 730
| 100W MBI |  | 21
| 100W MBI FLOODLIGHT |  | 5
| 100W SON |  | 938
| 100W SON - PARKVILLE |  | 13
| 100W SON FLOODLIGHT |  | 8
| 100W SON -PLAIN |  | 435
| 125W MBF |  | 2415
| 125W MBF - BOURKE HILL |  | 29
| 125W MBF - HYDE PARK |  | 13
| 125W MBF - NOSTALGIA |  | 1
| 125W MBF - PARKVILLE |  | 5
| 125W MBF -PLAIN |  | 772
| 125W/250W MBF FLOODLIGHT |  | 48
| 135W SOX |  | 28
| 150W SON |  | 18988
| 150W SON - HYDE PARK |  | 6
| 150W SON - PARKVILLE |  | 34
| 150W SON - PARKWAY 1 |  | 232
| 150W SON ACTIVE REACTOR |  | 3339
| 150W SON FLOODLIGHT |  | 232
| 150W SON GEC 'BOSTON 3' |  | 81
| 150W/250W MBI FLOODLIGHT |  | 38
| 17W LED GE P4/P5 |  | 9664
| 17W LED SY AERO P4/P5 |  | 2584
| 17W LED SY RRW |  | 3301
| 2*14W TF - T5 PIERLITE M |  | 68
| 2*20W TF |  | 7255
| 2*20W TF - WAVERLEY |  | 1
| 2*250W SON FLOODLIGHT |  | 25
| 2*26W TF MACQUARIE DEC. |  | 14
| 2*400W SON FLOODLIGHT |  | 5
| 2*40W TF |  | 13
| 2*70W SON - BOURKE HILL |  | 1
| 2*80W MBF - BOURKE HILL |  | 16
| 200W LED ALD |  | 571
| 20W LED GE |  | 24
| 250W MBF |  | 13167
| 250W MBF - PARKWAY 1 |  | 693
| 250W MBI - SMARTPOLE |  | 18
| 250W SON |  | 22219
| 250W SON - PARKVILLE |  | 13
| 250W SON - PARKWAY 1 |  | 49
| 250W SON ACTIVE REACTOR |  | 4364
| 250W SON FLOODLIGHT |  | 1625
| 250W SON GEC 'BOSTON 3' |  | 92
| 28W LED SY |  | 1526
| 298W LED ALD |  | 15
| 2X14W TF - T5 PIERLIGHT |  | 55
| 4*20W TF |  | 1
| 4*20W TF - WAVERLEY |  | 10
| 4*250W SON |  | 6
| 4*40W TF - WAVERLEY |  | 2
| 4*600W SON |  | 2
| 400W MBF |  | 4593
| 400W MBF - B2229 |  | 105
| 400W MBF - PARKWAY 1 |  | 176
| 400W MBF FLOODLIGHT |  | 87
| 400W MBI |  | 24
| 400W MBI - SMARTPOLE |  | 14
| 400W MBI FLOODLIGHT |  | 79
| 400W SON |  | 1582
| 400W SON - PARKWAY 1 |  | 14
| 400W SON ACTIVE REACTOR |  | 440
| 400W SON FLOODLIGHT |  | 500
| 42W CFL- BOURKE HILL |  | 247
| 42W LED LRL |  | 19
| 42W MBF SYLVANIA SUB ECO |  | 38473
| 50W MBF |  | 7579
| 50W MBF - BOURKE HILL |  | 19
| 50W MBF - NOSTALGIA |  | 94
| 50W MBF - PLAIN |  | 127
| 50W SON |  | 289
| 50W SON - NOSTALGIA |  | 2
| 50W SON -PLAIN |  | 2
| 600W SON |  | 1
| 700W MBF FLOODLIGHT |  | 1
| 70W MBI |  | 140
| 70W MBI - MACQUARIE DEC. |  | 116
| 70W MBI II |  | 340
| 70W MBI II AERO |  | 17
| 70W SON |  | 1144
| 70W SON - BOURKE HILL |  | 6
| 70W SON - GEC BOSTON 2 |  | 1
| 70W SON - NOSTALGIA |  | 105
| 70W SON - PARKVILLE |  | 10
| 70W SON - REGAL/FLINDERS |  | 3
| 70W SON BOLLARD |  | 2
| 70W SON FLOODLIGHT |  | 35
| 70W SON -PLAIN |  | 177
| 80W MBF |  | 13750
| 80W MBF - BEGA+CURVE BRA |  | 58
| 80W MBF - BOURKE HILL |  | 1206
| 80W MBF - GEC BOSTON 2 |  | 12
| 80W MBF - NOSTALGIA |  | 587
| 80W MBF - PLAIN |  | 444
| 80W MBF - REGAL/FLINDERS |  | 48
| 80W MBF - SYLVANIA SUBUR |  | 36986
| 80W MBF BOLLARD |  | 69
| 80W MBF TOORAK |  | 140
| LED TRIAL |  | 78
| PRIVATE |  | 3
| TH FLOODLIGHT |  | 24
| Grand Total |  | 254409
4.1.2 - DESCRIPTOR METRICS ANNUALLY
VOLUMES & EXPENDITURE
SERVICE/SERVICE QUALITY | DESCRIPTOR METRIC | UNITS | 2018-19
LIGHT INSTALLATION | Major road light installation | 0's | 520
| Minor road light installation | 0's | 931
| Number of poles installed | 0's | 922
| Total cost | $0s | 5667368.98
LIGHT REPLACEMENT | Major road light replacement | 0's | 1155
| Minor road light replacement | 0's | 4480
| Number of poles replaced | 0's | 244
| Total cost | $0s | 22101640.89
LIGHT MAINTENANCE | Major road light maintenance | 0's | 18395
| Minor road light maintenance | 0's | 25422
| Number of poles installed | 0's | 254409
| Total cost | $0s | 14439850
QUALITY OF SUPPLY | Mean days to rectify/replace public lighting assets | days | 6.2
| GSO breaches | 0's | 206
| GSL payments | $0s | 3090
| Customer complaints | 0's | 2849
4.1.3 - COST METRICS
AVERAGE UNIT COST ($)
ACTIVITY TYPE | LIGHT TYPE |  | 2018-19
LIGHT INSTALLATION | 10.1 LRL P3 2016 |  | 515.68
| 10.1 Gerard P3 2016 |  | 468.53
| 10.2 LRL P3 Cut Off 2016 |  | 515.68
| 10.2 Gerard P3 Cut Off 2016 |  | 447.83
| 10.3 Gerard P4/P5 2016 |  | 437.48
| 10.3 GE Evolve P4/P5 2016 |  | 370.78
| 10.4 Gerard P4/P5 Cut off 16 |  | 447.83
| 10.5 Gerard P4/P5 RRRW 2016 |  | 447.83
| 11.1 LRL V5 2016 |  | 659.54
| 11.2 LRL V5 Cut Off 2016 |  | 659.54
| 11.3 Aldridge V3 2016 |  | 1154.04
| 11.5 Aldridge V1 2016 |  | 1154.04
| 11.6 Aldridge V1 Cut Off 2016 |  | 1141.39
| 11.8 Aldridge V1 High Cut Off 2016 |  | 1292.04
| 100W SON (P09) |  | 549.09
| 150W SON Active Reactor |  | 808.06
| 250W SON Active Reactor |  | 808.06
| 400W SON Active Reactor |  | 903.98
LIGHT REPLACEMENT | 10.1 LRL P3 2016 |  | 515.68
| 10.1 Gerard P3 2016 |  | 468.53
| 10.2 LRL P3 Cut Off 2016 |  | 515.68
| 10.2 Gerard P3 Cut Off 2016 |  | 447.83
| 10.3 Gerard P4/P5 2016 |  | 437.48
| 10.3 GE Evolve P4/P5 2016 |  | 370.78
| 10.4 Gerard P4/P5 Cut off 16 |  | 447.83
| 10.5 Gerard P4/P5 RRRW 2016 |  | 447.83
| 11.1 LRL V5 2016 |  | 659.54
| 11.2 LRL V5 Cut Off 2016 |  | 659.54
| 11.3 Aldridge V3 2016 |  | 1154.04
| 11.5 Aldridge V1 2016 |  | 1154.04
| 11.6 Aldridge V1 Cut Off 2016 |  | 1141.39
| 11.8 Aldridge V1 High Cut Off 2016 |  | 1292.04
| 100W SON (P09) |  | 549.09
| 150W SON Active Reactor |  | 808.06
| 250W SON Active Reactor |  | 808.06
| 400W SON Active Reactor |  | 903.98
LIGHT MAINTENANCE | MBI1x100 |  | 63.49
| SOX1x180 |  | 136
| MBI1x1000 |  | 115.88
| TF1x16 |  | 47.75
| MBI1x150 |  | 97.13
| TF1x176 |  | 55.45
| MBI1x1500 |  | 93.76
| TF1x20 |  | 47.75
| MBI1x250 |  | 62.81
| TF1x236 |  | 55.45
| MBI1x3745 |  | 47.96
| TF1x26 |  | 47.75
| MBI1x400 |  | 63.82
| TF1x40 |  | 70.14
| MBI1x500 |  | 81.28
| TF1x60 |  | 47.75
| MBI1x70 |  | 58.75
| TF1x80 |  | 48.12
| MBI1x70 Internal Ignitor |  | 70.72
| TF2x14 T5 |  | 55.48
| MBI2x400 |  | 77.98
| TF2x20 |  | 58.13
| MBI4x150 |  | 228.83
| TF2x26 |  | 48.33
| SON1x100 |  | 88.12
| TF2x40 |  | 48.33
| SON1x1000 |  | 90.86
| TF2x58 |  | 48.33
| SON1x120 |  | 57.84
| TF2x80 |  | 48.33
| SON1x150 |  | 75.65
| TF4x20 |  | 49.49
| SON1x150 AR |  | 67.75
| TF4x40 |  | 49.49
| SON1x220 |  | 70.08
| TH1x1000 |  | 65.32
| SON1x250 |  | 79.24
| TH1x1500 |  | 63.18
| SON1x250 AR |  | 68.85
| TH1x400 |  | 71.05
| SON1x310 |  | 69
| TH1x500 |  | 59.29
| SON1x360 |  | 69
| TH1x750 |  | 66.07
| SON1x400 |  | 77.08
| INC1x100 |  | 48.1
| SON1x400 AR |  | 95.04
| MBF1x1000 |  | 92.06
| SON1x50 |  | 50.38
| MBF1x125 |  | 47.66
| SON1x70 |  | 67.51
| MBF1x160 |  | 46.4
| SON2x250 |  | 127.96
| MBF1x250 |  | 54.45
| SON2x400 |  | 119.81
| MBF1x400 |  | 54.45
| SON2x70 |  | 98.44
| MBF1x42 (CFL) |  | 44.4
| SON3x70 |  | 186.79
| MBF1x50 |  | 47.85
| SON4x250 |  | 228.72
| MBF1x500 |  | 85.22
| SON4x600 |  | 243.13
| MBF1x700 |  | 75.12
| SOX1x135 |  | 64.29
| MBF1x80 |  | 46.53
| SOX1x150 |  | 64.29
| MBF1x800 |  | 85.22
| MBF2x125 |  | 67.07
| MBF2x175 |  | 53.18
| MBF2x400 |  | 67.5
| MBF2x80 |  | 57.38
| LED1x22 |  | 30.71
| LED1x29 |  | 30.71
| LED1*17 |  | 33.93
| LED1*25 |  | 33.93
| LED1*20 |  | 33.93
| LED1*28 |  | 33.93
| LED1*33 |  | 33.93
| LED1*42 |  | 36.63
| LED1*100 |  | 36.63
| LED1*200 |  | 36.63
| LED1*298 |  | 36.63
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.2 Metering
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
4.2 METERING
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.2.1 - METERING DESCRIPTOR METRIC
VOLUMES (0's)
Asset Category | Asset Subcategory | 2018-19
Meter Type 4 | Single phase meter population
Multi phase meter population
Current transformer connected meter population
Direct connect meter population
Meter Type 5 | Single phase meter population | 427537.24
| Multi phase meter population | 129386.27
| Current transformer connected meter population | 5625.49
| Direct connect meter population | 562549
Meter Type 6 | Single phase meter population | 1535821.44
| Multi phase meter population | 62392.75
| Current transformer connected meter population | 1599.81
| Direct connect meter population | 1599814
4.2.2 - COST METRICS
|  | VOLUMES (0's) | EXPENDITURE ($0's)
Service Subcategory | Meter Type | 2018-19 | 2018-19
Meter purchase | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter testing | Meter Type 4 | 0 | 0
| Meter Type 5 | 525 | 39379.26
| Meter Type 6 | 0 | 0
Meter investigation | Meter Type 4 | 0 | 0
| Meter Type 5 | 5463 | 1476347.94
| Meter Type 6 | 0 | 0
Scheduled meter reading | Meter Type 4 | 0 | 0
| Meter Type 5 | 1939130 | 4167104.48
| Meter Type 6 | 4768911 | 6832342.44
Special meter reading | Meter Type 4 | 0 | 0
| Meter Type 5 | 29501 | 1544237.52
| Meter Type 6 | 0 | 0
New meter installation | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter replacement | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter maintenance | Meter Type 4 | 0 | 0
| Meter Type 5 | 3940 | 1516452.42
| Meter Type 6 | 0 | 0
Remote meter reading | Meter Type 4 | 0 | 0
Remote meter re-configuration | Meter Type 4 | 0 | 0
Other metering | Meter Type 4 |  | 0
| Meter Type 5 |  | 11209018.68
| Meter Type 6 |  | 0
| Meter Type 7 |  | 0
IT infrastructure capex | Meter Type 4 |  | 0
IT infrastructure opex | Meter Type 4 |  | 0
Communications infrastructure capex | Meter Type 4 |  | 0
Communications infrastructure opex | Meter Type 4 |  | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.3 Fee-based services
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
4.3 ANCILLARY SERVICES - FEE BASED SERVICES
4.3.1 - COST METRICS FOR FEE-BASED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2018-19 |  | 2018-19
Common Fee-Based Services | Energisation |  | ED_FEE431_00001
| De-energisation |  | ED_FEE431_00002
| Re-energisation |  | ED_FEE431_00003
Miscellaneous Fee-Based Services | Administration relating to work performed by ASPs - underground urban residential subdivision (vacant lots) up to 5 lots | 7280 | ED_FEE431_00004 | 8
| Administration relating to work performed by ASPs - underground urban residential subdivision (vacant lots) 6 to 10 lots | 12926 | ED_FEE431_00005 | 13
| Administration relating to work performed by ASPs - underground urban residential subdivision (vacant lots) 11 to 40 lots | 74718 | ED_FEE431_00006 | 56
| Administration relating to work performed by ASPs - underground urban residential subdivision (vacant lots) over 40 lots | 32537 | ED_FEE431_00007 | 15
| Administration relating to work perfromed by ASPs - rural overhead subdivisions and rural extensions up to 5 poles | 30521 | ED_FEE431_00008 | 37
| Administration relating to work perfromed by ASPs - rural overhead subdivisions and rural extensions 6 to 10 poles | 2897 | ED_FEE431_00009 | 5
| Administration relating to work perfromed by ASPs - rural overhead subdivisions and rural extensions 11 or more poles | 1672 | ED_FEE431_00010 | 2
| Administration relating to work perfromed by ASPs - subdivision involving substation/s (NOTE: Subset of overall Admin costs.) | 16421 | ED_FEE431_00011 | 92
| Design Information - underground urban residential subdivision (vacant lots) up to 5 lots | 2288 | ED_FEE431_00012 | 8
| Design Information - underground urban residential subdivision (vacant lots) 6 to 10 lots | 7178 | ED_FEE431_00013 | 12
| Design Information - underground urban residential subdivision (vacant lots) 11 to 40 lots | 33887 | ED_FEE431_00014 | 56
| Design Information - underground urban residential subdivision (vacant lots) over 40 lots | 17302 | ED_FEE431_00015 | 15
| Design Information - URD including Kisosk/HVC/PT (NOTE: Subset of overall Des Info costs.) | 10519 | ED_FEE431_00016 | 34
| Design Certification - underground urban residential subdivision (vacant lots) up to 5 lots | 4665 | ED_FEE431_00017 | 19
| Design Certification - underground urban residential subdivision (vacant lots) 6 to 10 lots | 8839 | ED_FEE431_00018 | 15
| Design Certification - underground urban residential subdivision (vacant lots) 11 to 40 lots | 65045 | ED_FEE431_00019 | 66
| Design Certification - underground urban residential subdivision (vacant lots) over 40 lots | 33886 | ED_FEE431_00020 | 18
| Design Certification - rural overhead subdivisions and rural extensions 1 to 5 poles | 10968 | ED_FEE431_00021 | 41
| Design Certification - rural overhead subdivisions and rural extensions 6 to 10 poles | 987 | ED_FEE431_00022 | 5
| Design Certification - rural overhead subdivisions and rural extensions 11 or more poles | 1751 | ED_FEE431_00023 | 2
| Design Certification - underground commercial and industrial or rural subdivisions (vacant lots - no developments) up to 10 lots | 8848 | ED_FEE431_00024 | 16
| Design Certification - underground commercial and industrial or rural subdivisions (vacant lots - no developments) 11 to 40 lots | 2941 | ED_FEE431_00025 | 2
| Design Certification - underground commercial and industrial or rural subdivisions (vacant lots - no developments) over 40 lots | 1873 | ED_FEE431_00026 | 2
| Design Certification - Kisosk/HVC/PT (NOTE: Subset of overall Des Cert costs.) | 100551 | ED_FEE431_00027 | 91
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) first 10 lots - A Grade | 34653 | ED_FEE431_00028 | 647
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) first 10 lots - B Grade | 75783 | ED_FEE431_00029 | 279
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) first 10 lots - C Grade | 2532 | ED_FEE431_00030 | 0
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) next 40 lots - A Grade | 42962 | ED_FEE431_00031 | 1093
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) next 40 lots - B Grade | 45487 | ED_FEE431_00032 | 413
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) next 40 lots - C Grade | 5237 | ED_FEE431_00033 | 0
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) remainder lots - A Grade | 48 | ED_FEE431_00034 | 54
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) remainder lots - B Grade | 1734 | ED_FEE431_00035 | 50
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) remainder lots - C Grade | 491 | ED_FEE431_00036 | 0
| Inspection of service works by level 1 ASPs - underground urban residential subdivisions (vacant lots - no development) travel | 12301 | ED_FEE431_00037 | 303
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 1-5 poles - A Grade | 15703 | ED_FEE431_00038 | 26
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 1-5 poles - B Grade | 36763 | ED_FEE431_00039 | 24
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 1-5 poles - C Grade | 0 | ED_FEE431_00040 | 0
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 6-10 poles - A Grade | 1571 | ED_FEE431_00041 | 7
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 6-10 poles - B Grade | 3421 | ED_FEE431_00042 | 9
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 6-10 poles - C Grade | 0 | ED_FEE431_00043 | 0
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 11+ poles - A Grade | 2507 | ED_FEE431_00044 | 0
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 11+ poles - B Grade | 3807 | ED_FEE431_00045 | 0
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions 11+ poles - C Grade | 0 | ED_FEE431_00046 | 0
| Inspection of service works by level 1 ASPs - Rural overhead subdivisions and rural extensions - travel | 2569 | ED_FEE431_00047 | 97
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) first 10 lots A | 5917 | ED_FEE431_00048 | 27
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) first 10 lots B | 5369 | ED_FEE431_00049 | 60
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) first 10 lots C | 23 | ED_FEE431_00050 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) next 40 lots A | 6121 | ED_FEE431_00051 | 36
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) next 40 lots B | 3167 | ED_FEE431_00052 | 67
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) next 40 lots C | 0 | ED_FEE431_00053 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) remainder A | 0 | ED_FEE431_00054 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) remainder B | 0 | ED_FEE431_00055 | 8
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) remainder C | 0 | ED_FEE431_00056 | 0
| Inspection of service works by level 1 ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) travel | 2517 | ED_FEE431_00057 | 38
| Inspection of service works by level 1 ASPs - HV or LV UG joint, ABS/enclosed switch | 37175 | ED_FEE431_00058 | 155
| Inspection of service works by level 1 ASPs - decommission substation | 41278 | ED_FEE431_00059 | 14
| Inspection of service works by level 1 ASPs - substation (kiosk/PT) or HV Sw cubicle | 159870 | ED_FEE431_00060 | 86
| Inspection of service work by level 2 ASPs - NOSW A Grade | 276088 | ED_FEE431_00061 | 2932
| Inspection of service work by level 2 ASPs - NOSW B Grade | 175374 | ED_FEE431_00062 | 2325
| Inspection of service work by level 2 ASPs - NOSW C Grade | 11293 | ED_FEE431_00063 | 13
| Contestable substation commissioning - underground urban residential subdivisions (vacant lots) | 114709 | ED_FEE431_00064 | 46
| Contestable substation commissioning - rural overhead subdivisions and rural extensions | 40417 | ED_FEE431_00065 | 29
| Contestable substation commissioning - underground commercial and industrial or rural subdivisions (vacant lots - no developments) | 126710 | ED_FEE431_00066 | 12
| Access Permits - underground residential urban subdivisions (vacant lots) | 627784 | ED_FEE431_00067 | 142
| Access Permits - rural overhead subdivisions and rural extensions | 195420 | ED_FEE431_00068 | 36
| Access Permits - underground commercial and industrial or rural subdivisions (vacant lots - no developments) | 137822 | ED_FEE431_00069 | 23
| Access Permits - commercial and industrial developments | 4238866 | ED_FEE431_00070 | 738
| Access Permits - asset relocation or street lighting | 2377437 | ED_FEE431_00071 | 421
| Clearance to Work | 1687667 | ED_FEE431_00072 | 428
| Notices of Arrangement | 137550 | ED_FEE431_00073 | 358
| Supply of conveyancing information: Desk enquiry | 375 | ED_FEE431_00074 | 0
| Supply of conveyancing information: Field visit | 0 | ED_FEE431_00075 | 0
| Connection offers : Basic 100A Connections NOT requiring a load slip | 374019 | ED_FEE431_00076 | 41454
| Connection offers: Basic 100A Connections requiring a load slip / Basic Micro EG Connections >5kW / Basic Over 100A Connection Offer (new or existing site) | 982222 | ED_FEE431_00077 | 2223
| Connection Offers: Standard Off-site or On-site augmentation work | 0 | ED_FEE431_00078 | 1
| Connection Offers: Standard ASP 1 Connections | 134815 | ED_FEE431_00079 | 745
| Authorisation of ASP Level 1 | 102159 | ED_FEE431_00080 | 1183
| Authorisation of ASP Level 2 | 189788 | ED_FEE431_00081 | 790
| Supply & connect temporary supply to one or more customers: Install & remove HV LL links | 0 | ED_FEE431_00082 | 0
| Supply & connect temporary supply to one or more customers: Break & remake HV bonds | 30398 | ED_FEE431_00083 | 6
| Supply & connect temporary supply to one or more customers: Break & remake LV bonds | 97132 | ED_FEE431_00084 | 24
| Rectification of Illegal Connections | 1358 | ED_FEE431_00085 | 7
| Supply & connect temporary supply to one or more customers: Connect & disconnect MG to OH mains | 0 | ED_FEE431_00086 | 0
| Supply & connect temporary supply to one or more customers: Connect & disconnect MG to LV board in Kiosk | 0 | ED_FEE431_00087 | 0
| Site Establishment Fee | 691887 | ED_FEE431_00088 | 24969
| Special Meter Reading for T5&6 meters & MIMO | 6515719 | ED_FEE431_00089 | 499656
| Meter Test (for type 5&6 meters) | 401608 | ED_FEE431_00090 | 257
| Franchise CT Meter Install | 0 | ED_FEE431_00091 | 0
| Off Peak Conversion | 51424 | ED_FEE431_00092 | 489
| Disconnection Visit (Site Visit Completed) | 75673 | ED_FEE431_00093 | 6945
| Disconnection Completed | 1356160 | ED_FEE431_00094 | 13577
| Disconnection Completed Technical/Advanced | 2361614 | ED_FEE431_00095 | 727
| Pillar/Pole Top Disconnection Completed | 68306 | ED_FEE431_00096 | 63
| Pillar/Pole Top Site Visit | 14275 | ED_FEE431_00097 | 66
| Reconnection/Disconnection Outside Business Hours | 160146 | ED_FEE431_00098 | 4166
| Vacant Property Disconnection | 2618047 | ED_FEE431_00099 | 43813
| Vacant Property Site Visit | 653567 | ED_FEE431_00100 | 30664
| TIGS - shared fuse isolation (new category) | 466707 | ED_FEE431_00101 | 614
| Indirect costs - corporate allocations | 923168 | ED_FEE431_00102
ED_FEE431_00103
ED_FEE431_00104
ED_FEE431_00105
ED_FEE431_00106
ED_FEE431_00107
ED_FEE431_00108
ED_FEE431_00109
ED_FEE431_00110
ED_FEE431_00111
ED_FEE431_00112
ED_FEE431_00113
ED_FEE431_00114
ED_FEE431_00115
ED_FEE431_00116
ED_FEE431_00117
ED_FEE431_00118
ED_FEE431_00119
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00164
ED_FEE431_00165
ED_FEE431_00166
ED_FEE431_00167
ED_FEE431_00168
ED_FEE431_00169
ED_FEE431_00170
ED_FEE431_00171
ED_FEE431_00172
ED_FEE431_00173
ED_FEE431_00174
ED_FEE431_00175
ED_FEE431_00176
ED_FEE431_00177
ED_FEE431_00178
ED_FEE431_00179
ED_FEE431_00180
ED_FEE431_00181
ED_FEE431_00182
ED_FEE431_00183
ED_FEE431_00184
ED_FEE431_00185
ED_FEE431_00186
ED_FEE431_00187
ED_FEE431_00188
ED_FEE431_00189
ED_FEE431_00190
ED_FEE431_00191
ED_FEE431_00192
ED_FEE431_00193
ED_FEE431_00194
ED_FEE431_00195
ED_FEE431_00196
ED_FEE431_00197
ED_FEE431_00198
ED_FEE431_00199
ED_FEE431_00200
ED_FEE431_00201
ED_FEE431_00202
ED_FEE431_00203
ED_FEE431_00204
ED_FEE431_00205
ED_FEE431_00206
ED_FEE431_00207
ED_FEE431_00208
ED_FEE431_00209
ED_FEE431_00210
ED_FEE431_00211
ED_FEE431_00212
ED_FEE431_00213
ED_FEE431_00214
ED_FEE431_00215
ED_FEE431_00216
ED_FEE431_00217
ED_FEE431_00218
ED_FEE431_00219
ED_FEE431_00220
ED_FEE431_00221
ED_FEE431_00222
ED_FEE431_00223
ED_FEE431_00224
ED_FEE431_00225
ED_FEE431_00226
ED_FEE431_00227
ED_FEE431_00228
ED_FEE431_00229
ED_FEE431_00230
ED_FEE431_00231
ED_FEE431_00232
ED_FEE431_00233
ED_FEE431_00234
ED_FEE431_00235
ED_FEE431_00236
ED_FEE431_00237
ED_FEE431_00238
ED_FEE431_00239
ED_FEE431_00240
ED_FEE431_00241
ED_FEE431_00242
ED_FEE431_00243
ED_FEE431_00244
ED_FEE431_00245
ED_FEE431_00246
ED_FEE431_00247
ED_FEE431_00248
ED_FEE431_00249
ED_FEE431_00250
ED_FEE431_00251
ED_FEE431_00252
ED_FEE431_00253
ED_FEE431_00254
ED_FEE431_00255
ED_FEE431_00256
ED_FEE431_00257
ED_FEE431_00258
ED_FEE431_00259
ED_FEE431_00260
ED_FEE431_00261
ED_FEE431_00262
ED_FEE431_00263
ED_FEE431_00264
ED_FEE431_00265
ED_FEE431_00266
ED_FEE431_00267
ED_FEE431_00268
ED_FEE431_00269
ED_FEE431_00270
ED_FEE431_00271
ED_FEE431_00272
ED_FEE431_00273
ED_FEE431_00274
ED_FEE431_00275
ED_FEE431_00276
ED_FEE431_00277
ED_FEE431_00278
ED_FEE431_00279
ED_FEE431_00280
ED_FEE431_00281
ED_FEE431_00282
ED_FEE431_00283
ED_FEE431_00284
ED_FEE431_00285
ED_FEE431_00286
ED_FEE431_00287
ED_FEE431_00288
ED_FEE431_00289
ED_FEE431_00290
ED_FEE431_00291
ED_FEE431_00292
ED_FEE431_00293
ED_FEE431_00294
ED_FEE431_00295
ED_FEE431_00296
ED_FEE431_00297
ED_FEE431_00298
ED_FEE431_00299
ED_FEE431_00300
ED_FEE431_00301
ED_FEE431_00302
ED_FEE431_00303
ED_FEE431_00304
ED_FEE431_00305
ED_FEE431_00306
ED_FEE431_00307
ED_FEE431_00308
ED_FEE431_00309
ED_FEE431_00310
ED_FEE431_00311
ED_FEE431_00312
ED_FEE431_00313
ED_FEE431_00314
ED_FEE431_00315
ED_FEE431_00316
ED_FEE431_00317
ED_FEE431_00318
ED_FEE431_00319
ED_FEE431_00320
ED_FEE431_00321
ED_FEE431_00322
ED_FEE431_00323
ED_FEE431_00324
ED_FEE431_00325
ED_FEE431_00326
ED_FEE431_00327
ED_FEE431_00328
ED_FEE431_00329
ED_FEE431_00330
ED_FEE431_00331
ED_FEE431_00332
ED_FEE431_00333
ED_FEE431_00334
ED_FEE431_00335
ED_FEE431_00336
ED_FEE431_00337
ED_FEE431_00338
ED_FEE431_00339
ED_FEE431_00340
ED_FEE431_00341
ED_FEE431_00342
ED_FEE431_00343
ED_FEE431_00344
ED_FEE431_00345
ED_FEE431_00346
ED_FEE431_00347
ED_FEE431_00348
ED_FEE431_00349
ED_FEE431_00350
ED_FEE431_00351
ED_FEE431_00352
ED_FEE431_00353
ED_FEE431_00354
ED_FEE431_00355
ED_FEE431_00356
ED_FEE431_00357
ED_FEE431_00358
ED_FEE431_00359
ED_FEE431_00360
ED_FEE431_00361
ED_FEE431_00362
ED_FEE431_00363
ED_FEE431_00364
ED_FEE431_00365
ED_FEE431_00366
ED_FEE431_00367
ED_FEE431_00368
ED_FEE431_00369
ED_FEE431_00370
ED_FEE431_00371
ED_FEE431_00372
ED_FEE431_00373
ED_FEE431_00374
ED_FEE431_00375
ED_FEE431_00376
ED_FEE431_00377
ED_FEE431_00378
ED_FEE431_00379
ED_FEE431_00380
ED_FEE431_00381
ED_FEE431_00382
ED_FEE431_00383
ED_FEE431_00384
ED_FEE431_00385
ED_FEE431_00386
ED_FEE431_00387
ED_FEE431_00388
ED_FEE431_00389
ED_FEE431_00390
ED_FEE431_00391
ED_FEE431_00392
ED_FEE431_00393
ED_FEE431_00394
ED_FEE431_00395
ED_FEE431_00396
ED_FEE431_00397
ED_FEE431_00398
ED_FEE431_00399
ED_FEE431_00400
ED_FEE431_00401
ED_FEE431_00402
ED_FEE431_00403
ED_FEE431_00404
ED_FEE431_00405
ED_FEE431_00406
ED_FEE431_00407
ED_FEE431_00408
ED_FEE431_00409
ED_FEE431_00410
ED_FEE431_00411
ED_FEE431_00412
ED_FEE431_00413
ED_FEE431_00414
ED_FEE431_00415
ED_FEE431_00416
ED_FEE431_00417
ED_FEE431_00418
ED_FEE431_00419
ED_FEE431_00420
ED_FEE431_00421
ED_FEE431_00422
ED_FEE431_00423
ED_FEE431_00424
ED_FEE431_00425
ED_FEE431_00426
ED_FEE431_00427
ED_FEE431_00428
ED_FEE431_00429
ED_FEE431_00430
ED_FEE431_00431
ED_FEE431_00432
ED_FEE431_00433
ED_FEE431_00434
ED_FEE431_00435
ED_FEE431_00436
ED_FEE431_00437
ED_FEE431_00438
ED_FEE431_00439
ED_FEE431_00440
ED_FEE431_00441
ED_FEE431_00442
ED_FEE431_00443
ED_FEE431_00444
ED_FEE431_00445
ED_FEE431_00446
ED_FEE431_00447
ED_FEE431_00448
ED_FEE431_00449
ED_FEE431_00450
ED_FEE431_00451
ED_FEE431_00452
ED_FEE431_00453
ED_FEE431_00454
ED_FEE431_00455
ED_FEE431_00456
ED_FEE431_00457
ED_FEE431_00458
ED_FEE431_00459
ED_FEE431_00460
ED_FEE431_00461
ED_FEE431_00462
ED_FEE431_00463
ED_FEE431_00464
ED_FEE431_00465
ED_FEE431_00466
ED_FEE431_00467
ED_FEE431_00468
ED_FEE431_00469
ED_FEE431_00470
ED_FEE431_00471
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.4 Quoted services
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
4.4 ANCILLARY SERVICES - QUOTED SERVICES
4.4.1 - COST METRICS FOR QUOTED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2018-19 |  | 2018-19
Quoted Services | Design Information - rural overhead subdivisions and rural extensions | 25161 | ED_QUO441_00001 | 46
| Design Information - underground commercial and industrial or rural subdivisions (vacant lots - no development) | 33516 | ED_QUO441_00002 | 18
| Design Information - commercial and industrial developments | 1227121 | ED_QUO441_00003 | 654
| Design Information - asset relocation or street lighting | 378451 | ED_QUO441_00004 | 386
| Design Information - chambers, multi-kiosk, CBD Chambers (NOTE: Subset of overall Des Info costs.) | 284183 | ED_QUO441_00005 | 69
| Design Certification - commercial and industrial development | 1403544 | ED_QUO441_00006 | 682
| Design Certification - asset relocation or street lighting | 627513 | ED_QUO441_00007 | 454
| Design Certification - chambers, multi-kiosks, CBD chambers (NOTE: Subset of overall Des Cert costs.) | 764293 | ED_QUO441_00008 | 62
| Design Rechecking - underground urban residential subdivision (vacant lots) | 12276 | ED_QUO441_00009 | 26
| Design Rechecking - rural overhead subdivisions and rural extensions | 3355 | ED_QUO441_00010 | 11
| Design Rechecking - underground commercial and industrial or rural subdivisions (vacant lots - no development) | 6331 | ED_QUO441_00011 | 5
| Design Rechecking - commercial and industrial developments | 111104 | ED_QUO441_00012 | 130
| Design Rechecking - asset relocation or street lighting | 42063 | ED_QUO441_00013 | 60
| Inspection of service works by level 1 ASPs - commercial and industrial developments | 2549414 | ED_QUO441_00014 | 1197
| Inspection of service works by level 1 ASPs - asset relocation or street lighting | 1722211 | ED_QUO441_00015 | 639
| Level 1 ASP Reinspections | 30280 | ED_QUO441_00016 | 182
| Level 2 ASP Reinspections | 31150 | ED_QUO441_00017 | 195
| Reinspection of Installation (CoCEW) | 30824 | ED_QUO441_00018 | 527
| Contestable substation commissioning - commercial and industrial developments | 765967 | ED_QUO441_00019 | 262
| Contestable substation commissioning - asset relocation or street lighting. Volumes are a subset of the figures above. | 122995 | ED_QUO441_00020 | 15
| Contestable substation commissioning - complex and chamber substations (NOTE: Subset of overall Sub Commissioning costs.) | 1654764 | ED_QUO441_00021 | 76
| Access Permits - complex and chamber substations | 1161319 | ED_QUO441_00022 | 104
| Administration relating to work perfromed by ASPs - underground commercial and industrial or rural subdivisions (vacant lots - no development) | 46497 | ED_QUO441_00023 | 17
| Administration relating to work perfromed by ASPs - commercial and industrial developments | 873867 | ED_QUO441_00024 | 770
| Administration relating to work perfromed by ASPs - asset relocation or street lighting | 418161 | ED_QUO441_00025 | 694
| Administration relating to work perfromed by ASPs - guarantee of revenue, clarification meetings, variations to contract, reinspections etc. (NOTE: Service in addition to overall Admin volumes) | 7560 | ED_QUO441_00026 | 39
| Customer interface coodrination for contestable works | 1042 | ED_QUO441_00027 | 0
| Preliminary enquiry service | 292743 | ED_QUO441_00028 | 419
| Connection Offers: Standard Embedded Generation >5MVA capacity | 0 | ED_QUO441_00029 | 0
| Connection/relocation process facilitation | 1998623 | ED_QUO441_00030 | 2395
| Carrying out planning studies and analysis relating to distribution (including subtransmission and dual function assets) connection applications | 75784 | ED_QUO441_00031 | 67
| Services involved in obtaining deeds of agreement in relation to property rights associated with contestable connection works | 209112 | ED_QUO441_00032 | 342
| Investigation review and implementation of remedial actions associated with ASPs connection works | 28390 | ED_QUO441_00033 | 14
| Access Stand-by-person | 1039087 | ED_QUO441_00034 | 286
| Rectification Works - Provision of service/additional crew | 178004 | ED_QUO441_00035 | 35
| Rectification Works - fitting of tigrer tails | 3268356 | ED_QUO441_00036 | 1587
| Rectification Works - high load escorts | 107308 | ED_QUO441_00037 | 6
| Indirect costs - corporate allocations | 20148446 | ED_QUO441_00038
ED_QUO441_00039
ED_QUO441_00040
ED_QUO441_00041
ED_QUO441_00042
ED_QUO441_00043
ED_QUO441_00044
ED_QUO441_00045
ED_QUO441_00046
ED_QUO441_00047
ED_QUO441_00048
ED_QUO441_00049
ED_QUO441_00050
ED_QUO441_00051
ED_QUO441_00052
ED_QUO441_00053
ED_QUO441_00054
ED_QUO441_00055
ED_QUO441_00056
ED_QUO441_00057
ED_QUO441_00058
ED_QUO441_00059
ED_QUO441_00060
ED_QUO441_00061
ED_QUO441_00062
ED_QUO441_00063
ED_QUO441_00064
ED_QUO441_00065
ED_QUO441_00066
ED_QUO441_00067
ED_QUO441_00068
ED_QUO441_00069
ED_QUO441_00070
ED_QUO441_00071
ED_QUO441_00072
ED_QUO441_00073
ED_QUO441_00074
ED_QUO441_00075
ED_QUO441_00076
ED_QUO441_00077
ED_QUO441_00078
ED_QUO441_00079
ED_QUO441_00080
ED_QUO441_00081
ED_QUO441_00082
ED_QUO441_00083
ED_QUO441_00084
ED_QUO441_00085
ED_QUO441_00086
ED_QUO441_00087
ED_QUO441_00088
ED_QUO441_00089
ED_QUO441_00090
ED_QUO441_00091
ED_QUO441_00092
ED_QUO441_00093
ED_QUO441_00094
ED_QUO441_00095
ED_QUO441_00096
ED_QUO441_00097
ED_QUO441_00098
ED_QUO441_00099
ED_QUO441_00100
ED_QUO441_00101
ED_QUO441_00102
ED_QUO441_00103
ED_QUO441_00104
ED_QUO441_00105
ED_QUO441_00106
ED_QUO441_00107
ED_QUO441_00108
ED_QUO441_00109
ED_QUO441_00110
ED_QUO441_00111
ED_QUO441_00112
ED_QUO441_00113
ED_QUO441_00114
ED_QUO441_00115
ED_QUO441_00116
ED_QUO441_00117
ED_QUO441_00118
ED_QUO441_00119
ED_QUO441_00120
ED_QUO441_00121
ED_QUO441_00122
ED_QUO441_00123
ED_QUO441_00124
ED_QUO441_00125
ED_QUO441_00126
ED_QUO441_00127
ED_QUO441_00128
ED_QUO441_00129
ED_QUO441_00130
ED_QUO441_00131
ED_QUO441_00132
ED_QUO441_00133
ED_QUO441_00134
ED_QUO441_00135
ED_QUO441_00136
ED_QUO441_00137
ED_QUO441_00138
ED_QUO441_00139
ED_QUO441_00140
ED_QUO441_00141
ED_QUO441_00142
ED_QUO441_00143
ED_QUO441_00144
ED_QUO441_00145
ED_QUO441_00146
ED_QUO441_00147
ED_QUO441_00148
ED_QUO441_00149
ED_QUO441_00150
ED_QUO441_00151
ED_QUO441_00152
ED_QUO441_00153
ED_QUO441_00154
ED_QUO441_00155
ED_QUO441_00156
ED_QUO441_00157
ED_QUO441_00158
ED_QUO441_00159
ED_QUO441_00160
ED_QUO441_00161
ED_QUO441_00162
ED_QUO441_00163
ED_QUO441_00164
ED_QUO441_00165
ED_QUO441_00166
ED_QUO441_00167
ED_QUO441_00168
ED_QUO441_00169
ED_QUO441_00170
ED_QUO441_00171
ED_QUO441_00172
ED_QUO441_00173
ED_QUO441_00174
ED_QUO441_00175
ED_QUO441_00176
ED_QUO441_00177
ED_QUO441_00178
ED_QUO441_00179
ED_QUO441_00180
ED_QUO441_00181
ED_QUO441_00182
ED_QUO441_00183
ED_QUO441_00184
ED_QUO441_00185
ED_QUO441_00186
ED_QUO441_00187
ED_QUO441_00188
ED_QUO441_00189
ED_QUO441_00190
ED_QUO441_00191
ED_QUO441_00192
ED_QUO441_00193
ED_QUO441_00194
ED_QUO441_00195
ED_QUO441_00196
ED_QUO441_00197
ED_QUO441_00198
ED_QUO441_00199
ED_QUO441_00200
ED_QUO441_00201
ED_QUO441_00202
ED_QUO441_00203
ED_QUO441_00204
ED_QUO441_00205
ED_QUO441_00206
ED_QUO441_00207
ED_QUO441_00208
ED_QUO441_00209
ED_QUO441_00210
ED_QUO441_00211
ED_QUO441_00212
ED_QUO441_00213
ED_QUO441_00214
ED_QUO441_00215
ED_QUO441_00216
ED_QUO441_00217
ED_QUO441_00218
ED_QUO441_00219
ED_QUO441_00220
ED_QUO441_00221
ED_QUO441_00222
ED_QUO441_00223
ED_QUO441_00224
ED_QUO441_00225
ED_QUO441_00226
ED_QUO441_00227
ED_QUO441_00228
ED_QUO441_00229
ED_QUO441_00230
ED_QUO441_00231
ED_QUO441_00232
ED_QUO441_00233
ED_QUO441_00234
ED_QUO441_00235
ED_QUO441_00236
ED_QUO441_00237
ED_QUO441_00238
ED_QUO441_00239
ED_QUO441_00240
ED_QUO441_00241
ED_QUO441_00242
ED_QUO441_00243
ED_QUO441_00244
ED_QUO441_00245
ED_QUO441_00246
ED_QUO441_00247
ED_QUO441_00248
ED_QUO441_00249
ED_QUO441_00250
ED_QUO441_00251
ED_QUO441_00252
ED_QUO441_00253
ED_QUO441_00254
ED_QUO441_00255
ED_QUO441_00256
ED_QUO441_00257
ED_QUO441_00258
ED_QUO441_00259
ED_QUO441_00260
ED_QUO441_00261
ED_QUO441_00262
ED_QUO441_00263
ED_QUO441_00264
ED_QUO441_00265
ED_QUO441_00266
ED_QUO441_00267
ED_QUO441_00268
ED_QUO441_00269
ED_QUO441_00270
ED_QUO441_00271
ED_QUO441_00272
ED_QUO441_00273
ED_QUO441_00274
ED_QUO441_00275
ED_QUO441_00276
ED_QUO441_00277
ED_QUO441_00278
ED_QUO441_00279
ED_QUO441_00280
ED_QUO441_00281
ED_QUO441_00282
ED_QUO441_00283
ED_QUO441_00284
ED_QUO441_00285
ED_QUO441_00286
ED_QUO441_00287
ED_QUO441_00288
ED_QUO441_00289
ED_QUO441_00290
ED_QUO441_00291
ED_QUO441_00292
ED_QUO441_00293
ED_QUO441_00294
ED_QUO441_00295
ED_QUO441_00296
ED_QUO441_00297
ED_QUO441_00298
ED_QUO441_00299
ED_QUO441_00300
ED_QUO441_00301
ED_QUO441_00302
ED_QUO441_00303
ED_QUO441_00304
ED_QUO441_00305
ED_QUO441_00306
ED_QUO441_00307
ED_QUO441_00308
ED_QUO441_00309
ED_QUO441_00310
ED_QUO441_00311
ED_QUO441_00312
ED_QUO441_00313
ED_QUO441_00314
ED_QUO441_00315
ED_QUO441_00316
ED_QUO441_00317
ED_QUO441_00318
ED_QUO441_00319
ED_QUO441_00320
ED_QUO441_00321
ED_QUO441_00322
ED_QUO441_00323
ED_QUO441_00324
ED_QUO441_00325
ED_QUO441_00326
ED_QUO441_00327
ED_QUO441_00328
ED_QUO441_00329
ED_QUO441_00330
ED_QUO441_00331
ED_QUO441_00332
ED_QUO441_00333
ED_QUO441_00334
ED_QUO441_00335
ED_QUO441_00336
ED_QUO441_00337
ED_QUO441_00338
ED_QUO441_00339
ED_QUO441_00340
ED_QUO441_00341
ED_QUO441_00342
ED_QUO441_00343
ED_QUO441_00344
ED_QUO441_00345
ED_QUO441_00346
ED_QUO441_00347
ED_QUO441_00348
ED_QUO441_00349
ED_QUO441_00350
ED_QUO441_00351
ED_QUO441_00352
ED_QUO441_00353
ED_QUO441_00354
ED_QUO441_00355
ED_QUO441_00356
ED_QUO441_00357
ED_QUO441_00358
ED_QUO441_00359
ED_QUO441_00360
ED_QUO441_00361
ED_QUO441_00362
ED_QUO441_00363
ED_QUO441_00364
ED_QUO441_00365
ED_QUO441_00366
ED_QUO441_00367
ED_QUO441_00368
ED_QUO441_00369
ED_QUO441_00370
ED_QUO441_00371
ED_QUO441_00372
ED_QUO441_00373
ED_QUO441_00374
ED_QUO441_00375
ED_QUO441_00376
ED_QUO441_00377
ED_QUO441_00378
ED_QUO441_00379
ED_QUO441_00380
ED_QUO441_00381
ED_QUO441_00382
ED_QUO441_00383
ED_QUO441_00384
ED_QUO441_00385
ED_QUO441_00386
ED_QUO441_00387
ED_QUO441_00388
ED_QUO441_00389
ED_QUO441_00390
ED_QUO441_00391
ED_QUO441_00392
ED_QUO441_00393
ED_QUO441_00394
ED_QUO441_00395
ED_QUO441_00396
ED_QUO441_00397
ED_QUO441_00398
ED_QUO441_00399
ED_QUO441_00400
ED_QUO441_00401
ED_QUO441_00402
ED_QUO441_00403
ED_QUO441_00404
ED_QUO441_00405
ED_QUO441_00406
ED_QUO441_00407
ED_QUO441_00408
ED_QUO441_00409
ED_QUO441_00410
ED_QUO441_00411
ED_QUO441_00412
ED_QUO441_00413
ED_QUO441_00414
ED_QUO441_00415
ED_QUO441_00416
ED_QUO441_00417
ED_QUO441_00418
ED_QUO441_00419
ED_QUO441_00420
ED_QUO441_00421
ED_QUO441_00422
ED_QUO441_00423
ED_QUO441_00424
ED_QUO441_00425
ED_QUO441_00426
ED_QUO441_00427
ED_QUO441_00428
ED_QUO441_00429
ED_QUO441_00430
ED_QUO441_00431
ED_QUO441_00432
ED_QUO441_00433
ED_QUO441_00434
ED_QUO441_00435
ED_QUO441_00436
ED_QUO441_00437
ED_QUO441_00438
ED_QUO441_00439
ED_QUO441_00440
ED_QUO441_00441
ED_QUO441_00442
ED_QUO441_00443
ED_QUO441_00444
ED_QUO441_00445
ED_QUO441_00446
ED_QUO441_00447
ED_QUO441_00448
ED_QUO441_00449
ED_QUO441_00450
ED_QUO441_00451
ED_QUO441_00452
ED_QUO441_00453
ED_QUO441_00454
ED_QUO441_00455
ED_QUO441_00456
ED_QUO441_00457
ED_QUO441_00458
ED_QUO441_00459
ED_QUO441_00460
ED_QUO441_00461
ED_QUO441_00462
ED_QUO441_00463
ED_QUO441_00464
ED_QUO441_00465
ED_QUO441_00466
ED_QUO441_00467
ED_QUO441_00468
ED_QUO441_00469
ED_QUO441_00470
ED_QUO441_00471
ED_QUO441_00472
ED_QUO441_00473
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.2 Asset Age Profile
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
5.2 ASSET AGE PROFILE
There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data.
5.2.1 - ASSET AGE PROFILE
|  | ECONOMIC LIFE (YEARS) |  | INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR
ASSET GROUP | ASSET CATEGORY | MEAN | STANDARD DEVIATION | 2018-19 | 2017-18 | 2016-17 | 2015-16 | 2014-15 | 2013-14 | 2012-13 | 2011-12 | 2010-11 | 2009-10 | 2008-09 | 2007-08 | 2006-07 | 2005-06 | 2004-05 | 2003-04 | 2002-03 | 2001-02 | 2000-01 | 1999-00 | 1998-99 | 1997-98 | 1996-97 | 1995-96 | 1994-95 | 1993-94 | 1992-93 | 1991-92 | 1990-91 | 1989-90 | 1988-89 | 1987-88 | 1986-87 | 1985-86 | 1984-85 | 1983-84 | 1982-83 | 1981-82 | 1980-81 | 1979-80 | 1978-79 | 1977-78 | 1976-77 | 1975-76 | 1974-75 | 1973-74 | 1972-73 | 1971-72 | 1970-71 | 1969-70 | 1968-69 | 1967-68 | 1966-67 | 1965-66 | 1964-65 | 1963-64 | 1962-63 | 1961-62 | 1960-61 | 1959-60 | 1958-59 | 1957-58 | 1956-57 | 1955-56 | 1954-55 | 1953-54 | 1952-53 | 1951-52 | 1950-51 | 1949-50 | 1948-49 | 1947-48 | 1946-47 | 1945-46 | 1944-45 | 1943-44 | 1942-43 | 1941-42 | 1940-41 | 1939-40 | 1938-39 | 1937-38 | 1936-37 | 1935-36 | 1934-35 | 1933-34 | 1932-33 | 1931-32 | 1930-31 | 1929-30 | 1928-29 | 1927-28 | 1926-27 | 1925-26 | 1924-25 | 1923-24 | 1922-23 | 1921-22 | 1920-21 | 1919-20 | 1918-19 | 1917-18 | 1916-17 | 1915-16 | 1914-15 | 1913-14 | 1912-13 | 1911-12 | 1910-11
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole | 7 | 4 | 542 | 575 | 982 | 1000 | 1290 | 2091 | 1881 | 2063 | 1804 | 2949 | 2226 | 2800 | 1374 | 1035 | 920 | 785 | 872 | 202 | 44 | 19 | 9 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Wood | 44 | 14 | 2356 | 2668 | 2403 | 2099 | 2737 | 3224 | 3543 | 4232 | 3860 | 3707 | 3075 | 3029 | 2640 | 2258 | 1930 | 2231 | 1745 | 1690 | 1467 | 1515 | 1530 | 1909 | 2077 | 2998 | 3034 | 2658 | 1819 | 1523 | 3784 | 3866 | 3265 | 2767 | 4451 | 3716 | 3255 | 2399 | 3634 | 6178 | 5600 | 5399 | 4447 | 3339 | 3717 | 2604 | 3539 | 4472 | 3369 | 6580 | 6413 | 5579 | 6638 | 9610 | 12003 | 10524 | 13363 | 9148 | 13604 | 7212 | 8911 | 5735 | 7177 | 4376 | 2242 | 609 | 3134 | 620 | 1227 | 533 | 820 | 150 | 26 | 697 | 608 | 0 | 10 | 0 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; Wood | 44 | 14 | 601 | 1407 | 1472 | 2013 | 2020 | 2587 | 2909 | 2861 | 2797 | 2635 | 2853 | 2252 | 2110 | 1864 | 1914 | 2004 | 1517 | 1578 | 1538 | 2119 | 1414 | 1506 | 1178 | 1480 | 1904 | 1607 | 1359 | 1485 | 2418 | 2444 | 1900 | 1899 | 2467 | 2591 | 2258 | 1437 | 2383 | 3545 | 2754 | 2035 | 1939 | 1706 | 1831 | 1706 | 2958 | 2734 | 2032 | 2986 | 2766 | 3069 | 1837 | 3200 | 3705 | 3079 | 3473 | 2209 | 1742 | 878 | 1586 | 1066 | 600 | 214 | 106 | 106 | 41 | 36 | 14 | 1 | 1 | 0 | 24 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Wood | 44 | 14 | 0 | 3 | 7 | 4 | 8 | 4 | 12 | 18 | 1 | 22 | 37 | 8 | 5 | 16 | 13 | 31 | 25 | 28 | 15 | 42 | 34 | 14 | 7 | 2 | 8 | 4 | 21 | 12 | 8 | 31 | 40 | 14 | 9 | 8 | 14 | 5 | 5 | 13 | 11 | 2 | 5 | 5 | 7 | 16 | 3 | 15 | 34 | 40 | 6 | 172 | 0 | 2 | 23 | 17 | 1 | 0 | 1 | 0 | 37 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Wood | 44 | 14 | 53 | 166 | 142 | 169 | 208 | 178 | 289 | 251 | 278 | 335 | 355 | 256 | 205 | 124 | 188 | 186 | 198 | 188 | 138 | 114 | 89 | 109 | 86 | 130 | 175 | 209 | 172 | 310 | 177 | 209 | 134 | 99 | 297 | 261 | 225 | 241 | 508 | 611 | 266 | 343 | 232 | 233 | 379 | 188 | 206 | 312 | 189 | 446 | 565 | 488 | 387 | 586 | 673 | 687 | 519 | 391 | 203 | 103 | 195 | 193 | 16 | 0 | 0 | 0 | 16 | 12 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Wood | 44 | 14 | 3 | 17 | 39 | 27 | 18 | 4 | 14 | 21 | 22 | 47 | 35 | 56 | 16 | 9 | 18 | 11 | 12 | 7 | 35 | 73 | 11 | 8 | 16 | 19 | 35 | 61 | 13 | 14 | 31 | 40 | 11 | 15 | 17 | 18 | 19 | 30 | 406 | 323 | 47 | 33 | 74 | 107 | 71 | 501 | 129 | 102 | 17 | 163 | 141 | 362 | 239 | 182 | 60 | 164 | 91 | 101 | 68 | 0 | 46 | 99 | 14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Concrete | 40 | 19 | 16 | 16 | 6 | 2 | 2 | 17 | 58 | 48 | 30 | 24 | 2 | 7 | 6 | 11 | 4 | 14 | 10 | 3 | 10 | 7 | 1 | 1 | 0 | 23 | 18 | 42 | 3 | 60 | 12 | 52 | 0 | 0 | 2 | 25 | 7 | 11 | 0 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 21 | 6 | 4 | 3 | 0 | 1 | 0 | 0 | 0 | 8 | 0 | 1 | 16 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; Concrete | 40 | 19 | 8 | 10 | 24 | 9 | 9 | 20 | 11 | 13 | 16 | 7 | 2 | 3 | 9 | 6 | 3 | 7 | 3 | 6 | 9 | 0 | 4 | 0 | 0 | 51 | 8 | 61 | 28 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Concrete | 40 | 19 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Concrete | 40 | 19 | 6 | 55 | 111 | 67 | 42 | 88 | 146 | 160 | 346 | 327 | 101 | 111 | 413 | 405 | 305 | 153 | 104 | 83 | 73 | 85 | 13 | 59 | 6 | 56 | 9 | 51 | 15 | 85 | 40 | 38 | 38 | 0 | 38 | 6 | 0 | 56 | 4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 20 | 0 | 0 | 0 | 2 | 1 | 0 | 7 | 1 | 44 | 22 | 1 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Concrete | 40 | 19 | 7 | 13 | 28 | 36 | 38 | 32 | 35 | 245 | 284 | 401 | 182 | 64 | 80 | 34 | 43 | 142 | 248 | 62 | 141 | 65 | 1 | 1 | 17 | 30 | 2 | 1 | 4 | 0 | 99 | 28 | 2 | 46 | 14 | 96 | 29 | 7 | 15 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 7 | 2 | 7 | 7 | 2 | 10 | 0 | 3 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Steel | 34 | 18 | 20 | 36 | 37 | 19 | 18 | 65 | 8 | 35 | 37 | 62 | 22 | 146 | 421 | 328 | 274 | 172 | 145 | 102 | 84 | 530 | 11 | 47 | 33 | 41 | 10 | 23 | 10 | 165 | 111 | 186 | 4 | 113 | 2 | 2 | 156 | 280 | 940 | 574 | 325 | 76 | 53 | 8 | 73 | 13 | 3 | 29 | 13 | 198 | 9 | 42 | 38 | 88 | 29 | 82 | 55 | 72 | 32 | 18 | 25 | 20 | 16 | 4 | 8 | 1 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; Steel | 34 | 18 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 5 | 0 | 1 | 1 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Steel | 34 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Steel | 34 | 18 | 3 | 5 | 2 | 0 | 8 | 8 | 9 | 24 | 107 | 2 | 1 | 24 | 48 | 36 | 0 | 25 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3 | 12 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 7 | 4 | 6 | 0 | 3 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Steel | 34 | 18 | 5 | 14 | 54 | 11 | 66 | 101 | 6 | 9 | 25 | 15 | 7 | 12 | 4 | 17 | 14 | 11 | 0 | 0 | 14 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 2 | 0 | 0 | 10 | 21 | 43 | 0 | 0 | 11 | 5 | 0 | 7 | 0 | 11 | 4 | 3 | 10 | 6 | 5 | 0 | 16 | 6 | 4 | 0 | 0 | 0 | 14 | 0 | 4 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV | 44 | 14 | 32.3 | 62.4 | 66 | 71 | 91.3 | 137.9 | 105 | 147.4 | 156.1 | 126.5 | 137.4 | 120.6 | 103.3 | 117.7 | 105 | 86.7 | 100.3 | 71.1 | 64.6 | 69.7 | 58.8 | 47.7 | 53.8 | 52 | 64.5 | 64.3 | 46.2 | 38.8 | 86.2 | 98.9 | 91.6 | 67.6 | 104.4 | 100.4 | 114.5 | 94.2 | 85.9 | 165.4 | 160.7 | 335.7 | 216.6 | 145.5 | 148.2 | 150 | 161.8 | 266.3 | 170.7 | 280 | 191.1 | 225.5 | 306.2 | 422.1 | 343.6 | 505.8 | 511.3 | 530.8 | 850.5 | 504.9 | 454.4 | 591.1 | 535.6 | 286.6 | 356.5 | 362.5 | 102.2 | 59.2 | 50.5 | 40.4 | 56.1 | 22.2 | 40.8 | 19.9 | 6.2 | 9.8 | 22.9 | 40.3 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4 | 63.9 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 44 | 14 | 182.5 | 219.3 | 161.1 | 193.5 | 113.6 | 161.6 | 161.5 | 129.7 | 166.7 | 143.1 | 163.2 | 127.9 | 137.5 | 117.8 | 172.8 | 104.1 | 133.9 | 117.1 | 118.5 | 152.8 | 130.7 | 96.1 | 68.8 | 61.5 | 61.9 | 61.5 | 56.4 | 51.3 | 76.6 | 82.1 | 66.5 | 63.4 | 81.8 | 95.4 | 79.7 | 55.2 | 52.5 | 107.2 | 99.4 | 259.6 | 167.9 | 118.3 | 161.9 | 139.1 | 136.1 | 181.7 | 219.6 | 307.1 | 178.1 | 164.6 | 301 | 325.8 | 239.6 | 241.6 | 280.9 | 201.2 | 484.6 | 158.7 | 267.1 | 202.2 | 195.2 | 98.3 | 83.1 | 130.9 | 15.6 | 31.2 | 12.9 | 27.4 | 1.2 | 0 | 0 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; SWER | 44 | 14 | 1.4 | 0 | 0 | 0 | 0.1 | 0 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0.3 | 0.1 | 0 | 0.3 | 0 | 0 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0.9 | 0.1 | 0.1 | 0.3 | 0.1 | 36.7 | 1.6 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 2.4 | 0 | 0 | 4.5 | 0.1 | 0 | 0.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2 | 6.2 | 0 | 0 | 0 | 0 | 42.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Single-Phase | 44 | 14 | 1.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.3 | 0 | 0 | 2.1 | 5.7 | 0.2 | 0.4 | 2.2 | 11.4 | 2.9 | 3.6 | 0.7 | 0 | 0.5 | 0 | 0 | 0.2 | 1.2 | 1.2 | 0 | 0.8 | 0 | 0.2 | 0 | 0.2 | 0.8 | 0.6 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 6.2 | 5.5 | 4.4 | 5.6 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase | 44 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.7 | 2.9 | 5.2 | 0 | 0.7 | 0 | 1.2 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0.1 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.9 | 0 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV | 44 | 14 | 6 | 9.6 | 37.2 | 10.9 | 6.3 | 12.9 | 31.7 | 21.4 | 49.3 | 69.5 | 21.1 | 58.6 | 34.1 | 78.5 | 31.7 | 5.8 | 16 | 16.2 | 17.5 | 13 | 2.7 | 24.6 | 1.8 | 6.9 | 3.4 | 25.9 | 1.8 | 20.7 | 2.4 | 15.1 | 6.4 | 0.9 | 1 | 1 | 21.7 | 8.3 | 12.2 | 25.6 | 41.6 | 70.4 | 16.9 | 9.5 | 38.4 | 18.7 | 12.3 | 20 | 7.1 | 16 | 13 | 23.2 | 59.4 | 95.3 | 48.2 | 10.1 | 130.8 | 72.9 | 85.7 | 26.1 | 25.2 | 63 | 0 | 0 | 3 | 19.8 | 11.2 | 5.4 | 4.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 44 | 14 | 0.5 | 0.4 | 6.3 | 3.4 | 16.4 | 49.4 | 12 | 20.6 | 73.6 | 19.3 | 0.3 | 10.5 | 7.6 | 0 | 4.3 | 10.5 | 19.2 | 13.5 | 3.5 | 3.9 | 0 | 4.7 | 1.7 | 0 | 35.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 3.9 | 4.5 | 50.7 | 0 | 8.8 | 16.2 | 2.1 | 0.7 | 29 | 28.8 | 20.7 | 0.5 | 12.7 | 27.5 | 24.6 | 32.2 | 6.4 | 3.7 | 13.1 | 115.9 | 8.6 | 0.4 | 14.6 | 48.5 | 42.6 | 10.2 | 53.2 | 187.9 | 0 | 0 | 0 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV | 44 | 17 | 144.7 | 195.3 | 189.6 | 155.2 | 154.3 | 174.9 | 171.3 | 222 | 188 | 133.1 | 151.9 | 132.5 | 122.4 | 147.9 | 170.8 | 136.1 | 140.3 | 100.8 | 96.3 | 99.6 | 100.3 | 64.8 | 65 | 62.6 | 75.3 | 53.2 | 70.4 | 50.8 | 42.8 | 26.7 | 53.1 | 74.9 | 34 | 38.6 | 49.2 | 44.3 | 58.7 | 117.8 | 113.6 | 97.5 | 133.5 | 96.8 | 105.5 | 68.5 | 50.5 | 89.2 | 43.2 | 82.8 | 43.9 | 57.4 | 69.7 | 108.9 | 37.5 | 95 | 99.2 | 83.7 | 121.1 | 72.9 | 104.5 | 100.1 | 84 | 55.4 | 72.2 | 48.1 | 78.8 | 13.6 | 6.3 | 15.6 | 13.7 | 4.9 | 19.3 | 8.3 | 0.9 | 2.9 | 5.1 | 11.2 | 0.7 | 0.7 | 0.9 | 4.4 | 0.9 | 0.9 | 0.7 | 0.7 | 0.6 | 0.8 | 0.6 | 0.7 | 1.1 | 0.9 | 0.8 | 24 | 13 | 0.7 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 46 | 19 | 104.8 | 142.6 | 134.7 | 119.8 | 119.1 | 254.8 | 267 | 282.6 | 287.6 | 235 | 213.5 | 159.9 | 188.6 | 143.6 | 129 | 102.9 | 111.8 | 90.8 | 120.1 | 115.5 | 109.7 | 85.3 | 50.1 | 61 | 89.2 | 55.4 | 70.2 | 82.9 | 62.2 | 50.7 | 56.9 | 82.9 | 43.9 | 43.2 | 68.8 | 38.5 | 70.6 | 90.3 | 106 | 131.1 | 153.9 | 133.1 | 117.8 | 90.4 | 90.8 | 109.1 | 70 | 93.4 | 61.7 | 113.7 | 72.3 | 136.1 | 87.5 | 123.3 | 121.6 | 175.1 | 237.2 | 130.4 | 158.7 | 157.8 | 173.7 | 149.5 | 160.1 | 180.4 | 188.1 | 25.7 | 34.3 | 24.3 | 25.7 | 16.9 | 29.5 | 15.6 | 1.8 | 4.4 | 13.6 | 27.5 | 2.4 | 2 | 1.8 | 27.5 | 4.1 | 6.5 | 3 | 2.3 | 1.2 | 1 | 0.9 | 2.1 | 2.8 | 17.3 | 10.7 | 62.7 | 51.3 | 3 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV | 45 | 20 | 10.7 | 13.2 | 15.5 | 4.7 | 2.5 | 7.3 | 15.1 | 19 | 20.1 | 28.9 | 19.3 | 8.1 | 18.2 | 5.3 | 10.7 | 0.5 | 0.9 | 4.9 | 5.6 | 9.4 | 1 | 2.5 | 0.7 | 7.3 | 0.2 | 2.2 | 0.3 | 0.5 | 0.9 | 0.6 | 0.7 | 0.2 | 1.1 | 0.5 | 0.1 | 0.5 | 0.3 | 0 | 0.2 | 0 | 0.3 | 0.3 | 0.6 | 3.3 | 9 | 1.2 | 0.7 | 5.2 | 2.6 | 3 | 0.7 | 10 | 16.6 | 13.4 | 21.5 | 11.9 | 22.4 | 0 | 0 | 0.3 | 0.1 | 0.5 | 2.5 | 43.5 | 5.2 | 0.1 | 19.8 | 6.9 | 4.1 | 0.7 | 14.6 | 1.4 | 42.2 | 0.7 | 0 | 0.1 | 2.4 | 0.1 | 0 | 0 | 1.4 | 1.1 | 20.5 | 0 | 0 | 0 | 0 | 18.4 | 1.4 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV | 45 | 20 | 0 | 0 | 0 | 0 | 0.6 | 6.9 | 0.5 | 0.6 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 54 | 8 | 17.3 | 11.7 | 46.8 | 17.6 | 39 | 32.1 | 23.1 | 19.1 | 26.8 | 24 | 0.3 | 18.7 | 0.1 | 0.2 | 5.5 | 4.2 | 15.3 | 8.2 | 0 | 6.5 | 0.1 | 6.9 | 0.1 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0.9 | 0 | 11 | 0 | 0 | 0 | 0 | 3.2 | 3.3 | 14.6 | 18.8 | 7.5 | 13.7 | 3.8 | 4.7 | 10.4 | 2.9 | 50.9 | 34.7 | 27 | 8.8 | 37.5 | 6 | 4.9 | 27.1 | 0 | 0 | 11.4 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 39 | 21 | 1385 | 1814 | 1998 | 2142 | 2349 | 2504 | 2376 | 2139 | 1430 | 1431 | 3551 | 1425 | 1695 | 1711 | 2045 | 1711 | 895 | 738 | 704 | 977 | 1002 | 715 | 429 | 871 | 1117 | 1215 | 1377 | 932 | 1120 | 726 | 457 | 481 | 316 | 765 | 482 | 859 | 550 | 1677 | 1141 | 668 | 432 | 610 | 763 | 585 | 333 | 385 | 683 | 439 | 425 | 489 | 227 | 263 | 109 | 241 | 159 | 192 | 11483 | 105 | 82 | 3174 | 7 | 8 | 6 | 8 | 6 | 13 | 7 | 7 | 4 | 3 | 1 | 2 | 1 | 2 | 3 | 0 | 5 | 0 | 0 | 5 | 1 | 7 | 4 | 1 | 1 | 0 | 1 | 12 | 11 | 4 | 9 | 9 | 11 | 10 | 0 | 4 | 3 | 0 | 7 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type | 30 | 5 | 14800 | 23139 | 22287 | 23264 | 24363 | 25383 | 18069 | 23000 | 18684 | 21374 | 25427 | 20028 | 15937 | 14937 | 9452 | 9287 | 7574 | 6901 | 5649 | 8327 | 3803 | 4133 | 4221 | 5269 | 5652 | 5030 | 3687 | 3213 | 7422 | 7390 | 5936 | 5103 | 6865 | 6909 | 5685 | 4487 | 3223 | 5549 | 5515 | 11309 | 5632 | 4093 | 3687 | 3642 | 3387 | 6992 | 3161 | 5607 | 4265 | 5432 | 8289 | 9470 | 6740 | 10146 | 13476 | 12074 | 20650 | 11083 | 13712 | 17648 | 15456 | 6805 | 7995 | 10264 | 2988 | 1934 | 1266 | 1182 | 1469 | 664 | 880 | 314 | 35 | 264 | 781 | 0 | 0 | 1 | 0 | 1378 | 1 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2933 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 3115 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type | 30 | 5 | 772 | 833 | 632 | 649 | 718 | 758 | 626 | 725 | 533 | 654 | 621 | 568 | 516 | 1060 | 1581 | 676 | 481 | 433 | 513 | 640 | 395 | 352 | 357 | 397 | 434 | 384 | 309 | 312 | 487 | 492 | 456 | 362 | 508 | 475 | 420 | 319 | 289 | 428 | 421 | 755 | 445 | 326 | 268 | 234 | 245 | 332 | 328 | 412 | 290 | 497 | 491 | 860 | 373 | 686 | 931 | 984 | 1187 | 725 | 1043 | 1147 | 887 | 542 | 509 | 641 | 226 | 119 | 65 | 48 | 68 | 54 | 75 | 8 | 13 | 5 | 44 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Residential ; Complex Type | 44.88 | 21.5 | 13330 | 7172 | 8432 | 4649 | 4246 | 4679 | 4322 | 6861 | 4354 | 3765 | 3370 | 3249 | 3576 | 3469 | 2708 | 3034 | 2700 | 2117 | 2511 | 2350 | 2944 | 2037 | 3315 | 2407 | 3223 | 2467 | 2425 | 2216 | 2061 | 1843 | 3424 | 1398 | 2078 | 1746 | 2346 | 1025 | 2932 | 4259 | 6160 | 8078 | 6494 | 5077 | 4109 | 590 | 1149 | 2514 | 227 | 3833 | 1231 | 1575 | 2109 | 2783 | 887 | 3221 | 2730 | 1995 | 3849 | 1414 | 3957 | 3358 | 2049 | 2467 | 1005 | 921 | 538 | 399 | 143 | 267 | 471 | 498 | 143 | 480 | 33 | 194 | 695 | 0 | 0 | 0 | 0 | 22 | 1 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1143 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type | 44.88 | 21.5 | 1058 | 1188 | 865 | 894 | 1215 | 731 | 811 | 885 | 711 | 634 | 795 | 798 | 796 | 977 | 825 | 563 | 414 | 360 | 596 | 272 | 176 | 167 | 139 | 112 | 232 | 120 | 90 | 87 | 101 | 158 | 120 | 193 | 95 | 153 | 286 | 73 | 276 | 75 | 88 | 494 | 245 | 120 | 173 | 60 | 124 | 253 | 82 | 206 | 93 | 277 | 184 | 862 | 187 | 531 | 777 | 720 | 777 | 500 | 731 | 616 | 612 | 602 | 665 | 313 | 974 | 79 | 59 | 118 | 156 | 64 | 74 | 92 | 2 | 15 | 96 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Subdivision ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 34 | 17 | 38 | 44 | 39 | 59 | 66 | 97 | 73 | 71 | 78 | 79 | 127 | 199 | 105 | 68 | 45 | 60 | 52 | 20 | 183 | 42 | 21 | 11 | 7 | 10 | 3 | 16 | 6 | 9 | 9 | 12 | 17 | 11 | 15 | 26 | 21 | 16 | 67 | 35 | 53 | 69 | 50 | 38 | 42 | 24 | 30 | 24 | 37 | 17 | 15 | 19 | 16 | 17 | 12 | 9 | 16 | 11 | 10 | 11 | 27 | 6 | 8 | 17 | 10 | 3 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 34 | 17 | 2 | 9 | 5 | 5 | 6 | 18 | 5 | 19 | 25 | 25 | 27 | 29 | 39 | 18 | 14 | 12 | 8 | 3 | 52 | 2 | 0 | 0 | 0 | 1 | 43 | 2 | 13 | 4 | 0 | 5 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 33 | 12 | 21 | 24 | 12 | 20 | 27 | 27 | 16 | 18 | 33 | 23 | 40 | 76 | 32 | 26 | 15 | 15 | 14 | 4 | 77 | 17 | 15 | 56 | 134 | 113 | 240 | 164 | 244 | 100 | 116 | 384 | 101 | 83 | 128 | 108 | 83 | 57 | 141 | 141 | 99 | 58 | 44 | 32 | 41 | 31 | 35 | 41 | 28 | 23 | 52 | 31 | 22 | 36 | 23 | 15 | 33 | 26 | 16 | 22 | 28 | 16 | 13 | 20 | 10 | 16 | 5 | 1 | 0 | 0 | 1 | 132 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 34 | 16 | 149 | 118 | 127 | 210 | 160 | 217 | 180 | 188 | 223 | 310 | 314 | 479 | 279 | 228 | 91 | 95 | 75 | 45 | 446 | 46 | 44 | 80 | 114 | 126 | 295 | 88 | 167 | 165 | 89 | 166 | 69 | 78 | 82 | 104 | 84 | 122 | 276 | 79 | 87 | 103 | 78 | 50 | 50 | 120 | 85 | 113 | 147 | 133 | 137 | 206 | 156 | 170 | 130 | 141 | 161 | 109 | 99 | 73 | 82 | 45 | 63 | 11 | 15 | 12 | 3 | 6 | 1 | 5 | 2 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 32 | 15 | 120 | 144 | 168 | 111 | 133 | 160 | 143 | 194 | 197 | 160 | 227 | 197 | 176 | 203 | 155 | 180 | 121 | 77 | 110 | 28 | 29 | 36 | 33 | 92 | 241 | 480 | 197 | 120 | 88 | 62 | 122 | 88 | 176 | 106 | 27 | 68 | 167 | 137 | 312 | 192 | 246 | 253 | 191 | 208 | 178 | 132 | 148 | 155 | 122 | 96 | 58 | 104 | 39 | 40 | 66 | 70 | 42 | 18 | 7 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 9 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 32 | 15 | 123 | 158 | 144 | 181 | 177 | 285 | 315 | 336 | 374 | 278 | 294 | 280 | 281 | 219 | 132 | 131 | 124 | 97 | 178 | 40 | 23 | 20 | 10 | 26 | 41 | 548 | 17 | 31 | 48 | 21 | 38 | 11 | 25 | 18 | 22 | 14 | 10 | 25 | 15 | 10 | 2 | 3 | 1 | 5 | 10 | 4 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase | 59 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 59 | 11 | 7 | 3 | 7 | 1 | 2 | 5 | 2 | 9 | 6 | 0 | 3 | 2 | 3 | 4 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 2 | 5 | 1 | 1 | 0 | 2 | 2 | 1 | 2 | 1 | 0 | 1 | 10 | 10 | 4 | 5 | 4 | 3 | 9 | 9 | 4 | 11 | 41 | 36 | 34 | 20 | 39 | 15 | 9 | 22 | 6 | 17 | 22 | 18 | 30 | 16 | 12 | 5 | 9 | 1 | 3 | 3 | 54 | 1 | 1 | 60 | 6 | 15 | 2 | 0 | 0 | 21 | 6 | 0 | 2 | 0 | 0 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase | 40 | 12 | 80 | 118 | 91 | 95 | 97 | 97 | 92 | 76 | 84 | 86 | 53 | 77 | 69 | 63 | 54 | 56 | 40 | 13 | 45 | 9 | 19 | 41 | 18 | 34 | 133 | 546 | 47 | 88 | 91 | 160 | 110 | 125 | 104 | 48 | 34 | 38 | 62 | 48 | 71 | 37 | 23 | 21 | 18 | 40 | 15 | 40 | 111 | 173 | 91 | 90 | 30 | 47 | 58 | 43 | 66 | 71 | 12 | 26 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA | 55 | 7 | 0 | 0 | 0 | 3 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 0 | 3 | 4 | 0 | 11 | 4 | 4 | 2 | 3 | 1 | 1 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA | 49 | 6 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 7 | 12 | 2 | 5 | 16 | 14 | 18 | 10 | 6 | 11 | 1 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 3 | 3 | 2 | 3 | 2 | 4 | 8 | 5 | 3 | 9 | 2 | 0 | 4 | 2 | 7 | 3 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA | 55 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA | 55 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 4 | 0 | 2 | 5 | 1 | 2 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA | 53 | 11 | 2 | 3 | 6 | 8 | 9 | 1 | 6 | 17 | 8 | 20 | 8 | 12 | 10 | 8 | 8 | 6 | 4 | 6 | 3 | 1 | 4 | 4 | 1 | 0 | 0 | 4 | 3 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 3 | 2 | 2 | 3 | 4 | 4 | 2 | 1 | 0 | 3 | 3 | 6 | 4 | 0 | 2 | 2 | 1 | 0 | 1 | 0 | 2 | 3 | 2 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA | 48 | 2 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 6 | 6 | 1 | 1 | 2 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 22 | 20 | 147 | 121 | 102 | 28 | 65 | 70 | 87 | 152 | 94 | 102 | 64 | 77 | 56 | 110 | 62 | 9 | 11 | 10 | 23 | 26 | 8 | 3 | 10 | 9 | 4 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 4 | 0 | 0 | 0 | 18 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 5 | 0 | 4 | 0 | 10 | 6 | 4 | 0 | 0 | 11 | 63 | 0 | 1 | 0 | 15 | 8 | 4 | 2 | 0 | 12 | 3 | 0 | 9 | 2 | 4 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; Fuse | 20 | 18 | 2889 | 3956 | 2257 | 1316 | 1514 | 1994 | 1982 | 2047 | 1840 | 1944 | 1670 | 1273 | 1074 | 1161 | 997 | 928 | 663 | 361 | 221 | 354 | 316 | 296 | 277 | 366 | 359 | 297 | 257 | 387 | 303 | 251 | 169 | 177 | 205 | 147 | 137 | 144 | 968 | 181 | 84 | 84 | 90 | 88 | 93 | 123 | 134 | 163 | 185 | 199 | 227 | 287 | 172 | 124 | 173 | 187 | 160 | 181 | 158 | 192 | 191 | 119 | 214 | 95 | 60 | 58 | 77 | 131 | 99 | 86 | 37 | 42 | 8 | 29 | 27 | 0 | 9 | 4 | 13 | 16 | 18 | 45 | 33 | 57 | 31 | 19 | 6 | 5 | 0 | 58 | 65 | 29 | 27 | 28 | 41 | 5 | 0 | 6 | 8 | 1 | 17 | 12 | 4 | 0 | 0 | 6 | 36 | 20 | 0
| ˂ = 11 kV ; Switch | 31 | 19 | 2177 | 2798 | 2502 | 2976 | 3057 | 3656 | 3893 | 3827 | 3629 | 3442 | 3986 | 3692 | 2927 | 3091 | 2108 | 2241 | 1779 | 1215 | 1049 | 1235 | 1157 | 1118 | 1017 | 1263 | 1066 | 1237 | 1246 | 1290 | 1200 | 993 | 799 | 876 | 862 | 876 | 868 | 878 | 3148 | 1316 | 1124 | 1112 | 1239 | 1238 | 1527 | 1569 | 1473 | 1120 | 1280 | 1277 | 1413 | 1564 | 1366 | 1185 | 1161 | 1113 | 1131 | 1321 | 1261 | 563 | 480 | 305 | 509 | 260 | 151 | 99 | 136 | 117 | 130 | 80 | 74 | 64 | 47 | 41 | 46 | 5 | 14 | 4 | 19 | 24 | 15 | 45 | 31 | 57 | 25 | 15 | 4 | 17 | 10 | 67 | 72 | 38 | 98 | 73 | 28 | 20 | 0 | 18 | 9 | 9 | 9 | 12 | 4 | 0 | 0 | 2 | 30 | 21 | 7
| ˂ = 11 kV ; Circuit Breaker | 50 | 20 | 364 | 453 | 395 | 354 | 344 | 430 | 496 | 430 | 436 | 555 | 270 | 300 | 300 | 261 | 225 | 202 | 158 | 257 | 189 | 145 | 155 | 172 | 89 | 93 | 87 | 64 | 56 | 71 | 73 | 68 | 64 | 56 | 86 | 14 | 78 | 33 | 43 | 34 | 37 | 55 | 47 | 37 | 34 | 72 | 48 | 67 | 65 | 83 | 73 | 67 | 37 | 31 | 57 | 56 | 73 | 47 | 29 | 56 | 9 | 10 | 34 | 29 | 8 | 8 | 37 | 35 | 20 | 28 | 49 | 22 | 4 | 3 | 5 | 28 | 3 | 0 | 11 | 16 | 1 | 32 | 21 | 33 | 12 | 6 | 7 | 0 | 0 | 5 | 6 | 0 | 8 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 0
| > 11 kV & < = 22 kV ; Switch | 16 | 7 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 4 | 3 | 1 | 0 | 1 | 19 | 1 | 1 | 6 | 1 | 0 | 0 | 0 | 1 | 0 | 13 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker | 50.28 | 13.74 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Switch | 53 | 13 | 82 | 188 | 95 | 136 | 71 | 48 | 86 | 76 | 45 | 108 | 41 | 27 | 48 | 51 | 84 | 23 | 5 | 3 | 3 | 0 | 1 | 0 | 0 | 87 | 1 | 7 | 0 | 7 | 1 | 4 | 0 | 2 | 0 | 4 | 0 | 0 | 0 | 10 | 0 | 1 | 44 | 24 | 9 | 8 | 0 | 18 | 10 | 32 | 13 | 0 | 0 | 166 | 127 | 19 | 51 | 404 | 11 | 62 | 12 | 44 | 36 | 2 | 36 | 0 | 0 | 13 | 0 | 39 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker | 50 | 14 | 11 | 62 | 43 | 48 | 32 | 37 | 58 | 65 | 35 | 54 | 22 | 18 | 21 | 15 | 23 | 15 | 7 | 1 | 14 | 27 | 1 | 0 | 0 | 31 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 6 | 0 | 0 | 0 | 0 | 9 | 23 | 17 | 0 | 0 | 56 | 0 | 9 | 1 | 13 | 11 | 0 | 0 | 0 | 0 | 4 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Switch | 27 | 26 | 4 | 0 | 0 | 2 | 0 | 18 | 59 | 6 | 30 | 54 | 5 | 30 | 13 | 9 | 17 | 6 | 1 | 7 | 3 | 15 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 10 | 7 | 9 | 43 | 19 | 0 | 8 | 0 | 45 | 0 | 3 | 0 | 9 | 0 | 2 | 0 | 11 | 2 | 0 | 0 | 10 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker | 29 | 10 | 2 | 0 | 3 | 4 | 7 | 8 | 20 | 11 | 19 | 19 | 2 | 11 | 1 | 3 | 7 | 5 | 2 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Switch | 43 | 16 | 32 | 115 | 133 | 75 | 162 | 223 | 201 | 152 | 190 | 188 | 46 | 26 | 82 | 77 | 42 | 44 | 40 | 45 | 54 | 0 | 10 | 25 | 0 | 24 | 19 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 33 | 12 | 0 | 26 | 33 | 26 | 0 | 11 | 5 | 1 | 11 | 11 | 5 | 30 | 1 | 36 | 30 | 2 | 6 | 93 | 14 | 4 | 0 | 34 | 8 | 2 | 0 | 0 | 27 | 3 | 0 | 28 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Circuit Breaker | 29 | 14 | 0 | 17 | 29 | 26 | 38 | 56 | 41 | 34 | 41 | 62 | 33 | 37 | 40 | 29 | 17 | 14 | 22 | 8 | 19 | 5 | 10 | 4 | 2 | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 14 | 13 | 14 | 11 | 14 | 1 | 6 | 9 | 3 | 9 | 2 | 21 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 0 | 4 | 3 | 1 | 1 | 0 | 0 | 1 | 3 | 3 | 2 | 1 | 2 | 2 | 0 | 0 | 2 | 0 | 1 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road | 18 | 17 | 2109 | 2323 | 2043 | 2363 | 2503 | 2439 | 2588 | 2852 | 2910 | 3504 | 4127 | 2342 | 1154 | 568 | 500 | 461 | 303 | 358 | 478 | 512 | 1557 | 181 | 373 | 459 | 459 | 421 | 459 | 674 | 439 | 454 | 568 | 569 | 653 | 422 | 285 | 278 | 187 | 227 | 273 | 261 | 562 | 315 | 189 | 323 | 209 | 238 | 245 | 589 | 1035 | 1084 | 1582 | 1666 | 1190 | 283 | 87 | 58 | 21 | 28 | 0 | 1 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Luminaires ; Minor Road | 11 | 12 | 21448 | 8363 | 9809 | 12811 | 12855 | 12735 | 11172 | 10841 | 10424 | 8270 | 6841 | 7737 | 9659 | 5648 | 6777 | 7011 | 1213 | 971 | 1263 | 1538 | 4068 | 688 | 808 | 1401 | 1049 | 993 | 955 | 1010 | 840 | 780 | 582 | 555 | 628 | 507 | 241 | 326 | 268 | 349 | 477 | 702 | 879 | 450 | 495 | 473 | 370 | 313 | 367 | 563 | 717 | 811 | 1564 | 742 | 794 | 481 | 387 | 407 | 265 | 143 | 29 | 15 | 9 | 9 | 2 | 1 | 0 | 2 | 0 | 0 | 20 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets ; Major Road | 30 | 17 | 394 | 699 | 1710 | 385 | 481 | 2084 | 805 | 1247 | 1178 | 1301 | 1971 | 1292 | 884 | 1526 | 436 | 441 | 267 | 249 | 324 | 358 | 2322 | 335 | 551 | 703 | 613 | 571 | 669 | 1451 | 641 | 691 | 995 | 831 | 955 | 765 | 495 | 552 | 501 | 571 | 620 | 745 | 1450 | 982 | 556 | 1034 | 779 | 804 | 741 | 1230 | 1919 | 2346 | 2910 | 2865 | 2520 | 865 | 318 | 178 | 103 | 97 | 6 | 6 | 0 | 12 | 1 | 3 | 0 | 0 | 0 | 1 | 14 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets ; Minor Road | 24 | 17 | 2493 | 2606 | 7310 | 1831 | 2421 | 8255 | 5314 | 5407 | 5511 | 5646 | 7814 | 7688 | 7656 | 5339 | 6270 | 7209 | 1189 | 972 | 1375 | 2141 | 11046 | 1615 | 2311 | 3325 | 2549 | 2637 | 2538 | 4621 | 2254 | 2399 | 1850 | 1590 | 2142 | 2282 | 1336 | 1118 | 1315 | 1635 | 2103 | 3319 | 3996 | 2231 | 2075 | 2233 | 2511 | 1468 | 1720 | 2165 | 2505 | 2800 | 5113 | 2974 | 3504 | 2755 | 2382 | 3446 | 1388 | 886 | 123 | 46 | 30 | 20 | 3 | 4 | 1 | 4 | 1 | 1 | 79 | 3 | 2 | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 10 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| Lamps ; Major Road | 3 | 5 | 10222 | 13978 | 10310 | 15968 | 1568 | 865 | 743 | 276 | 303 | 179 | 114 | 37 | 20 | 6 | 17 | 12 | 9 | 10 | 17 | 17 | 127 | 4 | 5 | 12 | 5 | 10 | 3 | 8 | 4 | 10 | 8 | 6 | 12 | 16 | 5 | 5 | 8 | 5 | 8 | 8 | 17 | 8 | 2 | 6 | 4 | 11 | 6 | 19 | 36 | 53 | 75 | 98 | 60 | 11 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamps ; Minor Road | 3 | 3 | 37963 | 39956 | 40031 | 48562 | 13077 | 7835 | 3342 | 1457 | 974 | 453 | 127 | 128 | 100 | 82 | 64 | 76 | 34 | 36 | 23 | 23 | 125 | 13 | 27 | 25 | 7 | 18 | 17 | 14 | 11 | 13 | 10 | 11 | 13 | 12 | 9 | 21 | 4 | 8 | 11 | 10 | 20 | 8 | 20 | 14 | 9 | 9 | 13 | 25 | 10 | 20 | 24 | 10 | 8 | 3 | 2 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns ; Major Road | 42 | 18 | 167 | 198 | 326 | 195 | 286 | 318 | 231 | 298 | 298 | 373 | 351 | 251 | 266 | 216 | 202 | 124 | 122 | 147 | 88 | 84 | 66 | 125 | 97 | 122 | 95 | 104 | 106 | 51 | 132 | 183 | 101 | 241 | 210 | 298 | 164 | 75 | 192 | 277 | 390 | 293 | 203 | 209 | 268 | 205 | 104 | 183 | 195 | 254 | 465 | 258 | 192 | 579 | 560 | 418 | 412 | 427 | 650 | 379 | 398 | 362 | 261 | 412 | 104 | 34 | 393 | 101 | 167 | 35 | 41 | 37 | 16 | 37 | 67 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns ; Minor Road | 38 | 17 | 1000 | 1323 | 1577 | 1623 | 1708 | 1877 | 1808 | 2048 | 1400 | 1281 | 1343 | 1105 | 822 | 1078 | 1216 | 1107 | 744 | 582 | 566 | 798 | 350 | 554 | 212 | 368 | 391 | 289 | 264 | 249 | 311 | 310 | 250 | 370 | 237 | 321 | 184 | 353 | 586 | 531 | 854 | 772 | 519 | 397 | 709 | 577 | 237 | 317 | 197 | 467 | 326 | 538 | 348 | 552 | 845 | 961 | 801 | 808 | 959 | 471 | 1051 | 581 | 436 | 705 | 239 | 248 | 647 | 43 | 233 | 239 | 123 | 76 | 54 | 145 | 30 | 0 | 1 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices | 52 | 18 | 1516 | 2412 | 2032 | 1989 | 1584 | 1132 | 1902 | 1333 | 1868 | 3709 | 734 | 1002 | 884 | 1404 | 950 | 1085 | 498 | 1750 | 1197 | 832 | 887 | 909 | 377 | 946 | 501 | 824 | 411 | 551 | 554 | 3073 | 442 | 548 | 664 | 285 | 521 | 228 | 1218 | 819 | 346 | 2125 | 907 | 1357 | 897 | 1810 | 1039 | 543 | 1718 | 1197 | 811 | 1876 | 1370 | 448 | 1090 | 1078 | 914 | 1905 | 678 | 656 | 135 | 585 | 671 | 820 | 274 | 120 | 734 | 315 | 194 | 530 | 449 | 40 | 99 | 197 | 35 | 200 | 32 | 0 | 22 | 26 | 9 | 163 | 37 | 223 | 44 | 8 | 8 | 9 | 1 | 75 | 32 | 114 | 38 | 24 | 22 | 14 | 0 | 13 | 80 | 6 | 17 | 1 | 0 | 0 | 0 | 0 | 27 | 10 | 0
| Local Network Wiring Assets | 40 | 10 | 77 | 221.8 | 213.4 | 78 | 239.5 | 157.1 | 258.3 | 220.2 | 262.9 | 432.7 | 183.2 | 114.3 | 91.3 | 139.1 | 200.7 | 134 | 33.4 | 176.6 | 113.7 | 78 | 73.8 | 92.1 | 25.6 | 28.2 | 54.2 | 44.8 | 12.8 | 21.8 | 24.2 | 341.9 | 79.7 | 41.4 | 71.3 | 64.1 | 76.7 | 27.4 | 224.5 | 107 | 9.4 | 72.9 | 134.6 | 176.1 | 115.4 | 153.2 | 94.7 | 88.9 | 198.7 | 261.8 | 99.9 | 165 | 227.5 | 148 | 333.7 | 178.5 | 224.1 | 456.4 | 202.1 | 149.4 | 105.1 | 296.7 | 170.8 | 209.9 | 146.8 | 61.7 | 111.9 | 121.8 | 35.6 | 80.5 | 70.9 | 4.6 | 30.2 | 30.8 | 31.8 | 35.6 | 0.6 | 0 | 3.4 | 5.2 | 0 | 38.6 | 5.8 | 38 | 4 | 1.4 | 1.6 | 0 | 0 | 30.4 | 2.2 | 60.5 | 3.6 | 0.6 | 3 | 0.6 | 0 | 0.6 | 29.4 | 0.6 | 3 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Network Assets | 8 | 2 | 40 | 47 | 892 | 450 | 50 | 150 | 150 | 150 | 150 | 150 | 150 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Master Station Assets | 5.6 | 2 | 117 | 0 | 2 | 19 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Site Infrastructure | 10 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Linear Assets | 37 | 13 | 182.6 | 0 | 111 | 280.3 | 159.7 | 437.5 | 176.3 | 236.9 | 241.8 | 235.9 | 228.7 | 230.8 | 230.8 | 231 | 95.3 | 12.6 | 5.6 | 9.9 | 8.9 | 4.1 | 2.4 | 0.2 | 0.2 | 47.1 | 65.8 | 44 | 44.4 | 55.6 | 58 | 33.7 | 48.9 | 29.5 | 65.8 | 31.8 | 39 | 40.9 | 44.6 | 55.5 | 62.3 | 111.4 | 99.8 | 119.8 | 82 | 78.3 | 71.3 | 71.9 | 59.2 | 62.8 | 53.4 | 87.4 | 41.5 | 95 | 84 | 77.7 | 85.2 | 93.2 | 171.4 | 143.8 | 91.1 | 163.2 | 125.8 | 139.4 | 86.8 | 136.4 | 196.3 | 24.1 | 8.5 | 37.2 | 24.1 | 14.4 | 17 | 16.7 | 9.4 | 3.9 | 9.6 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AFLC | 35 | 18 | 0 | 3 | 2 | 3 | 6 | 11 | 5 | 7 | 4 | 10 | 7 | 8 | 6 | 8 | 28 | 5 | 4 | 4 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 3 | 2 | 4 | 1 | 4 | 1 | 5 | 7 | 1 | 8 | 7 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BY: DNSP DEFINED | DISTRIBUTION SUBSTATIONS - OTHER | 39 | 16 | 416 | 492 | 515 | 521 | 550 | 779 | 731 | 770 | 816 | 782 | 674 | 561 | 517 | 590 | 521 | 573 | 519 | 473 | 435 | 554 | 483 | 491 | 441 | 480 | 497 | 520 | 468 | 539 | 533 | 524 | 474 | 484 | 509 | 509 | 446 | 445 | 1120 | 615 | 556 | 541 | 538 | 469 | 546 | 560 | 551 | 468 | 519 | 491 | 528 | 480 | 479 | 464 | 405 | 420 | 425 | 429 | 360 | 214 | 294 | 174 | 210 | 129 | 99 | 111 | 68 | 44 | 36 | 27 | 32 | 23 | 16 | 15 | 16 | 3 | 6 | 1 | 3 | 9 | 3 | 16 | 9 | 10 | 6 | 4 | 1 | 3 | 3 | 14 | 21 | 12 | 19 | 14 | 9 | 4 | 0 | 6 | 1 | 2 | 3 | 2 | 1 | 0 | 0 | 1 | 5 | 5 | 1
| DISTRIBUTION VOLTAGE REGULATION | 11 | 4 | 1 | 0 | 3 | 11 | 18 | 33 | 31 | 17 | 1 | 13 | 12 | 10 | 7 | 16 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OVERHEAD CONDUCTORS - OTHER | 44 | 14 | 3 | 4 | 2 | 3 | 2 | 4 | 3 | 6 | 5 | 7 | 5 | 6 | 4 | 8 | 13 | 6 | 8 | 6 | 9 | 13 | 7 | 6 | 9 | 9 | 15 | 12 | 7 | 4 | 19 | 38 | 19 | 18 | 24 | 25 | 34 | 30 | 22 | 50 | 59 | 99 | 65 | 40 | 49 | 41 | 56 | 103 | 34 | 95 | 49 | 122 | 140 | 206 | 113 | 268 | 293 | 314 | 496 | 293 | 339 | 418 | 330 | 178 | 209 | 262 | 67 | 26 | 29 | 27 | 42 | 15 | 32 | 11 | 0 | 7 | 42 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
| TOWERS - > = 33 KV ; REFURBISHMENT | 51 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 26 | 0 | 1 | 0 | 23 | 12 | 98 | 7 | 0 | 0 | 81 | 43 | 1 | 91 | 42 | 15 | 121 | 73 | 40 | 38 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRANSFORMERS - OTHER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNDERGROUND CABLES - OTHER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ZONE & SUBTRANSMISSION SUBSTATIONS - OTHER | 57 | 18 | 2 | 4 | 4 | 1 | 6 | 3 | 7 | 4 | 7 | 9 | 3 | 3 | 3 | 4 | 4 | 3 | 0 | 3 | 2 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 2 | 3 | 2 | 1 | 3 | 4 | 0 | 2 | 3 | 5 | 4 | 4 | 3 | 3 | 6 | 8 | 4 | 4 | 8 | 2 | 8 | 6 | 5 | 10 | 5 | 3 | 2 | 6 | 3 | 6 | 4 | 2 | 2 | 2 | 1 | 1 | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DISTRIBUTION SUBSTATIONS - NOT AGE RELATED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OVERHEAD CONDUCTORS - NOT AGE RELATED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ZONE & SUBTRANSMISSION SUBSTATIONS - NOT AGE RELATED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FIELD DEVICES - NOT AGE RELATED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNDERGROUND CABLES - NOT AGE RELATED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SWITCHGEAR - NOT AGE RELATED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRANSFORMERS - NOT AGE RELATED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LAND (I.E. STRATEGIC SYSTEM PROPERTY) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; < = 11 KV ; CIRCUIT BREAKER REFURBISHMENT | 51 | 19 | 61 | 141 | 137 | 208 | 113 | 59 | 168 | 174 | 144 | 250 | 65 | 97 | 79 | 131 | 61 | 41 | 20 | 172 | 101 | 0 | 38 | 25 | 36 | 2 | 40 | 26 | 4 | 0 | 0 | 1 | 5 | 10 | 38 | 6 | 68 | 26 | 39 | 54 | 18 | 51 | 68 | 75 | 51 | 143 | 85 | 65 | 157 | 157 | 122 | 174 | 119 | 12 | 90 | 88 | 64 | 54 | 47 | 41 | 1 | 9 | 20 | 43 | 20 | 10 | 39 | 18 | 9 | 5 | 37 | 10 | 0 | 0 | 7 | 29 | 0 | 0 | 11 | 16 | 0 | 32 | 14 | 29 | 5 | 1 | 5 | 0 | 0 | 3 | 2 | 0 | 6 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.3 MD - Network level
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
5.3 MAXIMUM DEMAND AT NETWORK LEVEL
5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL (Summed at transmission connection point)
| UNIT | 2018-19
Raw network coincident MD | MW | 5434
Date MD occurred |  | 31/01/2019
Half hour time period MD occurred |  | 17:30:00
Winter/summer peaking |  | Summer
Embedded generation | MW | -165
Weather corrected (10% POE) network coincident MD | MW | 5994
Weather corrected (50% POE) network coincident MD | MW | 5424
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.4 MD & utilisation-Spatial
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL
There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data.
5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2018-19
SUBTRANSMISSION SUBSTATION | Argenton 132_33kV | Substation Rating | MVA | Non-Coincident | 142.9
|  |  |  | Coincident | 142.9
|  | Raw Adjusted MD | MW | Non-Coincident | 81.03
|  |  |  | Coincident | 70.33
|  | Raw Adjusted MD | MVA | Non-Coincident | 84.15
|  |  |  | Coincident | 73.04
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.069
|  |  |  | Coincident | -3.097
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 107.9
|  |  |  | Coincident | 93.63
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 112
|  |  |  | Coincident | 97.23
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 90.85
|  |  |  | Coincident | 78.86
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 94.35
|  |  |  | Coincident | 81.89
| Awaba 132_33kV | Substation Rating | MVA | Non-Coincident | 68.59
|  |  |  | Coincident | 68.59
|  | Raw Adjusted MD | MW | Non-Coincident | 7.353
|  |  |  | Coincident | 3.32
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.808
|  |  |  | Coincident | 3.526
|  | Date MD occurred |  | Non-Coincident | 18-12-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.406
|  |  |  | Coincident | 4.248
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.989
|  |  |  | Coincident | 4.511
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.476
|  |  |  | Coincident | 3.828
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.001
|  |  |  | Coincident | 4.065
| Bankstown 132_33kV | Substation Rating | MVA | Non-Coincident | 118
|  |  |  | Coincident | 118
|  | Raw Adjusted MD | MW | Non-Coincident | 59.72
|  |  |  | Coincident | 56.34
|  | Raw Adjusted MD | MVA | Non-Coincident | 60.97
|  |  |  | Coincident | 57.52
|  | Date MD occurred |  | Non-Coincident | 16-07-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.928
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 60.98
|  |  |  | Coincident | 62.39
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 62.26
|  |  |  | Coincident | 63.69
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 58.12
|  |  |  | Coincident | 56.77
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 59.34
|  |  |  | Coincident | 57.96
| Beresfield 132_33kV | Substation Rating | MVA | Non-Coincident | 150.1
|  |  |  | Coincident | 150.1
|  | Raw Adjusted MD | MW | Non-Coincident | 91.44
|  |  |  | Coincident | 76.96
|  | Raw Adjusted MD | MVA | Non-Coincident | 95.3
|  |  |  | Coincident | 80.22
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.624
|  |  |  | Coincident | -3.047
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 102.2
|  |  |  | Coincident | 86
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 106.5
|  |  |  | Coincident | 89.63
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 92.07
|  |  |  | Coincident | 77.5
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 95.97
|  |  |  | Coincident | 80.77
| Bunnerong North 132_33kV | Substation Rating | MVA | Non-Coincident | 312.6
|  |  |  | Coincident | 312.6
|  | Raw Adjusted MD | MW | Non-Coincident | 211.3
|  |  |  | Coincident | 209.9
|  | Raw Adjusted MD | MVA | Non-Coincident | 211.8
|  |  |  | Coincident | 210.4
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.898
|  |  |  | Coincident | -1.11
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 212.3
|  |  |  | Coincident | 210.9
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 212.8
|  |  |  | Coincident | 211.4
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 202
|  |  |  | Coincident | 200.7
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 202.5
|  |  |  | Coincident | 201.2
| Canterbury 132_33kV | Substation Rating | MVA | Non-Coincident | 186.6
|  |  |  | Coincident | 186.6
|  | Raw Adjusted MD | MW | Non-Coincident | 147.3
|  |  |  | Coincident | 147.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 157.6
|  |  |  | Coincident | 157.3
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.68
|  |  |  | Coincident | -2.255
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 171.7
|  |  |  | Coincident | 171.4
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 183.6
|  |  |  | Coincident | 183.3
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 146.6
|  |  |  | Coincident | 146.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 156.8
|  |  |  | Coincident | 156.6
| Eraring 132_33kV | Substation Rating | MVA | Non-Coincident | 57.16
|  |  |  | Coincident | 57.16
|  | Raw Adjusted MD | MW | Non-Coincident | 29.93
|  |  |  | Coincident | 21.65
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.61
|  |  |  | Coincident | 22.77
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.588
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.93
|  |  |  | Coincident | 21.65
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.61
|  |  |  | Coincident | 22.77
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.93
|  |  |  | Coincident | 21.65
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.61
|  |  |  | Coincident | 22.77
| Gosford 132_33kV | Substation Rating | MVA | Non-Coincident | 0.06
|  |  |  | Coincident | 0.06
|  | Raw Adjusted MD | MW | Non-Coincident | 23.74
|  |  |  | Coincident | 22.08
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.58
|  |  |  | Coincident | 22.85
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.009
|  |  |  | Coincident | -0.751
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.02
|  |  |  | Coincident | 25.12
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.97
|  |  |  | Coincident | 26.01
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.78
|  |  |  | Coincident | 22.11
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.62
|  |  |  | Coincident | 22.89
| Gosford 132_66kV | Substation Rating | MVA | Non-Coincident | 225.4
|  |  |  | Coincident | 225.4
|  | Raw Adjusted MD | MW | Non-Coincident | 130.2
|  |  |  | Coincident | 122.9
|  | Raw Adjusted MD | MVA | Non-Coincident | 134.4
|  |  |  | Coincident | 126.9
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.23
|  |  |  | Coincident | -3.856
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 150.5
|  |  |  | Coincident | 142
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 155.3
|  |  |  | Coincident | 146.6
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 130.8
|  |  |  | Coincident | 123.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 135
|  |  |  | Coincident | 127.4
| Homebush 132_33kV | Substation Rating | MVA | Non-Coincident | 140.3
|  |  |  | Coincident | 140.3
|  | Raw Adjusted MD | MW | Non-Coincident | 84.9
|  |  |  | Coincident | 84.27
|  | Raw Adjusted MD | MVA | Non-Coincident | 86.41
|  |  |  | Coincident | 85.77
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.824
|  |  |  | Coincident | -1.019
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 96.57
|  |  |  | Coincident | 95.85
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 98.29
|  |  |  | Coincident | 97.56
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 86.5
|  |  |  | Coincident | 85.85
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 88.04
|  |  |  | Coincident | 87.38
| Kooragang 132_33kV | Substation Rating | MVA | Non-Coincident | 142.9
|  |  |  | Coincident | 142.9
|  | Raw Adjusted MD | MW | Non-Coincident | 49.22
|  |  |  | Coincident | 29.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 72.17
|  |  |  | Coincident | 42.65
|  | Date MD occurred |  | Non-Coincident | 15-02-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.008
|  |  |  | Coincident | -0.003
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.22
|  |  |  | Coincident | 29.09
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 72.17
|  |  |  | Coincident | 42.65
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 49.22
|  |  |  | Coincident | 29.09
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 72.17
|  |  |  | Coincident | 42.65
| Kuring-gai 132_33kV | Substation Rating | MVA | Non-Coincident | 261
|  |  |  | Coincident | 261
|  | Raw Adjusted MD | MW | Non-Coincident | 143.8
|  |  |  | Coincident | 139.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 146.6
|  |  |  | Coincident | 142.1
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.545
|  |  |  | Coincident | -2.66
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 168.9
|  |  |  | Coincident | 163.7
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 172.2
|  |  |  | Coincident | 166.9
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 146.3
|  |  |  | Coincident | 141.8
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 149.2
|  |  |  | Coincident | 144.6
| Kurri 132_33kV | Substation Rating | MVA | Non-Coincident | 156.2
|  |  |  | Coincident | 156.2
|  | Raw Adjusted MD | MW | Non-Coincident | 127.9
|  |  |  | Coincident | 110.6
|  | Raw Adjusted MD | MVA | Non-Coincident | 134.7
|  |  |  | Coincident | 116.5
|  | Date MD occurred |  | Non-Coincident | 29-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.344
|  |  |  | Coincident | -3.185
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 149.5
|  |  |  | Coincident | 129.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 157.4
|  |  |  | Coincident | 136
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 134.7
|  |  |  | Coincident | 116.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 141.8
|  |  |  | Coincident | 122.6
| Macquarie 132_33kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Merewether 132_33kV | Substation Rating | MVA | Non-Coincident | 274.4
|  |  |  | Coincident | 274.4
|  | Raw Adjusted MD | MW | Non-Coincident | 146.4
|  |  |  | Coincident | 141.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 152.8
|  |  |  | Coincident | 147.5
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.671
|  |  |  | Coincident | -3.278
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 176.8
|  |  |  | Coincident | 170.7
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 184.6
|  |  |  | Coincident | 178.2
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 156.4
|  |  |  | Coincident | 150.9
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 163.3
|  |  |  | Coincident | 157.6
| Mitchell Line 132_66kV | Substation Rating | MVA | Non-Coincident | 141.3
|  |  |  | Coincident | 141.3
|  | Raw Adjusted MD | MW | Non-Coincident | 72.93
|  |  |  | Coincident | 66.88
|  | Raw Adjusted MD | MVA | Non-Coincident | 77.16
|  |  |  | Coincident | 70.75
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.003
|  |  |  | Coincident | -1.428
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 80.24
|  |  |  | Coincident | 73.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 84.89
|  |  |  | Coincident | 77.84
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 75.24
|  |  |  | Coincident | 68.99
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 79.6
|  |  |  | Coincident | 72.99
| Morisset 132_33kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Munmorah 132_33kV | Substation Rating | MVA | Non-Coincident | 80.99
|  |  |  | Coincident | 80.99
|  | Raw Adjusted MD | MW | Non-Coincident | 26.28
|  |  |  | Coincident | 23.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.53
|  |  |  | Coincident | 24.65
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.939
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.38
|  |  |  | Coincident | 25.32
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.67
|  |  |  | Coincident | 26.62
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.01
|  |  |  | Coincident | 22.53
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 27.24
|  |  |  | Coincident | 23.68
| Muswellbrook 132_33kV | Substation Rating | MVA | Non-Coincident | 47.1
|  |  |  | Coincident | 47.1
|  | Raw Adjusted MD | MW | Non-Coincident | 19.11
|  |  |  | Coincident | 15.81
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.39
|  |  |  | Coincident | 16.04
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.004
|  |  |  | Coincident | -0.528
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.79
|  |  |  | Coincident | 17.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.09
|  |  |  | Coincident | 17.45
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.73
|  |  |  | Coincident | 15.5
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.01
|  |  |  | Coincident | 15.73
| Muswellbrook North 132_33kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Ourimbah 132_33kV | Substation Rating | MVA | Non-Coincident | 22.3
|  |  |  | Coincident | 21.7
|  | Raw Adjusted MD | MW | Non-Coincident | 26.82
|  |  |  | Coincident | 11.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.34
|  |  |  | Coincident | 13.07
|  | Date MD occurred |  | Non-Coincident | 19-07-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.564
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.42
|  |  |  | Coincident | 14.12
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.8
|  |  |  | Coincident | 15.48
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.73
|  |  |  | Coincident | 12.73
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.08
|  |  |  | Coincident | 13.96
| Ourimbah 132_66kV | Substation Rating | MVA | Non-Coincident | 0.01
|  |  |  | Coincident | 0.01
|  | Raw Adjusted MD | MW | Non-Coincident | 46.72
|  |  |  | Coincident | 42.39
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.07
|  |  |  | Coincident | 43.61
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.014
|  |  |  | Coincident | -1.256
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.46
|  |  |  | Coincident | 44.87
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.89
|  |  |  | Coincident | 46.17
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.77
|  |  |  | Coincident | 40.62
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.07
|  |  |  | Coincident | 41.8
| Peakhurst 132_33kV | Substation Rating | MVA | Non-Coincident | 233.2
|  |  |  | Coincident | 233.2
|  | Raw Adjusted MD | MW | Non-Coincident | 107.8
|  |  |  | Coincident | 107.8
|  | Raw Adjusted MD | MVA | Non-Coincident | 109.2
|  |  |  | Coincident | 109.2
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.949
|  |  |  | Coincident | -2.289
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 120.3
|  |  |  | Coincident | 120.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 122
|  |  |  | Coincident | 122
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 101.7
|  |  |  | Coincident | 101.7
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 103.1
|  |  |  | Coincident | 103.1
| Port Hacking 132_33kV | Substation Rating | MVA | Non-Coincident | 159.1
|  |  |  | Coincident | 159.1
|  | Raw Adjusted MD | MW | Non-Coincident | 104.1
|  |  |  | Coincident | 98.94
|  | Raw Adjusted MD | MVA | Non-Coincident | 115.7
|  |  |  | Coincident | 109.9
|  | Date MD occurred |  | Non-Coincident | 16-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.596
|  |  |  | Coincident | -1.437
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 113.1
|  |  |  | Coincident | 107.5
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 125.7
|  |  |  | Coincident | 119.4
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 100.4
|  |  |  | Coincident | 95.35
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 111.5
|  |  |  | Coincident | 105.9
| Pyrmont 132_33kV | Substation Rating | MVA | Non-Coincident | 131.7
|  |  |  | Coincident | 131.7
|  | Raw Adjusted MD | MW | Non-Coincident | 93.26
|  |  |  | Coincident | 87.37
|  | Raw Adjusted MD | MVA | Non-Coincident | 93.4
|  |  |  | Coincident | 87.5
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 10:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.743
|  |  |  | Coincident | -0.327
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 99.02
|  |  |  | Coincident | 92.76
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 99.18
|  |  |  | Coincident | 92.91
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 93.36
|  |  |  | Coincident | 87.46
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 93.51
|  |  |  | Coincident | 87.6
| Rozelle 132_33kV | Substation Rating | MVA | Non-Coincident | 40
|  |  |  | Coincident | 40
|  | Raw Adjusted MD | MW | Non-Coincident | 10.82
|  |  |  | Coincident | 0.192
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.02
|  |  |  | Coincident | 0.213
|  | Date MD occurred |  | Non-Coincident | 15-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 9:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.01
|  |  |  | Coincident | 0.213
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.34
|  |  |  | Coincident | 0.237
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.82
|  |  |  | Coincident | 0.192
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.02
|  |  |  | Coincident | 0.213
| Singleton 132_66kV | Substation Rating | MVA | Non-Coincident | 300.7
|  |  |  | Coincident | 284.4
|  | Raw Adjusted MD | MW | Non-Coincident | 132.7
|  |  |  | Coincident | 101.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 141.5
|  |  |  | Coincident | 111.4
|  | Date MD occurred |  | Non-Coincident | 20-08-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 0:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.001
|  |  |  | Coincident | -1.997
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 136.9
|  |  |  | Coincident | 116.8
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 146
|  |  |  | Coincident | 128.5
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 132.8
|  |  |  | Coincident | 105.2
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 141.6
|  |  |  | Coincident | 115.8
| Strathfield 132_33kV | Substation Rating | MVA | Non-Coincident | 68.59
|  |  |  | Coincident | 68.59
|  | Raw Adjusted MD | MW | Non-Coincident | 21.13
|  |  |  | Coincident | 18.28
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.11
|  |  |  | Coincident | 25.19
|  | Date MD occurred |  | Non-Coincident | 22-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.77
|  |  |  | Coincident | 18.83
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30
|  |  |  | Coincident | 25.95
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.79
|  |  |  | Coincident | 17.99
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.65
|  |  |  | Coincident | 24.78
| Surry Hills 132_33kV | Substation Rating | MVA | Non-Coincident | 346.7
|  |  |  | Coincident | 346.7
|  | Raw Adjusted MD | MW | Non-Coincident | 157.5
|  |  |  | Coincident | 152.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 157.9
|  |  |  | Coincident | 152.8
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.241
|  |  |  | Coincident | -0.361
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 164.3
|  |  |  | Coincident | 158.9
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 164.8
|  |  |  | Coincident | 159.3
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 155.3
|  |  |  | Coincident | 150.2
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 155.8
|  |  |  | Coincident | 150.6
| Sydney East 132_33kV | Substation Rating | MVA | Non-Coincident | 149
|  |  |  | Coincident | 141
|  | Raw Adjusted MD | MW | Non-Coincident | 74.62
|  |  |  | Coincident | 70.38
|  | Raw Adjusted MD | MVA | Non-Coincident | 76.04
|  |  |  | Coincident | 70.6
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.001
|  |  |  | Coincident | -1.885
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 77.24
|  |  |  | Coincident | 76.06
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 78.72
|  |  |  | Coincident | 76.29
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 73.9
|  |  |  | Coincident | 68.31
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 75.31
|  |  |  | Coincident | 68.52
| Tomago 132_33kV | Substation Rating | MVA | Non-Coincident | 153.1
|  |  |  | Coincident | 153.1
|  | Raw Adjusted MD | MW | Non-Coincident | 111
|  |  |  | Coincident | 97.44
|  | Raw Adjusted MD | MVA | Non-Coincident | 115.2
|  |  |  | Coincident | 101.2
|  | Date MD occurred |  | Non-Coincident | 26-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.834
|  |  |  | Coincident | -4.073
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 128.4
|  |  |  | Coincident | 112.8
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 133.3
|  |  |  | Coincident | 117.1
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 115.7
|  |  |  | Coincident | 101.6
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 120.1
|  |  |  | Coincident | 105.5
| Waratah (Comsteel) 132_33kV | Substation Rating | MVA | Non-Coincident | 60
|  |  |  | Coincident | 60
|  | Raw Adjusted MD | MW | Non-Coincident | 55.12
|  |  |  | Coincident | 16.07
|  | Raw Adjusted MD | MVA | Non-Coincident | 55.67
|  |  |  | Coincident | 16.23
|  | Date MD occurred |  | Non-Coincident | 20-02-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 55.12
|  |  |  | Coincident | 16.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 55.67
|  |  |  | Coincident | 16.23
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 55.12
|  |  |  | Coincident | 16.07
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 55.67
|  |  |  | Coincident | 16.23
| Waratah (Domestic) 132_33kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident | 0
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 0
Coincident
|  | Date MD occurred |  | Non-Coincident | 25-02-19
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 10:00:00
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Warringah 132_33kV | Substation Rating | MVA | Non-Coincident | 217.4
|  |  |  | Coincident | 217.4
|  | Raw Adjusted MD | MW | Non-Coincident | 161.6
|  |  |  | Coincident | 160.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 164.9
|  |  |  | Coincident | 163.6
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.713
|  |  |  | Coincident | -3.483
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 169.6
|  |  |  | Coincident | 168.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 173
|  |  |  | Coincident | 171.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 152.7
|  |  |  | Coincident | 151.6
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 155.8
|  |  |  | Coincident | 154.6
| Willoughby 132_33kV | Substation Rating | MVA | Non-Coincident | 233.2
|  |  |  | Coincident | 233.2
|  | Raw Adjusted MD | MW | Non-Coincident | 115.5
|  |  |  | Coincident | 115.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 121.7
|  |  |  | Coincident | 121.7
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.359
|  |  |  | Coincident | -0.865
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 119.9
|  |  |  | Coincident | 119.9
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 126.3
|  |  |  | Coincident | 126.3
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 111.1
|  |  |  | Coincident | 111.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 117
|  |  |  | Coincident | 117
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident | 25.53
|  |  |  | Coincident | 25.53
|  | Raw Adjusted MD | MW | Non-Coincident | 5.915
|  |  |  | Coincident | 4.779
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.02
|  |  |  | Coincident | 4.863
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.239
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.489
|  |  |  | Coincident | 5.243
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.604
|  |  |  | Coincident | 5.336
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.982
|  |  |  | Coincident | 4.833
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.088
|  |  |  | Coincident | 4.919
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2018-19
ZONE SUBSTATION | Aberdeen 66_11kV | Substation Rating | MVA | Non-Coincident | 63.03
|  |  |  | Coincident | 63.03
|  | Raw Adjusted MD | MW | Non-Coincident | 27.36
|  |  |  | Coincident | 24.75
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.77
|  |  |  | Coincident | 25.12
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.005
|  |  |  | Coincident | -0.748
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.77
|  |  |  | Coincident | 30.55
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.28
|  |  |  | Coincident | 31.01
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.44
|  |  |  | Coincident | 26.63
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.88
|  |  |  | Coincident | 27.03
| Adamstown 132_11kV | Substation Rating | MVA | Non-Coincident | 60.8
|  |  |  | Coincident | 60.8
|  | Raw Adjusted MD | MW | Non-Coincident | 28.61
|  |  |  | Coincident | 26.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.41
|  |  |  | Coincident | 27.19
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.007
|  |  |  | Coincident | -1.023
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.46
|  |  |  | Coincident | 30.94
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.4
|  |  |  | Coincident | 31.81
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.15
|  |  |  | Coincident | 27.88
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31
|  |  |  | Coincident | 28.66
| Argenton 132_11kV | Substation Rating | MVA | Non-Coincident | 21.43
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident | 14.01
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.75
Coincident
|  | Date MD occurred |  | Non-Coincident | 19-06-18
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.25
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.9
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.76
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.38
Coincident
| Arncliffe 33_11kV | Substation Rating | MVA | Non-Coincident | 41.01
|  |  |  | Coincident | 41.01
|  | Raw Adjusted MD | MW | Non-Coincident | 25.14
|  |  |  | Coincident | 21.8
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.67
|  |  |  | Coincident | 23.13
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.678
|  |  |  | Coincident | -0.254
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.91
|  |  |  | Coincident | 25.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.67
|  |  |  | Coincident | 26.6
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.39
|  |  |  | Coincident | 22.89
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28
|  |  |  | Coincident | 24.28
| Auburn 33_11kV | Substation Rating | MVA | Non-Coincident | 63.67
|  |  |  | Coincident | 59.83
|  | Raw Adjusted MD | MW | Non-Coincident | 35.34
|  |  |  | Coincident | 32.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.49
|  |  |  | Coincident | 32.42
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.001
|  |  |  | Coincident | -1.188
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.11
|  |  |  | Coincident | 37.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.27
|  |  |  | Coincident | 37.2
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 36.81
|  |  |  | Coincident | 32.63
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.96
|  |  |  | Coincident | 32.75
| Avoca 66_11kV | Substation Rating | MVA | Non-Coincident | 23.59
|  |  |  | Coincident | 23.59
|  | Raw Adjusted MD | MW | Non-Coincident | 9.442
|  |  |  | Coincident | 8.331
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.569
|  |  |  | Coincident | 8.444
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.809
|  |  |  | Coincident | -0.588
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.45
|  |  |  | Coincident | 10.1
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.6
|  |  |  | Coincident | 10.24
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.812
|  |  |  | Coincident | 8.658
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.944
|  |  |  | Coincident | 8.774
| Avondale 33_11kV | Substation Rating | MVA | Non-Coincident | 2.44
|  |  |  | Coincident | 2.44
|  | Raw Adjusted MD | MW | Non-Coincident | 0.953
|  |  |  | Coincident | 0.617
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.985
|  |  |  | Coincident | 0.637
|  | Date MD occurred |  | Non-Coincident | 20-12-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.004
|  |  |  | Coincident | -0.021
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.948
|  |  |  | Coincident | 0.614
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.98
|  |  |  | Coincident | 0.634
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.876
|  |  |  | Coincident | 0.566
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.905
|  |  |  | Coincident | 0.585
| Baerami 33_11kV | Substation Rating | MVA | Non-Coincident | 43.92
|  |  |  | Coincident | 43.92
|  | Raw Adjusted MD | MW | Non-Coincident | 32.51
|  |  |  | Coincident | 28.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.6
|  |  |  | Coincident | 28.72
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.679
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.26
|  |  |  | Coincident | 28.35
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.36
|  |  |  | Coincident | 28.63
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.68
|  |  |  | Coincident | 25.18
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.78
|  |  |  | Coincident | 25.42
| Balgowlah North 132_11kV | Substation Rating | MVA | Non-Coincident | 63.52
|  |  |  | Coincident | 63.52
|  | Raw Adjusted MD | MW | Non-Coincident | 45.6
|  |  |  | Coincident | 44.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 47.12
|  |  |  | Coincident | 45.88
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.339
|  |  |  | Coincident | -1.124
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.3
|  |  |  | Coincident | 48
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.94
|  |  |  | Coincident | 49.6
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.56
|  |  |  | Coincident | 43.39
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.05
|  |  |  | Coincident | 44.84
| Bankstown 132_11kV | Substation Rating | MVA | Non-Coincident | 20.69
|  |  |  | Coincident | 20.69
|  | Raw Adjusted MD | MW | Non-Coincident | 17.8
|  |  |  | Coincident | 17.69
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.06
|  |  |  | Coincident | 18.05
|  | Date MD occurred |  | Non-Coincident | 04-07-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 8:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.166
|  |  |  | Coincident | -0.315
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.28
|  |  |  | Coincident | 19.65
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.56
|  |  |  | Coincident | 20.06
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.35
|  |  |  | Coincident | 17.42
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.62
|  |  |  | Coincident | 17.78
| Bass Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 26.67
|  |  |  | Coincident | 26.67
|  | Raw Adjusted MD | MW | Non-Coincident | 22.36
|  |  |  | Coincident | 22.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.89
|  |  |  | Coincident | 23.64
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.298
|  |  |  | Coincident | -0.369
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.52
|  |  |  | Coincident | 23.28
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.13
|  |  |  | Coincident | 24.87
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.51
|  |  |  | Coincident | 21.28
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.98
|  |  |  | Coincident | 22.74
| Beacon Hill 33_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Belmore Park 132_11kV | Substation Rating | MVA | Non-Coincident | 40.29
|  |  |  | Coincident | 40.29
|  | Raw Adjusted MD | MW | Non-Coincident | 27.72
|  |  |  | Coincident | 26.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.6
|  |  |  | Coincident | 26.92
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.156
|  |  |  | Coincident | -0.762
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.86
|  |  |  | Coincident | 30
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.88
|  |  |  | Coincident | 30.95
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 27.6
|  |  |  | Coincident | 25.98
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.48
|  |  |  | Coincident | 26.81
| Belrose 33_11kV | Substation Rating | MVA | Non-Coincident | 59.9
|  |  |  | Coincident | 59.9
|  | Raw Adjusted MD | MW | Non-Coincident | 42.43
|  |  |  | Coincident | 41.22
|  | Raw Adjusted MD | MVA | Non-Coincident | 43.89
|  |  |  | Coincident | 42.64
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.057
|  |  |  | Coincident | -0.954
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.05
|  |  |  | Coincident | 47.65
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.74
|  |  |  | Coincident | 49.29
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.21
|  |  |  | Coincident | 42.94
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.73
|  |  |  | Coincident | 44.42
| Berkeley Vale 132_11kV | Substation Rating | MVA | Non-Coincident | 42.33
|  |  |  | Coincident | 42.33
|  | Raw Adjusted MD | MW | Non-Coincident | 22.33
|  |  |  | Coincident | 21.79
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.99
|  |  |  | Coincident | 23.42
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.076
|  |  |  | Coincident | -0.707
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.91
|  |  |  | Coincident | 28.22
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.06
|  |  |  | Coincident | 30.32
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.81
|  |  |  | Coincident | 24.22
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.66
|  |  |  | Coincident | 26.02
| Berowra 132_11kV | Substation Rating | MVA | Non-Coincident | 44.78
|  |  |  | Coincident | 41.67
|  | Raw Adjusted MD | MW | Non-Coincident | 14.04
|  |  |  | Coincident | 13.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.91
|  |  |  | Coincident | 15.08
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.016
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.87
|  |  |  | Coincident | 14.79
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.8
|  |  |  | Coincident | 16.36
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.4
|  |  |  | Coincident | 13.9
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.3
|  |  |  | Coincident | 15.38
| Blackwattle Bay 33_5kV | Substation Rating | MVA | Non-Coincident | 31.59
|  |  |  | Coincident | 31.59
|  | Raw Adjusted MD | MW | Non-Coincident | 19.66
|  |  |  | Coincident | 19.66
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.1
|  |  |  | Coincident | 20.1
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.166
|  |  |  | Coincident | -0.4
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.75
|  |  |  | Coincident | 20.75
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.22
|  |  |  | Coincident | 21.22
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.01
|  |  |  | Coincident | 18.01
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.42
|  |  |  | Coincident | 18.42
| Blakehurst 33_11kV | Substation Rating | MVA | Non-Coincident | 55.16
|  |  |  | Coincident | 55.16
|  | Raw Adjusted MD | MW | Non-Coincident | 25.15
|  |  |  | Coincident | 24.93
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.58
|  |  |  | Coincident | 28.33
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.19
|  |  |  | Coincident | -0.285
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.37
|  |  |  | Coincident | 25.14
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.82
|  |  |  | Coincident | 28.57
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.48
|  |  |  | Coincident | 23.27
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.68
|  |  |  | Coincident | 26.44
| Botany 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 8.909
|  |  |  | Coincident | 6.804
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.03
|  |  |  | Coincident | 6.897
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.005
|  |  |  | Coincident | -0.433
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.34
|  |  |  | Coincident | 8.66
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.49
|  |  |  | Coincident | 8.777
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.916
|  |  |  | Coincident | 7.573
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.05
|  |  |  | Coincident | 7.676
| Brandy Hill 132_11kV | Substation Rating | MVA | Non-Coincident | 15.07
|  |  |  | Coincident | 15.07
|  | Raw Adjusted MD | MW | Non-Coincident | 13.18
|  |  |  | Coincident | 10.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.41
|  |  |  | Coincident | 10.31
|  | Date MD occurred |  | Non-Coincident | 16-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.006
|  |  |  | Coincident | -0.527
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.67
|  |  |  | Coincident | 12.05
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.95
|  |  |  | Coincident | 12.27
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.12
|  |  |  | Coincident | 10.86
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.37
|  |  |  | Coincident | 11.05
| Branxton 66_11kV | Substation Rating | MVA | Non-Coincident | 40.66
|  |  |  | Coincident | 40.66
|  | Raw Adjusted MD | MW | Non-Coincident | 24.28
|  |  |  | Coincident | 21.94
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.06
|  |  |  | Coincident | 22.65
|  | Date MD occurred |  | Non-Coincident | 30-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.552
|  |  |  | Coincident | -0.61
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.59
|  |  |  | Coincident | 25.85
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.51
|  |  |  | Coincident | 26.68
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.77
|  |  |  | Coincident | 23.29
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.6
|  |  |  | Coincident | 24.04
| Broadmeadow 132_11kV | Substation Rating | MVA | Non-Coincident | 54.33
|  |  |  | Coincident | 54.33
|  | Raw Adjusted MD | MW | Non-Coincident | 41.07
|  |  |  | Coincident | 36.68
|  | Raw Adjusted MD | MVA | Non-Coincident | 43
|  |  |  | Coincident | 38.41
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.718
|  |  |  | Coincident | -0.381
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 42.52
|  |  |  | Coincident | 37.98
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 44.52
|  |  |  | Coincident | 39.77
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.48
|  |  |  | Coincident | 36.16
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.38
|  |  |  | Coincident | 37.86
| Brookvale 33_11kV | Substation Rating | MVA | Non-Coincident | 83.6
|  |  |  | Coincident | 83.6
|  | Raw Adjusted MD | MW | Non-Coincident | 83.67
|  |  |  | Coincident | 83.67
|  | Raw Adjusted MD | MVA | Non-Coincident | 84.44
|  |  |  | Coincident | 84.44
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.339
|  |  |  | Coincident | -0.817
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 91.76
|  |  |  | Coincident | 91.76
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 92.61
|  |  |  | Coincident | 92.61
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 81.48
|  |  |  | Coincident | 81.48
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 82.24
|  |  |  | Coincident | 82.24
| Burwood 132_11kV | Substation Rating | MVA | Non-Coincident | 62.8
|  |  |  | Coincident | 62.8
|  | Raw Adjusted MD | MW | Non-Coincident | 40.11
|  |  |  | Coincident | 38.73
|  | Raw Adjusted MD | MVA | Non-Coincident | 41.38
|  |  |  | Coincident | 39.95
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.08
|  |  |  | Coincident | -0.08
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.73
|  |  |  | Coincident | 43.19
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.15
|  |  |  | Coincident | 44.56
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.29
|  |  |  | Coincident | 39.86
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.59
|  |  |  | Coincident | 41.12
| Campbell St 132_11kV | Substation Rating | MVA | Non-Coincident | 60.8
|  |  |  | Coincident | 60.8
|  | Raw Adjusted MD | MW | Non-Coincident | 25.99
|  |  |  | Coincident | 25.28
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.25
|  |  |  | Coincident | 25.53
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.251
|  |  |  | Coincident | -0.31
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.18
|  |  |  | Coincident | 27.4
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.46
|  |  |  | Coincident | 27.68
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.88
|  |  |  | Coincident | 25.16
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.14
|  |  |  | Coincident | 25.42
| Camperdown 33_11kV | Substation Rating | MVA | Non-Coincident | 13.86
|  |  |  | Coincident | 13.86
|  | Raw Adjusted MD | MW | Non-Coincident | 3.018
|  |  |  | Coincident | 2.917
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.161
|  |  |  | Coincident | 3.126
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.046
|  |  |  | Coincident | 3.091
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.191
|  |  |  | Coincident | 3.313
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.941
|  |  |  | Coincident | 2.854
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.081
|  |  |  | Coincident | 3.058
| Camperdown 33_5kV | Substation Rating | MVA | Non-Coincident | 87.01
|  |  |  | Coincident | 87.01
|  | Raw Adjusted MD | MW | Non-Coincident | 72.24
|  |  |  | Coincident | 72.24
|  | Raw Adjusted MD | MVA | Non-Coincident | 73.2
|  |  |  | Coincident | 73.2
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.499
|  |  |  | Coincident | -1.203
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 86.95
|  |  |  | Coincident | 86.95
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 88.1
|  |  |  | Coincident | 88.1
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 72.1
|  |  |  | Coincident | 72.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 73.05
|  |  |  | Coincident | 73.05
| Campsie 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 17.56
|  |  |  | Coincident | 15.9
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.94
|  |  |  | Coincident | 16.25
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.266
|  |  |  | Coincident | -0.642
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.14
|  |  |  | Coincident | 19.15
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.6
|  |  |  | Coincident | 19.56
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.05
|  |  |  | Coincident | 17.25
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.47
|  |  |  | Coincident | 17.63
| Cardiff 33_11kV | Substation Rating | MVA | Non-Coincident | 21.68
|  |  |  | Coincident | 19.7
|  | Raw Adjusted MD | MW | Non-Coincident | 11.17
|  |  |  | Coincident | 9.427
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.68
|  |  |  | Coincident | 9.427
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.295
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.93
|  |  |  | Coincident | 11.33
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.48
|  |  |  | Coincident | 11.33
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.43
|  |  |  | Coincident | 9.884
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.95
|  |  |  | Coincident | 9.884
| Careel Bay 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 24.69
|  |  |  | Coincident | 23.08
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.52
|  |  |  | Coincident | 24.79
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.52
|  |  |  | Coincident | -0.237
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.94
|  |  |  | Coincident | 24.25
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.86
|  |  |  | Coincident | 26.04
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.81
|  |  |  | Coincident | 22.26
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.58
|  |  |  | Coincident | 23.9
| Caringbah 33_11kV | Substation Rating | MVA | Non-Coincident | 90.65
|  |  |  | Coincident | 90.65
|  | Raw Adjusted MD | MW | Non-Coincident | 64.11
|  |  |  | Coincident | 64.11
|  | Raw Adjusted MD | MVA | Non-Coincident | 69.73
|  |  |  | Coincident | 69.73
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.211
|  |  |  | Coincident | -0.699
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 66.66
|  |  |  | Coincident | 66.66
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 72.51
|  |  |  | Coincident | 72.51
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 61.42
|  |  |  | Coincident | 61.42
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 66.81
|  |  |  | Coincident | 66.81
| Castle Cove 132_11kV | Substation Rating | MVA | Non-Coincident | 26.5
|  |  |  | Coincident | 26.5
|  | Raw Adjusted MD | MW | Non-Coincident | 25
|  |  |  | Coincident | 18.66
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.57
|  |  |  | Coincident | 19.08
|  | Date MD occurred |  | Non-Coincident | 18-02-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.55
|  |  |  | Coincident | 24.29
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.29
|  |  |  | Coincident | 24.84
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.33
|  |  |  | Coincident | 21.89
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30
|  |  |  | Coincident | 22.38
| Cessnock South 33_11kV | Substation Rating | MVA | Non-Coincident | 60.17
|  |  |  | Coincident | 60.17
|  | Raw Adjusted MD | MW | Non-Coincident | 33.07
|  |  |  | Coincident | 30.83
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.27
|  |  |  | Coincident | 31.02
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.671
|  |  |  | Coincident | -0.83
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.69
|  |  |  | Coincident | 34.21
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.92
|  |  |  | Coincident | 34.42
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.06
|  |  |  | Coincident | 30.83
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.27
|  |  |  | Coincident | 31.02
| Charlestown 132_11kV | Substation Rating | MVA | Non-Coincident | 63.25
|  |  |  | Coincident | 63.25
|  | Raw Adjusted MD | MW | Non-Coincident | 44.41
|  |  |  | Coincident | 41.16
|  | Raw Adjusted MD | MVA | Non-Coincident | 45.54
|  |  |  | Coincident | 42.2
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.02
|  |  |  | Coincident | -1.745
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 52.41
|  |  |  | Coincident | 48.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 53.74
|  |  |  | Coincident | 49.81
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 45.88
|  |  |  | Coincident | 42.52
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 47.04
|  |  |  | Coincident | 43.6
| Charmhaven 132_11kV | Substation Rating | MVA | Non-Coincident | 67.14
|  |  |  | Coincident | 67.14
|  | Raw Adjusted MD | MW | Non-Coincident | 43.05
|  |  |  | Coincident | 42.98
|  | Raw Adjusted MD | MVA | Non-Coincident | 47.04
|  |  |  | Coincident | 46.96
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.324
|  |  |  | Coincident | -0.615
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 46.92
|  |  |  | Coincident | 46.84
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.28
|  |  |  | Coincident | 51.19
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 42.37
|  |  |  | Coincident | 42.3
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.31
|  |  |  | Coincident | 46.23
| Chatswood 33_11kV | Substation Rating | MVA | Non-Coincident | 128
|  |  |  | Coincident | 128
|  | Raw Adjusted MD | MW | Non-Coincident | 90.07
|  |  |  | Coincident | 85.26
|  | Raw Adjusted MD | MVA | Non-Coincident | 97.09
|  |  |  | Coincident | 91.91
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.054
|  |  |  | Coincident | -0.046
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 95.45
|  |  |  | Coincident | 90.36
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 102.9
|  |  |  | Coincident | 97.41
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 91.15
|  |  |  | Coincident | 86.28
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 98.26
|  |  |  | Coincident | 93.01
| City Central 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| City East 132_11kV | Substation Rating | MVA | Non-Coincident | 70.66
|  |  |  | Coincident | 70.66
|  | Raw Adjusted MD | MW | Non-Coincident | 33.75
|  |  |  | Coincident | 30.25
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.89
|  |  |  | Coincident | 31.27
|  | Date MD occurred |  | Non-Coincident | 29-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 10:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.069
|  |  |  | Coincident | -0.03
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.86
|  |  |  | Coincident | 31.24
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.03
|  |  |  | Coincident | 32.29
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.42
|  |  |  | Coincident | 29.95
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.54
|  |  |  | Coincident | 30.96
| City East 33_11kV | Substation Rating | MVA | Non-Coincident | 167.9
|  |  |  | Coincident | 167.9
|  | Raw Adjusted MD | MW | Non-Coincident | 94.51
|  |  |  | Coincident | 89.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 99.63
|  |  |  | Coincident | 94.79
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.146
|  |  |  | Coincident | -0.059
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 100.8
|  |  |  | Coincident | 95.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 106.3
|  |  |  | Coincident | 101.1
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 96.63
|  |  |  | Coincident | 91.94
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 101.9
|  |  |  | Coincident | 96.91
| City North 132_11kV | Substation Rating | MVA | Non-Coincident | 130.3
|  |  |  | Coincident | 130.3
|  | Raw Adjusted MD | MW | Non-Coincident | 116.1
|  |  |  | Coincident | 111.7
|  | Raw Adjusted MD | MVA | Non-Coincident | 122.2
|  |  |  | Coincident | 117.6
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 14:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.118
|  |  |  | Coincident | -0.048
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 122.1
|  |  |  | Coincident | 117.5
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 128.6
|  |  |  | Coincident | 123.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 117
|  |  |  | Coincident | 112.5
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 123.1
|  |  |  | Coincident | 118.5
| City South 132_11kV | Substation Rating | MVA | Non-Coincident | 92.98
|  |  |  | Coincident | 87.64
|  | Raw Adjusted MD | MW | Non-Coincident | 73.66
|  |  |  | Coincident | 56.46
|  | Raw Adjusted MD | MVA | Non-Coincident | 73.83
|  |  |  | Coincident | 57.08
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.766
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 76.47
|  |  |  | Coincident | 57.12
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 76.64
|  |  |  | Coincident | 57.75
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 73.17
|  |  |  | Coincident | 54.05
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 73.34
|  |  |  | Coincident | 54.65
| Clovelly 132_11kV | Substation Rating | MVA | Non-Coincident | 54.41
|  |  |  | Coincident | 54.41
|  | Raw Adjusted MD | MW | Non-Coincident | 43.63
|  |  |  | Coincident | 43.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.64
|  |  |  | Coincident | 44.64
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.209
|  |  |  | Coincident | -0.503
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.51
|  |  |  | Coincident | 50.51
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.68
|  |  |  | Coincident | 51.68
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.02
|  |  |  | Coincident | 44.02
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.04
|  |  |  | Coincident | 45.04
| Concord 33_11kV | Substation Rating | MVA | Non-Coincident | 64.17
|  |  |  | Coincident | 53.46
|  | Raw Adjusted MD | MW | Non-Coincident | 51.1
|  |  |  | Coincident | 47.59
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.8
|  |  |  | Coincident | 48.47
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.993
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 54.61
|  |  |  | Coincident | 50.38
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 55.36
|  |  |  | Coincident | 51.31
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 52.27
|  |  |  | Coincident | 43.97
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 52.99
|  |  |  | Coincident | 44.79
| Cronulla 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 21.93
|  |  |  | Coincident | 18.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.54
|  |  |  | Coincident | 18.71
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.599
|  |  |  | Coincident | -0.741
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.55
|  |  |  | Coincident | 23.7
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.34
|  |  |  | Coincident | 24.35
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.33
|  |  |  | Coincident | 20.2
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25
|  |  |  | Coincident | 20.76
| Croudace Bay 33_11kV | Substation Rating | MVA | Non-Coincident | 61.64
|  |  |  | Coincident | 61.64
|  | Raw Adjusted MD | MW | Non-Coincident | 37.64
|  |  |  | Coincident | 37.57
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.04
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.08
|  |  |  | Coincident | -0.266
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.28
|  |  |  | Coincident | 39.21
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.78
|  |  |  | Coincident | 39.71
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 36.23
|  |  |  | Coincident | 36.16
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.69
|  |  |  | Coincident | 36.62
| Crows Nest 132_11kV | Substation Rating | MVA | Non-Coincident | 59.84
|  |  |  | Coincident | 59.84
|  | Raw Adjusted MD | MW | Non-Coincident | 34.8
|  |  |  | Coincident | 34.8
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.8
|  |  |  | Coincident | 34.8
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.209
|  |  |  | Coincident | -0.503
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.2
|  |  |  | Coincident | 39.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.2
|  |  |  | Coincident | 39.2
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.31
|  |  |  | Coincident | 34.31
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.31
|  |  |  | Coincident | 34.31
| Croydon 132_11kV | Substation Rating | MVA | Non-Coincident | 123.6
|  |  |  | Coincident | 123.6
|  | Raw Adjusted MD | MW | Non-Coincident | 65.46
|  |  |  | Coincident | 62.73
|  | Raw Adjusted MD | MVA | Non-Coincident | 67.1
|  |  |  | Coincident | 64.3
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 14:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.167
|  |  |  | Coincident | -0.072
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 69.21
|  |  |  | Coincident | 66.32
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 70.95
|  |  |  | Coincident | 67.99
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 66.38
|  |  |  | Coincident | 63.61
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 68.05
|  |  |  | Coincident | 65.21
| Dalley St 132_11kV | Substation Rating | MVA | Non-Coincident | 70.3
|  |  |  | Coincident | 70.3
|  | Raw Adjusted MD | MW | Non-Coincident | 51.22
|  |  |  | Coincident | 51.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 52.72
|  |  |  | Coincident | 52.55
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.066
|  |  |  | Coincident | -0.099
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 55.41
|  |  |  | Coincident | 55.23
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.03
|  |  |  | Coincident | 56.85
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 51.95
|  |  |  | Coincident | 51.78
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 53.46
|  |  |  | Coincident | 53.29
| Darling Harbour 132_11kV | Substation Rating | MVA | Non-Coincident | 80.59
|  |  |  | Coincident | 80.59
|  | Raw Adjusted MD | MW | Non-Coincident | 47.61
|  |  |  | Coincident | 42.68
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.97
|  |  |  | Coincident | 43.9
|  | Date MD occurred |  | Non-Coincident | 06-03-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.266
|  |  |  | Coincident | -0.1
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.08
|  |  |  | Coincident | 44.89
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.5
|  |  |  | Coincident | 46.17
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 47.11
|  |  |  | Coincident | 42.23
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 48.45
|  |  |  | Coincident | 43.43
| Darlinghurst 33_11kV | Substation Rating | MVA | Non-Coincident | 58.78
|  |  |  | Coincident | 53.45
|  | Raw Adjusted MD | MW | Non-Coincident | 39.99
|  |  |  | Coincident | 31.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.94
|  |  |  | Coincident | 34.22
|  | Date MD occurred |  | Non-Coincident | 16-07-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.767
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 43.47
|  |  |  | Coincident | 32.19
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 44.5
|  |  |  | Coincident | 34.62
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.52
|  |  |  | Coincident | 29.42
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.51
|  |  |  | Coincident | 31.63
| Dee Why West 33_11kV | Substation Rating | MVA | Non-Coincident | 13.36
|  |  |  | Coincident | 13.36
|  | Raw Adjusted MD | MW | Non-Coincident | 5.735
|  |  |  | Coincident | 4.406
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.927
|  |  |  | Coincident | 4.554
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.193
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.468
|  |  |  | Coincident | 4.97
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.685
|  |  |  | Coincident | 5.137
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.829
|  |  |  | Coincident | 4.478
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.025
|  |  |  | Coincident | 4.629
| Denman 66_11kV | Substation Rating | MVA | Non-Coincident | 87.79
|  |  |  | Coincident | 81.28
|  | Raw Adjusted MD | MW | Non-Coincident | 59.86
|  |  |  | Coincident | 59.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 60.51
|  |  |  | Coincident | 60.74
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.306
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 61.36
|  |  |  | Coincident | 61.16
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 62.02
|  |  |  | Coincident | 62.87
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 59.24
|  |  |  | Coincident | 56.13
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 59.89
|  |  |  | Coincident | 57.7
| Double Bay 132_11kV | Substation Rating | MVA | Non-Coincident | 61.77
|  |  |  | Coincident | 56.15
|  | Raw Adjusted MD | MW | Non-Coincident | 55.55
|  |  |  | Coincident | 54.62
|  | Raw Adjusted MD | MVA | Non-Coincident | 56.38
|  |  |  | Coincident | 56.17
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.644
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 60.67
|  |  |  | Coincident | 61.27
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 61.57
|  |  |  | Coincident | 63
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 57.84
|  |  |  | Coincident | 52.64
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 58.7
|  |  |  | Coincident | 54.13
| Drummoyne 132_11kV | Substation Rating | MVA | Non-Coincident | 61.9
|  |  |  | Coincident | 61.9
|  | Raw Adjusted MD | MW | Non-Coincident | 42.6
|  |  |  | Coincident | 42.16
|  | Raw Adjusted MD | MVA | Non-Coincident | 43.67
|  |  |  | Coincident | 42.75
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.696
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.9
|  |  |  | Coincident | 47.89
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 47.05
|  |  |  | Coincident | 48.57
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.83
|  |  |  | Coincident | 41.07
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.94
|  |  |  | Coincident | 41.64
| Dulwich Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 24.35
|  |  |  | Coincident | 19.56
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.79
|  |  |  | Coincident | 19.91
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.012
|  |  |  | Coincident | -1.021
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.34
|  |  |  | Coincident | 22.77
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.85
|  |  |  | Coincident | 23.18
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.54
|  |  |  | Coincident | 20.52
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26
|  |  |  | Coincident | 20.88
| Edgeworth 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 11.99
|  |  |  | Coincident | 9.701
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.17
|  |  |  | Coincident | 9.853
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.006
|  |  |  | Coincident | -0.565
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.04
|  |  |  | Coincident | 10.56
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.25
|  |  |  | Coincident | 10.72
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.36
|  |  |  | Coincident | 9.196
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.54
|  |  |  | Coincident | 9.341
| Empire Bay 66_11kV | Substation Rating | MVA | Non-Coincident | 44.76
|  |  |  | Coincident | 44.76
|  | Raw Adjusted MD | MW | Non-Coincident | 21.78
|  |  |  | Coincident | 21.52
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.09
|  |  |  | Coincident | 22.81
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.188
|  |  |  | Coincident | -0.356
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.12
|  |  |  | Coincident | 25.8
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.69
|  |  |  | Coincident | 27.35
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.58
|  |  |  | Coincident | 21.32
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.88
|  |  |  | Coincident | 22.6
| Enfield 33_11kV | Substation Rating | MVA | Non-Coincident | 60.1
|  |  |  | Coincident | 60.1
|  | Raw Adjusted MD | MW | Non-Coincident | 28.21
|  |  |  | Coincident | 24.98
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.21
|  |  |  | Coincident | 24.98
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.455
|  |  |  | Coincident | -0.862
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33
|  |  |  | Coincident | 29.22
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33
|  |  |  | Coincident | 29.22
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.61
|  |  |  | Coincident | 25.33
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.61
|  |  |  | Coincident | 25.33
| Engadine 132_11kV | Substation Rating | MVA | Non-Coincident | 74.91
|  |  |  | Coincident | 74.91
|  | Raw Adjusted MD | MW | Non-Coincident | 61.96
|  |  |  | Coincident | 61.76
|  | Raw Adjusted MD | MVA | Non-Coincident | 62.54
|  |  |  | Coincident | 62.34
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.149
|  |  |  | Coincident | -0.729
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 71.74
|  |  |  | Coincident | 71.51
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 72.42
|  |  |  | Coincident | 72.18
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 63.35
|  |  |  | Coincident | 63.14
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 63.94
|  |  |  | Coincident | 63.74
| Epping 66_11kV | Substation Rating | MVA | Non-Coincident | 49.26
|  |  |  | Coincident | 49.26
|  | Raw Adjusted MD | MW | Non-Coincident | 32.19
|  |  |  | Coincident | 31.85
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.9
|  |  |  | Coincident | 32.56
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.132
|  |  |  | Coincident | -0.642
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.23
|  |  |  | Coincident | 36.84
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.06
|  |  |  | Coincident | 37.66
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.55
|  |  |  | Coincident | 33.2
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.29
|  |  |  | Coincident | 33.94
| Erina 66_11kV | Substation Rating | MVA | Non-Coincident | 98.69
|  |  |  | Coincident | 98.69
|  | Raw Adjusted MD | MW | Non-Coincident | 78.03
|  |  |  | Coincident | 75.61
|  | Raw Adjusted MD | MVA | Non-Coincident | 82.27
|  |  |  | Coincident | 79.72
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.386
|  |  |  | Coincident | -0.578
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 83.71
|  |  |  | Coincident | 81.11
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 88.26
|  |  |  | Coincident | 85.52
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 78.75
|  |  |  | Coincident | 76.3
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 83.02
|  |  |  | Coincident | 80.45
| Flemington 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 13.98
|  |  |  | Coincident | 12.37
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.6
|  |  |  | Coincident | 12.92
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.077
|  |  |  | Coincident | -0.378
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.5
|  |  |  | Coincident | 13.72
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.19
|  |  |  | Coincident | 14.33
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.97
|  |  |  | Coincident | 12.36
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.59
|  |  |  | Coincident | 12.91
| Galston 132_11kV | Substation Rating | MVA | Non-Coincident | 24.08
|  |  |  | Coincident | 24.08
|  | Raw Adjusted MD | MW | Non-Coincident | 14.29
|  |  |  | Coincident | 13.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.88
|  |  |  | Coincident | 14.59
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.004
|  |  |  | Coincident | -0.557
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.25
|  |  |  | Coincident | 14.93
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.05
|  |  |  | Coincident | 16.59
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.33
|  |  |  | Coincident | 13.17
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.93
|  |  |  | Coincident | 14.63
| Gateshead 33_11kV | Substation Rating | MVA | Non-Coincident | 96.9
|  |  |  | Coincident | 96.9
|  | Raw Adjusted MD | MW | Non-Coincident | 52.83
|  |  |  | Coincident | 49.16
|  | Raw Adjusted MD | MVA | Non-Coincident | 55.36
|  |  |  | Coincident | 51.51
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.25
|  |  |  | Coincident | -0.25
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 56.06
|  |  |  | Coincident | 52.16
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 58.74
|  |  |  | Coincident | 54.66
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 53
|  |  |  | Coincident | 49.32
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 55.53
|  |  |  | Coincident | 51.68
| Gore Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 22.18
|  |  |  | Coincident | 22.18
|  | Raw Adjusted MD | MW | Non-Coincident | 8.145
|  |  |  | Coincident | 3.035
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.05
|  |  |  | Coincident | 3.372
|  | Date MD occurred |  | Non-Coincident | 14-05-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 7:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.835
|  |  |  | Coincident | 3.317
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.706
|  |  |  | Coincident | 3.686
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.988
|  |  |  | Coincident | 3.043
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.764
|  |  |  | Coincident | 3.381
| Graving Dock No 1 33_11kV | Substation Rating | MVA | Non-Coincident | 20.75
|  |  |  | Coincident | 18.69
|  | Raw Adjusted MD | MW | Non-Coincident | 9.928
|  |  |  | Coincident | 4.03
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.03
|  |  |  | Coincident | 4.477
|  | Date MD occurred |  | Non-Coincident | 20-07-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.08
|  |  |  | Coincident | 5.82
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.31
|  |  |  | Coincident | 6.467
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.816
|  |  |  | Coincident | 4.987
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.91
|  |  |  | Coincident | 5.541
| Graving Dock No 2 33_11kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 53.82
|  |  |  | Coincident | 50.59
|  | Raw Adjusted MD | MVA | Non-Coincident | 54.93
|  |  |  | Coincident | 51.63
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.386
|  |  |  | Coincident | -0.28
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 57.54
|  |  |  | Coincident | 54.09
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 58.72
|  |  |  | Coincident | 55.2
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 53.77
|  |  |  | Coincident | 50.54
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 54.87
|  |  |  | Coincident | 51.58
| Green Square 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Greenacre 132_11kV | Substation Rating | MVA | Non-Coincident | 86.16
|  |  |  | Coincident | 86.16
|  | Raw Adjusted MD | MW | Non-Coincident | 61.67
|  |  |  | Coincident | 59.94
|  | Raw Adjusted MD | MVA | Non-Coincident | 63.2
|  |  |  | Coincident | 61.43
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.466
|  |  |  | Coincident | -0.698
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 70.16
|  |  |  | Coincident | 68.19
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 71.9
|  |  |  | Coincident | 69.88
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 63.26
|  |  |  | Coincident | 61.49
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 64.83
|  |  |  | Coincident | 63.01
| Greenacre Park 132_11kV | Substation Rating | MVA | Non-Coincident | 45.1
|  |  |  | Coincident | 45.1
|  | Raw Adjusted MD | MW | Non-Coincident | 31.69
|  |  |  | Coincident | 30.58
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.58
|  |  |  | Coincident | 31.44
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.405
|  |  |  | Coincident | -0.5
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.17
|  |  |  | Coincident | 33.93
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.15
|  |  |  | Coincident | 34.88
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.69
|  |  |  | Coincident | 30.58
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.58
|  |  |  | Coincident | 31.44
| Gwawley Bay 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 21.56
|  |  |  | Coincident | 13.81
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.46
|  |  |  | Coincident | 15.01
|  | Date MD occurred |  | Non-Coincident | 25-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.568
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.68
|  |  |  | Coincident | 13.78
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.67
|  |  |  | Coincident | 14.97
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.38
|  |  |  | Coincident | 12.62
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.31
|  |  |  | Coincident | 13.72
| Harbord 33_11kV | Substation Rating | MVA | Non-Coincident | 53.18
|  |  |  | Coincident | 53.18
|  | Raw Adjusted MD | MW | Non-Coincident | 45.18
|  |  |  | Coincident | 41.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 45.75
|  |  |  | Coincident | 41.92
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.113
|  |  |  | Coincident | -0.438
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.51
|  |  |  | Coincident | 45.36
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.13
|  |  |  | Coincident | 45.93
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 46.36
|  |  |  | Coincident | 42.48
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.94
|  |  |  | Coincident | 43.01
| Homebush Bay 132_11kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 71.79
|  |  |  | Coincident | 70.39
|  | Raw Adjusted MD | MVA | Non-Coincident | 72.93
|  |  |  | Coincident | 71.5
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.245
|  |  |  | Coincident | -1.197
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 84.31
|  |  |  | Coincident | 82.66
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 85.65
|  |  |  | Coincident | 83.97
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 74.97
|  |  |  | Coincident | 73.51
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 76.16
|  |  |  | Coincident | 74.67
| Hornsby 132_11kV | Substation Rating | MVA | Non-Coincident | 69.83
|  |  |  | Coincident | 69.83
|  | Raw Adjusted MD | MW | Non-Coincident | 54.11
|  |  |  | Coincident | 53.55
|  | Raw Adjusted MD | MVA | Non-Coincident | 58.04
|  |  |  | Coincident | 57.45
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.257
|  |  |  | Coincident | -0.851
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 62.23
|  |  |  | Coincident | 61.6
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 66.76
|  |  |  | Coincident | 66.07
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 53.92
|  |  |  | Coincident | 53.37
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 57.84
|  |  |  | Coincident | 57.25
| Hunters Hill 66_11kV | Substation Rating | MVA | Non-Coincident | 59.56
|  |  |  | Coincident | 59.56
|  | Raw Adjusted MD | MW | Non-Coincident | 23.3
|  |  |  | Coincident | 23.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.1
|  |  |  | Coincident | 24.1
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.251
|  |  |  | Coincident | -0.31
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.08
|  |  |  | Coincident | 24.08
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.9
|  |  |  | Coincident | 24.9
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.78
|  |  |  | Coincident | 21.78
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.53
|  |  |  | Coincident | 22.53
| Hurstville North 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 31.44
|  |  |  | Coincident | 31.44
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.51
|  |  |  | Coincident | 31.51
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.331
|  |  |  | Coincident | -0.798
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.59
|  |  |  | Coincident | 34.59
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.67
|  |  |  | Coincident | 34.67
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.79
|  |  |  | Coincident | 29.79
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.86
|  |  |  | Coincident | 29.86
| Jannali 33_11kV | Substation Rating | MVA | Non-Coincident | 57.48
|  |  |  | Coincident | 57.48
|  | Raw Adjusted MD | MW | Non-Coincident | 41.44
|  |  |  | Coincident | 37.27
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.21
|  |  |  | Coincident | 37.96
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.456
|  |  |  | Coincident | -1.1
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.98
|  |  |  | Coincident | 41.35
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.84
|  |  |  | Coincident | 42.12
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.44
|  |  |  | Coincident | 37.27
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.21
|  |  |  | Coincident | 37.96
| Jesmond 132_11kV | Substation Rating | MVA | Non-Coincident | 16.92
|  |  |  | Coincident | 16.92
|  | Raw Adjusted MD | MW | Non-Coincident | 14.42
|  |  |  | Coincident | 12.72
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.69
|  |  |  | Coincident | 12.96
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.004
|  |  |  | Coincident | -0.598
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.57
|  |  |  | Coincident | 15.49
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.9
|  |  |  | Coincident | 15.78
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.2
|  |  |  | Coincident | 13.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.48
|  |  |  | Coincident | 13.65
| Jewells 33_11kV | Substation Rating | MVA | Non-Coincident | 21.09
|  |  |  | Coincident | 21.09
|  | Raw Adjusted MD | MW | Non-Coincident | 15.24
|  |  |  | Coincident | 14.26
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.43
|  |  |  | Coincident | 14.44
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.09
|  |  |  | Coincident | -0.438
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.82
|  |  |  | Coincident | 15.74
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.03
|  |  |  | Coincident | 15.94
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.53
|  |  |  | Coincident | 13.59
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.71
|  |  |  | Coincident | 13.76
| Killarney 33_11kV | Substation Rating | MVA | Non-Coincident | 65.01
|  |  |  | Coincident | 62.24
|  | Raw Adjusted MD | MW | Non-Coincident | 57.35
|  |  |  | Coincident | 50.41
|  | Raw Adjusted MD | MVA | Non-Coincident | 57.46
|  |  |  | Coincident | 50.79
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.566
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 58.72
|  |  |  | Coincident | 50.68
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 58.84
|  |  |  | Coincident | 51.07
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 56.64
|  |  |  | Coincident | 47.11
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 56.75
|  |  |  | Coincident | 47.47
| Kingsford 132_11kV | Substation Rating | MVA | Non-Coincident | 44.56
|  |  |  | Coincident | 44.56
|  | Raw Adjusted MD | MW | Non-Coincident | 35.63
|  |  |  | Coincident | 34.44
|  | Raw Adjusted MD | MVA | Non-Coincident | 39.61
|  |  |  | Coincident | 38.3
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.39
|  |  |  | Coincident | -0.739
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.55
|  |  |  | Coincident | 36.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.75
|  |  |  | Coincident | 40.36
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.69
|  |  |  | Coincident | 31.61
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.35
|  |  |  | Coincident | 35.14
| Kirrawee 132_11kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 72.62
|  |  |  | Coincident | 72.39
|  | Raw Adjusted MD | MVA | Non-Coincident | 84.94
|  |  |  | Coincident | 84.67
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.797
|  |  |  | Coincident | -1.192
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 75.27
|  |  |  | Coincident | 75.04
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 88.04
|  |  |  | Coincident | 87.76
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 67.31
|  |  |  | Coincident | 67.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 78.72
|  |  |  | Coincident | 78.47
| Kogarah 132_11kV | Substation Rating | MVA | Non-Coincident | 30.48
|  |  |  | Coincident | 30.48
|  | Raw Adjusted MD | MW | Non-Coincident | 22.58
|  |  |  | Coincident | 20.88
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.17
|  |  |  | Coincident | 21.43
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.328
|  |  |  | Coincident | -0.406
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.42
|  |  |  | Coincident | 25.36
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.14
|  |  |  | Coincident | 26.02
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.6
|  |  |  | Coincident | 22.75
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.24
|  |  |  | Coincident | 23.34
| Kotara 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 8.437
|  |  |  | Coincident | 4.062
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.761
|  |  |  | Coincident | 4.142
|  | Date MD occurred |  | Non-Coincident | 27-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.191
|  |  |  | Coincident | -0.115
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.064
|  |  |  | Coincident | 4.219
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.374
|  |  |  | Coincident | 4.303
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.453
|  |  |  | Coincident | 4.008
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.739
|  |  |  | Coincident | 4.087
| Kurnell South 132_11kV | Substation Rating | MVA | Non-Coincident | 57.27
|  |  |  | Coincident | 57.27
|  | Raw Adjusted MD | MW | Non-Coincident | 31.92
|  |  |  | Coincident | 26.41
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.69
|  |  |  | Coincident | 27.04
|  | Date MD occurred |  | Non-Coincident | 16-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.25
|  |  |  | Coincident | -1.219
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.79
|  |  |  | Coincident | 31.26
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.7
|  |  |  | Coincident | 32.01
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.05
|  |  |  | Coincident | 28.17
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.87
|  |  |  | Coincident | 28.85
| Kurri 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 21.28
|  |  |  | Coincident | 18.33
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.61
|  |  |  | Coincident | 18.61
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.007
|  |  |  | Coincident | -1.087
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.39
|  |  |  | Coincident | 21.01
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.76
|  |  |  | Coincident | 21.33
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.2
|  |  |  | Coincident | 18.27
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.53
|  |  |  | Coincident | 18.55
| Lake Munmorah 132_11kV | Substation Rating | MVA | Non-Coincident | 59.5
|  |  |  | Coincident | 59.5
|  | Raw Adjusted MD | MW | Non-Coincident | 27.64
|  |  |  | Coincident | 27.48
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.04
|  |  |  | Coincident | 27.86
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.409
|  |  |  | Coincident | -0.506
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.91
|  |  |  | Coincident | 28.74
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.32
|  |  |  | Coincident | 29.14
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.1
|  |  |  | Coincident | 25.94
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.47
|  |  |  | Coincident | 26.31
| Leichhardt 132_11kV | Substation Rating | MVA | Non-Coincident | 69.07
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident | 9.071
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.08
Coincident
|  | Date MD occurred |  | Non-Coincident | 19-06-18
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.621
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.69
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.307
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.34
Coincident
| Leichhardt 33_11kV | Substation Rating | MVA | Non-Coincident | 38.81
|  |  |  | Coincident | 38.81
|  | Raw Adjusted MD | MW | Non-Coincident | 23.85
|  |  |  | Coincident | 22.97
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.26
|  |  |  | Coincident | 24.33
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.329
|  |  |  | Coincident | -0.407
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.09
|  |  |  | Coincident | 25.12
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.64
|  |  |  | Coincident | 26.61
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.93
|  |  |  | Coincident | 23.04
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.35
|  |  |  | Coincident | 24.41
| Leightonfield 33_11kV | Substation Rating | MVA | Non-Coincident | 6.74
|  |  |  | Coincident | 6.74
|  | Raw Adjusted MD | MW | Non-Coincident | 2.637
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.93
Coincident
|  | Date MD occurred |  | Non-Coincident | 02-01-19
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.926
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.251
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.637
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.93
Coincident
| Lemington 66_11kV | Substation Rating | MVA | Non-Coincident | 33.41
|  |  |  | Coincident | 33.41
|  | Raw Adjusted MD | MW | Non-Coincident | 17.61
|  |  |  | Coincident | 17.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.51
|  |  |  | Coincident | 19.03
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.262
|  |  |  | Coincident | -0.262
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.1
|  |  |  | Coincident | 20.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.37
|  |  |  | Coincident | 22.8
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.87
|  |  |  | Coincident | 18.41
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.91
|  |  |  | Coincident | 20.4
| Lidcombe 33_11kV | Substation Rating | MVA | Non-Coincident | 36.81
|  |  |  | Coincident | 36.81
|  | Raw Adjusted MD | MW | Non-Coincident | 31.6
|  |  |  | Coincident | 30.62
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.45
|  |  |  | Coincident | 31.44
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.116
|  |  |  | Coincident | -0.568
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.05
|  |  |  | Coincident | 34.93
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.01
|  |  |  | Coincident | 35.86
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.36
|  |  |  | Coincident | 30.39
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.2
|  |  |  | Coincident | 31.2
| Lindfield 33_11kV | Substation Rating | MVA | Non-Coincident | 23.82
|  |  |  | Coincident | 23.82
|  | Raw Adjusted MD | MW | Non-Coincident | 23.52
|  |  |  | Coincident | 21.94
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.2
|  |  |  | Coincident | 22.58
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.005
|  |  |  | Coincident | -0.751
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.71
|  |  |  | Coincident | 24.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.48
|  |  |  | Coincident | 25.65
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.07
|  |  |  | Coincident | 22.46
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.77
|  |  |  | Coincident | 23.11
| Lisarow 33_11kV | Substation Rating | MVA | Non-Coincident | 76.21
|  |  |  | Coincident | 71.69
|  | Raw Adjusted MD | MW | Non-Coincident | 37.24
|  |  |  | Coincident | 35.37
|  | Raw Adjusted MD | MVA | Non-Coincident | 41.38
|  |  |  | Coincident | 39.3
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.001
|  |  |  | Coincident | -1.256
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.12
|  |  |  | Coincident | 38.9
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 43.47
|  |  |  | Coincident | 43.22
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 37.11
|  |  |  | Coincident | 34.58
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.24
|  |  |  | Coincident | 38.42
| Long Jetty 66_11kV | Substation Rating | MVA | Non-Coincident | 19.22
|  |  |  | Coincident | 19.22
|  | Raw Adjusted MD | MW | Non-Coincident | 8.09
|  |  |  | Coincident | 7.172
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.898
|  |  |  | Coincident | 7.888
|  | Date MD occurred |  | Non-Coincident | 16-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.09
|  |  |  | Coincident | 7.172
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.898
|  |  |  | Coincident | 7.888
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.09
|  |  |  | Coincident | 7.172
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.898
|  |  |  | Coincident | 7.888
| Lucas Heights 33_11kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 81.78
|  |  |  | Coincident | 77
|  | Raw Adjusted MD | MVA | Non-Coincident | 83.51
|  |  |  | Coincident | 78.63
|  | Date MD occurred |  | Non-Coincident | 30-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.574
|  |  |  | Coincident | -0.262
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 88.22
|  |  |  | Coincident | 83.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 90.09
|  |  |  | Coincident | 84.82
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 83.71
|  |  |  | Coincident | 78.81
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 85.48
|  |  |  | Coincident | 80.48
| Macquarie Park 132_11kV | Substation Rating | MVA | Non-Coincident | 36.66
|  |  |  | Coincident | 36.66
|  | Raw Adjusted MD | MW | Non-Coincident | 26.05
|  |  |  | Coincident | 21.66
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.09
|  |  |  | Coincident | 22.52
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.078
|  |  |  | Coincident | -0.721
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.39
|  |  |  | Coincident | 25.26
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.59
|  |  |  | Coincident | 26.26
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 27.39
|  |  |  | Coincident | 22.77
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.47
|  |  |  | Coincident | 23.67
| Maitland 33_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 17.42
|  |  |  | Coincident | 15.35
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.26
|  |  |  | Coincident | 16.8
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.133
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.57
|  |  |  | Coincident | 16.35
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.47
|  |  |  | Coincident | 17.9
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.88
|  |  |  | Coincident | 15.15
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.74
|  |  |  | Coincident | 16.58
| Manly 33_11kV | Substation Rating | MVA | Non-Coincident | 102.8
|  |  |  | Coincident | 102.8
|  | Raw Adjusted MD | MW | Non-Coincident | 42.99
|  |  |  | Coincident | 41.94
|  | Raw Adjusted MD | MVA | Non-Coincident | 43.74
|  |  |  | Coincident | 42.93
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.503
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.04
|  |  |  | Coincident | 41.66
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 44.81
|  |  |  | Coincident | 42.64
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 42.69
|  |  |  | Coincident | 39.49
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 43.44
|  |  |  | Coincident | 40.41
| Maroubra 132_11kV | Substation Rating | MVA | Non-Coincident | 72.67
|  |  |  | Coincident | 71.89
|  | Raw Adjusted MD | MW | Non-Coincident | 53.04
|  |  |  | Coincident | 49.07
|  | Raw Adjusted MD | MVA | Non-Coincident | 53.77
|  |  |  | Coincident | 51.04
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.954
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 56.71
|  |  |  | Coincident | 49.53
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.48
|  |  |  | Coincident | 51.51
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 54.34
|  |  |  | Coincident | 45.72
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 55.09
|  |  |  | Coincident | 47.55
| Marrickville 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 22.79
|  |  |  | Coincident | 20.38
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.34
|  |  |  | Coincident | 20.87
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.007
|  |  |  | Coincident | -1.004
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.71
|  |  |  | Coincident | 24.77
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.38
|  |  |  | Coincident | 25.37
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.97
|  |  |  | Coincident | 22.33
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.57
|  |  |  | Coincident | 22.86
| Maryland 132_11kV | Substation Rating | MVA | Non-Coincident | 78.44
|  |  |  | Coincident | 78.44
|  | Raw Adjusted MD | MW | Non-Coincident | 50.05
|  |  |  | Coincident | 48.47
|  | Raw Adjusted MD | MVA | Non-Coincident | 52.26
|  |  |  | Coincident | 50.6
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.28
|  |  |  | Coincident | -0.235
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 52.13
|  |  |  | Coincident | 50.48
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 54.43
|  |  |  | Coincident | 52.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 48.87
|  |  |  | Coincident | 47.32
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 51.02
|  |  |  | Coincident | 49.4
| Mascot 33_11kV | Substation Rating | MVA | Non-Coincident | 72.67
|  |  |  | Coincident | 68.09
|  | Raw Adjusted MD | MW | Non-Coincident | 29.51
|  |  |  | Coincident | 25.32
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.44
|  |  |  | Coincident | 27.44
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.553
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.06
|  |  |  | Coincident | 24.68
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.16
|  |  |  | Coincident | 26.74
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.68
|  |  |  | Coincident | 22.89
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.69
|  |  |  | Coincident | 24.81
| Matraville 33_11kV | Substation Rating | MVA | Non-Coincident | 62.59
|  |  |  | Coincident | 62.59
|  | Raw Adjusted MD | MW | Non-Coincident | 23.23
|  |  |  | Coincident | 18.62
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.74
|  |  |  | Coincident | 19.83
|  | Date MD occurred |  | Non-Coincident | 30-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.592
|  |  |  | Coincident | -0.626
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.63
|  |  |  | Coincident | 20.54
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.29
|  |  |  | Coincident | 21.87
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.1
|  |  |  | Coincident | 18.51
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.6
|  |  |  | Coincident | 19.71
| Mayfield West 132_11kV | Substation Rating | MVA | Non-Coincident | 103.8
|  |  |  | Coincident | 103.8
|  | Raw Adjusted MD | MW | Non-Coincident | 69.12
|  |  |  | Coincident | 64.97
|  | Raw Adjusted MD | MVA | Non-Coincident | 72.69
|  |  |  | Coincident | 68.32
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.179
|  |  |  | Coincident | -0.873
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 83.54
|  |  |  | Coincident | 78.53
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 87.85
|  |  |  | Coincident | 82.58
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 72.22
|  |  |  | Coincident | 67.88
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 75.94
|  |  |  | Coincident | 71.38
| Meadowbank 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 12.25
|  |  |  | Coincident | 10.14
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.42
|  |  |  | Coincident | 10.28
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.041
|  |  |  | Coincident | -0.693
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.73
|  |  |  | Coincident | 11.37
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.92
|  |  |  | Coincident | 11.52
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.38
|  |  |  | Coincident | 10.25
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.54
|  |  |  | Coincident | 10.39
| Medowie 33_11kV | Substation Rating | MVA | Non-Coincident | 60.72
|  |  |  | Coincident | 60.72
|  | Raw Adjusted MD | MW | Non-Coincident | 43.68
|  |  |  | Coincident | 43.68
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.13
|  |  |  | Coincident | 44.13
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.463
|  |  |  | Coincident | -1.116
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.72
|  |  |  | Coincident | 51.72
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 52.25
|  |  |  | Coincident | 52.25
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.52
|  |  |  | Coincident | 44.52
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.98
|  |  |  | Coincident | 44.98
| Menai 132_11kV | Substation Rating | MVA | Non-Coincident | 6.94
|  |  |  | Coincident | 6.94
|  | Raw Adjusted MD | MW | Non-Coincident | 3.52
|  |  |  | Coincident | 2.663
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.597
|  |  |  | Coincident | 2.722
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.169
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.97
|  |  |  | Coincident | 3.004
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.057
|  |  |  | Coincident | 3.07
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.649
|  |  |  | Coincident | 2.761
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.729
|  |  |  | Coincident | 2.821
| Merriwa 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 38.14
|  |  |  | Coincident | 32.32
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.72
|  |  |  | Coincident | 32.8
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.236
|  |  |  | Coincident | -1.15
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 42.33
|  |  |  | Coincident | 35.86
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 42.97
|  |  |  | Coincident | 36.4
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 38.15
|  |  |  | Coincident | 32.32
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 38.72
|  |  |  | Coincident | 32.81
| Metford 33_11kV | Substation Rating | MVA | Non-Coincident | 61.18
|  |  |  | Coincident | 61.18
|  | Raw Adjusted MD | MW | Non-Coincident | 49.58
|  |  |  | Coincident | 48.01
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.78
|  |  |  | Coincident | 50.15
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.137
|  |  |  | Coincident | -0.955
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 53.9
|  |  |  | Coincident | 52.19
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 56.29
|  |  |  | Coincident | 54.51
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 49.37
|  |  |  | Coincident | 47.81
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 51.56
|  |  |  | Coincident | 49.93
| Milperra 132_11kV | Substation Rating | MVA | Non-Coincident | 41.97
|  |  |  | Coincident | 41.97
|  | Raw Adjusted MD | MW | Non-Coincident | 32.46
|  |  |  | Coincident | 32.25
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.67
|  |  |  | Coincident | 33.46
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.212
|  |  |  | Coincident | -0.402
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.37
|  |  |  | Coincident | 34.15
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.66
|  |  |  | Coincident | 35.43
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.21
|  |  |  | Coincident | 30.01
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.34
|  |  |  | Coincident | 31.14
| Miranda 33_11kV | Substation Rating | MVA | Non-Coincident | 23.82
|  |  |  | Coincident | 23.82
|  | Raw Adjusted MD | MW | Non-Coincident | 8.911
|  |  |  | Coincident | 7.507
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.045
|  |  |  | Coincident | 7.619
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.001
|  |  |  | Coincident | -0.196
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.767
|  |  |  | Coincident | 8.227
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.913
|  |  |  | Coincident | 8.35
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.802
|  |  |  | Coincident | 7.414
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.933
|  |  |  | Coincident | 7.525
| Mitchell Line 66_11kV | Substation Rating | MVA | Non-Coincident | 6.69
|  |  |  | Coincident | 6.69
|  | Raw Adjusted MD | MW | Non-Coincident | 1.526
|  |  |  | Coincident | 1.149
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.696
|  |  |  | Coincident | 1.277
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.079
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.803
|  |  |  | Coincident | 1.357
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.003
|  |  |  | Coincident | 1.508
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.625
|  |  |  | Coincident | 1.223
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.805
|  |  |  | Coincident | 1.359
| Mitchells Flat 66_11kV | Substation Rating | MVA | Non-Coincident | 57.41
|  |  |  | Coincident | 57.41
|  | Raw Adjusted MD | MW | Non-Coincident | 31.27
|  |  |  | Coincident | 30.36
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.75
|  |  |  | Coincident | 33.74
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.567
|  |  |  | Coincident | -0.702
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.07
|  |  |  | Coincident | 31.14
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.64
|  |  |  | Coincident | 34.6
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.52
|  |  |  | Coincident | 27.69
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.69
|  |  |  | Coincident | 30.77
| Mona Vale 33_11kV | Substation Rating | MVA | Non-Coincident | 2.86
|  |  |  | Coincident | 2.86
|  | Raw Adjusted MD | MW | Non-Coincident | 1.233
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.37
Coincident
|  | Date MD occurred |  | Non-Coincident | 26-11-18
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.368
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.52
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.233
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.37
Coincident
| Moonan 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 24.32
|  |  |  | Coincident | 21.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.85
|  |  |  | Coincident | 21.92
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.008
|  |  |  | Coincident | -1.182
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.07
|  |  |  | Coincident | 23.87
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.66
|  |  |  | Coincident | 24.39
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.4
|  |  |  | Coincident | 20.64
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.91
|  |  |  | Coincident | 21.08
| Morisset 132_11kV | Substation Rating | MVA | Non-Coincident | 64.25
|  |  |  | Coincident | 64.25
|  | Raw Adjusted MD | MW | Non-Coincident | 45.31
|  |  |  | Coincident | 45.31
|  | Raw Adjusted MD | MVA | Non-Coincident | 46.37
|  |  |  | Coincident | 46.37
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.395
|  |  |  | Coincident | -0.952
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.96
|  |  |  | Coincident | 50.96
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 52.16
|  |  |  | Coincident | 52.16
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.26
|  |  |  | Coincident | 43.26
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.28
|  |  |  | Coincident | 44.28
| Mortdale 33_11kV | Substation Rating | MVA | Non-Coincident | 89.05
|  |  |  | Coincident | 82.46
|  | Raw Adjusted MD | MW | Non-Coincident | 76.83
|  |  |  | Coincident | 64.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 77.07
|  |  |  | Coincident | 64.95
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.764
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 80.7
|  |  |  | Coincident | 66.22
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 80.95
|  |  |  | Coincident | 67.11
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 77.02
|  |  |  | Coincident | 58.42
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 77.26
|  |  |  | Coincident | 59.2
| Mosman 132_11kV | Substation Rating | MVA | Non-Coincident | 26.01
|  |  |  | Coincident | 26.01
|  | Raw Adjusted MD | MW | Non-Coincident | 19.12
|  |  |  | Coincident | 16.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.4
|  |  |  | Coincident | 16.33
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.005
|  |  |  | Coincident | -0.692
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.81
|  |  |  | Coincident | 20.04
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.16
|  |  |  | Coincident | 20.34
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.46
|  |  |  | Coincident | 18.06
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.77
|  |  |  | Coincident | 18.33
| Mt Hutton 33_11kV | Substation Rating | MVA | Non-Coincident | 20.25
|  |  |  | Coincident | 20.25
|  | Raw Adjusted MD | MW | Non-Coincident | 6.276
|  |  |  | Coincident | 4.052
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.689
|  |  |  | Coincident | 4.319
|  | Date MD occurred |  | Non-Coincident | 18-02-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.588
|  |  |  | Coincident | -0.288
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.523
|  |  |  | Coincident | 4.212
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.952
|  |  |  | Coincident | 4.489
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.878
|  |  |  | Coincident | 3.795
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.265
|  |  |  | Coincident | 4.045
| Mt Thorley 66_11kV | Substation Rating | MVA | Non-Coincident | 23.82
|  |  |  | Coincident | 23.82
|  | Raw Adjusted MD | MW | Non-Coincident | 16.84
|  |  |  | Coincident | 13.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.72
|  |  |  | Coincident | 15.36
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.004
|  |  |  | Coincident | -0.528
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.83
|  |  |  | Coincident | 14.63
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.81
|  |  |  | Coincident | 16.26
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.07
|  |  |  | Coincident | 13.19
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.85
|  |  |  | Coincident | 14.65
| Muswellbrook 33_11kV | Substation Rating | MVA | Non-Coincident | 20.25
|  |  |  | Coincident | 19.62
|  | Raw Adjusted MD | MW | Non-Coincident | 11.78
|  |  |  | Coincident | 9.895
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.27
|  |  |  | Coincident | 10.57
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.342
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.5
|  |  |  | Coincident | 10.68
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.02
|  |  |  | Coincident | 11.42
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.05
|  |  |  | Coincident | 9.679
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.55
|  |  |  | Coincident | 10.34
| Narrabeen 33_11kV | Substation Rating | MVA | Non-Coincident | 45.73
|  |  |  | Coincident | 45.73
|  | Raw Adjusted MD | MW | Non-Coincident | 22.87
|  |  |  | Coincident | 17.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.12
|  |  |  | Coincident | 17.27
|  | Date MD occurred |  | Non-Coincident | 26-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.204
|  |  |  | Coincident | -0.995
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.1
|  |  |  | Coincident | 21.74
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.41
|  |  |  | Coincident | 21.98
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.81
|  |  |  | Coincident | 19.28
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.09
|  |  |  | Coincident | 19.49
| Nelson Bay 33_11kV | Substation Rating | MVA | Non-Coincident | 23.59
|  |  |  | Coincident | 23.59
|  | Raw Adjusted MD | MW | Non-Coincident | 16.16
|  |  |  | Coincident | 15.06
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.01
|  |  |  | Coincident | 15.86
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.135
|  |  |  | Coincident | -0.326
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.93
|  |  |  | Coincident | 17.65
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.92
|  |  |  | Coincident | 18.58
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.05
|  |  |  | Coincident | 15.9
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.95
|  |  |  | Coincident | 16.74
| New Lambton 33_11kV | Substation Rating | MVA | Non-Coincident | 76.21
|  |  |  | Coincident | 76.21
|  | Raw Adjusted MD | MW | Non-Coincident | 40.07
|  |  |  | Coincident | 37.82
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.79
|  |  |  | Coincident | 38.5
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.75
|  |  |  | Coincident | -0.545
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.85
|  |  |  | Coincident | 42.33
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.65
|  |  |  | Coincident | 43.09
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.42
|  |  |  | Coincident | 38.15
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.14
|  |  |  | Coincident | 38.83
| Newcastle CBD 33_11kV | Substation Rating | MVA | Non-Coincident | 23.82
|  |  |  | Coincident | 23.82
|  | Raw Adjusted MD | MW | Non-Coincident | 3.07
|  |  |  | Coincident | 1.929
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.412
|  |  |  | Coincident | 2.143
|  | Date MD occurred |  | Non-Coincident | 22-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 10:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.044
|  |  |  | Coincident | -0.019
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.069
|  |  |  | Coincident | 1.928
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.41
|  |  |  | Coincident | 2.142
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.069
|  |  |  | Coincident | 1.928
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.41
|  |  |  | Coincident | 2.142
| Newdell 66_11kV | Substation Rating | MVA | Non-Coincident | 22.38
|  |  |  | Coincident | 20.75
|  | Raw Adjusted MD | MW | Non-Coincident | 14.17
|  |  |  | Coincident | 11.59
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.46
|  |  |  | Coincident | 11.74
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.283
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.07
|  |  |  | Coincident | 12.03
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.38
|  |  |  | Coincident | 12.19
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.43
|  |  |  | Coincident | 10.81
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.73
|  |  |  | Coincident | 10.95
| Newport 33_11kV | Substation Rating | MVA | Non-Coincident | 37.5
|  |  |  | Coincident | 34.37
|  | Raw Adjusted MD | MW | Non-Coincident | 22.7
|  |  |  | Coincident | 18.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.17
|  |  |  | Coincident | 19.83
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.939
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.69
|  |  |  | Coincident | 19.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.17
|  |  |  | Coincident | 21.42
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.39
|  |  |  | Coincident | 17.73
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.84
|  |  |  | Coincident | 19.07
| Noraville 33_11kV | Substation Rating | MVA | Non-Coincident | 23.64
|  |  |  | Coincident | 23.64
|  | Raw Adjusted MD | MW | Non-Coincident | 16.18
|  |  |  | Coincident | 8.298
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.68
|  |  |  | Coincident | 9.069
|  | Date MD occurred |  | Non-Coincident | 28-11-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 10:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.154
|  |  |  | Coincident | -0.065
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.27
|  |  |  | Coincident | 9.883
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.06
|  |  |  | Coincident | 10.8
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.36
|  |  |  | Coincident | 8.907
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.98
|  |  |  | Coincident | 9.734
| North Head 33_11kV | Substation Rating | MVA | Non-Coincident | 136.8
|  |  |  | Coincident | 136.8
|  | Raw Adjusted MD | MW | Non-Coincident | 63.81
|  |  |  | Coincident | 61.54
|  | Raw Adjusted MD | MVA | Non-Coincident | 65.32
|  |  |  | Coincident | 62.99
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.12
|  |  |  | Coincident | -0.148
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 69.06
|  |  |  | Coincident | 66.6
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 70.69
|  |  |  | Coincident | 68.18
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 64.36
|  |  |  | Coincident | 62.07
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 65.88
|  |  |  | Coincident | 63.54
| North Sydney 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 15.24
|  |  |  | Coincident | 16.72
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.74
|  |  |  | Coincident | 17.27
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.003
|  |  |  | Coincident | -0.465
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.74
|  |  |  | Coincident | 18.99
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.38
|  |  |  | Coincident | 19.61
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.79
|  |  |  | Coincident | 17.11
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.37
|  |  |  | Coincident | 17.67
| Nulkaba 33_11kV | Substation Rating | MVA | Non-Coincident | 55.73
|  |  |  | Coincident | 55.73
|  | Raw Adjusted MD | MW | Non-Coincident | 3.182
|  |  |  | Coincident | 2.263
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.262
|  |  |  | Coincident | 2.319
|  | Date MD occurred |  | Non-Coincident | 14-03-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.069
|  |  |  | Coincident | -0.026
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.182
|  |  |  | Coincident | 2.263
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.262
|  |  |  | Coincident | 2.319
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.182
|  |  |  | Coincident | 2.263
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.262
|  |  |  | Coincident | 2.319
| Olympic Park 132_11kV | Substation Rating | MVA | Non-Coincident | 69.83
|  |  |  | Coincident | 66.47
|  | Raw Adjusted MD | MW | Non-Coincident | 32.03
|  |  |  | Coincident | 29.97
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.9
|  |  |  | Coincident | 31.49
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.095
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.28
|  |  |  | Coincident | 31.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.22
|  |  |  | Coincident | 33.19
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.01
|  |  |  | Coincident | 29.16
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.91
|  |  |  | Coincident | 30.64
| Paddington 33_11kV | Substation Rating | MVA | Non-Coincident | 25.45
|  |  |  | Coincident | 25.45
|  | Raw Adjusted MD | MW | Non-Coincident | 6.362
|  |  |  | Coincident | 4.441
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.068
|  |  |  | Coincident | 4.935
|  | Date MD occurred |  | Non-Coincident | 26-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.063
|  |  |  | Coincident | -0.307
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.374
|  |  |  | Coincident | 5.148
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.193
|  |  |  | Coincident | 5.72
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.628
|  |  |  | Coincident | 4.627
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.364
|  |  |  | Coincident | 5.141
| Paxton 33_11kV | Substation Rating | MVA | Non-Coincident | 17.09
|  |  |  | Coincident | 17.09
|  | Raw Adjusted MD | MW | Non-Coincident | 9.922
|  |  |  | Coincident | 8.552
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.84
|  |  |  | Coincident | 9.341
|  | Date MD occurred |  | Non-Coincident | 16-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.298
|  |  |  | Coincident | -0.564
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.98
|  |  |  | Coincident | 9.463
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.99
|  |  |  | Coincident | 10.33
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.21
|  |  |  | Coincident | 8.798
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.15
|  |  |  | Coincident | 9.609
| Peats Ridge 33_11kV | Substation Rating | MVA | Non-Coincident | 25.64
|  |  |  | Coincident | 25.64
|  | Raw Adjusted MD | MW | Non-Coincident | 11.51
|  |  |  | Coincident | 10.81
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.64
|  |  |  | Coincident | 10.98
|  | Date MD occurred |  | Non-Coincident | 19-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.001
|  |  |  | Coincident | -0.307
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.81
|  |  |  | Coincident | 12.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.93
|  |  |  | Coincident | 12.78
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.29
|  |  |  | Coincident | 11.14
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.4
|  |  |  | Coincident | 11.32
| Pelican 33_11kV | Substation Rating | MVA | Non-Coincident | 106.9
|  |  |  | Coincident | 106.9
|  | Raw Adjusted MD | MW | Non-Coincident | 77.48
|  |  |  | Coincident | 76.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 80.38
|  |  |  | Coincident | 78.97
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.378
|  |  |  | Coincident | -1.848
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 98.31
|  |  |  | Coincident | 96.59
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 102
|  |  |  | Coincident | 100.2
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 82.23
|  |  |  | Coincident | 80.79
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 85.31
|  |  |  | Coincident | 83.81
| Pennant Hills 132_11kV | Substation Rating | MVA | Non-Coincident | 59.16
|  |  |  | Coincident | 59.16
|  | Raw Adjusted MD | MW | Non-Coincident | 17.62
|  |  |  | Coincident | 16.34
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.98
|  |  |  | Coincident | 19.45
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.06
|  |  |  | Coincident | -0.038
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.65
|  |  |  | Coincident | 17.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 22.21
|  |  |  | Coincident | 20.59
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.96
|  |  |  | Coincident | 16.66
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.39
|  |  |  | Coincident | 19.84
| Port Botany 33_11kV | Substation Rating | MVA | Non-Coincident | 54.87
|  |  |  | Coincident | 54.87
|  | Raw Adjusted MD | MW | Non-Coincident | 45.91
|  |  |  | Coincident | 45.06
|  | Raw Adjusted MD | MVA | Non-Coincident | 46.7
|  |  |  | Coincident | 45.84
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.23
|  |  |  | Coincident | -0.762
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.81
|  |  |  | Coincident | 48.89
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.67
|  |  |  | Coincident | 49.73
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.79
|  |  |  | Coincident | 43.96
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.56
|  |  |  | Coincident | 44.72
| Potts Hill 132_11kV | Substation Rating | MVA | Non-Coincident | 40.35
|  |  |  | Coincident | 40.35
|  | Raw Adjusted MD | MW | Non-Coincident | 33.98
|  |  |  | Coincident | 33.98
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.75
|  |  |  | Coincident | 37.75
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.254
|  |  |  | Coincident | -0.613
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.37
|  |  |  | Coincident | 38.37
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 42.64
|  |  |  | Coincident | 42.64
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.96
|  |  |  | Coincident | 33.96
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 37.74
|  |  |  | Coincident | 37.74
| Punchbowl 33_11kV | Substation Rating | MVA | Non-Coincident | 39.43
|  |  |  | Coincident | 39.43
|  | Raw Adjusted MD | MW | Non-Coincident | 33.51
|  |  |  | Coincident | 33.28
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.47
|  |  |  | Coincident | 36.22
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.175
|  |  |  | Coincident | -0.581
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.19
|  |  |  | Coincident | 37.93
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.56
|  |  |  | Coincident | 41.28
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.42
|  |  |  | Coincident | 33.19
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.37
|  |  |  | Coincident | 36.13
| Pymble 33_11kV | Substation Rating | MVA | Non-Coincident | 53.54
|  |  |  | Coincident | 53.54
|  | Raw Adjusted MD | MW | Non-Coincident | 12.97
|  |  |  | Coincident | 11.91
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.99
|  |  |  | Coincident | 11.93
|  | Date MD occurred |  | Non-Coincident | 07-02-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 9:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.026
|  |  |  | Coincident | -0.013
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.24
|  |  |  | Coincident | 13.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.27
|  |  |  | Coincident | 13.1
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.34
|  |  |  | Coincident | 12.24
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.36
|  |  |  | Coincident | 12.26
| RNS Hospital 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 14.44
|  |  |  | Coincident | 11.76
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.79
|  |  |  | Coincident | 12.03
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.785
|  |  |  | Coincident | -0.785
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.53
|  |  |  | Coincident | 12.64
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.9
|  |  |  | Coincident | 12.94
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.51
|  |  |  | Coincident | 11
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.83
|  |  |  | Coincident | 11.26
| Rathmines 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 22.42
|  |  |  | Coincident | 19.78
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 20.17
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.14
|  |  |  | Coincident | -0.681
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.14
|  |  |  | Coincident | 22.19
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.63
|  |  |  | Coincident | 22.62
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.66
|  |  |  | Coincident | 19.99
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.1
|  |  |  | Coincident | 20.39
| Raymond Terr NEW 33_11kV | Substation Rating | MVA | Non-Coincident | 44.93
|  |  |  | Coincident | 44.93
|  | Raw Adjusted MD | MW | Non-Coincident | 43.44
|  |  |  | Coincident | 43.44
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.75
|  |  |  | Coincident | 44.75
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.377
|  |  |  | Coincident | -0.909
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.35
|  |  |  | Coincident | 51.35
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 52.91
|  |  |  | Coincident | 52.91
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.35
|  |  |  | Coincident | 44.35
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.69
|  |  |  | Coincident | 45.69
| Revesby 132_11kV | Substation Rating | MVA | Non-Coincident | 42.81
|  |  |  | Coincident | 42.81
|  | Raw Adjusted MD | MW | Non-Coincident | 26.76
|  |  |  | Coincident | 26.76
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.18
|  |  |  | Coincident | 28.18
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.277
|  |  |  | Coincident | -0.669
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.46
|  |  |  | Coincident | 30.46
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.07
|  |  |  | Coincident | 32.07
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.14
|  |  |  | Coincident | 26.14
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 27.53
|  |  |  | Coincident | 27.53
| Riverwood 33_11kV | Substation Rating | MVA | Non-Coincident | 53.54
|  |  |  | Coincident | 53.54
|  | Raw Adjusted MD | MW | Non-Coincident | 33.57
|  |  |  | Coincident | 33.34
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.31
|  |  |  | Coincident | 35.08
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.235
|  |  |  | Coincident | -0.445
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.98
|  |  |  | Coincident | 35.74
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.85
|  |  |  | Coincident | 37.59
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.41
|  |  |  | Coincident | 32.19
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.1
|  |  |  | Coincident | 33.87
| Rockdale 132_11kV | Substation Rating | MVA | Non-Coincident | 59.25
|  |  |  | Coincident | 59.25
|  | Raw Adjusted MD | MW | Non-Coincident | 40.56
|  |  |  | Coincident | 31.53
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.68
|  |  |  | Coincident | 31.85
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.472
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 41.67
|  |  |  | Coincident | 34.07
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.79
|  |  |  | Coincident | 34.42
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 39.75
|  |  |  | Coincident | 31.34
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 39.87
|  |  |  | Coincident | 31.66
| Rose Bay 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 12.8
|  |  |  | Coincident | 10.26
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.92
|  |  |  | Coincident | 10.36
|  | Date MD occurred |  | Non-Coincident | 26-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.18
|  |  |  | Coincident | -0.434
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.45
|  |  |  | Coincident | 11.59
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.59
|  |  |  | Coincident | 11.7
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.02
|  |  |  | Coincident | 10.44
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.15
|  |  |  | Coincident | 10.54
| Rothbury 132_11kV | Substation Rating | MVA | Non-Coincident | 6.34
|  |  |  | Coincident | 5.77
|  | Raw Adjusted MD | MW | Non-Coincident | 1.17
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.3
Coincident
|  | Date MD occurred |  | Non-Coincident | 01-05-18
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30:00
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.219
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.354
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.17
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.3
Coincident
| Rouchel 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 30.52
|  |  |  | Coincident | 25.58
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.74
|  |  |  | Coincident | 25.77
|  | Date MD occurred |  | Non-Coincident | 30-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -2.955
|  |  |  | Coincident | -1.188
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.74
|  |  |  | Coincident | 28.28
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.99
|  |  |  | Coincident | 28.49
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.41
|  |  |  | Coincident | 25.49
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.63
|  |  |  | Coincident | 25.68
| Rutherford 33_11kV | Substation Rating | MVA | Non-Coincident | 24.29
|  |  |  | Coincident | 24.29
|  | Raw Adjusted MD | MW | Non-Coincident | 16.18
|  |  |  | Coincident | 16.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.42
|  |  |  | Coincident | 16.42
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.112
|  |  |  | Coincident | -0.269
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.08
|  |  |  | Coincident | 17.08
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.34
|  |  |  | Coincident | 17.34
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.76
|  |  |  | Coincident | 14.76
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.98
|  |  |  | Coincident | 14.98
| Sans Souci 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 17
|  |  |  | Coincident | 14.07
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.33
|  |  |  | Coincident | 14.35
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.001
|  |  |  | Coincident | -0.61
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.52
|  |  |  | Coincident | 15.33
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.88
|  |  |  | Coincident | 15.63
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.69
|  |  |  | Coincident | 13.82
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.02
|  |  |  | Coincident | 14.08
| Scone 66_11kV | Substation Rating | MVA | Non-Coincident | 94.58
|  |  |  | Coincident | 94.58
|  | Raw Adjusted MD | MW | Non-Coincident | 50.59
|  |  |  | Coincident | 50.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 52.3
|  |  |  | Coincident | 51.9
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.335
|  |  |  | Coincident | -1.109
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 59.14
|  |  |  | Coincident | 58.69
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 61.14
|  |  |  | Coincident | 60.67
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 52.05
|  |  |  | Coincident | 51.66
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 53.81
|  |  |  | Coincident | 53.4
| Sefton 132_11kV | Substation Rating | MVA | Non-Coincident | 22.86
|  |  |  | Coincident | 22.86
|  | Raw Adjusted MD | MW | Non-Coincident | 19.77
|  |  |  | Coincident | 17.86
|  | Raw Adjusted MD | MVA | Non-Coincident | 21
|  |  |  | Coincident | 18.98
|  | Date MD occurred |  | Non-Coincident | 29-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.302
|  |  |  | Coincident | -0.373
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.92
|  |  |  | Coincident | 20.72
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.36
|  |  |  | Coincident | 22.01
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.66
|  |  |  | Coincident | 18.67
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.95
|  |  |  | Coincident | 19.84
| Singleton 66_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 17.3
|  |  |  | Coincident | 13.55
|  | Raw Adjusted MD | MVA | Non-Coincident | 18
|  |  |  | Coincident | 14.1
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.001
|  |  |  | Coincident | -0.711
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.04
|  |  |  | Coincident | 15.7
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.85
|  |  |  | Coincident | 16.33
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.06
|  |  |  | Coincident | 14.15
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.79
|  |  |  | Coincident | 14.72
| Singleton North 66_11kV | Substation Rating | MVA | Non-Coincident | 51.9
|  |  |  | Coincident | 51.9
|  | Raw Adjusted MD | MW | Non-Coincident | 17.98
|  |  |  | Coincident | 17.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.33
|  |  |  | Coincident | 18.51
|  | Date MD occurred |  | Non-Coincident | 22-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.705
|  |  |  | Coincident | -0.512
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.69
|  |  |  | Coincident | 18.85
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.17
|  |  |  | Coincident | 20.27
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.49
|  |  |  | Coincident | 17.7
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.88
|  |  |  | Coincident | 19.03
| Somersby 132_11kV | Substation Rating | MVA | Non-Coincident | 58.47
|  |  |  | Coincident | 58.47
|  | Raw Adjusted MD | MW | Non-Coincident | 45.42
|  |  |  | Coincident | 43.77
|  | Raw Adjusted MD | MVA | Non-Coincident | 47.08
|  |  |  | Coincident | 45.36
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.187
|  |  |  | Coincident | -0.915
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 57.5
|  |  |  | Coincident | 55.41
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 59.6
|  |  |  | Coincident | 57.43
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 48.16
|  |  |  | Coincident | 46.41
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 49.92
|  |  |  | Coincident | 48.1
| St Ives 33_11kV | Substation Rating | MVA | Non-Coincident | 88.63
|  |  |  | Coincident | 88.63
|  | Raw Adjusted MD | MW | Non-Coincident | 64
|  |  |  | Coincident | 62.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 69.22
|  |  |  | Coincident | 67.1
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.226
|  |  |  | Coincident | -0.651
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 67.46
|  |  |  | Coincident | 65.39
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 72.95
|  |  |  | Coincident | 70.72
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 63.91
|  |  |  | Coincident | 61.96
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 69.12
|  |  |  | Coincident | 67.01
| St Peters 132_11kV | Substation Rating | MVA | Non-Coincident | 20.01
|  |  |  | Coincident | 20.01
|  | Raw Adjusted MD | MW | Non-Coincident | 7.901
|  |  |  | Coincident | 6.722
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.032
|  |  |  | Coincident | 6.833
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.003
|  |  |  | Coincident | -0.263
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.07
|  |  |  | Coincident | 8.566
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.24
|  |  |  | Coincident | 8.707
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.708
|  |  |  | Coincident | 7.408
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.852
|  |  |  | Coincident | 7.531
| Stockton 33_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Strathfield South 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Summer Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 30.48
|  |  |  | Coincident | 30.48
|  | Raw Adjusted MD | MW | Non-Coincident | 31.75
|  |  |  | Coincident | 30.08
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.7
|  |  |  | Coincident | 31.93
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.162
|  |  |  | Coincident | -0.136
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.02
|  |  |  | Coincident | 32.23
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.12
|  |  |  | Coincident | 34.22
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.04
|  |  |  | Coincident | 30.36
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.02
|  |  |  | Coincident | 32.23
| Surry Hills 33_11kV | Substation Rating | MVA | Non-Coincident | 16.42
|  |  |  | Coincident | 16.42
|  | Raw Adjusted MD | MW | Non-Coincident | 12.73
|  |  |  | Coincident | 11.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.91
|  |  |  | Coincident | 11.25
|  | Date MD occurred |  | Non-Coincident | 05-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.541
|  |  |  | Coincident | -0.541
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.4
|  |  |  | Coincident | 13.42
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.61
|  |  |  | Coincident | 13.61
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.16
|  |  |  | Coincident | 11.47
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.35
|  |  |  | Coincident | 11.64
| Swansea 33_11kV | Substation Rating | MVA | Non-Coincident | 18.73
|  |  |  | Coincident | 18.73
|  | Raw Adjusted MD | MW | Non-Coincident | 10.32
|  |  |  | Coincident | 8.636
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.42
|  |  |  | Coincident | 8.716
|  | Date MD occurred |  | Non-Coincident | 12-02-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.056
|  |  |  | Coincident | -0.522
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.9
|  |  |  | Coincident | 9.958
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.01
|  |  |  | Coincident | 10.05
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.73
|  |  |  | Coincident | 8.974
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.82
|  |  |  | Coincident | 9.057
| Tanilba Bay 33_11kV | Substation Rating | MVA | Non-Coincident | 23.82
|  |  |  | Coincident | 23.82
|  | Raw Adjusted MD | MW | Non-Coincident | 21.39
|  |  |  | Coincident | 15.62
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.74
|  |  |  | Coincident | 16.6
|  | Date MD occurred |  | Non-Coincident | 23-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -1.318
|  |  |  | Coincident | -0.489
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.29
|  |  |  | Coincident | 16.27
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.7
|  |  |  | Coincident | 17.3
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.08
|  |  |  | Coincident | 14.66
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.35
|  |  |  | Coincident | 15.59
| Tarro 33_11kV | Substation Rating | MVA | Non-Coincident | 15.24
|  |  |  | Coincident | 15.24
|  | Raw Adjusted MD | MW | Non-Coincident | 14.86
|  |  |  | Coincident | 11.78
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.07
|  |  |  | Coincident | 11.94
|  | Date MD occurred |  | Non-Coincident | 18-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.006
|  |  |  | Coincident | -0.504
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.15
|  |  |  | Coincident | 14.39
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.4
|  |  |  | Coincident | 14.58
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.36
|  |  |  | Coincident | 12.97
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.58
|  |  |  | Coincident | 13.14
| Telarah 33_11kV | Substation Rating | MVA | Non-Coincident | 30.48
|  |  |  | Coincident | 30.48
|  | Raw Adjusted MD | MW | Non-Coincident | 14.85
|  |  |  | Coincident | 14.36
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.79
|  |  |  | Coincident | 15.28
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.264
|  |  |  | Coincident | -0.264
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.69
|  |  |  | Coincident | 16.15
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.76
|  |  |  | Coincident | 17.18
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.19
|  |  |  | Coincident | 14.7
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.16
|  |  |  | Coincident | 15.63
| Terrey Hills 33_11kV | Substation Rating | MVA | Non-Coincident | 61.01
|  |  |  | Coincident | 61.01
|  | Raw Adjusted MD | MW | Non-Coincident | 29.76
|  |  |  | Coincident | 25.76
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.28
|  |  |  | Coincident | 27.08
|  | Date MD occurred |  | Non-Coincident | 29-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.084
|  |  |  | Coincident | -1.408
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.99
|  |  |  | Coincident | 30.29
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.78
|  |  |  | Coincident | 31.84
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.53
|  |  |  | Coincident | 27.3
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.14
|  |  |  | Coincident | 28.69
| Thornton 33_11kV | Substation Rating | MVA | Non-Coincident | 23.82
|  |  |  | Coincident | 23.82
|  | Raw Adjusted MD | MW | Non-Coincident | 21
|  |  |  | Coincident | 17.15
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.01
|  |  |  | Coincident | 17.98
|  | Date MD occurred |  | Non-Coincident | 23-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.6
|  |  |  | Coincident | 20.09
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.79
|  |  |  | Coincident | 21.06
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.17
|  |  |  | Coincident | 18.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.24
|  |  |  | Coincident | 18.98
| Tighes Hill 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 10.41
|  |  |  | Coincident | 5.085
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.26
|  |  |  | Coincident | 5.505
|  | Date MD occurred |  | Non-Coincident | 17-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.455
|  |  |  | Coincident | -0.17
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.42
|  |  |  | Coincident | 5.579
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.36
|  |  |  | Coincident | 6.039
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.84
|  |  |  | Coincident | 5.299
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.74
|  |  |  | Coincident | 5.736
| Tomago 33_11kV | Substation Rating | MVA | Non-Coincident | 22.16
|  |  |  | Coincident | 20.77
|  | Raw Adjusted MD | MW | Non-Coincident | 1.316
|  |  |  | Coincident | 0.861
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.317
|  |  |  | Coincident | 0.863
|  | Date MD occurred |  | Non-Coincident | 23-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 9:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.616
|  |  |  | Coincident | 1.276
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.617
|  |  |  | Coincident | 1.278
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.344
|  |  |  | Coincident | 1.165
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.345
|  |  |  | Coincident | 1.168
| Tomalpin 33_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 15.57
|  |  |  | Coincident | 9.861
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.84
|  |  |  | Coincident | 10.03
|  | Date MD occurred |  | Non-Coincident | 26-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.115
|  |  |  | Coincident | -0.562
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.14
|  |  |  | Coincident | 11.49
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.45
|  |  |  | Coincident | 11.69
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.73
|  |  |  | Coincident | 9.961
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16
|  |  |  | Coincident | 10.13
| Tomaree 33_11kV | Substation Rating | MVA | Non-Coincident | 61.25
|  |  |  | Coincident | 61.25
|  | Raw Adjusted MD | MW | Non-Coincident | 50.46
|  |  |  | Coincident | 49.95
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.23
|  |  |  | Coincident | 50.72
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.191
|  |  |  | Coincident | -0.633
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 56.43
|  |  |  | Coincident | 55.86
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.29
|  |  |  | Coincident | 56.72
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 49.16
|  |  |  | Coincident | 48.67
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 49.92
|  |  |  | Coincident | 49.41
| Top Ryde 132_11kV | Substation Rating | MVA | Non-Coincident | 38.11
|  |  |  | Coincident | 38.11
|  | Raw Adjusted MD | MW | Non-Coincident | 19.95
|  |  |  | Coincident | 18.53
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.37
|  |  |  | Coincident | 18.92
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.005
|  |  |  | Coincident | -0.747
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.1
|  |  |  | Coincident | 22.39
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.61
|  |  |  | Coincident | 22.86
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.93
|  |  |  | Coincident | 19.45
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.38
|  |  |  | Coincident | 19.86
| Toronto West 132_11kV | Substation Rating | MVA | Non-Coincident | 43.32
|  |  |  | Coincident | 43.32
|  | Raw Adjusted MD | MW | Non-Coincident | 36.15
|  |  |  | Coincident | 35.04
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.47
|  |  |  | Coincident | 35.35
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.122
|  |  |  | Coincident | -0.595
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 43.73
|  |  |  | Coincident | 42.39
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 44.13
|  |  |  | Coincident | 42.77
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 37.91
|  |  |  | Coincident | 36.74
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 38.25
|  |  |  | Coincident | 37.07
| Turramurra 33_11kV | Substation Rating | MVA | Non-Coincident | 35.7
|  |  |  | Coincident | 35.7
|  | Raw Adjusted MD | MW | Non-Coincident | 29.29
|  |  |  | Coincident | 26.9
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.81
|  |  |  | Coincident | 28.29
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.01
|  |  |  | Coincident | -0.841
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.8
|  |  |  | Coincident | 31.96
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.6
|  |  |  | Coincident | 33.61
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.09
|  |  |  | Coincident | 27.63
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.64
|  |  |  | Coincident | 29.06
| Umina 66_11kV | Substation Rating | MVA | Non-Coincident | 15.24
|  |  |  | Coincident | 15.24
|  | Raw Adjusted MD | MW | Non-Coincident | 5.369
|  |  |  | Coincident | 3.304
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.469
|  |  |  | Coincident | 4.182
|  | Date MD occurred |  | Non-Coincident | 20-08-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 2:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.377
|  |  |  | Coincident | 3.301
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.478
|  |  |  | Coincident | 4.179
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.377
|  |  |  | Coincident | 3.301
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.478
|  |  |  | Coincident | 4.179
| Vales Point 33_11kV | Substation Rating | MVA | Non-Coincident | 36.9
|  |  |  | Coincident | 34.4
|  | Raw Adjusted MD | MW | Non-Coincident | 12.53
|  |  |  | Coincident | 11.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.92
|  |  |  | Coincident | 12.37
|  | Date MD occurred |  | Non-Coincident | 27-08-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.603
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.53
|  |  |  | Coincident | 11.74
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.04
|  |  |  | Coincident | 13.04
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.83
|  |  |  | Coincident | 10.43
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.25
|  |  |  | Coincident | 11.59
| Wamberal 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Wamberal 66_11kV | Substation Rating | MVA | Non-Coincident | 65.01
|  |  |  | Coincident | 61.79
|  | Raw Adjusted MD | MW | Non-Coincident | 28.49
|  |  |  | Coincident | 21.94
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.03
|  |  |  | Coincident | 22.06
|  | Date MD occurred |  | Non-Coincident | 18-06-18
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Winter
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | -0.165
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.54
|  |  |  | Coincident | 23.99
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.12
|  |  |  | Coincident | 24.12
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.02
|  |  |  | Coincident | 21.96
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.57
|  |  |  | Coincident | 22.08
| Waverley 132_11kV | Substation Rating | MVA | Non-Coincident | 65.01
|  |  |  | Coincident | 65.01
|  | Raw Adjusted MD | MW | Non-Coincident | 48.68
|  |  |  | Coincident | 47.73
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.96
|  |  |  | Coincident | 48.98
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.766
|  |  |  | Coincident | -1.146
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 55.62
|  |  |  | Coincident | 54.54
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.08
|  |  |  | Coincident | 55.97
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 50.13
|  |  |  | Coincident | 49.15
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 51.44
|  |  |  | Coincident | 50.44
| West Gosford 132_11kV | Substation Rating | MVA | Non-Coincident | 24.75
|  |  |  | Coincident | 24.75
|  | Raw Adjusted MD | MW | Non-Coincident | 5.652
|  |  |  | Coincident | 5.357
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.793
|  |  |  | Coincident | 5.491
|  | Date MD occurred |  | Non-Coincident | 06-03-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.351
|  |  |  | Coincident | -0.187
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.135
|  |  |  | Coincident | 5.815
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.289
|  |  |  | Coincident | 5.961
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.528
|  |  |  | Coincident | 5.24
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.667
|  |  |  | Coincident | 5.372
| Williamtown 33_11kV | Substation Rating | MVA | Non-Coincident | 30.75
|  |  |  | Coincident | 30.75
|  | Raw Adjusted MD | MW | Non-Coincident | 19.39
|  |  |  | Coincident | 18.32
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.46
|  |  |  | Coincident | 19.34
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.007
|  |  |  | Coincident | -0.62
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.31
|  |  |  | Coincident | 22.03
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.6
|  |  |  | Coincident | 23.25
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.19
|  |  |  | Coincident | 19.08
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.3
|  |  |  | Coincident | 20.13
| Woy Woy 66_11kV | Substation Rating | MVA | Non-Coincident | 54.01
|  |  |  | Coincident | 54.01
|  | Raw Adjusted MD | MW | Non-Coincident | 38.53
|  |  |  | Coincident | 36.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 39.72
|  |  |  | Coincident | 37.63
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.018
|  |  |  | Coincident | -1.56
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 46.91
|  |  |  | Coincident | 44.43
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 48.36
|  |  |  | Coincident | 45.81
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.88
|  |  |  | Coincident | 38.72
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.15
|  |  |  | Coincident | 39.92
| Wyong 132_11kV | Substation Rating | MVA | Non-Coincident | 83.6
|  |  |  | Coincident | 83.6
|  | Raw Adjusted MD | MW | Non-Coincident | 61.63
|  |  |  | Coincident | 59.43
|  | Raw Adjusted MD | MVA | Non-Coincident | 62.42
|  |  |  | Coincident | 60.19
|  | Date MD occurred |  | Non-Coincident | 31-01-19
|  |  |  | Coincident | 31-01-19
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | -0.532
|  |  |  | Coincident | -0.386
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 62.83
|  |  |  | Coincident | 60.59
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 63.63
|  |  |  | Coincident | 61.36
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 58.98
|  |  |  | Coincident | 56.88
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 59.73
|  |  |  | Coincident | 57.6
| Zetland 132_11kV | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 6.3 Sustained interruptions
REGULATORY REPORTING STATEMENT
Ausgrid
CATEGORY ANALYSIS 2018-19
6.3 SUSTAINED INTERRUPTIONS TO SUPPLY
6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2018-19)
There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data.
Definitions:
Feeder classification definitions (column E) |  |  |  |  | Average duration of sustained customer interruption (column I) |  | Effect on unplanned SAIDI (column J) |  | Effect on unplanned SAIFI (column K)
CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km. Short rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km. Long rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km. |  |  |  |  | The average duration of an interruption experienced by an affected customer. |  | The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less). |  | The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
Date of event | Time of interruption | Asset ID | Feeder classification | Reason for interruption | Detailed reason for interruption | Number of customers affected by the interruption | Average duration of sustained customer interruption | Effect on unplanned SAIDI | Effect on unplanned SAIFI | MED
(DD/MM/YYYY) | (HH:MM) | (eg. feeder ID) | (drop down) | (select from options in drop-down box) | (select from options in column 'O' that correspond with reason in column 'F') |  | (minutes)
01-07-18 | 06:54 | ZN9700:PA17 | URBAN | Asset Failure | LV | 9 | 92 | 0.000548 | 6e-06 | N
01-07-18 | 03:02 | ZN129:PA35 | URBAN | Third Party | Other | 1 | 484 | 0.000321 | 1e-06 | N
01-07-18 | 10:46 | ZN35500:PA32 | URBAN | Asset Failure | LV | 1 | 145 | 9.6e-05 | 1e-06 | N
01-07-18 | 11:11 | 238:34141 | SHORT RURAL | Asset Failure | LV | 1 | 343 | 0.001794 | 5e-06 | N
01-07-18 | 16:39 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 56 | 0.000293 | 5e-06 | N
01-07-18 | 22:38 | ZN15005:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 282 | 0.006158 | 2.2e-05 | N
02-07-18 | 08:44 | ZN35800:PA3 | URBAN | Asset Failure | LV | 1 | 525 | 0.000348 | 1e-06 | N
02-07-18 | 10:19 | ZN195:PA4 | URBAN | Asset Failure | HV | 1,126 | 70 | 0.052209 | 0.000745 | N
02-07-18 | 15:02 | ZN12630:PA11 | SHORT RURAL | Other | Other | 1 | 79 | 0.000413 | 5e-06 | N
02-07-18 | 16:23 | ZN15004:PA1 | URBAN | Asset Failure | LV | 43 | 127 | 0.003614 | 2.8e-05 | N
02-07-18 | 16:36 | ZN7900:PA24 | URBAN | Other | Other - Self Clearing Trigger | 111 | 154 | 0.011311 | 7.3e-05 | N
02-07-18 | 16:36 | ZN901:PA18 | URBAN | Other | Other - Self Clearing Trigger | 1 | 154 | 0.000102 | 1e-06 | N
02-07-18 | 16:59 | ZN35500:PA28 | URBAN | Asset Failure | LV | 1 | 240 | 0.000159 | 1e-06 | N
02-07-18 | 18:00 | ZN35600:PA16 | URBAN | Asset Failure | LV | 131 | 220 | 0.01905 | 8.7e-05 | N
02-07-18 | 20:05 | ZN15008:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 101 | 180 | 0.01203 | 6.7e-05 | N
02-07-18 | 20:05 | ZN15008:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 2,547 | 145 | 0.24358 | 0.001685 | N
02-07-18 | 22:57 | ZN10993:PA39 | URBAN | Other | Other - Arcing | 1 | 123 | 8.1e-05 | 1e-06 | N
03-07-18 | 01:39 | ZN12690:PA1 | URBAN | Other | Other - Self Clearing Trigger | 1 | 994 | 0.000657 | 1e-06 | N
03-07-18 | 06:43 | 515:35193 | SHORT RURAL | Asset Failure | HV | 6 | 87 | 0.002727 | 3.1e-05 | N
03-07-18 | 09:03 | 270:83587 | URBAN | Third Party | Dig-in | 1,238 | 65 | 0.053249 | 0.000819 | N
03-07-18 | 09:18 | ZN262:PA31 | URBAN | Asset Failure | HV | 1,359 | 74 | 0.066762 | 0.000899 | N
03-07-18 | 10:26 | 414:LD2 | URBAN | Other | Other - Self Clearing Trigger | 2 | 167 | 0.000221 | 1e-06 | N
03-07-18 | 11:12 | ZN1290:PA9 | URBAN | Other | Other - Self Clearing Trigger | 58 | 159 | 0.006085 | 3.8e-05 | N
03-07-18 | 12:33 | ZN36100:PA19 | URBAN | Third Party | Other | 1 | 237 | 0.000157 | 1e-06 | N
03-07-18 | 14:56 | ZN384:PA70 | URBAN | Asset Failure | LV | 1 | 333 | 0.00022 | 1e-06 | N
03-07-18 | 16:11 | ZN2835:PA27 | URBAN | Asset Failure | LV | 1 | 299 | 0.000198 | 1e-06 | N
03-07-18 | 17:30 | ZN5868:PA27 | URBAN | Other | Other | 1 | 172 | 0.000114 | 1e-06 | N
03-07-18 | 19:20 | ZN2635:PA57 | URBAN | Asset Failure | LV | 54 | 60 | 0.002144 | 3.6e-05 | N
03-07-18 | 22:33 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 128 | 0.004681 | 3.7e-05 | N
04-07-18 | 00:59 | ZN14891:PA16 | SHORT RURAL | Asset Failure | HV | 119 | 66 | 0.040968 | 0.000621 | N
04-07-18 | 05:35 | 522:83123 | SHORT RURAL | Asset Failure | LV | 32 | 235 | 0.039159 | 0.000167 | N
04-07-18 | 11:45 | ZN965:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 22 | 0.000466 | 2.1e-05 | N
04-07-18 | 07:25 | ZN12650:PA12 | URBAN | Other | Other | 1 | 72 | 4.8e-05 | 1e-06 | N
04-07-18 | 09:21 | 221:11898 | SHORT RURAL | Asset Failure | LV | 5 | 90 | 0.002347 | 2.6e-05 | N
04-07-18 | 09:34 | ZN15005:PA4 | URBAN | Asset Failure | LV | 1 | 265 | 0.000176 | 1e-06 | N
04-07-18 | 09:37 | ZN15014:PA16 | URBAN | Asset Failure | LV | 2 | 262 | 0.000347 | 1e-06 | N
04-07-18 | 10:19 | ZN10990:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 85 | 398 | 0.02241 | 5.6e-05 | N
04-07-18 | 09:47 | ZN10990:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 673 | 0.000445 | 1e-06 | N
04-07-18 | 10:04 | 523:33508 | SHORT RURAL | Asset Failure | LV | 1 | 93 | 0.000483 | 5e-06 | N
04-07-18 | 10:19 | ZN10990:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 641 | 0.000424 | 1e-06 | N
04-07-18 | 10:57 | ZN342:PA17 | URBAN | Other | Other - Self Clearing Trigger | 89 | 87 | 0.005147 | 5.9e-05 | N
04-07-18 | 11:02 | 256:80647 | URBAN | Asset Failure | LV | 1 | 137 | 9.1e-05 | 1e-06 | N
04-07-18 | 11:05 | 515:35200 | URBAN | Other | Other - Self Clearing Trigger | 71 | 81 | 0.003817 | 4.7e-05 | N
04-07-18 | 13:36 | ZN340:PA20 | URBAN | Other | Other - Arcing | 1 | 485 | 0.000321 | 1e-06 | N
04-07-18 | 14:12 | ZN1287:PA21 | URBAN | Other | Other - Self Clearing Trigger | 56 | 150 | 0.005558 | 3.7e-05 | N
04-07-18 | 14:15 | ZN188:PA37 | URBAN | Other | Other - Self Clearing Trigger | 33 | 120 | 0.002612 | 2.2e-05 | N
04-07-18 | 14:15 | ZN901:PA18 | URBAN | Other | Other - Self Clearing Trigger | 28 | 120 | 0.002224 | 1.9e-05 | N
04-07-18 | 15:25 | 532:83301 | URBAN | Other | Other - Self Clearing Trigger | 136 | 120 | 0.01079 | 9e-05 | N
04-07-18 | 18:24 | 507:80923 | SHORT RURAL | Other | Other | 53 | 75 | 0.020826 | 0.000276 | N
04-07-18 | 18:48 | ZN10991:PA1 | URBAN | Animal | Animal impact | 1,521 | 114 | 0.11476 | 0.001007 | N
04-07-18 | 18:48 | ZN10991:PA12 | URBAN | Animal | Animal impact | 84 | 114 | 0.006338 | 5.6e-05 | N
04-07-18 | 18:48 | ZN10991:PA13 | URBAN | Animal | Animal impact | 1 | 114 | 7.5e-05 | 1e-06 | N
05-07-18 | 06:41 | ZN8700:PA63 64KLM | CBD | Other | Other - Self Clearing Trigger | 1 | 169 | 0.005444 | 3.2e-05 | N
05-07-18 | 07:27 | 532:83298 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1,176 | 68 | 0.41801 | 0.006134 | N
05-07-18 | 07:54 | 224:80331 | URBAN | Other | Other - Arcing | 1 | 275 | 0.000182 | 1e-06 | N
05-07-18 | 07:55 | ZN4545:PA41 | SHORT RURAL | Asset Failure | LV | 61 | 115 | 0.036641 | 0.000318 | N
04-07-18 | 21:50 | 238:34148 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 30 | 0.000156 | 5e-06 | N
05-07-18 | 08:51 | ZN14144:PA1 | URBAN | Asset Failure | LV | 1 | 216 | 0.000143 | 1e-06 | N
05-07-18 | 10:38 | ZN711:PA27 | URBAN | Other | Other - Self Clearing Trigger | 2 | 157 | 0.000208 | 1e-06 | N
05-07-18 | 11:23 | ZN1610:PA2 | URBAN | Asset Failure | LV | 1 | 171 | 0.000113 | 1e-06 | N
05-07-18 | 15:36 | 511:29872 | URBAN | Third Party | Vehicle impact | 1 | 414 | 0.000274 | 1e-06 | N
05-07-18 | 16:15 | 532:83298 | SHORT RURAL | Asset Failure | HV | 8 | 135 | 0.005633 | 4.2e-05 | N
05-07-18 | 16:37 | ZN690:PA34 | URBAN | Third Party | Vehicle impact | 64 | 138 | 0.005846 | 4.2e-05 | N
05-07-18 | 17:11 | 223:14393 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 240 | 0.000159 | 1e-06 | N
05-07-18 | 19:14 | ZN36300:PA5 | URBAN | Other | Other - Arcing | 1 | 856 | 0.000566 | 1e-06 | N
05-07-18 | 20:00 | ZN15008:PA5 | URBAN | Asset Failure | LV | 82 | 75 | 0.004071 | 5.4e-05 | N
06-07-18 | 02:42 | ZN14143:PA6 | URBAN | Asset Failure | LV | 3 | 68 | 0.000135 | 2e-06 | N
06-07-18 | 05:32 | ZN1290:PA12 | URBAN | Asset Failure | HV | 1,034 | 172 | 0.11806 | 0.000685 | N
06-07-18 | 12:54 | 514:18137 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 176 | 0.000918 | 5e-06 | N
06-07-18 | 12:31 | ZN35500:PA27 | URBAN | Asset Failure | LV | 56 | 598 | 0.022172 | 3.7e-05 | N
06-07-18 | 13:17 | ZN35500:PA34 | URBAN | Third Party | Other | 301 | 159 | 0.031685 | 0.000199 | N
06-07-18 | 13:17 | ZN4545:PA4 | URBAN | Third Party | Other | 1,060 | 106 | 0.074686 | 0.000702 | N
06-07-18 | 13:22 | ZN1287:PA24 | URBAN | Weather |  | 98 | 132 | 0.008566 | 6.5e-05 | N
06-07-18 | 13:27 | 230:81434 | URBAN | Other | Other - Self Clearing Trigger | 1 | 43 | 2.8e-05 | 1e-06 | N
06-07-18 | 13:31 | 526:34640 | SHORT RURAL | Third Party | Other | 3 | 71 | 0.001111 | 1.6e-05 | N
06-07-18 | 13:35 | ZN4545:PA21 | URBAN | Network business | Network error | 89 | 190 | 0.011195 | 5.9e-05 | N
06-07-18 | 14:15 | ZN1287:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 322 | 0.000213 | 1e-06 | N
06-07-18 | 14:55 | ZN4545:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 150 | 9.9e-05 | 1e-06 | N
06-07-18 | 15:08 | ZN965:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,298 | 57 | 0.048982 | 0.000859 | N
06-07-18 | 17:29 | ZN2466:PA5 | URBAN | Third Party | Other | 3 | 204 | 0.000405 | 2e-06 | N
06-07-18 | 17:46 | 512:48049 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 269 | 0.002806 | 1e-05 | N
06-07-18 | 18:01 | ZN847:PA44 | URBAN | Asset Failure | LV | 21 | 1,424 | 0.019794 | 1.4e-05 | N
06-07-18 | 23:20 | 229:34995 | SHORT RURAL | Asset Failure | HV | 675 | 53 | 0.18576 | 0.003521 | N
06-07-18 | 23:59 | 213:33773 | URBAN | Other | Other | 1 | 472 | 0.000313 | 1e-06 | N
07-07-18 | 06:33 | ZN2310:PA15 | URBAN | Other | Other - Arcing | 1 | 464 | 0.000307 | 1e-06 | N
07-07-18 | 07:39 | ZN15008:PA10 | URBAN | Asset Failure | LV | 77 | 559 | 0.028482 | 5.1e-05 | N
07-07-18 | 07:47 | ZN35900:PA10 | URBAN | Asset Failure | HV | 11 | 832 | 0.00606 | 7e-06 | N
07-07-18 | 10:01 | ZN5868:PA17 | URBAN | Other | Other | 1 | 101 | 6.7e-05 | 1e-06 | N
07-07-18 | 10:21 | ZN167:PA11 | URBAN | Third Party | Vehicle impact | 2 | 399 | 0.000528 | 1e-06 | N
07-07-18 | 10:37 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 143 | 0.002238 | 1.6e-05 | N
07-07-18 | 10:51 | ZN129:PA47 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 32 | 2.1e-05 | 1e-06 | N
07-07-18 | 11:25 | ZN1193:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 491 | 0.000325 | 1e-06 | N
07-07-18 | 11:38 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 18 | 342 | 2.1737 | 0.006356 | N
07-07-18 | 11:28 | ZN1193:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 63 | 487 | 0.020312 | 4.2e-05 | N
07-07-18 | 12:46 | ZN14144:PA2 | SHORT RURAL | Other | Other | 1 | 212 | 0.001105 | 5e-06 | N
07-07-18 | 12:51 | 220:8689 | URBAN | Other | Other | 1 | 58 | 3.8e-05 | 1e-06 | N
07-07-18 | 12:55 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 357 | 0.000237 | 1e-06 | N
07-07-18 | 15:30 | ZN12630:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 85 | 0.000443 | 5e-06 | N
07-07-18 | 15:26 | ZN14891:PA16 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,351 | 84 | 0.5889 | 0.007047 | N
07-07-18 | 15:35 | ZN15008:PA7 | URBAN | Asset Failure | LV | 1 | 255 | 0.000169 | 1e-06 | N
07-07-18 | 18:10 | 807:74179 | SHORT RURAL | Asset Failure | HV | 4 | 35 | 0.00073 | 2.1e-05 | N
07-07-18 | 16:06 | ZN195:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 144 | 0.002193 | 1.5e-05 | N
07-07-18 | 16:42 | 243:80084 | SHORT RURAL | Other | Other | 1 | 183 | 0.000953 | 5e-06 | N
07-07-18 | 19:58 | ZN9900:PA21 | URBAN | Asset Failure | LV | 29 | 171 | 0.003292 | 1.9e-05 | N
08-07-18 | 07:33 | ZN4545:PA21 | URBAN | Third Party | Other | 33 | 273 | 0.00596 | 2.2e-05 | N
08-07-18 | 08:21 | ZN15008:PA7 | URBAN | Asset Failure | LV | 1 | 287 | 0.00019 | 1e-06 | N
08-07-18 | 08:34 | ZN35500:PA32 | URBAN | Overloads |  | 1 | 136 | 9e-05 | 1e-06 | N
09-07-18 | 13:45 | ZN711:PA27 | URBAN | Asset Failure | LV | 2 | 1,245 | 0.001648 | 1e-06 | N
08-07-18 | 14:16 | ZN12650:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 98 | 0.009157 | 9.4e-05 | N
08-07-18 | 18:01 | ZN3154:PA18 | URBAN | Asset Failure | LV | 53 | 179 | 0.006278 | 3.5e-05 | N
08-07-18 | 19:59 | ZN3922:PA14 | URBAN | Other | Other | 1 | 390 | 0.000258 | 1e-06 | N
08-07-18 | 21:35 | 520:48172 | SHORT RURAL | Asset Failure | LV | 1 | 75 | 0.000391 | 5e-06 | N
08-07-18 | 23:25 | ZN12620:PA10 | SHORT RURAL | Asset Failure | HV | 46 | 85 | 0.020389 | 0.00024 | N
09-07-18 | 06:49 | ZN180:PA32 | URBAN | Third Party | Vehicle impact | 70 | 296 | 0.013712 | 4.6e-05 | N
09-07-18 | 08:48 | ZN12650:PA6 | URBAN | Other | Other | 1 | 89 | 5.9e-05 | 1e-06 | N
09-07-18 | 09:17 | ZN3922:PA10 | URBAN | Other | Other | 1 | 57 | 3.8e-05 | 1e-06 | N
06-07-18 | 10:36 | ZN3154:PA19 | URBAN | Network business | Network error | 38 | 2 | 5e-05 | 2.5e-05 | N
07-07-18 | 22:00 | 522:83132 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 120 | 0.001878 | 1.6e-05 | N
05-07-18 | 07:30 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 205 | 0.21716 | 0.001059 | N
06-07-18 | 10:08 | 514:18137 | SHORT RURAL | Third Party | Other | 1 | 7 | 3.7e-05 | 5e-06 | N
09-07-18 | 11:51 | ZN2602:PA15 | URBAN | Asset Failure | LV | 43 | 396 | 0.011274 | 2.8e-05 | N
09-07-18 | 12:00 | ZN12650:PA2 | URBAN | Third Party | Vehicle impact | 1 | 330 | 0.000218 | 1e-06 | N
09-07-18 | 13:42 | ZN35800:PA2 | URBAN | Third Party | Vehicle impact | 1 | 78 | 5.2e-05 | 1e-06 | N
09-07-18 | 16:12 | ZN35800:PA2 | URBAN | Third Party | Vehicle impact | 99 | 37 | 0.002427 | 6.6e-05 | N
09-07-18 | 19:07 | ZN12610:PA18 | URBAN | Asset Failure | HV | 1,182 | 98 | 0.076614 | 0.000782 | N
09-07-18 | 22:31 | ZN15010:PA24 | URBAN | Asset Failure | LV | 1 | 628 | 0.000416 | 1e-06 | N
10-07-18 | 04:14 | ZN9700:PA17 | URBAN | Asset Failure | HV | 4,131 | 99 | 0.2705 | 0.002734 | N
10-07-18 | 06:30 | ZN8700:PA63 64KLM | CBD | Other | Other - Self Clearing Trigger | 1 | 59 | 0.001909 | 3.2e-05 | N
10-07-18 | 06:57 | ZN15010:PA30 | URBAN | Asset Failure | LV | 1 | 273 | 0.00018 | 1e-06 | N
10-07-18 | 08:03 | 811:74234 | SHORT RURAL | Asset Failure | HV | 2 | 171 | 0.001783 | 1e-05 | N
10-07-18 | 11:13 | 202:34238 43 48 | URBAN | Other | Other - Self Clearing Trigger | 6 | 39 | 0.000156 | 4e-06 | N
10-07-18 | 12:15 | ZN12580:PA1 | URBAN | Other | Other | 1 | 244 | 0.000162 | 1e-06 | N
10-07-18 | 13:01 | ZN15006:PA16 | URBAN | Third Party | Vehicle impact | 71 | 79 | 0.003706 | 4.7e-05 | N
10-07-18 | 13:20 | ZN15012:PA4 | URBAN | Third Party | Vehicle impact | 31 | 540 | 0.011078 | 2.1e-05 | N
10-07-18 | 13:27 | ZN15014:PA12 | SHORT RURAL | Other | Other | 1 | 208 | 0.001084 | 5e-06 | N
10-07-18 | 14:35 | ZN8700:PA63 64KLM | CBD | Asset Failure | LV | 1 | 154 | 0.004978 | 3.2e-05 | N
10-07-18 | 16:14 | ZN35800:PA22 | URBAN | Third Party | Vehicle impact | 11 | 61 | 0.000444 | 7e-06 | N
10-07-18 | 17:09 | 221:11898 | SHORT RURAL | Third Party | Vehicle impact | 3 | 131 | 0.002049 | 1.6e-05 | N
10-07-18 | 17:40 | 515:35192 | SHORT RURAL | Asset Failure | HV | 4 | 95 | 0.001982 | 2.1e-05 | N
10-07-18 | 18:05 | ZN35600:PA19 | URBAN | Other | Other | 1 | 144 | 9.6e-05 | 1e-06 | N
10-07-18 | 18:15 | 227:13019 | SHORT RURAL | Third Party | Unauthorised access | 1 | 10 | 5.2e-05 | 5e-06 | N
11-07-18 | 09:01 | ZN10994:PA13 | URBAN | Other | Other - Arcing | 1 | 118 | 7.8e-05 | 1e-06 | N
11-07-18 | 10:20 | ZN188:PA31 | URBAN | Third Party | Other | 3 | 495 | 0.000983 | 2e-06 | N
11-07-18 | 10:22 | ZN2835:PA10 | URBAN | Asset Failure | LV | 1 | 277 | 0.000184 | 1e-06 | N
11-07-18 | 14:46 | ZN12570:PA41 | URBAN | Other | Other | 1 | 196 | 0.00013 | 1e-06 | N
11-07-18 | 12:41 | ZN10991:PA1 | URBAN | Third Party | Vehicle impact | 21 | 189 | 0.002627 | 1.4e-05 | N
11-07-18 | 17:26 | ZN12580:PA1 | URBAN | Other | Other | 1 | 1,176 | 0.000778 | 1e-06 | N
11-07-18 | 21:13 | 526:34637 | SHORT RURAL | Asset Failure | HV | 157 | 55 | 0.044977 | 0.000819 | N
11-07-18 | 22:52 | 801:74121 | LONG RURAL | Asset Failure | LV | 1 | 98 | 0.034605 | 0.000353 | N
12-07-18 | 02:27 | ZN2635:PA35 | URBAN | Asset Failure | LV | 45 | 856 | 0.025502 | 3e-05 | N
12-07-18 | 08:27 | ZN15013:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 32 | 143 | 0.02381 | 0.000167 | N
12-07-18 | 08:58 | ZN15001:PA6 | URBAN | Other | Other | 1 | 82 | 5.4e-05 | 1e-06 | N
12-07-18 | 09:44 | ZN384:PA70 | URBAN | Asset Failure | LV | 6 | 55 | 0.000219 | 4e-06 | N
12-07-18 | 11:29 | ZN15013:PA4 | SHORT RURAL | Asset Failure | LV | 32 | 1,376 | 0.22961 | 0.000167 | N
12-07-18 | 11:31 | 513:48050 | SHORT RURAL | Asset Failure | HV | 5 | 299 | 0.007796 | 2.6e-05 | N
12-07-18 | 13:59 | ZN35800:PA22 | URBAN | Third Party | Vehicle impact | 11 | 141 | 0.001026 | 7e-06 | N
12-07-18 | 14:13 | ZN340:PA8 | URBAN | Other | Other | 1 | 2 | 2e-06 | 1e-06 | N
05-07-18 | 17:45 | ZN965:PA42 | URBAN | Asset Failure | LV | 25 | 11 | 0.000182 | 1.7e-05 | N
12-07-18 | 18:15 | 512:48049 | SHORT RURAL | Asset Failure | LV | 2 | 115 | 0.001199 | 1e-05 | N
12-07-18 | 19:58 | ZN35500:PA34 | URBAN | Other | Other - Arcing | 16 | 811 | 0.008589 | 1.1e-05 | N
13-07-18 | 00:37 | ZN12620:PA1 | SHORT RURAL | Asset Failure | HV | 2,705 | 99 | 1.393 | 0.014106 | N
13-07-18 | 04:21 | ZN35500:PA28 | URBAN | Animal | Animal impact | 3,502 | 73 | 0.16951 | 0.002318 | N
13-07-18 | 04:21 | ZN35500:PA34 | URBAN | Animal | Animal impact | 301 | 72 | 0.014343 | 0.000199 | N
13-07-18 | 06:33 | ZN35500:PA34 | URBAN | Other | Other - Arcing | 1 | 176 | 0.000117 | 1e-06 | N
13-07-18 | 06:41 | ZN36300:PA5 | URBAN | Third Party | Vehicle impact | 61 | 103 | 0.00416 | 4e-05 | N
13-07-18 | 09:10 | ZN10993:PA27 | URBAN | Other | Other | 1 | 128 | 8.4e-05 | 1e-06 | N
13-07-18 | 10:45 | ZN13000:PA11 | SHORT RURAL | Asset Failure | LV | 10 | 373 | 0.019451 | 5.2e-05 | N
13-07-18 | 11:03 | ZN35500:PA22 | URBAN | Other | Other | 1 | 35 | 2.3e-05 | 1e-06 | N
13-07-18 | 12:04 | ZN7900:PA24 | URBAN | Other | Other - Self Clearing Trigger | 1 | 290 | 0.000192 | 1e-06 | N
13-07-18 | 12:24 | 502:48002 | URBAN | Other | Other | 1 | 145 | 9.6e-05 | 1e-06 | N
13-07-18 | 13:21 | ZN10995:PA1 | URBAN | Third Party | Vehicle impact | 108 | 139 | 0.009935 | 7.1e-05 | N
13-07-18 | 14:27 | 502:48004 | URBAN | Other | Other | 1 | 71 | 4.7e-05 | 1e-06 | N
13-07-18 | 21:12 | ZN3154:PA25 | URBAN | Animal | Animal impact | 607 | 227 | 0.091074 | 0.000402 | N
13-07-18 | 23:15 | ZN3154:PA3 | URBAN | Network business | Switching and protection error | 28 | 275 | 0.005096 | 1.9e-05 | N
13-07-18 | 23:46 | ZN12610:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2,101 | 71 | 0.78202 | 0.010956 | N
14-07-18 | 07:09 | 524:33580 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 101 | 0.002633 | 2.6e-05 | N
14-07-18 | 08:19 | ZN398:PA3 | URBAN | Other | Other - Arcing | 1 | 401 | 0.000265 | 1e-06 | N
14-07-18 | 12:56 | ZN690:PA14 | URBAN | Third Party | Vehicle impact | 61 | 389 | 0.015704 | 4e-05 | N
14-07-18 | 13:16 | ZN14144:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 314 | 0.001636 | 5e-06 | N
15-07-18 | 13:21 | 242:81539 | URBAN | Asset Failure | LV | 40 | 113 | 0.003004 | 2.6e-05 | N
15-07-18 | 13:38 | 801:74118 | URBAN | Other | Other | 1 | 306 | 0.000202 | 1e-06 | N
15-07-18 | 13:44 | 813:89061 | LONG RURAL | Asset Failure | LV | 1 | 196 | 0.069056 | 0.000353 | N
15-07-18 | 15:07 | ZN10993:PA33 | URBAN | Asset Failure | HV | 19 | 208 | 0.002616 | 1.3e-05 | N
15-07-18 | 17:42 | 243:80083 | SHORT RURAL | Asset Failure | LV | 1 | 129 | 0.000673 | 5e-06 | N
15-07-18 | 19:48 | ZN965:PA13 | URBAN | Network business | Network error | 89 | 86 | 0.00508 | 5.9e-05 | N
15-07-18 | 19:48 | ZN965:PA28 | URBAN | Network business | Network error | 28 | 87 | 0.001612 | 1.9e-05 | N
15-07-18 | 20:26 | 520:48172 | SHORT RURAL | Asset Failure | LV | 4 | 167 | 0.003488 | 2.1e-05 | N
15-07-18 | 21:30 | ZN3154:PA18 | URBAN | Other | Other - Self Clearing Trigger | 81 | 70 | 0.003753 | 5.4e-05 | N
16-07-18 | 03:31 | ZN15005:PA12 | URBAN | Asset Failure | HV | 1,445 | 44 | 0.042078 | 0.000956 | N
16-07-18 | 06:49 | ZN12600:PA5 | URBAN | Other | Other | 5 | 266 | 0.00088 | 3e-06 | N
13-07-18 | 13:37 | 414:LD1 | URBAN | Other | Other - Self Clearing Trigger | 5 | 31 | 0.000103 | 3e-06 | N
13-07-18 | 13:37 | 414:LD734 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 503 | 0.002623 | 5e-06 | N
16-07-18 | 07:14 | ZN35900:PA1 | SHORT RURAL | Third Party | Other | 41 | 676 | 0.14447 | 0.000214 | N
16-07-18 | 13:21 | ZN36100:PA23 | URBAN | Third Party | Vehicle impact | 7 | 199 | 0.000922 | 5e-06 | N
16-07-18 | 13:36 | ZN630:PA41 | URBAN | Other | Other - Arcing | 2 | 267 | 0.000354 | 1e-06 | N
16-07-18 | 16:54 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 196 | 0.001022 | 5e-06 | N
16-07-18 | 17:15 | ZN15005:PA12 | URBAN | Other | Other | 1,445 | 90 | 0.086244 | 0.000956 | N
16-07-18 | 17:20 | 523:33501 | SHORT RURAL | Asset Failure | LV | 1 | 280 | 0.00146 | 5e-06 | N
16-07-18 | 17:54 | ZN14892:PA3 | SHORT RURAL | Other | Other | 1 | 138 | 0.000717 | 5e-06 | N
16-07-18 | 19:55 | ZN1290:PA11 | URBAN | Asset Failure | LV | 42 | 77 | 0.002151 | 2.8e-05 | N
16-07-18 | 19:56 | ZN965:PA43 | URBAN | Other | Other | 1 | 116 | 7.7e-05 | 1e-06 | N
16-07-18 | 20:26 | ZN4545:PA17 | URBAN | Asset Failure | HV | 1,262 | 60 | 0.050068 | 0.000835 | N
16-07-18 | 20:26 | ZN4545:PA19 | URBAN | Asset Failure | HV | 37 | 84 | 0.002057 | 2.4e-05 | N
16-07-18 | 20:26 | ZN4545:PA25 | URBAN | Asset Failure | HV | 1 | 84 | 5.6e-05 | 1e-06 | N
16-07-18 | 20:26 | ZN4545:PA26 | URBAN | Asset Failure | HV | 13 | 56 | 0.000484 | 9e-06 | N
16-07-18 | 20:47 | ZN10994:PA12 | URBAN | Other | Other - Self Clearing Trigger | 125 | 47 | 0.003917 | 8.3e-05 | N
16-07-18 | 22:25 | 813:89061 | LONG RURAL | Other | Other - Arcing | 1 | 584 | 0.20624 | 0.000353 | N
16-07-18 | 22:46 | ZN2568:PA8 | URBAN | Asset Failure | HV | 5 | 108 | 0.000357 | 3e-06 | N
17-07-18 | 00:44 | ZN3154:PA18 | URBAN | Other | Other - Self Clearing Trigger | 81 | 65 | 0.003494 | 5.4e-05 | N
17-07-18 | 05:15 | ZN14891:PA17 | SHORT RURAL | Asset Failure | LV | 1 | 194 | 0.001013 | 5e-06 | N
17-07-18 | 11:12 | 813:89061 | LONG RURAL | Asset Failure | HV | 7 | 158 | 0.39067 | 0.002473 | N
17-07-18 | 13:03 | ZN5868:PA30 | URBAN | Third Party | Vehicle impact | 29 | 72 | 0.001382 | 1.9e-05 | N
17-07-18 | 16:12 | ZN15005:PA2 | URBAN | Other | Other | 1 | 137 | 9.1e-05 | 1e-06 | N
17-07-18 | 17:30 | ZN12610:PA23 | URBAN | Third Party | Vehicle impact | 12 | 30 | 0.000238 | 8e-06 | N
17-07-18 | 17:18 | 807:74184 | SHORT RURAL | Asset Failure | LV | 1 | 237 | 0.001236 | 5e-06 | N
17-07-18 | 21:02 | 502:48010 | SHORT RURAL | Asset Failure | LV | 1 | 88 | 0.000459 | 5e-06 | N
17-07-18 | 23:47 | ZN14891:PA5 | SHORT RURAL | Asset Failure | LV | 80 | 53 | 0.022007 | 0.000417 | N
18-07-18 | 00:06 | ZN80:PA40 | URBAN | Asset Failure | HV | 3,918 | 100 | 0.2586 | 0.002593 | N
18-07-18 | 07:08 | ZN3922:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 68 | 113 | 0.040071 | 0.000355 | N
18-07-18 | 08:25 | 232:33407 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 250 | 0.005215 | 2.1e-05 | N
17-07-18 | 17:30 | ZN12610:PA23 | URBAN | Third Party | Vehicle impact | 35 | 30 | 0.000695 | 2.3e-05 | N
18-07-18 | 10:21 | ZN12610:PA6 | URBAN | Third Party | Vehicle impact | 1 | 399 | 0.000264 | 1e-06 | N
18-07-18 | 10:23 | 813:89055 | SHORT RURAL | Other | Other - Arcing | 1 | 277 | 0.001444 | 5e-06 | N
18-07-18 | 11:00 | ZN690:PA28 | URBAN | Asset Failure | LV | 148 | 105 | 0.010285 | 9.8e-05 | N
18-07-18 | 14:52 | ZN398:PA16 | URBAN | Third Party | Vehicle impact | 1 | 218 | 0.000144 | 1e-06 | N
18-07-18 | 16:30 | 514:18156 | SHORT RURAL | Asset Failure | HV | 4 | 115 | 0.002399 | 2.1e-05 | N
18-07-18 | 20:10 | ZN847:PA2 | URBAN | Third Party | Vehicle impact | 53 | 164 | 0.005761 | 3.5e-05 | N
18-07-18 | 21:02 | 238:34136 | URBAN | Third Party | Unauthorised access | 14 | 68 | 0.00063 | 9e-06 | N
19-07-18 | 01:35 | 242:81539 | URBAN | Animal | Animal impact | 1,590 | 43 | 0.044942 | 0.001052 | N
19-07-18 | 06:14 | ZN9118:PA17 | URBAN | Asset Failure | LV | 59 | 86 | 0.003341 | 3.9e-05 | N
19-07-18 | 08:11 | 523:33501 | SHORT RURAL | Third Party | Fire | 1 | 107 | 0.000556 | 5e-06 | N
19-07-18 | 10:25 | 239:82129 | SHORT RURAL | Third Party | Vehicle impact | 1 | 125 | 0.000651 | 5e-06 | N
19-07-18 | 11:06 | 213:33771 | URBAN | Other | Other | 1 | 95 | 6.3e-05 | 1e-06 | N
19-07-18 | 11:56 | ZN12610:PA10 | URBAN | Asset Failure | Distribution substation | 40 | 53 | 0.001414 | 2.6e-05 | N
19-07-18 | 14:09 | 205:12203 | URBAN | Other | Other | 1 | 137 | 9e-05 | 1e-06 | N
19-07-18 | 15:40 | 228:7490 | URBAN | Asset Failure | HV | 1,432 | 86 | 0.081342 | 0.000947 | N
19-07-18 | 15:53 | ZN15014:PA5 | URBAN | Other | Other | 1 | 75 | 4.9e-05 | 1e-06 | N
19-07-18 | 19:19 | ZN15006:PA16 | URBAN | Asset Failure | LV | 92 | 132 | 0.008034 | 6.1e-05 | N
19-07-18 | 19:59 | 261:81885 | URBAN | Third Party | Other | 1 | 73 | 4.8e-05 | 1e-06 | N
20-07-18 | 04:25 | ZN1673:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 545 | 0.015144 | 2.8e-05 | N
20-07-18 | 07:48 | ZN4545:PA39 | URBAN | Other | Other | 1 | 17 | 1.2e-05 | 1e-06 | N
20-07-18 | 09:55 | ZN2466:PA45 | URBAN | Other | Other - Self Clearing Trigger | 92 | 95 | 0.005773 | 6.1e-05 | N
20-07-18 | 10:33 | 512:48049 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 282 | 0.00294 | 1e-05 | N
20-07-18 | 18:00 | ZN3155:PA23 | URBAN | Vegetation | Vegetation Grow In | 92 | 440 | 0.026781 | 6.1e-05 | N
20-07-18 | 16:44 | 509:33395 | LONG RURAL | Third Party | Vehicle impact | 65 | 198 | 4.5445 | 0.022952 | N
20-07-18 | 12:23 | ZN9700:PA15 | URBAN | Weather |  | 30 | 282 | 0.005597 | 2e-05 | N
20-07-18 | 12:54 | ZN10991:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 126 | 0.002913 | 2.3e-05 | N
20-07-18 | 13:03 | ZN1287:PA15 | URBAN | Vegetation | Vegetation Grow In | 1 | 446 | 0.000295 | 1e-06 | N
20-07-18 | 12:59 | 509:33395 | LONG RURAL | Asset Failure | HV | 92 | 243 | 7.8856 | 0.032486 | N
20-07-18 | 13:28 | ZN10999:PA16 | URBAN | Asset Failure | LV | 1 | 31 | 2.1e-05 | 1e-06 | N
20-07-18 | 13:46 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 88 | 0.001631 | 1.9e-05 | N
20-07-18 | 13:52 | 243:80081 | SHORT RURAL | Other | Other | 1 | 86 | 0.000446 | 5e-06 | N
20-07-18 | 14:19 | 243:80081 | SHORT RURAL | Other | Other | 1 | 61 | 0.000318 | 5e-06 | N
20-07-18 | 14:52 | 524:33578 | URBAN | Other | Other | 1 | 46 | 3e-05 | 1e-06 | N
20-07-18 | 14:55 | 216:10723 | URBAN | Other | Other | 1 | 111 | 7.4e-05 | 1e-06 | N
20-07-18 | 15:09 | ZN35370:PA4 | SHORT RURAL | Other | Other | 142 | 194 | 0.14389 | 0.00074 | N
20-07-18 | 15:44 | 229:34995 | SHORT RURAL | Other | Other | 1 | 80 | 0.000418 | 5e-06 | N
20-07-18 | 17:08 | ZN15010:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 348 | 0.00023 | 1e-06 | N
20-07-18 | 17:22 | 213:33771 | URBAN | Asset Failure | LV | 7 | 130 | 0.000602 | 5e-06 | N
20-07-18 | 17:29 | ZN12620:PA3 | URBAN | Asset Failure | LV | 1 | 259 | 0.000172 | 1e-06 | N
20-07-18 | 17:06 | ZN10999:PA36 | URBAN | Asset Failure | LV | 23 | 994 | 0.015125 | 1.5e-05 | N
20-07-18 | 19:28 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 5 | 204 | 0.000675 | 3e-06 | N
20-07-18 | 19:34 | ZN2602:PA4 | URBAN | Other | Other - Arcing | 1 | 198 | 0.000131 | 1e-06 | N
20-07-18 | 20:37 | ZN901:PA13 | URBAN | Asset Failure | LV | 127 | 103 | 0.008654 | 8.4e-05 | N
21-07-18 | 09:45 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 9 | 225 | 0.010555 | 4.7e-05 | N
21-07-18 | 08:27 | ZN129:PA64 | URBAN | Asset Failure | LV | 1 | 438 | 0.00029 | 1e-06 | N
21-07-18 | 10:57 | ZN12600:PA9 | SHORT RURAL | Other | Other | 1 | 103 | 0.000535 | 5e-06 | N
21-07-18 | 11:40 | ZN3154:PA11 | URBAN | Other | Other | 1 | 129 | 8.5e-05 | 1e-06 | N
21-07-18 | 13:05 | 239:82132 | URBAN | Asset Failure | LV | 1 | 374 | 0.000248 | 1e-06 | N
21-07-18 | 16:09 | ZN15012:PA8 | URBAN | Other | Other | 1 | 72 | 4.7e-05 | 1e-06 | N
21-07-18 | 17:17 | ZN965:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 229 | 0.006666 | 2.9e-05 | N
21-07-18 | 17:25 | ZN847:PA22 | URBAN | Other | Other - Self Clearing Trigger | 35 | 140 | 0.003242 | 2.3e-05 | N
21-07-18 | 17:51 | ZN10999:PA12 | URBAN | Asset Failure | LV | 1 | 262 | 0.000174 | 1e-06 | N
21-07-18 | 22:12 | 221:11893 | URBAN | Third Party | Vehicle impact | 116 | 549 | 0.042143 | 7.7e-05 | N
22-07-18 | 08:04 | 512:48046 | SHORT RURAL | Asset Failure | Zone substation | 853 | 89 | 0.39674 | 0.004446 | N
22-07-18 | 08:04 | 512:48049 | SHORT RURAL | Asset Failure | Zone substation | 2,356 | 25 | 0.3093 | 0.01228 | N
22-07-18 | 08:04 | 526:34637 | SHORT RURAL | Asset Failure | Zone substation | 63 | 4 | 0.001313 | 0.000328 | N
22-07-18 | 16:00 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 37 | 20 | 0.003857 | 0.000193 | N
22-07-18 | 09:34 | ZN10998:PA25 | URBAN | Asset Failure | LV | 2 | 610 | 0.000807 | 1e-06 | N
22-07-18 | 10:09 | ZN10994:PA4 | URBAN | Asset Failure | HV | 208 | 81 | 0.011147 | 0.000138 | N
22-07-18 | 11:30 | 810:74054 | LONG RURAL | Asset Failure | LV | 1 | 130 | 0.045904 | 0.000353 | N
22-07-18 | 17:43 | 220:8689 | URBAN | Other | Other | 1 | 136 | 9e-05 | 1e-06 | N
22-07-18 | 18:13 | ZN15014:PA19 | URBAN | Asset Failure | LV | 43 | 341 | 0.00969 | 2.8e-05 | N
22-07-18 | 21:48 | 524:33570 | SHORT RURAL | Asset Failure | LV | 60 | 116 | 0.036387 | 0.000313 | N
23-07-18 | 00:45 | ZN15011:PA2 | URBAN | Network business | Network error | 22 | 125 | 0.001819 | 1.5e-05 | N
23-07-18 | 08:46 | ZN15014:PA19 | URBAN | Asset Failure | LV | 14 | 299 | 0.002769 | 9e-06 | N
23-07-18 | 10:33 | ZN3425:PA28 | SHORT RURAL | Asset Failure | LV | 1 | 461 | 0.002403 | 5e-06 | N
23-07-18 | 11:18 | ZN15006:PA13 | URBAN | Asset Failure | HV | 1,376 | 104 | 0.094511 | 0.00091 | N
23-07-18 | 12:07 | ZN14891:PA20 | SHORT RURAL | Other | Other | 1 | 412 | 0.002148 | 5e-06 | N
23-07-18 | 12:29 | ZN14144:PA7 | SHORT RURAL | Other | Other | 1 | 149 | 0.000774 | 5e-06 | N
23-07-18 | 13:47 | ZN12580:PA16 | URBAN | Other | Other | 1 | 230 | 0.000152 | 1e-06 | N
23-07-18 | 13:59 | ZN9035:PA1 | URBAN | Third Party | Vehicle impact | 9 | 151 | 0.000899 | 6e-06 | N
23-07-18 | 19:30 | 243:80075 | SHORT RURAL | Third Party | Unauthorised access | 1 | 70 | 0.000365 | 5e-06 | N
23-07-18 | 16:46 | 216:10728 | URBAN | Other | Other | 1 | 54 | 3.6e-05 | 1e-06 | N
23-07-18 | 16:49 | ZN10998:PA16 | SHORT RURAL | Network business | Network error | 74 | 329 | 0.12687 | 0.000386 | N
23-07-18 | 16:49 | ZN10998:PA25 | URBAN | Network business | Network error | 87 | 221 | 0.012718 | 5.8e-05 | N
23-07-18 | 16:49 | ZN10999:PA38 | URBAN | Network business | Network error | 36 | 281 | 0.006691 | 2.4e-05 | N
23-07-18 | 17:21 | ZN180:PA34 | URBAN | Asset Failure | LV | 51 | 1,433 | 0.048352 | 3.4e-05 | N
23-07-18 | 18:04 | 258:80778 | URBAN | Asset Failure | LV | 2 | 66 | 8.7e-05 | 1e-06 | N
24-07-18 | 08:57 | 232:11455 | SHORT RURAL | Asset Failure | HV | 103 | 433 | 0.2324 | 0.000537 | N
24-07-18 | 10:02 | ZN188:PA16 | URBAN | Asset Failure | LV | 62 | 46 | 0.001887 | 4.1e-05 | N
24-07-18 | 10:13 | ZN630:PA31 | URBAN | Other | Other - Arcing | 6 | 437 | 0.001734 | 4e-06 | N
24-07-18 | 11:04 | 216:10728 | URBAN | Asset Failure | LV | 1 | 96 | 6.3e-05 | 1e-06 | N
24-07-18 | 12:52 | 526:34637 | SHORT RURAL | Asset Failure | HV | 158 | 52 | 0.042709 | 0.000823 | N
24-07-18 | 12:52 | 526:34644 | SHORT RURAL | Asset Failure | HV | 2 | 84 | 0.00087 | 1e-05 | N
24-07-18 | 16:35 | ZN4990:PA53 54GHJ | CBD | Other | Other | 1 | 171 | 0.005526 | 3.2e-05 | N
24-07-18 | 18:50 | 238:34148 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 10 | 29 | 0.001511 | 5.2e-05 | N
25-07-18 | 02:24 | ZN847:PA7 | URBAN | Animal | Animal impact | 1,315 | 76 | 0.066104 | 0.00087 | N
25-07-18 | 07:51 | 814:82283 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 164 | 0.001707 | 1e-05 | N
25-07-18 | 09:21 | 508:82576 | SHORT RURAL | Asset Failure | Distribution substation | 8 | 123 | 0.005139 | 4.2e-05 | N
25-07-18 | 09:25 | ZN15001:PA3 | URBAN | Other | Other | 1 | 102 | 6.8e-05 | 1e-06 | N
25-07-18 | 13:53 | 512:48049 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 6 | 212 | 0.006621 | 3.1e-05 | N
25-07-18 | 14:22 | ZN129:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 105 | 6.9e-05 | 1e-06 | N
25-07-18 | 14:27 | ZN1673:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 518 | 0.000343 | 1e-06 | N
25-07-18 | 18:11 | 513:48059 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 83 | 0.000869 | 1e-05 | N
25-07-18 | 21:19 | 512:48049 | SHORT RURAL | Other | Other | 1 | 93 | 0.000482 | 5e-06 | N
26-07-18 | 02:40 | ZN36300:PA3 | URBAN | Other | Other - Self Clearing Trigger | 2,017 | 105 | 0.13957 | 0.001334 | N
26-07-18 | 03:33 | 224:80346 | URBAN | Animal | Animal impact | 846 | 85 | 0.047554 | 0.000559 | N
26-07-18 | 07:20 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 90 | 0.000937 | 1e-05 | N
25-07-18 | 12:00 | ZN263:PA33 34KLM | CBD | Third Party | Dig-in | 1 | 240 | 0.00775 | 3.2e-05 | N
26-07-18 | 09:49 | ZN36300:PA11 | URBAN | Asset Failure | LV | 1 | 400 | 0.000265 | 1e-06 | N
26-07-18 | 12:35 | ZN3154:PA4 | URBAN | Third Party | Vehicle impact | 1 | 176 | 0.000116 | 1e-06 | N
26-07-18 | 14:20 | 216:10722 | SHORT RURAL | Asset Failure | LV | 1 | 160 | 0.000832 | 5e-06 | N
26-07-18 | 15:01 | ZN9700:PA20 | URBAN | Third Party | Vehicle impact | 4 | 169 | 0.000447 | 3e-06 | N
26-07-18 | 02:45 | ZN1673:PA14 | URBAN | Asset Failure | LV | 20 | 45 | 0.000595 | 1.3e-05 | N
26-07-18 | 15:59 | 223:14395 | SHORT RURAL | Asset Failure | Distribution substation | 4 | 61 | 0.00127 | 2.1e-05 | N
26-07-18 | 16:17 | 512:48049 | SHORT RURAL | Asset Failure | HV | 36 | 306 | 0.057334 | 0.000187 | N
26-07-18 | 16:21 | 520:48172 | SHORT RURAL | Third Party | Vehicle impact | 173 | 28 | 0.024935 | 0.0009 | N
26-07-18 | 16:40 | ZN36100:PA27 | URBAN | Third Party | Dig-in | 114 | 45 | 0.003392 | 7.5e-05 | N
27-07-18 | 01:20 | ZN14892:PA13 | SHORT RURAL | Asset Failure | LV | 85 | 380 | 0.16932 | 0.000445 | N
27-07-18 | 06:10 | 807:74180 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 41 | 311 | 0.066742 | 0.000215 | N
27-07-18 | 08:23 | ZN384:PA73 | URBAN | Other | Other - Self Clearing Trigger | 17 | 196 | 0.002202 | 1.1e-05 | N
27-07-18 | 08:51 | 240:34843 | URBAN | Other | Other - Arcing | 1 | 312 | 0.000206 | 1e-06 | N
27-07-18 | 09:02 | 240:34843 | URBAN | Other | Other - Arcing | 1 | 298 | 0.000197 | 1e-06 | N
27-07-18 | 14:28 | 243:80083 | SHORT RURAL | Third Party | Vehicle impact | 1 | 211 | 0.001108 | 5e-06 | N
27-07-18 | 14:32 | ZN3288:PA41 42KLM | CBD | Asset Failure | LV | 8 | 208 | 0.053684 | 0.000258 | N
27-07-18 | 18:40 | ZN9900:PA20 | URBAN | Asset Failure | HV | 15 | 280 | 0.002777 | 1e-05 | N
27-07-18 | 21:22 | ZN15005:PA2 | URBAN | Asset Failure | LV | 1 | 352 | 0.000233 | 1e-06 | N
27-07-18 | 21:50 | 810:74054 | LONG RURAL | Asset Failure | HV | 23 | 142 | 1.1506 | 0.00811 | N
27-07-18 | 23:24 | 206:34440 | URBAN | Animal | Animal impact | 73 | 56 | 0.002703 | 4.8e-05 | N
28-07-18 | 02:00 | ZN2466:PA29 | URBAN | Asset Failure | Distribution substation | 11 | 44 | 0.00032 | 7e-06 | N
28-07-18 | 07:27 | ZN847:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 303 | 0.0002 | 1e-06 | N
28-07-18 | 08:15 | ZN8100:PA2 | URBAN | Asset Failure | LV | 1 | 235 | 0.000155 | 1e-06 | N
28-07-18 | 15:38 | ZN1788:PA15 | URBAN | Third Party | Dig-in | 1 | 37 | 2.4e-05 | 1e-06 | N
28-07-18 | 15:38 | ZN1788:PA29 | URBAN | Third Party | Dig-in | 13 | 37 | 0.000317 | 9e-06 | N
28-07-18 | 21:38 | ZN2635:PA57 | URBAN | Animal | Animal impact | 1 | 104 | 6.9e-05 | 1e-06 | N
28-07-18 | 21:38 | ZN4545:PA31 | URBAN | Animal | Animal impact | 3,013 | 104 | 0.20722 | 0.001992 | N
29-07-18 | 04:24 | 261:81879 | URBAN | Animal | Animal impact | 103 | 151 | 0.010285 | 6.8e-05 | N
29-07-18 | 07:45 | 205:12210 | URBAN | Asset Failure | LV | 1 | 180 | 0.000119 | 1e-06 | N
29-07-18 | 08:52 | ZN4545:PA44 | URBAN | Asset Failure | LV | 1 | 308 | 0.000204 | 1e-06 | N
29-07-18 | 11:15 | 221:11899 | SHORT RURAL | Other | Other | 1 | 120 | 0.000623 | 5e-06 | N
29-07-18 | 13:59 | 256:80644 | URBAN | Other | Other | 19 | 35 | 0.00044 | 1.3e-05 | N
29-07-18 | 13:59 | 257:81999 | URBAN | Other | Other | 938 | 35 | 0.02171 | 0.00062 | N
29-07-18 | 15:34 | ZN9700:PA17 | URBAN | Asset Failure | LV | 9 | 151 | 0.000899 | 6e-06 | N
29-07-18 | 18:08 | ZN1788:PA32 | URBAN | Other | Other | 1 | 62 | 4.1e-05 | 1e-06 | N
29-07-18 | 19:36 | ZN3154:PA18 | URBAN | Other | Other | 1 | 92 | 6.1e-05 | 1e-06 | N
30-07-18 | 08:27 | ZN14892:PA5 | URBAN | Other | Other - Self Clearing Trigger | 7 | 298 | 0.001379 | 5e-06 | N
30-07-18 | 09:35 | 214:8669 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 49 | 3.2e-05 | 1e-06 | N
30-07-18 | 10:37 | ZN2568:PA25 | URBAN | Overloads |  | 1 | 82 | 5.4e-05 | 1e-06 | N
30-07-18 | 13:49 | ZN15011:PA10 | URBAN | Asset Failure | LV | 39 | 171 | 0.004409 | 2.6e-05 | N
30-07-18 | 15:02 | 509:33399 | SHORT RURAL | Asset Failure | HV | 1 | 328 | 0.001707 | 5e-06 | N
30-07-18 | 15:10 | ZN262:PA34 | URBAN | Third Party | Fire | 88 | 320 | 0.018606 | 5.8e-05 | N
30-07-18 | 15:37 | ZN167:PA21 | URBAN | Vegetation | Vegetation Grow In | 1 | 1,043 | 0.00069 | 1e-06 | N
30-07-18 | 15:45 | ZN690:PA10 | URBAN | Other | Other - Arcing | 1 | 487 | 0.000322 | 1e-06 | N
30-07-18 | 15:59 | ZN36100:PA12 | URBAN | Asset Failure | LV | 1 | 473 | 0.000313 | 1e-06 | N
30-07-18 | 16:50 | ZN2835:PA24 | URBAN | Asset Failure | HV | 257 | 95 | 0.016195 | 0.00017 | N
31-07-18 | 02:20 | ZN2568:PA14 | URBAN | Asset Failure | HV | 1,477 | 59 | 0.057986 | 0.000977 | N
31-07-18 | 02:41 | ZN9037:PA2 | URBAN | Other | Other - Self Clearing Trigger | 1,051 | 71 | 0.049421 | 0.000695 | N
31-07-18 | 04:49 | 227:13018 | URBAN | Animal | Animal impact | 89 | 196 | 0.011525 | 5.9e-05 | N
31-07-18 | 07:29 | 220:8691 | URBAN | Other | Other - Self Clearing Trigger | 108 | 75 | 0.005388 | 7.1e-05 | N
31-07-18 | 07:20 | ZN9700:PA23 | URBAN | Asset Failure | LV | 4 | 265 | 0.000701 | 3e-06 | N
31-07-18 | 07:43 | ZN4545:PA28 | URBAN | Asset Failure | LV | 2 | 287 | 0.000379 | 1e-06 | N
31-07-18 | 08:41 | 264:81241 | URBAN | Other | Other - Self Clearing Trigger | 19 | 174 | 0.002187 | 1.3e-05 | N
31-07-18 | 10:25 | ZN3154:PA5 | URBAN | Other | Other - Arcing | 1,153 | 11 | 0.008744 | 0.000763 | N
31-07-18 | 09:57 | 524:33570 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 217 | 0.00113 | 5e-06 | N
31-07-18 | 10:15 | 813:89062 | SHORT RURAL | Third Party | Other | 1 | 172 | 0.000895 | 5e-06 | N
31-07-18 | 13:11 | ZN12570:PA37 | SHORT RURAL | Other | Other | 1 | 205 | 0.001064 | 5e-06 | N
31-07-18 | 13:45 | ZN15006:PA9 | URBAN | Asset Failure | HV | 2,602 | 63 | 0.10759 | 0.001721 | N
31-07-18 | 18:09 | ZN7481:PA9 | URBAN | Third Party | Other | 121 | 66 | 0.005271 | 8e-05 | N
31-07-18 | 22:07 | ZN9037:PA16 | URBAN | Asset Failure | Distribution substation | 97 | 72 | 0.004621 | 6.4e-05 | N
01-08-18 | 01:56 | ZN9700:PA11 | URBAN | Third Party | Dig-in | 1,962 | 55 | 0.070851 | 0.001297 | N
01-08-18 | 08:06 | 258:80775 | URBAN | Weather |  | 1 | 174 | 0.000115 | 1e-06 | N
01-08-18 | 08:16 | ZN35800:PA2 | URBAN | Asset Failure | LV | 60 | 174 | 0.006902 | 4e-05 | N
31-07-18 | 12:20 | ZN2310:PA55 | URBAN | Other | Other | 45 | 40 | 0.001191 | 3e-05 | N
01-08-18 | 13:10 | 513:48059 | SHORT RURAL | Asset Failure | LV | 1 | 114 | 0.000591 | 5e-06 | N
01-08-18 | 16:03 | ZN15006:PA13 | URBAN | Other | Other | 1 | 402 | 0.000266 | 1e-06 | N
01-08-18 | 18:29 | ZN3425:PA30 | URBAN | Third Party | Vehicle impact | 1 | 420 | 0.000278 | 1e-06 | N
02-08-18 | 06:53 | ZN2310:PA55 | URBAN | Third Party | Vehicle impact | 1 | 426 | 0.000282 | 1e-06 | N
02-08-18 | 07:38 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 202 | 0.001051 | 5e-06 | N
02-08-18 | 11:34 | 502:48008 | URBAN | Asset Failure | LV | 5 | 326 | 0.001078 | 3e-06 | N
21-07-18 | 19:35 | ZN15006:PA16 | URBAN | Asset Failure | LV | 92 | 249 | 0.015156 | 6.1e-05 | N
02-08-18 | 12:33 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 267 | 0.09408 | 0.000352 | N
02-08-18 | 12:48 | ZN1193:PA12 | URBAN | Other | Other - Self Clearing Trigger | 184 | 92 | 0.011191 | 0.000122 | N
02-08-18 | 12:48 | ZN3154:PA16 | URBAN | Other | Other - Self Clearing Trigger | 607 | 86 | 0.034592 | 0.000401 | N
02-08-18 | 13:29 | ZN15001:PA3 | URBAN | Third Party | Dig-in | 4 | 501 | 0.001325 | 3e-06 | N
02-08-18 | 19:14 | 257:81988 | URBAN | Third Party | Vehicle impact | 4 | 231 | 0.000611 | 3e-06 | N
02-08-18 | 15:29 | ZN340:PA14 | URBAN | Asset Failure | LV | 1 | 361 | 0.000239 | 1e-06 | N
02-08-18 | 18:24 | ZN9035:PA1 | URBAN | Animal | Animal impact | 462 | 76 | 0.023213 | 0.000305 | N
02-08-18 | 18:24 | ZN9035:PA10 | URBAN | Animal | Animal impact | 603 | 77 | 0.030696 | 0.000399 | N
02-08-18 | 18:24 | ZN9035:PA11 | URBAN | Animal | Animal impact | 1,968 | 77 | 0.10018 | 0.001301 | N
02-08-18 | 18:24 | ZN9035:PA2 | URBAN | Animal | Animal impact | 810 | 76 | 0.040698 | 0.000535 | N
02-08-18 | 18:24 | ZN9035:PA4 | URBAN | Animal | Animal impact | 2,041 | 77 | 0.1039 | 0.001349 | N
02-08-18 | 18:24 | ZN9035:PA5 | URBAN | Animal | Animal impact | 324 | 76 | 0.016279 | 0.000214 | N
02-08-18 | 18:24 | ZN9035:PA7 | URBAN | Animal | Animal impact | 1,119 | 77 | 0.056963 | 0.00074 | N
02-08-18 | 18:24 | ZN9035:PA8 | URBAN | Animal | Animal impact | 112 | 77 | 0.005701 | 7.4e-05 | N
02-08-18 | 18:24 | ZN9118:PA7 | URBAN | Animal | Animal impact | 198 | 77 | 0.010079 | 0.000131 | N
02-08-18 | 18:24 | ZN9550:PA11 | URBAN | Animal | Animal impact | 1 | 77 | 5.1e-05 | 1e-06 | N
02-08-18 | 19:41 | ZN9118:PA7 | URBAN | Third Party | Dig-in | 1 | 1,227 | 0.000811 | 1e-06 | N
02-08-18 | 19:03 | ZN2635:PA38 | URBAN | Asset Failure | LV | 55 | 67 | 0.002426 | 3.6e-05 | N
02-08-18 | 23:35 | ZN711:PA28 | URBAN | Other | Other | 79 | 10 | 0.000522 | 5.2e-05 | N
02-08-18 | 23:35 | ZN711:PA33 | URBAN | Other | Other | 1 | 5 | 3e-06 | 1e-06 | N
03-08-18 | 01:24 | ZN13000:PA1 | URBAN | Asset Failure | HV | 34 | 366 | 0.008224 | 2.2e-05 | N
03-08-18 | 01:24 | ZN13000:PA2 | SHORT RURAL | Asset Failure | HV | 1 | 366 | 0.001904 | 5e-06 | N
03-08-18 | 07:04 | ZN195:PA11 | URBAN | Other | Other | 99 | 181 | 0.011832 | 6.5e-05 | N
03-08-18 | 07:43 | 270:83587 | URBAN | Other | Other | 1 | 68 | 4.5e-05 | 1e-06 | N
03-08-18 | 07:58 | 270:83587 | URBAN | Other | Other | 1 | 53 | 3.5e-05 | 1e-06 | N
03-08-18 | 08:13 | 214:8667 | URBAN | Asset Failure | LV | 1 | 287 | 0.00019 | 1e-06 | N
03-08-18 | 10:52 | ZN35600:PA9 | URBAN | Other | Other | 1 | 218 | 0.000144 | 1e-06 | N
03-08-18 | 11:52 | ZN262:PA42 | URBAN | Third Party | Other | 1 | 58 | 3.8e-05 | 1e-06 | N
03-08-18 | 13:15 | 515:35193 | SHORT RURAL | Asset Failure | HV | 10 | 30 | 0.001561 | 5.2e-05 | N
03-08-18 | 13:24 | ZN12570:PA39 | URBAN | Other | Other | 1 | 62 | 4.1e-05 | 1e-06 | N
03-08-18 | 23:40 | ZN15004:PA1 | URBAN | Asset Failure | LV | 72 | 519 | 0.024714 | 4.8e-05 | N
04-08-18 | 07:56 | ZN3288:PA41 42KLM | CBD | Asset Failure | LV | 12 | 184 | 0.071549 | 0.000389 | N
04-08-18 | 09:20 | ZN2400:PA15 | SHORT RURAL | Other | Other | 1 | 114 | 0.00059 | 5e-06 | N
04-08-18 | 16:36 | ZN12600:PA12 | URBAN | Asset Failure | LV | 1 | 324 | 0.000214 | 1e-06 | N
04-08-18 | 22:29 | ZN10998:PA2 | URBAN | Other | Other - Self Clearing Trigger | 42 | 105 | 0.00292 | 2.8e-05 | N
05-08-18 | 06:05 | ZN2310:PA3 | URBAN | Third Party | Vehicle impact | 72 | 5 | 0.000238 | 4.8e-05 | N
05-08-18 | 09:20 | ZN2310:PA55 | URBAN | Third Party | Vehicle impact | 45 | 545 | 0.016212 | 3e-05 | N
05-08-18 | 09:17 | 522:83132 | SHORT RURAL | Asset Failure | HV | 2 | 243 | 0.002548 | 1e-05 | N
05-08-18 | 09:21 | ZN2635:PA59 | URBAN | Asset Failure | LV | 3 | 459 | 0.00091 | 2e-06 | N
05-08-18 | 12:16 | 261:81886 | URBAN | Third Party | Vehicle impact | 3 | 284 | 0.000563 | 2e-06 | N
05-08-18 | 15:19 | ZN690:PA36 | URBAN | Asset Failure | HV | 1,302 | 104 | 0.089511 | 0.000861 | N
05-08-18 | 17:22 | ZN9252:PA25 | URBAN | Network business | Network error | 127 | 1,628 | 0.13664 | 8.4e-05 | N
05-08-18 | 19:14 | ZN12620:PA13 | SHORT RURAL | Asset Failure | LV | 17 | 123 | 0.010962 | 8.9e-05 | N
03-08-18 | 11:45 | 227:13014 | SHORT RURAL | Third Party | Other | 2 | 205 | 0.002133 | 1e-05 | N
01-08-18 | 13:25 | 524:33572 | SHORT RURAL | Network business | Network error | 1,608 | 4 | 0.033466 | 0.008366 | N
01-08-18 | 13:25 | 524:33576 | SHORT RURAL | Network business | Network error | 178 | 4 | 0.003705 | 0.000926 | N
04-08-18 | 13:00 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 220 | 0.002285 | 1e-05 | N
06-08-18 | 11:38 | ZN2568:PA27 | URBAN | Other | Other - Arcing | 1 | 352 | 0.000233 | 1e-06 | N
06-08-18 | 12:39 | ZN15014:PA9 | URBAN | Third Party | Other | 1 | 351 | 0.000232 | 1e-06 | N
06-08-18 | 13:58 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 60 | 0.000312 | 5e-06 | N
06-08-18 | 16:56 | 257:81999 | URBAN | Asset Failure | LV | 102 | 143 | 0.009638 | 6.7e-05 | N
06-08-18 | 17:00 | ZN1610:PA19 | URBAN | Third Party | Vehicle impact | 3 | 20 | 4e-05 | 2e-06 | N
06-08-18 | 18:10 | ZN10995:PA1 | URBAN | Asset Failure | LV | 85 | 165 | 0.00927 | 5.6e-05 | N
06-08-18 | 19:10 | ZN12570:PA21 | URBAN | Animal | Animal impact | 2,300 | 163 | 0.24716 | 0.00152 | N
06-08-18 | 19:19 | ZN15006:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 66 | 0.002655 | 4e-05 | N
06-08-18 | 19:28 | ZN15013:PA8 | URBAN | Other | Other - Arcing | 1 | 991 | 0.000655 | 1e-06 | N
06-08-18 | 20:49 | ZN10994:PA19 | URBAN | Animal | Animal impact | 1,018 | 85 | 0.057201 | 0.000673 | N
06-08-18 | 22:40 | ZN35900:PA24 | URBAN | Network business | Network error | 71 | 105 | 0.004928 | 4.7e-05 | N
06-08-18 | 22:43 | ZN3472:PA33 | URBAN | Network business | Network error | 111 | 101 | 0.007413 | 7.3e-05 | N
07-08-18 | 00:39 | ZN10991:PA1 | URBAN | Animal | Animal impact | 1,519 | 61 | 0.061253 | 0.001004 | N
07-08-18 | 05:36 | 257:81999 | URBAN | Asset Failure | LV | 96 | 139 | 0.008821 | 6.3e-05 | N
07-08-18 | 06:47 | ZN965:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 483 | 0.00925 | 1.9e-05 | N
07-08-18 | 10:24 | ZN9037:PA8 | URBAN | Asset Failure | LV | 1 | 216 | 0.000143 | 1e-06 | N
07-08-18 | 11:03 | 511:29877 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 357 | 0.001853 | 5e-06 | N
07-08-18 | 11:29 | ZN12570:PA34 | SHORT RURAL | Third Party | Other | 853 | 84 | 0.37383 | 0.004429 | N
07-08-18 | 12:31 | ZN36100:PA7 | URBAN | Other | Other - Arcing | 1 | 268 | 0.000177 | 1e-06 | N
07-08-18 | 12:34 | ZN2635:PA39 | URBAN | Third Party | Unauthorised access | 1 | 167 | 0.00011 | 1e-06 | N
07-08-18 | 16:10 | ZN1193:PA15 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 46 | 75 | 0.017915 | 0.000239 | N
07-08-18 | 13:05 | ZN965:PA42 | URBAN | Third Party | Dig-in | 3 | 310 | 0.000615 | 2e-06 | N
07-08-18 | 13:08 | ZN14891:PA12 | SHORT RURAL | Asset Failure | HV | 385 | 150 | 0.30024 | 0.001999 | N
07-08-18 | 13:17 | ZN3922:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,087 | 0.000719 | 1e-06 | N
07-08-18 | 13:36 | ZN9245:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 144 | 0.007477 | 5.2e-05 | N
07-08-18 | 13:36 | ZN1287:PA24 | URBAN | Asset Failure | LV | 100 | 213 | 0.014097 | 6.6e-05 | N
07-08-18 | 13:57 | ZN965:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 81 | 5.4e-05 | 1e-06 | N
07-08-18 | 15:09 | ZN4545:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 446 | 0.000295 | 1e-06 | N
07-08-18 | 16:05 | ZN10993:PA23 | URBAN | Asset Failure | LV | 1 | 234 | 0.000155 | 1e-06 | N
07-08-18 | 16:22 | ZN4545:PA26 | URBAN | Weather |  | 7 | 288 | 0.001333 | 5e-06 | N
07-08-18 | 16:32 | 520:48172 | SHORT RURAL | Asset Failure | HV | 2 | 388 | 0.00403 | 1e-05 | N
07-08-18 | 16:45 | ZN14144:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 200 | 0.007263 | 3.6e-05 | N
07-08-18 | 16:45 | ZN4545:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 375 | 0.000248 | 1e-06 | N
06-08-18 | 23:50 | ZN12570:PA21 | URBAN | Asset Failure | HV | 47 | 90 | 0.002796 | 3.1e-05 | N
07-08-18 | 19:56 | 220:8691 | URBAN | Third Party | Vehicle impact | 1 | 120 | 7.9e-05 | 1e-06 | N
07-08-18 | 20:15 | ZN15006:PA16 | URBAN | Asset Failure | LV | 1 | 824 | 0.000545 | 1e-06 | N
07-08-18 | 22:08 | ZN262:PA42 | URBAN | Other | Other - Arcing | 1 | 771 | 0.00051 | 1e-06 | N
07-08-18 | 23:25 | 210:83465 | URBAN | Other | Other - Self Clearing Trigger | 87 | 59 | 0.003417 | 5.8e-05 | N
08-08-18 | 01:09 | ZN9245:PA1 | URBAN | Other | Other - Self Clearing Trigger | 552 | 195 | 0.070997 | 0.000365 | N
08-08-18 | 01:09 | ZN9245:PA15 | URBAN | Other | Other - Self Clearing Trigger | 958 | 174 | 0.11019 | 0.000633 | N
08-08-18 | 08:57 | ZN12580:PA1 | URBAN | Other | Other | 1 | 245 | 0.000162 | 1e-06 | N
08-08-18 | 09:04 | 801:74121 | LONG RURAL | Asset Failure | LV | 3 | 56 | 0.059134 | 0.001056 | N
08-08-18 | 10:51 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 64 | 0.000331 | 5e-06 | N
08-08-18 | 11:44 | ZN9252:PA21 | URBAN | Asset Failure | LV | 1 | 1,062 | 0.000702 | 1e-06 | N
08-08-18 | 11:49 | ZN9245:PA1 | URBAN | Other | Other - Self Clearing Trigger | 46 | 110 | 0.003349 | 3e-05 | N
08-08-18 | 12:03 | ZN9245:PA21 | URBAN | Network business | Network error | 54 | 251 | 0.008976 | 3.6e-05 | N
08-08-18 | 13:40 | ZN9700:PA20 | URBAN | Third Party | Other | 64 | 40 | 0.001692 | 4.2e-05 | N
08-08-18 | 14:51 | ZN35370:PA2 | SHORT RURAL | Asset Failure | LV | 1 | 219 | 0.001136 | 5e-06 | N
08-08-18 | 14:52 | ZN180:PA24 | URBAN | Third Party | Dig-in | 1,080 | 94 | 0.066921 | 0.000714 | N
08-08-18 | 14:56 | ZN35555:PA20 | URBAN | Asset Failure | HV | 1,662 | 76 | 0.083542 | 0.001099 | N
08-08-18 | 15:52 | ZN80:PA37 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 98 | 0.003952 | 4e-05 | N
08-08-18 | 16:39 | ZN1285:PA20 | URBAN | Asset Failure | LV | 1 | 766 | 0.000507 | 1e-06 | N
08-08-18 | 16:40 | 240:34849 | URBAN | Other | Other | 1 | 60 | 3.9e-05 | 1e-06 | N
08-08-18 | 16:51 | ZN35400:PA81 | URBAN | Third Party | Vehicle impact | 1 | 263 | 0.000174 | 1e-06 | N
08-08-18 | 17:17 | ZN1285:PA20 | URBAN | Asset Failure | LV | 1 | 728 | 0.000482 | 1e-06 | N
08-08-18 | 18:25 | 205:12205 | URBAN | Other | Other | 1 | 76 | 5e-05 | 1e-06 | N
08-08-18 | 21:02 | ZN35900:PA24 | URBAN | Other | Other - Self Clearing Trigger | 71 | 43 | 0.002002 | 4.7e-05 | N
08-08-18 | 22:35 | ZN35900:PA24 | URBAN | Asset Failure | LV | 71 | 925 | 0.043415 | 4.7e-05 | N
09-08-18 | 00:14 | ZN340:PA19 | URBAN | Third Party | Vehicle impact | 1 | 766 | 0.000506 | 1e-06 | N
09-08-18 | 00:46 | ZN901:PA20 | URBAN | Asset Failure | HV | 1,510 | 50 | 0.049616 | 0.000998 | N
08-08-18 | 13:55 | ZN9700:PA20 | URBAN | Third Party | Other | 66 | 25 | 0.001091 | 4.4e-05 | N
09-08-18 | 08:47 | 243:80081 | SHORT RURAL | Other | Other | 1 | 87 | 0.000451 | 5e-06 | N
09-08-18 | 09:10 | 502:48002 | URBAN | Other | Other | 1 | 178 | 0.000118 | 1e-06 | N
09-08-18 | 09:37 | ZN12570:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 60 | 4e-05 | 1e-06 | N
09-08-18 | 11:37 | ZN9245:PA1 | URBAN | Other | Other - Self Clearing Trigger | 37 | 193 | 0.00472 | 2.4e-05 | N
09-08-18 | 13:09 | 221:11900 | URBAN | Other | Other | 1 | 43 | 2.8e-05 | 1e-06 | N
09-08-18 | 15:40 | ZN2635:PA52 | URBAN | Asset Failure | LV | 43 | 140 | 0.003974 | 2.8e-05 | N
09-08-18 | 16:03 | ZN116:PA2 | URBAN | Third Party | Vehicle impact | 57 | 57 | 0.002137 | 3.8e-05 | N
09-08-18 | 16:48 | ZN10999:PA12 | URBAN | Other | Other | 1 | 281 | 0.000186 | 1e-06 | N
09-08-18 | 19:37 | ZN4545:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 82 | 0.002716 | 3.3e-05 | N
09-08-18 | 23:36 | ZN12640:PA4 | URBAN | Other | Other - Arcing | 1 | 1,253 | 0.000828 | 1e-06 | N
10-08-18 | 03:39 | ZN1850:PA10 | URBAN | Third Party | Other | 1 | 326 | 0.000216 | 1e-06 | N
10-08-18 | 07:34 | 220:8689 | URBAN | Asset Failure | LV | 1 | 301 | 0.0002 | 1e-06 | N
10-08-18 | 08:48 | 509:33399 | SHORT RURAL | Other | Other | 1 | 69 | 0.000362 | 5e-06 | N
10-08-18 | 11:06 | ZN3154:PA23 | URBAN | Third Party | Other | 13 | 144 | 0.001237 | 9e-06 | N
10-08-18 | 12:11 | ZN14144:PA10 | SHORT RURAL | Other | Other | 1 | 77 | 0.000403 | 5e-06 | N
10-08-18 | 12:41 | ZN1285:PA10 | URBAN | Asset Failure | LV | 16 | 123 | 0.001305 | 1.1e-05 | N
10-08-18 | 13:22 | ZN15009:PA9 | URBAN | Asset Failure | LV | 23 | 397 | 0.006054 | 1.5e-05 | N
10-08-18 | 13:30 | ZN12610:PA6 | URBAN | Third Party | Vehicle impact | 1 | 450 | 0.000298 | 1e-06 | N
10-08-18 | 14:59 | ZN7481:PA3 | URBAN | Asset Failure | LV | 94 | 1,850 | 0.11531 | 6.2e-05 | N
09-08-18 | 13:20 | ZN2635:PA59 | URBAN | Other | Other | 3 | 70 | 0.000139 | 2e-06 | N
10-08-18 | 14:55 | 810:74054 | LONG RURAL | Asset Failure | HV | 2 | 85 | 0.059838 | 0.000704 | N
10-08-18 | 15:38 | 202:34260 | URBAN | Other | Other | 1 | 48 | 3.2e-05 | 1e-06 | N
10-08-18 | 16:04 | ZN12640:PA4 | URBAN | Other | Other | 1 | 126 | 8.3e-05 | 1e-06 | N
10-08-18 | 18:08 | ZN262:PA20 | URBAN | Asset Failure | HV | 615 | 102 | 0.04161 | 0.000408 | N
10-08-18 | 19:26 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 94 | 0.004928 | 5.2e-05 | N
10-08-18 | 19:47 | ZN15005:PA6 | URBAN | Asset Failure | LV | 66 | 193 | 0.008445 | 4.4e-05 | N
10-08-18 | 21:44 | 502:48010 | SHORT RURAL | Asset Failure | LV | 1 | 76 | 0.000398 | 5e-06 | N
11-08-18 | 10:23 | ZN12580:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 551 | 0.000364 | 1e-06 | N
11-08-18 | 12:33 | ZN15005:PA6 | URBAN | Asset Failure | LV | 1 | 186 | 0.000123 | 1e-06 | N
11-08-18 | 12:31 | ZN14143:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 163 | 1,624 | 1.3874 | 0.000854 | N
11-08-18 | 15:00 | 515:35193 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 3 | 45 | 0.000708 | 1.6e-05 | N
11-08-18 | 14:55 | 242:81539 | URBAN | Asset Failure | HV | 1,591 | 37 | 0.038956 | 0.00105 | N
11-08-18 | 16:43 | ZN3472:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 57 | 0.000151 | 3e-06 | N
11-08-18 | 19:30 | ZN12610:PA10 | URBAN | Other | Other - Arcing | 30 | 980 | 0.019408 | 2e-05 | N
11-08-18 | 20:56 | ZN10994:PA10 | URBAN | Animal | Animal impact | 1,108 | 70 | 0.051201 | 0.000731 | N
11-08-18 | 23:31 | ZN12620:PA8 | SHORT RURAL | Other | Other | 1 | 465 | 0.002439 | 5e-06 | N
12-08-18 | 09:10 | ZN10991:PA1 | URBAN | Asset Failure | LV | 26 | 95 | 0.001631 | 1.7e-05 | N
12-08-18 | 09:21 | ZN167:PA11 | URBAN | Other | Other - Self Clearing Trigger | 1 | 38 | 2.5e-05 | 1e-06 | N
12-08-18 | 10:05 | ZN3672:PA36 | URBAN | Vegetation | Vegetation Grow In | 1 | 372 | 0.000246 | 1e-06 | N
12-08-18 | 10:23 | ZN14891:PA5 | SHORT RURAL | Asset Failure | Distribution substation | 12 | 364 | 0.022894 | 6.3e-05 | N
12-08-18 | 14:38 | 232:33407 | SHORT RURAL | Third Party | Fire | 128 | 90 | 0.060478 | 0.000671 | N
12-08-18 | 17:49 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 76 | 0.001195 | 1.6e-05 | N
12-08-18 | 18:49 | ZN3155:PA16 | URBAN | Asset Failure | HV | 1 | 57 | 3.8e-05 | 1e-06 | N
12-08-18 | 18:49 | ZN3155:PA29 | URBAN | Asset Failure | HV | 1,796 | 74 | 0.087679 | 0.001186 | N
12-08-18 | 18:49 | ZN3155:PA33 | URBAN | Asset Failure | HV | 152 | 62 | 0.006214 | 0.0001 | N
12-08-18 | 18:49 | ZN3155:PA44 | URBAN | Asset Failure | HV | 162 | 306 | 0.032728 | 0.000107 | N
12-08-18 | 19:00 | ZN3155:PA33 | URBAN | Overloads |  | 43 | 870 | 0.024696 | 2.8e-05 | N
11-08-18 | 12:11 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 94 | 0.000493 | 5e-06 | N
13-08-18 | 08:59 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 4 | 71 | 0.09993 | 0.001407 | N
13-08-18 | 09:11 | ZN847:PA18 | SHORT RURAL | Other | Other | 1 | 76 | 0.000396 | 5e-06 | N
13-08-18 | 12:10 | ZN690:PA26 | URBAN | Third Party | Other | 1 | 1,159 | 0.000765 | 1e-06 | N
13-08-18 | 13:52 | 532:83314 | URBAN | Asset Failure | LV | 4 | 78 | 0.000206 | 3e-06 | N
13-08-18 | 14:03 | 222:33602 | URBAN | Asset Failure | LV | 1 | 191 | 0.000126 | 1e-06 | N
13-08-18 | 15:32 | ZN965:PA22 | URBAN | Other | Other | 1 | 54 | 3.6e-05 | 1e-06 | N
13-08-18 | 21:01 | ZN129:PA39 | URBAN | Asset Failure | LV | 1 | 494 | 0.000326 | 1e-06 | N
13-08-18 | 22:43 | ZN398:PA15 | URBAN | Other | Other | 1 | 1,438 | 0.000949 | 1e-06 | N
14-08-18 | 03:49 | 227:13019 | SHORT RURAL | Asset Failure | HV | 1 | 801 | 0.004205 | 5e-06 | N
13-08-18 | 09:50 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 20 | 0.001048 | 5.2e-05 | N
14-08-18 | 09:21 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 58 | 3.9e-05 | 1e-06 | N
14-08-18 | 09:24 | ZN12570:PA37 | SHORT RURAL | Other | Other | 1 | 139 | 0.000729 | 5e-06 | N
14-08-18 | 11:06 | ZN35800:PA1 | URBAN | Other | Other | 1 | 244 | 0.000161 | 1e-06 | N
14-08-18 | 12:01 | 204:82699 | URBAN | Other | Other | 1 | 1,239 | 0.000818 | 1e-06 | N
14-08-18 | 12:44 | ZN8000:PA6 | URBAN | Other | Other | 1 | 571 | 0.000377 | 1e-06 | N
14-08-18 | 16:47 | ZN3154:PA18 | URBAN | Other | Other | 1 | 63 | 4.2e-05 | 1e-06 | N
14-08-18 | 17:33 | ZN2635:PA44 | URBAN | Asset Failure | LV | 90 | 257 | 0.015249 | 5.9e-05 | N
14-08-18 | 18:17 | ZN1673:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 73 | 0.00159 | 2.2e-05 | N
14-08-18 | 19:52 | ZN384:PA76 | URBAN | Asset Failure | LV | 24 | 173 | 0.00274 | 1.6e-05 | N
15-08-18 | 07:26 | 807:74183 | SHORT RURAL | Asset Failure | HV | 2 | 49 | 0.000514 | 1e-05 | N
15-08-18 | 11:15 | ZN12630:PA8 | SHORT RURAL | Asset Failure | HV | 2 | 23 | 0.000236 | 1e-05 | N
15-08-18 | 11:31 | ZN3155:PA23 | URBAN | Third Party | Vehicle impact | 24 | 329 | 0.00522 | 1.6e-05 | N
15-08-18 | 10:31 | ZN2835:PA31 | URBAN | Other | Other - Self Clearing Trigger | 4 | 284 | 0.000751 | 3e-06 | N
15-08-18 | 10:36 | ZN9900:PA17 | URBAN | Asset Failure | LV | 1 | 189 | 0.000125 | 1e-06 | N
15-08-18 | 12:18 | ZN10995:PA1 | URBAN | Weather |  | 67 | 51 | 0.002274 | 4.4e-05 | N
15-08-18 | 12:36 | ZN847:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 59 | 244 | 0.009517 | 3.9e-05 | N
15-08-18 | 12:41 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 36 | 379 | 0.07163 | 0.000189 | N
15-08-18 | 12:59 | ZN4545:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,346 | 56 | 0.04983 | 0.00089 | N
15-08-18 | 14:01 | ZN12620:PA7 | URBAN | Asset Failure | LV | 1 | 539 | 0.000356 | 1e-06 | N
15-08-18 | 14:20 | ZN1193:PA15 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 66 | 54 | 0.018855 | 0.000346 | N
15-08-18 | 14:24 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 98 | 125 | 0.064343 | 0.000514 | N
15-08-18 | 14:54 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 325 | 0.000215 | 1e-06 | N
15-08-18 | 16:34 | ZN4545:PA25 | URBAN | Third Party | Other | 1 | 395 | 0.000261 | 1e-06 | N
15-08-18 | 16:51 | ZN36200:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 330 | 0.001734 | 5e-06 | N
15-08-18 | 17:02 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 197 | 0.000131 | 1e-06 | N
15-08-18 | 17:06 | ZN965:PA13 | URBAN | Other | Other | 1 | 169 | 0.000112 | 1e-06 | N
15-08-18 | 18:40 | 224:80329 | SHORT RURAL | Asset Failure | LV | 1 | 246 | 0.001293 | 5e-06 | N
15-08-18 | 18:50 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 25 | 0.00038 | 1.5e-05 | N
15-08-18 | 19:19 | 532:83309 | URBAN | Other | Other | 1 | 85 | 5.6e-05 | 1e-06 | N
16-08-18 | 01:01 | ZN9700:PA20 | URBAN | Animal | Animal impact | 117 | 379 | 0.029274 | 7.7e-05 | N
16-08-18 | 05:02 | ZN12620:PA10 | SHORT RURAL | Asset Failure | HV | 1,114 | 80 | 0.46787 | 0.00584 | N
15-08-18 | 09:00 | 242:81535 | URBAN | Network business | Network error | 61 | 370 | 0.014921 | 4e-05 | N
16-08-18 | 09:12 | 205:12205 | URBAN | Third Party | Vehicle impact | 1 | 333 | 0.00022 | 1e-06 | N
16-08-18 | 10:00 | ZN12640:PA7 | URBAN | Other | Other | 1 | 188 | 0.000124 | 1e-06 | N
16-08-18 | 13:07 | ZN14891:PA21 | SHORT RURAL | Other | Other | 1 | 66 | 0.000345 | 5e-06 | N
16-08-18 | 16:04 | ZN9245:PA15 | URBAN | Third Party | Other | 1 | 56 | 3.7e-05 | 1e-06 | N
16-08-18 | 17:24 | 512:83743 | SHORT RURAL | Asset Failure | HV | 1 | 76 | 0.000398 | 5e-06 | N
16-08-18 | 18:15 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 490 | 128 | 0.32804 | 0.002569 | N
16-08-18 | 19:50 | ZN965:PA3 | URBAN | Other | Other - Arcing | 1 | 258 | 0.00017 | 1e-06 | N
17-08-18 | 07:43 | ZN874:PA9 | URBAN | Third Party | Other | 44 | 32 | 0.000915 | 2.9e-05 | N
17-08-18 | 08:03 | 221:11894 | URBAN | Other | Other | 1 | 103 | 6.8e-05 | 1e-06 | N
17-08-18 | 10:40 | ZN10995:PA1 | URBAN | Asset Failure | HV | 541 | 69 | 0.024644 | 0.000357 | N
17-08-18 | 10:40 | ZN10995:PA7 | URBAN | Asset Failure | HV | 2,125 | 69 | 0.096799 | 0.001403 | N
17-08-18 | 11:37 | 522:83126 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 50 | 0.000261 | 5e-06 | N
17-08-18 | 10:45 | 232:33409 | SHORT RURAL | Third Party | Vehicle impact | 53 | 255 | 0.070856 | 0.000278 | N
17-08-18 | 14:24 | ZN36100:PA5 | URBAN | Other | Other - Self Clearing Trigger | 49 | 135 | 0.004374 | 3.2e-05 | N
18-08-18 | 02:44 | 213:33773 | URBAN | Other | Other | 1 | 81 | 5.3e-05 | 1e-06 | N
18-08-18 | 04:19 | 213:33773 | URBAN | Other | Other - Self Clearing Trigger | 44 | 668 | 0.019408 | 2.9e-05 | N
18-08-18 | 07:03 | ZN80:PA30 | URBAN | Asset Failure | HV | 169 | 177 | 0.019722 | 0.000112 | N
18-08-18 | 08:25 | ZN630:PA4 | URBAN | Third Party | Vehicle impact | 43 | 130 | 0.00369 | 2.8e-05 | N
18-08-18 | 09:55 | ZN80:PA24 | URBAN | Network business | Network error | 33 | 45 | 0.00098 | 2.2e-05 | N
18-08-18 | 11:59 | ZN2568:PA38 | URBAN | Other | Other - Self Clearing Trigger | 7 | 231 | 0.001067 | 5e-06 | N
18-08-18 | 14:56 | ZN10994:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 254 | 0.003018 | 1.2e-05 | N
18-08-18 | 15:03 | ZN2568:PA31 | URBAN | Asset Failure | Distribution substation | 254 | 716 | 0.12004 | 0.000168 | N
18-08-18 | 15:41 | ZN14143:PA6 | URBAN | Asset Failure | HV | 56 | 48 | 0.00179 | 3.7e-05 | N
18-08-18 | 17:33 | ZN10999:PA17 | URBAN | Other | Other - Arcing | 1 | 257 | 0.00017 | 1e-06 | N
18-08-18 | 17:23 | 230:81438 | SHORT RURAL | Third Party | Fire | 549 | 55 | 0.15688 | 0.002877 | N
18-08-18 | 21:53 | ZN9700:PA17 | URBAN | Animal | Animal impact | 1,225 | 54 | 0.043295 | 0.000809 | N
18-08-18 | 22:09 | 224:80346 | URBAN | Other | Other | 1 | 57 | 3.8e-05 | 1e-06 | N
19-08-18 | 05:48 | ZN36200:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 68 | 48 | 0.017107 | 0.000356 | N
19-08-18 | 06:09 | 229:34995 | SHORT RURAL | Third Party | Vehicle impact | 1 | 145 | 0.000761 | 5e-06 | N
19-08-18 | 06:51 | 230:81438 | SHORT RURAL | Asset Failure | HV | 2 | 354 | 0.003711 | 1e-05 | N
19-08-18 | 08:33 | 256:80640 | URBAN | Other | Other | 1 | 67 | 4.4e-05 | 1e-06 | N
19-08-18 | 10:22 | 243:80081 | SHORT RURAL | Third Party | Fire | 60 | 78 | 0.024528 | 0.000314 | N
19-08-18 | 09:59 | ZN9700:PA17 | URBAN | Asset Failure | LV | 9 | 116 | 0.000689 | 6e-06 | N
19-08-18 | 13:35 | 814:82289 | SHORT RURAL | Asset Failure | HV | 7 | 281 | 0.010309 | 3.7e-05 | N
19-08-18 | 13:55 | ZN15002:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 306 | 0.000202 | 1e-06 | N
19-08-18 | 15:41 | ZN5868:PA7 | URBAN | Asset Failure | LV | 46 | 64 | 0.001941 | 3e-05 | N
19-08-18 | 16:16 | 512:83743 | SHORT RURAL | Asset Failure | LV | 1 | 74 | 0.000388 | 5e-06 | N
19-08-18 | 17:49 | 810:74054 | LONG RURAL | Asset Failure | HV | 15 | 71 | 0.3746 | 0.005276 | N
19-08-18 | 20:05 | 513:48051 | URBAN | Weather |  | 1 | 105 | 6.9e-05 | 1e-06 | N
19-08-18 | 22:39 | ZN12600:PA12 | URBAN | Asset Failure | LV | 1 | 290 | 0.000191 | 1e-06 | N
20-08-18 | 05:41 | ZN1193:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 338 | 0.006701 | 2e-05 | N
20-08-18 | 06:50 | 243:80081 | SHORT RURAL | Asset Failure | LV | 67 | 100 | 0.035115 | 0.000351 | N
20-08-18 | 07:21 | 229:34983 | SHORT RURAL | Other | Other | 1 | 129 | 0.000676 | 5e-06 | N
20-08-18 | 07:46 | ZN14143:PA17 | SHORT RURAL | Overloads |  | 857 | 9 | 0.041059 | 0.004492 | N
20-08-18 | 07:46 | ZN14143:PA6 | URBAN | Overloads |  | 44 | 2 | 5.8e-05 | 2.9e-05 | N
20-08-18 | 08:13 | ZN13000:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 631 | 0.000417 | 1e-06 | N
20-08-18 | 09:27 | ZN35900:PA2 | URBAN | Asset Failure | LV | 2 | 123 | 0.000162 | 1e-06 | N
19-08-18 | 13:35 | 812:19066 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 255 | 0.002673 | 1e-05 | N
20-08-18 | 09:46 | ZN12570:PA22 | SHORT RURAL | Other | Other | 1 | 51 | 0.000267 | 5e-06 | N
20-08-18 | 09:52 | ZN2466:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 234 | 0.000309 | 1e-06 | N
20-08-18 | 10:38 | ZN14891:PA8 | SHORT RURAL | Asset Failure | LV | 1 | 412 | 0.002161 | 5e-06 | N
20-08-18 | 12:12 | ZN12570:PA40 | SHORT RURAL | Other | Other | 1 | 123 | 0.000647 | 5e-06 | N
20-08-18 | 12:22 | 515:35197 | LONG RURAL | Asset Failure | Distribution substation | 1 | 172 | 0.060517 | 0.000352 | N
20-08-18 | 13:26 | ZN2310:PA14 | URBAN | Other | Other - Self Clearing Trigger | 69 | 113 | 0.00515 | 4.6e-05 | N
20-08-18 | 15:50 | ZN35800:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 41 | 60 | 0.001624 | 2.7e-05 | N
20-08-18 | 15:55 | ZN711:PA22 | SHORT RURAL | Asset Failure | HV | 383 | 94 | 0.18911 | 0.002007 | N
20-08-18 | 16:00 | ZN2310:PA14 | URBAN | Third Party | Other | 7 | 262 | 0.001211 | 5e-06 | N
20-08-18 | 17:55 | 512:83732 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 125 | 0.00131 | 1e-05 | N
21-08-18 | 01:18 | ZN2635:PA65 | URBAN | Asset Failure | HV | 6 | 70 | 0.000277 | 4e-06 | N
21-08-18 | 02:39 | ZN187:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 341 | 0.011248 | 3.3e-05 | N
21-08-18 | 07:04 | ZN80:PA37 | URBAN | Network business | Network error | 60 | 136 | 0.00539 | 4e-05 | N
21-08-18 | 07:04 | ZN80:PA40 | URBAN | Network business | Network error | 26 | 136 | 0.002335 | 1.7e-05 | N
21-08-18 | 09:35 | ZN2196:PA2 | URBAN | Asset Failure | LV | 1 | 414 | 0.000273 | 1e-06 | N
21-08-18 | 11:36 | 258:80793 | URBAN | Other | Other | 1 | 65 | 4.3e-05 | 1e-06 | N
21-08-18 | 12:00 | ZN10999:PA7 | URBAN | Asset Failure | LV | 127 | 72 | 0.006063 | 8.4e-05 | N
21-08-18 | 12:03 | ZN10997:PA8 | URBAN | Asset Failure | LV | 1 | 146 | 9.7e-05 | 1e-06 | N
21-08-18 | 14:43 | 256:80644 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 64 | 4.2e-05 | 1e-06 | N
21-08-18 | 15:11 | ZN1285:PA27 | URBAN | Asset Failure | LV | 1 | 419 | 0.000277 | 1e-06 | N
21-08-18 | 15:35 | ZN3155:PA18 | URBAN | Weather |  | 1 | 290 | 0.000191 | 1e-06 | N
21-08-18 | 15:35 | ZN3155:PA20 | URBAN | Weather |  | 28 | 290 | 0.005363 | 1.8e-05 | N
21-08-18 | 19:19 | ZN1290:PA13 | URBAN | Asset Failure | LV | 1 | 41 | 2.7e-05 | 1e-06 | N
21-08-18 | 20:11 | ZN12580:PA4 | URBAN | Other | Other | 1 | 126 | 8.3e-05 | 1e-06 | N
21-08-18 | 21:44 | ZN80:PA37 | URBAN | Network business | Network error | 60 | 76 | 0.003012 | 4e-05 | N
21-08-18 | 21:44 | ZN80:PA40 | URBAN | Network business | Network error | 122 | 76 | 0.006124 | 8.1e-05 | N
22-08-18 | 11:41 | ZN10991:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 79 | 5.2e-05 | 1e-06 | N
22-08-18 | 14:36 | 532:83307 | SHORT RURAL | Other | Other - Self Clearing Trigger | 59 | 49 | 0.015152 | 0.000309 | N
22-08-18 | 14:39 | ZN874:PA7 | URBAN | Other | Other | 1 | 137 | 9e-05 | 1e-06 | N
22-08-18 | 18:07 | 814:82291 | SHORT RURAL | Other | Other | 1 | 115 | 0.000603 | 5e-06 | N
22-08-18 | 19:23 | ZN195:PA30 | SHORT RURAL | Asset Failure | LV | 61 | 61 | 0.019572 | 0.00032 | N
23-08-18 | 06:33 | ZN36200:PA1 | URBAN | Other | Other - Arcing | 1 | 747 | 0.000493 | 1e-06 | N
23-08-18 | 09:33 | ZN9252:PA22 | URBAN | Network business | Switching and protection error | 74 | 132 | 0.006448 | 4.9e-05 | N
23-08-18 | 09:33 | ZN9252:PA28 | URBAN | Network business | Switching and protection error | 21 | 132 | 0.00183 | 1.4e-05 | N
23-08-18 | 16:33 | ZN15015:PA15 | SHORT RURAL | Other | Other | 1 | 60 | 0.000313 | 5e-06 | N
23-08-18 | 18:56 | ZN2466:PA45 | URBAN | Third Party | Vehicle impact | 1 | 246 | 0.000163 | 1e-06 | N
23-08-18 | 22:53 | 258:80784 | URBAN | Animal | Animal impact | 89 | 42 | 0.002465 | 5.9e-05 | N
24-08-18 | 02:29 | ZN9245:PA13 | URBAN | Other | Other - Arcing | 1 | 480 | 0.000317 | 1e-06 | N
24-08-18 | 04:29 | ZN1193:PA27 | URBAN | Other | Other - Arcing | 1 | 391 | 0.000258 | 1e-06 | N
24-08-18 | 05:29 | ZN1287:PA21 | URBAN | Other | Other - Self Clearing Trigger | 55 | 116 | 0.004211 | 3.6e-05 | N
24-08-18 | 05:32 | ZN180:PA9 | URBAN | Other | Other - Arcing | 1 | 250 | 0.000165 | 1e-06 | N
24-08-18 | 05:36 | ZN15002:PA6 | URBAN | Other | Other - Arcing | 1 | 564 | 0.000372 | 1e-06 | N
24-08-18 | 05:44 | ZN35600:PA3 | URBAN | Other | Other - Arcing | 1 | 345 | 0.000228 | 1e-06 | N
24-08-18 | 05:47 | ZN15012:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 218 | 0.000576 | 3e-06 | N
24-08-18 | 08:31 | ZN10995:PA13 | URBAN | Third Party | Vehicle impact | 55 | 189 | 0.006846 | 3.6e-05 | N
24-08-18 | 09:45 | ZN9700:PA11 | URBAN | Other | Other - Arcing | 6 | 256 | 0.001014 | 4e-06 | N
24-08-18 | 09:57 | 261:81865 | URBAN | Asset Failure | LV | 1 | 437 | 0.000288 | 1e-06 | N
24-08-18 | 10:13 | ZN12610:PA6 | URBAN | Other | Other | 1 | 73 | 4.8e-05 | 1e-06 | N
24-08-18 | 10:26 | ZN2635:PA46 | URBAN | Third Party | Other | 1 | 154 | 0.000102 | 1e-06 | N
24-08-18 | 11:17 | 528:83019 | SHORT RURAL | Other | Other | 1 | 227 | 0.001191 | 5e-06 | N
24-08-18 | 11:35 | ZN847:PA1 | URBAN | Asset Failure | LV | 34 | 279 | 0.006267 | 2.2e-05 | N
24-08-18 | 14:03 | ZN12600:PA3 | URBAN | Other | Other - Arcing | 1 | 57 | 3.7e-05 | 1e-06 | N
24-08-18 | 14:55 | ZN1287:PA21 | URBAN | Asset Failure | LV | 55 | 210 | 0.007611 | 3.6e-05 | N
24-08-18 | 16:30 | ZN1290:PA9 | URBAN | Third Party | Vehicle impact | 1 | 301 | 0.000198 | 1e-06 | N
24-08-18 | 17:09 | 258:80781 | URBAN | Asset Failure | HV | 1,122 | 47 | 0.034808 | 0.000741 | N
24-08-18 | 17:37 | ZN12630:PA3 | SHORT RURAL | Other | Other - Arcing | 1 | 292 | 0.001531 | 5e-06 | N
24-08-18 | 20:30 | ZN10990:PA7 | URBAN | Other | Other - Arcing | 1 | 149 | 9.9e-05 | 1e-06 | N
25-08-18 | 02:30 | ZN9245:PA4 | URBAN | Third Party | Vehicle impact | 49 | 125 | 0.004042 | 3.2e-05 | N
25-08-18 | 07:41 | 807:74183 | SHORT RURAL | Asset Failure | HV | 1 | 179 | 0.000938 | 5e-06 | N
25-08-18 | 08:30 | ZN2835:PA9 | URBAN | Other | Other | 1 | 356 | 0.000235 | 1e-06 | N
25-08-18 | 09:27 | 507:80925 | SHORT RURAL | Asset Failure | LV | 1 | 272 | 0.001425 | 5e-06 | N
25-08-18 | 10:09 | ZN3154:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 933 | 153 | 0.094178 | 0.000616 | N
25-08-18 | 11:12 | ZN15006:PA16 | URBAN | Asset Failure | LV | 13 | 48 | 0.000412 | 9e-06 | N
25-08-18 | 12:03 | 511:29873 | URBAN | Asset Failure | LV | 1 | 356 | 0.000235 | 1e-06 | N
25-08-18 | 12:16 | ZN15010:PA29 | URBAN | Other | Other - Arcing | 1 | 407 | 0.000269 | 1e-06 | N
25-08-18 | 15:20 | ZN2835:PA30 | URBAN | Network business | Network error | 71 | 35 | 0.00164 | 4.7e-05 | N
25-08-18 | 13:53 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 216 | 163 | 0.1846 | 0.001132 | N
25-08-18 | 14:45 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 210 | 0.003301 | 1.6e-05 | N
25-08-18 | 15:30 | ZN12650:PA1 | SHORT RURAL | Weather |  | 9 | 107 | 0.005046 | 4.7e-05 | N
25-08-18 | 14:03 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 162 | 0.000849 | 5e-06 | N
25-08-18 | 16:37 | 227:13016 | SHORT RURAL | Other | Other | 1 | 77 | 0.000402 | 5e-06 | N
25-08-18 | 17:19 | 224:80331 | URBAN | Third Party | Vehicle impact | 3 | 71 | 0.000141 | 2e-06 | N
25-08-18 | 20:03 | ZN342:PA18 | URBAN | Other | Other - Self Clearing Trigger | 222 | 92 | 0.013463 | 0.000146 | N
26-08-18 | 09:08 | 532:83314 | URBAN | Other | Other - Arcing | 1 | 399 | 0.000263 | 1e-06 | N
26-08-18 | 09:35 | ZN12650:PA20 | URBAN | Other | Other - Arcing | 1 | 264 | 0.000174 | 1e-06 | N
26-08-18 | 09:39 | ZN10999:PA17 | URBAN | Asset Failure | LV | 70 | 45 | 0.002084 | 4.6e-05 | N
26-08-18 | 10:39 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 161 | 0.000844 | 5e-06 | N
26-08-18 | 13:37 | ZN3472:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 72 | 0.002053 | 2.8e-05 | N
26-08-18 | 14:57 | 806:82667 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 103 | 0.00054 | 5e-06 | N
26-08-18 | 16:27 | 524:33578 | URBAN | Other | Other - Self Clearing Trigger | 101 | 78 | 0.005199 | 6.7e-05 | N
26-08-18 | 18:24 | ZN129:PA35 | URBAN | Asset Failure | LV | 70 | 106 | 0.004896 | 4.6e-05 | N
26-08-18 | 18:24 | ZN129:PA49 | URBAN | Asset Failure | LV | 1 | 105 | 7e-05 | 1e-06 | N
26-08-18 | 19:54 | ZN9118:PA11 | URBAN | Animal | Animal impact | 1,872 | 43 | 0.053167 | 0.001235 | N
26-08-18 | 20:56 | ZN35555:PA20 | URBAN | Network business | Network error | 18 | 114 | 0.001354 | 1.2e-05 | N
27-08-18 | 02:36 | ZN2602:PA17 | URBAN | Other | Other - Arcing | 16 | 504 | 0.005318 | 1.1e-05 | N
27-08-18 | 07:24 | 508:82574 | SHORT RURAL | Asset Failure | HV | 4 | 356 | 0.007461 | 2.1e-05 | N
27-08-18 | 08:01 | ZN4545:PA29 | URBAN | Third Party | Vehicle impact | 27 | 194 | 0.003457 | 1.8e-05 | N
27-08-18 | 08:09 | 814:82285 | SHORT RURAL | Other | Other - Arcing | 1 | 131 | 0.000685 | 5e-06 | N
27-08-18 | 08:27 | ZN3154:PA16 | URBAN | Third Party | Vehicle impact | 1 | 573 | 0.000378 | 1e-06 | N
27-08-18 | 08:28 | ZN4545:PA31 | URBAN | Asset Failure | LV | 63 | 216 | 0.008999 | 4.2e-05 | N
27-08-18 | 09:03 | 230:81440 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1 | 386 | 0.000255 | 1e-06 | N
25-08-18 | 11:30 | 807:74184 | SHORT RURAL | Asset Failure | LV | 1 | 80 | 0.000419 | 5e-06 | N
25-08-18 | 14:04 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 184 | 0.001928 | 1e-05 | N
27-08-18 | 10:06 | ZN35800:PA19 | URBAN | Asset Failure | LV | 1 | 315 | 0.000208 | 1e-06 | N
27-08-18 | 10:58 | ZN965:PA46 | URBAN | Asset Failure | LV | 1 | 74 | 4.9e-05 | 1e-06 | N
27-08-18 | 11:36 | 813:89063 | SHORT RURAL | Third Party | Unauthorised access | 386 | 64 | 0.12944 | 0.002022 | N
27-08-18 | 12:41 | 235:2120 | SHORT RURAL | Asset Failure | HV | 65 | 63 | 0.021507 | 0.000341 | N
27-08-18 | 12:49 | ZN1290:PA13 | URBAN | Asset Failure | HV | 161 | 79 | 0.008437 | 0.000106 | N
27-08-18 | 12:55 | ZN10991:PA7 | URBAN | Other | Other - Arcing | 1 | 305 | 0.000201 | 1e-06 | N
27-08-18 | 14:03 | ZN180:PA21 | URBAN | Asset Failure | LV | 89 | 112 | 0.006578 | 5.9e-05 | N
27-08-18 | 14:03 | ZN180:PA7 | URBAN | Asset Failure | LV | 18 | 112 | 0.00133 | 1.2e-05 | N
27-08-18 | 14:36 | ZN15010:PA26 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,014 | 0.005313 | 5e-06 | N
27-08-18 | 14:49 | 801:74119 | URBAN | Other | Other | 1 | 160 | 0.000106 | 1e-06 | N
27-08-18 | 20:17 | ZN36100:PA20 | URBAN | Asset Failure | LV | 112 | 243 | 0.017931 | 7.4e-05 | N
27-08-18 | 22:36 | ZN8000:PA24 | URBAN | Third Party | Dig-in | 42 | 77 | 0.002134 | 2.8e-05 | N
27-08-18 | 23:58 | ZN10997:PA7 | URBAN | Asset Failure | LV | 82 | 62 | 0.00334 | 5.4e-05 | N
28-08-18 | 06:25 | ZN15001:PA10 | URBAN | Asset Failure | Subtransmission | 168 | 25 | 0.002775 | 0.000111 | N
28-08-18 | 06:25 | ZN15001:PA11 | URBAN | Asset Failure | Subtransmission | 914 | 25 | 0.015097 | 0.000604 | N
28-08-18 | 06:25 | ZN15001:PA13 | URBAN | Asset Failure | Subtransmission | 92 | 34 | 0.002067 | 6.1e-05 | N
28-08-18 | 06:25 | ZN15001:PA15 | URBAN | Asset Failure | Subtransmission | 2,300 | 45 | 0.068383 | 0.00152 | N
28-08-18 | 06:25 | ZN15001:PA16 | URBAN | Asset Failure | Subtransmission | 540 | 29 | 0.010347 | 0.000357 | N
28-08-18 | 06:25 | ZN15001:PA17 | URBAN | Asset Failure | Subtransmission | 2 | 34 | 4.5e-05 | 1e-06 | N
28-08-18 | 06:25 | ZN15001:PA18 | URBAN | Asset Failure | Subtransmission | 2,367 | 29 | 0.045353 | 0.001564 | N
28-08-18 | 06:25 | ZN15001:PA8 | URBAN | Asset Failure | Subtransmission | 683 | 25 | 0.011282 | 0.000451 | N
28-08-18 | 06:52 | ZN15008:PA10 | URBAN | Network business | Network error | 186 | 203 | 0.024947 | 0.000123 | N
28-08-18 | 06:52 | ZN15008:PA9 | URBAN | Network business | Network error | 4 | 203 | 0.000536 | 3e-06 | N
28-08-18 | 09:26 | 264:81238 | SHORT RURAL | Other | Other | 1 | 76 | 0.000394 | 5e-06 | N
28-08-18 | 12:25 | 230:81432 | SHORT RURAL | Asset Failure | HV | 29 | 75 | 0.011287 | 0.00015 | N
28-08-18 | 10:42 | ZN14143:PA5 | URBAN | Asset Failure | LV | 1 | 272 | 0.00018 | 1e-06 | N
28-08-18 | 14:50 | 512:83743 | SHORT RURAL | Asset Failure | HV | 9 | 50 | 0.002335 | 4.7e-05 | N
28-08-18 | 14:49 | ZN931:PA2 | URBAN | Other | Other - Self Clearing Trigger | 85 | 181 | 0.010165 | 5.6e-05 | N
28-08-18 | 16:22 | ZN398:PA15 | URBAN | Third Party | Vehicle impact | 1 | 247 | 0.000163 | 1e-06 | N
28-08-18 | 17:00 | 526:34640 | SHORT RURAL | Asset Failure | HV | 34 | 276 | 0.048622 | 0.000176 | N
28-08-18 | 18:02 | ZN15001:PA18 | URBAN | Asset Failure | LV | 91 | 148 | 0.008898 | 6e-05 | N
28-08-18 | 18:02 | ZN15011:PA4 | URBAN | Asset Failure | LV | 71 | 208 | 0.009757 | 4.7e-05 | N
28-08-18 | 19:33 | ZN711:PA21 | SHORT RURAL | Asset Failure | LV | 82 | 2,667 | 1.1349 | 0.000426 | N
28-08-18 | 18:05 | ZN14143:PA5 | URBAN | Asset Failure | LV | 32 | 120 | 0.002537 | 2.1e-05 | N
28-08-18 | 21:06 | ZN262:PA17 | URBAN | Other | Other - Self Clearing Trigger | 90 | 88 | 0.005239 | 5.9e-05 | N
28-08-18 | 21:25 | ZN2602:PA31 | URBAN | Asset Failure | LV | 68 | 110 | 0.004942 | 4.5e-05 | N
28-08-18 | 23:29 | ZN10999:PA7 | URBAN | Asset Failure | LV | 127 | 103 | 0.008678 | 8.4e-05 | N
29-08-18 | 00:22 | ZN2602:PA31 | URBAN | Asset Failure | LV | 1 | 697 | 0.000461 | 1e-06 | N
29-08-18 | 07:30 | 524:33576 | SHORT RURAL | Other | Other | 1 | 127 | 0.000658 | 5e-06 | N
29-08-18 | 08:25 | 257:81987 | URBAN | Asset Failure | Distribution substation | 97 | 55 | 0.003507 | 6.4e-05 | N
29-08-18 | 09:49 | ZN10995:PA13 | URBAN | Third Party | Other | 1 | 71 | 4.7e-05 | 1e-06 | N
29-08-18 | 11:05 | 526:34637 | SHORT RURAL | Other | Other | 2 | 130 | 0.001349 | 1e-05 | N
29-08-18 | 12:24 | ZN2400:PA22 | SHORT RURAL | Other | Other | 27 | 126 | 0.017656 | 0.00014 | N
29-08-18 | 14:57 | 522:83124 | URBAN | Asset Failure | HV | 54 | 143 | 0.005102 | 3.6e-05 | N
29-08-18 | 15:38 | 224:80346 | URBAN | Third Party | Vehicle impact | 1 | 484 | 0.00032 | 1e-06 | N
29-08-18 | 17:05 | ZN180:PA15 | URBAN | Asset Failure | LV | 22 | 265 | 0.003852 | 1.5e-05 | N
29-08-18 | 18:30 | 256:80646 | URBAN | Asset Failure | LV | 88 | 65 | 0.003779 | 5.8e-05 | N
29-08-18 | 18:33 | ZN10999:PA24 | URBAN | Asset Failure | LV | 76 | 105 | 0.00525 | 5e-05 | N
29-08-18 | 21:53 | ZN3472:PA12 | URBAN | Other | Other | 1 | 122 | 8.1e-05 | 1e-06 | N
30-08-18 | 05:39 | 508:82579 | SHORT RURAL | Asset Failure | HV | 375 | 284 | 0.55182 | 0.001946 | N
30-08-18 | 07:40 | 524:33572 | SHORT RURAL | Third Party | Dig-in | 159 | 93 | 0.076806 | 0.000825 | N
30-08-18 | 08:41 | 807:74184 | SHORT RURAL | Other | Other - Arcing | 1 | 214 | 0.00111 | 5e-06 | N
30-08-18 | 07:46 | ZN12610:PA24 | URBAN | Animal | Animal nesting/burrowing, etc and other | 50 | 104 | 0.003436 | 3.3e-05 | N
30-08-18 | 09:13 | ZN10995:PA1 | URBAN | Third Party | Vehicle impact | 107 | 97 | 0.006858 | 7.1e-05 | N
29-08-18 | 16:29 | 522:83123 | SHORT RURAL | Asset Failure | HV | 1,293 | 2 | 0.013421 | 0.006711 | N
29-08-18 | 16:32 | 522:83123 | SHORT RURAL | Asset Failure | HV | 1,293 | 5 | 0.033553 | 0.006711 | N
30-08-18 | 11:09 | 524:33572 | SHORT RURAL | Other | Other - Self Clearing Trigger | 17 | 66 | 0.005823 | 8.8e-05 | N
30-08-18 | 11:52 | 522:83131 | URBAN | Other | Other | 1 | 327 | 0.000216 | 1e-06 | N
30-08-18 | 13:32 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 612 | 0.003178 | 5e-06 | N
28-08-18 | 11:45 | ZN3154:PA17 | URBAN | Network business | Network error | 48 | 75 | 0.002379 | 3.2e-05 | N
30-08-18 | 15:00 | ZN195:PA29 | URBAN | Other | Other | 1 | 346 | 0.000229 | 1e-06 | N
30-08-18 | 15:27 | ZN3288:PA41 42KLM | CBD | Other | Other - Self Clearing Trigger | 12 | 163 | 0.06388 | 0.000392 | N
30-08-18 | 15:49 | ZN167:PA4 | URBAN | Other | Other | 1 | 217 | 0.000143 | 1e-06 | N
30-08-18 | 18:54 | ZN9245:PA21 | URBAN | Other | Other - Self Clearing Trigger | 75 | 86 | 0.004249 | 5e-05 | N
30-08-18 | 19:44 | 526:34640 | SHORT RURAL | Asset Failure | LV | 1 | 131 | 0.00068 | 5e-06 | N
30-08-18 | 21:32 | ZN80:PA40 | URBAN | Other | Other | 1 | 876 | 0.000579 | 1e-06 | N
30-08-18 | 21:52 | ZN9118:PA21 | URBAN | Animal | Animal impact | 1,336 | 62 | 0.054729 | 0.000883 | N
31-08-18 | 11:30 | 528:83019 | SHORT RURAL | Asset Failure | HV | 1 | 105 | 0.000545 | 5e-06 | N
31-08-18 | 14:35 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 75 | 0.02639 | 0.000352 | N
22-08-18 | 23:35 | ZN874:PA22 | URBAN | Asset Failure | HV | 1,510 | 106 | 0.10534 | 0.000997 | N
31-08-18 | 16:10 | ZN3672:PA44 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 260 | 0.000344 | 1e-06 | N
25-08-18 | 15:20 | ZN2835:PA30 | URBAN | Network business | Network error | 84 | 35 | 0.00194 | 5.5e-05 | N
31-08-18 | 16:55 | ZN2400:PA18 | SHORT RURAL | Other | Other | 1 | 304 | 0.00158 | 5e-06 | N
31-08-18 | 18:54 | 801:74121 | LONG RURAL | Asset Failure | HV | 238 | 2 | 0.16749 | 0.083744 | N
31-08-18 | 18:42 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 118 | 0.001837 | 1.6e-05 | N
31-08-18 | 18:50 | ZN262:PA6 | URBAN | Other | Other - Self Clearing Trigger | 107 | 89 | 0.006324 | 7.1e-05 | N
31-08-18 | 18:59 | ZN3155:PA20 | URBAN | Other | Other - Self Clearing Trigger | 82 | 194 | 0.010511 | 5.4e-05 | N
31-08-18 | 19:56 | ZN10995:PA12 | URBAN | Asset Failure | LV | 64 | 64 | 0.002693 | 4.2e-05 | N
31-08-18 | 20:31 | ZN340:PA3 | URBAN | Other | Other - Arcing | 1 | 119 | 7.9e-05 | 1e-06 | N
31-08-18 | 22:15 | 513:48051 | URBAN | Other | Other | 1 | 89 | 5.9e-05 | 1e-06 | N
01-09-18 | 08:21 | ZN12610:PA24 | URBAN | Animal | Animal nesting/burrowing, etc and other | 50 | 69 | 0.00228 | 3.3e-05 | N
01-09-18 | 09:15 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.031668 | 0.000352 | N
01-09-18 | 14:43 | ZN262:PA25 | URBAN | Network business | Switching and protection error | 12 | 147 | 0.001166 | 8e-06 | N
01-09-18 | 14:43 | ZN262:PA29 | URBAN | Network business | Switching and protection error | 11 | 147 | 0.001068 | 7e-06 | N
01-09-18 | 11:25 | ZN10990:PA8 | URBAN | Asset Failure | LV | 55 | 190 | 0.006905 | 3.6e-05 | N
01-09-18 | 13:38 | ZN2635:PA38 | URBAN | Other | Other | 1 | 171 | 0.000113 | 1e-06 | N
01-09-18 | 16:02 | ZN80:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 329 | 0.000218 | 1e-06 | N
01-09-18 | 19:26 | ZN35700:PA13 | URBAN | Asset Failure | HV | 40 | 137 | 0.003624 | 2.6e-05 | N
01-09-18 | 22:02 | ZN9252:PA27 | URBAN | Asset Failure | Distribution substation | 63 | 83 | 0.003454 | 4.2e-05 | N
02-09-18 | 02:29 | ZN398:PA2 | URBAN | Other | Other - Self Clearing Trigger | 79 | 90 | 0.00471 | 5.2e-05 | N
02-09-18 | 12:31 | 812:19072 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 1,184 | 0.006145 | 5e-06 | N
02-09-18 | 20:19 | ZN398:PA2 | URBAN | Other | Other - Self Clearing Trigger | 79 | 100 | 0.005229 | 5.2e-05 | N
03-09-18 | 02:12 | ZN931:PA2 | URBAN | Other | Other - Self Clearing Trigger | 72 | 342 | 0.016293 | 4.8e-05 | N
03-09-18 | 07:05 | 224:80346 | URBAN | Third Party | Vehicle impact | 1 | 264 | 0.000175 | 1e-06 | N
03-09-18 | 07:13 | ZN9550:PA33 | URBAN | Other | Other - Arcing | 1 | 376 | 0.000249 | 1e-06 | N
03-09-18 | 07:49 | ZN9118:PA21 | URBAN | Asset Failure | LV | 52 | 145 | 0.004987 | 3.4e-05 | N
03-09-18 | 08:14 | ZN195:PA10 | URBAN | Third Party | Vehicle impact | 1 | 427 | 0.000282 | 1e-06 | N
03-09-18 | 08:32 | ZN80:PA28 | URBAN | Asset Failure | LV | 1 | 207 | 0.000137 | 1e-06 | N
30-08-18 | 10:20 | ZN9037:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 11 | 80 | 0.000581 | 7e-06 | N
03-09-18 | 09:05 | 810:74050 | SHORT RURAL | Asset Failure | LV | 1 | 455 | 0.002362 | 5e-06 | N
03-09-18 | 09:15 | 810:74050 | SHORT RURAL | Asset Failure | HV | 47 | 52 | 0.012696 | 0.000244 | N
03-09-18 | 09:13 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 317 | 0.003291 | 1e-05 | N
30-08-18 | 17:40 | 806:82662 | SHORT RURAL | Other | Other | 3 | 50 | 0.000778 | 1.6e-05 | N
03-09-18 | 10:38 | 806:82662 | SHORT RURAL | Animal | Animal impact | 1 | 177 | 0.000917 | 5e-06 | N
03-09-18 | 11:10 | ZN12570:PA37 | SHORT RURAL | Asset Failure | HV | 1,519 | 53 | 0.4201 | 0.007884 | N
03-09-18 | 11:27 | ZN342:PA18 | URBAN | Other | Other - Self Clearing Trigger | 33 | 218 | 0.004747 | 2.2e-05 | N
03-09-18 | 11:35 | ZN14144:PA2 | SHORT RURAL | Other | Other | 1 | 40 | 0.000208 | 5e-06 | N
03-09-18 | 11:59 | ZN195:PA10 | URBAN | Other | Other | 1 | 42 | 2.8e-05 | 1e-06 | N
03-09-18 | 13:46 | 512:83732 | SHORT RURAL | Other | Other | 1 | 62 | 0.00032 | 5e-06 | N
06-09-18 | 13:59 | ZN10995:PA12 | URBAN | Third Party | Vehicle impact | 45 | 131 | 0.003896 | 3e-05 | N
03-09-18 | 15:18 | 512:83732 | SHORT RURAL | Asset Failure | HV | 2 | 135 | 0.001401 | 1e-05 | N
03-09-18 | 18:21 | 221:11899 | SHORT RURAL | Other | Other - Arcing | 1 | 194 | 0.001007 | 5e-06 | N
03-09-18 | 19:20 | 222:33600 | URBAN | Other | Other - Arcing | 3 | 190 | 0.000377 | 2e-06 | N
03-09-18 | 20:58 | ZN15014:PA18 | URBAN | Other | Other - Arcing | 1 | 219 | 0.000144 | 1e-06 | N
03-09-18 | 22:00 | 206:34440 | URBAN | Other | Other - Arcing | 1 | 210 | 0.000138 | 1e-06 | N
03-09-18 | 22:46 | ZN398:PA25 | URBAN | Asset Failure | HV | 859 | 64 | 0.036326 | 0.000568 | N
04-09-18 | 06:00 | 522:83132 | SHORT RURAL | Asset Failure | HV | 3 | 350 | 0.00545 | 1.6e-05 | N
03-09-18 | 18:10 | 243:80075 | SHORT RURAL | Third Party | Unauthorised access | 1 | 25 | 0.00013 | 5e-06 | N
04-09-18 | 08:30 | 238:34147 | URBAN | Other | Other - Arcing | 1 | 299 | 0.000198 | 1e-06 | N
04-09-18 | 11:11 | 507:80923 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 135 | 0.006981 | 5.2e-05 | N
04-09-18 | 21:05 | 243:80075 | SHORT RURAL | Third Party | Unauthorised access | 1 | 15 | 7.8e-05 | 5e-06 | N
04-09-18 | 13:09 | ZN12600:PA2 | SHORT RURAL | Other | Other | 1 | 66 | 0.000342 | 5e-06 | N
04-09-18 | 16:12 | 507:80923 | SHORT RURAL | Asset Failure | LV | 1 | 312 | 0.001621 | 5e-06 | N
04-09-18 | 17:41 | 524:33570 | SHORT RURAL | Other | Other | 1 | 96 | 0.000496 | 5e-06 | N
04-09-18 | 19:09 | 417:80507 | URBAN | Asset Failure | LV | 1 | 51 | 3.4e-05 | 1e-06 | N
05-09-18 | 06:07 | ZN12610:PA7 | URBAN | Asset Failure | LV | 1 | 173 | 0.000114 | 1e-06 | N
05-09-18 | 07:51 | ZN7900:PA6 | URBAN | Third Party | Vehicle impact | 99 | 257 | 0.016812 | 6.5e-05 | N
05-09-18 | 09:05 | ZN8700:PA67 68ABC | CBD | Network business | Switching and protection error | 1 | 27 | 0.000882 | 3.3e-05 | N
05-09-18 | 09:27 | 524:33570 | SHORT RURAL | Other | Other | 1 | 107 | 0.000557 | 5e-06 | N
05-09-18 | 09:56 | ZN10997:PA1 | URBAN | Asset Failure | LV | 1 | 144 | 9.5e-05 | 1e-06 | N
05-09-18 | 10:01 | ZN180:PA41 | URBAN | Other | Other | 1 | 32 | 2.1e-05 | 1e-06 | N
05-09-18 | 14:03 | ZN7900:PA12 | URBAN | Asset Failure | LV | 12 | 306 | 0.002429 | 8e-06 | N
05-09-18 | 16:06 | 258:80784 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 144 | 9.5e-05 | 1e-06 | N
05-09-18 | 20:47 | ZN2310:PA62 | URBAN | Third Party | Vehicle impact | 1 | 491 | 0.000324 | 1e-06 | N
06-09-18 | 06:11 | ZN116:PA12 | URBAN | Other | Other - Self Clearing Trigger | 51 | 143 | 0.004831 | 3.4e-05 | N
06-09-18 | 10:33 | ZN36100:PA27 | URBAN | Third Party | Vehicle impact | 1 | 446 | 0.000295 | 1e-06 | N
06-09-18 | 12:39 | ZN2602:PA20 | URBAN | Asset Failure | HV | 1,496 | 56 | 0.055195 | 0.000989 | N
06-09-18 | 15:42 | ZN180:PA16 | URBAN | Third Party | Other | 41 | 93 | 0.00252 | 2.7e-05 | N
06-09-18 | 15:50 | ZN1287:PA5 | URBAN | Third Party | Vehicle impact | 11 | 125 | 0.000909 | 7e-06 | N
06-09-18 | 15:50 | ZN847:PA15 | URBAN | Other | Other | 57 | 30 | 0.00113 | 3.8e-05 | N
06-09-18 | 18:27 | 520:48172 | SHORT RURAL | Animal | Other | 1 | 113 | 0.000586 | 5e-06 | N
06-09-18 | 18:31 | 238:34141 | SHORT RURAL | Other | Other | 1 | 54 | 0.000278 | 5e-06 | N
06-09-18 | 18:43 | ZN9118:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 61 | 0.001775 | 2.9e-05 | N
07-09-18 | 00:23 | ZN10999:PA11 | URBAN | Other | Other - Arcing | 1 | 547 | 0.000361 | 1e-06 | N
07-09-18 | 01:39 | 523:33501 | SHORT RURAL | Animal | Animal impact | 57 | 113 | 0.033419 | 0.000296 | N
07-09-18 | 06:47 | 516:48067 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 228 | 0.001183 | 5e-06 | N
07-09-18 | 05:58 | ZN9700:PA18 | URBAN | Third Party | Fire | 1 | 197 | 0.00013 | 1e-06 | N
07-09-18 | 07:54 | 526:34639 | SHORT RURAL | Asset Failure | HV | 1 | 241 | 0.00125 | 5e-06 | N
07-09-18 | 08:22 | ZN35600:PA19 | URBAN | Third Party | Vehicle impact | 14 | 153 | 0.001415 | 9e-06 | N
06-09-18 | 08:05 | 812:19072 | SHORT RURAL | Other | Other | 1 | 75 | 0.000389 | 5e-06 | N
07-09-18 | 09:39 | 514:18137 | SHORT RURAL | Asset Failure | HV | 29 | 125 | 0.018819 | 0.00015 | N
07-09-18 | 11:01 | 206:34441 | URBAN | Third Party | Unauthorised access | 1 | 208 | 0.000138 | 1e-06 | N
07-09-18 | 11:27 | 243:80084 | SHORT RURAL | Asset Failure | LV | 1 | 373 | 0.001933 | 5e-06 | N
07-09-18 | 12:35 | 511:29877 | SHORT RURAL | Other | Other | 1 | 104 | 0.000538 | 5e-06 | N
07-09-18 | 17:37 | ZN10990:PA11 | URBAN | Weather |  | 1,134 | 157 | 0.11762 | 0.000749 | N
07-09-18 | 17:37 | ZN10990:PA12 | URBAN | Weather |  | 900 | 157 | 0.09335 | 0.000595 | N
07-09-18 | 17:37 | ZN10990:PA2 | URBAN | Weather |  | 2,191 | 157 | 0.22726 | 0.001447 | N
07-09-18 | 17:37 | ZN10990:PA5 | URBAN | Weather |  | 907 | 157 | 0.094076 | 0.000599 | N
07-09-18 | 17:37 | ZN10990:PA6 | URBAN | Weather |  | 1,114 | 157 | 0.11555 | 0.000736 | N
07-09-18 | 17:37 | ZN10990:PA8 | URBAN | Weather |  | 1,881 | 157 | 0.1951 | 0.001243 | N
07-09-18 | 17:40 | ZN1850:PA32 | URBAN | Other | Other | 5 | 111 | 0.000367 | 3e-06 | N
07-09-18 | 17:40 | ZN3472:PA30 | URBAN | Other | Other | 1,937 | 117 | 0.14928 | 0.00128 | N
07-09-18 | 17:49 | ZN10994:PA19 | URBAN | Asset Failure | HV | 1,017 | 119 | 0.079702 | 0.000672 | N
07-09-18 | 18:14 | ZN1850:PA41 | URBAN | Other | Other - Self Clearing Trigger | 131 | 156 | 0.013534 | 8.7e-05 | N
07-09-18 | 18:23 | ZN1850:PA41 | URBAN | Other | Other - Self Clearing Trigger | 80 | 177 | 0.009341 | 5.3e-05 | N
07-09-18 | 20:14 | ZN10990:PA2 | URBAN | Other | Other - Self Clearing Trigger | 141 | 1,256 | 0.117 | 9.3e-05 | N
07-09-18 | 18:50 | ZN1850:PA41 | URBAN | Other | Other - Self Clearing Trigger | 45 | 59 | 0.001759 | 3e-05 | N
07-09-18 | 18:58 | ZN80:PA37 | URBAN | Other | Other - Arcing | 1 | 274 | 0.000181 | 1e-06 | N
07-09-18 | 19:23 | 807:74181 | SHORT RURAL | Other | Other - Arcing | 1 | 234 | 0.001215 | 5e-06 | N
07-09-18 | 18:50 | ZN2602:PA9 | URBAN | Third Party | Other | 80 | 133 | 0.007016 | 5.3e-05 | N
07-09-18 | 20:10 | ZN9035:PA2 | URBAN | Asset Failure | HV | 809 | 154 | 0.082105 | 0.000534 | N
07-09-18 | 20:10 | ZN9035:PA4 | URBAN | Asset Failure | HV | 1 | 149 | 9.8e-05 | 1e-06 | N
07-09-18 | 20:39 | ZN10990:PA12 | URBAN | Weather |  | 651 | 96 | 0.041268 | 0.00043 | N
07-09-18 | 20:51 | ZN10990:PA11 | URBAN | Other | Other - Self Clearing Trigger | 53 | 234 | 0.008189 | 3.5e-05 | N
07-09-18 | 20:59 | ZN10990:PA2 | URBAN | Other | Other - Self Clearing Trigger | 58 | 241 | 0.009226 | 3.8e-05 | N
07-09-18 | 21:38 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 59 | 0.000306 | 5e-06 | N
07-09-18 | 21:46 | 221:11900 | URBAN | Other | Other - Self Clearing Trigger | 107 | 104 | 0.007336 | 7.1e-05 | N
08-09-18 | 00:33 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 44 | 900 | 0.20546 | 0.000228 | N
07-09-18 | 22:43 | ZN398:PA2 | URBAN | Asset Failure | LV | 80 | 675 | 0.035666 | 5.3e-05 | N
08-09-18 | 07:37 | 221:11900 | URBAN | Asset Failure | HV | 107 | 58 | 0.004099 | 7.1e-05 | N
08-09-18 | 07:44 | ZN10999:PA12 | URBAN | Asset Failure | LV | 111 | 199 | 0.014617 | 7.3e-05 | N
08-09-18 | 09:12 | 512:83733 | SHORT RURAL | Other | Other | 1 | 132 | 0.000686 | 5e-06 | N
08-09-18 | 11:02 | ZN2835:PA31 | URBAN | Network business | Switching and protection error | 11 | 224 | 0.001625 | 7e-06 | N
08-09-18 | 09:56 | ZN12640:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 480 | 0.002492 | 5e-06 | N
08-09-18 | 10:00 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 78 | 0.000405 | 5e-06 | N
08-09-18 | 10:42 | ZN2602:PA36 | URBAN | Other | Other - Arcing | 2 | 400 | 0.000528 | 1e-06 | N
08-09-18 | 11:13 | 813:89055 | SHORT RURAL | Asset Failure | HV | 1 | 352 | 0.001824 | 5e-06 | N
08-09-18 | 13:07 | 239:82131 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 172 | 0.000894 | 5e-06 | N
08-09-18 | 14:59 | ZN2568:PA32 | URBAN | Other | Other - Self Clearing Trigger | 80 | 55 | 0.002932 | 5.3e-05 | N
08-09-18 | 15:30 | ZN2635:PA43 | SHORT RURAL | Vegetation | Vegetation Grow In | 1 | 300 | 0.001555 | 5e-06 | N
08-09-18 | 15:51 | ZN690:PA28 | URBAN | Asset Failure | LV | 1 | 328 | 0.000217 | 1e-06 | N
08-09-18 | 18:33 | 213:33777 | SHORT RURAL | Other | Other | 1 | 96 | 0.0005 | 5e-06 | N
08-09-18 | 19:19 | 512:83743 | SHORT RURAL | Other | Other - Arcing | 1 | 124 | 0.000642 | 5e-06 | N
08-09-18 | 19:23 | 813:89055 | SHORT RURAL | Asset Failure | HV | 1 | 377 | 0.001956 | 5e-06 | N
09-09-18 | 07:50 | ZN12580:PA16 | URBAN | Third Party | Vehicle impact | 4 | 60 | 0.000159 | 3e-06 | N
09-09-18 | 08:53 | 507:80925 | SHORT RURAL | Other | Other | 1 | 98 | 0.00051 | 5e-06 | N
09-09-18 | 09:07 | 512:83743 | SHORT RURAL | Asset Failure | LV | 1 | 98 | 0.000509 | 5e-06 | N
09-09-18 | 11:04 | ZN12600:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 425 | 0.002206 | 5e-06 | N
09-09-18 | 12:41 | ZN12640:PA10 | URBAN | Third Party | Fire | 30 | 216 | 0.00428 | 2e-05 | N
09-09-18 | 17:37 | 202:34254 | URBAN | Asset Failure | LV | 55 | 133 | 0.004839 | 3.6e-05 | N
10-09-18 | 01:46 | ZN15008:PA7 | URBAN | Animal | Animal impact | 5,094 | 127 | 0.42772 | 0.003364 | N
10-09-18 | 04:14 | ZN15009:PA1 | URBAN | Asset Failure | HV | 85 | 801 | 0.044969 | 5.6e-05 | N
10-09-18 | 04:14 | ZN15009:PA12 | URBAN | Asset Failure | HV | 1 | 267 | 0.000176 | 1e-06 | N
10-09-18 | 04:14 | ZN15009:PA5 | URBAN | Asset Failure | HV | 104 | 626 | 0.043 | 6.9e-05 | N
10-09-18 | 04:14 | ZN15015:PA5 | URBAN | Asset Failure | HV | 1,621 | 298 | 0.31916 | 0.001071 | N
10-09-18 | 08:46 | ZN1850:PA41 | URBAN | Other | Other - Self Clearing Trigger | 23 | 164 | 0.002491 | 1.5e-05 | N
07-09-18 | 16:32 | TS7270:704SRA | URBAN | Third Party | Other | 1 | 318 | 0.00021 | 1e-06 | N
10-09-18 | 10:05 | ZN2602:PA36 | URBAN | Third Party | Dig-in | 1 | 94 | 6.2e-05 | 1e-06 | N
10-09-18 | 10:05 | ZN2602:PA42 | URBAN | Third Party | Dig-in | 2 | 94 | 0.000124 | 1e-06 | N
10-09-18 | 10:05 | ZN35600:PA1 | URBAN | Third Party | Dig-in | 2,660 | 91 | 0.15934 | 0.001757 | N
10-09-18 | 11:09 | ZN15006:PA8 | URBAN | Other | Other | 1 | 1,865 | 0.001232 | 1e-06 | N
10-09-18 | 11:24 | ZN14143:PA17 | SHORT RURAL | Asset Failure | LV | 1 | 160 | 0.000829 | 5e-06 | N
10-09-18 | 11:26 | 202:34231 37 42 | URBAN | Third Party | Vehicle impact | 34 | 37 | 0.000841 | 2.2e-05 | N
10-09-18 | 11:48 | ZN35600:PA1 | URBAN | Third Party | Other | 1 | 522 | 0.000345 | 1e-06 | N
10-09-18 | 11:26 | 202:34231 37 42 | URBAN | Third Party | Vehicle impact | 159 | 206 | 0.021633 | 0.000105 | N
10-09-18 | 12:34 | ZN35900:PA24 | URBAN | Third Party | Vehicle impact | 1,683 | 120 | 0.13291 | 0.001112 | N
10-09-18 | 14:26 | ZN965:PA38 | URBAN | Third Party | Dig-in | 27 | 179 | 0.003183 | 1.8e-05 | N
10-09-18 | 14:14 | ZN2568:PA25 | URBAN | Overloads |  | 1 | 131 | 8.7e-05 | 1e-06 | N
10-09-18 | 15:30 | 512:83743 | SHORT RURAL | Third Party | Other | 1 | 40 | 0.000208 | 5e-06 | N
10-09-18 | 15:58 | 217:33610 | URBAN | Other | Other | 1 | 1,352 | 0.000893 | 1e-06 | N
10-09-18 | 20:06 | ZN711:PA22 | SHORT RURAL | Asset Failure | HV | 151 | 194 | 0.15187 | 0.000784 | N
10-09-18 | 22:07 | ZN262:PA21 | URBAN | Third Party | Vehicle impact | 7 | 238 | 0.0011 | 5e-06 | N
11-09-18 | 06:27 | ZN35600:PA1 | URBAN | Other | Other | 1 | 3 | 2e-06 | 1e-06 | N
11-09-18 | 08:44 | ZN1648:PA2 | URBAN | Network business | Network error | 17 | 179 | 0.00207 | 1.2e-05 | N
11-09-18 | 11:47 | ZN12650:PA5 | URBAN | Asset Failure | HV | 116 | 39 | 0.00308 | 7.9e-05 | N
11-09-18 | 17:57 | 813:89061 | LONG RURAL | Asset Failure | LV | 1 | 148 | 0.052127 | 0.000352 | N
11-09-18 | 23:45 | ZN3672:PA32 | URBAN | Asset Failure | Zone substation | 95 | 50 | 0.003234 | 6.5e-05 | N
11-09-18 | 23:45 | ZN3672:PA34 | URBAN | Asset Failure | Zone substation | 162 | 50 | 0.005514 | 0.00011 | N
11-09-18 | 23:45 | ZN3672:PA35 | SHORT RURAL | Asset Failure | Zone substation | 657 | 50 | 0.13833 | 0.002767 | N
11-09-18 | 23:45 | ZN3672:PA36 | URBAN | Asset Failure | Zone substation | 1,837 | 50 | 0.062531 | 0.001251 | N
11-09-18 | 23:45 | ZN3672:PA37 | URBAN | Asset Failure | Zone substation | 1,526 | 50 | 0.051944 | 0.001039 | N
11-09-18 | 23:45 | ZN3672:PA4 | URBAN | Asset Failure | Zone substation | 112 | 50 | 0.003812 | 7.6e-05 | N
11-09-18 | 23:45 | ZN3672:PA42 | URBAN | Asset Failure | Zone substation | 347 | 50 | 0.011812 | 0.000236 | N
11-09-18 | 23:45 | ZN3672:PA43 | URBAN | Asset Failure | Zone substation | 2,048 | 50 | 0.069713 | 0.001394 | N
11-09-18 | 23:45 | ZN3672:PA44 | URBAN | Asset Failure | Zone substation | 1,921 | 50 | 0.06539 | 0.001308 | N
11-09-18 | 23:45 | ZN3672:PA46 | URBAN | Asset Failure | Zone substation | 1,614 | 50 | 0.05494 | 0.001099 | N
11-09-18 | 23:45 | ZN3672:PA6 | URBAN | Asset Failure | Zone substation | 1,270 | 79 | 0.068514 | 0.000865 | N
12-09-18 | 04:13 | 213:33775 | URBAN | Asset Failure | LV | 1 | 196 | 0.000134 | 1e-06 | N
12-09-18 | 05:10 | ZN195:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 52 | 279 | 0.009896 | 3.5e-05 | N
12-09-18 | 05:49 | ZN12650:PA20 | URBAN | Asset Failure | LV | 1 | 460 | 0.000314 | 1e-06 | N
11-09-18 | 23:45 | ZN3672:PA37 | URBAN | Asset Failure | Distribution substation | 297 | 148 | 0.029925 | 0.000202 | N
12-09-18 | 09:26 | 239:82133 | URBAN | Asset Failure | LV | 1 | 122 | 8.3e-05 | 1e-06 | N
12-09-18 | 11:33 | ZN12650:PA20 | URBAN | Asset Failure | LV | 28 | 79 | 0.001513 | 1.9e-05 | N
12-09-18 | 13:01 | 270:83593 | SHORT RURAL | Other | Other | 1 | 103 | 0.000435 | 4e-06 | N
12-09-18 | 14:20 | 238:34151 | URBAN | Asset Failure | HV | 1,253 | 47 | 0.040207 | 0.000854 | N
12-09-18 | 14:25 | ZN10998:PA5 | URBAN | Asset Failure | LV | 1 | 263 | 0.000179 | 1e-06 | N
12-09-18 | 14:58 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 364 | 101 | 0.15512 | 0.001533 | N
12-09-18 | 17:02 | ZN167:PA11 | URBAN | Asset Failure | LV | 1 | 348 | 0.000237 | 1e-06 | N
12-09-18 | 17:45 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 256 | 168 | 15.1667 | 0.090046 | N
12-09-18 | 18:35 | ZN1068:PA19 | SHORT RURAL | Network business | Network error | 50 | 84 | 0.017754 | 0.000211 | N
12-09-18 | 18:36 | ZN1068:PA26 | URBAN | Network business | Network error | 93 | 84 | 0.005323 | 6.3e-05 | N
12-09-18 | 18:42 | ZN167:PA21 | URBAN | Network business | Network error | 54 | 78 | 0.00287 | 3.7e-05 | N
12-09-18 | 21:26 | ZN35400:PA101 | URBAN | Asset Failure | LV | 92 | 64 | 0.004013 | 6.3e-05 | N
12-09-18 | 23:07 | ZN15011:PA4 | URBAN | Asset Failure | HV | 1,984 | 108 | 0.14599 | 0.001352 | N
12-09-18 | 23:54 | ZN35400:PA101 | URBAN | Asset Failure | LV | 92 | 55 | 0.003457 | 6.3e-05 | N
13-09-18 | 07:36 | ZN35400:PA101 | URBAN | Asset Failure | LV | 92 | 109 | 0.006813 | 6.3e-05 | N
13-09-18 | 10:26 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 16 | 94 | 0.001023 | 1.1e-05 | N
13-09-18 | 12:19 | 202:34232 | URBAN | Asset Failure | LV | 96 | 50 | 0.003296 | 6.5e-05 | N
13-09-18 | 13:26 | ZN711:PA34 | URBAN | Asset Failure | LV | 2 | 5 | 7e-06 | 1e-06 | N
13-09-18 | 13:50 | ZN2835:PA15 | URBAN | Asset Failure | LV | 15 | 150 | 0.001531 | 1e-05 | N
13-09-18 | 14:06 | ZN965:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 922 | 85 | 0.053625 | 0.000627 | N
13-09-18 | 14:07 | ZN847:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 57 | 323 | 0.012528 | 3.9e-05 | N
13-09-18 | 15:08 | ZN4545:PA39 | URBAN | Asset Failure | LV | 4 | 132 | 0.000359 | 3e-06 | N
13-09-18 | 14:46 | ZN2602:PA21 | URBAN | Asset Failure | LV | 1 | 532 | 0.000362 | 1e-06 | N
13-09-18 | 16:26 | ZN1850:PA44 | URBAN | Asset Failure | LV | 1 | 1,114 | 0.000758 | 1e-06 | N
13-09-18 | 17:36 | ZN262:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 189 | 0.005016 | 2.7e-05 | N
14-09-18 | 09:58 | ZN901:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 226 | 0.000154 | 1e-06 | N
14-09-18 | 10:09 | 813:89055 | SHORT RURAL | Other | Other | 1 | 90 | 0.000381 | 4e-06 | N
14-09-18 | 11:14 | ZN35800:PA16 | URBAN | Other | Other - Arcing | 1 | 226 | 0.000154 | 1e-06 | N
14-09-18 | 12:19 | ZN4545:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 143 | 9.7e-05 | 1e-06 | N
14-09-18 | 14:44 | 511:29873 | URBAN | Asset Failure | HV | 480 | 36 | 0.011767 | 0.000327 | N
14-09-18 | 14:44 | 511:29876 | SHORT RURAL | Asset Failure | HV | 1,655 | 31 | 0.21298 | 0.006968 | N
14-09-18 | 15:19 | ZN15001:PA16 | URBAN | Third Party | Vehicle impact | 37 | 97 | 0.002444 | 2.5e-05 | N
14-09-18 | 17:00 | ZN1285:PA20 | URBAN | Third Party | Other | 3 | 1,110 | 0.002268 | 2e-06 | N
15-09-18 | 00:32 | 507:80922 | SHORT RURAL | Other | Other | 1 | 57 | 0.000241 | 4e-06 | N
15-09-18 | 01:58 | 233:82812 | SHORT RURAL | Animal | Animal impact | 28 | 69 | 0.008095 | 0.000118 | N
15-09-18 | 03:48 | ZN12610:PA25 | URBAN | Other | Other - Arcing | 1 | 432 | 0.000294 | 1e-06 | N
15-09-18 | 05:23 | ZN1788:PA36 | URBAN | Other | Other - Arcing | 1 | 550 | 0.000374 | 1e-06 | N
15-09-18 | 07:31 | ZN2568:PA9 | URBAN | Other | Other | 1 | 637 | 0.000433 | 1e-06 | N
15-09-18 | 12:05 | ZN12690:PA16 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 45 | 0.001516 | 3.4e-05 | N
15-09-18 | 12:15 | 217:33610 | URBAN | Other | Other | 1 | 5 | 3e-06 | 1e-06 | N
15-09-18 | 09:20 | ZN12690:PA16 | SHORT RURAL | Other | Other | 3 | 145 | 0.001831 | 1.3e-05 | N
15-09-18 | 13:06 | 512:83733 | SHORT RURAL | Asset Failure | HV | 3 | 159 | 0.002008 | 1.3e-05 | N
15-09-18 | 10:38 | ZN4545:PA25 | URBAN | Third Party | Vehicle impact | 1 | 547 | 0.000372 | 1e-06 | N
15-09-18 | 15:42 | ZN4545:PA26 | URBAN | Other | Other - Self Clearing Trigger | 7 | 83 | 0.000395 | 5e-06 | N
15-09-18 | 15:44 | ZN12610:PA25 | URBAN | Asset Failure | LV | 1 | 330 | 0.000225 | 1e-06 | N
15-09-18 | 17:15 | ZN9118:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 71 | 525 | 0.025364 | 4.8e-05 | N
15-09-18 | 20:09 | ZN1673:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 25 | 71 | 0.001205 | 1.7e-05 | N
15-09-18 | 18:36 | 270:83590 | URBAN | Asset Failure | LV | 1 | 202 | 0.000137 | 1e-06 | N
15-09-18 | 18:36 | 270:83590 | URBAN | Asset Failure | LV | 1 | 202 | 0.000137 | 1e-06 | N
15-09-18 | 20:31 | ZN9037:PA16 | URBAN | Weather |  | 29 | 500 | 0.009867 | 2e-05 | N
15-09-18 | 22:15 | ZN12620:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,114 | 97 | 0.45261 | 0.00469 | N
16-09-18 | 07:53 | 258:80787 | URBAN | Asset Failure | LV | 1 | 146 | 0.0001 | 1e-06 | N
16-09-18 | 08:15 | 264:81244 | SHORT RURAL | Asset Failure | LV | 1 | 74 | 0.000312 | 4e-06 | N
16-09-18 | 09:20 | ZN14892:PA17 | URBAN | Asset Failure | LV | 1 | 479 | 0.000326 | 1e-06 | N
16-09-18 | 12:26 | ZN3472:PA34 | URBAN | Asset Failure | LV | 1 | 479 | 0.000326 | 1e-06 | N
16-09-18 | 13:15 | 232:33413 | SHORT RURAL | Asset Failure | LV | 1 | 586 | 0.002467 | 4e-06 | N
16-09-18 | 14:07 | ZN340:PA12 | URBAN | Asset Failure | Subtransmission | 1 | 145 | 9.9e-05 | 1e-06 | N
16-09-18 | 14:07 | ZN340:PA14 | URBAN | Asset Failure | Subtransmission | 1,125 | 149 | 0.11407 | 0.000766 | N
16-09-18 | 14:07 | ZN340:PA18 | SHORT RURAL | Asset Failure | Subtransmission | 323 | 115 | 0.15639 | 0.00136 | N
16-09-18 | 14:07 | ZN340:PA19 | URBAN | Asset Failure | Subtransmission | 17 | 151 | 0.001747 | 1.2e-05 | N
16-09-18 | 14:07 | ZN340:PA20 | URBAN | Asset Failure | Subtransmission | 1,323 | 116 | 0.10429 | 0.0009 | N
16-09-18 | 14:07 | ZN340:PA4 | URBAN | Asset Failure | Subtransmission | 1 | 115 | 7.8e-05 | 1e-06 | N
16-09-18 | 14:07 | ZN340:PA40 | URBAN | Asset Failure | Subtransmission | 968 | 149 | 0.098152 | 0.000659 | N
16-09-18 | 14:07 | ZN340:PA45 | URBAN | Asset Failure | Subtransmission | 692 | 147 | 0.069224 | 0.000471 | N
16-09-18 | 14:07 | ZN340:PA8 | URBAN | Asset Failure | Subtransmission | 3 | 147 | 0.0003 | 2e-06 | N
16-09-18 | 14:07 | ZN630:PA3 | URBAN | Asset Failure | Subtransmission | 1 | 149 | 0.000101 | 1e-06 | N
16-09-18 | 14:07 | ZN630:PA38 | URBAN | Asset Failure | Subtransmission | 1 | 105 | 7.1e-05 | 1e-06 | N
16-09-18 | 16:40 | ZN262:PA30 | URBAN | Other | Other - Self Clearing Trigger | 65 | 75 | 0.003317 | 4.4e-05 | N
16-09-18 | 21:22 | 801:74118 | URBAN | Third Party | Other | 18 | 227 | 0.002777 | 1.2e-05 | N
16-09-18 | 23:24 | 507:80923 | SHORT RURAL | Other | Other | 37 | 160 | 0.024909 | 0.000156 | N
13-09-18 | 11:58 | 512:83733 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 132 | 0.001112 | 8e-06 | N
17-09-18 | 08:00 | ZN12570:PA24 | SHORT RURAL | Other | Other | 1 | 156 | 0.000655 | 4e-06 | N
17-09-18 | 09:05 | ZN10993:PA39 | URBAN | Other | Other - Arcing | 1 | 310 | 0.000211 | 1e-06 | N
17-09-18 | 09:39 | 232:33409 | SHORT RURAL | Other | Other | 1 | 96 | 0.000404 | 4e-06 | N
13-09-18 | 13:40 | 801:74121 | LONG RURAL | Asset Failure | Distribution substation | 1 | 100 | 0.035174 | 0.000352 | N
17-09-18 | 10:29 | 258:80776 | URBAN | Other | Other | 1 | 92 | 6.3e-05 | 1e-06 | N
17-09-18 | 11:02 | 242:81539 | URBAN | Other | Other | 1 | 57 | 3.9e-05 | 1e-06 | N
17-09-18 | 11:42 | 240:34849 | URBAN | Other | Other | 1 | 59 | 4e-05 | 1e-06 | N
17-09-18 | 11:58 | ZN80:PA30 | URBAN | Asset Failure | LV | 1 | 315 | 0.000214 | 1e-06 | N
17-09-18 | 14:59 | ZN2835:PA29 | URBAN | Third Party | Other | 24 | 725 | 0.011845 | 1.6e-05 | N
17-09-18 | 14:59 | ZN2835:PA9 | URBAN | Third Party | Other | 31 | 726 | 0.015316 | 2.1e-05 | N
14-09-18 | 10:00 | ZN188:PA31 | URBAN | Third Party | Dig-in | 22 | 330 | 0.004944 | 1.5e-05 | N
17-09-18 | 15:31 | 814:82291 | SHORT RURAL | Asset Failure | LV | 6 | 199 | 0.005027 | 2.5e-05 | N
17-09-18 | 17:04 | ZN14144:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 115 | 0.000485 | 4e-06 | N
17-09-18 | 19:23 | ZN15010:PA29 | URBAN | Other | Other - Self Clearing Trigger | 60 | 101 | 0.004131 | 4.1e-05 | N
17-09-18 | 20:23 | 515:35197 | LONG RURAL | Asset Failure | Distribution substation | 1 | 172 | 0.060478 | 0.000352 | N
17-09-18 | 22:32 | ZN36800:PA32 | URBAN | Network business | Network error | 45 | 110 | 0.003369 | 3.1e-05 | N
17-09-18 | 22:32 | ZN36800:PA42 | URBAN | Network business | Network error | 93 | 80 | 0.005063 | 6.3e-05 | N
17-09-18 | 22:40 | ZN15008:PA5 | URBAN | Asset Failure | LV | 1 | 257 | 0.000175 | 1e-06 | N
18-09-18 | 00:52 | 258:80785 | URBAN | Asset Failure | HV | 1,590 | 63 | 0.06788 | 0.001083 | N
18-09-18 | 00:49 | 528:83020 | SHORT RURAL | Asset Failure | HV | 896 | 152 | 0.57444 | 0.003771 | N
18-09-18 | 03:54 | ZN690:PA33 | URBAN | Third Party | Vehicle impact | 1 | 305 | 0.000208 | 1e-06 | N
17-09-18 | 10:34 | 813:89061 | LONG RURAL | Asset Failure | Distribution substation | 18 | 216 | 1.3671 | 0.006329 | N
18-09-18 | 10:16 | ZN10999:PA17 | URBAN | Other | Other - Self Clearing Trigger | 74 | 89 | 0.004475 | 5e-05 | N
18-09-18 | 14:30 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 185 | 0.001557 | 8e-06 | N
19-09-18 | 06:13 | 223:14397 | URBAN | Asset Failure | HV | 49 | 62 | 0.002067 | 3.3e-05 | N
19-09-18 | 08:03 | ZN15013:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 96 | 0.000406 | 4e-06 | N
19-09-18 | 10:20 | ZN14892:PA21 | URBAN | Asset Failure | LV | 1 | 117 | 7.9e-05 | 1e-06 | N
19-09-18 | 10:36 | ZN3672:PA42 | URBAN | Third Party | Vehicle impact | 92 | 124 | 0.00773 | 6.3e-05 | N
19-09-18 | 11:01 | ZN9550:PA43 | URBAN | Third Party | Vehicle impact | 28 | 114 | 0.002172 | 1.9e-05 | N
19-09-18 | 14:35 | 810:74050 | SHORT RURAL | Asset Failure | HV | 3 | 25 | 0.000316 | 1.3e-05 | N
15-09-18 | 20:29 | ZN10999:PA16 | URBAN | Asset Failure | LV | 1 | 171 | 0.000116 | 1e-06 | N
16-09-18 | 20:31 | ZN9037:PA16 | URBAN | Asset Failure | LV | 29 | 464 | 0.009157 | 2e-05 | N
19-09-18 | 12:53 | ZN35500:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 245 | 0.006323 | 2.6e-05 | N
19-09-18 | 15:00 | ZN4545:PA28 | URBAN | Asset Failure | LV | 136 | 105 | 0.009715 | 9.3e-05 | N
19-09-18 | 13:10 | ZN4545:PA27 | URBAN | Other | Other | 1 | 20 | 1.4e-05 | 1e-06 | N
19-09-18 | 15:20 | 812:19072 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 95 | 0.0004 | 4e-06 | N
19-09-18 | 15:48 | ZN12630:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 203 | 0.000855 | 4e-06 | N
19-09-18 | 16:33 | ZN15010:PA29 | URBAN | Asset Failure | LV | 1 | 382 | 0.00026 | 1e-06 | N
19-09-18 | 18:26 | ZN8000:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 453 | 0.000308 | 1e-06 | N
20-09-18 | 08:00 | ZN965:PA42 | URBAN | Other | Other | 111 | 70 | 0.005297 | 7.6e-05 | N
20-09-18 | 06:55 | ZN262:PA31 | URBAN | Other | Other | 1 | 124 | 8.5e-05 | 1e-06 | N
20-09-18 | 07:07 | ZN15006:PA16 | URBAN | Asset Failure | LV | 1 | 413 | 0.000282 | 1e-06 | N
20-09-18 | 08:02 | 223:14395 | SHORT RURAL | Third Party | Vehicle impact | 1 | 237 | 0.000998 | 4e-06 | N
20-09-18 | 08:09 | 528:83022 | URBAN | Other | Other | 1 | 81 | 5.5e-05 | 1e-06 | N
20-09-18 | 08:16 | 511:29878 | SHORT RURAL | Other | Other | 1 | 123 | 0.00052 | 4e-06 | N
20-09-18 | 09:09 | 801:74121 | LONG RURAL | Asset Failure | LV | 1 | 166 | 0.058398 | 0.000352 | N
20-09-18 | 10:11 | ZN690:PA30 | URBAN | Other | Other | 1 | 55 | 3.7e-05 | 1e-06 | N
20-09-18 | 10:52 | ZN1290:PA12 | URBAN | Asset Failure | HV | 1,035 | 91 | 0.064127 | 0.000706 | N
20-09-18 | 11:00 | ZN2310:PA3 | URBAN | Third Party | Vehicle impact | 41 | 315 | 0.008805 | 2.8e-05 | N
20-09-18 | 11:10 | 216:10724 | SHORT RURAL | Other | Other | 1 | 63 | 0.000266 | 4e-06 | N
20-09-18 | 12:21 | ZN1788:PA14 | URBAN | Asset Failure | LV | 28 | 1,314 | 0.025078 | 1.9e-05 | N
20-09-18 | 14:12 | 509:33395 | LONG RURAL | Asset Failure | HV | 33 | 47 | 0.54536 | 0.011603 | N
20-09-18 | 14:49 | 216:10723 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 26 | 1.7e-05 | 1e-06 | N
20-09-18 | 17:36 | 507:80931 | URBAN | Other | Other - Self Clearing Trigger | 115 | 44 | 0.00345 | 7.8e-05 | N
21-09-18 | 07:56 | ZN180:PA41 | URBAN | Third Party | Vehicle impact | 1 | 214 | 0.000145 | 1e-06 | N
21-09-18 | 08:38 | 522:83126 | SHORT RURAL | Other | Other | 1 | 73 | 0.000309 | 4e-06 | N
21-09-18 | 08:44 | ZN12620:PA3 | URBAN | Asset Failure | LV | 1 | 246 | 0.000167 | 1e-06 | N
21-09-18 | 09:14 | ZN10995:PA8 | URBAN | Third Party | Vehicle impact | 6 | 101 | 0.000412 | 4e-06 | N
21-09-18 | 09:14 | ZN36800:PA42 | URBAN | Network business | Network error | 111 | 286 | 0.021599 | 7.6e-05 | N
21-09-18 | 09:39 | ZN14144:PA2 | SHORT RURAL | Other | Other | 1 | 132 | 0.000554 | 4e-06 | N
21-09-18 | 12:29 | ZN180:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 331 | 0.000225 | 1e-06 | N
21-09-18 | 14:44 | ZN3672:PA42 | URBAN | Asset Failure | LV | 50 | 180 | 0.006116 | 3.4e-05 | N
22-09-18 | 04:01 | ZN931:PA10 | URBAN | Other | Other - Self Clearing Trigger | 58 | 116 | 0.004578 | 3.9e-05 | N
22-09-18 | 09:51 | 814:82289 | SHORT RURAL | Asset Failure | LV | 1 | 158 | 0.000666 | 4e-06 | N
22-09-18 | 12:05 | 528:83014 | SHORT RURAL | Asset Failure | LV | 1 | 173 | 0.000727 | 4e-06 | N
22-09-18 | 12:50 | ZN12660:PA17 | URBAN | Other | Other | 1 | 59 | 4e-05 | 1e-06 | N
22-09-18 | 20:57 | ZN3155:PA34 | URBAN | Vegetation | Vegetation Grow In | 1 | 192 | 0.00013 | 1e-06 | N
23-09-18 | 01:05 | ZN9035:PA2 | URBAN | Asset Failure | HV | 258 | 430 | 0.075481 | 0.000176 | N
23-09-18 | 01:05 | ZN9035:PA4 | URBAN | Asset Failure | HV | 2,081 | 181 | 0.25684 | 0.001416 | N
23-09-18 | 10:04 | ZN12690:PA3 | SHORT RURAL | Other | Other - Arcing | 1 | 415 | 0.001747 | 4e-06 | N
23-09-18 | 10:58 | ZN931:PA2 | URBAN | Asset Failure | LV | 47 | 1,066 | 0.034097 | 3.2e-05 | N
23-09-18 | 11:59 | ZN342:PA18 | URBAN | Other | Other - Arcing | 49 | 1,068 | 0.035621 | 3.3e-05 | N
23-09-18 | 12:50 | ZN9900:PA19 | URBAN | Third Party | Other | 1 | 369 | 0.000251 | 1e-06 | N
23-09-18 | 18:59 | ZN9118:PA20 | URBAN | Asset Failure | LV | 49 | 51 | 0.001693 | 3.3e-05 | N
24-09-18 | 00:08 | ZN2635:PA55 | SHORT RURAL | Asset Failure | HV | 1,381 | 59 | 0.34421 | 0.005813 | N
24-09-18 | 05:01 | ZN12610:PA22 | URBAN | Animal | Animal impact | 65 | 207 | 0.009156 | 4.4e-05 | N
24-09-18 | 07:08 | ZN12650:PA1 | SHORT RURAL | Other | Other - Arcing | 1 | 172 | 0.000723 | 4e-06 | N
24-09-18 | 08:29 | ZN9118:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 27 | 160 | 0.018211 | 0.000114 | N
24-09-18 | 09:52 | ZN36100:PA2 | URBAN | Asset Failure | LV | 49 | 132 | 0.004402 | 3.3e-05 | N
24-09-18 | 11:04 | 511:29876 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 166 | 0.001398 | 8e-06 | N
24-09-18 | 11:02 | ZN3154:PA5 | URBAN | Asset Failure | LV | 1 | 177 | 0.00012 | 1e-06 | N
24-09-18 | 11:57 | ZN35900:PA24 | URBAN | Asset Failure | LV | 164 | 173 | 0.019279 | 0.000112 | N
24-09-18 | 13:10 | ZN690:PA34 | URBAN | Other | Other | 1 | 118 | 8e-05 | 1e-06 | N
24-09-18 | 15:47 | ZN2568:PA27 | URBAN | Third Party | Other | 1 | 355 | 0.000242 | 1e-06 | N
24-09-18 | 17:44 | ZN80:PA40 | URBAN | Other | Other - Self Clearing Trigger | 19 | 95 | 0.00123 | 1.3e-05 | N
24-09-18 | 19:27 | ZN3472:PA22 | URBAN | Asset Failure | LV | 1 | 183 | 0.000124 | 1e-06 | N
25-09-18 | 01:50 | ZN80:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 3 | 75 | 0.000153 | 2e-06 | N
25-09-18 | 05:30 | ZN15006:PA13 | URBAN | Asset Failure | LV | 33 | 139 | 0.003124 | 2.2e-05 | N
25-09-18 | 06:22 | ZN2466:PA16 | URBAN | Other | Other - Self Clearing Trigger | 18 | 168 | 0.002057 | 1.2e-05 | N
25-09-18 | 07:44 | ZN36200:PA4 | SHORT RURAL | Other | Other | 1 | 56 | 0.000237 | 4e-06 | N
25-09-18 | 09:24 | ZN2568:PA40 | URBAN | Vegetation | Vegetation Blow/Fall In | 7 | 86 | 0.000408 | 5e-06 | N
25-09-18 | 10:06 | ZN690:PA35 | URBAN | Other | Other | 1 | 206 | 0.00014 | 1e-06 | N
25-09-18 | 14:30 | 511:29878 | SHORT RURAL | Other | Other | 1 | 55 | 0.000231 | 4e-06 | N
25-09-18 | 11:30 | ZN2400:PA11 | SHORT RURAL | Other | Other | 141 | 24 | 0.01424 | 0.000593 | N
25-09-18 | 11:50 | ZN9252:PA28 | URBAN | Network business | Network error | 29 | 140 | 0.002753 | 2e-05 | N
25-09-18 | 14:52 | ZN167:PA11 | URBAN | Third Party | Vehicle impact | 1 | 158 | 0.000107 | 1e-06 | N
25-09-18 | 15:05 | ZN2196:PA25 | URBAN | Weather |  | 56 | 204 | 0.007774 | 3.8e-05 | N
25-09-18 | 19:18 | ZN965:PA4 | URBAN | Animal | Animal impact | 1,114 | 67 | 0.050773 | 0.000758 | N
25-09-18 | 19:18 | ZN965:PA46 | URBAN | Animal | Animal impact | 1 | 67 | 4.6e-05 | 1e-06 | N
25-09-18 | 20:08 | ZN10995:PA7 | URBAN | Asset Failure | Distribution substation | 73 | 52 | 0.00258 | 5e-05 | N
26-09-18 | 07:12 | ZN167:PA21 | URBAN | Other | Other - Arcing | 5 | 239 | 0.000813 | 3e-06 | N
26-09-18 | 06:31 | ZN2835:PA27 | URBAN | Asset Failure | LV | 52 | 163 | 0.005778 | 3.5e-05 | N
26-09-18 | 06:31 | ZN2835:PA30 | URBAN | Asset Failure | LV | 44 | 164 | 0.004909 | 3e-05 | N
26-09-18 | 06:41 | ZN965:PA38 | URBAN | Other | Other - Arcing | 1 | 214 | 0.000145 | 1e-06 | N
26-09-18 | 06:43 | ZN4545:PA24 | URBAN | Asset Failure | LV | 1 | 317 | 0.000216 | 1e-06 | N
26-09-18 | 06:51 | ZN167:PA20 | URBAN | Other | Other | 1 | 260 | 0.000177 | 1e-06 | N
26-09-18 | 07:29 | ZN167:PA1 | URBAN | Other | Other | 1 | 224 | 0.000152 | 1e-06 | N
26-09-18 | 08:14 | ZN180:PA19 | URBAN | Asset Failure | LV | 76 | 322 | 0.016645 | 5.2e-05 | N
26-09-18 | 09:19 | ZN12640:PA13 | SHORT RURAL | Other | Other | 1 | 201 | 0.000844 | 4e-06 | N
26-09-18 | 10:12 | ZN15006:PA15 | URBAN | Asset Failure | LV | 1 | 197 | 0.000134 | 1e-06 | N
26-09-18 | 10:18 | ZN2196:PA18 | URBAN | Other | Other - Arcing | 1 | 102 | 6.9e-05 | 1e-06 | N
26-09-18 | 11:10 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 130 | 0.001641 | 1.3e-05 | N
26-09-18 | 11:47 | ZN12690:PA14 | SHORT RURAL | Asset Failure | LV | 1 | 1,573 | 0.006618 | 4e-06 | N
26-09-18 | 12:04 | ZN10999:PA11 | URBAN | Other | Other - Self Clearing Trigger | 17 | 178 | 0.002056 | 1.2e-05 | N
26-09-18 | 11:59 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 26 | 106 | 0.011597 | 0.000109 | N
26-09-18 | 12:56 | 511:29877 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 79 | 0.000665 | 8e-06 | N
26-09-18 | 15:16 | ZN15006:PA12 | URBAN | Asset Failure | LV | 112 | 170 | 0.012976 | 7.6e-05 | N
26-09-18 | 16:02 | ZN847:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 92 | 93 | 0.00582 | 6.3e-05 | N
26-09-18 | 16:28 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 182 | 0.000765 | 4e-06 | N
26-09-18 | 16:30 | ZN36300:PA17 | URBAN | Other | Other | 1 | 256 | 0.000174 | 1e-06 | N
26-09-18 | 21:48 | ZN10994:PA18 | URBAN | Animal | Animal impact | 998 | 56 | 0.038019 | 0.000679 | N
27-09-18 | 02:06 | 402:H785 | URBAN | Asset Failure | Subtransmission | 3 | 425 | 0.000867 | 2e-06 | N
27-09-18 | 03:06 | ZN5868:PA14 | URBAN | Asset Failure | HV | 1,941 | 90 | 0.11833 | 0.00132 | N
27-09-18 | 03:41 | 513:48058 | URBAN | Other | Other | 1 | 82 | 5.5e-05 | 1e-06 | N
27-09-18 | 08:39 | ZN8700:PA65 66GHJ | CBD | Other | Other - Self Clearing Trigger | 6 | 246 | 0.048474 | 0.000197 | N
27-09-18 | 09:18 | ZN188:PA31 | URBAN | Third Party | Other | 34 | 282 | 0.006522 | 2.3e-05 | N
27-09-18 | 10:58 | ZN10993:PA39 | URBAN | Asset Failure | HV | 821 | 73 | 0.040881 | 0.000559 | N
27-09-18 | 11:24 | ZN2196:PA25 | URBAN | Other | Other | 2 | 152 | 0.000207 | 1e-06 | N
27-09-18 | 11:35 | ZN2602:PA3 | URBAN | Other | Other | 1 | 504 | 0.000343 | 1e-06 | N
27-09-18 | 11:53 | ZN1193:PA12 | URBAN | Third Party | Vehicle impact | 1 | 517 | 0.000352 | 1e-06 | N
27-09-18 | 12:01 | ZN1193:PA12 | URBAN | Other | Other | 1 | 91 | 6.2e-05 | 1e-06 | N
27-09-18 | 12:32 | ZN1287:PA21 | URBAN | Other | Other - Self Clearing Trigger | 66 | 88 | 0.003937 | 4.5e-05 | N
27-09-18 | 14:01 | 801:74119 | URBAN | Other | Other | 1 | 28 | 1.9e-05 | 1e-06 | N
27-09-18 | 14:04 | ZN10995:PA12 | URBAN | Third Party | Vehicle impact | 35 | 56 | 0.001333 | 2.4e-05 | N
27-09-18 | 15:23 | ZN36100:PA27 | URBAN | Other | Other - Arcing | 1 | 365 | 0.000248 | 1e-06 | N
27-09-18 | 15:50 | ZN10991:PA5 | URBAN | Asset Failure | HV | 1,510 | 66 | 0.067722 | 0.001027 | N
27-09-18 | 15:50 | ZN10991:PA6 | URBAN | Asset Failure | HV | 1,396 | 64 | 0.060778 | 0.00095 | N
27-09-18 | 16:51 | 522:83132 | SHORT RURAL | Other | Other | 1 | 133 | 0.000561 | 4e-06 | N
27-09-18 | 18:18 | 801:74118 | URBAN | Asset Failure | LV | 1 | 89 | 6.1e-05 | 1e-06 | N
27-09-18 | 18:47 | ZN10999:PA11 | URBAN | Asset Failure | LV | 18 | 808 | 0.009894 | 1.2e-05 | N
27-09-18 | 22:24 | ZN9900:PA9 | URBAN | Other | Other | 1 | 52 | 3.5e-05 | 1e-06 | N
28-09-18 | 08:05 | ZN262:PA21 | URBAN | Other | Other - Self Clearing Trigger | 7 | 150 | 0.000713 | 5e-06 | N
27-09-18 | 11:19 | ZN262:PA6 | URBAN | Asset Failure | LV | 89 | 176 | 0.010656 | 6.1e-05 | N
28-09-18 | 09:39 | ZN9534:PA17 | URBAN | Asset Failure | LV | 1 | 290 | 0.000197 | 1e-06 | N
28-09-18 | 09:56 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 159 | 0.000669 | 4e-06 | N
25-09-18 | 04:09 | ZN3672:PA23 | URBAN | Asset Failure | LV | 37 | 101 | 0.002542 | 2.5e-05 | N
28-09-18 | 12:45 | ZN3154:PA16 | URBAN | Asset Failure | LV | 28 | 145 | 0.002762 | 1.9e-05 | N
28-09-18 | 10:05 | ZN12630:PA3 | SHORT RURAL | Asset Failure | HV | 20 | 155 | 0.013032 | 8.4e-05 | N
28-09-18 | 10:40 | ZN2310:PA4 | URBAN | Other | Other - Self Clearing Trigger | 66 | 104 | 0.004679 | 4.5e-05 | N
28-09-18 | 17:22 | ZN14144:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 16 | 18 | 0.000195 | 1.1e-05 | N
28-09-18 | 11:59 | ZN4545:PA40 | URBAN | Third Party | Vehicle impact | 39 | 121 | 0.0032 | 2.7e-05 | N
28-09-18 | 13:19 | ZN12580:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 101 | 0.000412 | 4e-06 | N
28-09-18 | 13:44 | ZN4545:PA26 | URBAN | Third Party | Vehicle impact | 7 | 148 | 0.000705 | 5e-06 | N
28-09-18 | 15:14 | 522:83129 | URBAN | Other | Other | 1 | 158 | 0.000108 | 1e-06 | N
28-09-18 | 16:13 | ZN2310:PA4 | URBAN | Third Party | Vehicle impact | 1 | 88 | 6e-05 | 1e-06 | N
28-09-18 | 17:34 | ZN3922:PA29 | URBAN | Asset Failure | LV | 1 | 291 | 0.000198 | 1e-06 | N
28-09-18 | 21:22 | ZN2635:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 90 | 23 | 0.001408 | 6.1e-05 | N
28-09-18 | 18:22 | 507:80931 | URBAN | Other | Other | 1 | 97 | 6.6e-05 | 1e-06 | N
28-09-18 | 11:00 | 813:89059 | URBAN | Asset Failure | LV | 6 | 800 | 0.003265 | 4e-06 | N
28-09-18 | 20:33 | ZN12620:PA7 | URBAN | Weather |  | 26 | 147 | 0.002593 | 1.8e-05 | N
28-09-18 | 20:23 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 277 | 0.001164 | 4e-06 | N
29-09-18 | 06:04 | 222:33596 | URBAN | Third Party | Unauthorised access | 1,205 | 38 | 0.031524 | 0.00082 | N
29-09-18 | 09:13 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 34 | 127 | 0.018165 | 0.000143 | N
29-09-18 | 09:57 | ZN965:PA20 | URBAN | Asset Failure | LV | 27 | 381 | 0.006999 | 1.8e-05 | N
29-09-18 | 15:12 | ZN12650:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 44 | 71 | 0.013142 | 0.000185 | N
29-09-18 | 15:41 | ZN195:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 16 | 179 | 0.012048 | 6.7e-05 | N
29-09-18 | 17:54 | ZN12610:PA22 | URBAN | Other | Other - Arcing | 1 | 130 | 8.8e-05 | 1e-06 | N
30-09-18 | 06:57 | 224:80346 | URBAN | Animal | Animal impact | 101 | 63 | 0.004328 | 6.9e-05 | N
30-09-18 | 09:29 | 242:81533 | SHORT RURAL | Animal | Animal impact | 1 | 76 | 0.00032 | 4e-06 | N
30-09-18 | 16:47 | ZN3154:PA3 | URBAN | Animal | Animal impact | 25 | 271 | 0.004608 | 1.7e-05 | N
30-09-18 | 23:21 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 18 | 188 | 1.1886 | 0.006322 | N
01-10-18 | 06:04 | ZN15014:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 742 | 0.003121 | 4e-06 | N
01-10-18 | 11:32 | 813:89055 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 12 | 48 | 0.002423 | 5e-05 | N
01-10-18 | 12:19 | 238:34148 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 63 | 0.00053 | 8e-06 | N
01-10-18 | 13:15 | ZN10999:PA10 | URBAN | Asset Failure | LV | 1 | 199 | 0.000135 | 1e-06 | N
01-10-18 | 18:23 | 258:80779 | URBAN | Other | Other | 1 | 73 | 5e-05 | 1e-06 | N
01-10-18 | 21:40 | 507:80917 | URBAN | Other | Other | 1 | 44 | 3e-05 | 1e-06 | N
01-10-18 | 22:28 | ZN931:PA26 | URBAN | Other | Other - Self Clearing Trigger | 81 | 77 | 0.004229 | 5.5e-05 | N
02-10-18 | 00:05 | ZN847:PA14 | URBAN | Animal | Animal impact | 391 | 43 | 0.011435 | 0.000266 | N
02-10-18 | 01:49 | ZN2635:PA38 | URBAN | Other | Other | 22 | 381 | 0.005701 | 1.5e-05 | N
02-10-18 | 07:07 | 512:83743 | SHORT RURAL | Other | Other | 1 | 73 | 0.000307 | 4e-06 | N
02-10-18 | 07:28 | ZN965:PA6 | URBAN | Third Party | Vehicle impact | 27 | 119 | 0.002185 | 1.8e-05 | N
02-10-18 | 07:34 | 220:8691 | URBAN | Other | Other | 1 | 61 | 4.1e-05 | 1e-06 | N
02-10-18 | 07:50 | 238:34148 | SHORT RURAL | Asset Failure | LV | 1 | 370 | 0.001555 | 4e-06 | N
02-10-18 | 07:51 | ZN15014:PA19 | URBAN | Third Party | Vehicle impact | 1 | 369 | 0.000251 | 1e-06 | N
02-10-18 | 08:16 | ZN2568:PA27 | URBAN | Third Party | Vehicle impact | 14 | 330 | 0.003143 | 1e-05 | N
02-10-18 | 08:16 | ZN2568:PA29 | URBAN | Third Party | Vehicle impact | 43 | 159 | 0.00465 | 2.9e-05 | N
02-10-18 | 08:21 | ZN14891:PA20 | SHORT RURAL | Other | Other | 1 | 68 | 0.000287 | 4e-06 | N
02-10-18 | 08:43 | ZN3155:PA23 | URBAN | Asset Failure | HV | 1,317 | 63 | 0.056395 | 0.000896 | N
02-10-18 | 09:41 | 810:74062 | SHORT RURAL | Other | Other | 1 | 51 | 0.000213 | 4e-06 | N
02-10-18 | 09:45 | ZN14143:PA6 | URBAN | Overloads |  | 1 | 255 | 0.000173 | 1e-06 | N
02-10-18 | 13:05 | 807:74183 | SHORT RURAL | Other | Other | 3 | 65 | 0.00082 | 1.3e-05 | N
28-09-18 | 10:15 | 813:89063 | SHORT RURAL | Asset Failure | LV | 18 | 25 | 0.001894 | 7.6e-05 | N
02-10-18 | 13:56 | ZN3472:PA17 | URBAN | Third Party | Vehicle impact | 94 | 124 | 0.007928 | 6.4e-05 | N
02-10-18 | 14:22 | ZN10998:PA25 | URBAN | Other | Other - Self Clearing Trigger | 87 | 88 | 0.005226 | 5.9e-05 | N
02-10-18 | 15:35 | ZN1287:PA23 | URBAN | Other | Other | 1 | 387 | 0.000263 | 1e-06 | N
02-10-18 | 21:27 | ZN35900:PA23 | SHORT RURAL | Third Party | Vehicle impact | 1 | 579 | 0.002434 | 4e-06 | N
03-10-18 | 02:38 | ZN180:PA7 | URBAN | Asset Failure | LV | 79 | 1,051 | 0.056491 | 5.4e-05 | N
03-10-18 | 07:13 | ZN690:PA14 | URBAN | Asset Failure | LV | 1 | 482 | 0.000328 | 1e-06 | N
03-10-18 | 09:28 | 205:12213 | SHORT RURAL | Other | Other | 1 | 31 | 0.000131 | 4e-06 | N
03-10-18 | 18:00 | ZN10999:PA17 | URBAN | Asset Failure | LV | 25 | 144 | 0.002449 | 1.7e-05 | N
03-10-18 | 16:33 | 513:48059 | SHORT RURAL | Asset Failure | HV | 7 | 77 | 0.002268 | 2.9e-05 | N
03-10-18 | 20:11 | ZN398:PA3 | URBAN | Asset Failure | LV | 1 | 239 | 0.000162 | 1e-06 | N
03-10-18 | 21:12 | ZN10990:PA6 | URBAN | Asset Failure | LV | 62 | 62 | 0.002626 | 4.2e-05 | N
04-10-18 | 05:02 | ZN2602:PA41 | URBAN | Third Party | Vehicle impact | 52 | 358 | 0.012662 | 3.5e-05 | N
04-10-18 | 07:04 | ZN35600:PA14 | URBAN | Other | Other | 1 | 340 | 0.000231 | 1e-06 | N
04-10-18 | 07:32 | ZN2602:PA35 | URBAN | Other | Other - Self Clearing Trigger | 12 | 238 | 0.001943 | 8e-06 | N
04-10-18 | 10:31 | 256:80632 | URBAN | Other | Other | 1 | 67 | 4.5e-05 | 1e-06 | N
04-10-18 | 11:06 | ZN2602:PA41 | URBAN | Other | Other | 2 | 108 | 0.000147 | 1e-06 | N
04-10-18 | 12:27 | ZN1287:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,181 | 0.000803 | 1e-06 | N
03-10-18 | 09:14 | ZN12630:PA8 | SHORT RURAL | Asset Failure | LV | 1 | 331 | 0.001392 | 4e-06 | N
04-10-18 | 14:33 | ZN116:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 66 | 208 | 0.00933 | 4.5e-05 | N
04-10-18 | 14:08 | ZN847:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 202 | 0.000137 | 1e-06 | N
04-10-18 | 14:27 | ZN15012:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,153 | 171 | 0.13376 | 0.000784 | N
04-10-18 | 15:43 | 220:8689 | URBAN | Other | Other - Arcing | 1 | 200 | 0.000136 | 1e-06 | N
04-10-18 | 18:51 | ZN1068:PA26 | URBAN | Other | Other - Self Clearing Trigger | 93 | 83 | 0.005276 | 6.3e-05 | N
04-10-18 | 18:54 | ZN12690:PA6 | URBAN | Third Party | Vehicle impact | 2 | 996 | 0.001355 | 1e-06 | N
04-10-18 | 22:47 | 257:81987 | URBAN | Asset Failure | LV | 1 | 702 | 0.000478 | 1e-06 | N
04-10-18 | 23:17 | ZN1788:PA14 | URBAN | Asset Failure | LV | 1 | 282 | 0.000192 | 1e-06 | N
05-10-18 | 00:11 | ZN12650:PA9 | URBAN | Asset Failure | HV | 1,281 | 134 | 0.11671 | 0.000871 | N
05-10-18 | 00:14 | ZN3472:PA33 | URBAN | Third Party | Vehicle impact | 123 | 60 | 0.005021 | 8.4e-05 | N
05-10-18 | 00:25 | ZN36100:PA2 | URBAN | Asset Failure | LV | 1 | 755 | 0.000514 | 1e-06 | N
05-10-18 | 00:52 | ZN14144:PA1 | URBAN | Asset Failure | LV | 81 | 523 | 0.028797 | 5.5e-05 | N
05-10-18 | 01:03 | ZN15014:PA7 | URBAN | Asset Failure | LV | 1 | 641 | 0.000436 | 1e-06 | N
05-10-18 | 01:07 | ZN15002:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 50 | 83 | 0.017421 | 0.00021 | N
05-10-18 | 01:06 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 309 | 0.005885 | 1.9e-05 | N
05-10-18 | 03:35 | ZN10998:PA17 | URBAN | Other | Other | 1 | 52 | 3.6e-05 | 1e-06 | N
05-10-18 | 03:42 | ZN10998:PA17 | URBAN | Other | Other | 1 | 45 | 3.1e-05 | 1e-06 | N
05-10-18 | 04:46 | ZN12620:PA10 | SHORT RURAL | Asset Failure | HV | 339 | 59 | 0.084145 | 0.001426 | N
05-10-18 | 05:10 | 221:11897 | URBAN | Vegetation | Vegetation Blow/Fall In | 861 | 186 | 0.10871 | 0.000586 | N
05-10-18 | 05:27 | ZN12650:PA2 | URBAN | Animal | Animal impact | 33 | 198 | 0.004444 | 2.2e-05 | N
05-10-18 | 06:08 | ZN9037:PA2 | URBAN | Third Party | Other | 1 | 142 | 9.6e-05 | 1e-06 | N
05-10-18 | 05:32 | ZN15006:PA16 | URBAN | Other | Other - Self Clearing Trigger | 64 | 112 | 0.00489 | 4.4e-05 | N
05-10-18 | 05:41 | ZN10994:PA11 | URBAN | Other | Other - Self Clearing Trigger | 49 | 132 | 0.004393 | 3.3e-05 | N
05-10-18 | 06:20 | ZN1285:PA35 | URBAN | Asset Failure | HV | 677 | 90 | 0.041342 | 0.00046 | N
05-10-18 | 07:09 | ZN10991:PA13 | URBAN | Third Party | Other | 1 | 126 | 8.6e-05 | 1e-06 | N
05-10-18 | 07:37 | ZN14892:PA13 | SHORT RURAL | Asset Failure | LV | 85 | 262 | 0.093839 | 0.000358 | N
05-10-18 | 08:41 | ZN12600:PA1 | SHORT RURAL | Other | Other | 1 | 219 | 0.00092 | 4e-06 | N
05-10-18 | 08:57 | ZN1068:PA18 | URBAN | Asset Failure | LV | 11 | 2,282 | 0.017075 | 7e-06 | N
05-10-18 | 08:59 | ZN180:PA30 | URBAN | Other | Other - Self Clearing Trigger | 36 | 91 | 0.002221 | 2.4e-05 | N
05-10-18 | 08:59 | 806:82662 | SHORT RURAL | Other | Other | 225 | 464 | 0.439 | 0.000947 | N
05-10-18 | 08:59 | 806:82667 | SHORT RURAL | Other | Other | 40 | 8 | 0.001346 | 0.000168 | N
05-10-18 | 09:11 | ZN167:PA10 | URBAN | Asset Failure | LV | 71 | 79 | 0.003795 | 4.8e-05 | N
05-10-18 | 10:02 | ZN15010:PA30 | URBAN | Other | Other - Arcing | 1 | 657 | 0.000447 | 1e-06 | N
05-10-18 | 04:40 | 206:34440 | URBAN | Asset Failure | HV | 1,615 | 94 | 0.10358 | 0.001098 | N
05-10-18 | 10:45 | 239:82131 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 89 | 0.000375 | 4e-06 | N
05-10-18 | 10:48 | ZN15004:PA9 | URBAN | Asset Failure | LV | 1 | 217 | 0.000147 | 1e-06 | N
05-10-18 | 10:51 | 221:11897 | URBAN | Other | Other - Self Clearing Trigger | 64 | 48 | 0.002106 | 4.4e-05 | N
05-10-18 | 11:09 | ZN180:PA30 | URBAN | Asset Failure | LV | 36 | 111 | 0.002718 | 2.4e-05 | N
05-10-18 | 11:14 | 810:74050 | SHORT RURAL | Other | Other | 137 | 4 | 0.002305 | 0.000576 | N
05-10-18 | 11:14 | 810:74054 | LONG RURAL | Other | Other | 316 | 4 | 0.44398 | 0.11099 | N
05-10-18 | 11:14 | 810:74058 | SHORT RURAL | Other | Other | 197 | 4 | 0.003315 | 0.000829 | N
05-10-18 | 11:14 | 810:74062 | SHORT RURAL | Other | Other | 574 | 4 | 0.009659 | 0.002415 | N
05-10-18 | 11:29 | 515:35197 | LONG RURAL | Asset Failure | HV | 141 | 79 | 3.9125 | 0.049526 | N
04-10-18 | 23:26 | 228:7486 | URBAN | Asset Failure | Distribution substation | 3 | 19 | 3.9e-05 | 2e-06 | N
05-10-18 | 13:40 | 264:81236 | URBAN | Other | Other | 1 | 44 | 3e-05 | 1e-06 | N
05-10-18 | 14:14 | 511:29878 | SHORT RURAL | Asset Failure | LV | 6 | 121 | 0.003054 | 2.5e-05 | N
05-10-18 | 14:16 | ZN14892:PA16 | URBAN | Asset Failure | LV | 1 | 314 | 0.000213 | 1e-06 | N
05-10-18 | 14:38 | ZN12580:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 68 | 37 | 0.001693 | 4.6e-05 | N
05-10-18 | 15:27 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 173 | 0.004367 | 2.5e-05 | N
05-10-18 | 15:23 | ZN12580:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,030 | 49 | 0.034056 | 0.000701 | N
05-10-18 | 15:58 | ZN14891:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 87 | 0.002562 | 2.9e-05 | N
05-10-18 | 16:51 | 509:33395 | LONG RURAL | Asset Failure | HV | 45 | 364 | 5.7492 | 0.015806 | N
05-10-18 | 16:53 | ZN9700:PA20 | URBAN | Weather |  | 1 | 242 | 0.000164 | 1e-06 | N
05-10-18 | 19:07 | ZN1673:PA20 | URBAN | Other | Other - Self Clearing Trigger | 3 | 108 | 0.00022 | 2e-06 | N
05-10-18 | 19:30 | ZN2635:PA46 | URBAN | Vegetation | Vegetation Blow/Fall In | 501 | 36 | 0.012267 | 0.000341 | N
05-10-18 | 19:30 | ZN2635:PA57 | URBAN | Vegetation | Vegetation Blow/Fall In | 109 | 36 | 0.002669 | 7.4e-05 | N
05-10-18 | 21:47 | ZN15012:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,130 | 0.000769 | 1e-06 | N
05-10-18 | 22:09 | ZN4545:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 741 | 0.01764 | 2.4e-05 | N
05-10-18 | 22:10 | ZN4545:PA41 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 52 | 740 | 0.16182 | 0.000219 | N
05-10-18 | 22:03 | ZN12580:PA1 | URBAN | Third Party | Vehicle impact | 1,179 | 110 | 0.088229 | 0.000802 | N
05-10-18 | 22:56 | ZN931:PA2 | URBAN | Asset Failure | LV | 73 | 1,354 | 0.067219 | 5e-05 | N
06-10-18 | 03:16 | ZN2635:PA44 | URBAN | Asset Failure | HV | 993 | 80 | 0.053875 | 0.000675 | N
06-10-18 | 05:23 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 312 | 0.003938 | 1.3e-05 | N
06-10-18 | 05:58 | ZN398:PA4 | URBAN | Asset Failure | LV | 54 | 322 | 0.011827 | 3.7e-05 | N
06-10-18 | 05:58 | ZN690:PA30 | URBAN | Asset Failure | LV | 72 | 322 | 0.015769 | 4.9e-05 | N
06-10-18 | 07:33 | ZN3155:PA44 | URBAN | Asset Failure | LV | 1 | 635 | 0.000432 | 1e-06 | N
06-10-18 | 08:54 | ZN35500:PA35 | URBAN | Other | Other - Self Clearing Trigger | 8 | 351 | 0.00191 | 5e-06 | N
06-10-18 | 09:08 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 47 | 0.000198 | 4e-06 | N
06-10-18 | 10:07 | 243:80081 | SHORT RURAL | Asset Failure | LV | 1 | 715 | 0.003009 | 4e-06 | N
06-10-18 | 11:45 | ZN965:PA28 | URBAN | Third Party | Vehicle impact | 1 | 255 | 0.000173 | 1e-06 | N
06-10-18 | 12:18 | ZN847:PA18 | SHORT RURAL | Third Party | Vehicle impact | 1 | 3,039 | 0.012784 | 4e-06 | N
06-10-18 | 12:10 | ZN4545:PA41 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 52 | 50 | 0.010938 | 0.000219 | N
06-10-18 | 17:00 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 35 | 0.001119 | 3.2e-05 | N
06-10-18 | 13:50 | 257:81991 | URBAN | Third Party | Other | 1 | 175 | 0.000119 | 1e-06 | N
06-10-18 | 13:31 | ZN12570:PA40 | SHORT RURAL | Other | Other - Arcing | 1 | 178 | 0.000749 | 4e-06 | N
06-10-18 | 14:03 | ZN1193:PA10 | URBAN | Other | Other | 1 | 128 | 8.7e-05 | 1e-06 | N
06-10-18 | 19:54 | ZN10999:PA28 | URBAN | Asset Failure | LV | 1 | 165 | 0.000112 | 1e-06 | N
06-10-18 | 20:00 | ZN35500:PA18 | URBAN | Third Party | Vehicle impact | 51 | 70 | 0.002423 | 3.5e-05 | N
06-10-18 | 23:06 | ZN12620:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 710 | 0.002989 | 4e-06 | N
07-10-18 | 00:16 | ZN12610:PA20 | SHORT RURAL | Third Party | Vehicle impact | 1 | 1,094 | 0.004602 | 4e-06 | N
07-10-18 | 00:41 | ZN14892:PA19 | URBAN | Third Party | Vehicle impact | 1 | 649 | 0.000441 | 1e-06 | N
07-10-18 | 07:09 | 224:80337 | URBAN | Third Party | Vehicle impact | 1,648 | 46 | 0.051562 | 0.001121 | N
07-10-18 | 07:09 | 224:80340 | SHORT RURAL | Third Party | Vehicle impact | 1,089 | 135 | 0.61966 | 0.004581 | N
07-10-18 | 07:09 | 224:80341 | URBAN | Third Party | Vehicle impact | 1,247 | 47 | 0.039864 | 0.000848 | N
07-10-18 | 07:47 | ZN35500:PA35 | URBAN | Asset Failure | LV | 8 | 160 | 0.000871 | 5e-06 | N
07-10-18 | 09:25 | 256:80635 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 73 | 5e-05 | 1e-06 | N
07-10-18 | 10:45 | ZN1673:PA20 | URBAN | Asset Failure | LV | 3 | 170 | 0.000347 | 2e-06 | N
07-10-18 | 11:47 | ZN9900:PA2 | URBAN | Other | Other - Self Clearing Trigger | 40 | 71 | 0.001932 | 2.7e-05 | N
08-10-18 | 00:40 | ZN2602:PA36 | URBAN | Asset Failure | LV | 43 | 30 | 0.000877 | 2.9e-05 | N
07-10-18 | 13:04 | ZN10991:PA1 | URBAN | Asset Failure | Zone substation | 1,514 | 46 | 0.04737 | 0.00103 | N
07-10-18 | 13:04 | ZN10991:PA13 | URBAN | Asset Failure | Zone substation | 1 | 46 | 3.1e-05 | 1e-06 | N
07-10-18 | 13:04 | ZN10991:PA5 | URBAN | Asset Failure | Zone substation | 1,509 | 46 | 0.047213 | 0.001026 | N
07-10-18 | 13:04 | ZN10991:PA6 | URBAN | Asset Failure | Zone substation | 1,395 | 46 | 0.043647 | 0.000949 | N
07-10-18 | 13:04 | ZN10999:PA36 | URBAN | Asset Failure | Zone substation | 160 | 46 | 0.005006 | 0.000109 | N
07-10-18 | 13:30 | ZN4545:PA31 | URBAN | Asset Failure | LV | 52 | 329 | 0.011646 | 3.5e-05 | N
07-10-18 | 17:30 | ZN3472:PA35 | URBAN | Third Party | Vehicle impact | 12 | 555 | 0.00453 | 8e-06 | N
07-10-18 | 14:30 | ZN14892:PA21 | URBAN | Asset Failure | LV | 4 | 194 | 0.000528 | 3e-06 | N
07-10-18 | 13:50 | ZN10991:PA5 | URBAN | Network business | Network error | 119 | 220 | 0.017807 | 8.1e-05 | N
07-10-18 | 15:42 | 238:34141 | SHORT RURAL | Asset Failure | LV | 9 | 183 | 0.006929 | 3.8e-05 | N
07-10-18 | 18:01 | ZN3472:PA35 | URBAN | Third Party | Vehicle impact | 10 | 543 | 0.003693 | 7e-06 | N
07-10-18 | 21:13 | ZN2635:PA57 | URBAN | Other | Other - Arcing | 1,566 | 38 | 0.040472 | 0.001065 | N
07-10-18 | 20:45 | ZN15012:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 1,125 | 0.003061 | 3e-06 | N
07-10-18 | 21:13 | ZN2635:PA46 | URBAN | Other | Other - Arcing | 501 | 28 | 0.009541 | 0.000341 | N
07-10-18 | 21:13 | ZN2635:PA57 | URBAN | Other | Other - Arcing | 109 | 92 | 0.006821 | 7.4e-05 | N
07-10-18 | 21:27 | ZN398:PA4 | URBAN | Asset Failure | Distribution substation | 208 | 277 | 0.039245 | 0.000141 | N
07-10-18 | 22:11 | ZN36300:PA8 | URBAN | Other | Other - Arcing | 1 | 1,188 | 0.000808 | 1e-06 | N
07-10-18 | 22:26 | 256:80638 | URBAN | Animal | Animal impact | 41 | 69 | 0.001924 | 2.8e-05 | N
07-10-18 | 23:22 | ZN15004:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 63 | 543 | 0.023262 | 4.3e-05 | N
08-10-18 | 00:03 | ZN36300:PA11 | URBAN | Other | Other - Arcing | 3 | 1,152 | 0.002351 | 2e-06 | N
08-10-18 | 00:32 | ZN965:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 257 | 0.006645 | 2.6e-05 | N
08-10-18 | 04:53 | ZN35370:PA4 | SHORT RURAL | Third Party | Unauthorised access | 40 | 155 | 0.026084 | 0.000168 | N
08-10-18 | 08:30 | ZN15002:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 55 | 285 | 0.010662 | 3.7e-05 | N
08-10-18 | 07:28 | ZN10991:PA1 | URBAN | Asset Failure | Zone substation | 1,514 | 6 | 0.006179 | 0.00103 | N
08-10-18 | 07:28 | ZN10991:PA5 | URBAN | Asset Failure | Zone substation | 1,509 | 6 | 0.006158 | 0.001026 | N
08-10-18 | 07:28 | ZN10991:PA6 | URBAN | Asset Failure | Zone substation | 1,395 | 6 | 0.005693 | 0.000949 | N
08-10-18 | 07:52 | ZN14143:PA6 | URBAN | Asset Failure | HV | 56 | 60 | 0.002288 | 3.8e-05 | N
08-10-18 | 08:29 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 79 | 126 | 0.041877 | 0.000332 | N
08-10-18 | 08:30 | ZN129:PA56 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 344 | 0.000234 | 1e-06 | N
08-10-18 | 10:57 | ZN12660:PA14 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 152 | 0.00064 | 4e-06 | N
08-10-18 | 11:10 | ZN3472:PA8 | URBAN | Third Party | Other | 32 | 69 | 0.001502 | 2.2e-05 | N
08-10-18 | 14:58 | ZN2196:PA25 | URBAN | Other | Other | 1 | 1,206 | 0.00082 | 1e-06 | N
08-10-18 | 15:46 | ZN14892:PA13 | SHORT RURAL | Other | Other | 1 | 57 | 0.00024 | 4e-06 | N
08-10-18 | 16:41 | ZN9252:PA22 | URBAN | Asset Failure | LV | 1 | 272 | 0.000185 | 1e-06 | N
08-10-18 | 17:14 | ZN15010:PA25 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 161 | 0.000676 | 4e-06 | N
08-10-18 | 21:22 | ZN15010:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 397 | 0.00027 | 1e-06 | N
09-10-18 | 06:14 | ZN14143:PA17 | SHORT RURAL | Other | Other - Arcing | 237 | 745 | 0.74308 | 0.000997 | N
09-10-18 | 06:55 | 407:MS4 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1 | 110 | 7.5e-05 | 1e-06 | N
09-10-18 | 06:55 | 801:74117 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 513 | 79 | 0.1705 | 0.002158 | N
09-10-18 | 06:55 | 801:74118 | URBAN | Animal | Animal nesting/burrowing, etc and other | 893 | 79 | 0.047985 | 0.000607 | N
09-10-18 | 06:55 | 801:74119 | URBAN | Animal | Animal nesting/burrowing, etc and other | 654 | 79 | 0.035142 | 0.000445 | N
09-10-18 | 06:55 | 801:74120 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 572 | 79 | 0.19011 | 0.002406 | N
09-10-18 | 06:55 | 801:74121 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 457 | 79 | 12.6811 | 0.16052 | N
09-10-18 | 06:55 | 801:74122 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,115 | 79 | 0.059914 | 0.000758 | N
09-10-18 | 06:55 | 801:74123 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 277 | 79 | 0.092063 | 0.001165 | N
09-10-18 | 04:29 | ZN262:PA34 | URBAN | Third Party | Vehicle impact | 10 | 421 | 0.002864 | 7e-06 | N
09-10-18 | 07:49 | ZN9550:PA11 | URBAN | Asset Failure | HV | 449 | 56 | 0.017069 | 0.000305 | N
09-10-18 | 08:22 | 524:33576 | SHORT RURAL | Other | Other | 1 | 87 | 0.000366 | 4e-06 | N
09-10-18 | 10:49 | ZN36100:PA8 | URBAN | Asset Failure | LV | 1 | 221 | 0.00015 | 1e-06 | N
09-10-18 | 11:51 | ZN36300:PA3 | URBAN | Asset Failure | LV | 1 | 489 | 0.000332 | 1e-06 | N
09-10-18 | 15:00 | 239:82136 | URBAN | Other | Other | 1 | 108 | 7.4e-05 | 1e-06 | N
09-10-18 | 16:05 | ZN262:PA31 | URBAN | Network business | Network error | 107 | 85 | 0.00616 | 7.3e-05 | N
09-10-18 | 17:10 | ZN14143:PA17 | SHORT RURAL | Asset Failure | HV | 165 | 97 | 0.067334 | 0.000694 | N
09-10-18 | 18:03 | ZN15010:PA25 | SHORT RURAL | Third Party | Vehicle impact | 1 | 237 | 0.000995 | 4e-06 | N
09-10-18 | 20:20 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 3 | 62 | 0.000783 | 1.3e-05 | N
09-10-18 | 07:27 | 813:89061 | LONG RURAL | Asset Failure | HV | 5 | 333 | 0.58483 | 0.001756 | N
10-10-18 | 11:30 | ZN12690:PA12 | SHORT RURAL | Asset Failure | HV | 5 | 500 | 0.010518 | 2.1e-05 | N
10-10-18 | 10:02 | 224:80346 | URBAN | Weather |  | 93 | 118 | 0.007448 | 6.3e-05 | N
10-10-18 | 10:04 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 61 | 0.001027 | 1.7e-05 | N
10-10-18 | 10:30 | 261:81882 | URBAN | Weather |  | 33 | 64 | 0.001443 | 2.2e-05 | N
10-10-18 | 11:29 | ZN4545:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 375 | 0.007406 | 2e-05 | N
10-10-18 | 11:17 | ZN7481:PA1 | URBAN | Other | Other | 1 | 101 | 6.8e-05 | 1e-06 | N
10-10-18 | 11:18 | 242:81538 | URBAN | Asset Failure | HV | 735 | 98 | 0.049149 | 0.0005 | N
10-10-18 | 11:34 | 210:83466 | URBAN | Other | Other - Self Clearing Trigger | 122 | 111 | 0.009211 | 8.3e-05 | N
10-10-18 | 12:07 | ZN180:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 61 | 4.1e-05 | 1e-06 | N
10-10-18 | 17:05 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 50 | 0.000918 | 1.8e-05 | N
10-10-18 | 11:27 | ZN10993:PA39 | URBAN | Asset Failure | HV | 567 | 168 | 0.064792 | 0.000386 | N
10-10-18 | 11:27 | ZN10994:PA4 | URBAN | Asset Failure | HV | 1 | 543 | 0.000369 | 1e-06 | N
10-10-18 | 12:51 | ZN12580:PA16 | URBAN | Asset Failure | HV | 68 | 59 | 0.002729 | 4.6e-05 | N
10-10-18 | 13:12 | ZN630:PA14 | URBAN | Asset Failure | LV | 1 | 227 | 0.000155 | 1e-06 | N
10-10-18 | 13:31 | 509:33397 | SHORT RURAL | Asset Failure | LV | 2 | 89 | 0.000749 | 8e-06 | N
10-10-18 | 13:34 | ZN2635:PA41 | URBAN | Asset Failure | LV | 12 | 144 | 0.001175 | 8e-06 | N
10-10-18 | 14:42 | 258:80791 | URBAN | Weather |  | 1 | 1,370 | 0.000932 | 1e-06 | N
10-10-18 | 15:02 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 322 | 196 | 0.26611 | 0.001355 | N
10-10-18 | 11:20 | 813:89062 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 90 | 0.000379 | 4e-06 | N
10-10-18 | 16:56 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 124 | 0.000522 | 4e-06 | N
10-10-18 | 17:27 | 213:33771 | URBAN | Other | Other | 1 | 31 | 2.1e-05 | 1e-06 | N
10-10-18 | 19:19 | 508:82578 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 76 | 0.000319 | 4e-06 | N
10-10-18 | 19:58 | ZN12570:PA39 | URBAN | Overloads |  | 1 | 151 | 0.000103 | 1e-06 | N
10-10-18 | 22:45 | 810:74062 | SHORT RURAL | Asset Failure | HV | 66 | 85 | 0.023602 | 0.000278 | N
10-10-18 | 21:28 | ZN9252:PA21 | URBAN | Asset Failure | LV | 1 | 695 | 0.000473 | 1e-06 | N
10-10-18 | 21:13 | 810:74050 | SHORT RURAL | Asset Failure | HV | 90 | 177 | 0.067019 | 0.000379 | N
11-10-18 | 04:41 | ZN15009:PA5 | URBAN | Other | Other - Arcing | 1 | 349 | 0.000237 | 1e-06 | N
11-10-18 | 06:15 | 264:81240 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 97 | 0.002449 | 2.5e-05 | N
11-10-18 | 08:20 | ZN1193:PA28 | URBAN | Asset Failure | LV | 13 | 265 | 0.002343 | 9e-06 | N
11-10-18 | 09:50 | ZN2635:PA43 | SHORT RURAL | Other | Other - Arcing | 1 | 1,750 | 0.007362 | 4e-06 | N
11-10-18 | 10:03 | ZN12640:PA14 | URBAN | Other | Other - Arcing | 1 | 537 | 0.000365 | 1e-06 | N
11-10-18 | 11:55 | ZN35600:PA6 | URBAN | Other | Other - Arcing | 1 | 184 | 0.000125 | 1e-06 | N
11-10-18 | 13:21 | ZN2568:PA32 | URBAN | Other | Other - Self Clearing Trigger | 80 | 58 | 0.003158 | 5.4e-05 | N
11-10-18 | 13:45 | ZN263:PA33 34ABC | CBD | Other | Other | 2 | 75 | 0.004928 | 6.6e-05 | N
11-10-18 | 14:21 | ZN1285:PA27 | URBAN | Network business | Switching and protection error | 61 | 108 | 0.004498 | 4.1e-05 | N
11-10-18 | 15:23 | 216:10722 | SHORT RURAL | Other | Other | 1 | 1,059 | 0.004455 | 4e-06 | N
11-10-18 | 16:10 | 813:89061 | LONG RURAL | Asset Failure | LV | 3 | 130 | 0.13699 | 0.001054 | N
11-10-18 | 16:30 | ZN180:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 67 | 4.5e-05 | 1e-06 | N
11-10-18 | 18:13 | ZN384:PA70 | URBAN | Third Party | Other | 1 | 242 | 0.000164 | 1e-06 | N
11-10-18 | 19:57 | 511:29878 | SHORT RURAL | Asset Failure | LV | 1 | 565 | 0.002378 | 4e-06 | N
11-10-18 | 21:48 | ZN12570:PA33 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 13 | 87 | 0.004758 | 5.5e-05 | N
11-10-18 | 22:50 | ZN1673:PA2 | URBAN | Other | Other - Arcing | 1 | 370 | 0.000251 | 1e-06 | N
12-10-18 | 01:47 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 313 | 0.009201 | 2.9e-05 | N
12-10-18 | 04:14 | ZN15005:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 246 | 0.000167 | 1e-06 | N
12-10-18 | 04:23 | ZN965:PA47 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 202 | 0.004535 | 2.2e-05 | N
12-10-18 | 04:47 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 419 | 169 | 0.29718 | 0.00176 | N
12-10-18 | 07:41 | ZN1285:PA17 | URBAN | Asset Failure | LV | 74 | 244 | 0.012283 | 5e-05 | N
12-10-18 | 07:41 | ZN35900:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 244 | 0.001025 | 4e-06 | N
12-10-18 | 08:04 | ZN2602:PA20 | URBAN | Asset Failure | LV | 1 | 55 | 3.7e-05 | 1e-06 | N
12-10-18 | 11:10 | ZN10998:PA32 | SHORT RURAL | Other | Other - Arcing | 1 | 259 | 0.001089 | 4e-06 | N
12-10-18 | 11:17 | ZN2196:PA2 | URBAN | Asset Failure | LV | 1 | 203 | 0.000138 | 1e-06 | N
12-10-18 | 11:28 | ZN15001:PA18 | URBAN | Third Party | Vehicle impact | 1 | 182 | 0.000124 | 1e-06 | N
12-10-18 | 11:44 | ZN10999:PA24 | URBAN | Asset Failure | LV | 75 | 75 | 0.003833 | 5.1e-05 | N
12-10-18 | 12:19 | 235:2857 | SHORT RURAL | Other | Other | 1 | 98 | 0.000413 | 4e-06 | N
12-10-18 | 12:44 | ZN12650:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 276 | 0.008074 | 2.9e-05 | N
12-10-18 | 13:39 | ZN12630:PA3 | SHORT RURAL | Asset Failure | HV | 414 | 179 | 0.31173 | 0.001739 | N
10-10-18 | 14:00 | ZN15002:PA6 | URBAN | Other | Other - Self Clearing Trigger | 52 | 10 | 0.000354 | 3.5e-05 | N
12-10-18 | 04:00 | 238:34136 | URBAN | Asset Failure | LV | 1 | 1,067 | 0.000726 | 1e-06 | N
12-10-18 | 17:09 | ZN4545:PA35 | URBAN | Asset Failure | LV | 1 | 1,070 | 0.000728 | 1e-06 | N
12-10-18 | 17:37 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 63 | 0.000265 | 4e-06 | N
12-10-18 | 22:35 | 801:74122 | URBAN | Asset Failure | LV | 1 | 605 | 0.000411 | 1e-06 | N
13-10-18 | 00:55 | ZN965:PA3 | URBAN | Other | Other - Self Clearing Trigger | 99 | 345 | 0.023232 | 6.7e-05 | N
13-10-18 | 04:20 | ZN12570:PA37 | SHORT RURAL | Asset Failure | HV | 1,944 | 181 | 1.4763 | 0.008168 | N
13-10-18 | 05:53 | ZN12570:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 16 | 782 | 0.00851 | 1.1e-05 | N
13-10-18 | 07:10 | 415:33904 | URBAN | Third Party | Other | 1 | 90 | 6.1e-05 | 1e-06 | N
13-10-18 | 06:55 | ZN965:PA29 | URBAN | Asset Failure | HV | 762 | 95 | 0.049064 | 0.000518 | N
13-10-18 | 10:25 | ZN690:PA17 | URBAN | Other | Other | 1 | 286 | 0.000194 | 1e-06 | N
13-10-18 | 10:56 | 230:81440 | URBAN | Other | Other | 1 | 108 | 7.4e-05 | 1e-06 | N
13-10-18 | 11:59 | ZN12650:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 25 | 362 | 0.037973 | 0.000105 | N
13-10-18 | 15:24 | ZN35600:PA25 | URBAN | Third Party | Other | 18 | 248 | 0.003036 | 1.2e-05 | N
13-10-18 | 16:57 | ZN35500:PA28 | URBAN | Other | Other - Arcing | 1 | 244 | 0.000166 | 1e-06 | N
13-10-18 | 17:44 | 532:83293 | URBAN | Other | Other | 50 | 240 | 0.008172 | 3.4e-05 | N
13-10-18 | 21:02 | 227:13018 | URBAN | Vegetation | Vegetation Blow/Fall In | 67 | 147 | 0.006711 | 4.6e-05 | N
13-10-18 | 19:10 | ZN1193:PA10 | URBAN | Asset Failure | LV | 38 | 100 | 0.002585 | 2.6e-05 | N
13-10-18 | 20:07 | ZN931:PA18 | URBAN | Other | Other - Self Clearing Trigger | 71 | 183 | 0.008816 | 4.8e-05 | N
13-10-18 | 21:08 | ZN3472:PA12 | URBAN | Asset Failure | LV | 71 | 242 | 0.011663 | 4.8e-05 | N
13-10-18 | 21:43 | ZN36100:PA27 | URBAN | Asset Failure | HV | 1,595 | 91 | 0.098664 | 0.001085 | N
13-10-18 | 22:10 | ZN10993:PA35 | URBAN | Other | Other - Arcing | 1 | 319 | 0.000217 | 1e-06 | N
12-10-18 | 23:57 | 512:83743 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 118 | 0.000992 | 8e-06 | N
14-10-18 | 00:39 | ZN14891:PA1 | URBAN | Asset Failure | LV | 64 | 221 | 0.009613 | 4.4e-05 | N
14-10-18 | 14:55 | ZN15010:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 57 | 220 | 0.008534 | 3.9e-05 | N
14-10-18 | 07:26 | ZN12650:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 559 | 0.000381 | 1e-06 | N
14-10-18 | 07:59 | 520:48172 | SHORT RURAL | Asset Failure | HV | 1 | 126 | 0.000529 | 4e-06 | N
14-10-18 | 08:31 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 388 | 0.000264 | 1e-06 | N
14-10-18 | 10:33 | 238:34148 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 164 | 0.000687 | 4e-06 | N
14-10-18 | 10:35 | ZN12630:PA8 | SHORT RURAL | Asset Failure | LV | 3 | 118 | 0.001487 | 1.3e-05 | N
14-10-18 | 10:44 | ZN14144:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 436 | 0.00183 | 4e-06 | N
14-10-18 | 11:36 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 489 | 0.002054 | 4e-06 | N
14-10-18 | 12:21 | ZN12650:PA13 | SHORT RURAL | Third Party | Other | 1 | 504 | 0.002116 | 4e-06 | N
14-10-18 | 12:41 | ZN10991:PA7 | URBAN | Other | Other - Arcing | 1 | 213 | 0.000145 | 1e-06 | N
14-10-18 | 13:03 | ZN3154:PA3 | URBAN | Asset Failure | LV | 25 | 132 | 0.002242 | 1.7e-05 | N
14-10-18 | 15:49 | ZN10999:PA19 | URBAN | Network business | Network error | 4 | 98 | 0.000267 | 3e-06 | N
14-10-18 | 15:40 | ZN10999:PA25 | URBAN | Asset Failure | HV | 1,201 | 110 | 0.089969 | 0.000817 | N
14-10-18 | 16:24 | ZN2602:PA15 | URBAN | Asset Failure | HV | 2,044 | 127 | 0.17724 | 0.001391 | N
14-10-18 | 18:54 | 257:81994 | URBAN | Other | Other | 1 | 60 | 4.1e-05 | 1e-06 | N
14-10-18 | 19:24 | ZN965:PA8 | URBAN | Other | Other - Self Clearing Trigger | 41 | 81 | 0.002259 | 2.8e-05 | N
14-10-18 | 19:31 | ZN36800:PA40 | URBAN | Network business | Network error | 157 | 189 | 0.020203 | 0.000107 | N
14-10-18 | 19:31 | ZN36800:PA42 | URBAN | Network business | Network error | 204 | 124 | 0.017216 | 0.000139 | N
14-10-18 | 22:33 | ZN965:PA8 | URBAN | Other | Other | 41 | 806 | 0.022495 | 2.8e-05 | N
14-10-18 | 23:05 | ZN10999:PA25 | URBAN | Asset Failure | LV | 1 | 716 | 0.000487 | 1e-06 | N
15-10-18 | 04:35 | ZN36100:PA5 | URBAN | Asset Failure | LV | 86 | 365 | 0.021363 | 5.9e-05 | N
15-10-18 | 07:12 | ZN9037:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 377 | 0.000257 | 1e-06 | N
15-10-18 | 08:11 | ZN10999:PA39 | URBAN | Other | Other - Arcing | 1 | 409 | 0.000278 | 1e-06 | N
15-10-18 | 09:25 | ZN35555:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 80 | 5.4e-05 | 1e-06 | N
15-10-18 | 09:46 | ZN2196:PA26 | URBAN | Other | Other | 1 | 184 | 0.000125 | 1e-06 | N
13-10-18 | 17:47 | 245:72 | URBAN | Third Party | Other | 1 | 60 | 4.1e-05 | 1e-06 | N
15-10-18 | 11:20 | ZN36100:PA5 | URBAN | Asset Failure | LV | 86 | 115 | 0.006731 | 5.9e-05 | N
15-10-18 | 12:18 | ZN36200:PA4 | SHORT RURAL | Asset Failure | LV | 1 | 657 | 0.00276 | 4e-06 | N
15-10-18 | 13:29 | ZN12650:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 241 | 0.001012 | 4e-06 | N
15-10-18 | 13:50 | ZN36100:PA5 | URBAN | Asset Failure | LV | 86 | 1,635 | 0.095695 | 5.9e-05 | N
15-10-18 | 13:55 | 224:80340 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 105 | 0.003087 | 2.9e-05 | N
15-10-18 | 14:22 | ZN2400:PA18 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 98 | 2,963 | 1.2197 | 0.000412 | N
15-10-18 | 16:43 | ZN15008:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 67 | 0.00118 | 1.8e-05 | N
15-10-18 | 19:34 | ZN12620:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 265 | 0.001115 | 4e-06 | N
15-10-18 | 23:18 | 813:89059 | URBAN | Animal | Animal impact | 275 | 47 | 0.008796 | 0.000187 | N
16-10-18 | 01:11 | ZN35900:PA4 | SHORT RURAL | Asset Failure | HV | 1,152 | 58 | 0.28101 | 0.004839 | N
16-10-18 | 04:57 | ZN187:PA30 | URBAN | Asset Failure | LV | 1 | 422 | 0.000287 | 1e-06 | N
16-10-18 | 08:55 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 28 | 265 | 0.031167 | 0.000118 | N
16-10-18 | 07:39 | 233:82819 | SHORT RURAL | Other | Other | 1 | 107 | 0.000448 | 4e-06 | N
16-10-18 | 09:00 | 202:34254 | URBAN | Other | Other | 1 | 154 | 0.000105 | 1e-06 | N
16-10-18 | 09:37 | ZN2635:PA44 | URBAN | Other | Other - Arcing | 23 | 293 | 0.004586 | 1.6e-05 | N
16-10-18 | 09:40 | ZN9700:PA20 | URBAN | Asset Failure | HV | 3 | 322 | 0.000657 | 2e-06 | N
16-10-18 | 10:52 | ZN12650:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 608 | 0.002554 | 4e-06 | N
16-10-18 | 11:40 | ZN15014:PA22 | URBAN | Third Party | Other | 13 | 1,680 | 0.014862 | 9e-06 | N
16-10-18 | 13:50 | ZN2568:PA32 | URBAN | Other | Other - Self Clearing Trigger | 80 | 105 | 0.005703 | 5.4e-05 | N
16-10-18 | 14:34 | 814:82283 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 3 | 81 | 0.001021 | 1.3e-05 | N
16-10-18 | 14:22 | ZN35370:PA8 | SHORT RURAL | Third Party | Unauthorised access | 7 | 338 | 0.009938 | 2.9e-05 | N
16-10-18 | 23:08 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,102 | 0.004629 | 4e-06 | N
16-10-18 | 14:48 | 220:8689 | URBAN | Asset Failure | HV | 1,515 | 65 | 0.066985 | 0.001031 | N
16-10-18 | 15:18 | ZN5868:PA13 | URBAN | Third Party | Vehicle impact | 1 | 431 | 0.000293 | 1e-06 | N
16-10-18 | 14:32 | ZN5868:PA13 | URBAN | Asset Failure | LV | 53 | 371 | 0.013382 | 3.6e-05 | N
16-10-18 | 19:15 | 228:7491 | URBAN | Other | Other - Arcing | 2 | 15 | 2e-05 | 1e-06 | N
16-10-18 | 17:54 | ZN12610:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 39 | 2.6e-05 | 1e-06 | N
16-10-18 | 18:26 | ZN35370:PA4 | SHORT RURAL | Other | Other | 1 | 116 | 0.000486 | 4e-06 | N
16-10-18 | 18:38 | ZN12640:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 302 | 0.001267 | 4e-06 | N
16-10-18 | 20:29 | ZN35370:PA8 | SHORT RURAL | Third Party | Unauthorised access | 10 | 71 | 0.002982 | 4.2e-05 | N
17-10-18 | 02:58 | ZN4545:PA2 | URBAN | Asset Failure | LV | 45 | 311 | 0.009528 | 3.1e-05 | N
17-10-18 | 03:15 | ZN9245:PA3 | SHORT RURAL | Network business | Network error | 9 | 35 | 0.001323 | 3.8e-05 | N
17-10-18 | 03:38 | ZN129:PA47 | URBAN | Third Party | Vehicle impact | 17 | 412 | 0.004764 | 1.2e-05 | N
17-10-18 | 06:46 | 515:35198 | SHORT RURAL | Asset Failure | LV | 5 | 124 | 0.002604 | 2.1e-05 | N
17-10-18 | 11:01 | ZN4545:PA24 | URBAN | Other | Other | 91 | 59 | 0.003654 | 6.2e-05 | N
17-10-18 | 07:05 | ZN3154:PA17 | URBAN | Asset Failure | HV | 896 | 67 | 0.040856 | 0.00061 | N
17-10-18 | 07:05 | ZN3154:PA18 | URBAN | Asset Failure | HV | 1 | 67 | 4.6e-05 | 1e-06 | N
17-10-18 | 07:05 | ZN3154:PA23 | URBAN | Asset Failure | HV | 239 | 56 | 0.009069 | 0.000163 | N
17-10-18 | 09:14 | ZN15002:PA2 | URBAN | Asset Failure | LV | 37 | 265 | 0.006675 | 2.5e-05 | N
17-10-18 | 08:49 | ZN9037:PA2 | URBAN | Third Party | Other | 1 | 191 | 0.00013 | 1e-06 | N
17-10-18 | 08:51 | ZN12620:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 489 | 0.002052 | 4e-06 | N
17-10-18 | 09:01 | ZN15014:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 208 | 0.000875 | 4e-06 | N
17-10-18 | 09:20 | 811:74234 | SHORT RURAL | Asset Failure | HV | 11 | 75 | 0.003465 | 4.6e-05 | N
17-10-18 | 10:01 | ZN12690:PA24 | SHORT RURAL | Asset Failure | LV | 1 | 689 | 0.002892 | 4e-06 | N
17-10-18 | 10:35 | ZN874:PA4 | URBAN | Other | Other | 1 | 142 | 9.7e-05 | 1e-06 | N
17-10-18 | 18:33 | ZN2400:PA23 | URBAN | Asset Failure | LV | 29 | 5 | 9.9e-05 | 2e-05 | N
17-10-18 | 11:20 | 811:74234 | SHORT RURAL | Asset Failure | HV | 13 | 95 | 0.005188 | 5.5e-05 | N
17-10-18 | 11:01 | ZN35500:PA24 | URBAN | Other | Other - Arcing | 88 | 58 | 0.003495 | 6e-05 | N
17-10-18 | 11:35 | ZN35555:PA20 | URBAN | Asset Failure | HV | 104 | 175 | 0.012386 | 7.1e-05 | N
17-10-18 | 11:35 | ZN35555:PA5 | SHORT RURAL | Asset Failure | HV | 2,226 | 83 | 0.77609 | 0.009351 | N
17-10-18 | 11:44 | 524:33572 | SHORT RURAL | Third Party | Vehicle impact | 53 | 86 | 0.019146 | 0.000223 | N
17-10-18 | 12:38 | 202:34231 37 42 | URBAN | Other | Other | 1 | 71 | 4.8e-05 | 1e-06 | N
17-10-18 | 13:33 | 810:74050 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 9 | 32 | 0.00121 | 3.8e-05 | N
17-10-18 | 14:03 | ZN36100:PA12 | URBAN | Third Party | Vehicle impact | 1 | 627 | 0.000427 | 1e-06 | N
17-10-18 | 14:21 | ZN690:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 91 | 128 | 0.00793 | 6.2e-05 | N
17-10-18 | 15:05 | ZN4545:PA36 | URBAN | Other | Other | 1 | 140 | 9.6e-05 | 1e-06 | N
17-10-18 | 15:27 | ZN35500:PA18 | URBAN | Other | Other | 1 | 169 | 0.000115 | 1e-06 | N
17-10-18 | 16:04 | ZN262:PA7 | URBAN | Asset Failure | HV | 4 | 291 | 0.000792 | 3e-06 | N
17-10-18 | 16:04 | ZN35555:PA2 | URBAN | Asset Failure | HV | 287 | 291 | 0.056839 | 0.000195 | N
17-10-18 | 17:01 | ZN342:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 145 | 193 | 0.019047 | 9.9e-05 | N
17-10-18 | 17:29 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 96 | 0.000802 | 8e-06 | N
17-10-18 | 17:41 | ZN36100:PA20 | URBAN | Other | Other - Arcing | 1 | 409 | 0.000278 | 1e-06 | N
17-10-18 | 16:38 | 526:34636 | SHORT RURAL | Asset Failure | HV | 112 | 97 | 0.045635 | 0.00047 | N
17-10-18 | 17:43 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 55 | 0.001385 | 2.5e-05 | N
17-10-18 | 18:03 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 68 | 0.000571 | 8e-06 | N
17-10-18 | 18:07 | ZN2835:PA15 | URBAN | Asset Failure | LV | 2 | 382 | 0.00052 | 1e-06 | N
17-10-18 | 18:49 | 222:33596 | URBAN | Other | Other - Arcing | 1 | 178 | 0.000121 | 1e-06 | N
17-10-18 | 18:54 | 813:89059 | URBAN | Other | Other - Arcing | 1 | 966 | 0.000657 | 1e-06 | N
17-10-18 | 19:48 | 213:33777 | SHORT RURAL | Asset Failure | LV | 25 | 72 | 0.007509 | 0.000105 | N
17-10-18 | 19:48 | 802:82215 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 81 | 0.00034 | 4e-06 | N
17-10-18 | 19:50 | 523:33503 | URBAN | Asset Failure | LV | 1 | 72 | 4.9e-05 | 1e-06 | N
17-10-18 | 19:56 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 105 | 5 | 0.002205 | 0.000441 | N
17-10-18 | 20:34 | 813:89062 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 196 | 0.000823 | 4e-06 | N
17-10-18 | 21:00 | 223:14393 | URBAN | Asset Failure | LV | 1 | 150 | 0.000102 | 1e-06 | N
17-10-18 | 21:36 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 5 | 969 | 1.7018 | 0.001756 | N
17-10-18 | 21:38 | ZN1287:PA17 | URBAN | Weather |  | 1,242 | 85 | 0.071848 | 0.000845 | N
17-10-18 | 21:50 | 810:74050 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 850 | 0.007141 | 8e-06 | N
17-10-18 | 22:10 | 223:14393 | URBAN | Other | Other | 1 | 10 | 7e-06 | 1e-06 | N
17-10-18 | 22:14 | ZN4545:PA32 | URBAN | Other | Other - Arcing | 1 | 89 | 6.1e-05 | 1e-06 | N
18-10-18 | 01:20 | ZN3472:PA22 | URBAN | Asset Failure | LV | 76 | 465 | 0.024049 | 5.2e-05 | N
18-10-18 | 02:02 | ZN9252:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 513 | 108 | 0.037695 | 0.000349 | N
18-10-18 | 07:10 | 802:82215 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.000378 | 4e-06 | N
18-10-18 | 08:12 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 138 | 0.00058 | 4e-06 | N
18-10-18 | 09:05 | ZN36200:PA1 | URBAN | Asset Failure | LV | 1 | 580 | 0.000395 | 1e-06 | N
18-10-18 | 10:47 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 53 | 0.000221 | 4e-06 | N
18-10-18 | 11:15 | 813:89062 | SHORT RURAL | Asset Failure | HV | 26 | 97 | 0.010564 | 0.000109 | N
18-10-18 | 01:13 | ZN3288:PA41 42KLM | CBD | Network business | Network error | 22 | 11 | 0.007947 | 0.000722 | N
18-10-18 | 11:32 | ZN14144:PA1 | URBAN | Asset Failure | LV | 61 | 52 | 0.002175 | 4.2e-05 | N
18-10-18 | 12:42 | ZN2568:PA32 | URBAN | Other | Other - Self Clearing Trigger | 80 | 170 | 0.009274 | 5.4e-05 | N
18-10-18 | 13:55 | ZN188:PA44 | URBAN | Other | Other - Arcing | 1 | 566 | 0.000385 | 1e-06 | N
18-10-18 | 14:37 | ZN12600:PA9 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,472 | 125 | 0.77562 | 0.006183 | N
18-10-18 | 15:45 | ZN12630:PA8 | SHORT RURAL | Weather |  | 373 | 41 | 0.063929 | 0.001567 | N
18-10-18 | 15:52 | ZN12630:PA3 | SHORT RURAL | Weather |  | 414 | 314 | 0.54554 | 0.001739 | N
18-10-18 | 18:50 | ZN14144:PA1 | URBAN | Weather |  | 38 | 30 | 0.000776 | 2.6e-05 | N
18-10-18 | 16:30 | TS14450:757 | URBAN | Other | Other - Self Clearing Trigger | 1 | 191 | 0.00013 | 1e-06 | N
18-10-18 | 16:30 | ZN12630:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 454 | 191 | 0.36425 | 0.001907 | N
18-10-18 | 16:30 | ZN12630:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 321 | 191 | 0.25754 | 0.001348 | N
18-10-18 | 16:30 | ZN12630:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 238 | 191 | 0.19095 | 0.001 | N
18-10-18 | 16:30 | ZN12630:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 95 | 191 | 0.07622 | 0.000399 | N
18-10-18 | 16:30 | ZN12630:PA6 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 191 | 0.005616 | 2.9e-05 | N
18-10-18 | 16:30 | ZN12630:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 370 | 191 | 0.29685 | 0.001554 | N
16-10-18 | 14:00 | ZN14144:PA2 | SHORT RURAL | Network business | Network error | 35 | 14 | 0.002058 | 0.000147 | N
18-10-18 | 16:31 | ZN14144:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 7 | 488 | 0.002327 | 5e-06 | N
18-10-18 | 16:36 | ZN180:PA41 | URBAN | Third Party | Vehicle impact | 1 | 234 | 0.000159 | 1e-06 | N
16-10-18 | 14:32 | ZN5868:PA13 | URBAN | Third Party | Vehicle impact | 5 | 123 | 0.000419 | 3e-06 | N
18-10-18 | 16:36 | ZN12610:PA10 | URBAN | Asset Failure | HV | 1 | 342 | 0.000233 | 1e-06 | N
18-10-18 | 16:36 | ZN12610:PA20 | SHORT RURAL | Asset Failure | HV | 919 | 179 | 0.6905 | 0.00386 | N
18-10-18 | 16:36 | ZN12610:PA24 | URBAN | Asset Failure | HV | 581 | 342 | 0.13523 | 0.000395 | N
18-10-18 | 17:23 | ZN35555:PA6 | URBAN | Other | Other | 1 | 57 | 3.9e-05 | 1e-06 | N
18-10-18 | 17:33 | ZN12600:PA13 | SHORT RURAL | Asset Failure | LV | 19 | 397 | 0.031681 | 8e-05 | N
18-10-18 | 17:40 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 250 | 0.00105 | 4e-06 | N
18-10-18 | 17:53 | ZN13000:PA11 | SHORT RURAL | Asset Failure | HV | 1,619 | 142 | 0.9633 | 0.006801 | N
18-10-18 | 17:47 | 810:74050 | SHORT RURAL | Asset Failure | HV | 9 | 291 | 0.011001 | 3.8e-05 | N
18-10-18 | 18:12 | 515:35193 | SHORT RURAL | Asset Failure | HV | 5 | 947 | 0.01989 | 2.1e-05 | N
18-10-18 | 18:16 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 226 | 0.079353 | 0.000351 | N
18-10-18 | 18:17 | 515:35198 | SHORT RURAL | Weather |  | 27 | 418 | 0.047408 | 0.000113 | N
18-10-18 | 18:20 | 227:13015 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 235 | 0.008884 | 3.8e-05 | N
18-10-18 | 18:21 | 243:80080 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 82 | 0.001033 | 1.3e-05 | N
18-10-18 | 18:23 | 523:33508 | SHORT RURAL | Weather |  | 1 | 312 | 0.00131 | 4e-06 | N
18-10-18 | 18:25 | 243:80080 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 115 | 0.003381 | 2.9e-05 | N
18-10-18 | 18:30 | 526:34637 | SHORT RURAL | Weather |  | 19 | 140 | 0.011174 | 8e-05 | N
18-10-18 | 18:30 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 89 | 107 | 0.04004 | 0.000374 | N
18-10-18 | 18:49 | 512:83743 | SHORT RURAL | Other | Other - Arcing | 1 | 114 | 0.00048 | 4e-06 | N
18-10-18 | 19:03 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 401 | 0.001686 | 4e-06 | N
18-10-18 | 19:08 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 1,491 | 265 | 1.6601 | 0.006263 | N
18-10-18 | 19:35 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 155 | 0.001302 | 8e-06 | N
18-10-18 | 19:38 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 257 | 0.012955 | 5e-05 | N
18-10-18 | 19:46 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 89 | 0.000373 | 4e-06 | N
18-10-18 | 20:44 | ZN14891:PA14 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 791 | 0.013291 | 1.7e-05 | N
18-10-18 | 20:51 | ZN2835:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 182 | 0.000124 | 1e-06 | N
18-10-18 | 21:04 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 65 | 0.000546 | 8e-06 | N
18-10-18 | 22:13 | 511:29878 | SHORT RURAL | Asset Failure | HV | 2 | 752 | 0.006318 | 8e-06 | N
19-10-18 | 04:33 | ZN12630:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 467 | 0.005885 | 1.3e-05 | N
19-10-18 | 05:07 | 512:83733 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 243 | 0.002041 | 8e-06 | N
19-10-18 | 05:57 | ZN2400:PA18 | SHORT RURAL | Weather |  | 1 | 393 | 0.001649 | 4e-06 | N
19-10-18 | 06:30 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 100 | 0.000419 | 4e-06 | N
19-10-18 | 07:42 | ZN15004:PA1 | URBAN | Asset Failure | HV | 56 | 117 | 0.004459 | 3.8e-05 | N
19-10-18 | 07:42 | ZN15014:PA19 | URBAN | Asset Failure | HV | 1,906 | 89 | 0.11609 | 0.001297 | N
19-10-18 | 07:43 | ZN2568:PA6 | URBAN | Asset Failure | HV | 25 | 55 | 0.000936 | 1.7e-05 | N
19-10-18 | 07:58 | ZN15014:PA16 | URBAN | Other | Other | 1 | 120 | 8.2e-05 | 1e-06 | N
19-10-18 | 08:39 | 270:83591 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 5 | 2.2e-05 | 4e-06 | N
18-10-18 | 12:20 | ZN1600:PA22ABC | CBD | Asset Failure | HV | 34 | 10 | 0.011165 | 0.001117 | N
19-10-18 | 09:58 | ZN195:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 752 | 0.000512 | 1e-06 | N
19-10-18 | 10:34 | ZN15012:PA4 | URBAN | Asset Failure | LV | 1 | 176 | 0.00012 | 1e-06 | N
19-10-18 | 10:34 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 101 | 0.000424 | 4e-06 | N
19-10-18 | 11:05 | ZN12690:PA24 | SHORT RURAL | Asset Failure | HV | 5 | 265 | 0.005566 | 2.1e-05 | N
19-10-18 | 11:08 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 177 | 0.000744 | 4e-06 | N
19-10-18 | 11:30 | ZN14891:PA1 | URBAN | Other | Other | 1 | 15 | 1e-05 | 1e-06 | N
19-10-18 | 12:14 | ZN9900:PA2 | URBAN | Asset Failure | LV | 75 | 151 | 0.007708 | 5.1e-05 | N
19-10-18 | 12:11 | ZN10999:PA25 | URBAN | Asset Failure | HV | 998 | 58 | 0.039373 | 0.000679 | N
19-10-18 | 12:11 | ZN10999:PA28 | URBAN | Asset Failure | HV | 1 | 31 | 2.1e-05 | 1e-06 | N
19-10-18 | 12:40 | 528:83019 | SHORT RURAL | Other | Other | 1 | 61 | 0.000255 | 4e-06 | N
19-10-18 | 13:08 | ZN2835:PA41 | URBAN | Other | Other - Self Clearing Trigger | 1 | 138 | 9.4e-05 | 1e-06 | N
19-10-18 | 13:53 | ZN10999:PA10 | URBAN | Third Party | Vehicle impact | 58 | 167 | 0.006592 | 3.9e-05 | N
19-10-18 | 14:11 | ZN4545:PA40 | URBAN | Third Party | Vehicle impact | 23 | 63 | 0.000989 | 1.6e-05 | N
19-10-18 | 16:50 | ZN35400:PA97 | URBAN | Third Party | Other | 1 | 100 | 6.8e-05 | 1e-06 | N
19-10-18 | 16:30 | ZN195:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 370 | 0.006044 | 1.6e-05 | N
19-10-18 | 17:03 | 528:83011 | SHORT RURAL | Other | Other - Self Clearing Trigger | 17 | 63 | 0.004499 | 7.1e-05 | N
19-10-18 | 17:44 | ZN9900:PA2 | URBAN | Asset Failure | LV | 38 | 325 | 0.008413 | 2.6e-05 | N
19-10-18 | 17:51 | ZN12620:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 308 | 0.001292 | 4e-06 | N
19-10-18 | 18:08 | 515:35198 | SHORT RURAL | Asset Failure | HV | 2 | 192 | 0.001613 | 8e-06 | N
20-10-18 | 00:53 | 813:89055 | SHORT RURAL | Asset Failure | HV | 38 | 48 | 0.007662 | 0.00016 | Y
19-10-18 | 19:04 | 801:74121 | LONG RURAL | Asset Failure | Distribution substation | 5 | 136 | 0.23927 | 0.001759 | N
19-10-18 | 20:20 | ZN9035:PA4 | URBAN | Other | Other - Arcing | 1 | 879 | 0.000598 | 1e-06 | N
19-10-18 | 20:35 | ZN9035:PA4 | URBAN | Third Party | Vehicle impact | 1 | 864 | 0.000588 | 1e-06 | N
19-10-18 | 20:47 | 512:83741 | SHORT RURAL | Asset Failure | LV | 1 | 192 | 0.000806 | 4e-06 | N
20-10-18 | 06:16 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 88 | 0.001844 | 2.1e-05 | Y
20-10-18 | 07:04 | ZN1788:PA14 | URBAN | Asset Failure | LV | 1 | 341 | 0.000232 | 1e-06 | Y
20-10-18 | 09:10 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 179 | 0.005268 | 2.9e-05 | Y
20-10-18 | 13:00 | ZN4545:PA44 | URBAN | Third Party | Vehicle impact | 31 | 35 | 0.000738 | 2.1e-05 | Y
20-10-18 | 15:41 | ZN35500:PA16 | URBAN | Third Party | Vehicle impact | 40 | 438 | 0.011934 | 2.7e-05 | Y
20-10-18 | 11:20 | 813:89055 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 145 | 0.000609 | 4e-06 | Y
20-10-18 | 13:03 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2,577 | 0.001754 | 1e-06 | Y
20-10-18 | 13:06 | ZN4545:PA44 | URBAN | Asset Failure | LV | 14 | 47 | 0.000451 | 1e-05 | Y
20-10-18 | 14:36 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2,483 | 0.00169 | 1e-06 | Y
20-10-18 | 14:58 | 232:11457 | SHORT RURAL | Asset Failure | HV | 564 | 219 | 0.51922 | 0.002369 | Y
20-10-18 | 16:35 | 256:80641 | URBAN | Asset Failure | LV | 1 | 89 | 6.1e-05 | 1e-06 | Y
20-10-18 | 17:27 | ZN847:PA18 | SHORT RURAL | Weather |  | 966 | 206 | 0.83461 | 0.004058 | Y
20-10-18 | 17:30 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 19 | 594 | 0.047424 | 8e-05 | Y
20-10-18 | 17:32 | ZN965:PA33 | URBAN | Other | Other - Self Clearing Trigger | 1,294 | 115 | 0.10128 | 0.000881 | Y
20-10-18 | 17:32 | ZN965:PA43 | URBAN | Other | Other - Self Clearing Trigger | 1,020 | 114 | 0.079139 | 0.000694 | Y
20-10-18 | 17:38 | ZN847:PA45 | SHORT RURAL | Weather |  | 619 | 202 | 0.52601 | 0.0026 | Y
20-10-18 | 17:43 | ZN9245:PA19 | URBAN | Weather |  | 862 | 96 | 0.056485 | 0.000587 | Y
20-10-18 | 17:33 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 69 | 233 | 0.067398 | 0.00029 | Y
20-10-18 | 17:45 | ZN3154:PA23 | URBAN | Weather |  | 324 | 74 | 0.016383 | 0.000221 | Y
20-10-18 | 17:49 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 501 | 0.017042 | 3.4e-05 | Y
20-10-18 | 17:52 | ZN965:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 48 | 288 | 0.009408 | 3.3e-05 | Y
20-10-18 | 18:41 | ZN2568:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 127 | 378 | 0.032695 | 8.6e-05 | Y
20-10-18 | 18:41 | ZN2568:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 73 | 189 | 0.00939 | 5e-05 | Y
20-10-18 | 17:52 | ZN10998:PA5 | URBAN | Asset Failure | HV | 63 | 298 | 0.012777 | 4.3e-05 | Y
20-10-18 | 17:52 | ZN10999:PA17 | URBAN | Asset Failure | HV | 5,056 | 136 | 0.46904 | 0.003441 | Y
20-10-18 | 17:56 | ZN847:PA47 | SHORT RURAL | Asset Failure | Distribution substation | 109 | 422 | 0.193 | 0.000458 | Y
20-10-18 | 17:52 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 1,275 | 527 | 236.208 | 0.44863 | Y
20-10-18 | 17:50 | ZN9550:PA43 | URBAN | Weather |  | 1,094 | 103 | 0.07669 | 0.000745 | Y
20-10-18 | 17:55 | ZN10999:PA10 | URBAN | Weather |  | 135 | 221 | 0.020305 | 9.2e-05 | Y
20-10-18 | 17:55 | ZN10999:PA22 | URBAN | Weather |  | 2,118 | 221 | 0.31885 | 0.001441 | Y
20-10-18 | 17:59 | ZN2635:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,058 | 0.00072 | 1e-06 | Y
20-10-18 | 17:55 | ZN10998:PA2 | URBAN | Weather |  | 880 | 296 | 0.1771 | 0.000599 | Y
20-10-18 | 18:02 | ZN10998:PA32 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,412 | 173 | 1.0261 | 0.005931 | Y
20-10-18 | 18:08 | ZN35800:PA10 | URBAN | Other | Other - Arcing | 1 | 397 | 0.00027 | 1e-06 | Y
20-10-18 | 18:08 | ZN630:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 96 | 1,357 | 0.088662 | 6.5e-05 | Y
20-10-18 | 18:07 | ZN12630:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 99 | 522 | 0.21705 | 0.000416 | Y
20-10-18 | 18:13 | ZN262:PA16 | URBAN | Vegetation | Vegetation Grow In | 2 | 1,457 | 0.001984 | 1e-06 | Y
20-10-18 | 18:14 | ZN262:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 56 | 86 | 0.003262 | 3.8e-05 | Y
20-10-18 | 18:14 | ZN15002:PA6 | URBAN | Weather |  | 20 | 143 | 0.001953 | 1.4e-05 | Y
20-10-18 | 18:14 | ZN15002:PA8 | URBAN | Weather |  | 1,059 | 133 | 0.095864 | 0.000721 | Y
20-10-18 | 18:17 | ZN965:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 458 | 0.01184 | 2.6e-05 | Y
20-10-18 | 18:19 | ZN262:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 671 | 0.000457 | 1e-06 | Y
20-10-18 | 18:19 | ZN965:PA29 | URBAN | Other | Other - Self Clearing Trigger | 23 | 281 | 0.004397 | 1.6e-05 | Y
20-10-18 | 18:25 | ZN12650:PA1 | SHORT RURAL | Weather |  | 2,890 | 89 | 1.0809 | 0.01214 | Y
20-10-18 | 18:38 | ZN10991:PA8 | URBAN | Network business | Network error | 36 | 292 | 0.007154 | 2.5e-05 | Y
20-10-18 | 18:38 | ZN10998:PA9 | URBAN | Network business | Network error | 148 | 234 | 0.023614 | 0.000101 | Y
20-10-18 | 20:39 | ZN14892:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 72 | 1,036 | 0.050765 | 4.9e-05 | Y
20-10-18 | 18:37 | ZN965:PA29 | URBAN | Asset Failure | LV | 1 | 825 | 0.000562 | 1e-06 | Y
20-10-18 | 18:39 | ZN262:PA20 | URBAN | Third Party | Other | 1 | 110 | 7.5e-05 | 1e-06 | Y
20-10-18 | 18:37 | ZN14891:PA14 | SHORT RURAL | Weather |  | 474 | 158 | 0.31366 | 0.001991 | Y
20-10-18 | 18:38 | ZN12610:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2,106 | 78 | 0.68939 | 0.008846 | Y
20-10-18 | 18:41 | 526:34641 | SHORT RURAL | Other | Other - Self Clearing Trigger | 61 | 364 | 0.093269 | 0.000256 | Y
20-10-18 | 19:32 | ZN15004:PA3 | SHORT RURAL | Other | Other - Arcing | 1 | 1,227 | 0.005156 | 4e-06 | Y
20-10-18 | 18:41 | ZN12620:PA1 | SHORT RURAL | Weather |  | 2,700 | 195 | 2.211 | 0.011342 | Y
20-10-18 | 18:41 | ZN12620:PA10 | SHORT RURAL | Weather |  | 1,117 | 201 | 0.9431 | 0.004692 | Y
20-10-18 | 18:41 | ZN12620:PA11 | SHORT RURAL | Weather |  | 1,652 | 175 | 1.2144 | 0.006939 | Y
20-10-18 | 18:41 | ZN12620:PA13 | SHORT RURAL | Weather |  | 398 | 175 | 0.29257 | 0.001672 | Y
20-10-18 | 18:41 | ZN12620:PA2 | SHORT RURAL | Weather |  | 516 | 175 | 0.37931 | 0.002167 | Y
20-10-18 | 18:41 | ZN12620:PA3 | URBAN | Weather |  | 1,101 | 175 | 0.13113 | 0.000749 | Y
20-10-18 | 18:41 | ZN12620:PA7 | URBAN | Weather |  | 2,167 | 175 | 0.2581 | 0.001475 | Y
20-10-18 | 18:41 | ZN12620:PA8 | SHORT RURAL | Weather |  | 1,253 | 175 | 0.92108 | 0.005263 | Y
20-10-18 | 18:41 | ZN14460:PA661 | URBAN | Weather |  | 1 | 216 | 0.000147 | 1e-06 | Y
20-10-18 | 18:41 | ZN14460:PA662 | URBAN | Weather |  | 1 | 215 | 0.000146 | 1e-06 | Y
20-10-18 | 18:41 | ZN14460:PA664 | URBAN | Weather |  | 1 | 216 | 0.000147 | 1e-06 | Y
20-10-18 | 18:48 | ZN10991:PA8 | URBAN | Asset Failure | LV | 1 | 832 | 0.000566 | 1e-06 | Y
20-10-18 | 18:48 | ZN10994:PA7 | URBAN | Asset Failure | LV | 36 | 832 | 0.020385 | 2.5e-05 | Y
20-10-18 | 18:51 | 524:33580 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 363 | 0.041134 | 0.000113 | Y
20-10-18 | 18:53 | 243:80081 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 268 | 0.001127 | 4e-06 | Y
20-10-18 | 18:54 | 524:33572 | SHORT RURAL | Other | Other - Self Clearing Trigger | 17 | 189 | 0.013492 | 7.1e-05 | Y
20-10-18 | 18:54 | 524:33576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 61 | 0.000512 | 8e-06 | Y
21-10-18 | 10:33 | ZN15012:PA2 | URBAN | Asset Failure | LV | 45 | 626 | 0.019161 | 3.1e-05 | N
20-10-18 | 18:58 | ZN13000:PA2 | SHORT RURAL | Other | Other - Self Clearing Trigger | 73 | 372 | 0.11407 | 0.000307 | Y
20-10-18 | 19:08 | 243:80081 | SHORT RURAL | Other | Other | 1 | 136 | 0.000571 | 4e-06 | Y
20-10-18 | 19:13 | ZN10993:PA34 | URBAN | Other | Other - Self Clearing Trigger | 41 | 122 | 0.003395 | 2.8e-05 | Y
20-10-18 | 19:19 | ZN2635:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,210 | 0.000824 | 1e-06 | Y
20-10-18 | 19:22 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 132 | 0.000556 | 4e-06 | Y
21-10-18 | 19:24 | ZN847:PA22 | URBAN | Weather |  | 95 | 275 | 0.017781 | 6.5e-05 | N
20-10-18 | 19:29 | ZN13000:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 15 | 206 | 0.01298 | 6.3e-05 | Y
20-10-18 | 19:33 | 509:33397 | SHORT RURAL | Asset Failure | HV | 17 | 234 | 0.01671 | 7.1e-05 | Y
20-10-18 | 19:42 | 238:34141 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 853 | 0.017915 | 2.1e-05 | Y
20-10-18 | 19:44 | ZN847:PA15 | URBAN | Weather |  | 23 | 216 | 0.003381 | 1.6e-05 | Y
20-10-18 | 20:17 | 508:82575 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 78 | 0.000983 | 1.3e-05 | Y
20-10-18 | 20:55 | ZN262:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 482 | 0.000328 | 1e-06 | Y
20-10-18 | 20:56 | ZN9245:PA19 | URBAN | Asset Failure | LV | 23 | 124 | 0.001933 | 1.6e-05 | Y
20-10-18 | 21:19 | ZN10998:PA32 | SHORT RURAL | Weather |  | 1,412 | 101 | 0.5971 | 0.005931 | Y
20-10-18 | 21:51 | ZN847:PA21 | URBAN | Asset Failure | Distribution substation | 52 | 138 | 0.004897 | 3.5e-05 | Y
20-10-18 | 22:06 | ZN36300:PA9 | URBAN | Other | Other - Arcing | 1 | 1,268 | 0.000863 | 1e-06 | Y
20-10-18 | 22:39 | ZN12620:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 770 | 0.003236 | 4e-06 | Y
20-10-18 | 22:55 | ZN14891:PA12 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 390 | 0.016368 | 4.2e-05 | Y
21-10-18 | 01:58 | ZN10993:PA23 | URBAN | Asset Failure | Distribution substation | 208 | 72 | 0.010193 | 0.000142 | N
21-10-18 | 03:53 | ZN10994:PA10 | URBAN | Animal | Animal impact | 1,111 | 107 | 0.080907 | 0.000756 | N
21-10-18 | 04:31 | ZN931:PA11 | URBAN | Third Party | Dig-in | 216 | 1,449 | 0.21302 | 0.000147 | N
21-10-18 | 05:15 | 229:34992 | SHORT RURAL | Weather |  | 1 | 465 | 0.001952 | 4e-06 | N
21-10-18 | 06:21 | ZN180:PA20 | URBAN | Other | Other - Arcing | 1 | 698 | 0.000475 | 1e-06 | N
21-10-18 | 07:30 | 523:33501 | SHORT RURAL | Asset Failure | HV | 2 | 70 | 0.000588 | 8e-06 | N
21-10-18 | 06:28 | ZN9037:PA7 | URBAN | Asset Failure | HV | 662 | 68 | 0.030756 | 0.000451 | N
21-10-18 | 11:00 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 70 | 0.001764 | 2.5e-05 | N
21-10-18 | 06:33 | 511:29873 | URBAN | Other | Other - Self Clearing Trigger | 7 | 356 | 0.001698 | 5e-06 | N
21-10-18 | 06:41 | ZN35800:PA1 | URBAN | Other | Other - Arcing | 1 | 663 | 0.000451 | 1e-06 | N
21-10-18 | 06:51 | ZN12650:PA1 | SHORT RURAL | Weather |  | 9 | 124 | 0.004688 | 3.8e-05 | N
21-10-18 | 07:24 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 681 | 0.013905 | 2e-05 | N
21-10-18 | 07:49 | ZN262:PA16 | URBAN | Vegetation | Vegetation Grow In | 1 | 746 | 0.000508 | 1e-06 | N
21-10-18 | 08:07 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 12 | 813 | 0.040981 | 5e-05 | N
21-10-18 | 08:05 | ZN12620:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 43 | 590 | 0.10648 | 0.000181 | N
21-10-18 | 08:59 | ZN13000:PA11 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 389 | 0.001633 | 4e-06 | N
21-10-18 | 09:23 | ZN12570:PA37 | SHORT RURAL | Other | Other | 1 | 103 | 0.000431 | 4e-06 | N
21-10-18 | 11:45 | 508:82574 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 80 | 0.000336 | 4e-06 | N
21-10-18 | 09:42 | ZN10991:PA8 | URBAN | Asset Failure | LV | 1 | 358 | 0.000244 | 1e-06 | N
21-10-18 | 09:42 | ZN10994:PA7 | URBAN | Asset Failure | LV | 34 | 358 | 0.00828 | 2.3e-05 | N
21-10-18 | 09:49 | 227:13020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 137 | 0.001726 | 1.3e-05 | N
21-10-18 | 10:32 | 524:33576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 113 | 0.000475 | 4e-06 | N
21-10-18 | 11:39 | ZN167:PA21 | URBAN | Third Party | Vehicle impact | 41 | 586 | 0.016361 | 2.8e-05 | N
21-10-18 | 11:37 | ZN9252:PA27 | URBAN | Network business | Network error | 61 | 113 | 0.004691 | 4.2e-05 | N
21-10-18 | 12:36 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 2 | 8e-06 | 4e-06 | N
21-10-18 | 13:11 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 68 | 0.000286 | 4e-06 | N
21-10-18 | 13:27 | ZN167:PA21 | URBAN | Third Party | Vehicle impact | 41 | 198 | 0.005525 | 2.8e-05 | N
21-10-18 | 22:30 | 235:8684 | SHORT RURAL | Other | Other | 42 | 65 | 0.011468 | 0.000176 | N
21-10-18 | 18:09 | 806:82662 | SHORT RURAL | Weather |  | 1 | 966 | 0.004058 | 4e-06 | N
21-10-18 | 18:47 | ZN14144:PA8 | URBAN | Overloads |  | 1 | 313 | 0.000213 | 1e-06 | N
21-10-18 | 18:51 | ZN15014:PA10 | SHORT RURAL | Other | Other | 1 | 134 | 0.000562 | 4e-06 | N
21-10-18 | 19:50 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 175 | 0.061524 | 0.000352 | N
22-10-18 | 04:22 | ZN10994:PA7 | URBAN | Asset Failure | LV | 34 | 18 | 0.000417 | 2.3e-05 | N
22-10-18 | 00:22 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 103 | 0.002163 | 2.1e-05 | N
22-10-18 | 00:05 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 57 | 50 | 0.00194 | 3.9e-05 | N
22-10-18 | 02:56 | 261:81879 | URBAN | Other | Other - Arcing | 1 | 364 | 0.000247 | 1e-06 | N
22-10-18 | 06:07 | ZN35600:PA25 | URBAN | Third Party | Vehicle impact | 5 | 503 | 0.001712 | 3e-06 | N
22-10-18 | 06:36 | 508:82575 | SHORT RURAL | Asset Failure | HV | 171 | 42 | 0.03045 | 0.000718 | N
22-10-18 | 07:50 | ZN2196:PA9 | URBAN | Asset Failure | LV | 2 | 295 | 0.000402 | 1e-06 | N
22-10-18 | 08:05 | ZN2466:PA2 | URBAN | Other | Other - Arcing | 1 | 85 | 5.8e-05 | 1e-06 | N
22-10-18 | 08:51 | 524:33572 | SHORT RURAL | Other | Other | 1 | 150 | 0.000631 | 4e-06 | N
18-10-18 | 19:30 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 26 | 0.000218 | 8e-06 | N
22-10-18 | 10:15 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 141 | 232 | 11.5102 | 0.049613 | N
22-10-18 | 11:05 | 515:35193 | SHORT RURAL | Asset Failure | HV | 33 | 80 | 0.011153 | 0.000139 | N
22-10-18 | 11:10 | 261:81876 | URBAN | Third Party | Other | 1 | 334 | 0.000228 | 1e-06 | N
22-10-18 | 11:35 | 242:81538 | URBAN | Asset Failure | LV | 1 | 512 | 0.000349 | 1e-06 | N
22-10-18 | 12:27 | ZN4545:PA44 | URBAN | Other | Other | 1 | 66 | 4.5e-05 | 1e-06 | N
20-10-18 | 17:48 | TS9200:749 | URBAN | Weather |  | 2 | 24 | 3.3e-05 | 1e-06 | Y
20-10-18 | 18:42 | TS9200:749 | URBAN | Weather |  | 2 | 108 | 0.000147 | 1e-06 | Y
19-10-18 | 07:40 | ZN2568:PA33 | URBAN | Network business | Switching and protection error | 51 | 3 | 0.000104 | 3.5e-05 | N
22-10-18 | 12:44 | 256:80644 | URBAN | Other | Other - Self Clearing Trigger | 88 | 66 | 0.003929 | 6e-05 | N
20-10-18 | 19:30 | 524:33572 | SHORT RURAL | Other | Other - Self Clearing Trigger | 24 | 232 | 0.023389 | 0.000101 | Y
18-10-18 | 14:32 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 173 | 0.000727 | 4e-06 | N
18-10-18 | 22:55 | ZN12610:PA20 | SHORT RURAL | Asset Failure | HV | 225 | 3 | 0.002835 | 0.000945 | N
22-10-18 | 14:31 | ZN129:PA39 | URBAN | Asset Failure | LV | 1 | 448 | 0.000305 | 1e-06 | N
22-10-18 | 17:30 | ZN35500:PA32 | URBAN | Asset Failure | LV | 75 | 308 | 0.015737 | 5.1e-05 | N
22-10-18 | 15:57 | ZN12610:PA11 | URBAN | Other | Other - Arcing | 2 | 393 | 0.000535 | 1e-06 | N
22-10-18 | 17:06 | ZN12600:PA9 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 144 | 0.001207 | 8e-06 | N
22-10-18 | 17:39 | ZN36100:PA23 | URBAN | Third Party | Dig-in | 983 | 66 | 0.043974 | 0.000669 | N
22-10-18 | 18:30 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 135 | 0.000567 | 4e-06 | N
22-10-18 | 19:52 | 812:19072 | SHORT RURAL | Third Party | Other | 1 | 135 | 0.000567 | 4e-06 | N
23-10-18 | 05:37 | ZN12690:PA6 | URBAN | Asset Failure | HV | 35 | 113 | 0.002692 | 2.4e-05 | N
23-10-18 | 06:22 | 516:48065 | SHORT RURAL | Third Party | Unauthorised access | 35 | 137 | 0.020197 | 0.000147 | N
23-10-18 | 06:38 | ZN9900:PA8 | URBAN | Asset Failure | LV | 1 | 861 | 0.000586 | 1e-06 | N
22-10-18 | 13:20 | 243:80080 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 60 | 0.000252 | 4e-06 | N
19-10-18 | 12:40 | ZN3425:PA30 | URBAN | Third Party | Other | 13 | 4,640 | 0.041053 | 9e-06 | N
22-10-18 | 09:45 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 50 | 0.00042 | 8e-06 | N
23-10-18 | 12:32 | 812:19072 | SHORT RURAL | Asset Failure | HV | 66 | 28 | 0.007675 | 0.000277 | N
23-10-18 | 12:40 | 514:18137 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 350 | 0.00294 | 8e-06 | N
23-10-18 | 13:02 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 375 | 0.00315 | 8e-06 | N
23-10-18 | 14:40 | ZN7481:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 229 | 0.000156 | 1e-06 | N
23-10-18 | 14:55 | ZN129:PA36 | URBAN | Asset Failure | LV | 1 | 259 | 0.000176 | 1e-06 | N
23-10-18 | 15:32 | 515:35198 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 83 | 0.000697 | 8e-06 | N
23-10-18 | 22:30 | ZN9245:PA3 | SHORT RURAL | Weather |  | 2 | 150 | 0.00126 | 8e-06 | N
23-10-18 | 17:09 | ZN35900:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 3 | 382 | 0.00078 | 2e-06 | N
23-10-18 | 17:36 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 84 | 0.000706 | 8e-06 | N
23-10-18 | 18:33 | 814:82291 | SHORT RURAL | Other | Other | 1 | 123 | 0.000516 | 4e-06 | N
24-10-18 | 02:47 | ZN12580:PA10 | URBAN | Other | Other - Self Clearing Trigger | 1,611 | 65 | 0.070911 | 0.001096 | N
24-10-18 | 02:34 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 57 | 216 | 0.051743 | 0.000239 | N
24-10-18 | 03:09 | ZN10999:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 2,118 | 147 | 0.21132 | 0.001442 | N
24-10-18 | 03:32 | ZN3672:PA37 | URBAN | Weather |  | 32 | 192 | 0.004174 | 2.2e-05 | N
24-10-18 | 03:37 | ZN13000:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 103 | 0.002103 | 2e-05 | N
24-10-18 | 04:46 | ZN10994:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 250 | 0.005285 | 2.1e-05 | N
24-10-18 | 09:26 | ZN690:PA35 | URBAN | Third Party | Vehicle impact | 8 | 274 | 0.00149 | 5e-06 | N
24-10-18 | 12:30 | 205:12210 | URBAN | Other | Other | 1 | 30 | 2e-05 | 1e-06 | N
24-10-18 | 12:51 | ZN180:PA41 | URBAN | Third Party | Other | 1 | 143 | 9.7e-05 | 1e-06 | N
24-10-18 | 14:05 | ZN2466:PA45 | URBAN | Asset Failure | LV | 53 | 200 | 0.007207 | 3.6e-05 | N
24-10-18 | 14:54 | ZN9252:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 68 | 439 | 0.020318 | 4.6e-05 | N
24-10-18 | 15:21 | ZN15004:PA9 | URBAN | Other | Other - Arcing | 1 | 204 | 0.000139 | 1e-06 | N
24-10-18 | 16:12 | ZN2568:PA26 | URBAN | Other | Other | 1 | 132 | 9e-05 | 1e-06 | N
24-10-18 | 16:50 | 265:81651 | SHORT RURAL | Third Party | Unauthorised access | 20 | 45 | 0.003781 | 8.4e-05 | N
24-10-18 | 18:06 | 502:48004 | URBAN | Asset Failure | LV | 1 | 278 | 0.000189 | 1e-06 | N
24-10-18 | 18:51 | ZN12610:PA25 | URBAN | Other | Other - Arcing | 1 | 174 | 0.000118 | 1e-06 | N
24-10-18 | 19:09 | ZN13000:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 645 | 0.002708 | 4e-06 | N
24-10-18 | 20:21 | ZN14892:PA6 | URBAN | Other | Other - Arcing | 1 | 243 | 0.000166 | 1e-06 | N
24-10-18 | 20:50 | ZN9900:PA19 | URBAN | Other | Other - Self Clearing Trigger | 1 | 55 | 3.7e-05 | 1e-06 | N
24-10-18 | 20:50 | ZN9900:PA2 | URBAN | Other | Other - Self Clearing Trigger | 23 | 55 | 0.000861 | 1.6e-05 | N
25-10-18 | 00:01 | ZN35700:PA10 | URBAN | Third Party | Vehicle impact | 90 | 120 | 0.007364 | 6.1e-05 | N
25-10-18 | 02:58 | ZN9252:PA24 | URBAN | Asset Failure | HV | 881 | 54 | 0.032084 | 0.000599 | N
25-10-18 | 07:06 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 104 | 0.036581 | 0.000352 | N
25-10-18 | 07:31 | ZN14892:PA19 | URBAN | Other | Other - Arcing | 1 | 749 | 0.000509 | 1e-06 | N
25-10-18 | 08:12 | ZN12650:PA6 | URBAN | Third Party | Vehicle impact | 1,273 | 63 | 0.054503 | 0.000866 | N
25-10-18 | 10:50 | ZN847:PA19 | URBAN | Asset Failure | LV | 31 | 550 | 0.011601 | 2.1e-05 | N
15-10-18 | 12:18 | ZN36200:PA4 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 48 | 657 | 0.13246 | 0.000202 | N
24-10-18 | 14:15 | ZN10999:PA22 | URBAN | Third Party | Vehicle impact | 49 | 70 | 0.002334 | 3.3e-05 | N
25-10-18 | 12:05 | ZN2400:PA13 | URBAN | Asset Failure | HV | 72 | 141 | 0.006922 | 4.9e-05 | N
25-10-18 | 19:24 | ZN1068:PA26 | URBAN | Other | Other | 1 | 389 | 0.000265 | 1e-06 | N
25-10-18 | 23:34 | ZN15014:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 595 | 0.0025 | 4e-06 | N
26-10-18 | 02:37 | ZN847:PA22 | URBAN | Third Party | Vehicle impact | 67 | 283 | 0.012901 | 4.6e-05 | N
26-10-18 | 09:21 | 520:48172 | SHORT RURAL | Asset Failure | HV | 57 | 66 | 0.015797 | 0.000239 | N
26-10-18 | 09:50 | ZN36200:PA8 | SHORT RURAL | Asset Failure | LV | 1 | 690 | 0.002897 | 4e-06 | N
26-10-18 | 09:58 | 812:19072 | SHORT RURAL | Asset Failure | LV | 1 | 82 | 0.000344 | 4e-06 | N
26-10-18 | 10:23 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 111 | 0.039131 | 0.000352 | N
26-10-18 | 12:57 | ZN12640:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 67 | 0.000283 | 4e-06 | N
26-10-18 | 13:58 | ZN2635:PA31 | URBAN | Asset Failure | LV | 28 | 257 | 0.004896 | 1.9e-05 | N
26-10-18 | 14:26 | ZN2635:PA55 | SHORT RURAL | Asset Failure | LV | 47 | 77 | 0.015196 | 0.000197 | N
26-10-18 | 14:54 | ZN14143:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 859 | 74 | 0.26857 | 0.003607 | N
26-10-18 | 14:54 | ZN14143:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 21 | 72 | 0.001029 | 1.4e-05 | N
26-10-18 | 15:17 | ZN1285:PA20 | URBAN | Overloads |  | 1 | 466 | 0.000317 | 1e-06 | N
26-10-18 | 15:35 | ZN2466:PA45 | URBAN | Asset Failure | LV | 1 | 446 | 0.000304 | 1e-06 | N
26-10-18 | 17:11 | 264:81236 | URBAN | Other | Other | 1 | 129 | 8.8e-05 | 1e-06 | N
26-10-18 | 17:50 | 216:10726 | URBAN | Other | Other | 1 | 86 | 5.8e-05 | 1e-06 | N
26-10-18 | 17:52 | ZN965:PA8 | URBAN | Asset Failure | LV | 10 | 1,003 | 0.006822 | 7e-06 | N
26-10-18 | 18:08 | ZN965:PA8 | URBAN | Network business | Network error | 22 | 986 | 0.014761 | 1.5e-05 | N
26-10-18 | 20:42 | ZN35555:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 238 | 0.000162 | 1e-06 | N
27-10-18 | 04:12 | ZN35370:PA8 | SHORT RURAL | Third Party | Unauthorised access | 69 | 256 | 0.074173 | 0.00029 | N
27-10-18 | 09:50 | ZN12630:PA11 | SHORT RURAL | Asset Failure | LV | 2 | 438 | 0.003678 | 8e-06 | N
27-10-18 | 11:08 | ZN1673:PA6 | URBAN | Third Party | Vehicle impact | 2 | 342 | 0.000465 | 1e-06 | N
27-10-18 | 16:53 | ZN3288:PA45 46ABC | CBD | Asset Failure | HV | 115 | 55 | 0.20751 | 0.003776 | N
27-10-18 | 19:34 | 502:48010 | SHORT RURAL | Third Party | Vehicle impact | 1 | 123 | 0.000516 | 4e-06 | N
27-10-18 | 21:06 | 202:34260 | URBAN | Other | Other - Arcing | 1 | 237 | 0.000161 | 1e-06 | N
27-10-18 | 21:20 | ZN15010:PA24 | URBAN | Other | Other - Arcing | 1 | 1,466 | 0.000997 | 1e-06 | N
27-10-18 | 21:27 | 232:33413 | SHORT RURAL | Other | Other | 1 | 84 | 0.000353 | 4e-06 | N
27-10-18 | 23:45 | ZN15013:PA4 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 123 | 83 | 0.042868 | 0.000516 | N
28-10-18 | 04:06 | ZN711:PA33 | URBAN | Asset Failure | LV | 1 | 635 | 0.000432 | 1e-06 | N
28-10-18 | 04:38 | ZN180:PA24 | URBAN | Other | Other - Arcing | 1 | 1,028 | 0.000699 | 1e-06 | N
28-10-18 | 04:42 | ZN35370:PA8 | SHORT RURAL | Third Party | Unauthorised access | 69 | 106 | 0.030712 | 0.00029 | N
28-10-18 | 06:45 | ZN14891:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 374 | 0.001572 | 4e-06 | N
28-10-18 | 07:37 | 270:83590 | URBAN | Asset Failure | LV | 1 | 129 | 8.8e-05 | 1e-06 | N
28-10-18 | 08:37 | ZN711:PA33 | URBAN | Asset Failure | LV | 1 | 364 | 0.000248 | 1e-06 | N
28-10-18 | 10:31 | ZN3155:PA24 | URBAN | Other | Other - Self Clearing Trigger | 13 | 194 | 0.001715 | 9e-06 | N
28-10-18 | 10:44 | ZN3154:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 896 | 130 | 0.079265 | 0.000609 | N
28-10-18 | 10:44 | ZN3154:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 143 | 130 | 0.012639 | 9.7e-05 | N
28-10-18 | 11:49 | 528:83014 | SHORT RURAL | Other | Other - Arcing | 1 | 360 | 0.001513 | 4e-06 | N
28-10-18 | 12:15 | ZN36200:PA8 | SHORT RURAL | Network business | Network error | 1 | 153 | 0.000642 | 4e-06 | N
28-10-18 | 21:30 | ZN3472:PA12 | URBAN | Other | Other - Arcing | 1 | 312 | 0.000212 | 1e-06 | N
28-10-18 | 22:48 | 812:19072 | SHORT RURAL | Asset Failure | HV | 58 | 200 | 0.048781 | 0.000244 | N
29-10-18 | 00:30 | ZN35370:PA8 | SHORT RURAL | Third Party | Unauthorised access | 69 | 206 | 0.05954 | 0.00029 | N
29-10-18 | 07:17 | ZN12620:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 427 | 0.001793 | 4e-06 | N
29-10-18 | 07:33 | ZN2568:PA26 | URBAN | Third Party | Vehicle impact | 110 | 131 | 0.009818 | 7.5e-05 | N
29-10-18 | 09:59 | ZN167:PA20 | URBAN | Third Party | Vehicle impact | 9 | 126 | 0.000771 | 6e-06 | N
29-10-18 | 10:35 | 217:33612 | URBAN | Other | Other - Arcing | 1 | 279 | 0.00019 | 1e-06 | N
29-10-18 | 10:40 | ZN340:PA35 | URBAN | Third Party | Vehicle impact | 58 | 56 | 0.002217 | 3.9e-05 | N
29-10-18 | 12:40 | ZN12600:PA9 | SHORT RURAL | Other | Other - Arcing | 1 | 260 | 0.00109 | 4e-06 | N
29-10-18 | 16:35 | ZN10993:PA22 | URBAN | Third Party | Other | 75 | 50 | 0.002549 | 5.1e-05 | N
29-10-18 | 16:38 | 227:13015 | SHORT RURAL | Third Party | Other | 2 | 162 | 0.00136 | 8e-06 | N
29-10-18 | 15:42 | ZN15013:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 49 | 129 | 0.004296 | 3.3e-05 | N
29-10-18 | 15:45 | ZN3154:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 5 | 135 | 0.000459 | 3e-06 | N
29-10-18 | 17:25 | ZN965:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 41 | 415 | 0.011556 | 2.8e-05 | N
29-10-18 | 17:46 | ZN965:PA13 | URBAN | Asset Failure | HV | 61 | 169 | 0.006996 | 4.1e-05 | N
29-10-18 | 17:46 | ZN965:PA4 | URBAN | Asset Failure | HV | 1 | 169 | 0.000115 | 1e-06 | N
29-10-18 | 20:40 | ZN9118:PA21 | URBAN | Other | Other - Self Clearing Trigger | 1 | 160 | 0.000109 | 1e-06 | N
29-10-18 | 20:40 | ZN9118:PA8 | URBAN | Other | Other - Self Clearing Trigger | 1,284 | 62 | 0.054108 | 0.000873 | N
30-10-18 | 02:47 | ZN9245:PA1 | URBAN | Other | Other - Self Clearing Trigger | 551 | 140 | 0.052431 | 0.000375 | N
30-10-18 | 02:47 | ZN9245:PA15 | URBAN | Other | Other - Self Clearing Trigger | 961 | 90 | 0.058786 | 0.000653 | N
30-10-18 | 05:45 | ZN35800:PA19 | URBAN | Third Party | Vehicle impact | 22 | 150 | 0.002243 | 1.5e-05 | N
30-10-18 | 05:33 | 205:12213 | SHORT RURAL | Asset Failure | LV | 1 | 126 | 0.00053 | 4e-06 | N
30-10-18 | 07:17 | 807:74183 | SHORT RURAL | Asset Failure | LV | 1 | 343 | 0.001439 | 4e-06 | N
30-10-18 | 07:57 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 138 | 0.006951 | 5e-05 | N
30-10-18 | 09:31 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 55 | 124 | 0.028628 | 0.000231 | N
30-10-18 | 10:33 | 526:34640 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 166 | 118 | 0.082498 | 0.000697 | N
30-10-18 | 10:39 | 264:81238 | SHORT RURAL | Other | Other | 1 | 61 | 0.000255 | 4e-06 | N
30-10-18 | 17:40 | 508:82574 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 10 | 10 | 0.00042 | 4.2e-05 | N
30-10-18 | 16:01 | ZN10995:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 389 | 0.000529 | 1e-06 | N
30-10-18 | 16:09 | 270:83583 | URBAN | Other | Other | 1 | 37 | 2.5e-05 | 1e-06 | N
30-10-18 | 16:12 | ZN14144:PA8 | URBAN | Other | Other | 1 | 57 | 3.9e-05 | 1e-06 | N
30-10-18 | 16:13 | ZN14144:PA8 | URBAN | Other | Other | 1 | 89 | 6.1e-05 | 1e-06 | N
30-10-18 | 16:13 | ZN9550:PA1 | URBAN | Asset Failure | HV | 880 | 75 | 0.044872 | 0.000598 | N
30-10-18 | 17:34 | 224:80341 | URBAN | Third Party | Other | 1 | 184 | 0.000125 | 1e-06 | N
30-10-18 | 16:20 | ZN12660:PA14 | SHORT RURAL | Asset Failure | LV | 4 | 2,635 | 0.044244 | 1.7e-05 | N
30-10-18 | 23:01 | ZN15012:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 85 | 0.002253 | 2.7e-05 | N
31-10-18 | 06:48 | ZN340:PA3 | URBAN | Third Party | Vehicle impact | 29 | 211 | 0.004166 | 2e-05 | N
31-10-18 | 06:48 | ZN340:PA40 | URBAN | Third Party | Vehicle impact | 1 | 212 | 0.000144 | 1e-06 | N
30-10-18 | 19:45 | 240:34843 | URBAN | Other | Other - Self Clearing Trigger | 2 | 220 | 0.000299 | 1e-06 | N
30-10-18 | 08:00 | ZN1610:PA23 | URBAN | Third Party | Vehicle impact | 3 | 140 | 0.000285 | 2e-06 | N
31-10-18 | 09:27 | ZN690:PA26 | URBAN | Other | Other | 1 | 307 | 0.000209 | 1e-06 | N
31-10-18 | 10:04 | ZN263:PA33 34ABC | CBD | Other | Other | 2 | 301 | 0.019759 | 6.6e-05 | N
31-10-18 | 12:12 | ZN8700:PA65 66GHJ | CBD | Asset Failure | LV | 6 | 1,338 | 0.2635 | 0.000197 | N
31-10-18 | 14:07 | ZN12610:PA11 | URBAN | Other | Other | 1 | 43 | 2.9e-05 | 1e-06 | N
31-10-18 | 15:12 | ZN80:PA37 | URBAN | Asset Failure | HV | 1,248 | 82 | 0.069542 | 0.000848 | N
31-10-18 | 15:12 | ZN80:PA40 | URBAN | Asset Failure | HV | 58 | 88 | 0.003469 | 3.9e-05 | N
31-10-18 | 16:43 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 271 | 0.001139 | 4e-06 | N
31-10-18 | 16:52 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 954 | 52 | 0.033718 | 0.000648 | N
31-10-18 | 17:00 | ZN9700:PA20 | URBAN | Third Party | Vehicle impact | 44 | 165 | 0.004935 | 3e-05 | N
31-10-18 | 17:44 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 210 | 0.000143 | 1e-06 | N
31-10-18 | 19:01 | ZN12620:PA13 | SHORT RURAL | Asset Failure | HV | 109 | 163 | 0.074804 | 0.000458 | N
31-10-18 | 20:05 | 528:83020 | SHORT RURAL | Asset Failure | HV | 6 | 185 | 0.00466 | 2.5e-05 | N
31-10-18 | 20:21 | 224:80326 | URBAN | Other | Other - Self Clearing Trigger | 26 | 369 | 0.006521 | 1.8e-05 | N
31-10-18 | 21:52 | ZN2196:PA21 | URBAN | Other | Other | 1 | 103 | 7e-05 | 1e-06 | N
01-11-18 | 01:09 | ZN12580:PA10 | URBAN | Asset Failure | HV | 1,611 | 61 | 0.066794 | 0.001095 | N
01-11-18 | 01:09 | ZN12580:PA7 | URBAN | Asset Failure | HV | 176 | 59 | 0.007058 | 0.00012 | N
01-11-18 | 01:09 | ZN12580:PA8 | URBAN | Asset Failure | HV | 328 | 60 | 0.013376 | 0.000223 | N
01-11-18 | 02:54 | 261:81879 | URBAN | Other | Other - Arcing | 1 | 162 | 0.00011 | 1e-06 | N
01-11-18 | 03:30 | ZN9037:PA7 | URBAN | Animal | Animal impact | 93 | 41 | 0.002592 | 6.3e-05 | N
01-11-18 | 07:11 | ZN1285:PA30 | URBAN | Third Party | Vehicle impact | 11 | 188 | 0.001406 | 7e-06 | N
01-11-18 | 07:11 | ZN1285:PA8 | URBAN | Third Party | Vehicle impact | 1 | 189 | 0.000128 | 1e-06 | N
01-11-18 | 07:31 | ZN1673:PA2 | URBAN | Asset Failure | HV | 801 | 100 | 0.054607 | 0.000544 | N
01-11-18 | 08:33 | ZN3154:PA10 | URBAN | Third Party | Vehicle impact | 46 | 222 | 0.006941 | 3.1e-05 | N
01-11-18 | 09:28 | ZN262:PA39 | URBAN | Other | Other - Arcing | 1 | 181 | 0.000123 | 1e-06 | N
01-11-18 | 09:40 | ZN263:PA33 34ABC | CBD | Other | Other | 2 | 80 | 0.005252 | 6.6e-05 | N
31-10-18 | 21:07 | ZN2196:PA17 | URBAN | Asset Failure | Zone substation | 98 | 5 | 0.000333 | 6.7e-05 | N
31-10-18 | 21:07 | ZN2196:PA18 | URBAN | Asset Failure | Zone substation | 1,687 | 4 | 0.004587 | 0.001147 | N
31-10-18 | 21:07 | ZN2196:PA19 | URBAN | Asset Failure | Zone substation | 1 | 5 | 3e-06 | 1e-06 | N
31-10-18 | 21:07 | ZN2196:PA20 | URBAN | Asset Failure | Zone substation | 101 | 4 | 0.000275 | 6.9e-05 | N
31-10-18 | 21:07 | ZN2196:PA21 | URBAN | Asset Failure | Zone substation | 691 | 4 | 0.001879 | 0.00047 | N
31-10-18 | 21:07 | ZN2196:PA22 | URBAN | Asset Failure | Zone substation | 25 | 5 | 8.5e-05 | 1.7e-05 | N
31-10-18 | 21:07 | ZN2196:PA25 | URBAN | Asset Failure | Zone substation | 2,209 | 4 | 0.006006 | 0.001501 | N
31-10-18 | 21:07 | ZN2196:PA26 | URBAN | Asset Failure | Zone substation | 706 | 5 | 0.002399 | 0.00048 | N
31-10-18 | 21:07 | ZN2196:PA28 | URBAN | Asset Failure | Zone substation | 146 | 4 | 0.000397 | 9.9e-05 | N
01-11-18 | 11:47 | ZN2310:PA59 | URBAN | Other | Other | 1 | 92 | 6.2e-05 | 1e-06 | N
01-11-18 | 13:41 | 507:80926 | URBAN | Third Party | Other | 1 | 68 | 4.6e-05 | 1e-06 | N
01-11-18 | 13:44 | ZN129:PA57 | URBAN | Vegetation | Vegetation Blow/Fall In | 113 | 155 | 0.011933 | 7.7e-05 | N
01-11-18 | 15:20 | ZN14891:PA5 | SHORT RURAL | Asset Failure | LV | 1 | 30 | 0.000126 | 4e-06 | N
01-11-18 | 15:28 | ZN15010:PA30 | URBAN | Asset Failure | LV | 1 | 274 | 0.000186 | 1e-06 | N
01-11-18 | 16:04 | ZN1610:PA3 | URBAN | Other | Other | 1 | 995 | 0.000676 | 1e-06 | N
01-11-18 | 17:11 | ZN847:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 109 | 7.4e-05 | 1e-06 | N
01-11-18 | 17:19 | ZN12570:PA24 | SHORT RURAL | Other | Other | 1 | 52 | 0.000217 | 4e-06 | N
01-11-18 | 18:27 | ZN1850:PA31 | URBAN | Other | Other | 1 | 634 | 0.000431 | 1e-06 | N
01-11-18 | 20:06 | ZN3154:PA16 | URBAN | Third Party | Other | 1 | 202 | 0.000137 | 1e-06 | N
02-11-18 | 02:51 | ZN1788:PA17 | URBAN | Asset Failure | HV | 1,565 | 73 | 0.077823 | 0.001064 | N
02-11-18 | 03:10 | ZN3922:PA7 | URBAN | Asset Failure | LV | 51 | 109 | 0.003767 | 3.5e-05 | N
02-11-18 | 03:50 | ZN10991:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 339 | 0.000231 | 1e-06 | N
02-11-18 | 06:55 | ZN3922:PA26 | URBAN | Other | Other - Self Clearing Trigger | 16 | 220 | 0.002393 | 1.1e-05 | N
02-11-18 | 07:37 | ZN36800:PA58 | URBAN | Third Party | Dig-in | 110 | 353 | 0.026393 | 7.5e-05 | N
02-11-18 | 07:39 | ZN1290:PA11 | URBAN | Other | Other | 1 | 315 | 0.000214 | 1e-06 | N
01-11-18 | 13:00 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 15 | 0.000265 | 1.8e-05 | N
02-11-18 | 08:22 | ZN2310:PA59 | URBAN | Other | Other | 1 | 411 | 0.000279 | 1e-06 | N
02-11-18 | 08:41 | ZN35370:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 18 | 539 | 0.040727 | 7.6e-05 | N
02-11-18 | 08:44 | 807:74184 | SHORT RURAL | Other | Other | 1 | 285 | 0.001196 | 4e-06 | N
02-11-18 | 10:16 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 171 | 149 | 0.017318 | 0.000116 | N
02-11-18 | 12:09 | ZN12570:PA34 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 53 | 0.000223 | 4e-06 | N
01-11-18 | 13:44 | ZN12690:PA10 | SHORT RURAL | Network business | Network error | 705 | 3 | 0.008878 | 0.002959 | N
01-11-18 | 13:44 | ZN12690:PA11 | URBAN | Network business | Network error | 10 | 3 | 2e-05 | 7e-06 | N
01-11-18 | 13:44 | ZN12690:PA12 | SHORT RURAL | Network business | Network error | 1,046 | 3 | 0.013173 | 0.004391 | N
02-11-18 | 12:41 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 4 | 252 | 0.004236 | 1.7e-05 | N
02-11-18 | 13:05 | ZN3425:PA44 | URBAN | Asset Failure | LV | 82 | 285 | 0.015907 | 5.6e-05 | N
02-11-18 | 13:20 | ZN1068:PA18 | URBAN | Other | Other - Self Clearing Trigger | 81 | 130 | 0.007146 | 5.5e-05 | N
02-11-18 | 13:20 | ZN10991:PA7 | URBAN | Asset Failure | LV | 1 | 579 | 0.000394 | 1e-06 | N
02-11-18 | 13:34 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 372 | 133 | 0.20799 | 0.001562 | N
02-11-18 | 13:50 | ZN187:PA14 | URBAN | Asset Failure | HV | 2 | 210 | 0.000285 | 1e-06 | N
02-11-18 | 13:50 | ZN187:PA4 | URBAN | Asset Failure | HV | 80 | 350 | 0.019013 | 5.4e-05 | N
02-11-18 | 14:01 | ZN1290:PA12 | URBAN | Other | Other | 1 | 389 | 0.000264 | 1e-06 | N
02-11-18 | 14:17 | 239:82131 | SHORT RURAL | Asset Failure | LV | 2 | 293 | 0.00246 | 8e-06 | N
02-11-18 | 15:28 | ZN9252:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 331 | 0.000225 | 1e-06 | N
02-11-18 | 17:06 | ZN15012:PA8 | URBAN | Asset Failure | LV | 40 | 104 | 0.002828 | 2.7e-05 | N
02-11-18 | 16:55 | ZN3154:PA18 | URBAN | Network business | Network error | 52 | 235 | 0.008298 | 3.5e-05 | N
02-11-18 | 18:02 | ZN1788:PA21 | URBAN | Asset Failure | Subtransmission | 1 | 56 | 3.8e-05 | 1e-06 | N
02-11-18 | 18:02 | ZN340:PA3 | URBAN | Asset Failure | Subtransmission | 1 | 56 | 3.8e-05 | 1e-06 | N
02-11-18 | 18:02 | ZN340:PA32 | URBAN | Asset Failure | Subtransmission | 296 | 56 | 0.011267 | 0.000201 | N
02-11-18 | 18:02 | ZN340:PA34 | SHORT RURAL | Asset Failure | Subtransmission | 324 | 56 | 0.076165 | 0.00136 | N
02-11-18 | 18:02 | ZN340:PA35 | URBAN | Asset Failure | Subtransmission | 1,122 | 56 | 0.042707 | 0.000763 | N
02-11-18 | 18:02 | ZN340:PA37 | URBAN | Asset Failure | Subtransmission | 1 | 56 | 3.8e-05 | 1e-06 | N
02-11-18 | 18:02 | ZN340:PA40 | URBAN | Asset Failure | Subtransmission | 963 | 56 | 0.036655 | 0.000655 | N
02-11-18 | 18:02 | ZN340:PA42 | URBAN | Asset Failure | Subtransmission | 13 | 55 | 0.000486 | 9e-06 | N
02-11-18 | 18:02 | ZN340:PA44 | URBAN | Asset Failure | Subtransmission | 1,211 | 55 | 0.045272 | 0.000823 | N
02-11-18 | 18:02 | ZN340:PA45 | URBAN | Asset Failure | Subtransmission | 694 | 55 | 0.025944 | 0.000472 | N
02-11-18 | 18:02 | ZN340:PA8 | URBAN | Asset Failure | Subtransmission | 2 | 56 | 7.6e-05 | 1e-06 | N
02-11-18 | 17:35 | ZN12640:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,075 | 0.004513 | 4e-06 | N
02-11-18 | 17:38 | 227:13015 | SHORT RURAL | Other | Other | 1 | 119 | 0.000499 | 4e-06 | N
02-11-18 | 18:00 | ZN847:PA1 | URBAN | Other | Other | 1 | 70 | 4.8e-05 | 1e-06 | N
02-11-18 | 18:07 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 90 | 0.000756 | 8e-06 | N
02-11-18 | 18:55 | ZN10993:PA33 | URBAN | Asset Failure | LV | 58 | 507 | 0.019974 | 3.9e-05 | N
02-11-18 | 19:00 | ZN35600:PA25 | URBAN | Network business | Network error | 64 | 145 | 0.006308 | 4.4e-05 | N
02-11-18 | 19:05 | ZN10998:PA32 | SHORT RURAL | Asset Failure | LV | 120 | 278 | 0.14021 | 0.000504 | N
02-11-18 | 19:40 | ZN10994:PA10 | URBAN | Asset Failure | HV | 1,112 | 102 | 0.077095 | 0.000756 | N
02-11-18 | 19:40 | ZN10994:PA21 | URBAN | Asset Failure | HV | 1,020 | 102 | 0.070716 | 0.000693 | N
02-11-18 | 20:16 | 227:13020 | SHORT RURAL | Asset Failure | LV | 7 | 164 | 0.004819 | 2.9e-05 | N
02-11-18 | 20:57 | ZN4545:PA32 | URBAN | Vegetation | Vegetation Blow/Fall In | 52 | 438 | 0.015481 | 3.5e-05 | N
02-11-18 | 20:56 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 1,174 | 0.033507 | 2.9e-05 | N
02-11-18 | 21:39 | ZN195:PA30 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 53 | 220 | 0.049024 | 0.000222 | N
02-11-18 | 22:01 | ZN9900:PA9 | URBAN | Asset Failure | LV | 13 | 929 | 0.008209 | 9e-06 | N
02-11-18 | 22:10 | ZN12650:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,492 | 122 | 0.76275 | 0.006263 | N
02-11-18 | 22:19 | ZN965:PA20 | URBAN | Asset Failure | HV | 867 | 108 | 0.063645 | 0.000589 | N
02-11-18 | 22:28 | ZN2568:PA29 | URBAN | Asset Failure | LV | 1 | 1,281 | 0.000871 | 1e-06 | N
02-11-18 | 22:40 | ZN15001:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,213 | 0.000825 | 1e-06 | N
02-11-18 | 22:43 | ZN9245:PA3 | SHORT RURAL | Other | Other | 1 | 1,097 | 0.004604 | 4e-06 | N
02-11-18 | 22:45 | ZN3672:PA35 | SHORT RURAL | Other | Other - Arcing | 1 | 914 | 0.003837 | 4e-06 | N
02-11-18 | 22:57 | 214:8669 | URBAN | Other | Other | 1 | 49 | 3.3e-05 | 1e-06 | N
02-11-18 | 23:33 | ZN9252:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 68 | 91 | 0.004208 | 4.6e-05 | N
03-11-18 | 01:38 | 239:82133 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 608 | 0.000413 | 1e-06 | N
03-11-18 | 03:07 | ZN129:PA52 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 143 | 0.004858 | 3.4e-05 | N
03-11-18 | 04:41 | ZN12580:PA10 | URBAN | Other | Other | 1,620 | 96 | 0.10567 | 0.001101 | N
03-11-18 | 04:41 | ZN12580:PA7 | URBAN | Other | Other | 176 | 85 | 0.010165 | 0.00012 | N
03-11-18 | 04:41 | ZN12580:PA8 | URBAN | Other | Other | 328 | 93 | 0.020727 | 0.000223 | N
03-11-18 | 07:10 | 224:80337 | URBAN | Other | Other | 1 | 74 | 5e-05 | 1e-06 | N
03-11-18 | 07:12 | 242:81539 | URBAN | Other | Other | 1 | 248 | 0.000168 | 1e-06 | N
03-11-18 | 07:48 | 814:82289 | SHORT RURAL | Asset Failure | Distribution substation | 4 | 42 | 0.000705 | 1.7e-05 | N
03-11-18 | 07:54 | ZN129:PA63 | URBAN | Asset Failure | LV | 25 | 732 | 0.012436 | 1.7e-05 | N
03-11-18 | 08:29 | ZN15001:PA18 | URBAN | Asset Failure | LV | 1 | 623 | 0.000424 | 1e-06 | N
03-11-18 | 09:19 | 221:11900 | URBAN | Other | Other | 1 | 75 | 5.1e-05 | 1e-06 | N
03-11-18 | 10:30 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 294 | 0.001233 | 4e-06 | N
03-11-18 | 10:39 | 227:13015 | SHORT RURAL | Asset Failure | LV | 1 | 70 | 0.000294 | 4e-06 | N
03-11-18 | 11:43 | ZN15006:PA1 | SHORT RURAL | Asset Failure | LV | 9 | 362 | 0.013674 | 3.8e-05 | N
03-11-18 | 12:34 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 120 | 0.002196 | 1.8e-05 | N
03-11-18 | 13:33 | ZN965:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 114 | 0.003641 | 3.2e-05 | N
03-11-18 | 14:33 | ZN9550:PA3 | URBAN | Asset Failure | LV | 1 | 296 | 0.000201 | 1e-06 | N
03-11-18 | 16:18 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 219 | 0.000921 | 4e-06 | N
03-11-18 | 16:21 | ZN14144:PA7 | SHORT RURAL | Other | Other - Arcing | 1 | 174 | 0.000728 | 4e-06 | N
03-11-18 | 16:50 | ZN847:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 395 | 0.000269 | 1e-06 | N
03-11-18 | 17:30 | ZN12690:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 200 | 0.000839 | 4e-06 | N
03-11-18 | 18:39 | ZN12660:PA10 | SHORT RURAL | Third Party | Vehicle impact | 1 | 1,280 | 0.005373 | 4e-06 | N
03-11-18 | 18:51 | ZN9550:PA36 | URBAN | Asset Failure | HV | 770 | 86 | 0.044965 | 0.000523 | N
03-11-18 | 19:28 | 224:80328 | URBAN | Other | Other | 56 | 69 | 0.002617 | 3.8e-05 | N
03-11-18 | 20:42 | 524:33572 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 123 | 0.000516 | 4e-06 | N
03-11-18 | 21:13 | 238:34151 | URBAN | Asset Failure | LV | 12 | 158 | 0.001286 | 8e-06 | N
04-11-18 | 02:59 | 230:81440 | URBAN | Asset Failure | HV | 729 | 196 | 0.096964 | 0.000495 | N
04-11-18 | 04:48 | 256:80632 | URBAN | Asset Failure | Distribution substation | 39 | 151 | 0.004007 | 2.7e-05 | N
04-11-18 | 06:28 | 523:33501 | SHORT RURAL | Asset Failure | HV | 734 | 28 | 0.087508 | 0.003081 | N
04-11-18 | 09:20 | ZN187:PA21 | URBAN | Asset Failure | HV | 1,149 | 55 | 0.042876 | 0.000781 | N
04-11-18 | 18:40 | ZN35500:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 25 | 10 | 0.00017 | 1.7e-05 | N
04-11-18 | 19:16 | 512:83743 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 2 | 774 | 0.006497 | 8e-06 | N
04-11-18 | 21:39 | ZN2568:PA32 | URBAN | Asset Failure | HV | 2,394 | 40 | 0.064432 | 0.001627 | N
05-11-18 | 02:18 | ZN12620:PA3 | URBAN | Other | Other - Arcing | 1 | 941 | 0.000639 | 1e-06 | N
05-11-18 | 05:31 | 221:11899 | SHORT RURAL | Other | Other | 1 | 118 | 0.000496 | 4e-06 | N
05-11-18 | 07:49 | ZN195:PA8 | URBAN | Asset Failure | LV | 14 | 865 | 0.008231 | 1e-05 | N
05-11-18 | 08:00 | 240:34846 | URBAN | Other | Other - Self Clearing Trigger | 2 | 77 | 0.000105 | 1e-06 | N
05-11-18 | 08:48 | ZN3155:PA34 | URBAN | Other | Other - Self Clearing Trigger | 22 | 87 | 0.0013 | 1.5e-05 | N
05-11-18 | 11:15 | 270:83593 | SHORT RURAL | Other | Other - Arcing | 1 | 164 | 0.000689 | 4e-06 | N
05-11-18 | 11:48 | 801:74119 | URBAN | Third Party | Vehicle impact | 11 | 152 | 0.001134 | 7e-06 | N
05-11-18 | 12:40 | ZN3155:PA34 | URBAN | Third Party | Other | 22 | 250 | 0.003737 | 1.5e-05 | N
05-11-18 | 15:17 | ZN1285:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 53 | 117 | 0.004214 | 3.6e-05 | N
05-11-18 | 16:39 | ZN15006:PA9 | URBAN | Third Party | Vehicle impact | 42 | 96 | 0.00274 | 2.9e-05 | N
01-11-18 | 22:40 | ZN2196:PA6 | URBAN | Third Party | Vehicle impact | 4 | 270 | 0.000734 | 3e-06 | N
05-11-18 | 18:46 | ZN187:PA17 | URBAN | Asset Failure | HV | 1,308 | 43 | 0.038218 | 0.000889 | N
05-11-18 | 21:58 | 270:83594 | URBAN | Third Party | Vehicle impact | 1 | 551 | 0.000374 | 1e-06 | N
05-11-18 | 22:42 | ZN2310:PA4 | URBAN | Other | Other | 1 | 73 | 4.9e-05 | 1e-06 | N
05-11-18 | 23:20 | ZN15006:PA9 | URBAN | Asset Failure | LV | 42 | 344 | 0.009822 | 2.9e-05 | N
06-11-18 | 02:18 | ZN3472:PA15 | URBAN | Asset Failure | HV | 183 | 73 | 0.009076 | 0.000124 | N
06-11-18 | 05:03 | 508:82575 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 116 | 0.000487 | 4e-06 | N
06-11-18 | 05:42 | ZN3425:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 378 | 0.000257 | 1e-06 | N
06-11-18 | 06:56 | ZN15006:PA9 | URBAN | Other | Other | 1 | 214 | 0.000145 | 1e-06 | N
03-11-18 | 19:15 | ZN187:PA4 | URBAN | Other | Other | 31 | 10 | 0.000211 | 2.1e-05 | N
05-11-18 | 08:30 | 515:35192 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 75 | 0.000944 | 1.3e-05 | N
06-11-18 | 09:44 | ZN35800:PA19 | URBAN | Other | Other | 1 | 55 | 3.7e-05 | 1e-06 | N
06-11-18 | 09:45 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 195 | 0.000132 | 1e-06 | N
06-11-18 | 09:57 | 813:89061 | LONG RURAL | Asset Failure | HV | 1 | 213 | 0.074895 | 0.000352 | N
06-11-18 | 10:40 | 528:83014 | SHORT RURAL | Asset Failure | LV | 1 | 215 | 0.000901 | 4e-06 | N
06-11-18 | 10:59 | ZN4545:PA4 | URBAN | Other | Other | 1 | 195 | 0.000133 | 1e-06 | N
03-11-18 | 21:20 | ZN12660:PA10 | SHORT RURAL | Third Party | Vehicle impact | 9 | 1,095 | 0.041361 | 3.8e-05 | N
06-11-18 | 11:09 | ZN10998:PA2 | URBAN | Third Party | Fire | 1 | 231 | 0.000157 | 1e-06 | N
06-11-18 | 11:50 | ZN15011:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 64 | 55 | 0.002379 | 4.3e-05 | N
06-11-18 | 12:16 | 502:48010 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 43 | 0.000181 | 4e-06 | N
06-11-18 | 13:57 | ZN965:PA3 | URBAN | Other | Other | 1 | 281 | 0.000191 | 1e-06 | N
06-11-18 | 14:46 | 220:8689 | URBAN | Other | Other | 1 | 48 | 3.2e-05 | 1e-06 | N
06-11-18 | 15:38 | ZN35555:PA13 | URBAN | Asset Failure | HV | 2,819 | 101 | 0.19363 | 0.001916 | N
06-11-18 | 15:38 | ZN35555:PA20 | URBAN | Asset Failure | HV | 133 | 397 | 0.035878 | 9e-05 | N
06-11-18 | 19:25 | ZN80:PA25 | URBAN | Asset Failure | LV | 1 | 190 | 0.000129 | 1e-06 | N
06-11-18 | 19:37 | ZN965:PA20 | URBAN | Asset Failure | HV | 868 | 73 | 0.043056 | 0.00059 | N
06-11-18 | 19:37 | ZN965:PA8 | URBAN | Asset Failure | HV | 1,194 | 112 | 0.091215 | 0.000811 | N
06-11-18 | 19:51 | ZN1673:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 119 | 0.002992 | 2.5e-05 | N
06-11-18 | 23:07 | ZN15006:PA9 | URBAN | Other | Other - Self Clearing Trigger | 42 | 118 | 0.003368 | 2.9e-05 | N
06-11-18 | 23:56 | ZN2400:PA18 | SHORT RURAL | Animal | Animal impact | 98 | 732 | 0.30108 | 0.000411 | N
07-11-18 | 02:55 | ZN847:PA44 | URBAN | Asset Failure | LV | 28 | 310 | 0.00589 | 1.9e-05 | N
07-11-18 | 04:30 | 233:82819 | SHORT RURAL | Other | Other - Self Clearing Trigger | 76 | 75 | 0.023924 | 0.000319 | N
07-11-18 | 08:30 | 522:83129 | URBAN | Other | Other | 1 | 73 | 5e-05 | 1e-06 | N
07-11-18 | 09:26 | ZN9245:PA4 | URBAN | Third Party | Dig-in | 1,039 | 69 | 0.048715 | 0.000706 | N
07-11-18 | 09:43 | 507:80925 | SHORT RURAL | Other | Other | 1 | 34 | 0.000141 | 4e-06 | N
02-11-18 | 22:11 | ZN35600:PA25 | URBAN | Asset Failure | LV | 85 | 229 | 0.01323 | 5.8e-05 | N
07-11-18 | 09:47 | ZN12650:PA2 | URBAN | Third Party | Vehicle impact | 1 | 283 | 0.000192 | 1e-06 | N
07-11-18 | 13:06 | ZN14143:PA12 | SHORT RURAL | Asset Failure | LV | 16 | 256 | 0.017191 | 6.7e-05 | N
07-11-18 | 12:28 | ZN3154:PA18 | URBAN | Asset Failure | LV | 30 | 352 | 0.007166 | 2e-05 | N
07-11-18 | 13:53 | ZN3672:PA21 | SHORT RURAL | Asset Failure | LV | 1 | 186 | 0.000781 | 4e-06 | N
07-11-18 | 17:09 | ZN847:PA18 | SHORT RURAL | Asset Failure | LV | 45 | 50 | 0.00945 | 0.000189 | N
07-11-18 | 15:01 | 229:34995 | SHORT RURAL | Asset Failure | LV | 1 | 478 | 0.002008 | 4e-06 | N
07-11-18 | 15:17 | 235:8685 | URBAN | Other | Other - Arcing | 1 | 253 | 0.000172 | 1e-06 | N
07-11-18 | 15:46 | ZN2400:PA18 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 32 | 0.000135 | 4e-06 | N
07-11-18 | 16:09 | ZN12620:PA11 | SHORT RURAL | Asset Failure | HV | 1 | 61 | 0.000256 | 4e-06 | N
07-11-18 | 17:04 | ZN2602:PA28 | URBAN | Other | Other | 1 | 275 | 0.000187 | 1e-06 | N
07-11-18 | 17:20 | ZN398:PA26 | URBAN | Other | Other | 2 | 106 | 0.000144 | 1e-06 | N
07-11-18 | 17:27 | 513:48056 | SHORT RURAL | Other | Other | 1 | 180 | 0.000755 | 4e-06 | N
07-11-18 | 17:43 | ZN12630:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 184 | 0.000773 | 4e-06 | N
07-11-18 | 20:48 | ZN2196:PA2 | URBAN | Asset Failure | LV | 36 | 231 | 0.005653 | 2.4e-05 | N
07-11-18 | 20:48 | ZN9700:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 3 | 112 | 0.000228 | 2e-06 | N
07-11-18 | 21:12 | ZN3154:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 48 | 88 | 0.00287 | 3.3e-05 | N
07-11-18 | 21:28 | ZN35600:PA25 | URBAN | Asset Failure | LV | 1 | 211 | 0.000143 | 1e-06 | N
07-11-18 | 21:22 | ZN3425:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 112 | 0.002436 | 2.2e-05 | N
08-11-18 | 00:20 | 228:7491 | URBAN | Asset Failure | LV | 1 | 200 | 0.000136 | 1e-06 | N
08-11-18 | 04:27 | 206:34441 | URBAN | Other | Other - Self Clearing Trigger | 188 | 168 | 0.021462 | 0.000128 | N
08-11-18 | 06:07 | 520:48172 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 3 | 173 | 0.002178 | 1.3e-05 | N
08-11-18 | 06:14 | ZN3154:PA18 | URBAN | Other | Other | 1 | 73 | 5e-05 | 1e-06 | N
08-11-18 | 06:59 | ZN2835:PA20 | URBAN | Third Party | Other | 328 | 745 | 0.16609 | 0.000223 | N
08-11-18 | 07:02 | ZN2568:PA32 | URBAN | Other | Other - Self Clearing Trigger | 80 | 57 | 0.003123 | 5.4e-05 | N
07-11-18 | 12:30 | 516:48065 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 165 | 0.000693 | 4e-06 | N
08-11-18 | 07:25 | ZN3154:PA18 | URBAN | Other | Other | 1 | 53 | 3.6e-05 | 1e-06 | N
08-11-18 | 07:30 | 232:11457 | SHORT RURAL | Asset Failure | LV | 1 | 89 | 0.000374 | 4e-06 | N
08-11-18 | 07:59 | ZN12570:PA37 | SHORT RURAL | Other | Other | 1 | 74 | 0.000312 | 4e-06 | N
08-11-18 | 08:30 | ZN35900:PA2 | URBAN | Other | Other - Arcing | 1 | 389 | 0.000265 | 1e-06 | N
08-11-18 | 08:43 | 202:34260 | URBAN | Other | Other - Self Clearing Trigger | 126 | 62 | 0.005267 | 8.6e-05 | N
08-11-18 | 08:46 | ZN2568:PA39 | URBAN | Other | Other - Arcing | 1 | 35 | 2.4e-05 | 1e-06 | N
08-11-18 | 08:46 | 807:74184 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 3 | 79 | 0.000995 | 1.3e-05 | N
08-11-18 | 11:49 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 121 | 0.000508 | 4e-06 | N
08-11-18 | 14:20 | ZN15014:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 23 | 100 | 0.009653 | 9.7e-05 | N
08-11-18 | 13:00 | ZN10999:PA22 | URBAN | Asset Failure | LV | 218 | 215 | 0.031802 | 0.000148 | N
08-11-18 | 14:44 | ZN1193:PA15 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 27 | 66 | 0.007479 | 0.000113 | N
08-11-18 | 15:53 | ZN3922:PA26 | URBAN | Other | Other - Self Clearing Trigger | 16 | 121 | 0.001316 | 1.1e-05 | N
08-11-18 | 16:49 | ZN2568:PA32 | URBAN | Other | Other - Self Clearing Trigger | 80 | 81 | 0.004381 | 5.4e-05 | N
08-11-18 | 17:35 | 807:74179 | SHORT RURAL | Asset Failure | HV | 50 | 127 | 0.026602 | 0.00021 | N
09-11-18 | 02:11 | ZN2568:PA9 | URBAN | Asset Failure | HV | 1,161 | 47 | 0.037054 | 0.000788 | N
09-11-18 | 08:26 | ZN630:PA16 | URBAN | Network business | Network error | 1 | 74 | 5e-05 | 1e-06 | N
09-11-18 | 08:26 | ZN630:PA25 | URBAN | Network business | Network error | 1 | 74 | 5e-05 | 1e-06 | N
09-11-18 | 08:26 | ZN630:PA26 | URBAN | Network business | Network error | 560 | 70 | 0.026539 | 0.00038 | N
09-11-18 | 08:26 | ZN630:PA41 | URBAN | Network business | Network error | 141 | 80 | 0.00766 | 9.6e-05 | N
09-11-18 | 09:07 | ZN36300:PA19 | URBAN | Third Party | Vehicle impact | 1 | 233 | 0.000158 | 1e-06 | N
09-11-18 | 09:35 | ZN3154:PA16 | URBAN | Third Party | Other | 29 | 173 | 0.003404 | 2e-05 | N
09-11-18 | 10:36 | ZN9700:PA23 | URBAN | Asset Failure | HV | 130 | 329 | 0.029043 | 8.8e-05 | N
09-11-18 | 14:10 | ZN36100:PA12 | URBAN | Asset Failure | LV | 1 | 290 | 0.000197 | 1e-06 | N
09-11-18 | 15:58 | ZN1193:PA26 | URBAN | Third Party | Vehicle impact | 1 | 159 | 0.000108 | 1e-06 | N
09-11-18 | 17:24 | ZN2196:PA5 | URBAN | Other | Other - Arcing | 1 | 349 | 0.000237 | 1e-06 | N
09-11-18 | 18:28 | ZN14891:PA1 | URBAN | Other | Other | 1 | 242 | 0.000164 | 1e-06 | N
09-11-18 | 19:26 | ZN10999:PA29 | URBAN | Other | Other - Self Clearing Trigger | 37 | 64 | 0.001604 | 2.5e-05 | N
09-11-18 | 20:49 | 222:33601 | SHORT RURAL | Other | Other | 1 | 70 | 0.000295 | 4e-06 | N
09-11-18 | 20:56 | ZN9550:PA36 | URBAN | Asset Failure | HV | 772 | 42 | 0.022018 | 0.000524 | N
09-11-18 | 20:56 | ZN9550:PA4 | URBAN | Asset Failure | HV | 467 | 42 | 0.013319 | 0.000317 | N
09-11-18 | 20:56 | ZN9550:PA6 | URBAN | Asset Failure | HV | 45 | 42 | 0.001283 | 3.1e-05 | N
09-11-18 | 22:13 | ZN129:PA41 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 127 | 8.7e-05 | 1e-06 | N
10-11-18 | 00:17 | ZN965:PA20 | URBAN | Asset Failure | HV | 869 | 71 | 0.041897 | 0.00059 | N
10-11-18 | 00:54 | ZN2196:PA18 | URBAN | Third Party | Vehicle impact | 1 | 331 | 0.000225 | 1e-06 | N
10-11-18 | 02:26 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 388 | 0.00765 | 2e-05 | N
10-11-18 | 04:53 | 204:82697 | URBAN | Other | Other | 1 | 46 | 3.1e-05 | 1e-06 | N
10-11-18 | 07:32 | ZN1287:PA17 | URBAN | Third Party | Vehicle impact | 40 | 258 | 0.007001 | 2.7e-05 | N
10-11-18 | 09:20 | 814:82283 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 2 | 50 | 0.000422 | 8e-06 | N
10-11-18 | 09:52 | ZN630:PA32 | URBAN | Third Party | Dig-in | 51 | 101 | 0.003507 | 3.5e-05 | N
10-11-18 | 10:10 | ZN2835:PA24 | URBAN | Asset Failure | LV | 49 | 154 | 0.005131 | 3.3e-05 | N
10-11-18 | 11:13 | ZN12570:PA37 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 19 | 232 | 0.018583 | 8e-05 | N
10-11-18 | 13:57 | ZN4545:PA32 | URBAN | Asset Failure | LV | 1 | 422 | 0.000287 | 1e-06 | N
10-11-18 | 17:43 | ZN12690:PA24 | SHORT RURAL | Asset Failure | LV | 1 | 317 | 0.001336 | 4e-06 | N
10-11-18 | 17:45 | ZN690:PA25 | URBAN | Other | Other | 1 | 315 | 0.000214 | 1e-06 | N
10-11-18 | 20:07 | ZN965:PA8 | URBAN | Asset Failure | LV | 33 | 997 | 0.022346 | 2.2e-05 | N
10-11-18 | 23:48 | ZN13000:PA5 | SHORT RURAL | Third Party | Vehicle impact | 25 | 582 | 0.06134 | 0.000105 | N
11-11-18 | 15:15 | ZN80:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 102 | 19 | 0.001335 | 6.9e-05 | N
11-11-18 | 17:33 | 814:82283 | SHORT RURAL | Asset Failure | LV | 1 | 87 | 0.000367 | 4e-06 | N
11-11-18 | 18:38 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,012 | 0.004265 | 4e-06 | N
11-11-18 | 20:41 | ZN3288:PA41 42KLM | CBD | Asset Failure | Subtransmission | 1 | 28 | 0.000919 | 3.3e-05 | N
11-11-18 | 20:41 | ZN384:PA70 | URBAN | Asset Failure | Subtransmission | 2 | 28 | 3.8e-05 | 1e-06 | N
11-11-18 | 20:41 | ZN711:PA11 | URBAN | Asset Failure | Subtransmission | 1 | 28 | 1.9e-05 | 1e-06 | N
11-11-18 | 20:41 | ZN711:PA28 | URBAN | Asset Failure | Subtransmission | 1 | 28 | 1.9e-05 | 1e-06 | N
11-11-18 | 20:41 | ZN711:PA33 | URBAN | Asset Failure | Subtransmission | 1 | 28 | 1.9e-05 | 1e-06 | N
11-11-18 | 20:41 | ZN7481:PA1 | URBAN | Asset Failure | Subtransmission | 2,052 | 28 | 0.039017 | 0.001393 | N
11-11-18 | 20:41 | ZN7481:PA10 | URBAN | Asset Failure | Subtransmission | 23 | 28 | 0.000437 | 1.6e-05 | N
11-11-18 | 20:41 | ZN7481:PA12 | URBAN | Asset Failure | Subtransmission | 966 | 28 | 0.018367 | 0.000656 | N
11-11-18 | 20:41 | ZN7481:PA13 | URBAN | Asset Failure | Subtransmission | 233 | 27 | 0.004272 | 0.000158 | N
11-11-18 | 20:41 | ZN7481:PA14 | URBAN | Asset Failure | Subtransmission | 1,395 | 28 | 0.026524 | 0.000947 | N
11-11-18 | 20:41 | ZN7481:PA16 | URBAN | Asset Failure | Subtransmission | 571 | 28 | 0.010857 | 0.000388 | N
11-11-18 | 20:41 | ZN7481:PA17 | URBAN | Asset Failure | Subtransmission | 319 | 28 | 0.006065 | 0.000217 | N
11-11-18 | 20:41 | ZN7481:PA19 | URBAN | Asset Failure | Subtransmission | 143 | 27 | 0.002622 | 9.7e-05 | N
11-11-18 | 20:41 | ZN7481:PA2 | URBAN | Asset Failure | Subtransmission | 10 | 28 | 0.00019 | 7e-06 | N
11-11-18 | 20:41 | ZN7481:PA20 | URBAN | Asset Failure | Subtransmission | 1,501 | 28 | 0.02854 | 0.001019 | N
11-11-18 | 20:41 | ZN7481:PA21 | URBAN | Asset Failure | Subtransmission | 129 | 27 | 0.002365 | 8.8e-05 | N
11-11-18 | 20:41 | ZN7481:PA3 | URBAN | Asset Failure | Subtransmission | 659 | 28 | 0.01253 | 0.000448 | N
11-11-18 | 20:41 | ZN7481:PA5 | URBAN | Asset Failure | Subtransmission | 8 | 28 | 0.000152 | 5e-06 | N
11-11-18 | 20:41 | ZN7481:PA8 | URBAN | Asset Failure | Subtransmission | 1 | 28 | 1.9e-05 | 1e-06 | N
11-11-18 | 20:41 | ZN7481:PA9 | URBAN | Asset Failure | Subtransmission | 1,319 | 28 | 0.025079 | 0.000896 | N
11-11-18 | 23:00 | ZN2635:PA31 | URBAN | Animal | Animal nesting/burrowing, etc and other | 51 | 70 | 0.002424 | 3.5e-05 | N
11-11-18 | 23:00 | ZN2635:PA58 | URBAN | Animal | Animal nesting/burrowing, etc and other | 2,086 | 70 | 0.099158 | 0.001417 | N
08-11-18 | 13:50 | 516:48066 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 26 | 0.000109 | 4e-06 | N
12-11-18 | 09:06 | ZN690:PA10 | URBAN | Third Party | Vehicle impact | 75 | 108 | 0.005517 | 5.1e-05 | N
12-11-18 | 09:15 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 145 | 0.000611 | 4e-06 | N
12-11-18 | 10:31 | 802:82215 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 208 | 0.000878 | 4e-06 | N
12-11-18 | 11:05 | 806:82662 | SHORT RURAL | Asset Failure | LV | 1 | 170 | 0.000717 | 4e-06 | N
12-11-18 | 13:46 | ZN12650:PA6 | URBAN | Third Party | Vehicle impact | 1,273 | 74 | 0.06397 | 0.000864 | N
12-11-18 | 15:03 | ZN5868:PA14 | URBAN | Asset Failure | LV | 40 | 167 | 0.004531 | 2.7e-05 | N
12-11-18 | 14:59 | ZN965:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 390 | 0.000265 | 1e-06 | N
12-11-18 | 15:18 | ZN8100:PA7 | URBAN | Third Party | Other | 72 | 342 | 0.016704 | 4.9e-05 | N
12-11-18 | 15:58 | ZN690:PA33 | URBAN | Third Party | Vehicle impact | 37 | 132 | 0.003317 | 2.5e-05 | N
12-11-18 | 16:32 | ZN12690:PA16 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 208 | 0.000877 | 4e-06 | N
12-11-18 | 16:44 | ZN9900:PA2 | URBAN | Asset Failure | LV | 30 | 271 | 0.005511 | 2e-05 | N
12-11-18 | 17:36 | ZN80:PA36 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 223 | 0.006973 | 3.1e-05 | N
12-11-18 | 17:58 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 212 | 0.000144 | 1e-06 | N
12-11-18 | 17:58 | 238:34140 | SHORT RURAL | Third Party | Other | 3 | 377 | 0.004768 | 1.3e-05 | N
12-11-18 | 21:29 | ZN15010:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 70 | 220 | 0.010469 | 4.8e-05 | N
12-11-18 | 22:50 | ZN15010:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 140 | 0.003327 | 2.4e-05 | N
12-11-18 | 22:10 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 54 | 105 | 0.023904 | 0.000228 | N
13-11-18 | 06:21 | ZN1193:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 218 | 0.000148 | 1e-06 | N
13-11-18 | 08:01 | 270:83593 | SHORT RURAL | Other | Other - Arcing | 1 | 410 | 0.00173 | 4e-06 | N
13-11-18 | 09:12 | ZN4545:PA31 | URBAN | Other | Other | 1 | 138 | 9.4e-05 | 1e-06 | N
13-11-18 | 09:54 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 211 | 0.00089 | 4e-06 | N
13-11-18 | 10:47 | 810:74054 | LONG RURAL | Asset Failure | HV | 180 | 82 | 5.1783 | 0.063291 | N
12-11-18 | 15:20 | ZN35370:PA4 | SHORT RURAL | Asset Failure | LV | 3 | 25 | 0.000316 | 1.3e-05 | N
13-11-18 | 13:10 | ZN14144:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 22 | 160 | 0.014806 | 9.3e-05 | N
13-11-18 | 16:47 | ZN847:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 62 | 0.001823 | 2.9e-05 | N
13-11-18 | 17:31 | 507:80914 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 149 | 0.001256 | 8e-06 | N
13-11-18 | 18:50 | ZN12620:PA11 | SHORT RURAL | Other | Other | 1 | 90 | 0.000379 | 4e-06 | N
13-11-18 | 17:00 | 415:33884 | URBAN | Other | Other - Arcing | 1 | 195 | 0.000132 | 1e-06 | N
13-11-18 | 22:48 | ZN965:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 672 | 0.000456 | 1e-06 | N
14-11-18 | 04:48 | 202:34250 | URBAN | Animal | Animal impact | 1,157 | 75 | 0.058929 | 0.000786 | N
14-11-18 | 04:52 | ZN12660:PA16 | URBAN | Animal | Animal impact | 950 | 60 | 0.039029 | 0.000645 | N
14-11-18 | 06:13 | 814:82285 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 145 | 141 | 0.086099 | 0.000611 | N
14-11-18 | 08:35 | ZN1673:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 9 | 0.000232 | 2.6e-05 | N
14-11-18 | 10:05 | 232:11454 | SHORT RURAL | Third Party | Vehicle impact | 142 | 461 | 0.27593 | 0.000599 | N
14-11-18 | 10:46 | ZN15008:PA5 | URBAN | Third Party | Vehicle impact | 1,289 | 33 | 0.028887 | 0.000875 | N
14-11-18 | 11:25 | ZN15008:PA5 | URBAN | Asset Failure | LV | 61 | 111 | 0.004579 | 4.1e-05 | N
14-11-18 | 14:33 | 258:80775 | URBAN | Other | Other | 1 | 107 | 7.3e-05 | 1e-06 | N
14-11-18 | 20:51 | ZN10993:PA27 | URBAN | Asset Failure | HV | 1 | 66 | 4.5e-05 | 1e-06 | N
14-11-18 | 20:51 | ZN10993:PA35 | URBAN | Asset Failure | HV | 1 | 87 | 5.9e-05 | 1e-06 | N
14-11-18 | 20:51 | ZN10995:PA1 | URBAN | Asset Failure | HV | 2,068 | 66 | 0.092689 | 0.001404 | N
14-11-18 | 20:51 | ZN10995:PA2 | URBAN | Asset Failure | HV | 2,038 | 79 | 0.10997 | 0.001384 | N
14-11-18 | 22:22 | ZN3922:PA22 | URBAN | Asset Failure | LV | 48 | 267 | 0.008715 | 3.3e-05 | N
14-11-18 | 22:41 | ZN3922:PA22 | URBAN | Asset Failure | LV | 1 | 270 | 0.000183 | 1e-06 | N
15-11-18 | 10:16 | ZN195:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 127 | 8.6e-05 | 1e-06 | N
15-11-18 | 11:05 | ZN9550:PA28 | URBAN | Asset Failure | LV | 79 | 54 | 0.002914 | 5.4e-05 | N
15-11-18 | 11:31 | 509:33395 | LONG RURAL | Asset Failure | HV | 63 | 16 | 0.35456 | 0.02216 | N
15-11-18 | 13:33 | ZN14144:PA8 | URBAN | Other | Other | 1 | 75 | 5.1e-05 | 1e-06 | N
15-11-18 | 13:35 | ZN1648:PA4 | URBAN | Third Party | Vehicle impact | 105 | 95 | 0.006774 | 7.1e-05 | N
15-11-18 | 13:49 | 258:80784 | URBAN | Other | Other | 1 | 1,099 | 0.000747 | 1e-06 | N
15-11-18 | 13:59 | ZN15008:PA5 | URBAN | Asset Failure | LV | 61 | 424 | 0.017579 | 4.1e-05 | N
15-11-18 | 14:12 | ZN195:PA10 | URBAN | Other | Other - Self Clearing Trigger | 43 | 20 | 0.000583 | 2.9e-05 | N
15-11-18 | 14:58 | 414:LD1 | URBAN | Animal | Animal impact | 5 | 98 | 0.000333 | 3e-06 | N
15-11-18 | 14:59 | 414:LD734 | SHORT RURAL | Animal | Animal impact | 1 | 101 | 0.000426 | 4e-06 | N
15-11-18 | 16:10 | 239:82131 | SHORT RURAL | Asset Failure | HV | 190 | 146 | 0.11723 | 0.000801 | N
15-11-18 | 17:58 | 261:81870 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 227 | 0.000154 | 1e-06 | N
15-11-18 | 18:00 | 261:81870 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 225 | 0.000153 | 1e-06 | N
15-11-18 | 18:01 | 261:81870 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 224 | 0.000152 | 1e-06 | N
15-11-18 | 18:44 | ZN80:PA24 | URBAN | Other | Other - Self Clearing Trigger | 54 | 275 | 0.01009 | 3.7e-05 | N
15-11-18 | 20:00 | ZN965:PA47 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 150 | 0.000102 | 1e-06 | N
15-11-18 | 20:05 | ZN10999:PA29 | URBAN | Other | Other - Self Clearing Trigger | 65 | 84 | 0.003712 | 4.4e-05 | N
15-11-18 | 23:32 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 57 | 0.001202 | 2.1e-05 | N
16-11-18 | 00:06 | 240:34849 | URBAN | Other | Other - Arcing | 1 | 294 | 0.000199 | 1e-06 | N
16-11-18 | 08:38 | ZN12610:PA13 | SHORT RURAL | Other | Other - Arcing | 1 | 292 | 0.00123 | 4e-06 | N
16-11-18 | 08:54 | 813:89061 | LONG RURAL | Animal | Animal impact | 1 | 131 | 0.046078 | 0.000352 | N
16-11-18 | 10:53 | 243:80080 | SHORT RURAL | Third Party | Other | 1 | 88 | 0.00037 | 4e-06 | N
16-11-18 | 10:57 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 68 | 0.000287 | 4e-06 | N
16-11-18 | 11:13 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 61 | 0.000257 | 4e-06 | N
16-11-18 | 14:08 | ZN262:PA41 | URBAN | Asset Failure | LV | 96 | 127 | 0.00828 | 6.5e-05 | N
16-11-18 | 14:43 | ZN3922:PA12 | URBAN | Other | Other - Self Clearing Trigger | 23 | 72 | 0.001121 | 1.6e-05 | N
16-11-18 | 16:00 | 810:74054 | LONG RURAL | Asset Failure | HV | 15 | 70 | 0.36933 | 0.005276 | N
16-11-18 | 15:40 | 814:82289 | SHORT RURAL | Other | Other | 1 | 45 | 0.00019 | 4e-06 | N
16-11-18 | 16:03 | ZN12610:PA13 | SHORT RURAL | Asset Failure | Distribution substation | 95 | 51 | 0.02044 | 0.000401 | N
16-11-18 | 17:07 | ZN4545:PA32 | URBAN | Third Party | Vehicle impact | 1 | 166 | 0.000113 | 1e-06 | N
16-11-18 | 19:46 | ZN931:PA26 | URBAN | Asset Failure | HV | 230 | 55 | 0.008591 | 0.000156 | N
16-11-18 | 21:01 | 524:33580 | SHORT RURAL | Other | Other | 1 | 126 | 0.000532 | 4e-06 | N
16-11-18 | 23:04 | 813:89063 | SHORT RURAL | Asset Failure | LV | 25 | 95 | 0.010019 | 0.000105 | N
16-11-18 | 23:54 | ZN15005:PA6 | URBAN | Asset Failure | LV | 72 | 590 | 0.028837 | 4.9e-05 | N
17-11-18 | 08:38 | ZN4545:PA36 | URBAN | Asset Failure | LV | 1 | 441 | 0.000301 | 1e-06 | N
17-11-18 | 09:06 | 522:83132 | SHORT RURAL | Third Party | Other | 1 | 144 | 0.000606 | 4e-06 | N
17-11-18 | 09:59 | ZN15009:PA5 | URBAN | Asset Failure | LV | 57 | 115 | 0.004473 | 3.9e-05 | N
17-11-18 | 10:13 | ZN7481:PA16 | URBAN | Network business | Switching and protection error | 571 | 2 | 0.000777 | 0.000389 | N
17-11-18 | 11:56 | ZN10993:PA35 | URBAN | Third Party | Vehicle impact | 1 | 244 | 0.000166 | 1e-06 | N
17-11-18 | 12:25 | ZN15009:PA5 | URBAN | Asset Failure | LV | 57 | 1,400 | 0.054319 | 3.9e-05 | N
17-11-18 | 12:54 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 126 | 0.000531 | 4e-06 | N
17-11-18 | 17:25 | ZN10999:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 31 | 2.1e-05 | 1e-06 | N
17-11-18 | 18:27 | 261:81879 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 42 | 2.9e-05 | 1e-06 | N
17-11-18 | 20:04 | ZN14891:PA12 | SHORT RURAL | Asset Failure | HV | 386 | 50 | 0.080954 | 0.001626 | N
18-11-18 | 08:50 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 47 | 60 | 0.011834 | 0.000198 | N
18-11-18 | 07:27 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 547 | 0.002304 | 4e-06 | N
18-11-18 | 16:29 | 243:80081 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 241 | 0.001013 | 4e-06 | N
18-11-18 | 17:11 | ZN195:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 227 | 0.000954 | 4e-06 | N
18-11-18 | 17:15 | ZN10994:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 915 | 0.000622 | 1e-06 | N
18-11-18 | 17:57 | 512:83743 | SHORT RURAL | Asset Failure | HV | 4 | 238 | 0.00401 | 1.7e-05 | N
18-11-18 | 21:06 | ZN14891:PA20 | SHORT RURAL | Asset Failure | HV | 544 | 55 | 0.12602 | 0.002291 | N
18-11-18 | 21:44 | ZN80:PA22 | URBAN | Asset Failure | LV | 159 | 56 | 0.006003 | 0.000108 | N
19-11-18 | 07:41 | 511:29877 | SHORT RURAL | Asset Failure | Distribution substation | 7 | 43 | 0.001278 | 2.9e-05 | N
16-11-18 | 12:28 | ZN7481:PA1 | URBAN | Asset Failure | Zone substation | 2,056 | 2 | 0.002793 | 0.001396 | N
16-11-18 | 12:28 | ZN7481:PA3 | URBAN | Asset Failure | Zone substation | 659 | 2 | 0.000895 | 0.000448 | N
19-11-18 | 08:26 | ZN2400:PA18 | SHORT RURAL | Asset Failure | HV | 4 | 299 | 0.005037 | 1.7e-05 | N
16-11-18 | 12:45 | 216:10722 | SHORT RURAL | Asset Failure | HV | 7 | 160 | 0.004722 | 3e-05 | N
16-11-18 | 19:30 | 222:33602 | URBAN | Other | Other - Self Clearing Trigger | 1 | 180 | 0.000122 | 1e-06 | N
19-11-18 | 09:02 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 328 | 0.000223 | 1e-06 | N
16-11-18 | 13:25 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 55 | 0.000232 | 4e-06 | N
19-11-18 | 11:35 | ZN3472:PA18 | URBAN | Other | Other - Arcing | 2 | 1,175 | 0.001598 | 1e-06 | N
19-11-18 | 14:10 | 520:48172 | SHORT RURAL | Asset Failure | HV | 24 | 23 | 0.002325 | 0.000101 | N
19-11-18 | 14:35 | ZN965:PA28 | URBAN | Asset Failure | LV | 30 | 775 | 0.015802 | 2e-05 | N
19-11-18 | 16:02 | 522:83123 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 105 | 0.000442 | 4e-06 | N
19-11-18 | 18:02 | ZN12640:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 207 | 0.000141 | 1e-06 | N
19-11-18 | 19:03 | 210:83466 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 47 | 3.2e-05 | 1e-06 | N
19-11-18 | 20:28 | 264:81236 | URBAN | Other | Other | 1 | 67 | 4.6e-05 | 1e-06 | N
20-11-18 | 00:13 | 238:34143 | URBAN | Third Party | Vehicle impact | 1 | 706 | 0.00048 | 1e-06 | N
20-11-18 | 00:15 | 238:34143 | URBAN | Other | Other | 1 | 54 | 3.7e-05 | 1e-06 | N
20-11-18 | 01:20 | ZN12620:PA8 | SHORT RURAL | Asset Failure | HV | 1,250 | 103 | 0.54281 | 0.005264 | N
20-11-18 | 07:33 | ZN3922:PA26 | URBAN | Asset Failure | LV | 17 | 250 | 0.00289 | 1.2e-05 | N
20-11-18 | 07:51 | ZN3922:PA11 | URBAN | Other | Other | 1 | 277 | 0.000188 | 1e-06 | N
20-11-18 | 08:32 | ZN340:PA32 | URBAN | Asset Failure | LV | 1 | 237 | 0.000161 | 1e-06 | N
20-11-18 | 08:48 | 238:34141 | SHORT RURAL | Asset Failure | LV | 9 | 214 | 0.008111 | 3.8e-05 | N
20-11-18 | 09:30 | 257:82006 | URBAN | Other | Other | 1 | 89 | 6.1e-05 | 1e-06 | N
20-11-18 | 09:46 | 257:82006 | URBAN | Other | Other | 1 | 73 | 5e-05 | 1e-06 | N
20-11-18 | 15:07 | ZN12660:PA6 | SHORT RURAL | Other | Other | 1 | 108 | 0.000453 | 4e-06 | N
20-11-18 | 16:35 | 224:80337 | URBAN | Other | Other | 1 | 1,119 | 0.000761 | 1e-06 | N
20-11-18 | 18:52 | ZN1193:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 298 | 0.006883 | 2.3e-05 | N
20-11-18 | 16:43 | ZN1193:PA28 | URBAN | Other | Other | 1 | 83 | 5.7e-05 | 1e-06 | N
20-11-18 | 16:43 | ZN35900:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 217 | 0.000914 | 4e-06 | N
20-11-18 | 16:41 | ZN3288:PA45 46ABC | CBD | Asset Failure | HV | 990 | 7 | 0.23753 | 0.032525 | N
20-11-18 | 18:36 | ZN3155:PA32 | URBAN | Other | Other - Arcing | 1 | 587 | 0.000399 | 1e-06 | N
20-11-18 | 19:45 | 801:74120 | SHORT RURAL | Third Party | Vehicle impact | 1 | 975 | 0.004104 | 4e-06 | N
20-11-18 | 22:40 | ZN10999:PA23 | URBAN | Animal | Other | 1 | 845 | 0.000575 | 1e-06 | N
20-11-18 | 23:06 | ZN12630:PA3 | SHORT RURAL | Weather |  | 15 | 200 | 0.012634 | 6.3e-05 | N
21-11-18 | 01:00 | 507:80932 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 422 | 160 | 0.28466 | 0.001777 | N
21-11-18 | 01:59 | ZN12570:PA21 | URBAN | Asset Failure | LV | 80 | 286 | 0.015537 | 5.4e-05 | N
21-11-18 | 03:55 | ZN35500:PA34 | URBAN | Other | Other - Self Clearing Trigger | 312 | 62 | 0.013154 | 0.000212 | N
20-11-18 | 16:15 | 227:13015 | SHORT RURAL | Third Party | Unauthorised access | 2 | 38 | 0.00032 | 8e-06 | N
21-11-18 | 03:01 | ZN14891:PA12 | SHORT RURAL | Weather |  | 5 | 609 | 0.012818 | 2.1e-05 | N
21-11-18 | 09:12 | ZN690:PA10 | URBAN | Other | Other | 1 | 245 | 0.000166 | 1e-06 | N
21-11-18 | 14:24 | 228:7491 | URBAN | Other | Other | 1 | 55 | 3.8e-05 | 1e-06 | N
21-11-18 | 14:40 | ZN2466:PA2 | URBAN | Third Party | Vehicle impact | 13 | 100 | 0.000884 | 9e-06 | N
21-11-18 | 17:50 | ZN80:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 41 | 175 | 0.004879 | 2.8e-05 | N
21-11-18 | 17:51 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 69 | 0.000291 | 4e-06 | N
21-11-18 | 22:45 | ZN1193:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 60 | 0.00204 | 3.4e-05 | N
21-11-18 | 18:23 | ZN80:PA32 | URBAN | Network business | Network error | 2 | 172 | 0.000234 | 1e-06 | N
21-11-18 | 18:55 | ZN10999:PA32 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 294 | 0.0002 | 1e-06 | N
21-11-18 | 19:11 | ZN630:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 80 | 94 | 0.005114 | 5.4e-05 | N
21-11-18 | 19:24 | ZN9252:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 76 | 0.001964 | 2.6e-05 | N
21-11-18 | 19:51 | ZN36100:PA15 | URBAN | Third Party | Other | 1 | 393 | 0.000267 | 1e-06 | N
21-11-18 | 23:45 | ZN630:PA10 | URBAN | Asset Failure | LV | 80 | 60 | 0.003264 | 5.4e-05 | N
21-11-18 | 21:23 | 210:83473 | URBAN | Asset Failure | LV | 61 | 61 | 0.002534 | 4.1e-05 | N
21-11-18 | 21:25 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 75 | 0.001674 | 2.2e-05 | N
21-11-18 | 21:27 | ZN12570:PA25 | SHORT RURAL | Other | Other - Self Clearing Trigger | 28 | 663 | 0.07818 | 0.000118 | N
21-11-18 | 21:30 | 223:14393 | URBAN | Other | Other | 1 | 674 | 0.000459 | 1e-06 | N
22-11-18 | 05:47 | ZN965:PA24 | URBAN | Third Party | Other | 31 | 192 | 0.004054 | 2.1e-05 | N
22-11-18 | 09:33 | 257:81987 | URBAN | Third Party | Other | 1 | 48 | 3.3e-05 | 1e-06 | N
22-11-18 | 09:56 | ZN12620:PA11 | SHORT RURAL | Other | Other | 1 | 20 | 8.6e-05 | 4e-06 | N
22-11-18 | 10:29 | 507:80914 | SHORT RURAL | Asset Failure | HV | 7 | 559 | 0.016479 | 2.9e-05 | N
22-11-18 | 11:43 | 239:82133 | URBAN | Other | Other | 1 | 97 | 6.6e-05 | 1e-06 | N
22-11-18 | 12:13 | ZN10999:PA38 | URBAN | Other | Other - Arcing | 1 | 137 | 9.3e-05 | 1e-06 | N
23-11-18 | 13:03 | 522:83132 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 220 | 15 | 0.013898 | 0.000927 | N
22-11-18 | 14:23 | 229:34983 | SHORT RURAL | Asset Failure | LV | 31 | 646 | 0.084384 | 0.000131 | N
22-11-18 | 12:46 | 526:34641 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 21 | 399 | 0.035288 | 8.8e-05 | N
22-11-18 | 12:52 | 509:33397 | SHORT RURAL | Asset Failure | HV | 393 | 220 | 0.36349 | 0.001655 | N
22-11-18 | 12:55 | ZN965:PA15 | URBAN | Other | Other - Arcing | 1 | 395 | 0.000269 | 1e-06 | N
22-11-18 | 12:51 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 106 | 130 | 0.058114 | 0.000446 | N
22-11-18 | 12:59 | 264:81236 | URBAN | Other | Other | 1 | 155 | 0.000105 | 1e-06 | N
22-11-18 | 13:13 | ZN14891:PA12 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 276 | 0.020953 | 7.6e-05 | N
22-11-18 | 13:14 | ZN188:PA44 | URBAN | Vegetation | Vegetation Blow/Fall In | 107 | 80 | 0.005828 | 7.3e-05 | N
22-11-18 | 13:22 | 270:83587 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,237 | 4 | 0.003365 | 0.000841 | N
21-11-18 | 10:00 | 516:48065 | SHORT RURAL | Asset Failure | LV | 1 | 70 | 0.000295 | 4e-06 | N
22-11-18 | 13:22 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 78 | 108 | 0.035477 | 0.000328 | N
22-11-18 | 13:57 | ZN690:PA30 | URBAN | Asset Failure | LV | 1 | 445 | 0.000303 | 1e-06 | N
22-11-18 | 14:06 | ZN12610:PA25 | URBAN | Asset Failure | HV | 428 | 83 | 0.024157 | 0.000291 | N
22-11-18 | 14:07 | 512:83743 | SHORT RURAL | Asset Failure | HV | 3 | 153 | 0.001933 | 1.3e-05 | N
22-11-18 | 14:15 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 196 | 643 | 0.53096 | 0.000825 | N
22-11-18 | 14:26 | ZN3425:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 214 | 0.004646 | 2.2e-05 | N
22-11-18 | 14:21 | 258:80787 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 158 | 0.000108 | 1e-06 | N
22-11-18 | 14:27 | 522:83126 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 179 | 157 | 0.11843 | 0.000754 | N
22-11-18 | 14:38 | 264:81244 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 31 | 216 | 0.028254 | 0.000131 | N
22-11-18 | 14:38 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 20 | 366 | 0.030857 | 8.4e-05 | N
22-11-18 | 14:59 | ZN10999:PA36 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 140 | 0.002761 | 2e-05 | N
22-11-18 | 15:29 | 264:81236 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 398 | 0.00027 | 1e-06 | N
22-11-18 | 15:48 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 274 | 0.006924 | 2.5e-05 | N
22-11-18 | 15:50 | 515:35198 | SHORT RURAL | Asset Failure | HV | 2 | 170 | 0.001432 | 8e-06 | N
22-11-18 | 15:58 | ZN180:PA24 | URBAN | Third Party | Vehicle impact | 1 | 317 | 0.000216 | 1e-06 | N
22-11-18 | 16:31 | ZN965:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 71 | 0.001549 | 2.2e-05 | N
22-11-18 | 16:03 | ZN965:PA38 | URBAN | Third Party | Other | 1 | 235 | 0.00016 | 1e-06 | N
22-11-18 | 16:01 | 233:82819 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 298 | 0.001257 | 4e-06 | N
22-11-18 | 16:16 | 264:81232 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 264 | 0.001113 | 4e-06 | N
22-11-18 | 16:22 | ZN1673:PA18 | URBAN | Asset Failure | HV | 1,180 | 51 | 0.040923 | 0.000802 | N
22-11-18 | 16:22 | ZN1673:PA2 | URBAN | Asset Failure | HV | 43 | 51 | 0.001491 | 2.9e-05 | N
22-11-18 | 16:26 | 229:34995 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 677 | 175 | 0.49948 | 0.002851 | N
22-11-18 | 16:47 | 227:13018 | URBAN | Vegetation | Vegetation Blow/Fall In | 67 | 108 | 0.004921 | 4.6e-05 | N
22-11-18 | 16:52 | 205:12205 | URBAN | Other | Other | 1 | 107 | 7.3e-05 | 1e-06 | N
22-11-18 | 17:11 | 526:34640 | SHORT RURAL | Asset Failure | HV | 1 | 1,149 | 0.004839 | 4e-06 | N
22-11-18 | 17:08 | ZN12600:PA9 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,467 | 101 | 0.62603 | 0.006178 | N
22-11-18 | 17:24 | ZN2835:PA10 | URBAN | Asset Failure | LV | 1 | 9 | 6e-06 | 1e-06 | N
22-11-18 | 17:27 | ZN398:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 126 | 108 | 0.009225 | 8.6e-05 | N
22-11-18 | 17:30 | ZN2568:PA27 | URBAN | Vegetation | Vegetation Grow In | 1 | 263 | 0.000179 | 1e-06 | N
22-11-18 | 17:30 | ZN262:PA29 | URBAN | Other | Other - Self Clearing Trigger | 53 | 110 | 0.003965 | 3.6e-05 | N
22-11-18 | 18:19 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 356 | 0.000242 | 1e-06 | N
22-11-18 | 18:27 | ZN10999:PA1 | URBAN | Weather |  | 29 | 478 | 0.009426 | 2e-05 | N
22-11-18 | 18:32 | 223:14394 | URBAN | Other | Other | 1 | 68 | 4.6e-05 | 1e-06 | N
22-11-18 | 18:36 | ZN690:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 9 | 167 | 0.001022 | 6e-06 | N
22-11-18 | 18:38 | 507:80931 | URBAN | Asset Failure | HV | 43 | 62 | 0.001813 | 2.9e-05 | N
22-11-18 | 18:46 | ZN384:PA76 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 449 | 0.000305 | 1e-06 | N
22-11-18 | 19:31 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 149 | 0.001255 | 8e-06 | N
22-11-18 | 19:31 | ZN340:PA40 | URBAN | Asset Failure | LV | 1 | 448 | 0.000305 | 1e-06 | N
22-11-18 | 20:48 | ZN3154:PA3 | URBAN | Asset Failure | LV | 33 | 137 | 0.003074 | 2.2e-05 | N
22-11-18 | 21:12 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 54 | 171 | 0.038981 | 0.000227 | N
23-11-18 | 00:10 | ZN9700:PA23 | URBAN | Other | Other - Self Clearing Trigger | 50 | 105 | 0.00357 | 3.4e-05 | N
23-11-18 | 03:55 | ZN15008:PA10 | URBAN | Other | Other - Self Clearing Trigger | 61 | 205 | 0.008489 | 4.1e-05 | N
23-11-18 | 05:01 | ZN180:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 224 | 0.004111 | 1.8e-05 | N
23-11-18 | 06:16 | ZN36100:PA5 | URBAN | Other | Other - Self Clearing Trigger | 73 | 194 | 0.009631 | 5e-05 | N
23-11-18 | 06:37 | 264:81240 | SHORT RURAL | Asset Failure | HV | 1 | 333 | 0.001402 | 4e-06 | N
23-11-18 | 07:01 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,456 | 64 | 0.39244 | 0.006132 | N
23-11-18 | 07:13 | ZN9118:PA21 | URBAN | Third Party | Other | 25 | 62 | 0.001049 | 1.7e-05 | N
23-11-18 | 07:45 | ZN3922:PA26 | URBAN | Asset Failure | LV | 17 | 125 | 0.001445 | 1.2e-05 | N
23-11-18 | 08:10 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 140 | 0.00059 | 4e-06 | N
23-11-18 | 08:23 | ZN9252:PA30 | URBAN | Other | Other - Self Clearing Trigger | 35 | 120 | 0.00286 | 2.4e-05 | N
23-11-18 | 08:23 | ZN9118:PA21 | URBAN | Third Party | Other | 1 | 8 | 5e-06 | 1e-06 | N
23-11-18 | 09:02 | ZN15005:PA2 | URBAN | Weather |  | 1 | 327 | 0.000223 | 1e-06 | N
23-11-18 | 09:06 | ZN1287:PA6 | URBAN | Other | Other - Arcing | 1 | 143 | 9.7e-05 | 1e-06 | N
23-11-18 | 09:25 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 372 | 223 | 0.34986 | 0.001567 | N
23-11-18 | 09:57 | ZN12570:PA34 | SHORT RURAL | Other | Other | 1 | 71 | 0.0003 | 4e-06 | N
23-11-18 | 10:02 | ZN847:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 238 | 0.000162 | 1e-06 | N
23-11-18 | 12:15 | 511:29878 | SHORT RURAL | Asset Failure | HV | 1,058 | 3 | 0.013367 | 0.004456 | N
23-11-18 | 10:45 | 228:7487 | URBAN | Weather |  | 1 | 704 | 0.000479 | 1e-06 | N
23-11-18 | 10:49 | 206:34434 | URBAN | Other | Other | 1 | 160 | 0.000109 | 1e-06 | N
23-11-18 | 10:51 | 511:29873 | URBAN | Other | Other | 1 | 259 | 0.000176 | 1e-06 | N
23-11-18 | 10:45 | ZN15006:PA16 | URBAN | Asset Failure | LV | 31 | 15 | 0.000316 | 2.1e-05 | N
23-11-18 | 10:54 | ZN12630:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,438 | 0.006054 | 4e-06 | N
23-11-18 | 11:08 | 525:34580 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 95 | 0.0008 | 8e-06 | N
23-11-18 | 11:08 | 525:34586 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 95 | 0.0008 | 8e-06 | N
23-11-18 | 11:08 | 525:34589 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 95 | 6.5e-05 | 1e-06 | N
23-11-18 | 11:11 | 257:81985 | URBAN | Other | Other - Self Clearing Trigger | 993 | 73 | 0.049402 | 0.000675 | N
23-11-18 | 11:12 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 372 | 0.009109 | 2.4e-05 | N
23-11-18 | 11:20 | 257:81988 | URBAN | Weather |  | 1 | 169 | 0.000115 | 1e-06 | N
23-11-18 | 11:21 | 238:34150 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 458 | 0.001929 | 4e-06 | N
23-11-18 | 11:21 | ZN3154:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 323 | 93 | 0.020427 | 0.00022 | N
23-11-18 | 11:25 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 25 | 1,630 | 0.17162 | 0.000105 | N
23-11-18 | 11:25 | ZN847:PA18 | SHORT RURAL | Asset Failure | HV | 968 | 178 | 0.72721 | 0.004077 | N
23-11-18 | 11:35 | ZN3154:PA18 | URBAN | Weather |  | 30 | 784 | 0.015999 | 2e-05 | N
23-11-18 | 12:45 | ZN195:PA10 | URBAN | Asset Failure | LV | 13 | 80 | 0.000707 | 9e-06 | N
23-11-18 | 11:43 | 532:83309 | URBAN | Other | Other | 1 | 519 | 0.000353 | 1e-06 | N
23-11-18 | 11:44 | 238:34137 | SHORT RURAL | Asset Failure | HV | 804 | 120 | 0.407 | 0.003386 | N
23-11-18 | 11:49 | 240:34846 | URBAN | Asset Failure | HV | 8 | 91 | 0.000495 | 5e-06 | N
23-11-18 | 11:52 | ZN14892:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,697 | 0.001154 | 1e-06 | N
23-11-18 | 11:40 | ZN14143:PA17 | SHORT RURAL | Asset Failure | HV | 408 | 616 | 1.0585 | 0.001718 | N
23-11-18 | 11:57 | ZN12640:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,503 | 0.001022 | 1e-06 | N
23-11-18 | 12:03 | ZN9550:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 124 | 66 | 0.005584 | 8.4e-05 | N
23-11-18 | 12:05 | ZN965:PA42 | URBAN | Other | Other | 1 | 44 | 3e-05 | 1e-06 | N
23-11-18 | 12:13 | 507:80922 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 70 | 121 | 0.035686 | 0.000295 | N
23-11-18 | 12:16 | ZN15008:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 863 | 0.035815 | 4.1e-05 | N
23-11-18 | 12:27 | ZN2400:PA11 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 676 | 162 | 0.46083 | 0.002847 | N
23-11-18 | 12:27 | 270:83591 | SHORT RURAL | Other | Other | 1 | 39 | 0.000165 | 4e-06 | N
23-11-18 | 12:41 | ZN1673:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 1,189 | 0.019404 | 1.6e-05 | N
23-11-18 | 12:41 | 270:83590 | URBAN | Other | Other | 1 | 112 | 7.6e-05 | 1e-06 | N
23-11-18 | 12:44 | ZN10993:PA22 | URBAN | Asset Failure | LV | 79 | 95 | 0.00511 | 5.4e-05 | N
23-11-18 | 12:45 | 508:82579 | SHORT RURAL | Vegetation | Vegetation Grow In | 1 | 825 | 0.003473 | 4e-06 | N
23-11-18 | 20:30 | ZN36200:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 30 | 90 | 0.011371 | 0.000126 | N
23-11-18 | 12:41 | ZN15011:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 16 | 57 | 0.00062 | 1.1e-05 | N
23-11-18 | 13:27 | ZN965:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 85 | 318 | 0.018381 | 5.8e-05 | N
23-11-18 | 12:56 | ZN3154:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 74 | 0.002301 | 3.1e-05 | N
23-11-18 | 13:09 | ZN2400:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 961 | 58 | 0.037904 | 0.000654 | N
23-11-18 | 13:23 | ZN1648:PA19 | URBAN | Asset Failure | LV | 48 | 261 | 0.008522 | 3.3e-05 | N
23-11-18 | 13:28 | ZN3922:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 187 | 506 | 0.064346 | 0.000127 | N
23-11-18 | 13:46 | ZN1287:PA3 | URBAN | Other | Other - Self Clearing Trigger | 1,555 | 102 | 0.10786 | 0.001057 | N
23-11-18 | 13:48 | ZN12630:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 95 | 112 | 0.044642 | 0.0004 | N
23-11-18 | 17:50 | ZN12660:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 25 | 25 | 0.000425 | 1.7e-05 | N
23-11-18 | 13:52 | ZN35370:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 90 | 133 | 0.050454 | 0.000379 | N
23-11-18 | 14:00 | ZN15014:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 28 | 0.000724 | 2.6e-05 | N
23-11-18 | 13:50 | ZN3425:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 60 | 0.001714 | 2.9e-05 | N
23-11-18 | 14:04 | 228:7491 | URBAN | Weather |  | 1 | 179 | 0.000122 | 1e-06 | N
23-11-18 | 14:10 | 528:83019 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 514 | 0.002166 | 4e-06 | N
23-11-18 | 14:16 | ZN3154:PA19 | URBAN | Other | Other - Self Clearing Trigger | 86 | 539 | 0.031522 | 5.8e-05 | N
23-11-18 | 14:50 | ZN4545:PA36 | URBAN | Weather |  | 59 | 1,189 | 0.047716 | 4e-05 | N
23-11-18 | 14:33 | 507:80925 | SHORT RURAL | Other | Other | 1 | 267 | 0.001123 | 4e-06 | N
23-11-18 | 14:37 | 528:83019 | SHORT RURAL | Asset Failure | HV | 522 | 37 | 0.081341 | 0.002198 | N
23-11-18 | 14:40 | ZN9700:PA17 | URBAN | Weather |  | 33 | 164 | 0.003684 | 2.2e-05 | N
23-11-18 | 14:39 | ZN15005:PA10 | URBAN | Weather |  | 40 | 220 | 0.005992 | 2.7e-05 | N
23-11-18 | 14:44 | ZN187:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 615 | 0.007529 | 1.2e-05 | N
23-11-18 | 14:49 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 41 | 1,310 | 0.22618 | 0.000173 | N
23-11-18 | 14:49 | 528:83011 | SHORT RURAL | Other | Other | 1 | 266 | 0.001118 | 4e-06 | N
23-11-18 | 14:51 | ZN262:PA19 | URBAN | Asset Failure | LV | 1 | 232 | 0.000158 | 1e-06 | N
23-11-18 | 14:53 | ZN847:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 62 | 961 | 0.040499 | 4.2e-05 | N
23-11-18 | 14:55 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 1,495 | 0.034565 | 2.3e-05 | N
23-11-18 | 14:53 | ZN14891:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 913 | 73 | 0.045618 | 0.000621 | N
23-11-18 | 14:56 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 574 | 0.002417 | 4e-06 | N
23-11-18 | 14:58 | 224:80337 | URBAN | Other | Other | 1 | 61 | 4.2e-05 | 1e-06 | N
23-11-18 | 15:03 | 224:80337 | URBAN | Other | Other | 1 | 56 | 3.8e-05 | 1e-06 | N
23-11-18 | 15:02 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 150 | 141 | 0.088778 | 0.000632 | N
23-11-18 | 14:44 | ZN12690:PA24 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 4 | 86 | 0.001449 | 1.7e-05 | N
24-11-18 | 08:31 | ZN4545:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 505 | 0.000343 | 1e-06 | N
23-11-18 | 15:07 | 532:83293 | URBAN | Asset Failure | HV | 1 | 313 | 0.000213 | 1e-06 | N
23-11-18 | 15:18 | ZN195:PA22 | URBAN | Other | Other | 11 | 852 | 0.00637 | 7e-06 | N
23-11-18 | 15:18 | ZN9900:PA2 | URBAN | Asset Failure | LV | 30 | 1,060 | 0.021626 | 2e-05 | N
23-11-18 | 15:23 | ZN847:PA10 | URBAN | Other | Other | 19 | 667 | 0.008615 | 1.3e-05 | N
23-11-18 | 15:25 | ZN965:PA42 | URBAN | Asset Failure | LV | 6 | 2,735 | 0.011159 | 4e-06 | N
23-11-18 | 15:30 | ZN195:PA29 | URBAN | Asset Failure | LV | 35 | 1,094 | 0.02604 | 2.4e-05 | N
23-11-18 | 15:40 | 801:74121 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 45 | 0.015839 | 0.000352 | N
23-11-18 | 15:41 | ZN4545:PA39 | URBAN | Other | Other - Self Clearing Trigger | 51 | 479 | 0.016612 | 3.5e-05 | N
23-11-18 | 15:43 | ZN9252:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 73 | 166 | 0.008256 | 5e-05 | N
23-11-18 | 15:44 | 258:80787 | URBAN | Other | Other | 1 | 217 | 0.000148 | 1e-06 | N
23-11-18 | 15:44 | ZN3154:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 465 | 0.015812 | 3.4e-05 | N
23-11-18 | 15:49 | ZN15005:PA12 | URBAN | Other | Other - Self Clearing Trigger | 20 | 580 | 0.007889 | 1.4e-05 | N
23-11-18 | 15:51 | 502:48004 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 20 | 1.4e-05 | 1e-06 | N
23-11-18 | 16:02 | ZN3425:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,167 | 0.000794 | 1e-06 | N
23-11-18 | 16:00 | ZN35500:PA28 | URBAN | Other | Other - Self Clearing Trigger | 137 | 559 | 0.052108 | 9.3e-05 | N
23-11-18 | 15:54 | ZN14891:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 54 | 296 | 0.067401 | 0.000227 | N
23-11-18 | 17:04 | ZN9245:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 166 | 0.004737 | 2.9e-05 | N
23-11-18 | 16:11 | ZN15013:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 209 | 574 | 0.50537 | 0.00088 | N
23-11-18 | 16:14 | 243:80081 | SHORT RURAL | Other | Other - Self Clearing Trigger | 61 | 170 | 0.043742 | 0.000257 | N
23-11-18 | 17:50 | 513:48059 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 65 | 86 | 0.023542 | 0.000274 | N
23-11-18 | 16:27 | 270:83591 | SHORT RURAL | Other | Other | 1 | 108 | 0.000453 | 4e-06 | N
23-11-18 | 16:28 | ZN3154:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 301 | 0.006348 | 2.1e-05 | N
23-11-18 | 16:30 | 239:82133 | URBAN | Other | Other | 1 | 195 | 0.000132 | 1e-06 | N
23-11-18 | 17:32 | ZN3425:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 1,263 | 0.036073 | 2.9e-05 | N
23-11-18 | 16:39 | ZN1673:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 13 | 1,469 | 0.012982 | 9e-06 | N
23-11-18 | 16:34 | ZN847:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 1,450 | 0.046352 | 3.2e-05 | N
23-11-18 | 16:37 | ZN9700:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 21 | 182 | 0.002605 | 1.4e-05 | N
23-11-18 | 16:35 | ZN12580:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,626 | 136 | 0.15 | 0.001106 | N
23-11-18 | 16:40 | ZN2400:PA18 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 37 | 2,866 | 0.44667 | 0.000156 | N
23-11-18 | 16:44 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 465 | 0.00196 | 4e-06 | N
23-11-18 | 16:45 | 258:80775 | URBAN | Weather |  | 1 | 78 | 5.3e-05 | 1e-06 | N
23-11-18 | 17:41 | ZN1673:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 968 | 0.019093 | 2e-05 | N
23-11-18 | 17:40 | ZN35370:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 17 | 50 | 0.00358 | 7.2e-05 | N
23-11-18 | 17:29 | ZN2635:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 531 | 0.010101 | 1.9e-05 | N
23-11-18 | 17:30 | 270:83590 | URBAN | Weather |  | 1 | 364 | 0.000248 | 1e-06 | N
23-11-18 | 17:38 | 229:34983 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 442 | 0.00186 | 4e-06 | N
23-11-18 | 17:39 | 216:10727 | URBAN | Third Party | Other | 1 | 65 | 4.4e-05 | 1e-06 | N
23-11-18 | 17:54 | 202:34260 | URBAN | Other | Other | 1 | 961 | 0.000653 | 1e-06 | N
23-11-18 | 18:05 | 243:80081 | SHORT RURAL | Weather |  | 1 | 326 | 0.001373 | 4e-06 | N
23-11-18 | 18:17 | ZN15010:PA28 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 4,195 | 0.017667 | 4e-06 | N
23-11-18 | 18:21 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 174 | 0.000731 | 4e-06 | N
23-11-18 | 18:26 | 228:7487 | URBAN | Weather |  | 1 | 243 | 0.000165 | 1e-06 | N
23-11-18 | 18:44 | ZN15013:PA8 | URBAN | Other | Other - Arcing | 102 | 15 | 0.00104 | 6.9e-05 | N
23-11-18 | 18:54 | ZN15002:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 309 | 0.00021 | 1e-06 | N
24-11-18 | 11:20 | ZN180:PA34 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 25 | 0.000799 | 3.2e-05 | N
23-11-18 | 18:59 | ZN12640:PA5 | URBAN | Other | Other | 1 | 96 | 6.5e-05 | 1e-06 | N
23-11-18 | 18:11 | ZN12640:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,308 | 0.00089 | 1e-06 | N
23-11-18 | 19:26 | ZN12630:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,444 | 0.006081 | 4e-06 | N
23-11-18 | 18:01 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 56 | 188 | 0.007166 | 3.8e-05 | N
23-11-18 | 15:41 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 349 | 0.006638 | 1.9e-05 | N
23-11-18 | 20:21 | ZN2400:PA15 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 364 | 0.001534 | 4e-06 | N
23-11-18 | 20:23 | ZN15013:PA10 | SHORT RURAL | Asset Failure | HV | 41 | 34 | 0.005871 | 0.000173 | N
23-11-18 | 20:23 | ZN15013:PA4 | SHORT RURAL | Asset Failure | HV | 876 | 34 | 0.12543 | 0.003689 | N
23-11-18 | 20:30 | ZN14891:PA20 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 200 | 0.009265 | 4.6e-05 | N
23-11-18 | 19:34 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 122 | 840 | 0.43184 | 0.000514 | N
23-11-18 | 20:38 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 2,298 | 0.009678 | 4e-06 | N
23-11-18 | 21:39 | ZN15014:PA14 | URBAN | Network business | Network error | 10 | 1,266 | 0.008609 | 7e-06 | N
23-11-18 | 23:30 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 47 | 0.001151 | 2.4e-05 | N
24-11-18 | 01:52 | 221:11900 | URBAN | Vegetation | Vegetation Blow/Fall In | 77 | 53 | 0.002775 | 5.2e-05 | N
24-11-18 | 03:19 | ZN3922:PA26 | URBAN | Asset Failure | LV | 17 | 566 | 0.006538 | 1.2e-05 | N
24-11-18 | 07:01 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 789 | 0.003322 | 4e-06 | N
24-11-18 | 07:44 | ZN847:PA15 | URBAN | Asset Failure | LV | 18 | 465 | 0.005696 | 1.2e-05 | N
23-11-18 | 17:47 | ZN2635:PA59 | URBAN | Other | Other - Self Clearing Trigger | 8 | 1,152 | 0.006269 | 5e-06 | N
24-11-18 | 07:57 | ZN14143:PA17 | SHORT RURAL | Other | Other - Self Clearing Trigger | 17 | 283 | 0.020262 | 7.2e-05 | N
24-11-18 | 08:47 | ZN12570:PA24 | SHORT RURAL | Other | Other | 1 | 92 | 0.000389 | 4e-06 | N
25-11-18 | 11:05 | ZN9900:PA2 | URBAN | Network business | Network error | 38 | 104 | 0.002689 | 2.6e-05 | N
24-11-18 | 09:05 | ZN14891:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 235 | 0.001979 | 8e-06 | N
24-11-18 | 09:06 | ZN15011:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 283 | 0.000192 | 1e-06 | N
24-11-18 | 09:08 | ZN35555:PA20 | URBAN | Third Party | Other | 1 | 54 | 3.7e-05 | 1e-06 | N
24-11-18 | 09:13 | ZN9118:PA22 | URBAN | Other | Other - Arcing | 1 | 706 | 0.00048 | 1e-06 | N
24-11-18 | 09:29 | 532:83293 | URBAN | Other | Other | 1 | 137 | 9.3e-05 | 1e-06 | N
24-11-18 | 09:53 | ZN12690:PA6 | URBAN | Asset Failure | Distribution substation | 37 | 66 | 0.001667 | 2.5e-05 | N
24-11-18 | 09:54 | ZN12690:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 66 | 0.000804 | 1.2e-05 | N
24-11-18 | 10:14 | ZN195:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 16 | 0.000381 | 2.4e-05 | N
24-11-18 | 11:58 | ZN12650:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 72 | 0.002097 | 2.9e-05 | N
24-11-18 | 12:57 | ZN965:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 74 | 302 | 0.015206 | 5e-05 | N
24-11-18 | 13:59 | 528:83020 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 76 | 0.00032 | 4e-06 | N
24-11-18 | 14:39 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 2 | 245 | 0.17271 | 0.000704 | N
24-11-18 | 15:06 | ZN1193:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 54 | 0.000986 | 1.8e-05 | N
24-11-18 | 17:37 | 240:34849 | URBAN | Other | Other | 1 | 23 | 1.5e-05 | 1e-06 | N
24-11-18 | 17:56 | ZN12650:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 55 | 3.8e-05 | 1e-06 | N
24-11-18 | 21:03 | 202:34253 | URBAN | Animal | Animal impact | 105 | 64 | 0.004585 | 7.1e-05 | N
24-11-18 | 23:47 | ZN2568:PA14 | URBAN | Third Party | Fire | 4 | 120 | 0.000326 | 3e-06 | N
24-11-18 | 23:47 | ZN2568:PA29 | URBAN | Third Party | Fire | 34 | 120 | 0.002775 | 2.3e-05 | N
25-11-18 | 07:56 | 513:48056 | SHORT RURAL | Other | Other | 1 | 54 | 0.000227 | 4e-06 | N
25-11-18 | 08:49 | 512:83732 | SHORT RURAL | Asset Failure | LV | 1 | 251 | 0.001056 | 4e-06 | N
25-11-18 | 09:20 | 814:82285 | SHORT RURAL | Asset Failure | HV | 1 | 145 | 0.000611 | 4e-06 | N
25-11-18 | 09:34 | ZN847:PA10 | URBAN | Asset Failure | LV | 13 | 332 | 0.002932 | 9e-06 | N
25-11-18 | 10:14 | ZN36300:PA7 | URBAN | Network business | Switching and protection error | 1 | 1,426 | 0.00097 | 1e-06 | N
25-11-18 | 21:06 | ZN10994:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 194 | 0.005673 | 2.9e-05 | N
25-11-18 | 23:03 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 532 | 0.000362 | 1e-06 | N
26-11-18 | 03:12 | ZN116:PA7 | SHORT RURAL | Asset Failure | HV | 1 | 138 | 0.000581 | 4e-06 | N
26-11-18 | 05:48 | 801:74121 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 2 | 167 | 0.11756 | 0.000704 | N
26-11-18 | 10:50 | ZN15001:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 20 | 0.000321 | 1.6e-05 | N
26-11-18 | 07:15 | ZN36800:PA57 | URBAN | Asset Failure | LV | 1 | 405 | 0.000275 | 1e-06 | N
26-11-18 | 07:43 | ZN36800:PA57 | URBAN | Asset Failure | LV | 1 | 376 | 0.000255 | 1e-06 | N
26-11-18 | 07:47 | ZN847:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 78 | 0.001956 | 2.5e-05 | N
26-11-18 | 08:07 | ZN15012:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 892 | 0.000606 | 1e-06 | N
26-11-18 | 08:28 | ZN36800:PA49 | URBAN | Asset Failure | LV | 2 | 331 | 0.00045 | 1e-06 | N
26-11-18 | 08:50 | ZN36800:PA49 | URBAN | Asset Failure | LV | 1 | 310 | 0.00021 | 1e-06 | N
26-11-18 | 09:45 | ZN12630:PA10 | SHORT RURAL | Other | Other | 1 | 174 | 0.000732 | 4e-06 | N
26-11-18 | 10:55 | 507:80925 | SHORT RURAL | Asset Failure | LV | 1 | 665 | 0.002801 | 4e-06 | N
26-11-18 | 11:59 | 526:34640 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 466 | 0.001962 | 4e-06 | N
26-11-18 | 14:35 | 507:80914 | SHORT RURAL | Other | Other | 1 | 76 | 0.000322 | 4e-06 | N
26-11-18 | 14:40 | ZN1673:PA6 | URBAN | Asset Failure | LV | 2 | 453 | 0.000615 | 1e-06 | N
26-11-18 | 15:13 | ZN35500:PA19 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 347 | 0.00146 | 4e-06 | N
26-11-18 | 17:27 | 216:10728 | URBAN | Other | Other | 1 | 32 | 2.1e-05 | 1e-06 | N
26-11-18 | 18:30 | 509:33395 | LONG RURAL | Asset Failure | HV | 41 | 60 | 0.86589 | 0.014432 | N
26-11-18 | 18:22 | 214:8665 | URBAN | Other | Other - Self Clearing Trigger | 77 | 53 | 0.00277 | 5.2e-05 | N
26-11-18 | 18:24 | 526:34640 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 81 | 0.000341 | 4e-06 | N
26-11-18 | 18:35 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 74 | 0.000312 | 4e-06 | N
26-11-18 | 18:58 | 220:8688 | URBAN | Other | Other | 1 | 141 | 9.6e-05 | 1e-06 | N
26-11-18 | 20:13 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 17 | 66 | 0.000764 | 1.2e-05 | N
26-11-18 | 23:40 | ZN167:PA10 | URBAN | Third Party | Vehicle impact | 69 | 21 | 0.000983 | 4.7e-05 | N
21-11-18 | 03:01 | ZN14891:PA12 | SHORT RURAL | Weather |  | 3 | 609 | 0.007694 | 1.3e-05 | N
27-11-18 | 06:56 | ZN35500:PA22 | URBAN | Other | Other | 1 | 70 | 4.7e-05 | 1e-06 | N
27-11-18 | 10:26 | ZN167:PA20 | URBAN | Third Party | Vehicle impact | 1 | 233 | 0.000158 | 1e-06 | N
27-11-18 | 10:41 | ZN167:PA20 | URBAN | Other | Other | 1 | 118 | 8e-05 | 1e-06 | N
23-11-18 | 16:02 | ZN36100:PA5 | URBAN | Weather |  | 73 | 208 | 0.010326 | 5e-05 | N
27-11-18 | 12:02 | ZN167:PA20 | URBAN | Third Party | Vehicle impact | 5 | 497 | 0.001688 | 3e-06 | N
27-11-18 | 10:56 | ZN35800:PA2 | URBAN | Other | Other | 1 | 1,385 | 0.00094 | 1e-06 | N
27-11-18 | 12:24 | 801:74121 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 3 | 116 | 0.12249 | 0.001056 | N
27-11-18 | 12:50 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 43 | 2.9e-05 | 1e-06 | N
27-11-18 | 13:12 | 224:80340 | SHORT RURAL | Other | Other | 1 | 43 | 0.000183 | 4e-06 | N
27-11-18 | 14:41 | ZN14892:PA17 | URBAN | Asset Failure | LV | 26 | 566 | 0.009988 | 1.8e-05 | N
27-11-18 | 15:19 | ZN1193:PA11 | URBAN | Third Party | Other | 1 | 258 | 0.000175 | 1e-06 | N
27-11-18 | 15:47 | ZN2400:PA11 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 972 | 0.004095 | 4e-06 | N
27-11-18 | 16:59 | 221:11899 | SHORT RURAL | Asset Failure | LV | 1 | 150 | 0.000632 | 4e-06 | N
27-11-18 | 22:32 | ZN129:PA38 | URBAN | Asset Failure | HV | 1,216 | 101 | 0.083707 | 0.000825 | N
27-11-18 | 22:32 | ZN129:PA46 | URBAN | Asset Failure | HV | 13 | 60 | 0.000529 | 9e-06 | N
28-11-18 | 02:21 | 214:8669 | URBAN | Animal | Animal impact | 107 | 39 | 0.002807 | 7.3e-05 | N
28-11-18 | 04:51 | ZN12640:PA7 | URBAN | Other | Other - Arcing | 1 | 323 | 0.000219 | 1e-06 | N
28-11-18 | 05:16 | ZN35500:PA23 | URBAN | Asset Failure | HV | 1 | 334 | 0.000227 | 1e-06 | N
28-11-18 | 05:16 | ZN35500:PA28 | URBAN | Asset Failure | HV | 4,699 | 180 | 0.57331 | 0.003189 | N
28-11-18 | 05:34 | ZN3154:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 952 | 198 | 0.12768 | 0.000646 | N
28-11-18 | 05:39 | 270:83584 | URBAN | Third Party | Unauthorised access | 25 | 123 | 0.002091 | 1.7e-05 | N
28-11-18 | 05:46 | ZN15008:PA7 | URBAN | Other | Other - Arcing | 1 | 253 | 0.000172 | 1e-06 | N
28-11-18 | 05:51 | ZN35800:PA13 | URBAN | Weather |  | 11 | 99 | 0.000739 | 7e-06 | N
28-11-18 | 05:52 | ZN2835:PA27 | URBAN | Other | Other - Arcing | 1 | 297 | 0.000202 | 1e-06 | N
28-11-18 | 06:01 | ZN167:PA20 | URBAN | Other | Other | 1 | 201 | 0.000136 | 1e-06 | N
28-11-18 | 06:40 | ZN14892:PA6 | URBAN | Weather |  | 1,709 | 108 | 0.12543 | 0.00116 | N
28-11-18 | 07:48 | ZN3425:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 271 | 0.007366 | 2.7e-05 | N
28-11-18 | 06:46 | ZN3425:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 373 | 0.008107 | 2.2e-05 | N
28-11-18 | 06:46 | ZN3425:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 374 | 0.000254 | 1e-06 | N
28-11-18 | 06:33 | ZN4990:PA51 52ABC | CBD | Other | Other | 1,593 | 228 | 11.9524 | 0.052358 | N
28-11-18 | 07:06 | ZN3288:PA41 42DEF | CBD | Other | Other | 1 | 334 | 0.010978 | 3.3e-05 | N
28-11-18 | 07:08 | 214:8669 | URBAN | Other | Other | 1 | 83 | 5.6e-05 | 1e-06 | N
28-11-18 | 07:20 | ZN180:PA22 | URBAN | Other | Other - Self Clearing Trigger | 86 | 115 | 0.006713 | 5.8e-05 | N
28-11-18 | 07:24 | ZN3425:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 48 | 1,006 | 0.032775 | 3.3e-05 | N
28-11-18 | 07:39 | ZN9700:PA24 | URBAN | Asset Failure | Distribution substation | 1 | 395 | 0.000268 | 1e-06 | N
28-11-18 | 07:45 | ZN12690:PA12 | SHORT RURAL | Asset Failure | HV | 1 | 750 | 0.003159 | 4e-06 | N
28-11-18 | 07:46 | ZN3672:PA46 | URBAN | Other | Other - Arcing | 1 | 103 | 7e-05 | 1e-06 | N
28-11-18 | 08:19 | 270:83584 | URBAN | Other | Other | 1 | 34 | 2.3e-05 | 1e-06 | N
28-11-18 | 08:32 | ZN847:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 455 | 0.000309 | 1e-06 | N
28-11-18 | 08:54 | 257:81985 | URBAN | Other | Other | 1 | 76 | 5.2e-05 | 1e-06 | N
28-11-18 | 08:54 | ZN180:PA32 | URBAN | Asset Failure | HV | 62 | 523 | 0.02201 | 4.2e-05 | N
28-11-18 | 09:00 | ZN3425:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 51 | 495 | 0.017135 | 3.5e-05 | N
28-11-18 | 09:13 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 147 | 0.000619 | 4e-06 | N
28-11-18 | 07:09 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 359 | 0.01512 | 4.2e-05 | N
28-11-18 | 10:01 | ZN8700:PA63 64ABC | CBD | Other | Other | 26 | 1,338 | 1.1438 | 0.000855 | N
28-11-18 | 10:05 | ZN2196:PA3 | URBAN | Third Party | Vehicle impact | 1 | 60 | 4.1e-05 | 1e-06 | N
28-11-18 | 10:05 | ZN2196:PA5 | URBAN | Third Party | Vehicle impact | 1,616 | 70 | 0.076644 | 0.001097 | N
28-11-18 | 10:28 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 87 | 0.001762 | 2e-05 | N
28-11-18 | 10:41 | ZN3154:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 124 | 0.002603 | 2.1e-05 | N
28-11-18 | 11:02 | 233:82815 | SHORT RURAL | Asset Failure | HV | 1,334 | 132 | 0.74175 | 0.005618 | N
28-11-18 | 09:42 | ZN35370:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,149 | 108 | 0.52209 | 0.004839 | N
28-11-18 | 09:42 | ZN35370:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 278 | 224 | 0.26268 | 0.001171 | N
28-11-18 | 11:22 | 232:11457 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,412 | 76 | 0.45332 | 0.005947 | N
28-11-18 | 11:08 | ZN14144:PA7 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,038 | 83 | 0.36113 | 0.004372 | N
28-11-18 | 11:38 | ZN35500:PA35 | URBAN | Other | Other - Self Clearing Trigger | 8 | 102 | 0.000554 | 5e-06 | N
28-11-18 | 11:40 | ZN1673:PA7 | URBAN | Weather |  | 47 | 109 | 0.003485 | 3.2e-05 | N
28-11-18 | 11:46 | ZN2196:PA5 | URBAN | Other | Other - Arcing | 1 | 164 | 0.000111 | 1e-06 | N
28-11-18 | 11:48 | 814:82289 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 72 | 0.002123 | 2.9e-05 | N
28-11-18 | 11:07 | ZN8700:PA63 64ABC | CBD | Asset Failure | Distribution substation | 101 | 648 | 2.1511 | 0.00332 | N
28-11-18 | 11:57 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,090 | 51 | 0.23239 | 0.004591 | N
28-11-18 | 12:09 | ZN12570:PA33 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 170 | 0.000717 | 4e-06 | N
28-11-18 | 12:15 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 152 | 0.000103 | 1e-06 | N
28-11-18 | 12:19 | ZN12580:PA4 | URBAN | Other | Other - Arcing | 1 | 49 | 3.3e-05 | 1e-06 | N
28-11-18 | 12:21 | ZN965:PA42 | URBAN | Other | Other - Self Clearing Trigger | 11 | 1,369 | 0.010221 | 7e-06 | N
28-11-18 | 14:02 | 232:33407 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 8 | 128 | 0.004313 | 3.4e-05 | N
29-11-18 | 12:33 | ZN35370:PA10 | SHORT RURAL | Asset Failure | HV | 6 | 217 | 0.005484 | 2.5e-05 | N
28-11-18 | 12:35 | 270:83591 | SHORT RURAL | Other | Other | 1 | 60 | 0.000254 | 4e-06 | N
28-11-18 | 12:40 | ZN1193:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 75 | 61 | 0.003098 | 5.1e-05 | N
28-11-18 | 12:50 | 512:83743 | SHORT RURAL | Weather |  | 1 | 415 | 0.001748 | 4e-06 | N
28-11-18 | 13:23 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 18 | 223 | 0.01688 | 7.6e-05 | N
28-11-18 | 13:34 | ZN931:PA26 | URBAN | Other | Other - Self Clearing Trigger | 81 | 165 | 0.009072 | 5.5e-05 | N
28-11-18 | 13:43 | ZN36800:PA42 | URBAN | Other | Other - Self Clearing Trigger | 1 | 67 | 4.5e-05 | 1e-06 | N
28-11-18 | 13:43 | ZN36800:PA58 | URBAN | Other | Other - Self Clearing Trigger | 152 | 67 | 0.006881 | 0.000103 | N
28-11-18 | 13:58 | 205:12203 | URBAN | Other | Other | 1 | 1,197 | 0.000812 | 1e-06 | N
28-11-18 | 13:51 | ZN180:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 124 | 0.003872 | 3.1e-05 | N
28-11-18 | 14:30 | ZN36100:PA6 | URBAN | Asset Failure | LV | 1 | 299 | 0.000203 | 1e-06 | N
28-11-18 | 14:46 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 13 | 174 | 0.009527 | 5.5e-05 | N
28-11-18 | 14:43 | 224:80340 | SHORT RURAL | Asset Failure | LV | 77 | 87 | 0.028214 | 0.000324 | N
28-11-18 | 14:46 | ZN35400:PA101 | URBAN | Other | Other - Self Clearing Trigger | 92 | 158 | 0.009874 | 6.2e-05 | N
28-11-18 | 14:57 | ZN15006:PA6 | URBAN | Other | Other | 17 | 279 | 0.003221 | 1.2e-05 | N
28-11-18 | 14:58 | ZN195:PA30 | SHORT RURAL | Asset Failure | LV | 36 | 77 | 0.011604 | 0.000152 | N
28-11-18 | 15:01 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 119 | 0.004511 | 3.8e-05 | N
28-11-18 | 15:02 | ZN3472:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 173 | 0.00715 | 4.1e-05 | N
28-11-18 | 15:06 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 24 | 0.000101 | 4e-06 | N
28-11-18 | 15:08 | ZN35400:PA101 | URBAN | Other | Other - Self Clearing Trigger | 52 | 396 | 0.013963 | 3.5e-05 | N
28-11-18 | 15:48 | ZN180:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 172 | 0.003035 | 1.8e-05 | N
28-11-18 | 15:22 | ZN2568:PA32 | URBAN | Weather |  | 80 | 63 | 0.003431 | 5.4e-05 | N
28-11-18 | 15:25 | 507:80932 | SHORT RURAL | Other | Other - Self Clearing Trigger | 41 | 105 | 0.018117 | 0.000173 | N
28-11-18 | 13:23 | ZN3425:PA44 | URBAN | Asset Failure | LV | 1 | 242 | 0.000164 | 1e-06 | N
28-11-18 | 15:25 | ZN9118:PA12 | URBAN | Weather |  | 44 | 84 | 0.002519 | 3e-05 | N
28-11-18 | 15:29 | ZN195:PA30 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 21 | 670 | 0.059274 | 8.8e-05 | N
28-11-18 | 15:33 | 513:48056 | SHORT RURAL | Asset Failure | HV | 8 | 297 | 0.010007 | 3.4e-05 | N
28-11-18 | 15:36 | ZN9245:PA1 | URBAN | Weather |  | 38 | 113 | 0.002916 | 2.6e-05 | N
28-11-18 | 14:05 | ZN2602:PA4 | URBAN | Weather |  | 53 | 190 | 0.006835 | 3.6e-05 | N
28-11-18 | 15:58 | ZN9700:PA24 | URBAN | Asset Failure | Distribution substation | 1 | 1,567 | 0.001064 | 1e-06 | N
28-11-18 | 15:58 | ZN10994:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 447 | 0.000304 | 1e-06 | N
28-11-18 | 15:59 | 508:82576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 116 | 0.003908 | 3.4e-05 | N
28-11-18 | 16:02 | 508:82580 | SHORT RURAL | Other | Other - Self Clearing Trigger | 15 | 78 | 0.004928 | 6.3e-05 | N
28-11-18 | 16:04 | ZN195:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 11 | 86 | 0.003978 | 4.6e-05 | N
28-11-18 | 16:06 | 512:83743 | SHORT RURAL | Asset Failure | HV | 4 | 434 | 0.007311 | 1.7e-05 | N
28-11-18 | 16:10 | ZN9245:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 270 | 0.007687 | 2.9e-05 | N
28-11-18 | 16:10 | ZN12580:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 14 | 135 | 0.00796 | 5.9e-05 | N
28-11-18 | 16:18 | 513:48059 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 319 | 0.001344 | 4e-06 | N
28-11-18 | 16:25 | ZN10999:PA1 | URBAN | Asset Failure | LV | 1 | 24 | 1.7e-05 | 1e-06 | N
28-11-18 | 16:26 | ZN1193:PA12 | URBAN | Weather |  | 43 | 274 | 0.007992 | 2.9e-05 | N
28-11-18 | 17:18 | 810:74050 | SHORT RURAL | Asset Failure | HV | 46 | 266 | 0.051533 | 0.000194 | N
28-11-18 | 16:45 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 244 | 95 | 0.097423 | 0.001028 | N
28-11-18 | 17:21 | ZN35800:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 183 | 0.007592 | 4.1e-05 | N
28-11-18 | 17:34 | ZN180:PA22 | URBAN | Weather |  | 86 | 81 | 0.004716 | 5.8e-05 | N
28-11-18 | 19:27 | ZN12580:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 20 | 202 | 0.017046 | 8.4e-05 | N
28-11-18 | 17:46 | ZN342:PA17 | URBAN | Weather |  | 52 | 34 | 0.001192 | 3.5e-05 | N
28-11-18 | 17:52 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 68 | 0.000286 | 4e-06 | N
28-11-18 | 18:05 | ZN3425:PA12 | URBAN | Other | Other - Self Clearing Trigger | 21 | 19 | 0.000277 | 1.4e-05 | N
28-11-18 | 18:23 | ZN14144:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 112 | 0.00047 | 4e-06 | N
28-11-18 | 18:20 | ZN3425:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 30 | 0.000814 | 2.7e-05 | N
28-11-18 | 18:41 | ZN12570:PA37 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 36 | 254 | 0.038458 | 0.000152 | N
28-11-18 | 18:41 | ZN36100:PA12 | URBAN | Asset Failure | LV | 1 | 939 | 0.000637 | 1e-06 | N
28-11-18 | 18:42 | 264:81240 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 153 | 0.000644 | 4e-06 | N
28-11-18 | 18:45 | ZN35400:PA101 | URBAN | Asset Failure | LV | 92 | 795 | 0.049643 | 6.2e-05 | N
28-11-18 | 18:52 | ZN2400:PA15 | SHORT RURAL | Asset Failure | LV | 31 | 848 | 0.1107 | 0.000131 | N
28-11-18 | 18:55 | 238:34148 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 140 | 0.001179 | 8e-06 | N
28-11-18 | 18:58 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 896 | 0.003774 | 4e-06 | N
28-11-18 | 19:15 | ZN2635:PA46 | URBAN | Vegetation | Vegetation Blow/Fall In | 548 | 151 | 0.056122 | 0.000372 | N
28-11-18 | 19:18 | 270:83587 | URBAN | Other | Other | 1 | 116 | 7.9e-05 | 1e-06 | N
28-11-18 | 19:45 | 512:83733 | SHORT RURAL | Asset Failure | HV | 2 | 1,395 | 0.01175 | 8e-06 | N
28-11-18 | 19:56 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 143 | 0.000603 | 4e-06 | N
28-11-18 | 19:45 | ZN3154:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 115 | 0.003903 | 3.4e-05 | N
28-11-18 | 20:12 | ZN80:PA25 | URBAN | Asset Failure | LV | 123 | 708 | 0.059108 | 8.3e-05 | N
28-11-18 | 20:14 | ZN965:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,161 | 206 | 0.16203 | 0.000788 | N
28-11-18 | 20:14 | ZN965:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 205 | 0.000139 | 1e-06 | N
28-11-18 | 20:20 | ZN15012:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 49 | 15 | 0.000499 | 3.3e-05 | N
28-11-18 | 20:59 | ZN14891:PA12 | SHORT RURAL | Asset Failure | HV | 710 | 235 | 0.70418 | 0.00299 | N
28-11-18 | 21:52 | ZN2635:PA46 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 68 | 4.6e-05 | 1e-06 | N
28-11-18 | 22:43 | ZN129:PA40 | URBAN | Asset Failure | LV | 1 | 46 | 3.1e-05 | 1e-06 | N
28-11-18 | 22:51 | ZN12600:PA2 | SHORT RURAL | Asset Failure | HV | 98 | 119 | 0.048964 | 0.000413 | N
28-11-18 | 23:03 | ZN2635:PA46 | URBAN | Weather |  | 47 | 212 | 0.006763 | 3.2e-05 | N
29-11-18 | 01:20 | ZN35500:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 59 | 25 | 0.001001 | 4e-05 | N
29-11-18 | 01:25 | ZN1193:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 56 | 35 | 0.00133 | 3.8e-05 | N
29-11-18 | 03:02 | ZN2835:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 608 | 0.000413 | 1e-06 | N
29-11-18 | 03:06 | 261:81870 | URBAN | Animal | Animal impact | 74 | 99 | 0.004973 | 5e-05 | N
29-11-18 | 13:00 | ZN2635:PA46 | URBAN | Asset Failure | LV | 46 | 22 | 0.000687 | 3.1e-05 | N
29-11-18 | 07:12 | ZN36100:PA13 | URBAN | Other | Other - Arcing | 1 | 257 | 0.000175 | 1e-06 | N
29-11-18 | 07:41 | ZN1788:PA17 | URBAN | Other | Other - Arcing | 1 | 738 | 0.000501 | 1e-06 | N
29-11-18 | 07:49 | ZN12620:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 550 | 0.002317 | 4e-06 | N
29-11-18 | 08:23 | ZN12600:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 277 | 0.001167 | 4e-06 | N
29-11-18 | 08:31 | ZN3425:PA35 | URBAN | Network business | Network error | 1,008 | 36 | 0.024736 | 0.000684 | N
28-11-18 | 19:30 | 264:81240 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 20 | 8.4e-05 | 4e-06 | N
29-11-18 | 09:35 | 235:2124 | URBAN | Other | Other | 1 | 43 | 2.9e-05 | 1e-06 | N
28-11-18 | 15:38 | 512:83743 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 272 | 0.002291 | 8e-06 | N
29-11-18 | 10:02 | 511:29877 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 92 | 0.000389 | 4e-06 | N
29-11-18 | 10:16 | ZN1290:PA11 | URBAN | Asset Failure | LV | 1 | 810 | 0.00055 | 1e-06 | N
29-11-18 | 10:12 | ZN12630:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 3 | 10 | 0.000126 | 1.3e-05 | N
29-11-18 | 10:32 | ZN15011:PA4 | URBAN | Other | Other | 1 | 126 | 8.6e-05 | 1e-06 | N
29-11-18 | 11:02 | ZN2568:PA32 | URBAN | Asset Failure | LV | 80 | 78 | 0.004213 | 5.4e-05 | N
29-11-18 | 15:00 | ZN14891:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 235 | 0.001979 | 8e-06 | N
29-11-18 | 11:41 | 526:34639 | SHORT RURAL | Asset Failure | HV | 3 | 398 | 0.005033 | 1.3e-05 | N
29-11-18 | 09:51 | ZN12630:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 329 | 0.008314 | 2.5e-05 | N
28-11-18 | 17:55 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 22 | 15 | 0.000224 | 1.5e-05 | N
29-11-18 | 13:21 | ZN35600:PA9 | URBAN | Asset Failure | LV | 1 | 368 | 0.00025 | 1e-06 | N
29-11-18 | 13:24 | 509:33399 | SHORT RURAL | Other | Other | 1 | 146 | 0.000616 | 4e-06 | N
28-11-18 | 13:25 | ZN180:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 125 | 0.00297 | 2.4e-05 | N
24-11-18 | 14:30 | ZN14891:PA12 | SHORT RURAL | Asset Failure | LV | 10 | 200 | 0.008423 | 4.2e-05 | N
22-11-18 | 23:20 | ZN3922:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 129 | 33 | 0.017928 | 0.000543 | N
29-11-18 | 14:15 | ZN4545:PA32 | URBAN | Other | Other | 1 | 585 | 0.000397 | 1e-06 | N
23-11-18 | 22:01 | ZN14143:PA17 | SHORT RURAL | Asset Failure | HV | 665 | 918 | 2.5714 | 0.002801 | N
29-11-18 | 15:33 | ZN340:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 117 | 0.002621 | 2.2e-05 | N
28-11-18 | 18:00 | ZN15004:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 15 | 0.000468 | 3.1e-05 | N
29-11-18 | 16:31 | ZN4990:PA53 54GHJ | CBD | Other | Other - Self Clearing Trigger | 1 | 119 | 0.003911 | 3.3e-05 | N
29-11-18 | 16:32 | ZN342:PA17 | URBAN | Third Party | Other | 1 | 608 | 0.000412 | 1e-06 | N
29-11-18 | 16:45 | ZN2635:PA46 | URBAN | Asset Failure | LV | 46 | 120 | 0.003734 | 3.1e-05 | N
24-11-18 | 15:22 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 106 | 148 | 0.06607 | 0.000446 | N
29-11-18 | 17:24 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 12 | 11 | 0.000541 | 5.1e-05 | N
26-11-18 | 15:50 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 58 | 45 | 0.001771 | 3.9e-05 | N
26-11-18 | 17:05 | ZN15005:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 73 | 10 | 0.000495 | 5e-05 | N
24-11-18 | 04:10 | ZN965:PA33 | URBAN | Asset Failure | HV | 2 | 890 | 0.00121 | 1e-06 | N
29-11-18 | 18:04 | ZN10995:PA13 | URBAN | Other | Other - Arcing | 1 | 596 | 0.000404 | 1e-06 | N
29-11-18 | 18:06 | 261:81879 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 74 | 5e-05 | 1e-06 | N
29-11-18 | 19:46 | ZN10994:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 573 | 0.000389 | 1e-06 | N
29-11-18 | 19:48 | ZN10994:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 570 | 0.000387 | 1e-06 | N
29-11-18 | 19:50 | ZN10994:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 568 | 0.000386 | 1e-06 | N
24-11-18 | 01:03 | ZN15013:PA10 | SHORT RURAL | Network business | Network error | 56 | 1,062 | 0.25047 | 0.000236 | N
23-11-18 | 16:35 | ZN15013:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 85 | 0.00289 | 3.4e-05 | N
29-11-18 | 21:52 | ZN9900:PA19 | URBAN | Asset Failure | LV | 1 | 778 | 0.000528 | 1e-06 | N
29-11-18 | 22:42 | 233:82819 | SHORT RURAL | Animal | Animal impact | 28 | 76 | 0.008996 | 0.000118 | N
29-11-18 | 22:47 | ZN690:PA28 | URBAN | Asset Failure | HV | 2,431 | 65 | 0.10741 | 0.00165 | N
29-11-18 | 22:47 | ZN690:PA30 | URBAN | Asset Failure | HV | 1 | 89 | 6e-05 | 1e-06 | N
29-11-18 | 22:55 | 221:11895 | URBAN | Other | Other - Self Clearing Trigger | 58 | 394 | 0.01553 | 3.9e-05 | N
29-11-18 | 23:01 | ZN1648:PA4 | URBAN | Third Party | Vehicle impact | 71 | 49 | 0.002357 | 4.8e-05 | N
29-11-18 | 23:45 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 74 | 0.000935 | 1.3e-05 | N
30-11-18 | 04:38 | ZN1648:PA8 | SHORT RURAL | Other | Other | 1 | 14 | 6.1e-05 | 4e-06 | N
30-11-18 | 06:22 | ZN12570:PA39 | URBAN | Third Party | Vehicle impact | 2 | 247 | 0.000335 | 1e-06 | N
30-11-18 | 06:28 | 227:13015 | SHORT RURAL | Animal | Animal impact | 2 | 207 | 0.001744 | 8e-06 | N
28-11-18 | 15:10 | ZN7481:PA20 | URBAN | Third Party | Other | 1 | 1,550 | 0.001052 | 1e-06 | N
28-11-18 | 18:20 | ZN35500:PA35 | URBAN | Asset Failure | LV | 8 | 955 | 0.005186 | 5e-06 | N
29-11-18 | 10:30 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 55 | 0.000232 | 4e-06 | N
30-11-18 | 09:02 | ZN2635:PA32 | URBAN | Other | Other | 1 | 688 | 0.000467 | 1e-06 | N
30-11-18 | 09:28 | ZN2635:PA43 | SHORT RURAL | Third Party | Other | 38 | 127 | 0.020333 | 0.00016 | N
30-11-18 | 11:06 | ZN1193:PA28 | URBAN | Third Party | Vehicle impact | 1 | 174 | 0.000118 | 1e-06 | N
30-11-18 | 11:48 | ZN12610:PA20 | SHORT RURAL | Other | Other - Self Clearing Trigger | 25 | 31 | 0.003278 | 0.000105 | N
30-11-18 | 11:46 | ZN1648:PA15 | URBAN | Third Party | Other | 1,114 | 102 | 0.077415 | 0.000756 | N
30-11-18 | 12:35 | ZN690:PA25 | URBAN | Network business | Network error | 210 | 696 | 0.099127 | 0.000142 | N
30-11-18 | 12:02 | ZN2835:PA16 | URBAN | Asset Failure | LV | 1 | 59 | 4e-05 | 1e-06 | N
30-11-18 | 12:38 | ZN3425:PA35 | URBAN | Other | Other - Self Clearing Trigger | 185 | 57 | 0.007154 | 0.000126 | N
30-11-18 | 14:03 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 197 | 0.00083 | 4e-06 | N
30-11-18 | 15:22 | ZN15006:PA6 | URBAN | Asset Failure | LV | 1 | 473 | 0.000321 | 1e-06 | N
30-11-18 | 15:31 | ZN35400:PA61 | URBAN | Other | Other | 1 | 88 | 6e-05 | 1e-06 | N
30-11-18 | 15:56 | ZN965:PA3 | URBAN | Other | Other - Self Clearing Trigger | 23 | 79 | 0.001229 | 1.6e-05 | N
30-11-18 | 16:11 | 224:80340 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 38 | 0.000162 | 4e-06 | N
30-11-18 | 18:20 | 807:74183 | SHORT RURAL | Asset Failure | LV | 2 | 140 | 0.00118 | 8e-06 | N
30-11-18 | 19:30 | ZN1287:PA4 | URBAN | Asset Failure | HV | 224 | 30 | 0.004559 | 0.000152 | N
30-11-18 | 19:18 | ZN10997:PA1 | URBAN | Other | Other | 1 | 1,099 | 0.000746 | 1e-06 | N
30-11-18 | 23:03 | ZN3922:PA29 | URBAN | Other | Other - Arcing | 1 | 262 | 0.000177 | 1e-06 | N
30-11-18 | 23:40 | ZN3922:PA29 | URBAN | Other | Other - Arcing | 1 | 37 | 2.5e-05 | 1e-06 | N
01-12-18 | 07:07 | ZN874:PA9 | URBAN | Other | Other | 1 | 178 | 0.00012 | 1e-06 | N
01-12-18 | 08:11 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 109 | 0.005511 | 5.1e-05 | N
01-12-18 | 08:42 | 507:80923 | SHORT RURAL | Asset Failure | LV | 37 | 93 | 0.014428 | 0.000156 | N
01-12-18 | 09:12 | 522:83131 | URBAN | Other | Other - Self Clearing Trigger | 1 | 68 | 4.6e-05 | 1e-06 | N
01-12-18 | 15:45 | ZN4545:PA27 | URBAN | Asset Failure | HV | 227 | 83 | 0.012782 | 0.000154 | N
01-12-18 | 15:45 | ZN4545:PA35 | URBAN | Asset Failure | HV | 1,253 | 89 | 0.07547 | 0.00085 | N
01-12-18 | 15:17 | ZN3425:PA32 | URBAN | Other | Other - Self Clearing Trigger | 2 | 127 | 0.000172 | 1e-06 | N
01-12-18 | 15:57 | ZN35400:PA101 | URBAN | Asset Failure | LV | 99 | 1,473 | 0.0989 | 6.7e-05 | N
01-12-18 | 16:59 | ZN195:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 101 | 0.002397 | 2.4e-05 | N
01-12-18 | 17:03 | ZN9035:PA4 | URBAN | Asset Failure | LV | 39 | 611 | 0.016172 | 2.6e-05 | N
01-12-18 | 19:07 | ZN129:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 60 | 263 | 0.010705 | 4.1e-05 | N
01-12-18 | 23:25 | ZN12650:PA12 | URBAN | Asset Failure | LV | 1 | 113 | 7.6e-05 | 1e-06 | N
02-12-18 | 02:12 | 404:30095 | URBAN | Other | Other - Self Clearing Trigger | 1 | 265 | 0.00018 | 1e-06 | N
02-12-18 | 08:45 | ZN35500:PA35 | URBAN | Asset Failure | LV | 8 | 1,125 | 0.006106 | 5e-06 | N
02-12-18 | 08:48 | ZN35400:PA110 | URBAN | Other | Other | 2 | 319 | 0.000432 | 1e-06 | N
02-12-18 | 09:04 | ZN187:PA20 | URBAN | Asset Failure | HV | 2,131 | 133 | 0.19158 | 0.001446 | N
02-12-18 | 12:10 | ZN2602:PA30 | URBAN | Third Party | Other | 1 | 425 | 0.000288 | 1e-06 | N
02-12-18 | 12:29 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 952 | 136 | 0.087836 | 0.000646 | N
02-12-18 | 12:38 | ZN35800:PA10 | URBAN | Other | Other - Self Clearing Trigger | 79 | 67 | 0.003587 | 5.4e-05 | N
02-12-18 | 12:49 | ZN129:PA41 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 533 | 0.011576 | 2.2e-05 | N
02-12-18 | 12:47 | 528:83019 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 487 | 61 | 0.12569 | 0.002052 | N
02-12-18 | 12:53 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 276 | 0.001164 | 4e-06 | N
02-12-18 | 12:55 | ZN129:PA35 | URBAN | Asset Failure | LV | 1 | 697 | 0.000473 | 1e-06 | N
02-12-18 | 12:56 | ZN2835:PA23 | URBAN | Weather |  | 30 | 268 | 0.005455 | 2e-05 | N
02-12-18 | 13:17 | ZN36300:PA13 | URBAN | Other | Other - Self Clearing Trigger | 84 | 325 | 0.018533 | 5.7e-05 | N
02-12-18 | 13:42 | ZN1193:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 185 | 0.000126 | 1e-06 | N
02-12-18 | 13:45 | ZN10999:PA1 | URBAN | Other | Other - Self Clearing Trigger | 29 | 480 | 0.009438 | 2e-05 | N
02-12-18 | 13:53 | ZN2196:PA5 | URBAN | Weather |  | 19 | 117 | 0.001508 | 1.3e-05 | N
02-12-18 | 14:00 | ZN15013:PA10 | SHORT RURAL | Weather |  | 96 | 135 | 0.05474 | 0.000404 | N
02-12-18 | 14:04 | ZN10999:PA17 | URBAN | Asset Failure | HV | 926 | 100 | 0.062753 | 0.000628 | N
02-12-18 | 14:10 | ZN195:PA10 | URBAN | Other | Other | 1 | 342 | 0.000232 | 1e-06 | N
02-12-18 | 14:20 | ZN2568:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 65 | 69 | 0.003053 | 4.4e-05 | N
02-12-18 | 14:34 | 508:82576 | SHORT RURAL | Asset Failure | HV | 3 | 361 | 0.004563 | 1.3e-05 | N
02-12-18 | 14:42 | 801:74121 | LONG RURAL | Animal | Other | 1 | 63 | 0.022175 | 0.000352 | N
02-12-18 | 14:50 | ZN36200:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,020 | 0.004296 | 4e-06 | N
02-12-18 | 15:00 | ZN15004:PA1 | URBAN | Other | Other - Self Clearing Trigger | 40 | 325 | 0.008811 | 2.7e-05 | N
29-11-18 | 14:00 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 25 | 70 | 0.001188 | 1.7e-05 | N
02-12-18 | 15:22 | 508:82574 | SHORT RURAL | Asset Failure | LV | 1 | 143 | 0.000603 | 4e-06 | N
29-11-18 | 11:21 | ZN15010:PA28 | SHORT RURAL | Other | Other | 24 | 95 | 0.009603 | 0.000101 | N
02-12-18 | 15:29 | 513:48056 | SHORT RURAL | Asset Failure | LV | 1 | 188 | 0.000794 | 4e-06 | N
02-12-18 | 15:35 | ZN9252:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 265 | 0.006652 | 2.5e-05 | N
02-12-18 | 15:35 | ZN9252:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 120 | 205 | 0.016672 | 8.1e-05 | N
02-12-18 | 15:38 | ZN36100:PA5 | URBAN | Other | Other - Self Clearing Trigger | 73 | 35 | 0.00175 | 5e-05 | N
02-12-18 | 15:37 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 150 | 157 | 0.098937 | 0.000632 | N
29-11-18 | 15:40 | ZN15002:PA2 | URBAN | Other | Other - Self Clearing Trigger | 1,236 | 2 | 0.001678 | 0.000839 | N
29-11-18 | 15:40 | ZN15002:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 775 | 2 | 0.006528 | 0.003264 | N
29-11-18 | 15:40 | ZN15002:PA6 | URBAN | Other | Other - Self Clearing Trigger | 1,650 | 2 | 0.00224 | 0.00112 | N
29-11-18 | 15:40 | ZN15002:PA8 | URBAN | Other | Other - Self Clearing Trigger | 1,060 | 2 | 0.001439 | 0.000719 | N
29-11-18 | 15:40 | ZN15002:PA9 | URBAN | Other | Other - Self Clearing Trigger | 13 | 2 | 1.8e-05 | 9e-06 | N
02-12-18 | 15:46 | ZN3472:PA27 | URBAN | Overloads |  | 1 | 314 | 0.000213 | 1e-06 | N
02-12-18 | 15:55 | ZN129:PA57 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 232 | 0.000157 | 1e-06 | N
02-12-18 | 15:57 | ZN12690:PA6 | URBAN | Other | Other - Self Clearing Trigger | 68 | 124 | 0.00572 | 4.6e-05 | N
02-12-18 | 16:07 | 213:33770 | URBAN | Other | Other | 1 | 42 | 2.8e-05 | 1e-06 | N
02-12-18 | 16:09 | 524:33570 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 71 | 0.000299 | 4e-06 | N
02-12-18 | 16:13 | 513:48056 | SHORT RURAL | Asset Failure | HV | 56 | 77 | 0.018168 | 0.000236 | N
02-12-18 | 16:38 | 258:80775 | URBAN | Asset Failure | LV | 77 | 202 | 0.010535 | 5.2e-05 | N
02-12-18 | 16:47 | 515:35193 | SHORT RURAL | Asset Failure | HV | 9 | 383 | 0.014523 | 3.8e-05 | N
02-12-18 | 17:21 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 93 | 549 | 0.21499 | 0.000392 | N
02-12-18 | 17:34 | ZN12610:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 236 | 0.00016 | 1e-06 | N
02-12-18 | 14:34 | 807:74183 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 236 | 0.000994 | 4e-06 | N
02-12-18 | 17:37 | ZN15012:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 308 | 0.000209 | 1e-06 | N
02-12-18 | 18:29 | ZN2635:PA52 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 571 | 0.000387 | 1e-06 | N
02-12-18 | 18:26 | ZN14891:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 496 | 190 | 0.39734 | 0.00209 | N
02-12-18 | 18:26 | ZN14891:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 35 | 99 | 0.014599 | 0.000147 | N
02-12-18 | 18:59 | 258:80787 | URBAN | Other | Other | 1 | 21 | 1.4e-05 | 1e-06 | N
02-12-18 | 18:54 | 227:13020 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 134 | 546 | 0.30826 | 0.000565 | N
02-12-18 | 19:07 | 812:19071 | SHORT RURAL | Asset Failure | LV | 1 | 127 | 0.000536 | 4e-06 | N
02-12-18 | 19:08 | ZN12690:PA7 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 232 | 0.000976 | 4e-06 | N
02-12-18 | 15:45 | ZN2635:PA58 | URBAN | Asset Failure | LV | 46 | 250 | 0.007802 | 3.1e-05 | N
02-12-18 | 19:18 | ZN12570:PA37 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 20 | 0.000169 | 8e-06 | N
02-12-18 | 19:20 | ZN36300:PA13 | URBAN | Other | Other | 1 | 8 | 5e-06 | 1e-06 | N
02-12-18 | 19:25 | ZN9550:PA28 | URBAN | Other | Other | 1 | 1,054 | 0.000715 | 1e-06 | N
02-12-18 | 20:08 | ZN12600:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 891 | 0.000604 | 1e-06 | N
02-12-18 | 20:11 | ZN12610:PA22 | URBAN | Asset Failure | LV | 1 | 844 | 0.000573 | 1e-06 | N
02-12-18 | 16:11 | ZN12630:PA3 | SHORT RURAL | Asset Failure | HV | 62 | 120 | 0.031339 | 0.000261 | N
02-12-18 | 21:16 | ZN15009:PA9 | URBAN | Asset Failure | HV | 643 | 90 | 0.039166 | 0.000436 | N
02-12-18 | 21:15 | ZN15012:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 70 | 0.001757 | 2.5e-05 | N
03-12-18 | 02:39 | ZN36200:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 426 | 0.000289 | 1e-06 | N
03-12-18 | 01:40 | ZN12630:PA3 | SHORT RURAL | Asset Failure | LV | 5 | 540 | 0.011376 | 2.1e-05 | N
03-12-18 | 05:07 | ZN10991:PA1 | URBAN | Other | Other | 1 | 352 | 0.000239 | 1e-06 | N
03-12-18 | 06:52 | ZN4545:PA31 | URBAN | Asset Failure | LV | 73 | 157 | 0.007795 | 5e-05 | N
03-12-18 | 06:53 | ZN195:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 287 | 0.005452 | 1.9e-05 | N
03-12-18 | 07:15 | ZN2310:PA19 | URBAN | Asset Failure | LV | 38 | 173 | 0.00446 | 2.6e-05 | N
03-12-18 | 08:30 | 264:81240 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 149 | 0.000628 | 4e-06 | N
03-12-18 | 09:05 | ZN1287:PA17 | URBAN | Other | Other - Self Clearing Trigger | 47 | 85 | 0.00271 | 3.2e-05 | N
03-12-18 | 09:54 | 512:83732 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 86 | 0.000725 | 8e-06 | N
03-12-18 | 11:12 | 239:82133 | URBAN | Other | Other | 1 | 54 | 3.7e-05 | 1e-06 | N
03-12-18 | 11:32 | 205:12210 | URBAN | Asset Failure | Distribution substation | 1 | 447 | 0.000303 | 1e-06 | N
03-12-18 | 12:09 | ZN12580:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 305 | 0.000207 | 1e-06 | N
03-12-18 | 12:19 | ZN10997:PA1 | URBAN | Other | Other | 1 | 321 | 0.000218 | 1e-06 | N
03-12-18 | 13:02 | ZN36100:PA19 | URBAN | Asset Failure | LV | 1 | 589 | 0.0004 | 1e-06 | N
04-12-18 | 09:45 | 513:48059 | SHORT RURAL | Other | Other | 1 | 45 | 0.00019 | 4e-06 | N
03-12-18 | 13:20 | ZN3472:PA33 | URBAN | Third Party | Vehicle impact | 1 | 249 | 0.000169 | 1e-06 | N
03-12-18 | 14:14 | 224:80346 | URBAN | Asset Failure | HV | 1,654 | 93 | 0.10471 | 0.001122 | N
03-12-18 | 15:19 | ZN167:PA17 | URBAN | Third Party | Other | 1 | 103 | 7e-05 | 1e-06 | N
03-12-18 | 15:25 | ZN2835:PA41 | URBAN | Third Party | Other | 1 | 170 | 0.000115 | 1e-06 | N
03-12-18 | 16:30 | ZN10991:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 179 | 0.000122 | 1e-06 | N
03-12-18 | 17:45 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 89 | 0.002366 | 2.6e-05 | N
03-12-18 | 18:18 | ZN14891:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 222 | 0.000935 | 4e-06 | N
03-12-18 | 18:37 | ZN10999:PA17 | URBAN | Network business | Network error | 89 | 203 | 0.012257 | 6e-05 | N
30-11-18 | 09:45 | ZN8000:PA12 | URBAN | Asset Failure | LV | 1 | 195 | 0.000132 | 1e-06 | N
03-12-18 | 20:54 | ZN2635:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,021 | 30 | 0.02078 | 0.000693 | N
03-12-18 | 21:52 | ZN9900:PA3 | URBAN | Asset Failure | HV | 887 | 79 | 0.047506 | 0.000602 | N
03-12-18 | 21:52 | ZN9900:PA9 | URBAN | Asset Failure | HV | 1 | 73 | 5e-05 | 1e-06 | N
03-12-18 | 22:59 | ZN15012:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,051 | 0.000713 | 1e-06 | N
04-12-18 | 01:43 | ZN188:PA37 | URBAN | Vegetation | Vegetation Blow/Fall In | 141 | 72 | 0.006867 | 9.6e-05 | N
04-12-18 | 02:31 | ZN262:PA15 | URBAN | Other | Other - Self Clearing Trigger | 72 | 109 | 0.005314 | 4.9e-05 | N
04-12-18 | 03:02 | 232:33413 | SHORT RURAL | Third Party | Vehicle impact | 1 | 627 | 0.002643 | 4e-06 | N
04-12-18 | 07:09 | 523:33501 | SHORT RURAL | Animal | Animal impact | 1 | 63 | 0.000267 | 4e-06 | N
04-12-18 | 08:12 | 206:34441 | URBAN | Asset Failure | HV | 1 | 63 | 4.3e-05 | 1e-06 | N
04-12-18 | 08:32 | ZN2835:PA41 | URBAN | Third Party | Other | 1 | 302 | 0.000205 | 1e-06 | N
04-12-18 | 08:00 | ZN2400:PA15 | SHORT RURAL | Other | Other | 13 | 155 | 0.00849 | 5.5e-05 | N
04-12-18 | 09:25 | ZN36300:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 53 | 55 | 0.001978 | 3.6e-05 | N
04-12-18 | 09:52 | ZN3472:PA30 | URBAN | Vegetation | Vegetation Grow In | 1 | 325 | 0.000221 | 1e-06 | N
04-12-18 | 12:00 | 532:83309 | URBAN | Asset Failure | LV | 10 | 170 | 0.001153 | 7e-06 | N
04-12-18 | 12:41 | ZN3425:PA12 | URBAN | Asset Failure | HV | 1,239 | 71 | 0.059814 | 0.000841 | N
04-12-18 | 13:36 | ZN10991:PA1 | URBAN | Third Party | Vehicle impact | 105 | 124 | 0.008833 | 7.1e-05 | N
04-12-18 | 14:02 | 512:83741 | SHORT RURAL | Other | Other | 1 | 64 | 0.00027 | 4e-06 | N
04-12-18 | 14:06 | 258:80785 | URBAN | Other | Other | 1 | 75 | 5.1e-05 | 1e-06 | N
04-12-18 | 16:35 | ZN12620:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 175 | 0.000735 | 4e-06 | N
04-12-18 | 16:46 | ZN35900:PA24 | URBAN | Other | Other - Arcing | 1 | 304 | 0.000206 | 1e-06 | N
04-12-18 | 18:15 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 48 | 25 | 0.000814 | 3.3e-05 | N
04-12-18 | 18:47 | ZN690:PA12 | URBAN | Other | Other | 1 | 1,090 | 0.000739 | 1e-06 | N
04-12-18 | 21:41 | ZN80:PA40 | URBAN | Other | Other - Arcing | 1 | 678 | 0.00046 | 1e-06 | N
04-12-18 | 23:07 | ZN15006:PA12 | URBAN | Asset Failure | Distribution substation | 90 | 65 | 0.003986 | 6.1e-05 | N
05-12-18 | 00:02 | ZN116:PA12 | URBAN | Asset Failure | HV | 3,427 | 55 | 0.1275 | 0.002324 | N
05-12-18 | 00:22 | ZN80:PA22 | URBAN | Other | Other - Arcing | 1 | 638 | 0.000433 | 1e-06 | N
05-12-18 | 00:26 | ZN180:PA19 | URBAN | Asset Failure | LV | 1 | 135 | 9.1e-05 | 1e-06 | N
05-12-18 | 00:30 | ZN8100:PA30 | URBAN | Other | Other - Arcing | 1 | 539 | 0.000365 | 1e-06 | N
05-12-18 | 04:06 | ZN3922:PA17 | SHORT RURAL | Network business | Network error | 80 | 413 | 0.13917 | 0.000337 | N
05-12-18 | 02:25 | ZN262:PA26 | URBAN | Other | Other - Arcing | 1 | 394 | 0.000267 | 1e-06 | N
05-12-18 | 02:58 | ZN35600:PA14 | URBAN | Asset Failure | LV | 1 | 722 | 0.000489 | 1e-06 | N
05-12-18 | 03:20 | ZN690:PA34 | URBAN | Third Party | Other | 1 | 567 | 0.000385 | 1e-06 | N
05-12-18 | 04:06 | ZN4545:PA35 | URBAN | Other | Other - Arcing | 1 | 323 | 0.000219 | 1e-06 | N
05-12-18 | 04:58 | ZN1673:PA11 | URBAN | Third Party | Unauthorised access | 42 | 163 | 0.004636 | 2.8e-05 | N
05-12-18 | 06:13 | ZN15006:PA16 | URBAN | Other | Other - Arcing | 1 | 151 | 0.000103 | 1e-06 | N
05-12-18 | 06:41 | ZN690:PA18 | URBAN | Third Party | Other | 1 | 384 | 0.00026 | 1e-06 | N
05-12-18 | 06:58 | ZN3922:PA17 | SHORT RURAL | Other | Other | 60 | 237 | 0.059808 | 0.000253 | N
05-12-18 | 07:07 | ZN2196:PA14 | URBAN | Network business | Network error | 4 | 187 | 0.000507 | 3e-06 | N
05-12-18 | 07:20 | ZN2196:PA14 | URBAN | Network business | Network error | 5 | 175 | 0.000592 | 3e-06 | N
05-12-18 | 07:39 | ZN398:PA25 | URBAN | Third Party | Vehicle impact | 50 | 126 | 0.004272 | 3.4e-05 | N
05-12-18 | 08:33 | 227:13020 | SHORT RURAL | Other | Other | 1 | 87 | 0.000366 | 4e-06 | N
05-12-18 | 09:57 | ZN35900:PA12 | URBAN | Asset Failure | LV | 1 | 308 | 0.000209 | 1e-06 | N
05-12-18 | 14:01 | ZN14892:PA3 | SHORT RURAL | Other | Other | 1 | 179 | 0.000753 | 4e-06 | N
05-12-18 | 16:34 | ZN36300:PA3 | URBAN | Other | Other | 1 | 260 | 0.000176 | 1e-06 | N
05-12-18 | 21:11 | 227:13016 | SHORT RURAL | Animal | Animal impact | 70 | 69 | 0.020342 | 0.000295 | N
05-12-18 | 23:04 | ZN1648:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 981 | 0.004133 | 4e-06 | N
06-12-18 | 00:29 | ZN874:PA7 | URBAN | Other | Other - Arcing | 1 | 870 | 0.00059 | 1e-06 | N
06-12-18 | 04:07 | ZN2835:PA30 | URBAN | Other | Other - Arcing | 1 | 653 | 0.000443 | 1e-06 | N
06-12-18 | 04:59 | ZN35800:PA7 | URBAN | Asset Failure | LV | 1 | 541 | 0.000367 | 1e-06 | N
06-12-18 | 05:18 | ZN1648:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 608 | 0.002562 | 4e-06 | N
06-12-18 | 08:05 | ZN3155:PA19 | URBAN | Other | Other - Arcing | 1 | 385 | 0.000261 | 1e-06 | N
06-12-18 | 08:00 | 213:33775 | URBAN | Asset Failure | LV | 1 | 165 | 0.000112 | 1e-06 | N
05-12-18 | 15:10 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 60 | 0.000253 | 4e-06 | N
06-12-18 | 09:22 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 68 | 0.000286 | 4e-06 | N
06-12-18 | 09:25 | ZN14892:PA6 | URBAN | Asset Failure | LV | 1 | 1,311 | 0.000889 | 1e-06 | N
06-12-18 | 09:31 | ZN12650:PA17 | URBAN | Other | Other - Arcing | 1 | 493 | 0.000335 | 1e-06 | N
06-12-18 | 09:56 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 53 | 0.000224 | 4e-06 | N
06-12-18 | 10:24 | ZN14892:PA21 | URBAN | Asset Failure | LV | 1 | 215 | 0.000146 | 1e-06 | N
06-12-18 | 10:35 | ZN398:PA4 | URBAN | Vegetation | Vegetation Grow In | 1 | 264 | 0.000179 | 1e-06 | N
06-12-18 | 12:18 | ZN36000:PA12 | URBAN | Asset Failure | LV | 1 | 121 | 8.2e-05 | 1e-06 | N
06-12-18 | 13:53 | 807:74184 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 137 | 0.000577 | 4e-06 | N
06-12-18 | 14:39 | ZN2602:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 85 | 90 | 0.005198 | 5.8e-05 | N
06-12-18 | 15:33 | ZN2310:PA61 | URBAN | Other | Other - Self Clearing Trigger | 44 | 146 | 0.004367 | 3e-05 | N
06-12-18 | 16:17 | ZN965:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 538 | 0.000365 | 1e-06 | N
06-12-18 | 16:42 | 229:34995 | SHORT RURAL | Other | Other | 1 | 48 | 0.0002 | 4e-06 | N
06-12-18 | 16:59 | ZN10997:PA7 | URBAN | Asset Failure | LV | 76 | 480 | 0.024757 | 5.2e-05 | N
06-12-18 | 17:14 | 508:82576 | SHORT RURAL | Other | Other | 1 | 51 | 0.000216 | 4e-06 | N
06-12-18 | 17:28 | ZN874:PA18 | URBAN | Asset Failure | LV | 40 | 212 | 0.005748 | 2.7e-05 | N
06-12-18 | 17:24 | 508:82576 | SHORT RURAL | Other | Other | 1 | 41 | 0.000174 | 4e-06 | N
06-12-18 | 17:41 | 233:82812 | SHORT RURAL | Asset Failure | LV | 1 | 189 | 0.000795 | 4e-06 | N
06-12-18 | 17:41 | ZN180:PA20 | URBAN | Asset Failure | HV | 1,147 | 120 | 0.093407 | 0.000778 | N
06-12-18 | 17:48 | 233:82812 | SHORT RURAL | Asset Failure | LV | 1 | 182 | 0.000766 | 4e-06 | N
06-12-18 | 17:51 | ZN3425:PA44 | URBAN | Asset Failure | LV | 1 | 235 | 0.000159 | 1e-06 | N
06-12-18 | 18:07 | 238:34140 | SHORT RURAL | Asset Failure | LV | 1 | 91 | 0.000381 | 4e-06 | N
06-12-18 | 18:14 | ZN15004:PA9 | URBAN | Other | Other | 1 | 203 | 0.000137 | 1e-06 | N
06-12-18 | 19:27 | 238:34150 | SHORT RURAL | Asset Failure | LV | 65 | 246 | 0.067337 | 0.000274 | N
06-12-18 | 19:27 | ZN12630:PA3 | SHORT RURAL | Weather |  | 19 | 14 | 0.001084 | 8e-05 | N
06-12-18 | 19:46 | ZN180:PA34 | URBAN | Asset Failure | LV | 33 | 318 | 0.007107 | 2.2e-05 | N
06-12-18 | 23:07 | ZN10999:PA36 | URBAN | Asset Failure | HV | 2,368 | 81 | 0.1306 | 0.001606 | N
07-12-18 | 06:53 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 216 | 0.000147 | 1e-06 | N
07-12-18 | 08:10 | ZN690:PA35 | URBAN | Other | Other | 1 | 227 | 0.000154 | 1e-06 | N
07-12-18 | 10:22 | 515:35192 | SHORT RURAL | Asset Failure | LV | 1 | 104 | 0.000436 | 4e-06 | N
07-12-18 | 11:24 | 222:33602 | URBAN | Other | Other | 1 | 76 | 5.1e-05 | 1e-06 | N
07-12-18 | 11:31 | 509:33395 | LONG RURAL | Asset Failure | LV | 1 | 114 | 0.040127 | 0.000352 | N
07-12-18 | 12:27 | ZN1285:PA27 | URBAN | Third Party | Vehicle impact | 1 | 152 | 0.000103 | 1e-06 | N
07-12-18 | 12:53 | ZN10995:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 102 | 0.00249 | 2.4e-05 | N
07-12-18 | 13:43 | ZN12650:PA17 | URBAN | Other | Other | 1 | 42 | 2.9e-05 | 1e-06 | N
07-12-18 | 15:47 | 228:7491 | URBAN | Asset Failure | LV | 1 | 298 | 0.000202 | 1e-06 | N
07-12-18 | 16:28 | 509:33395 | LONG RURAL | Asset Failure | HV | 37 | 111 | 1.4456 | 0.013024 | N
07-12-18 | 18:00 | 264:81236 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 129 | 8.8e-05 | 1e-06 | N
07-12-18 | 18:41 | 232:11457 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 4 | 305 | 0.005145 | 1.7e-05 | N
07-12-18 | 18:42 | ZN195:PA11 | URBAN | Asset Failure | LV | 46 | 237 | 0.007394 | 3.1e-05 | N
08-12-18 | 01:10 | ZN10997:PA2 | URBAN | Third Party | Vehicle impact | 72 | 240 | 0.011722 | 4.9e-05 | N
08-12-18 | 05:33 | ZN1648:PA2 | URBAN | Other | Other - Self Clearing Trigger | 17 | 252 | 0.002901 | 1.2e-05 | N
08-12-18 | 14:10 | ZN3154:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 25 | 0.000746 | 3e-05 | N
08-12-18 | 08:21 | 513:48056 | SHORT RURAL | Asset Failure | LV | 1 | 129 | 0.000543 | 4e-06 | N
08-12-18 | 08:26 | ZN15006:PA2 | URBAN | Other | Other | 1 | 14 | 9e-06 | 1e-06 | N
08-12-18 | 12:03 | 802:82225 | SHORT RURAL | Asset Failure | HV | 56 | 60 | 0.014113 | 0.000236 | N
08-12-18 | 12:53 | ZN12640:PA8 | SHORT RURAL | Asset Failure | HV | 908 | 126 | 0.48044 | 0.003823 | N
08-12-18 | 15:28 | 502:48010 | SHORT RURAL | Third Party | Vehicle impact | 1 | 121 | 0.00051 | 4e-06 | N
08-12-18 | 16:20 | ZN1648:PA2 | URBAN | Asset Failure | LV | 17 | 154 | 0.001777 | 1.2e-05 | N
08-12-18 | 16:37 | ZN15006:PA6 | URBAN | Asset Failure | LV | 1 | 496 | 0.000337 | 1e-06 | N
08-12-18 | 17:06 | ZN15011:PA4 | URBAN | Other | Other - Self Clearing Trigger | 36 | 63 | 0.001547 | 2.4e-05 | N
08-12-18 | 17:28 | 238:34141 | SHORT RURAL | Asset Failure | LV | 5 | 170 | 0.003579 | 2.1e-05 | N
08-12-18 | 17:40 | 807:74184 | SHORT RURAL | Asset Failure | HV | 1 | 105 | 0.000442 | 4e-06 | N
08-12-18 | 17:56 | ZN180:PA21 | URBAN | Asset Failure | LV | 206 | 834 | 0.11654 | 0.00014 | N
08-12-18 | 18:15 | ZN15012:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 236 | 0.00016 | 1e-06 | N
08-12-18 | 18:33 | ZN15010:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 147 | 9.9e-05 | 1e-06 | N
08-12-18 | 18:39 | 515:35197 | LONG RURAL | Third Party | Other | 1 | 172 | 0.06057 | 0.000352 | N
08-12-18 | 19:12 | ZN9900:PA6 | URBAN | Asset Failure | LV | 20 | 117 | 0.001593 | 1.4e-05 | N
09-12-18 | 03:35 | ZN7900:PA6 | URBAN | Asset Failure | HV | 980 | 23 | 0.015289 | 0.000665 | N
09-12-18 | 03:35 | ZN7900:PA7 | URBAN | Asset Failure | HV | 441 | 13 | 0.003889 | 0.000299 | N
09-12-18 | 06:50 | 213:33775 | URBAN | Other | Other | 1 | 64 | 4.3e-05 | 1e-06 | N
09-12-18 | 10:08 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 148 | 0.052193 | 0.000352 | N
09-12-18 | 17:11 | 240:34849 | URBAN | Other | Other - Self Clearing Trigger | 142 | 48 | 0.004617 | 9.6e-05 | N
09-12-18 | 20:14 | ZN12640:PA10 | URBAN | Other | Other - Arcing | 28 | 60 | 0.001145 | 1.9e-05 | N
09-12-18 | 21:15 | ZN15002:PA2 | URBAN | Other | Other | 1 | 620 | 0.000421 | 1e-06 | N
09-12-18 | 21:31 | ZN35335:PA14 | URBAN | Other | Other - Arcing | 1 | 1,079 | 0.000732 | 1e-06 | N
10-12-18 | 01:55 | ZN12690:PA6 | URBAN | Animal | Animal impact | 73 | 95 | 0.004704 | 5e-05 | N
10-12-18 | 02:18 | 243:80080 | SHORT RURAL | Animal | Animal impact | 518 | 16 | 0.034894 | 0.002181 | N
10-12-18 | 03:24 | 232:11460 | URBAN | Asset Failure | HV | 221 | 93 | 0.013942 | 0.00015 | N
10-12-18 | 07:11 | ZN195:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 49 | 349 | 0.011588 | 3.3e-05 | N
10-12-18 | 07:55 | ZN3922:PA18 | URBAN | Other | Other - Self Clearing Trigger | 66 | 140 | 0.006248 | 4.5e-05 | N
10-12-18 | 08:36 | ZN2310:PA14 | URBAN | Third Party | Vehicle impact | 112 | 454 | 0.034492 | 7.6e-05 | N
10-12-18 | 08:36 | ZN2310:PA62 | URBAN | Third Party | Vehicle impact | 63 | 249 | 0.010641 | 4.3e-05 | N
10-12-18 | 09:42 | 812:19072 | SHORT RURAL | Other | Other | 1 | 133 | 0.00056 | 4e-06 | N
10-12-18 | 10:10 | ZN10999:PA17 | URBAN | Third Party | Other | 1 | 289 | 0.000196 | 1e-06 | N
10-12-18 | 10:46 | 230:81438 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 29 | 0.000122 | 4e-06 | N
10-12-18 | 11:21 | 229:34995 | SHORT RURAL | Other | Other | 1 | 29 | 0.000122 | 4e-06 | N
10-12-18 | 11:24 | ZN3154:PA24 | URBAN | Other | Other - Self Clearing Trigger | 33 | 111 | 0.002478 | 2.2e-05 | N
10-12-18 | 11:58 | ZN2310:PA10 | URBAN | Third Party | Vehicle impact | 70 | 438 | 0.020816 | 4.7e-05 | N
10-12-18 | 12:18 | ZN1068:PA27 | URBAN | Third Party | Vehicle impact | 55 | 177 | 0.006604 | 3.7e-05 | N
10-12-18 | 13:40 | 257:81985 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 105 | 7.1e-05 | 1e-06 | N
10-12-18 | 13:42 | ZN12570:PA34 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 848 | 60 | 0.21422 | 0.00357 | N
10-12-18 | 13:42 | ZN12570:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 337 | 60 | 0.013716 | 0.000229 | N
10-12-18 | 14:08 | 802:82220 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 181 | 0.000762 | 4e-06 | N
10-12-18 | 15:26 | ZN2310:PA10 | URBAN | Third Party | Vehicle impact | 45 | 222 | 0.006778 | 3.1e-05 | N
10-12-18 | 15:26 | ZN1287:PA4 | URBAN | Third Party | Vehicle impact | 31 | 214 | 0.0045 | 2.1e-05 | N
10-12-18 | 16:33 | ZN14144:PA4 | URBAN | Other | Other | 1 | 58 | 3.9e-05 | 1e-06 | N
07-12-18 | 22:30 | ZN12650:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 25 | 0.000712 | 2.8e-05 | N
10-12-18 | 18:07 | ZN14891:PA16 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 54 | 0.000226 | 4e-06 | N
10-12-18 | 18:40 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 50 | 0.017587 | 0.000352 | N
10-12-18 | 18:58 | ZN15002:PA8 | URBAN | Third Party | Other | 1 | 1,052 | 0.000713 | 1e-06 | N
10-12-18 | 19:59 | ZN36300:PA8 | URBAN | Asset Failure | LV | 1 | 119 | 8.1e-05 | 1e-06 | N
10-12-18 | 20:02 | ZN36300:PA19 | URBAN | Asset Failure | LV | 1 | 116 | 7.9e-05 | 1e-06 | N
10-12-18 | 20:33 | ZN36300:PA8 | URBAN | Asset Failure | LV | 1 | 85 | 5.8e-05 | 1e-06 | N
10-12-18 | 22:27 | ZN965:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 83 | 0.001013 | 1.2e-05 | N
11-12-18 | 05:03 | ZN15006:PA8 | URBAN | Weather |  | 987 | 49 | 0.032788 | 0.000669 | N
11-12-18 | 04:26 | ZN3154:PA19 | URBAN | Asset Failure | LV | 25 | 399 | 0.006763 | 1.7e-05 | N
11-12-18 | 06:13 | 264:81238 | SHORT RURAL | Other | Other - Arcing | 1 | 167 | 0.000702 | 4e-06 | N
11-12-18 | 07:20 | 227:13020 | SHORT RURAL | Asset Failure | HV | 1 | 360 | 0.001516 | 4e-06 | N
11-12-18 | 08:16 | ZN2635:PA31 | URBAN | Asset Failure | LV | 28 | 169 | 0.003208 | 1.9e-05 | N
10-12-18 | 09:50 | 242:81535 | URBAN | Other | Other | 17 | 37 | 0.000427 | 1.2e-05 | N
11-12-18 | 09:59 | ZN12570:PA39 | URBAN | Asset Failure | LV | 1 | 336 | 0.000228 | 1e-06 | N
08-12-18 | 14:47 | ZN12640:PA14 | URBAN | Asset Failure | HV | 1,815 | 2 | 0.002462 | 0.001231 | N
08-12-18 | 14:47 | ZN12640:PA8 | SHORT RURAL | Asset Failure | HV | 488 | 2 | 0.004109 | 0.002055 | N
11-12-18 | 10:33 | ZN3472:PA12 | URBAN | Third Party | Vehicle impact | 74 | 112 | 0.005619 | 5e-05 | N
11-12-18 | 11:17 | ZN35400:PA52 | URBAN | Third Party | Other | 2 | 343 | 0.000465 | 1e-06 | N
11-12-18 | 11:56 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 64 | 0.022377 | 0.000352 | N
11-12-18 | 14:16 | ZN14891:PA12 | SHORT RURAL | Asset Failure | HV | 710 | 56 | 0.1674 | 0.002989 | N
11-12-18 | 15:30 | 243:80081 | SHORT RURAL | Other | Other - Arcing | 1 | 240 | 0.001008 | 4e-06 | N
11-12-18 | 15:52 | ZN1068:PA17 | URBAN | Asset Failure | HV | 900 | 64 | 0.039249 | 0.00061 | N
11-12-18 | 16:07 | ZN1068:PA27 | URBAN | Network business | Network error | 61 | 51 | 0.002109 | 4.1e-05 | N
10-12-18 | 14:05 | ZN2602:PA41 | URBAN | Third Party | Vehicle impact | 67 | 195 | 0.008862 | 4.5e-05 | N
11-12-18 | 17:30 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 1 | 371 | 0.000251 | 1e-06 | N
11-12-18 | 17:50 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 1 | 351 | 0.000238 | 1e-06 | N
11-12-18 | 20:10 | 813:89061 | LONG RURAL | Asset Failure | LV | 2 | 350 | 0.24622 | 0.000703 | N
11-12-18 | 23:16 | 242:81539 | URBAN | Asset Failure | LV | 4 | 263 | 0.000713 | 3e-06 | N
12-12-18 | 09:16 | 202:34260 | URBAN | Other | Other | 1 | 62 | 4.2e-05 | 1e-06 | N
12-12-18 | 09:20 | ZN188:PA15 | URBAN | Third Party | Vehicle impact | 22 | 605 | 0.009024 | 1.5e-05 | N
12-12-18 | 09:20 | ZN8100:PA10 | URBAN | Third Party | Vehicle impact | 12 | 160 | 0.001302 | 8e-06 | N
12-12-18 | 09:28 | 532:83309 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 391 | 0.000265 | 1e-06 | N
12-12-18 | 10:59 | ZN2400:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 810 | 0.000549 | 1e-06 | N
12-12-18 | 11:10 | ZN10998:PA32 | SHORT RURAL | Third Party | Vehicle impact | 1 | 1,335 | 0.005619 | 4e-06 | N
12-12-18 | 11:17 | ZN35600:PA16 | URBAN | Third Party | Other | 1 | 103 | 7e-05 | 1e-06 | N
12-12-18 | 11:21 | ZN10999:PA16 | URBAN | Other | Other - Arcing | 1 | 698 | 0.000473 | 1e-06 | N
12-12-18 | 14:06 | ZN965:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 143 | 0.002231 | 1.6e-05 | N
12-12-18 | 14:41 | ZN4545:PA35 | URBAN | Other | Other | 1 | 152 | 0.000103 | 1e-06 | N
12-12-18 | 17:16 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 78 | 269 | 0.088336 | 0.000328 | N
12-12-18 | 18:39 | 512:83743 | SHORT RURAL | Other | Other | 238 | 23 | 0.023374 | 0.001002 | N
12-12-18 | 19:37 | ZN12660:PA14 | SHORT RURAL | Other | Other - Arcing | 1 | 243 | 0.001022 | 4e-06 | N
12-12-18 | 21:04 | ZN36200:PA1 | URBAN | Other | Other - Arcing | 1 | 157 | 0.000106 | 1e-06 | N
13-12-18 | 03:24 | ZN35600:PA19 | URBAN | Other | Other - Arcing | 1 | 58 | 3.9e-05 | 1e-06 | N
13-12-18 | 03:46 | ZN10999:PA4 | URBAN | Asset Failure | LV | 1 | 329 | 0.000223 | 1e-06 | N
13-12-18 | 04:01 | ZN36300:PA8 | URBAN | Other | Other - Arcing | 1 | 538 | 0.000365 | 1e-06 | N
13-12-18 | 04:22 | ZN35600:PA19 | URBAN | Other | Other - Arcing | 1 | 2 | 2e-06 | 1e-06 | N
13-12-18 | 06:13 | 222:33602 | URBAN | Other | Other - Arcing | 1 | 245 | 0.000166 | 1e-06 | N
13-12-18 | 07:02 | ZN14891:PA21 | SHORT RURAL | Third Party | Vehicle impact | 1 | 658 | 0.002769 | 4e-06 | N
13-12-18 | 07:15 | ZN15009:PA1 | URBAN | Other | Other - Arcing | 1 | 374 | 0.000254 | 1e-06 | N
13-12-18 | 10:30 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 11 | 205 | 0.009478 | 4.6e-05 | N
13-12-18 | 10:36 | ZN1788:PA29 | URBAN | Other | Other - Arcing | 1 | 53 | 3.6e-05 | 1e-06 | N
13-12-18 | 12:06 | ZN36300:PA11 | URBAN | Other | Other - Arcing | 1 | 324 | 0.000219 | 1e-06 | N
13-12-18 | 12:32 | ZN2568:PA38 | URBAN | Asset Failure | LV | 1 | 417 | 0.000283 | 1e-06 | N
13-12-18 | 13:18 | 508:82575 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 57 | 0.0012 | 2.1e-05 | N
13-12-18 | 16:20 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 264 | 0.001112 | 4e-06 | N
13-12-18 | 17:22 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 16 | 113 | 0.63595 | 0.005628 | N
13-12-18 | 17:27 | 511:29878 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 52 | 0.00022 | 4e-06 | N
13-12-18 | 17:57 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 112 | 0.009439 | 8.4e-05 | N
13-12-18 | 18:20 | 801:74123 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 140 | 0.002947 | 2.1e-05 | N
13-12-18 | 18:41 | ZN3425:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 84 | 0.001932 | 2.3e-05 | N
13-12-18 | 18:50 | 802:82215 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 200 | 0.000842 | 4e-06 | N
13-12-18 | 19:11 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 171 | 0.008656 | 5.1e-05 | N
13-12-18 | 19:23 | ZN3472:PA11 | URBAN | Weather |  | 155 | 77 | 0.008091 | 0.000105 | N
13-12-18 | 19:23 | ZN3472:PA34 | URBAN | Weather |  | 548 | 77 | 0.028607 | 0.000372 | N
13-12-18 | 19:26 | 512:83743 | SHORT RURAL | Asset Failure | HV | 1 | 224 | 0.000943 | 4e-06 | N
13-12-18 | 19:27 | 232:11454 | SHORT RURAL | Other | Other | 1 | 52 | 0.000219 | 4e-06 | N
13-12-18 | 19:29 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 166 | 0.001398 | 8e-06 | N
13-12-18 | 19:24 | 206:34434 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,518 | 102 | 0.10485 | 0.001029 | N
13-12-18 | 19:35 | 511:29880 | URBAN | Other | Other | 1 | 160 | 0.000108 | 1e-06 | N
13-12-18 | 19:36 | ZN35800:PA16 | URBAN | Weather |  | 1,482 | 136 | 0.13664 | 0.001005 | N
13-12-18 | 19:36 | ZN35800:PA7 | URBAN | Weather |  | 1,031 | 148 | 0.10345 | 0.000699 | N
13-12-18 | 19:40 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 130 | 0.000547 | 4e-06 | N
13-12-18 | 19:40 | 238:34141 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 278 | 0.005852 | 2.1e-05 | N
13-12-18 | 19:46 | 206:34440 | URBAN | Third Party | Other | 1 | 58 | 3.9e-05 | 1e-06 | N
13-12-18 | 19:47 | ZN10994:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,021 | 113 | 0.078228 | 0.000692 | N
13-12-18 | 19:14 | 238:34148 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 996 | 0.029353 | 2.9e-05 | N
13-12-18 | 19:23 | ZN1850:PA32 | URBAN | Asset Failure | HV | 835 | 160 | 0.090601 | 0.000566 | N
13-12-18 | 19:23 | ZN1850:PA40 | URBAN | Asset Failure | HV | 915 | 167 | 0.1036 | 0.00062 | N
13-12-18 | 19:55 | ZN10999:PA24 | URBAN | Asset Failure | HV | 2,524 | 251 | 0.42961 | 0.001711 | N
13-12-18 | 19:55 | ZN10999:PA7 | URBAN | Asset Failure | HV | 257 | 394 | 0.068705 | 0.000174 | N
14-12-18 | 04:16 | 512:83732 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 454 | 0.015291 | 3.4e-05 | N
13-12-18 | 20:02 | ZN10998:PA2 | URBAN | Other | Other - Self Clearing Trigger | 882 | 118 | 0.070393 | 0.000598 | N
13-12-18 | 20:02 | ZN10998:PA32 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 137 | 0.000577 | 4e-06 | N
13-12-18 | 20:06 | ZN3425:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 144 | 9.7e-05 | 1e-06 | N
13-12-18 | 20:10 | 204:82697 | URBAN | Other | Other - Arcing | 1 | 62 | 4.2e-05 | 1e-06 | N
13-12-18 | 22:07 | ZN35800:PA22 | URBAN | Other | Other - Self Clearing Trigger | 41 | 272 | 0.007573 | 2.8e-05 | N
13-12-18 | 20:13 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 72 | 0.008179 | 0.000114 | N
13-12-18 | 20:13 | 265:81651 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 92 | 0.001937 | 2.1e-05 | N
13-12-18 | 20:14 | 257:81987 | URBAN | Weather |  | 1 | 989 | 0.000671 | 1e-06 | N
13-12-18 | 20:19 | ZN10994:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 172 | 0.000117 | 1e-06 | N
13-12-18 | 20:41 | ZN2568:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 89 | 334 | 0.020146 | 6e-05 | N
13-12-18 | 20:20 | ZN2196:PA5 | URBAN | Vegetation | Vegetation Grow In | 1 | 295 | 0.0002 | 1e-06 | N
14-12-18 | 07:19 | ZN2196:PA14 | URBAN | Other | Other - Self Clearing Trigger | 4 | 231 | 0.000626 | 3e-06 | N
13-12-18 | 20:24 | ZN1285:PA31 | URBAN | Weather |  | 54 | 165 | 0.00605 | 3.7e-05 | N
13-12-18 | 20:33 | 528:83019 | SHORT RURAL | Asset Failure | Distribution substation | 30 | 222 | 0.027985 | 0.000126 | N
13-12-18 | 20:34 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 86 | 0.00036 | 4e-06 | N
13-12-18 | 20:47 | ZN35900:PA4 | SHORT RURAL | Asset Failure | LV | 61 | 173 | 0.044429 | 0.000257 | N
13-12-18 | 19:55 | ZN10991:PA12 | URBAN | Other | Other - Self Clearing Trigger | 39 | 285 | 0.007536 | 2.6e-05 | N
13-12-18 | 21:05 | ZN14892:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 94 | 0.001984 | 2.1e-05 | N
13-12-18 | 21:09 | 206:34440 | URBAN | Other | Other | 1 | 900 | 0.00061 | 1e-06 | N
15-12-18 | 21:13 | 507:80923 | SHORT RURAL | Weather |  | 2 | 137 | 0.001153 | 8e-06 | Y
13-12-18 | 21:14 | 238:34148 | SHORT RURAL | Asset Failure | HV | 2 | 316 | 0.002661 | 8e-06 | N
13-12-18 | 21:18 | ZN15001:PA11 | URBAN | Other | Other - Arcing | 1 | 942 | 0.000638 | 1e-06 | N
13-12-18 | 21:21 | 512:83743 | SHORT RURAL | Asset Failure | HV | 3 | 849 | 0.010723 | 1.3e-05 | N
13-12-18 | 21:42 | ZN36800:PA58 | URBAN | Other | Other | 151 | 193 | 0.019758 | 0.000102 | N
13-12-18 | 22:04 | ZN35800:PA16 | URBAN | Asset Failure | Distribution substation | 203 | 220 | 0.030335 | 0.000138 | N
13-12-18 | 22:04 | ZN35800:PA16 | URBAN | Asset Failure | Distribution substation | 84 | 555 | 0.031625 | 5.7e-05 | N
13-12-18 | 22:21 | 224:80340 | SHORT RURAL | Asset Failure | LV | 1 | 133 | 0.000562 | 4e-06 | N
13-12-18 | 22:37 | ZN9037:PA7 | URBAN | Asset Failure | LV | 28 | 278 | 0.005277 | 1.9e-05 | N
14-12-18 | 02:57 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 1 | 63 | 4.2e-05 | 1e-06 | N
14-12-18 | 04:42 | ZN10994:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 584 | 0.000396 | 1e-06 | N
14-12-18 | 05:55 | ZN2602:PA15 | URBAN | Other | Other | 1 | 199 | 0.000135 | 1e-06 | N
14-12-18 | 06:21 | 257:81997 | URBAN | Other | Other - Self Clearing Trigger | 10 | 85 | 0.000576 | 7e-06 | N
14-12-18 | 06:29 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 161 | 0.000676 | 4e-06 | N
14-12-18 | 06:41 | ZN10997:PA11 | URBAN | Other | Other - Self Clearing Trigger | 19 | 233 | 0.003004 | 1.3e-05 | N
14-12-18 | 07:50 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 265 | 0.002231 | 8e-06 | N
14-12-18 | 08:14 | ZN15014:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 435 | 0.00183 | 4e-06 | N
14-12-18 | 08:21 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 134 | 0.000563 | 4e-06 | N
14-12-18 | 08:55 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 225 | 0.079112 | 0.000352 | N
14-12-18 | 08:58 | 224:80326 | URBAN | Other | Other | 1 | 62 | 4.2e-05 | 1e-06 | N
14-12-18 | 09:03 | ZN10991:PA5 | URBAN | Asset Failure | LV | 10 | 520 | 0.003529 | 7e-06 | N
14-12-18 | 09:13 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 5 | 104 | 0.18291 | 0.001759 | N
13-12-18 | 21:17 | 512:83743 | SHORT RURAL | Asset Failure | HV | 4 | 733 | 0.012344 | 1.7e-05 | N
14-12-18 | 09:47 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 178 | 0.000749 | 4e-06 | N
14-12-18 | 09:57 | 270:83591 | SHORT RURAL | Other | Other | 1 | 82 | 0.000343 | 4e-06 | N
14-12-18 | 10:26 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 64 | 0.001078 | 1.7e-05 | N
14-12-18 | 10:41 | ZN10997:PA2 | URBAN | Other | Other - Self Clearing Trigger | 83 | 127 | 0.007153 | 5.6e-05 | N
14-12-18 | 10:49 | ZN2835:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 45 | 3.1e-05 | 1e-06 | N
14-12-18 | 18:50 | 223:14395 | SHORT RURAL | Third Party | Unauthorised access | 1 | 40 | 0.000168 | 4e-06 | N
14-12-18 | 11:10 | ZN12610:PA25 | URBAN | Asset Failure | LV | 1 | 335 | 0.000227 | 1e-06 | N
14-12-18 | 11:43 | 261:81876 | URBAN | Other | Other | 1 | 452 | 0.000306 | 1e-06 | N
14-12-18 | 08:00 | 810:74062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 145 | 0.00061 | 4e-06 | N
14-12-18 | 12:26 | 238:34148 | SHORT RURAL | Asset Failure | HV | 1 | 189 | 0.000796 | 4e-06 | N
14-12-18 | 12:12 | ZN12570:PA21 | URBAN | Other | Other - Arcing | 4 | 408 | 0.001106 | 3e-06 | N
14-12-18 | 12:20 | ZN9245:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 662 | 0.005573 | 8e-06 | N
14-12-18 | 12:22 | ZN2466:PA16 | URBAN | Other | Other | 1 | 553 | 0.000375 | 1e-06 | N
14-12-18 | 12:26 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 17 | 158 | 0.001826 | 1.2e-05 | N
14-12-18 | 12:35 | 807:74184 | SHORT RURAL | Weather |  | 1 | 215 | 0.000905 | 4e-06 | N
14-12-18 | 12:27 | ZN195:PA30 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 38 | 180 | 0.028717 | 0.00016 | N
14-12-18 | 12:35 | 807:74184 | SHORT RURAL | Weather |  | 1 | 160 | 0.000674 | 4e-06 | N
14-12-18 | 13:20 | 801:74121 | LONG RURAL | Weather |  | 254 | 129 | 11.56 | 0.089342 | N
14-12-18 | 13:27 | ZN10995:PA1 | URBAN | Third Party | Other | 1 | 760 | 0.000515 | 1e-06 | N
14-12-18 | 14:27 | 520:48172 | SHORT RURAL | Weather |  | 3 | 528 | 0.006669 | 1.3e-05 | N
14-12-18 | 14:31 | 526:34633 | SHORT RURAL | Other | Other - Arcing | 1 | 483 | 0.002035 | 4e-06 | N
14-12-18 | 14:03 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 158 | 48 | 0.03193 | 0.000665 | N
14-12-18 | 14:42 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 490 | 278 | 47.9247 | 0.17235 | N
14-12-18 | 14:58 | ZN12630:PA10 | SHORT RURAL | Weather |  | 323 | 329 | 0.447 | 0.00136 | N
14-12-18 | 15:00 | 230:81434 | URBAN | Vegetation | Vegetation Blow/Fall In | 78 | 255 | 0.013485 | 5.3e-05 | N
14-12-18 | 15:31 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 99 | 0.000834 | 8e-06 | N
14-12-18 | 15:32 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 58 | 0.000488 | 8e-06 | N
14-12-18 | 15:32 | ZN12640:PA1 | URBAN | Weather |  | 643 | 94 | 0.040978 | 0.000436 | N
14-12-18 | 15:32 | ZN12640:PA10 | URBAN | Weather |  | 1,684 | 94 | 0.10732 | 0.001142 | N
14-12-18 | 15:32 | ZN12640:PA12 | URBAN | Weather |  | 1,276 | 94 | 0.081319 | 0.000865 | N
14-12-18 | 15:32 | ZN12640:PA13 | SHORT RURAL | Weather |  | 2,046 | 94 | 0.80971 | 0.008614 | N
14-12-18 | 15:32 | ZN12640:PA14 | URBAN | Weather |  | 1,814 | 94 | 0.1156 | 0.00123 | N
14-12-18 | 15:32 | ZN12640:PA2 | URBAN | Weather |  | 1,355 | 94 | 0.086353 | 0.000919 | N
14-12-18 | 15:32 | ZN12640:PA4 | URBAN | Weather |  | 1,346 | 94 | 0.08578 | 0.000913 | N
14-12-18 | 15:32 | ZN12640:PA5 | URBAN | Weather |  | 1,507 | 94 | 0.09604 | 0.001022 | N
14-12-18 | 15:32 | ZN12640:PA7 | URBAN | Weather |  | 1,705 | 94 | 0.10866 | 0.001156 | N
14-12-18 | 15:32 | ZN12640:PA8 | SHORT RURAL | Weather |  | 908 | 94 | 0.35934 | 0.003823 | N
14-12-18 | 15:32 | ZN12660:PA10 | SHORT RURAL | Weather |  | 1,798 | 68 | 0.51475 | 0.00757 | N
14-12-18 | 15:32 | ZN12660:PA11 | URBAN | Weather |  | 762 | 68 | 0.03513 | 0.000517 | N
14-12-18 | 15:32 | ZN12660:PA13 | URBAN | Weather |  | 645 | 68 | 0.029736 | 0.000437 | N
14-12-18 | 15:32 | ZN12660:PA14 | SHORT RURAL | Weather |  | 1,239 | 68 | 0.35471 | 0.005216 | N
14-12-18 | 15:32 | ZN12660:PA16 | URBAN | Weather |  | 952 | 68 | 0.043889 | 0.000645 | N
14-12-18 | 15:32 | ZN12660:PA17 | URBAN | Weather |  | 1,274 | 68 | 0.058734 | 0.000864 | N
14-12-18 | 15:32 | ZN12660:PA5 | SHORT RURAL | Weather |  | 281 | 68 | 0.080447 | 0.001183 | N
14-12-18 | 15:32 | ZN12660:PA6 | SHORT RURAL | Weather |  | 468 | 68 | 0.13398 | 0.00197 | N
14-12-18 | 15:32 | ZN12660:PA8 | URBAN | Weather |  | 1,296 | 68 | 0.059748 | 0.000879 | N
14-12-18 | 15:32 | ZN36200:PA1 | URBAN | Weather |  | 1,391 | 7 | 0.006601 | 0.000943 | N
14-12-18 | 15:32 | ZN36200:PA11 | URBAN | Weather |  | 1,300 | 7 | 0.00617 | 0.000881 | N
14-12-18 | 15:32 | ZN36200:PA4 | SHORT RURAL | Weather |  | 930 | 7 | 0.027408 | 0.003915 | N
14-12-18 | 15:32 | ZN36200:PA8 | SHORT RURAL | Weather |  | 1,378 | 7 | 0.040611 | 0.005802 | N
14-12-18 | 15:39 | 511:29878 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 131 | 15 | 0.008483 | 0.000552 | N
14-12-18 | 15:54 | ZN398:PA9 | URBAN | Other | Other - Self Clearing Trigger | 113 | 171 | 0.0131 | 7.7e-05 | N
14-12-18 | 15:54 | 230:81434 | URBAN | Other | Other | 1 | 146 | 9.9e-05 | 1e-06 | N
14-12-18 | 15:55 | 526:34639 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 100 | 0.00042 | 4e-06 | N
14-12-18 | 16:11 | 522:83123 | SHORT RURAL | Asset Failure | HV | 2 | 324 | 0.002728 | 8e-06 | N
14-12-18 | 16:17 | 223:14393 | URBAN | Other | Other | 1 | 123 | 8.3e-05 | 1e-06 | N
14-12-18 | 14:57 | TS14450:757 | URBAN | Other | Other - Self Clearing Trigger | 1 | 1,459 | 0.000989 | 1e-06 | N
14-12-18 | 18:59 | ZN3472:PA28 | URBAN | Asset Failure | LV | 38 | 31 | 0.000792 | 2.6e-05 | N
14-12-18 | 16:37 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 17 | 7e-05 | 4e-06 | N
14-12-18 | 16:42 | ZN35600:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 637 | 0.002682 | 4e-06 | N
14-12-18 | 15:44 | ZN15014:PA18 | URBAN | Weather |  | 696 | 76 | 0.036065 | 0.000472 | N
14-12-18 | 14:57 | ZN12630:PA3 | SHORT RURAL | Other | Other | 416 | 581 | 1.0167 | 0.001751 | N
14-12-18 | 16:46 | 522:83124 | URBAN | Other | Other - Self Clearing Trigger | 24 | 79 | 0.001285 | 1.6e-05 | N
14-12-18 | 16:59 | ZN14143:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 8 | 151 | 0.005086 | 3.4e-05 | N
14-12-18 | 17:06 | ZN1673:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 474 | 0.000321 | 1e-06 | N
14-12-18 | 17:10 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 255 | 0.003221 | 1.3e-05 | N
14-12-18 | 17:21 | 512:83743 | SHORT RURAL | Asset Failure | HV | 55 | 90 | 0.020794 | 0.000232 | N
14-12-18 | 17:26 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 269 | 0.005663 | 2.1e-05 | N
14-12-18 | 17:38 | ZN15014:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 1,037 | 0.004366 | 4e-06 | N
14-12-18 | 17:38 | ZN690:PA17 | URBAN | Other | Other | 1 | 417 | 0.000282 | 1e-06 | N
14-12-18 | 17:45 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 360 | 0.006063 | 1.7e-05 | N
14-12-18 | 17:46 | ZN3155:PA29 | URBAN | Other | Other - Self Clearing Trigger | 169 | 94 | 0.010719 | 0.000115 | N
14-12-18 | 17:47 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 228 | 0.00192 | 8e-06 | N
14-12-18 | 17:48 | 213:33775 | URBAN | Asset Failure | LV | 1 | 315 | 0.000213 | 1e-06 | N
14-12-18 | 18:05 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 50 | 0.000209 | 4e-06 | N
14-12-18 | 18:06 | ZN1673:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 684 | 0.019477 | 2.8e-05 | N
14-12-18 | 18:12 | ZN262:PA41 | URBAN | Asset Failure | LV | 12 | 108 | 0.000879 | 8e-06 | N
14-12-18 | 18:12 | ZN262:PA42 | URBAN | Asset Failure | LV | 60 | 107 | 0.004372 | 4.1e-05 | N
14-12-18 | 19:19 | ZN15008:PA9 | URBAN | Other | Other - Arcing | 1 | 3,612 | 0.002449 | 1e-06 | N
14-12-18 | 19:19 | 232:11457 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,430 | 213 | 1.2795 | 0.00602 | N
15-12-18 | 00:24 | 232:33413 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 11 | 7 | 0.000324 | 4.6e-05 | Y
14-12-18 | 20:22 | ZN3155:PA29 | URBAN | Asset Failure | LV | 169 | 108 | 0.012371 | 0.000115 | N
14-12-18 | 20:53 | ZN2196:PA18 | URBAN | Third Party | Other | 1 | 1,291 | 0.000875 | 1e-06 | N
14-12-18 | 22:04 | ZN2400:PA11 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,001 | 0.004215 | 4e-06 | N
14-12-18 | 22:16 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 151 | 759 | 40.3173 | 0.053113 | N
14-12-18 | 22:27 | ZN15014:PA7 | URBAN | Other | Other - Self Clearing Trigger | 38 | 78 | 0.002005 | 2.6e-05 | N
15-12-18 | 00:24 | ZN15014:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 756 | 0.01947 | 2.6e-05 | Y
15-12-18 | 00:54 | 227:13018 | URBAN | Other | Other | 1 | 54 | 3.7e-05 | 1e-06 | Y
15-12-18 | 04:00 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 1,020 | 0.029034 | 2.8e-05 | Y
15-12-18 | 05:07 | ZN12630:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 254 | 165 | 0.17638 | 0.001069 | Y
15-12-18 | 05:53 | ZN2400:PA22 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 33 | 202 | 0.028058 | 0.000139 | Y
15-12-18 | 06:35 | 511:29873 | URBAN | Other | Other - Self Clearing Trigger | 7 | 146 | 0.000693 | 5e-06 | Y
15-12-18 | 05:38 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 9 | 268 | 0.8481 | 0.003165 | Y
15-12-18 | 07:01 | ZN12630:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 146 | 0.001229 | 8e-06 | Y
15-12-18 | 07:24 | 522:83124 | URBAN | Asset Failure | Distribution substation | 1 | 421 | 0.000285 | 1e-06 | Y
15-12-18 | 07:35 | 230:81434 | URBAN | Vegetation | Vegetation Grow In | 1 | 382 | 0.000259 | 1e-06 | Y
15-12-18 | 08:25 | ZN10995:PA7 | URBAN | Other | Other - Arcing | 73 | 50 | 0.002451 | 4.9e-05 | Y
15-12-18 | 09:34 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 125 | 0.044087 | 0.000352 | Y
15-12-18 | 10:02 | ZN9700:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 456 | 0.000309 | 1e-06 | Y
15-12-18 | 10:23 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 141 | 0.000593 | 4e-06 | Y
15-12-18 | 12:20 | ZN15010:PA25 | SHORT RURAL | Other | Other - Arcing | 1 | 1,420 | 0.005977 | 4e-06 | Y
15-12-18 | 12:48 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 232 | 0.081575 | 0.000352 | Y
15-12-18 | 16:30 | 511:29878 | SHORT RURAL | Weather |  | 882 | 437 | 1.6233 | 0.003712 | Y
15-12-18 | 14:05 | ZN35900:PA17 | URBAN | Third Party | Other | 1 | 260 | 0.000176 | 1e-06 | Y
15-12-18 | 14:17 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 205 | 0.000864 | 4e-06 | Y
15-12-18 | 15:27 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 88 | 175 | 0.064906 | 0.00037 | Y
15-12-18 | 15:28 | 806:82662 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 225 | 167 | 0.15802 | 0.000947 | Y
15-12-18 | 15:56 | 812:19072 | SHORT RURAL | Asset Failure | HV | 41 | 278 | 0.047959 | 0.000173 | Y
15-12-18 | 16:09 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 1,046 | 0.36779 | 0.000352 | Y
15-12-18 | 16:06 | ZN2400:PA26 | URBAN | Weather |  | 962 | 149 | 0.097146 | 0.000652 | Y
15-12-18 | 16:18 | ZN1285:PA24 | URBAN | Other | Other | 1,535 | 77 | 0.080105 | 0.00104 | Y
15-12-18 | 16:18 | ZN1285:PA33 | URBAN | Other | Other | 1 | 77 | 5.2e-05 | 1e-06 | Y
15-12-18 | 16:22 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 15 | 38 | 0.002399 | 6.3e-05 | Y
15-12-18 | 16:24 | ZN35370:PA8 | SHORT RURAL | Weather |  | 450 | 2,521 | 4.7751 | 0.001894 | Y
15-12-18 | 16:17 | ZN35370:PA10 | SHORT RURAL | Weather |  | 507 | 2,783 | 5.9394 | 0.002134 | Y
15-12-18 | 16:17 | ZN35370:PA2 | SHORT RURAL | Weather |  | 372 | 2,137 | 3.3461 | 0.001566 | Y
15-12-18 | 16:15 | ZN3154:PA11 | URBAN | Weather |  | 806 | 150 | 0.081938 | 0.000546 | Y
15-12-18 | 16:15 | ZN3154:PA5 | URBAN | Weather |  | 488 | 150 | 0.04961 | 0.000331 | Y
15-12-18 | 16:32 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 71 | 158 | 0.047261 | 0.000299 | Y
15-12-18 | 16:31 | ZN12630:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 67 | 225 | 0.063415 | 0.000282 | Y
15-12-18 | 16:40 | 512:83732 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 140 | 0.003536 | 2.5e-05 | Y
15-12-18 | 16:22 | ZN965:PA33 | URBAN | Asset Failure | HV | 1,297 | 1,763 | 1.5498 | 0.000879 | Y
15-12-18 | 16:47 | ZN3154:PA5 | URBAN | Other | Other - Self Clearing Trigger | 27 | 152 | 0.002779 | 1.8e-05 | Y
15-12-18 | 16:47 | 214:8666 | URBAN | Asset Failure | HV | 1,486 | 92 | 0.092735 | 0.001007 | Y
15-12-18 | 16:45 | ZN1290:PA10 | URBAN | Other | Other - Self Clearing Trigger | 36 | 129 | 0.003147 | 2.4e-05 | Y
15-12-18 | 16:45 | ZN1290:PA11 | URBAN | Other | Other - Self Clearing Trigger | 1,191 | 129 | 0.10413 | 0.000807 | Y
15-12-18 | 16:45 | ZN1290:PA12 | URBAN | Other | Other - Self Clearing Trigger | 1,042 | 129 | 0.0911 | 0.000706 | Y
15-12-18 | 16:45 | ZN1290:PA13 | URBAN | Other | Other - Self Clearing Trigger | 157 | 129 | 0.013726 | 0.000106 | Y
15-12-18 | 16:45 | ZN1290:PA16 | URBAN | Other | Other - Self Clearing Trigger | 22 | 129 | 0.001923 | 1.5e-05 | Y
15-12-18 | 16:45 | ZN1290:PA17 | URBAN | Other | Other - Self Clearing Trigger | 176 | 129 | 0.015387 | 0.000119 | Y
15-12-18 | 16:45 | ZN1290:PA8 | URBAN | Other | Other - Self Clearing Trigger | 712 | 129 | 0.062249 | 0.000483 | Y
15-12-18 | 16:45 | ZN1290:PA9 | URBAN | Other | Other - Self Clearing Trigger | 1,256 | 129 | 0.10981 | 0.000851 | Y
15-12-18 | 16:48 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 117 | 2,493 | 1.2276 | 0.000492 | Y
15-12-18 | 16:22 | ZN965:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,161 | 1,108 | 0.87196 | 0.000787 | Y
15-12-18 | 16:22 | ZN965:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 617 | 1,916 | 0.8012 | 0.000418 | Y
15-12-18 | 16:22 | ZN965:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,160 | 1,547 | 1.2162 | 0.000786 | Y
15-12-18 | 16:22 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 536 | 1,101 | 2.484 | 0.002256 | Y
15-12-18 | 16:22 | ZN965:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 926 | 1,657 | 1.0397 | 0.000628 | Y
15-12-18 | 16:22 | ZN965:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 661 | 1,872 | 0.83849 | 0.000448 | Y
15-12-18 | 16:22 | ZN965:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 568 | 500 | 0.19248 | 0.000385 | Y
15-12-18 | 16:22 | ZN965:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,101 | 2,213 | 1.6516 | 0.000746 | Y
15-12-18 | 16:22 | ZN965:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 449 | 0.000304 | 1e-06 | Y
15-12-18 | 16:22 | ZN965:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 923 | 1,358 | 0.8495 | 0.000626 | Y
15-12-18 | 16:22 | ZN965:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,004 | 1,352 | 0.91997 | 0.00068 | Y
15-12-18 | 16:22 | ZN965:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 764 | 1,922 | 0.9952 | 0.000518 | Y
15-12-18 | 16:22 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,179 | 1,763 | 1.4087 | 0.000799 | Y
15-12-18 | 16:22 | ZN965:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 69 | 889 | 0.041573 | 4.7e-05 | Y
15-12-18 | 16:22 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 953 | 1,891 | 1.2216 | 0.000646 | Y
15-12-18 | 16:22 | ZN965:PA37 | URBAN | Vegetation | Vegetation Blow/Fall In | 465 | 1,011 | 0.31861 | 0.000315 | Y
15-12-18 | 16:22 | ZN965:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 776 | 1,851 | 0.97349 | 0.000526 | Y
15-12-18 | 16:22 | ZN965:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,115 | 1,816 | 1.3721 | 0.000756 | Y
15-12-18 | 16:22 | ZN965:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,131 | 2,167 | 1.661 | 0.000767 | Y
15-12-18 | 16:22 | ZN965:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,023 | 1,398 | 0.96927 | 0.000693 | Y
15-12-18 | 16:22 | ZN965:PA46 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,134 | 1,781 | 1.3688 | 0.000769 | Y
15-12-18 | 16:22 | ZN965:PA47 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,157 | 1,239 | 0.97177 | 0.000784 | Y
15-12-18 | 16:22 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,059 | 1,082 | 0.77658 | 0.000718 | Y
15-12-18 | 16:22 | ZN965:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,195 | 1,770 | 1.4333 | 0.00081 | Y
15-12-18 | 17:01 | ZN2635:PA43 | SHORT RURAL | Weather |  | 67 | 3,583 | 1.0105 | 0.000282 | Y
15-12-18 | 17:15 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 4 | 40 | 0.056259 | 0.001406 | Y
15-12-18 | 17:22 | ZN398:PA20 | URBAN | Other | Other - Arcing | 1 | 1,191 | 0.000807 | 1e-06 | Y
15-12-18 | 17:22 | ZN4545:PA29 | URBAN | Weather |  | 54 | 2,767 | 0.10127 | 3.7e-05 | Y
20-11-18 | 16:41 | ZN3288:PA45 46ABC | CBD | Weather |  | 57 | 2 | 0.003745 | 0.001873 | N
20-11-18 | 16:41 | ZN4545:PA25 | URBAN | Weather |  | 35 | 2,827 | 0.067282 | 2.4e-05 | N
15-12-18 | 17:25 | ZN1068:PA27 | URBAN | Other | Other | 1 | 814 | 0.000552 | 1e-06 | Y
15-12-18 | 17:25 | ZN1287:PA21 | URBAN | Other | Other - Self Clearing Trigger | 1,657 | 94 | 0.10561 | 0.001123 | Y
15-12-18 | 16:40 | TS14450:757 | URBAN | Other | Other - Self Clearing Trigger | 1 | 1,185 | 0.000803 | 1e-06 | Y
15-12-18 | 17:33 | ZN1287:PA4 | URBAN | Other | Other | 1 | 101 | 6.9e-05 | 1e-06 | Y
15-12-18 | 17:36 | ZN1673:PA21 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 53 | 3,834 | 0.85537 | 0.000223 | Y
15-12-18 | 17:40 | ZN35800:PA16 | URBAN | Other | Other | 1 | 800 | 0.000542 | 1e-06 | Y
15-12-18 | 17:40 | ZN1285:PA27 | URBAN | Asset Failure | LV | 40 | 915 | 0.024794 | 2.7e-05 | Y
17-12-18 | 00:27 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 17 | 1,053 | 0.012132 | 1.2e-05 | N
15-12-18 | 17:45 | ZN9245:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 158 | 0.000107 | 1e-06 | Y
15-12-18 | 17:45 | ZN1287:PA15 | URBAN | Other | Other | 1 | 195 | 0.000132 | 1e-06 | Y
15-12-18 | 17:46 | ZN1287:PA15 | URBAN | Other | Other | 1 | 194 | 0.000131 | 1e-06 | Y
16-12-18 | 21:45 | ZN965:PA3 | URBAN | Weather |  | 88 | 905 | 0.053975 | 6e-05 | Y
15-12-18 | 18:01 | 532:83293 | URBAN | Asset Failure | HV | 914 | 173 | 0.10692 | 0.000619 | Y
15-12-18 | 18:06 | ZN847:PA47 | SHORT RURAL | Weather |  | 3 | 3,579 | 0.045194 | 1.3e-05 | Y
15-12-18 | 18:06 | ZN10995:PA2 | URBAN | Asset Failure | LV | 2 | 1,392 | 0.001887 | 1e-06 | Y
15-12-18 | 23:26 | 532:83293 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 850 | 0.003456 | 4e-06 | Y
15-12-18 | 18:22 | ZN35800:PA16 | URBAN | Other | Other | 1 | 758 | 0.000514 | 1e-06 | Y
15-12-18 | 18:24 | 526:34641 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 619 | 0.002604 | 4e-06 | Y
15-12-18 | 19:15 | 528:83011 | SHORT RURAL | Asset Failure | LV | 13 | 838 | 0.045855 | 5.5e-05 | Y
15-12-18 | 18:57 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 183 | 0.12869 | 0.000703 | Y
15-12-18 | 18:55 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 180 | 0.003031 | 1.7e-05 | Y
15-12-18 | 19:03 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 73 | 129 | 0.03976 | 0.000307 | Y
15-12-18 | 19:12 | ZN180:PA15 | URBAN | Asset Failure | LV | 1 | 1,427 | 0.000967 | 1e-06 | Y
15-12-18 | 19:13 | ZN12630:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 5,777 | 0.19453 | 3.4e-05 | Y
15-12-18 | 19:18 | 522:83132 | SHORT RURAL | Other | Other - Self Clearing Trigger | 25 | 112 | 0.011786 | 0.000105 | Y
15-12-18 | 19:21 | ZN12660:PA14 | SHORT RURAL | Asset Failure | HV | 1,241 | 471 | 2.4619 | 0.005224 | Y
15-12-18 | 19:13 | ZN12630:PA10 | SHORT RURAL | Weather |  | 323 | 1,102 | 1.4989 | 0.00136 | Y
15-12-18 | 19:24 | ZN14143:PA17 | SHORT RURAL | Weather |  | 664 | 926 | 2.5893 | 0.002795 | Y
15-12-18 | 19:30 | ZN12640:PA7 | URBAN | Weather |  | 1,705 | 308 | 0.35617 | 0.001156 | Y
15-12-18 | 19:30 | ZN12640:PA12 | URBAN | Other | Other - Self Clearing Trigger | 1,276 | 243 | 0.21014 | 0.000865 | Y
15-12-18 | 19:33 | ZN14143:PA12 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,325 | 501 | 2.7946 | 0.005577 | Y
15-12-18 | 19:36 | ZN2400:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 615 | 104 | 0.26892 | 0.002589 | Y
15-12-18 | 19:40 | ZN2196:PA3 | URBAN | Other | Other - Arcing | 1 | 739 | 0.000501 | 1e-06 | Y
15-12-18 | 19:45 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 210 | 0.000882 | 4e-06 | Y
15-12-18 | 19:44 | ZN2196:PA3 | URBAN | Network business | Switching and protection error | 378 | 29 | 0.007461 | 0.000256 | Y
15-12-18 | 19:57 | ZN965:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 4,093 | 0.005549 | 1e-06 | Y
16-12-18 | 20:02 | ZN12630:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 2,548 | 0.021449 | 8e-06 | Y
15-12-18 | 20:03 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 231 | 0.081347 | 0.000352 | Y
15-12-18 | 23:00 | ZN12630:PA8 | SHORT RURAL | Weather |  | 8 | 460 | 0.01549 | 3.4e-05 | Y
15-12-18 | 20:12 | ZN2635:PA58 | URBAN | Weather |  | 67 | 3,708 | 0.16837 | 4.5e-05 | Y
15-12-18 | 20:13 | ZN15006:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 2,537 | 0.003439 | 1e-06 | Y
15-12-18 | 20:14 | ZN2310:PA3 | URBAN | Other | Other - Arcing | 1 | 20 | 1.3e-05 | 1e-06 | Y
15-12-18 | 20:09 | ZN9252:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,287 | 150 | 0.13116 | 0.000872 | Y
16-12-18 | 03:25 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 35 | 1,879 | 0.27683 | 0.000147 | Y
16-12-18 | 06:29 | ZN10994:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 231 | 0.005636 | 2.4e-05 | Y
15-12-18 | 20:07 | ZN10994:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,020 | 172 | 0.11867 | 0.000691 | Y
15-12-18 | 20:28 | ZN35800:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 656 | 0.017352 | 2.6e-05 | Y
15-12-18 | 20:28 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2,568 | 0.001741 | 1e-06 | Y
15-12-18 | 20:28 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2,511 | 0.001702 | 1e-06 | Y
15-12-18 | 20:30 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2,461 | 0.001668 | 1e-06 | Y
15-12-18 | 20:30 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,463 | 0.000992 | 1e-06 | Y
15-12-18 | 20:32 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 708 | 0.021113 | 3e-05 | Y
15-12-18 | 20:17 | ZN9700:PA20 | URBAN | Asset Failure | HV | 3 | 2,319 | 0.004716 | 2e-06 | Y
15-12-18 | 20:34 | ZN35800:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 326 | 0.000221 | 1e-06 | Y
16-12-18 | 11:56 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 16 | 423 | 0.004588 | 1.1e-05 | Y
15-12-18 | 20:36 | ZN9700:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,142 | 0.000774 | 1e-06 | Y
15-12-18 | 20:36 | ZN1285:PA31 | URBAN | Other | Other | 1 | 83 | 5.7e-05 | 1e-06 | Y
16-12-18 | 06:22 | ZN12630:PA1 | SHORT RURAL | Asset Failure | LV | 4 | 1,898 | 0.031955 | 1.7e-05 | Y
15-12-18 | 20:39 | ZN9700:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 1,251 | 0.025429 | 2e-05 | Y
15-12-18 | 20:43 | ZN9700:PA15 | URBAN | Other | Other | 1 | 6 | 4e-06 | 1e-06 | Y
15-12-18 | 20:44 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 4,145 | 0.017447 | 4e-06 | Y
15-12-18 | 20:06 | ZN15004:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 20 | 904 | 0.012248 | 1.4e-05 | Y
15-12-18 | 16:13 | ZN35370:PA4 | SHORT RURAL | Weather |  | 759 | 2,610 | 8.3393 | 0.003195 | Y
15-12-18 | 16:13 | ZN35370:PA8 | SHORT RURAL | Weather |  | 278 | 3,236 | 3.7866 | 0.00117 | Y
15-12-18 | 20:50 | ZN9252:PA22 | URBAN | Other | Other | 1 | 69 | 4.7e-05 | 1e-06 | Y
15-12-18 | 20:51 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 9 | 6e-06 | 1e-06 | Y
15-12-18 | 20:51 | ZN9700:PA18 | URBAN | Vegetation | Vegetation Grow In | 1 | 1,113 | 0.000754 | 1e-06 | Y
15-12-18 | 20:53 | ZN9700:PA15 | URBAN | Network business | Switching and protection error | 71 | 1,536 | 0.073895 | 4.8e-05 | Y
15-12-18 | 21:01 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 4,099 | 0.017253 | 4e-06 | Y
15-12-18 | 21:01 | ZN9700:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 59 | 4e-05 | 1e-06 | Y
15-12-18 | 21:08 | ZN398:PA20 | URBAN | Weather |  | 1 | 1,810 | 0.001227 | 1e-06 | Y
15-12-18 | 21:30 | ZN9700:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 29 | 1.9e-05 | 1e-06 | Y
15-12-18 | 22:12 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2 | 1e-06 | 1e-06 | Y
15-12-18 | 23:00 | ZN2310:PA3 | URBAN | Other | Other - Arcing | 1 | 164 | 0.000111 | 1e-06 | Y
15-12-18 | 23:09 | ZN9252:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,713 | 0.001161 | 1e-06 | Y
15-12-18 | 23:36 | 502:48010 | SHORT RURAL | Third Party | Other | 1 | 69 | 0.00029 | 4e-06 | Y
16-12-18 | 00:41 | ZN690:PA25 | URBAN | Third Party | Vehicle impact | 2 | 2,629 | 0.003563 | 1e-06 | Y
16-12-18 | 03:57 | ZN180:PA41 | URBAN | Vegetation | Vegetation Blow/Fall In | 60 | 297 | 0.012083 | 4.1e-05 | Y
16-12-18 | 04:39 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 386 | 0.003249 | 8e-06 | Y
16-12-18 | 05:45 | ZN2635:PA58 | URBAN | Weather |  | 22 | 3,200 | 0.047713 | 1.5e-05 | Y
16-12-18 | 06:25 | ZN9700:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 35 | 2.3e-05 | 1e-06 | Y
16-12-18 | 06:52 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 44 | 3e-05 | 1e-06 | Y
16-12-18 | 10:44 | ZN12630:PA1 | SHORT RURAL | Asset Failure | Distribution substation | 6 | 113 | 0.002841 | 2.5e-05 | Y
16-12-18 | 07:51 | ZN2635:PA31 | URBAN | Weather |  | 13 | 2,915 | 0.025683 | 9e-06 | Y
16-12-18 | 07:52 | 522:83132 | SHORT RURAL | Weather |  | 2 | 458 | 0.003855 | 8e-06 | Y
16-12-18 | 08:13 | ZN398:PA20 | URBAN | Other | Other - Arcing | 1 | 1,147 | 0.000777 | 1e-06 | Y
16-12-18 | 08:29 | 508:82578 | SHORT RURAL | Other | Other | 1 | 200 | 0.000843 | 4e-06 | Y
16-12-18 | 08:39 | ZN2196:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 9 | 3,216 | 0.019617 | 6e-06 | Y
16-12-18 | 11:15 | ZN9700:PA12 | URBAN | Network business | Switching and protection error | 69 | 360 | 0.016835 | 4.7e-05 | Y
16-12-18 | 07:49 | ZN1673:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 3,300 | 0.076048 | 2.3e-05 | Y
15-12-18 | 20:35 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 75 | 890 | 0.045239 | 5.1e-05 | Y
15-12-18 | 20:35 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 45 | 1,155 | 0.035225 | 3e-05 | Y
15-12-18 | 20:35 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 60 | 1,085 | 0.044121 | 4.1e-05 | Y
16-12-18 | 10:49 | ZN9700:PA19 | URBAN | Weather |  | 1 | 1,651 | 0.001119 | 1e-06 | Y
19-12-18 | 08:19 | ZN965:PA4 | URBAN | Other | Other | 1 | 513 | 0.000348 | 1e-06 | N
16-12-18 | 11:07 | ZN9252:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,894 | 0.001284 | 1e-06 | Y
16-12-18 | 11:39 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 110 | 0.000464 | 4e-06 | Y
16-12-18 | 11:54 | ZN847:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 3,066 | 0.002078 | 1e-06 | Y
16-12-18 | 12:01 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 13 | 264 | 0.014445 | 5.5e-05 | Y
16-12-18 | 12:34 | ZN12620:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 516 | 131 | 0.28529 | 0.002172 | Y
16-12-18 | 12:31 | ZN9700:PA21 | URBAN | Other | Other - Self Clearing Trigger | 3 | 1,524 | 0.003099 | 2e-06 | Y
16-12-18 | 10:43 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 29 | 2,432 | 0.29686 | 0.000122 | Y
16-12-18 | 12:46 | 217:33611 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 194 | 0.000131 | 1e-06 | Y
15-12-18 | 17:11 | ZN847:PA45 | SHORT RURAL | Weather |  | 488 | 762 | 1.5661 | 0.002054 | Y
16-12-18 | 12:15 | ZN965:PA42 | URBAN | Weather |  | 47 | 1,815 | 0.057815 | 3.2e-05 | Y
16-12-18 | 13:36 | ZN35555:PA16 | URBAN | Asset Failure | HV | 1,586 | 110 | 0.11824 | 0.001075 | Y
16-12-18 | 01:26 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 595 | 1,056 | 2.6457 | 0.002504 | Y
16-12-18 | 14:03 | ZN3922:PA29 | URBAN | Asset Failure | HV | 2,256 | 124 | 0.18977 | 0.001529 | Y
16-12-18 | 14:03 | ZN3922:PA5 | SHORT RURAL | Asset Failure | HV | 14 | 119 | 0.007012 | 5.9e-05 | Y
16-12-18 | 10:43 | ZN965:PA2 | SHORT RURAL | Weather |  | 60 | 1,804 | 0.45563 | 0.000253 | Y
16-12-18 | 15:00 | ZN129:PA62 | URBAN | Other | Other | 1 | 3,353 | 0.002272 | 1e-06 | Y
16-12-18 | 15:08 | 202:34254 | URBAN | Vegetation | Vegetation Blow/Fall In | 14 | 134 | 0.001271 | 9e-06 | Y
16-12-18 | 10:43 | ZN965:PA2 | SHORT RURAL | Weather |  | 42 | 1,798 | 0.31782 | 0.000177 | Y
16-12-18 | 15:38 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 34 | 1,222 | 0.17486 | 0.000143 | Y
16-12-18 | 15:25 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 69 | 36 | 0.010455 | 0.00029 | Y
16-12-18 | 10:43 | ZN965:PA2 | SHORT RURAL | Weather |  | 31 | 1,542 | 0.2012 | 0.00013 | Y
16-12-18 | 15:34 | 513:48056 | SHORT RURAL | Asset Failure | HV | 412 | 71 | 0.1225 | 0.001734 | Y
16-12-18 | 16:04 | 239:82129 | SHORT RURAL | Third Party | Other | 1 | 94 | 0.000397 | 4e-06 | Y
16-12-18 | 15:54 | ZN13000:PA7 | SHORT RURAL | Asset Failure | HV | 1,418 | 113 | 0.67327 | 0.005968 | Y
16-12-18 | 16:00 | 239:82133 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 363 | 0.000246 | 1e-06 | Y
16-12-18 | 16:02 | ZN14892:PA6 | URBAN | Asset Failure | HV | 1,707 | 127 | 0.14685 | 0.001157 | Y
16-12-18 | 16:07 | 243:80084 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 293 | 0.001232 | 4e-06 | Y
16-12-18 | 16:28 | ZN13000:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,022 | 0.0043 | 4e-06 | Y
16-12-18 | 16:15 | 232:33413 | SHORT RURAL | Asset Failure | HV | 2,067 | 108 | 0.93782 | 0.0087 | Y
16-12-18 | 16:18 | ZN12630:PA3 | SHORT RURAL | Asset Failure | HV | 212 | 252 | 0.22498 | 0.000892 | Y
16-12-18 | 16:25 | ZN10994:PA8 | URBAN | Asset Failure | HV | 362 | 237 | 0.058069 | 0.000245 | Y
16-12-18 | 00:42 | ZN965:PA22 | URBAN | Weather |  | 48 | 3,518 | 0.11445 | 3.3e-05 | Y
16-12-18 | 16:26 | ZN12630:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 2,778 | 0.011694 | 4e-06 | Y
16-12-18 | 16:28 | 243:80081 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 421 | 0.001773 | 4e-06 | Y
16-12-18 | 16:46 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 354 | 0.37355 | 0.001055 | Y
16-12-18 | 16:48 | 812:19072 | SHORT RURAL | Asset Failure | HV | 66 | 127 | 0.03528 | 0.000278 | Y
16-12-18 | 16:49 | 523:33501 | SHORT RURAL | Asset Failure | HV | 21 | 2,104 | 0.186 | 8.8e-05 | Y
16-12-18 | 16:55 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 140 | 0.049068 | 0.000352 | Y
16-12-18 | 17:01 | ZN12630:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 634 | 0.010674 | 1.7e-05 | Y
16-12-18 | 17:02 | ZN35900:PA17 | URBAN | Other | Other | 1 | 1,225 | 0.00083 | 1e-06 | Y
16-12-18 | 16:19 | ZN2400:PA11 | SHORT RURAL | Asset Failure | HV | 698 | 1,783 | 5.2373 | 0.002938 | Y
16-12-18 | 17:40 | ZN10994:PA21 | URBAN | Network business | Network error | 107 | 200 | 0.014504 | 7.3e-05 | Y
16-12-18 | 17:54 | 511:29873 | URBAN | Other | Other - Self Clearing Trigger | 9 | 136 | 0.00083 | 6e-06 | Y
16-12-18 | 17:13 | 223:14395 | SHORT RURAL | Other | Other - Self Clearing Trigger | 16 | 257 | 0.017283 | 6.7e-05 | Y
16-12-18 | 18:18 | 239:82136 | URBAN | Other | Other | 1 | 155 | 0.000105 | 1e-06 | Y
16-12-18 | 18:35 | ZN9700:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 21 | 34 | 0.000484 | 1.4e-05 | Y
16-12-18 | 17:40 | ZN10994:PA14 | URBAN | Network business | Network error | 34 | 370 | 0.008526 | 2.3e-05 | Y
16-12-18 | 14:54 | ZN965:PA28 | URBAN | Weather |  | 28 | 1,630 | 0.030932 | 1.9e-05 | Y
16-12-18 | 21:49 | ZN15013:PA4 | SHORT RURAL | Asset Failure | LV | 27 | 1,336 | 0.15183 | 0.000114 | Y
16-12-18 | 18:55 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 155 | 0.000652 | 4e-06 | Y
16-12-18 | 21:30 | 233:82812 | SHORT RURAL | Other | Other - Self Clearing Trigger | 13 | 75 | 0.004104 | 5.5e-05 | Y
16-12-18 | 19:11 | ZN9037:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 120 | 0.003174 | 2.6e-05 | Y
16-12-18 | 20:10 | 270:83586 | URBAN | Third Party | Other | 1 | 1,225 | 0.00083 | 1e-06 | Y
16-12-18 | 12:15 | ZN965:PA42 | URBAN | Weather |  | 113 | 1,839 | 0.14084 | 7.7e-05 | Y
16-12-18 | 19:43 | ZN9700:PA15 | URBAN | Weather |  | 1 | 1,221 | 0.000828 | 1e-06 | Y
16-12-18 | 20:07 | 814:82283 | SHORT RURAL | Weather |  | 3 | 213 | 0.00269 | 1.3e-05 | Y
16-12-18 | 20:13 | 229:34995 | SHORT RURAL | Other | Other | 1 | 154 | 0.000647 | 4e-06 | Y
16-12-18 | 00:42 | ZN965:PA22 | URBAN | Weather |  | 27 | 3,558 | 0.065108 | 1.8e-05 | Y
16-12-18 | 21:03 | 230:81434 | URBAN | Vegetation | Vegetation Blow/Fall In | 689 | 311 | 0.1451 | 0.000467 | Y
16-12-18 | 21:04 | ZN12630:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 9 | 891 | 0.033752 | 3.8e-05 | Y
16-12-18 | 21:40 | 230:81440 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 765 | 0.016073 | 2.1e-05 | Y
16-12-18 | 21:47 | 233:82812 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 883 | 0.033449 | 3.8e-05 | Y
16-12-18 | 22:50 | ZN13000:PA5 | SHORT RURAL | Other | Other | 60 | 213 | 0.053665 | 0.000253 | Y
16-12-18 | 22:50 | 232:33413 | SHORT RURAL | Asset Failure | HV | 19 | 60 | 0.004798 | 8e-05 | Y
17-12-18 | 00:44 | ZN2196:PA25 | URBAN | Asset Failure | LV | 62 | 726 | 0.030512 | 4.2e-05 | N
17-12-18 | 02:59 | ZN3425:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 133 | 0.003598 | 2.7e-05 | N
16-12-18 | 21:45 | ZN965:PA3 | URBAN | Weather |  | 37 | 1,640 | 0.041125 | 2.5e-05 | Y
17-12-18 | 02:47 | ZN1193:PA28 | URBAN | Weather |  | 77 | 482 | 0.025169 | 5.2e-05 | N
17-12-18 | 05:32 | 520:48172 | SHORT RURAL | Asset Failure | HV | 1 | 163 | 0.000686 | 4e-06 | N
17-12-18 | 06:08 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 207 | 0.001743 | 8e-06 | N
17-12-18 | 07:57 | 502:48004 | URBAN | Asset Failure | HV | 285 | 46 | 0.008916 | 0.000193 | N
13-12-18 | 19:26 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 154 | 0.002593 | 1.7e-05 | N
17-12-18 | 07:30 | ZN9700:PA21 | URBAN | Weather |  | 1 | 409 | 0.000277 | 1e-06 | N
17-12-18 | 07:35 | ZN965:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 4,495 | 0.006093 | 1e-06 | N
17-12-18 | 07:40 | ZN9700:PA21 | URBAN | Weather |  | 2 | 399 | 0.000541 | 1e-06 | N
17-12-18 | 07:48 | ZN965:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 3,161 | 0.002142 | 1e-06 | N
17-12-18 | 07:57 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 83 | 0.000699 | 8e-06 | N
17-12-18 | 08:00 | ZN847:PA45 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 1,140 | 0.047983 | 4.2e-05 | N
17-12-18 | 08:20 | 523:33501 | SHORT RURAL | Asset Failure | HV | 121 | 26 | 0.013364 | 0.000509 | N
17-12-18 | 08:25 | 213:33775 | URBAN | Asset Failure | LV | 1 | 455 | 0.000308 | 1e-06 | N
17-12-18 | 08:58 | 202:34259 | URBAN | Overloads |  | 5 | 192 | 0.000651 | 3e-06 | N
17-12-18 | 09:03 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 97 | 0.000408 | 4e-06 | N
17-12-18 | 09:07 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 573 | 0.000389 | 1e-06 | N
17-12-18 | 09:54 | 230:81434 | URBAN | Other | Other | 1 | 86 | 5.8e-05 | 1e-06 | N
17-12-18 | 10:55 | ZN965:PA35 | URBAN | Other | Other | 27 | 354 | 0.006471 | 1.8e-05 | N
17-12-18 | 11:14 | ZN9700:PA21 | URBAN | Weather |  | 1 | 185 | 0.000125 | 1e-06 | N
17-12-18 | 11:16 | ZN2310:PA62 | URBAN | Third Party | Other | 1 | 184 | 0.000124 | 1e-06 | N
14-12-18 | 18:05 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 60 | 0.000253 | 4e-06 | N
14-12-18 | 18:05 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 65 | 0.000274 | 4e-06 | N
17-12-18 | 11:40 | ZN4545:PA17 | URBAN | Third Party | Other | 1 | 3,049 | 0.002067 | 1e-06 | N
17-12-18 | 11:45 | 532:83293 | URBAN | Network business | Network error | 20 | 60 | 0.000813 | 1.4e-05 | N
17-12-18 | 11:46 | ZN965:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,226 | 0.000831 | 1e-06 | N
17-12-18 | 12:00 | ZN9900:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 120 | 0.002603 | 2.2e-05 | N
17-12-18 | 12:06 | ZN10999:PA25 | URBAN | Third Party | Vehicle impact | 1 | 398 | 0.00027 | 1e-06 | N
17-12-18 | 12:07 | 532:83293 | URBAN | Other | Other | 1 | 145 | 9.8e-05 | 1e-06 | N
17-12-18 | 12:27 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 195 | 0.005148 | 2.6e-05 | N
17-12-18 | 12:24 | ZN187:PA23 | URBAN | Asset Failure | HV | 386 | 112 | 0.029386 | 0.000262 | N
14-12-18 | 22:40 | 232:11457 | SHORT RURAL | Asset Failure | HV | 1,080 | 213 | 0.96934 | 0.004547 | N
17-12-18 | 12:52 | ZN10995:PA13 | URBAN | Asset Failure | LV | 1 | 755 | 0.000512 | 1e-06 | N
16-12-18 | 21:45 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 1,295 | 0.02282 | 1.8e-05 | Y
17-12-18 | 13:00 | 216:10727 | URBAN | Other | Other | 1 | 70 | 4.7e-05 | 1e-06 | N
17-12-18 | 13:09 | ZN35370:PA8 | SHORT RURAL | Weather |  | 12 | 660 | 0.033341 | 5.1e-05 | N
17-12-18 | 13:15 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 10 | 1,139 | 0.047936 | 4.2e-05 | N
17-12-18 | 14:01 | 261:81870 | URBAN | Third Party | Other | 115 | 73 | 0.005723 | 7.8e-05 | N
17-12-18 | 13:45 | ZN1788:PA20 | URBAN | Other | Other - Arcing | 1 | 374 | 0.000254 | 1e-06 | N
17-12-18 | 13:48 | ZN36200:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,481 | 0.006234 | 4e-06 | N
17-12-18 | 13:54 | 243:80081 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 901 | 151 | 0.57114 | 0.003792 | N
17-12-18 | 14:13 | ZN180:PA22 | URBAN | Asset Failure | LV | 92 | 196 | 0.01224 | 6.2e-05 | N
17-12-18 | 16:15 | 230:81440 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 32 | 0.000781 | 2.4e-05 | N
17-12-18 | 15:14 | ZN4545:PA44 | URBAN | Asset Failure | LV | 1 | 1,653 | 0.00112 | 1e-06 | N
18-12-18 | 13:50 | ZN80:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 57 | 5 | 0.000193 | 3.9e-05 | N
17-12-18 | 15:54 | 813:89063 | SHORT RURAL | Asset Failure | LV | 1 | 397 | 0.001671 | 4e-06 | N
17-12-18 | 16:15 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 45 | 0.000947 | 2.1e-05 | N
17-12-18 | 16:23 | ZN3425:PA28 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 382 | 0.001608 | 4e-06 | N
17-12-18 | 16:24 | 513:48050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 96 | 0.00202 | 2.1e-05 | N
17-12-18 | 16:30 | 513:48050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 29 | 0.000122 | 4e-06 | N
17-12-18 | 16:36 | 515:35198 | SHORT RURAL | Weather |  | 5 | 114 | 0.002399 | 2.1e-05 | N
17-12-18 | 17:28 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 106 | 0.000447 | 4e-06 | N
14-12-18 | 16:59 | ZN14143:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 156 | 0.003941 | 2.5e-05 | N
17-12-18 | 17:30 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 135 | 0.002928 | 2.2e-05 | N
14-12-18 | 16:59 | ZN14143:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 160 | 0.004042 | 2.5e-05 | N
17-12-18 | 17:54 | ZN965:PA8 | URBAN | Other | Other | 12 | 1,066 | 0.00867 | 8e-06 | N
17-12-18 | 17:50 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 12 | 10 | 0.000505 | 5.1e-05 | N
17-12-18 | 17:56 | 811:74234 | SHORT RURAL | Asset Failure | LV | 1 | 275 | 0.001158 | 4e-06 | N
17-12-18 | 20:32 | ZN14143:PA12 | SHORT RURAL | Asset Failure | Distribution substation | 53 | 1,177 | 0.2626 | 0.000223 | N
17-12-18 | 23:20 | ZN965:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 7 | 2,919 | 0.013848 | 5e-06 | N
17-12-18 | 20:00 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 112 | 10 | 0.000733 | 7.6e-05 | N
17-12-18 | 20:14 | ZN12630:PA11 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 80 | 0.002023 | 2.5e-05 | N
17-12-18 | 20:14 | ZN12630:PA11 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 5 | 80 | 0.001684 | 2.1e-05 | N
17-12-18 | 20:31 | 502:48004 | URBAN | Asset Failure | Distribution substation | 65 | 44 | 0.001945 | 4.4e-05 | N
17-12-18 | 21:00 | ZN14143:PA12 | SHORT RURAL | Asset Failure | LV | 26 | 1,270 | 0.139 | 0.000109 | N
17-12-18 | 21:14 | ZN180:PA31 | URBAN | Other | Other - Arcing | 1 | 885 | 0.0006 | 1e-06 | N
17-12-18 | 18:22 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 2,477 | 0.010427 | 4e-06 | N
17-12-18 | 23:39 | ZN965:PA8 | URBAN | Other | Other | 1 | 756 | 0.000513 | 1e-06 | N
18-12-18 | 06:49 | ZN965:PA42 | URBAN | Weather |  | 18 | 167 | 0.002034 | 1.2e-05 | N
18-12-18 | 06:51 | ZN965:PA13 | URBAN | Other | Other | 29 | 262 | 0.005147 | 2e-05 | N
18-12-18 | 07:17 | ZN195:PA22 | URBAN | Other | Other - Self Clearing Trigger | 58 | 207 | 0.008155 | 3.9e-05 | N
18-12-18 | 07:23 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 547 | 0.000371 | 1e-06 | N
18-12-18 | 07:24 | ZN965:PA35 | URBAN | Vegetation | Vegetation Grow In | 1 | 383 | 0.00026 | 1e-06 | N
18-12-18 | 08:16 | ZN847:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 294 | 0.004583 | 1.6e-05 | N
18-12-18 | 07:36 | ZN965:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 1,970 | 0.008011 | 4e-06 | N
18-12-18 | 07:57 | 232:11455 | SHORT RURAL | Asset Failure | HV | 4,242 | 14 | 0.25735 | 0.017854 | N
18-12-18 | 07:57 | 232:11460 | URBAN | Asset Failure | HV | 221 | 23 | 0.003445 | 0.00015 | N
18-12-18 | 08:07 | ZN965:PA42 | URBAN | Asset Failure | LV | 11 | 3,074 | 0.022917 | 7e-06 | N
18-12-18 | 08:26 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 115 | 0.12135 | 0.001055 | N
18-12-18 | 08:28 | 235:2120 | SHORT RURAL | Other | Other | 1 | 106 | 0.000445 | 4e-06 | N
18-12-18 | 08:56 | 514:18137 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 83 | 0.000698 | 8e-06 | N
18-12-18 | 10:11 | ZN15013:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 264 | 175 | 0.19445 | 0.001111 | N
18-12-18 | 09:04 | 512:83732 | SHORT RURAL | Asset Failure | HV | 2 | 336 | 0.002828 | 8e-06 | N
15-12-18 | 20:53 | ZN9700:PA15 | URBAN | Network business | Switching and protection error | 25 | 1,512 | 0.025618 | 1.7e-05 | Y
15-12-18 | 23:50 | 528:83011 | SHORT RURAL | Asset Failure | Distribution substation | 4 | 140 | 0.002357 | 1.7e-05 | Y
18-12-18 | 10:00 | 512:83743 | SHORT RURAL | Weather |  | 2 | 259 | 0.00218 | 8e-06 | N
18-12-18 | 10:10 | ZN9700:PA23 | URBAN | Other | Other | 58 | 185 | 0.007272 | 3.9e-05 | N
14-12-18 | 15:57 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 43 | 0.000181 | 4e-06 | N
18-12-18 | 10:42 | ZN9252:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 118 | 0.002718 | 2.3e-05 | N
18-12-18 | 11:17 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 73 | 0.001483 | 2e-05 | N
18-12-18 | 11:38 | ZN2568:PA25 | URBAN | Other | Other - Self Clearing Trigger | 2 | 502 | 0.00068 | 1e-06 | N
14-12-18 | 07:50 | 516:48067 | SHORT RURAL | Weather |  | 1 | 420 | 0.001768 | 4e-06 | N
18-12-18 | 11:44 | 801:74123 | SHORT RURAL | Asset Failure | HV | 3 | 151 | 0.001907 | 1.3e-05 | N
15-12-18 | 22:16 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 4,155 | 0.005632 | 1e-06 | Y
18-12-18 | 12:38 | ZN14892:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 39 | 2.6e-05 | 1e-06 | N
18-12-18 | 15:10 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 110 | 0.000463 | 4e-06 | N
18-12-18 | 15:30 | ZN180:PA15 | URBAN | Asset Failure | LV | 1 | 476 | 0.000322 | 1e-06 | N
18-12-18 | 15:39 | ZN36200:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 291 | 0.000197 | 1e-06 | N
18-12-18 | 16:31 | ZN965:PA33 | URBAN | Other | Other | 34 | 168 | 0.003875 | 2.3e-05 | N
18-12-18 | 16:45 | ZN3154:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 17 | 0.000426 | 2.5e-05 | N
18-12-18 | 16:58 | 522:83124 | URBAN | Other | Other - Self Clearing Trigger | 1 | 132 | 8.9e-05 | 1e-06 | N
18-12-18 | 17:54 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 71 | 0.000598 | 8e-06 | N
18-12-18 | 17:54 | ZN965:PA8 | URBAN | Other | Other - Self Clearing Trigger | 50 | 126 | 0.00427 | 3.4e-05 | N
18-12-18 | 18:30 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 75 | 0.000316 | 4e-06 | N
18-12-18 | 18:53 | 270:83586 | URBAN | Asset Failure | LV | 1 | 239 | 0.000162 | 1e-06 | N
18-12-18 | 19:01 | ZN9700:PA15 | URBAN | Third Party | Other | 1 | 184 | 0.000125 | 1e-06 | N
18-12-18 | 19:19 | ZN36100:PA15 | URBAN | Third Party | Other | 1 | 250 | 0.00017 | 1e-06 | N
18-12-18 | 19:15 | ZN2466:PA41 | URBAN | Asset Failure | HV | 1,215 | 76 | 0.062841 | 0.000823 | N
18-12-18 | 17:54 | ZN847:PA45 | SHORT RURAL | Asset Failure | Distribution substation | 4 | 1,346 | 0.022661 | 1.7e-05 | N
18-12-18 | 21:43 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 706 | 0.002972 | 4e-06 | N
18-12-18 | 23:43 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 2,206 | 0.009286 | 4e-06 | N
18-12-18 | 23:50 | ZN7481:PA1 | URBAN | Other | Other - Arcing | 1 | 729 | 0.000494 | 1e-06 | N
19-12-18 | 00:40 | ZN15001:PA8 | URBAN | Animal | Animal impact | 683 | 71 | 0.032866 | 0.000463 | N
19-12-18 | 06:28 | 512:83732 | SHORT RURAL | Other | Other - Self Clearing Trigger | 29 | 97 | 0.01184 | 0.000122 | N
19-12-18 | 07:06 | ZN35600:PA19 | URBAN | Other | Other - Arcing | 1 | 293 | 0.000199 | 1e-06 | N
19-12-18 | 07:07 | ZN965:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 17 | 1,740 | 0.020044 | 1.2e-05 | N
19-12-18 | 10:08 | ZN2466:PA45 | URBAN | Other | Other | 1 | 1,258 | 0.000852 | 1e-06 | N
19-12-18 | 10:12 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 213 | 0.14984 | 0.000703 | N
19-12-18 | 10:22 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 248 | 0.001042 | 4e-06 | N
19-12-18 | 10:27 | 239:82132 | URBAN | Other | Other | 1 | 64 | 4.4e-05 | 1e-06 | N
19-12-18 | 14:02 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 33 | 0.00085 | 2.6e-05 | N
19-12-18 | 11:03 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 158 | 0.000665 | 4e-06 | N
19-12-18 | 11:08 | ZN10999:PA17 | URBAN | Third Party | Vehicle impact | 41 | 142 | 0.003933 | 2.8e-05 | N
17-12-18 | 11:00 | ZN2568:PA19 | URBAN | Network business | Switching and protection error | 4 | 110 | 0.000298 | 3e-06 | N
19-12-18 | 12:30 | ZN35370:PA2 | SHORT RURAL | Other | Other | 1 | 1,349 | 0.005678 | 4e-06 | N
19-12-18 | 13:09 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 471 | 0.001982 | 4e-06 | N
19-12-18 | 13:10 | ZN15002:PA4 | SHORT RURAL | Other | Other | 1 | 98 | 0.000412 | 4e-06 | N
19-12-18 | 15:35 | 813:89061 | LONG RURAL | Other | Other | 1 | 25 | 0.008794 | 0.000352 | N
19-12-18 | 14:21 | ZN10998:PA28 | URBAN | Other | Other - Arcing | 1 | 519 | 0.000351 | 1e-06 | N
19-12-18 | 14:24 | ZN2602:PA28 | URBAN | Other | Other - Arcing | 1 | 566 | 0.000384 | 1e-06 | N
19-12-18 | 14:33 | ZN12570:PA39 | URBAN | Other | Other | 1 | 172 | 0.000117 | 1e-06 | N
15-12-18 | 16:22 | ZN965:PA48 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 450 | 0.000305 | 1e-06 | Y
19-12-18 | 16:36 | 230:81434 | URBAN | Other | Other | 1 | 59 | 4e-05 | 1e-06 | N
19-12-18 | 17:07 | ZN129:PA56 | URBAN | Other | Other - Self Clearing Trigger | 11 | 463 | 0.003451 | 7e-06 | N
19-12-18 | 17:49 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 201 | 0.001692 | 8e-06 | N
19-12-18 | 17:58 | ZN3155:PA20 | URBAN | Other | Other - Arcing | 1 | 353 | 0.000239 | 1e-06 | N
19-12-18 | 18:00 | 210:83474 | URBAN | Other | Other | 1 | 179 | 0.000122 | 1e-06 | N
19-12-18 | 18:16 | 810:74050 | SHORT RURAL | Asset Failure | HV | 46 | 273 | 0.052805 | 0.000194 | N
19-12-18 | 18:37 | 216:10727 | URBAN | Other | Other | 1 | 79 | 5.3e-05 | 1e-06 | N
19-12-18 | 18:45 | 810:74050 | SHORT RURAL | Other | Other | 1 | 1,017 | 0.004279 | 4e-06 | N
19-12-18 | 19:18 | 811:74234 | SHORT RURAL | Asset Failure | HV | 134 | 295 | 0.16621 | 0.000564 | N
19-12-18 | 19:05 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 110 | 60 | 2.3215 | 0.038692 | N
19-12-18 | 19:05 | ZN965:PA43 | URBAN | Asset Failure | HV | 1,023 | 110 | 0.076274 | 0.000693 | N
19-12-18 | 19:26 | ZN2400:PA18 | SHORT RURAL | Weather |  | 14 | 12,524 | 0.73797 | 5.9e-05 | N
19-12-18 | 19:35 | 814:82285 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 345 | 0.002904 | 8e-06 | N
19-12-18 | 19:36 | ZN35370:PA10 | SHORT RURAL | Weather |  | 189 | 301 | 0.23943 | 0.000795 | N
19-12-18 | 19:36 | ZN35370:PA2 | SHORT RURAL | Weather |  | 79 | 301 | 0.10008 | 0.000333 | N
19-12-18 | 20:02 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 42 | 248 | 0.04384 | 0.000177 | N
19-12-18 | 20:02 | ZN12630:PA1 | SHORT RURAL | Asset Failure | HV | 2 | 1,333 | 0.011221 | 8e-06 | N
19-12-18 | 20:06 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 169 | 0.001423 | 8e-06 | N
19-12-18 | 20:09 | 813:89061 | LONG RURAL | Weather |  | 1 | 226 | 0.079353 | 0.000352 | N
19-12-18 | 20:26 | ZN12610:PA25 | URBAN | Other | Other - Arcing | 1 | 211 | 0.000143 | 1e-06 | N
19-12-18 | 20:32 | ZN847:PA23 | URBAN | Weather |  | 1 | 679 | 0.00046 | 1e-06 | N
19-12-18 | 20:53 | ZN12610:PA6 | URBAN | Other | Other - Arcing | 1 | 947 | 0.000642 | 1e-06 | N
19-12-18 | 21:42 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 908 | 0.31932 | 0.000352 | N
19-12-18 | 21:43 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 82 | 0.000346 | 4e-06 | N
19-12-18 | 21:48 | ZN12620:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 162 | 0.000682 | 4e-06 | N
19-12-18 | 21:33 | ZN36200:PA8 | SHORT RURAL | Asset Failure | Distribution substation | 72 | 190 | 0.057578 | 0.000303 | N
19-12-18 | 22:03 | 238:34148 | SHORT RURAL | Asset Failure | HV | 2 | 921 | 0.007753 | 8e-06 | N
19-12-18 | 22:23 | ZN2400:PA21 | URBAN | Third Party | Vehicle impact | 24 | 711 | 0.011572 | 1.6e-05 | N
19-12-18 | 22:21 | 810:74050 | SHORT RURAL | Other | Other - Arcing | 1 | 788 | 0.003317 | 4e-06 | N
19-12-18 | 22:39 | 813:89061 | LONG RURAL | Asset Failure | HV | 3 | 801 | 0.84523 | 0.001055 | N
20-12-18 | 00:44 | ZN965:PA8 | URBAN | Weather |  | 50 | 420 | 0.014231 | 3.4e-05 | Y
20-12-18 | 01:59 | ZN129:PA56 | URBAN | Asset Failure | LV | 11 | 506 | 0.00377 | 7e-06 | Y
20-12-18 | 02:01 | ZN14892:PA16 | URBAN | Asset Failure | HV | 2,001 | 81 | 0.10917 | 0.001356 | Y
20-12-18 | 07:30 | ZN14892:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 85 | 0.001843 | 2.2e-05 | Y
20-12-18 | 11:38 | ZN15013:PA10 | SHORT RURAL | Asset Failure | HV | 264 | 22 | 0.024445 | 0.001111 | Y
20-12-18 | 06:38 | 810:74050 | SHORT RURAL | Other | Other - Arcing | 1 | 202 | 0.000848 | 4e-06 | Y
20-12-18 | 06:50 | ZN15005:PA8 | URBAN | Asset Failure | Distribution substation | 65 | 284 | 0.012531 | 4.4e-05 | Y
20-12-18 | 06:59 | 270:83587 | URBAN | Asset Failure | LV | 1 | 133 | 9e-05 | 1e-06 | Y
20-12-18 | 07:31 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 179 | 0.000753 | 4e-06 | Y
20-12-18 | 08:11 | ZN7900:PA15 | URBAN | Asset Failure | HV | 463 | 93 | 0.029232 | 0.000314 | Y
20-12-18 | 08:11 | ZN7900:PA7 | URBAN | Asset Failure | HV | 440 | 70 | 0.020873 | 0.000298 | Y
20-12-18 | 08:35 | ZN14143:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 8 | 524 | 0.017645 | 3.4e-05 | Y
20-12-18 | 08:38 | ZN167:PA2 | URBAN | Other | Other | 1 | 215 | 0.000146 | 1e-06 | Y
20-12-18 | 08:40 | ZN10994:PA4 | URBAN | Asset Failure | LV | 90 | 95 | 0.005773 | 6.1e-05 | Y
20-12-18 | 09:22 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 138 | 0.04854 | 0.000352 | Y
20-12-18 | 09:30 | 810:74054 | LONG RURAL | Asset Failure | HV | 19 | 60 | 0.40098 | 0.006683 | Y
20-12-18 | 09:39 | 258:80781 | URBAN | Other | Other | 1 | 66 | 4.5e-05 | 1e-06 | Y
19-12-18 | 21:50 | ZN2635:PA43 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,062 | 0.00447 | 4e-06 | N
20-12-18 | 09:46 | ZN167:PA2 | URBAN | Asset Failure | LV | 13 | 124 | 0.001092 | 9e-06 | Y
20-12-18 | 09:54 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 236 | 0.001987 | 8e-06 | Y
20-12-18 | 09:57 | ZN9550:PA6 | URBAN | Third Party | Vehicle impact | 52 | 68 | 0.002396 | 3.5e-05 | Y
20-12-18 | 11:11 | 813:89061 | LONG RURAL | Asset Failure | HV | 1 | 259 | 0.091101 | 0.000352 | Y
20-12-18 | 18:23 | ZN12610:PA10 | URBAN | Asset Failure | HV | 1,993 | 56 | 0.075069 | 0.001351 | Y
20-12-18 | 11:46 | 806:82662 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 193 | 0.000814 | 4e-06 | Y
20-12-18 | 11:48 | 202:34260 | URBAN | Other | Other | 1 | 186 | 0.000126 | 1e-06 | Y
20-12-18 | 12:05 | 222:33597 | URBAN | Third Party | Vehicle impact | 26 | 85 | 0.001498 | 1.8e-05 | Y
19-12-18 | 18:30 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 235 | 0.000989 | 4e-06 | N
20-12-18 | 14:29 | ZN15014:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 171 | 0.002665 | 1.6e-05 | Y
20-12-18 | 14:15 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 165 | 0.001389 | 8e-06 | Y
20-12-18 | 14:23 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 161 | 0.000678 | 4e-06 | Y
20-12-18 | 14:34 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 40 | 0.014152 | 0.000352 | Y
20-12-18 | 14:46 | ZN847:PA2 | URBAN | Asset Failure | LV | 19 | 1,229 | 0.015825 | 1.3e-05 | Y
19-12-18 | 19:04 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 14 | 5.9e-05 | 4e-06 | N
20-12-18 | 15:04 | 810:74050 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 90 | 0.00038 | 4e-06 | Y
19-12-18 | 20:20 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 270 | 0.007955 | 2.9e-05 | N
20-12-18 | 15:54 | 810:74050 | SHORT RURAL | Other | Other | 1 | 98 | 0.000413 | 4e-06 | Y
20-12-18 | 16:52 | ZN847:PA47 | SHORT RURAL | Asset Failure | HV | 703 | 169 | 0.49953 | 0.002959 | Y
20-12-18 | 17:02 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,168 | 0.004914 | 4e-06 | Y
20-12-18 | 19:28 | ZN15001:PA6 | URBAN | Asset Failure | LV | 8 | 87 | 0.000472 | 5e-06 | Y
20-12-18 | 17:14 | ZN12640:PA13 | SHORT RURAL | Weather |  | 87 | 4,244 | 1.554 | 0.000366 | Y
14-12-18 | 00:15 | ZN1850:PA32 | URBAN | Network business | Network error | 11 | 90 | 0.000671 | 7e-06 | N
20-12-18 | 17:25 | ZN12690:PA16 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 107 | 103 | 0.046386 | 0.00045 | Y
20-12-18 | 17:42 | ZN10999:PA17 | URBAN | Asset Failure | HV | 1,218 | 163 | 0.13454 | 0.000825 | Y
20-12-18 | 17:48 | ZN12690:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 24 | 776 | 0.078398 | 0.000101 | Y
20-12-18 | 18:19 | 515:35197 | LONG RURAL | Asset Failure | HV | 99 | 444 | 15.4583 | 0.034822 | Y
20-12-18 | 18:10 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 27 | 329 | 3.1266 | 0.009497 | Y
20-12-18 | 18:13 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 16 | 636 | 3.5798 | 0.005628 | Y
20-12-18 | 18:30 | 217:33611 | URBAN | Other | Other | 1 | 30 | 2e-05 | 1e-06 | Y
20-12-18 | 18:33 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,310 | 0.46065 | 0.000352 | Y
20-12-18 | 18:38 | ZN2635:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 51 | 282 | 0.009746 | 3.5e-05 | Y
20-12-18 | 18:38 | ZN2635:PA58 | URBAN | Vegetation | Vegetation Blow/Fall In | 2,086 | 129 | 0.18236 | 0.001414 | Y
20-12-18 | 18:33 | 509:33395 | LONG RURAL | Asset Failure | HV | 184 | 1,560 | 100.9525 | 0.06472 | Y
20-12-18 | 18:37 | ZN14143:PA17 | SHORT RURAL | Weather |  | 1,962 | 748 | 6.1795 | 0.008258 | Y
20-12-18 | 18:44 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,054 | 0.37066 | 0.000352 | Y
20-12-18 | 17:56 | ZN12600:PA1 | SHORT RURAL | Weather |  | 1 | 199 | 0.000836 | 4e-06 | Y
20-12-18 | 18:40 | 813:89062 | SHORT RURAL | Asset Failure | HV | 291 | 1,119 | 1.3701 | 0.001225 | Y
20-12-18 | 18:44 | 523:33503 | URBAN | Other | Other - Self Clearing Trigger | 770 | 121 | 0.063093 | 0.000522 | Y
20-12-18 | 18:48 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 93 | 0.000392 | 4e-06 | Y
20-12-18 | 18:37 | 513:48056 | SHORT RURAL | Asset Failure | HV | 91 | 479 | 0.18362 | 0.000383 | Y
20-12-18 | 18:49 | ZN965:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 205 | 0.002503 | 1.2e-05 | Y
20-12-18 | 18:51 | ZN35370:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 159 | 0.000669 | 4e-06 | Y
20-12-18 | 18:51 | 813:89062 | SHORT RURAL | Asset Failure | LV | 5 | 345 | 0.00726 | 2.1e-05 | Y
20-12-18 | 18:34 | ZN12630:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 99 | 1,733 | 0.72202 | 0.000417 | Y
20-12-18 | 18:52 | ZN12570:PA41 | URBAN | Weather |  | 540 | 323 | 0.1182 | 0.000366 | Y
20-12-18 | 18:52 | ZN14144:PA1 | URBAN | Weather |  | 1,202 | 321 | 0.26148 | 0.000815 | Y
20-12-18 | 18:52 | ZN14144:PA10 | SHORT RURAL | Weather |  | 682 | 323 | 0.92716 | 0.00287 | Y
20-12-18 | 18:52 | ZN14144:PA2 | SHORT RURAL | Weather |  | 1,029 | 321 | 1.3902 | 0.004331 | Y
20-12-18 | 18:52 | ZN14144:PA4 | URBAN | Weather |  | 847 | 321 | 0.18425 | 0.000574 | Y
20-12-18 | 18:52 | ZN14144:PA5 | URBAN | Weather |  | 284 | 321 | 0.06178 | 0.000192 | Y
20-12-18 | 18:52 | ZN14144:PA7 | SHORT RURAL | Weather |  | 1,039 | 323 | 1.4125 | 0.004373 | Y
20-12-18 | 18:52 | ZN14144:PA8 | URBAN | Weather |  | 477 | 323 | 0.10441 | 0.000323 | Y
20-12-18 | 18:44 | ZN12630:PA11 | SHORT RURAL | Weather |  | 240 | 1,043 | 1.0537 | 0.00101 | Y
20-12-18 | 18:52 | ZN15014:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 899 | 115 | 0.069789 | 0.000609 | Y
20-12-18 | 18:36 | ZN12630:PA3 | SHORT RURAL | Weather |  | 71 | 3,575 | 1.0684 | 0.000299 | Y
20-12-18 | 18:45 | 520:48172 | SHORT RURAL | Asset Failure | HV | 176 | 408 | 0.30193 | 0.000741 | Y
20-12-18 | 18:42 | ZN12630:PA10 | SHORT RURAL | Weather |  | 323 | 1,599 | 2.1741 | 0.001359 | Y
20-12-18 | 18:50 | ZN12570:PA24 | SHORT RURAL | Weather |  | 1,781 | 381 | 2.8578 | 0.007496 | Y
20-12-18 | 18:41 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 3 | 90 | 0.001136 | 1.3e-05 | Y
20-12-18 | 18:41 | ZN12630:PA6 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 2,269 | 0.06685 | 2.9e-05 | Y
20-12-18 | 18:50 | ZN12570:PA22 | SHORT RURAL | Weather |  | 1,599 | 377 | 2.5369 | 0.00673 | Y
20-12-18 | 18:55 | ZN12570:PA37 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,523 | 487 | 3.1186 | 0.00641 | Y
20-12-18 | 18:52 | 520:48172 | SHORT RURAL | Asset Failure | HV | 114 | 668 | 0.32036 | 0.00048 | Y
20-12-18 | 19:12 | 513:48059 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,638 | 0.006894 | 4e-06 | Y
20-12-18 | 19:13 | 227:13020 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 296 | 0.001247 | 4e-06 | Y
20-12-18 | 18:53 | 513:48056 | SHORT RURAL | Asset Failure | HV | 155 | 267 | 0.17419 | 0.000652 | Y
20-12-18 | 18:59 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 149 | 2,150 | 1.3486 | 0.000627 | Y
15-12-18 | 21:26 | ZN2400:PA11 | SHORT RURAL | Asset Failure | LV | 123 | 4,244 | 2.1972 | 0.000518 | Y
20-12-18 | 18:47 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 467 | 0.039345 | 8.4e-05 | Y
20-12-18 | 19:19 | 261:81864 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 970 | 0.000658 | 1e-06 | Y
20-12-18 | 19:22 | 508:82578 | SHORT RURAL | Other | Other | 1 | 2,333 | 0.009819 | 4e-06 | Y
20-12-18 | 18:40 | 814:82289 | SHORT RURAL | Asset Failure | HV | 115 | 236 | 0.11423 | 0.000484 | Y
20-12-18 | 19:23 | 512:83743 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 362 | 0.004571 | 1.3e-05 | Y
20-12-18 | 18:55 | ZN12660:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 39 | 945 | 0.15512 | 0.000164 | Y
20-12-18 | 19:28 | 508:82578 | SHORT RURAL | Asset Failure | LV | 1 | 2,326 | 0.009792 | 4e-06 | Y
20-12-18 | 19:28 | 261:81864 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 961 | 0.000651 | 1e-06 | Y
20-12-18 | 19:32 | 813:89065 | SHORT RURAL | Other | Other - Self Clearing Trigger | 15 | 248 | 0.015657 | 6.3e-05 | Y
20-12-18 | 19:38 | ZN1673:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 956 | 0.000648 | 1e-06 | Y
20-12-18 | 19:41 | 813:89055 | SHORT RURAL | Other | Other | 1 | 1,132 | 0.004763 | 4e-06 | Y
20-12-18 | 19:45 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 1,010 | 0.71052 | 0.000703 | Y
15-12-18 | 16:38 | ZN15014:PA14 | URBAN | Other | Other - Self Clearing Trigger | 329 | 11 | 0.002453 | 0.000223 | Y
20-12-18 | 19:45 | 813:89063 | SHORT RURAL | Other | Other | 1 | 345 | 0.00145 | 4e-06 | Y
20-12-18 | 19:48 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 387 | 0.01466 | 3.8e-05 | Y
20-12-18 | 19:49 | 508:82578 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 265 | 0.001116 | 4e-06 | Y
20-12-18 | 19:54 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 25 | 319 | 0.033557 | 0.000105 | Y
20-12-18 | 22:55 | ZN2602:PA31 | URBAN | Asset Failure | LV | 54 | 100 | 0.003659 | 3.7e-05 | Y
20-12-18 | 19:56 | 508:82575 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 397 | 164 | 0.27353 | 0.001671 | Y
20-12-18 | 20:02 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 4 | 1,058 | 1.4886 | 0.001407 | Y
20-12-18 | 20:14 | 813:89062 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 64 | 331 | 0.089031 | 0.000269 | Y
20-12-18 | 20:33 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 161 | 0.000678 | 4e-06 | Y
20-12-18 | 20:36 | ZN12600:PA12 | URBAN | Weather |  | 36 | 949 | 0.023152 | 2.4e-05 | Y
20-12-18 | 20:40 | 515:35197 | LONG RURAL | Asset Failure | HV | 4 | 1,385 | 1.9486 | 0.001407 | Y
20-12-18 | 19:49 | ZN9252:PA21 | URBAN | Weather |  | 63 | 241 | 0.010289 | 4.3e-05 | Y
20-12-18 | 20:49 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 701 | 0.00295 | 4e-06 | Y
20-12-18 | 20:50 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 770 | 0.012963 | 1.7e-05 | Y
20-12-18 | 21:02 | ZN2635:PA58 | URBAN | Weather |  | 23 | 179 | 0.00279 | 1.6e-05 | Y
20-12-18 | 18:37 | ZN12630:PA3 | SHORT RURAL | Weather |  | 83 | 2,162 | 0.75513 | 0.000349 | Y
20-12-18 | 21:29 | 813:89062 | SHORT RURAL | Weather |  | 1 | 1,158 | 0.004873 | 4e-06 | Y
20-12-18 | 21:44 | ZN3154:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,574 | 0.001067 | 1e-06 | Y
20-12-18 | 22:08 | 509:33399 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 309 | 0.007803 | 2.5e-05 | Y
20-12-18 | 22:19 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 941 | 0.015842 | 1.7e-05 | Y
20-12-18 | 22:25 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 650 | 0.002734 | 4e-06 | Y
20-12-18 | 18:33 | ZN847:PA45 | SHORT RURAL | Asset Failure | HV | 196 | 346 | 0.28543 | 0.000825 | Y
20-12-18 | 18:55 | ZN12570:PA21 | URBAN | Asset Failure | Distribution substation | 18 | 2,420 | 0.02952 | 1.2e-05 | Y
21-12-18 | 20:15 | 806:82662 | SHORT RURAL | Asset Failure | HV | 13 | 70 | 0.00383 | 5.5e-05 | N
21-12-18 | 02:54 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 309 | 0.025994 | 8.4e-05 | N
21-12-18 | 04:12 | ZN2466:PA25 | SHORT RURAL | Weather |  | 105 | 63 | 0.027842 | 0.000442 | N
21-12-18 | 04:17 | 526:34637 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 57 | 0.00024 | 4e-06 | N
21-12-18 | 04:48 | ZN2635:PA46 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 141 | 0.004409 | 3.1e-05 | N
20-12-18 | 21:15 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 26 | 885 | 0.096847 | 0.000109 | Y
21-12-18 | 05:10 | 512:83732 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 79 | 0.000333 | 4e-06 | N
20-12-18 | 18:50 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 78 | 563 | 0.18489 | 0.000328 | Y
21-12-18 | 05:54 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 376 | 0.13216 | 0.000351 | N
21-12-18 | 06:05 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 145 | 0.001831 | 1.3e-05 | N
21-12-18 | 06:32 | 520:48172 | SHORT RURAL | Asset Failure | HV | 1 | 158 | 0.000665 | 4e-06 | N
21-12-18 | 11:27 | 813:89062 | SHORT RURAL | Asset Failure | HV | 42 | 58 | 0.010253 | 0.000177 | N
21-12-18 | 07:57 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 58 | 0.000976 | 1.7e-05 | N
21-12-18 | 07:31 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,211 | 0.005099 | 4e-06 | N
21-12-18 | 07:32 | ZN1673:PA1 | URBAN | Other | Other | 29 | 139 | 0.002729 | 2e-05 | N
21-12-18 | 07:38 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 167 | 0.0586 | 0.000351 | N
21-12-18 | 07:58 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 232 | 0.001953 | 8e-06 | N
21-12-18 | 08:10 | ZN3288:PA41 42DEF | CBD | Other | Other - Self Clearing Trigger | 10 | 1,475 | 0.48388 | 0.000328 | N
21-12-18 | 08:18 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 710 | 0.002989 | 4e-06 | N
21-12-18 | 08:19 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 401 | 0.001687 | 4e-06 | N
21-12-18 | 08:20 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 7 | 155 | 0.38137 | 0.00246 | N
21-12-18 | 08:43 | ZN2400:PA15 | SHORT RURAL | Weather |  | 44 | 107 | 0.019815 | 0.000185 | N
21-12-18 | 08:45 | 243:80080 | SHORT RURAL | Asset Failure | HV | 7 | 550 | 0.016204 | 2.9e-05 | N
21-12-18 | 09:11 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 131 | 0.000551 | 4e-06 | N
21-12-18 | 09:33 | 235:2120 | SHORT RURAL | Other | Other | 1 | 177 | 0.000745 | 4e-06 | N
21-12-18 | 09:44 | 508:82574 | SHORT RURAL | Asset Failure | LV | 1 | 166 | 0.000699 | 4e-06 | N
21-12-18 | 09:47 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 38 | 0.00064 | 1.7e-05 | N
21-12-18 | 13:23 | 532:83301 | URBAN | Other | Other | 1 | 141 | 9.6e-05 | 1e-06 | N
21-12-18 | 10:11 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 159 | 0.11177 | 0.000703 | N
21-12-18 | 10:27 | ZN10997:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 253 | 0.000171 | 1e-06 | N
21-12-18 | 10:45 | 813:89061 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 23 | 110 | 0.88928 | 0.008084 | N
21-12-18 | 10:59 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 1,486 | 0.043781 | 2.9e-05 | N
21-12-18 | 11:44 | ZN9035:PA10 | URBAN | Third Party | Vehicle impact | 17 | 177 | 0.002039 | 1.2e-05 | N
21-12-18 | 12:09 | 235:2120 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 305 | 0.001284 | 4e-06 | N
21-12-18 | 12:43 | 227:13020 | SHORT RURAL | Other | Other | 1 | 33 | 0.00014 | 4e-06 | N
21-12-18 | 13:15 | ZN965:PA8 | URBAN | Asset Failure | LV | 41 | 323 | 0.008967 | 2.8e-05 | N
21-12-18 | 13:48 | ZN2400:PA15 | SHORT RURAL | Asset Failure | LV | 44 | 681 | 0.12612 | 0.000185 | N
21-12-18 | 13:49 | ZN12690:PA24 | SHORT RURAL | Weather |  | 2 | 2,481 | 0.020884 | 8e-06 | N
20-12-18 | 17:20 | ZN12610:PA13 | SHORT RURAL | Asset Failure | LV | 45 | 180 | 0.034092 | 0.000189 | Y
21-12-18 | 16:35 | 814:82285 | SHORT RURAL | Asset Failure | HV | 9 | 25 | 0.000947 | 3.8e-05 | N
21-12-18 | 15:22 | 243:80078 | URBAN | Other | Other | 1 | 72 | 4.9e-05 | 1e-06 | N
21-12-18 | 15:40 | ZN2602:PA28 | URBAN | Third Party | Vehicle impact | 45 | 229 | 0.006983 | 3e-05 | N
21-12-18 | 15:59 | ZN12640:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 46 | 53 | 0.010261 | 0.000194 | N
21-12-18 | 16:29 | ZN12600:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 11 | 51 | 0.002351 | 4.6e-05 | N
21-12-18 | 17:13 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 127 | 0.000535 | 4e-06 | N
20-12-18 | 11:12 | ZN12610:PA10 | URBAN | Other | Other - Self Clearing Trigger | 1 | 431 | 0.000292 | 1e-06 | Y
21-12-18 | 17:25 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 110 | 0.001852 | 1.7e-05 | N
21-12-18 | 18:20 | ZN1285:PA33 | URBAN | Third Party | Vehicle impact | 66 | 190 | 0.008498 | 4.5e-05 | N
21-12-18 | 18:38 | ZN965:PA47 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,072 | 0.000726 | 1e-06 | N
21-12-18 | 19:11 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 74 | 0.001869 | 2.5e-05 | N
16-12-18 | 12:15 | ZN965:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 2,725 | 0.049865 | 1.8e-05 | Y
16-12-18 | 12:15 | ZN965:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 1,710 | 0.004636 | 3e-06 | Y
21-12-18 | 20:12 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 933 | 0.011781 | 1.3e-05 | N
21-12-18 | 09:59 | ZN14892:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 433 | 0.000294 | 1e-06 | N
22-12-18 | 00:05 | ZN9900:PA17 | URBAN | Other | Other - Self Clearing Trigger | 31 | 60 | 0.001254 | 2.1e-05 | N
22-12-18 | 08:11 | ZN1673:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 75 | 0.001883 | 2.5e-05 | N
22-12-18 | 05:01 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 568 | 0.000385 | 1e-06 | N
22-12-18 | 07:10 | ZN36100:PA15 | URBAN | Other | Other - Self Clearing Trigger | 12 | 199 | 0.001621 | 8e-06 | N
22-12-18 | 00:28 | ZN36300:PA19 | URBAN | Animal | Animal impact | 1,381 | 3 | 0.002807 | 0.000936 | N
20-12-18 | 19:46 | ZN15004:PA5 | URBAN | Asset Failure | LV | 47 | 84 | 0.002675 | 3.2e-05 | Y
22-12-18 | 08:30 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 106 | 0.000446 | 4e-06 | N
22-12-18 | 08:48 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 207 | 0.00014 | 1e-06 | N
22-12-18 | 08:48 | ZN36100:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 492 | 0.000333 | 1e-06 | N
22-12-18 | 09:04 | 513:48050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 91 | 0.000763 | 8e-06 | N
22-12-18 | 08:30 | ZN12630:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 13 | 220 | 0.012034 | 5.5e-05 | N
21-12-18 | 05:09 | ZN12570:PA37 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 58 | 136 | 0.033199 | 0.000244 | N
22-12-18 | 09:58 | 523:33501 | SHORT RURAL | Asset Failure | LV | 1 | 632 | 0.002659 | 4e-06 | N
22-12-18 | 10:05 | ZN2602:PA29 | URBAN | Other | Other - Arcing | 1 | 295 | 0.0002 | 1e-06 | N
22-12-18 | 11:07 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 298 | 0.001254 | 4e-06 | N
16-12-18 | 15:24 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 52 | 1,484 | 0.3249 | 0.000219 | Y
22-12-18 | 11:40 | ZN12630:PA1 | SHORT RURAL | Asset Failure | HV | 318 | 265 | 0.35458 | 0.001338 | N
22-12-18 | 11:46 | ZN3155:PA19 | URBAN | Asset Failure | LV | 1 | 411 | 0.000279 | 1e-06 | N
22-12-18 | 13:10 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 190 | 0.004797 | 2.5e-05 | N
19-12-18 | 04:01 | ZN2310:PA3 | URBAN | Third Party | Vehicle impact | 41 | 94 | 0.002612 | 2.8e-05 | N
22-12-18 | 13:50 | ZN9900:PA19 | URBAN | Asset Failure | LV | 1 | 1,420 | 0.000962 | 1e-06 | N
22-12-18 | 13:50 | ZN9900:PA2 | URBAN | Asset Failure | LV | 23 | 1,419 | 0.022114 | 1.6e-05 | N
22-12-18 | 14:24 | ZN690:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 325 | 0.00022 | 1e-06 | N
22-12-18 | 14:32 | 224:80346 | URBAN | Vegetation | Vegetation Blow/Fall In | 54 | 93 | 0.003402 | 3.7e-05 | N
22-12-18 | 15:27 | ZN1285:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 135 | 108 | 0.009878 | 9.1e-05 | N
22-12-18 | 14:55 | ZN2196:PA2 | URBAN | Asset Failure | HV | 749 | 60 | 0.030436 | 0.000507 | N
22-12-18 | 15:12 | ZN10994:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 428 | 0.00029 | 1e-06 | N
22-12-18 | 15:22 | 243:80081 | SHORT RURAL | Other | Other | 1 | 109 | 0.000457 | 4e-06 | N
22-12-18 | 15:34 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 76 | 0.00064 | 8e-06 | N
22-12-18 | 16:18 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 91 | 0.000385 | 4e-06 | N
22-12-18 | 17:12 | ZN262:PA7 | URBAN | Asset Failure | LV | 1 | 279 | 0.000189 | 1e-06 | N
22-12-18 | 17:23 | 513:48059 | SHORT RURAL | Other | Other | 132 | 51 | 0.028326 | 0.000555 | N
22-12-18 | 18:32 | ZN340:PA4 | URBAN | Third Party | Vehicle impact | 1 | 134 | 9.1e-05 | 1e-06 | N
22-12-18 | 18:53 | ZN12690:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 28 | 134 | 0.015787 | 0.000118 | N
22-12-18 | 19:45 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 110 | 0.000463 | 4e-06 | N
23-12-18 | 14:53 | ZN12610:PA10 | URBAN | Asset Failure | LV | 7 | 267 | 0.001266 | 5e-06 | N
22-12-18 | 20:33 | ZN129:PA40 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,160 | 48 | 0.037724 | 0.000786 | N
22-12-18 | 22:36 | ZN15014:PA7 | URBAN | Asset Failure | LV | 1 | 870 | 0.000589 | 1e-06 | N
23-12-18 | 04:05 | ZN10994:PA13 | URBAN | Third Party | Vehicle impact | 42 | 25 | 0.000711 | 2.8e-05 | N
23-12-18 | 06:35 | 523:33507 | URBAN | Third Party | Other | 15 | 179 | 0.001821 | 1e-05 | N
23-12-18 | 07:19 | ZN15009:PA5 | URBAN | Asset Failure | LV | 1 | 1,414 | 0.000958 | 1e-06 | N
23-12-18 | 07:58 | ZN3154:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 662 | 0.000448 | 1e-06 | N
23-12-18 | 14:55 | ZN2400:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 25 | 0.000639 | 2.6e-05 | N
23-12-18 | 13:23 | 220:8689 | URBAN | Other | Other - Arcing | 1 | 345 | 0.000234 | 1e-06 | N
23-12-18 | 13:44 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 360 | 0.000244 | 1e-06 | N
23-12-18 | 16:35 | ZN2400:PA22 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,269 | 108 | 0.57541 | 0.005339 | N
23-12-18 | 17:09 | ZN2835:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 113 | 7.6e-05 | 1e-06 | N
23-12-18 | 18:28 | 239:82133 | URBAN | Asset Failure | Distribution substation | 82 | 61 | 0.003392 | 5.6e-05 | N
23-12-18 | 20:05 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 189 | 0.000797 | 4e-06 | N
23-12-18 | 21:04 | ZN15012:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 828 | 0.002245 | 3e-06 | N
24-12-18 | 05:48 | ZN9900:PA2 | URBAN | Asset Failure | LV | 37 | 207 | 0.005182 | 2.5e-05 | N
24-12-18 | 06:46 | ZN3922:PA7 | URBAN | Asset Failure | HV | 1,839 | 107 | 0.13323 | 0.001246 | N
16-12-18 | 19:58 | ZN965:PA8 | URBAN | Asset Failure | LV | 46 | 987 | 0.030771 | 3.1e-05 | Y
24-12-18 | 08:57 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 140 | 0.14752 | 0.001054 | N
16-12-18 | 23:14 | ZN965:PA24 | URBAN | Weather |  | 25 | 1,586 | 0.026873 | 1.7e-05 | Y
24-12-18 | 09:16 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 124 | 0.00052 | 4e-06 | N
18-12-18 | 19:15 | ZN12630:PA10 | SHORT RURAL | Weather |  | 7 | 80 | 0.002357 | 2.9e-05 | N
17-12-18 | 00:27 | ZN965:PA35 | URBAN | Weather |  | 39 | 1,023 | 0.02704 | 2.6e-05 | N
24-12-18 | 10:42 | ZN398:PA15 | URBAN | Other | Other - Arcing | 1 | 257 | 0.000174 | 1e-06 | N
24-12-18 | 11:09 | ZN35400:PA101 | URBAN | Asset Failure | LV | 1 | 230 | 0.000156 | 1e-06 | N
24-12-18 | 12:26 | 213:33774 | URBAN | Other | Other | 1 | 84 | 5.7e-05 | 1e-06 | N
24-12-18 | 13:41 | ZN12630:PA1 | SHORT RURAL | Asset Failure | LV | 8 | 381 | 0.012825 | 3.4e-05 | N
24-12-18 | 14:38 | 523:33501 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 442 | 0.005579 | 1.3e-05 | N
24-12-18 | 14:45 | ZN188:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 50 | 0.001298 | 2.6e-05 | N
24-12-18 | 17:30 | ZN36000:PA2 | SHORT RURAL | Network business | Switching and protection error | 335 | 315 | 0.444 | 0.00141 | N
24-12-18 | 16:36 | 206:34440 | URBAN | Other | Other | 1 | 49 | 3.3e-05 | 1e-06 | N
24-12-18 | 16:55 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 130 | 0.045662 | 0.000351 | N
24-12-18 | 17:20 | ZN2635:PA55 | SHORT RURAL | Asset Failure | LV | 82 | 635 | 0.21909 | 0.000345 | N
24-12-18 | 20:45 | ZN9700:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 29 | 0.000766 | 2.6e-05 | N
24-12-18 | 20:14 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 231 | 0.081115 | 0.000351 | N
24-12-18 | 20:19 | 214:8669 | URBAN | Vegetation | Vegetation Grow In | 111 | 46 | 0.00346 | 7.5e-05 | N
24-12-18 | 21:14 | 206:34432 | URBAN | Animal | Animal impact | 1,163 | 46 | 0.036319 | 0.000788 | N
24-12-18 | 21:30 | ZN965:PA3 | URBAN | Other | Other | 1 | 193 | 0.000131 | 1e-06 | N
25-12-18 | 01:43 | 206:34432 | URBAN | Asset Failure | LV | 1 | 362 | 0.000245 | 1e-06 | N
25-12-18 | 01:55 | ZN9900:PA1 | URBAN | Asset Failure | LV | 40 | 1,245 | 0.033728 | 2.7e-05 | N
25-12-18 | 09:49 | ZN180:PA7 | URBAN | Other | Other - Self Clearing Trigger | 43 | 75 | 0.002193 | 2.9e-05 | N
25-12-18 | 14:03 | ZN3154:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 296 | 0.000201 | 1e-06 | N
25-12-18 | 14:23 | 515:35193 | SHORT RURAL | Asset Failure | HV | 2 | 182 | 0.001531 | 8e-06 | N
25-12-18 | 16:16 | 515:35192 | SHORT RURAL | Overloads |  | 3 | 124 | 0.001565 | 1.3e-05 | N
25-12-18 | 17:49 | ZN2635:PA46 | URBAN | Other | Other | 33 | 51 | 0.001138 | 2.2e-05 | N
25-12-18 | 20:06 | ZN965:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 83 | 5.6e-05 | 1e-06 | N
25-12-18 | 21:14 | ZN2835:PA41 | URBAN | Third Party | Other | 1 | 136 | 9.2e-05 | 1e-06 | N
25-12-18 | 21:32 | ZN15008:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 88 | 0.00155 | 1.8e-05 | N
25-12-18 | 21:19 | ZN965:PA43 | URBAN | Other | Other | 1 | 401 | 0.000271 | 1e-06 | N
25-12-18 | 22:07 | ZN1673:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 892 | 0.000604 | 1e-06 | N
26-12-18 | 05:56 | ZN3155:PA20 | URBAN | Asset Failure | LV | 1 | 399 | 0.00027 | 1e-06 | N
26-12-18 | 06:36 | ZN3425:PA43 | URBAN | Asset Failure | LV | 2 | 478 | 0.000648 | 1e-06 | N
26-12-18 | 07:21 | 205:12210 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 190 | 0.000129 | 1e-06 | N
26-12-18 | 07:53 | ZN2568:PA38 | URBAN | Asset Failure | HV | 767 | 75 | 0.038991 | 0.00052 | N
26-12-18 | 07:53 | ZN2568:PA39 | URBAN | Asset Failure | HV | 866 | 107 | 0.062796 | 0.000587 | N
26-12-18 | 08:40 | ZN15009:PA5 | URBAN | Other | Other - Arcing | 1 | 626 | 0.000425 | 1e-06 | N
26-12-18 | 14:00 | ZN9252:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 243 | 0.000164 | 1e-06 | N
26-12-18 | 15:51 | ZN2196:PA9 | URBAN | Other | Other - Self Clearing Trigger | 1 | 139 | 9.4e-05 | 1e-06 | N
26-12-18 | 16:40 | ZN965:PA13 | URBAN | Other | Other | 2 | 1,010 | 0.001369 | 1e-06 | N
26-12-18 | 17:43 | ZN36800:PA33 | URBAN | Asset Failure | LV | 132 | 1,667 | 0.14915 | 8.9e-05 | N
26-12-18 | 21:31 | ZN2196:PA12 | URBAN | Asset Failure | HV | 6 | 115 | 0.000468 | 4e-06 | N
26-12-18 | 22:35 | ZN12690:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 654 | 0.000443 | 1e-06 | N
26-12-18 | 23:53 | 227:13020 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 3 | 381 | 0.004809 | 1.3e-05 | N
27-12-18 | 07:35 | 511:29878 | SHORT RURAL | Third Party | Other | 1 | 244 | 0.001025 | 4e-06 | N
27-12-18 | 09:07 | 264:81240 | SHORT RURAL | Third Party | Vehicle impact | 1 | 323 | 0.001359 | 4e-06 | N
27-12-18 | 09:53 | ZN2466:PA26 | URBAN | Third Party | Other | 203 | 92 | 0.012647 | 0.000138 | N
14-12-18 | 18:04 | ZN12630:PA3 | SHORT RURAL | Asset Failure | Distribution substation | 8 | 296 | 0.00997 | 3.4e-05 | N
27-12-18 | 10:42 | ZN10999:PA10 | URBAN | Asset Failure | LV | 1 | 468 | 0.000317 | 1e-06 | N
15-12-18 | 09:14 | ZN12630:PA3 | SHORT RURAL | Overloads |  | 253 | 3 | 0.00277 | 0.001065 | Y
27-12-18 | 10:58 | ZN14892:PA16 | URBAN | Other | Other | 1 | 175 | 0.000119 | 1e-06 | N
27-12-18 | 11:17 | 264:81236 | URBAN | Vegetation | Vegetation Blow/Fall In | 72 | 268 | 0.013071 | 4.9e-05 | N
27-12-18 | 12:10 | ZN10993:PA22 | URBAN | Third Party | Vehicle impact | 1 | 200 | 0.000135 | 1e-06 | N
27-12-18 | 12:32 | ZN13000:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 49 | 0.000207 | 4e-06 | N
27-12-18 | 13:11 | ZN398:PA11 | URBAN | Other | Other - Self Clearing Trigger | 16 | 138 | 0.001497 | 1.1e-05 | N
27-12-18 | 14:33 | 238:34144 | URBAN | Other | Other - Self Clearing Trigger | 16 | 1,307 | 0.014163 | 1.1e-05 | N
27-12-18 | 15:31 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 73 | 0.025682 | 0.000351 | N
27-12-18 | 15:43 | 206:34441 | URBAN | Other | Other - Arcing | 1 | 124 | 8.4e-05 | 1e-06 | N
27-12-18 | 16:43 | ZN167:PA1 | URBAN | Third Party | Vehicle impact | 1 | 292 | 0.000198 | 1e-06 | N
27-12-18 | 18:07 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 88 | 0.03091 | 0.000351 | N
27-12-18 | 18:08 | 270:83591 | SHORT RURAL | Other | Other | 1 | 126 | 0.000532 | 4e-06 | N
27-12-18 | 19:54 | 243:80083 | SHORT RURAL | Asset Failure | LV | 1 | 56 | 0.000236 | 4e-06 | N
27-12-18 | 22:40 | ZN14143:PA17 | SHORT RURAL | Other | Other - Self Clearing Trigger | 166 | 1,057 | 0.73813 | 0.000698 | N
27-12-18 | 23:55 | ZN195:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 60 | 124 | 0.005052 | 4.1e-05 | N
28-12-18 | 01:15 | ZN3155:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 405 | 0.000274 | 1e-06 | N
28-12-18 | 02:56 | 205:12210 | URBAN | Animal | Animal impact | 47 | 64 | 0.002038 | 3.2e-05 | N
28-12-18 | 04:03 | ZN180:PA23 | URBAN | Animal | Animal impact | 199 | 40 | 0.005451 | 0.000135 | N
28-12-18 | 04:03 | ZN180:PA29 | URBAN | Animal | Animal impact | 1,195 | 60 | 0.048578 | 0.00081 | N
28-12-18 | 04:03 | ZN180:PA30 | URBAN | Animal | Animal impact | 1,757 | 60 | 0.071423 | 0.00119 | N
28-12-18 | 04:03 | ZN180:PA31 | URBAN | Animal | Animal impact | 1,605 | 60 | 0.065244 | 0.001087 | N
28-12-18 | 04:03 | ZN180:PA33 | URBAN | Animal | Animal impact | 897 | 60 | 0.036464 | 0.000608 | N
28-12-18 | 04:03 | ZN180:PA42 | URBAN | Animal | Animal impact | 1,905 | 60 | 0.07744 | 0.001291 | N
28-12-18 | 04:03 | ZN180:PA43 | URBAN | Animal | Animal impact | 1,197 | 60 | 0.048659 | 0.000811 | N
28-12-18 | 07:26 | ZN15004:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 185 | 0.000125 | 1e-06 | N
28-12-18 | 07:40 | ZN3472:PA20 | URBAN | Other | Other - Self Clearing Trigger | 95 | 74 | 0.004791 | 6.4e-05 | N
28-12-18 | 10:12 | ZN12610:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 52 | 0.002164 | 4.1e-05 | N
28-12-18 | 11:17 | ZN847:PA45 | SHORT RURAL | Asset Failure | LV | 10 | 143 | 0.006017 | 4.2e-05 | N
28-12-18 | 11:26 | ZN35400:PA101 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 118 | 8e-05 | 1e-06 | N
28-12-18 | 12:27 | ZN35800:PA16 | URBAN | Asset Failure | HV | 60 | 93 | 0.003781 | 4.1e-05 | N
28-12-18 | 12:27 | ZN35800:PA7 | URBAN | Asset Failure | HV | 1,164 | 97 | 0.076253 | 0.000789 | N
28-12-18 | 12:47 | ZN3425:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 77 | 5.2e-05 | 1e-06 | N
28-12-18 | 14:40 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 170 | 0.000715 | 4e-06 | N
28-12-18 | 14:50 | ZN2835:PA21 | SHORT RURAL | Other | Other | 1 | 1,150 | 0.004837 | 4e-06 | N
28-12-18 | 14:50 | ZN1285:PA22 | URBAN | Asset Failure | HV | 581 | 57 | 0.022285 | 0.000394 | N
28-12-18 | 15:06 | ZN965:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 45 | 136 | 0.004158 | 3e-05 | N
28-12-18 | 15:08 | ZN965:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 13 | 77 | 0.000676 | 9e-06 | N
28-12-18 | 16:01 | 522:83121 | URBAN | Asset Failure | HV | 309 | 73 | 0.015344 | 0.000209 | N
28-12-18 | 16:20 | ZN847:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,878 | 0.001273 | 1e-06 | N
28-12-18 | 16:22 | ZN965:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 142 | 9.6e-05 | 1e-06 | N
28-12-18 | 17:02 | ZN965:PA20 | URBAN | Asset Failure | HV | 868 | 96 | 0.056288 | 0.000588 | N
28-12-18 | 17:02 | ZN965:PA8 | URBAN | Asset Failure | HV | 999 | 115 | 0.077836 | 0.000677 | N
28-12-18 | 17:05 | ZN4545:PA6 | URBAN | Asset Failure | HV | 1 | 205 | 0.000139 | 1e-06 | N
28-12-18 | 18:12 | 224:80340 | SHORT RURAL | Asset Failure | LV | 28 | 112 | 0.013223 | 0.000118 | N
28-12-18 | 18:58 | ZN9245:PA3 | SHORT RURAL | Asset Failure | HV | 1,188 | 84 | 0.42147 | 0.004999 | N
28-12-18 | 19:36 | ZN1673:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,087 | 89 | 0.065686 | 0.000736 | N
28-12-18 | 19:48 | ZN195:PA11 | URBAN | Network business | Network error | 46 | 64 | 0.002002 | 3.1e-05 | N
28-12-18 | 21:19 | ZN2602:PA29 | URBAN | Asset Failure | LV | 1 | 224 | 0.000151 | 1e-06 | N
28-12-18 | 21:08 | ZN4545:PA6 | URBAN | Asset Failure | HV | 1 | 2,613 | 0.00177 | 1e-06 | N
28-12-18 | 21:45 | ZN12570:PA22 | SHORT RURAL | Asset Failure | LV | 63 | 95 | 0.025205 | 0.000265 | N
28-12-18 | 22:05 | 512:83743 | SHORT RURAL | Asset Failure | LV | 4 | 140 | 0.002356 | 1.7e-05 | N
28-12-18 | 22:41 | 512:83732 | SHORT RURAL | Asset Failure | LV | 1 | 130 | 0.000546 | 4e-06 | N
28-12-18 | 23:13 | ZN847:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,251 | 0.000847 | 1e-06 | N
28-12-18 | 23:18 | ZN195:PA23 | URBAN | Third Party | Other | 35 | 204 | 0.004847 | 2.4e-05 | N
28-12-18 | 23:19 | ZN1673:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 1,140 | 0.020859 | 1.8e-05 | N
28-12-18 | 23:19 | ZN1673:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 70 | 1,141 | 0.054113 | 4.7e-05 | N
28-12-18 | 23:19 | ZN3154:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,141 | 0.004801 | 4e-06 | N
29-12-18 | 01:20 | 523:33501 | SHORT RURAL | Asset Failure | LV | 2 | 155 | 0.001304 | 8e-06 | N
29-12-18 | 00:07 | ZN965:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 173 | 0.003165 | 1.8e-05 | N
29-12-18 | 05:16 | ZN9900:PA5 | URBAN | Asset Failure | HV | 463 | 108 | 0.033879 | 0.000314 | N
29-12-18 | 05:31 | ZN4545:PA31 | URBAN | Asset Failure | LV | 1 | 521 | 0.000353 | 1e-06 | N
29-12-18 | 06:48 | ZN195:PA23 | URBAN | Third Party | Other | 35 | 369 | 0.008758 | 2.4e-05 | N
29-12-18 | 12:01 | ZN690:PA18 | URBAN | Asset Failure | HV | 2 | 39 | 5.3e-05 | 1e-06 | N
29-12-18 | 12:28 | ZN690:PA6 | URBAN | Network business | Network error | 75 | 81 | 0.004139 | 5.1e-05 | N
29-12-18 | 13:13 | ZN14891:PA5 | SHORT RURAL | Other | Other | 2 | 255 | 0.00215 | 8e-06 | N
29-12-18 | 14:19 | ZN10999:PA10 | URBAN | Other | Other - Self Clearing Trigger | 76 | 70 | 0.003621 | 5.1e-05 | N
29-12-18 | 15:21 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 54 | 0.000227 | 4e-06 | N
29-12-18 | 15:37 | ZN2400:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 223 | 0.000151 | 1e-06 | N
29-12-18 | 15:58 | ZN14144:PA10 | SHORT RURAL | Asset Failure | HV | 166 | 116 | 0.080733 | 0.000699 | N
29-12-18 | 16:58 | ZN12600:PA2 | SHORT RURAL | Other | Other | 1 | 64 | 0.00027 | 4e-06 | N
29-12-18 | 17:26 | 214:8665 | URBAN | Other | Other - Arcing | 93 | 53 | 0.003342 | 6.3e-05 | N
29-12-18 | 18:21 | 264:81240 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 162 | 0.000683 | 4e-06 | N
29-12-18 | 18:30 | 265:81651 | SHORT RURAL | Third Party | Vehicle impact | 150 | 342 | 0.21595 | 0.000631 | N
29-12-18 | 18:32 | 238:34137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 21 | 238 | 0.021006 | 8.8e-05 | N
29-12-18 | 19:09 | ZN12570:PA39 | URBAN | Asset Failure | Distribution substation | 91 | 71 | 0.004354 | 6.2e-05 | N
29-12-18 | 20:51 | 513:48059 | SHORT RURAL | Asset Failure | LV | 1 | 114 | 0.00048 | 4e-06 | N
29-12-18 | 20:59 | ZN15006:PA2 | URBAN | Asset Failure | LV | 1 | 155 | 0.000105 | 1e-06 | N
29-12-18 | 21:39 | 515:35198 | SHORT RURAL | Asset Failure | LV | 4 | 156 | 0.002626 | 1.7e-05 | N
29-12-18 | 22:42 | 511:29877 | SHORT RURAL | Asset Failure | LV | 1 | 58 | 0.000244 | 4e-06 | N
29-12-18 | 23:56 | ZN35400:PA52 | URBAN | Vegetation | Vegetation Blow/Fall In | 104 | 73 | 0.00516 | 7e-05 | N
30-12-18 | 01:39 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 703 | 0.24693 | 0.000351 | N
30-12-18 | 02:48 | 217:33610 | URBAN | Animal | Animal impact | 90 | 198 | 0.012101 | 6.1e-05 | N
30-12-18 | 03:03 | ZN14891:PA20 | SHORT RURAL | Other | Other - Arcing | 1 | 510 | 0.002147 | 4e-06 | N
30-12-18 | 06:05 | ZN15012:PA4 | URBAN | Asset Failure | HV | 1,221 | 100 | 0.083059 | 0.000827 | N
30-12-18 | 06:05 | ZN15012:PA8 | URBAN | Asset Failure | HV | 849 | 94 | 0.05407 | 0.000575 | N
30-12-18 | 08:11 | ZN129:PA63 | URBAN | Asset Failure | HV | 707 | 146 | 0.069743 | 0.000479 | N
30-12-18 | 09:52 | ZN3672:PA35 | SHORT RURAL | Asset Failure | LV | 1 | 399 | 0.00168 | 4e-06 | N
30-12-18 | 10:51 | ZN35555:PA2 | URBAN | Network business | Network error | 106 | 108 | 0.007771 | 7.2e-05 | N
30-12-18 | 15:20 | 214:8669 | URBAN | Vegetation | Vegetation Grow In | 111 | 99 | 0.007452 | 7.5e-05 | N
30-12-18 | 14:09 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 71 | 0.003573 | 5e-05 | N
30-12-18 | 16:57 | 520:48172 | SHORT RURAL | Asset Failure | LV | 1 | 201 | 0.000846 | 4e-06 | N
30-12-18 | 18:01 | ZN9900:PA13 | URBAN | Network business | Network error | 33 | 246 | 0.005499 | 2.2e-05 | N
30-12-18 | 18:01 | ZN9900:PA13 | URBAN | Network business | Network error | 51 | 119 | 0.004112 | 3.5e-05 | N
30-12-18 | 21:06 | 524:33570 | SHORT RURAL | Other | Other | 1 | 1,388 | 0.005841 | 4e-06 | N
30-12-18 | 22:10 | ZN847:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 101 | 65 | 0.004448 | 6.8e-05 | N
30-12-18 | 21:30 | ZN1290:PA8 | URBAN | Other | Other | 1 | 494 | 0.000335 | 1e-06 | N
31-12-18 | 02:50 | 205:12205 | URBAN | Asset Failure | HV | 1,217 | 71 | 0.058479 | 0.000825 | N
31-12-18 | 09:51 | ZN35555:PA5 | SHORT RURAL | Network business | Network error | 22 | 219 | 0.02027 | 9.3e-05 | N
31-12-18 | 09:52 | ZN167:PA12 | URBAN | Asset Failure | HV | 1 | 4,418 | 0.002993 | 1e-06 | N
31-12-18 | 09:55 | ZN3472:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 7 | 395 | 0.001873 | 5e-06 | N
31-12-18 | 11:35 | ZN12570:PA34 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 36 | 190 | 0.028769 | 0.000151 | N
31-12-18 | 13:10 | 802:82225 | SHORT RURAL | Other | Other | 1 | 20 | 8.4e-05 | 4e-06 | N
31-12-18 | 11:10 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 319 | 0.001344 | 4e-06 | N
31-12-18 | 11:33 | ZN3425:PA43 | URBAN | Asset Failure | LV | 1 | 237 | 0.00016 | 1e-06 | N
31-12-18 | 15:12 | ZN340:PA8 | URBAN | Network business | Network error | 82 | 313 | 0.017389 | 5.6e-05 | N
31-12-18 | 13:03 | ZN10999:PA11 | URBAN | Other | Other | 1 | 1,395 | 0.000945 | 1e-06 | N
31-12-18 | 19:38 | ZN12690:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,045 | 71 | 0.31222 | 0.004398 | N
31-12-18 | 15:35 | ZN7481:PA14 | URBAN | Asset Failure | HV | 1,399 | 76 | 0.072072 | 0.000948 | N
31-12-18 | 16:17 | ZN195:PA30 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 743 | 29 | 0.090673 | 0.003127 | N
31-12-18 | 17:06 | ZN14892:PA17 | URBAN | Asset Failure | HV | 513 | 73 | 0.025271 | 0.000348 | N
31-12-18 | 17:14 | 223:14399 | SHORT RURAL | Asset Failure | LV | 1 | 1,444 | 0.006075 | 4e-06 | N
31-12-18 | 17:34 | 232:11453 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 78 | 0.00033 | 4e-06 | N
31-12-18 | 18:16 | 507:80925 | SHORT RURAL | Third Party | Other | 1 | 208 | 0.000875 | 4e-06 | N
31-12-18 | 18:15 | 524:33570 | SHORT RURAL | Other | Other | 64 | 30 | 0.00808 | 0.000269 | N
31-12-18 | 19:48 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 897 | 0.011324 | 1.3e-05 | N
31-12-18 | 19:53 | 516:48066 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 2,461 | 0.010358 | 4e-06 | N
31-12-18 | 19:56 | 512:83732 | SHORT RURAL | Other | Other | 855 | 34 | 0.12233 | 0.003598 | N
31-12-18 | 19:56 | 512:83733 | SHORT RURAL | Other | Other | 918 | 34 | 0.13134 | 0.003863 | N
31-12-18 | 19:56 | 512:83734 | SHORT RURAL | Other | Other | 1 | 34 | 0.000143 | 4e-06 | N
31-12-18 | 19:56 | 512:83741 | SHORT RURAL | Other | Other | 827 | 34 | 0.11832 | 0.00348 | N
31-12-18 | 19:56 | 512:83743 | SHORT RURAL | Other | Other | 969 | 34 | 0.13864 | 0.004078 | N
31-12-18 | 20:01 | 243:80081 | SHORT RURAL | Asset Failure | Distribution substation | 116 | 256 | 0.125 | 0.000488 | N
31-12-18 | 19:59 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 91 | 305 | 0.11661 | 0.000383 | N
31-12-18 | 20:17 | ZN1193:PA25 | URBAN | Other | Other - Arcing | 1 | 217 | 0.000147 | 1e-06 | N
31-12-18 | 20:24 | ZN10999:PA36 | URBAN | Asset Failure | LV | 23 | 866 | 0.013492 | 1.6e-05 | N
31-12-18 | 20:43 | 508:82579 | SHORT RURAL | Other | Other | 457 | 166 | 0.32001 | 0.001923 | N
31-12-18 | 20:49 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 326 | 0.01644 | 5e-05 | N
31-12-18 | 20:58 | 511:29878 | SHORT RURAL | Asset Failure | HV | 1 | 352 | 0.001481 | 4e-06 | N
31-12-18 | 20:31 | 512:83743 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 76 | 247 | 0.07889 | 0.00032 | N
31-12-18 | 20:53 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 54 | 169 | 0.038404 | 0.000227 | N
31-12-18 | 21:14 | 522:83124 | URBAN | Other | Other - Self Clearing Trigger | 11 | 546 | 0.004068 | 7e-06 | N
31-12-18 | 21:18 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 19 | 182 | 0.014552 | 8e-05 | N
31-12-18 | 21:36 | 238:34150 | SHORT RURAL | Other | Other - Self Clearing Trigger | 106 | 143 | 0.063638 | 0.000446 | N
31-12-18 | 21:41 | 526:34641 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 709 | 0.011934 | 1.7e-05 | N
31-12-18 | 21:44 | 524:33576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 226 | 0.007608 | 3.4e-05 | N
31-12-18 | 21:50 | 523:33508 | SHORT RURAL | Other | Other - Arcing | 1 | 784 | 0.0033 | 4e-06 | N
31-12-18 | 21:50 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 41 | 153 | 2.2034 | 0.014401 | N
31-12-18 | 21:58 | ZN847:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 64 | 212 | 0.009193 | 4.3e-05 | N
01-01-19 | 08:05 | 526:34633 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 23 | 0.000194 | 8e-06 | N
31-12-18 | 20:15 | 258:80785 | URBAN | Asset Failure | Distribution substation | 77 | 165 | 0.008608 | 5.2e-05 | N
31-12-18 | 22:19 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 351 | 0.002953 | 8e-06 | N
31-12-18 | 22:30 | 532:83309 | URBAN | Other | Other | 1 | 186 | 0.000126 | 1e-06 | N
31-12-18 | 22:49 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 660 | 0.002779 | 4e-06 | N
31-12-18 | 23:19 | 513:48050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 176 | 0.000741 | 4e-06 | N
01-01-19 | 01:58 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 366 | 0.003082 | 8e-06 | N
01-01-19 | 03:03 | ZN965:PA20 | URBAN | Animal | Animal impact | 58 | 151 | 0.005934 | 3.9e-05 | N
01-01-19 | 03:03 | ZN965:PA42 | URBAN | Animal | Animal impact | 1,133 | 152 | 0.11689 | 0.000768 | N
01-01-19 | 05:54 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 81 | 0.000341 | 4e-06 | N
01-01-19 | 06:26 | 238:34150 | SHORT RURAL | Weather |  | 2 | 484 | 0.004074 | 8e-06 | N
01-01-19 | 06:49 | 511:29876 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 336 | 0.009898 | 2.9e-05 | N
01-01-19 | 06:57 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 320 | 0.001348 | 4e-06 | N
01-01-19 | 06:59 | ZN1287:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 92 | 0.002306 | 2.5e-05 | N
01-01-19 | 07:31 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 287 | 0.002415 | 8e-06 | N
01-01-19 | 07:47 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 368 | 0.004646 | 1.3e-05 | N
01-01-19 | 11:23 | 516:48066 | SHORT RURAL | Asset Failure | HV | 1 | 256 | 0.001078 | 4e-06 | N
01-01-19 | 08:27 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 176 | 0.000742 | 4e-06 | N
01-01-19 | 08:38 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 152 | 0.000638 | 4e-06 | N
01-01-19 | 12:03 | 526:34639 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 322 | 0.00271 | 8e-06 | N
01-01-19 | 09:49 | 526:34635 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 156 | 0.000656 | 4e-06 | N
01-01-19 | 09:53 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 297 | 0.001248 | 4e-06 | N
01-01-19 | 07:44 | 514:18137 | SHORT RURAL | Asset Failure | HV | 1 | 1,620 | 0.006817 | 4e-06 | N
01-01-19 | 10:10 | ZN10999:PA38 | URBAN | Other | Other - Self Clearing Trigger | 84 | 96 | 0.005446 | 5.7e-05 | N
01-01-19 | 10:21 | ZN12580:PA16 | URBAN | Asset Failure | Distribution substation | 16 | 69 | 0.00075 | 1.1e-05 | N
01-01-19 | 10:54 | ZN12640:PA4 | URBAN | Other | Other | 1 | 56 | 3.8e-05 | 1e-06 | N
01-01-19 | 12:05 | ZN3672:PA13 | URBAN | Asset Failure | LV | 1 | 735 | 0.000498 | 1e-06 | N
01-01-19 | 12:06 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 234 | 0.000985 | 4e-06 | N
01-01-19 | 12:51 | 522:83124 | URBAN | Other | Other - Self Clearing Trigger | 1 | 69 | 4.7e-05 | 1e-06 | N
01-01-19 | 14:26 | ZN2602:PA15 | URBAN | Asset Failure | LV | 1 | 408 | 0.000277 | 1e-06 | N
01-01-19 | 15:02 | 515:35197 | LONG RURAL | Other | Other - Arcing | 1 | 159 | 0.055725 | 0.000351 | N
01-01-19 | 15:22 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 58 | 0.000488 | 8e-06 | N
01-01-19 | 15:28 | ZN2602:PA15 | URBAN | Asset Failure | LV | 1 | 346 | 0.000235 | 1e-06 | N
01-01-19 | 15:33 | ZN2602:PA15 | URBAN | Asset Failure | LV | 1 | 341 | 0.000231 | 1e-06 | N
01-01-19 | 15:55 | ZN965:PA46 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 190 | 0.004634 | 2.4e-05 | N
01-01-19 | 16:24 | 235:2123 | URBAN | Asset Failure | LV | 70 | 60 | 0.002864 | 4.7e-05 | N
01-01-19 | 16:26 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 134 | 0.000564 | 4e-06 | N
01-01-19 | 17:13 | ZN12640:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 107 | 0.001667 | 1.6e-05 | N
01-01-19 | 18:24 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 126 | 0.00106 | 8e-06 | N
01-01-19 | 19:17 | ZN14891:PA12 | SHORT RURAL | Third Party | Other | 39 | 113 | 0.018545 | 0.000164 | N
01-01-19 | 19:04 | 511:29873 | URBAN | Asset Failure | HV | 1,513 | 85 | 0.08738 | 0.001025 | N
01-01-19 | 19:52 | ZN9252:PA22 | URBAN | Asset Failure | HV | 1,556 | 93 | 0.09839 | 0.001054 | N
01-01-19 | 19:52 | ZN9700:PA20 | URBAN | Asset Failure | HV | 1 | 96 | 6.5e-05 | 1e-06 | N
01-01-19 | 20:26 | 813:89061 | LONG RURAL | Asset Failure | HV | 2 | 239 | 0.1679 | 0.000702 | N
01-01-19 | 21:32 | ZN2400:PA18 | SHORT RURAL | Asset Failure | Distribution substation | 76 | 67 | 0.021583 | 0.00032 | N
01-01-19 | 21:50 | 213:33771 | URBAN | Other | Other | 1 | 22 | 1.5e-05 | 1e-06 | N
01-01-19 | 22:50 | ZN35400:PA68 | URBAN | Asset Failure | LV | 69 | 69 | 0.003244 | 4.7e-05 | N
01-01-19 | 22:41 | ZN195:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 389 | 0.004744 | 1.2e-05 | N
01-01-19 | 22:52 | 814:82291 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 134 | 0.005058 | 3.8e-05 | N
02-01-19 | 00:46 | ZN1673:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 553 | 0.000375 | 1e-06 | N
02-01-19 | 01:36 | ZN15006:PA6 | URBAN | Other | Other - Arcing | 2 | 574 | 0.000778 | 1e-06 | N
20-12-18 | 12:00 | 509:33399 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 190 | 0.0008 | 4e-06 | Y
02-01-19 | 08:13 | ZN12570:PA22 | SHORT RURAL | Other | Other - Arcing | 1 | 196 | 0.000826 | 4e-06 | N
02-01-19 | 08:52 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 153 | 0.000644 | 4e-06 | N
02-01-19 | 09:05 | ZN10997:PA1 | URBAN | Other | Other - Self Clearing Trigger | 39 | 54 | 0.001437 | 2.6e-05 | N
31-12-18 | 17:00 | ZN3472:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 56 | 8 | 0.000304 | 3.8e-05 | N
02-01-19 | 12:00 | ZN2602:PA29 | URBAN | Other | Other | 101 | 826 | 0.056551 | 6.8e-05 | N
02-01-19 | 09:11 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 163 | 0.000686 | 4e-06 | N
02-01-19 | 09:39 | 511:29877 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 28 | 0.000118 | 4e-06 | N
20-12-18 | 19:22 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 1,565 | 0.55048 | 0.000352 | Y
02-01-19 | 10:08 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 17 | 0.000143 | 8e-06 | N
02-01-19 | 11:45 | 526:34637 | SHORT RURAL | Asset Failure | HV | 113 | 19 | 0.009212 | 0.000476 | N
19-12-18 | 17:55 | 810:74054 | LONG RURAL | Asset Failure | HV | 56 | 1,074 | 21.1551 | 0.019698 | N
02-01-19 | 11:15 | 258:80778 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 34 | 2.3e-05 | 1e-06 | N
02-01-19 | 11:17 | 807:74183 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 114 | 0.000481 | 4e-06 | N
20-12-18 | 03:14 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 616 | 0.002593 | 4e-06 | Y
02-01-19 | 11:50 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,360 | 0.005721 | 4e-06 | N
02-01-19 | 13:24 | 526:34635 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 81 | 0.000682 | 8e-06 | N
02-01-19 | 15:18 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 107 | 0.00045 | 4e-06 | N
02-01-19 | 15:51 | ZN3154:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 782 | 66 | 0.034799 | 0.00053 | N
02-01-19 | 15:53 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 102 | 0.001288 | 1.3e-05 | N
02-01-19 | 16:11 | 220:8687 | URBAN | Other | Other | 1 | 83 | 5.6e-05 | 1e-06 | N
02-01-19 | 16:54 | ZN12610:PA18 | URBAN | Weather |  | 1 | 285 | 0.000193 | 1e-06 | N
02-01-19 | 19:43 | ZN12570:PA22 | SHORT RURAL | Other | Other - Arcing | 43 | 77 | 0.013933 | 0.000181 | N
02-01-19 | 19:43 | ZN12580:PA1 | URBAN | Other | Other - Arcing | 19 | 77 | 0.000991 | 1.3e-05 | N
02-01-19 | 21:30 | 813:89055 | SHORT RURAL | Asset Failure | HV | 1 | 80 | 0.000337 | 4e-06 | N
02-01-19 | 20:54 | ZN10994:PA12 | URBAN | Asset Failure | LV | 89 | 46 | 0.002757 | 6e-05 | N
02-01-19 | 21:03 | 511:29873 | URBAN | Asset Failure | Distribution substation | 62 | 46 | 0.001946 | 4.2e-05 | N
02-01-19 | 21:47 | ZN36800:PA49 | URBAN | Asset Failure | LV | 124 | 283 | 0.023742 | 8.4e-05 | N
03-01-19 | 03:30 | ZN931:PA26 | URBAN | Other | Other - Self Clearing Trigger | 81 | 330 | 0.01811 | 5.5e-05 | N
03-01-19 | 05:54 | ZN262:PA32 | URBAN | Asset Failure | LV | 87 | 171 | 0.010053 | 5.9e-05 | N
03-01-19 | 06:02 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 128 | 0.001077 | 8e-06 | N
03-01-19 | 06:15 | 239:82136 | URBAN | Other | Other | 1 | 73 | 5e-05 | 1e-06 | N
03-01-19 | 08:00 | 528:83014 | SHORT RURAL | Third Party | Vehicle impact | 1 | 179 | 0.000753 | 4e-06 | N
03-01-19 | 09:43 | ZN35500:PA18 | URBAN | Other | Other - Self Clearing Trigger | 1 | 106 | 7.2e-05 | 1e-06 | N
03-01-19 | 10:10 | 524:33576 | SHORT RURAL | Other | Other | 1 | 90 | 0.000378 | 4e-06 | N
03-01-19 | 10:11 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 89 | 0.001124 | 1.3e-05 | N
03-01-19 | 10:42 | ZN9700:PA16 | URBAN | Other | Other - Self Clearing Trigger | 31 | 110 | 0.00231 | 2.1e-05 | N
03-01-19 | 10:50 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 150 | 0.000631 | 4e-06 | N
03-01-19 | 11:37 | ZN847:PA45 | SHORT RURAL | Other | Other | 1 | 133 | 0.000561 | 4e-06 | N
03-01-19 | 11:43 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 62 | 0.000259 | 4e-06 | N
21-12-18 | 11:53 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 187 | 0.003148 | 1.7e-05 | N
21-12-18 | 14:35 | 814:82289 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 50 | 0.00021 | 4e-06 | N
21-12-18 | 20:50 | 812:19072 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 48 | 0.000202 | 4e-06 | N
03-01-19 | 12:27 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 188 | 0.005538 | 2.9e-05 | N
03-01-19 | 12:39 | 243:80084 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 31 | 0.000261 | 8e-06 | N
23-12-18 | 11:00 | 516:48065 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 115 | 0.000484 | 4e-06 | N
03-01-19 | 15:01 | 230:81432 | SHORT RURAL | Asset Failure | LV | 23 | 201 | 0.019454 | 9.7e-05 | N
03-01-19 | 14:38 | 810:74054 | LONG RURAL | Asset Failure | Distribution substation | 1 | 371 | 0.13034 | 0.000351 | N
03-01-19 | 14:53 | 243:80080 | SHORT RURAL | Other | Other | 1 | 95 | 0.000399 | 4e-06 | N
03-01-19 | 15:15 | ZN12630:PA1 | SHORT RURAL | Asset Failure | HV | 160 | 20 | 0.013466 | 0.000673 | N
03-01-19 | 17:17 | ZN12630:PA1 | SHORT RURAL | Asset Failure | HV | 173 | 22 | 0.01584 | 0.000728 | N
03-01-19 | 18:04 | ZN342:PA16 | URBAN | Asset Failure | HV | 1,014 | 64 | 0.043679 | 0.000687 | N
03-01-19 | 18:04 | ZN342:PA24 | URBAN | Asset Failure | HV | 45 | 53 | 0.001616 | 3e-05 | N
03-01-19 | 18:30 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.000379 | 4e-06 | N
03-01-19 | 19:24 | ZN12600:PA2 | SHORT RURAL | Asset Failure | LV | 1 | 291 | 0.001223 | 4e-06 | N
03-01-19 | 19:34 | ZN12600:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 857 | 37 | 0.13344 | 0.003606 | N
03-01-19 | 19:48 | 258:80778 | URBAN | Other | Other | 1 | 172 | 0.000116 | 1e-06 | N
03-01-19 | 20:14 | ZN129:PA40 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 27 | 1.8e-05 | 1e-06 | N
03-01-19 | 20:52 | ZN1287:PA24 | URBAN | Asset Failure | HV | 558 | 143 | 0.05413 | 0.000378 | N
03-01-19 | 21:00 | ZN2196:PA25 | URBAN | Other | Other - Self Clearing Trigger | 1 | 146 | 9.9e-05 | 1e-06 | N
03-01-19 | 22:01 | ZN15005:PA10 | URBAN | Asset Failure | Subtransmission | 752 | 163 | 0.083048 | 0.000509 | N
03-01-19 | 22:01 | ZN15005:PA12 | URBAN | Asset Failure | Subtransmission | 1,445 | 163 | 0.15958 | 0.000979 | N
03-01-19 | 22:01 | ZN15005:PA2 | URBAN | Asset Failure | Subtransmission | 1,679 | 180 | 0.20468 | 0.001138 | N
03-01-19 | 22:01 | ZN15005:PA4 | URBAN | Asset Failure | Subtransmission | 1,233 | 162 | 0.13533 | 0.000835 | N
03-01-19 | 22:01 | ZN15005:PA6 | URBAN | Asset Failure | Subtransmission | 1,271 | 163 | 0.14036 | 0.000861 | N
03-01-19 | 22:01 | ZN15005:PA8 | URBAN | Asset Failure | Subtransmission | 1,585 | 163 | 0.17504 | 0.001074 | N
04-01-19 | 23:07 | ZN15006:PA13 | URBAN | Asset Failure | Distribution substation | 97 | 66 | 0.004338 | 6.6e-05 | N
03-01-19 | 23:42 | ZN1673:PA7 | URBAN | Other | Other - Self Clearing Trigger | 1,029 | 109 | 0.075841 | 0.000697 | N
03-01-19 | 23:42 | ZN3154:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 91 | 0.000383 | 4e-06 | N
04-01-19 | 01:55 | ZN4545:PA31 | URBAN | Other | Other - Self Clearing Trigger | 3,024 | 97 | 0.19874 | 0.002049 | N
04-01-19 | 02:14 | ZN4545:PA31 | URBAN | Network business | Network error | 81 | 341 | 0.018714 | 5.5e-05 | N
04-01-19 | 02:14 | ZN4545:PA40 | URBAN | Network business | Network error | 48 | 326 | 0.010602 | 3.3e-05 | N
04-01-19 | 03:22 | ZN12650:PA1 | SHORT RURAL | Third Party | Vehicle impact | 23 | 238 | 0.023036 | 9.7e-05 | N
04-01-19 | 03:22 | ZN12650:PA1 | SHORT RURAL | Third Party | Vehicle impact | 1 | 457 | 0.001925 | 4e-06 | N
27-12-18 | 09:00 | 511:29878 | SHORT RURAL | Third Party | Other | 1 | 100 | 0.000421 | 4e-06 | N
04-01-19 | 07:25 | 812:19072 | SHORT RURAL | Animal | Other | 41 | 68 | 0.011733 | 0.000173 | N
04-01-19 | 09:20 | ZN3472:PA34 | URBAN | Asset Failure | LV | 12 | 324 | 0.002634 | 8e-06 | N
04-01-19 | 10:57 | 813:89062 | SHORT RURAL | Asset Failure | HV | 1 | 78 | 0.000328 | 4e-06 | N
04-01-19 | 11:20 | 515:35197 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 85 | 0.029844 | 0.000351 | N
04-01-19 | 11:28 | ZN2568:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 108 | 7.3e-05 | 1e-06 | N
04-01-19 | 13:02 | 264:81244 | SHORT RURAL | Other | Other | 1 | 123 | 0.000519 | 4e-06 | N
04-01-19 | 13:25 | 202:34259 | URBAN | Third Party | Other | 8 | 10 | 5.4e-05 | 5e-06 | N
01-01-19 | 07:30 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 20 | 8.4e-05 | 4e-06 | N
01-01-19 | 08:15 | 507:80914 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 15 | 0.000252 | 1.7e-05 | N
01-01-19 | 10:00 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 20 | 0.000337 | 1.7e-05 | N
04-01-19 | 13:56 | 222:33597 | URBAN | Other | Other | 1 | 43 | 2.9e-05 | 1e-06 | N
04-01-19 | 14:50 | 532:83309 | URBAN | Asset Failure | HV | 16 | 45 | 0.000488 | 1.1e-05 | N
31-12-18 | 07:57 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,553 | 0.006535 | 4e-06 | N
31-12-18 | 07:57 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,553 | 0.006535 | 4e-06 | N
04-01-19 | 15:59 | ZN35800:PA2 | URBAN | Third Party | Vehicle impact | 1 | 121 | 8.2e-05 | 1e-06 | N
04-01-19 | 18:18 | ZN4545:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 86 | 0.002215 | 2.6e-05 | N
04-01-19 | 23:35 | 223:14395 | SHORT RURAL | Asset Failure | LV | 5 | 20 | 0.000421 | 2.1e-05 | N
04-01-19 | 19:14 | 806:82662 | SHORT RURAL | Asset Failure | HV | 34 | 390 | 0.055849 | 0.000143 | N
05-01-19 | 10:20 | 509:33395 | LONG RURAL | Other | Other | 11 | 75 | 0.28978 | 0.003864 | Y
04-01-19 | 19:43 | 261:81879 | URBAN | Other | Other | 1 | 178 | 0.000121 | 1e-06 | N
04-01-19 | 19:51 | ZN15004:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 63 | 134 | 0.00572 | 4.3e-05 | N
04-01-19 | 20:01 | ZN3155:PA33 | URBAN | Asset Failure | LV | 58 | 76 | 0.002987 | 3.9e-05 | N
04-01-19 | 20:42 | 514:18137 | SHORT RURAL | Asset Failure | LV | 3 | 108 | 0.001363 | 1.3e-05 | N
05-01-19 | 05:49 | ZN12620:PA1 | SHORT RURAL | Other | Other - Arcing | 23 | 485 | 0.046943 | 9.7e-05 | Y
05-01-19 | 07:27 | ZN3922:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 392 | 0.000266 | 1e-06 | Y
05-01-19 | 09:13 | ZN15014:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,025 | 109 | 0.075519 | 0.000694 | Y
05-01-19 | 09:50 | ZN12650:PA10 | URBAN | Asset Failure | HV | 699 | 119 | 0.056497 | 0.000474 | Y
05-01-19 | 10:10 | ZN1287:PA12 | URBAN | Other | Other - Arcing | 1 | 697 | 0.000472 | 1e-06 | Y
05-01-19 | 10:12 | ZN15010:PA26 | SHORT RURAL | Other | Other - Arcing | 1 | 586 | 0.002465 | 4e-06 | Y
05-01-19 | 10:22 | 222:33601 | SHORT RURAL | Asset Failure | HV | 781 | 100 | 0.32853 | 0.003287 | Y
05-01-19 | 04:51 | ZN13000:PA5 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 17 | 559 | 0.039991 | 7.2e-05 | Y
05-01-19 | 10:54 | 235:8684 | SHORT RURAL | Asset Failure | HV | 120 | 74 | 0.03723 | 0.000505 | Y
05-01-19 | 12:41 | ZN9252:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 370 | 0.00025 | 1e-06 | Y
05-01-19 | 13:05 | ZN3425:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 83 | 155 | 0.008689 | 5.6e-05 | Y
05-01-19 | 13:12 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 339 | 0.00023 | 1e-06 | Y
05-01-19 | 14:04 | ZN9035:PA4 | URBAN | Asset Failure | LV | 1 | 287 | 0.000195 | 1e-06 | Y
05-01-19 | 15:00 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 50 | 0.000209 | 4e-06 | Y
05-01-19 | 15:05 | 233:82812 | SHORT RURAL | Other | Other - Self Clearing Trigger | 13 | 70 | 0.00383 | 5.5e-05 | Y
05-01-19 | 15:07 | 223:14394 | URBAN | Other | Other | 1 | 82 | 5.6e-05 | 1e-06 | Y
05-01-19 | 15:18 | 523:33501 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 2 | 74 | 0.000623 | 8e-06 | Y
05-01-19 | 15:24 | 417:80491 | SHORT RURAL | Other | Bushfire | 6 | 393 | 0.009923 | 2.5e-05 | Y
05-01-19 | 15:26 | ZN1850:PA32 | URBAN | Weather |  | 837 | 80 | 0.045366 | 0.000567 | Y
05-01-19 | 15:26 | ZN1850:PA40 | URBAN | Weather |  | 913 | 81 | 0.050104 | 0.000619 | Y
05-01-19 | 16:18 | ZN3922:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 71 | 282 | 0.013548 | 4.8e-05 | Y
05-01-19 | 17:27 | ZN1290:PA10 | URBAN | Weather |  | 36 | 72 | 0.001756 | 2.4e-05 | Y
05-01-19 | 17:27 | ZN1290:PA11 | URBAN | Weather |  | 1,191 | 72 | 0.058097 | 0.000807 | Y
05-01-19 | 17:27 | ZN1290:PA12 | URBAN | Weather |  | 1,042 | 86 | 0.060713 | 0.000706 | Y
05-01-19 | 17:27 | ZN1290:PA13 | URBAN | Weather |  | 158 | 72 | 0.007707 | 0.000107 | Y
05-01-19 | 17:27 | ZN1290:PA16 | URBAN | Weather |  | 22 | 72 | 0.001073 | 1.5e-05 | Y
05-01-19 | 17:27 | ZN1290:PA17 | URBAN | Weather |  | 178 | 72 | 0.008683 | 0.000121 | Y
05-01-19 | 17:27 | ZN1290:PA8 | URBAN | Weather |  | 712 | 72 | 0.034732 | 0.000482 | Y
05-01-19 | 17:27 | ZN1290:PA9 | URBAN | Weather |  | 1,259 | 83 | 0.070797 | 0.000853 | Y
05-01-19 | 15:43 | ZN847:PA22 | URBAN | Asset Failure | HV | 352 | 113 | 0.026875 | 0.000238 | Y
05-01-19 | 16:04 | ZN12650:PA6 | URBAN | Other | Other - Self Clearing Trigger | 1,084 | 110 | 0.080786 | 0.000734 | Y
05-01-19 | 16:16 | ZN9245:PA13 | URBAN | Other | Other | 42 | 248 | 0.007071 | 2.8e-05 | Y
05-01-19 | 16:23 | ZN12620:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 28 | 362 | 0.042655 | 0.000118 | Y
05-01-19 | 18:01 | ZN12620:PA7 | URBAN | Other | Other - Self Clearing Trigger | 78 | 193 | 0.010222 | 5.3e-05 | Y
05-01-19 | 16:29 | ZN12620:PA10 | SHORT RURAL | Weather |  | 47 | 196 | 0.038701 | 0.000198 | Y
05-01-19 | 16:42 | ZN80:PA31 | URBAN | Weather |  | 60 | 68 | 0.002759 | 4.1e-05 | Y
05-01-19 | 16:44 | ZN12620:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 31 | 2.1e-05 | 1e-06 | Y
05-01-19 | 16:44 | ZN12620:PA11 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,080 | 0.004547 | 4e-06 | Y
05-01-19 | 17:04 | 206:34441 | URBAN | Other | Other - Self Clearing Trigger | 112 | 36 | 0.002718 | 7.6e-05 | Y
05-01-19 | 17:06 | ZN15005:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 62 | 4.2e-05 | 1e-06 | Y
05-01-19 | 17:07 | ZN10998:PA1 | SHORT RURAL | Weather |  | 9 | 200 | 0.007592 | 3.8e-05 | Y
05-01-19 | 17:07 | ZN10998:PA10 | URBAN | Weather |  | 2,008 | 199 | 0.27073 | 0.00136 | Y
05-01-19 | 17:07 | ZN10998:PA13 | URBAN | Weather |  | 1,251 | 67 | 0.056786 | 0.000848 | Y
05-01-19 | 17:07 | ZN10998:PA16 | SHORT RURAL | Weather |  | 628 | 68 | 0.17971 | 0.002643 | Y
05-01-19 | 17:07 | ZN10998:PA32 | SHORT RURAL | Weather |  | 1,295 | 204 | 1.1118 | 0.00545 | Y
05-01-19 | 17:07 | ZN10998:PA8 | URBAN | Weather |  | 1,034 | 212 | 0.14852 | 0.000701 | Y
05-01-19 | 17:07 | ZN10998:PA9 | URBAN | Weather |  | 797 | 199 | 0.10745 | 0.00054 | Y
05-01-19 | 17:10 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 124 | 0.000523 | 4e-06 | Y
05-01-19 | 17:17 | ZN9534:PA11 | URBAN | Weather |  | 234 | 127 | 0.020085 | 0.000159 | Y
05-01-19 | 17:23 | ZN12610:PA13 | SHORT RURAL | Other | Other | 1 | 1,026 | 0.004318 | 4e-06 | Y
05-01-19 | 17:37 | 202:34254 | URBAN | Asset Failure | LV | 84 | 208 | 0.011821 | 5.7e-05 | Y
05-01-19 | 17:43 | ZN12620:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,277 | 0.005372 | 4e-06 | Y
05-01-19 | 18:03 | ZN3472:PA11 | URBAN | Weather |  | 168 | 76 | 0.00865 | 0.000114 | Y
05-01-19 | 18:03 | ZN3472:PA22 | URBAN | Weather |  | 877 | 76 | 0.045157 | 0.000594 | Y
05-01-19 | 18:09 | ZN35900:PA23 | SHORT RURAL | Other | Other - Arcing | 1 | 261 | 0.001097 | 4e-06 | Y
05-01-19 | 18:46 | ZN847:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 64 | 149 | 0.006461 | 4.3e-05 | Y
05-01-19 | 18:28 | ZN35400:PA85 | URBAN | Vegetation | Vegetation Blow/Fall In | 72 | 152 | 0.007415 | 4.9e-05 | Y
05-01-19 | 18:16 | ZN35500:PA24 | URBAN | Asset Failure | HV | 2,075 | 176 | 0.24686 | 0.001406 | Y
05-01-19 | 18:16 | ZN35500:PA28 | URBAN | Asset Failure | HV | 366 | 394 | 0.097699 | 0.000248 | Y
05-01-19 | 18:16 | ZN4545:PA4 | URBAN | Asset Failure | HV | 2 | 188 | 0.000255 | 1e-06 | Y
05-01-19 | 18:23 | ZN35900:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 166 | 0.004055 | 2.4e-05 | Y
05-01-19 | 21:42 | ZN690:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 100 | 18 | 0.00122 | 6.8e-05 | Y
05-01-19 | 18:34 | ZN3154:PA16 | URBAN | Other | Other - Self Clearing Trigger | 1,001 | 103 | 0.069837 | 0.000678 | Y
05-01-19 | 18:37 | 222:33601 | SHORT RURAL | Other | Other | 1 | 47 | 0.000199 | 4e-06 | Y
05-01-19 | 19:01 | ZN1193:PA12 | URBAN | Network business | Network error | 25 | 183 | 0.003105 | 1.7e-05 | Y
05-01-19 | 19:21 | ZN690:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 12 | 1,403 | 0.011409 | 8e-06 | Y
05-01-19 | 19:21 | ZN690:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 1,403 | 0.041834 | 3e-05 | Y
05-01-19 | 19:14 | ZN12650:PA1 | SHORT RURAL | Weather |  | 1,715 | 474 | 3.4224 | 0.007217 | Y
05-01-19 | 19:14 | ZN12650:PA13 | SHORT RURAL | Weather |  | 1,813 | 467 | 3.563 | 0.00763 | Y
05-01-19 | 19:17 | 270:83593 | SHORT RURAL | Asset Failure | LV | 1 | 281 | 0.001184 | 4e-06 | Y
05-01-19 | 18:21 | ZN35500:PA28 | URBAN | Network business | Network error | 55 | 368 | 0.01373 | 3.7e-05 | Y
05-01-19 | 18:21 | ZN4545:PA4 | URBAN | Network business | Network error | 46 | 369 | 0.0115 | 3.1e-05 | Y
05-01-19 | 19:28 | 270:83593 | SHORT RURAL | Asset Failure | LV | 1 | 271 | 0.001141 | 4e-06 | Y
05-01-19 | 19:27 | ZN12610:PA20 | SHORT RURAL | Other | Other - Self Clearing Trigger | 907 | 181 | 0.69268 | 0.003817 | Y
05-01-19 | 19:27 | ZN12610:PA23 | URBAN | Other | Other - Self Clearing Trigger | 32 | 209 | 0.004531 | 2.2e-05 | Y
05-01-19 | 19:41 | ZN14891:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 8 | 304 | 0.010234 | 3.4e-05 | Y
05-01-19 | 19:43 | 257:82006 | URBAN | Other | Other | 1 | 736 | 0.000498 | 1e-06 | Y
05-01-19 | 19:48 | 228:7487 | URBAN | Third Party | Other | 1 | 59 | 4e-05 | 1e-06 | Y
05-01-19 | 19:47 | 233:82812 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 269 | 210 | 0.23772 | 0.001132 | Y
05-01-19 | 19:59 | 235:2124 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 34 | 2.3e-05 | 1e-06 | Y
05-01-19 | 19:58 | ZN12630:PA3 | SHORT RURAL | Asset Failure | HV | 71 | 238 | 0.071149 | 0.000299 | Y
05-01-19 | 20:14 | 214:8665 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 115 | 7.8e-05 | 1e-06 | Y
05-01-19 | 20:19 | ZN2635:PA43 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 29 | 91 | 0.011106 | 0.000122 | Y
05-01-19 | 20:20 | 224:80337 | URBAN | Third Party | Other | 1 | 197 | 0.000134 | 1e-06 | Y
05-01-19 | 20:22 | ZN2568:PA26 | URBAN | Other | Other - Arcing | 1 | 183 | 0.000124 | 1e-06 | Y
05-01-19 | 20:25 | ZN2310:PA14 | URBAN | Other | Other | 1 | 1,201 | 0.000814 | 1e-06 | Y
05-01-19 | 20:32 | ZN2635:PA31 | URBAN | Network business | Network error | 12 | 145 | 0.001179 | 8e-06 | Y
05-01-19 | 20:39 | ZN3672:PA46 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 320 | 0.000217 | 1e-06 | Y
05-01-19 | 20:40 | ZN2568:PA26 | URBAN | Other | Other - Arcing | 1 | 165 | 0.000112 | 1e-06 | Y
05-01-19 | 20:55 | ZN12620:PA8 | SHORT RURAL | Other | Other | 1 | 810 | 0.003407 | 4e-06 | Y
05-01-19 | 21:00 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 885 | 0.93256 | 0.001054 | Y
05-01-19 | 21:34 | ZN12610:PA17 | URBAN | Third Party | Vehicle impact | 1 | 1,019 | 0.000691 | 1e-06 | Y
05-01-19 | 22:11 | ZN12630:PA1 | SHORT RURAL | Asset Failure | HV | 318 | 684 | 0.91597 | 0.001338 | Y
05-01-19 | 22:23 | ZN2310:PA23 | URBAN | Asset Failure | HV | 1,573 | 145 | 0.15462 | 0.001066 | Y
05-01-19 | 22:31 | ZN15014:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 54 | 209 | 0.007646 | 3.7e-05 | Y
05-01-19 | 21:56 | ZN14144:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 11 | 664 | 0.030737 | 4.6e-05 | Y
05-01-19 | 22:47 | 807:74184 | SHORT RURAL | Weather |  | 1 | 134 | 0.000563 | 4e-06 | Y
06-01-19 | 08:18 | 238:34141 | SHORT RURAL | Asset Failure | HV | 7 | 192 | 0.005656 | 2.9e-05 | N
05-01-19 | 22:54 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,056 | 0.004443 | 4e-06 | Y
05-01-19 | 22:55 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,054 | 0.004437 | 4e-06 | Y
05-01-19 | 22:56 | ZN35800:PA2 | URBAN | Network business | Network error | 76 | 94 | 0.004819 | 5.1e-05 | Y
05-01-19 | 23:03 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,046 | 0.004403 | 4e-06 | Y
05-01-19 | 23:15 | ZN12660:PA8 | URBAN | Weather |  | 1,298 | 121 | 0.10636 | 0.000879 | Y
06-01-19 | 00:22 | ZN10999:PA32 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 764 | 0.000518 | 1e-06 | N
06-01-19 | 01:55 | ZN15013:PA10 | SHORT RURAL | Other | Other | 1 | 611 | 0.002573 | 4e-06 | N
06-01-19 | 03:01 | ZN15013:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 486 | 0.020458 | 4.2e-05 | N
06-01-19 | 04:06 | 232:11454 | SHORT RURAL | Animal | Animal impact | 140 | 169 | 0.09942 | 0.000589 | N
06-01-19 | 06:13 | 257:81999 | URBAN | Other | Other | 1 | 68 | 4.6e-05 | 1e-06 | N
06-01-19 | 06:15 | ZN9700:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 604 | 0.000409 | 1e-06 | N
06-01-19 | 08:00 | 513:48050 | SHORT RURAL | Third Party | Vehicle impact | 71 | 160 | 0.047806 | 0.000299 | N
06-01-19 | 06:42 | ZN9252:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 467 | 0.000317 | 1e-06 | N
06-01-19 | 07:30 | 807:74179 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 110 | 0.000463 | 4e-06 | N
06-01-19 | 07:34 | 243:80083 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 246 | 0.001035 | 4e-06 | N
06-01-19 | 08:26 | ZN12620:PA7 | URBAN | Other | Other | 1 | 63 | 4.3e-05 | 1e-06 | N
06-01-19 | 08:34 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 126 | 0.002121 | 1.7e-05 | N
06-01-19 | 08:38 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 162 | 0.001363 | 8e-06 | N
06-01-19 | 08:54 | 222:33596 | URBAN | Other | Other | 1 | 77 | 5.2e-05 | 1e-06 | N
06-01-19 | 09:19 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 413 | 0.001738 | 4e-06 | N
06-01-19 | 13:09 | 513:48056 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 15 | 203 | 0.012814 | 6.3e-05 | N
06-01-19 | 14:15 | ZN14891:PA12 | SHORT RURAL | Asset Failure | HV | 473 | 215 | 0.42796 | 0.00199 | N
06-01-19 | 16:08 | ZN14892:PA12 | URBAN | Asset Failure | LV | 35 | 246 | 0.00584 | 2.4e-05 | N
06-01-19 | 16:18 | ZN9245:PA10 | URBAN | Asset Failure | LV | 1 | 313 | 0.000212 | 1e-06 | N
06-01-19 | 17:22 | ZN36800:PA40 | URBAN | Asset Failure | LV | 1 | 315 | 0.000213 | 1e-06 | N
06-01-19 | 18:56 | 802:82225 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 184 | 0.000774 | 4e-06 | N
06-01-19 | 19:29 | 214:8666 | URBAN | Asset Failure | LV | 1 | 529 | 0.000358 | 1e-06 | N
06-01-19 | 20:34 | 261:81870 | URBAN | Asset Failure | HV | 157 | 26 | 0.002766 | 0.000106 | N
06-01-19 | 22:12 | 220:8689 | URBAN | Other | Other | 1 | 152 | 0.000103 | 1e-06 | N
06-01-19 | 20:43 | ZN187:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 931 | 0.000631 | 1e-06 | N
06-01-19 | 20:55 | 220:8689 | URBAN | Other | Other | 1 | 229 | 0.000155 | 1e-06 | N
06-01-19 | 21:40 | 261:81870 | URBAN | Asset Failure | HV | 104 | 275 | 0.019358 | 7e-05 | N
06-01-19 | 21:55 | 228:7487 | URBAN | Other | Other | 1 | 327 | 0.000221 | 1e-06 | N
06-01-19 | 21:58 | 220:8689 | URBAN | Other | Other | 1 | 166 | 0.000112 | 1e-06 | N
07-01-19 | 02:46 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 219 | 0.004887 | 2.2e-05 | N
07-01-19 | 05:07 | ZN2310:PA4 | URBAN | Asset Failure | HV | 2,985 | 94 | 0.19046 | 0.002022 | N
07-01-19 | 07:26 | ZN12660:PA16 | URBAN | Other | Other - Arcing | 1 | 363 | 0.000246 | 1e-06 | N
07-01-19 | 08:05 | 811:74234 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 8 | 270 | 0.009089 | 3.4e-05 | N
07-01-19 | 08:40 | ZN10994:PA4 | URBAN | Asset Failure | LV | 90 | 70 | 0.004298 | 6.1e-05 | N
07-01-19 | 09:00 | ZN12620:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 159 | 0.000108 | 1e-06 | N
07-01-19 | 09:30 | ZN12620:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 800 | 0.003366 | 4e-06 | N
07-01-19 | 10:12 | ZN12610:PA16 | URBAN | Asset Failure | LV | 1 | 408 | 0.000276 | 1e-06 | N
07-01-19 | 10:44 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 256 | 0.001076 | 4e-06 | N
07-01-19 | 12:07 | 235:8684 | SHORT RURAL | Asset Failure | LV | 1 | 1,523 | 0.006409 | 4e-06 | N
17-12-18 | 08:43 | ZN965:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 4,427 | 0.003 | 1e-06 | N
17-12-18 | 00:27 | ZN965:PA35 | URBAN | Weather |  | 59 | 1,558 | 0.062299 | 4e-05 | N
17-12-18 | 08:45 | ZN965:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 4,425 | 0.002999 | 1e-06 | N
07-01-19 | 12:05 | 812:19066 | SHORT RURAL | Other | Other | 1 | 175 | 0.000734 | 4e-06 | N
07-01-19 | 12:23 | ZN1193:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 107 | 37 | 0.002682 | 7.2e-05 | N
07-01-19 | 12:51 | ZN35555:PA17 | URBAN | Other | Other - Self Clearing Trigger | 1 | 128 | 8.7e-05 | 1e-06 | N
02-01-19 | 14:00 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 133 | 0.001119 | 8e-06 | N
07-01-19 | 13:02 | ZN2466:PA21 | URBAN | Third Party | Other | 3 | 77 | 0.000157 | 2e-06 | N
07-01-19 | 13:02 | ZN2466:PA27 | URBAN | Third Party | Other | 233 | 69 | 0.010942 | 0.000158 | N
07-01-19 | 13:26 | ZN2466:PA20 | URBAN | Network business | Network error | 83 | 53 | 0.002972 | 5.6e-05 | N
05-01-19 | 15:34 | ZN1290:PA9 | URBAN | Weather |  | 68 | 112 | 0.00516 | 4.6e-05 | Y
07-01-19 | 16:49 | ZN8000:PA38 | URBAN | Asset Failure | HV | 97 | 54 | 0.003535 | 6.6e-05 | N
07-01-19 | 19:35 | ZN36200:PA8 | SHORT RURAL | Asset Failure | HV | 72 | 60 | 0.018177 | 0.000303 | N
07-01-19 | 20:55 | ZN12570:PA37 | SHORT RURAL | Asset Failure | LV | 58 | 95 | 0.023136 | 0.000244 | N
08-01-19 | 03:51 | ZN398:PA2 | URBAN | Other | Other - Arcing | 1 | 309 | 0.000209 | 1e-06 | N
08-01-19 | 06:05 | ZN2310:PA14 | URBAN | Asset Failure | LV | 1 | 400 | 0.000271 | 1e-06 | N
08-01-19 | 07:45 | ZN12620:PA10 | SHORT RURAL | Other | Other | 1 | 52 | 0.000218 | 4e-06 | N
08-01-19 | 09:24 | ZN14143:PA12 | SHORT RURAL | Asset Failure | HV | 1,325 | 116 | 0.64428 | 0.005575 | N
04-01-19 | 10:00 | 513:48059 | SHORT RURAL | Third Party | Other | 3 | 75 | 0.000947 | 1.3e-05 | N
08-01-19 | 10:42 | ZN10994:PA1 | URBAN | Third Party | Vehicle impact | 1 | 227 | 0.000154 | 1e-06 | N
05-01-19 | 22:23 | ZN35800:PA15 | URBAN | Network business | Network error | 37 | 252 | 0.006317 | 2.5e-05 | Y
06-01-19 | 04:48 | ZN2310:PA23 | URBAN | Network business | Switching and protection error | 59 | 32 | 0.001279 | 4e-05 | N
08-01-19 | 12:06 | ZN2310:PA23 | URBAN | Other | Other - Self Clearing Trigger | 31 | 323 | 0.006791 | 2.1e-05 | N
08-01-19 | 12:32 | ZN10998:PA32 | SHORT RURAL | Asset Failure | LV | 1 | 159 | 0.000667 | 4e-06 | N
08-01-19 | 13:09 | ZN931:PA11 | URBAN | Other | Other | 141 | 160 | 0.01531 | 9.6e-05 | N
08-01-19 | 13:16 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 76 | 4 | 0.001279 | 0.00032 | N
08-01-19 | 13:30 | ZN15014:PA22 | URBAN | Asset Failure | LV | 1 | 380 | 0.000257 | 1e-06 | N
07-01-19 | 13:45 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 10 | 4.2e-05 | 4e-06 | N
07-01-19 | 14:00 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 10 | 4.2e-05 | 4e-06 | N
08-01-19 | 17:10 | ZN9035:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 59 | 25 | 0.000999 | 4e-05 | N
08-01-19 | 15:10 | ZN1673:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 157 | 0.000638 | 4e-06 | N
08-01-19 | 15:46 | ZN12620:PA3 | URBAN | Other | Other - Self Clearing Trigger | 1 | 197 | 0.000133 | 1e-06 | N
08-01-19 | 17:13 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 137 | 0.000576 | 4e-06 | N
08-01-19 | 18:15 | 526:34637 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 219 | 0.000922 | 4e-06 | N
08-01-19 | 19:01 | 257:81999 | URBAN | Asset Failure | LV | 102 | 84 | 0.005805 | 6.9e-05 | N
08-01-19 | 19:16 | ZN3155:PA31 | URBAN | Asset Failure | Distribution substation | 1 | 44 | 3e-05 | 1e-06 | N
08-01-19 | 20:17 | ZN9035:PA7 | URBAN | Asset Failure | LV | 17 | 332 | 0.003824 | 1.2e-05 | N
08-01-19 | 20:16 | ZN36100:PA13 | URBAN | Asset Failure | HV | 502 | 50 | 0.017162 | 0.00034 | N
08-01-19 | 21:16 | 228:7490 | URBAN | Third Party | Vehicle impact | 1,450 | 41 | 0.040693 | 0.000982 | N
08-01-19 | 21:53 | ZN2635:PA31 | URBAN | Asset Failure | HV | 2,070 | 82 | 0.11504 | 0.001402 | N
08-01-19 | 21:53 | ZN965:PA35 | URBAN | Asset Failure | HV | 1 | 94 | 6.4e-05 | 1e-06 | N
08-01-19 | 22:18 | ZN3425:PA28 | SHORT RURAL | Animal | Animal impact | 642 | 82 | 0.22151 | 0.002701 | N
08-01-19 | 22:18 | ZN3425:PA33 | URBAN | Animal | Animal impact | 461 | 82 | 0.025612 | 0.000312 | N
09-01-19 | 05:37 | ZN15008:PA1 | URBAN | Asset Failure | LV | 21 | 293 | 0.004169 | 1.4e-05 | N
09-01-19 | 06:55 | ZN9118:PA15 | URBAN | Asset Failure | HV | 1 | 77 | 5.2e-05 | 1e-06 | N
09-01-19 | 06:55 | ZN9118:PA22 | URBAN | Asset Failure | HV | 1,453 | 80 | 0.078604 | 0.000984 | N
09-01-19 | 10:33 | ZN129:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 122 | 0.005042 | 4.1e-05 | N
09-01-19 | 07:41 | ZN180:PA10 | URBAN | Third Party | Other | 105 | 49 | 0.003486 | 7.1e-05 | N
19-12-18 | 14:30 | 258:80781 | URBAN | Asset Failure | Distribution substation | 2 | 45 | 6.1e-05 | 1e-06 | N
09-01-19 | 08:19 | 233:82815 | SHORT RURAL | Asset Failure | Distribution substation | 22 | 85 | 0.007899 | 9.3e-05 | N
09-01-19 | 09:21 | ZN35900:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 103 | 7e-05 | 1e-06 | N
09-01-19 | 11:49 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 161 | 0.001355 | 8e-06 | N
09-01-19 | 13:13 | 221:11899 | SHORT RURAL | Asset Failure | LV | 2 | 267 | 0.002243 | 8e-06 | N
09-01-19 | 14:08 | 230:81438 | SHORT RURAL | Other | Other | 1 | 47 | 0.000196 | 4e-06 | N
09-01-19 | 14:10 | ZN12660:PA17 | URBAN | Other | Other - Arcing | 1 | 229 | 0.000155 | 1e-06 | N
09-01-19 | 14:30 | ZN342:PA21 | URBAN | Other | Other - Self Clearing Trigger | 1 | 260 | 0.000176 | 1e-06 | N
09-01-19 | 14:30 | ZN931:PA9 | URBAN | Other | Other - Self Clearing Trigger | 30 | 260 | 0.005285 | 2e-05 | N
09-01-19 | 15:44 | ZN15011:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,035 | 0.000702 | 1e-06 | N
09-01-19 | 15:48 | 511:29878 | SHORT RURAL | Other | Other | 1 | 68 | 0.000284 | 4e-06 | N
09-01-19 | 16:46 | 512:83733 | SHORT RURAL | Asset Failure | HV | 89 | 279 | 0.10439 | 0.000374 | N
09-01-19 | 17:06 | 512:83733 | SHORT RURAL | Other | Other - Self Clearing Trigger | 15 | 239 | 0.015085 | 6.3e-05 | N
09-01-19 | 17:25 | 508:82579 | SHORT RURAL | Asset Failure | HV | 384 | 245 | 0.39619 | 0.001616 | N
09-01-19 | 17:24 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 76 | 0.080084 | 0.001054 | N
09-01-19 | 17:27 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 86 | 0.00036 | 4e-06 | N
09-01-19 | 17:52 | 511:29873 | URBAN | Other | Other - Self Clearing Trigger | 2 | 68 | 9.2e-05 | 1e-06 | N
09-01-19 | 17:54 | 813:89058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 17 | 101 | 0.007229 | 7.2e-05 | N
09-01-19 | 18:10 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 275 | 0.004629 | 1.7e-05 | N
09-01-19 | 18:35 | 511:29878 | SHORT RURAL | Asset Failure | LV | 1 | 271 | 0.001141 | 4e-06 | N
09-01-19 | 18:39 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 211 | 0.003551 | 1.7e-05 | N
09-01-19 | 19:08 | 814:82289 | SHORT RURAL | Weather |  | 1 | 26 | 0.00011 | 4e-06 | N
09-01-19 | 19:14 | ZN15001:PA8 | URBAN | Asset Failure | HV | 573 | 1,272 | 0.49395 | 0.000388 | N
09-01-19 | 20:03 | 512:83733 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 66 | 0.000833 | 1.3e-05 | N
09-01-19 | 21:54 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 95 | 0.000401 | 4e-06 | N
09-01-19 | 23:10 | ZN12660:PA8 | URBAN | Weather |  | 1,298 | 28 | 0.024993 | 0.000879 | N
09-01-19 | 22:40 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 70 | 0.001178 | 1.7e-05 | N
10-01-19 | 03:09 | ZN1673:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,028 | 113 | 0.078705 | 0.000697 | N
10-01-19 | 06:05 | ZN965:PA8 | URBAN | Other | Other - Self Clearing Trigger | 33 | 150 | 0.003355 | 2.2e-05 | N
10-01-19 | 06:51 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 308 | 0.001298 | 4e-06 | N
10-01-19 | 16:40 | 813:89061 | LONG RURAL | Asset Failure | Distribution substation | 1 | 35 | 0.012294 | 0.000351 | N
10-01-19 | 08:11 | 807:74183 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 129 | 0.0038 | 2.9e-05 | N
10-01-19 | 09:05 | ZN3155:PA24 | URBAN | Other | Other - Self Clearing Trigger | 13 | 92 | 0.000806 | 9e-06 | N
10-01-19 | 09:30 | 509:33399 | SHORT RURAL | Asset Failure | HV | 51 | 54 | 0.011626 | 0.000215 | N
10-01-19 | 09:41 | ZN35800:PA13 | URBAN | Asset Failure | LV | 1 | 331 | 0.000224 | 1e-06 | N
09-01-19 | 22:00 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 110 | 0.000463 | 4e-06 | N
10-01-19 | 11:16 | ZN1673:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 209 | 0.006228 | 3e-05 | N
10-01-19 | 11:16 | ZN847:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 41 | 200 | 0.005565 | 2.8e-05 | N
10-01-19 | 11:19 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 130 | 0.000548 | 4e-06 | N
09-01-19 | 22:18 | 514:18137 | SHORT RURAL | Third Party | Other | 1 | 8,193 | 0.034474 | 4e-06 | N
10-01-19 | 11:38 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 51 | 80 | 0.002757 | 3.5e-05 | N
10-01-19 | 12:28 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 57 | 0.00024 | 4e-06 | N
10-01-19 | 13:32 | ZN9118:PA20 | URBAN | Network business | Switching and protection error | 192 | 555 | 0.072193 | 0.00013 | N
10-01-19 | 13:34 | ZN35600:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 78 | 0.00033 | 4e-06 | N
10-01-19 | 14:04 | ZN690:PA34 | URBAN | Other | Other | 1 | 55 | 3.7e-05 | 1e-06 | N
10-01-19 | 15:09 | ZN35800:PA16 | URBAN | Other | Other - Self Clearing Trigger | 60 | 80 | 0.00327 | 4.1e-05 | N
10-01-19 | 15:09 | ZN35800:PA7 | URBAN | Other | Other - Self Clearing Trigger | 1 | 81 | 5.5e-05 | 1e-06 | N
10-01-19 | 16:20 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 80 | 0.000337 | 4e-06 | N
10-01-19 | 17:18 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 102 | 0.001288 | 1.3e-05 | N
10-01-19 | 18:01 | ZN15011:PA2 | URBAN | Other | Other - Arcing | 1 | 129 | 8.7e-05 | 1e-06 | N
10-01-19 | 18:47 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 358 | 0.003009 | 8e-06 | N
10-01-19 | 18:35 | 813:89055 | SHORT RURAL | Asset Failure | HV | 15 | 50 | 0.003156 | 6.3e-05 | N
10-01-19 | 20:15 | 221:11895 | URBAN | Other | Other | 1 | 262 | 0.000177 | 1e-06 | N
10-01-19 | 23:45 | ZN129:PA40 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 45 | 0.000823 | 1.8e-05 | N
11-01-19 | 00:46 | ZN195:PA30 | SHORT RURAL | Other | Other - Arcing | 1 | 553 | 0.002329 | 4e-06 | N
11-01-19 | 09:07 | ZN15006:PA15 | URBAN | Third Party | Vehicle impact | 1 | 203 | 0.000137 | 1e-06 | N
11-01-19 | 09:16 | ZN1610:PA26 | URBAN | Other | Other - Arcing | 1 | 373 | 0.000253 | 1e-06 | N
11-01-19 | 09:29 | ZN3154:PA16 | URBAN | Other | Other - Self Clearing Trigger | 31 | 71 | 0.001483 | 2.1e-05 | N
11-01-19 | 09:36 | ZN3472:PA30 | URBAN | Asset Failure | LV | 1 | 564 | 0.000382 | 1e-06 | N
11-01-19 | 09:54 | ZN1610:PA26 | URBAN | Other | Other - Arcing | 1 | 336 | 0.000227 | 1e-06 | N
11-01-19 | 10:18 | ZN2466:PA27 | URBAN | Other | Other - Self Clearing Trigger | 1 | 62 | 4.2e-05 | 1e-06 | N
11-01-19 | 10:33 | ZN5868:PA30 | URBAN | Third Party | Vehicle impact | 55 | 117 | 0.00436 | 3.7e-05 | N
11-01-19 | 10:39 | ZN5868:PA30 | URBAN | Third Party | Vehicle impact | 1 | 125 | 8.5e-05 | 1e-06 | N
11-01-19 | 10:43 | ZN262:PA16 | URBAN | Asset Failure | LV | 1 | 256 | 0.000174 | 1e-06 | N
11-01-19 | 11:19 | ZN3672:PA36 | URBAN | Asset Failure | LV | 1 | 295 | 0.0002 | 1e-06 | N
11-01-19 | 12:04 | ZN12650:PA17 | URBAN | Other | Other | 11 | 371 | 0.002765 | 7e-06 | N
11-01-19 | 12:15 | ZN965:PA47 | URBAN | Asset Failure | LV | 53 | 40 | 0.001436 | 3.6e-05 | N
11-01-19 | 12:27 | ZN12570:PA39 | URBAN | Other | Other | 1 | 244 | 0.000165 | 1e-06 | N
11-01-19 | 13:22 | 204:82710 | URBAN | Asset Failure | LV | 1 | 247 | 0.000168 | 1e-06 | N
11-01-19 | 15:58 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 112 | 0.000471 | 4e-06 | N
11-01-19 | 16:29 | ZN262:PA30 | URBAN | Other | Other - Self Clearing Trigger | 4 | 71 | 0.000192 | 3e-06 | N
11-01-19 | 16:29 | ZN262:PA6 | URBAN | Other | Other - Self Clearing Trigger | 55 | 70 | 0.002621 | 3.7e-05 | N
11-01-19 | 17:20 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 175 | 0.000736 | 4e-06 | N
11-01-19 | 17:23 | ZN2635:PA38 | URBAN | Other | Other - Self Clearing Trigger | 1 | 67 | 4.5e-05 | 1e-06 | N
11-01-19 | 17:23 | ZN2635:PA52 | URBAN | Other | Other - Self Clearing Trigger | 86 | 67 | 0.003904 | 5.8e-05 | N
11-01-19 | 17:43 | 512:83741 | SHORT RURAL | Other | Other | 1 | 106 | 0.000447 | 4e-06 | N
11-01-19 | 17:46 | ZN14891:PA16 | SHORT RURAL | Other | Other | 1 | 78 | 0.000328 | 4e-06 | N
11-01-19 | 19:02 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 88 | 0.03091 | 0.000351 | N
11-01-19 | 19:09 | 802:82225 | SHORT RURAL | Asset Failure | HV | 12 | 1,109 | 0.055997 | 5e-05 | N
11-01-19 | 19:24 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 91 | 0.031963 | 0.000351 | N
11-01-19 | 19:50 | ZN1193:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 49 | 10 | 0.000332 | 3.3e-05 | N
11-01-19 | 20:23 | ZN3922:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 366 | 0.001541 | 4e-06 | N
11-01-19 | 20:58 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 196 | 0.000825 | 4e-06 | N
11-01-19 | 21:02 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 143 | 0.15069 | 0.001054 | N
11-01-19 | 21:04 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 96 | 0.033597 | 0.000351 | N
11-01-19 | 21:28 | ZN262:PA30 | URBAN | Other | Other | 4 | 52 | 0.000141 | 3e-06 | N
11-01-19 | 21:28 | ZN262:PA6 | URBAN | Other | Other | 55 | 51 | 0.001902 | 3.7e-05 | N
11-01-19 | 21:57 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 98 | 0.000412 | 4e-06 | N
11-01-19 | 22:02 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 103 | 0.000867 | 8e-06 | N
11-01-19 | 22:31 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 209 | 0.000879 | 4e-06 | N
11-01-19 | 22:49 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 220 | 0.000928 | 4e-06 | N
11-01-19 | 23:10 | 502:48008 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,085 | 139 | 0.10239 | 0.000735 | N
11-01-19 | 23:20 | ZN14144:PA7 | SHORT RURAL | Asset Failure | LV | 2 | 936 | 0.007877 | 8e-06 | N
12-01-19 | 01:15 | ZN12660:PA8 | URBAN | Other | Other | 348 | 12 | 0.002789 | 0.000236 | N
12-01-19 | 00:13 | ZN1193:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 766 | 0.000519 | 1e-06 | N
12-01-19 | 04:27 | ZN262:PA30 | URBAN | Other | Other | 4 | 53 | 0.000144 | 3e-06 | N
12-01-19 | 04:27 | ZN262:PA6 | URBAN | Other | Other | 55 | 53 | 0.001975 | 3.7e-05 | N
12-01-19 | 05:29 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 26 | 116 | 0.012691 | 0.000109 | N
12-01-19 | 07:03 | ZN12580:PA1 | URBAN | Other | Other | 19 | 111 | 0.00143 | 1.3e-05 | N
12-01-19 | 08:29 | ZN262:PA30 | URBAN | Asset Failure | LV | 4 | 101 | 0.000274 | 3e-06 | N
12-01-19 | 08:29 | ZN262:PA6 | URBAN | Asset Failure | LV | 55 | 100 | 0.003731 | 3.7e-05 | N
12-01-19 | 08:31 | ZN9700:PA23 | URBAN | Network business | Network error | 50 | 56 | 0.001904 | 3.4e-05 | N
12-01-19 | 08:41 | ZN15008:PA5 | URBAN | Asset Failure | LV | 11 | 587 | 0.004375 | 7e-06 | N
12-01-19 | 08:49 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 51 | 0.000429 | 8e-06 | N
12-01-19 | 09:07 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 183 | 0.064278 | 0.000351 | N
12-01-19 | 09:12 | ZN36800:PA43 | URBAN | Asset Failure | LV | 79 | 645 | 0.034538 | 5.4e-05 | N
12-01-19 | 09:27 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 122 | 0.085704 | 0.000702 | N
12-01-19 | 11:27 | ZN12630:PA3 | SHORT RURAL | Asset Failure | Distribution substation | 8 | 217 | 0.007311 | 3.4e-05 | N
12-01-19 | 12:18 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 111 | 0.000468 | 4e-06 | N
12-01-19 | 17:50 | ZN965:PA15 | URBAN | Other | Other - Self Clearing Trigger | 11 | 90 | 0.000671 | 7e-06 | N
12-01-19 | 17:50 | ZN965:PA3 | URBAN | Other | Other - Self Clearing Trigger | 32 | 70 | 0.001518 | 2.2e-05 | N
12-01-19 | 12:33 | ZN10998:PA2 | URBAN | Asset Failure | LV | 1 | 417 | 0.000282 | 1e-06 | N
12-01-19 | 13:50 | 528:83020 | SHORT RURAL | Third Party | Vehicle impact | 12 | 25 | 0.001262 | 5e-05 | N
12-01-19 | 12:55 | 509:33395 | LONG RURAL | Asset Failure | LV | 1 | 268 | 0.094134 | 0.000351 | N
12-01-19 | 15:01 | ZN14892:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 24 | 114 | 0.011513 | 0.000101 | N
12-01-19 | 13:05 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 115 | 0.000968 | 8e-06 | N
12-01-19 | 13:25 | 217:33612 | URBAN | Other | Other | 4 | 50 | 0.000136 | 3e-06 | N
12-01-19 | 14:09 | 515:35197 | LONG RURAL | Asset Failure | HV | 33 | 229 | 2.6544 | 0.011591 | N
12-01-19 | 15:32 | ZN1193:PA28 | URBAN | Other | Other | 1 | 102 | 6.9e-05 | 1e-06 | N
12-01-19 | 15:43 | 512:83733 | SHORT RURAL | Asset Failure | HV | 2 | 177 | 0.00149 | 8e-06 | N
12-01-19 | 16:32 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 32 | 0.011275 | 0.000351 | N
12-01-19 | 17:44 | ZN1673:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 128 | 0.002959 | 2.3e-05 | N
12-01-19 | 15:10 | ZN1193:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 208 | 0.000282 | 1e-06 | N
12-01-19 | 15:10 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 77 | 211 | 0.011022 | 5.2e-05 | N
12-01-19 | 18:12 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 233 | 0.001961 | 8e-06 | N
12-01-19 | 18:14 | 243:80081 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 225 | 0.000948 | 4e-06 | N
12-01-19 | 19:07 | ZN12660:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 20 | 1.4e-05 | 1e-06 | N
12-01-19 | 21:24 | ZN14144:PA1 | URBAN | Other | Other | 1 | 725 | 0.000491 | 1e-06 | N
12-01-19 | 23:01 | 507:80925 | SHORT RURAL | Third Party | Vehicle impact | 248 | 366 | 0.3815 | 0.001044 | N
12-01-19 | 23:25 | 206:34440 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 244 | 0.000166 | 1e-06 | N
13-01-19 | 03:22 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 248 | 0.00313 | 1.3e-05 | N
13-01-19 | 03:40 | ZN12640:PA5 | URBAN | Third Party | Fire | 14 | 126 | 0.001194 | 9e-06 | N
13-01-19 | 09:29 | 507:80914 | SHORT RURAL | Asset Failure | HV | 20 | 290 | 0.024417 | 8.4e-05 | N
13-01-19 | 09:46 | ZN14891:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 99 | 0.002544 | 2.6e-05 | N
13-01-19 | 10:24 | ZN15010:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 206 | 0.000139 | 1e-06 | N
13-01-19 | 10:57 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 88 | 0.030888 | 0.000351 | N
13-01-19 | 10:59 | ZN15012:PA8 | URBAN | Asset Failure | LV | 45 | 241 | 0.007346 | 3e-05 | N
13-01-19 | 12:46 | ZN9035:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 385 | 0.000261 | 1e-06 | N
13-01-19 | 13:27 | 261:81882 | URBAN | Other | Other | 1 | 57 | 3.8e-05 | 1e-06 | N
13-01-19 | 14:06 | ZN4545:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 195 | 133 | 0.017583 | 0.000132 | N
13-01-19 | 14:28 | 811:74234 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 255 | 32 | 0.03413 | 0.001073 | N
13-01-19 | 17:55 | ZN3472:PA30 | URBAN | Asset Failure | LV | 28 | 181 | 0.00344 | 1.9e-05 | N
13-01-19 | 19:34 | ZN12640:PA2 | URBAN | Other | Other | 1 | 44 | 3e-05 | 1e-06 | N
13-01-19 | 21:48 | ZN15010:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 187 | 0.005827 | 3.1e-05 | N
13-01-19 | 20:31 | 243:80075 | SHORT RURAL | Other | Other - Arcing | 2 | 329 | 0.002768 | 8e-06 | N
13-01-19 | 23:14 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 125 | 0.000527 | 4e-06 | N
11-01-19 | 21:55 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 145 | 0.00122 | 8e-06 | N
11-01-19 | 21:55 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 160 | 0.00202 | 1.3e-05 | N
11-01-19 | 21:55 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 124 | 0.001565 | 1.3e-05 | N
14-01-19 | 07:56 | ZN12690:PA16 | SHORT RURAL | Asset Failure | HV | 335 | 123 | 0.17335 | 0.001409 | N
14-01-19 | 11:45 | ZN12690:PA16 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 22 | 15 | 0.001388 | 9.3e-05 | N
14-01-19 | 08:27 | 511:29878 | SHORT RURAL | Other | Other | 4 | 188 | 0.003163 | 1.7e-05 | N
14-01-19 | 08:35 | ZN3922:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 34 | 415 | 0.059356 | 0.000143 | N
14-01-19 | 08:56 | ZN2835:PA31 | URBAN | Other | Other | 1 | 361 | 0.000245 | 1e-06 | N
10-01-19 | 18:47 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 93 | 0.002739 | 2.9e-05 | N
14-01-19 | 09:25 | ZN1673:PA7 | URBAN | Asset Failure | HV | 1,028 | 97 | 0.067664 | 0.000697 | N
14-01-19 | 09:48 | 205:12205 | URBAN | Other | Other | 1 | 26 | 1.8e-05 | 1e-06 | N
14-01-19 | 09:58 | ZN15012:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 241 | 0.000164 | 1e-06 | N
11-01-19 | 12:40 | ZN1068:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 12 | 0.000358 | 3e-05 | N
14-01-19 | 10:15 | 801:74118 | URBAN | Other | Other | 1 | 75 | 5.1e-05 | 1e-06 | N
12-01-19 | 09:40 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 25 | 0.000316 | 1.3e-05 | N
12-01-19 | 09:40 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 45 | 0.000379 | 8e-06 | N
12-01-19 | 09:40 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 65 | 0.001368 | 2.1e-05 | N
12-01-19 | 09:40 | 526:34637 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 225 | 0.00284 | 1.3e-05 | N
14-01-19 | 10:31 | 532:83309 | URBAN | Asset Failure | LV | 40 | 54 | 0.001464 | 2.7e-05 | N
14-01-19 | 10:39 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 126 | 0.00053 | 4e-06 | N
14-01-19 | 10:58 | 513:48058 | URBAN | Other | Other | 1 | 69 | 4.7e-05 | 1e-06 | N
12-01-19 | 15:34 | ZN2835:PA41 | URBAN | Asset Failure | Distribution substation | 1 | 131 | 8.9e-05 | 1e-06 | N
14-01-19 | 11:45 | ZN188:PA45 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 70 | 0.00265 | 3.8e-05 | N
10-01-19 | 12:00 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 30 | 0.000379 | 1.3e-05 | N
14-01-19 | 12:03 | 238:34148 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 72 | 0.000303 | 4e-06 | N
14-01-19 | 12:11 | ZN12600:PA3 | URBAN | Network business | Network error | 22 | 123 | 0.001839 | 1.5e-05 | N
13-01-19 | 21:48 | ZN15010:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 69 | 242 | 0.01131 | 4.7e-05 | N
13-01-19 | 21:48 | ZN15010:PA30 | URBAN | Asset Failure | LV | 42 | 282 | 0.008023 | 2.8e-05 | N
14-01-19 | 14:47 | ZN14891:PA16 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 52 | 0.000218 | 4e-06 | N
14-01-19 | 14:49 | ZN3672:PA29 | SHORT RURAL | Third Party | Other | 28 | 191 | 0.022497 | 0.000118 | N
14-01-19 | 15:51 | 810:74054 | LONG RURAL | Asset Failure | Distribution substation | 1 | 234 | 0.082099 | 0.000351 | N
14-01-19 | 16:56 | ZN35400:PA68 | URBAN | Asset Failure | LV | 69 | 43 | 0.002013 | 4.7e-05 | N
14-01-19 | 19:58 | ZN15012:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 301 | 0.000204 | 1e-06 | N
14-01-19 | 20:17 | ZN3672:PA21 | SHORT RURAL | Asset Failure | LV | 1 | 403 | 0.001694 | 4e-06 | N
14-01-19 | 20:47 | ZN15014:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 251 | 0.00017 | 1e-06 | N
14-01-19 | 20:17 | ZN3672:PA21 | SHORT RURAL | Asset Failure | LV | 49 | 373 | 0.076886 | 0.000206 | N
14-01-19 | 23:45 | 513:48050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 196 | 216 | 0.17782 | 0.000825 | N
15-01-19 | 00:51 | ZN1068:PA17 | URBAN | Asset Failure | LV | 62 | 1,067 | 0.044883 | 4.2e-05 | N
15-01-19 | 04:32 | ZN9252:PA21 | URBAN | Animal | Animal nesting/burrowing, etc and other | 36 | 155 | 0.003796 | 2.4e-05 | N
15-01-19 | 04:32 | ZN9252:PA22 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,296 | 207 | 0.18166 | 0.000879 | N
15-01-19 | 04:32 | ZN9252:PA27 | URBAN | Animal | Animal nesting/burrowing, etc and other | 440 | 87 | 0.025971 | 0.000299 | N
15-01-19 | 04:32 | ZN9252:PA28 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,746 | 87 | 0.10306 | 0.001185 | N
15-01-19 | 04:42 | ZN3425:PA27 | URBAN | Asset Failure | HV | 178 | 30 | 0.003589 | 0.000121 | N
11-01-19 | 21:02 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 73 | 0.025641 | 0.000351 | N
11-01-19 | 21:02 | 813:89061 | LONG RURAL | Asset Failure | Distribution substation | 1 | 208 | 0.073059 | 0.000351 | N
15-01-19 | 08:18 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 92 | 0.000774 | 8e-06 | N
15-01-19 | 11:00 | ZN931:PA23 | URBAN | Third Party | Other | 18 | 180 | 0.002198 | 1.2e-05 | N
15-01-19 | 09:36 | ZN1788:PA15 | URBAN | Asset Failure | HV | 76 | 58 | 0.002991 | 5.2e-05 | N
15-01-19 | 09:36 | ZN1788:PA17 | URBAN | Asset Failure | HV | 1,574 | 65 | 0.069548 | 0.001068 | N
15-01-19 | 09:36 | ZN1788:PA29 | URBAN | Asset Failure | HV | 812 | 58 | 0.031953 | 0.000551 | N
15-01-19 | 10:11 | 801:74118 | URBAN | Other | Other | 1 | 61 | 4.1e-05 | 1e-06 | N
15-01-19 | 20:10 | 235:8684 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 370 | 0.001556 | 4e-06 | N
15-01-19 | 13:24 | ZN1648:PA4 | URBAN | Network business | Network error | 3 | 106 | 0.000215 | 2e-06 | N
15-01-19 | 13:50 | ZN1285:PA32 | URBAN | Asset Failure | HV | 47 | 92 | 0.002934 | 3.2e-05 | N
15-01-19 | 13:50 | ZN1285:PA35 | URBAN | Asset Failure | HV | 439 | 78 | 0.023093 | 0.000298 | N
15-01-19 | 14:25 | ZN340:PA45 | URBAN | Asset Failure | HV | 690 | 76 | 0.035408 | 0.000468 | N
15-01-19 | 14:25 | ZN340:PA8 | URBAN | Asset Failure | HV | 82 | 72 | 0.004006 | 5.6e-05 | N
15-01-19 | 16:00 | ZN2635:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 13 | 370 | 0.003263 | 9e-06 | N
15-01-19 | 16:17 | ZN931:PA2 | URBAN | Third Party | Other | 168 | 418 | 0.047644 | 0.000114 | N
15-01-19 | 16:59 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 35 | 0.000147 | 4e-06 | N
15-01-19 | 19:50 | ZN12610:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 40 | 0.001655 | 4.1e-05 | N
15-01-19 | 17:27 | ZN12610:PA2 | URBAN | Other | Other | 1 | 116 | 7.9e-05 | 1e-06 | N
15-01-19 | 17:42 | ZN15010:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 268 | 0.000182 | 1e-06 | N
15-01-19 | 17:56 | ZN1193:PA27 | URBAN | Other | Other - Arcing | 1 | 327 | 0.000222 | 1e-06 | N
15-01-19 | 18:03 | 511:29877 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 210 | 0.000885 | 4e-06 | N
15-01-19 | 18:07 | ZN188:PA44 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 354 | 0.00024 | 1e-06 | N
15-01-19 | 18:40 | ZN9118:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 254 | 0.000172 | 1e-06 | N
15-01-19 | 18:46 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 73 | 110 | 2.8196 | 0.025623 | N
15-01-19 | 18:50 | ZN36200:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 29 | 0.000122 | 4e-06 | N
15-01-19 | 19:04 | 217:33610 | URBAN | Other | Other | 1 | 47 | 3.2e-05 | 1e-06 | N
15-01-19 | 19:15 | ZN9118:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 218 | 0.000148 | 1e-06 | N
15-01-19 | 18:02 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 140 | 298 | 14.6437 | 0.04914 | N
15-01-19 | 20:49 | 220:8689 | URBAN | Other | Other | 1 | 286 | 0.000194 | 1e-06 | N
15-01-19 | 20:56 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 174 | 0.000731 | 4e-06 | N
15-01-19 | 22:32 | ZN14892:PA10 | URBAN | Other | Other - Arcing | 42 | 658 | 0.018745 | 2.8e-05 | N
15-01-19 | 21:17 | ZN188:PA45 | SHORT RURAL | Asset Failure | LV | 9 | 238 | 0.009011 | 3.8e-05 | N
15-01-19 | 21:50 | ZN35600:PA1 | URBAN | Asset Failure | LV | 40 | 179 | 0.004863 | 2.7e-05 | N
16-01-19 | 05:11 | ZN35600:PA6 | URBAN | Asset Failure | HV | 1,261 | 99 | 0.08453 | 0.000856 | N
16-01-19 | 06:53 | 801:74121 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 2 | 117 | 0.082134 | 0.000702 | N
16-01-19 | 06:54 | ZN2310:PA2 | URBAN | Third Party | Vehicle impact | 31 | 41 | 0.000868 | 2.1e-05 | N
16-01-19 | 08:53 | ZN965:PA29 | URBAN | Asset Failure | LV | 29 | 237 | 0.004664 | 2e-05 | N
16-01-19 | 10:02 | ZN9118:PA11 | URBAN | Vegetation | Vegetation Grow In | 1 | 158 | 0.000107 | 1e-06 | N
16-01-19 | 10:04 | ZN2310:PA18 | URBAN | Asset Failure | LV | 55 | 161 | 0.006011 | 3.7e-05 | N
16-01-19 | 10:25 | ZN3154:PA10 | URBAN | Other | Other | 1 | 196 | 0.000133 | 1e-06 | N
16-01-19 | 10:38 | ZN3155:PA30 | URBAN | Network business | Network error | 1 | 1,761 | 0.001196 | 1e-06 | N
16-01-19 | 10:46 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 194 | 0.000816 | 4e-06 | N
16-01-19 | 11:01 | ZN14891:PA5 | SHORT RURAL | Overloads |  | 1 | 358 | 0.001507 | 4e-06 | N
16-01-19 | 12:50 | ZN15008:PA5 | URBAN | Third Party | Vehicle impact | 1 | 415 | 0.000282 | 1e-06 | N
16-01-19 | 14:55 | ZN340:PA45 | URBAN | Network business | Network error | 17 | 340 | 0.003924 | 1.2e-05 | N
16-01-19 | 14:57 | ZN36100:PA19 | URBAN | Other | Other - Self Clearing Trigger | 42 | 163 | 0.004642 | 2.9e-05 | N
16-01-19 | 15:27 | ZN1610:PA29 | URBAN | Asset Failure | HV | 1,004 | 80 | 0.05458 | 0.000682 | N
16-01-19 | 15:50 | ZN35400:PA68 | URBAN | Other | Other - Self Clearing Trigger | 69 | 40 | 0.001874 | 4.7e-05 | N
16-01-19 | 16:33 | ZN80:PA36 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 56 | 0.001755 | 3.1e-05 | N
16-01-19 | 16:48 | ZN15008:PA5 | URBAN | Other | Other - Arcing | 1 | 420 | 0.000285 | 1e-06 | N
16-01-19 | 16:55 | 526:34633 | SHORT RURAL | Asset Failure | LV | 1 | 233 | 0.00098 | 4e-06 | N
16-01-19 | 17:00 | ZN2196:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 76 | 120 | 0.006183 | 5.2e-05 | N
16-01-19 | 17:01 | ZN1285:PA31 | URBAN | Other | Other - Self Clearing Trigger | 85 | 84 | 0.004835 | 5.8e-05 | N
16-01-19 | 17:04 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 106 | 0.037206 | 0.000351 | N
16-01-19 | 17:30 | 513:48058 | URBAN | Other | Other - Self Clearing Trigger | 86 | 75 | 0.004379 | 5.8e-05 | N
16-01-19 | 17:30 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 100 | 0.1053 | 0.001053 | N
16-01-19 | 19:05 | 222:33597 | URBAN | Asset Failure | LV | 26 | 85 | 0.0015 | 1.8e-05 | N
16-01-19 | 19:15 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 67 | 90 | 0.025264 | 0.000282 | N
16-01-19 | 19:15 | ZN10999:PA17 | URBAN | Asset Failure | LV | 64 | 209 | 0.009088 | 4.3e-05 | N
16-01-19 | 19:29 | 507:80914 | SHORT RURAL | Other | Other | 1 | 198 | 0.000834 | 4e-06 | N
16-01-19 | 19:40 | ZN35370:PA4 | SHORT RURAL | Asset Failure | LV | 40 | 90 | 0.015114 | 0.000168 | N
16-01-19 | 20:16 | ZN12570:PA33 | SHORT RURAL | Other | Other - Arcing | 12 | 823 | 0.041556 | 5e-05 | N
16-01-19 | 22:44 | 812:19071 | SHORT RURAL | Third Party | Fire | 1 | 107 | 0.000451 | 4e-06 | N
17-01-19 | 15:05 | ZN36100:PA19 | URBAN | Asset Failure | LV | 42 | 155 | 0.004417 | 2.8e-05 | N
17-01-19 | 02:39 | ZN931:PA11 | URBAN | Asset Failure | Distribution substation | 244 | 73 | 0.012085 | 0.000166 | N
17-01-19 | 05:31 | ZN12620:PA7 | URBAN | Asset Failure | HV | 2,171 | 70 | 0.10327 | 0.001473 | N
17-01-19 | 05:40 | ZN12620:PA3 | URBAN | Other | Other | 1 | 244 | 0.000166 | 1e-06 | N
17-01-19 | 08:07 | 220:8691 | URBAN | Other | Other | 1 | 16 | 1.1e-05 | 1e-06 | N
17-01-19 | 08:16 | ZN180:PA32 | URBAN | Other | Other | 83 | 324 | 0.018238 | 5.6e-05 | N
17-01-19 | 11:30 | ZN1648:PA2 | URBAN | Asset Failure | LV | 14 | 37 | 0.000351 | 9e-06 | N
17-01-19 | 09:50 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 240 | 0.003029 | 1.3e-05 | N
17-01-19 | 10:04 | ZN2602:PA33 | URBAN | Asset Failure | LV | 1 | 445 | 0.000302 | 1e-06 | N
17-01-19 | 11:19 | ZN931:PA11 | URBAN | Other | Other | 101 | 80 | 0.00549 | 6.9e-05 | N
17-01-19 | 12:09 | 205:12203 | URBAN | Other | Other - Self Clearing Trigger | 111 | 59 | 0.004443 | 7.5e-05 | N
17-01-19 | 12:25 | ZN35370:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 507 | 171 | 0.3638 | 0.002133 | N
17-01-19 | 12:25 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 49 | 171 | 0.035248 | 0.000206 | N
17-01-19 | 12:25 | ZN965:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 989 | 171 | 0.11474 | 0.000671 | N
17-01-19 | 12:34 | 508:82579 | SHORT RURAL | Other | Other | 1 | 89 | 0.000374 | 4e-06 | N
17-01-19 | 12:52 | ZN12690:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 307 | 0.001293 | 4e-06 | N
17-01-19 | 13:02 | ZN3425:PA15 | URBAN | Asset Failure | LV | 57 | 148 | 0.005716 | 3.9e-05 | N
17-01-19 | 13:18 | ZN2466:PA2 | URBAN | Asset Failure | HV | 139 | 90 | 0.008488 | 9.4e-05 | N
17-01-19 | 14:26 | 243:80081 | SHORT RURAL | Other | Other | 1 | 67 | 0.000283 | 4e-06 | N
17-01-19 | 14:28 | ZN188:PA15 | URBAN | Network business | Network error | 116 | 152 | 0.011963 | 7.9e-05 | N
17-01-19 | 14:28 | ZN8100:PA28 | SHORT RURAL | Network business | Network error | 1 | 152 | 0.000639 | 4e-06 | N
17-01-19 | 14:54 | ZN2635:PA46 | URBAN | Other | Other | 1 | 407 | 0.000276 | 1e-06 | N
17-01-19 | 17:14 | ZN965:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 37 | 331 | 0.051519 | 0.000156 | N
17-01-19 | 17:44 | ZN2310:PA10 | URBAN | Asset Failure | LV | 37 | 148 | 0.003725 | 2.5e-05 | N
17-01-19 | 17:50 | ZN14892:PA1 | SHORT RURAL | Asset Failure | HV | 1 | 450 | 0.001893 | 4e-06 | N
17-01-19 | 17:52 | ZN398:PA2 | URBAN | Asset Failure | LV | 89 | 503 | 0.030347 | 6e-05 | N
17-01-19 | 17:58 | 810:74054 | LONG RURAL | Asset Failure | Distribution substation | 1 | 300 | 0.10542 | 0.000351 | N
17-01-19 | 18:00 | ZN340:PA32 | URBAN | Other | Other - Self Clearing Trigger | 33 | 80 | 0.001785 | 2.2e-05 | N
17-01-19 | 18:01 | ZN12660:PA17 | URBAN | Other | Other | 1 | 102 | 6.9e-05 | 1e-06 | N
17-01-19 | 20:55 | ZN14143:PA12 | SHORT RURAL | Third Party | Dig-in | 1 | 1,085 | 0.004564 | 4e-06 | N
17-01-19 | 19:53 | 256:80646 | URBAN | Asset Failure | LV | 57 | 186 | 0.007202 | 3.9e-05 | N
17-01-19 | 21:59 | ZN2635:PA35 | URBAN | Network business | Network error | 26 | 171 | 0.003017 | 1.8e-05 | N
17-01-19 | 21:59 | ZN2635:PA44 | URBAN | Network business | Network error | 277 | 150 | 0.02823 | 0.000188 | N
17-01-19 | 23:42 | ZN965:PA8 | URBAN | Network business | Network error | 46 | 108 | 0.003359 | 3.1e-05 | N
18-01-19 | 03:43 | ZN12650:PA17 | URBAN | Third Party | Vehicle impact | 1 | 587 | 0.000398 | 1e-06 | N
18-01-19 | 06:50 | ZN847:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 370 | 0.000251 | 1e-06 | N
18-01-19 | 10:25 | 232:11454 | SHORT RURAL | Other | Other | 2 | 199 | 0.001676 | 8e-06 | N
18-01-19 | 10:45 | 213:33774 | URBAN | Asset Failure | LV | 1 | 68 | 4.6e-05 | 1e-06 | N
18-01-19 | 11:09 | ZN180:PA30 | URBAN | Other | Other - Self Clearing Trigger | 28 | 115 | 0.002191 | 1.9e-05 | N
18-01-19 | 11:53 | ZN129:PA56 | URBAN | Other | Other | 17 | 267 | 0.003083 | 1.2e-05 | N
18-01-19 | 13:00 | ZN2310:PA10 | URBAN | Network business | Network error | 107 | 60 | 0.00436 | 7.3e-05 | N
18-01-19 | 13:24 | ZN195:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 231 | 0.000157 | 1e-06 | N
18-01-19 | 14:26 | ZN965:PA20 | URBAN | Asset Failure | LV | 1 | 4,113 | 0.002793 | 1e-06 | N
18-01-19 | 17:00 | 243:80080 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 218 | 0.000919 | 4e-06 | N
18-01-19 | 19:53 | ZN10995:PA1 | URBAN | Network business | Network error | 66 | 87 | 0.0039 | 4.5e-05 | N
18-01-19 | 19:53 | ZN10995:PA7 | URBAN | Network business | Network error | 172 | 87 | 0.010163 | 0.000117 | N
18-01-19 | 17:41 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 73 | 0.000308 | 4e-06 | N
18-01-19 | 17:50 | ZN1285:PA17 | URBAN | Network business | Network error | 66 | 85 | 0.00381 | 4.5e-05 | N
18-01-19 | 18:41 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 67 | 109 | 0.030657 | 0.000282 | N
18-01-19 | 19:08 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 102 | 0.001288 | 1.3e-05 | N
18-01-19 | 19:13 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 51 | 76 | 0.002646 | 3.5e-05 | N
18-01-19 | 19:44 | ZN195:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 106 | 7.2e-05 | 1e-06 | N
18-01-19 | 20:25 | ZN3155:PA24 | URBAN | Other | Other | 41 | 162 | 0.004511 | 2.8e-05 | N
18-01-19 | 20:49 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 51 | 0.017901 | 0.000351 | N
18-01-19 | 21:24 | ZN9550:PA36 | URBAN | Network business | Network error | 100 | 106 | 0.007199 | 6.8e-05 | N
18-01-19 | 21:24 | ZN9550:PA6 | URBAN | Network business | Network error | 45 | 106 | 0.003239 | 3.1e-05 | N
18-01-19 | 21:29 | ZN1285:PA17 | URBAN | Network business | Network error | 66 | 91 | 0.004079 | 4.5e-05 | N
18-01-19 | 21:33 | ZN15014:PA7 | URBAN | Other | Other | 1 | 106 | 7.2e-05 | 1e-06 | N
18-01-19 | 23:42 | 240:34846 | URBAN | Asset Failure | Distribution substation | 132 | 58 | 0.005184 | 9e-05 | N
19-01-19 | 02:20 | ZN12570:PA22 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 10 | 610 | 0.025659 | 4.2e-05 | N
19-01-19 | 04:21 | ZN1610:PA5 | URBAN | Asset Failure | HV | 7 | 75 | 0.000358 | 5e-06 | N
19-01-19 | 12:07 | ZN35600:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 121 | 54 | 0.004409 | 8.2e-05 | N
18-01-19 | 23:39 | ZN35370:PA2 | SHORT RURAL | Asset Failure | HV | 36 | 836 | 0.12663 | 0.000151 | N
19-01-19 | 09:20 | 240:34846 | URBAN | Asset Failure | HV | 227 | 130 | 0.020019 | 0.000154 | N
19-01-19 | 09:09 | ZN35600:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 231 | 0.000157 | 1e-06 | N
19-01-19 | 09:09 | ZN2196:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 234 | 0.000159 | 1e-06 | N
19-01-19 | 10:51 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 139 | 0.000585 | 4e-06 | N
19-01-19 | 11:15 | 526:34639 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 165 | 0.000693 | 4e-06 | N
19-01-19 | 11:21 | ZN36200:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,380 | 63 | 0.3657 | 0.005805 | N
19-01-19 | 11:35 | ZN847:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 128 | 0.002431 | 1.9e-05 | N
19-01-19 | 12:09 | ZN15006:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 223 | 0.000151 | 1e-06 | N
19-01-19 | 12:33 | ZN12570:PA34 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 846 | 43 | 0.15468 | 0.003559 | N
19-01-19 | 12:38 | 224:80329 | SHORT RURAL | Vegetation | Vegetation Grow In | 1 | 154 | 0.00065 | 4e-06 | N
19-01-19 | 12:42 | 224:80329 | SHORT RURAL | Vegetation | Vegetation Grow In | 1 | 150 | 0.000633 | 4e-06 | N
19-01-19 | 12:50 | 224:80329 | SHORT RURAL | Vegetation | Vegetation Grow In | 1 | 143 | 0.000602 | 4e-06 | N
19-01-19 | 13:13 | 224:80341 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 160 | 0.000108 | 1e-06 | N
19-01-19 | 13:42 | ZN2568:PA19 | URBAN | Asset Failure | HV | 1,046 | 92 | 0.065172 | 0.00071 | N
19-01-19 | 13:46 | 507:80932 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 84 | 0.000353 | 4e-06 | N
19-01-19 | 14:30 | 235:2120 | SHORT RURAL | Asset Failure | Distribution substation | 30 | 220 | 0.027743 | 0.000126 | N
19-01-19 | 15:15 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.000379 | 4e-06 | N
19-01-19 | 17:09 | ZN9035:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 255 | 0.000173 | 1e-06 | N
19-01-19 | 17:16 | 240:34846 | URBAN | Asset Failure | HV | 227 | 162 | 0.02488 | 0.000154 | N
19-01-19 | 17:58 | ZN129:PA52 | URBAN | Asset Failure | LV | 38 | 142 | 0.003661 | 2.6e-05 | N
19-01-19 | 20:08 | ZN15015:PA5 | URBAN | Asset Failure | HV | 1,631 | 59 | 0.065733 | 0.001106 | N
19-01-19 | 21:03 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 156 | 0.000658 | 4e-06 | N
19-01-19 | 21:10 | ZN12610:PA18 | URBAN | Other | Other | 1 | 44 | 3e-05 | 1e-06 | N
19-01-19 | 21:35 | 507:80914 | SHORT RURAL | Asset Failure | HV | 650 | 148 | 0.4042 | 0.002734 | N
19-01-19 | 21:20 | ZN14891:PA5 | SHORT RURAL | Third Party | Unauthorised access | 60 | 395 | 0.099712 | 0.000252 | N
19-01-19 | 22:42 | ZN129:PA57 | URBAN | Other | Other - Self Clearing Trigger | 1,582 | 101 | 0.1085 | 0.001073 | N
19-01-19 | 22:42 | ZN129:PA63 | URBAN | Other | Other - Self Clearing Trigger | 83 | 113 | 0.006363 | 5.6e-05 | N
19-01-19 | 22:47 | ZN4990:PA53 54GHJ | CBD | Other | Other - Self Clearing Trigger | 1 | 1,218 | 0.039812 | 3.3e-05 | N
20-01-19 | 00:42 | 229:34995 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 17 | 398 | 0.02846 | 7.2e-05 | N
20-01-19 | 06:08 | ZN35600:PA22 | URBAN | Other | Other - Arcing | 1 | 437 | 0.000297 | 1e-06 | N
20-01-19 | 06:45 | ZN2602:PA29 | URBAN | Other | Other - Arcing | 1 | 400 | 0.000271 | 1e-06 | N
20-01-19 | 07:41 | ZN35600:PA12 | SHORT RURAL | Other | Other - Self Clearing Trigger | 38 | 48 | 0.007699 | 0.00016 | N
20-01-19 | 08:46 | 230:81432 | SHORT RURAL | Asset Failure | LV | 1 | 222 | 0.000934 | 4e-06 | N
20-01-19 | 08:55 | ZN2196:PA3 | URBAN | Third Party | Vehicle impact | 2 | 215 | 0.000292 | 1e-06 | N
20-01-19 | 14:12 | ZN2602:PA21 | URBAN | Other | Other | 1 | 267 | 0.000181 | 1e-06 | N
20-01-19 | 18:57 | ZN2635:PA38 | URBAN | Other | Other - Arcing | 1 | 363 | 0.000246 | 1e-06 | N
20-01-19 | 19:49 | ZN965:PA20 | URBAN | Asset Failure | LV | 1 | 311 | 0.000211 | 1e-06 | N
20-01-19 | 20:46 | ZN1648:PA8 | SHORT RURAL | Third Party | Vehicle impact | 42 | 804 | 0.14204 | 0.000177 | N
20-01-19 | 20:46 | ZN2835:PA23 | URBAN | Third Party | Vehicle impact | 46 | 804 | 0.025085 | 3.1e-05 | N
20-01-19 | 21:46 | 239:82136 | URBAN | Asset Failure | HV | 54 | 49 | 0.001795 | 3.7e-05 | N
21-01-19 | 01:04 | ZN12610:PA6 | URBAN | Animal | Animal impact | 50 | 71 | 0.002392 | 3.4e-05 | N
21-01-19 | 01:31 | ZN12570:PA33 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 658 | 46 | 0.12732 | 0.002768 | N
21-01-19 | 02:56 | ZN12630:PA13 | SHORT RURAL | Other | Other | 95 | 179 | 0.071585 | 0.0004 | N
21-01-19 | 03:13 | ZN12630:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 457 | 0.007689 | 1.7e-05 | N
21-01-19 | 03:16 | ZN12690:PA16 | SHORT RURAL | Other | Other - Self Clearing Trigger | 343 | 229 | 0.33031 | 0.001443 | N
21-01-19 | 03:45 | ZN12620:PA1 | SHORT RURAL | Weather |  | 979 | 250 | 1.0295 | 0.004118 | N
21-01-19 | 03:46 | ZN35370:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 451 | 98 | 0.18591 | 0.001897 | N
21-01-19 | 04:01 | ZN1850:PA32 | URBAN | Asset Failure | LV | 1 | 419 | 0.000284 | 1e-06 | N
21-01-19 | 04:16 | ZN15004:PA3 | SHORT RURAL | Other | Other - Arcing | 1 | 524 | 0.002203 | 4e-06 | N
21-01-19 | 04:18 | ZN12620:PA1 | SHORT RURAL | Weather |  | 272 | 144 | 0.16476 | 0.001144 | N
21-01-19 | 04:22 | ZN180:PA43 | URBAN | Other | Other - Arcing | 1 | 278 | 0.000189 | 1e-06 | N
21-01-19 | 04:31 | ZN690:PA28 | URBAN | Other | Other - Arcing | 1 | 298 | 0.000202 | 1e-06 | N
21-01-19 | 06:19 | ZN1673:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 52 | 140 | 0.00495 | 3.5e-05 | N
21-01-19 | 06:24 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 22 | 66 | 0.006097 | 9.3e-05 | N
21-01-19 | 06:35 | ZN12630:PA1 | SHORT RURAL | Weather |  | 4 | 685 | 0.011526 | 1.7e-05 | N
21-01-19 | 06:36 | 220:8689 | URBAN | Other | Other - Arcing | 1 | 174 | 0.000118 | 1e-06 | N
21-01-19 | 06:50 | ZN931:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 78 | 125 | 0.006614 | 5.3e-05 | N
21-01-19 | 07:57 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 108 | 0.000909 | 8e-06 | N
21-01-19 | 08:04 | 210:83472 | URBAN | Asset Failure | LV | 1 | 50 | 3.4e-05 | 1e-06 | N
21-01-19 | 08:50 | ZN35370:PA2 | SHORT RURAL | Weather |  | 8 | 167 | 0.00562 | 3.4e-05 | N
21-01-19 | 08:58 | ZN15013:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 316 | 0.00133 | 4e-06 | N
21-01-19 | 09:47 | 814:82291 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 98 | 0.000412 | 4e-06 | N
21-01-19 | 10:24 | ZN9245:PA21 | URBAN | Other | Other - Arcing | 1 | 226 | 0.000153 | 1e-06 | N
19-01-19 | 21:03 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 117 | 0.000492 | 4e-06 | N
19-01-19 | 21:03 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 137 | 0.000576 | 4e-06 | N
21-01-19 | 10:52 | ZN9252:PA24 | URBAN | Other | Other - Arcing | 1 | 238 | 0.000161 | 1e-06 | N
21-01-19 | 10:57 | ZN14891:PA12 | SHORT RURAL | Weather |  | 4 | 141 | 0.002372 | 1.7e-05 | N
21-01-19 | 11:07 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 53 | 0.018591 | 0.000351 | N
21-01-19 | 11:12 | 233:82819 | SHORT RURAL | Other | Other | 1 | 116 | 0.000488 | 4e-06 | N
21-01-19 | 11:29 | ZN2835:PA27 | URBAN | Other | Other | 1 | 226 | 0.000153 | 1e-06 | N
21-01-19 | 12:16 | ZN10994:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 845 | 41 | 0.023502 | 0.000573 | N
21-01-19 | 13:35 | ZN12630:PA13 | SHORT RURAL | Asset Failure | HV | 95 | 188 | 0.075257 | 0.0004 | N
21-01-19 | 14:12 | ZN10999:PA36 | URBAN | Other | Other - Arcing | 1 | 307 | 0.000208 | 1e-06 | N
21-01-19 | 14:19 | ZN12630:PA11 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 169 | 0.000709 | 4e-06 | N
21-01-19 | 14:40 | ZN9700:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 403 | 0.000274 | 1e-06 | N
21-01-19 | 15:35 | ZN262:PA42 | URBAN | Other | Other | 62 | 285 | 0.011987 | 4.2e-05 | N
21-01-19 | 17:26 | ZN80:PA32 | URBAN | Asset Failure | LV | 69 | 49 | 0.002287 | 4.7e-05 | N
21-01-19 | 16:47 | 511:29877 | SHORT RURAL | Asset Failure | LV | 1 | 251 | 0.001058 | 4e-06 | N
21-01-19 | 17:26 | ZN15009:PA1 | URBAN | Other | Other - Arcing | 1 | 439 | 0.000298 | 1e-06 | N
21-01-19 | 18:58 | 811:74234 | SHORT RURAL | Asset Failure | HV | 13 | 365 | 0.019947 | 5.5e-05 | N
21-01-19 | 19:15 | ZN12640:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 135 | 9.2e-05 | 1e-06 | N
21-01-19 | 19:52 | ZN14892:PA17 | URBAN | Asset Failure | LV | 31 | 112 | 0.002357 | 2.1e-05 | N
21-01-19 | 21:43 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 83 | 0.000349 | 4e-06 | N
21-01-19 | 23:11 | ZN4545:PA41 | SHORT RURAL | Animal | Animal impact | 1,159 | 37 | 0.18279 | 0.004875 | N
22-01-19 | 03:17 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 88 | 0.00037 | 4e-06 | N
22-01-19 | 06:36 | ZN14891:PA20 | SHORT RURAL | Network business | Switching and protection error | 1 | 143 | 0.000602 | 4e-06 | N
22-01-19 | 07:17 | ZN9118:PA22 | URBAN | Other | Other | 1 | 85 | 5.8e-05 | 1e-06 | N
22-01-19 | 07:19 | ZN9118:PA22 | URBAN | Other | Other | 1 | 63 | 4.2e-05 | 1e-06 | N
21-01-19 | 11:07 | 807:74180 | SHORT RURAL | Other | Other - Self Clearing Trigger | 40 | 53 | 0.008918 | 0.000168 | N
22-01-19 | 10:47 | ZN262:PA8 | URBAN | Asset Failure | LV | 7 | 93 | 0.000442 | 5e-06 | N
21-01-19 | 13:20 | ZN9700:PA17 | URBAN | Network business | Network error | 18 | 40 | 0.000488 | 1.2e-05 | N
22-01-19 | 13:22 | 232:11455 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 43 | 0.00018 | 4e-06 | N
22-01-19 | 14:14 | ZN3425:PA8 | URBAN | Asset Failure | LV | 19 | 76 | 0.00098 | 1.3e-05 | N
22-01-19 | 14:20 | ZN12580:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,293 | 0.005439 | 4e-06 | N
22-01-19 | 15:12 | ZN690:PA25 | URBAN | Asset Failure | LV | 1 | 286 | 0.000194 | 1e-06 | N
22-01-19 | 10:02 | ZN14144:PA8 | URBAN | Third Party | Other | 1 | 627 | 0.000426 | 1e-06 | N
22-01-19 | 17:15 | 513:48058 | URBAN | Other | Other | 1 | 173 | 0.000117 | 1e-06 | N
22-01-19 | 17:16 | 502:48010 | SHORT RURAL | Asset Failure | LV | 5 | 163 | 0.003432 | 2.1e-05 | N
22-01-19 | 19:40 | ZN35370:PA2 | SHORT RURAL | Network business | Switching and protection error | 276 | 97 | 0.11227 | 0.001161 | N
22-01-19 | 17:56 | ZN3672:PA43 | URBAN | Asset Failure | LV | 1 | 276 | 0.000187 | 1e-06 | N
22-01-19 | 20:23 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 82 | 0.000344 | 4e-06 | N
22-01-19 | 22:15 | 204:82691 | URBAN | Asset Failure | LV | 1 | 105 | 7.1e-05 | 1e-06 | N
23-01-19 | 03:14 | ZN9550:PA36 | URBAN | Other | Other - Self Clearing Trigger | 708 | 74 | 0.035485 | 0.00048 | N
23-01-19 | 03:14 | ZN9550:PA4 | URBAN | Other | Other - Self Clearing Trigger | 466 | 74 | 0.023356 | 0.000316 | N
23-01-19 | 04:16 | ZN9550:PA6 | URBAN | Network business | Network error | 45 | 510 | 0.015544 | 3e-05 | N
23-01-19 | 07:54 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 56 | 0.000236 | 4e-06 | N
22-01-19 | 17:25 | 507:80914 | SHORT RURAL | Asset Failure | Distribution substation | 100 | 5 | 0.002103 | 0.000421 | N
21-01-19 | 03:00 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 3 | 930 | 0.97929 | 0.001053 | N
23-01-19 | 09:56 | 814:82285 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 184 | 0.000774 | 4e-06 | N
23-01-19 | 01:17 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 493 | 0.002072 | 4e-06 | N
23-01-19 | 10:14 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 106 | 0.000445 | 4e-06 | N
23-01-19 | 11:09 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 140 | 0.000589 | 4e-06 | N
23-01-19 | 12:04 | ZN35400:PA110 | URBAN | Asset Failure | HV | 1,858 | 70 | 0.088089 | 0.001258 | N
23-01-19 | 12:56 | ZN12690:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 81 | 149 | 0.050761 | 0.000341 | N
23-01-19 | 13:32 | 257:81999 | URBAN | Asset Failure | HV | 63 | 61 | 0.002603 | 4.3e-05 | N
23-01-19 | 13:37 | ZN398:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 88 | 5.9e-05 | 1e-06 | N
23-01-19 | 14:03 | ZN2196:PA5 | URBAN | Other | Other - Self Clearing Trigger | 19 | 402 | 0.00517 | 1.3e-05 | N
23-01-19 | 14:08 | ZN9118:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 45 | 210 | 0.006399 | 3e-05 | N
23-01-19 | 14:10 | ZN9245:PA13 | URBAN | Weather |  | 42 | 345 | 0.009808 | 2.8e-05 | N
23-01-19 | 14:11 | ZN9550:PA36 | URBAN | Other | Other - Self Clearing Trigger | 33 | 133 | 0.002974 | 2.2e-05 | N
23-01-19 | 14:11 | ZN195:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 109 | 0.001772 | 1.6e-05 | N
23-01-19 | 14:31 | ZN3472:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 111 | 129 | 0.009677 | 7.5e-05 | N
23-01-19 | 14:37 | ZN35555:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 213 | 0.00476 | 2.2e-05 | N
23-01-19 | 14:35 | ZN1290:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,260 | 137 | 0.11671 | 0.000853 | N
23-01-19 | 14:44 | ZN10995:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 151 | 0.003882 | 2.6e-05 | N
23-01-19 | 14:41 | ZN9118:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 66 | 133 | 0.005957 | 4.5e-05 | N
23-01-19 | 14:59 | ZN965:PA42 | URBAN | Asset Failure | LV | 1 | 792 | 0.000537 | 1e-06 | N
23-01-19 | 14:57 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 317 | 0.008171 | 2.6e-05 | N
23-01-19 | 15:04 | ZN116:PA12 | URBAN | Other | Other | 1 | 92 | 6.2e-05 | 1e-06 | N
23-01-19 | 13:38 | ZN12610:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 51 | 401 | 0.013865 | 3.5e-05 | N
23-01-19 | 17:43 | ZN2635:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 217 | 0.006314 | 2.9e-05 | N
23-01-19 | 19:40 | ZN965:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 50 | 0.00149 | 3e-05 | N
23-01-19 | 16:48 | ZN9037:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 270 | 0.000183 | 1e-06 | N
23-01-19 | 17:01 | ZN3922:PA5 | SHORT RURAL | Other | Other | 1 | 1,305 | 0.00549 | 4e-06 | N
23-01-19 | 17:19 | ZN9037:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 593 | 0.000402 | 1e-06 | N
23-01-19 | 17:32 | ZN3154:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 7 | 331 | 0.001569 | 5e-06 | N
23-01-19 | 21:08 | 238:34143 | URBAN | Asset Failure | LV | 34 | 52 | 0.001197 | 2.3e-05 | N
23-01-19 | 18:08 | ZN15012:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 5 | 296 | 0.001002 | 3e-06 | N
23-01-19 | 18:59 | ZN15014:PA7 | URBAN | Other | Other - Arcing | 1 | 291 | 0.000197 | 1e-06 | N
23-01-19 | 19:11 | ZN180:PA34 | URBAN | Asset Failure | LV | 50 | 658 | 0.022292 | 3.4e-05 | N
23-01-19 | 19:22 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 158 | 0.003987 | 2.5e-05 | N
23-01-19 | 19:45 | 516:48065 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 200 | 0.001682 | 8e-06 | N
23-01-19 | 20:44 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 186 | 0.001565 | 8e-06 | N
23-01-19 | 20:58 | ZN9550:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 107 | 0.002021 | 1.9e-05 | N
23-01-19 | 22:11 | ZN188:PA26 | URBAN | Other | Other - Arcing | 1 | 302 | 0.000204 | 1e-06 | N
24-01-19 | 00:10 | 532:83293 | URBAN | Asset Failure | LV | 1 | 530 | 0.000359 | 1e-06 | N
24-01-19 | 07:19 | 513:48050 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 61 | 0.000257 | 4e-06 | N
24-01-19 | 08:23 | ZN15004:PA1 | URBAN | Other | Other - Self Clearing Trigger | 8 | 412 | 0.002232 | 5e-06 | N
24-01-19 | 09:14 | 242:81541 | URBAN | Other | Other | 1 | 101 | 6.8e-05 | 1e-06 | N
24-01-19 | 11:03 | ZN12690:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 19 | 127 | 0.001634 | 1.3e-05 | N
24-01-19 | 14:52 | 223:14395 | SHORT RURAL | Third Party | Vehicle impact | 36 | 445 | 0.0673 | 0.000151 | N
24-01-19 | 15:30 | ZN12650:PA1 | SHORT RURAL | Asset Failure | Distribution substation | 5 | 60 | 0.001262 | 2.1e-05 | N
24-01-19 | 16:45 | ZN965:PA42 | URBAN | Other | Other | 1 | 345 | 0.000233 | 1e-06 | N
24-01-19 | 17:29 | 243:80074 | SHORT RURAL | Asset Failure | LV | 1 | 47 | 0.0002 | 4e-06 | N
24-01-19 | 22:39 | ZN12690:PA6 | URBAN | Asset Failure | HV | 666 | 58 | 0.026163 | 0.000451 | N
25-01-19 | 00:03 | 415:33904 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1 | 157 | 0.000106 | 1e-06 | N
25-01-19 | 00:48 | ZN14892:PA8 | URBAN | Other | Other | 886 | 68 | 0.040668 | 0.0006 | N
25-01-19 | 05:13 | ZN1193:PA11 | URBAN | Other | Other - Self Clearing Trigger | 19 | 121 | 0.001559 | 1.3e-05 | N
25-01-19 | 07:37 | ZN10994:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 229 | 0.000155 | 1e-06 | N
23-01-19 | 16:15 | ZN10998:PA18 | URBAN | Weather |  | 109 | 165 | 0.012181 | 7.4e-05 | N
23-01-19 | 17:00 | ZN9700:PA16 | URBAN | Weather |  | 26 | 90 | 0.001585 | 1.8e-05 | N
25-01-19 | 09:05 | ZN3154:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 125 | 0.003133 | 2.5e-05 | N
25-01-19 | 09:13 | 265:81651 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 44 | 0.000186 | 4e-06 | N
25-01-19 | 10:43 | ZN35555:PA19 | URBAN | Other | Other | 1 | 215 | 0.000146 | 1e-06 | N
25-01-19 | 11:08 | ZN12600:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 561 | 0.00038 | 1e-06 | N
25-01-19 | 13:18 | ZN12650:PA17 | URBAN | Third Party | Vehicle impact | 1 | 282 | 0.000191 | 1e-06 | N
25-01-19 | 13:50 | ZN3672:PA42 | URBAN | Asset Failure | LV | 1 | 279 | 0.000189 | 1e-06 | N
25-01-19 | 14:03 | ZN195:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 15 | 270 | 0.017032 | 6.3e-05 | N
25-01-19 | 15:59 | ZN10997:PA7 | URBAN | Third Party | Vehicle impact | 277 | 189 | 0.035456 | 0.000188 | N
25-01-19 | 14:22 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 88 | 0.00111 | 1.3e-05 | N
25-01-19 | 12:49 | 515:35197 | LONG RURAL | Asset Failure | HV | 2 | 221 | 0.1552 | 0.000702 | N
25-01-19 | 14:50 | ZN2310:PA21 | URBAN | Other | Other - Self Clearing Trigger | 1 | 85 | 5.8e-05 | 1e-06 | N
25-01-19 | 14:50 | ZN2310:PA4 | URBAN | Other | Other - Self Clearing Trigger | 73 | 85 | 0.004203 | 4.9e-05 | N
25-01-19 | 14:51 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 474 | 0.000321 | 1e-06 | N
25-01-19 | 15:13 | ZN2835:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 313 | 0.000212 | 1e-06 | N
25-01-19 | 15:30 | ZN965:PA35 | URBAN | Asset Failure | LV | 39 | 187 | 0.00494 | 2.6e-05 | N
25-01-19 | 15:34 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 52 | 100 | 0.003534 | 3.5e-05 | N
25-01-19 | 15:56 | 802:82225 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 180 | 0.000755 | 4e-06 | N
25-01-19 | 16:52 | ZN12640:PA13 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 2,045 | 58 | 0.50041 | 0.0086 | N
25-01-19 | 17:36 | ZN3425:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 983 | 0.000666 | 1e-06 | N
25-01-19 | 17:57 | 204:82697 | URBAN | Other | Other - Self Clearing Trigger | 105 | 68 | 0.004836 | 7.1e-05 | N
25-01-19 | 18:19 | ZN10999:PA36 | URBAN | Asset Failure | LV | 44 | 176 | 0.005235 | 3e-05 | N
25-01-19 | 18:59 | 801:74122 | URBAN | Other | Other - Self Clearing Trigger | 102 | 51 | 0.003517 | 6.9e-05 | N
25-01-19 | 19:39 | 258:80775 | URBAN | Asset Failure | LV | 1 | 125 | 8.5e-05 | 1e-06 | N
26-01-19 | 23:24 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 81 | 0.00034 | 4e-06 | N
26-01-19 | 05:31 | ZN13000:PA11 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 349 | 0.001466 | 4e-06 | N
26-01-19 | 07:16 | ZN36200:PA8 | SHORT RURAL | Asset Failure | LV | 51 | 389 | 0.083379 | 0.000214 | N
26-01-19 | 08:42 | 409:6011 | URBAN | Asset Failure | Subtransmission | 4 | 208 | 0.000562 | 3e-06 | N
26-01-19 | 09:18 | 224:80340 | SHORT RURAL | Asset Failure | LV | 1 | 376 | 0.001582 | 4e-06 | N
26-01-19 | 09:20 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 152 | 0.003909 | 2.6e-05 | N
26-01-19 | 09:23 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 81 | 94 | 0.031881 | 0.00034 | N
26-01-19 | 09:32 | ZN15006:PA9 | URBAN | Asset Failure | LV | 1 | 465 | 0.000315 | 1e-06 | N
26-01-19 | 09:59 | ZN847:PA44 | URBAN | Asset Failure | LV | 1 | 660 | 0.000447 | 1e-06 | N
26-01-19 | 10:37 | ZN9245:PA19 | URBAN | Asset Failure | HV | 493 | 89 | 0.029717 | 0.000334 | N
26-01-19 | 10:37 | ZN9245:PA21 | URBAN | Asset Failure | HV | 1,208 | 80 | 0.065502 | 0.000818 | N
26-01-19 | 11:06 | ZN12580:PA10 | URBAN | Third Party | Other | 1 | 219 | 0.000148 | 1e-06 | N
26-01-19 | 11:16 | 202:34254 | URBAN | Other | Other | 1 | 53 | 3.6e-05 | 1e-06 | N
26-01-19 | 11:55 | ZN195:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 59 | 0.000247 | 4e-06 | N
26-01-19 | 13:03 | 523:33503 | URBAN | Other | Other - Self Clearing Trigger | 51 | 57 | 0.001969 | 3.5e-05 | N
26-01-19 | 13:49 | ZN3922:PA17 | SHORT RURAL | Network business | Network error | 11 | 136 | 0.006287 | 4.6e-05 | N
26-01-19 | 14:00 | ZN15012:PA6 | URBAN | Other | Other - Arcing | 1 | 318 | 0.000215 | 1e-06 | N
26-01-19 | 14:29 | ZN4545:PA17 | URBAN | Asset Failure | LV | 76 | 316 | 0.016277 | 5.1e-05 | N
26-01-19 | 14:41 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 138 | 0.000582 | 4e-06 | N
26-01-19 | 14:55 | ZN965:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 6 | 0.000179 | 3e-05 | N
26-01-19 | 16:21 | ZN10994:PA20 | URBAN | Asset Failure | LV | 87 | 230 | 0.013564 | 5.9e-05 | N
26-01-19 | 16:56 | 206:34432 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 71 | 4.8e-05 | 1e-06 | N
26-01-19 | 18:59 | ZN12650:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,101 | 0.000746 | 1e-06 | N
26-01-19 | 19:19 | ZN14144:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 13 | 101 | 0.000889 | 9e-06 | N
26-01-19 | 20:28 | 205:12213 | SHORT RURAL | Asset Failure | LV | 53 | 61 | 0.013606 | 0.000223 | N
26-01-19 | 21:26 | 515:35198 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 44 | 0.00074 | 1.7e-05 | N
26-01-19 | 22:01 | ZN35400:PA110 | URBAN | Network business | Network error | 95 | 122 | 0.00785 | 6.4e-05 | N
27-01-19 | 01:42 | ZN847:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 368 | 0.008471 | 2.3e-05 | N
27-01-19 | 02:40 | 210:83466 | URBAN | Animal | Animal nesting/burrowing, etc and other | 129 | 40 | 0.00347 | 8.7e-05 | N
27-01-19 | 08:01 | ZN10999:PA10 | URBAN | Other | Other - Self Clearing Trigger | 103 | 118 | 0.008253 | 7e-05 | N
27-01-19 | 08:50 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 79 | 0.027795 | 0.000351 | N
27-01-19 | 10:39 | 528:83011 | SHORT RURAL | Other | Other | 1 | 99 | 0.000415 | 4e-06 | N
27-01-19 | 14:18 | ZN15014:PA19 | URBAN | Asset Failure | Distribution substation | 56 | 104 | 0.003928 | 3.8e-05 | N
27-01-19 | 14:12 | ZN965:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,299 | 90 | 0.079181 | 0.00088 | N
27-01-19 | 14:12 | ZN965:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 100 | 90 | 0.006096 | 6.8e-05 | N
27-01-19 | 14:46 | ZN35370:PA4 | SHORT RURAL | Asset Failure | HV | 310 | 49 | 0.06384 | 0.001303 | N
27-01-19 | 14:46 | ZN35370:PA8 | SHORT RURAL | Asset Failure | HV | 279 | 171 | 0.20094 | 0.001173 | N
27-01-19 | 15:20 | ZN12690:PA11 | URBAN | Asset Failure | HV | 10 | 35 | 0.000237 | 7e-06 | N
27-01-19 | 16:46 | ZN1287:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 11 | 51 | 0.00038 | 7e-06 | N
27-01-19 | 16:51 | ZN15014:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 191 | 0.00013 | 1e-06 | N
27-01-19 | 17:29 | ZN1290:PA11 | URBAN | Weather |  | 181 | 56 | 0.006877 | 0.000123 | N
27-01-19 | 17:58 | ZN965:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 121 | 8.2e-05 | 1e-06 | N
27-01-19 | 18:15 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 97 | 0.00224 | 2.3e-05 | N
27-01-19 | 18:23 | ZN3472:PA34 | URBAN | Asset Failure | HV | 151 | 107 | 0.010943 | 0.000102 | N
27-01-19 | 18:23 | ZN3922:PA11 | URBAN | Asset Failure | HV | 1,942 | 105 | 0.13764 | 0.001315 | N
27-01-19 | 18:23 | ZN3922:PA13 | SHORT RURAL | Asset Failure | HV | 1 | 107 | 0.00045 | 4e-06 | N
27-01-19 | 18:23 | ZN3922:PA29 | URBAN | Asset Failure | HV | 926 | 106 | 0.066479 | 0.000627 | N
27-01-19 | 18:27 | ZN36200:PA8 | SHORT RURAL | Asset Failure | HV | 1,380 | 70 | 0.40645 | 0.0058 | N
27-01-19 | 18:45 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 10 | 149 | 0.52409 | 0.003509 | N
27-01-19 | 19:07 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 303 | 0.001273 | 4e-06 | N
27-01-19 | 19:10 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 320 | 0.001345 | 4e-06 | N
27-01-19 | 19:17 | 257:81987 | URBAN | Other | Other | 1 | 50 | 3.4e-05 | 1e-06 | N
27-01-19 | 19:30 | ZN36100:PA2 | URBAN | Asset Failure | LV | 100 | 104 | 0.007055 | 6.8e-05 | N
27-01-19 | 19:30 | ZN36100:PA23 | URBAN | Asset Failure | LV | 86 | 310 | 0.018056 | 5.8e-05 | N
27-01-19 | 19:47 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 207 | 0.000871 | 4e-06 | N
27-01-19 | 20:05 | ZN12620:PA7 | URBAN | Asset Failure | HV | 2,112 | 136 | 0.19514 | 0.00143 | N
27-01-19 | 20:09 | 508:82579 | SHORT RURAL | Other | Other | 1 | 121 | 0.000508 | 4e-06 | N
27-01-19 | 20:19 | 807:74184 | SHORT RURAL | Other | Other | 1 | 201 | 0.000843 | 4e-06 | N
27-01-19 | 20:58 | ZN1290:PA11 | URBAN | Asset Failure | HV | 1 | 180 | 0.000122 | 1e-06 | N
27-01-19 | 20:58 | ZN3472:PA20 | URBAN | Asset Failure | HV | 8 | 157 | 0.000851 | 5e-06 | N
27-01-19 | 20:58 | ZN3472:PA28 | URBAN | Asset Failure | HV | 1,547 | 173 | 0.18075 | 0.001048 | N
27-01-19 | 21:44 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 183 | 87 | 0.066584 | 0.000769 | N
27-01-19 | 21:53 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 226 | 0.000952 | 4e-06 | N
27-01-19 | 22:04 | ZN9245:PA13 | URBAN | Asset Failure | HV | 1 | 771 | 0.000522 | 1e-06 | N
27-01-19 | 22:04 | ZN9245:PA19 | URBAN | Asset Failure | HV | 493 | 758 | 0.2531 | 0.000334 | N
27-01-19 | 22:04 | ZN9245:PA21 | URBAN | Asset Failure | HV | 488 | 758 | 0.25053 | 0.000331 | N
27-01-19 | 22:04 | ZN9252:PA25 | URBAN | Asset Failure | HV | 869 | 606 | 0.3564 | 0.000589 | N
27-01-19 | 22:24 | ZN15013:PA10 | SHORT RURAL | Weather |  | 96 | 975 | 0.39353 | 0.000403 | N
27-01-19 | 21:51 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 124 | 0.00052 | 4e-06 | N
27-01-19 | 23:53 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 127 | 0.000534 | 4e-06 | N
28-01-19 | 00:25 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 260 | 0.004351 | 1.7e-05 | N
28-01-19 | 01:23 | ZN2196:PA18 | URBAN | Asset Failure | LV | 43 | 197 | 0.005741 | 2.9e-05 | N
28-01-19 | 08:38 | ZN35800:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 3 | 112 | 0.000228 | 2e-06 | N
28-01-19 | 08:45 | ZN7481:PA20 | URBAN | Asset Failure | LV | 1 | 74 | 5e-05 | 1e-06 | N
28-01-19 | 08:56 | ZN12660:PA14 | SHORT RURAL | Other | Other | 1 | 63 | 0.000264 | 4e-06 | N
28-01-19 | 09:13 | 512:83743 | SHORT RURAL | Asset Failure | HV | 6 | 184 | 0.004606 | 2.5e-05 | N
28-01-19 | 10:30 | ZN3155:PA35 | URBAN | Other | Other - Self Clearing Trigger | 43 | 79 | 0.002296 | 2.9e-05 | N
28-01-19 | 11:06 | ZN3922:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 338 | 0.001416 | 4e-06 | N
28-01-19 | 11:11 | ZN12600:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 193 | 0.000806 | 4e-06 | N
28-01-19 | 12:18 | 509:33399 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 27 | 0.000114 | 4e-06 | N
28-01-19 | 16:32 | ZN847:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 19 | 38 | 0.000487 | 1.3e-05 | N
28-01-19 | 14:26 | ZN3425:PA28 | SHORT RURAL | Asset Failure | LV | 14 | 259 | 0.01514 | 5.9e-05 | N
28-01-19 | 14:25 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 116 | 82 | 0.039659 | 0.000485 | N
28-01-19 | 17:11 | 806:82667 | SHORT RURAL | Asset Failure | HV | 40 | 167 | 0.027912 | 0.000167 | N
28-01-19 | 17:50 | 507:80932 | SHORT RURAL | Other | Other | 1 | 31 | 0.000129 | 4e-06 | N
28-01-19 | 17:52 | 814:82289 | SHORT RURAL | Asset Failure | HV | 651 | 64 | 0.17495 | 0.002723 | N
28-01-19 | 18:01 | 814:82291 | SHORT RURAL | Other | Other - Self Clearing Trigger | 463 | 76 | 0.14641 | 0.001937 | N
28-01-19 | 18:20 | ZN965:PA4 | URBAN | Third Party | Other | 1 | 84 | 5.7e-05 | 1e-06 | N
28-01-19 | 18:51 | 257:81999 | URBAN | Asset Failure | HV | 935 | 89 | 0.056359 | 0.000634 | N
28-01-19 | 19:14 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 308 | 0.003866 | 1.3e-05 | N
28-01-19 | 20:33 | ZN14144:PA1 | URBAN | Other | Other | 1 | 52 | 3.5e-05 | 1e-06 | N
28-01-19 | 20:58 | 813:89062 | SHORT RURAL | Asset Failure | HV | 1 | 167 | 0.000699 | 4e-06 | N
28-01-19 | 22:22 | ZN12570:PA26 | URBAN | Asset Failure | HV | 2 | 73 | 9.9e-05 | 1e-06 | N
28-01-19 | 22:47 | 814:82291 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 183 | 0.000764 | 4e-06 | N
28-01-19 | 23:01 | 813:89062 | SHORT RURAL | Asset Failure | HV | 53 | 12 | 0.002661 | 0.000222 | N
29-01-19 | 07:16 | 515:35200 | URBAN | Asset Failure | HV | 2 | 230 | 0.000312 | 1e-06 | N
29-01-19 | 07:54 | 509:33395 | LONG RURAL | Other | Other | 1 | 279 | 0.097836 | 0.000351 | N
29-01-19 | 08:10 | 814:82289 | SHORT RURAL | Other | Other | 1 | 566 | 0.002366 | 4e-06 | N
29-01-19 | 08:27 | ZN9900:PA5 | URBAN | Asset Failure | LV | 36 | 572 | 0.013968 | 2.4e-05 | N
29-01-19 | 09:35 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 5 | 330 | 0.57895 | 0.001754 | N
29-01-19 | 08:59 | ZN3472:PA17 | URBAN | Other | Other | 1 | 27 | 1.8e-05 | 1e-06 | N
29-01-19 | 09:01 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 304 | 0.002544 | 8e-06 | N
25-01-19 | 21:30 | 812:19072 | SHORT RURAL | Asset Failure | HV | 3 | 45 | 0.000568 | 1.3e-05 | N
29-01-19 | 22:00 | 509:33399 | SHORT RURAL | Asset Failure | HV | 1 | 95 | 0.000397 | 4e-06 | N
29-01-19 | 10:33 | ZN15002:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 290 | 0.007663 | 2.6e-05 | N
29-01-19 | 11:20 | ZN12690:PA8 | URBAN | Asset Failure | LV | 1 | 190 | 0.000129 | 1e-06 | N
29-01-19 | 12:04 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 251 | 0.08807 | 0.000351 | N
29-01-19 | 12:18 | 812:19071 | SHORT RURAL | Other | Other | 1 | 83 | 0.000349 | 4e-06 | N
29-01-19 | 12:56 | 232:11457 | SHORT RURAL | Asset Failure | LV | 1 | 423 | 0.001771 | 4e-06 | N
29-01-19 | 13:04 | 516:48067 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 75 | 0.000314 | 4e-06 | N
29-01-19 | 13:30 | 522:83131 | URBAN | Asset Failure | LV | 1 | 300 | 0.000203 | 1e-06 | N
29-01-19 | 13:49 | ZN35900:PA2 | URBAN | Other | Other | 1 | 1,057 | 0.000717 | 1e-06 | N
29-01-19 | 14:07 | ZN12570:PA25 | SHORT RURAL | Asset Failure | LV | 1 | 261 | 0.00109 | 4e-06 | N
29-01-19 | 14:16 | 522:83131 | URBAN | Asset Failure | LV | 1 | 128 | 8.7e-05 | 1e-06 | N
29-01-19 | 16:28 | 508:82575 | SHORT RURAL | Third Party | Other | 3 | 92 | 0.001155 | 1.3e-05 | N
29-01-19 | 16:07 | ZN690:PA30 | URBAN | Other | Other | 1 | 435 | 0.000295 | 1e-06 | N
29-01-19 | 16:19 | ZN35370:PA10 | SHORT RURAL | Other | Other - Arcing | 507 | 164 | 0.34793 | 0.002121 | N
29-01-19 | 16:19 | ZN35370:PA2 | SHORT RURAL | Other | Other - Arcing | 49 | 87 | 0.017834 | 0.000205 | N
29-01-19 | 16:19 | ZN965:PA24 | URBAN | Other | Other - Arcing | 989 | 184 | 0.12303 | 0.00067 | N
29-01-19 | 16:37 | ZN2835:PA21 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 50 | 132 | 0.027681 | 0.000209 | N
29-01-19 | 16:55 | ZN9900:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 69 | 0.001082 | 1.6e-05 | N
29-01-19 | 17:43 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 101 | 0.000422 | 4e-06 | N
29-01-19 | 17:55 | 242:81539 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 184 | 0.004989 | 2.7e-05 | N
29-01-19 | 19:33 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 147 | 0.00123 | 8e-06 | N
29-01-19 | 19:49 | ZN398:PA9 | URBAN | Other | Other - Self Clearing Trigger | 114 | 91 | 0.007031 | 7.7e-05 | N
29-01-19 | 19:47 | 235:2120 | SHORT RURAL | Asset Failure | HV | 711 | 75 | 0.22308 | 0.002974 | N
29-01-19 | 19:47 | 235:2121 | SHORT RURAL | Asset Failure | HV | 23 | 157 | 0.015132 | 9.6e-05 | N
29-01-19 | 19:47 | 235:2123 | URBAN | Asset Failure | HV | 1,363 | 55 | 0.05081 | 0.000924 | N
29-01-19 | 19:47 | 235:2124 | URBAN | Asset Failure | HV | 929 | 55 | 0.034631 | 0.00063 | N
29-01-19 | 19:47 | 235:2728 | URBAN | Asset Failure | HV | 318 | 59 | 0.012717 | 0.000216 | N
29-01-19 | 19:47 | 235:2857 | SHORT RURAL | Asset Failure | HV | 312 | 82 | 0.10703 | 0.001305 | N
29-01-19 | 19:47 | 235:8684 | SHORT RURAL | Asset Failure | HV | 120 | 56 | 0.028113 | 0.000502 | N
29-01-19 | 19:47 | 235:8685 | URBAN | Asset Failure | HV | 114 | 59 | 0.004559 | 7.7e-05 | N
29-01-19 | 22:19 | ZN1673:PA21 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 27 | 7 | 0.000791 | 0.000113 | N
29-01-19 | 20:48 | ZN15013:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 837 | 0.003501 | 4e-06 | N
29-01-19 | 20:56 | 526:34639 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 304 | 0.001272 | 4e-06 | N
29-01-19 | 23:13 | 807:74181 | SHORT RURAL | Other | Other | 1 | 710 | 0.002971 | 4e-06 | N
30-01-19 | 00:23 | ZN35400:PA73 | URBAN | Asset Failure | LV | 74 | 322 | 0.01615 | 5e-05 | N
30-01-19 | 02:21 | ZN9015:PA1 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 462 | 0.003866 | 8e-06 | N
30-01-19 | 07:51 | ZN1285:PA31 | URBAN | Asset Failure | HV | 2,639 | 63 | 0.11344 | 0.001789 | N
30-01-19 | 08:03 | ZN4545:PA41 | SHORT RURAL | Third Party | Fire | 1 | 130 | 0.000542 | 4e-06 | N
30-01-19 | 08:12 | 228:7487 | URBAN | Third Party | Other | 1 | 97 | 6.6e-05 | 1e-06 | N
30-01-19 | 10:08 | ZN3672:PA29 | SHORT RURAL | Network business | Network error | 148 | 72 | 0.044579 | 0.000619 | N
30-01-19 | 08:36 | 814:82285 | SHORT RURAL | Other | Other | 1 | 201 | 0.000839 | 4e-06 | N
30-01-19 | 08:41 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 163 | 0.000683 | 4e-06 | N
30-01-19 | 08:55 | 511:29873 | URBAN | Other | Other | 1 | 65 | 4.4e-05 | 1e-06 | N
28-01-19 | 09:43 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 62 | 0.000259 | 4e-06 | N
30-01-19 | 10:46 | ZN36100:PA12 | URBAN | Asset Failure | LV | 25 | 84 | 0.001423 | 1.7e-05 | N
30-01-19 | 11:01 | 217:33605 | URBAN | Third Party | Vehicle impact | 1 | 1,546 | 0.001048 | 1e-06 | N
30-01-19 | 12:02 | ZN847:PA19 | URBAN | Other | Other | 1 | 87 | 5.9e-05 | 1e-06 | N
30-01-19 | 14:55 | ZN10998:PA2 | URBAN | Other | Other | 1 | 129 | 8.8e-05 | 1e-06 | N
30-01-19 | 16:47 | ZN1648:PA15 | URBAN | Third Party | Other | 1 | 189 | 0.000128 | 1e-06 | N
30-01-19 | 17:32 | ZN35555:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 214 | 0.000145 | 1e-06 | N
30-01-19 | 18:11 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 39 | 0.000163 | 4e-06 | N
30-01-19 | 19:45 | ZN80:PA40 | URBAN | Asset Failure | LV | 84 | 10 | 0.000569 | 5.7e-05 | N
30-01-19 | 20:19 | 205:12213 | SHORT RURAL | Other | Other - Self Clearing Trigger | 89 | 51 | 0.018815 | 0.000372 | N
30-01-19 | 22:18 | ZN13000:PA5 | SHORT RURAL | Asset Failure | HV | 25 | 312 | 0.032631 | 0.000105 | N
31-01-19 | 02:59 | ZN9245:PA13 | URBAN | Other | Other - Self Clearing Trigger | 1,803 | 140 | 0.17149 | 0.001222 | Y
31-01-19 | 05:26 | 509:33395 | LONG RURAL | Animal | Animal impact | 77 | 430 | 11.6063 | 0.027018 | Y
31-01-19 | 06:55 | 801:74123 | SHORT RURAL | Animal | Animal impact | 1 | 95 | 0.000396 | 4e-06 | Y
31-01-19 | 09:30 | 810:74054 | LONG RURAL | Asset Failure | HV | 107 | 44 | 1.6449 | 0.037544 | Y
23-01-19 | 19:24 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 2,528 | 0.010633 | 4e-06 | N
31-01-19 | 07:57 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,863 | 0.007794 | 4e-06 | Y
31-01-19 | 08:28 | 239:82136 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 63 | 4.3e-05 | 1e-06 | Y
31-01-19 | 10:04 | ZN35400:PA101 | URBAN | Asset Failure | LV | 59 | 112 | 0.004479 | 4e-05 | Y
31-01-19 | 10:30 | 806:82667 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 190 | 0.000795 | 4e-06 | Y
31-01-19 | 11:22 | ZN2602:PA10 | URBAN | Asset Failure | Subtransmission | 695 | 64 | 0.030148 | 0.000471 | Y
31-01-19 | 11:22 | ZN2602:PA15 | URBAN | Asset Failure | Subtransmission | 2,049 | 64 | 0.088882 | 0.001389 | Y
31-01-19 | 11:22 | ZN2602:PA17 | URBAN | Asset Failure | Subtransmission | 1,558 | 64 | 0.067583 | 0.001056 | Y
31-01-19 | 11:22 | ZN2602:PA18 | URBAN | Asset Failure | Subtransmission | 1,422 | 64 | 0.061684 | 0.000964 | Y
31-01-19 | 11:22 | ZN2602:PA19 | URBAN | Asset Failure | Subtransmission | 5 | 64 | 0.000217 | 3e-06 | Y
31-01-19 | 11:22 | ZN2602:PA20 | URBAN | Asset Failure | Subtransmission | 1,497 | 64 | 0.064937 | 0.001015 | Y
31-01-19 | 11:22 | ZN2602:PA21 | URBAN | Asset Failure | Subtransmission | 1,837 | 64 | 0.079686 | 0.001245 | Y
31-01-19 | 11:22 | ZN2602:PA22 | URBAN | Asset Failure | Subtransmission | 354 | 64 | 0.015356 | 0.00024 | Y
31-01-19 | 11:22 | ZN2602:PA24 | URBAN | Asset Failure | Subtransmission | 40 | 64 | 0.001735 | 2.7e-05 | Y
31-01-19 | 11:22 | ZN2602:PA27 | URBAN | Asset Failure | Subtransmission | 2,042 | 68 | 0.094115 | 0.001384 | Y
31-01-19 | 11:22 | ZN2602:PA28 | URBAN | Asset Failure | Subtransmission | 1,224 | 68 | 0.056413 | 0.00083 | Y
31-01-19 | 11:22 | ZN2602:PA29 | URBAN | Asset Failure | Subtransmission | 2,192 | 68 | 0.10103 | 0.001486 | Y
31-01-19 | 11:22 | ZN2602:PA3 | URBAN | Asset Failure | Subtransmission | 1,530 | 64 | 0.066369 | 0.001037 | Y
31-01-19 | 11:22 | ZN2602:PA30 | URBAN | Asset Failure | Subtransmission | 1,910 | 68 | 0.088031 | 0.001295 | Y
31-01-19 | 11:22 | ZN2602:PA31 | URBAN | Asset Failure | Subtransmission | 1,098 | 68 | 0.050606 | 0.000744 | Y
31-01-19 | 11:22 | ZN2602:PA32 | URBAN | Asset Failure | Subtransmission | 1,008 | 68 | 0.046458 | 0.000683 | Y
31-01-19 | 11:22 | ZN2602:PA33 | URBAN | Asset Failure | Subtransmission | 1,034 | 68 | 0.047656 | 0.000701 | Y
31-01-19 | 11:22 | ZN2602:PA34 | URBAN | Asset Failure | Subtransmission | 1,231 | 68 | 0.056736 | 0.000834 | Y
31-01-19 | 11:22 | ZN2602:PA35 | URBAN | Asset Failure | Subtransmission | 1,585 | 68 | 0.073052 | 0.001074 | Y
31-01-19 | 11:22 | ZN2602:PA36 | URBAN | Asset Failure | Subtransmission | 1,360 | 68 | 0.062682 | 0.000922 | Y
31-01-19 | 11:22 | ZN2602:PA4 | URBAN | Asset Failure | Subtransmission | 1,785 | 64 | 0.07743 | 0.00121 | Y
31-01-19 | 11:22 | ZN2602:PA41 | URBAN | Asset Failure | Subtransmission | 1,496 | 68 | 0.06895 | 0.001014 | Y
31-01-19 | 11:22 | ZN2602:PA42 | URBAN | Asset Failure | Subtransmission | 2,638 | 68 | 0.12158 | 0.001788 | Y
31-01-19 | 11:22 | ZN2602:PA7 | URBAN | Asset Failure | Subtransmission | 2 | 64 | 8.7e-05 | 1e-06 | Y
31-01-19 | 11:22 | ZN2602:PA8 | URBAN | Asset Failure | Subtransmission | 999 | 64 | 0.043335 | 0.000677 | Y
31-01-19 | 11:22 | ZN2602:PA9 | URBAN | Asset Failure | Subtransmission | 1,059 | 64 | 0.045938 | 0.000718 | Y
31-01-19 | 11:22 | ZN3155:PA11 | URBAN | Asset Failure | Subtransmission | 538 | 53 | 0.019326 | 0.000365 | Y
31-01-19 | 11:22 | ZN3155:PA12 | URBAN | Asset Failure | Subtransmission | 1,205 | 53 | 0.043287 | 0.000817 | Y
31-01-19 | 11:22 | ZN3155:PA15 | URBAN | Asset Failure | Subtransmission | 878 | 53 | 0.03154 | 0.000595 | Y
31-01-19 | 11:22 | ZN3155:PA16 | URBAN | Asset Failure | Subtransmission | 718 | 53 | 0.025792 | 0.000487 | Y
31-01-19 | 11:22 | ZN3155:PA17 | URBAN | Asset Failure | Subtransmission | 1,136 | 53 | 0.040808 | 0.00077 | Y
31-01-19 | 11:22 | ZN3155:PA18 | URBAN | Asset Failure | Subtransmission | 453 | 53 | 0.016273 | 0.000307 | Y
31-01-19 | 11:22 | ZN3155:PA19 | URBAN | Asset Failure | Subtransmission | 973 | 53 | 0.034953 | 0.000659 | Y
31-01-19 | 11:22 | ZN3155:PA20 | URBAN | Asset Failure | Subtransmission | 1,165 | 53 | 0.04185 | 0.00079 | Y
31-01-19 | 11:22 | ZN3155:PA21 | URBAN | Asset Failure | Subtransmission | 498 | 53 | 0.017889 | 0.000338 | Y
31-01-19 | 11:22 | ZN3155:PA22 | URBAN | Asset Failure | Subtransmission | 657 | 53 | 0.023601 | 0.000445 | Y
31-01-19 | 11:22 | ZN3155:PA23 | URBAN | Asset Failure | Subtransmission | 2,145 | 53 | 0.077054 | 0.001454 | Y
31-01-19 | 11:22 | ZN3155:PA24 | URBAN | Asset Failure | Subtransmission | 701 | 53 | 0.025182 | 0.000475 | Y
29-01-19 | 17:43 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 87 | 0.000364 | 4e-06 | N
31-01-19 | 11:23 | ZN36800:PA56 | URBAN | Network business | Network error | 55 | 20 | 0.000746 | 3.7e-05 | Y
31-01-19 | 12:23 | ZN3472:PA8 | URBAN | Other | Other | 1 | 76 | 5.2e-05 | 1e-06 | Y
31-01-19 | 12:37 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 64 | 0.044912 | 0.000702 | Y
31-01-19 | 15:00 | ZN80:PA32 | URBAN | Vegetation | Vegetation Blow/Fall In | 56 | 20 | 0.000759 | 3.8e-05 | Y
31-01-19 | 12:57 | ZN2602:PA31 | URBAN | Asset Failure | LV | 87 | 213 | 0.012555 | 5.9e-05 | Y
31-01-19 | 13:09 | ZN15001:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 151 | 0.002449 | 1.6e-05 | Y
31-01-19 | 13:09 | ZN15008:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 151 | 0.000102 | 1e-06 | Y
30-01-19 | 15:40 | 810:74054 | LONG RURAL | Asset Failure | HV | 2 | 95 | 0.066667 | 0.000702 | N
31-01-19 | 13:34 | ZN15006:PA15 | URBAN | Asset Failure | LV | 1 | 477 | 0.000323 | 1e-06 | Y
31-01-19 | 14:04 | ZN35900:PA6 | URBAN | Third Party | Vehicle impact | 338 | 123 | 0.028163 | 0.000229 | Y
31-01-19 | 14:11 | ZN12660:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 500 | 0.002092 | 4e-06 | Y
31-01-19 | 14:14 | 227:13015 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 126 | 0.004745 | 3.8e-05 | Y
31-01-19 | 14:24 | 239:82136 | URBAN | Other | Other | 1 | 124 | 8.4e-05 | 1e-06 | Y
31-01-19 | 14:31 | ZN3154:PA18 | URBAN | Other | Other - Self Clearing Trigger | 52 | 259 | 0.009114 | 3.5e-05 | Y
31-01-19 | 14:55 | ZN116:PA2 | URBAN | Other | Other - Self Clearing Trigger | 1 | 365 | 0.000247 | 1e-06 | Y
31-01-19 | 15:09 | ZN4545:PA29 | URBAN | Asset Failure | HV | 64 | 154 | 0.006693 | 4.3e-05 | Y
31-01-19 | 15:09 | ZN4545:PA36 | URBAN | Asset Failure | HV | 77 | 155 | 0.008089 | 5.2e-05 | Y
31-01-19 | 15:24 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 86 | 0.001574 | 1.8e-05 | Y
31-01-19 | 15:41 | ZN10993:PA22 | URBAN | Other | Other | 793 | 4 | 0.00215 | 0.000537 | Y
31-01-19 | 15:41 | ZN10999:PA10 | URBAN | Other | Other | 2,754 | 4 | 0.007466 | 0.001867 | Y
31-01-19 | 15:44 | ZN36300:PA5 | URBAN | Asset Failure | HV | 1,316 | 74 | 0.065593 | 0.000892 | Y
28-01-19 | 12:38 | ZN129:PA35 | URBAN | Network business | Network error | 34 | 4 | 9.2e-05 | 2.3e-05 | N
31-01-19 | 15:59 | ZN2310:PA18 | URBAN | Asset Failure | LV | 44 | 1,096 | 0.032681 | 3e-05 | Y
31-01-19 | 16:06 | ZN10999:PA10 | URBAN | Asset Failure | LV | 73 | 92 | 0.004573 | 4.9e-05 | Y
31-01-19 | 16:08 | ZN12620:PA1 | SHORT RURAL | Other | Other - Arcing | 1 | 385 | 0.001612 | 4e-06 | Y
31-01-19 | 16:16 | ZN874:PA8 | URBAN | Overloads |  | 1 | 403 | 0.000273 | 1e-06 | Y
31-01-19 | 16:27 | ZN35400:PA101 | URBAN | Network business | Network error | 59 | 238 | 0.009517 | 4e-05 | Y
31-01-19 | 16:26 | ZN9252:PA30 | URBAN | Asset Failure | LV | 53 | 584 | 0.020979 | 3.6e-05 | Y
31-01-19 | 16:28 | ZN690:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 107 | 0.002891 | 2.7e-05 | Y
31-01-19 | 16:35 | ZN129:PA52 | URBAN | Asset Failure | HV | 1,057 | 134 | 0.095856 | 0.000716 | Y
31-01-19 | 16:51 | ZN1610:PA17 | URBAN | Asset Failure | HV | 375 | 63 | 0.01596 | 0.000254 | Y
31-01-19 | 16:42 | 515:35192 | SHORT RURAL | Asset Failure | HV | 2 | 38 | 0.000318 | 8e-06 | Y
31-01-19 | 17:08 | ZN1285:PA17 | URBAN | Network business | Network error | 142 | 862 | 0.082964 | 9.6e-05 | Y
31-01-19 | 17:25 | ZN9245:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,070 | 337 | 0.24432 | 0.000725 | Y
31-01-19 | 17:25 | ZN9245:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 14 | 358 | 0.003397 | 9e-06 | Y
31-01-19 | 17:34 | ZN690:PA10 | URBAN | Overloads |  | 12 | 16 | 0.000134 | 8e-06 | Y
31-01-19 | 17:34 | ZN690:PA5 | URBAN | Overloads |  | 585 | 16 | 0.006529 | 0.000397 | Y
31-01-19 | 17:38 | ZN36200:PA8 | SHORT RURAL | Asset Failure | Distribution substation | 81 | 114 | 0.03857 | 0.000339 | Y
31-01-19 | 17:38 | ZN1287:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 134 | 132 | 0.011955 | 9.1e-05 | Y
31-01-19 | 17:45 | ZN35900:PA7 | SHORT RURAL | Asset Failure | HV | 8 | 91 | 0.003046 | 3.3e-05 | Y
31-01-19 | 17:49 | ZN1287:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 75 | 121 | 0.006142 | 5.1e-05 | Y
31-01-19 | 17:52 | ZN2310:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 468 | 0.011734 | 2.5e-05 | Y
31-01-19 | 17:52 | ZN2466:PA5 | URBAN | Other | Other - Self Clearing Trigger | 83 | 87 | 0.00491 | 5.6e-05 | Y
31-01-19 | 17:52 | ZN9550:PA36 | URBAN | Weather |  | 62 | 1,047 | 0.044004 | 4.2e-05 | Y
31-01-19 | 17:53 | ZN9252:PA27 | URBAN | Weather |  | 58 | 526 | 0.020693 | 3.9e-05 | Y
31-01-19 | 18:36 | ZN9700:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 19 | 1,579 | 0.020334 | 1.3e-05 | Y
31-01-19 | 17:58 | ZN690:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 572 | 0.015506 | 2.7e-05 | Y
31-01-19 | 18:05 | ZN10994:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 845 | 127 | 0.072693 | 0.000573 | Y
31-01-19 | 18:35 | ZN1193:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 15 | 250 | 0.00254 | 1e-05 | Y
31-01-19 | 18:48 | ZN262:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 94 | 1,212 | 0.077188 | 6.4e-05 | Y
31-01-19 | 18:25 | ZN116:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,234 | 0.000837 | 1e-06 | Y
31-01-19 | 18:25 | ZN874:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 934 | 0.027225 | 2.9e-05 | Y
31-01-19 | 18:41 | ZN262:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 348 | 0.010862 | 3.1e-05 | Y
31-01-19 | 18:29 | ZN9035:PA7 | URBAN | Vegetation | Vegetation Grow In | 1 | 270 | 0.000183 | 1e-06 | Y
31-01-19 | 18:31 | ZN3672:PA21 | SHORT RURAL | Asset Failure | LV | 60 | 109 | 0.02724 | 0.000251 | Y
31-01-19 | 18:37 | ZN15012:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 3 | 333 | 0.000677 | 2e-06 | Y
31-01-19 | 18:41 | ZN9118:PA26 | URBAN | Other | Other - Self Clearing Trigger | 24 | 608 | 0.009891 | 1.6e-05 | Y
31-01-19 | 18:43 | ZN10995:PA13 | URBAN | Asset Failure | LV | 1 | 906 | 0.000614 | 1e-06 | Y
31-01-19 | 18:44 | ZN1287:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 135 | 9.2e-05 | 1e-06 | Y
31-01-19 | 18:45 | ZN80:PA31 | URBAN | Weather |  | 68 | 135 | 0.006222 | 4.6e-05 | Y
31-01-19 | 18:47 | ZN10999:PA12 | URBAN | Other | Other - Self Clearing Trigger | 3,152 | 140 | 0.29945 | 0.002136 | Y
31-01-19 | 18:48 | ZN9118:PA8 | URBAN | Other | Other - Self Clearing Trigger | 45 | 551 | 0.016816 | 3.1e-05 | Y
31-01-19 | 19:44 | ZN1287:PA5 | URBAN | Weather |  | 35 | 150 | 0.003562 | 2.4e-05 | Y
31-01-19 | 18:52 | ZN10995:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 748 | 0.021287 | 2.8e-05 | Y
31-01-19 | 18:53 | ZN1285:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 1,322 | 0.034049 | 2.6e-05 | Y
31-01-19 | 18:54 | ZN2835:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,566 | 0.001061 | 1e-06 | Y
31-01-19 | 18:56 | ZN35900:PA20 | URBAN | Other | Other | 1 | 63 | 4.3e-05 | 1e-06 | Y
31-01-19 | 18:59 | ZN262:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 15 | 1,283 | 0.013044 | 1e-05 | Y
31-01-19 | 19:39 | ZN1287:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 986 | 0.040766 | 4.1e-05 | Y
31-01-19 | 21:22 | ZN12650:PA10 | URBAN | Third Party | Other | 43 | 55 | 0.001603 | 2.9e-05 | Y
31-01-19 | 19:06 | ZN9252:PA24 | URBAN | Asset Failure | LV | 1 | 353 | 0.000239 | 1e-06 | Y
31-01-19 | 20:20 | ZN36800:PA56 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 1,060 | 0.024427 | 2.3e-05 | Y
31-01-19 | 19:12 | ZN2400:PA22 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 40 | 267 | 0.044727 | 0.000167 | Y
31-01-19 | 19:18 | ZN847:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 116 | 277 | 0.021803 | 7.9e-05 | Y
31-01-19 | 20:14 | ZN2310:PA3 | URBAN | Other | Other - Self Clearing Trigger | 42 | 271 | 0.00771 | 2.8e-05 | Y
31-01-19 | 19:21 | ZN1673:PA11 | URBAN | Network business | Network error | 36 | 219 | 0.005344 | 2.4e-05 | Y
31-01-19 | 19:22 | ZN9252:PA30 | URBAN | Asset Failure | LV | 1 | 247 | 0.000168 | 1e-06 | Y
31-01-19 | 19:54 | ZN9700:PA16 | URBAN | Other | Other - Self Clearing Trigger | 29 | 474 | 0.009315 | 2e-05 | Y
31-01-19 | 19:23 | ZN1285:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 67 | 696 | 0.031617 | 4.5e-05 | Y
31-01-19 | 19:32 | ZN1287:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 178 | 0.00012 | 1e-06 | Y
31-01-19 | 19:27 | ZN9900:PA12 | URBAN | Other | Other | 1 | 27 | 1.9e-05 | 1e-06 | Y
31-01-19 | 19:29 | ZN9252:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 840 | 0.000569 | 1e-06 | Y
01-02-19 | 21:33 | ZN35600:PA1 | URBAN | Asset Failure | LV | 74 | 21 | 0.001068 | 5e-05 | N
31-01-19 | 19:34 | ZN2568:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,451 | 0.000983 | 1e-06 | Y
31-01-19 | 19:48 | ZN9037:PA9 | URBAN | Weather |  | 1 | 371 | 0.000252 | 1e-06 | Y
31-01-19 | 19:49 | ZN1285:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,151 | 0.00078 | 1e-06 | Y
31-01-19 | 19:55 | ZN10994:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 138 | 884 | 0.082643 | 9.4e-05 | Y
31-01-19 | 20:00 | ZN9245:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 66 | 827 | 0.03698 | 4.5e-05 | Y
31-01-19 | 19:59 | ZN690:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 68 | 516 | 0.023769 | 4.6e-05 | Y
31-01-19 | 19:59 | ZN9037:PA9 | URBAN | Weather |  | 1 | 360 | 0.000244 | 1e-06 | Y
31-01-19 | 20:01 | ZN15010:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 109 | 0.004502 | 4.1e-05 | Y
31-01-19 | 20:01 | ZN8000:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 899 | 0.000609 | 1e-06 | Y
31-01-19 | 20:01 | ZN2310:PA14 | URBAN | Weather |  | 39 | 759 | 0.02005 | 2.6e-05 | Y
31-01-19 | 20:03 | ZN15006:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 538 | 0.000365 | 1e-06 | Y
31-01-19 | 20:03 | ZN10993:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 837 | 0.000567 | 1e-06 | Y
31-01-19 | 20:26 | ZN1287:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 199 | 0.008219 | 4.1e-05 | Y
31-01-19 | 20:12 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,271 | 0.005316 | 4e-06 | Y
31-01-19 | 20:15 | ZN35555:PA20 | URBAN | Weather |  | 1 | 1,125 | 0.000762 | 1e-06 | Y
01-02-19 | 00:40 | ZN129:PA63 | URBAN | Asset Failure | LV | 62 | 631 | 0.026517 | 4.2e-05 | N
31-01-19 | 19:56 | ZN129:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 915 | 0.037831 | 4.1e-05 | Y
31-01-19 | 20:25 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 125 | 0.002027 | 1.6e-05 | Y
31-01-19 | 20:29 | ZN3154:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 240 | 0.000163 | 1e-06 | Y
31-01-19 | 20:30 | ZN15014:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 63 | 72 | 0.003067 | 4.3e-05 | Y
31-01-19 | 20:42 | ZN15010:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 228 | 0.000154 | 1e-06 | Y
31-01-19 | 21:19 | 227:13018 | URBAN | Asset Failure | HV | 637 | 89 | 0.038426 | 0.000432 | Y
31-01-19 | 21:23 | ZN12690:PA16 | SHORT RURAL | Weather |  | 1 | 206 | 0.000864 | 4e-06 | Y
01-02-19 | 02:20 | ZN15002:PA6 | URBAN | Asset Failure | LV | 27 | 110 | 0.002013 | 1.8e-05 | N
31-01-19 | 21:59 | ZN262:PA41 | URBAN | Asset Failure | Distribution substation | 1 | 270 | 0.000183 | 1e-06 | Y
31-01-19 | 22:12 | ZN12610:PA13 | SHORT RURAL | Other | Other | 1 | 1,200 | 0.005022 | 4e-06 | Y
31-01-19 | 22:13 | 257:81985 | URBAN | Asset Failure | LV | 1 | 220 | 0.000149 | 1e-06 | Y
31-01-19 | 22:13 | 257:81991 | URBAN | Asset Failure | LV | 21 | 212 | 0.003018 | 1.4e-05 | Y
31-01-19 | 22:15 | 210:83466 | URBAN | Other | Other | 1 | 340 | 0.000231 | 1e-06 | Y
01-02-19 | 01:34 | ZN12610:PA18 | URBAN | Other | Other - Self Clearing Trigger | 88 | 565 | 0.033704 | 6e-05 | N
31-01-19 | 22:25 | ZN398:PA24 | URBAN | Other | Other | 1 | 167 | 0.000113 | 1e-06 | Y
31-01-19 | 23:04 | 222:33602 | URBAN | Asset Failure | HV | 930 | 335 | 0.21137 | 0.00063 | Y
31-01-19 | 23:14 | ZN12620:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 319 | 0.001334 | 4e-06 | Y
31-01-19 | 23:21 | ZN9118:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 309 | 0.005444 | 1.8e-05 | Y
01-02-19 | 02:31 | 228:7487 | URBAN | Asset Failure | HV | 1,079 | 88 | 0.06451 | 0.000731 | N
01-02-19 | 00:55 | 417:80491 | SHORT RURAL | Asset Failure | HV | 6 | 701 | 0.017599 | 2.5e-05 | N
01-02-19 | 01:30 | ZN1193:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 16 | 30 | 0.000325 | 1.1e-05 | N
01-02-19 | 01:50 | ZN9037:PA9 | URBAN | Other | Other - Self Clearing Trigger | 57 | 415 | 0.016028 | 3.9e-05 | N
01-02-19 | 03:49 | ZN9550:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 80 | 220 | 0.011955 | 5.4e-05 | N
01-02-19 | 04:11 | ZN2310:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 341 | 0.008555 | 2.5e-05 | N
01-02-19 | 04:11 | ZN35800:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 494 | 0.002009 | 4e-06 | N
01-02-19 | 04:11 | ZN35800:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 15 | 494 | 0.005022 | 1e-05 | N
01-02-19 | 04:15 | 256:80638 | URBAN | Other | Other | 1 | 158 | 0.000107 | 1e-06 | N
01-02-19 | 04:17 | 202:34250 | URBAN | Other | Other | 1 | 115 | 7.8e-05 | 1e-06 | N
01-02-19 | 04:28 | ZN188:PA26 | URBAN | Other | Other - Arcing | 1 | 421 | 0.000286 | 1e-06 | N
01-02-19 | 04:32 | ZN8000:PA1 | URBAN | Other | Other - Arcing | 1 | 403 | 0.000273 | 1e-06 | N
01-02-19 | 05:19 | ZN12570:PA37 | SHORT RURAL | Asset Failure | HV | 1,523 | 152 | 0.96699 | 0.006373 | N
01-02-19 | 05:25 | ZN2310:PA14 | URBAN | Other | Other - Self Clearing Trigger | 28 | 245 | 0.00465 | 1.9e-05 | N
01-02-19 | 05:29 | ZN9900:PA1 | URBAN | Other | Other - Self Clearing Trigger | 24 | 371 | 0.006032 | 1.6e-05 | N
01-02-19 | 06:03 | ZN15011:PA10 | URBAN | Other | Other - Arcing | 1 | 337 | 0.000229 | 1e-06 | N
01-02-19 | 06:17 | 812:19071 | SHORT RURAL | Asset Failure | HV | 28 | 90 | 0.010515 | 0.000117 | N
01-02-19 | 06:20 | ZN2466:PA7 | URBAN | Third Party | Vehicle impact | 1 | 1,600 | 0.001084 | 1e-06 | N
01-02-19 | 06:37 | ZN36800:PA49 | URBAN | Asset Failure | LV | 32 | 583 | 0.012638 | 2.2e-05 | N
01-02-19 | 07:16 | ZN35600:PA1 | URBAN | Other | Other - Arcing | 1 | 463 | 0.000314 | 1e-06 | N
01-02-19 | 07:36 | 240:34849 | URBAN | Asset Failure | Distribution substation | 97 | 49 | 0.003203 | 6.6e-05 | N
01-02-19 | 23:18 | ZN12580:PA1 | URBAN | Other | Other - Arcing | 1 | 1,207 | 0.000818 | 1e-06 | N
01-02-19 | 07:38 | ZN8000:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 357 | 0.006299 | 1.8e-05 | N
01-02-19 | 07:47 | ZN4545:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 19 | 3,102 | 0.039949 | 1.3e-05 | N
01-02-19 | 08:21 | 239:82133 | URBAN | Other | Other - Arcing | 1 | 219 | 0.000148 | 1e-06 | N
01-02-19 | 08:27 | ZN342:PA18 | URBAN | Weather |  | 1 | 212 | 0.000144 | 1e-06 | N
01-02-19 | 08:35 | ZN36300:PA5 | URBAN | Other | Other - Arcing | 1 | 1,405 | 0.000952 | 1e-06 | N
01-02-19 | 08:49 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 196 | 0.00082 | 4e-06 | N
01-02-19 | 09:10 | 256:80646 | URBAN | Other | Other | 1 | 91 | 6.1e-05 | 1e-06 | N
01-02-19 | 09:21 | ZN2602:PA30 | URBAN | Other | Other - Arcing | 2 | 519 | 0.000703 | 1e-06 | N
01-02-19 | 09:37 | ZN12610:PA25 | URBAN | Other | Other - Arcing | 2 | 469 | 0.000635 | 1e-06 | N
01-02-19 | 10:11 | ZN4545:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 229 | 0.000155 | 1e-06 | N
01-02-19 | 11:09 | ZN690:PA34 | URBAN | Weather |  | 6 | 500 | 0.002034 | 4e-06 | N
01-02-19 | 11:31 | ZN195:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 4,709 | 0.003191 | 1e-06 | N
01-02-19 | 11:32 | ZN7481:PA1 | URBAN | Vegetation | Vegetation Grow In | 1 | 448 | 0.000304 | 1e-06 | N
01-02-19 | 13:55 | 526:34641 | SHORT RURAL | Asset Failure | LV | 1 | 79 | 0.000331 | 4e-06 | N
01-02-19 | 14:08 | ZN12610:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 140 | 0.000585 | 4e-06 | N
01-02-19 | 14:50 | ZN9252:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 53 | 48 | 0.001724 | 3.6e-05 | N
01-02-19 | 15:22 | 261:81864 | URBAN | Asset Failure | LV | 1 | 344 | 0.000233 | 1e-06 | N
01-02-19 | 16:42 | ZN12650:PA12 | URBAN | Other | Other - Arcing | 1 | 1,579 | 0.00107 | 1e-06 | N
01-02-19 | 16:49 | ZN12650:PA2 | URBAN | Asset Failure | HV | 372 | 97 | 0.024566 | 0.000252 | N
01-02-19 | 16:56 | ZN15009:PA5 | URBAN | Asset Failure | LV | 1 | 1,324 | 0.000897 | 1e-06 | N
01-02-19 | 17:02 | ZN342:PA17 | URBAN | Other | Other - Arcing | 1 | 267 | 0.000181 | 1e-06 | N
01-02-19 | 17:05 | ZN12650:PA9 | URBAN | Other | Other - Arcing | 1 | 180 | 0.000122 | 1e-06 | N
01-02-19 | 17:11 | ZN1193:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 889 | 0.000602 | 1e-06 | N
01-02-19 | 17:11 | ZN12650:PA17 | URBAN | Other | Other - Arcing | 1 | 172 | 0.000117 | 1e-06 | N
01-02-19 | 17:27 | ZN180:PA42 | URBAN | Other | Other - Arcing | 1 | 479 | 0.000325 | 1e-06 | N
01-02-19 | 17:34 | ZN12640:PA5 | URBAN | Other | Other - Arcing | 5 | 358 | 0.001213 | 3e-06 | N
01-02-19 | 17:43 | ZN3155:PA35 | URBAN | Asset Failure | LV | 1 | 814 | 0.000552 | 1e-06 | N
01-02-19 | 17:47 | ZN1193:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2,159 | 0.001463 | 1e-06 | N
01-02-19 | 17:57 | ZN180:PA42 | URBAN | Other | Other - Arcing | 1 | 450 | 0.000305 | 1e-06 | N
01-02-19 | 17:59 | ZN847:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2,671 | 0.00181 | 1e-06 | N
01-02-19 | 18:00 | ZN36200:PA1 | URBAN | Other | Other - Arcing | 1 | 1,349 | 0.000914 | 1e-06 | N
01-02-19 | 18:01 | ZN12570:PA35 | URBAN | Other | Other - Arcing | 1 | 1,523 | 0.001033 | 1e-06 | N
01-02-19 | 18:02 | ZN129:PA41 | URBAN | Other | Other - Arcing | 1 | 2,860 | 0.001938 | 1e-06 | N
01-02-19 | 18:50 | ZN1068:PA26 | URBAN | Other | Other - Arcing | 3 | 1,345 | 0.002735 | 2e-06 | N
01-02-19 | 19:05 | ZN9037:PA7 | URBAN | Other | Other - Arcing | 1 | 955 | 0.000647 | 1e-06 | N
01-02-19 | 19:19 | ZN187:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 368 | 0.00025 | 1e-06 | N
01-02-19 | 19:23 | ZN35600:PA22 | URBAN | Other | Other - Arcing | 1 | 715 | 0.000484 | 1e-06 | N
01-02-19 | 19:26 | ZN15006:PA16 | URBAN | Other | Other - Arcing | 1 | 711 | 0.000482 | 1e-06 | N
01-02-19 | 19:36 | ZN262:PA32 | URBAN | Other | Other - Arcing | 2 | 1,191 | 0.001615 | 1e-06 | N
01-02-19 | 19:51 | ZN15006:PA16 | URBAN | Other | Other - Arcing | 1 | 686 | 0.000465 | 1e-06 | N
01-02-19 | 19:55 | ZN1068:PA26 | URBAN | Other | Other - Arcing | 1 | 3,567 | 0.002418 | 1e-06 | N
01-02-19 | 20:01 | ZN10994:PA21 | URBAN | Asset Failure | LV | 56 | 239 | 0.009068 | 3.8e-05 | N
01-02-19 | 20:09 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 271 | 38 | 0.04309 | 0.001134 | N
01-02-19 | 20:15 | 235:2123 | URBAN | Other | Other - Arcing | 1 | 232 | 0.000157 | 1e-06 | N
01-02-19 | 20:20 | ZN2602:PA15 | URBAN | Other | Other - Arcing | 1 | 453 | 0.000307 | 1e-06 | N
01-02-19 | 20:28 | ZN9037:PA16 | URBAN | Other | Other - Arcing | 1 | 337 | 0.000228 | 1e-06 | N
01-02-19 | 20:32 | ZN188:PA34 | URBAN | Other | Other - Arcing | 1 | 387 | 0.000262 | 1e-06 | N
01-02-19 | 20:33 | ZN36200:PA1 | URBAN | Other | Other - Arcing | 1 | 181 | 0.000122 | 1e-06 | N
01-02-19 | 20:55 | ZN9037:PA8 | URBAN | Other | Other - Arcing | 1 | 418 | 0.000283 | 1e-06 | N
01-02-19 | 20:38 | ZN10994:PA18 | URBAN | Other | Other - Arcing | 1 | 529 | 0.000359 | 1e-06 | N
01-02-19 | 20:39 | 235:2123 | URBAN | Other | Other | 1 | 55 | 3.8e-05 | 1e-06 | N
01-02-19 | 20:41 | ZN690:PA12 | URBAN | Asset Failure | LV | 48 | 69 | 0.002231 | 3.3e-05 | N
01-02-19 | 20:49 | ZN36100:PA21 | URBAN | Other | Other - Arcing | 1 | 628 | 0.000426 | 1e-06 | N
01-02-19 | 20:49 | ZN12570:PA26 | URBAN | Other | Other - Arcing | 1 | 1,332 | 0.000903 | 1e-06 | N
01-02-19 | 20:59 | ZN2400:PA11 | SHORT RURAL | Other | Other - Arcing | 1 | 1,580 | 0.006612 | 4e-06 | N
01-02-19 | 21:10 | ZN12690:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 1,312 | 0.005488 | 4e-06 | N
01-02-19 | 21:19 | ZN36100:PA12 | URBAN | Other | Other - Arcing | 1 | 1,252 | 0.000849 | 1e-06 | N
01-02-19 | 21:35 | ZN35370:PA10 | SHORT RURAL | Asset Failure | HV | 189 | 102 | 0.080284 | 0.000791 | N
01-02-19 | 21:35 | ZN965:PA24 | URBAN | Asset Failure | HV | 489 | 131 | 0.043419 | 0.000331 | N
01-02-19 | 21:44 | ZN9252:PA27 | URBAN | Other | Other - Arcing | 1 | 885 | 0.0006 | 1e-06 | N
01-02-19 | 21:50 | 508:82575 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 397 | 61 | 0.10205 | 0.001661 | N
02-02-19 | 00:03 | ZN10998:PA31 | URBAN | Other | Other - Self Clearing Trigger | 1 | 652 | 0.000442 | 1e-06 | N
02-02-19 | 00:03 | ZN10998:PA8 | URBAN | Other | Other - Self Clearing Trigger | 15 | 611 | 0.006215 | 1e-05 | N
01-02-19 | 22:16 | 512:83743 | SHORT RURAL | Asset Failure | LV | 1 | 114 | 0.000476 | 4e-06 | N
01-02-19 | 23:46 | ZN2466:PA25 | SHORT RURAL | Asset Failure | LV | 93 | 1,154 | 0.44893 | 0.000389 | N
01-02-19 | 23:47 | ZN12600:PA11 | URBAN | Asset Failure | HV | 937 | 103 | 0.065459 | 0.000635 | N
02-02-19 | 03:43 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 141 | 193 | 9.5551 | 0.049508 | N
02-02-19 | 04:02 | ZN7481:PA1 | URBAN | Other | Other - Arcing | 1 | 427 | 0.000289 | 1e-06 | N
02-02-19 | 05:05 | ZN2568:PA18 | URBAN | Third Party | Dig-in | 1 | 50 | 3.4e-05 | 1e-06 | N
02-02-19 | 05:16 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 404 | 0.00169 | 4e-06 | N
02-02-19 | 05:39 | ZN12600:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 857 | 132 | 0.47386 | 0.003586 | N
02-02-19 | 06:44 | ZN690:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 481 | 0.016296 | 3.4e-05 | N
02-02-19 | 06:48 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 587 | 0.007165 | 1.2e-05 | N
02-02-19 | 06:51 | ZN5868:PA30 | URBAN | Other | Other - Arcing | 1 | 1,375 | 0.000932 | 1e-06 | N
02-02-19 | 08:35 | ZN9118:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 78 | 403 | 0.13159 | 0.000326 | N
02-02-19 | 08:42 | ZN2635:PA31 | URBAN | Third Party | Dig-in | 2,072 | 99 | 0.13897 | 0.001405 | N
02-02-19 | 09:04 | 206:34438 | URBAN | Vegetation | Vegetation Blow/Fall In | 51 | 171 | 0.005914 | 3.5e-05 | N
02-02-19 | 09:28 | 239:82136 | URBAN | Other | Other | 1 | 71 | 4.8e-05 | 1e-06 | N
02-02-19 | 10:22 | 814:82291 | SHORT RURAL | Other | Other - Self Clearing Trigger | 463 | 180 | 0.34929 | 0.001937 | N
02-02-19 | 10:26 | ZN1648:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 283 | 0.000192 | 1e-06 | N
02-02-19 | 10:43 | ZN36100:PA23 | URBAN | Third Party | Vehicle impact | 104 | 452 | 0.031879 | 7.1e-05 | N
02-02-19 | 10:59 | ZN8700:PA63 64ABC | CBD | Asset Failure | LV | 19 | 326 | 0.20241 | 0.000621 | N
02-02-19 | 11:12 | ZN2568:PA27 | URBAN | Other | Other - Arcing | 1 | 418 | 0.000284 | 1e-06 | N
02-02-19 | 11:44 | ZN4545:PA25 | URBAN | Other | Other | 1 | 267 | 0.000181 | 1e-06 | N
02-02-19 | 12:28 | ZN2568:PA29 | URBAN | Asset Failure | LV | 1 | 207 | 0.00014 | 1e-06 | N
02-02-19 | 14:30 | ZN847:PA7 | URBAN | Asset Failure | HV | 1,319 | 131 | 0.11718 | 0.000894 | N
02-02-19 | 15:02 | 222:33602 | URBAN | Other | Other - Self Clearing Trigger | 69 | 68 | 0.003182 | 4.7e-05 | N
02-02-19 | 16:17 | ZN10994:PA3 | URBAN | Asset Failure | LV | 1 | 1,601 | 0.001086 | 1e-06 | N
02-02-19 | 17:45 | 807:74179 | SHORT RURAL | Asset Failure | HV | 107 | 202 | 0.090625 | 0.000448 | N
02-02-19 | 19:25 | ZN129:PA41 | URBAN | Asset Failure | HV | 262 | 59 | 0.010483 | 0.000178 | N
03-02-19 | 01:28 | ZN2602:PA30 | URBAN | Asset Failure | HV | 1,910 | 95 | 0.12353 | 0.001295 | N
02-02-19 | 20:54 | 222:33602 | URBAN | Asset Failure | HV | 69 | 45 | 0.002113 | 4.7e-05 | N
02-02-19 | 22:08 | ZN12610:PA10 | URBAN | Other | Other - Arcing | 1 | 1,074 | 0.000728 | 1e-06 | N
02-02-19 | 22:36 | ZN9037:PA16 | URBAN | Other | Other - Arcing | 1 | 1,516 | 0.001028 | 1e-06 | N
03-02-19 | 02:30 | 507:80923 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1,013 | 97 | 0.41295 | 0.004239 | N
03-02-19 | 02:57 | ZN2602:PA8 | URBAN | Other | Other - Self Clearing Trigger | 56 | 353 | 0.013389 | 3.8e-05 | N
03-02-19 | 08:42 | ZN15008:PA5 | URBAN | Asset Failure | LV | 1 | 301 | 0.000204 | 1e-06 | N
03-02-19 | 09:20 | ZN15009:PA7 | URBAN | Other | Other - Arcing | 1 | 502 | 0.00034 | 1e-06 | N
03-02-19 | 09:17 | 515:35198 | SHORT RURAL | Other | Other - Self Clearing Trigger | 27 | 113 | 0.012766 | 0.000113 | N
03-02-19 | 11:56 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 21 | 64 | 0.000907 | 1.4e-05 | N
03-02-19 | 13:05 | ZN1285:PA33 | URBAN | Network business | Network error | 81 | 109 | 0.006008 | 5.5e-05 | N
03-02-19 | 13:35 | 243:80083 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 195 | 0.000814 | 4e-06 | N
03-02-19 | 15:47 | ZN36200:PA11 | URBAN | Other | Other | 1 | 82 | 5.6e-05 | 1e-06 | N
03-02-19 | 16:34 | 243:80074 | SHORT RURAL | Asset Failure | LV | 32 | 64 | 0.008532 | 0.000134 | N
03-02-19 | 16:35 | 415:33884 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1 | 97 | 6.6e-05 | 1e-06 | N
03-02-19 | 17:27 | ZN8000:PA17 | URBAN | Asset Failure | Distribution substation | 5 | 673 | 0.002281 | 3e-06 | N
03-02-19 | 17:56 | ZN195:PA22 | URBAN | Third Party | Vehicle impact | 5 | 193 | 0.000654 | 3e-06 | N
03-02-19 | 18:03 | ZN35900:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 272 | 0.001137 | 4e-06 | N
03-02-19 | 18:12 | ZN10997:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 49 | 93 | 0.003089 | 3.3e-05 | N
03-02-19 | 18:27 | ZN12620:PA7 | URBAN | Asset Failure | LV | 45 | 77 | 0.002357 | 3.1e-05 | N
03-02-19 | 18:52 | ZN9118:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 143 | 9.7e-05 | 1e-06 | N
03-02-19 | 18:56 | 807:74179 | SHORT RURAL | Third Party | Other | 1 | 124 | 0.000519 | 4e-06 | N
03-02-19 | 19:54 | ZN9118:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 116 | 7.8e-05 | 1e-06 | N
04-02-19 | 00:53 | ZN12650:PA20 | URBAN | Other | Other - Self Clearing Trigger | 1,537 | 107 | 0.11155 | 0.001042 | N
04-02-19 | 04:56 | ZN195:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 344 | 0.006527 | 1.9e-05 | N
04-02-19 | 09:04 | ZN690:PA12 | URBAN | Other | Other - Arcing | 1 | 296 | 0.0002 | 1e-06 | N
04-02-19 | 09:24 | ZN901:PA20 | URBAN | Other | Other | 1 | 108 | 7.3e-05 | 1e-06 | N
04-02-19 | 09:57 | ZN10995:PA2 | URBAN | Asset Failure | HV | 1 | 125 | 8.5e-05 | 1e-06 | N
04-02-19 | 09:57 | ZN35800:PA22 | URBAN | Asset Failure | HV | 1,710 | 123 | 0.14303 | 0.001159 | N
01-02-19 | 13:00 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 95 | 0.000398 | 4e-06 | N
04-02-19 | 10:50 | ZN15015:PA15 | SHORT RURAL | Third Party | Vehicle impact | 15 | 610 | 0.038255 | 6.3e-05 | N
04-02-19 | 10:56 | 528:83024 | URBAN | Other | Other | 1 | 112 | 7.6e-05 | 1e-06 | N
04-02-19 | 11:57 | 513:48057 | URBAN | Asset Failure | LV | 1 | 196 | 0.000133 | 1e-06 | N
04-02-19 | 12:09 | ZN35800:PA3 | URBAN | Other | Other | 1 | 7 | 5e-06 | 1e-06 | N
04-02-19 | 12:14 | ZN35800:PA22 | URBAN | Asset Failure | HV | 891 | 52 | 0.031469 | 0.000604 | N
04-02-19 | 12:27 | ZN847:PA15 | URBAN | Third Party | Vehicle impact | 40 | 128 | 0.00346 | 2.7e-05 | N
31-01-19 | 23:30 | ZN262:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 90 | 0.003721 | 4.1e-05 | Y
04-02-19 | 15:03 | 232:11455 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,555 | 78 | 0.5055 | 0.006505 | N
04-02-19 | 15:15 | ZN36200:PA11 | URBAN | Third Party | Dig-in | 1 | 209 | 0.000142 | 1e-06 | N
04-02-19 | 15:33 | ZN15012:PA4 | URBAN | Asset Failure | LV | 1 | 292 | 0.000198 | 1e-06 | N
29-01-19 | 15:46 | ZN5868:PA17 | URBAN | Asset Failure | HV | 242 | 2 | 0.000328 | 0.000164 | N
04-02-19 | 15:56 | ZN35500:PA28 | URBAN | Other | Other | 1 | 17 | 1.1e-05 | 1e-06 | N
01-02-19 | 10:08 | ZN12620:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 37 | 130 | 0.020126 | 0.000155 | N
04-02-19 | 17:08 | ZN10998:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 292 | 0.000198 | 1e-06 | N
04-02-19 | 17:16 | ZN36200:PA8 | SHORT RURAL | Asset Failure | Distribution substation | 81 | 75 | 0.02525 | 0.000339 | N
04-02-19 | 17:22 | ZN3155:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 427 | 0.000289 | 1e-06 | N
04-02-19 | 18:26 | ZN1648:PA16 | URBAN | Asset Failure | LV | 2 | 362 | 0.000491 | 1e-06 | N
04-02-19 | 18:31 | ZN15005:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 167 | 0.000113 | 1e-06 | N
04-02-19 | 19:21 | ZN3155:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 51 | 83 | 0.002875 | 3.5e-05 | N
04-02-19 | 19:49 | 515:35198 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 61 | 0.000255 | 4e-06 | N
04-02-19 | 20:09 | ZN15013:PA10 | SHORT RURAL | Asset Failure | HV | 10 | 91 | 0.003807 | 4.2e-05 | N
04-02-19 | 22:25 | ZN965:PA28 | URBAN | Asset Failure | LV | 14 | 610 | 0.005787 | 9e-06 | N
05-02-19 | 01:23 | ZN9900:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 327 | 0.005318 | 1.6e-05 | N
05-02-19 | 01:40 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 260 | 0.021716 | 8.4e-05 | N
05-02-19 | 08:42 | ZN965:PA28 | URBAN | Other | Other - Self Clearing Trigger | 35 | 427 | 0.010127 | 2.4e-05 | N
05-02-19 | 09:54 | ZN129:PA47 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 891 | 0.000604 | 1e-06 | N
02-02-19 | 10:20 | ZN180:PA41 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 43 | 0.001371 | 3.2e-05 | N
05-02-19 | 12:04 | ZN35500:PA32 | URBAN | Other | Other | 1 | 218 | 0.000148 | 1e-06 | N
05-02-19 | 13:12 | 233:82821 | SHORT RURAL | Other | Other | 1 | 92 | 0.000386 | 4e-06 | N
05-02-19 | 13:47 | 801:74123 | SHORT RURAL | Asset Failure | LV | 5 | 104 | 0.002175 | 2.1e-05 | N
05-02-19 | 13:52 | ZN1673:PA6 | URBAN | Weather |  | 18 | 118 | 0.001439 | 1.2e-05 | N
05-02-19 | 15:08 | ZN12690:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 233 | 0.000975 | 4e-06 | N
05-02-19 | 17:09 | 807:74179 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 46 | 170 | 0.032668 | 0.000192 | N
05-02-19 | 17:37 | ZN10999:PA17 | URBAN | Network business | Network error | 52 | 88 | 0.003099 | 3.5e-05 | N
05-02-19 | 18:13 | 526:34633 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 213 | 0.000891 | 4e-06 | N
05-02-19 | 19:06 | ZN2310:PA15 | URBAN | Other | Other | 2 | 288 | 0.00039 | 1e-06 | N
05-02-19 | 20:34 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 116 | 0.002426 | 2.1e-05 | N
05-02-19 | 21:47 | 515:35192 | SHORT RURAL | Asset Failure | Distribution substation | 34 | 73 | 0.010314 | 0.000142 | N
05-02-19 | 21:51 | 205:12213 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 145 | 0.000606 | 4e-06 | N
06-02-19 | 00:10 | ZN10994:PA9 | URBAN | Asset Failure | LV | 141 | 70 | 0.006688 | 9.6e-05 | N
06-02-19 | 01:56 | ZN3425:PA15 | URBAN | Other | Other - Arcing | 1 | 423 | 0.000287 | 1e-06 | N
06-02-19 | 02:42 | ZN2196:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 705 | 207 | 0.098892 | 0.000478 | N
06-02-19 | 07:47 | 807:74184 | SHORT RURAL | Other | Other | 1 | 132 | 0.000553 | 4e-06 | N
06-02-19 | 08:04 | 512:83732 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 168 | 0.007731 | 4.6e-05 | N
06-02-19 | 08:21 | ZN1068:PA16 | URBAN | Other | Other | 1 | 166 | 0.000113 | 1e-06 | N
06-02-19 | 08:24 | 512:83732 | SHORT RURAL | Other | Other | 1 | 153 | 0.00064 | 4e-06 | N
06-02-19 | 08:31 | 512:83743 | SHORT RURAL | Other | Other | 1 | 85 | 0.000357 | 4e-06 | N
09-02-19 | 05:37 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 4 | 743 | 0.012434 | 1.7e-05 | N
06-02-19 | 09:13 | 221:11895 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 49 | 3.3e-05 | 1e-06 | N
06-02-19 | 09:29 | ZN15002:PA6 | URBAN | Asset Failure | LV | 1 | 781 | 0.000529 | 1e-06 | N
06-02-19 | 09:33 | ZN711:PA22 | SHORT RURAL | Asset Failure | LV | 82 | 266 | 0.091321 | 0.000343 | N
06-02-19 | 09:55 | ZN3154:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 20 | 135 | 0.00183 | 1.4e-05 | N
06-02-19 | 10:10 | ZN35555:PA6 | URBAN | Other | Other | 1 | 57 | 3.8e-05 | 1e-06 | N
06-02-19 | 10:44 | 233:82815 | SHORT RURAL | Other | Other | 1 | 126 | 0.000528 | 4e-06 | N
06-02-19 | 10:52 | ZN15004:PA5 | URBAN | Asset Failure | LV | 1 | 427 | 0.000289 | 1e-06 | N
06-02-19 | 11:12 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 20 | 148 | 0.012383 | 8.4e-05 | N
06-02-19 | 11:55 | ZN342:PA26 | URBAN | Asset Failure | LV | 17 | 384 | 0.004424 | 1.2e-05 | N
06-02-19 | 12:02 | 216:10722 | SHORT RURAL | Asset Failure | LV | 13 | 293 | 0.015935 | 5.4e-05 | N
06-02-19 | 13:16 | ZN2635:PA52 | URBAN | Asset Failure | HV | 86 | 199 | 0.011597 | 5.8e-05 | N
06-02-19 | 13:19 | 812:19066 | SHORT RURAL | Other | Other | 1 | 126 | 0.000529 | 4e-06 | N
06-02-19 | 13:31 | 814:82285 | SHORT RURAL | Asset Failure | LV | 1 | 79 | 0.000331 | 4e-06 | N
06-02-19 | 22:17 | ZN180:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 8 | 9 | 4.9e-05 | 5e-06 | N
06-02-19 | 15:24 | ZN1850:PA31 | URBAN | Network business | Network error | 33 | 86 | 0.001923 | 2.2e-05 | N
06-02-19 | 16:26 | ZN1287:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 293 | 0.000198 | 1e-06 | N
06-02-19 | 16:50 | ZN2635:PA52 | URBAN | Other | Other | 1 | 70 | 4.7e-05 | 1e-06 | N
06-02-19 | 17:00 | ZN12600:PA2 | SHORT RURAL | Asset Failure | LV | 1 | 164 | 0.000687 | 4e-06 | N
06-02-19 | 17:52 | 239:82136 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 52 | 3.5e-05 | 1e-06 | N
06-02-19 | 18:39 | ZN35370:PA8 | SHORT RURAL | Network business | Network error | 20 | 111 | 0.009288 | 8.4e-05 | N
06-02-19 | 21:13 | ZN3922:PA26 | URBAN | Other | Other | 1 | 44 | 3e-05 | 1e-06 | N
06-02-19 | 21:14 | ZN9900:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 85 | 0.002305 | 2.7e-05 | N
07-02-19 | 06:53 | ZN7900:PA23 | URBAN | Asset Failure | LV | 2 | 3,113 | 0.004219 | 1e-06 | N
07-02-19 | 06:53 | ZN901:PA17 | URBAN | Asset Failure | LV | 3 | 3,113 | 0.006328 | 2e-06 | N
07-02-19 | 07:02 | 507:80925 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 83 | 0.000347 | 4e-06 | N
07-02-19 | 08:30 | ZN1285:PA24 | URBAN | Third Party | Vehicle impact | 96 | 89 | 0.005804 | 6.5e-05 | N
07-02-19 | 08:32 | ZN398:PA20 | URBAN | Weather |  | 1 | 267 | 0.000181 | 1e-06 | N
07-02-19 | 08:34 | ZN690:PA14 | URBAN | Third Party | Dig-in | 2,104 | 130 | 0.1857 | 0.001426 | N
07-02-19 | 08:34 | ZN690:PA28 | URBAN | Third Party | Dig-in | 111 | 208 | 0.015645 | 7.5e-05 | N
07-02-19 | 13:13 | ZN180:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 167 | 0.005314 | 3.2e-05 | N
07-02-19 | 08:57 | ZN2466:PA45 | URBAN | Other | Other | 1 | 240 | 0.000163 | 1e-06 | N
07-02-19 | 09:05 | ZN2196:PA5 | URBAN | Weather |  | 58 | 164 | 0.006457 | 3.9e-05 | N
07-02-19 | 09:12 | 243:80081 | SHORT RURAL | Other | Other | 1 | 96 | 0.000403 | 4e-06 | N
07-02-19 | 10:34 | ZN1673:PA6 | URBAN | Asset Failure | LV | 18 | 266 | 0.003245 | 1.2e-05 | N
07-02-19 | 11:29 | ZN35400:PA77 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 99 | 6.7e-05 | 1e-06 | N
07-02-19 | 13:00 | ZN1285:PA24 | URBAN | Asset Failure | LV | 96 | 69 | 0.004515 | 6.5e-05 | N
07-02-19 | 14:24 | 502:48010 | SHORT RURAL | Other | Other | 1 | 62 | 0.00026 | 4e-06 | N
07-02-19 | 14:59 | ZN4545:PA36 | URBAN | Asset Failure | LV | 26 | 106 | 0.001868 | 1.8e-05 | N
07-02-19 | 19:40 | ZN167:PA21 | URBAN | Asset Failure | LV | 7 | 30 | 0.000142 | 5e-06 | N
07-02-19 | 15:49 | 511:29877 | SHORT RURAL | Other | Other | 1 | 86 | 0.000359 | 4e-06 | N
07-02-19 | 15:52 | 812:19071 | SHORT RURAL | Asset Failure | LV | 1 | 353 | 0.001477 | 4e-06 | N
07-02-19 | 16:04 | 801:74120 | SHORT RURAL | Asset Failure | LV | 1 | 169 | 0.000708 | 4e-06 | N
07-02-19 | 16:35 | ZN10995:PA12 | URBAN | Third Party | Other | 1 | 310 | 0.00021 | 1e-06 | N
07-02-19 | 17:00 | 243:80075 | SHORT RURAL | Third Party | Vehicle impact | 3 | 625 | 0.007844 | 1.3e-05 | N
07-02-19 | 16:39 | ZN10995:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 408 | 0.000276 | 1e-06 | N
07-02-19 | 17:36 | ZN9037:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 204 | 0.000138 | 1e-06 | N
07-02-19 | 17:51 | 507:80932 | SHORT RURAL | Other | Other | 1 | 158 | 0.000662 | 4e-06 | N
07-02-19 | 17:48 | ZN1193:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 246 | 40 | 0.006668 | 0.000167 | N
07-02-19 | 18:00 | ZN10993:PA33 | URBAN | Other | Other | 1 | 270 | 0.000183 | 1e-06 | N
07-02-19 | 17:58 | ZN12690:PA24 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 78 | 68 | 0.022186 | 0.000326 | N
07-02-19 | 18:01 | ZN3154:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 20 | 69 | 0.000935 | 1.4e-05 | N
07-02-19 | 20:50 | ZN1673:PA6 | URBAN | Asset Failure | LV | 19 | 25 | 0.000322 | 1.3e-05 | N
07-02-19 | 22:27 | ZN9035:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 572 | 0.000388 | 1e-06 | N
08-02-19 | 00:24 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 576 | 0.002409 | 4e-06 | N
08-02-19 | 03:25 | 206:34434 | URBAN | Other | Other - Self Clearing Trigger | 14 | 79 | 0.000751 | 9e-06 | N
08-02-19 | 08:18 | ZN630:PA34 | URBAN | Other | Other - Self Clearing Trigger | 10 | 132 | 0.000892 | 7e-06 | N
08-02-19 | 09:11 | ZN15005:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,609 | 0.00109 | 1e-06 | N
08-02-19 | 09:54 | ZN129:PA56 | URBAN | Vegetation | Vegetation Blow/Fall In | 57 | 185 | 0.007155 | 3.9e-05 | N
08-02-19 | 09:30 | ZN12690:PA24 | SHORT RURAL | Asset Failure | LV | 11 | 240 | 0.011046 | 4.6e-05 | N
08-02-19 | 09:54 | ZN15004:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 2,885 | 0.00391 | 1e-06 | N
08-02-19 | 10:13 | ZN12610:PA13 | SHORT RURAL | Other | Other | 1 | 66 | 0.000276 | 4e-06 | N
08-02-19 | 12:04 | 258:80778 | URBAN | Other | Other | 1 | 79 | 5.4e-05 | 1e-06 | N
08-02-19 | 12:58 | ZN1850:PA33 | URBAN | Other | Other - Arcing | 1 | 119 | 8.1e-05 | 1e-06 | N
08-02-19 | 13:38 | ZN10994:PA1 | URBAN | Asset Failure | LV | 1 | 254 | 0.000172 | 1e-06 | N
08-02-19 | 13:38 | ZN10994:PA3 | URBAN | Asset Failure | LV | 69 | 253 | 0.011848 | 4.7e-05 | N
08-02-19 | 15:02 | ZN2835:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 66 | 4.5e-05 | 1e-06 | N
08-02-19 | 15:14 | ZN10995:PA8 | URBAN | Other | Other | 1 | 109 | 7.4e-05 | 1e-06 | N
08-02-19 | 15:32 | ZN931:PA26 | URBAN | Other | Other - Self Clearing Trigger | 13 | 153 | 0.001348 | 9e-06 | N
08-02-19 | 15:38 | 810:74058 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 2 | 192 | 0.001607 | 8e-06 | N
08-02-19 | 15:48 | ZN1287:PA6 | URBAN | Asset Failure | LV | 1 | 431 | 0.000292 | 1e-06 | N
08-02-19 | 15:51 | ZN14143:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 200 | 0.000837 | 4e-06 | N
08-02-19 | 15:52 | ZN12690:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 58 | 4e-05 | 1e-06 | N
08-02-19 | 16:49 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 881 | 0.022116 | 2.5e-05 | N
08-02-19 | 17:13 | 528:83019 | SHORT RURAL | Asset Failure | HV | 1 | 532 | 0.002226 | 4e-06 | N
08-02-19 | 17:17 | 814:82291 | SHORT RURAL | Weather |  | 462 | 192 | 0.37094 | 0.001933 | N
08-02-19 | 19:13 | ZN965:PA8 | URBAN | Other | Other - Self Clearing Trigger | 17 | 997 | 0.011485 | 1.2e-05 | N
08-02-19 | 18:09 | ZN1290:PA9 | URBAN | Weather |  | 1,264 | 257 | 0.22002 | 0.000857 | N
08-02-19 | 18:14 | ZN1287:PA21 | URBAN | Asset Failure | HV | 1,658 | 150 | 0.16853 | 0.001124 | N
08-02-19 | 17:56 | 515:35197 | LONG RURAL | Asset Failure | HV | 36 | 423 | 5.3511 | 0.01264 | N
08-02-19 | 18:23 | 515:35197 | LONG RURAL | Asset Failure | HV | 2 | 1,257 | 0.88272 | 0.000702 | N
08-02-19 | 18:37 | ZN965:PA26 | URBAN | Asset Failure | HV | 923 | 151 | 0.094446 | 0.000625 | N
08-02-19 | 18:47 | ZN4545:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 223 | 0.000151 | 1e-06 | N
08-02-19 | 18:52 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 83 | 0.002431 | 2.9e-05 | N
08-02-19 | 18:53 | ZN35500:PA32 | URBAN | Other | Other - Self Clearing Trigger | 80 | 447 | 0.024227 | 5.4e-05 | N
08-02-19 | 18:56 | 512:83743 | SHORT RURAL | Asset Failure | HV | 2 | 1,064 | 0.008903 | 8e-06 | N
08-02-19 | 18:56 | ZN4545:PA41 | SHORT RURAL | Weather |  | 562 | 168 | 0.39422 | 0.002351 | N
08-02-19 | 19:01 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 41 | 964 | 0.026783 | 2.8e-05 | N
08-02-19 | 18:56 | ZN2400:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 72 | 536 | 0.026151 | 4.9e-05 | N
08-02-19 | 18:56 | ZN847:PA47 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 366 | 920 | 1.4091 | 0.001531 | N
08-02-19 | 18:56 | ZN2400:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 939 | 490 | 0.31205 | 0.000636 | N
08-02-19 | 18:58 | ZN3922:PA3 | URBAN | Asset Failure | HV | 781 | 106 | 0.056099 | 0.000529 | N
08-02-19 | 18:54 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 196 | 503 | 0.4128 | 0.00082 | N
08-02-19 | 19:03 | ZN12640:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 125 | 8.5e-05 | 1e-06 | N
08-02-19 | 19:03 | ZN4545:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 206 | 0.00014 | 1e-06 | N
08-02-19 | 18:59 | ZN129:PA35 | URBAN | Weather |  | 1,312 | 354 | 0.31441 | 0.000889 | N
08-02-19 | 19:06 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 504 | 0.000341 | 1e-06 | N
08-02-19 | 19:06 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 903 | 0.01775 | 2e-05 | N
08-02-19 | 19:07 | ZN847:PA47 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 29 | 2,723 | 0.33039 | 0.000121 | N
08-02-19 | 19:19 | ZN847:PA47 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 43 | 1,251 | 0.22507 | 0.00018 | N
08-02-19 | 18:48 | ZN35370:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 759 | 463 | 1.4708 | 0.003176 | N
08-02-19 | 18:48 | ZN35370:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 279 | 964 | 1.1256 | 0.001167 | N
08-02-19 | 19:20 | ZN2400:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 3 | 1,497 | 0.003043 | 2e-06 | N
08-02-19 | 18:28 | 513:48056 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 362 | 0.010602 | 2.9e-05 | N
08-02-19 | 19:28 | ZN12600:PA3 | URBAN | Weather |  | 1,729 | 60 | 0.070772 | 0.001172 | N
08-02-19 | 19:37 | ZN2400:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,342 | 0.00091 | 1e-06 | N
08-02-19 | 19:32 | ZN15014:PA7 | URBAN | Other | Other - Self Clearing Trigger | 1,025 | 105 | 0.072931 | 0.000695 | N
08-02-19 | 20:15 | ZN965:PA46 | URBAN | Asset Failure | LV | 22 | 1,409 | 0.021005 | 1.5e-05 | N
08-02-19 | 19:40 | ZN12650:PA6 | URBAN | Weather |  | 1 | 379 | 0.000257 | 1e-06 | N
08-02-19 | 22:13 | ZN2835:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 17 | 37 | 0.000426 | 1.2e-05 | N
08-02-19 | 19:55 | ZN10991:PA8 | URBAN | Weather |  | 20 | 244 | 0.003303 | 1.4e-05 | N
08-02-19 | 19:57 | ZN12580:PA4 | URBAN | Other | Other - Arcing | 1 | 1,354 | 0.000918 | 1e-06 | N
08-02-19 | 20:03 | ZN3155:PA22 | URBAN | Other | Other - Self Clearing Trigger | 72 | 76 | 0.003732 | 4.9e-05 | N
08-02-19 | 20:07 | ZN14891:PA12 | SHORT RURAL | Weather |  | 1 | 227 | 0.000952 | 4e-06 | N
08-02-19 | 20:07 | ZN10991:PA7 | URBAN | Other | Other | 1 | 1,432 | 0.00097 | 1e-06 | N
07-02-19 | 20:07 | 522:83124 | URBAN | Asset Failure | HV | 1,394 | 138 | 0.13077 | 0.000945 | N
08-02-19 | 20:27 | ZN965:PA46 | URBAN | Asset Failure | LV | 34 | 2,188 | 0.050402 | 2.3e-05 | N
08-02-19 | 20:37 | ZN14891:PA5 | SHORT RURAL | Weather |  | 7 | 153 | 0.004481 | 2.9e-05 | N
08-02-19 | 19:31 | ZN12610:PA17 | URBAN | Weather |  | 1,064 | 140 | 0.10065 | 0.000721 | N
08-02-19 | 19:31 | ZN12610:PA23 | URBAN | Weather |  | 1 | 142 | 9.6e-05 | 1e-06 | N
08-02-19 | 19:31 | ZN12610:PA7 | URBAN | Weather |  | 1 | 142 | 9.6e-05 | 1e-06 | N
08-02-19 | 20:46 | ZN12650:PA6 | URBAN | Weather |  | 33 | 375 | 0.008388 | 2.2e-05 | N
08-02-19 | 20:47 | ZN15012:PA6 | URBAN | Asset Failure | LV | 1 | 2,702 | 0.001831 | 1e-06 | N
08-02-19 | 20:57 | ZN2400:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 883 | 0.022731 | 2.6e-05 | N
08-02-19 | 20:00 | TS14450:757 | URBAN | Weather |  | 1 | 1,180 | 0.0008 | 1e-06 | N
09-02-19 | 02:00 | 522:83132 | SHORT RURAL | Asset Failure | LV | 5 | 150 | 0.003138 | 2.1e-05 | N
08-02-19 | 23:13 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 732 | 0.003063 | 4e-06 | N
08-02-19 | 23:27 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 753 | 0.006301 | 8e-06 | N
09-02-19 | 03:30 | ZN4545:PA40 | URBAN | Asset Failure | HV | 1,836 | 192 | 0.23913 | 0.001244 | N
09-02-19 | 09:52 | ZN3288:PA41 42GHJ | CBD | Other | Other - Self Clearing Trigger | 12 | 318 | 0.1246 | 0.000392 | N
09-02-19 | 06:18 | ZN4545:PA44 | URBAN | Network business | Network error | 82 | 277 | 0.015392 | 5.6e-05 | N
09-02-19 | 07:02 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 533 | 0.024507 | 4.6e-05 | N
09-02-19 | 07:17 | ZN15005:PA10 | URBAN | Other | Other - Self Clearing Trigger | 2 | 143 | 0.000194 | 1e-06 | N
09-02-19 | 07:28 | ZN36200:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 486 | 0.00033 | 1e-06 | N
09-02-19 | 07:39 | ZN15002:PA4 | SHORT RURAL | Other | Other | 1 | 411 | 0.001719 | 4e-06 | N
09-02-19 | 08:07 | ZN2400:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 668 | 0.002716 | 4e-06 | N
09-02-19 | 08:21 | ZN15005:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 102 | 6.9e-05 | 1e-06 | N
09-02-19 | 08:56 | ZN847:PA47 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 667 | 0.008372 | 1.3e-05 | N
09-02-19 | 08:57 | ZN4545:PA26 | URBAN | Other | Other - Self Clearing Trigger | 7 | 393 | 0.001864 | 5e-06 | N
09-02-19 | 10:18 | ZN35555:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 885 | 0.003702 | 4e-06 | N
09-02-19 | 10:29 | ZN2400:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 686 | 0.000465 | 1e-06 | N
09-02-19 | 10:41 | ZN12640:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 293 | 0.000198 | 1e-06 | N
09-02-19 | 10:46 | ZN2400:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 897 | 0.003647 | 4e-06 | N
09-02-19 | 11:00 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 5 | 370 | 0.64958 | 0.001756 | N
09-02-19 | 11:02 | ZN12650:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 449 | 0.000304 | 1e-06 | N
09-02-19 | 11:08 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 322 | 0.002694 | 8e-06 | N
09-02-19 | 11:15 | ZN35900:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 296 | 0.0002 | 1e-06 | N
09-02-19 | 11:20 | ZN262:PA25 | URBAN | Third Party | Vehicle impact | 3 | 115 | 0.000234 | 2e-06 | N
09-02-19 | 05:37 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 537 | 0.015735 | 2.9e-05 | N
09-02-19 | 12:39 | ZN1673:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 286 | 0.006002 | 2.1e-05 | N
09-02-19 | 12:50 | ZN35370:PA8 | SHORT RURAL | Asset Failure | HV | 35 | 70 | 0.01025 | 0.000146 | N
09-02-19 | 13:49 | 509:33395 | LONG RURAL | Vegetation | Vegetation Grow In | 3 | 169 | 0.17802 | 0.001053 | N
09-02-19 | 14:21 | ZN1287:PA15 | URBAN | Network business | Network error | 57 | 140 | 0.005419 | 3.9e-05 | N
09-02-19 | 14:21 | ZN1287:PA21 | URBAN | Network business | Network error | 110 | 144 | 0.010734 | 7.5e-05 | N
09-02-19 | 15:12 | ZN80:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 138 | 0.002712 | 2e-05 | N
09-02-19 | 15:32 | 812:19071 | SHORT RURAL | Third Party | Vehicle impact | 62 | 358 | 0.092775 | 0.000259 | N
09-02-19 | 16:00 | 227:13015 | SHORT RURAL | Other | Other | 1 | 199 | 0.000834 | 4e-06 | N
09-02-19 | 16:00 | ZN2400:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 165 | 0.002683 | 1.6e-05 | N
09-02-19 | 17:00 | ZN1850:PA40 | URBAN | Other | Other | 1 | 269 | 0.000182 | 1e-06 | N
09-02-19 | 15:05 | ZN35370:PA8 | SHORT RURAL | Other | Other | 14 | 10 | 0.000586 | 5.9e-05 | N
09-02-19 | 17:21 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 13 | 264 | 0.014358 | 5.4e-05 | N
09-02-19 | 17:47 | 232:11455 | SHORT RURAL | Asset Failure | LV | 1 | 382 | 0.001599 | 4e-06 | N
09-02-19 | 17:51 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 149 | 0.052276 | 0.000351 | N
09-02-19 | 18:05 | 202:34260 | URBAN | Other | Other - Self Clearing Trigger | 102 | 55 | 0.003785 | 6.9e-05 | N
09-02-19 | 18:15 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 184 | 0.000772 | 4e-06 | N
09-02-19 | 18:16 | ZN847:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 45 | 3.1e-05 | 1e-06 | N
09-02-19 | 18:37 | 502:48008 | URBAN | Other | Other | 1 | 143 | 9.7e-05 | 1e-06 | N
09-02-19 | 18:39 | 256:80632 | URBAN | Other | Other - Self Clearing Trigger | 22 | 531 | 0.007916 | 1.5e-05 | N
09-02-19 | 18:40 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 281 | 0.00438 | 1.6e-05 | N
09-02-19 | 19:26 | ZN195:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 363 | 0.007389 | 2e-05 | N
09-02-19 | 19:49 | ZN3154:PA18 | URBAN | Other | Other | 1 | 99 | 6.7e-05 | 1e-06 | N
09-02-19 | 20:48 | 202:34260 | URBAN | Asset Failure | LV | 102 | 234 | 0.016174 | 6.9e-05 | N
09-02-19 | 21:36 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 19 | 0.000159 | 8e-06 | N
10-02-19 | 00:45 | 213:33771 | URBAN | Third Party | Vehicle impact | 42 | 105 | 0.002988 | 2.8e-05 | N
10-02-19 | 03:20 | ZN3154:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 17 | 760 | 0.008755 | 1.2e-05 | N
10-02-19 | 02:54 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 116 | 0.000485 | 4e-06 | N
10-02-19 | 05:30 | ZN1287:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,140 | 62 | 0.047896 | 0.000773 | N
10-02-19 | 08:03 | 227:13020 | SHORT RURAL | Other | Other | 1 | 107 | 0.000447 | 4e-06 | N
10-02-19 | 08:40 | 512:83743 | SHORT RURAL | Asset Failure | HV | 2 | 630 | 0.005271 | 8e-06 | N
10-02-19 | 10:01 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 167 | 0.002096 | 1.3e-05 | N
10-02-19 | 10:00 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 56 | 445 | 0.10415 | 0.000234 | N
10-02-19 | 11:20 | 512:83743 | SHORT RURAL | Animal | Animal impact | 7 | 90 | 0.002636 | 2.9e-05 | N
10-02-19 | 11:50 | ZN195:PA25 | URBAN | Asset Failure | LV | 35 | 275 | 0.006522 | 2.4e-05 | N
10-02-19 | 11:50 | ZN195:PA25 | URBAN | Asset Failure | LV | 28 | 275 | 0.005218 | 1.9e-05 | N
10-02-19 | 12:37 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 88 | 0.000368 | 4e-06 | N
14-02-19 | 13:22 | ZN9245:PA1 | URBAN | Third Party | Vehicle impact | 42 | 71 | 0.002021 | 2.8e-05 | N
10-02-19 | 12:56 | 258:80784 | URBAN | Other | Other | 1 | 331 | 0.000224 | 1e-06 | N
10-02-19 | 14:00 | ZN35800:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 90 | 100 | 0.006099 | 6.1e-05 | N
10-02-19 | 16:28 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 45 | 72 | 0.002193 | 3e-05 | N
10-02-19 | 19:13 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 81 | 71 | 0.024044 | 0.000339 | N
10-02-19 | 20:11 | ZN195:PA11 | URBAN | Asset Failure | LV | 22 | 369 | 0.005494 | 1.5e-05 | N
10-02-19 | 23:23 | ZN9245:PA1 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,070 | 29 | 0.021028 | 0.000725 | N
11-02-19 | 01:31 | ZN14143:PA12 | SHORT RURAL | Asset Failure | Distribution substation | 36 | 419 | 0.063089 | 0.000151 | N
11-02-19 | 02:00 | ZN195:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 125 | 0.002965 | 2.4e-05 | N
11-02-19 | 02:47 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 288 | 0.007229 | 2.5e-05 | N
11-02-19 | 03:36 | ZN3425:PA33 | URBAN | Animal | Animal impact | 236 | 68 | 0.010875 | 0.00016 | N
11-02-19 | 07:07 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 101 | 0.001268 | 1.3e-05 | N
11-02-19 | 08:17 | ZN7481:PA1 | URBAN | Other | Other - Arcing | 1 | 463 | 0.000313 | 1e-06 | N
11-02-19 | 08:24 | ZN15012:PA8 | URBAN | Other | Other | 1 | 5 | 4e-06 | 1e-06 | N
11-02-19 | 08:59 | ZN35370:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 331 | 0.006924 | 2.1e-05 | N
08-02-19 | 17:13 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 107 | 0.000448 | 4e-06 | N
11-02-19 | 13:50 | 524:33576 | SHORT RURAL | Asset Failure | HV | 6 | 50 | 0.001255 | 2.5e-05 | N
11-02-19 | 11:27 | 813:89061 | LONG RURAL | Asset Failure | HV | 5 | 282 | 0.49541 | 0.001756 | N
11-02-19 | 11:34 | ZN36000:PA12 | URBAN | Asset Failure | LV | 1 | 198 | 0.000134 | 1e-06 | N
11-02-19 | 11:40 | ZN35500:PA16 | URBAN | Third Party | Vehicle impact | 1 | 710 | 0.000481 | 1e-06 | N
11-02-19 | 12:25 | ZN187:PA21 | URBAN | Asset Failure | LV | 62 | 140 | 0.005882 | 4.2e-05 | N
11-02-19 | 12:28 | 814:82285 | SHORT RURAL | Asset Failure | LV | 5 | 227 | 0.004748 | 2.1e-05 | N
11-02-19 | 13:39 | ZN2400:PA18 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 291 | 0.001216 | 4e-06 | N
08-02-19 | 17:17 | 814:82291 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,163 | 0.004866 | 4e-06 | N
11-02-19 | 14:15 | ZN847:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 315 | 0.000213 | 1e-06 | N
11-02-19 | 14:37 | 508:82574 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 118 | 0.000493 | 4e-06 | N
11-02-19 | 15:47 | 239:82129 | SHORT RURAL | Other | Other | 1 | 111 | 0.000463 | 4e-06 | N
11-02-19 | 15:53 | ZN35500:PA16 | URBAN | Third Party | Vehicle impact | 1 | 457 | 0.000309 | 1e-06 | N
11-02-19 | 16:00 | 224:80337 | URBAN | Weather |  | 2 | 60 | 8.1e-05 | 1e-06 | N
11-02-19 | 16:34 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 80 | 0.000336 | 4e-06 | N
11-02-19 | 16:39 | ZN180:PA43 | URBAN | Third Party | Vehicle impact | 1 | 392 | 0.000266 | 1e-06 | N
11-02-19 | 17:58 | 512:83732 | SHORT RURAL | Other | Other - Self Clearing Trigger | 853 | 15 | 0.05353 | 0.003569 | N
11-02-19 | 17:58 | 512:83733 | SHORT RURAL | Other | Other - Self Clearing Trigger | 926 | 15 | 0.058112 | 0.003874 | N
11-02-19 | 17:58 | 512:83734 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 15 | 6.3e-05 | 4e-06 | N
11-02-19 | 17:58 | 512:83741 | SHORT RURAL | Other | Other - Self Clearing Trigger | 833 | 16 | 0.05576 | 0.003485 | N
11-02-19 | 17:58 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 970 | 16 | 0.064931 | 0.004058 | N
11-02-19 | 19:57 | ZN12570:PA33 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 658 | 39 | 0.10736 | 0.002753 | N
11-02-19 | 23:34 | 522:83124 | URBAN | Animal | Animal nesting/burrowing, etc and other | 11 | 155 | 0.001156 | 7e-06 | N
12-02-19 | 03:37 | ZN10994:PA19 | URBAN | Animal | Animal impact | 1,021 | 106 | 0.073341 | 0.000692 | N
12-02-19 | 05:58 | ZN10994:PA19 | URBAN | Asset Failure | HV | 97 | 257 | 0.016897 | 6.6e-05 | N
12-02-19 | 08:51 | ZN14143:PA17 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 124 | 0.001556 | 1.3e-05 | N
12-02-19 | 09:13 | 206:34434 | URBAN | Third Party | Vehicle impact | 1 | 266 | 0.00018 | 1e-06 | N
12-02-19 | 09:44 | ZN2196:PA26 | URBAN | Third Party | Other | 1 | 166 | 0.000112 | 1e-06 | N
12-02-19 | 10:59 | ZN12570:PA37 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 630 | 0.002636 | 4e-06 | N
12-02-19 | 11:27 | 210:83465 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 68 | 0.001475 | 2.2e-05 | N
12-02-19 | 11:55 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 35 | 0.000146 | 4e-06 | N
12-02-19 | 13:23 | 265:81648 | SHORT RURAL | Other | Other - Self Clearing Trigger | 182 | 93 | 0.07114 | 0.000761 | N
09-02-19 | 14:35 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 4 | 205 | 0.003431 | 1.7e-05 | N
09-02-19 | 17:30 | ZN2400:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 50 | 0.000203 | 4e-06 | N
09-02-19 | 17:30 | ZN2400:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 75 | 0.001474 | 2e-05 | N
12-02-19 | 13:53 | ZN12630:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 71 | 194 | 0.057576 | 0.000297 | N
12-02-19 | 14:36 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 154 | 0.0024 | 1.6e-05 | N
12-02-19 | 14:50 | ZN3155:PA20 | URBAN | Asset Failure | LV | 175 | 130 | 0.015417 | 0.000119 | N
12-02-19 | 15:12 | 802:82215 | SHORT RURAL | Other | Other | 1 | 153 | 0.000639 | 4e-06 | N
12-02-19 | 15:28 | ZN3154:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 25 | 136 | 0.002309 | 1.7e-05 | N
12-02-19 | 16:02 | ZN12640:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 68 | 0.001055 | 1.6e-05 | N
12-02-19 | 16:06 | ZN12660:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 25 | 68 | 0.007154 | 0.000105 | N
12-02-19 | 16:07 | ZN180:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 11 | 138 | 0.001029 | 7e-06 | N
12-02-19 | 16:10 | ZN3154:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 560 | 0.000759 | 1e-06 | N
12-02-19 | 16:12 | ZN3154:PA16 | URBAN | Weather |  | 31 | 212 | 0.00446 | 2.1e-05 | N
12-02-19 | 16:18 | ZN2400:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 102 | 0.002625 | 2.6e-05 | N
12-02-19 | 16:23 | ZN10999:PA36 | URBAN | Vegetation | Vegetation Blow/Fall In | 45 | 181 | 0.005533 | 3e-05 | N
12-02-19 | 16:39 | ZN12580:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 824 | 94 | 0.052564 | 0.000558 | N
12-02-19 | 16:46 | ZN12620:PA8 | SHORT RURAL | Asset Failure | LV | 1 | 214 | 0.000895 | 4e-06 | N
12-02-19 | 16:59 | ZN3154:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 151 | 0.003377 | 2.2e-05 | N
12-02-19 | 18:30 | ZN3154:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 90 | 0.00183 | 2e-05 | N
12-02-19 | 17:30 | ZN10998:PA29 | URBAN | Asset Failure | LV | 1 | 540 | 0.000366 | 1e-06 | N
12-02-19 | 17:45 | ZN15002:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 239 | 0.000162 | 1e-06 | N
12-02-19 | 17:50 | 261:81879 | URBAN | Other | Other - Self Clearing Trigger | 222 | 72 | 0.010832 | 0.00015 | N
12-02-19 | 18:15 | ZN9015:PA1 | SHORT RURAL | Asset Failure | Subtransmission | 2 | 4,158 | 0.034792 | 8e-06 | N
12-02-19 | 19:35 | 261:81879 | URBAN | Other | Other | 1 | 92 | 6.2e-05 | 1e-06 | N
12-02-19 | 19:36 | ZN10997:PA7 | URBAN | Other | Other - Self Clearing Trigger | 83 | 44 | 0.00247 | 5.6e-05 | N
12-02-19 | 19:56 | 256:80652 | URBAN | Other | Other | 1 | 65 | 4.4e-05 | 1e-06 | N
12-02-19 | 20:01 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 120 | 0.002444 | 2e-05 | N
12-02-19 | 20:19 | ZN965:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 151 | 0.004804 | 3.2e-05 | N
12-02-19 | 20:53 | ZN35800:PA22 | URBAN | Asset Failure | LV | 108 | 171 | 0.012514 | 7.3e-05 | N
13-02-19 | 02:43 | ZN12650:PA20 | URBAN | Asset Failure | LV | 1 | 662 | 0.000448 | 1e-06 | Y
13-02-19 | 01:57 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 768 | 0.003214 | 4e-06 | Y
13-02-19 | 02:20 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 100 | 0.002507 | 2.5e-05 | Y
13-02-19 | 04:23 | ZN12580:PA4 | URBAN | Asset Failure | LV | 1 | 217 | 0.000147 | 1e-06 | Y
13-02-19 | 04:39 | ZN9118:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 50 | 0.00078 | 1.6e-05 | Y
13-02-19 | 05:57 | 239:82132 | URBAN | Other | Other | 1 | 80 | 5.4e-05 | 1e-06 | Y
13-02-19 | 06:08 | 239:82128 | URBAN | Animal | Animal impact | 8 | 32 | 0.000173 | 5e-06 | Y
13-02-19 | 07:06 | ZN1287:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 77 | 5.2e-05 | 1e-06 | Y
12-02-19 | 12:05 | 520:48172 | SHORT RURAL | Other | Other | 1 | 60 | 0.000251 | 4e-06 | N
13-02-19 | 10:06 | 258:80791 | URBAN | Other | Other | 1 | 71 | 4.8e-05 | 1e-06 | Y
13-02-19 | 05:20 | ZN12580:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 12 | 124 | 0.001008 | 8e-06 | Y
13-02-19 | 11:53 | ZN847:PA1 | URBAN | Asset Failure | Zone substation | 1,221 | 435 | 0.36012 | 0.000827 | Y
13-02-19 | 11:53 | ZN847:PA10 | URBAN | Asset Failure | Zone substation | 1,318 | 718 | 0.64124 | 0.000893 | Y
13-02-19 | 11:53 | ZN847:PA12 | URBAN | Asset Failure | Zone substation | 321 | 1,012 | 0.22011 | 0.000217 | Y
13-02-19 | 11:53 | ZN847:PA14 | URBAN | Asset Failure | Zone substation | 387 | 519 | 0.13612 | 0.000262 | Y
13-02-19 | 11:53 | ZN847:PA15 | URBAN | Asset Failure | Zone substation | 1,346 | 480 | 0.43763 | 0.000912 | Y
13-02-19 | 11:53 | ZN847:PA18 | SHORT RURAL | Asset Failure | Zone substation | 971 | 1,092 | 4.435 | 0.004061 | Y
13-02-19 | 11:53 | ZN847:PA19 | URBAN | Asset Failure | Zone substation | 1,284 | 975 | 0.84823 | 0.00087 | Y
13-02-19 | 11:53 | ZN847:PA2 | URBAN | Asset Failure | Zone substation | 1,560 | 836 | 0.88364 | 0.001057 | Y
13-02-19 | 11:53 | ZN847:PA21 | URBAN | Asset Failure | Zone substation | 1,823 | 1,095 | 1.3525 | 0.001235 | Y
13-02-19 | 11:53 | ZN847:PA22 | URBAN | Asset Failure | Zone substation | 1,234 | 962 | 0.80433 | 0.000836 | Y
13-02-19 | 11:53 | ZN847:PA23 | URBAN | Asset Failure | Zone substation | 1,295 | 791 | 0.69416 | 0.000877 | Y
13-02-19 | 11:53 | ZN847:PA26 | SHORT RURAL | Asset Failure | Zone substation | 176 | 837 | 0.61616 | 0.000736 | Y
13-02-19 | 11:53 | ZN847:PA28 | URBAN | Asset Failure | Zone substation | 1,093 | 978 | 0.72428 | 0.000741 | Y
13-02-19 | 11:53 | ZN847:PA29 | URBAN | Asset Failure | Zone substation | 276 | 940 | 0.17579 | 0.000187 | Y
13-02-19 | 11:53 | ZN847:PA30 | URBAN | Asset Failure | Zone substation | 596 | 1,005 | 0.40584 | 0.000404 | Y
13-02-19 | 11:53 | ZN847:PA31 | URBAN | Asset Failure | Zone substation | 165 | 984 | 0.11005 | 0.000112 | Y
13-02-19 | 11:53 | ZN847:PA35 | URBAN | Asset Failure | Zone substation | 384 | 1,030 | 0.26799 | 0.00026 | Y
13-02-19 | 11:53 | ZN847:PA36 | URBAN | Asset Failure | Zone substation | 2,134 | 1,041 | 1.5052 | 0.001446 | Y
13-02-19 | 11:53 | ZN847:PA38 | URBAN | Asset Failure | Zone substation | 275 | 909 | 0.16937 | 0.000186 | Y
13-02-19 | 11:53 | ZN847:PA39 | URBAN | Asset Failure | Zone substation | 1,704 | 1,124 | 1.2982 | 0.001155 | Y
13-02-19 | 11:53 | ZN847:PA43 | URBAN | Asset Failure | Zone substation | 1 | 1,016 | 0.000688 | 1e-06 | Y
13-02-19 | 11:53 | ZN847:PA44 | URBAN | Asset Failure | Zone substation | 1,038 | 1,021 | 0.71807 | 0.000703 | Y
13-02-19 | 11:53 | ZN847:PA45 | SHORT RURAL | Asset Failure | Zone substation | 488 | 331 | 0.67516 | 0.002041 | Y
13-02-19 | 11:53 | ZN847:PA46 | URBAN | Asset Failure | Zone substation | 1,161 | 837 | 0.65842 | 0.000787 | Y
13-02-19 | 11:53 | ZN847:PA47 | SHORT RURAL | Asset Failure | Zone substation | 1,069 | 465 | 2.0785 | 0.004471 | Y
13-02-19 | 11:53 | ZN847:PA48 | URBAN | Asset Failure | Zone substation | 472 | 932 | 0.29806 | 0.00032 | Y
13-02-19 | 11:53 | ZN847:PA5 | URBAN | Asset Failure | Zone substation | 924 | 875 | 0.5478 | 0.000626 | Y
13-02-19 | 11:53 | ZN847:PA7 | URBAN | Asset Failure | Zone substation | 1,320 | 975 | 0.87202 | 0.000894 | Y
13-02-19 | 11:58 | ZN10999:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 117 | 8e-05 | 1e-06 | Y
13-02-19 | 12:27 | ZN2602:PA36 | URBAN | Asset Failure | LV | 34 | 83 | 0.001912 | 2.3e-05 | Y
13-02-19 | 14:14 | ZN1285:PA33 | URBAN | Asset Failure | LV | 1 | 1,226 | 0.000831 | 1e-06 | Y
13-02-19 | 14:31 | ZN9534:PA17 | URBAN | Asset Failure | LV | 1 | 491 | 0.000333 | 1e-06 | Y
13-02-19 | 15:50 | ZN2568:PA39 | URBAN | Asset Failure | LV | 53 | 215 | 0.007706 | 3.6e-05 | Y
13-02-19 | 15:58 | 230:81438 | SHORT RURAL | Other | Other | 1 | 91 | 0.000382 | 4e-06 | Y
13-02-19 | 16:15 | 522:83132 | SHORT RURAL | Asset Failure | LV | 1 | 297 | 0.001242 | 4e-06 | Y
13-02-19 | 19:07 | 810:74054 | LONG RURAL | Asset Failure | HV | 107 | 68 | 2.5613 | 0.037583 | Y
13-02-19 | 19:29 | 210:83466 | URBAN | Other | Other | 1 | 40 | 2.7e-05 | 1e-06 | Y
13-02-19 | 19:31 | ZN129:PA64 | URBAN | Asset Failure | LV | 1 | 148 | 0.000101 | 1e-06 | Y
13-02-19 | 20:15 | 523:33501 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 147 | 0.00123 | 8e-06 | Y
13-02-19 | 20:26 | ZN14144:PA4 | URBAN | Other | Other | 1 | 59 | 4e-05 | 1e-06 | Y
13-02-19 | 20:37 | ZN847:PA14 | URBAN | Other | Other - Self Clearing Trigger | 95 | 163 | 0.010492 | 6.4e-05 | Y
14-02-19 | 01:58 | 522:83124 | URBAN | Animal | Animal nesting/burrowing, etc and other | 11 | 206 | 0.001539 | 7e-06 | N
14-02-19 | 05:02 | ZN340:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 393 | 0.004793 | 1.2e-05 | N
14-02-19 | 05:26 | ZN340:PA8 | URBAN | Third Party | Vehicle impact | 1 | 904 | 0.000612 | 1e-06 | N
14-02-19 | 06:23 | ZN3672:PA9 | URBAN | Asset Failure | LV | 52 | 192 | 0.00675 | 3.5e-05 | N
15-02-19 | 07:46 | ZN847:PA22 | URBAN | Asset Failure | HV | 352 | 216 | 0.051519 | 0.000239 | N
14-02-19 | 07:52 | ZN847:PA48 | URBAN | Other | Other - Self Clearing Trigger | 87 | 88 | 0.005163 | 5.9e-05 | N
14-02-19 | 07:57 | ZN7481:PA20 | URBAN | Third Party | Other | 1 | 232 | 0.000157 | 1e-06 | N
14-02-19 | 11:12 | 807:74179 | SHORT RURAL | Asset Failure | HV | 48 | 56 | 0.011327 | 0.000201 | N
14-02-19 | 11:01 | 526:34640 | SHORT RURAL | Animal | Animal impact | 2 | 101 | 0.000845 | 8e-06 | N
14-02-19 | 11:15 | 526:34640 | SHORT RURAL | Other | Other | 1 | 103 | 0.00043 | 4e-06 | N
14-02-19 | 12:14 | 532:83314 | URBAN | Other | Other | 1 | 150 | 0.000101 | 1e-06 | N
28-12-18 | 12:27 | ZN35800:PA16 | URBAN | Network business | Network error | 60 | 93 | 0.003781 | 4.1e-05 | N
14-02-19 | 12:42 | ZN2400:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 407 | 0.000276 | 1e-06 | N
14-02-19 | 14:06 | ZN2466:PA45 | URBAN | Other | Other | 53 | 166 | 0.005945 | 3.6e-05 | N
14-02-19 | 14:23 | ZN10999:PA12 | URBAN | Asset Failure | LV | 36 | 322 | 0.007855 | 2.4e-05 | N
14-02-19 | 14:29 | ZN9252:PA31 | URBAN | Asset Failure | LV | 1 | 439 | 0.000297 | 1e-06 | N
14-02-19 | 15:29 | ZN3425:PA43 | URBAN | Weather |  | 41 | 211 | 0.005862 | 2.8e-05 | N
14-02-19 | 20:10 | 235:2120 | SHORT RURAL | Asset Failure | LV | 1 | 310 | 0.001297 | 4e-06 | N
14-02-19 | 19:18 | 232:33407 | SHORT RURAL | Other | Other | 1 | 177 | 0.000742 | 4e-06 | N
14-02-19 | 19:23 | ZN35370:PA10 | SHORT RURAL | Asset Failure | HV | 24 | 77 | 0.007715 | 0.0001 | N
14-02-19 | 20:58 | 513:48058 | URBAN | Asset Failure | LV | 1 | 153 | 0.000104 | 1e-06 | N
14-02-19 | 22:05 | 258:80791 | URBAN | Third Party | Fire | 1 | 63 | 4.3e-05 | 1e-06 | N
14-02-19 | 23:46 | ZN1287:PA15 | URBAN | Animal | Animal nesting/burrowing, etc and other | 9 | 84 | 0.000512 | 6e-06 | N
14-02-19 | 23:46 | ZN1287:PA4 | URBAN | Animal | Animal nesting/burrowing, etc and other | 991 | 84 | 0.056405 | 0.000671 | N
15-02-19 | 02:27 | ZN9252:PA31 | URBAN | Other | Other - Self Clearing Trigger | 723 | 81 | 0.039682 | 0.00049 | N
15-02-19 | 03:03 | ZN14892:PA1 | SHORT RURAL | Asset Failure | LV | 14 | 582 | 0.034081 | 5.9e-05 | N
15-02-19 | 06:41 | ZN9118:PA8 | URBAN | Asset Failure | LV | 1 | 364 | 0.000247 | 1e-06 | N
15-02-19 | 07:53 | ZN931:PA22 | URBAN | Other | Other - Self Clearing Trigger | 12 | 161 | 0.001307 | 8e-06 | N
15-02-19 | 08:31 | ZN9118:PA2 | URBAN | Third Party | Vehicle impact | 1 | 134 | 9.1e-05 | 1e-06 | N
15-02-19 | 09:40 | 526:34636 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 350 | 0.001464 | 4e-06 | N
31-01-19 | 20:16 | TS9200:749 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 955 | 0.001295 | 1e-06 | Y
15-02-19 | 10:03 | 232:33409 | SHORT RURAL | Other | Other | 1 | 157 | 0.000655 | 4e-06 | N
15-02-19 | 10:11 | ZN35900:PA3 | URBAN | Third Party | Vehicle impact | 54 | 93 | 0.003408 | 3.7e-05 | N
15-02-19 | 10:21 | ZN167:PA2 | URBAN | Third Party | Vehicle impact | 1 | 40 | 2.7e-05 | 1e-06 | N
15-02-19 | 10:31 | ZN167:PA2 | URBAN | Third Party | Vehicle impact | 1 | 206 | 0.00014 | 1e-06 | N
13-02-19 | 18:54 | ZN1287:PA17 | URBAN | Asset Failure | Distribution substation | 70 | 31 | 0.00147 | 4.7e-05 | Y
15-02-19 | 11:47 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 257 | 0.004877 | 1.9e-05 | N
15-02-19 | 12:02 | ZN10999:PA25 | URBAN | Third Party | Fire | 34 | 106 | 0.002442 | 2.3e-05 | N
15-02-19 | 12:09 | ZN965:PA3 | URBAN | Other | Other | 1 | 471 | 0.000319 | 1e-06 | N
15-02-19 | 13:47 | 512:83743 | SHORT RURAL | Other | Other | 1 | 86 | 0.000361 | 4e-06 | N
15-02-19 | 15:17 | 230:81440 | URBAN | Other | Other | 1 | 62 | 4.2e-05 | 1e-06 | N
15-02-19 | 16:36 | ZN13000:PA11 | SHORT RURAL | Third Party | Vehicle impact | 1,623 | 24 | 0.1652 | 0.006789 | N
15-02-19 | 17:20 | ZN14891:PA10 | SHORT RURAL | Asset Failure | LV | 27 | 130 | 0.014682 | 0.000113 | N
15-02-19 | 17:30 | ZN35370:PA10 | SHORT RURAL | Asset Failure | HV | 24 | 125 | 0.012548 | 0.0001 | N
15-02-19 | 17:53 | ZN3922:PA10 | URBAN | Asset Failure | LV | 1 | 342 | 0.000232 | 1e-06 | N
15-02-19 | 18:25 | ZN9900:PA8 | URBAN | Asset Failure | HV | 125 | 360 | 0.030492 | 8.5e-05 | N
15-02-19 | 19:37 | 270:83590 | URBAN | Other | Other | 1 | 78 | 5.3e-05 | 1e-06 | N
15-02-19 | 21:33 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 17 | 0.000379 | 2.2e-05 | N
15-02-19 | 23:57 | ZN690:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 568 | 0.01501 | 2.6e-05 | N
16-02-19 | 03:15 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 175 | 0.003439 | 2e-05 | N
16-02-19 | 09:29 | ZN180:PA31 | URBAN | Asset Failure | LV | 1 | 408 | 0.000276 | 1e-06 | N
16-02-19 | 10:27 | 206:34440 | URBAN | Other | Other | 1 | 68 | 4.6e-05 | 1e-06 | N
16-02-19 | 12:02 | 810:74054 | LONG RURAL | Asset Failure | LV | 1 | 85 | 0.029803 | 0.000351 | N
16-02-19 | 13:06 | ZN35500:PA32 | URBAN | Other | Other - Self Clearing Trigger | 9 | 84 | 0.000512 | 6e-06 | N
16-02-19 | 16:37 | ZN2602:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 54 | 142 | 0.005206 | 3.7e-05 | N
16-02-19 | 14:34 | ZN35500:PA32 | URBAN | Other | Other | 1 | 94 | 6.4e-05 | 1e-06 | N
16-02-19 | 15:22 | 217:33608 | URBAN | Asset Failure | LV | 12 | 458 | 0.003728 | 8e-06 | N
16-02-19 | 15:32 | 528:83020 | SHORT RURAL | Asset Failure | LV | 1 | 78 | 0.000326 | 4e-06 | N
16-02-19 | 16:19 | ZN2635:PA58 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 101 | 6.8e-05 | 1e-06 | N
16-02-19 | 18:57 | ZN9700:PA17 | URBAN | Asset Failure | HV | 2,269 | 90 | 0.13764 | 0.001537 | N
16-02-19 | 19:17 | ZN2635:PA31 | URBAN | Weather |  | 17 | 123 | 0.001417 | 1.2e-05 | N
16-02-19 | 20:24 | ZN9700:PA17 | URBAN | Other | Other - Arcing | 17 | 259 | 0.002983 | 1.2e-05 | N
16-02-19 | 21:58 | 526:34640 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 221 | 124 | 0.11439 | 0.000924 | N
16-02-19 | 23:49 | 206:34441 | URBAN | Asset Failure | LV | 2 | 850 | 0.001152 | 1e-06 | N
16-02-19 | 23:52 | ZN847:PA28 | URBAN | Other | Other - Self Clearing Trigger | 36 | 83 | 0.002025 | 2.4e-05 | N
17-02-19 | 05:12 | ZN4545:PA6 | URBAN | Third Party | Vehicle impact | 14 | 133 | 0.001262 | 9e-06 | N
17-02-19 | 06:41 | ZN847:PA28 | URBAN | Other | Other - Self Clearing Trigger | 36 | 139 | 0.003391 | 2.4e-05 | N
17-02-19 | 07:04 | ZN15006:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 204 | 0.000853 | 4e-06 | N
17-02-19 | 07:15 | ZN9118:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 3 | 195 | 0.000396 | 2e-06 | N
17-02-19 | 11:36 | ZN14144:PA1 | URBAN | Other | Other | 1 | 95 | 6.4e-05 | 1e-06 | N
17-02-19 | 12:28 | ZN1285:PA24 | URBAN | Other | Other | 1 | 388 | 0.000263 | 1e-06 | N
17-02-19 | 15:20 | ZN35500:PA28 | URBAN | Asset Failure | LV | 72 | 332 | 0.016192 | 4.9e-05 | N
17-02-19 | 16:49 | ZN398:PA3 | URBAN | Asset Failure | LV | 1 | 1,301 | 0.000881 | 1e-06 | N
17-02-19 | 18:04 | ZN12620:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 265 | 0.001109 | 4e-06 | N
17-02-19 | 18:33 | ZN2400:PA21 | URBAN | Other | Other | 1 | 29 | 2e-05 | 1e-06 | N
17-02-19 | 19:28 | ZN2602:PA41 | URBAN | Vegetation | Vegetation Grow In | 1 | 530 | 0.000359 | 1e-06 | N
17-02-19 | 19:55 | ZN35900:PA25 | SHORT RURAL | Other | Other | 1 | 275 | 0.00115 | 4e-06 | N
17-02-19 | 22:13 | 515:35192 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 162 | 102 | 0.069042 | 0.000678 | N
17-02-19 | 22:42 | 526:34640 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 167 | 100 | 0.070121 | 0.000699 | N
18-02-19 | 00:15 | ZN1287:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 49 | 119 | 0.003951 | 3.3e-05 | N
18-02-19 | 04:47 | ZN15008:PA10 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,855 | 79 | 0.098851 | 0.001257 | N
18-02-19 | 08:50 | ZN2400:PA22 | SHORT RURAL | Asset Failure | HV | 1,272 | 77 | 0.40968 | 0.005321 | N
18-02-19 | 08:50 | ZN847:PA47 | SHORT RURAL | Asset Failure | HV | 575 | 108 | 0.26007 | 0.002405 | N
18-02-19 | 09:35 | ZN36100:PA13 | URBAN | Third Party | Other | 212 | 103 | 0.014796 | 0.000144 | N
18-02-19 | 09:35 | ZN36100:PA5 | URBAN | Third Party | Other | 1,428 | 97 | 0.094178 | 0.000968 | N
18-02-19 | 09:53 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 72 | 0.000301 | 4e-06 | N
18-02-19 | 10:02 | ZN12630:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 38 | 0.000159 | 4e-06 | N
18-02-19 | 10:40 | ZN3922:PA19 | URBAN | Asset Failure | LV | 1 | 255 | 0.000173 | 1e-06 | N
18-02-19 | 10:46 | ZN3154:PA18 | URBAN | Other | Other | 1 | 196 | 0.000133 | 1e-06 | N
18-02-19 | 11:32 | ZN15015:PA5 | URBAN | Other | Other | 1 | 91 | 6.2e-05 | 1e-06 | N
18-02-19 | 11:56 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 99 | 0.000413 | 4e-06 | N
18-02-19 | 12:16 | 217:33605 | URBAN | Other | Other | 1 | 73 | 5e-05 | 1e-06 | N
18-02-19 | 13:19 | ZN15012:PA6 | URBAN | Asset Failure | LV | 1 | 430 | 0.000292 | 1e-06 | N
18-02-19 | 13:36 | ZN1673:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 248 | 0.000168 | 1e-06 | N
18-02-19 | 14:12 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 57 | 0.00024 | 4e-06 | N
18-02-19 | 15:56 | ZN15006:PA9 | URBAN | Asset Failure | LV | 1 | 258 | 0.000175 | 1e-06 | N
18-02-19 | 16:10 | 515:35197 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 44 | 0.015543 | 0.000351 | N
18-02-19 | 17:05 | 270:83591 | SHORT RURAL | Asset Failure | LV | 1 | 179 | 0.000748 | 4e-06 | N
18-02-19 | 17:23 | 532:83298 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 822 | 0.003437 | 4e-06 | N
18-02-19 | 17:57 | ZN9900:PA1 | URBAN | Network business | Network error | 79 | 35 | 0.001873 | 5.4e-05 | N
18-02-19 | 17:57 | ZN9900:PA8 | URBAN | Network business | Network error | 125 | 62 | 0.005263 | 8.5e-05 | N
18-02-19 | 20:17 | ZN1673:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 147 | 0.002898 | 2e-05 | N
19-02-19 | 00:47 | 524:33576 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 46 | 88 | 0.01686 | 0.000192 | N
19-02-19 | 01:23 | 213:33774 | URBAN | Third Party | Vehicle impact | 1 | 346 | 0.000235 | 1e-06 | N
19-02-19 | 05:02 | 239:82136 | URBAN | Other | Other - Arcing | 1 | 228 | 0.000154 | 1e-06 | N
18-02-19 | 22:45 | ZN1673:PA1 | URBAN | Other | Other - Self Clearing Trigger | 1 | 1,262 | 0.000855 | 1e-06 | N
19-02-19 | 07:27 | ZN9550:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 893 | 0.00242 | 3e-06 | N
19-02-19 | 09:40 | ZN10999:PA39 | URBAN | Third Party | Other | 876 | 69 | 0.040747 | 0.000594 | N
19-02-19 | 10:34 | 221:11900 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 127 | 8.6e-05 | 1e-06 | N
19-02-19 | 13:59 | ZN12690:PA24 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 260 | 0.001088 | 4e-06 | N
19-02-19 | 14:32 | 224:80331 | URBAN | Asset Failure | HV | 317 | 231 | 0.04958 | 0.000215 | N
19-02-19 | 15:12 | 523:33501 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 47 | 0.000198 | 4e-06 | N
19-02-19 | 15:36 | ZN12570:PA26 | URBAN | Weather |  | 51 | 139 | 0.004793 | 3.5e-05 | N
19-02-19 | 17:58 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 44 | 29 | 0.000855 | 3e-05 | N
19-02-19 | 16:09 | ZN2466:PA45 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 610 | 0.000413 | 1e-06 | N
19-02-19 | 16:28 | ZN7900:PA12 | URBAN | Asset Failure | HV | 466 | 60 | 0.018945 | 0.000316 | N
19-02-19 | 16:28 | ZN7900:PA2 | URBAN | Asset Failure | HV | 1,841 | 60 | 0.074844 | 0.001247 | N
19-02-19 | 16:28 | ZN7900:PA6 | URBAN | Asset Failure | HV | 978 | 60 | 0.039759 | 0.000663 | N
19-02-19 | 22:04 | ZN195:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 43 | 220 | 0.039648 | 0.00018 | N
19-02-19 | 17:31 | 261:81865 | URBAN | Other | Other - Arcing | 1 | 372 | 0.000252 | 1e-06 | N
19-02-19 | 17:38 | ZN1673:PA7 | URBAN | Asset Failure | LV | 25 | 86 | 0.001464 | 1.7e-05 | N
19-02-19 | 17:52 | ZN1673:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 108 | 0.003138 | 2.9e-05 | N
19-02-19 | 18:00 | 257:81987 | URBAN | Other | Other - Self Clearing Trigger | 95 | 105 | 0.006758 | 6.4e-05 | N
19-02-19 | 18:00 | ZN129:PA40 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 105 | 0.001921 | 1.8e-05 | N
20-02-19 | 02:45 | ZN180:PA43 | URBAN | Network business | Switching and protection error | 15 | 35 | 0.000356 | 1e-05 | N
19-02-19 | 19:34 | 801:74118 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 105 | 7.1e-05 | 1e-06 | N
19-02-19 | 20:17 | 220:8689 | URBAN | Other | Other | 1 | 265 | 0.00018 | 1e-06 | N
19-02-19 | 20:30 | 214:8665 | URBAN | Other | Other | 1 | 118 | 8e-05 | 1e-06 | N
19-02-19 | 21:17 | ZN2400:PA18 | SHORT RURAL | Other | Other | 1,358 | 192 | 1.0923 | 0.00568 | N
19-02-19 | 21:17 | ZN35370:PA4 | SHORT RURAL | Other | Other | 142 | 205 | 0.12175 | 0.000594 | N
19-02-19 | 20:47 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 78 | 0.000652 | 8e-06 | N
19-02-19 | 21:35 | ZN9118:PA24 | URBAN | Other | Other - Arcing | 13 | 283 | 0.002493 | 9e-06 | N
19-02-19 | 21:51 | ZN3472:PA11 | URBAN | Other | Other - Arcing | 1 | 74 | 5e-05 | 1e-06 | N
20-02-19 | 00:36 | ZN116:PA30 | URBAN | Other | Other | 1 | 876 | 0.000594 | 1e-06 | N
19-02-19 | 22:33 | ZN3155:PA35 | URBAN | Other | Other - Arcing | 1 | 346 | 0.000234 | 1e-06 | N
19-02-19 | 22:40 | ZN3155:PA35 | URBAN | Other | Other - Arcing | 1 | 339 | 0.00023 | 1e-06 | N
19-02-19 | 23:03 | ZN36300:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 867 | 0.000587 | 1e-06 | N
19-02-19 | 22:48 | ZN36800:PA36 | URBAN | Other | Other - Arcing | 1 | 522 | 0.000354 | 1e-06 | N
19-02-19 | 22:56 | ZN3472:PA27 | URBAN | Other | Other - Arcing | 1 | 26 | 1.8e-05 | 1e-06 | N
19-02-19 | 22:36 | ZN10993:PA22 | URBAN | Other | Other - Self Clearing Trigger | 2,088 | 61 | 0.0863 | 0.001415 | N
19-02-19 | 23:21 | ZN874:PA2 | URBAN | Other | Other | 1 | 639 | 0.000433 | 1e-06 | N
19-02-19 | 23:21 | ZN874:PA15 | URBAN | Other | Other | 1 | 640 | 0.000434 | 1e-06 | N
19-02-19 | 23:43 | ZN3155:PA19 | URBAN | Other | Other - Arcing | 1 | 617 | 0.000418 | 1e-06 | N
19-02-19 | 23:51 | ZN340:PA3 | URBAN | Asset Failure | LV | 1 | 149 | 0.000101 | 1e-06 | N
19-02-19 | 23:50 | ZN10993:PA23 | URBAN | Animal | Animal nesting/burrowing, etc and other | 737 | 35 | 0.017478 | 0.000499 | N
19-02-19 | 23:48 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 373 | 235 | 0.36622 | 0.00156 | N
19-02-19 | 23:55 | ZN3155:PA19 | URBAN | Other | Other - Arcing | 1 | 605 | 0.00041 | 1e-06 | N
19-02-19 | 23:59 | ZN1850:PA45 | URBAN | Other | Other | 1 | 140 | 9.5e-05 | 1e-06 | N
20-02-19 | 00:11 | ZN398:PA31 | URBAN | Other | Other | 1 | 650 | 0.00044 | 1e-06 | N
20-02-19 | 00:24 | 261:81865 | URBAN | Other | Other | 1 | 81 | 5.5e-05 | 1e-06 | N
20-02-19 | 00:31 | ZN10993:PA35 | URBAN | Asset Failure | LV | 90 | 44 | 0.002683 | 6.1e-05 | N
20-02-19 | 01:19 | ZN180:PA22 | URBAN | Other | Other - Arcing | 1 | 461 | 0.000312 | 1e-06 | N
20-02-19 | 01:20 | ZN15012:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 65 | 0.001761 | 2.7e-05 | N
20-02-19 | 04:16 | ZN12610:PA6 | URBAN | Other | Other - Arcing | 38 | 74 | 0.001905 | 2.6e-05 | N
20-02-19 | 04:13 | ZN35600:PA1 | URBAN | Asset Failure | LV | 18 | 222 | 0.002707 | 1.2e-05 | N
20-02-19 | 06:13 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 332 | 0.000225 | 1e-06 | N
20-02-19 | 13:29 | ZN15015:PA15 | SHORT RURAL | Asset Failure | LV | 1 | 61 | 0.000256 | 4e-06 | N
20-02-19 | 09:00 | ZN10993:PA22 | URBAN | Network business | Switching and protection error | 77 | 162 | 0.008462 | 5.2e-05 | N
20-02-19 | 08:21 | ZN35800:PA2 | URBAN | Other | Other | 1 | 402 | 0.000272 | 1e-06 | N
20-02-19 | 08:22 | ZN35800:PA2 | URBAN | Other | Other - Arcing | 1 | 401 | 0.000272 | 1e-06 | N
20-02-19 | 08:32 | ZN15006:PA12 | URBAN | Asset Failure | LV | 1 | 538 | 0.000364 | 1e-06 | N
20-02-19 | 09:25 | ZN2196:PA5 | URBAN | Other | Other | 1 | 320 | 0.000217 | 1e-06 | N
20-02-19 | 09:28 | 230:81440 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 73 | 5e-05 | 1e-06 | N
20-02-19 | 09:54 | ZN15014:PA19 | URBAN | Asset Failure | LV | 1 | 711 | 0.000481 | 1e-06 | N
20-02-19 | 10:15 | 512:83743 | SHORT RURAL | Asset Failure | HV | 3 | 65 | 0.000816 | 1.3e-05 | N
20-02-19 | 10:16 | 511:29878 | SHORT RURAL | Other | Other - Arcing | 1 | 283 | 0.001185 | 4e-06 | N
20-02-19 | 10:35 | ZN129:PA36 | URBAN | Other | Other - Arcing | 1 | 175 | 0.000118 | 1e-06 | N
20-02-19 | 10:47 | ZN14891:PA16 | SHORT RURAL | Other | Other | 1 | 223 | 0.000933 | 4e-06 | N
19-02-19 | 07:00 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 135 | 0.000565 | 4e-06 | N
20-02-19 | 11:20 | ZN10999:PA36 | URBAN | Other | Other - Arcing | 15 | 150 | 0.001524 | 1e-05 | N
20-02-19 | 13:18 | ZN965:PA38 | URBAN | Third Party | Vehicle impact | 1 | 311 | 0.000211 | 1e-06 | N
20-02-19 | 14:15 | ZN1290:PA11 | URBAN | Third Party | Other | 1 | 280 | 0.00019 | 1e-06 | N
19-02-19 | 22:22 | ZN12630:PA3 | SHORT RURAL | Asset Failure | HV | 153 | 122 | 0.078192 | 0.00064 | N
20-02-19 | 16:35 | 265:81649 | URBAN | Asset Failure | HV | 4 | 110 | 0.000298 | 3e-06 | N
20-02-19 | 17:19 | ZN9700:PA17 | URBAN | Other | Other | 1 | 140 | 9.5e-05 | 1e-06 | N
20-02-19 | 17:31 | ZN9550:PA9 | URBAN | Asset Failure | LV | 1 | 148 | 0.0001 | 1e-06 | N
20-02-19 | 19:51 | ZN15008:PA5 | URBAN | Asset Failure | Distribution substation | 186 | 69 | 0.008672 | 0.000126 | N
21-02-19 | 04:16 | ZN9037:PA10 | URBAN | Other | Other - Arcing | 1 | 423 | 0.000287 | 1e-06 | N
20-02-19 | 19:35 | ZN10998:PA10 | URBAN | Other | Other - Arcing | 2 | 1,172 | 0.001588 | 1e-06 | N
20-02-19 | 19:36 | 512:83743 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 226 | 0.000946 | 4e-06 | N
20-02-19 | 20:17 | ZN10997:PA2 | URBAN | Other | Other - Arcing | 1 | 253 | 0.000171 | 1e-06 | N
20-02-19 | 21:23 | 526:34636 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 11 | 142 | 0.006533 | 4.6e-05 | N
20-02-19 | 22:37 | 222:33602 | URBAN | Other | Other - Arcing | 1 | 189 | 0.000128 | 1e-06 | N
21-02-19 | 03:02 | ZN15002:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 136 | 538 | 0.049581 | 9.2e-05 | N
21-02-19 | 03:42 | 511:29877 | SHORT RURAL | Third Party | Vehicle impact | 1,041 | 74 | 0.32015 | 0.004354 | N
21-02-19 | 06:20 | ZN3922:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 580 | 0.000393 | 1e-06 | N
21-02-19 | 07:14 | ZN1193:PA12 | URBAN | Asset Failure | HV | 922 | 141 | 0.088078 | 0.000625 | N
21-02-19 | 08:10 | ZN35800:PA16 | URBAN | Asset Failure | LV | 7 | 214 | 0.001016 | 5e-06 | N
21-02-19 | 09:02 | ZN2196:PA25 | URBAN | Other | Other | 1 | 1,347 | 0.000912 | 1e-06 | N
21-02-19 | 09:11 | 812:19066 | SHORT RURAL | Other | Other | 1 | 106 | 0.000445 | 4e-06 | N
21-02-19 | 09:28 | 532:83293 | URBAN | Other | Other - Arcing | 1 | 166 | 0.000113 | 1e-06 | N
21-02-19 | 09:19 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 36 | 146 | 0.021984 | 0.000151 | N
20-02-19 | 18:22 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 149 | 0.000623 | 4e-06 | N
21-02-19 | 11:43 | 270:83591 | SHORT RURAL | Asset Failure | LV | 1 | 182 | 0.00076 | 4e-06 | N
21-02-19 | 12:03 | 202:34260 | URBAN | Other | Other | 1 | 177 | 0.00012 | 1e-06 | N
21-02-19 | 12:28 | ZN15004:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 377 | 0.000255 | 1e-06 | N
21-02-19 | 12:43 | ZN2310:PA24 | URBAN | Other | Other - Self Clearing Trigger | 45 | 76 | 0.002331 | 3e-05 | N
21-02-19 | 13:10 | 520:48172 | SHORT RURAL | Asset Failure | HV | 10 | 45 | 0.001882 | 4.2e-05 | N
21-02-19 | 08:00 | ZN2602:PA21 | URBAN | Network business | Network error | 44 | 440 | 0.013117 | 3e-05 | N
21-02-19 | 14:12 | ZN1193:PA15 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 78 | 0.000327 | 4e-06 | N
21-02-19 | 14:28 | 502:48010 | SHORT RURAL | Asset Failure | HV | 1 | 187 | 0.000782 | 4e-06 | N
21-02-19 | 17:22 | ZN35600:PA4 | URBAN | Other | Other - Arcing | 1 | 217 | 0.000147 | 1e-06 | N
21-02-19 | 17:28 | 243:80075 | SHORT RURAL | Asset Failure | LV | 1 | 288 | 0.001206 | 4e-06 | N
21-02-19 | 19:59 | ZN35600:PA9 | URBAN | Other | Other - Arcing | 1 | 93 | 6.3e-05 | 1e-06 | N
21-02-19 | 20:50 | 232:33413 | SHORT RURAL | Asset Failure | HV | 1,063 | 78 | 0.34639 | 0.004446 | N
21-02-19 | 21:06 | ZN3922:PA29 | URBAN | Asset Failure | LV | 1 | 266 | 0.00018 | 1e-06 | N
21-02-19 | 21:33 | ZN15010:PA24 | URBAN | Other | Other - Arcing | 1 | 197 | 0.000133 | 1e-06 | N
21-02-19 | 22:00 | ZN35555:PA16 | URBAN | Other | Other - Arcing | 1 | 212 | 0.000144 | 1e-06 | N
21-02-19 | 23:01 | ZN3425:PA43 | URBAN | Other | Other - Arcing | 1 | 629 | 0.000426 | 1e-06 | N
21-02-19 | 23:23 | ZN3155:PA21 | URBAN | Other | Other - Self Clearing Trigger | 54 | 67 | 0.002451 | 3.7e-05 | N
22-02-19 | 07:20 | ZN262:PA31 | URBAN | Other | Other - Arcing | 1 | 370 | 0.000251 | 1e-06 | N
22-02-19 | 07:43 | ZN15008:PA7 | URBAN | Other | Other | 1 | 601 | 0.000407 | 1e-06 | N
22-02-19 | 08:18 | 220:8692 | URBAN | Other | Other | 1 | 92 | 6.2e-05 | 1e-06 | N
22-02-19 | 08:31 | 220:8691 | URBAN | Other | Other | 1 | 78 | 5.3e-05 | 1e-06 | N
22-02-19 | 08:55 | ZN35900:PA4 | SHORT RURAL | Network business | Switching and protection error | 49 | 25 | 0.005124 | 0.000205 | N
22-02-19 | 09:12 | ZN9037:PA10 | URBAN | Other | Other - Arcing | 1 | 107 | 7.3e-05 | 1e-06 | N
22-02-19 | 09:15 | ZN15011:PA4 | URBAN | Third Party | Vehicle impact | 63 | 60 | 0.002561 | 4.3e-05 | N
22-02-19 | 09:37 | ZN2196:PA20 | URBAN | Asset Failure | LV | 4 | 193 | 0.000523 | 3e-06 | N
22-02-19 | 09:43 | 213:33777 | SHORT RURAL | Other | Other | 1 | 69 | 0.000288 | 4e-06 | N
22-02-19 | 10:39 | 216:10723 | URBAN | Other | Other | 1 | 54 | 3.7e-05 | 1e-06 | N
22-02-19 | 10:39 | ZN262:PA31 | URBAN | Other | Other - Arcing | 1 | 275 | 0.000186 | 1e-06 | N
22-02-19 | 15:05 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 164 | 0.000687 | 4e-06 | N
22-02-19 | 15:12 | ZN14144:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 407 | 0.001703 | 4e-06 | N
22-02-19 | 16:32 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 142 | 0.049889 | 0.000351 | N
22-02-19 | 18:40 | 509:33395 | LONG RURAL | Asset Failure | HV | 15 | 80 | 0.42061 | 0.005258 | N
23-02-19 | 04:14 | 524:33572 | SHORT RURAL | Asset Failure | LV | 1 | 419 | 0.00175 | 4e-06 | N
23-02-19 | 05:37 | ZN15010:PA28 | SHORT RURAL | Other | Other - Arcing | 1 | 582 | 0.002432 | 4e-06 | N
23-02-19 | 06:58 | ZN80:PA27 | URBAN | Vegetation | Vegetation Grow In | 1 | 501 | 0.000339 | 1e-06 | N
23-02-19 | 09:15 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 210 | 0.14721 | 0.000701 | N
23-02-19 | 12:55 | ZN10998:PA32 | SHORT RURAL | Other | Other - Arcing | 1 | 300 | 0.001253 | 4e-06 | N
23-02-19 | 12:55 | 522:83132 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 206 | 0.000862 | 4e-06 | N
23-02-19 | 12:56 | ZN36200:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 69 | 307 | 0.088629 | 0.000289 | N
23-02-19 | 14:17 | ZN12640:PA2 | URBAN | Third Party | Vehicle impact | 143 | 288 | 0.027856 | 9.7e-05 | N
23-02-19 | 15:15 | ZN12640:PA2 | URBAN | Third Party | Vehicle impact | 91 | 185 | 0.011403 | 6.2e-05 | N
23-02-19 | 14:49 | ZN2466:PA45 | URBAN | Vegetation | Vegetation Blow/Fall In | 53 | 55 | 0.001985 | 3.6e-05 | N
23-02-19 | 15:19 | ZN9245:PA13 | URBAN | Weather |  | 37 | 61 | 0.001522 | 2.5e-05 | N
23-02-19 | 16:12 | ZN1788:PA15 | URBAN | Asset Failure | LV | 1 | 239 | 0.000162 | 1e-06 | N
23-02-19 | 16:30 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.000376 | 4e-06 | N
24-02-19 | 01:07 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 194 | 57 | 0.04648 | 0.000811 | N
24-02-19 | 03:47 | ZN15014:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 328 | 58 | 0.012812 | 0.000222 | N
24-02-19 | 04:57 | 258:80779 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 198 | 0.000134 | 1e-06 | N
24-02-19 | 07:00 | ZN342:PA18 | URBAN | Other | Other - Self Clearing Trigger | 33 | 294 | 0.006572 | 2.2e-05 | N
24-02-19 | 07:00 | 222:33601 | SHORT RURAL | Third Party | Vehicle impact | 78 | 630 | 0.20544 | 0.000326 | N
24-02-19 | 10:44 | 513:48056 | SHORT RURAL | Other | Other - Arcing | 1 | 267 | 0.001116 | 4e-06 | N
24-02-19 | 11:38 | 524:33578 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 381 | 0.000258 | 1e-06 | N
24-02-19 | 11:51 | 230:81432 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 64 | 0.000268 | 4e-06 | N
24-02-19 | 12:45 | ZN2196:PA18 | URBAN | Other | Other | 1 | 138 | 9.3e-05 | 1e-06 | N
24-02-19 | 14:10 | 256:80650 | URBAN | Other | Other | 1 | 75 | 5.1e-05 | 1e-06 | N
24-02-19 | 16:10 | ZN1673:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 77 | 0.001356 | 1.8e-05 | N
24-02-19 | 16:19 | 224:80341 | URBAN | Other | Other | 1 | 41 | 2.8e-05 | 1e-06 | N
24-02-19 | 16:26 | ZN10999:PA38 | URBAN | Asset Failure | LV | 103 | 103 | 0.007214 | 7e-05 | N
24-02-19 | 18:28 | ZN36200:PA4 | SHORT RURAL | Asset Failure | LV | 8 | 51 | 0.001715 | 3.3e-05 | N
25-02-19 | 03:58 | ZN3922:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 53 | 87 | 0.019277 | 0.000222 | N
25-02-19 | 04:52 | ZN3472:PA30 | URBAN | Other | Other | 1 | 553 | 0.000375 | 1e-06 | N
25-02-19 | 07:00 | ZN10997:PA2 | URBAN | Other | Other | 1 | 180 | 0.000122 | 1e-06 | N
25-02-19 | 07:21 | ZN36300:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 98 | 6.6e-05 | 1e-06 | N
25-02-19 | 08:39 | ZN15012:PA2 | URBAN | Asset Failure | Zone substation | 1,299 | 26 | 0.022878 | 0.00088 | N
25-02-19 | 08:39 | ZN15012:PA4 | URBAN | Asset Failure | Zone substation | 1,219 | 26 | 0.021469 | 0.000826 | N
25-02-19 | 08:39 | ZN15012:PA6 | URBAN | Asset Failure | Zone substation | 1,449 | 26 | 0.025519 | 0.000982 | N
25-02-19 | 08:39 | ZN15012:PA8 | URBAN | Asset Failure | Zone substation | 1,159 | 26 | 0.020412 | 0.000785 | N
25-02-19 | 11:59 | 509:33395 | LONG RURAL | Asset Failure | LV | 2 | 1,189 | 0.83351 | 0.000701 | N
24-02-19 | 14:30 | 232:33413 | SHORT RURAL | Other | Other | 55 | 20 | 0.004599 | 0.00023 | N
25-02-19 | 09:49 | ZN15012:PA4 | URBAN | Other | Other | 1 | 39 | 2.6e-05 | 1e-06 | N
23-02-19 | 09:45 | ZN129:PA63 | URBAN | Third Party | Vehicle impact | 3 | 225 | 0.000457 | 2e-06 | N
21-02-19 | 16:00 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 30 | 0.000251 | 8e-06 | N
25-02-19 | 10:05 | ZN5868:PA14 | URBAN | Asset Failure | LV | 2 | 120 | 0.000163 | 1e-06 | N
25-02-19 | 10:58 | ZN35555:PA14 | URBAN | Third Party | Other | 244 | 54 | 0.008964 | 0.000165 | N
25-02-19 | 13:05 | 814:82289 | SHORT RURAL | Other | Other | 3 | 55 | 0.00069 | 1.3e-05 | N
25-02-19 | 11:45 | ZN9118:PA8 | URBAN | Asset Failure | LV | 1 | 1,266 | 0.000858 | 1e-06 | N
25-02-19 | 12:19 | ZN15012:PA2 | URBAN | Other | Other | 1 | 47 | 3.2e-05 | 1e-06 | N
25-02-19 | 15:45 | ZN9245:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 338 | 0.000229 | 1e-06 | N
25-02-19 | 16:30 | ZN10997:PA1 | URBAN | Asset Failure | LV | 39 | 189 | 0.005006 | 2.6e-05 | N
25-02-19 | 20:02 | 511:29878 | SHORT RURAL | Asset Failure | HV | 131 | 275 | 0.15061 | 0.000548 | N
25-02-19 | 21:05 | ZN931:PA2 | URBAN | Asset Failure | LV | 123 | 1,650 | 0.13746 | 8.3e-05 | N
25-02-19 | 21:55 | ZN9245:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 28 | 1.9e-05 | 1e-06 | N
25-02-19 | 21:55 | ZN9245:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 28 | 1.9e-05 | 1e-06 | N
26-02-19 | 06:59 | ZN262:PA16 | URBAN | Other | Other - Self Clearing Trigger | 70 | 121 | 0.005716 | 4.7e-05 | N
25-02-19 | 08:50 | 813:89061 | LONG RURAL | Asset Failure | HV | 4 | 140 | 0.19628 | 0.001402 | N
26-02-19 | 08:20 | ZN965:PA42 | URBAN | Third Party | Vehicle impact | 1 | 129 | 8.7e-05 | 1e-06 | N
26-02-19 | 12:10 | 812:19072 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 240 | 0.001003 | 4e-06 | N
26-02-19 | 08:46 | 814:82289 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 89 | 0.000744 | 8e-06 | N
26-02-19 | 09:46 | ZN14892:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 619 | 0.00259 | 4e-06 | N
26-02-19 | 12:06 | ZN35600:PA9 | URBAN | Third Party | Vehicle impact | 63 | 453 | 0.019334 | 4.3e-05 | N
26-02-19 | 13:32 | ZN15013:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 268 | 0.011204 | 4.2e-05 | N
26-02-19 | 13:35 | 258:80794 | URBAN | Other | Other - Self Clearing Trigger | 2 | 48 | 6.5e-05 | 1e-06 | N
26-02-19 | 15:37 | 508:82578 | SHORT RURAL | Other | Other | 1 | 123 | 0.000514 | 4e-06 | N
26-02-19 | 16:47 | ZN3672:PA22 | URBAN | Third Party | Vehicle impact | 1 | 502 | 0.00034 | 1e-06 | N
26-02-19 | 17:49 | ZN690:PA36 | URBAN | Other | Other | 1 | 292 | 0.000198 | 1e-06 | N
26-02-19 | 23:41 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 509 | 0.002126 | 4e-06 | N
27-02-19 | 00:58 | ZN12650:PA12 | URBAN | Third Party | Vehicle impact | 12 | 152 | 0.001236 | 8e-06 | N
27-02-19 | 02:13 | ZN35555:PA13 | URBAN | Asset Failure | LV | 51 | 447 | 0.01544 | 3.5e-05 | N
27-02-19 | 03:51 | ZN1287:PA5 | URBAN | Asset Failure | HV | 1,143 | 55 | 0.042584 | 0.000774 | N
27-02-19 | 05:34 | ZN12570:PA22 | SHORT RURAL | Other | Other - Arcing | 1 | 446 | 0.001863 | 4e-06 | N
27-02-19 | 07:11 | 507:80923 | SHORT RURAL | Asset Failure | HV | 1,734 | 29 | 0.21124 | 0.00725 | N
27-02-19 | 07:41 | ZN262:PA16 | URBAN | Asset Failure | LV | 1 | 78 | 5.3e-05 | 1e-06 | N
27-02-19 | 08:18 | ZN3154:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 317 | 0.007301 | 2.3e-05 | N
27-02-19 | 08:57 | 507:80932 | SHORT RURAL | Other | Other - Arcing | 1 | 1,692 | 0.007075 | 4e-06 | N
27-02-19 | 09:20 | ZN2835:PA15 | URBAN | Asset Failure | HV | 2,899 | 116 | 0.22729 | 0.001964 | N
27-02-19 | 09:20 | ZN2835:PA41 | URBAN | Asset Failure | HV | 8 | 113 | 0.000612 | 5e-06 | N
27-02-19 | 09:20 | ZN874:PA16 | URBAN | Asset Failure | HV | 73 | 121 | 0.005983 | 4.9e-05 | N
27-02-19 | 09:34 | ZN36100:PA19 | URBAN | Third Party | Vehicle impact | 1 | 86 | 5.8e-05 | 1e-06 | N
27-02-19 | 16:35 | ZN15008:PA7 | URBAN | Other | Other | 1 | 864 | 0.000586 | 1e-06 | N
27-02-19 | 18:12 | ZN15008:PA7 | URBAN | Other | Other | 1 | 767 | 0.00052 | 1e-06 | N
27-02-19 | 18:58 | ZN262:PA30 | URBAN | Asset Failure | LV | 1 | 759 | 0.000514 | 1e-06 | N
27-02-19 | 19:31 | ZN129:PA57 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 231 | 0.000157 | 1e-06 | N
27-02-19 | 23:02 | ZN965:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 628 | 0.000425 | 1e-06 | N
28-02-19 | 07:48 | ZN3672:PA13 | URBAN | Asset Failure | LV | 1 | 71 | 4.8e-05 | 1e-06 | N
14-02-19 | 07:22 | ZN847:PA21 | URBAN | Asset Failure | HV | 1,141 | 83 | 0.06417 | 0.000773 | N
14-02-19 | 07:51 | ZN847:PA22 | URBAN | Network business | Network error | 48 | 149 | 0.004846 | 3.3e-05 | N
28-02-19 | 12:02 | ZN2835:PA15 | URBAN | Network business | Network error | 12 | 108 | 0.000878 | 8e-06 | N
28-02-19 | 14:50 | ZN2196:PA6 | URBAN | Asset Failure | HV | 65 | 160 | 0.007023 | 4.4e-05 | N
28-02-19 | 14:50 | ZN2196:PA11 | URBAN | Asset Failure | HV | 106 | 94 | 0.006756 | 7.2e-05 | N
28-02-19 | 18:17 | ZN3672:PA37 | URBAN | Other | Other - Arcing | 86 | 223 | 0.012979 | 5.8e-05 | N
28-02-19 | 20:28 | 217:33610 | URBAN | Animal | Animal impact | 1,950 | 27 | 0.035665 | 0.001321 | N
28-02-19 | 22:28 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 137 | 0.002875 | 2.1e-05 | N
01-03-19 | 04:04 | 256:80640 | URBAN | Third Party | Vehicle impact | 1 | 1,105 | 0.000749 | 1e-06 | N
01-03-19 | 04:11 | 256:80640 | URBAN | Third Party | Vehicle impact | 1 | 1,040 | 0.000704 | 1e-06 | N
01-03-19 | 08:16 | ZN2400:PA23 | URBAN | Other | Other | 1 | 50 | 3.4e-05 | 1e-06 | N
01-03-19 | 11:11 | ZN1068:PA27 | URBAN | Third Party | Vehicle impact | 1 | 229 | 0.000155 | 1e-06 | N
01-03-19 | 11:21 | 522:83123 | SHORT RURAL | Third Party | Vehicle impact | 1 | 188 | 0.000788 | 4e-06 | N
01-03-19 | 12:10 | 221:11894 | URBAN | Third Party | Vehicle impact | 99 | 240 | 0.016095 | 6.7e-05 | N
01-03-19 | 13:34 | 233:82812 | SHORT RURAL | Other | Other | 1 | 110 | 0.00046 | 4e-06 | N
01-03-19 | 14:48 | 233:82813 | SHORT RURAL | Other | Other | 1 | 52 | 0.000217 | 4e-06 | N
01-03-19 | 15:11 | 813:89062 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 108 | 0.000452 | 4e-06 | N
01-03-19 | 15:25 | ZN14892:PA6 | URBAN | Third Party | Vehicle impact | 1 | 140 | 9.5e-05 | 1e-06 | N
01-03-19 | 17:15 | ZN3155:PA22 | URBAN | Third Party | Other | 27 | 30 | 0.000549 | 1.8e-05 | N
01-03-19 | 17:22 | 523:33501 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 58 | 56 | 0.013496 | 0.000242 | N
01-03-19 | 18:55 | ZN36100:PA15 | URBAN | Asset Failure | LV | 1 | 266 | 0.00018 | 1e-06 | N
01-03-19 | 19:55 | 222:33600 | URBAN | Asset Failure | LV | 1 | 169 | 0.000115 | 1e-06 | N
01-03-19 | 20:26 | ZN35370:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 187 | 199 | 0.15568 | 0.000782 | N
01-03-19 | 20:26 | ZN965:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 488 | 88 | 0.02909 | 0.000331 | N
01-03-19 | 21:38 | 522:83124 | URBAN | Animal | Animal nesting/burrowing, etc and other | 17 | 131 | 0.00151 | 1.2e-05 | N
02-03-19 | 00:19 | ZN116:PA30 | URBAN | Other | Other - Arcing | 1 | 736 | 0.000498 | 1e-06 | N
02-03-19 | 01:21 | 516:48065 | SHORT RURAL | Other | Other - Self Clearing Trigger | 35 | 224 | 0.032778 | 0.000146 | N
02-03-19 | 01:21 | 516:48066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 89 | 226 | 0.084095 | 0.000372 | N
02-03-19 | 01:21 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 281 | 225 | 0.26434 | 0.001175 | N
02-03-19 | 03:46 | ZN2466:PA16 | URBAN | Other | Other | 1 | 529 | 0.000358 | 1e-06 | N
02-03-19 | 07:37 | 511:29877 | SHORT RURAL | Other | Other - Arcing | 1 | 283 | 0.001182 | 4e-06 | N
02-03-19 | 10:30 | ZN36100:PA19 | URBAN | Asset Failure | LV | 1 | 41 | 2.7e-05 | 1e-06 | N
02-03-19 | 10:45 | ZN116:PA2 | URBAN | Other | Other | 1 | 326 | 0.000221 | 1e-06 | N
02-03-19 | 11:15 | ZN10994:PA1 | URBAN | Asset Failure | LV | 1 | 381 | 0.000258 | 1e-06 | N
02-03-19 | 12:10 | ZN2835:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 241 | 0.000163 | 1e-06 | N
02-03-19 | 14:20 | ZN14144:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 285 | 73 | 0.014038 | 0.000193 | N
02-03-19 | 17:10 | ZN12570:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 125 | 8.5e-05 | 1e-06 | N
03-03-19 | 02:32 | ZN690:PA28 | URBAN | Asset Failure | HV | 1,689 | 88 | 0.10041 | 0.001144 | N
03-03-19 | 00:28 | ZN12660:PA14 | SHORT RURAL | Other | Other - Self Clearing Trigger | 47 | 432 | 0.08485 | 0.000196 | N
03-03-19 | 07:17 | 516:48067 | SHORT RURAL | Asset Failure | LV | 7 | 268 | 0.00784 | 2.9e-05 | N
03-03-19 | 07:42 | ZN3154:PA22 | SHORT RURAL | Other | Other - Arcing | 1 | 287 | 0.0012 | 4e-06 | N
03-03-19 | 09:04 | ZN630:PA31 | URBAN | Third Party | Vehicle impact | 1 | 333 | 0.000225 | 1e-06 | N
03-03-19 | 12:46 | ZN15004:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 387 | 0.000262 | 1e-06 | N
03-03-19 | 17:18 | ZN15005:PA10 | URBAN | Asset Failure | HV | 750 | 155 | 0.078495 | 0.000508 | N
03-03-19 | 17:18 | ZN15005:PA12 | URBAN | Asset Failure | HV | 395 | 171 | 0.045737 | 0.000267 | N
03-03-19 | 17:18 | ZN15013:PA8 | URBAN | Asset Failure | HV | 32 | 167 | 0.003619 | 2.2e-05 | N
03-03-19 | 17:38 | ZN847:PA5 | URBAN | Other | Other | 1 | 77 | 5.2e-05 | 1e-06 | N
03-03-19 | 18:08 | ZN9035:PA10 | URBAN | Other | Other - Self Clearing Trigger | 17 | 92 | 0.001059 | 1.2e-05 | N
03-03-19 | 18:39 | ZN3672:PA9 | URBAN | Other | Other - Arcing | 1 | 316 | 0.000214 | 1e-06 | N
03-03-19 | 19:55 | ZN9035:PA4 | URBAN | Asset Failure | HV | 2,091 | 66 | 0.093773 | 0.001416 | N
03-03-19 | 21:44 | ZN15001:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 886 | 0.0006 | 1e-06 | N
03-03-19 | 22:06 | ZN4545:PA44 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 263 | 0.000178 | 1e-06 | N
04-03-19 | 00:26 | ZN3672:PA13 | URBAN | Other | Other - Arcing | 1 | 63 | 4.3e-05 | 1e-06 | N
04-03-19 | 03:46 | ZN10993:PA23 | URBAN | Animal | Animal nesting/burrowing, etc and other | 736 | 93 | 0.046175 | 0.000498 | N
04-03-19 | 06:25 | 258:80790 | URBAN | Asset Failure | LV | 18 | 52 | 0.000634 | 1.2e-05 | N
05-03-19 | 07:39 | ZN35370:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 351 | 0.001467 | 4e-06 | N
04-03-19 | 08:24 | 258:80790 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 76 | 5.1e-05 | 1e-06 | N
04-03-19 | 09:01 | ZN1610:PA17 | URBAN | Asset Failure | LV | 1 | 103 | 7e-05 | 1e-06 | N
04-03-19 | 09:20 | 508:82579 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 13 | 90 | 0.004891 | 5.4e-05 | N
28-02-19 | 08:45 | 814:82283 | SHORT RURAL | Other | Other | 1 | 5 | 2.1e-05 | 4e-06 | N
04-03-19 | 10:03 | 221:11899 | SHORT RURAL | Asset Failure | LV | 1 | 462 | 0.00193 | 4e-06 | N
04-03-19 | 10:57 | 509:33395 | LONG RURAL | Other | Other - Arcing | 1 | 453 | 0.15877 | 0.000351 | N
04-03-19 | 13:38 | ZN1193:PA28 | URBAN | Other | Other - Arcing | 1 | 504 | 0.000341 | 1e-06 | N
04-03-19 | 15:38 | ZN690:PA33 | URBAN | Third Party | Vehicle impact | 1 | 600 | 0.000406 | 1e-06 | N
04-03-19 | 15:40 | ZN35900:PA20 | URBAN | Third Party | Vehicle impact | 20 | 200 | 0.002708 | 1.4e-05 | N
04-03-19 | 15:57 | 213:33775 | URBAN | Other | Other | 1 | 42 | 2.9e-05 | 1e-06 | N
04-03-19 | 17:19 | ZN340:PA40 | URBAN | Other | Other | 51 | 136 | 0.004689 | 3.5e-05 | N
04-03-19 | 17:48 | ZN1673:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 221 | 0.00015 | 1e-06 | N
04-03-19 | 17:49 | ZN1673:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 221 | 0.00015 | 1e-06 | N
04-03-19 | 19:55 | 807:74183 | SHORT RURAL | Asset Failure | LV | 1 | 110 | 0.00046 | 4e-06 | N
04-03-19 | 20:08 | ZN1673:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 82 | 5.5e-05 | 1e-06 | N
04-03-19 | 21:48 | 261:81864 | URBAN | Other | Other - Arcing | 1 | 913 | 0.000618 | 1e-06 | N
05-03-19 | 01:24 | ZN3672:PA35 | SHORT RURAL | Third Party | Dig-in | 69 | 143 | 0.041292 | 0.000288 | N
05-03-19 | 05:15 | ZN12570:PA37 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 34 | 270 | 0.038343 | 0.000142 | N
05-03-19 | 06:31 | ZN847:PA15 | URBAN | Asset Failure | LV | 18 | 229 | 0.002789 | 1.2e-05 | N
05-03-19 | 06:35 | ZN9118:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 96 | 113 | 0.007313 | 6.5e-05 | N
05-03-19 | 07:05 | ZN15009:PA7 | URBAN | Other | Other - Self Clearing Trigger | 19 | 144 | 0.001854 | 1.3e-05 | N
05-03-19 | 07:09 | ZN10991:PA13 | URBAN | Weather |  | 1 | 170 | 0.000115 | 1e-06 | N
05-03-19 | 10:31 | ZN15004:PA3 | SHORT RURAL | Third Party | Other | 36 | 223 | 0.03356 | 0.00015 | N
05-03-19 | 11:02 | ZN80:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 208 | 0.000141 | 1e-06 | N
05-03-19 | 11:48 | 221:11900 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 71 | 4.8e-05 | 1e-06 | N
05-03-19 | 13:15 | 813:89061 | LONG RURAL | Asset Failure | HV | 50 | 50 | 0.87658 | 0.017532 | N
05-03-19 | 15:54 | ZN1673:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 75 | 0.00148 | 2e-05 | N
05-03-19 | 16:33 | ZN9700:PA17 | URBAN | Other | Other | 1 | 140 | 9.5e-05 | 1e-06 | N
05-03-19 | 18:12 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 118 | 0.00296 | 2.5e-05 | N
05-03-19 | 21:45 | 217:33611 | URBAN | Asset Failure | LV | 14 | 75 | 0.000711 | 9e-06 | N
05-03-19 | 19:30 | ZN10995:PA6 | URBAN | Third Party | Vehicle impact | 1 | 174 | 0.000118 | 1e-06 | N
05-03-19 | 19:37 | 217:33611 | URBAN | Asset Failure | LV | 19 | 83 | 0.001063 | 1.3e-05 | N
05-03-19 | 20:46 | ZN965:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 54 | 0.00128 | 2.4e-05 | N
05-03-19 | 23:58 | ZN1673:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 542 | 0.002202 | 4e-06 | N
06-03-19 | 02:00 | ZN14892:PA9 | URBAN | Other | Other - Self Clearing Trigger | 704 | 117 | 0.055887 | 0.000477 | N
06-03-19 | 07:13 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 87 | 0.001091 | 1.3e-05 | N
06-03-19 | 09:05 | ZN10995:PA6 | URBAN | Asset Failure | HV | 1,725 | 96 | 0.11232 | 0.001168 | N
06-03-19 | 09:30 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 184 | 15 | 0.96774 | 0.064516 | N
06-03-19 | 09:31 | ZN9245:PA19 | URBAN | Other | Other | 1 | 119 | 8e-05 | 1e-06 | N
05-03-19 | 13:30 | 513:48059 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 60 | 0.000752 | 1.3e-05 | N
06-03-19 | 09:53 | 230:81434 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 32 | 2.2e-05 | 1e-06 | N
06-03-19 | 12:28 | ZN12620:PA10 | SHORT RURAL | Asset Failure | LV | 1 | 331 | 0.001385 | 4e-06 | N
06-03-19 | 12:56 | 216:10722 | SHORT RURAL | Other | Other | 1 | 37 | 0.000156 | 4e-06 | N
06-03-19 | 13:14 | ZN398:PA3 | URBAN | Other | Other - Self Clearing Trigger | 38 | 160 | 0.004127 | 2.6e-05 | N
06-03-19 | 13:23 | ZN1850:PA45 | URBAN | Other | Other - Self Clearing Trigger | 2 | 102 | 0.000138 | 1e-06 | N
06-03-19 | 13:28 | ZN1850:PA32 | URBAN | Other | Other | 363 | 111 | 0.027283 | 0.000246 | N
06-03-19 | 14:07 | ZN9700:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 62 | 0.002105 | 3.4e-05 | N
06-03-19 | 14:51 | ZN3154:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 339 | 0.008257 | 2.4e-05 | N
06-03-19 | 15:01 | ZN129:PA34 | URBAN | Weather |  | 441 | 162 | 0.048374 | 0.000299 | N
06-03-19 | 15:01 | ZN129:PA35 | URBAN | Weather |  | 1,315 | 162 | 0.14425 | 0.00089 | N
06-03-19 | 15:01 | ZN129:PA36 | URBAN | Weather |  | 1,233 | 162 | 0.13525 | 0.000835 | N
06-03-19 | 15:01 | ZN129:PA38 | URBAN | Weather |  | 1,200 | 162 | 0.13163 | 0.000813 | N
06-03-19 | 15:01 | ZN129:PA39 | URBAN | Weather |  | 950 | 162 | 0.10421 | 0.000643 | N
06-03-19 | 15:01 | ZN129:PA40 | URBAN | Weather |  | 1,158 | 162 | 0.12702 | 0.000784 | N
06-03-19 | 15:01 | ZN129:PA41 | URBAN | Weather |  | 1,079 | 162 | 0.11836 | 0.000731 | N
06-03-19 | 15:01 | ZN129:PA43 | URBAN | Weather |  | 105 | 163 | 0.011589 | 7.1e-05 | N
06-03-19 | 15:01 | ZN129:PA46 | URBAN | Weather |  | 1,516 | 163 | 0.16732 | 0.001026 | N
06-03-19 | 15:01 | ZN129:PA47 | URBAN | Weather |  | 888 | 163 | 0.098008 | 0.000601 | N
06-03-19 | 15:01 | ZN129:PA49 | URBAN | Weather |  | 153 | 163 | 0.016886 | 0.000104 | N
06-03-19 | 15:01 | ZN129:PA51 | URBAN | Weather |  | 209 | 163 | 0.023067 | 0.000142 | N
06-03-19 | 15:01 | ZN129:PA52 | URBAN | Weather |  | 1,060 | 163 | 0.11699 | 0.000718 | N
06-03-19 | 15:01 | ZN129:PA55 | URBAN | Weather |  | 176 | 160 | 0.019067 | 0.000119 | N
06-03-19 | 15:01 | ZN129:PA56 | URBAN | Weather |  | 1,394 | 160 | 0.15102 | 0.000944 | N
06-03-19 | 15:01 | ZN129:PA57 | URBAN | Weather |  | 1,582 | 160 | 0.17139 | 0.001071 | N
06-03-19 | 15:01 | ZN129:PA62 | URBAN | Weather |  | 356 | 160 | 0.038568 | 0.000241 | N
06-03-19 | 15:01 | ZN129:PA63 | URBAN | Weather |  | 708 | 160 | 0.076703 | 0.000479 | N
06-03-19 | 15:01 | ZN129:PA64 | URBAN | Weather |  | 1,786 | 160 | 0.19349 | 0.001209 | N
06-03-19 | 15:04 | 813:89065 | SHORT RURAL | Weather |  | 2 | 71 | 0.000594 | 8e-06 | N
06-03-19 | 15:12 | ZN15008:PA5 | URBAN | Other | Other | 1 | 113 | 7.6e-05 | 1e-06 | N
06-03-19 | 15:16 | ZN12580:PA8 | URBAN | Other | Other - Self Clearing Trigger | 79 | 34 | 0.001802 | 5.3e-05 | N
06-03-19 | 15:19 | 406:6028 | URBAN | Third Party | Other | 2 | 154 | 0.000208 | 1e-06 | N
06-03-19 | 15:35 | ZN36100:PA27 | URBAN | Other | Other - Arcing | 1 | 375 | 0.000254 | 1e-06 | N
06-03-19 | 15:34 | ZN14891:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 386 | 182 | 0.29353 | 0.001614 | N
06-03-19 | 15:54 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 281 | 141 | 0.16622 | 0.001175 | N
06-03-19 | 16:00 | ZN14891:PA20 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 29 | 0.000122 | 4e-06 | N
06-03-19 | 16:02 | ZN14891:PA20 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 156 | 0.000654 | 4e-06 | N
06-03-19 | 16:03 | 801:74118 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 359 | 0.000243 | 1e-06 | N
06-03-19 | 16:15 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 143 | 0.000597 | 4e-06 | N
06-03-19 | 16:30 | 814:82285 | SHORT RURAL | Asset Failure | LV | 1 | 331 | 0.001384 | 4e-06 | N
06-03-19 | 16:58 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 21 | 101 | 0.008905 | 8.8e-05 | N
06-03-19 | 17:12 | 814:82285 | SHORT RURAL | Asset Failure | LV | 1 | 107 | 0.000448 | 4e-06 | N
06-03-19 | 17:27 | ZN2635:PA41 | URBAN | Other | Other - Self Clearing Trigger | 6 | 193 | 0.000782 | 4e-06 | N
06-03-19 | 17:31 | ZN36300:PA13 | URBAN | Asset Failure | LV | 54 | 369 | 0.013492 | 3.7e-05 | N
06-03-19 | 17:31 | 258:80791 | URBAN | Other | Other - Self Clearing Trigger | 99 | 213 | 0.01428 | 6.7e-05 | N
06-03-19 | 17:34 | 813:89055 | SHORT RURAL | Asset Failure | HV | 7 | 641 | 0.018758 | 2.9e-05 | N
06-03-19 | 17:40 | ZN35500:PA31 | URBAN | Other | Other | 1 | 143 | 9.7e-05 | 1e-06 | N
06-03-19 | 17:58 | 205:12213 | SHORT RURAL | Asset Failure | Distribution substation | 79 | 92 | 0.030317 | 0.00033 | N
06-03-19 | 18:05 | 256:80641 | URBAN | Other | Other - Self Clearing Trigger | 181 | 40 | 0.004902 | 0.000123 | N
06-03-19 | 17:55 | 814:82283 | SHORT RURAL | Asset Failure | HV | 175 | 180 | 0.132 | 0.000732 | N
06-03-19 | 18:19 | 811:74234 | SHORT RURAL | Asset Failure | HV | 17 | 618 | 0.043899 | 7.1e-05 | N
06-03-19 | 18:28 | 257:82003 | URBAN | Asset Failure | HV | 20 | 402 | 0.005444 | 1.4e-05 | N
06-03-19 | 18:30 | ZN195:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 60 | 0.001745 | 2.9e-05 | N
06-03-19 | 18:44 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 211 | 0.008817 | 4.2e-05 | N
06-03-19 | 19:22 | 256:80650 | URBAN | Asset Failure | LV | 1 | 165 | 0.000112 | 1e-06 | N
06-03-19 | 19:51 | 813:89062 | SHORT RURAL | Other | Other - Arcing | 1 | 342 | 0.001429 | 4e-06 | N
06-03-19 | 20:03 | 813:89061 | LONG RURAL | Asset Failure | Distribution substation | 4 | 196 | 0.2751 | 0.001403 | N
06-03-19 | 20:07 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 133 | 0.000556 | 4e-06 | N
06-03-19 | 20:16 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 94 | 0.000786 | 8e-06 | N
06-03-19 | 20:23 | 813:89063 | SHORT RURAL | Other | Other - Arcing | 1 | 308 | 0.001288 | 4e-06 | N
06-03-19 | 20:26 | ZN9252:PA21 | URBAN | Other | Other - Arcing | 1 | 272 | 0.000184 | 1e-06 | N
06-03-19 | 21:22 | ZN35400:PA101 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 395 | 0.000268 | 1e-06 | N
06-03-19 | 21:27 | ZN9037:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 79 | 67 | 0.003594 | 5.3e-05 | N
06-03-19 | 23:27 | 813:89062 | SHORT RURAL | Other | Other | 1 | 182 | 0.000763 | 4e-06 | N
07-03-19 | 01:23 | ZN35555:PA3 | URBAN | Third Party | Vehicle impact | 1 | 609 | 0.000412 | 1e-06 | N
07-03-19 | 03:15 | ZN1648:PA10 | URBAN | Other | Other | 1 | 673 | 0.000455 | 1e-06 | N
07-03-19 | 08:39 | ZN847:PA15 | URBAN | Other | Other | 1 | 132 | 8.9e-05 | 1e-06 | N
07-03-19 | 09:22 | ZN180:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 667 | 0.000452 | 1e-06 | N
07-03-19 | 19:30 | ZN15001:PA6 | URBAN | Asset Failure | LV | 8 | 45 | 0.000244 | 5e-06 | N
07-03-19 | 16:47 | 258:80791 | URBAN | Other | Other | 1 | 213 | 0.000144 | 1e-06 | N
07-03-19 | 16:55 | 205:12213 | SHORT RURAL | Other | Other - Arcing | 1 | 125 | 0.000524 | 4e-06 | N
07-03-19 | 17:58 | ZN15009:PA7 | URBAN | Asset Failure | LV | 19 | 225 | 0.002896 | 1.3e-05 | N
07-03-19 | 18:30 | ZN3472:PA8 | URBAN | Other | Other | 1 | 84 | 5.7e-05 | 1e-06 | N
07-03-19 | 19:34 | ZN35600:PA7 | URBAN | Other | Other - Arcing | 1 | 119 | 8.1e-05 | 1e-06 | N
08-03-19 | 05:58 | 502:48002 | URBAN | Other | Other | 1 | 117 | 7.9e-05 | 1e-06 | N
08-03-19 | 07:12 | ZN262:PA25 | URBAN | Other | Other - Arcing | 1 | 303 | 0.000205 | 1e-06 | N
08-03-19 | 07:29 | ZN3425:PA28 | SHORT RURAL | Asset Failure | LV | 15 | 1,270 | 0.079617 | 6.3e-05 | N
08-03-19 | 09:38 | 233:82821 | SHORT RURAL | Other | Other | 1 | 292 | 0.001223 | 4e-06 | N
08-03-19 | 11:37 | ZN9118:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 62 | 383 | 0.016095 | 4.2e-05 | N
08-03-19 | 12:59 | ZN35555:PA13 | URBAN | Other | Other | 1 | 48 | 3.3e-05 | 1e-06 | N
08-03-19 | 13:02 | 205:12206 | URBAN | Other | Other | 1 | 233 | 0.000158 | 1e-06 | N
08-03-19 | 13:31 | 257:81987 | URBAN | Other | Other - Self Clearing Trigger | 1 | 162 | 0.00011 | 1e-06 | N
08-03-19 | 14:10 | ZN3154:PA5 | URBAN | Asset Failure | LV | 4 | 574 | 0.001555 | 3e-06 | N
08-03-19 | 18:00 | ZN14891:PA12 | SHORT RURAL | Third Party | Vehicle impact | 2 | 40 | 0.000334 | 8e-06 | N
08-03-19 | 18:40 | 270:83584 | URBAN | Asset Failure | Distribution substation | 2 | 230 | 0.000311 | 1e-06 | N
08-03-19 | 17:31 | ZN12620:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 81 | 0.000337 | 4e-06 | N
08-03-19 | 20:43 | ZN35600:PA3 | URBAN | Third Party | Vehicle impact | 9 | 236 | 0.00144 | 6e-06 | N
08-03-19 | 18:59 | 810:74054 | LONG RURAL | Asset Failure | HV | 1 | 236 | 0.082749 | 0.000351 | N
08-03-19 | 19:25 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 55 | 0.00023 | 4e-06 | N
08-03-19 | 21:33 | ZN35500:PA28 | URBAN | Asset Failure | LV | 1 | 1,147 | 0.000776 | 1e-06 | N
09-03-19 | 00:03 | ZN36100:PA12 | URBAN | Asset Failure | LV | 34 | 47 | 0.001073 | 2.3e-05 | N
09-03-19 | 04:14 | 217:33610 | URBAN | Animal | Animal impact | 1,950 | 50 | 0.066009 | 0.00132 | N
09-03-19 | 05:01 | ZN12570:PA39 | URBAN | Other | Other - Arcing | 1 | 329 | 0.000223 | 1e-06 | N
09-03-19 | 06:10 | 802:82215 | SHORT RURAL | Other | Other - Self Clearing Trigger | 36 | 111 | 0.016703 | 0.00015 | N
09-03-19 | 06:10 | 802:82220 | SHORT RURAL | Other | Other - Self Clearing Trigger | 63 | 111 | 0.029231 | 0.000263 | N
09-03-19 | 06:10 | 802:82225 | SHORT RURAL | Other | Other - Self Clearing Trigger | 106 | 111 | 0.049182 | 0.000443 | N
09-03-19 | 06:51 | ZN36100:PA12 | URBAN | Asset Failure | LV | 1 | 381 | 0.000258 | 1e-06 | N
09-03-19 | 07:41 | ZN36100:PA12 | URBAN | Asset Failure | LV | 1 | 332 | 0.000225 | 1e-06 | N
09-03-19 | 09:30 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 140 | 0.049088 | 0.000351 | N
09-03-19 | 11:05 | ZN14891:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 108 | 10 | 0.004514 | 0.000451 | N
09-03-19 | 11:59 | ZN5868:PA27 | URBAN | Other | Other - Self Clearing Trigger | 4 | 391 | 0.001059 | 3e-06 | N
09-03-19 | 12:04 | ZN690:PA26 | URBAN | Other | Other | 1 | 376 | 0.000255 | 1e-06 | N
09-03-19 | 12:08 | ZN1287:PA12 | URBAN | Other | Other - Arcing | 1 | 182 | 0.000123 | 1e-06 | N
09-03-19 | 12:19 | ZN9035:PA2 | URBAN | Other | Other | 59 | 199 | 0.007949 | 4e-05 | N
09-03-19 | 12:39 | ZN129:PA36 | URBAN | Other | Other - Arcing | 1 | 441 | 0.000298 | 1e-06 | N
09-03-19 | 13:43 | 801:74121 | LONG RURAL | Weather |  | 165 | 152 | 8.8026 | 0.057854 | N
09-03-19 | 14:09 | 801:74119 | URBAN | Asset Failure | LV | 1 | 1,017 | 0.000689 | 1e-06 | N
09-03-19 | 14:07 | 801:74118 | URBAN | Vegetation | Vegetation Blow/Fall In | 898 | 68 | 0.041467 | 0.000608 | N
09-03-19 | 14:12 | 801:74122 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 338 | 0.008467 | 2.5e-05 | N
09-03-19 | 14:34 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 56 | 0.000468 | 8e-06 | N
09-03-19 | 15:12 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 1,423 | 0.4988 | 0.000351 | N
09-03-19 | 15:26 | ZN12610:PA10 | URBAN | Other | Other - Arcing | 1 | 364 | 0.000246 | 1e-06 | N
09-03-19 | 15:37 | 526:34639 | SHORT RURAL | Asset Failure | HV | 16 | 213 | 0.014245 | 6.7e-05 | N
09-03-19 | 15:39 | 814:82291 | SHORT RURAL | Asset Failure | HV | 463 | 80 | 0.15387 | 0.001935 | N
09-03-19 | 15:42 | 508:82578 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 427 | 0.001784 | 4e-06 | N
09-03-19 | 15:44 | ZN4545:PA4 | URBAN | Other | Other - Arcing | 1 | 85 | 5.8e-05 | 1e-06 | N
09-03-19 | 15:45 | 511:29880 | URBAN | Asset Failure | LV | 1 | 224 | 0.000152 | 1e-06 | N
09-03-19 | 15:46 | ZN180:PA19 | URBAN | Other | Other - Arcing | 1 | 258 | 0.000175 | 1e-06 | N
09-03-19 | 15:29 | 811:74234 | SHORT RURAL | Asset Failure | HV | 108 | 506 | 0.22833 | 0.000451 | N
09-03-19 | 16:12 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 343 | 0.002867 | 8e-06 | N
09-03-19 | 16:14 | ZN1788:PA20 | URBAN | Asset Failure | LV | 1 | 488 | 0.00033 | 1e-06 | N
09-03-19 | 16:22 | 526:34637 | SHORT RURAL | Other | Other - Self Clearing Trigger | 19 | 188 | 0.014931 | 7.9e-05 | N
09-03-19 | 16:21 | 812:19066 | SHORT RURAL | Other | Other - Self Clearing Trigger | 856 | 237 | 0.84741 | 0.003578 | N
09-03-19 | 17:00 | 801:74121 | LONG RURAL | Asset Failure | HV | 31 | 360 | 3.913 | 0.01087 | N
09-03-19 | 16:29 | 515:35197 | LONG RURAL | Asset Failure | HV | 33 | 455 | 5.2598 | 0.011571 | N
09-03-19 | 16:43 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 327 | 0.002734 | 8e-06 | N
09-03-19 | 17:00 | ZN342:PA18 | URBAN | Asset Failure | LV | 52 | 1,800 | 0.063368 | 3.5e-05 | N
09-03-19 | 17:04 | 526:34639 | SHORT RURAL | Asset Failure | HV | 37 | 100 | 0.015466 | 0.000155 | N
09-03-19 | 17:09 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 326 | 0.11431 | 0.000351 | N
09-03-19 | 17:18 | 524:33580 | SHORT RURAL | Other | Other - Arcing | 1 | 1,321 | 0.005521 | 4e-06 | N
09-03-19 | 17:21 | 813:89055 | SHORT RURAL | Asset Failure | HV | 1 | 404 | 0.001689 | 4e-06 | N
09-03-19 | 17:21 | ZN14891:PA19 | URBAN | Other | Other - Arcing | 1 | 158 | 0.000107 | 1e-06 | N
09-03-19 | 17:31 | ZN9118:PA26 | URBAN | Other | Other - Arcing | 1 | 283 | 0.000192 | 1e-06 | N
09-03-19 | 17:34 | 526:34640 | SHORT RURAL | Asset Failure | HV | 3 | 363 | 0.004552 | 1.3e-05 | N
09-03-19 | 17:34 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 406 | 0.001697 | 4e-06 | N
09-03-19 | 17:38 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 65 | 12 | 0.003238 | 0.000272 | N
09-03-19 | 17:53 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 52 | 0.000217 | 4e-06 | N
09-03-19 | 18:29 | 806:82667 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 1,186 | 0.004957 | 4e-06 | N
09-03-19 | 18:38 | 238:34148 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 112 | 0.000467 | 4e-06 | N
09-03-19 | 18:41 | 528:83011 | SHORT RURAL | Weather |  | 1 | 84 | 0.000349 | 4e-06 | N
09-03-19 | 19:07 | ZN14891:PA8 | SHORT RURAL | Other | Other - Arcing | 1 | 308 | 0.001287 | 4e-06 | N
09-03-19 | 19:03 | 813:89061 | LONG RURAL | Asset Failure | HV | 1 | 1,152 | 0.40393 | 0.000351 | N
09-03-19 | 19:50 | ZN2310:PA15 | URBAN | Other | Other - Arcing | 1 | 849 | 0.000575 | 1e-06 | N
09-03-19 | 20:12 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 43 | 0.000179 | 4e-06 | N
09-03-19 | 21:00 | 264:81244 | SHORT RURAL | Asset Failure | LV | 22 | 25 | 0.002299 | 9.2e-05 | N
09-03-19 | 21:02 | 813:89061 | LONG RURAL | Asset Failure | HV | 19 | 1,096 | 7.3008 | 0.006662 | N
09-03-19 | 21:42 | 522:83123 | SHORT RURAL | Asset Failure | Distribution substation | 62 | 153 | 0.039604 | 0.000259 | N
09-03-19 | 22:59 | 807:74184 | SHORT RURAL | Third Party | Other | 1 | 116 | 0.000486 | 4e-06 | N
09-03-19 | 23:20 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 50 | 0.000208 | 4e-06 | N
10-03-19 | 01:31 | 502:48010 | SHORT RURAL | Other | Other | 39 | 149 | 0.02429 | 0.000163 | N
10-03-19 | 01:53 | ZN4545:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,363 | 80 | 0.073821 | 0.000923 | N
10-03-19 | 02:29 | 221:11900 | URBAN | Animal | Animal impact | 93 | 76 | 0.004773 | 6.3e-05 | N
10-03-19 | 03:21 | ZN3672:PA35 | SHORT RURAL | Vegetation | Vegetation Grow In | 1 | 836 | 0.003495 | 4e-06 | N
10-03-19 | 03:50 | ZN12690:PA6 | URBAN | Other | Other - Self Clearing Trigger | 967 | 65 | 0.042554 | 0.000655 | N
10-03-19 | 04:04 | 214:8667 | URBAN | Other | Other - Arcing | 1 | 267 | 0.000181 | 1e-06 | N
10-03-19 | 11:00 | 509:33395 | LONG RURAL | Asset Failure | LV | 4 | 40 | 0.056101 | 0.001403 | N
10-03-19 | 07:15 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 125 | 0.000523 | 4e-06 | N
10-03-19 | 08:18 | ZN2310:PA15 | URBAN | Other | Other - Arcing | 1 | 310 | 0.00021 | 1e-06 | N
10-03-19 | 08:23 | 242:81532 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 477 | 0.013957 | 2.9e-05 | N
09-03-19 | 15:29 | 811:74234 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 1,621 | 0.006776 | 4e-06 | N
10-03-19 | 08:37 | ZN9700:PA19 | URBAN | Other | Other | 1 | 152 | 0.000103 | 1e-06 | N
10-03-19 | 08:42 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 163 | 0.000681 | 4e-06 | N
10-03-19 | 09:18 | ZN10994:PA9 | URBAN | Asset Failure | LV | 103 | 432 | 0.030115 | 7e-05 | N
10-03-19 | 10:32 | 515:35192 | SHORT RURAL | Asset Failure | HV | 323 | 12 | 0.016871 | 0.00135 | N
10-03-19 | 11:43 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 262 | 0.001095 | 4e-06 | N
10-03-19 | 11:57 | 524:33580 | SHORT RURAL | Other | Other - Arcing | 1 | 201 | 0.000842 | 4e-06 | N
10-03-19 | 13:30 | ZN14144:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 60 | 175 | 0.007109 | 4.1e-05 | N
10-03-19 | 13:40 | 264:81236 | URBAN | Other | Other | 1 | 69 | 4.7e-05 | 1e-06 | N
10-03-19 | 14:54 | 258:80785 | URBAN | Other | Other | 1 | 65 | 4.4e-05 | 1e-06 | N
10-03-19 | 15:17 | ZN12600:PA2 | SHORT RURAL | Asset Failure | HV | 17 | 63 | 0.004477 | 7.1e-05 | N
10-03-19 | 16:20 | 814:82289 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 152 | 0.000634 | 4e-06 | N
10-03-19 | 18:42 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 48 | 0.016743 | 0.000351 | N
10-03-19 | 19:05 | 224:80346 | URBAN | Other | Other - Arcing | 1 | 475 | 0.000321 | 1e-06 | N
10-03-19 | 19:22 | 258:80791 | URBAN | Asset Failure | HV | 99 | 39 | 0.002614 | 6.7e-05 | N
10-03-19 | 21:12 | 261:81879 | URBAN | Other | Other - Arcing | 1 | 468 | 0.000317 | 1e-06 | N
10-03-19 | 21:20 | ZN1648:PA16 | URBAN | Other | Other - Arcing | 1 | 931 | 0.00063 | 1e-06 | N
10-03-19 | 22:16 | ZN12610:PA16 | URBAN | Other | Other - Arcing | 1 | 1,153 | 0.000781 | 1e-06 | N
11-03-19 | 03:21 | 522:83129 | URBAN | Third Party | Fire | 1 | 100 | 6.7e-05 | 1e-06 | N
11-03-19 | 06:59 | ZN80:PA31 | URBAN | Asset Failure | LV | 1 | 470 | 0.000318 | 1e-06 | N
11-03-19 | 10:00 | 812:19072 | SHORT RURAL | Asset Failure | HV | 6 | 400 | 0.010032 | 2.5e-05 | N
11-03-19 | 07:32 | ZN15013:PA6 | SHORT RURAL | Other | Other - Arcing | 1 | 362 | 0.001513 | 4e-06 | N
11-03-19 | 07:50 | 508:82574 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 85 | 0.000355 | 4e-06 | N
11-03-19 | 08:13 | 813:89061 | LONG RURAL | Asset Failure | HV | 1 | 117 | 0.041024 | 0.000351 | N
11-03-19 | 09:11 | 526:34636 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 139 | 0.001743 | 1.3e-05 | N
08-03-19 | 11:00 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 60 | 0.000753 | 1.3e-05 | N
11-03-19 | 10:10 | 257:81997 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 220 | 0.000149 | 1e-06 | N
11-03-19 | 10:41 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 109 | 0.000456 | 4e-06 | N
11-03-19 | 11:48 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 182 | 0.063815 | 0.000351 | N
11-03-19 | 11:50 | ZN9035:PA4 | URBAN | Vegetation | Vegetation Grow In | 2 | 194 | 0.000263 | 1e-06 | N
11-03-19 | 13:16 | ZN36800:PA49 | URBAN | Asset Failure | LV | 78 | 88 | 0.00465 | 5.3e-05 | N
11-03-19 | 14:31 | ZN12620:PA10 | SHORT RURAL | Other | Other | 1 | 235 | 0.000983 | 4e-06 | N
06-03-19 | 21:20 | ZN36300:PA13 | URBAN | Asset Failure | Distribution substation | 201 | 140 | 0.019054 | 0.000136 | N
11-03-19 | 15:26 | ZN129:PA38 | URBAN | Asset Failure | HV | 1,200 | 69 | 0.056302 | 0.000812 | N
11-03-19 | 15:26 | ZN129:PA46 | URBAN | Asset Failure | HV | 85 | 46 | 0.00265 | 5.8e-05 | N
11-03-19 | 15:38 | ZN2310:PA25 | URBAN | Third Party | Vehicle impact | 47 | 202 | 0.006428 | 3.2e-05 | N
11-03-19 | 16:38 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 142 | 0.04979 | 0.000351 | N
11-03-19 | 20:19 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 19 | 147 | 0.97931 | 0.006662 | N
11-03-19 | 22:58 | ZN180:PA21 | URBAN | Asset Failure | LV | 61 | 91 | 0.003759 | 4.1e-05 | N
12-03-19 | 05:34 | ZN2635:PA51 | URBAN | Third Party | Other | 3 | 376 | 0.000764 | 2e-06 | N
12-03-19 | 06:34 | ZN1285:PA27 | URBAN | Other | Other - Arcing | 1 | 141 | 9.5e-05 | 1e-06 | N
12-03-19 | 06:55 | ZN10994:PA13 | URBAN | Third Party | Vehicle impact | 20 | 120 | 0.001624 | 1.4e-05 | N
12-03-19 | 08:39 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 51 | 0.000213 | 4e-06 | N
12-03-19 | 08:50 | 528:83011 | SHORT RURAL | Asset Failure | LV | 1 | 300 | 0.001252 | 4e-06 | N
12-03-19 | 09:22 | ZN2835:PA10 | URBAN | Other | Other | 1 | 15 | 1e-05 | 1e-06 | N
12-03-19 | 09:38 | 810:74054 | LONG RURAL | Asset Failure | LV | 1 | 262 | 0.091865 | 0.000351 | N
12-03-19 | 11:09 | ZN690:PA6 | URBAN | Asset Failure | LV | 1 | 257 | 0.000174 | 1e-06 | N
12-03-19 | 11:51 | 256:80641 | URBAN | Other | Other - Arcing | 1 | 1,179 | 0.000798 | 1e-06 | N
12-03-19 | 12:53 | ZN15001:PA18 | URBAN | Other | Other - Arcing | 1 | 432 | 0.000293 | 1e-06 | N
10-03-19 | 00:30 | 813:89055 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 35 | 0.000293 | 8e-06 | N
10-03-19 | 19:52 | 258:80791 | URBAN | Asset Failure | HV | 734 | 9 | 0.004472 | 0.000497 | N
12-03-19 | 15:14 | ZN129:PA51 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 96 | 0.00234 | 2.4e-05 | N
12-03-19 | 15:17 | ZN15006:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 366 | 0.000248 | 1e-06 | N
12-03-19 | 16:50 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 60 | 0.000251 | 4e-06 | N
12-03-19 | 09:16 | ZN10994:PA13 | URBAN | Asset Failure | LV | 5 | 737 | 0.002495 | 3e-06 | N
12-03-19 | 18:59 | ZN2602:PA15 | URBAN | Asset Failure | LV | 82 | 67 | 0.00372 | 5.6e-05 | N
12-03-19 | 18:59 | ZN2602:PA4 | URBAN | Asset Failure | LV | 49 | 254 | 0.008431 | 3.3e-05 | N
12-03-19 | 19:05 | ZN1610:PA17 | URBAN | Asset Failure | HV | 46 | 105 | 0.00327 | 3.1e-05 | N
12-03-19 | 19:05 | ZN1610:PA19 | URBAN | Asset Failure | HV | 1,842 | 99 | 0.12383 | 0.001247 | N
12-03-19 | 20:54 | ZN1068:PA17 | URBAN | Other | Other - Arcing | 1 | 267 | 0.00018 | 1e-06 | N
12-03-19 | 21:12 | ZN10994:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 367 | 0.000249 | 1e-06 | N
12-03-19 | 21:22 | ZN1673:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 307 | 0.000208 | 1e-06 | N
13-03-19 | 02:21 | ZN1193:PA15 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 27 | 18 | 0.002033 | 0.000113 | N
12-03-19 | 22:45 | ZN10999:PA17 | URBAN | Third Party | Vehicle impact | 1 | 615 | 0.000416 | 1e-06 | N
13-03-19 | 05:36 | ZN36300:PA19 | URBAN | Other | Other - Self Clearing Trigger | 1,382 | 71 | 0.066696 | 0.000936 | N
11-03-19 | 11:32 | 801:74121 | LONG RURAL | Asset Failure | Distribution substation | 1 | 358 | 0.12553 | 0.000351 | N
13-03-19 | 07:51 | ZN14891:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 509 | 0.012766 | 2.5e-05 | N
13-03-19 | 07:52 | 222:33600 | URBAN | Other | Other - Arcing | 1 | 82 | 5.6e-05 | 1e-06 | N
13-03-19 | 13:26 | ZN15002:PA6 | URBAN | Other | Other - Arcing | 1 | 94 | 6.4e-05 | 1e-06 | N
13-03-19 | 08:12 | ZN36300:PA19 | URBAN | Other | Other - Arcing | 1 | 537 | 0.000363 | 1e-06 | N
13-03-19 | 12:03 | ZN12640:PA13 | SHORT RURAL | Other | Other - Arcing | 1 | 641 | 0.00268 | 4e-06 | N
13-03-19 | 13:17 | 221:11899 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 40 | 0.000169 | 4e-06 | N
13-03-19 | 13:45 | ZN384:PA63 | SHORT RURAL | Asset Failure | HV | 352 | 64 | 0.094168 | 0.001471 | N
13-03-19 | 14:12 | 522:83124 | URBAN | Asset Failure | LV | 1 | 446 | 0.000302 | 1e-06 | N
13-03-19 | 14:30 | ZN9035:PA8 | URBAN | Asset Failure | HV | 110 | 39 | 0.002904 | 7.4e-05 | N
13-03-19 | 14:38 | ZN14891:PA8 | SHORT RURAL | Other | Other | 1 | 303 | 0.001265 | 4e-06 | N
13-03-19 | 15:02 | ZN2835:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 29 | 8 | 0.000157 | 2e-05 | N
13-03-19 | 15:32 | 210:83473 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 75 | 5.1e-05 | 1e-06 | N
13-03-19 | 16:20 | ZN14891:PA8 | SHORT RURAL | Asset Failure | HV | 17 | 170 | 0.01208 | 7.1e-05 | N
13-03-19 | 16:40 | 528:83020 | SHORT RURAL | Third Party | Other | 1 | 59 | 0.000248 | 4e-06 | N
13-03-19 | 17:05 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 18 | 72 | 0.005394 | 7.5e-05 | N
13-03-19 | 18:37 | ZN12650:PA1 | SHORT RURAL | Asset Failure | HV | 2 | 148 | 0.001237 | 8e-06 | N
13-03-19 | 19:37 | ZN2310:PA15 | URBAN | Other | Other | 1 | 725 | 0.000491 | 1e-06 | N
13-03-19 | 21:29 | ZN36300:PA11 | URBAN | Other | Other - Arcing | 1 | 750 | 0.000508 | 1e-06 | N
14-03-19 | 00:12 | ZN4545:PA31 | URBAN | Other | Other - Arcing | 1 | 618 | 0.000418 | 1e-06 | Y
15-03-19 | 13:35 | ZN195:PA25 | URBAN | Other | Other - Arcing | 1 | 505 | 0.000342 | 1e-06 | N
14-03-19 | 00:39 | ZN2635:PA31 | URBAN | Other | Other - Arcing | 1 | 770 | 0.000522 | 1e-06 | Y
14-03-19 | 02:24 | ZN12610:PA11 | URBAN | Animal | Animal impact | 117 | 66 | 0.005228 | 7.9e-05 | Y
14-03-19 | 05:38 | ZN2835:PA10 | URBAN | Other | Other - Arcing | 1 | 292 | 0.000198 | 1e-06 | Y
14-03-19 | 11:55 | 240:34843 | URBAN | Other | Other | 1 | 155 | 0.000105 | 1e-06 | Y
14-03-19 | 12:08 | 522:83132 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 291 | 0.001218 | 4e-06 | Y
14-03-19 | 12:51 | ZN15005:PA10 | URBAN | Other | Other - Self Clearing Trigger | 11 | 189 | 0.001408 | 7e-06 | Y
14-03-19 | 13:08 | ZN35800:PA22 | URBAN | Other | Other - Self Clearing Trigger | 35 | 112 | 0.002644 | 2.4e-05 | Y
14-03-19 | 15:19 | 512:83743 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 74 | 0.000619 | 8e-06 | Y
14-03-19 | 15:34 | ZN1290:PA11 | URBAN | Other | Other | 1 | 466 | 0.000315 | 1e-06 | Y
14-03-19 | 16:40 | 243:80078 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 140 | 9.5e-05 | 1e-06 | Y
14-03-19 | 17:15 | ZN180:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 30 | 0.000711 | 2.4e-05 | Y
14-03-19 | 17:30 | ZN9700:PA15 | URBAN | Third Party | Other | 1 | 280 | 0.00019 | 1e-06 | Y
14-03-19 | 18:26 | ZN10999:PA38 | URBAN | Other | Other - Self Clearing Trigger | 86 | 203 | 0.011845 | 5.8e-05 | Y
14-03-19 | 18:31 | ZN4545:PA27 | URBAN | Other | Other - Arcing | 1 | 259 | 0.000175 | 1e-06 | Y
14-03-19 | 18:57 | ZN965:PA42 | URBAN | Third Party | Other | 1 | 798 | 0.00054 | 1e-06 | Y
14-03-19 | 19:01 | ZN965:PA33 | URBAN | Other | Other | 27 | 171 | 0.003122 | 1.8e-05 | Y
14-03-19 | 19:21 | ZN965:PA47 | URBAN | Weather |  | 90 | 183 | 0.011166 | 6.1e-05 | Y
14-03-19 | 19:38 | ZN965:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 617 | 82 | 0.034254 | 0.000418 | Y
14-03-19 | 19:38 | ZN965:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 82 | 5.6e-05 | 1e-06 | Y
14-03-19 | 19:55 | ZN847:PA15 | URBAN | Weather |  | 1,346 | 136 | 0.12436 | 0.000911 | Y
14-03-19 | 23:57 | ZN1673:PA13 | URBAN | Weather |  | 34 | 635 | 0.014625 | 2.3e-05 | Y
14-03-19 | 20:27 | ZN15005:PA12 | URBAN | Third Party | Other | 1 | 450 | 0.000305 | 1e-06 | Y
14-03-19 | 20:27 | 522:83132 | SHORT RURAL | Asset Failure | LV | 1 | 153 | 0.00064 | 4e-06 | Y
14-03-19 | 20:29 | ZN15002:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 428 | 0.00029 | 1e-06 | Y
14-03-19 | 20:29 | ZN15002:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,059 | 426 | 0.30567 | 0.000717 | Y
14-03-19 | 20:55 | ZN9118:PA26 | URBAN | Third Party | Other | 1 | 232 | 0.000157 | 1e-06 | Y
14-03-19 | 20:48 | ZN80:PA31 | URBAN | Weather |  | 526 | 278 | 0.099003 | 0.000356 | Y
14-03-19 | 21:06 | ZN15008:PA1 | URBAN | Weather |  | 1,943 | 188 | 0.24731 | 0.001315 | Y
14-03-19 | 21:06 | ZN15008:PA10 | URBAN | Weather |  | 1,857 | 189 | 0.23762 | 0.001257 | Y
14-03-19 | 21:06 | ZN15008:PA5 | URBAN | Weather |  | 1,285 | 189 | 0.16443 | 0.00087 | Y
14-03-19 | 21:06 | ZN15008:PA6 | URBAN | Weather |  | 1,365 | 188 | 0.17374 | 0.000924 | Y
14-03-19 | 21:06 | ZN15008:PA7 | URBAN | Weather |  | 2,535 | 188 | 0.32267 | 0.001716 | Y
14-03-19 | 21:06 | ZN15008:PA9 | URBAN | Weather |  | 2,289 | 189 | 0.2929 | 0.00155 | Y
14-03-19 | 21:06 | ZN15009:PA1 | URBAN | Weather |  | 2,130 | 182 | 0.26246 | 0.001442 | Y
14-03-19 | 21:06 | ZN15009:PA11 | URBAN | Weather |  | 2,304 | 183 | 0.28546 | 0.00156 | Y
14-03-19 | 21:06 | ZN15009:PA12 | URBAN | Weather |  | 82 | 183 | 0.01016 | 5.6e-05 | Y
14-03-19 | 21:06 | ZN15009:PA3 | URBAN | Weather |  | 806 | 182 | 0.099317 | 0.000546 | Y
14-03-19 | 21:06 | ZN15009:PA5 | URBAN | Weather |  | 1,481 | 183 | 0.18349 | 0.001003 | Y
14-03-19 | 21:06 | ZN15009:PA7 | URBAN | Weather |  | 1,564 | 183 | 0.19378 | 0.001059 | Y
14-03-19 | 21:06 | ZN15009:PA9 | URBAN | Weather |  | 643 | 183 | 0.079667 | 0.000435 | Y
14-03-19 | 21:06 | ZN15015:PA15 | SHORT RURAL | Weather |  | 634 | 264 | 0.69969 | 0.00265 | Y
14-03-19 | 21:06 | ZN15015:PA5 | URBAN | Weather |  | 1,629 | 264 | 0.29117 | 0.001103 | Y
14-03-19 | 21:06 | ZN15015:PA9 | URBAN | Weather |  | 1 | 271 | 0.000183 | 1e-06 | Y
14-03-19 | 21:31 | ZN15013:PA10 | SHORT RURAL | Asset Failure | HV | 96 | 800 | 0.32099 | 0.000401 | Y
14-03-19 | 21:51 | ZN262:PA30 | URBAN | Third Party | Vehicle impact | 49 | 128 | 0.004241 | 3.3e-05 | Y
14-03-19 | 21:43 | ZN180:PA7 | URBAN | Other | Other - Self Clearing Trigger | 90 | 258 | 0.015691 | 6.1e-05 | Y
14-03-19 | 21:47 | ZN398:PA30 | URBAN | Other | Other - Arcing | 1 | 122 | 8.3e-05 | 1e-06 | Y
14-03-19 | 21:52 | ZN15002:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 168 | 0.000113 | 1e-06 | Y
14-03-19 | 22:00 | ZN15006:PA16 | URBAN | Other | Other - Arcing | 1 | 570 | 0.000386 | 1e-06 | Y
14-03-19 | 22:39 | ZN15014:PA5 | URBAN | Weather |  | 1 | 185 | 0.000125 | 1e-06 | Y
14-03-19 | 23:42 | ZN12610:PA20 | SHORT RURAL | Asset Failure | HV | 907 | 194 | 0.73685 | 0.003792 | Y
14-03-19 | 23:55 | ZN12650:PA1 | SHORT RURAL | Weather |  | 6 | 595 | 0.014924 | 2.5e-05 | Y
15-03-19 | 00:06 | ZN14891:PA8 | SHORT RURAL | Weather |  | 64 | 683 | 0.18279 | 0.000268 | N
15-03-19 | 00:20 | ZN10999:PA7 | URBAN | Animal | Animal impact | 259 | 147 | 0.025778 | 0.000175 | N
15-03-19 | 00:31 | 507:80932 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 164 | 0.000684 | 4e-06 | N
15-03-19 | 00:06 | ZN14891:PA8 | SHORT RURAL | Weather |  | 43 | 654 | 0.11756 | 0.00018 | N
15-03-19 | 01:57 | ZN14891:PA5 | SHORT RURAL | Asset Failure | HV | 1,429 | 82 | 0.49267 | 0.005974 | N
15-03-19 | 02:45 | ZN1673:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 24 | 75 | 0.001219 | 1.6e-05 | N
15-03-19 | 03:30 | ZN2635:PA65 | URBAN | Asset Failure | Distribution substation | 2 | 2,089 | 0.002829 | 1e-06 | N
15-03-19 | 03:38 | ZN15004:PA5 | URBAN | Other | Other - Arcing | 1 | 352 | 0.000238 | 1e-06 | N
15-03-19 | 05:27 | ZN15002:PA8 | URBAN | Asset Failure | HV | 223 | 333 | 0.050277 | 0.000151 | N
15-03-19 | 06:18 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 171 | 0.059975 | 0.000351 | N
15-03-19 | 06:20 | 261:81879 | URBAN | Other | Other - Arcing | 1 | 114 | 7.7e-05 | 1e-06 | N
15-03-19 | 07:20 | ZN15014:PA14 | URBAN | Other | Other - Self Clearing Trigger | 15 | 285 | 0.002891 | 1e-05 | N
16-03-19 | 12:40 | ZN180:PA7 | URBAN | Asset Failure | LV | 90 | 280 | 0.017058 | 6.1e-05 | N
15-03-19 | 07:42 | 811:74234 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 388 | 0.001621 | 4e-06 | N
15-03-19 | 08:03 | ZN12570:PA33 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 186 | 0.001559 | 8e-06 | N
15-03-19 | 10:19 | ZN10994:PA13 | URBAN | Asset Failure | LV | 1 | 689 | 0.000467 | 1e-06 | N
15-03-19 | 10:48 | 224:80337 | URBAN | Other | Other | 1 | 137 | 9.3e-05 | 1e-06 | N
15-03-19 | 13:00 | ZN14143:PA17 | SHORT RURAL | Weather |  | 10 | 30 | 0.001254 | 4.2e-05 | N
15-03-19 | 14:48 | ZN35555:PA2 | URBAN | Other | Other | 1 | 606 | 0.00041 | 1e-06 | N
15-03-19 | 15:08 | ZN2196:PA25 | URBAN | Third Party | Vehicle impact | 1 | 401 | 0.000271 | 1e-06 | N
15-03-19 | 15:39 | 265:81649 | URBAN | Asset Failure | LV | 1 | 343 | 0.000232 | 1e-06 | N
15-03-19 | 15:40 | 256:80632 | URBAN | Asset Failure | LV | 1 | 260 | 0.000176 | 1e-06 | N
15-03-19 | 18:55 | 528:83020 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 85 | 183 | 0.065027 | 0.000355 | N
15-03-19 | 15:56 | 511:29878 | SHORT RURAL | Asset Failure | HV | 6 | 374 | 0.009381 | 2.5e-05 | N
15-03-19 | 16:27 | 261:81886 | URBAN | Asset Failure | HV | 32 | 153 | 0.003315 | 2.2e-05 | N
15-03-19 | 16:25 | ZN15012:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 265 | 0.000718 | 3e-06 | N
15-03-19 | 16:35 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 356 | 55 | 0.081853 | 0.001488 | N
15-03-19 | 16:55 | ZN15002:PA4 | SHORT RURAL | Other | Other | 1 | 575 | 0.002404 | 4e-06 | N
15-03-19 | 17:43 | ZN10991:PA1 | URBAN | Asset Failure | LV | 1 | 245 | 0.000166 | 1e-06 | N
15-03-19 | 18:11 | ZN3154:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 414 | 0.00028 | 1e-06 | N
16-03-19 | 00:21 | ZN195:PA30 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 741 | 46 | 0.14242 | 0.003096 | N
15-03-19 | 19:13 | ZN5868:PA17 | URBAN | Asset Failure | HV | 107 | 74 | 0.005358 | 7.2e-05 | N
15-03-19 | 19:19 | ZN2196:PA25 | URBAN | Third Party | Other | 1 | 151 | 0.000102 | 1e-06 | N
15-03-19 | 22:02 | 204:82691 | URBAN | Other | Other | 1 | 1,144 | 0.000775 | 1e-06 | N
15-03-19 | 22:41 | ZN1285:PA27 | URBAN | Other | Other - Arcing | 1 | 1,149 | 0.000778 | 1e-06 | N
15-03-19 | 22:46 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 10 | 158 | 0.006618 | 4.2e-05 | N
15-03-19 | 22:54 | ZN12610:PA13 | SHORT RURAL | Other | Other - Arcing | 1 | 1,115 | 0.004663 | 4e-06 | N
16-03-19 | 00:17 | ZN14144:PA7 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 84 | 63 | 0.022111 | 0.000351 | N
16-03-19 | 01:34 | ZN187:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 86 | 434 | 0.025252 | 5.8e-05 | N
16-03-19 | 02:41 | ZN3425:PA28 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 949 | 0.003965 | 4e-06 | N
16-03-19 | 05:19 | 222:33602 | URBAN | Other | Other - Arcing | 1 | 294 | 0.000199 | 1e-06 | N
16-03-19 | 05:35 | ZN12610:PA11 | URBAN | Asset Failure | Distribution substation | 84 | 300 | 0.017044 | 5.7e-05 | N
16-03-19 | 05:58 | ZN2466:PA21 | URBAN | Asset Failure | HV | 7 | 185 | 0.000876 | 5e-06 | N
16-03-19 | 06:53 | ZN12630:PA13 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 290 | 0.010905 | 3.8e-05 | N
16-03-19 | 07:11 | ZN12580:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 648 | 0.000439 | 1e-06 | N
16-03-19 | 07:12 | ZN4990:PA55 56GHJ | CBD | Other | Other - Self Clearing Trigger | 4 | 133 | 0.017412 | 0.000131 | N
16-03-19 | 07:24 | ZN1788:PA48 | URBAN | Third Party | Other | 1 | 905 | 0.000612 | 1e-06 | N
16-03-19 | 07:45 | 232:11457 | SHORT RURAL | Other | Other | 1 | 219 | 0.000917 | 4e-06 | N
16-03-19 | 07:57 | 206:34441 | URBAN | Other | Other | 8 | 240 | 0.001302 | 5e-06 | N
16-03-19 | 08:03 | 232:11457 | SHORT RURAL | Other | Other | 1 | 202 | 0.000844 | 4e-06 | N
16-03-19 | 08:04 | ZN35800:PA13 | URBAN | Other | Other | 1 | 586 | 0.000397 | 1e-06 | N
16-03-19 | 09:21 | ZN15009:PA5 | URBAN | Other | Other - Self Clearing Trigger | 24 | 233 | 0.00379 | 1.6e-05 | N
16-03-19 | 09:42 | 222:33600 | URBAN | Other | Other - Arcing | 1 | 308 | 0.000209 | 1e-06 | N
16-03-19 | 10:02 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 298 | 0.000201 | 1e-06 | N
16-03-19 | 12:00 | 204:82691 | URBAN | Other | Other | 1 | 73 | 4.9e-05 | 1e-06 | N
16-03-19 | 12:43 | ZN3155:PA34 | URBAN | Animal | Animal impact | 44 | 227 | 0.006761 | 3e-05 | N
16-03-19 | 14:14 | ZN9037:PA7 | URBAN | Third Party | Vehicle impact | 664 | 59 | 0.026519 | 0.000449 | N
16-03-19 | 14:14 | ZN9037:PA9 | URBAN | Third Party | Vehicle impact | 39 | 211 | 0.00557 | 2.6e-05 | N
16-03-19 | 14:21 | ZN36100:PA21 | URBAN | Asset Failure | LV | 1 | 206 | 0.000139 | 1e-06 | N
16-03-19 | 14:29 | ZN690:PA4 | URBAN | Other | Other | 1 | 646 | 0.000437 | 1e-06 | N
16-03-19 | 18:21 | ZN10998:PA32 | SHORT RURAL | Weather |  | 1 | 415 | 0.001733 | 4e-06 | N
16-03-19 | 18:52 | ZN398:PA24 | URBAN | Other | Other - Arcing | 1 | 18 | 1.2e-05 | 1e-06 | N
16-03-19 | 20:10 | 502:48010 | SHORT RURAL | Asset Failure | HV | 51 | 168 | 0.035798 | 0.000213 | N
16-03-19 | 22:00 | ZN9118:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 342 | 0.000232 | 1e-06 | N
16-03-19 | 22:59 | ZN1193:PA26 | URBAN | Asset Failure | LV | 1 | 1,650 | 0.001117 | 1e-06 | N
17-03-19 | 02:51 | ZN15013:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 122 | 89 | 0.045367 | 0.00051 | N
17-03-19 | 03:39 | 807:74180 | SHORT RURAL | Other | Other - Arcing | 1 | 207 | 0.000864 | 4e-06 | N
17-03-19 | 03:47 | 229:34995 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 329 | 0.001374 | 4e-06 | N
17-03-19 | 06:11 | ZN12620:PA8 | SHORT RURAL | Third Party | Vehicle impact | 1 | 529 | 0.002208 | 4e-06 | N
17-03-19 | 06:15 | ZN15012:PA4 | URBAN | Weather |  | 101 | 285 | 0.019483 | 6.8e-05 | N
17-03-19 | 06:54 | 224:80332 | URBAN | Third Party | Other | 1 | 81 | 5.5e-05 | 1e-06 | N
17-03-19 | 07:24 | ZN15006:PA16 | URBAN | Other | Other | 1 | 335 | 0.000227 | 1e-06 | N
17-03-19 | 08:11 | 264:81241 | URBAN | Other | Other | 1 | 143 | 9.7e-05 | 1e-06 | N
17-03-19 | 08:27 | ZN15006:PA16 | URBAN | Other | Other - Self Clearing Trigger | 63 | 263 | 0.011196 | 4.3e-05 | N
17-03-19 | 08:37 | ZN965:PA8 | URBAN | Asset Failure | LV | 41 | 103 | 0.002859 | 2.8e-05 | N
17-03-19 | 07:34 | ZN14891:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 766 | 127 | 0.40504 | 0.003201 | N
17-03-19 | 08:54 | ZN1610:PA17 | URBAN | Asset Failure | LV | 1 | 1,724 | 0.001167 | 1e-06 | N
17-03-19 | 08:57 | ZN12570:PA24 | SHORT RURAL | Other | Other - Arcing | 1 | 603 | 0.002518 | 4e-06 | N
17-03-19 | 08:58 | ZN15015:PA15 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 302 | 0.001261 | 4e-06 | N
17-03-19 | 09:18 | 222:33600 | URBAN | Other | Other - Self Clearing Trigger | 1,038 | 31 | 0.021681 | 0.000703 | N
17-03-19 | 09:30 | ZN1285:PA17 | URBAN | Asset Failure | LV | 11 | 130 | 0.000968 | 7e-06 | N
17-03-19 | 09:43 | 242:81533 | SHORT RURAL | Weather |  | 1 | 157 | 0.000656 | 4e-06 | N
17-03-19 | 09:37 | ZN931:PA26 | URBAN | Other | Other - Self Clearing Trigger | 81 | 108 | 0.005894 | 5.5e-05 | N
17-03-19 | 10:05 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 158 | 207 | 0.13669 | 0.00066 | N
17-03-19 | 10:13 | ZN195:PA9 | SHORT RURAL | Other | Other - Arcing | 1 | 857 | 0.003581 | 4e-06 | N
17-03-19 | 10:22 | ZN2602:PA17 | URBAN | Other | Other - Arcing | 1 | 276 | 0.000187 | 1e-06 | N
17-03-19 | 12:38 | ZN36200:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 74 | 318 | 0.015914 | 5e-05 | N
17-03-19 | 10:32 | ZN15004:PA5 | URBAN | Other | Other - Self Clearing Trigger | 35 | 133 | 0.003151 | 2.4e-05 | N
17-03-19 | 10:34 | ZN3672:PA36 | URBAN | Third Party | Other | 1 | 572 | 0.000387 | 1e-06 | N
17-03-19 | 11:29 | ZN180:PA21 | URBAN | Asset Failure | LV | 61 | 1,065 | 0.043976 | 4.1e-05 | N
17-03-19 | 11:39 | ZN3922:PA18 | URBAN | Asset Failure | LV | 99 | 2,931 | 0.19641 | 6.7e-05 | N
17-03-19 | 11:45 | ZN3155:PA21 | URBAN | Asset Failure | LV | 54 | 945 | 0.034534 | 3.7e-05 | N
17-03-19 | 12:11 | ZN35400:PA68 | URBAN | Asset Failure | LV | 68 | 1,343 | 0.061823 | 4.6e-05 | N
17-03-19 | 12:15 | ZN1290:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 415 | 0.000281 | 1e-06 | N
17-03-19 | 11:57 | ZN4990:PA51 52ABC | CBD | Asset Failure | HV | 362 | 642 | 7.6073 | 0.01185 | N
17-03-19 | 12:24 | ZN35900:PA24 | URBAN | Other | Other | 1 | 405 | 0.000274 | 1e-06 | N
17-03-19 | 12:28 | ZN965:PA8 | URBAN | Asset Failure | LV | 33 | 722 | 0.016123 | 2.2e-05 | N
17-03-19 | 12:47 | ZN2466:PA16 | URBAN | Other | Other - Self Clearing Trigger | 25 | 207 | 0.003508 | 1.7e-05 | N
17-03-19 | 12:56 | ZN12580:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 468 | 0.000317 | 1e-06 | N
17-03-19 | 13:17 | ZN12650:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 373 | 0.000252 | 1e-06 | N
17-03-19 | 13:22 | ZN931:PA26 | URBAN | Asset Failure | LV | 81 | 1,827 | 0.10019 | 5.5e-05 | N
17-03-19 | 13:53 | ZN12640:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 3 | 802 | 0.010049 | 1.3e-05 | N
17-03-19 | 14:24 | ZN3425:PA28 | SHORT RURAL | Other | Other - Self Clearing Trigger | 15 | 113 | 0.00708 | 6.3e-05 | N
17-03-19 | 14:29 | ZN116:PA14 | URBAN | Other | Other | 1 | 506 | 0.000342 | 1e-06 | N
17-03-19 | 15:31 | ZN15008:PA1 | URBAN | Other | Other - Arcing | 1 | 1,246 | 0.000844 | 1e-06 | N
17-03-19 | 15:33 | ZN1068:PA21 | URBAN | Other | Other - Self Clearing Trigger | 54 | 161 | 0.005897 | 3.7e-05 | N
17-03-19 | 23:08 | ZN195:PA10 | URBAN | Third Party | Vehicle impact | 40 | 232 | 0.006273 | 2.7e-05 | N
26-03-19 | 13:44 | ZN35400:PA82 | URBAN | Third Party | Fire | 1 | 268 | 0.000181 | 1e-06 | N
17-03-19 | 17:38 | ZN12620:PA2 | SHORT RURAL | Other | Other - Arcing | 1 | 305 | 0.001276 | 4e-06 | N
17-03-19 | 18:28 | ZN3425:PA28 | SHORT RURAL | Asset Failure | LV | 15 | 1,861 | 0.11664 | 6.3e-05 | N
17-03-19 | 18:59 | ZN35555:PA20 | URBAN | Other | Other | 1 | 1,117 | 0.000756 | 1e-06 | N
17-03-19 | 19:57 | ZN12650:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 1,413 | 0.005903 | 4e-06 | N
17-03-19 | 21:33 | ZN2635:PA46 | URBAN | Other | Other - Self Clearing Trigger | 46 | 106 | 0.003313 | 3.1e-05 | N
17-03-19 | 22:25 | ZN1068:PA16 | URBAN | Other | Other | 1 | 358 | 0.000242 | 1e-06 | N
17-03-19 | 23:38 | ZN116:PA29 | URBAN | Other | Other | 1 | 284 | 0.000192 | 1e-06 | N
18-03-19 | 03:06 | ZN15001:PA2 | URBAN | Asset Failure | LV | 126 | 469 | 0.039985 | 8.5e-05 | N
18-03-19 | 04:19 | ZN9900:PA2 | URBAN | Asset Failure | LV | 38 | 161 | 0.004134 | 2.6e-05 | N
18-03-19 | 04:48 | ZN12650:PA17 | URBAN | Asset Failure | LV | 21 | 372 | 0.005282 | 1.4e-05 | N
17-03-19 | 03:56 | 813:89061 | LONG RURAL | Other | Other - Arcing | 1 | 188 | 0.065872 | 0.00035 | N
18-03-19 | 07:22 | ZN36800:PA32 | URBAN | Third Party | Other | 1 | 578 | 0.000391 | 1e-06 | N
18-03-19 | 07:41 | ZN2400:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 14 | 189 | 0.001791 | 9e-06 | N
18-03-19 | 08:45 | 204:82691 | URBAN | Other | Other | 1 | 81 | 5.5e-05 | 1e-06 | N
18-03-19 | 08:52 | ZN9252:PA22 | URBAN | Asset Failure | HV | 1,573 | 65 | 0.0687 | 0.001065 | N
18-03-19 | 09:15 | ZN262:PA30 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,368 | 0.000926 | 1e-06 | N
18-03-19 | 09:17 | ZN340:PA11 | URBAN | Other | Other - Arcing | 1 | 493 | 0.000333 | 1e-06 | N
18-03-19 | 09:31 | 261:81882 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 86 | 5.8e-05 | 1e-06 | N
18-03-19 | 09:38 | ZN35600:PA3 | URBAN | Other | Other - Self Clearing Trigger | 63 | 221 | 0.009428 | 4.3e-05 | N
18-03-19 | 11:09 | ZN2835:PA15 | URBAN | Other | Other | 1 | 147 | 0.0001 | 1e-06 | N
18-03-19 | 11:14 | 222:33596 | URBAN | Other | Other - Arcing | 1 | 1,215 | 0.000822 | 1e-06 | N
18-03-19 | 11:47 | ZN9252:PA27 | URBAN | Third Party | Vehicle impact | 1 | 133 | 9e-05 | 1e-06 | N
18-03-19 | 13:02 | ZN36300:PA11 | URBAN | Other | Other | 1 | 418 | 0.000283 | 1e-06 | N
18-03-19 | 15:33 | ZN7481:PA20 | URBAN | Other | Other - Self Clearing Trigger | 1 | 102 | 6.9e-05 | 1e-06 | N
18-03-19 | 16:12 | ZN965:PA24 | URBAN | Network business | Network error | 60 | 118 | 0.004782 | 4.1e-05 | N
17-03-19 | 11:05 | ZN965:PA8 | URBAN | Asset Failure | LV | 41 | 15 | 0.000416 | 2.8e-05 | N
16-03-19 | 11:30 | ZN12570:PA40 | SHORT RURAL | Asset Failure | Distribution substation | 76 | 195 | 0.06192 | 0.000318 | N
18-03-19 | 18:10 | ZN3922:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 222 | 0.00015 | 1e-06 | N
18-03-19 | 19:27 | 508:82580 | SHORT RURAL | Other | Other | 4 | 151 | 0.002518 | 1.7e-05 | N
18-03-19 | 20:13 | ZN14891:PA16 | SHORT RURAL | Animal | Animal impact | 51 | 57 | 0.012146 | 0.000213 | N
18-03-19 | 21:44 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 708 | 0.002959 | 4e-06 | N
19-03-19 | 02:12 | ZN129:PA35 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,314 | 60 | 0.05337 | 0.00089 | Y
19-03-19 | 04:30 | ZN9900:PA2 | URBAN | Other | Other - Self Clearing Trigger | 38 | 130 | 0.003335 | 2.6e-05 | Y
19-03-19 | 06:11 | ZN35600:PA3 | URBAN | Asset Failure | LV | 64 | 204 | 0.008829 | 4.3e-05 | Y
19-03-19 | 06:52 | ZN14144:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 457 | 0.00191 | 4e-06 | Y
19-03-19 | 07:05 | ZN10999:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 234 | 0.000159 | 1e-06 | Y
19-03-19 | 07:15 | ZN847:PA28 | URBAN | Asset Failure | LV | 53 | 165 | 0.00592 | 3.6e-05 | Y
18-03-19 | 14:50 | ZN9245:PA6 | URBAN | Asset Failure | LV | 31 | 40 | 0.000839 | 2.1e-05 | N
19-03-19 | 07:46 | ZN9900:PA2 | URBAN | Other | Other - Self Clearing Trigger | 38 | 154 | 0.003951 | 2.6e-05 | Y
19-03-19 | 07:42 | ZN10999:PA11 | URBAN | Other | Other - Self Clearing Trigger | 18 | 147 | 0.001797 | 1.2e-05 | Y
19-03-19 | 09:12 | 417:80491 | SHORT RURAL | Asset Failure | HV | 6 | 161 | 0.004036 | 2.5e-05 | Y
19-03-19 | 08:08 | ZN9700:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 97 | 0.003283 | 3.4e-05 | Y
19-03-19 | 09:04 | ZN15009:PA1 | URBAN | Third Party | Fire | 154 | 253 | 0.026356 | 0.000104 | Y
19-03-19 | 09:31 | 227:13015 | SHORT RURAL | Other | Other | 1 | 89 | 0.000372 | 4e-06 | Y
19-03-19 | 09:46 | ZN9118:PA16 | URBAN | Asset Failure | LV | 58 | 434 | 0.017028 | 3.9e-05 | Y
19-03-19 | 08:04 | ZN847:PA45 | SHORT RURAL | Asset Failure | LV | 9 | 566 | 0.021284 | 3.8e-05 | Y
19-03-19 | 11:55 | ZN36200:PA8 | SHORT RURAL | Asset Failure | LV | 31 | 20 | 0.002591 | 0.00013 | Y
19-03-19 | 10:38 | 264:81236 | URBAN | Other | Other | 1 | 154 | 0.000104 | 1e-06 | Y
17-03-19 | 14:42 | ZN80:PA21 | URBAN | Asset Failure | LV | 103 | 186 | 0.012968 | 7e-05 | N
19-03-19 | 11:00 | ZN3155:PA33 | URBAN | Asset Failure | LV | 15 | 775 | 0.00787 | 1e-05 | Y
19-03-19 | 11:19 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 100 | 0.035044 | 0.00035 | Y
19-03-19 | 12:18 | ZN35600:PA3 | URBAN | Other | Other - Arcing | 16 | 432 | 0.004674 | 1.1e-05 | Y
19-03-19 | 03:18 | ZN3155:PA33 | URBAN | Asset Failure | LV | 96 | 1,237 | 0.080389 | 6.5e-05 | Y
19-03-19 | 12:54 | ZN384:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 51 | 226 | 0.048159 | 0.000213 | Y
19-03-19 | 13:46 | 528:83024 | URBAN | Asset Failure | HV | 72 | 49 | 0.002388 | 4.9e-05 | Y
19-03-19 | 14:00 | ZN9118:PA16 | URBAN | Network business | Switching and protection error | 12 | 180 | 0.001462 | 8e-06 | Y
19-03-19 | 14:10 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 319 | 0.001333 | 4e-06 | Y
19-03-19 | 15:27 | ZN15002:PA2 | URBAN | Asset Failure | Subtransmission | 2,488 | 94 | 0.15832 | 0.001684 | Y
19-03-19 | 15:27 | ZN15002:PA4 | SHORT RURAL | Asset Failure | Subtransmission | 1,548 | 94 | 0.60799 | 0.006468 | Y
19-03-19 | 15:27 | ZN15002:PA6 | URBAN | Asset Failure | Subtransmission | 3,322 | 94 | 0.21139 | 0.002249 | Y
19-03-19 | 15:27 | ZN15002:PA8 | URBAN | Asset Failure | Subtransmission | 2,068 | 94 | 0.13159 | 0.0014 | Y
19-03-19 | 15:27 | ZN15002:PA9 | URBAN | Asset Failure | Subtransmission | 26 | 94 | 0.001654 | 1.8e-05 | Y
19-03-19 | 15:27 | ZN15004:PA1 | URBAN | Asset Failure | Subtransmission | 1,718 | 198 | 0.23027 | 0.001163 | Y
19-03-19 | 15:27 | ZN15004:PA3 | SHORT RURAL | Asset Failure | Subtransmission | 1,358 | 198 | 1.1235 | 0.005674 | Y
19-03-19 | 15:27 | ZN15004:PA5 | URBAN | Asset Failure | Subtransmission | 1,731 | 198 | 0.23201 | 0.001172 | Y
19-03-19 | 15:27 | ZN15004:PA9 | URBAN | Asset Failure | Subtransmission | 1,561 | 198 | 0.20923 | 0.001057 | Y
19-03-19 | 15:27 | ZN15010:PA24 | URBAN | Asset Failure | Subtransmission | 1,411 | 208 | 0.19868 | 0.000955 | Y
19-03-19 | 15:27 | ZN15010:PA25 | SHORT RURAL | Asset Failure | Subtransmission | 479 | 208 | 0.41629 | 0.002001 | Y
19-03-19 | 15:27 | ZN15010:PA26 | SHORT RURAL | Asset Failure | Subtransmission | 337 | 208 | 0.29288 | 0.001408 | Y
19-03-19 | 15:27 | ZN15010:PA28 | SHORT RURAL | Asset Failure | Subtransmission | 1,108 | 208 | 0.96295 | 0.00463 | Y
19-03-19 | 15:27 | ZN15010:PA29 | URBAN | Asset Failure | Subtransmission | 579 | 208 | 0.081526 | 0.000392 | Y
19-03-19 | 15:27 | ZN15010:PA30 | URBAN | Asset Failure | Subtransmission | 1,805 | 208 | 0.25415 | 0.001222 | Y
19-03-19 | 15:27 | ZN15010:PA33 | URBAN | Asset Failure | Subtransmission | 87 | 208 | 0.01225 | 5.9e-05 | Y
19-03-19 | 15:27 | ZN15013:PA1 | URBAN | Asset Failure | Subtransmission | 322 | 158 | 0.03444 | 0.000218 | Y
19-03-19 | 15:27 | ZN15013:PA10 | SHORT RURAL | Asset Failure | Subtransmission | 626 | 158 | 0.41327 | 0.002616 | Y
19-03-19 | 15:27 | ZN15013:PA12 | URBAN | Asset Failure | Subtransmission | 104 | 158 | 0.011124 | 7e-05 | Y
19-03-19 | 15:27 | ZN15013:PA2 | SHORT RURAL | Asset Failure | Subtransmission | 67 | 158 | 0.044231 | 0.00028 | Y
19-03-19 | 15:27 | ZN15013:PA4 | SHORT RURAL | Asset Failure | Subtransmission | 874 | 158 | 0.57699 | 0.003652 | Y
19-03-19 | 15:27 | ZN15013:PA6 | SHORT RURAL | Asset Failure | Subtransmission | 229 | 158 | 0.15118 | 0.000957 | Y
19-03-19 | 15:27 | ZN15013:PA8 | URBAN | Asset Failure | Subtransmission | 133 | 158 | 0.014225 | 9e-05 | Y
19-03-19 | 15:27 | ZN15014:PA10 | SHORT RURAL | Asset Failure | Subtransmission | 1,832 | 126 | 0.96448 | 0.007655 | Y
19-03-19 | 15:27 | ZN15014:PA11 | URBAN | Asset Failure | Subtransmission | 396 | 126 | 0.033777 | 0.000268 | Y
19-03-19 | 15:27 | ZN15014:PA14 | URBAN | Asset Failure | Subtransmission | 867 | 115 | 0.067495 | 0.000587 | Y
19-03-19 | 15:27 | ZN15014:PA16 | URBAN | Asset Failure | Subtransmission | 374 | 115 | 0.029115 | 0.000253 | Y
19-03-19 | 15:27 | ZN15014:PA18 | URBAN | Asset Failure | Subtransmission | 697 | 115 | 0.054261 | 0.000472 | Y
19-03-19 | 15:27 | ZN15014:PA19 | URBAN | Asset Failure | Subtransmission | 1,917 | 115 | 0.14924 | 0.001298 | Y
19-03-19 | 15:27 | ZN15014:PA20 | URBAN | Asset Failure | Subtransmission | 911 | 115 | 0.07092 | 0.000617 | Y
19-03-19 | 15:27 | ZN15014:PA22 | URBAN | Asset Failure | Subtransmission | 901 | 115 | 0.070142 | 0.00061 | Y
19-03-19 | 15:27 | ZN15014:PA5 | URBAN | Asset Failure | Subtransmission | 1,784 | 126 | 0.15217 | 0.001208 | Y
19-03-19 | 15:27 | ZN15014:PA7 | URBAN | Asset Failure | Subtransmission | 1,225 | 126 | 0.10448 | 0.000829 | Y
19-03-19 | 15:27 | ZN15014:PA8 | URBAN | Asset Failure | Subtransmission | 1,022 | 126 | 0.087172 | 0.000692 | Y
19-03-19 | 15:57 | 524:33578 | URBAN | Asset Failure | LV | 1 | 114 | 7.7e-05 | 1e-06 | Y
19-03-19 | 15:57 | ZN2635:PA46 | URBAN | Asset Failure | LV | 46 | 243 | 0.007555 | 3.1e-05 | Y
19-03-19 | 16:40 | ZN15015:PA5 | URBAN | Third Party | Fire | 1 | 278 | 0.000188 | 1e-06 | Y
19-03-19 | 17:40 | 235:2123 | URBAN | Asset Failure | Distribution substation | 65 | 30 | 0.00132 | 4.4e-05 | Y
19-03-19 | 17:06 | ZN12630:PA1 | SHORT RURAL | Other | Other - Arcing | 417 | 111 | 0.19278 | 0.001742 | Y
19-03-19 | 18:52 | ZN15015:PA5 | URBAN | Third Party | Fire | 1 | 146 | 9.9e-05 | 1e-06 | Y
19-03-19 | 19:45 | ZN9118:PA11 | URBAN | Asset Failure | LV | 33 | 74 | 0.001659 | 2.2e-05 | Y
19-03-19 | 23:05 | 221:11899 | SHORT RURAL | Animal | Animal impact | 1,322 | 41 | 0.22647 | 0.005524 | Y
20-03-19 | 00:08 | ZN14891:PA17 | SHORT RURAL | Asset Failure | LV | 23 | 152 | 0.014575 | 9.6e-05 | N
20-03-19 | 03:57 | ZN12580:PA14 | URBAN | Other | Other - Self Clearing Trigger | 800 | 105 | 0.057013 | 0.000542 | N
20-03-19 | 03:57 | ZN12580:PA7 | URBAN | Other | Other - Self Clearing Trigger | 179 | 113 | 0.013693 | 0.000121 | N
20-03-19 | 06:19 | 217:33610 | URBAN | Animal | Animal impact | 1,952 | 77 | 0.10126 | 0.001321 | N
20-03-19 | 07:18 | ZN8000:PA38 | URBAN | Asset Failure | LV | 64 | 326 | 0.014124 | 4.3e-05 | N
20-03-19 | 07:37 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 343 | 0.000232 | 1e-06 | N
19-03-19 | 21:30 | ZN8000:PA38 | URBAN | Asset Failure | LV | 64 | 20 | 0.000866 | 4.3e-05 | Y
20-03-19 | 11:20 | ZN10993:PA35 | URBAN | Third Party | Vehicle impact | 1 | 99 | 6.7e-05 | 1e-06 | N
20-03-19 | 09:42 | ZN12650:PA2 | URBAN | Third Party | Vehicle impact | 1 | 227 | 0.000154 | 1e-06 | N
20-03-19 | 10:31 | 502:48010 | SHORT RURAL | Asset Failure | LV | 1 | 268 | 0.001121 | 4e-06 | N
20-03-19 | 10:47 | ZN12650:PA9 | URBAN | Third Party | Vehicle impact | 1 | 523 | 0.000354 | 1e-06 | N
20-03-19 | 10:52 | ZN15006:PA12 | URBAN | Other | Other | 1 | 128 | 8.6e-05 | 1e-06 | N
20-03-19 | 11:38 | ZN195:PA22 | URBAN | Asset Failure | Subtransmission | 692 | 24 | 0.011243 | 0.000468 | N
20-03-19 | 11:38 | ZN195:PA23 | URBAN | Asset Failure | Subtransmission | 675 | 24 | 0.010967 | 0.000457 | N
20-03-19 | 11:38 | ZN195:PA25 | URBAN | Asset Failure | Subtransmission | 763 | 24 | 0.012396 | 0.000517 | N
20-03-19 | 11:38 | ZN195:PA28 | URBAN | Asset Failure | Subtransmission | 903 | 25 | 0.015282 | 0.000611 | N
20-03-19 | 11:38 | ZN195:PA29 | URBAN | Asset Failure | Subtransmission | 1,119 | 25 | 0.018892 | 0.000758 | N
20-03-19 | 11:38 | ZN195:PA3 | URBAN | Asset Failure | Subtransmission | 1 | 25 | 1.7e-05 | 1e-06 | N
20-03-19 | 11:38 | ZN195:PA30 | SHORT RURAL | Asset Failure | Subtransmission | 1,235 | 25 | 0.12903 | 0.005161 | N
20-03-19 | 11:38 | ZN195:PA4 | URBAN | Asset Failure | Subtransmission | 5 | 24 | 8.1e-05 | 3e-06 | N
20-03-19 | 12:51 | ZN10999:PA11 | URBAN | Asset Failure | LV | 18 | 219 | 0.002665 | 1.2e-05 | N
20-03-19 | 13:02 | 257:82000 | SHORT RURAL | Other | Other | 1 | 72 | 0.000302 | 4e-06 | N
20-03-19 | 18:00 | 202:34254 | URBAN | Third Party | Dig-in | 5 | 61 | 0.000206 | 3e-06 | N
20-03-19 | 13:44 | ZN12570:PA34 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 513 | 30 | 0.064318 | 0.002144 | N
20-03-19 | 15:43 | ZN690:PA28 | URBAN | Other | Other | 1 | 151 | 0.000102 | 1e-06 | N
20-03-19 | 16:10 | 512:83732 | SHORT RURAL | Other | Other | 1 | 47 | 0.000198 | 4e-06 | N
20-03-19 | 18:10 | ZN195:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 130 | 0.002992 | 2.3e-05 | N
20-03-19 | 17:25 | 256:80652 | URBAN | Asset Failure | LV | 1 | 314 | 0.000212 | 1e-06 | N
20-03-19 | 17:39 | ZN7481:PA20 | URBAN | Third Party | Other | 1 | 99 | 6.7e-05 | 1e-06 | N
20-03-19 | 18:11 | ZN1290:PA10 | URBAN | Third Party | Other | 1 | 19 | 1.3e-05 | 1e-06 | N
20-03-19 | 18:42 | ZN10999:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,233 | 0.000835 | 1e-06 | N
20-03-19 | 19:19 | ZN15002:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 68 | 161 | 0.007411 | 4.6e-05 | N
20-03-19 | 19:33 | 216:10729 | URBAN | Other | Other | 1 | 47 | 3.2e-05 | 1e-06 | N
21-03-19 | 00:30 | ZN15009:PA11 | URBAN | Asset Failure | LV | 46 | 55 | 0.001713 | 3.1e-05 | N
20-03-19 | 22:57 | ZN1285:PA23 | URBAN | Asset Failure | LV | 110 | 93 | 0.006925 | 7.4e-05 | N
21-03-19 | 00:30 | ZN15009:PA11 | URBAN | Asset Failure | LV | 39 | 55 | 0.001452 | 2.6e-05 | N
21-03-19 | 07:09 | ZN1193:PA15 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 102 | 0.000425 | 4e-06 | N
30-12-18 | 13:22 | ZN129:PA63 | URBAN | Network business | Network error | 214 | 128 | 0.018559 | 0.000145 | N
21-03-19 | 10:53 | ZN931:PA26 | URBAN | Other | Other - Self Clearing Trigger | 46 | 86 | 0.002689 | 3.1e-05 | N
21-03-19 | 11:10 | 511:29877 | SHORT RURAL | Other | Other - Self Clearing Trigger | 82 | 99 | 0.033949 | 0.000343 | N
21-03-19 | 11:22 | ZN15010:PA24 | URBAN | Other | Other - Arcing | 1 | 503 | 0.00034 | 1e-06 | N
21-03-19 | 12:43 | ZN15008:PA1 | URBAN | Other | Other - Arcing | 2 | 660 | 0.000894 | 1e-06 | N
21-03-19 | 15:06 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 16 | 164 | 0.010958 | 6.7e-05 | N
21-03-19 | 16:21 | ZN15005:PA2 | URBAN | Other | Other | 1 | 69 | 4.7e-05 | 1e-06 | N
21-03-19 | 16:23 | 812:19065 | SHORT RURAL | Third Party | Vehicle impact | 204 | 48 | 0.040868 | 0.000853 | N
21-03-19 | 16:38 | ZN15010:PA30 | URBAN | Third Party | Vehicle impact | 29 | 252 | 0.004947 | 2e-05 | N
21-03-19 | 17:24 | ZN1285:PA31 | URBAN | Asset Failure | LV | 1 | 442 | 0.000299 | 1e-06 | N
21-03-19 | 22:47 | ZN2602:PA3 | URBAN | Asset Failure | LV | 1 | 117 | 7.9e-05 | 1e-06 | N
22-03-19 | 01:21 | ZN35600:PA17 | URBAN | Asset Failure | HV | 2 | 126 | 0.000171 | 1e-06 | N
22-03-19 | 01:21 | ZN35600:PA20 | URBAN | Asset Failure | HV | 203 | 126 | 0.017316 | 0.000137 | N
22-03-19 | 11:20 | 232:33407 | SHORT RURAL | Asset Failure | LV | 4 | 150 | 0.002507 | 1.7e-05 | N
22-03-19 | 12:20 | 232:33407 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 83 | 0.000346 | 4e-06 | N
22-03-19 | 12:09 | 526:34639 | SHORT RURAL | Asset Failure | HV | 508 | 180 | 0.38275 | 0.002123 | N
22-03-19 | 14:29 | ZN180:PA43 | URBAN | Third Party | Vehicle impact | 19 | 166 | 0.002135 | 1.3e-05 | N
22-03-19 | 17:47 | 802:82225 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 56 | 924 | 0.21629 | 0.000234 | N
22-03-19 | 18:03 | 807:74179 | SHORT RURAL | Asset Failure | HV | 46 | 354 | 0.068049 | 0.000192 | N
22-03-19 | 18:12 | ZN195:PA10 | URBAN | Third Party | Vehicle impact | 28 | 183 | 0.003469 | 1.9e-05 | N
22-03-19 | 18:14 | ZN35370:PA4 | SHORT RURAL | Weather |  | 142 | 139 | 0.082483 | 0.000593 | N
22-03-19 | 18:20 | ZN35370:PA4 | SHORT RURAL | Weather |  | 11 | 90 | 0.004131 | 4.6e-05 | N
22-03-19 | 18:31 | 515:35198 | SHORT RURAL | Other | Other - Self Clearing Trigger | 71 | 537 | 0.15919 | 0.000297 | N
22-03-19 | 18:31 | 515:35193 | SHORT RURAL | Asset Failure | HV | 135 | 95 | 0.053456 | 0.000564 | N
22-03-19 | 18:47 | 532:83309 | URBAN | Other | Other | 1 | 191 | 0.000129 | 1e-06 | N
22-03-19 | 18:29 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 202 | 96 | 0.081192 | 0.000844 | N
22-03-19 | 18:52 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 238 | 0.000995 | 4e-06 | N
22-03-19 | 19:06 | 810:74062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 139 | 0.000581 | 4e-06 | N
22-03-19 | 19:13 | 526:34639 | SHORT RURAL | Asset Failure | HV | 97 | 123 | 0.049783 | 0.000405 | N
22-03-19 | 19:23 | 810:74062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 147 | 0.004914 | 3.3e-05 | N
22-03-19 | 19:32 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 298 | 0.007472 | 2.5e-05 | N
22-03-19 | 19:37 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 386 | 0.001614 | 4e-06 | N
22-03-19 | 19:37 | 806:82662 | SHORT RURAL | Asset Failure | HV | 226 | 468 | 0.4424 | 0.000944 | N
22-03-19 | 20:00 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 140 | 0.049054 | 0.00035 | N
22-03-19 | 20:19 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 461 | 0.16136 | 0.00035 | N
22-03-19 | 22:49 | 516:48067 | SHORT RURAL | Asset Failure | HV | 51 | 99 | 0.021116 | 0.000213 | N
22-03-19 | 22:40 | ZN3922:PA14 | URBAN | Other | Other - Self Clearing Trigger | 103 | 20 | 0.001395 | 7e-05 | N
22-03-19 | 21:21 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 979 | 0.34303 | 0.00035 | N
22-03-19 | 21:34 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 796 | 0.013306 | 1.7e-05 | N
22-03-19 | 22:42 | 806:82662 | SHORT RURAL | Asset Failure | HV | 2 | 947 | 0.007919 | 8e-06 | N
23-03-19 | 03:05 | 812:19072 | SHORT RURAL | Asset Failure | HV | 202 | 161 | 0.1356 | 0.000844 | N
23-03-19 | 03:17 | 270:83590 | URBAN | Animal | Animal impact | 77 | 58 | 0.003023 | 5.2e-05 | N
22-03-19 | 19:07 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 24 | 448 | 3.7638 | 0.008409 | N
23-03-19 | 05:47 | ZN965:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 432 | 0.000293 | 1e-06 | N
23-03-19 | 07:38 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 659 | 0.002753 | 4e-06 | N
23-03-19 | 07:37 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 660 | 0.002756 | 4e-06 | N
23-03-19 | 08:45 | 511:29878 | SHORT RURAL | Asset Failure | HV | 89 | 126 | 0.04702 | 0.000372 | N
23-03-19 | 09:07 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 132 | 0.046322 | 0.00035 | N
22-03-19 | 20:33 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 942 | 0.003937 | 4e-06 | N
23-03-19 | 13:22 | 806:82662 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 417 | 0.001741 | 4e-06 | N
23-03-19 | 14:47 | ZN12650:PA6 | URBAN | Other | Other - Arcing | 1 | 65 | 4.4e-05 | 1e-06 | N
23-03-19 | 16:14 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 19 | 526 | 0.006764 | 1.3e-05 | N
23-03-19 | 16:44 | 522:83132 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 250 | 0.001046 | 4e-06 | N
23-03-19 | 18:38 | ZN9118:PA2 | URBAN | Asset Failure | LV | 44 | 231 | 0.006889 | 3e-05 | N
23-03-19 | 18:55 | 258:80793 | URBAN | Other | Other | 1 | 121 | 8.2e-05 | 1e-06 | N
23-03-19 | 19:57 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 198 | 0.001654 | 8e-06 | N
23-03-19 | 21:14 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 196 | 68 | 0.05591 | 0.000819 | N
23-03-19 | 20:46 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 60 | 99 | 0.024728 | 0.000251 | N
23-03-19 | 21:01 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 94 | 0.007042 | 7.5e-05 | N
23-03-19 | 21:10 | 515:35197 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 140 | 405 | 19.8739 | 0.049037 | N
23-03-19 | 21:45 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 95 | 416 | 0.1651 | 0.000397 | N
23-03-19 | 22:03 | 522:83124 | URBAN | Other | Other - Self Clearing Trigger | 24 | 200 | 0.003252 | 1.6e-05 | N
24-03-19 | 02:00 | 522:83121 | URBAN | Vegetation | Vegetation Blow/Fall In | 64 | 425 | 0.018411 | 4.3e-05 | N
23-03-19 | 22:03 | 216:10726 | URBAN | Asset Failure | HV | 764 | 251 | 0.12969 | 0.000517 | N
23-03-19 | 22:12 | 216:10722 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,703 | 308 | 2.1894 | 0.007115 | N
23-03-19 | 22:12 | 216:10723 | URBAN | Other | Other - Self Clearing Trigger | 803 | 225 | 0.12229 | 0.000544 | N
23-03-19 | 22:12 | 216:10724 | SHORT RURAL | Other | Other - Self Clearing Trigger | 986 | 170 | 0.70027 | 0.004119 | N
23-03-19 | 22:12 | 216:10727 | URBAN | Other | Other - Self Clearing Trigger | 585 | 194 | 0.076816 | 0.000396 | N
23-03-19 | 22:12 | 216:10728 | URBAN | Other | Other - Self Clearing Trigger | 1,501 | 187 | 0.1898 | 0.001016 | N
23-03-19 | 22:12 | 216:10729 | URBAN | Other | Other - Self Clearing Trigger | 1,127 | 99 | 0.075519 | 0.000763 | N
23-03-19 | 22:12 | 416:3587 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.000376 | 4e-06 | N
23-03-19 | 22:16 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 1,604 | 0.56169 | 0.00035 | N
23-03-19 | 22:16 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 888 | 0.003711 | 4e-06 | N
23-03-19 | 22:15 | 507:80914 | SHORT RURAL | Asset Failure | HV | 147 | 640 | 0.39276 | 0.000614 | N
23-03-19 | 22:19 | 227:13019 | SHORT RURAL | Asset Failure | HV | 50 | 652 | 0.13615 | 0.000209 | N
23-03-19 | 22:22 | 802:82220 | SHORT RURAL | Asset Failure | HV | 41 | 298 | 0.051043 | 0.000171 | N
23-03-19 | 22:28 | ZN14143:PA17 | SHORT RURAL | Weather |  | 772 | 120 | 0.38602 | 0.003225 | N
23-03-19 | 22:35 | 526:34639 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 628 | 0.007871 | 1.3e-05 | N
23-03-19 | 22:38 | 243:80083 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 577 | 0.009642 | 1.7e-05 | N
24-03-19 | 15:00 | 522:83124 | URBAN | Asset Failure | HV | 1 | 247 | 0.000167 | 1e-06 | N
23-03-19 | 22:49 | 520:48172 | SHORT RURAL | Weather |  | 1 | 485 | 0.002026 | 4e-06 | N
23-03-19 | 22:50 | 522:83132 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 910 | 0.003802 | 4e-06 | N
23-03-19 | 22:53 | 522:83132 | SHORT RURAL | Other | Other - Self Clearing Trigger | 8 | 811 | 0.027117 | 3.3e-05 | N
23-03-19 | 23:07 | 220:8687 | URBAN | Weather |  | 1 | 324 | 0.000219 | 1e-06 | N
23-03-19 | 23:17 | ZN14891:PA20 | SHORT RURAL | Asset Failure | Distribution substation | 12 | 493 | 0.024701 | 5e-05 | N
23-03-19 | 23:38 | 243:80083 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 822 | 0.013736 | 1.7e-05 | N
23-03-19 | 23:41 | 239:82127 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 629 | 0.018394 | 2.9e-05 | N
23-03-19 | 23:50 | ZN12640:PA4 | URBAN | Asset Failure | HV | 715 | 82 | 0.039644 | 0.000484 | N
24-03-19 | 01:19 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 111 | 0.005565 | 5e-05 | N
24-03-19 | 01:27 | 509:33395 | LONG RURAL | Asset Failure | HV | 281 | 778 | 76.6053 | 0.098424 | N
24-03-19 | 01:49 | 814:82285 | SHORT RURAL | Weather |  | 1 | 325 | 0.001358 | 4e-06 | N
24-03-19 | 02:48 | 807:74184 | SHORT RURAL | Weather |  | 2 | 600 | 0.005013 | 8e-06 | N
24-03-19 | 03:24 | 801:74123 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 249 | 0.00104 | 4e-06 | N
24-03-19 | 05:32 | ZN10999:PA4 | URBAN | Asset Failure | HV | 1,601 | 79 | 0.086114 | 0.001084 | N
24-03-19 | 05:49 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 40 | 0.000167 | 4e-06 | N
24-03-19 | 06:32 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 14 | 148 | 0.008656 | 5.8e-05 | N
24-03-19 | 06:46 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 413 | 0.14473 | 0.00035 | N
24-03-19 | 06:52 | 522:83126 | SHORT RURAL | Third Party | Other | 1 | 145 | 0.000604 | 4e-06 | N
24-03-19 | 07:06 | ZN10997:PA5 | URBAN | Other | Other - Self Clearing Trigger | 57 | 233 | 0.008997 | 3.9e-05 | N
24-03-19 | 07:34 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 735 | 0.006142 | 8e-06 | N
24-03-19 | 07:51 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 179 | 0.001496 | 8e-06 | N
24-03-19 | 07:57 | 221:11893 | URBAN | Asset Failure | LV | 1 | 145 | 9.8e-05 | 1e-06 | N
24-03-19 | 08:20 | 524:33570 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 565 | 0.007081 | 1.3e-05 | N
24-03-19 | 08:23 | 522:83132 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 277 | 0.001157 | 4e-06 | N
24-03-19 | 08:31 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 454 | 0.003793 | 8e-06 | N
24-03-19 | 08:33 | 522:83132 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 176 | 0.000737 | 4e-06 | N
24-03-19 | 08:59 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 196 | 0.001638 | 8e-06 | N
24-03-19 | 09:16 | 524:33576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 643 | 0.002688 | 4e-06 | N
24-03-19 | 09:24 | ZN12630:PA3 | SHORT RURAL | Third Party | Other | 1 | 424 | 0.001772 | 4e-06 | N
24-03-19 | 09:31 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 372 | 0.1303 | 0.00035 | N
24-03-19 | 09:34 | 524:33578 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 206 | 0.00014 | 1e-06 | N
24-03-19 | 09:36 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 224 | 0.001872 | 8e-06 | N
24-03-19 | 09:41 | 801:74123 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 19 | 7.8e-05 | 4e-06 | N
24-03-19 | 10:00 | ZN12640:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 330 | 0.001379 | 4e-06 | N
24-03-19 | 10:04 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 145 | 0.050887 | 0.00035 | N
24-03-19 | 10:26 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 244 | 0.003058 | 1.3e-05 | N
24-03-19 | 11:04 | ZN14144:PA5 | URBAN | Third Party | Other | 13 | 86 | 0.000757 | 9e-06 | N
24-03-19 | 11:20 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 214 | 0.000895 | 4e-06 | N
24-03-19 | 11:38 | 522:83132 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 317 | 0.001324 | 4e-06 | N
24-03-19 | 12:52 | 514:18137 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 662 | 0.008302 | 1.3e-05 | N
24-03-19 | 13:40 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 150 | 0.10483 | 0.000701 | N
24-03-19 | 13:48 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 57 | 0.019918 | 0.00035 | N
24-03-19 | 15:07 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 682 | 0.23897 | 0.00035 | N
24-03-19 | 15:55 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 682 | 0.23902 | 0.00035 | N
24-03-19 | 16:03 | ZN262:PA39 | URBAN | Asset Failure | LV | 40 | 1,577 | 0.042697 | 2.7e-05 | N
24-03-19 | 16:18 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 662 | 0.005529 | 8e-06 | N
24-03-19 | 16:42 | 515:35197 | LONG RURAL | Asset Failure | HV | 138 | 44 | 2.1268 | 0.048336 | N
24-03-19 | 17:19 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 222 | 0.001857 | 8e-06 | N
24-03-19 | 17:54 | 811:74234 | SHORT RURAL | Asset Failure | LV | 1 | 588 | 0.002458 | 4e-06 | N
24-03-19 | 18:02 | 814:82283 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 91 | 0.006843 | 7.5e-05 | N
24-03-19 | 18:04 | ZN12650:PA1 | SHORT RURAL | Other | Other - Arcing | 1 | 266 | 0.001111 | 4e-06 | N
24-03-19 | 18:16 | 813:89055 | SHORT RURAL | Third Party | Other | 1 | 130 | 0.000544 | 4e-06 | N
24-03-19 | 18:38 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 197 | 0.000823 | 4e-06 | N
24-03-19 | 19:02 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 379 | 156 | 0.24639 | 0.001583 | N
24-03-19 | 19:31 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 18 | 629 | 0.0473 | 7.5e-05 | N
24-03-19 | 07:56 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 21 | 688 | 0.060395 | 8.8e-05 | N
24-03-19 | 11:12 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 517 | 0.002161 | 4e-06 | N
24-03-19 | 14:26 | 509:33399 | SHORT RURAL | Asset Failure | Distribution substation | 3 | 454 | 0.005689 | 1.3e-05 | N
24-03-19 | 11:03 | 509:33399 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 447 | 0.003733 | 8e-06 | N
24-03-19 | 19:53 | 232:11454 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,890 | 119 | 0.9402 | 0.007896 | N
24-03-19 | 20:34 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 131 | 0.045884 | 0.00035 | N
24-03-19 | 23:24 | ZN2602:PA36 | URBAN | Third Party | Vehicle impact | 2 | 278 | 0.000376 | 1e-06 | N
24-03-19 | 23:31 | ZN2602:PA36 | URBAN | Third Party | Vehicle impact | 1 | 303 | 0.000205 | 1e-06 | N
25-03-19 | 03:50 | ZN4545:PA41 | SHORT RURAL | Asset Failure | HV | 1,000 | 80 | 0.3353 | 0.004178 | N
25-03-19 | 05:15 | ZN2602:PA36 | URBAN | Vegetation | Vegetation Blow/Fall In | 95 | 225 | 0.014468 | 6.4e-05 | N
25-03-19 | 05:15 | ZN2602:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 225 | 0.007615 | 3.4e-05 | N
25-03-19 | 07:18 | 810:74054 | LONG RURAL | Asset Failure | Distribution substation | 1 | 162 | 0.056678 | 0.00035 | N
25-03-19 | 07:21 | ZN14891:PA21 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 15 | 99 | 0.006204 | 6.3e-05 | N
22-03-19 | 21:03 | ZN3922:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 97 | 0.002101 | 2.2e-05 | N
25-03-19 | 07:51 | 524:33570 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 668 | 0.002791 | 4e-06 | N
25-03-19 | 07:57 | 520:48172 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 346 | 0.001447 | 4e-06 | N
25-03-19 | 09:35 | ZN14891:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 10 | 180 | 0.007499 | 4.2e-05 | N
25-03-19 | 08:30 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 177 | 0.00074 | 4e-06 | N
25-03-19 | 08:45 | 520:48172 | SHORT RURAL | Asset Failure | HV | 1 | 240 | 0.001003 | 4e-06 | N
25-03-19 | 08:54 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 146 | 0.00061 | 4e-06 | N
25-03-19 | 09:27 | 524:33576 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 303 | 0.001266 | 4e-06 | N
25-03-19 | 09:28 | ZN2602:PA36 | URBAN | Other | Other | 1 | 240 | 0.000163 | 1e-06 | N
25-03-19 | 11:05 | 220:8689 | URBAN | Asset Failure | LV | 62 | 284 | 0.011935 | 4.2e-05 | N
25-03-19 | 10:37 | 265:81645 | SHORT RURAL | Asset Failure | LV | 9 | 233 | 0.008749 | 3.8e-05 | N
25-03-19 | 10:47 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 343 | 0.24028 | 0.000701 | N
25-03-19 | 12:02 | 508:82578 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 153 | 0.001278 | 8e-06 | N
25-03-19 | 12:53 | ZN12610:PA16 | URBAN | Other | Other | 1 | 246 | 0.000167 | 1e-06 | N
25-03-19 | 13:00 | 528:83020 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 119 | 0.000499 | 4e-06 | N
25-03-19 | 13:32 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 128 | 0.000535 | 4e-06 | N
25-03-19 | 14:56 | 228:7491 | URBAN | Asset Failure | LV | 25 | 364 | 0.00616 | 1.7e-05 | N
25-03-19 | 15:06 | 233:82815 | SHORT RURAL | Third Party | Vehicle impact | 1 | 218 | 0.000911 | 4e-06 | N
25-03-19 | 15:25 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 119 | 0.000498 | 4e-06 | N
25-03-19 | 16:13 | 520:48172 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 131 | 0.001098 | 8e-06 | N
25-03-19 | 16:33 | ZN129:PA46 | URBAN | Third Party | Vehicle impact | 1 | 237 | 0.00016 | 1e-06 | N
25-03-19 | 16:38 | 511:29878 | SHORT RURAL | Asset Failure | HV | 1 | 572 | 0.00239 | 4e-06 | N
25-03-19 | 17:11 | ZN129:PA46 | URBAN | Third Party | Vehicle impact | 2 | 199 | 0.000269 | 1e-06 | N
25-03-19 | 17:11 | 515:35192 | SHORT RURAL | Asset Failure | HV | 338 | 4 | 0.005648 | 0.001412 | N
25-03-19 | 17:44 | 509:33395 | LONG RURAL | Asset Failure | HV | 3 | 516 | 0.54221 | 0.001051 | N
25-03-19 | 18:03 | ZN690:PA3 | URBAN | Asset Failure | LV | 15 | 161 | 0.001639 | 1e-05 | N
25-03-19 | 18:41 | 509:33399 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 298 | 0.001246 | 4e-06 | N
25-03-19 | 23:18 | ZN188:PA15 | URBAN | Asset Failure | HV | 349 | 75 | 0.01778 | 0.000236 | N
25-03-19 | 23:38 | ZN9118:PA11 | URBAN | Other | Other - Self Clearing Trigger | 74 | 381 | 0.019105 | 5e-05 | N
26-03-19 | 02:15 | 807:74180 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 103 | 104 | 0.044848 | 0.00043 | N
26-03-19 | 06:50 | ZN4545:PA36 | URBAN | Network business | Network error | 68 | 240 | 0.011047 | 4.6e-05 | N
26-03-19 | 07:21 | 807:74179 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 384 | 0.001604 | 4e-06 | N
26-03-19 | 07:43 | ZN5868:PA17 | URBAN | Network business | Network error | 76 | 374 | 0.019232 | 5.1e-05 | N
26-03-19 | 08:05 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 64 | 0.000267 | 4e-06 | N
26-03-19 | 08:12 | ZN3155:PA34 | URBAN | Third Party | Other | 44 | 88 | 0.002621 | 3e-05 | N
26-03-19 | 09:28 | ZN15013:PA10 | SHORT RURAL | Animal | Other | 2 | 332 | 0.002774 | 8e-06 | N
26-03-19 | 09:19 | 514:18137 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 101 | 0.002532 | 2.5e-05 | N
26-03-19 | 09:42 | ZN8000:PA10 | URBAN | Asset Failure | HV | 418 | 124 | 0.035023 | 0.000283 | N
23-03-19 | 21:45 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 465 | 0.009713 | 2.1e-05 | N
26-03-19 | 10:06 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 102 | 0.000426 | 4e-06 | N
26-03-19 | 10:34 | 511:29878 | SHORT RURAL | Other | Other | 1 | 90 | 0.000378 | 4e-06 | N
26-03-19 | 12:49 | ZN15011:PA2 | URBAN | Third Party | Vehicle impact | 16 | 131 | 0.001419 | 1.1e-05 | N
26-03-19 | 12:45 | ZN12640:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 101 | 0.000421 | 4e-06 | N
25-03-19 | 00:05 | 232:11457 | SHORT RURAL | Other | Other - Self Clearing Trigger | 12 | 40 | 0.002005 | 5e-05 | N
26-03-19 | 13:44 | 220:8688 | URBAN | Other | Other | 1 | 299 | 0.000203 | 1e-06 | N
26-03-19 | 14:17 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 63 | 0.000263 | 4e-06 | N
26-03-19 | 14:20 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 40 | 0.000167 | 4e-06 | N
26-03-19 | 14:36 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 99 | 0.000414 | 4e-06 | N
26-03-19 | 16:10 | ZN2635:PA62 | URBAN | Network business | Switching and protection error | 6 | 170 | 0.00069 | 4e-06 | N
26-03-19 | 15:58 | 216:10726 | URBAN | Other | Other | 1 | 111 | 7.5e-05 | 1e-06 | N
26-03-19 | 19:40 | ZN15004:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 44 | 45 | 0.008272 | 0.000184 | N
26-03-19 | 16:04 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 131 | 0.045844 | 0.00035 | N
26-03-19 | 16:13 | ZN2568:PA27 | URBAN | Other | Other | 1 | 69 | 4.7e-05 | 1e-06 | N
26-03-19 | 14:54 | ZN36200:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 201 | 0.005034 | 2.5e-05 | N
26-03-19 | 16:15 | 520:48172 | SHORT RURAL | Asset Failure | HV | 2 | 385 | 0.003217 | 8e-06 | N
26-03-19 | 17:13 | ZN262:PA15 | URBAN | Asset Failure | HV | 2,418 | 55 | 0.090601 | 0.001637 | N
26-03-19 | 17:13 | ZN262:PA39 | URBAN | Asset Failure | HV | 1 | 54 | 3.7e-05 | 1e-06 | N
26-03-19 | 19:57 | 206:34434 | URBAN | Asset Failure | LV | 14 | 423 | 0.004006 | 9e-06 | N
26-03-19 | 23:54 | ZN12620:PA11 | SHORT RURAL | Animal | Animal impact | 80 | 411 | 0.13736 | 0.000334 | N
27-03-19 | 03:35 | 233:82819 | SHORT RURAL | Asset Failure | LV | 13 | 304 | 0.016522 | 5.4e-05 | N
27-03-19 | 03:39 | ZN12600:PA3 | URBAN | Animal | Animal impact | 1,730 | 59 | 0.068935 | 0.001171 | N
27-03-19 | 09:41 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 94 | 0.000393 | 4e-06 | N
27-03-19 | 10:40 | 222:33600 | URBAN | Other | Other | 1 | 87 | 5.9e-05 | 1e-06 | N
27-03-19 | 10:58 | ZN14144:PA2 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 77 | 0.000322 | 4e-06 | N
27-03-19 | 11:47 | 811:74234 | SHORT RURAL | Asset Failure | HV | 2 | 173 | 0.001446 | 8e-06 | N
27-03-19 | 12:30 | ZN10995:PA8 | URBAN | Other | Other - Arcing | 1 | 1,334 | 0.000903 | 1e-06 | N
27-03-19 | 15:30 | ZN15012:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 85 | 0.00023 | 3e-06 | N
27-03-19 | 16:28 | 811:74234 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 74 | 0.000309 | 4e-06 | N
27-03-19 | 16:29 | ZN15004:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 181 | 0.000122 | 1e-06 | N
27-03-19 | 16:29 | ZN9700:PA23 | URBAN | Other | Other - Self Clearing Trigger | 36 | 201 | 0.004898 | 2.4e-05 | N
27-03-19 | 16:42 | 222:33596 | URBAN | Weather |  | 1 | 305 | 0.000206 | 1e-06 | N
27-03-19 | 17:19 | 810:74050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 96 | 0.000401 | 4e-06 | N
27-03-19 | 17:19 | ZN116:PA12 | URBAN | Third Party | Other | 1 | 759 | 0.000514 | 1e-06 | N
27-03-19 | 19:00 | ZN1285:PA31 | URBAN | Third Party | Vehicle impact | 33 | 60 | 0.00134 | 2.2e-05 | N
27-03-19 | 19:00 | ZN1285:PA33 | URBAN | Third Party | Vehicle impact | 27 | 60 | 0.001097 | 1.8e-05 | N
27-03-19 | 22:27 | ZN1193:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,518 | 69 | 0.070899 | 0.001028 | N
28-03-19 | 01:27 | 232:11457 | SHORT RURAL | Asset Failure | Distribution substation | 12 | 300 | 0.015031 | 5e-05 | N
28-03-19 | 04:17 | ZN340:PA3 | URBAN | Third Party | Vehicle impact | 1 | 163 | 0.00011 | 1e-06 | N
28-03-19 | 04:40 | ZN35370:PA8 | SHORT RURAL | Third Party | Other | 76 | 170 | 0.05384 | 0.000318 | N
28-03-19 | 07:59 | 807:74184 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 131 | 0.001095 | 8e-06 | N
28-03-19 | 08:04 | ZN10998:PA31 | URBAN | Third Party | Vehicle impact | 1 | 212 | 0.000144 | 1e-06 | N
28-03-19 | 09:05 | ZN12640:PA13 | SHORT RURAL | Other | Other | 1 | 80 | 0.000335 | 4e-06 | N
28-03-19 | 09:20 | ZN931:PA31 | URBAN | Other | Other - Arcing | 1 | 1,331 | 0.000901 | 1e-06 | N
28-03-19 | 10:20 | 522:83123 | SHORT RURAL | Other | Other | 1 | 160 | 0.000668 | 4e-06 | N
27-03-19 | 13:30 | ZN12570:PA24 | SHORT RURAL | Network business | Network error | 43 | 40 | 0.007186 | 0.00018 | N
23-03-19 | 13:00 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 305 | 0.21366 | 0.000701 | N
23-03-19 | 02:21 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 1,558 | 0.026035 | 1.7e-05 | N
23-03-19 | 07:00 | 807:74183 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 465 | 0.013598 | 2.9e-05 | N
23-03-19 | 12:00 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 135 | 0.047285 | 0.00035 | N
28-03-19 | 12:22 | ZN12600:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 97 | 6.6e-05 | 1e-06 | N
24-03-19 | 03:24 | 801:74123 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 361 | 0.001508 | 4e-06 | N
24-03-19 | 10:00 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 390 | 0.1366 | 0.00035 | N
24-03-19 | 11:00 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 165 | 0.000689 | 4e-06 | N
28-03-19 | 07:30 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 5 | 665 | 0.013891 | 2.1e-05 | N
28-03-19 | 15:42 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 213 | 0.00178 | 8e-06 | N
28-03-19 | 16:03 | ZN129:PA41 | URBAN | Third Party | Vehicle impact | 44 | 127 | 0.003777 | 3e-05 | N
28-03-19 | 18:03 | ZN10998:PA9 | URBAN | Third Party | Vehicle impact | 26 | 487 | 0.008563 | 1.8e-05 | N
28-03-19 | 18:24 | ZN2602:PA36 | URBAN | Asset Failure | LV | 1 | 996 | 0.000674 | 1e-06 | N
28-03-19 | 18:51 | ZN965:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,169 | 0.000791 | 1e-06 | N
28-03-19 | 19:00 | ZN9245:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 120 | 0.002437 | 2e-05 | N
28-03-19 | 21:07 | 511:29878 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 92 | 0.000386 | 4e-06 | N
28-03-19 | 21:56 | 806:82662 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 24 | 0.000201 | 8e-06 | N
28-03-19 | 22:02 | ZN195:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 34 | 98 | 0.013921 | 0.000142 | N
29-03-19 | 00:12 | ZN3672:PA42 | URBAN | Third Party | Other | 18 | 358 | 0.00436 | 1.2e-05 | N
29-03-19 | 07:56 | 508:82578 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 64 | 0.001604 | 2.5e-05 | N
29-03-19 | 08:09 | ZN15010:PA30 | URBAN | Third Party | Vehicle impact | 30 | 121 | 0.00245 | 2e-05 | N
29-03-19 | 08:58 | 522:83132 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 132 | 0.00055 | 4e-06 | N
29-03-19 | 09:22 | ZN3672:PA13 | URBAN | Asset Failure | LV | 123 | 384 | 0.031951 | 8.3e-05 | N
29-03-19 | 12:57 | 508:82579 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 272 | 0.001138 | 4e-06 | N
29-03-19 | 13:17 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 123 | 0.000513 | 4e-06 | N
29-03-19 | 13:40 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 184 | 0.000771 | 4e-06 | N
26-03-19 | 15:40 | 812:19072 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 50 | 0.000209 | 4e-06 | N
30-03-19 | 09:15 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 152 | 0.004457 | 2.9e-05 | N
29-03-19 | 15:09 | 256:80644 | URBAN | Animal | Animal nesting/burrowing, etc and other | 90 | 47 | 0.002886 | 6.1e-05 | N
26-03-19 | 12:30 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 40 | 0.014011 | 0.00035 | N
26-03-19 | 18:04 | 520:48172 | SHORT RURAL | Network business | Switching and protection error | 32 | 5 | 0.000668 | 0.000134 | N
27-03-19 | 18:00 | 520:48172 | SHORT RURAL | Other | Other | 1 | 35 | 0.000146 | 4e-06 | N
29-03-19 | 16:05 | 515:35192 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 65 | 0.000543 | 8e-06 | N
29-03-19 | 16:08 | 502:48010 | SHORT RURAL | Other | Other | 1 | 42 | 0.000173 | 4e-06 | N
29-03-19 | 16:22 | 524:33570 | SHORT RURAL | Third Party | Vehicle impact | 1 | 347 | 0.001451 | 4e-06 | N
28-03-19 | 12:33 | 402:H786 | URBAN | Asset Failure | Subtransmission | 2 | 320 | 0.000433 | 1e-06 | N
29-03-19 | 16:54 | ZN262:PA26 | URBAN | Other | Other | 1 | 70 | 4.7e-05 | 1e-06 | N
28-03-19 | 10:10 | 520:48172 | SHORT RURAL | Other | Other | 1 | 170 | 0.00071 | 4e-06 | N
28-03-19 | 12:45 | 516:48067 | SHORT RURAL | Other | Other | 1 | 25 | 0.000104 | 4e-06 | N
29-03-19 | 18:38 | ZN3672:PA36 | URBAN | Other | Other - Arcing | 1 | 174 | 0.000118 | 1e-06 | N
29-03-19 | 18:57 | 221:11898 | SHORT RURAL | Other | Other | 1 | 150 | 0.000628 | 4e-06 | N
30-03-19 | 00:40 | ZN9245:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 54 | 79 | 0.002901 | 3.7e-05 | N
30-03-19 | 03:17 | ZN9550:PA36 | URBAN | Other | Other - Self Clearing Trigger | 771 | 77 | 0.040197 | 0.000522 | N
30-03-19 | 03:23 | ZN15006:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 889 | 0.000602 | 1e-06 | N
30-03-19 | 03:58 | ZN9700:PA17 | URBAN | Weather |  | 2,273 | 160 | 0.24543 | 0.001539 | N
30-03-19 | 07:32 | 232:11455 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 100 | 0.000418 | 4e-06 | N
30-03-19 | 12:15 | ZN847:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 60 | 260 | 0.01056 | 4.1e-05 | N
30-03-19 | 07:51 | ZN262:PA7 | URBAN | Asset Failure | LV | 1 | 639 | 0.000433 | 1e-06 | N
30-03-19 | 08:29 | ZN15006:PA2 | URBAN | Vegetation | Vegetation Grow In | 1 | 486 | 0.000329 | 1e-06 | N
30-03-19 | 08:58 | ZN847:PA2 | URBAN | Other | Other | 1 | 558 | 0.000378 | 1e-06 | N
30-03-19 | 16:20 | 238:34141 | SHORT RURAL | Asset Failure | HV | 23 | 195 | 0.018736 | 9.6e-05 | N
30-03-19 | 09:32 | ZN10999:PA7 | URBAN | Other | Other - Arcing | 13 | 453 | 0.003984 | 9e-06 | N
30-03-19 | 10:41 | ZN10995:PA2 | URBAN | Third Party | Other | 1 | 451 | 0.000305 | 1e-06 | N
30-03-19 | 11:19 | ZN12600:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 1,093 | 0.004566 | 4e-06 | N
30-03-19 | 12:33 | ZN35600:PA9 | URBAN | Asset Failure | LV | 1 | 295 | 0.0002 | 1e-06 | N
30-03-19 | 14:05 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 16 | 100 | 0.006684 | 6.7e-05 | N
30-03-19 | 14:07 | 532:83293 | URBAN | Third Party | Vehicle impact | 67 | 348 | 0.015784 | 4.5e-05 | N
30-03-19 | 15:08 | ZN4545:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 642 | 0.000435 | 1e-06 | N
30-03-19 | 15:16 | ZN965:PA33 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 764 | 0.000517 | 1e-06 | N
30-03-19 | 16:56 | ZN1673:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 45 | 213 | 0.006489 | 3e-05 | N
30-03-19 | 15:34 | ZN4545:PA40 | URBAN | Other | Other | 1 | 975 | 0.00066 | 1e-06 | N
30-03-19 | 15:37 | ZN3425:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 568 | 0.000384 | 1e-06 | N
30-03-19 | 15:42 | ZN1673:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 675 | 0.000457 | 1e-06 | N
30-03-19 | 15:45 | ZN35370:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 604 | 0.002522 | 4e-06 | N
30-03-19 | 15:45 | ZN262:PA15 | URBAN | Vegetation | Vegetation Grow In | 1 | 558 | 0.000378 | 1e-06 | N
30-03-19 | 15:47 | ZN195:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 66 | 4.5e-05 | 1e-06 | N
30-03-19 | 15:59 | ZN3154:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 476 | 0.000322 | 1e-06 | N
31-03-19 | 10:45 | ZN847:PA48 | URBAN | Vegetation | Vegetation Blow/Fall In | 9 | 270 | 0.001645 | 6e-06 | N
30-03-19 | 15:57 | ZN35370:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 142 | 196 | 0.11653 | 0.000593 | N
30-03-19 | 16:08 | ZN2635:PA58 | URBAN | Vegetation | Vegetation Blow/Fall In | 37 | 52 | 0.001302 | 2.5e-05 | N
30-03-19 | 16:11 | ZN35370:PA4 | SHORT RURAL | Other | Other | 1 | 116 | 0.000485 | 4e-06 | N
30-03-19 | 16:13 | ZN2635:PA52 | URBAN | Other | Other | 1 | 345 | 0.000234 | 1e-06 | N
30-03-19 | 16:11 | ZN15013:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 874 | 158 | 0.57739 | 0.003651 | N
30-03-19 | 16:23 | ZN15005:PA8 | URBAN | Other | Other - Self Clearing Trigger | 30 | 172 | 0.003492 | 2e-05 | N
30-03-19 | 17:26 | ZN847:PA46 | URBAN | Other | Other - Self Clearing Trigger | 46 | 874 | 0.027215 | 3.1e-05 | N
30-03-19 | 16:36 | ZN35500:PA28 | URBAN | Other | Other - Self Clearing Trigger | 29 | 834 | 0.016372 | 2e-05 | N
30-03-19 | 16:29 | ZN10995:PA8 | URBAN | Other | Other - Arcing | 1 | 117 | 7.9e-05 | 1e-06 | N
30-03-19 | 16:31 | ZN15008:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 61 | 228 | 0.009422 | 4.1e-05 | N
30-03-19 | 17:32 | ZN80:PA37 | URBAN | Vegetation | Vegetation Blow/Fall In | 49 | 372 | 0.012341 | 3.3e-05 | N
30-03-19 | 16:35 | ZN384:PA76 | URBAN | Weather |  | 97 | 64 | 0.004204 | 6.6e-05 | N
30-03-19 | 16:44 | ZN384:PA76 | URBAN | Weather |  | 46 | 292 | 0.009101 | 3.1e-05 | N
30-03-19 | 16:49 | ZN10997:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 79 | 191 | 0.010214 | 5.3e-05 | N
30-03-19 | 16:53 | ZN80:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 56 | 847 | 0.03209 | 3.8e-05 | N
30-03-19 | 16:54 | ZN384:PA70 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 275 | 0.005222 | 1.9e-05 | N
30-03-19 | 16:55 | ZN2635:PA59 | URBAN | Vegetation | Vegetation Blow/Fall In | 8 | 485 | 0.002627 | 5e-06 | N
30-03-19 | 17:04 | ZN2635:PA46 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 205 | 0.006391 | 3.1e-05 | N
30-03-19 | 17:11 | ZN3155:PA22 | URBAN | Third Party | Other | 1 | 139 | 9.4e-05 | 1e-06 | N
30-03-19 | 16:04 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 2,936 | 0.001987 | 1e-06 | N
30-03-19 | 17:16 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 69 | 0.000577 | 8e-06 | N
30-03-19 | 13:30 | 810:74054 | LONG RURAL | Asset Failure | HV | 19 | 655 | 4.3608 | 0.006655 | N
30-03-19 | 17:19 | ZN12650:PA1 | SHORT RURAL | Weather |  | 1,714 | 96 | 0.68644 | 0.00716 | N
30-03-19 | 17:23 | ZN2568:PA27 | URBAN | Other | Other - Arcing | 101 | 685 | 0.046808 | 6.8e-05 | N
30-03-19 | 18:30 | ZN1673:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 109 | 1,300 | 0.095922 | 7.4e-05 | N
30-03-19 | 17:30 | ZN12610:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 180 | 0.000122 | 1e-06 | N
30-03-19 | 17:42 | ZN36200:PA8 | SHORT RURAL | Weather |  | 10 | 173 | 0.007227 | 4.2e-05 | N
30-03-19 | 19:00 | 512:83743 | SHORT RURAL | Asset Failure | HV | 26 | 205 | 0.022266 | 0.000109 | N
30-03-19 | 18:11 | 813:89062 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 88 | 0.000367 | 4e-06 | N
30-03-19 | 18:19 | 508:82578 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 111 | 0.002782 | 2.5e-05 | N
30-03-19 | 18:41 | 522:83132 | SHORT RURAL | Asset Failure | HV | 95 | 143 | 0.056836 | 0.000397 | N
30-03-19 | 18:35 | ZN1068:PA26 | URBAN | Asset Failure | LV | 1 | 389 | 0.000263 | 1e-06 | N
30-03-19 | 18:38 | ZN965:PA24 | URBAN | Other | Other - Self Clearing Trigger | 35 | 292 | 0.006918 | 2.4e-05 | N
30-03-19 | 19:01 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,479 | 129 | 0.79956 | 0.006179 | N
30-03-19 | 19:04 | ZN965:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,021 | 264 | 0.18234 | 0.000691 | N
30-03-19 | 19:11 | ZN1673:PA6 | URBAN | Other | Other | 1 | 448 | 0.000303 | 1e-06 | N
30-03-19 | 19:11 | ZN3154:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 19 | 304 | 0.003905 | 1.3e-05 | N
30-03-19 | 19:12 | ZN2400:PA15 | SHORT RURAL | Other | Other | 68 | 437 | 0.1242 | 0.000284 | N
30-03-19 | 19:40 | 222:33601 | SHORT RURAL | Other | Other | 1 | 44 | 0.000182 | 4e-06 | N
30-03-19 | 20:15 | ZN1068:PA26 | URBAN | Asset Failure | LV | 1 | 290 | 0.000196 | 1e-06 | N
30-03-19 | 20:35 | ZN384:PA76 | URBAN | Weather |  | 97 | 61 | 0.003988 | 6.6e-05 | N
30-03-19 | 20:39 | ZN965:PA33 | URBAN | Other | Other | 1,299 | 16 | 0.013837 | 0.000879 | N
30-03-19 | 20:45 | 507:80932 | SHORT RURAL | Weather |  | 5 | 797 | 0.016648 | 2.1e-05 | N
30-03-19 | 21:30 | 507:80925 | SHORT RURAL | Network business | Network error | 72 | 94 | 0.028319 | 0.000301 | N
31-03-19 | 01:50 | ZN2635:PA52 | URBAN | Asset Failure | LV | 94 | 810 | 0.051542 | 6.4e-05 | N
31-03-19 | 04:28 | 523:33509 | URBAN | Weather |  | 47 | 222 | 0.007063 | 3.2e-05 | N
31-03-19 | 06:29 | ZN188:PA33 | URBAN | Asset Failure | LV | 30 | 318 | 0.006465 | 2e-05 | N
31-03-19 | 06:56 | ZN195:PA29 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 508 | 0.000344 | 1e-06 | N
31-03-19 | 08:29 | ZN1673:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 661 | 0.000447 | 1e-06 | N
31-03-19 | 08:57 | ZN1648:PA19 | URBAN | Asset Failure | LV | 1 | 444 | 0.0003 | 1e-06 | N
31-03-19 | 09:08 | ZN1673:PA14 | URBAN | Other | Other | 1 | 37 | 2.5e-05 | 1e-06 | N
31-03-19 | 09:10 | ZN12570:PA33 | SHORT RURAL | Other | Other | 1 | 21 | 8.8e-05 | 4e-06 | N
31-03-19 | 09:24 | ZN36200:PA8 | SHORT RURAL | Other | Other | 1 | 89 | 0.000372 | 4e-06 | N
31-03-19 | 09:47 | ZN1068:PA26 | URBAN | Asset Failure | LV | 1 | 320 | 0.000216 | 1e-06 | N
31-03-19 | 10:37 | ZN15005:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 301 | 0.007947 | 2.6e-05 | N
31-03-19 | 11:08 | ZN847:PA48 | URBAN | Other | Other - Arcing | 1 | 112 | 7.6e-05 | 1e-06 | N
31-03-19 | 10:49 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 430 | 0.000291 | 1e-06 | N
31-03-19 | 10:51 | 807:74184 | SHORT RURAL | Weather |  | 3 | 69 | 0.000865 | 1.3e-05 | N
31-03-19 | 11:36 | ZN4545:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 670 | 0.000453 | 1e-06 | N
31-03-19 | 13:12 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 83 | 0.029072 | 0.00035 | N
31-03-19 | 10:45 | ZN847:PA48 | URBAN | Vegetation | Vegetation Blow/Fall In | 22 | 270 | 0.004021 | 1.5e-05 | N
31-03-19 | 14:35 | 232:11454 | SHORT RURAL | Other | Other - Arcing | 1 | 25 | 0.000102 | 4e-06 | N
31-03-19 | 14:46 | ZN9118:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 362 | 0.000245 | 1e-06 | N
31-03-19 | 14:53 | ZN1068:PA26 | URBAN | Asset Failure | LV | 1 | 69 | 4.6e-05 | 1e-06 | N
31-03-19 | 15:26 | ZN12630:PA10 | SHORT RURAL | Asset Failure | LV | 9 | 419 | 0.015754 | 3.8e-05 | N
31-03-19 | 15:32 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 133 | 0.000556 | 4e-06 | N
31-03-19 | 22:00 | ZN35370:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 16 | 30 | 0.002005 | 6.7e-05 | N
31-03-19 | 16:24 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 103 | 7e-05 | 1e-06 | N
31-03-19 | 16:54 | ZN3672:PA37 | URBAN | Other | Other | 1 | 62 | 4.2e-05 | 1e-06 | N
31-03-19 | 17:34 | ZN9245:PA6 | URBAN | Other | Other - Arcing | 1 | 316 | 0.000214 | 1e-06 | N
31-03-19 | 18:44 | ZN2568:PA21 | URBAN | Asset Failure | LV | 1 | 325 | 0.00022 | 1e-06 | N
31-03-19 | 18:45 | ZN2568:PA21 | URBAN | Asset Failure | LV | 1 | 325 | 0.00022 | 1e-06 | N
31-03-19 | 19:13 | 532:83300 | URBAN | Asset Failure | LV | 1 | 376 | 0.000255 | 1e-06 | N
31-03-19 | 20:34 | ZN80:PA27 | URBAN | Other | Other - Arcing | 1 | 534 | 0.000362 | 1e-06 | N
31-03-19 | 21:17 | ZN9700:PA23 | URBAN | Animal | Animal impact | 80 | 58 | 0.003141 | 5.4e-05 | N
01-04-19 | 01:08 | ZN15011:PA10 | URBAN | Other | Other - Self Clearing Trigger | 66 | 75 | 0.003364 | 4.5e-05 | N
01-04-19 | 02:25 | ZN12640:PA4 | URBAN | Animal | Animal impact | 105 | 70 | 0.004974 | 7.1e-05 | N
01-04-19 | 04:31 | ZN12620:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,115 | 85 | 0.39397 | 0.004656 | N
01-04-19 | 07:49 | ZN12600:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 805 | 0.003363 | 4e-06 | N
01-04-19 | 07:36 | ZN340:PA3 | URBAN | Other | Other - Arcing | 30 | 84 | 0.001698 | 2e-05 | N
01-04-19 | 10:14 | ZN262:PA8 | URBAN | Asset Failure | LV | 1 | 196 | 0.000132 | 1e-06 | N
01-04-19 | 11:25 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 80 | 0.028001 | 0.00035 | N
01-04-19 | 13:37 | ZN3425:PA44 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 128 | 0.003292 | 2.6e-05 | N
30-03-19 | 08:58 | ZN847:PA2 | URBAN | Asset Failure | LV | 55 | 362 | 0.013478 | 3.7e-05 | N
30-03-19 | 16:25 | ZN3154:PA24 | URBAN | Asset Failure | LV | 6 | 395 | 0.001604 | 4e-06 | N
31-03-19 | 01:40 | ZN3154:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 33 | 25 | 0.000558 | 2.2e-05 | N
30-03-19 | 15:55 | ZN12570:PA34 | SHORT RURAL | Weather |  | 849 | 3 | 0.01064 | 0.003547 | N
01-04-19 | 15:19 | ZN2602:PA30 | URBAN | Asset Failure | LV | 2 | 494 | 0.000668 | 1e-06 | N
01-04-19 | 16:46 | 210:83466 | URBAN | Other | Other | 1 | 159 | 0.000107 | 1e-06 | N
30-04-19 | 10:18 | ZN15008:PA5 | URBAN | Weather |  | 1,308 | 92 | 0.081023 | 0.000885 | N
01-04-19 | 22:54 | ZN1285:PA24 | URBAN | Asset Failure | LV | 63 | 245 | 0.01046 | 4.3e-05 | N
02-04-19 | 00:45 | ZN36800:PA46 | URBAN | Asset Failure | LV | 89 | 40 | 0.002409 | 6e-05 | N
02-04-19 | 00:35 | ZN15001:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 6 | 55 | 0.000222 | 4e-06 | N
02-04-19 | 04:47 | 265:81648 | SHORT RURAL | Asset Failure | LV | 1 | 392 | 0.001636 | 4e-06 | N
02-04-19 | 06:09 | 230:81440 | URBAN | Vegetation | Vegetation Blow/Fall In | 48 | 361 | 0.011728 | 3.2e-05 | N
02-04-19 | 06:28 | 507:80925 | SHORT RURAL | Third Party | Other | 1 | 542 | 0.002263 | 4e-06 | N
02-04-19 | 06:36 | ZN14143:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,327 | 65 | 0.36043 | 0.005541 | N
29-03-19 | 19:00 | 508:82579 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 125 | 0.000522 | 4e-06 | N
02-04-19 | 08:24 | ZN12600:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 856 | 40 | 0.14297 | 0.003574 | N
02-04-19 | 08:32 | 256:80652 | URBAN | Asset Failure | HV | 167 | 153 | 0.017303 | 0.000113 | N
01-04-19 | 12:00 | ZN1285:PA31 | URBAN | Asset Failure | LV | 5 | 60 | 0.000203 | 3e-06 | N
02-04-19 | 10:58 | ZN9900:PA1 | URBAN | Asset Failure | HV | 1,229 | 80 | 0.066465 | 0.000832 | N
02-04-19 | 10:58 | ZN9900:PA8 | URBAN | Asset Failure | HV | 125 | 71 | 0.006007 | 8.5e-05 | N
02-04-19 | 12:35 | 220:8692 | URBAN | Animal | Animal impact | 879 | 115 | 0.06848 | 0.000595 | N
02-04-19 | 15:03 | ZN342:PA17 | URBAN | Asset Failure | LV | 1 | 1,197 | 0.00081 | 1e-06 | N
02-04-19 | 15:12 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 88 | 0.000735 | 8e-06 | N
02-04-19 | 16:24 | 508:82578 | SHORT RURAL | Asset Failure | HV | 96 | 86 | 0.034603 | 0.000401 | N
02-04-19 | 17:13 | ZN9700:PA15 | URBAN | Other | Other - Arcing | 1 | 286 | 0.000194 | 1e-06 | N
02-04-19 | 17:27 | ZN14144:PA1 | URBAN | Asset Failure | LV | 1 | 277 | 0.000188 | 1e-06 | N
02-04-19 | 18:58 | ZN129:PA41 | URBAN | Other | Other | 29 | 111 | 0.002169 | 2e-05 | N
02-04-19 | 19:24 | 801:74120 | SHORT RURAL | Other | Other | 1 | 215 | 0.000898 | 4e-06 | N
02-04-19 | 20:57 | ZN15012:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 85 | 0.00023 | 3e-06 | N
03-04-19 | 01:35 | ZN14144:PA2 | SHORT RURAL | Animal | Animal impact | 16 | 427 | 0.028496 | 6.7e-05 | N
03-04-19 | 06:07 | ZN690:PA24 | SHORT RURAL | Third Party | Vehicle impact | 3 | 593 | 0.007428 | 1.3e-05 | N
03-04-19 | 07:42 | ZN15002:PA6 | URBAN | Asset Failure | LV | 67 | 180 | 0.008162 | 4.5e-05 | N
03-04-19 | 08:37 | 206:34441 | URBAN | Other | Other | 1 | 164 | 0.000111 | 1e-06 | N
03-04-19 | 09:34 | ZN15012:PA6 | URBAN | Asset Failure | LV | 1 | 266 | 0.00018 | 1e-06 | N
03-04-19 | 10:18 | 206:34441 | URBAN | Other | Other | 1 | 63 | 4.3e-05 | 1e-06 | N
03-04-19 | 10:21 | 224:80341 | URBAN | Other | Other | 1 | 181 | 0.000122 | 1e-06 | N
03-04-19 | 12:38 | 258:80785 | URBAN | Vegetation | Vegetation Grow In | 57 | 112 | 0.004321 | 3.9e-05 | N
01-04-19 | 10:46 | ZN15005:PA12 | URBAN | Network business | Network error | 39 | 89 | 0.002349 | 2.6e-05 | N
03-04-19 | 14:39 | ZN2196:PA17 | URBAN | Other | Other - Self Clearing Trigger | 15 | 225 | 0.002285 | 1e-05 | N
03-04-19 | 14:52 | 258:80785 | URBAN | Other | Other | 1 | 37 | 2.5e-05 | 1e-06 | N
03-04-19 | 15:48 | ZN1193:PA28 | URBAN | Third Party | Vehicle impact | 23 | 177 | 0.002755 | 1.6e-05 | N
03-04-19 | 16:28 | ZN35555:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 35 | 312 | 0.045598 | 0.000146 | N
03-04-19 | 18:08 | ZN10993:PA26 | URBAN | Other | Other - Arcing | 1 | 215 | 0.000145 | 1e-06 | N
03-04-19 | 18:59 | ZN36100:PA19 | URBAN | Third Party | Vehicle impact | 96 | 271 | 0.017608 | 6.5e-05 | N
03-04-19 | 23:20 | ZN630:PA27 | URBAN | Third Party | Vehicle impact | 6 | 555 | 0.002254 | 4e-06 | N
04-04-19 | 06:38 | ZN2835:PA22 | URBAN | Asset Failure | LV | 28 | 352 | 0.006671 | 1.9e-05 | N
04-04-19 | 10:02 | 239:82129 | SHORT RURAL | Other | Other | 118 | 160 | 0.078838 | 0.000493 | N
04-04-19 | 09:12 | 239:82129 | SHORT RURAL | Asset Failure | HV | 533 | 113 | 0.25175 | 0.002226 | N
04-04-19 | 09:49 | 523:33501 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 131 | 0.001094 | 8e-06 | N
04-04-19 | 10:28 | ZN2196:PA10 | URBAN | Other | Other | 1 | 202 | 0.000137 | 1e-06 | N
04-04-19 | 10:43 | ZN2196:PA17 | URBAN | Asset Failure | HV | 15 | 182 | 0.001848 | 1e-05 | N
04-04-19 | 10:54 | ZN35600:PA3 | URBAN | Third Party | Vehicle impact | 5 | 486 | 0.001645 | 3e-06 | N
04-04-19 | 13:15 | ZN15004:PA5 | URBAN | Asset Failure | LV | 1 | 345 | 0.000233 | 1e-06 | N
04-04-19 | 13:32 | ZN180:PA23 | URBAN | Other | Other - Self Clearing Trigger | 8 | 133 | 0.00072 | 5e-06 | N
04-04-19 | 18:37 | ZN9550:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 541 | 0.010253 | 1.9e-05 | N
04-04-19 | 20:12 | ZN965:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 5 | 1,908 | 0.006457 | 3e-06 | N
04-04-19 | 20:17 | ZN180:PA23 | URBAN | Asset Failure | LV | 46 | 33 | 0.001026 | 3.1e-05 | N
04-04-19 | 20:20 | ZN195:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,270 | 0.000859 | 1e-06 | N
04-04-19 | 21:03 | ZN1193:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 296 | 0.0002 | 1e-06 | N
04-04-19 | 21:05 | ZN9550:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 425 | 0.010931 | 2.6e-05 | N
04-04-19 | 21:04 | ZN847:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 22 | 156 | 0.002323 | 1.5e-05 | N
04-04-19 | 21:04 | ZN847:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 786 | 0.018088 | 2.3e-05 | N
04-04-19 | 23:45 | ZN931:PA13 | URBAN | Other | Other | 123 | 9 | 0.000782 | 8.3e-05 | N
05-04-19 | 06:50 | ZN195:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 1,075 | 0.029104 | 2.7e-05 | N
05-04-19 | 06:54 | ZN965:PA47 | URBAN | Other | Other - Self Clearing Trigger | 40 | 136 | 0.003675 | 2.7e-05 | N
05-04-19 | 07:50 | 264:81232 | SHORT RURAL | Third Party | Vehicle impact | 2 | 110 | 0.000919 | 8e-06 | N
05-04-19 | 09:03 | ZN12600:PA13 | SHORT RURAL | Third Party | Dig-in | 1 | 86 | 0.000359 | 4e-06 | N
05-04-19 | 09:17 | ZN342:PA28 | URBAN | Third Party | Dig-in | 1,290 | 97 | 0.084425 | 0.000873 | N
05-04-19 | 10:13 | 213:33771 | URBAN | Asset Failure | HV | 207 | 168 | 0.02356 | 0.00014 | N
05-04-19 | 10:18 | 213:33771 | URBAN | Other | Other | 1 | 72 | 4.9e-05 | 1e-06 | N
05-04-19 | 11:24 | ZN3922:PA13 | SHORT RURAL | Asset Failure | LV | 162 | 134 | 0.090457 | 0.000676 | N
05-04-19 | 11:24 | ZN3922:PA29 | URBAN | Asset Failure | LV | 1 | 133 | 9e-05 | 1e-06 | N
05-04-19 | 12:10 | ZN14144:PA8 | URBAN | Asset Failure | Distribution substation | 40 | 160 | 0.004332 | 2.7e-05 | N
05-04-19 | 13:47 | ZN9118:PA8 | URBAN | Other | Other - Self Clearing Trigger | 16 | 243 | 0.002632 | 1.1e-05 | N
05-04-19 | 14:06 | ZN2196:PA25 | URBAN | Third Party | Vehicle impact | 68 | 104 | 0.004787 | 4.6e-05 | N
05-04-19 | 14:30 | 214:8666 | URBAN | Asset Failure | LV | 1 | 255 | 0.000172 | 1e-06 | N
05-04-19 | 15:13 | ZN9118:PA26 | URBAN | Asset Failure | LV | 49 | 197 | 0.006534 | 3.3e-05 | N
05-04-19 | 17:27 | ZN965:PA47 | URBAN | Third Party | Vehicle impact | 1 | 527 | 0.000357 | 1e-06 | N
05-04-19 | 20:53 | ZN10991:PA8 | URBAN | Asset Failure | LV | 1 | 164 | 0.000111 | 1e-06 | N
06-04-19 | 00:26 | ZN116:PA29 | URBAN | Third Party | Vehicle impact | 59 | 799 | 0.031907 | 4e-05 | N
06-04-19 | 07:47 | 508:82578 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 208 | 0.005211 | 2.5e-05 | N
06-04-19 | 08:04 | ZN9118:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 565 | 0.000383 | 1e-06 | N
07-04-19 | 13:10 | ZN3922:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 74 | 14 | 0.004326 | 0.000309 | N
10-04-19 | 13:18 | 515:35198 | SHORT RURAL | Asset Failure | HV | 5 | 27 | 0.000564 | 2.1e-05 | N
06-04-19 | 14:37 | 229:34983 | SHORT RURAL | Asset Failure | LV | 1 | 306 | 0.001278 | 4e-06 | N
06-04-19 | 15:10 | 810:74054 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 135 | 0.047241 | 0.00035 | N
06-04-19 | 17:55 | ZN14892:PA13 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 26 | 60 | 0.006514 | 0.000109 | N
06-04-19 | 16:38 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 261 | 0.000177 | 1e-06 | N
06-04-19 | 22:50 | ZN3472:PA30 | URBAN | Asset Failure | HV | 2,035 | 65 | 0.088909 | 0.001377 | N
06-04-19 | 22:05 | ZN2635:PA58 | URBAN | Vegetation | Vegetation Blow/Fall In | 55 | 20 | 0.000745 | 3.7e-05 | N
06-04-19 | 20:19 | ZN12660:PA14 | SHORT RURAL | Asset Failure | LV | 1 | 939 | 0.003921 | 4e-06 | N
06-04-19 | 21:37 | 261:81879 | URBAN | Other | Other | 1 | 107 | 7.3e-05 | 1e-06 | N
07-04-19 | 00:18 | 812:19072 | SHORT RURAL | Asset Failure | HV | 40 | 119 | 0.019919 | 0.000167 | N
07-04-19 | 05:14 | 239:82129 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 256 | 0.001069 | 4e-06 | N
07-04-19 | 07:17 | 222:33601 | SHORT RURAL | Other | Other | 1 | 67 | 0.000282 | 4e-06 | N
07-04-19 | 12:19 | ZN9118:PA13 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 26 | 0.000405 | 1.6e-05 | N
07-04-19 | 09:00 | ZN2310:PA25 | URBAN | Asset Failure | LV | 77 | 75 | 0.003909 | 5.2e-05 | N
07-04-19 | 09:50 | 232:33413 | SHORT RURAL | Asset Failure | LV | 80 | 141 | 0.047193 | 0.000334 | N
07-04-19 | 15:40 | ZN10991:PA12 | URBAN | Asset Failure | LV | 22 | 70 | 0.001042 | 1.5e-05 | N
07-04-19 | 13:38 | ZN15013:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 201 | 0.000839 | 4e-06 | N
07-04-19 | 16:31 | 810:74054 | LONG RURAL | Asset Failure | HV | 180 | 10 | 0.65453 | 0.063003 | N
07-04-19 | 15:45 | ZN10991:PA12 | URBAN | Other | Other | 24 | 65 | 0.001056 | 1.6e-05 | N
07-04-19 | 20:50 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 182 | 0.12741 | 0.0007 | N
07-04-19 | 17:46 | ZN2466:PA45 | URBAN | Asset Failure | LV | 53 | 218 | 0.007824 | 3.6e-05 | N
07-04-19 | 22:20 | 812:19072 | SHORT RURAL | Asset Failure | LV | 8 | 30 | 0.001002 | 3.3e-05 | N
07-04-19 | 18:20 | 520:48172 | SHORT RURAL | Asset Failure | LV | 2 | 150 | 0.001253 | 8e-06 | N
07-04-19 | 18:55 | ZN847:PA22 | URBAN | Network business | Network error | 58 | 155 | 0.006085 | 3.9e-05 | N
07-04-19 | 16:55 | 801:74121 | LONG RURAL | Asset Failure | LV | 1 | 305 | 0.10661 | 0.00035 | N
07-04-19 | 22:04 | ZN12620:PA2 | SHORT RURAL | Other | Other | 1 | 85 | 0.000356 | 4e-06 | N
08-04-19 | 00:49 | 224:80326 | URBAN | Other | Other - Self Clearing Trigger | 80 | 116 | 0.006281 | 5.4e-05 | N
08-04-19 | 01:16 | ZN9037:PA9 | URBAN | Other | Other - Arcing | 2 | 739 | 0.001 | 1e-06 | N
08-04-19 | 05:43 | ZN1673:PA7 | URBAN | Other | Other - Self Clearing Trigger | 41 | 137 | 0.003789 | 2.8e-05 | N
08-04-19 | 05:55 | 229:34995 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 680 | 4 | 0.01046 | 0.00284 | N
08-04-19 | 05:55 | 232:33407 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 247 | 193 | 0.19879 | 0.001031 | N
08-04-19 | 07:33 | ZN847:PA39 | URBAN | Other | Other | 1 | 166 | 0.000112 | 1e-06 | N
06-04-19 | 05:40 | ZN116:PA29 | URBAN | Third Party | Vehicle impact | 83 | 20 | 0.001124 | 5.6e-05 | N
08-04-19 | 07:49 | ZN12570:PA22 | SHORT RURAL | Other | Other | 1 | 73 | 0.000306 | 4e-06 | N
08-04-19 | 08:03 | ZN12570:PA22 | SHORT RURAL | Other | Other | 1 | 60 | 0.00025 | 4e-06 | N
05-04-19 | 15:13 | ZN9118:PA26 | URBAN | Asset Failure | LV | 59 | 197 | 0.007867 | 4e-05 | N
08-04-19 | 08:13 | 270:83583 | URBAN | Third Party | Vehicle impact | 1 | 147 | 9.9e-05 | 1e-06 | N
07-04-19 | 14:55 | 232:33413 | SHORT RURAL | Asset Failure | LV | 80 | 85 | 0.028396 | 0.000334 | N
08-04-19 | 08:48 | ZN1850:PA45 | URBAN | Asset Failure | LV | 1 | 381 | 0.000258 | 1e-06 | N
08-04-19 | 08:51 | ZN9700:PA18 | URBAN | Third Party | Vehicle impact | 1 | 263 | 0.000178 | 1e-06 | N
08-04-19 | 08:56 | ZN2602:PA36 | URBAN | Other | Other - Arcing | 1 | 63 | 4.3e-05 | 1e-06 | N
08-04-19 | 09:05 | 224:80337 | URBAN | Other | Other | 1 | 191 | 0.000129 | 1e-06 | N
08-04-19 | 09:32 | ZN9245:PA13 | URBAN | Vegetation | Vegetation Grow In | 1 | 507 | 0.000343 | 1e-06 | N
08-04-19 | 10:10 | ZN2466:PA5 | URBAN | Network business | Switching and protection error | 66 | 20 | 0.000893 | 4.5e-05 | N
08-04-19 | 08:25 | 220:8687 | URBAN | Asset Failure | LV | 38 | 439 | 0.011294 | 2.6e-05 | N
08-04-19 | 10:36 | ZN7481:PA3 | URBAN | Other | Other | 64 | 24 | 0.001026 | 4.3e-05 | N
08-04-19 | 11:52 | ZN12570:PA40 | SHORT RURAL | Other | Other | 1 | 105 | 0.000437 | 4e-06 | N
08-04-19 | 13:23 | ZN12650:PA2 | URBAN | Asset Failure | LV | 22 | 69 | 0.001023 | 1.5e-05 | N
05-04-19 | 06:50 | ZN195:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 10 | 1,075 | 0.007276 | 7e-06 | N
08-04-19 | 17:25 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 25 | 0.00875 | 0.00035 | N
08-04-19 | 15:13 | 227:13015 | SHORT RURAL | Asset Failure | LV | 1 | 142 | 0.000593 | 4e-06 | N
08-04-19 | 15:36 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 56 | 1,389 | 0.052647 | 3.8e-05 | N
08-04-19 | 17:03 | ZN1673:PA7 | URBAN | Other | Other | 1 | 40 | 2.7e-05 | 1e-06 | N
08-04-19 | 18:16 | 512:83743 | SHORT RURAL | Asset Failure | LV | 2 | 129 | 0.001077 | 8e-06 | N
08-04-19 | 19:05 | ZN7481:PA3 | URBAN | Asset Failure | LV | 95 | 963 | 0.061891 | 6.4e-05 | N
09-04-19 | 03:52 | ZN2568:PA32 | URBAN | Asset Failure | HV | 2,400 | 82 | 0.13347 | 0.001624 | N
09-04-19 | 09:24 | 813:89062 | SHORT RURAL | Other | Other | 1 | 109 | 0.000455 | 4e-06 | N
09-04-19 | 09:28 | ZN9550:PA36 | URBAN | Animal | Animal nesting/burrowing, etc and other | 771 | 51 | 0.026609 | 0.000522 | N
09-04-19 | 12:20 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 10 | 80 | 0.28001 | 0.0035 | N
05-04-19 | 15:45 | ZN342:PA26 | URBAN | Third Party | Dig-in | 1 | 105 | 7.1e-05 | 1e-06 | N
05-04-19 | 17:55 | ZN342:PA28 | URBAN | Third Party | Dig-in | 2 | 185 | 0.00025 | 1e-06 | N
09-04-19 | 12:05 | 814:82289 | SHORT RURAL | Asset Failure | HV | 110 | 80 | 0.036734 | 0.000459 | N
09-04-19 | 17:43 | ZN12580:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 2,166 | 153 | 0.22411 | 0.001466 | N
09-04-19 | 13:45 | 810:74054 | LONG RURAL | Asset Failure | HV | 5 | 30 | 0.052503 | 0.00175 | N
09-04-19 | 14:03 | ZN12570:PA22 | SHORT RURAL | Other | Other | 1 | 37 | 0.000156 | 4e-06 | N
08-04-19 | 15:36 | ZN15013:PA6 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 229 | 63 | 0.060721 | 0.000956 | N
08-04-19 | 15:36 | ZN965:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 1,389 | 0.021623 | 1.6e-05 | N
09-04-19 | 14:29 | ZN9252:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 434 | 0.000294 | 1e-06 | N
09-04-19 | 15:32 | ZN12610:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 27 | 1.8e-05 | 1e-06 | N
10-04-19 | 03:02 | ZN129:PA34 | URBAN | Animal | Animal impact | 440 | 55 | 0.016376 | 0.000298 | N
10-04-19 | 03:02 | ZN129:PA35 | URBAN | Animal | Animal impact | 1,317 | 55 | 0.049017 | 0.000891 | N
10-04-19 | 03:02 | ZN129:PA36 | URBAN | Animal | Animal impact | 1,239 | 55 | 0.046114 | 0.000838 | N
10-04-19 | 03:02 | ZN129:PA38 | URBAN | Animal | Animal impact | 1,199 | 55 | 0.044625 | 0.000811 | N
10-04-19 | 03:02 | ZN129:PA39 | URBAN | Animal | Animal impact | 954 | 55 | 0.035507 | 0.000646 | N
10-04-19 | 03:02 | ZN129:PA40 | URBAN | Animal | Animal impact | 1,159 | 55 | 0.043137 | 0.000784 | N
10-04-19 | 03:02 | ZN129:PA41 | URBAN | Animal | Animal impact | 1,080 | 55 | 0.040196 | 0.000731 | N
10-04-19 | 03:02 | ZN129:PA43 | URBAN | Animal | Animal impact | 106 | 56 | 0.004017 | 7.2e-05 | N
10-04-19 | 03:02 | ZN129:PA46 | URBAN | Animal | Animal impact | 1,524 | 56 | 0.057753 | 0.001031 | N
10-04-19 | 03:02 | ZN129:PA47 | URBAN | Animal | Animal impact | 888 | 56 | 0.033651 | 0.000601 | N
10-04-19 | 03:02 | ZN129:PA49 | URBAN | Animal | Animal impact | 153 | 56 | 0.005798 | 0.000104 | N
10-04-19 | 03:02 | ZN129:PA51 | URBAN | Animal | Animal impact | 208 | 56 | 0.007882 | 0.000141 | N
10-04-19 | 03:02 | ZN129:PA52 | URBAN | Animal | Animal impact | 1,061 | 56 | 0.040207 | 0.000718 | N
10-04-19 | 03:02 | ZN129:PA55 | URBAN | Animal | Animal impact | 176 | 57 | 0.006789 | 0.000119 | N
10-04-19 | 03:02 | ZN129:PA56 | URBAN | Animal | Animal impact | 1,398 | 57 | 0.053924 | 0.000946 | N
10-04-19 | 03:02 | ZN129:PA57 | URBAN | Animal | Animal impact | 1,585 | 57 | 0.061137 | 0.001073 | N
10-04-19 | 03:02 | ZN129:PA62 | URBAN | Animal | Animal impact | 358 | 57 | 0.013809 | 0.000242 | N
10-04-19 | 03:02 | ZN129:PA63 | URBAN | Animal | Animal impact | 708 | 57 | 0.027309 | 0.000479 | N
10-04-19 | 03:02 | ZN129:PA64 | URBAN | Animal | Animal impact | 1,793 | 57 | 0.06916 | 0.001213 | N
09-04-19 | 16:37 | ZN398:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 305 | 0.000206 | 1e-06 | N
09-04-19 | 17:18 | ZN35600:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 70 | 127 | 0.006016 | 4.7e-05 | N
09-04-19 | 17:52 | ZN2602:PA20 | URBAN | Vegetation | Vegetation Grow In | 1 | 317 | 0.000215 | 1e-06 | N
09-04-19 | 17:56 | ZN2602:PA20 | URBAN | Vegetation | Vegetation Grow In | 1 | 314 | 0.000212 | 1e-06 | N
09-04-19 | 18:24 | ZN3472:PA30 | URBAN | Asset Failure | LV | 2 | 266 | 0.00036 | 1e-06 | N
09-04-19 | 19:13 | ZN15014:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 328 | 83 | 0.018448 | 0.000222 | N
09-04-19 | 19:35 | ZN35800:PA6 | URBAN | Other | Other - Self Clearing Trigger | 87 | 79 | 0.004656 | 5.9e-05 | N
09-04-19 | 20:02 | ZN1290:PA9 | URBAN | Asset Failure | HV | 1,266 | 85 | 0.072722 | 0.000857 | N
09-04-19 | 21:22 | 204:82703 | URBAN | Other | Other | 1 | 68 | 4.6e-05 | 1e-06 | N
10-04-19 | 07:48 | ZN9118:PA3 | SHORT RURAL | Third Party | Vehicle impact | 1 | 401 | 0.001675 | 4e-06 | N
10-04-19 | 08:52 | 216:10724 | SHORT RURAL | Other | Other | 1 | 124 | 0.000517 | 4e-06 | N
10-04-19 | 08:59 | ZN129:PA56 | URBAN | Asset Failure | LV | 11 | 256 | 0.001906 | 7e-06 | N
10-04-19 | 09:40 | ZN10993:PA35 | URBAN | Asset Failure | LV | 1 | 320 | 0.000216 | 1e-06 | N
10-04-19 | 09:55 | 216:10724 | SHORT RURAL | Other | Other | 1 | 61 | 0.000255 | 4e-06 | N
10-04-19 | 12:30 | ZN965:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 30 | 0.000365 | 1.2e-05 | N
10-04-19 | 14:27 | ZN12610:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 124 | 8.4e-05 | 1e-06 | N
10-04-19 | 17:35 | ZN690:PA36 | URBAN | Vegetation | Vegetation Blow/Fall In | 45 | 10 | 0.000305 | 3e-05 | N
10-04-19 | 15:52 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 186 | 0.000778 | 4e-06 | N
10-04-19 | 16:20 | 238:34136 | URBAN | Asset Failure | LV | 1 | 283 | 0.000192 | 1e-06 | N
07-04-19 | 00:05 | ZN12610:PA6 | URBAN | Asset Failure | LV | 73 | 40 | 0.001976 | 4.9e-05 | N
10-04-19 | 17:40 | ZN340:PA3 | URBAN | Asset Failure | LV | 86 | 70 | 0.004074 | 5.8e-05 | N
10-04-19 | 17:59 | 216:10726 | URBAN | Asset Failure | LV | 26 | 181 | 0.003179 | 1.8e-05 | N
10-04-19 | 20:47 | 513:48050 | SHORT RURAL | Asset Failure | HV | 20 | 103 | 0.008599 | 8.3e-05 | N
10-04-19 | 19:06 | ZN9900:PA12 | URBAN | Other | Other - Self Clearing Trigger | 27 | 77 | 0.001411 | 1.8e-05 | N
11-04-19 | 00:07 | ZN10995:PA2 | URBAN | Asset Failure | Distribution substation | 136 | 165 | 0.015227 | 9.2e-05 | N
11-04-19 | 05:39 | ZN15005:PA10 | URBAN | Asset Failure | LV | 11 | 350 | 0.002607 | 7e-06 | N
11-04-19 | 07:51 | 232:33409 | SHORT RURAL | Third Party | Vehicle impact | 44 | 255 | 0.046819 | 0.000184 | N
18-04-19 | 08:58 | ZN15002:PA6 | URBAN | Other | Other | 1 | 140 | 9.5e-05 | 1e-06 | N
11-04-19 | 12:22 | ZN14891:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 327 | 0.001365 | 4e-06 | N
11-04-19 | 12:25 | ZN1648:PA4 | URBAN | Asset Failure | LV | 49 | 140 | 0.004635 | 3.3e-05 | N
11-04-19 | 12:53 | 222:33601 | SHORT RURAL | Asset Failure | LV | 89 | 33 | 0.01226 | 0.000372 | N
11-04-19 | 13:20 | ZN10994:PA11 | URBAN | Asset Failure | LV | 1 | 250 | 0.000169 | 1e-06 | N
11-04-19 | 13:40 | 238:34138 | SHORT RURAL | Third Party | Dig-in | 11 | 380 | 0.017449 | 4.6e-05 | N
11-04-19 | 14:10 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 3 | 190 | 0.002379 | 1.3e-05 | N
11-04-19 | 16:13 | 802:82220 | SHORT RURAL | Network business | Network error | 1 | 107 | 0.000447 | 4e-06 | N
11-04-19 | 18:45 | ZN10999:PA11 | URBAN | Asset Failure | LV | 113 | 10 | 0.000765 | 7.6e-05 | N
11-04-19 | 16:40 | 265:81651 | SHORT RURAL | Asset Failure | HV | 48 | 107 | 0.02144 | 0.0002 | N
11-04-19 | 16:40 | 813:89061 | LONG RURAL | Asset Failure | HV | 9 | 65 | 0.20476 | 0.00315 | N
11-04-19 | 19:54 | ZN3672:PA13 | URBAN | Network business | Switching and protection error | 35 | 6 | 0.000142 | 2.4e-05 | N
12-04-19 | 02:09 | ZN15001:PA18 | URBAN | Other | Other - Self Clearing Trigger | 67 | 121 | 0.005486 | 4.5e-05 | N
12-04-19 | 07:58 | ZN10994:PA21 | URBAN | Vegetation | Vegetation Grow In | 1 | 122 | 8.2e-05 | 1e-06 | N
12-04-19 | 08:55 | ZN15008:PA10 | URBAN | Asset Failure | LV | 74 | 300 | 0.015024 | 5e-05 | N
12-04-19 | 11:18 | ZN15011:PA10 | URBAN | Asset Failure | HV | 1,563 | 70 | 0.074558 | 0.001058 | N
12-04-19 | 15:18 | 515:35193 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 117 | 0.000486 | 4e-06 | N
12-04-19 | 17:15 | ZN12650:PA12 | URBAN | Third Party | Vehicle impact | 51 | 325 | 0.011217 | 3.5e-05 | N
12-04-19 | 17:15 | ZN12660:PA10 | SHORT RURAL | Third Party | Vehicle impact | 30 | 325 | 0.040702 | 0.000125 | N
12-04-19 | 16:35 | 265:81651 | SHORT RURAL | Asset Failure | HV | 48 | 235 | 0.047089 | 0.0002 | N
12-04-19 | 16:54 | 206:34440 | URBAN | Third Party | Vehicle impact | 1 | 249 | 0.000168 | 1e-06 | N
12-04-19 | 18:55 | 502:48010 | SHORT RURAL | Asset Failure | LV | 1 | 284 | 0.001188 | 4e-06 | N
12-04-19 | 22:55 | ZN35600:PA4 | URBAN | Asset Failure | HV | 1,035 | 57 | 0.039925 | 0.0007 | N
13-04-19 | 07:14 | ZN36100:PA23 | URBAN | Asset Failure | LV | 27 | 166 | 0.003025 | 1.8e-05 | N
13-04-19 | 07:27 | ZN342:PA28 | URBAN | Asset Failure | LV | 145 | 92 | 0.009057 | 9.8e-05 | N
13-04-19 | 23:19 | ZN9252:PA28 | URBAN | Asset Failure | LV | 26 | 61 | 0.00107 | 1.8e-05 | N
14-04-19 | 09:22 | 243:80083 | SHORT RURAL | Third Party | Vehicle impact | 12 | 65 | 0.003256 | 5e-05 | N
14-04-19 | 11:34 | 524:33570 | SHORT RURAL | Asset Failure | LV | 1 | 313 | 0.001306 | 4e-06 | N
14-04-19 | 12:12 | ZN180:PA19 | URBAN | Third Party | Other | 1 | 672 | 0.000455 | 1e-06 | N
14-04-19 | 12:13 | ZN2602:PA33 | URBAN | Asset Failure | HV | 204 | 187 | 0.025817 | 0.000138 | N
14-04-19 | 12:13 | ZN2602:PA34 | URBAN | Asset Failure | HV | 1 | 135 | 9.1e-05 | 1e-06 | N
14-04-19 | 12:13 | ZN2602:PA41 | URBAN | Asset Failure | HV | 1,084 | 129 | 0.094272 | 0.000734 | N
14-04-19 | 13:47 | ZN630:PA31 | URBAN | Third Party | Other | 1 | 523 | 0.000354 | 1e-06 | N
14-04-19 | 17:10 | 513:48050 | SHORT RURAL | Asset Failure | HV | 7 | 50 | 0.001461 | 2.9e-05 | N
14-04-19 | 18:42 | ZN12600:PA2 | SHORT RURAL | Asset Failure | HV | 17 | 93 | 0.0066 | 7.1e-05 | N
14-04-19 | 19:09 | ZN342:PA28 | URBAN | Asset Failure | LV | 145 | 41 | 0.003994 | 9.8e-05 | N
14-04-19 | 23:10 | ZN2196:PA10 | URBAN | Other | Other | 1 | 750 | 0.000508 | 1e-06 | N
14-04-19 | 23:10 | ZN2196:PA5 | URBAN | Other | Other | 2 | 745 | 0.001008 | 1e-06 | N
14-04-19 | 19:53 | ZN630:PA31 | URBAN | Third Party | Other | 6 | 112 | 0.000453 | 4e-06 | N
14-04-19 | 21:26 | ZN12690:PA10 | SHORT RURAL | Asset Failure | HV | 698 | 49 | 0.14278 | 0.002914 | N
15-04-19 | 00:20 | ZN3472:PA20 | URBAN | Other | Other | 51 | 90 | 0.003106 | 3.5e-05 | N
15-04-19 | 04:20 | ZN342:PA28 | URBAN | Asset Failure | LV | 145 | 239 | 0.023474 | 9.8e-05 | N
15-04-19 | 09:26 | 807:74184 | SHORT RURAL | Asset Failure | HV | 1 | 219 | 0.000914 | 4e-06 | N
11-04-19 | 14:00 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 45 | 0.015751 | 0.00035 | N
15-04-19 | 10:27 | ZN9245:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,413 | 0.005897 | 4e-06 | N
15-04-19 | 10:35 | 264:81232 | SHORT RURAL | Asset Failure | LV | 127 | 230 | 0.12194 | 0.00053 | N
12-04-19 | 08:30 | 806:82667 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 50 | 0.000209 | 4e-06 | N
15-04-19 | 02:15 | ZN3472:PA28 | URBAN | Other | Other | 28 | 60 | 0.001137 | 1.9e-05 | N
15-04-19 | 01:45 | ZN3472:PA28 | URBAN | Other | Other | 30 | 90 | 0.001827 | 2e-05 | N
15-04-19 | 11:26 | 507:80917 | URBAN | Other | Other | 1 | 153 | 0.000104 | 1e-06 | N
15-04-19 | 12:26 | ZN8000:PA1 | URBAN | Third Party | Vehicle impact | 2 | 289 | 0.000391 | 1e-06 | N
15-04-19 | 18:50 | ZN4545:PA42 | URBAN | Asset Failure | HV | 207 | 170 | 0.023815 | 0.00014 | N
15-04-19 | 18:39 | ZN965:PA11 | URBAN | Asset Failure | Subtransmission | 1,162 | 50 | 0.039319 | 0.000786 | N
15-04-19 | 18:39 | ZN965:PA13 | URBAN | Asset Failure | Subtransmission | 617 | 50 | 0.020878 | 0.000418 | N
15-04-19 | 18:39 | ZN965:PA15 | URBAN | Asset Failure | Subtransmission | 1,162 | 50 | 0.039319 | 0.000786 | N
15-04-19 | 18:39 | ZN965:PA2 | SHORT RURAL | Asset Failure | Subtransmission | 540 | 51 | 0.11497 | 0.002254 | N
15-04-19 | 18:39 | ZN965:PA28 | URBAN | Asset Failure | Subtransmission | 1,007 | 48 | 0.032712 | 0.000681 | N
15-04-19 | 18:39 | ZN965:PA29 | URBAN | Asset Failure | Subtransmission | 761 | 48 | 0.02472 | 0.000515 | N
15-04-19 | 18:39 | ZN965:PA3 | URBAN | Asset Failure | Subtransmission | 1,179 | 51 | 0.040693 | 0.000798 | N
15-04-19 | 18:39 | ZN965:PA33 | URBAN | Asset Failure | Subtransmission | 1,300 | 48 | 0.042229 | 0.00088 | N
15-04-19 | 18:39 | ZN965:PA35 | URBAN | Asset Failure | Subtransmission | 958 | 48 | 0.03112 | 0.000648 | N
15-04-19 | 18:39 | ZN965:PA4 | URBAN | Asset Failure | Subtransmission | 1,158 | 51 | 0.039968 | 0.000784 | N
15-04-19 | 18:39 | ZN965:PA6 | URBAN | Asset Failure | Subtransmission | 1,063 | 51 | 0.036689 | 0.000719 | N
15-04-19 | 18:39 | ZN965:PA8 | URBAN | Asset Failure | Subtransmission | 1,193 | 51 | 0.041176 | 0.000807 | N
15-04-19 | 22:13 | ZN12600:PA13 | SHORT RURAL | Animal | Animal impact | 856 | 55 | 0.19654 | 0.003573 | N
16-04-19 | 02:31 | ZN12610:PA24 | URBAN | Asset Failure | HV | 2,355 | 83 | 0.13205 | 0.001594 | N
16-04-19 | 03:52 | ZN12610:PA5 | URBAN | Other | Other | 1 | 166 | 0.000112 | 1e-06 | N
16-04-19 | 05:36 | ZN342:PA28 | URBAN | Asset Failure | LV | 145 | 179 | 0.017521 | 9.8e-05 | N
12-04-19 | 17:46 | ZN12650:PA10 | URBAN | Other | Other | 38 | 141 | 0.003626 | 2.6e-05 | N
16-04-19 | 09:00 | 807:74183 | SHORT RURAL | Asset Failure | HV | 5 | 130 | 0.002713 | 2.1e-05 | N
12-04-19 | 17:46 | ZN12650:PA10 | URBAN | Other | Other | 44 | 141 | 0.004199 | 3e-05 | N
16-04-19 | 07:31 | 807:74179 | SHORT RURAL | Asset Failure | LV | 1 | 49 | 0.000205 | 4e-06 | N
16-04-19 | 07:34 | ZN12610:PA24 | URBAN | Other | Other | 1 | 30 | 2.1e-05 | 1e-06 | N
16-04-19 | 09:33 | 217:33612 | URBAN | Other | Other | 1 | 23 | 1.5e-05 | 1e-06 | N
16-04-19 | 12:08 | ZN3922:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 53 | 10 | 0.000359 | 3.6e-05 | N
16-04-19 | 12:25 | ZN35500:PA31 | URBAN | Asset Failure | LV | 1 | 334 | 0.000226 | 1e-06 | N
16-04-19 | 12:25 | ZN3672:PA21 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 61 | 40 | 0.010186 | 0.000255 | N
16-04-19 | 13:15 | ZN690:PA33 | URBAN | Third Party | Vehicle impact | 77 | 325 | 0.01693 | 5.2e-05 | N
16-04-19 | 13:15 | ZN690:PA34 | URBAN | Third Party | Vehicle impact | 50 | 19 | 0.000643 | 3.4e-05 | N
17-04-19 | 07:00 | 516:48067 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 435 | 0.007246 | 1.7e-05 | N
16-04-19 | 15:24 | ZN12600:PA9 | SHORT RURAL | Other | Other | 1 | 201 | 0.000838 | 4e-06 | N
16-04-19 | 15:26 | ZN9550:PA1 | URBAN | Third Party | Vehicle impact | 50 | 99 | 0.00335 | 3.4e-05 | N
16-04-19 | 16:41 | 511:29880 | URBAN | Other | Other - Self Clearing Trigger | 4 | 209 | 0.000566 | 3e-06 | N
16-04-19 | 16:43 | ZN9700:PA21 | URBAN | Third Party | Vehicle impact | 1 | 386 | 0.000261 | 1e-06 | N
16-04-19 | 17:42 | 256:80650 | URBAN | Network business | Network error | 10 | 38 | 0.000257 | 7e-06 | N
16-04-19 | 18:25 | ZN35600:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 81 | 305 | 0.016719 | 5.5e-05 | N
16-04-19 | 18:35 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 125 | 0.000522 | 4e-06 | N
17-04-19 | 03:17 | 214:8665 | URBAN | Asset Failure | LV | 1 | 403 | 0.000273 | 1e-06 | N
17-04-19 | 06:39 | ZN4545:PA36 | URBAN | Other | Other - Arcing | 1 | 440 | 0.000298 | 1e-06 | N
17-04-19 | 07:05 | ZN12570:PA37 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 195 | 0.00081 | 4e-06 | N
16-04-19 | 16:43 | ZN9700:PA21 | URBAN | Third Party | Other | 8 | 142 | 0.000769 | 5e-06 | N
17-04-19 | 16:20 | 526:34641 | SHORT RURAL | Third Party | Vehicle impact | 17 | 75 | 0.00531 | 7.1e-05 | N
17-04-19 | 12:26 | 801:74121 | LONG RURAL | Other | Other - Self Clearing Trigger | 2 | 109 | 0.076277 | 0.0007 | N
17-04-19 | 13:39 | ZN630:PA14 | URBAN | Third Party | Vehicle impact | 91 | 133 | 0.008193 | 6.2e-05 | N
17-04-19 | 18:16 | ZN1673:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 187 | 0.00379 | 2e-05 | N
17-04-19 | 17:22 | ZN2400:PA18 | SHORT RURAL | Other | Other | 1 | 45 | 0.000189 | 4e-06 | N
17-04-19 | 17:44 | ZN1673:PA6 | URBAN | Other | Other | 1 | 65 | 4.4e-05 | 1e-06 | N
17-04-19 | 18:10 | ZN1673:PA6 | URBAN | Other | Other | 1 | 40 | 2.7e-05 | 1e-06 | N
17-04-19 | 20:48 | ZN13000:PA11 | SHORT RURAL | Other | Other | 51 | 30 | 0.006372 | 0.000212 | N
17-04-19 | 21:35 | ZN9118:PA11 | URBAN | Other | Other - Arcing | 1 | 222 | 0.00015 | 1e-06 | N
17-04-19 | 23:20 | ZN10999:PA28 | URBAN | Other | Other | 46 | 14 | 0.000443 | 3.1e-05 | N
17-04-19 | 23:28 | 264:81241 | URBAN | Third Party | Vehicle impact | 1 | 355 | 0.00024 | 1e-06 | N
18-04-19 | 05:53 | ZN3425:PA12 | URBAN | Other | Other - Arcing | 1 | 157 | 0.000106 | 1e-06 | N
18-04-19 | 06:37 | ZN129:PA57 | URBAN | Other | Other - Arcing | 1 | 172 | 0.000117 | 1e-06 | N
18-04-19 | 06:15 | ZN262:PA6 | URBAN | Other | Other - Arcing | 1 | 405 | 0.000274 | 1e-06 | N
17-04-19 | 16:45 | ZN12570:PA37 | SHORT RURAL | Asset Failure | HV | 106 | 110 | 0.048558 | 0.000441 | N
18-04-19 | 06:53 | ZN12650:PA20 | URBAN | Other | Other | 1 | 43 | 2.9e-05 | 1e-06 | N
18-04-19 | 09:17 | ZN15004:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 282 | 0.000191 | 1e-06 | N
18-04-19 | 10:20 | ZN1287:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 82 | 70 | 0.003885 | 5.6e-05 | N
18-04-19 | 12:15 | ZN10995:PA7 | URBAN | Other | Other | 37 | 60 | 0.001503 | 2.5e-05 | N
18-04-19 | 13:47 | ZN3672:PA44 | URBAN | Other | Other | 1 | 4 | 3e-06 | 1e-06 | N
18-04-19 | 14:13 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 182 | 0.063512 | 0.00035 | N
18-04-19 | 16:00 | ZN9900:PA1 | URBAN | Asset Failure | HV | 2 | 481 | 0.000651 | 1e-06 | N
18-04-19 | 19:38 | ZN2196:PA9 | URBAN | Asset Failure | LV | 1 | 256 | 0.000173 | 1e-06 | N
18-04-19 | 19:48 | ZN690:PA36 | URBAN | Third Party | Vehicle impact | 1 | 227 | 0.000154 | 1e-06 | N
18-04-19 | 22:00 | ZN398:PA2 | URBAN | Other | Other - Arcing | 1 | 173 | 0.000117 | 1e-06 | N
19-04-19 | 10:45 | 813:89055 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 156 | 0.000652 | 4e-06 | N
19-04-19 | 14:20 | ZN9118:PA13 | URBAN | Animal | Animal impact | 1 | 316 | 0.000214 | 1e-06 | N
19-04-19 | 15:54 | ZN35500:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 3,123 | 2 | 0.004227 | 0.002114 | N
21-04-19 | 08:54 | ZN12640:PA13 | SHORT RURAL | Asset Failure | LV | 36 | 46 | 0.006899 | 0.00015 | N
19-04-19 | 16:32 | ZN12630:PA1 | SHORT RURAL | Third Party | Vehicle impact | 118 | 375 | 0.18433 | 0.000492 | N
19-04-19 | 17:59 | 513:48050 | SHORT RURAL | Other | Other - Self Clearing Trigger | 16 | 141 | 0.009403 | 6.7e-05 | N
20-04-19 | 06:44 | ZN9700:PA24 | URBAN | Other | Other - Arcing | 1 | 266 | 0.00018 | 1e-06 | N
20-04-19 | 09:14 | 502:48010 | SHORT RURAL | Asset Failure | LV | 1 | 165 | 0.000688 | 4e-06 | N
20-04-19 | 10:45 | 511:29878 | SHORT RURAL | Asset Failure | LV | 1 | 177 | 0.000738 | 4e-06 | N
20-04-19 | 10:47 | 807:74184 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 177 | 0.000739 | 4e-06 | N
20-04-19 | 11:00 | ZN12660:PA14 | SHORT RURAL | Other | Other - Arcing | 1 | 312 | 0.0013 | 4e-06 | N
20-04-19 | 09:17 | 243:80083 | SHORT RURAL | Asset Failure | HV | 4 | 398 | 0.006633 | 1.7e-05 | N
20-04-19 | 12:02 | ZN262:PA32 | URBAN | Asset Failure | LV | 49 | 308 | 0.010207 | 3.3e-05 | N
20-04-19 | 15:31 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 178 | 0.000742 | 4e-06 | N
20-04-19 | 17:02 | 807:74184 | SHORT RURAL | Asset Failure | HV | 1 | 153 | 0.000637 | 4e-06 | N
20-04-19 | 17:42 | ZN13000:PA5 | SHORT RURAL | Third Party | Other | 28 | 113 | 0.013182 | 0.000117 | N
20-04-19 | 20:52 | ZN35800:PA16 | URBAN | Animal | Animal nesting/burrowing, etc and other | 26 | 3 | 5.7e-05 | 1.8e-05 | N
20-04-19 | 21:12 | ZN15010:PA33 | URBAN | Asset Failure | LV | 38 | 407 | 0.010468 | 2.6e-05 | N
21-04-19 | 04:53 | ZN36300:PA11 | URBAN | Other | Other - Arcing | 1 | 168 | 0.000113 | 1e-06 | N
21-04-19 | 06:01 | ZN187:PA14 | URBAN | Other | Other - Arcing | 1 | 544 | 0.000368 | 1e-06 | N
21-04-19 | 07:17 | 515:35198 | SHORT RURAL | Other | Other - Arcing | 1 | 416 | 0.001734 | 4e-06 | N
21-04-19 | 09:03 | ZN5868:PA30 | URBAN | Other | Other - Arcing | 1 | 362 | 0.000245 | 1e-06 | N
21-04-19 | 10:48 | ZN10993:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 624 | 59 | 0.024912 | 0.000422 | N
21-04-19 | 10:48 | ZN10995:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,422 | 59 | 0.05677 | 0.000962 | N
21-04-19 | 16:00 | ZN965:PA8 | URBAN | Asset Failure | LV | 38 | 10 | 0.000257 | 2.6e-05 | N
21-04-19 | 20:30 | 514:18137 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 20 | 8.3e-05 | 4e-06 | N
21-04-19 | 21:01 | ZN15008:PA10 | URBAN | Other | Other - Arcing | 1 | 912 | 0.000617 | 1e-06 | N
22-04-19 | 07:40 | 235:2728 | URBAN | Animal | Animal nesting/burrowing, etc and other | 323 | 71 | 0.015518 | 0.000219 | N
22-04-19 | 12:40 | ZN8000:PA38 | URBAN | Third Party | Other | 3 | 478 | 0.00097 | 2e-06 | N
22-04-19 | 11:25 | ZN35500:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 42 | 35 | 0.000995 | 2.8e-05 | N
22-04-19 | 14:31 | ZN187:PA22 | URBAN | Network business | Network error | 34 | 10 | 0.00022 | 2.3e-05 | N
22-04-19 | 16:41 | ZN12620:PA10 | SHORT RURAL | Other | Other | 1 | 74 | 0.000306 | 4e-06 | N
22-04-19 | 17:08 | ZN129:PA40 | URBAN | Other | Other | 107 | 107 | 0.007772 | 7.2e-05 | N
22-04-19 | 20:01 | ZN10999:PA29 | URBAN | Other | Other - Self Clearing Trigger | 35 | 58 | 0.001374 | 2.4e-05 | N
22-04-19 | 20:10 | ZN35500:PA28 | URBAN | Other | Other | 28 | 80 | 0.001516 | 1.9e-05 | N
22-04-19 | 22:31 | ZN15010:PA28 | SHORT RURAL | Other | Other - Arcing | 1 | 658 | 0.002742 | 4e-06 | N
18-04-19 | 11:48 | ZN12580:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 15 | 3 | 3e-05 | 1e-05 | N
19-04-19 | 12:45 | ZN12630:PA3 | SHORT RURAL | Other | Other | 6 | 40 | 0.001 | 2.5e-05 | N
23-04-19 | 07:45 | ZN12630:PA1 | SHORT RURAL | Other | Other | 1 | 224 | 0.000933 | 4e-06 | N
23-04-19 | 07:57 | ZN12630:PA1 | SHORT RURAL | Other | Other - Arcing | 1 | 482 | 0.002009 | 4e-06 | N
23-04-19 | 08:33 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 41 | 545 | 0.01512 | 2.8e-05 | N
23-04-19 | 08:34 | ZN35600:PA19 | URBAN | Other | Other - Arcing | 1 | 86 | 5.8e-05 | 1e-06 | N
23-04-19 | 08:45 | ZN9118:PA13 | URBAN | Other | Other - Arcing | 1 | 75 | 5.1e-05 | 1e-06 | N
23-04-19 | 09:04 | ZN14144:PA8 | URBAN | Other | Other | 1 | 77 | 5.2e-05 | 1e-06 | N
23-04-19 | 09:13 | ZN9550:PA43 | URBAN | Other | Other - Arcing | 1 | 326 | 0.000221 | 1e-06 | N
23-04-19 | 10:11 | 802:82220 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 189 | 0.001575 | 8e-06 | N
23-04-19 | 12:30 | ZN35555:PA17 | URBAN | Other | Other | 213 | 90 | 0.012972 | 0.000144 | N
21-04-19 | 03:40 | ZN15010:PA33 | URBAN | Asset Failure | LV | 49 | 20 | 0.000663 | 3.3e-05 | N
23-04-19 | 11:24 | 502:48008 | URBAN | Other | Other | 1 | 64 | 4.4e-05 | 1e-06 | N
23-04-19 | 14:19 | 512:83733 | SHORT RURAL | Asset Failure | HV | 2 | 161 | 0.001342 | 8e-06 | N
23-04-19 | 13:52 | ZN2635:PA44 | URBAN | Other | Other | 1 | 123 | 8.3e-05 | 1e-06 | N
23-04-19 | 14:52 | 213:33771 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 353 | 0.000239 | 1e-06 | N
23-04-19 | 15:17 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 52 | 0.000217 | 4e-06 | N
27-04-19 | 01:20 | ZN2635:PA44 | URBAN | Asset Failure | LV | 103 | 730 | 0.050876 | 7e-05 | N
23-04-19 | 19:30 | ZN12690:PA16 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 11 | 60 | 0.00275 | 4.6e-05 | N
23-04-19 | 21:27 | ZN116:PA30 | URBAN | Asset Failure | LV | 49 | 938 | 0.031096 | 3.3e-05 | N
23-04-19 | 22:07 | 508:82574 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 147 | 115 | 0.070375 | 0.000612 | N
24-04-19 | 06:13 | ZN14891:PA10 | SHORT RURAL | Other | Other - Arcing | 1 | 346 | 0.001442 | 4e-06 | N
24-04-19 | 07:18 | 502:48008 | URBAN | Asset Failure | Distribution substation | 83 | 324 | 0.018175 | 5.6e-05 | N
24-04-19 | 07:21 | ZN187:PA22 | URBAN | Other | Other - Arcing | 1 | 176 | 0.000119 | 1e-06 | N
24-04-19 | 09:08 | ZN3472:PA33 | URBAN | Other | Other - Arcing | 1 | 141 | 9.5e-05 | 1e-06 | N
24-04-19 | 09:59 | ZN14891:PA1 | URBAN | Asset Failure | HV | 200 | 72 | 0.009744 | 0.000135 | N
24-04-19 | 10:46 | ZN9118:PA12 | URBAN | Other | Other - Arcing | 1 | 238 | 0.000161 | 1e-06 | N
24-04-19 | 11:28 | ZN35600:PA1 | URBAN | Other | Other - Arcing | 1 | 151 | 0.000102 | 1e-06 | N
24-04-19 | 13:27 | ZN15010:PA28 | SHORT RURAL | Other | Other - Arcing | 1 | 273 | 0.001136 | 4e-06 | N
24-04-19 | 14:26 | 243:80075 | SHORT RURAL | Asset Failure | HV | 85 | 52 | 0.018415 | 0.000354 | N
24-04-19 | 18:46 | 522:83123 | SHORT RURAL | Third Party | Other | 1 | 210 | 0.000874 | 4e-06 | N
24-04-19 | 19:31 | ZN3155:PA30 | URBAN | Asset Failure | LV | 11 | 1,219 | 0.009073 | 7e-06 | N
25-04-19 | 03:30 | ZN167:PA8 | URBAN | Asset Failure | HV | 13 | 82 | 0.000723 | 9e-06 | N
25-04-19 | 11:43 | ZN1285:PA20 | URBAN | Asset Failure | LV | 64 | 59 | 0.002574 | 4.3e-05 | N
25-04-19 | 11:32 | 204:82708 | URBAN | Vegetation | Vegetation Blow/Fall In | 4 | 313 | 0.000847 | 3e-06 | N
25-04-19 | 13:57 | ZN965:PA8 | URBAN | Other | Other - Self Clearing Trigger | 22 | 138 | 0.002054 | 1.5e-05 | N
25-04-19 | 15:04 | ZN15014:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 328 | 59 | 0.013094 | 0.000222 | N
25-04-19 | 20:51 | ZN262:PA27 | URBAN | Other | Other - Arcing | 1 | 159 | 0.000107 | 1e-06 | N
26-04-19 | 00:45 | ZN1287:PA16 | URBAN | Other | Other - Self Clearing Trigger | 1 | 55 | 3.7e-05 | 1e-06 | N
26-04-19 | 00:45 | ZN2196:PA21 | URBAN | Other | Other - Self Clearing Trigger | 61 | 55 | 0.002266 | 4.1e-05 | N
26-04-19 | 03:46 | ZN180:PA20 | URBAN | Asset Failure | Distribution substation | 100 | 334 | 0.022579 | 6.8e-05 | N
26-04-19 | 09:41 | ZN15002:PA6 | URBAN | Other | Other | 67 | 177 | 0.008016 | 4.5e-05 | N
26-04-19 | 08:23 | ZN342:PA28 | URBAN | Asset Failure | LV | 145 | 102 | 0.009975 | 9.8e-05 | N
26-04-19 | 11:00 | ZN12610:PA18 | URBAN | Other | Other - Arcing | 1 | 314 | 0.000213 | 1e-06 | N
26-04-19 | 11:44 | ZN10993:PA27 | URBAN | Asset Failure | LV | 1 | 212 | 0.000143 | 1e-06 | N
26-04-19 | 15:11 | ZN3155:PA30 | URBAN | Third Party | Other | 11 | 144 | 0.001072 | 7e-06 | N
26-04-19 | 16:44 | ZN35500:PA28 | URBAN | Vegetation | Vegetation Grow In | 1 | 434 | 0.000294 | 1e-06 | N
26-04-19 | 17:26 | 810:74058 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 86 | 0.000713 | 8e-06 | N
27-04-19 | 02:32 | ZN2635:PA51 | URBAN | Asset Failure | HV | 267 | 74 | 0.01343 | 0.000181 | N
27-04-19 | 03:28 | ZN2635:PA39 | URBAN | Asset Failure | LV | 29 | 1,247 | 0.024469 | 2e-05 | N
27-04-19 | 03:28 | ZN2635:PA40 | URBAN | Asset Failure | LV | 41 | 1,226 | 0.034017 | 2.8e-05 | N
27-04-19 | 07:33 | ZN35500:PA16 | URBAN | Other | Other - Arcing | 1 | 358 | 0.000242 | 1e-06 | N
27-04-19 | 07:34 | ZN8000:PA38 | URBAN | Asset Failure | LV | 65 | 1,995 | 0.087762 | 4.4e-05 | N
27-04-19 | 16:25 | ZN12580:PA1 | URBAN | Other | Other | 19 | 35 | 0.00045 | 1.3e-05 | N
27-04-19 | 11:21 | 270:83586 | URBAN | Third Party | Vehicle impact | 87 | 97 | 0.00571 | 5.9e-05 | N
27-04-19 | 09:21 | ZN2602:PA42 | URBAN | Other | Other - Arcing | 2 | 254 | 0.000344 | 1e-06 | N
27-04-19 | 10:47 | 217:33611 | URBAN | Asset Failure | LV | 1 | 273 | 0.000185 | 1e-06 | N
27-04-19 | 11:49 | ZN262:PA17 | URBAN | Other | Other - Arcing | 1 | 343 | 0.000232 | 1e-06 | N
27-04-19 | 12:18 | ZN12620:PA8 | SHORT RURAL | Other | Other - Self Clearing Trigger | 29 | 154 | 0.018607 | 0.000121 | N
27-04-19 | 12:30 | 807:74179 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 2 | 65 | 0.000542 | 8e-06 | N
27-04-19 | 12:55 | 224:80341 | URBAN | Other | Other - Arcing | 1 | 34 | 2.3e-05 | 1e-06 | N
27-04-19 | 14:11 | ZN847:PA19 | URBAN | Asset Failure | LV | 1 | 172 | 0.000117 | 1e-06 | N
27-04-19 | 16:57 | ZN4990:PA53 54GHJ | CBD | Asset Failure | LV | 1 | 167 | 0.005503 | 3.3e-05 | N
27-04-19 | 22:21 | ZN15006:PA4 | URBAN | Asset Failure | LV | 1 | 753 | 0.00051 | 1e-06 | N
28-04-19 | 10:00 | ZN2835:PA27 | URBAN | Third Party | Vehicle impact | 145 | 60 | 0.005886 | 9.8e-05 | N
28-04-19 | 07:40 | ZN2602:PA27 | URBAN | Other | Other - Arcing | 1 | 222 | 0.00015 | 1e-06 | N
28-04-19 | 08:36 | ZN15012:PA2 | URBAN | Other | Other | 1 | 42 | 2.9e-05 | 1e-06 | N
28-04-19 | 08:39 | ZN116:PA31 | URBAN | Other | Other - Arcing | 1 | 415 | 0.000281 | 1e-06 | N
28-04-19 | 09:49 | 511:29878 | SHORT RURAL | Asset Failure | HV | 4 | 84 | 0.001399 | 1.7e-05 | N
28-04-19 | 10:24 | 507:80922 | SHORT RURAL | Other | Other - Self Clearing Trigger | 26 | 56 | 0.006064 | 0.000108 | N
28-04-19 | 11:30 | 256:80632 | URBAN | Third Party | Vehicle impact | 44 | 205 | 0.006102 | 3e-05 | N
28-04-19 | 12:07 | ZN9252:PA28 | URBAN | Other | Other - Arcing | 1 | 255 | 0.000172 | 1e-06 | N
28-04-19 | 16:03 | ZN1193:PA28 | URBAN | Other | Other | 1 | 68 | 4.6e-05 | 1e-06 | N
28-04-19 | 18:57 | 261:81876 | URBAN | Animal | Animal impact | 53 | 43 | 0.001532 | 3.6e-05 | N
28-04-19 | 18:59 | ZN342:PA28 | URBAN | Asset Failure | LV | 145 | 154 | 0.015107 | 9.8e-05 | N
28-04-19 | 19:22 | ZN2310:PA4 | URBAN | Asset Failure | LV | 105 | 108 | 0.007672 | 7.1e-05 | N
28-04-19 | 20:20 | ZN262:PA25 | URBAN | Third Party | Other | 1 | 129 | 8.8e-05 | 1e-06 | N
28-04-19 | 21:28 | ZN1788:PA16 | URBAN | Asset Failure | LV | 1 | 841 | 0.000569 | 1e-06 | N
28-04-19 | 22:54 | ZN901:PA11 | URBAN | Other | Other - Self Clearing Trigger | 53 | 516 | 0.018501 | 3.6e-05 | N
29-04-19 | 04:40 | ZN3472:PA12 | URBAN | Asset Failure | HV | 1,658 | 72 | 0.080948 | 0.001122 | N
29-04-19 | 04:40 | ZN35900:PA24 | URBAN | Asset Failure | HV | 1 | 82 | 5.5e-05 | 1e-06 | N
29-04-19 | 05:37 | 807:74181 | SHORT RURAL | Other | Other | 1 | 278 | 0.001159 | 4e-06 | N
29-04-19 | 09:06 | ZN180:PA24 | URBAN | Other | Other | 1 | 28 | 1.9e-05 | 1e-06 | N
24-04-19 | 09:40 | 417:80507 | URBAN | Other | Other | 1 | 205 | 0.000139 | 1e-06 | N
29-04-19 | 10:09 | ZN12650:PA12 | URBAN | Asset Failure | HV | 86 | 93 | 0.005411 | 5.8e-05 | N
24-04-19 | 12:00 | 514:18137 | SHORT RURAL | Asset Failure | LV | 2 | 120 | 0.001 | 8e-06 | N
29-04-19 | 10:58 | ZN1648:PA2 | URBAN | Other | Other | 66 | 61 | 0.002737 | 4.5e-05 | N
29-04-19 | 11:07 | 516:48065 | SHORT RURAL | Asset Failure | Subtransmission | 35 | 183 | 0.026677 | 0.000146 | N
29-04-19 | 11:07 | 516:48066 | SHORT RURAL | Asset Failure | Subtransmission | 88 | 133 | 0.048748 | 0.000367 | N
29-04-19 | 11:07 | 516:48067 | SHORT RURAL | Asset Failure | Subtransmission | 279 | 208 | 0.24171 | 0.001162 | N
29-04-19 | 12:15 | 513:48050 | SHORT RURAL | Asset Failure | LV | 5 | 25 | 0.000521 | 2.1e-05 | N
29-04-19 | 12:26 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 94 | 0.000391 | 4e-06 | N
29-04-19 | 12:29 | ZN847:PA18 | SHORT RURAL | Other | Other | 1 | 90 | 0.000376 | 4e-06 | N
29-04-19 | 20:27 | 813:89063 | SHORT RURAL | Other | Other - Arcing | 1 | 737 | 0.00307 | 4e-06 | N
29-04-19 | 22:49 | ZN262:PA20 | URBAN | Third Party | Vehicle impact | 37 | 294 | 0.007357 | 2.5e-05 | N
30-04-19 | 05:25 | ZN342:PA28 | URBAN | Asset Failure | LV | 145 | 63 | 0.006151 | 9.8e-05 | N
30-04-19 | 06:47 | ZN9118:PA24 | URBAN | Other | Other - Self Clearing Trigger | 37 | 203 | 0.005073 | 2.5e-05 | N
29-04-19 | 10:05 | 513:48050 | SHORT RURAL | Asset Failure | LV | 5 | 85 | 0.00177 | 2.1e-05 | N
30-04-19 | 09:01 | ZN342:PA28 | URBAN | Asset Failure | LV | 145 | 1,059 | 0.10385 | 9.8e-05 | N
17-04-19 | 11:15 | ZN1788:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 66 | 45 | 0.00201 | 4.5e-05 | N
30-04-19 | 12:34 | ZN180:PA35 | URBAN | Asset Failure | LV | 39 | 30 | 0.000794 | 2.6e-05 | N
30-04-19 | 13:41 | 532:83307 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 94 | 0.000392 | 4e-06 | N
30-04-19 | 14:39 | ZN36100:PA12 | URBAN | Asset Failure | HV | 1,119 | 2 | 0.001514 | 0.000757 | N
30-04-19 | 14:39 | ZN36100:PA2 | URBAN | Asset Failure | HV | 1 | 82 | 5.5e-05 | 1e-06 | N
30-04-19 | 14:39 | ZN36100:PA23 | URBAN | Asset Failure | HV | 988 | 80 | 0.053475 | 0.000668 | N
30-04-19 | 14:59 | ZN2196:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 297 | 0.000201 | 1e-06 | N
30-04-19 | 14:55 | ZN14143:PA17 | SHORT RURAL | Other | Other - Self Clearing Trigger | 667 | 103 | 0.28539 | 0.002778 | N
30-04-19 | 16:10 | ZN15010:PA26 | SHORT RURAL | Asset Failure | LV | 89 | 82 | 0.03053 | 0.000371 | N
30-04-19 | 16:31 | 264:81244 | SHORT RURAL | Asset Failure | HV | 1,347 | 122 | 0.68475 | 0.00561 | N
30-04-19 | 17:25 | 801:74121 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 83 | 0.029041 | 0.00035 | N
30-04-19 | 21:49 | ZN2835:PA15 | URBAN | Asset Failure | LV | 42 | 161 | 0.004575 | 2.8e-05 | N
30-04-19 | 21:49 | ZN2835:PA41 | URBAN | Asset Failure | LV | 7 | 161 | 0.000762 | 5e-06 | N
30-04-19 | 22:19 | ZN3154:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 239 | 60 | 0.009702 | 0.000162 | N
30-04-19 | 23:40 | ZN342:PA28 | URBAN | Asset Failure | LV | 370 | 180 | 0.045058 | 0.00025 | N
01-05-19 | 03:30 | ZN3472:PA12 | URBAN | Third Party | Vehicle impact | 84 | 202 | 0.01148 | 5.7e-05 | N
01-05-19 | 06:55 | 523:33501 | SHORT RURAL | Third Party | Fire | 1 | 65 | 0.00027 | 4e-06 | N
01-05-19 | 08:49 | ZN2835:PA27 | URBAN | Asset Failure | LV | 82 | 101 | 0.005591 | 5.5e-05 | N
01-05-19 | 12:15 | ZN195:PA11 | URBAN | Third Party | Vehicle impact | 41 | 112 | 0.003107 | 2.8e-05 | N
01-05-19 | 09:46 | ZN14891:PA16 | SHORT RURAL | Asset Failure | HV | 280 | 66 | 0.076971 | 0.001166 | N
01-05-19 | 12:10 | 801:74121 | LONG RURAL | Asset Failure | LV | 2 | 35 | 0.024493 | 0.0007 | N
01-05-19 | 10:24 | 205:12213 | SHORT RURAL | Other | Other | 1 | 270 | 0.001123 | 4e-06 | N
01-05-19 | 11:04 | ZN15010:PA30 | URBAN | Asset Failure | LV | 13 | 326 | 0.002865 | 9e-06 | N
01-05-19 | 11:10 | ZN3154:PA13 | SHORT RURAL | Asset Failure | LV | 21 | 110 | 0.009621 | 8.7e-05 | N
01-05-19 | 12:07 | ZN12610:PA22 | URBAN | Asset Failure | LV | 1 | 382 | 0.000259 | 1e-06 | N
01-05-19 | 12:24 | ZN35500:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 12 | 101 | 0.00082 | 8e-06 | N
01-05-19 | 16:03 | ZN15014:PA19 | URBAN | Asset Failure | LV | 47 | 237 | 0.007524 | 3.2e-05 | N
01-05-19 | 16:30 | ZN3155:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 116 | 85 | 0.006671 | 7.8e-05 | N
01-05-19 | 19:50 | ZN35370:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 22 | 846 | 0.077513 | 9.2e-05 | N
01-05-19 | 21:46 | ZN1285:PA31 | URBAN | Asset Failure | LV | 89 | 319 | 0.0192 | 6e-05 | N
02-05-19 | 03:51 | ZN12660:PA17 | URBAN | Asset Failure | Distribution substation | 122 | 205 | 0.016906 | 8.3e-05 | N
29-04-19 | 12:50 | ZN36300:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 20 | 0.000365 | 1.8e-05 | N
02-05-19 | 08:35 | ZN15011:PA2 | URBAN | Third Party | Vehicle impact | 25 | 959 | 0.016223 | 1.7e-05 | N
02-05-19 | 08:36 | ZN15011:PA4 | URBAN | Third Party | Vehicle impact | 76 | 944 | 0.048528 | 5.1e-05 | N
02-05-19 | 09:18 | 508:82575 | SHORT RURAL | Other | Other | 1 | 97 | 0.000402 | 4e-06 | N
02-05-19 | 10:06 | ZN12660:PA10 | SHORT RURAL | Other | Other | 1 | 55 | 0.000229 | 4e-06 | N
02-05-19 | 19:10 | 509:33395 | LONG RURAL | Other | Other | 4 | 40 | 0.055983 | 0.0014 | N
02-05-19 | 10:31 | 509:33399 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 64 | 0.000267 | 4e-06 | N
02-05-19 | 10:41 | ZN630:PA19 | URBAN | Animal | Other | 156 | 169 | 0.017837 | 0.000106 | N
02-05-19 | 11:00 | 264:81244 | SHORT RURAL | Other | Other | 79 | 35 | 0.011517 | 0.000329 | N
02-05-19 | 10:50 | ZN2568:PA19 | URBAN | Asset Failure | LV | 32 | 104 | 0.002252 | 2.2e-05 | N
02-05-19 | 11:27 | ZN10998:PA17 | URBAN | Asset Failure | LV | 66 | 202 | 0.009032 | 4.5e-05 | N
02-05-19 | 13:13 | ZN167:PA10 | URBAN | Third Party | Other | 1 | 46 | 3.1e-05 | 1e-06 | N
02-05-19 | 13:40 | 232:11453 | SHORT RURAL | Other | Other | 1 | 33 | 0.000136 | 4e-06 | N
24-04-19 | 12:33 | ZN15005:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 82 | 2 | 0.000111 | 5.5e-05 | N
02-05-19 | 14:02 | ZN13000:PA11 | SHORT RURAL | Other | Other | 1 | 68 | 0.000284 | 4e-06 | N
02-05-19 | 14:25 | ZN2310:PA24 | URBAN | Asset Failure | LV | 23 | 80 | 0.001245 | 1.6e-05 | N
02-05-19 | 14:35 | ZN2310:PA24 | URBAN | Asset Failure | LV | 55 | 80 | 0.002977 | 3.7e-05 | N
02-05-19 | 14:57 | ZN4545:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 39 | 228 | 0.006003 | 2.6e-05 | N
02-05-19 | 16:40 | 235:2124 | URBAN | Third Party | Vehicle impact | 3 | 192 | 0.00039 | 2e-06 | N
03-05-19 | 05:25 | 205:12206 | URBAN | Other | Other - Self Clearing Trigger | 868 | 65 | 0.038172 | 0.000587 | N
03-05-19 | 06:23 | ZN4545:PA4 | URBAN | Other | Other - Arcing | 1 | 246 | 0.000166 | 1e-06 | N
02-05-19 | 14:22 | 812:19072 | SHORT RURAL | Asset Failure | LV | 6 | 128 | 0.003199 | 2.5e-05 | N
03-05-19 | 15:40 | ZN12630:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 9 | 120 | 0.004498 | 3.7e-05 | N
03-05-19 | 12:08 | ZN847:PA39 | URBAN | Vegetation | Vegetation Blow/Fall In | 52 | 91 | 0.003213 | 3.5e-05 | N
03-05-19 | 12:26 | ZN12640:PA5 | URBAN | Other | Other - Arcing | 1 | 304 | 0.000206 | 1e-06 | N
03-05-19 | 13:02 | ZN167:PA1 | URBAN | Other | Other | 11 | 124 | 0.000923 | 7e-06 | N
03-05-19 | 16:00 | ZN965:PA37 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 190 | 0.000129 | 1e-06 | N
03-05-19 | 13:38 | ZN847:PA2 | URBAN | Other | Other - Arcing | 1 | 487 | 0.000329 | 1e-06 | N
03-05-19 | 15:15 | 264:81238 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 3 | 1.3e-05 | 4e-06 | N
03-05-19 | 16:14 | ZN3154:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 335 | 0.000227 | 1e-06 | N
03-05-19 | 16:55 | ZN12620:PA10 | SHORT RURAL | Other | Other | 1 | 259 | 0.00108 | 4e-06 | N
03-05-19 | 17:20 | ZN14892:PA10 | URBAN | Asset Failure | LV | 1 | 1,240 | 0.000839 | 1e-06 | N
03-05-19 | 17:30 | ZN3154:PA12 | URBAN | Weather |  | 30 | 114 | 0.002316 | 2e-05 | N
03-05-19 | 21:45 | ZN2466:PA40 | URBAN | Other | Other - Arcing | 40 | 165 | 0.004465 | 2.7e-05 | N
03-05-19 | 19:27 | 522:83132 | SHORT RURAL | Asset Failure | LV | 1 | 162 | 0.000673 | 4e-06 | N
03-05-19 | 20:10 | ZN4545:PA32 | URBAN | Third Party | Vehicle impact | 27 | 995 | 0.018176 | 1.8e-05 | N
04-05-19 | 13:55 | ZN1287:PA15 | URBAN | Network business | Switching and protection error | 89 | 30 | 0.001806 | 6e-05 | N
03-05-19 | 20:55 | 227:13020 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 136 | 112 | 0.063198 | 0.000566 | N
04-05-19 | 11:10 | ZN2310:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 124 | 30 | 0.002516 | 8.4e-05 | N
04-05-19 | 12:15 | ZN3154:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 190 | 0.006426 | 3.4e-05 | N
04-05-19 | 09:43 | ZN14891:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 347 | 0.001445 | 4e-06 | N
03-05-19 | 20:37 | ZN3922:PA7 | URBAN | Other | Other | 1 | 1,094 | 0.00074 | 1e-06 | N
04-05-19 | 12:06 | ZN13000:PA5 | SHORT RURAL | Other | Other - Arcing | 1 | 413 | 0.00172 | 4e-06 | N
04-05-19 | 00:44 | ZN965:PA8 | URBAN | Asset Failure | LV | 43 | 1,470 | 0.042769 | 2.9e-05 | N
04-05-19 | 15:30 | ZN384:PA76 | URBAN | Vegetation | Vegetation Blow/Fall In | 65 | 30 | 0.001319 | 4.4e-05 | N
04-05-19 | 14:19 | 224:80341 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 26 | 1.7e-05 | 1e-06 | N
04-05-19 | 14:21 | 523:33508 | SHORT RURAL | Other | Other - Self Clearing Trigger | 25 | 160 | 0.01663 | 0.000104 | N
04-05-19 | 16:00 | ZN690:PA26 | URBAN | Third Party | Vehicle impact | 1 | 107 | 7.2e-05 | 1e-06 | N
05-05-19 | 03:10 | ZN398:PA3 | URBAN | Asset Failure | LV | 38 | 575 | 0.014768 | 2.6e-05 | N
05-05-19 | 09:21 | 813:89063 | SHORT RURAL | Asset Failure | LV | 1 | 106 | 0.00044 | 4e-06 | N
05-05-19 | 11:36 | ZN9900:PA12 | URBAN | Asset Failure | LV | 1 | 1,644 | 0.001112 | 1e-06 | N
05-05-19 | 13:06 | ZN9118:PA26 | URBAN | Asset Failure | LV | 1 | 1,926 | 0.001303 | 1e-06 | N
05-05-19 | 13:13 | ZN9550:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 256 | 0.000173 | 1e-06 | N
05-05-19 | 14:51 | ZN15001:PA11 | URBAN | Third Party | Vehicle impact | 1 | 981 | 0.000663 | 1e-06 | N
05-05-19 | 17:52 | ZN398:PA25 | URBAN | Other | Other - Arcing | 1 | 1,088 | 0.000736 | 1e-06 | N
05-05-19 | 18:03 | ZN398:PA3 | URBAN | Asset Failure | HV | 162 | 1,272 | 0.13939 | 0.00011 | N
05-05-19 | 18:50 | ZN14143:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 37 | 180 | 0.027732 | 0.000154 | N
05-05-19 | 19:21 | ZN15014:PA10 | SHORT RURAL | Other | Other - Self Clearing Trigger | 40 | 89 | 0.014824 | 0.000167 | N
05-05-19 | 19:21 | ZN15014:PA18 | URBAN | Other | Other - Self Clearing Trigger | 68 | 89 | 0.004094 | 4.6e-05 | N
06-05-19 | 12:00 | ZN129:PA40 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 45 | 0.001522 | 3.4e-05 | N
06-05-19 | 01:40 | ZN2835:PA23 | URBAN | Vegetation | Vegetation Blow/Fall In | 58 | 60 | 0.002354 | 3.9e-05 | N
05-05-19 | 23:25 | ZN12570:PA22 | SHORT RURAL | Asset Failure | HV | 687 | 87 | 0.24887 | 0.002861 | N
05-05-19 | 23:25 | ZN12570:PA40 | SHORT RURAL | Asset Failure | HV | 652 | 87 | 0.23619 | 0.002715 | N
06-05-19 | 08:33 | 257:81991 | URBAN | Other | Other | 1 | 26 | 1.8e-05 | 1e-06 | N
06-05-19 | 09:43 | ZN1068:PA26 | URBAN | Asset Failure | LV | 1 | 256 | 0.000173 | 1e-06 | N
06-05-19 | 09:44 | ZN1068:PA26 | URBAN | Asset Failure | LV | 1 | 256 | 0.000173 | 1e-06 | N
06-05-19 | 09:59 | ZN9700:PA11 | URBAN | Asset Failure | LV | 1 | 300 | 0.000203 | 1e-06 | N
06-05-19 | 10:10 | 812:19072 | SHORT RURAL | Asset Failure | HV | 5 | 20 | 0.000416 | 2.1e-05 | N
06-05-19 | 10:40 | ZN3472:PA12 | URBAN | Other | Other | 71 | 40 | 0.001921 | 4.8e-05 | N
06-05-19 | 10:49 | 223:14394 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 74 | 5e-05 | 1e-06 | N
06-05-19 | 10:58 | ZN9118:PA3 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 242 | 0.001007 | 4e-06 | N
06-05-19 | 11:25 | ZN10998:PA17 | URBAN | Third Party | Vehicle impact | 1 | 185 | 0.000125 | 1e-06 | N
06-05-19 | 12:40 | 509:33399 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 377 | 0.00157 | 4e-06 | N
06-05-19 | 12:42 | 532:83293 | URBAN | Other | Other | 1 | 222 | 0.00015 | 1e-06 | N
07-05-19 | 09:01 | ZN3425:PA24 | URBAN | Asset Failure | LV | 1 | 313 | 0.000212 | 1e-06 | N
07-05-19 | 09:35 | ZN2602:PA20 | URBAN | Asset Failure | LV | 76 | 100 | 0.005141 | 5.1e-05 | N
07-05-19 | 10:53 | ZN12600:PA3 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 247 | 0.000334 | 1e-06 | N
07-05-19 | 13:12 | 526:34639 | SHORT RURAL | Asset Failure | LV | 1 | 190 | 0.000791 | 4e-06 | N
07-05-19 | 18:08 | 507:80914 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 86 | 0.000358 | 4e-06 | N
07-05-19 | 18:24 | 523:33501 | SHORT RURAL | Asset Failure | HV | 1 | 196 | 0.000816 | 4e-06 | N
07-05-19 | 18:37 | 513:48052 | URBAN | Third Party | Other | 1 | 301 | 0.000204 | 1e-06 | N
08-05-19 | 05:14 | ZN847:PA28 | URBAN | Asset Failure | LV | 63 | 153 | 0.00652 | 4.3e-05 | N
02-05-19 | 16:10 | ZN2568:PA19 | URBAN | Asset Failure | LV | 32 | 60 | 0.001299 | 2.2e-05 | N
02-05-19 | 16:44 | ZN2568:PA19 | URBAN | Asset Failure | LV | 31 | 26 | 0.000545 | 2.1e-05 | N
08-05-19 | 09:25 | 230:81434 | URBAN | Other | Other | 1 | 143 | 9.6e-05 | 1e-06 | N
08-05-19 | 09:32 | 238:34148 | SHORT RURAL | Asset Failure | LV | 10 | 228 | 0.009494 | 4.2e-05 | N
08-05-19 | 10:00 | 507:80922 | SHORT RURAL | Asset Failure | HV | 38 | 62 | 0.009744 | 0.000158 | N
07-05-19 | 11:48 | 532:83307 | SHORT RURAL | Asset Failure | LV | 1 | 27 | 0.000112 | 4e-06 | N
08-05-19 | 10:59 | ZN847:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,344 | 68 | 0.061824 | 0.000909 | N
08-05-19 | 11:35 | ZN12630:PA11 | SHORT RURAL | Asset Failure | LV | 8 | 380 | 0.012658 | 3.3e-05 | N
08-05-19 | 12:15 | ZN12660:PA14 | SHORT RURAL | Asset Failure | LV | 50 | 40 | 0.008328 | 0.000208 | N
08-05-19 | 12:11 | 230:81434 | URBAN | Other | Other | 1 | 79 | 5.3e-05 | 1e-06 | N
09-05-19 | 11:30 | ZN10998:PA26 | URBAN | Third Party | Other | 55 | 35 | 0.001302 | 3.7e-05 | N
08-05-19 | 18:00 | ZN262:PA34 | URBAN | Asset Failure | LV | 71 | 50 | 0.002401 | 4.8e-05 | N
08-05-19 | 16:26 | ZN35400:PA88 | URBAN | Other | Other - Self Clearing Trigger | 1 | 64 | 4.3e-05 | 1e-06 | N
08-05-19 | 16:42 | 217:33610 | URBAN | Other | Other | 1 | 67 | 4.5e-05 | 1e-06 | N
08-05-19 | 19:15 | 240:34846 | URBAN | Asset Failure | HV | 56 | 120 | 0.004546 | 3.8e-05 | N
08-05-19 | 23:30 | ZN4545:PA2 | URBAN | Third Party | Vehicle impact | 156 | 965 | 0.10184 | 0.000106 | N
08-05-19 | 22:13 | 258:80784 | URBAN | Animal | Animal impact | 76 | 32 | 0.001629 | 5.1e-05 | N
09-05-19 | 00:25 | ZN4545:PA2 | URBAN | Third Party | Vehicle impact | 103 | 65 | 0.004529 | 7e-05 | N
09-05-19 | 05:20 | ZN35500:PA24 | URBAN | Animal | Animal impact | 2,070 | 55 | 0.076829 | 0.0014 | N
09-05-19 | 06:35 | ZN9118:PA13 | URBAN | Third Party | Vehicle impact | 1 | 144 | 9.8e-05 | 1e-06 | N
09-05-19 | 07:18 | ZN12690:PA16 | SHORT RURAL | Other | Other - Self Clearing Trigger | 11 | 162 | 0.007404 | 4.6e-05 | N
09-05-19 | 07:53 | 523:33508 | SHORT RURAL | Asset Failure | LV | 25 | 157 | 0.016343 | 0.000104 | N
09-05-19 | 14:16 | ZN35400:PA110 | URBAN | Asset Failure | LV | 66 | 1,188 | 0.053044 | 4.5e-05 | N
09-05-19 | 14:15 | 807:74181 | SHORT RURAL | Other | Other | 164 | 80 | 0.054631 | 0.000683 | N
09-05-19 | 14:38 | ZN9900:PA8 | URBAN | Asset Failure | LV | 37 | 351 | 0.008787 | 2.5e-05 | N
09-05-19 | 16:21 | ZN36100:PA15 | URBAN | Other | Other | 45 | 113 | 0.003446 | 3e-05 | N
09-05-19 | 18:55 | 239:82132 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 59 | 4e-05 | 1e-06 | N
09-05-19 | 20:19 | ZN1290:PA8 | URBAN | Asset Failure | LV | 23 | 201 | 0.003127 | 1.6e-05 | N
09-05-19 | 20:47 | 270:83591 | SHORT RURAL | Animal | Animal impact | 63 | 42 | 0.011075 | 0.000262 | N
10-05-19 | 00:45 | ZN965:PA21 | URBAN | Other | Other | 655 | 44 | 0.019496 | 0.000443 | N
10-05-19 | 02:00 | ZN2835:PA31 | URBAN | Asset Failure | HV | 1,280 | 99 | 0.086067 | 0.000866 | N
10-05-19 | 05:20 | ZN15004:PA3 | SHORT RURAL | Other | Other | 1 | 309 | 0.001288 | 4e-06 | N
10-05-19 | 06:30 | 508:82574 | SHORT RURAL | Asset Failure | HV | 1 | 350 | 0.001457 | 4e-06 | N
10-05-19 | 08:53 | ZN2635:PA32 | URBAN | Asset Failure | HV | 47 | 157 | 0.004992 | 3.2e-05 | N
10-05-19 | 08:53 | ZN2635:PA59 | URBAN | Asset Failure | HV | 138 | 79 | 0.007375 | 9.3e-05 | N
10-05-19 | 08:53 | ZN2635:PA62 | URBAN | Asset Failure | HV | 42 | 83 | 0.002369 | 2.8e-05 | N
10-05-19 | 07:25 | ZN15004:PA5 | URBAN | Other | Other | 1 | 275 | 0.000186 | 1e-06 | N
10-05-19 | 09:52 | ZN8000:PA14 | URBAN | Asset Failure | LV | 1 | 87 | 5.9e-05 | 1e-06 | N
10-05-19 | 09:59 | ZN35800:PA4 | URBAN | Other | Other - Self Clearing Trigger | 8 | 324 | 0.001754 | 5e-06 | N
10-05-19 | 13:25 | ZN3472:PA30 | URBAN | Asset Failure | LV | 44 | 135 | 0.004018 | 3e-05 | N
08-05-19 | 16:15 | ZN12630:PA11 | SHORT RURAL | Asset Failure | LV | 5 | 100 | 0.002082 | 2.1e-05 | N
09-05-19 | 10:00 | ZN10998:PA26 | URBAN | Asset Failure | LV | 55 | 15 | 0.000558 | 3.7e-05 | N
10-05-19 | 18:10 | 811:74234 | SHORT RURAL | Asset Failure | HV | 11 | 35 | 0.001603 | 4.6e-05 | N
10-05-19 | 17:05 | ZN80:PA32 | URBAN | Vegetation | Vegetation Blow/Fall In | 31 | 15 | 0.000315 | 2.1e-05 | N
10-05-19 | 17:58 | 205:12205 | URBAN | Other | Other | 1 | 66 | 4.5e-05 | 1e-06 | N
10-05-19 | 18:53 | 224:80337 | URBAN | Asset Failure | LV | 39 | 71 | 0.001873 | 2.6e-05 | N
10-05-19 | 20:15 | 220:8689 | URBAN | Asset Failure | LV | 1 | 221 | 0.000149 | 1e-06 | N
10-05-19 | 22:21 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 1 | 313 | 0.1095 | 0.00035 | N
11-05-19 | 01:49 | ZN3472:PA20 | URBAN | Asset Failure | LV | 85 | 141 | 0.008107 | 5.7e-05 | N
11-05-19 | 04:45 | 532:83309 | URBAN | Asset Failure | HV | 27 | 60 | 0.001096 | 1.8e-05 | N
11-05-19 | 06:47 | 214:8667 | URBAN | Asset Failure | HV | 922 | 96 | 0.059834 | 0.000624 | N
11-05-19 | 07:07 | 205:12203 | URBAN | Third Party | Other | 1 | 128 | 8.7e-05 | 1e-06 | N
11-05-19 | 07:34 | 502:48009 | SHORT RURAL | Other | Other | 1 | 141 | 0.000587 | 4e-06 | N
11-05-19 | 08:31 | 214:8667 | URBAN | Asset Failure | HV | 857 | 150 | 0.086966 | 0.00058 | N
11-05-19 | 08:31 | 214:8670 | URBAN | Asset Failure | HV | 971 | 101 | 0.066342 | 0.000657 | N
11-05-19 | 08:35 | ZN10995:PA1 | URBAN | Asset Failure | LV | 67 | 1,830 | 0.082942 | 4.5e-05 | N
11-05-19 | 08:49 | 528:83020 | SHORT RURAL | Other | Other | 1 | 401 | 0.001669 | 4e-06 | N
11-05-19 | 10:17 | 404:KU2 | URBAN | Network business | Network error | 1 | 73 | 4.9e-05 | 1e-06 | N
11-05-19 | 10:28 | ZN3155:PA11 | URBAN | Other | Other - Self Clearing Trigger | 15 | 76 | 0.000773 | 1e-05 | N
11-05-19 | 11:14 | ZN965:PA20 | URBAN | Asset Failure | LV | 32 | 166 | 0.003589 | 2.2e-05 | N
11-05-19 | 16:22 | ZN9245:PA13 | URBAN | Third Party | Vehicle impact | 1 | 382 | 0.000258 | 1e-06 | N
11-05-19 | 17:00 | ZN965:PA8 | URBAN | Other | Other | 24 | 45 | 0.000731 | 1.6e-05 | N
11-05-19 | 17:50 | 513:48059 | SHORT RURAL | Asset Failure | LV | 4 | 110 | 0.001832 | 1.7e-05 | N
11-05-19 | 19:51 | ZN12650:PA12 | URBAN | Other | Other | 1 | 134 | 9.1e-05 | 1e-06 | N
12-05-19 | 02:14 | ZN12640:PA12 | URBAN | Third Party | Vehicle impact | 22 | 885 | 0.013175 | 1.5e-05 | N
12-05-19 | 07:34 | 206:34438 | URBAN | Other | Other | 1 | 120 | 8.1e-05 | 1e-06 | N
12-05-19 | 11:47 | 508:82579 | SHORT RURAL | Asset Failure | LV | 1 | 28 | 0.000117 | 4e-06 | N
12-05-19 | 11:30 | ZN187:PA30 | URBAN | Asset Failure | LV | 3 | 360 | 0.000731 | 2e-06 | N
12-05-19 | 11:34 | ZN15013:PA2 | SHORT RURAL | Asset Failure | LV | 2 | 116 | 0.000966 | 8e-06 | N
12-05-19 | 17:50 | 257:82006 | URBAN | Other | Other | 1 | 76 | 5.2e-05 | 1e-06 | N
12-05-19 | 19:18 | 217:33610 | URBAN | Other | Other | 1 | 29 | 2e-05 | 1e-06 | N
12-05-19 | 21:58 | ZN35800:PA6 | URBAN | Other | Other - Self Clearing Trigger | 88 | 137 | 0.008136 | 6e-05 | N
13-05-19 | 07:01 | ZN15002:PA2 | URBAN | Asset Failure | Subtransmission | 1,247 | 263 | 0.22182 | 0.000843 | N
13-05-19 | 07:01 | ZN15002:PA4 | SHORT RURAL | Asset Failure | Subtransmission | 775 | 263 | 0.84893 | 0.003228 | N
13-05-19 | 07:01 | ZN15002:PA6 | URBAN | Asset Failure | Subtransmission | 1,657 | 263 | 0.29475 | 0.001121 | N
13-05-19 | 07:01 | ZN15002:PA8 | URBAN | Asset Failure | Subtransmission | 1,032 | 263 | 0.18358 | 0.000698 | N
13-05-19 | 07:01 | ZN15002:PA9 | URBAN | Asset Failure | Subtransmission | 13 | 263 | 0.002312 | 9e-06 | N
13-05-19 | 07:01 | ZN15013:PA10 | SHORT RURAL | Asset Failure | Subtransmission | 54 | 263 | 0.059152 | 0.000225 | N
13-05-19 | 07:35 | ZN4545:PA25 | URBAN | Other | Other - Arcing | 1 | 415 | 0.00028 | 1e-06 | N
10-05-19 | 12:32 | 205:12208 | URBAN | Network business | Network error | 1 | 2 | 1e-06 | 1e-06 | N
09-05-19 | 12:22 | ZN2835:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 50 | 6 | 0.000203 | 3.4e-05 | N
13-05-19 | 16:40 | 229:34992 | SHORT RURAL | Asset Failure | LV | 2 | 60 | 0.0005 | 8e-06 | N
11-05-19 | 18:10 | 532:83309 | URBAN | Asset Failure | Distribution substation | 27 | 40 | 0.000731 | 1.8e-05 | N
09-05-19 | 08:45 | 515:35193 | SHORT RURAL | Asset Failure | LV | 2 | 125 | 0.001041 | 8e-06 | N
13-05-19 | 11:17 | ZN12570:PA25 | SHORT RURAL | Other | Other | 1 | 67 | 0.00028 | 4e-06 | N
13-05-19 | 11:24 | ZN15002:PA2 | URBAN | Asset Failure | LV | 113 | 205 | 0.015668 | 7.6e-05 | N
11-05-19 | 16:25 | ZN965:PA20 | URBAN | Asset Failure | LV | 32 | 20 | 0.000433 | 2.2e-05 | N
13-05-19 | 16:55 | ZN690:PA33 | URBAN | Asset Failure | Distribution substation | 253 | 97 | 0.016627 | 0.000171 | N
13-05-19 | 17:10 | 509:33395 | LONG RURAL | Asset Failure | HV | 15 | 50 | 0.26242 | 0.005248 | N
14-05-19 | 12:30 | ZN12690:PA6 | URBAN | Asset Failure | Distribution substation | 43 | 90 | 0.002618 | 2.9e-05 | N
09-05-19 | 23:36 | ZN2635:PA59 | URBAN | Asset Failure | HV | 147 | 74 | 0.00731 | 9.9e-05 | N
14-05-19 | 09:10 | 509:33395 | LONG RURAL | Asset Failure | HV | 15 | 110 | 0.57733 | 0.005248 | N
14-05-19 | 09:06 | ZN1648:PA2 | URBAN | Third Party | Dig-in | 242 | 76 | 0.012508 | 0.000164 | N
14-05-19 | 10:32 | ZN1648:PA4 | URBAN | Other | Other | 1 | 75 | 5.1e-05 | 1e-06 | N
14-05-19 | 13:50 | 202:34245 | URBAN | Asset Failure | LV | 58 | 45 | 0.001765 | 3.9e-05 | N
14-05-19 | 12:34 | 243:80074 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 43 | 0.000181 | 4e-06 | N
14-05-19 | 14:12 | ZN129:PA34 | URBAN | Asset Failure | LV | 1 | 227 | 0.000154 | 1e-06 | N
14-05-19 | 18:23 | ZN1068:PA21 | URBAN | Third Party | Dig-in | 17 | 22 | 0.000253 | 1.1e-05 | N
14-05-19 | 15:16 | 238:34151 | URBAN | Asset Failure | HV | 1,257 | 75 | 0.063756 | 0.00085 | N
14-05-19 | 16:47 | 204:82701 | URBAN | Asset Failure | LV | 4 | 383 | 0.001036 | 3e-06 | N
14-05-19 | 17:08 | ZN12630:PA8 | SHORT RURAL | Asset Failure | LV | 4 | 136 | 0.002266 | 1.7e-05 | N
14-05-19 | 17:35 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 25 | 100 | 0.010413 | 0.000104 | N
14-05-19 | 21:26 | ZN1673:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 38 | 59 | 0.001506 | 2.6e-05 | N
14-05-19 | 22:26 | 801:74121 | LONG RURAL | Animal | Animal impact | 1 | 144 | 0.050385 | 0.00035 | N
15-05-19 | 09:47 | ZN15002:PA2 | URBAN | Other | Other | 1 | 312 | 0.000211 | 1e-06 | N
15-05-19 | 12:03 | 813:89055 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 217 | 0.000904 | 4e-06 | N
15-05-19 | 12:55 | ZN12650:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 371 | 79 | 0.019797 | 0.000251 | N
15-05-19 | 13:00 | ZN15012:PA2 | URBAN | Other | Other - Self Clearing Trigger | 13 | 20 | 0.000176 | 9e-06 | N
15-05-19 | 13:43 | 507:80914 | SHORT RURAL | Asset Failure | LV | 1 | 65 | 0.000272 | 4e-06 | N
15-05-19 | 14:50 | 807:74184 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 105 | 0.000437 | 4e-06 | N
15-05-19 | 17:36 | 508:82579 | SHORT RURAL | Asset Failure | LV | 1 | 180 | 0.000751 | 4e-06 | N
15-05-19 | 17:54 | 261:81864 | URBAN | Third Party | Other | 1 | 62 | 4.2e-05 | 1e-06 | N
15-05-19 | 17:58 | ZN3472:PA12 | URBAN | Other | Other | 1 | 69 | 4.7e-05 | 1e-06 | N
15-05-19 | 20:53 | 512:83743 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 56 | 0.000235 | 4e-06 | N
15-05-19 | 21:30 | ZN847:PA7 | URBAN | Animal | Animal impact | 1,323 | 56 | 0.050111 | 0.000895 | N
15-05-19 | 22:45 | ZN1673:PA19 | URBAN | Third Party | Dig-in | 82 | 175 | 0.009693 | 5.5e-05 | N
16-05-19 | 00:01 | 806:82667 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 2 | 539 | 0.004489 | 8e-06 | N
15-05-19 | 10:00 | 502:48010 | SHORT RURAL | Asset Failure | LV | 5 | 155 | 0.003228 | 2.1e-05 | N
16-05-19 | 09:32 | 813:89055 | SHORT RURAL | Asset Failure | HV | 36 | 88 | 0.013194 | 0.00015 | N
16-05-19 | 11:53 | 522:83132 | SHORT RURAL | Asset Failure | HV | 30 | 147 | 0.018366 | 0.000125 | N
16-05-19 | 11:03 | ZN965:PA11 | URBAN | Network business | Network error | 1,163 | 13 | 0.010225 | 0.000787 | N
16-05-19 | 11:03 | ZN965:PA13 | URBAN | Network business | Network error | 617 | 13 | 0.005425 | 0.000417 | N
16-05-19 | 11:03 | ZN965:PA15 | URBAN | Network business | Network error | 1,162 | 13 | 0.010217 | 0.000786 | N
16-05-19 | 11:03 | ZN965:PA2 | SHORT RURAL | Network business | Network error | 556 | 20 | 0.04577 | 0.002316 | N
16-05-19 | 11:03 | ZN965:PA28 | URBAN | Network business | Network error | 1,007 | 13 | 0.008854 | 0.000681 | N
16-05-19 | 11:03 | ZN965:PA29 | URBAN | Network business | Network error | 763 | 13 | 0.006709 | 0.000516 | N
16-05-19 | 11:03 | ZN965:PA3 | URBAN | Network business | Network error | 1,178 | 20 | 0.015748 | 0.000797 | N
16-05-19 | 11:03 | ZN965:PA30 | URBAN | Network business | Network error | 71 | 13 | 0.000624 | 4.8e-05 | N
16-05-19 | 11:03 | ZN965:PA33 | URBAN | Network business | Network error | 1,299 | 13 | 0.011421 | 0.000879 | N
16-05-19 | 11:03 | ZN965:PA35 | URBAN | Network business | Network error | 958 | 13 | 0.008423 | 0.000648 | N
16-05-19 | 11:03 | ZN965:PA4 | URBAN | Network business | Network error | 1,158 | 20 | 0.015481 | 0.000783 | N
16-05-19 | 11:03 | ZN965:PA6 | URBAN | Network business | Network error | 1,064 | 20 | 0.014224 | 0.00072 | N
16-05-19 | 11:03 | ZN965:PA8 | URBAN | Network business | Network error | 1,193 | 20 | 0.015949 | 0.000807 | N
16-05-19 | 14:50 | ZN9118:PA20 | URBAN | Vegetation | Vegetation Blow/Fall In | 101 | 10 | 0.000683 | 6.8e-05 | N
17-05-19 | 02:12 | ZN15004:PA1 | URBAN | Other | Other - Self Clearing Trigger | 1,717 | 109 | 0.12658 | 0.001161 | N
17-05-19 | 02:12 | ZN15004:PA3 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,357 | 109 | 0.61601 | 0.005651 | N
17-05-19 | 02:12 | ZN15004:PA5 | URBAN | Other | Other - Self Clearing Trigger | 1,734 | 109 | 0.12783 | 0.001173 | N
17-05-19 | 02:12 | ZN15004:PA9 | URBAN | Other | Other - Self Clearing Trigger | 1,555 | 109 | 0.11464 | 0.001052 | N
17-05-19 | 02:12 | ZN15010:PA24 | URBAN | Other | Other - Self Clearing Trigger | 1,411 | 108 | 0.10307 | 0.000954 | N
17-05-19 | 02:12 | ZN15010:PA25 | SHORT RURAL | Other | Other - Self Clearing Trigger | 479 | 108 | 0.21545 | 0.001995 | N
17-05-19 | 02:12 | ZN15010:PA26 | SHORT RURAL | Other | Other - Self Clearing Trigger | 338 | 108 | 0.15203 | 0.001408 | N
17-05-19 | 02:12 | ZN15010:PA28 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,108 | 108 | 0.49836 | 0.004614 | N
17-05-19 | 02:12 | ZN15010:PA29 | URBAN | Other | Other - Self Clearing Trigger | 578 | 108 | 0.04222 | 0.000391 | N
17-05-19 | 02:12 | ZN15010:PA30 | URBAN | Other | Other - Self Clearing Trigger | 1,807 | 108 | 0.13199 | 0.001222 | N
17-05-19 | 02:12 | ZN15010:PA33 | URBAN | Other | Other - Self Clearing Trigger | 87 | 108 | 0.006355 | 5.9e-05 | N
15-05-19 | 16:50 | ZN35800:PA13 | URBAN | Asset Failure | LV | 28 | 15 | 0.000284 | 1.9e-05 | N
15-05-19 | 13:45 | ZN2835:PA31 | URBAN | Third Party | Other | 2 | 315 | 0.000426 | 1e-06 | N
17-05-19 | 15:10 | ZN9534:PA18 | SHORT RURAL | Asset Failure | LV | 7 | 1,085 | 0.031631 | 2.9e-05 | N
17-05-19 | 17:25 | ZN874:PA18 | URBAN | Third Party | Vehicle impact | 80 | 575 | 0.031112 | 5.4e-05 | N
17-05-19 | 15:30 | ZN1788:PA20 | URBAN | Third Party | Vehicle impact | 1 | 1,818 | 0.00123 | 1e-06 | N
15-05-19 | 16:45 | ZN12650:PA2 | URBAN | Asset Failure | LV | 20 | 15 | 0.000203 | 1.4e-05 | N
17-05-19 | 15:57 | ZN9900:PA1 | URBAN | Asset Failure | LV | 1 | 352 | 0.000238 | 1e-06 | N
17-05-19 | 20:55 | ZN12570:PA21 | URBAN | Other | Other | 211 | 363 | 0.05181 | 0.000143 | N
17-05-19 | 21:03 | ZN9035:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 255 | 0.000173 | 1e-06 | N
18-05-19 | 06:15 | 243:80083 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 90 | 0.000375 | 4e-06 | N
18-05-19 | 12:02 | ZN340:PA45 | URBAN | Vegetation | Vegetation Blow/Fall In | 30 | 104 | 0.00211 | 2e-05 | N
18-05-19 | 12:46 | 222:33601 | SHORT RURAL | Other | Other | 1 | 131 | 0.000545 | 4e-06 | N
18-05-19 | 18:16 | ZN1673:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 57 | 49 | 0.001889 | 3.9e-05 | N
18-05-19 | 23:04 | 813:89063 | SHORT RURAL | Third Party | Fire | 1 | 65 | 0.00027 | 4e-06 | N
19-05-19 | 11:28 | 265:81649 | URBAN | Third Party | Other | 1 | 302 | 0.000204 | 1e-06 | N
19-05-19 | 14:06 | ZN35600:PA9 | URBAN | Asset Failure | HV | 3,000 | 46 | 0.093756 | 0.002029 | N
19-05-19 | 14:26 | ZN965:PA24 | URBAN | Asset Failure | LV | 1 | 69 | 4.7e-05 | 1e-06 | N
19-05-19 | 14:26 | ZN965:PA38 | URBAN | Asset Failure | LV | 42 | 249 | 0.00706 | 2.8e-05 | N
19-05-19 | 19:38 | 507:80923 | SHORT RURAL | Other | Other | 1 | 117 | 0.000485 | 4e-06 | N
20-05-19 | 00:03 | ZN10993:PA33 | URBAN | Asset Failure | LV | 73 | 57 | 0.002814 | 4.9e-05 | N
20-05-19 | 00:39 | ZN9252:PA27 | URBAN | Asset Failure | HV | 56 | 94 | 0.00356 | 3.8e-05 | N
20-05-19 | 00:39 | ZN9252:PA31 | URBAN | Asset Failure | HV | 1,359 | 94 | 0.086503 | 0.000919 | N
20-05-19 | 03:04 | ZN965:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 923 | 135 | 0.084276 | 0.000624 | N
20-05-19 | 05:18 | ZN262:PA14 | URBAN | Third Party | Vehicle impact | 1 | 166 | 0.000112 | 1e-06 | N
20-05-19 | 05:55 | ZN262:PA34 | URBAN | Other | Other - Self Clearing Trigger | 86 | 109 | 0.006357 | 5.8e-05 | N
20-05-19 | 08:47 | ZN15013:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 14 | 327 | 0.019064 | 5.8e-05 | N
18-05-19 | 13:28 | ZN384:PA70 | URBAN | Animal | Animal impact | 39 | 36 | 0.00095 | 2.6e-05 | N
20-05-19 | 09:43 | 526:34639 | SHORT RURAL | Asset Failure | HV | 1 | 217 | 0.000904 | 4e-06 | N
20-05-19 | 10:57 | 261:81864 | URBAN | Other | Other | 1 | 93 | 6.3e-05 | 1e-06 | N
20-05-19 | 14:03 | ZN1673:PA13 | URBAN | Other | Other - Self Clearing Trigger | 34 | 26 | 0.000603 | 2.3e-05 | N
20-05-19 | 16:05 | 204:82691 | URBAN | Asset Failure | LV | 1 | 183 | 0.000123 | 1e-06 | N
20-05-19 | 17:48 | ZN12610:PA13 | SHORT RURAL | Asset Failure | LV | 7 | 146 | 0.004256 | 2.9e-05 | N
21-05-19 | 05:29 | ZN180:PA7 | URBAN | Asset Failure | LV | 92 | 171 | 0.01064 | 6.2e-05 | N
20-05-19 | 03:36 | ZN3672:PA42 | URBAN | Third Party | Vehicle impact | 6 | 289 | 0.001173 | 4e-06 | N
21-05-19 | 09:44 | ZN36100:PA20 | URBAN | Third Party | Vehicle impact | 67 | 186 | 0.008429 | 4.5e-05 | N
21-05-19 | 09:30 | ZN35500:PA28 | URBAN | Other | Other | 1 | 105 | 7.1e-05 | 1e-06 | N
21-05-19 | 09:47 | ZN36100:PA20 | URBAN | Third Party | Other | 1 | 218 | 0.000148 | 1e-06 | N
21-05-19 | 09:50 | ZN36100:PA20 | URBAN | Third Party | Other | 1 | 216 | 0.000146 | 1e-06 | N
21-05-19 | 10:08 | ZN2835:PA33 | URBAN | Third Party | Vehicle impact | 12 | 547 | 0.004437 | 8e-06 | N
21-05-19 | 10:15 | ZN2466:PA17 | SHORT RURAL | Other | Other | 79 | 735 | 0.24183 | 0.000329 | N
21-05-19 | 12:32 | ZN12620:PA1 | SHORT RURAL | Other | Other | 1 | 78 | 0.000324 | 4e-06 | N
21-05-19 | 13:45 | ZN167:PA21 | URBAN | Third Party | Vehicle impact | 9 | 255 | 0.001552 | 6e-06 | N
21-05-19 | 14:09 | 238:34141 | SHORT RURAL | Other | Other | 1 | 72 | 0.0003 | 4e-06 | N
21-05-19 | 14:49 | ZN36300:PA3 | URBAN | Third Party | Other | 1 | 214 | 0.000145 | 1e-06 | N
21-05-19 | 15:04 | ZN965:PA47 | URBAN | Other | Other | 1 | 491 | 0.000332 | 1e-06 | N
21-05-19 | 18:55 | 801:74121 | LONG RURAL | Animal | Animal impact | 1 | 265 | 0.092646 | 0.00035 | N
21-05-19 | 22:30 | ZN3672:PA42 | URBAN | Third Party | Vehicle impact | 6 | 60 | 0.000243 | 4e-06 | N
22-05-19 | 02:52 | ZN2466:PA16 | URBAN | Asset Failure | HV | 261 | 86 | 0.01514 | 0.000177 | N
22-05-19 | 08:22 | ZN7481:PA12 | URBAN | Other | Other | 15 | 135 | 0.001374 | 1e-05 | N
21-05-19 | 12:00 | 213:33777 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 75 | 0.000312 | 4e-06 | N
22-05-19 | 09:24 | ZN129:PA47 | URBAN | Other | Other - Arcing | 1 | 275 | 0.000186 | 1e-06 | N
22-05-19 | 09:50 | ZN180:PA30 | URBAN | Third Party | Vehicle impact | 35 | 15 | 0.000355 | 2.4e-05 | N
22-05-19 | 16:45 | ZN3154:PA19 | URBAN | Third Party | Vehicle impact | 13 | 535 | 0.004704 | 9e-06 | N
22-05-19 | 13:40 | ZN9118:PA6 | URBAN | Other | Other | 1 | 119 | 8e-05 | 1e-06 | N
22-05-19 | 13:45 | ZN15011:PA10 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,335 | 0.000903 | 1e-06 | N
22-05-19 | 14:27 | 807:74183 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 108 | 0.00045 | 4e-06 | N
22-05-19 | 15:19 | ZN2196:PA18 | URBAN | Asset Failure | LV | 34 | 166 | 0.003817 | 2.3e-05 | N
22-05-19 | 15:51 | 812:19065 | SHORT RURAL | Asset Failure | LV | 1 | 187 | 0.000777 | 4e-06 | N
22-05-19 | 17:15 | 238:34141 | SHORT RURAL | Asset Failure | HV | 38 | 109 | 0.017205 | 0.000158 | N
23-05-19 | 07:53 | ZN1287:PA12 | URBAN | Asset Failure | LV | 40 | 259 | 0.006998 | 2.7e-05 | N
23-05-19 | 08:28 | 204:82699 | URBAN | Third Party | Vehicle impact | 982 | 110 | 0.072832 | 0.000664 | N
22-05-19 | 04:00 | 509:33395 | LONG RURAL | Asset Failure | Distribution substation | 2 | 405 | 0.28341 | 0.0007 | N
23-05-19 | 09:29 | ZN12650:PA1 | SHORT RURAL | Other | Other | 1 | 30 | 0.000127 | 4e-06 | N
23-05-19 | 10:29 | ZN15009:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 570 | 0.000386 | 1e-06 | N
23-05-19 | 11:06 | 814:82285 | SHORT RURAL | Asset Failure | HV | 9 | 132 | 0.004931 | 3.7e-05 | N
23-05-19 | 11:43 | ZN9900:PA12 | URBAN | Third Party | Other | 1 | 107 | 7.2e-05 | 1e-06 | N
23-05-19 | 12:37 | 508:82579 | SHORT RURAL | Asset Failure | LV | 2 | 383 | 0.00319 | 8e-06 | N
23-05-19 | 13:42 | 515:35197 | LONG RURAL | Asset Failure | HV | 39 | 230 | 3.1449 | 0.013646 | N
23-05-19 | 14:00 | ZN15006:PA13 | URBAN | Third Party | Vehicle impact | 1 | 1,050 | 0.00071 | 1e-06 | N
23-05-19 | 14:45 | 264:81240 | SHORT RURAL | Third Party | Vehicle impact | 1 | 207 | 0.000863 | 4e-06 | N
23-05-19 | 15:28 | ZN35900:PA1 | SHORT RURAL | Other | Other | 1 | 91 | 0.000378 | 4e-06 | N
23-05-19 | 20:50 | ZN35555:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 15 | 0.000355 | 2.4e-05 | N
23-05-19 | 15:36 | ZN847:PA7 | URBAN | Asset Failure | LV | 42 | 313 | 0.008895 | 2.8e-05 | N
23-05-19 | 15:46 | ZN1285:PA17 | URBAN | Third Party | Vehicle impact | 42 | 63 | 0.001797 | 2.8e-05 | N
23-05-19 | 11:34 | ZN15014:PA5 | URBAN | Asset Failure | LV | 34 | 426 | 0.009797 | 2.3e-05 | N
23-05-19 | 17:43 | ZN2310:PA10 | URBAN | Asset Failure | HV | 32 | 127 | 0.002749 | 2.2e-05 | N
23-05-19 | 17:43 | ZN2310:PA3 | URBAN | Asset Failure | HV | 1 | 127 | 8.6e-05 | 1e-06 | N
23-05-19 | 17:43 | ZN2310:PA4 | URBAN | Asset Failure | HV | 2,978 | 128 | 0.25865 | 0.002014 | N
24-05-19 | 04:28 | ZN35600:PA16 | URBAN | Other | Other | 1 | 175 | 0.000119 | 1e-06 | N
24-05-19 | 06:41 | 210:83474 | URBAN | Other | Other - Arcing | 1 | 19 | 1.3e-05 | 1e-06 | N
24-05-19 | 08:39 | 256:80640 | URBAN | Other | Other | 1 | 73 | 5e-05 | 1e-06 | N
24-05-19 | 18:30 | ZN35370:PA2 | SHORT RURAL | Asset Failure | HV | 32 | 165 | 0.02199 | 0.000133 | N
24-05-19 | 12:44 | ZN342:PA18 | URBAN | Asset Failure | LV | 34 | 3,405 | 0.078313 | 2.3e-05 | N
24-05-19 | 16:42 | ZN14892:PA1 | SHORT RURAL | Asset Failure | LV | 7 | 38 | 0.001103 | 2.9e-05 | N
24-05-19 | 14:32 | 810:74058 | SHORT RURAL | Other | Other - Self Clearing Trigger | 2 | 148 | 0.001233 | 8e-06 | N
24-05-19 | 16:33 | 516:48067 | SHORT RURAL | Third Party | Other | 2 | 142 | 0.001183 | 8e-06 | N
24-05-19 | 17:20 | ZN195:PA10 | URBAN | Asset Failure | LV | 28 | 455 | 0.008617 | 1.9e-05 | N
24-05-19 | 17:39 | ZN36100:PA2 | URBAN | Other | Other - Arcing | 1 | 230 | 0.000156 | 1e-06 | N
24-05-19 | 17:30 | ZN630:PA38 | URBAN | Asset Failure | LV | 52 | 55 | 0.001934 | 3.5e-05 | N
25-05-19 | 11:00 | 224:80341 | URBAN | Third Party | Vehicle impact | 1 | 15 | 1e-05 | 1e-06 | N
25-05-19 | 09:12 | 238:34137 | SHORT RURAL | Asset Failure | LV | 1 | 272 | 0.001133 | 4e-06 | N
25-05-19 | 09:21 | ZN340:PA4 | URBAN | Asset Failure | LV | 1 | 568 | 0.000385 | 1e-06 | N
25-05-19 | 10:05 | ZN35600:PA3 | URBAN | Third Party | Vehicle impact | 1 | 524 | 0.000355 | 1e-06 | N
25-05-19 | 12:07 | ZN965:PA4 | URBAN | Asset Failure | HV | 1,158 | 70 | 0.055062 | 0.000785 | N
25-05-19 | 16:20 | ZN180:PA10 | URBAN | Asset Failure | LV | 19 | 221 | 0.002846 | 1.3e-05 | N
25-05-19 | 16:06 | ZN3155:PA35 | URBAN | Other | Other | 1 | 3 | 2e-06 | 1e-06 | N
25-05-19 | 17:43 | 801:74120 | SHORT RURAL | Asset Failure | LV | 31 | 51 | 0.006605 | 0.000129 | N
26-05-19 | 03:01 | 232:11454 | SHORT RURAL | Asset Failure | HV | 69 | 314 | 0.090162 | 0.000287 | N
26-05-19 | 09:46 | ZN129:PA63 | URBAN | Asset Failure | HV | 707 | 70 | 0.033581 | 0.000479 | N
26-05-19 | 11:41 | 810:74054 | LONG RURAL | Asset Failure | HV | 55 | 253 | 4.865 | 0.019231 | N
26-05-19 | 15:40 | ZN4545:PA41 | SHORT RURAL | Other | Other | 1 | 45 | 0.000189 | 4e-06 | N
26-05-19 | 15:53 | ZN4545:PA41 | SHORT RURAL | Other | Other | 1 | 32 | 0.000135 | 4e-06 | N
26-05-19 | 22:44 | ZN9245:PA15 | URBAN | Animal | Animal impact | 947 | 47 | 0.030169 | 0.000642 | N
27-05-19 | 02:46 | ZN15008:PA10 | URBAN | Asset Failure | HV | 1,852 | 93 | 0.11645 | 0.001255 | N
27-05-19 | 04:18 | ZN15008:PA10 | URBAN | Asset Failure | LV | 74 | 192 | 0.00963 | 5e-05 | N
27-05-19 | 06:30 | ZN8100:PA28 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 68 | 180 | 0.050936 | 0.000283 | N
27-05-19 | 08:39 | ZN1673:PA13 | URBAN | Third Party | Vehicle impact | 3 | 81 | 0.000165 | 2e-06 | N
27-05-19 | 09:02 | 202:34250 | URBAN | Network business | Network error | 67 | 82 | 0.003728 | 4.5e-05 | N
27-05-19 | 10:34 | 532:83300 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 205 | 0.000139 | 1e-06 | N
27-05-19 | 11:09 | ZN9252:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 246 | 0.000167 | 1e-06 | N
27-05-19 | 11:37 | ZN847:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 84 | 233 | 0.013266 | 5.7e-05 | N
27-05-19 | 11:37 | ZN847:PA36 | URBAN | Vegetation | Vegetation Blow/Fall In | 22 | 233 | 0.003475 | 1.5e-05 | N
27-05-19 | 11:42 | ZN2400:PA11 | SHORT RURAL | Asset Failure | HV | 700 | 342 | 0.99567 | 0.002913 | N
27-05-19 | 13:48 | ZN35500:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 3,127 | 113 | 0.23906 | 0.00212 | N
27-05-19 | 11:59 | 528:83024 | URBAN | Other | Other | 1 | 77 | 5.3e-05 | 1e-06 | N
27-05-19 | 12:12 | 223:14398 | URBAN | Asset Failure | LV | 1 | 671 | 0.000455 | 1e-06 | N
27-05-19 | 12:30 | 512:83743 | SHORT RURAL | Other | Other | 1 | 122 | 0.000508 | 4e-06 | N
27-05-19 | 12:45 | ZN10991:PA8 | URBAN | Other | Other - Self Clearing Trigger | 58 | 184 | 0.007242 | 3.9e-05 | N
27-05-19 | 12:46 | 256:80646 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 29 | 1.9e-05 | 1e-06 | N
27-05-19 | 12:52 | ZN690:PA24 | SHORT RURAL | Other | Other - Self Clearing Trigger | 85 | 47 | 0.016737 | 0.000354 | N
27-05-19 | 12:52 | ZN35600:PA16 | URBAN | Other | Other | 1 | 78 | 5.3e-05 | 1e-06 | N
27-05-19 | 13:11 | 261:81879 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 79 | 5.3e-05 | 1e-06 | N
27-05-19 | 13:20 | ZN10994:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 100 | 6.8e-05 | 1e-06 | N
27-05-19 | 13:28 | ZN2835:PA36 | URBAN | Asset Failure | LV | 32 | 622 | 0.013491 | 2.2e-05 | N
27-05-19 | 13:30 | ZN15013:PA6 | SHORT RURAL | Weather |  | 229 | 275 | 0.26161 | 0.000953 | N
27-05-19 | 13:34 | 526:34641 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 341 | 0.005676 | 1.7e-05 | N
27-05-19 | 12:28 | ZN1290:PA12 | URBAN | Asset Failure | HV | 184 | 467 | 0.058244 | 0.000125 | N
27-05-19 | 13:37 | ZN36200:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 69 | 73 | 0.020861 | 0.000287 | N
27-05-19 | 13:45 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,098 | 152 | 0.69268 | 0.004569 | N
27-05-19 | 13:52 | 508:82574 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 188 | 0.000782 | 4e-06 | N
27-05-19 | 13:56 | ZN9252:PA30 | URBAN | Asset Failure | LV | 9 | 184 | 0.001123 | 6e-06 | N
27-05-19 | 14:31 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 24 | 165 | 0.016504 | 0.0001 | N
27-05-19 | 17:55 | ZN14891:PA12 | SHORT RURAL | Asset Failure | HV | 385 | 322 | 0.51526 | 0.001602 | N
27-05-19 | 14:12 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 216 | 298 | 0.26754 | 0.000899 | N
27-05-19 | 14:24 | ZN3472:PA28 | URBAN | Asset Failure | LV | 7 | 296 | 0.001403 | 5e-06 | N
27-05-19 | 14:29 | ZN14892:PA16 | URBAN | Other | Other | 1 | 64 | 4.3e-05 | 1e-06 | N
27-05-19 | 14:29 | 223:14395 | SHORT RURAL | Other | Other | 1 | 80 | 0.000331 | 4e-06 | N
27-05-19 | 16:50 | 243:80081 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 29 | 174 | 0.020999 | 0.000121 | N
27-05-19 | 19:25 | ZN14892:PA16 | URBAN | Vegetation | Vegetation Blow/Fall In | 43 | 105 | 0.00306 | 2.9e-05 | N
27-05-19 | 14:55 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 321 | 163 | 0.21802 | 0.001336 | N
27-05-19 | 14:41 | 243:80083 | SHORT RURAL | Asset Failure | HV | 2 | 424 | 0.003529 | 8e-06 | N
27-05-19 | 14:42 | ZN14892:PA6 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 378 | 0.000256 | 1e-06 | N
27-05-19 | 14:44 | 509:33395 | LONG RURAL | Third Party | Other | 1 | 333 | 0.1166 | 0.00035 | N
27-05-19 | 14:45 | ZN14892:PA16 | URBAN | Other | Other | 1 | 138 | 9.4e-05 | 1e-06 | N
27-05-19 | 14:45 | 243:80081 | SHORT RURAL | Asset Failure | LV | 1 | 254 | 0.001057 | 4e-06 | N
27-05-19 | 14:46 | ZN14892:PA16 | URBAN | Other | Other | 1 | 51 | 3.4e-05 | 1e-06 | N
27-05-19 | 14:48 | 270:83590 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 401 | 0.000272 | 1e-06 | N
27-05-19 | 14:49 | 522:83132 | SHORT RURAL | Third Party | Other | 1 | 131 | 0.000545 | 4e-06 | N
27-05-19 | 14:50 | 261:81870 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 190 | 0.000129 | 1e-06 | N
27-05-19 | 14:58 | 238:34147 | URBAN | Vegetation | Vegetation Blow/Fall In | 875 | 186 | 0.11052 | 0.000593 | N
27-05-19 | 15:02 | 202:34245 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 105 | 7.1e-05 | 1e-06 | N
27-05-19 | 15:04 | 206:34441 | URBAN | Third Party | Other | 1 | 294 | 0.000199 | 1e-06 | N
27-05-19 | 15:09 | 238:34148 | SHORT RURAL | Asset Failure | LV | 8 | 356 | 0.011852 | 3.3e-05 | N
27-05-19 | 15:05 | 264:81240 | SHORT RURAL | Asset Failure | HV | 123 | 146 | 0.074898 | 0.000512 | N
27-05-19 | 15:18 | 233:82815 | SHORT RURAL | Third Party | Other | 1 | 221 | 0.000921 | 4e-06 | N
27-05-19 | 15:19 | 223:14394 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,421 | 0.000963 | 1e-06 | N
27-05-19 | 15:22 | 202:34249 | URBAN | Third Party | Other | 1 | 187 | 0.000127 | 1e-06 | N
27-05-19 | 15:26 | 217:33611 | URBAN | Asset Failure | LV | 16 | 762 | 0.008261 | 1.1e-05 | N
27-05-19 | 15:09 | 512:83733 | SHORT RURAL | Weather |  | 16 | 311 | 0.020689 | 6.7e-05 | N
27-05-19 | 15:31 | 210:83465 | URBAN | Vegetation | Vegetation Blow/Fall In | 28 | 179 | 0.003397 | 1.9e-05 | N
27-05-19 | 15:32 | 232:11455 | SHORT RURAL | Other | Other - Self Clearing Trigger | 75 | 438 | 0.13656 | 0.000312 | N
27-05-19 | 15:33 | 221:11893 | URBAN | Third Party | Other | 1 | 1,075 | 0.000729 | 1e-06 | N
27-05-19 | 15:39 | 261:81876 | URBAN | Asset Failure | LV | 1 | 107 | 7.2e-05 | 1e-06 | N
27-05-19 | 15:48 | 239:82136 | URBAN | Asset Failure | LV | 1 | 516 | 0.00035 | 1e-06 | N
27-05-19 | 15:48 | 256:80646 | URBAN | Third Party | Other | 1 | 181 | 0.000123 | 1e-06 | N
27-05-19 | 15:50 | 224:80346 | URBAN | Other | Other - Self Clearing Trigger | 54 | 195 | 0.007137 | 3.7e-05 | N
27-05-19 | 15:55 | 522:83132 | SHORT RURAL | Asset Failure | LV | 1 | 121 | 0.000502 | 4e-06 | N
27-05-19 | 15:57 | 223:14393 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 364 | 0.000247 | 1e-06 | N
27-05-19 | 16:01 | 224:80346 | URBAN | Asset Failure | LV | 1 | 269 | 0.000182 | 1e-06 | N
27-05-19 | 16:08 | 270:83593 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 321 | 0.001338 | 4e-06 | N
27-05-19 | 16:08 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,185 | 0.00493 | 4e-06 | N
27-05-19 | 16:12 | 261:81870 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 431 | 0.000292 | 1e-06 | N
27-05-19 | 16:13 | 264:81238 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 102 | 0.000423 | 4e-06 | N
27-05-19 | 16:16 | 270:83593 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 224 | 0.000931 | 4e-06 | N
27-05-19 | 16:22 | 229:34983 | SHORT RURAL | Asset Failure | LV | 1 | 294 | 0.001225 | 4e-06 | N
27-05-19 | 15:19 | 512:83743 | SHORT RURAL | Other | Other | 2 | 186 | 0.001548 | 8e-06 | N
27-05-19 | 17:07 | ZN2635:PA59 | URBAN | Other | Other - Self Clearing Trigger | 8 | 337 | 0.00183 | 5e-06 | N
27-05-19 | 17:23 | ZN262:PA42 | URBAN | Vegetation | Vegetation Blow/Fall In | 125 | 61 | 0.005208 | 8.5e-05 | N
27-05-19 | 17:39 | ZN9035:PA2 | URBAN | Asset Failure | LV | 1 | 196 | 0.000133 | 1e-06 | N
27-05-19 | 17:39 | ZN9035:PA7 | URBAN | Asset Failure | LV | 28 | 197 | 0.003739 | 1.9e-05 | N
27-05-19 | 17:53 | 243:80075 | SHORT RURAL | Third Party | Other | 1 | 337 | 0.001401 | 4e-06 | N
27-05-19 | 17:45 | ZN1290:PA12 | URBAN | Network business | Switching and protection error | 38 | 150 | 0.003864 | 2.6e-05 | N
27-05-19 | 18:07 | ZN35500:PA28 | URBAN | Other | Other | 36 | 10 | 0.000244 | 2.4e-05 | N
27-05-19 | 18:00 | 270:83591 | SHORT RURAL | Asset Failure | LV | 63 | 120 | 0.031461 | 0.000262 | N
27-05-19 | 18:28 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 452 | 0.00188 | 4e-06 | N
27-05-19 | 18:30 | 528:83011 | SHORT RURAL | Other | Other | 1 | 870 | 0.00362 | 4e-06 | N
27-05-19 | 19:55 | ZN3154:PA11 | URBAN | Asset Failure | LV | 54 | 205 | 0.007503 | 3.7e-05 | N
27-05-19 | 18:37 | ZN2602:PA32 | URBAN | Other | Other - Arcing | 1 | 413 | 0.00028 | 1e-06 | N
27-05-19 | 18:44 | 511:29873 | URBAN | Other | Other | 1 | 812 | 0.00055 | 1e-06 | N
27-05-19 | 18:58 | 520:48172 | SHORT RURAL | Other | Other | 2 | 252 | 0.002097 | 8e-06 | N
27-05-19 | 19:14 | ZN35600:PA12 | SHORT RURAL | Asset Failure | LV | 69 | 151 | 0.043371 | 0.000287 | N
27-05-19 | 21:11 | 509:33399 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 21 | 489 | 0.042701 | 8.7e-05 | N
27-05-19 | 18:24 | ZN12570:PA24 | SHORT RURAL | Asset Failure | HV | 1,109 | 144 | 0.66419 | 0.004615 | N
27-05-19 | 21:55 | 265:81651 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 14 | 45 | 0.002622 | 5.8e-05 | N
27-05-19 | 22:09 | 270:83590 | URBAN | Asset Failure | LV | 69 | 36 | 0.001684 | 4.7e-05 | N
28-05-19 | 02:27 | 230:81440 | URBAN | Vegetation | Vegetation Blow/Fall In | 90 | 63 | 0.003843 | 6.1e-05 | N
28-05-19 | 12:55 | ZN14891:PA5 | SHORT RURAL | Asset Failure | HV | 13 | 185 | 0.010008 | 5.4e-05 | N
28-05-19 | 05:21 | ZN14891:PA5 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 664 | 0.019338 | 2.9e-05 | N
23-05-19 | 20:00 | ZN847:PA1 | URBAN | Asset Failure | LV | 34 | 60 | 0.00138 | 2.3e-05 | N
27-05-19 | 13:17 | 202:34250 | URBAN | Asset Failure | LV | 67 | 23 | 0.001045 | 4.5e-05 | N
28-05-19 | 05:54 | 507:80917 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 276 | 0.000187 | 1e-06 | N
28-05-19 | 07:45 | 526:34636 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 380 | 0.001581 | 4e-06 | N
27-05-19 | 15:34 | 230:81432 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 113 | 1,275 | 0.59959 | 0.00047 | N
28-05-19 | 08:15 | ZN80:PA30 | URBAN | Third Party | Dig-in | 169 | 329 | 0.037735 | 0.000115 | N
28-05-19 | 08:40 | 256:80650 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 10 | 7e-06 | 1e-06 | N
28-05-19 | 08:49 | 265:81641 | URBAN | Asset Failure | LV | 1 | 155 | 0.000105 | 1e-06 | N
28-05-19 | 10:27 | 238:34147 | URBAN | Vegetation | Vegetation Blow/Fall In | 875 | 52 | 0.030841 | 0.000593 | N
28-05-19 | 09:40 | 233:82812 | SHORT RURAL | Other | Other | 1 | 71 | 0.000297 | 4e-06 | N
28-05-19 | 10:27 | 511:29880 | URBAN | Asset Failure | HV | 16 | 48 | 0.000521 | 1.1e-05 | N
28-05-19 | 09:42 | ZN14891:PA12 | SHORT RURAL | Other | Other | 9 | 333 | 0.012472 | 3.7e-05 | N
27-05-19 | 15:00 | 512:83743 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 327 | 0.001361 | 4e-06 | N
28-05-19 | 10:50 | ZN80:PA30 | URBAN | Third Party | Dig-in | 41 | 160 | 0.004447 | 2.8e-05 | N
28-05-19 | 12:30 | ZN80:PA30 | URBAN | Third Party | Dig-in | 31 | 60 | 0.001261 | 2.1e-05 | N
28-05-19 | 13:27 | 206:34432 | URBAN | Asset Failure | LV | 1 | 118 | 8e-05 | 1e-06 | N
28-05-19 | 13:27 | ZN35500:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 40 | 32 | 0.000876 | 2.7e-05 | N
28-05-19 | 13:35 | ZN3472:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 122 | 10 | 0.000797 | 8.3e-05 | N
28-05-19 | 13:55 | 522:83126 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 24 | 440 | 0.043945 | 0.0001 | N
27-05-19 | 17:00 | ZN2400:PA11 | SHORT RURAL | Asset Failure | LV | 20 | 325 | 0.02705 | 8.3e-05 | N
28-05-19 | 15:23 | 205:12205 | URBAN | Asset Failure | LV | 1 | 81 | 5.5e-05 | 1e-06 | N
28-05-19 | 16:42 | ZN14891:PA16 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 206 | 0.000858 | 4e-06 | N
28-05-19 | 17:03 | ZN80:PA31 | URBAN | Other | Other | 15 | 32 | 0.000322 | 1e-05 | N
28-05-19 | 18:04 | 528:83020 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,452 | 30 | 0.18304 | 0.006042 | N
28-05-19 | 18:17 | ZN9245:PA19 | URBAN | Animal | Animal impact | 863 | 26 | 0.015209 | 0.000585 | N
29-05-19 | 02:52 | 221:11893 | URBAN | Third Party | Fire | 1 | 603 | 0.000409 | 1e-06 | N
29-05-19 | 07:23 | 217:33608 | URBAN | Asset Failure | LV | 1 | 462 | 0.000313 | 1e-06 | N
28-05-19 | 12:00 | 238:34148 | SHORT RURAL | Asset Failure | LV | 8 | 310 | 0.01032 | 3.3e-05 | N
29-05-19 | 09:04 | 807:74180 | SHORT RURAL | Asset Failure | LV | 1 | 366 | 0.001523 | 4e-06 | N
29-05-19 | 09:15 | ZN262:PA5 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,343 | 0.00091 | 1e-06 | N
29-05-19 | 11:32 | 221:11900 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 7 | 0.000223 | 3.2e-05 | N
29-05-19 | 10:25 | ZN36100:PA2 | URBAN | Third Party | Other | 21 | 140 | 0.001992 | 1.4e-05 | N
29-05-19 | 10:24 | 507:80925 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,514 | 77 | 0.48366 | 0.006298 | N
29-05-19 | 10:40 | ZN3472:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 55 | 25 | 0.000932 | 3.7e-05 | N
29-05-19 | 11:12 | ZN874:PA17 | URBAN | Third Party | Other | 5 | 243 | 0.000823 | 3e-06 | N
29-05-19 | 11:13 | 270:83594 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 95 | 6.4e-05 | 1e-06 | N
29-05-19 | 11:51 | 217:33611 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 194 | 0.000131 | 1e-06 | N
29-05-19 | 11:51 | ZN3472:PA11 | URBAN | Third Party | Vehicle impact | 7 | 74 | 0.000351 | 5e-06 | N
29-05-19 | 11:53 | 814:82285 | SHORT RURAL | Asset Failure | HV | 146 | 116 | 0.070583 | 0.000607 | N
29-05-19 | 12:00 | 238:34141 | SHORT RURAL | Other | Other | 1 | 163 | 0.000678 | 4e-06 | N
29-05-19 | 12:10 | ZN35400:PA77 | URBAN | Third Party | Other | 1 | 64 | 4.4e-05 | 1e-06 | N
29-05-19 | 12:16 | ZN3154:PA17 | URBAN | Other | Other - Self Clearing Trigger | 38 | 194 | 0.004996 | 2.6e-05 | N
29-05-19 | 12:17 | ZN12580:PA16 | URBAN | Other | Other - Self Clearing Trigger | 609 | 59 | 0.024349 | 0.000413 | N
29-05-19 | 12:36 | 256:80650 | URBAN | Other | Other | 25 | 119 | 0.002016 | 1.7e-05 | N
29-05-19 | 13:02 | ZN12650:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 2 | 378 | 0.003145 | 8e-06 | N
29-05-19 | 13:16 | ZN690:PA24 | SHORT RURAL | Other | Other - Self Clearing Trigger | 85 | 244 | 0.086114 | 0.000354 | N
29-05-19 | 13:20 | ZN195:PA30 | SHORT RURAL | Asset Failure | LV | 15 | 114 | 0.007122 | 6.2e-05 | N
29-05-19 | 14:01 | 229:34995 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 208 | 0.000866 | 4e-06 | N
29-05-19 | 14:17 | ZN15005:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 162 | 0.00011 | 1e-06 | N
29-05-19 | 15:51 | ZN14891:PA12 | SHORT RURAL | Other | Other - Self Clearing Trigger | 111 | 113 | 0.052179 | 0.000462 | N
29-05-19 | 16:51 | 210:83473 | URBAN | Asset Failure | LV | 1 | 138 | 9.4e-05 | 1e-06 | N
29-05-19 | 17:08 | 526:34637 | SHORT RURAL | Weather |  | 3 | 112 | 0.001398 | 1.2e-05 | N
29-05-19 | 17:43 | 509:33395 | LONG RURAL | Asset Failure | LV | 1 | 207 | 0.072378 | 0.00035 | N
30-05-19 | 13:44 | 228:7490 | URBAN | Asset Failure | HV | 55 | 126 | 0.004696 | 3.7e-05 | N
29-05-19 | 18:29 | 243:80075 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 291 | 0.00121 | 4e-06 | N
29-05-19 | 18:19 | 232:11457 | SHORT RURAL | Other | Other | 1 | 64 | 0.000267 | 4e-06 | N
29-05-19 | 18:47 | 512:83743 | SHORT RURAL | Third Party | Other | 1 | 167 | 0.000693 | 4e-06 | N
29-05-19 | 20:44 | ZN9252:PA27 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 116 | 0.000157 | 1e-06 | N
29-05-19 | 22:25 | ZN9118:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 710 | 0.000481 | 1e-06 | N
30-05-19 | 06:43 | 528:83014 | SHORT RURAL | Other | Other - Self Clearing Trigger | 6 | 197 | 0.004917 | 2.5e-05 | N
23-05-19 | 14:08 | ZN9118:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 202 | 0.006285 | 3.1e-05 | N
30-05-19 | 08:02 | 507:80917 | URBAN | Other | Other | 1 | 78 | 5.3e-05 | 1e-06 | N
23-05-19 | 16:15 | ZN10998:PA18 | URBAN | Weather |  | 109 | 165 | 0.012165 | 7.4e-05 | N
30-05-19 | 09:07 | 508:82579 | SHORT RURAL | Asset Failure | HV | 1 | 228 | 0.000948 | 4e-06 | N
30-05-19 | 09:20 | ZN1285:PA23 | URBAN | Other | Other | 1 | 70 | 4.7e-05 | 1e-06 | N
30-05-19 | 09:31 | ZN690:PA33 | URBAN | Asset Failure | HV | 1,321 | 69 | 0.061718 | 0.000895 | N
29-05-19 | 12:45 | 509:33395 | LONG RURAL | Other | Other | 1 | 55 | 0.019231 | 0.00035 | N
30-05-19 | 10:19 | ZN965:PA35 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 81 | 0.001482 | 1.8e-05 | N
30-05-19 | 10:26 | ZN12630:PA10 | SHORT RURAL | Other | Other | 9 | 99 | 0.003707 | 3.7e-05 | N
30-05-19 | 12:00 | ZN630:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 87 | 125 | 0.00737 | 5.9e-05 | N
30-05-19 | 12:52 | ZN10995:PA6 | URBAN | Asset Failure | LV | 17 | 488 | 0.005622 | 1.2e-05 | N
22-05-19 | 16:45 | ZN195:PA11 | URBAN | Asset Failure | LV | 69 | 512 | 0.023913 | 4.7e-05 | N
30-05-19 | 14:27 | ZN3154:PA18 | URBAN | Asset Failure | LV | 1 | 423 | 0.000286 | 1e-06 | N
27-05-19 | 13:39 | ZN12690:PA24 | SHORT RURAL | Other | Other - Self Clearing Trigger | 78 | 10 | 0.003246 | 0.000325 | N
27-05-19 | 16:40 | ZN12600:PA9 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 13 | 35 | 0.001893 | 5.4e-05 | N
30-05-19 | 16:53 | ZN9118:PA8 | URBAN | Asset Failure | LV | 1 | 302 | 0.000204 | 1e-06 | N
27-05-19 | 14:34 | ZN14891:PA12 | SHORT RURAL | Asset Failure | LV | 2 | 41 | 0.000341 | 8e-06 | N
30-05-19 | 18:27 | ZN35370:PA4 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 11 | 48 | 0.002197 | 4.6e-05 | N
30-05-19 | 19:12 | ZN2602:PA33 | URBAN | Network business | Network error | 273 | 88 | 0.016203 | 0.000185 | N
30-05-19 | 19:12 | ZN2602:PA35 | URBAN | Network business | Network error | 72 | 88 | 0.004294 | 4.9e-05 | N
30-05-19 | 20:38 | ZN9700:PA23 | URBAN | Other | Other - Self Clearing Trigger | 55 | 66 | 0.002469 | 3.7e-05 | N
31-05-19 | 01:00 | ZN2602:PA36 | URBAN | Third Party | Dig-in | 145 | 205 | 0.020142 | 9.8e-05 | N
31-05-19 | 01:00 | ZN2602:PA41 | URBAN | Third Party | Dig-in | 1 | 225 | 0.000152 | 1e-06 | N
31-05-19 | 01:00 | ZN35600:PA14 | URBAN | Third Party | Dig-in | 20 | 200 | 0.00271 | 1.4e-05 | N
31-05-19 | 01:00 | ZN35600:PA20 | URBAN | Third Party | Dig-in | 35 | 225 | 0.005336 | 2.4e-05 | N
31-05-19 | 01:01 | ZN15006:PA9 | URBAN | Asset Failure | HV | 2,618 | 73 | 0.12901 | 0.001774 | N
31-05-19 | 09:47 | ZN12650:PA12 | URBAN | Asset Failure | HV | 2,012 | 142 | 0.19406 | 0.001363 | N
31-05-19 | 09:55 | ZN35500:PA24 | URBAN | Third Party | Dig-in | 2,069 | 74 | 0.10375 | 0.001402 | N
31-05-19 | 09:59 | ZN35400:PA56 | URBAN | Other | Other | 18 | 271 | 0.003305 | 1.2e-05 | N
31-05-19 | 10:22 | 511:29873 | URBAN | Other | Other | 1 | 71 | 4.8e-05 | 1e-06 | N
31-05-19 | 12:09 | ZN35500:PA24 | URBAN | Third Party | Dig-in | 52 | 110 | 0.003889 | 3.5e-05 | N
31-05-19 | 11:17 | 258:80785 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 38 | 2.6e-05 | 1e-06 | N
31-05-19 | 12:55 | ZN1788:PA48 | URBAN | Asset Failure | LV | 82 | 35 | 0.001945 | 5.6e-05 | N
31-05-19 | 13:50 | ZN690:PA6 | URBAN | Other | Other | 1 | 438 | 0.000296 | 1e-06 | N
31-05-19 | 13:55 | 813:89055 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1 | 44 | 0.000185 | 4e-06 | N
31-05-19 | 15:11 | ZN10998:PA17 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 47 | 3.2e-05 | 1e-06 | N
29-05-19 | 16:36 | ZN14891:PA20 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 5 | 244 | 0.005075 | 2.1e-05 | N
31-05-19 | 15:45 | ZN2602:PA30 | URBAN | Other | Other - Arcing | 66 | 75 | 0.003343 | 4.5e-05 | N
31-05-19 | 16:30 | ZN12610:PA22 | URBAN | Other | Other | 1 | 120 | 8.1e-05 | 1e-06 | N
31-05-19 | 23:01 | 227:13015 | SHORT RURAL | Asset Failure | LV | 23 | 39 | 0.003734 | 9.6e-05 | N
31-05-19 | 19:10 | ZN1285:PA31 | URBAN | Network business | Switching and protection error | 72 | 20 | 0.000976 | 4.9e-05 | N
31-05-19 | 19:33 | 522:83126 | SHORT RURAL | Asset Failure | Distribution substation | 77 | 82 | 0.026208 | 0.000321 | N
01-06-19 | 03:29 | ZN36300:PA1 | URBAN | Animal | Animal impact | 463 | 37 | 0.011608 | 0.000314 | N
01-06-19 | 03:29 | ZN36300:PA3 | URBAN | Animal | Animal impact | 2,015 | 37 | 0.050519 | 0.001365 | N
01-06-19 | 06:29 | ZN12690:PA16 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 156 | 0.002593 | 1.7e-05 | N
01-06-19 | 06:40 | ZN340:PA32 | URBAN | Third Party | Vehicle impact | 127 | 70 | 0.006018 | 8.6e-05 | N
01-06-19 | 11:40 | 509:33395 | LONG RURAL | Asset Failure | LV | 1 | 170 | 0.059441 | 0.00035 | N
01-06-19 | 09:18 | 807:74184 | SHORT RURAL | Asset Failure | LV | 1 | 349 | 0.001453 | 4e-06 | N
01-06-19 | 12:26 | ZN12570:PA37 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,524 | 68 | 0.43255 | 0.006344 | N
01-06-19 | 12:54 | ZN1673:PA19 | URBAN | Other | Other | 1 | 160 | 0.000108 | 1e-06 | N
01-06-19 | 12:54 | ZN847:PA15 | URBAN | Other | Other | 1,346 | 160 | 0.14551 | 0.000912 | N
01-06-19 | 13:32 | 222:33600 | URBAN | Other | Other - Arcing | 1 | 269 | 0.000182 | 1e-06 | N
01-06-19 | 18:10 | ZN12600:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 8 | 22 | 0.000733 | 3.3e-05 | N
01-06-19 | 17:49 | 227:13020 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 12 | 91 | 0.004542 | 5e-05 | N
01-06-19 | 22:28 | ZN14143:PA17 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 931 | 0.003877 | 4e-06 | N
02-06-19 | 02:00 | ZN7481:PA3 | URBAN | Other | Other - Arcing | 74 | 135 | 0.006769 | 5e-05 | N
02-06-19 | 04:51 | 256:80650 | URBAN | Asset Failure | LV | 41 | 463 | 0.012864 | 2.8e-05 | N
02-06-19 | 05:38 | 221:11900 | URBAN | Other | Other | 2 | 162 | 0.000219 | 1e-06 | N
02-06-19 | 06:38 | 239:82132 | URBAN | Asset Failure | LV | 1 | 232 | 0.000157 | 1e-06 | N
02-06-19 | 08:38 | ZN14144:PA8 | URBAN | Asset Failure | LV | 1 | 507 | 0.000343 | 1e-06 | N
02-06-19 | 09:42 | ZN9245:PA15 | URBAN | Asset Failure | LV | 1 | 730 | 0.000495 | 1e-06 | N
02-06-19 | 10:43 | 228:7491 | URBAN | Asset Failure | LV | 1 | 107 | 7.2e-05 | 1e-06 | N
02-06-19 | 15:20 | ZN10999:PA4 | URBAN | Network business | Switching and protection error | 44 | 180 | 0.005367 | 3e-05 | N
02-06-19 | 16:56 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 311 | 0.10886 | 0.00035 | N
02-06-19 | 16:55 | ZN10999:PA4 | URBAN | Network business | Switching and protection error | 85 | 50 | 0.00288 | 5.8e-05 | N
02-06-19 | 19:40 | ZN10993:PA22 | URBAN | Asset Failure | LV | 68 | 96 | 0.004443 | 4.6e-05 | N
02-06-19 | 20:11 | 801:74122 | URBAN | Asset Failure | LV | 1 | 144 | 9.8e-05 | 1e-06 | N
02-06-19 | 21:46 | ZN35400:PA101 | URBAN | Third Party | Fire | 1 | 689 | 0.000467 | 1e-06 | N
03-06-19 | 00:05 | ZN35600:PA6 | URBAN | Third Party | Dig-in | 24 | 25 | 0.000407 | 1.6e-05 | N
03-06-19 | 05:06 | 258:80778 | URBAN | Other | Other - Self Clearing Trigger | 45 | 171 | 0.005214 | 3e-05 | N
03-06-19 | 09:50 | 810:74054 | LONG RURAL | Asset Failure | HV | 1 | 130 | 0.045455 | 0.00035 | N
03-06-19 | 06:31 | ZN36100:PA20 | URBAN | Other | Other - Arcing | 1 | 74 | 5e-05 | 1e-06 | N
03-06-19 | 08:42 | ZN9037:PA16 | URBAN | Other | Other | 1 | 149 | 0.000101 | 1e-06 | N
30-05-19 | 12:50 | ZN9534:PA18 | SHORT RURAL | Asset Failure | Distribution substation | 5 | 210 | 0.004368 | 2.1e-05 | N
06-05-19 | 23:00 | 523:33501 | SHORT RURAL | Animal | Animal impact | 1 | 740 | 0.003081 | 4e-06 | N
03-06-19 | 10:01 | ZN2568:PA39 | URBAN | Third Party | Dig-in | 968 | 62 | 0.040387 | 0.000656 | N
03-06-19 | 10:01 | ZN2568:PA9 | URBAN | Third Party | Dig-in | 1 | 74 | 5e-05 | 1e-06 | N
03-06-19 | 11:01 | ZN180:PA20 | URBAN | Asset Failure | LV | 132 | 88 | 0.00788 | 8.9e-05 | N
29-05-19 | 12:18 | ZN12630:PA11 | SHORT RURAL | Asset Failure | HV | 16 | 1,213 | 0.080705 | 6.7e-05 | N
03-06-19 | 12:14 | ZN2400:PA22 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,296 | 68 | 0.36685 | 0.005395 | N
03-06-19 | 12:14 | ZN847:PA47 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 78 | 0.000325 | 4e-06 | N
03-06-19 | 17:30 | ZN15008:PA7 | URBAN | Other | Other | 56 | 20 | 0.000759 | 3.8e-05 | N
03-06-19 | 18:30 | ZN2400:PA26 | URBAN | Third Party | Vehicle impact | 52 | 80 | 0.002808 | 3.5e-05 | N
03-06-19 | 17:30 | ZN1788:PA48 | URBAN | Asset Failure | LV | 61 | 45 | 0.00186 | 4.1e-05 | N
03-06-19 | 18:25 | ZN80:PA31 | URBAN | Other | Other | 1 | 177 | 0.00012 | 1e-06 | N
03-06-19 | 18:20 | ZN9035:PA8 | URBAN | Network business | Network error | 109 | 20 | 0.001477 | 7.4e-05 | N
03-06-19 | 18:40 | ZN1788:PA15 | URBAN | Animal | Animal nesting/burrowing, etc and other | 149 | 40 | 0.004039 | 0.000101 | N
03-06-19 | 19:53 | 515:35193 | SHORT RURAL | Weather |  | 1 | 61 | 0.000253 | 4e-06 | N
03-06-19 | 21:30 | ZN15014:PA7 | URBAN | Asset Failure | LV | 53 | 94 | 0.003378 | 3.6e-05 | N
03-06-19 | 21:30 | 202:34260 | URBAN | Network business | Network error | 43 | 27 | 0.000787 | 2.9e-05 | N
04-06-19 | 06:21 | ZN847:PA45 | SHORT RURAL | Other | Other - Self Clearing Trigger | 50 | 139 | 0.02892 | 0.000208 | N
03-06-19 | 11:52 | 243:80083 | SHORT RURAL | Other | Other | 1 | 2 | 8e-06 | 4e-06 | N
04-06-19 | 07:31 | 224:80341 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,250 | 48 | 0.040572 | 0.000847 | N
04-06-19 | 08:03 | ZN36200:PA8 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1,381 | 80 | 0.46252 | 0.005747 | N
04-06-19 | 08:38 | ZN12570:PA22 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1,600 | 122 | 0.81369 | 0.006658 | N
04-06-19 | 08:52 | ZN15012:PA4 | URBAN | Asset Failure | LV | 1 | 308 | 0.000209 | 1e-06 | N
04-06-19 | 09:03 | 206:34432 | URBAN | Other | Other | 1 | 131 | 8.9e-05 | 1e-06 | N
04-06-19 | 11:23 | ZN10993:PA22 | URBAN | Asset Failure | LV | 76 | 107 | 0.00549 | 5.1e-05 | N
04-06-19 | 09:54 | ZN1788:PA16 | URBAN | Weather |  | 22 | 86 | 0.001282 | 1.5e-05 | N
04-06-19 | 10:06 | ZN9700:PA15 | URBAN | Other | Other - Self Clearing Trigger | 36 | 273 | 0.006669 | 2.4e-05 | N
04-06-19 | 10:16 | ZN9118:PA8 | URBAN | Weather |  | 46 | 564 | 0.017577 | 3.1e-05 | N
04-06-19 | 10:31 | ZN2310:PA14 | URBAN | Vegetation | Vegetation Blow/Fall In | 11 | 448 | 0.00334 | 7e-06 | N
04-06-19 | 10:40 | ZN9035:PA2 | URBAN | Asset Failure | LV | 28 | 240 | 0.004549 | 1.9e-05 | N
04-06-19 | 10:37 | ZN9118:PA11 | URBAN | Asset Failure | HV | 811 | 88 | 0.048352 | 0.000549 | N
04-06-19 | 10:43 | ZN9550:PA9 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 73 | 4.9e-05 | 1e-06 | N
04-06-19 | 11:05 | ZN180:PA10 | URBAN | Other | Other - Arcing | 1 | 175 | 0.000119 | 1e-06 | N
04-06-19 | 11:03 | 507:80932 | SHORT RURAL | Asset Failure | HV | 113 | 83 | 0.038837 | 0.00047 | N
04-06-19 | 11:16 | ZN2310:PA14 | URBAN | Other | Other | 1 | 538 | 0.000365 | 1e-06 | N
04-06-19 | 11:24 | 224:80341 | URBAN | Other | Other | 1 | 55 | 3.7e-05 | 1e-06 | N
04-06-19 | 11:32 | 217:33612 | URBAN | Vegetation | Vegetation Blow/Fall In | 114 | 232 | 0.017953 | 7.7e-05 | N
04-06-19 | 11:32 | 230:81432 | SHORT RURAL | Asset Failure | HV | 700 | 137 | 0.39875 | 0.002913 | N
04-06-19 | 11:37 | ZN9700:PA18 | URBAN | Weather |  | 29 | 142 | 0.002795 | 2e-05 | N
04-06-19 | 11:43 | ZN35500:PA28 | URBAN | Other | Other - Self Clearing Trigger | 66 | 112 | 0.004992 | 4.5e-05 | N
04-06-19 | 11:45 | ZN36300:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 134 | 9.1e-05 | 1e-06 | N
04-06-19 | 12:01 | ZN14892:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 2 | 434 | 0.000588 | 1e-06 | N
04-06-19 | 12:05 | ZN15005:PA8 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 235 | 0.000159 | 1e-06 | N
04-06-19 | 12:08 | ZN14892:PA8 | URBAN | Other | Other | 1 | 39 | 2.7e-05 | 1e-06 | N
04-06-19 | 12:08 | ZN262:PA6 | URBAN | Other | Other - Self Clearing Trigger | 79 | 203 | 0.010872 | 5.4e-05 | N
04-06-19 | 12:10 | ZN35800:PA6 | URBAN | Other | Other - Self Clearing Trigger | 31 | 110 | 0.002308 | 2.1e-05 | N
04-06-19 | 12:11 | ZN15006:PA2 | URBAN | Asset Failure | LV | 65 | 184 | 0.008103 | 4.4e-05 | N
04-06-19 | 12:25 | ZN3672:PA46 | URBAN | Other | Other - Arcing | 1 | 215 | 0.000146 | 1e-06 | N
04-06-19 | 12:56 | ZN35600:PA1 | URBAN | Asset Failure | LV | 18 | 49 | 0.000595 | 1.2e-05 | N
04-06-19 | 13:06 | ZN3672:PA36 | URBAN | Asset Failure | LV | 1 | 174 | 0.000118 | 1e-06 | N
04-06-19 | 13:07 | ZN9550:PA36 | URBAN | Other | Other - Self Clearing Trigger | 49 | 207 | 0.006873 | 3.3e-05 | N
04-06-19 | 13:15 | ZN15006:PA13 | URBAN | Asset Failure | LV | 33 | 125 | 0.002795 | 2.2e-05 | N
04-06-19 | 14:50 | ZN180:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 70 | 200 | 0.009485 | 4.7e-05 | N
04-06-19 | 14:09 | ZN12640:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 24 | 196 | 0.019574 | 0.0001 | N
04-06-19 | 14:14 | 232:33413 | SHORT RURAL | Other | Other | 1 | 57 | 0.000237 | 4e-06 | N
04-06-19 | 14:15 | 232:33413 | SHORT RURAL | Other | Other | 1 | 54 | 0.000226 | 4e-06 | N
04-06-19 | 14:20 | ZN1788:PA43 | URBAN | Vegetation | Vegetation Blow/Fall In | 108 | 30 | 0.002195 | 7.3e-05 | N
04-06-19 | 14:38 | ZN15001:PA2 | URBAN | Asset Failure | LV | 2 | 414 | 0.000561 | 1e-06 | N
04-06-19 | 14:40 | ZN12620:PA11 | SHORT RURAL | Other | Other | 1 | 42 | 0.000174 | 4e-06 | N
04-06-19 | 14:50 | ZN1788:PA44 | URBAN | Other | Other - Arcing | 1 | 313 | 0.000212 | 1e-06 | N
04-06-19 | 14:53 | ZN15001:PA18 | URBAN | Asset Failure | LV | 1 | 632 | 0.000428 | 1e-06 | N
04-06-19 | 18:25 | ZN12600:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 18 | 30 | 0.002247 | 7.5e-05 | N
04-06-19 | 16:07 | ZN15010:PA28 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 68 | 283 | 0.080079 | 0.000283 | N
04-06-19 | 15:30 | ZN9252:PA31 | URBAN | Vegetation | Vegetation Blow/Fall In | 32 | 35 | 0.000759 | 2.2e-05 | N
04-06-19 | 15:30 | ZN847:PA47 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 35 | 80 | 0.011579 | 0.000146 | N
04-06-19 | 15:34 | ZN15002:PA4 | SHORT RURAL | Other | Other - Arcing | 1 | 591 | 0.002461 | 4e-06 | N
04-06-19 | 15:52 | 232:33413 | SHORT RURAL | Asset Failure | LV | 1 | 230 | 0.000956 | 4e-06 | N
04-06-19 | 16:08 | ZN262:PA19 | URBAN | Asset Failure | LV | 64 | 341 | 0.014792 | 4.3e-05 | N
04-06-19 | 16:17 | ZN12620:PA11 | SHORT RURAL | Asset Failure | HV | 831 | 164 | 0.56829 | 0.003458 | N
04-06-19 | 16:26 | ZN36300:PA5 | URBAN | Other | Other - Arcing | 1 | 1,053 | 0.000714 | 1e-06 | N
04-06-19 | 16:27 | ZN10995:PA13 | URBAN | Asset Failure | LV | 1 | 93 | 6.3e-05 | 1e-06 | N
05-06-19 | 12:28 | ZN2466:PA5 | URBAN | Other | Other - Self Clearing Trigger | 2 | 242 | 0.000328 | 1e-06 | N
04-06-19 | 16:17 | ZN12620:PA3 | URBAN | Other | Other | 74 | 188 | 0.009425 | 5e-05 | N
04-06-19 | 17:24 | ZN12570:PA22 | SHORT RURAL | Asset Failure | HV | 1,412 | 53 | 0.31141 | 0.005876 | N
04-06-19 | 17:39 | ZN12640:PA13 | SHORT RURAL | Other | Other | 1 | 193 | 0.000805 | 4e-06 | N
04-06-19 | 18:03 | ZN12610:PA6 | URBAN | Asset Failure | LV | 75 | 327 | 0.016605 | 5.1e-05 | N
04-06-19 | 18:11 | ZN12690:PA24 | SHORT RURAL | Other | Other - Arcing | 1 | 1,111 | 0.004622 | 4e-06 | N
04-06-19 | 18:35 | ZN15008:PA10 | URBAN | Asset Failure | LV | 74 | 309 | 0.015509 | 5e-05 | N
04-06-19 | 22:30 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 11 | 135 | 0.51887 | 0.003843 | N
04-06-19 | 18:55 | ZN4545:PA40 | URBAN | Other | Other | 1 | 148 | 0.0001 | 1e-06 | N
04-06-19 | 19:01 | ZN15004:PA5 | URBAN | Third Party | Other | 1 | 1,108 | 0.000751 | 1e-06 | N
04-06-19 | 19:44 | ZN12610:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 620 | 37 | 0.015542 | 0.00042 | N
04-06-19 | 20:12 | ZN9252:PA27 | URBAN | Asset Failure | LV | 1 | 879 | 0.000595 | 1e-06 | N
04-06-19 | 20:49 | ZN15006:PA9 | URBAN | Vegetation | Vegetation Grow In | 1 | 165 | 0.000112 | 1e-06 | N
05-06-19 | 00:30 | 232:33407 | SHORT RURAL | Asset Failure | HV | 22 | 414 | 0.037926 | 9.2e-05 | N
04-06-19 | 21:31 | ZN35600:PA6 | URBAN | Asset Failure | LV | 1 | 1,259 | 0.000853 | 1e-06 | N
04-06-19 | 22:33 | ZN10994:PA19 | URBAN | Third Party | Other | 1 | 387 | 0.000262 | 1e-06 | N
04-06-19 | 22:41 | ZN2310:PA24 | URBAN | Other | Other - Arcing | 70 | 38 | 0.001811 | 4.7e-05 | N
04-06-19 | 23:19 | ZN2568:PA29 | URBAN | Other | Other - Arcing | 89 | 81 | 0.004869 | 6e-05 | N
04-06-19 | 23:31 | ZN2602:PA28 | URBAN | Third Party | Fire | 1 | 49 | 3.3e-05 | 1e-06 | N
04-06-19 | 23:33 | ZN901:PA20 | URBAN | Asset Failure | LV | 1 | 116 | 7.9e-05 | 1e-06 | N
05-06-19 | 02:10 | 232:11454 | SHORT RURAL | Asset Failure | HV | 1,882 | 82 | 0.63925 | 0.007831 | N
05-06-19 | 07:30 | 213:33777 | SHORT RURAL | Other | Other | 1 | 89 | 0.000371 | 4e-06 | N
04-06-19 | 10:10 | ZN2310:PA14 | URBAN | Asset Failure | LV | 40 | 60 | 0.001626 | 2.7e-05 | N
05-06-19 | 08:02 | ZN4545:PA21 | URBAN | Other | Other - Arcing | 1 | 147 | 0.0001 | 1e-06 | N
05-06-19 | 08:50 | 270:83590 | URBAN | Other | Other | 1 | 70 | 4.7e-05 | 1e-06 | N
05-06-19 | 08:59 | ZN9700:PA17 | URBAN | Other | Other - Arcing | 1 | 1,381 | 0.000936 | 1e-06 | N
05-06-19 | 09:47 | 258:80784 | URBAN | Asset Failure | Distribution substation | 77 | 57 | 0.002989 | 5.2e-05 | N
05-06-19 | 09:58 | 229:34995 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 26 | 0.00011 | 4e-06 | N
05-06-19 | 09:59 | 229:34995 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 25 | 0.000104 | 4e-06 | N
05-06-19 | 09:58 | ZN15011:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1,703 | 104 | 0.12051 | 0.001154 | N
05-06-19 | 11:32 | 509:33395 | LONG RURAL | Vegetation | Vegetation Blow/Fall In | 754 | 211 | 55.5786 | 0.26345 | N
05-06-19 | 11:52 | 216:10726 | URBAN | Other | Other | 1 | 207 | 0.000141 | 1e-06 | N
05-06-19 | 11:59 | ZN12690:PA6 | URBAN | Other | Other | 1 | 496 | 0.000336 | 1e-06 | N
05-06-19 | 17:26 | ZN711:PA25 | URBAN | Asset Failure | LV | 30 | 219 | 0.004451 | 2e-05 | N
05-06-19 | 12:17 | 224:80326 | URBAN | Other | Other | 1 | 115 | 7.8e-05 | 1e-06 | N
05-06-19 | 13:38 | ZN36800:PA31 | URBAN | Asset Failure | LV | 1 | 81 | 5.5e-05 | 1e-06 | N
05-06-19 | 15:36 | ZN12620:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 248 | 0.001033 | 4e-06 | N
05-06-19 | 18:40 | ZN2568:PA32 | URBAN | Other | Other - Self Clearing Trigger | 101 | 50 | 0.00342 | 6.8e-05 | N
05-06-19 | 18:59 | ZN36800:PA33 | URBAN | Asset Failure | LV | 1 | 780 | 0.000529 | 1e-06 | N
05-06-19 | 18:59 | ZN36800:PA33 | URBAN | Third Party | Other | 1 | 1,440 | 0.000976 | 1e-06 | N
05-06-19 | 23:30 | ZN1850:PA31 | URBAN | Asset Failure | LV | 33 | 70 | 0.001565 | 2.2e-05 | N
05-06-19 | 23:30 | ZN3472:PA30 | URBAN | Asset Failure | LV | 43 | 70 | 0.002039 | 2.9e-05 | N
05-06-19 | 22:33 | ZN3672:PA44 | URBAN | Third Party | Vehicle impact | 50 | 1,261 | 0.0427 | 3.4e-05 | N
05-06-19 | 23:25 | 511:29877 | SHORT RURAL | Third Party | Vehicle impact | 75 | 75 | 0.023407 | 0.000312 | N
05-06-19 | 22:25 | ZN15001:PA15 | URBAN | Asset Failure | LV | 1 | 904 | 0.000613 | 1e-06 | N
05-06-19 | 23:10 | ZN188:PA44 | URBAN | Asset Failure | LV | 212 | 35 | 0.005027 | 0.000144 | N
06-06-19 | 02:40 | ZN690:PA24 | SHORT RURAL | Third Party | Fire | 2 | 695 | 0.005784 | 8e-06 | N
06-06-19 | 10:15 | ZN2568:PA39 | URBAN | Other | Other - Arcing | 1 | 871 | 0.00059 | 1e-06 | N
06-06-19 | 12:20 | ZN2568:PA32 | URBAN | Vegetation | Vegetation Blow/Fall In | 101 | 60 | 0.004106 | 6.8e-05 | N
06-06-19 | 13:17 | 502:48004 | URBAN | Other | Other | 1 | 185 | 0.000125 | 1e-06 | N
06-06-19 | 13:53 | ZN10995:PA13 | URBAN | Asset Failure | LV | 35 | 337 | 0.007986 | 2.4e-05 | N
06-06-19 | 14:09 | 265:81651 | SHORT RURAL | Other | Other - Self Clearing Trigger | 9 | 121 | 0.004532 | 3.7e-05 | N
06-06-19 | 14:49 | ZN35600:PA6 | URBAN | Asset Failure | HV | 1,256 | 143 | 0.12148 | 0.000851 | N
06-06-19 | 15:01 | ZN35600:PA2 | URBAN | Network business | Network error | 26 | 304 | 0.005358 | 1.8e-05 | N
06-06-19 | 15:05 | ZN36800:PA33 | URBAN | Asset Failure | LV | 104 | 185 | 0.013035 | 7e-05 | N
06-06-19 | 15:22 | ZN2400:PA21 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 380 | 0.000257 | 1e-06 | N
06-06-19 | 15:55 | 223:14397 | URBAN | Other | Other | 68 | 25 | 0.001152 | 4.6e-05 | N
06-06-19 | 16:30 | ZN342:PA28 | URBAN | Asset Failure | LV | 159 | 380 | 0.040936 | 0.000108 | N
06-06-19 | 16:57 | ZN15005:PA6 | URBAN | Third Party | Vehicle impact | 1 | 431 | 0.000292 | 1e-06 | N
06-06-19 | 18:39 | ZN4545:PA40 | URBAN | Other | Other | 1 | 129 | 8.7e-05 | 1e-06 | N
07-06-19 | 05:00 | ZN195:PA22 | URBAN | Third Party | Vehicle impact | 56 | 480 | 0.018205 | 3.8e-05 | N
07-06-19 | 07:55 | ZN129:PA34 | URBAN | Other | Other | 1 | 165 | 0.000112 | 1e-06 | N
07-06-19 | 08:17 | ZN129:PA47 | URBAN | Asset Failure | LV | 51 | 89 | 0.003091 | 3.5e-05 | N
07-06-19 | 09:00 | ZN1850:PA45 | URBAN | Other | Other - Self Clearing Trigger | 4 | 210 | 0.000569 | 3e-06 | N
07-06-19 | 09:01 | 202:34231 37 42 | URBAN | Other | Other - Self Clearing Trigger | 6 | 162 | 0.000659 | 4e-06 | N
07-06-19 | 09:01 | 202:34240 | URBAN | Other | Other - Self Clearing Trigger | 30 | 162 | 0.003293 | 2e-05 | N
07-06-19 | 12:00 | 801:74117 | SHORT RURAL | Asset Failure | LV | 31 | 45 | 0.005805 | 0.000129 | N
07-06-19 | 10:08 | ZN931:PA12 | URBAN | Asset Failure | LV | 22 | 24 | 0.000358 | 1.5e-05 | N
07-06-19 | 10:16 | ZN4545:PA40 | URBAN | Network business | Network error | 47 | 164 | 0.005222 | 3.2e-05 | N
07-06-19 | 08:55 | ZN2400:PA26 | URBAN | Third Party | Vehicle impact | 127 | 1,500 | 0.12907 | 8.6e-05 | N
07-06-19 | 10:43 | ZN12620:PA2 | SHORT RURAL | Asset Failure | Distribution substation | 45 | 95 | 0.017702 | 0.000187 | N
07-06-19 | 10:43 | ZN12620:PA2 | SHORT RURAL | Asset Failure | Distribution substation | 90 | 101 | 0.037838 | 0.000375 | N
07-06-19 | 13:30 | ZN36300:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 127 | 165 | 0.014198 | 8.6e-05 | N
07-06-19 | 11:20 | 256:80641 | URBAN | Asset Failure | LV | 29 | 30 | 0.000589 | 2e-05 | N
07-06-19 | 11:30 | ZN2835:PA15 | URBAN | Asset Failure | LV | 1 | 55 | 3.7e-05 | 1e-06 | N
07-06-19 | 13:00 | 810:74054 | LONG RURAL | Asset Failure | HV | 47 | 69 | 1.1405 | 0.016422 | N
07-06-19 | 14:35 | 202:34231 37 42 | URBAN | Third Party | Dig-in | 6 | 135 | 0.000549 | 4e-06 | N
07-06-19 | 14:35 | 202:34240 | URBAN | Third Party | Dig-in | 31 | 135 | 0.002835 | 2.1e-05 | N
07-06-19 | 12:31 | 511:29873 | URBAN | Other | Other | 1 | 75 | 5.1e-05 | 1e-06 | N
08-06-19 | 02:30 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 25 | 20 | 0.00208 | 0.000104 | N
07-06-19 | 13:51 | 520:48172 | SHORT RURAL | Asset Failure | HV | 5 | 73 | 0.001515 | 2.1e-05 | N
08-06-19 | 01:00 | ZN195:PA23 | URBAN | Third Party | Other | 19 | 25 | 0.000322 | 1.3e-05 | N
07-06-19 | 15:26 | 807:74180 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 44 | 0.001282 | 2.9e-05 | N
07-06-19 | 14:05 | ZN2400:PA26 | URBAN | Third Party | Vehicle impact | 81 | 145 | 0.007937 | 5.5e-05 | N
07-06-19 | 14:18 | ZN2196:PA26 | URBAN | Other | Other - Self Clearing Trigger | 1 | 32 | 2.2e-05 | 1e-06 | N
07-06-19 | 14:44 | ZN931:PA26 | URBAN | Other | Other - Self Clearing Trigger | 48 | 50 | 0.001631 | 3.3e-05 | N
07-06-19 | 18:30 | ZN15015:PA5 | URBAN | Other | Other - Arcing | 79 | 110 | 0.005888 | 5.4e-05 | N
07-06-19 | 16:19 | ZN36200:PA11 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 91 | 6.2e-05 | 1e-06 | N
07-06-19 | 17:08 | ZN12610:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 1,283 | 0.00534 | 4e-06 | N
07-06-19 | 08:50 | ZN3155:PA33 | URBAN | Asset Failure | LV | 52 | 610 | 0.021485 | 3.5e-05 | N
07-06-19 | 17:26 | 261:81870 | URBAN | Asset Failure | LV | 104 | 53 | 0.00374 | 7e-05 | N
07-06-19 | 19:00 | ZN901:PA18 | URBAN | Asset Failure | LV | 1 | 354 | 0.00024 | 1e-06 | N
07-06-19 | 19:59 | ZN10999:PA36 | URBAN | Third Party | Vehicle impact | 2,414 | 43 | 0.070329 | 0.001636 | N
07-06-19 | 20:22 | ZN12610:PA13 | SHORT RURAL | Asset Failure | LV | 59 | 276 | 0.067683 | 0.000246 | N
07-06-19 | 20:30 | ZN12610:PA13 | SHORT RURAL | Asset Failure | LV | 63 | 225 | 0.058985 | 0.000262 | N
08-06-19 | 07:42 | ZN2568:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 84 | 1,068 | 0.060771 | 5.7e-05 | N
08-06-19 | 11:36 | 223:14393 | URBAN | Asset Failure | LV | 111 | 49 | 0.003649 | 7.5e-05 | N
08-06-19 | 09:34 | 507:80914 | SHORT RURAL | Asset Failure | LV | 1 | 478 | 0.00199 | 4e-06 | N
08-06-19 | 11:57 | ZN2400:PA26 | URBAN | Asset Failure | LV | 38 | 542 | 0.013954 | 2.6e-05 | N
08-06-19 | 12:34 | 507:80931 | URBAN | Other | Other - Arcing | 1 | 235 | 0.000159 | 1e-06 | N
08-06-19 | 12:59 | ZN12570:PA24 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 475 | 0.001976 | 4e-06 | N
08-06-19 | 22:15 | ZN14892:PA16 | URBAN | Third Party | Vehicle impact | 26 | 128 | 0.002254 | 1.8e-05 | N
08-06-19 | 16:56 | ZN12630:PA1 | SHORT RURAL | Asset Failure | LV | 1 | 144 | 0.000599 | 4e-06 | N
08-06-19 | 20:30 | 261:81876 | URBAN | Third Party | Vehicle impact | 78 | 511 | 0.027007 | 5.3e-05 | N
08-06-19 | 21:07 | ZN2400:PA26 | URBAN | Asset Failure | HV | 127 | 923 | 0.079406 | 8.6e-05 | N
09-06-19 | 05:53 | ZN690:PA12 | URBAN | Third Party | Vehicle impact | 46 | 697 | 0.021718 | 3.1e-05 | N
09-06-19 | 12:58 | 232:33413 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 80 | 63 | 0.021005 | 0.000333 | N
09-06-19 | 14:50 | 227:13015 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 70 | 0.000291 | 4e-06 | N
09-06-19 | 11:57 | ZN3472:PA33 | URBAN | Other | Other | 1 | 363 | 0.000246 | 1e-06 | N
10-06-19 | 06:52 | ZN2835:PA31 | URBAN | Asset Failure | HV | 1,278 | 99 | 0.08605 | 0.000866 | N
10-06-19 | 09:36 | ZN12570:PA39 | URBAN | Other | Other | 1 | 68 | 4.6e-05 | 1e-06 | N
10-06-19 | 12:47 | ZN2310:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 51 | 283 | 0.009776 | 3.5e-05 | N
10-06-19 | 13:16 | ZN35800:PA16 | URBAN | Third Party | Vehicle impact | 1 | 1,183 | 0.000802 | 1e-06 | N
10-06-19 | 22:13 | ZN10991:PA12 | URBAN | Asset Failure | LV | 93 | 97 | 0.006081 | 6.3e-05 | N
10-06-19 | 23:30 | ZN262:PA15 | URBAN | Asset Failure | LV | 67 | 60 | 0.002723 | 4.5e-05 | N
10-06-19 | 23:53 | ZN965:PA8 | URBAN | Other | Other - Self Clearing Trigger | 21 | 116 | 0.001651 | 1.4e-05 | N
11-06-19 | 08:31 | 807:74184 | SHORT RURAL | Third Party | Other | 5 | 234 | 0.004867 | 2.1e-05 | N
09-06-19 | 10:55 | ZN180:PA20 | URBAN | Asset Failure | LV | 3 | 1,850 | 0.003759 | 2e-06 | N
09-06-19 | 10:55 | ZN180:PA21 | URBAN | Asset Failure | LV | 2 | 1,850 | 0.002506 | 1e-06 | N
11-06-19 | 09:02 | ZN10995:PA7 | URBAN | Third Party | Vehicle impact | 1 | 343 | 0.000232 | 1e-06 | N
11-06-19 | 13:10 | ZN10995:PA7 | URBAN | Other | Other | 884 | 13 | 0.007784 | 0.000599 | N
11-06-19 | 09:32 | 513:48050 | SHORT RURAL | Other | Other | 1 | 89 | 0.00037 | 4e-06 | N
11-06-19 | 10:39 | 229:34995 | SHORT RURAL | Other | Other | 1 | 115 | 0.000479 | 4e-06 | N
07-06-19 | 14:26 | 204:82689 | URBAN | Asset Failure | LV | 70 | 6 | 0.000285 | 4.7e-05 | N
11-06-19 | 11:31 | 204:82691 | URBAN | Network business | Network error | 35 | 164 | 0.003888 | 2.4e-05 | N
11-06-19 | 11:34 | 222:33602 | URBAN | Other | Other | 1 | 40 | 2.7e-05 | 1e-06 | N
11-06-19 | 12:07 | 528:83024 | URBAN | Asset Failure | LV | 1 | 503 | 0.00034 | 1e-06 | N
11-06-19 | 12:52 | 810:74050 | SHORT RURAL | Asset Failure | HV | 28 | 43 | 0.005042 | 0.000116 | N
11-06-19 | 16:43 | ZN12600:PA3 | URBAN | Other | Other | 1 | 78 | 5.3e-05 | 1e-06 | N
11-06-19 | 16:56 | ZN12600:PA3 | URBAN | Asset Failure | LV | 1 | 207 | 0.000141 | 1e-06 | N
11-06-19 | 15:30 | ZN3155:PA32 | URBAN | Asset Failure | LV | 113 | 288 | 0.022044 | 7.7e-05 | N
11-06-19 | 17:54 | 232:11457 | SHORT RURAL | Asset Failure | LV | 1 | 499 | 0.002077 | 4e-06 | N
11-06-19 | 22:45 | 202:34260 | URBAN | Asset Failure | LV | 43 | 70 | 0.002039 | 2.9e-05 | N
11-06-19 | 23:30 | ZN3672:PA13 | URBAN | Other | Other - Arcing | 1 | 204 | 0.000138 | 1e-06 | N
12-06-19 | 02:36 | 528:83011 | SHORT RURAL | Third Party | Vehicle impact | 68 | 170 | 0.048076 | 0.000283 | N
12-06-19 | 04:34 | ZN15005:PA2 | URBAN | Third Party | Vehicle impact | 63 | 440 | 0.01877 | 4.3e-05 | N
12-06-19 | 06:21 | ZN7900:PA1 | URBAN | Asset Failure | LV | 7 | 839 | 0.003978 | 5e-06 | N
12-06-19 | 06:48 | 806:82667 | SHORT RURAL | Asset Failure | HV | 1 | 457 | 0.001901 | 4e-06 | N
12-06-19 | 08:07 | ZN2466:PA26 | URBAN | Third Party | Dig-in | 234 | 89 | 0.014129 | 0.000159 | N
12-06-19 | 10:30 | ZN35900:PA24 | URBAN | Other | Other | 1 | 64 | 4.4e-05 | 1e-06 | N
12-06-19 | 11:49 | 261:81876 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,170 | 0.000792 | 1e-06 | N
08-06-19 | 03:40 | ZN10997:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 35 | 50 | 0.001185 | 2.4e-05 | N
08-06-19 | 03:40 | ZN10999:PA15 | URBAN | Vegetation | Vegetation Blow/Fall In | 15 | 50 | 0.000508 | 1e-05 | N
12-06-19 | 16:15 | 807:74184 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 75 | 0.000312 | 4e-06 | N
11-06-19 | 10:25 | 515:35197 | LONG RURAL | Asset Failure | LV | 4 | 125 | 0.17464 | 0.001397 | N
11-06-19 | 15:35 | 812:19072 | SHORT RURAL | Asset Failure | LV | 1 | 30 | 0.000125 | 4e-06 | N
11-06-19 | 09:50 | ZN15004:PA9 | URBAN | Other | Other | 32 | 20 | 0.000434 | 2.2e-05 | N
08-06-19 | 12:35 | ZN2568:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 72 | 775 | 0.037799 | 4.9e-05 | N
07-06-19 | 11:55 | 256:80641 | URBAN | Asset Failure | LV | 53 | 55 | 0.001975 | 3.6e-05 | N
12-06-19 | 21:30 | ZN3155:PA12 | URBAN | Other | Other | 35 | 100 | 0.002371 | 2.4e-05 | N
12-06-19 | 21:30 | ZN3155:PA16 | URBAN | Other | Other | 50 | 220 | 0.007451 | 3.4e-05 | N
13-06-19 | 04:35 | ZN9245:PA15 | URBAN | Asset Failure | HV | 947 | 66 | 0.042517 | 0.000641 | N
13-06-19 | 07:23 | ZN1788:PA47 | URBAN | Third Party | Vehicle impact | 46 | 416 | 0.01297 | 3.1e-05 | N
13-06-19 | 07:57 | 528:83019 | SHORT RURAL | Other | Other - Self Clearing Trigger | 4 | 138 | 0.002296 | 1.7e-05 | N
12-06-19 | 16:02 | 514:18137 | SHORT RURAL | Asset Failure | LV | 2 | 63 | 0.000524 | 8e-06 | N
13-06-19 | 13:52 | ZN9700:PA24 | URBAN | Asset Failure | LV | 1 | 466 | 0.000315 | 1e-06 | N
13-06-19 | 14:09 | ZN2835:PA28 | URBAN | Network business | Switching and protection error | 84 | 16 | 0.000904 | 5.7e-05 | N
13-06-19 | 14:38 | ZN10997:PA11 | URBAN | Asset Failure | LV | 1 | 420 | 0.000285 | 1e-06 | N
13-06-19 | 16:10 | 814:82283 | SHORT RURAL | Asset Failure | HV | 10 | 80 | 0.003328 | 4.2e-05 | N
13-06-19 | 20:10 | 511:29880 | URBAN | Asset Failure | HV | 227 | 60 | 0.009226 | 0.000154 | N
13-06-19 | 17:11 | ZN15002:PA6 | URBAN | Asset Failure | LV | 1 | 107 | 7.3e-05 | 1e-06 | N
14-06-19 | 02:36 | ZN1290:PA12 | URBAN | Other | Other | 30 | 566 | 0.011502 | 2e-05 | N
14-06-19 | 05:07 | ZN2196:PA20 | URBAN | Asset Failure | LV | 1 | 264 | 0.000179 | 1e-06 | N
14-06-19 | 07:52 | ZN15006:PA13 | URBAN | Third Party | Vehicle impact | 40 | 198 | 0.005365 | 2.7e-05 | N
14-06-19 | 07:20 | 217:33611 | URBAN | Asset Failure | LV | 20 | 340 | 0.004606 | 1.4e-05 | N
14-06-19 | 08:35 | ZN2196:PA20 | URBAN | Asset Failure | LV | 7 | 35 | 0.000166 | 5e-06 | N
14-06-19 | 10:20 | ZN2196:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 74 | 25 | 0.001253 | 5e-05 | N
07-06-19 | 05:00 | ZN195:PA22 | URBAN | Third Party | Vehicle impact | 16 | 490 | 0.005312 | 1.1e-05 | N
14-06-19 | 11:54 | ZN14144:PA7 | SHORT RURAL | Asset Failure | LV | 10 | 375 | 0.015617 | 4.2e-05 | N
14-06-19 | 11:51 | ZN3155:PA33 | URBAN | Asset Failure | HV | 1 | 57 | 3.9e-05 | 1e-06 | N
14-06-19 | 11:51 | ZN3155:PA44 | URBAN | Asset Failure | HV | 2,136 | 57 | 0.082473 | 0.001447 | N
14-06-19 | 21:30 | ZN10999:PA10 | URBAN | Other | Other - Arcing | 58 | 40 | 0.001572 | 3.9e-05 | N
14-06-19 | 12:56 | ZN35600:PA3 | URBAN | Asset Failure | LV | 50 | 474 | 0.016054 | 3.4e-05 | N
14-06-19 | 13:53 | ZN9037:PA10 | URBAN | Other | Other | 1 | 51 | 3.5e-05 | 1e-06 | N
14-06-19 | 13:55 | ZN9037:PA10 | URBAN | Other | Other | 1 | 50 | 3.4e-05 | 1e-06 | N
14-06-19 | 14:02 | ZN9037:PA10 | URBAN | Other | Other | 1 | 43 | 2.9e-05 | 1e-06 | N
14-06-19 | 14:07 | ZN9037:PA10 | URBAN | Other | Other | 1 | 37 | 2.5e-05 | 1e-06 | N
14-06-19 | 20:59 | ZN35800:PA21 | URBAN | Asset Failure | LV | 3 | 1,426 | 0.002898 | 2e-06 | N
14-06-19 | 21:08 | ZN3472:PA22 | URBAN | Vegetation | Vegetation Blow/Fall In | 53 | 10 | 0.000353 | 3.6e-05 | N
14-06-19 | 16:38 | 801:74121 | LONG RURAL | Asset Failure | HV | 15 | 48 | 0.25166 | 0.005243 | N
14-06-19 | 22:57 | ZN35500:PA32 | URBAN | Third Party | Dig-in | 539 | 90 | 0.032869 | 0.000365 | N
14-06-19 | 23:14 | ZN8000:PA1 | URBAN | Other | Other | 37 | 85 | 0.002138 | 2.5e-05 | N
14-06-19 | 23:52 | 524:33580 | SHORT RURAL | Other | Other | 1 | 308 | 0.001281 | 4e-06 | N
15-06-19 | 10:02 | 243:80083 | SHORT RURAL | Other | Other - Self Clearing Trigger | 20 | 127 | 0.010582 | 8.3e-05 | N
15-06-19 | 14:50 | 227:13020 | SHORT RURAL | Other | Other | 117 | 24 | 0.011673 | 0.000487 | N
15-06-19 | 10:35 | 524:33572 | SHORT RURAL | Asset Failure | LV | 16 | 354 | 0.023562 | 6.7e-05 | N
15-06-19 | 13:00 | ZN35600:PA3 | URBAN | Asset Failure | LV | 50 | 29 | 0.000977 | 3.4e-05 | N
15-06-19 | 18:37 | ZN188:PA37 | URBAN | Other | Other - Arcing | 1 | 397 | 0.000269 | 1e-06 | N
15-06-19 | 20:56 | ZN35500:PA28 | URBAN | Asset Failure | LV | 1 | 334 | 0.000226 | 1e-06 | N
15-06-19 | 21:45 | ZN1850:PA40 | URBAN | Asset Failure | HV | 925 | 53 | 0.03345 | 0.000627 | N
15-06-19 | 21:53 | ZN965:PA20 | URBAN | Asset Failure | HV | 8 | 177 | 0.000959 | 5e-06 | N
15-06-19 | 21:53 | ZN965:PA24 | URBAN | Asset Failure | HV | 1,053 | 114 | 0.081315 | 0.000713 | N
15-06-19 | 21:53 | ZN965:PA38 | URBAN | Asset Failure | HV | 776 | 115 | 0.060247 | 0.000526 | N
15-06-19 | 22:07 | ZN12570:PA22 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 683 | 98 | 0.27845 | 0.002841 | N
15-06-19 | 22:07 | ZN36200:PA1 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1,014 | 97 | 0.066626 | 0.000687 | N
16-06-19 | 00:45 | ZN15006:PA12 | URBAN | Other | Other - Arcing | 3 | 1,155 | 0.002347 | 2e-06 | N
16-06-19 | 00:28 | 214:8670 | URBAN | Other | Other - Self Clearing Trigger | 18 | 186 | 0.002268 | 1.2e-05 | N
16-06-19 | 08:26 | 205:12205 | URBAN | Third Party | Vehicle impact | 1,219 | 128 | 0.10562 | 0.000826 | N
16-06-19 | 08:29 | ZN2602:PA21 | URBAN | Asset Failure | LV | 25 | 275 | 0.004663 | 1.7e-05 | N
16-06-19 | 08:29 | ZN2602:PA30 | URBAN | Asset Failure | LV | 13 | 53 | 0.000467 | 9e-06 | N
16-06-19 | 08:29 | ZN2602:PA8 | URBAN | Asset Failure | LV | 56 | 53 | 0.00201 | 3.8e-05 | N
16-06-19 | 11:18 | 261:81870 | URBAN | Other | Other | 42 | 49 | 0.001394 | 2.8e-05 | N
16-06-19 | 09:48 | ZN342:PA18 | URBAN | Asset Failure | LV | 53 | 101 | 0.003636 | 3.6e-05 | N
16-06-19 | 14:55 | ZN3154:PA13 | SHORT RURAL | Asset Failure | LV | 42 | 140 | 0.024432 | 0.000175 | N
16-06-19 | 16:25 | ZN12640:PA7 | URBAN | Third Party | Vehicle impact | 60 | 88 | 0.00356 | 4.1e-05 | N
16-06-19 | 11:54 | ZN2400:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 233 | 0.000158 | 1e-06 | N
16-06-19 | 12:25 | ZN9900:PA12 | URBAN | Other | Other - Self Clearing Trigger | 27 | 130 | 0.002371 | 1.8e-05 | N
16-06-19 | 15:10 | 205:12205 | URBAN | Other | Other | 28 | 45 | 0.000854 | 1.9e-05 | N
16-06-19 | 15:59 | ZN3154:PA4 | URBAN | Other | Other - Self Clearing Trigger | 10 | 151 | 0.001023 | 7e-06 | N
16-06-19 | 17:21 | ZN1788:PA20 | URBAN | Asset Failure | LV | 70 | 91 | 0.004332 | 4.7e-05 | N
16-06-19 | 17:21 | ZN1788:PA44 | URBAN | Asset Failure | LV | 25 | 144 | 0.002432 | 1.7e-05 | N
16-06-19 | 22:22 | 227:13020 | SHORT RURAL | Other | Other | 32 | 28 | 0.003727 | 0.000133 | N
16-06-19 | 19:26 | ZN12650:PA6 | URBAN | Asset Failure | HV | 1,241 | 94 | 0.078827 | 0.000841 | N
16-06-19 | 22:30 | 507:80932 | SHORT RURAL | Other | Other | 3 | 255 | 0.003182 | 1.2e-05 | N
17-06-19 | 08:00 | 216:10728 | URBAN | Third Party | Other | 1 | 330 | 0.000224 | 1e-06 | N
14-06-19 | 14:08 | ZN35800:PA21 | URBAN | Other | Other - Self Clearing Trigger | 3 | 262 | 0.000532 | 2e-06 | N
17-06-19 | 09:12 | 532:83293 | URBAN | Other | Other | 1 | 98 | 6.6e-05 | 1e-06 | N
17-06-19 | 09:42 | ZN7481:PA12 | URBAN | Asset Failure | HV | 1 | 119 | 8.1e-05 | 1e-06 | N
17-06-19 | 09:42 | ZN7481:PA14 | URBAN | Asset Failure | HV | 1 | 119 | 8.1e-05 | 1e-06 | N
17-06-19 | 09:42 | ZN7481:PA17 | URBAN | Asset Failure | HV | 326 | 97 | 0.021456 | 0.000221 | N
17-06-19 | 10:36 | 522:83132 | SHORT RURAL | Asset Failure | Distribution substation | 1 | 44 | 0.000182 | 4e-06 | N
17-06-19 | 11:48 | ZN12620:PA3 | URBAN | Asset Failure | LV | 73 | 92 | 0.004525 | 4.9e-05 | N
17-06-19 | 13:04 | ZN12690:PA8 | URBAN | Other | Other - Self Clearing Trigger | 42 | 115 | 0.003286 | 2.8e-05 | N
17-06-19 | 13:06 | ZN2400:PA18 | SHORT RURAL | Other | Other | 55 | 190 | 0.043472 | 0.000229 | N
17-06-19 | 13:06 | ZN35370:PA4 | SHORT RURAL | Other | Other | 125 | 214 | 0.11123 | 0.00052 | N
17-06-19 | 13:06 | ZN35370:PA8 | SHORT RURAL | Other | Other | 97 | 181 | 0.073038 | 0.000404 | N
15-06-19 | 23:15 | ZN965:PA38 | URBAN | Network business | Network error | 31 | 65 | 0.001365 | 2.1e-05 | N
17-06-19 | 13:27 | ZN180:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 27 | 133 | 0.002432 | 1.8e-05 | N
17-06-19 | 15:00 | ZN384:PA70 | URBAN | Asset Failure | LV | 140 | 50 | 0.004742 | 9.5e-05 | N
17-06-19 | 16:43 | 204:82697 | URBAN | Third Party | Unauthorised access | 36 | 24 | 0.000585 | 2.4e-05 | N
17-06-19 | 16:33 | ZN12690:PA12 | SHORT RURAL | Other | Other - Arcing | 1 | 146 | 0.000608 | 4e-06 | N
17-06-19 | 16:50 | ZN2196:PA5 | URBAN | Network business | Switching and protection error | 27 | 30 | 0.00054 | 1.8e-05 | N
17-06-19 | 17:41 | ZN12620:PA7 | URBAN | Other | Other - Arcing | 1 | 319 | 0.000216 | 1e-06 | N
17-06-19 | 17:50 | ZN15004:PA3 | SHORT RURAL | Asset Failure | LV | 44 | 70 | 0.012798 | 0.000183 | N
17-06-19 | 17:59 | 522:83126 | SHORT RURAL | Asset Failure | LV | 1 | 222 | 0.000924 | 4e-06 | N
17-06-19 | 18:23 | ZN965:PA3 | URBAN | Asset Failure | LV | 40 | 442 | 0.011976 | 2.7e-05 | N
17-06-19 | 18:32 | 528:83011 | SHORT RURAL | Other | Other - Arcing | 1 | 189 | 0.000786 | 4e-06 | N
17-06-19 | 19:09 | ZN15002:PA2 | URBAN | Asset Failure | LV | 15 | 226 | 0.002296 | 1e-05 | N
17-06-19 | 19:26 | ZN36300:PA19 | URBAN | Asset Failure | LV | 51 | 67 | 0.002307 | 3.5e-05 | N
18-06-19 | 07:33 | ZN1193:PA28 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 327 | 0.000221 | 1e-06 | N
18-06-19 | 09:24 | ZN187:PA16 | URBAN | Third Party | Other | 224 | 441 | 0.06686 | 0.000152 | N
18-06-19 | 10:11 | ZN10994:PA9 | URBAN | Network business | Network error | 20 | 155 | 0.0021 | 1.4e-05 | N
18-06-19 | 16:20 | ZN12630:PA10 | SHORT RURAL | Vegetation | Vegetation Grow In | 16 | 50 | 0.003327 | 6.7e-05 | N
18-06-19 | 11:15 | 813:89061 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 180 | 0.062849 | 0.000349 | N
18-06-19 | 12:07 | 256:80646 | URBAN | Third Party | Vehicle impact | 122 | 16 | 0.001322 | 8.3e-05 | N
18-06-19 | 11:36 | 261:81870 | URBAN | Other | Other | 1 | 120 | 8.1e-05 | 1e-06 | N
18-06-19 | 13:47 | ZN2835:PA23 | URBAN | Asset Failure | HV | 1,913 | 137 | 0.177 | 0.001296 | N
18-06-19 | 13:47 | ZN2835:PA9 | URBAN | Asset Failure | HV | 1 | 162 | 0.00011 | 1e-06 | N
18-06-19 | 14:15 | 270:83590 | URBAN | Third Party | Vehicle impact | 70 | 30 | 0.001422 | 4.7e-05 | N
18-06-19 | 21:45 | ZN5868:PA10 | URBAN | Asset Failure | LV | 10 | 55 | 0.000373 | 7e-06 | N
18-06-19 | 18:00 | ZN15014:PA10 | SHORT RURAL | Asset Failure | LV | 17 | 25 | 0.001767 | 7.1e-05 | N
18-06-19 | 21:05 | ZN1788:PA44 | URBAN | Asset Failure | LV | 131 | 155 | 0.013747 | 8.9e-05 | N
18-06-19 | 19:18 | ZN4990:PA55 56GHJ | CBD | Other | Other - Self Clearing Trigger | 4 | 222 | 0.029273 | 0.000132 | N
18-06-19 | 19:25 | ZN5868:PA25 | URBAN | Asset Failure | LV | 9 | 195 | 0.001186 | 6e-06 | N
18-06-19 | 21:00 | ZN9118:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 34 | 45 | 0.001036 | 2.3e-05 | N
19-06-19 | 01:35 | ZN15014:PA22 | URBAN | Other | Other - Self Clearing Trigger | 44 | 387 | 0.011531 | 3e-05 | N
19-06-19 | 04:16 | ZN2196:PA26 | URBAN | Third Party | Vehicle impact | 707 | 178 | 0.085424 | 0.000479 | N
19-06-19 | 04:27 | ZN2196:PA5 | URBAN | Asset Failure | HV | 1,653 | 266 | 0.29795 | 0.00112 | N
19-06-19 | 08:03 | 508:82576 | SHORT RURAL | Asset Failure | HV | 239 | 86 | 0.085743 | 0.000994 | N
19-06-19 | 09:06 | ZN36100:PA19 | URBAN | Asset Failure | LV | 1 | 1,224 | 0.000829 | 1e-06 | N
19-06-19 | 09:10 | ZN15014:PA10 | SHORT RURAL | Asset Failure | LV | 32 | 98 | 0.012995 | 0.000133 | N
19-06-19 | 11:46 | 202:34240 | URBAN | Other | Other | 1 | 66 | 4.4e-05 | 1e-06 | N
19-06-19 | 13:57 | ZN2400:PA21 | URBAN | Asset Failure | LV | 1 | 272 | 0.000184 | 1e-06 | N
19-06-19 | 14:17 | ZN384:PA2 | URBAN | Other | Other | 1 | 70 | 4.7e-05 | 1e-06 | N
14-06-19 | 12:45 | 512:83743 | SHORT RURAL | Asset Failure | LV | 4 | 35 | 0.000582 | 1.7e-05 | N
18-06-19 | 11:15 | 812:19072 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 95 | 0.000395 | 4e-06 | N
19-06-19 | 15:29 | ZN15001:PA10 | URBAN | Asset Failure | LV | 11 | 237 | 0.001767 | 7e-06 | N
19-06-19 | 19:07 | ZN15006:PA9 | URBAN | Asset Failure | LV | 50 | 127 | 0.00431 | 3.4e-05 | N
19-06-19 | 04:00 | ZN36100:PA19 | URBAN | Asset Failure | LV | 211 | 74 | 0.010584 | 0.000143 | N
20-06-19 | 09:07 | ZN10999:PA38 | URBAN | Asset Failure | LV | 85 | 193 | 0.011119 | 5.8e-05 | N
19-06-19 | 12:10 | ZN2196:PA26 | URBAN | Network business | Switching and protection error | 3 | 30 | 6.1e-05 | 2e-06 | N
20-06-19 | 12:06 | 222:33600 | URBAN | Other | Other | 1 | 44 | 3e-05 | 1e-06 | N
20-06-19 | 12:18 | 512:83741 | SHORT RURAL | Asset Failure | LV | 1 | 216 | 0.000898 | 4e-06 | N
20-06-19 | 13:46 | ZN384:PA2 | URBAN | Asset Failure | HV | 850 | 107 | 0.061423 | 0.000576 | N
20-06-19 | 15:05 | ZN35555:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 47 | 205 | 0.006531 | 3.2e-05 | N
20-06-19 | 15:20 | 802:82220 | SHORT RURAL | Asset Failure | HV | 51 | 50 | 0.010604 | 0.000212 | N
20-06-19 | 15:10 | ZN2196:PA25 | URBAN | Asset Failure | LV | 42 | 270 | 0.007687 | 2.8e-05 | N
20-06-19 | 18:20 | 516:48067 | SHORT RURAL | Asset Failure | HV | 7 | 50 | 0.001456 | 2.9e-05 | N
20-06-19 | 16:02 | ZN1287:PA3 | URBAN | Other | Other | 1 | 423 | 0.000287 | 1e-06 | N
20-06-19 | 16:39 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 270 | 91 | 0.10243 | 0.001123 | N
20-06-19 | 18:24 | ZN15006:PA12 | URBAN | Asset Failure | LV | 34 | 305 | 0.007029 | 2.3e-05 | N
20-06-19 | 18:57 | 523:33503 | URBAN | Asset Failure | LV | 1 | 158 | 0.000107 | 1e-06 | N
20-06-19 | 19:10 | ZN15001:PA18 | URBAN | Asset Failure | LV | 99 | 180 | 0.01206 | 6.7e-05 | N
20-06-19 | 19:22 | ZN35600:PA2 | URBAN | Asset Failure | LV | 2 | 138 | 0.000187 | 1e-06 | N
20-06-19 | 19:22 | ZN35600:PA22 | URBAN | Asset Failure | LV | 92 | 138 | 0.008606 | 6.2e-05 | N
20-06-19 | 19:29 | ZN15006:PA12 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 159 | 0.000108 | 1e-06 | N
20-06-19 | 20:30 | ZN80:PA30 | URBAN | Third Party | Vehicle impact | 129 | 155 | 0.013534 | 8.7e-05 | N
21-06-19 | 01:40 | ZN15009:PA11 | URBAN | Asset Failure | LV | 86 | 55 | 0.003206 | 5.8e-05 | N
20-06-19 | 21:07 | ZN2635:PA46 | URBAN | Other | Other - Arcing | 65 | 38 | 0.001674 | 4.4e-05 | N
20-06-19 | 21:30 | ZN15001:PA18 | URBAN | Asset Failure | LV | 70 | 40 | 0.001898 | 4.7e-05 | N
21-06-19 | 03:43 | ZN9245:PA19 | URBAN | Asset Failure | HV | 493 | 110 | 0.03676 | 0.000334 | N
21-06-19 | 03:43 | ZN9252:PA25 | URBAN | Asset Failure | HV | 867 | 126 | 0.073885 | 0.000588 | N
21-06-19 | 07:43 | ZN35500:PA28 | URBAN | Other | Other | 1 | 167 | 0.000113 | 1e-06 | N
21-06-19 | 08:14 | ZN9118:PA22 | URBAN | Third Party | Other | 1 | 166 | 0.000112 | 1e-06 | N
21-06-19 | 08:41 | 232:33413 | SHORT RURAL | Asset Failure | LV | 80 | 347 | 0.11536 | 0.000333 | N
21-06-19 | 10:45 | ZN690:PA18 | URBAN | Network business | Switching and protection error | 77 | 105 | 0.00548 | 5.2e-05 | N
21-06-19 | 10:45 | 807:74180 | SHORT RURAL | Asset Failure | HV | 10 | 75 | 0.003119 | 4.2e-05 | N
21-06-19 | 11:14 | ZN180:PA41 | URBAN | Other | Other | 1 | 34 | 2.3e-05 | 1e-06 | N
21-06-19 | 12:14 | ZN1193:PA15 | SHORT RURAL | Other | Other - Self Clearing Trigger | 91 | 76 | 0.028578 | 0.000378 | N
21-06-19 | 15:26 | ZN630:PA31 | URBAN | Third Party | Vehicle impact | 59 | 106 | 0.00422 | 4e-05 | N
21-06-19 | 15:40 | 806:82667 | SHORT RURAL | Asset Failure | HV | 8 | 105 | 0.003493 | 3.3e-05 | N
21-06-19 | 17:00 | ZN195:PA30 | SHORT RURAL | Asset Failure | LV | 42 | 155 | 0.027072 | 0.000175 | N
21-06-19 | 18:08 | ZN2835:PA29 | URBAN | Other | Other - Self Clearing Trigger | 77 | 101 | 0.005295 | 5.2e-05 | N
21-06-19 | 18:35 | ZN340:PA35 | URBAN | Asset Failure | LV | 132 | 25 | 0.002237 | 8.9e-05 | N
21-06-19 | 20:03 | ZN12610:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 174 | 0.000722 | 4e-06 | N
21-06-19 | 21:40 | ZN36300:PA5 | URBAN | Other | Other | 34 | 124 | 0.002858 | 2.3e-05 | N
21-06-19 | 22:22 | 224:80337 | URBAN | Asset Failure | LV | 48 | 92 | 0.002993 | 3.3e-05 | N
22-06-19 | 00:20 | ZN2602:PA21 | URBAN | Asset Failure | LV | 178 | 40 | 0.004792 | 0.000121 | N
22-06-19 | 01:45 | ZN1673:PA7 | URBAN | Other | Other | 19 | 675 | 0.008693 | 1.3e-05 | N
22-06-19 | 01:50 | ZN1673:PA7 | URBAN | Other | Other | 38 | 680 | 0.017516 | 2.6e-05 | N
22-06-19 | 08:20 | 813:89063 | SHORT RURAL | Other | Other | 1 | 147 | 0.000609 | 4e-06 | N
22-06-19 | 09:13 | ZN35370:PA4 | SHORT RURAL | Asset Failure | LV | 2 | 346 | 0.002879 | 8e-06 | N
22-06-19 | 12:44 | ZN4990:PA55 56GHJ | CBD | Other | Other - Self Clearing Trigger | 4 | 276 | 0.0364 | 0.000132 | N
22-06-19 | 16:40 | ZN12610:PA11 | URBAN | Asset Failure | LV | 12 | 20 | 0.000163 | 8e-06 | N
22-06-19 | 13:43 | ZN2635:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,156 | 0.000784 | 1e-06 | N
23-06-19 | 02:30 | ZN2602:PA28 | URBAN | Asset Failure | LV | 99 | 10 | 0.000671 | 6.7e-05 | N
22-06-19 | 13:52 | ZN2635:PA38 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 1,297 | 0.000879 | 1e-06 | N
22-06-19 | 15:00 | ZN2602:PA21 | URBAN | Asset Failure | LV | 178 | 80 | 0.009598 | 0.000121 | N
22-06-19 | 16:55 | ZN4545:PA40 | URBAN | Other | Other | 47 | 23 | 0.000733 | 3.2e-05 | N
22-06-19 | 16:55 | ZN4545:PA44 | URBAN | Other | Other | 173 | 21 | 0.002488 | 0.000117 | N
22-06-19 | 16:43 | ZN35370:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 226 | 0.000942 | 4e-06 | N
22-06-19 | 17:00 | ZN36800:PA40 | URBAN | Asset Failure | LV | 41 | 45 | 0.001251 | 2.8e-05 | N
22-06-19 | 19:25 | ZN847:PA45 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 245 | 66 | 0.067245 | 0.001019 | N
23-06-19 | 12:30 | 522:83132 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 110 | 0.000915 | 8e-06 | N
22-06-19 | 20:00 | 232:33409 | SHORT RURAL | Vegetation | Vegetation Grow In | 1 | 222 | 0.000922 | 4e-06 | N
22-06-19 | 22:05 | ZN35370:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 20 | 77 | 0.006393 | 8.3e-05 | N
23-06-19 | 09:05 | ZN36800:PA46 | URBAN | Other | Other | 1 | 282 | 0.000191 | 1e-06 | N
23-06-19 | 09:10 | 242:81539 | URBAN | Asset Failure | Distribution substation | 100 | 265 | 0.017943 | 6.8e-05 | N
23-06-19 | 12:11 | ZN2568:PA32 | URBAN | Asset Failure | LV | 71 | 66 | 0.003166 | 4.8e-05 | N
23-06-19 | 12:20 | 213:33774 | URBAN | Asset Failure | LV | 15 | 315 | 0.003203 | 1e-05 | N
23-06-19 | 13:11 | ZN10994:PA14 | URBAN | Asset Failure | LV | 72 | 109 | 0.005329 | 4.9e-05 | N
23-06-19 | 12:20 | 213:33770 | URBAN | Asset Failure | LV | 20 | 315 | 0.00427 | 1.4e-05 | N
23-06-19 | 16:45 | ZN1290:PA9 | URBAN | Other | Other - Arcing | 1 | 180 | 0.000122 | 1e-06 | N
23-06-19 | 17:50 | 202:34260 | URBAN | Other | Other - Self Clearing Trigger | 274 | 175 | 0.032503 | 0.000186 | N
23-06-19 | 18:15 | 813:89062 | SHORT RURAL | Other | Other | 1 | 150 | 0.000624 | 4e-06 | N
23-06-19 | 18:39 | ZN10997:PA11 | URBAN | Other | Other - Arcing | 703 | 230 | 0.1096 | 0.000477 | N
23-06-19 | 18:39 | ZN10997:PA12 | URBAN | Other | Other - Arcing | 1,474 | 251 | 0.25069 | 0.000999 | N
24-06-19 | 03:00 | ZN10997:PA5 | URBAN | Asset Failure | LV | 23 | 70 | 0.001091 | 1.6e-05 | N
23-06-19 | 19:08 | ZN10997:PA8 | URBAN | Other | Other | 1 | 93 | 6.3e-05 | 1e-06 | N
23-06-19 | 20:37 | ZN129:PA34 | URBAN | Network business | Network error | 36 | 73 | 0.001781 | 2.4e-05 | N
23-06-19 | 20:37 | ZN129:PA47 | URBAN | Network business | Network error | 111 | 73 | 0.005493 | 7.5e-05 | N
23-06-19 | 21:39 | ZN12570:PA40 | SHORT RURAL | Weather |  | 36 | 81 | 0.012127 | 0.00015 | N
23-06-19 | 23:16 | ZN262:PA34 | URBAN | Asset Failure | LV | 86 | 88 | 0.005143 | 5.8e-05 | N
24-06-19 | 00:55 | ZN12570:PA40 | SHORT RURAL | Asset Failure | HV | 20 | 150 | 0.012476 | 8.3e-05 | N
24-06-19 | 04:00 | ZN15005:PA12 | URBAN | Other | Other - Self Clearing Trigger | 25 | 205 | 0.003474 | 1.7e-05 | N
24-06-19 | 06:58 | ZN12610:PA13 | SHORT RURAL | Weather |  | 30 | 377 | 0.047011 | 0.000125 | N
24-06-19 | 08:36 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 264 | 0.001096 | 4e-06 | N
24-06-19 | 09:00 | ZN15005:PA12 | URBAN | Asset Failure | LV | 25 | 30 | 0.000508 | 1.7e-05 | N
24-06-19 | 10:50 | ZN10995:PA1 | URBAN | Vegetation | Vegetation Blow/Fall In | 77 | 390 | 0.020356 | 5.2e-05 | N
24-06-19 | 05:33 | ZN14891:PA21 | SHORT RURAL | Asset Failure | HV | 605 | 228 | 0.57434 | 0.002516 | N
24-06-19 | 10:03 | 509:33395 | LONG RURAL | Other | Other - Self Clearing Trigger | 1 | 240 | 0.083887 | 0.00035 | N
24-06-19 | 10:14 | 227:13015 | SHORT RURAL | Asset Failure | LV | 1 | 1,334 | 0.005546 | 4e-06 | N
24-06-19 | 11:55 | 512:83733 | SHORT RURAL | Asset Failure | Distribution substation | 2 | 55 | 0.000457 | 8e-06 | N
24-06-19 | 12:08 | ZN15005:PA4 | URBAN | Third Party | Vehicle impact | 44 | 370 | 0.011036 | 3e-05 | N
24-06-19 | 12:43 | ZN13000:PA4 | SHORT RURAL | Asset Failure | Distribution substation | 5 | 286 | 0.00595 | 2.1e-05 | N
24-06-19 | 12:45 | ZN2635:PA46 | URBAN | Network business | Network error | 25 | 405 | 0.006863 | 1.7e-05 | N
24-06-19 | 16:55 | ZN965:PA26 | URBAN | Vegetation | Vegetation Blow/Fall In | 36 | 170 | 0.004148 | 2.4e-05 | N
24-06-19 | 15:00 | ZN80:PA32 | URBAN | Asset Failure | LV | 57 | 285 | 0.011012 | 3.9e-05 | N
24-06-19 | 14:55 | ZN15002:PA4 | SHORT RURAL | Other | Other - Self Clearing Trigger | 67 | 134 | 0.037429 | 0.000279 | N
24-06-19 | 15:15 | 513:48057 | URBAN | Asset Failure | HV | 54 | 40 | 0.001464 | 3.7e-05 | N
24-06-19 | 15:45 | 227:13015 | SHORT RURAL | Other | Other | 35 | 10 | 0.001456 | 0.000146 | N
24-06-19 | 16:30 | ZN116:PA19 | URBAN | Third Party | Other | 112 | 235 | 0.017841 | 7.6e-05 | N
24-06-19 | 16:30 | ZN116:PA25 | URBAN | Third Party | Other | 45 | 235 | 0.007168 | 3.1e-05 | N
24-06-19 | 16:00 | ZN14144:PA1 | URBAN | Asset Failure | LV | 1 | 1,379 | 0.000935 | 1e-06 | N
24-06-19 | 16:11 | ZN12610:PA2 | URBAN | Vegetation | Vegetation Blow/Fall In | 1 | 213 | 0.000145 | 1e-06 | N
24-06-19 | 16:27 | ZN14891:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 26 | 192 | 0.020771 | 0.000108 | N
24-06-19 | 21:00 | ZN15008:PA7 | URBAN | Other | Other | 91 | 30 | 0.001851 | 6.2e-05 | N
24-06-19 | 16:35 | ZN12600:PA2 | SHORT RURAL | Asset Failure | HV | 19 | 422 | 0.033344 | 7.9e-05 | N
24-06-19 | 17:45 | ZN262:PA16 | URBAN | Other | Other | 1 | 914 | 0.00062 | 1e-06 | N
24-06-19 | 19:50 | ZN180:PA31 | URBAN | Asset Failure | LV | 70 | 190 | 0.009015 | 4.7e-05 | N
24-06-19 | 19:48 | ZN12610:PA22 | URBAN | Other | Other | 1 | 56 | 3.8e-05 | 1e-06 | N
24-06-19 | 19:48 | ZN180:PA31 | URBAN | Asset Failure | LV | 131 | 191 | 0.016984 | 8.9e-05 | N
24-06-19 | 20:06 | ZN1193:PA15 | SHORT RURAL | Asset Failure | LV | 91 | 1,533 | 0.58019 | 0.000378 | N
24-06-19 | 20:29 | 522:83121 | URBAN | Other | Other - Arcing | 1 | 181 | 0.000123 | 1e-06 | N
24-06-19 | 22:36 | ZN9252:PA28 | URBAN | Third Party | Other | 26 | 1,014 | 0.01787 | 1.8e-05 | N
25-06-19 | 06:30 | ZN15014:PA22 | URBAN | Other | Other - Arcing | 1 | 249 | 0.000169 | 1e-06 | N
25-06-19 | 06:43 | 515:35197 | LONG RURAL | Asset Failure | LV | 1 | 302 | 0.10563 | 0.00035 | N
25-06-19 | 06:49 | 258:80779 | URBAN | Third Party | Other | 1 | 42 | 2.9e-05 | 1e-06 | N
25-06-19 | 07:51 | ZN901:PA18 | URBAN | Asset Failure | LV | 53 | 407 | 0.014609 | 3.6e-05 | N
25-06-19 | 08:15 | ZN8100:PA28 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 124 | 0.000517 | 4e-06 | N
25-06-19 | 09:30 | 814:82291 | SHORT RURAL | Other | Other | 1 | 90 | 0.000373 | 4e-06 | N
25-06-19 | 09:15 | 522:83131 | URBAN | Third Party | Vehicle impact | 1 | 289 | 0.000196 | 1e-06 | N
25-06-19 | 12:06 | 814:82285 | SHORT RURAL | Other | Other | 13 | 64 | 0.00346 | 5.4e-05 | N
25-06-19 | 11:56 | ZN2835:PA30 | URBAN | Other | Other - Self Clearing Trigger | 87 | 104 | 0.006133 | 5.9e-05 | N
25-06-19 | 13:22 | 239:82129 | SHORT RURAL | Vegetation | Vegetation Grow In | 1 | 1,339 | 0.005567 | 4e-06 | N
26-06-19 | 10:28 | ZN2466:PA45 | URBAN | Asset Failure | LV | 90 | 107 | 0.006501 | 6.1e-05 | N
25-06-19 | 15:30 | ZN15001:PA4 | URBAN | Third Party | Vehicle impact | 28 | 360 | 0.006833 | 1.9e-05 | N
25-06-19 | 14:46 | ZN690:PA5 | URBAN | Asset Failure | LV | 59 | 118 | 0.004731 | 4e-05 | N
25-06-19 | 15:30 | ZN15001:PA11 | URBAN | Third Party | Vehicle impact | 19 | 370 | 0.004765 | 1.3e-05 | N
25-06-19 | 18:15 | ZN12610:PA7 | URBAN | Other | Other - Arcing | 1 | 359 | 0.000243 | 1e-06 | N
25-06-19 | 18:48 | ZN195:PA25 | URBAN | Vegetation | Vegetation Blow/Fall In | 23 | 82 | 0.001272 | 1.6e-05 | N
25-06-19 | 20:09 | ZN10999:PA12 | URBAN | Asset Failure | HV | 1 | 75 | 5.1e-05 | 1e-06 | N
25-06-19 | 20:09 | ZN10999:PA17 | URBAN | Asset Failure | HV | 2,786 | 131 | 0.24666 | 0.001889 | N
25-06-19 | 20:19 | 528:83019 | SHORT RURAL | Asset Failure | LV | 1 | 160 | 0.000665 | 4e-06 | N
25-06-19 | 23:45 | ZN10999:PA17 | URBAN | Asset Failure | LV | 71 | 815 | 0.039225 | 4.8e-05 | N
25-06-19 | 23:19 | ZN10999:PA29 | URBAN | Asset Failure | LV | 39 | 851 | 0.022485 | 2.6e-05 | N
26-06-19 | 01:39 | ZN129:PA63 | URBAN | Asset Failure | HV | 181 | 196 | 0.023975 | 0.000122 | N
26-06-19 | 01:39 | ZN80:PA22 | URBAN | Asset Failure | HV | 1,436 | 94 | 0.091117 | 0.00097 | N
26-06-19 | 04:46 | ZN10994:PA10 | URBAN | Asset Failure | LV | 56 | 239 | 0.009043 | 3.8e-05 | N
26-06-19 | 06:37 | ZN12600:PA13 | SHORT RURAL | Asset Failure | LV | 1 | 803 | 0.003339 | 4e-06 | N
26-06-19 | 08:11 | 220:8689 | URBAN | Third Party | Other | 1 | 197 | 0.000133 | 1e-06 | N
26-06-19 | 08:45 | ZN847:PA45 | SHORT RURAL | Other | Other - Self Clearing Trigger | 7 | 180 | 0.00524 | 2.9e-05 | N
26-06-19 | 09:00 | ZN180:PA7 | URBAN | Third Party | Other | 1 | 300 | 0.000203 | 1e-06 | N
26-06-19 | 09:24 | ZN12690:PA12 | SHORT RURAL | Third Party | Other | 5 | 376 | 0.007818 | 2.1e-05 | N
26-06-19 | 09:41 | ZN15014:PA10 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 1,638 | 0.006812 | 4e-06 | N
26-06-19 | 10:28 | ZN4990:PA55 56GHJ | CBD | Asset Failure | LV | 4 | 212 | 0.027963 | 0.000132 | N
26-06-19 | 11:44 | ZN9118:PA26 | URBAN | Asset Failure | HV | 1,676 | 84 | 0.095143 | 0.001133 | N
26-06-19 | 12:40 | ZN8000:PA4 | URBAN | Vegetation | Vegetation Blow/Fall In | 16 | 88 | 0.000952 | 1.1e-05 | N
26-06-19 | 12:50 | ZN12650:PA13 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 33 | 190 | 0.026075 | 0.000137 | N
26-06-19 | 13:50 | 807:74184 | SHORT RURAL | Asset Failure | HV | 23 | 68 | 0.006504 | 9.6e-05 | N
06-06-19 | 15:22 | ZN14892:PA5 | URBAN | Network business | Network error | 2 | 68 | 9.2e-05 | 1e-06 | N
24-06-19 | 02:35 | ZN116:PA25 | URBAN | Other | Other | 83 | 35 | 0.001969 | 5.6e-05 | N
26-06-19 | 13:59 | ZN10993:PA22 | URBAN | Asset Failure | LV | 1 | 472 | 0.000319 | 1e-06 | N
26-06-19 | 14:43 | 507:80932 | SHORT RURAL | Asset Failure | LV | 8 | 356 | 0.011844 | 3.3e-05 | N
26-06-19 | 20:50 | ZN3425:PA44 | URBAN | Asset Failure | LV | 38 | 50 | 0.001284 | 2.6e-05 | N
26-06-19 | 15:29 | ZN15006:PA2 | URBAN | Asset Failure | LV | 20 | 308 | 0.004164 | 1.4e-05 | N
26-06-19 | 15:53 | ZN2635:PA39 | URBAN | Asset Failure | LV | 55 | 312 | 0.011587 | 3.7e-05 | N
26-06-19 | 16:29 | 221:11899 | SHORT RURAL | Asset Failure | LV | 54 | 414 | 0.092971 | 0.000225 | N
26-06-19 | 18:57 | 238:34151 | URBAN | Asset Failure | LV | 1 | 373 | 0.000252 | 1e-06 | N
26-06-19 | 21:19 | ZN12640:PA7 | URBAN | Animal | Animal impact | 129 | 90 | 0.007869 | 8.7e-05 | N
26-06-19 | 21:15 | ZN12570:PA29 | SHORT RURAL | Asset Failure | HV | 602 | 97 | 0.24284 | 0.002504 | N
27-06-19 | 00:32 | ZN12660:PA5 | SHORT RURAL | Other | Other - Self Clearing Trigger | 40 | 188 | 0.031262 | 0.000166 | N
27-06-19 | 01:05 | ZN12580:PA12 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 624 | 0.002594 | 4e-06 | N
27-06-19 | 02:00 | ZN188:PA17 | URBAN | Asset Failure | LV | 78 | 404 | 0.021296 | 5.3e-05 | N
27-06-19 | 09:53 | 243:80075 | SHORT RURAL | Other | Other - Self Clearing Trigger | 1 | 131 | 0.000545 | 4e-06 | N
25-06-19 | 10:17 | 522:83131 | URBAN | Other | Other - Self Clearing Trigger | 1,284 | 3 | 0.002611 | 0.00087 | N
27-06-19 | 11:37 | ZN3672:PA43 | URBAN | Asset Failure | LV | 55 | 372 | 0.013827 | 3.7e-05 | N
27-06-19 | 12:27 | ZN36100:PA5 | URBAN | Other | Other - Arcing | 1 | 62 | 4.2e-05 | 1e-06 | N
27-06-19 | 12:38 | ZN12650:PA12 | URBAN | Third Party | Dig-in | 44 | 132 | 0.003924 | 3e-05 | N
27-06-19 | 14:15 | ZN3154:PA19 | URBAN | Vegetation | Vegetation Blow/Fall In | 18 | 60 | 0.00073 | 1.2e-05 | N
27-06-19 | 16:02 | ZN2568:PA26 | URBAN | Asset Failure | LV | 195 | 216 | 0.028511 | 0.000132 | N
27-06-19 | 17:53 | ZN36800:PA58 | URBAN | Third Party | Other | 158 | 126 | 0.01347 | 0.000107 | N
27-06-19 | 20:06 | ZN965:PA8 | URBAN | Asset Failure | LV | 21 | 144 | 0.002043 | 1.4e-05 | N
27-06-19 | 16:55 | 522:83131 | URBAN | Other | Other | 1 | 95 | 6.4e-05 | 1e-06 | N
26-06-19 | 16:59 | ZN8000:PA28 | URBAN | Network business | Switching and protection error | 36 | 3 | 7.3e-05 | 2.4e-05 | N
26-06-19 | 16:59 | ZN8000:PA32L | URBAN | Network business | Switching and protection error | 5 | 3 | 1e-05 | 3e-06 | N
26-06-19 | 16:59 | ZN8000:PA34 | URBAN | Network business | Switching and protection error | 74 | 3 | 0.00015 | 5e-05 | N
26-06-19 | 16:59 | ZN8000:PA37 | SHORT RURAL | Network business | Switching and protection error | 9 | 3 | 0.000112 | 3.7e-05 | N
27-06-19 | 19:45 | 524:33576 | SHORT RURAL | Other | Other | 2 | 115 | 0.000956 | 8e-06 | N
28-06-19 | 12:45 | ZN10995:PA7 | URBAN | Vegetation | Vegetation Blow/Fall In | 202 | 15 | 0.002047 | 0.000136 | N
28-06-19 | 10:58 | ZN35600:PA17 | URBAN | Asset Failure | HV | 2 | 52 | 7e-05 | 1e-06 | N
28-06-19 | 10:58 | ZN35600:PA20 | URBAN | Asset Failure | HV | 201 | 53 | 0.007198 | 0.000136 | N
28-06-19 | 17:00 | ZN3154:PA18 | URBAN | Vegetation | Vegetation Blow/Fall In | 26 | 20 | 0.000351 | 1.8e-05 | N
28-06-19 | 13:54 | ZN12620:PA10 | SHORT RURAL | Other | Other | 37 | 70 | 0.010806 | 0.000154 | N
28-06-19 | 14:37 | ZN9900:PA1 | URBAN | Asset Failure | LV | 26 | 108 | 0.001897 | 1.8e-05 | N
28-06-19 | 19:14 | ZN2835:PA29 | URBAN | Other | Other | 77 | 81 | 0.004214 | 5.2e-05 | N
28-06-19 | 19:34 | 256:80647 | URBAN | Asset Failure | HV | 1,814 | 16 | 0.019883 | 0.001226 | N
28-06-19 | 20:34 | ZN3154:PA24 | URBAN | Other | Other | 1 | 161 | 0.000109 | 1e-06 | N
28-06-19 | 21:58 | ZN2835:PA29 | URBAN | Other | Other | 77 | 96 | 0.004998 | 5.2e-05 | N
29-06-19 | 07:19 | ZN2310:PA15 | URBAN | Other | Other - Arcing | 1 | 313 | 0.000211 | 1e-06 | N
29-06-19 | 08:05 | ZN15005:PA2 | URBAN | Asset Failure | HV | 5,657 | 31 | 0.11737 | 0.003822 | N
29-06-19 | 08:06 | 235:2120 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 69 | 206 | 0.059183 | 0.000287 | N
29-06-19 | 12:34 | ZN1287:PA22 | URBAN | Asset Failure | LV | 59 | 146 | 0.00582 | 4e-05 | N
29-06-19 | 09:25 | 230:81432 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 1 | 358 | 0.001487 | 4e-06 | N
29-06-19 | 09:43 | ZN15002:PA8 | URBAN | Third Party | Vehicle impact | 1 | 462 | 0.000312 | 1e-06 | N
29-06-19 | 10:57 | ZN3154:PA24 | URBAN | Asset Failure | LV | 24 | 83 | 0.001345 | 1.6e-05 | N
29-06-19 | 12:34 | ZN1287:PA22 | URBAN | Asset Failure | LV | 49 | 146 | 0.004834 | 3.3e-05 | N
29-06-19 | 12:43 | ZN1285:PA30 | URBAN | Third Party | Other | 34 | 47 | 0.001069 | 2.3e-05 | N
29-06-19 | 13:01 | ZN10999:PA17 | URBAN | Other | Other - Self Clearing Trigger | 1 | 102 | 6.9e-05 | 1e-06 | N
29-06-19 | 13:01 | ZN10999:PA32 | URBAN | Other | Other - Self Clearing Trigger | 1,589 | 101 | 0.10896 | 0.001074 | N
29-06-19 | 17:50 | ZN35700:PA10 | URBAN | Asset Failure | HV | 503 | 58 | 0.019733 | 0.00034 | N
29-06-19 | 18:05 | ZN180:PA7 | URBAN | Asset Failure | HV | 1,619 | 94 | 0.10254 | 0.001094 | N
29-06-19 | 18:12 | ZN14892:PA19 | URBAN | Other | Other | 1 | 80 | 5.4e-05 | 1e-06 | N
29-06-19 | 19:27 | ZN14892:PA19 | URBAN | Other | Other | 1 | 9 | 6e-06 | 1e-06 | N
29-06-19 | 20:26 | ZN2466:PA27 | URBAN | Asset Failure | HV | 296 | 108 | 0.021699 | 0.0002 | N
29-06-19 | 21:30 | ZN15005:PA2 | URBAN | Other | Other | 80 | 44 | 0.002401 | 5.4e-05 | N
30-06-19 | 07:14 | 232:11457 | SHORT RURAL | Asset Failure | HV | 115 | 207 | 0.099128 | 0.000478 | N
30-06-19 | 10:34 | ZN9252:PA27 | URBAN | Asset Failure | LV | 22 | 171 | 0.002535 | 1.5e-05 | N
30-06-19 | 13:10 | ZN15005:PA2 | URBAN | Other | Other | 80 | 25 | 0.001351 | 5.4e-05 | N
30-06-19 | 18:04 | 511:29873 | URBAN | Third Party | Vehicle impact | 13 | 216 | 0.001897 | 9e-06 | N
30-06-19 | 15:42 | 243:80081 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 97 | 388 | 0.15649 | 0.000403 | N
30-06-19 | 17:30 | 243:80081 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 43 | 280 | 0.050063 | 0.000179 | N
30-06-19 | 18:00 | ZN2400:PA26 | URBAN | Other | Other | 1 | 900 | 0.000608 | 1e-06 | N
30-06-19 | 18:04 | 515:35197 | LONG RURAL | Other | Other - Self Clearing Trigger | 4 | 156 | 0.21795 | 0.001397 | N
30-06-19 | 18:47 | ZN12640:PA14 | URBAN | Asset Failure | LV | 106 | 62 | 0.004441 | 7.2e-05 | N
30-06-19 | 23:15 | ZN1287:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 46 | 40 | 0.001243 | 3.1e-05 | N
30-06-19 | 19:41 | 515:35197 | LONG RURAL | Other | Other | 2 | 99 | 0.069158 | 0.000699 | N
30-06-19 | 23:10 | ZN1287:PA24 | URBAN | Vegetation | Vegetation Blow/Fall In | 100 | 45 | 0.00304 | 6.8e-05 | N
28-06-19 | 13:45 | ZN965:PA8 | URBAN | Other | Other - Self Clearing Trigger | 21 | 15 | 0.000213 | 1.4e-05 | N
30-06-19 | 09:10 | 232:11457 | SHORT RURAL | Asset Failure | LV | 33 | 15 | 0.002058 | 0.000137 | N
30-06-19 | 12:10 | 232:11457 | SHORT RURAL | Asset Failure | LV | 49 | 48 | 0.009738 | 0.000204 | N
30-06-19 | 16:00 | 511:29877 | SHORT RURAL | Other | Other | 1 | 360 | 0.001497 | 4e-06 | N
06-06-19 | 11:00 | 417:3020 | URBAN | Other | Other | 1 | 139 | 9.4e-05 | 1e-06 | N
24-06-19 | 13:40 | ZN12600:PA2 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 7 | 25 | 0.000728 | 2.9e-05 | N
08-01-19 | 16:30 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 6 | 270 | 0.006817 | 2.5e-05 | N
08-01-19 | 16:30 | ZN12630:PA1 | SHORT RURAL | Vegetation | Vegetation Blow/Fall In | 8 | 270 | 0.009089 | 3.4e-05 | N
12-06-19 | 20:10 | ZN3155:PA32 | URBAN | Asset Failure | LV | 113 | 142 | 0.010879 | 7.7e-05 | N
01-07-18 | 23:00 | 224:80344 | URBAN | Planned |  | 5 | 495 | 0.001638 | 3e-06 | N
01-07-18 | 08:00 | 232:33413 | SHORT RURAL | Planned |  | 1 | 12 | 6.3e-05 | 5e-06 | N
01-07-18 | 09:00 | 232:11457 | SHORT RURAL | Planned |  | 150 | 18 | 0.014106 | 0.000784 | N
01-07-18 | 10:00 | 232:11457 | SHORT RURAL | Planned |  | 13 | 15 | 0.001019 | 6.8e-05 | N
01-07-18 | 08:30 | 511:29869 | SHORT RURAL | Planned |  | 1 | 430 | 0.002246 | 5e-06 | N
02-07-18 | 08:25 | 801:74121 | LONG RURAL | Planned |  | 8 | 162 | 0.45763 | 0.002825 | N
02-07-18 | 10:25 | 233:82819 | SHORT RURAL | Planned |  | 1 | 200 | 0.001045 | 5e-06 | N
02-07-18 | 12:40 | 511:29876 | SHORT RURAL | Planned |  | 4 | 105 | 0.002194 | 2.1e-05 | N
03-07-18 | 09:55 | 204:82699 | URBAN | Planned |  | 100 | 285 | 0.018859 | 6.6e-05 | N
03-07-18 | 08:30 | 528:83019 | SHORT RURAL | Planned |  | 2 | 300 | 0.003135 | 1e-05 | N
03-07-18 | 13:37 | 528:83020 | SHORT RURAL | Planned |  | 1 | 53 | 0.000277 | 5e-06 | N
03-07-18 | 08:30 | 526:34640 | SHORT RURAL | Planned |  | 34 | 450 | 0.079934 | 0.000178 | N
03-07-18 | 08:00 | 532:83307 | SHORT RURAL | Planned |  | 47 | 499 | 0.12253 | 0.000246 | N
03-07-18 | 08:15 | 811:74234 | SHORT RURAL | Planned |  | 2 | 205 | 0.002142 | 1e-05 | N
03-07-18 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 59 | 480 | 0.14796 | 0.000308 | N
04-07-18 | 08:35 | 526:34637 | SHORT RURAL | Planned |  | 10 | 175 | 0.009128 | 5.2e-05 | N
04-07-18 | 07:35 | 235:2120 | SHORT RURAL | Planned |  | 47 | 725 | 0.17774 | 0.000245 | N
04-07-18 | 08:23 | 243:80083 | SHORT RURAL | Planned |  | 72 | 663 | 0.249 | 0.000376 | N
04-07-18 | 08:23 | 243:80074 | SHORT RURAL | Planned |  | 18 | 663 | 0.06225 | 9.4e-05 | N
04-07-18 | 09:20 | 509:33395 | LONG RURAL | Planned |  | 1 | 55 | 0.019421 | 0.000353 | N
04-07-18 | 08:10 | 509:33395 | LONG RURAL | Planned |  | 2 | 155 | 0.10946 | 0.000706 | N
04-07-18 | 11:05 | 509:33395 | LONG RURAL | Planned |  | 1 | 135 | 0.047669 | 0.000353 | N
04-07-18 | 12:50 | 238:34150 | SHORT RURAL | Planned |  | 1 | 90 | 0.000469 | 5e-06 | N
04-07-18 | 21:10 | 264:81232 | SHORT RURAL | Planned |  | 61 | 305 | 0.097047 | 0.000318 | N
04-07-18 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 14 | 347 | 0.02534 | 7.3e-05 | N
04-07-18 | 08:50 | 813:89062 | SHORT RURAL | Planned |  | 20 | 190 | 0.019821 | 0.000104 | N
04-07-18 | 09:01 | 807:74181 | SHORT RURAL | Planned |  | 126 | 109 | 0.071639 | 0.000657 | N
04-07-18 | 10:20 | 520:48172 | SHORT RURAL | Planned |  | 2 | 25 | 0.000261 | 1e-05 | N
04-07-18 | 08:15 | 814:82283 | SHORT RURAL | Planned |  | 13 | 290 | 0.019665 | 6.8e-05 | N
04-07-18 | 13:10 | 512:48049 | SHORT RURAL | Planned |  | 4 | 41 | 0.000855 | 2.1e-05 | N
05-07-18 | 09:00 | 801:74121 | LONG RURAL | Planned |  | 15 | 195 | 1.0328 | 0.005297 | N
05-07-18 | 08:00 | 810:74050 | SHORT RURAL | Planned |  | 14 | 285 | 0.020812 | 7.3e-05 | N
05-07-18 | 08:40 | 515:35193 | SHORT RURAL | Planned |  | 12 | 265 | 0.016587 | 6.3e-05 | N
06-07-18 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 15 | 180 | 0.95339 | 0.005297 | N
05-07-18 | 09:40 | 238:34140 | SHORT RURAL | Planned |  | 12 | 370 | 0.02316 | 6.3e-05 | N
08-07-18 | 08:35 | 202:34261 | URBAN | Planned |  | 27 | 505 | 0.009023 | 1.8e-05 | N
08-07-18 | 08:35 | 202:34249 | URBAN | Planned |  | 1 | 505 | 0.000334 | 1e-06 | N
05-07-18 | 11:15 | 532:83293 | URBAN | Planned |  | 1 | 65 | 4.3e-05 | 1e-06 | N
06-07-18 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 139 | 0.049082 | 0.000353 | N
06-07-18 | 12:30 | 509:33397 | SHORT RURAL | Planned |  | 3 | 60 | 0.000939 | 1.6e-05 | N
05-07-18 | 08:35 | 516:48067 | SHORT RURAL | Planned |  | 2 | 45 | 0.000469 | 1e-05 | N
05-07-18 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 2 | 165 | 0.11653 | 0.000706 | N
05-07-18 | 10:40 | 516:48067 | SHORT RURAL | Planned |  | 3 | 30 | 0.000469 | 1.6e-05 | N
06-07-18 | 09:00 | 513:48059 | SHORT RURAL | Planned |  | 15 | 15 | 0.001174 | 7.8e-05 | N
06-07-18 | 08:30 | 814:82285 | SHORT RURAL | Planned |  | 27 | 230 | 0.032392 | 0.000141 | N
06-07-18 | 08:40 | 813:89055 | SHORT RURAL | Planned |  | 11 | 220 | 0.012623 | 5.7e-05 | N
06-07-18 | 08:35 | 513:48059 | SHORT RURAL | Planned |  | 45 | 320 | 0.075112 | 0.000235 | N
08-07-18 | 07:41 | 407:MS4 | URBAN | Planned |  | 1 | 398 | 0.000263 | 1e-06 | N
09-07-18 | 09:45 | 801:74121 | LONG RURAL | Planned |  | 2 | 30 | 0.021186 | 0.000706 | N
09-07-18 | 08:10 | 202:34238 43 48 | URBAN | Planned |  | 2 | 790 | 0.001046 | 1e-06 | N
09-07-18 | 08:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 35 | 0.012359 | 0.000353 | N
09-07-18 | 08:30 | 812:19072 | SHORT RURAL | Planned |  | 3 | 130 | 0.002034 | 1.6e-05 | N
09-07-18 | 11:15 | 812:19072 | SHORT RURAL | Planned |  | 1 | 75 | 0.000391 | 5e-06 | N
10-07-18 | 08:40 | 524:33576 | SHORT RURAL | Planned |  | 9 | 430 | 0.020181 | 4.7e-05 | N
10-07-18 | 08:40 | 522:83123 | SHORT RURAL | Planned |  | 5 | 160 | 0.004172 | 2.6e-05 | N
10-07-18 | 09:55 | 508:82579 | SHORT RURAL | Planned |  | 7 | 167 | 0.006096 | 3.7e-05 | N
10-07-18 | 13:15 | 509:33395 | LONG RURAL | Planned |  | 1 | 55 | 0.019421 | 0.000353 | N
10-07-18 | 13:35 | 508:82579 | SHORT RURAL | Planned |  | 2 | 110 | 0.001147 | 1e-05 | N
10-07-18 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 2 | 60 | 0.000626 | 1e-05 | N
10-07-18 | 11:30 | 811:74234 | SHORT RURAL | Planned |  | 1 | 125 | 0.000652 | 5e-06 | N
10-07-18 | 11:00 | 802:82225 | SHORT RURAL | Planned |  | 1 | 55 | 0.000287 | 5e-06 | N
10-07-18 | 10:15 | 802:82225 | SHORT RURAL | Planned |  | 1 | 40 | 0.000209 | 5e-06 | N
10-07-18 | 13:00 | 802:82225 | SHORT RURAL | Planned |  | 1 | 40 | 0.000209 | 5e-06 | N
11-07-18 | 08:00 | 213:33775 | URBAN | Planned |  | 3 | 275 | 0.000546 | 2e-06 | N
11-07-18 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 2 | 167 | 0.001742 | 1e-05 | N
11-07-18 | 08:15 | 509:33397 | SHORT RURAL | Planned |  | 3 | 185 | 0.002894 | 1.6e-05 | N
11-07-18 | 08:55 | 238:34137 | SHORT RURAL | Planned |  | 1 | 160 | 0.000834 | 5e-06 | N
11-07-18 | 13:32 | 507:80932 | SHORT RURAL | Planned |  | 1 | 33 | 0.000172 | 5e-06 | N
11-07-18 | 11:45 | 511:29878 | SHORT RURAL | Planned |  | 2 | 230 | 0.002399 | 1e-05 | N
11-07-18 | 12:40 | 509:33397 | SHORT RURAL | Planned |  | 1 | 90 | 0.000469 | 5e-06 | N
11-07-18 | 08:30 | 238:34144 | URBAN | Planned |  | 4 | 390 | 0.001032 | 3e-06 | N
11-07-18 | 09:15 | 516:48067 | SHORT RURAL | Planned |  | 7 | 45 | 0.001643 | 3.7e-05 | N
11-07-18 | 09:10 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017655 | 0.000353 | N
11-07-18 | 09:00 | 813:89062 | SHORT RURAL | Planned |  | 1 | 100 | 0.000521 | 5e-06 | N
12-07-18 | 08:50 | 528:83019 | SHORT RURAL | Planned |  | 2 | 200 | 0.002086 | 1e-05 | N
11-07-18 | 10:40 | 516:48067 | SHORT RURAL | Planned |  | 1 | 45 | 0.000235 | 5e-06 | N
11-07-18 | 11:00 | 813:89061 | LONG RURAL | Planned |  | 1 | 60 | 0.021186 | 0.000353 | N
11-07-18 | 11:35 | 806:82667 | SHORT RURAL | Planned |  | 1 | 125 | 0.000652 | 5e-06 | N
11-07-18 | 12:20 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017655 | 0.000353 | N
11-07-18 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 13 | 360 | 1.6525 | 0.00459 | N
11-07-18 | 13:00 | 516:48067 | SHORT RURAL | Planned |  | 1 | 75 | 0.000391 | 5e-06 | N
11-07-18 | 08:00 | 513:48059 | SHORT RURAL | Planned |  | 16 | 460 | 0.038381 | 8.3e-05 | N
11-07-18 | 08:45 | 802:82225 | SHORT RURAL | Planned |  | 12 | 465 | 0.029098 | 6.3e-05 | N
12-07-18 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 31 | 225 | 0.036373 | 0.000162 | N
12-07-18 | 09:00 | 515:35192 | SHORT RURAL | Planned |  | 53 | 215 | 0.059423 | 0.000276 | N
12-07-18 | 08:15 | 227:13019 | SHORT RURAL | Planned |  | 38 | 455 | 0.090164 | 0.000198 | N
12-07-18 | 08:55 | 528:83020 | SHORT RURAL | Planned |  | 1 | 25 | 0.00013 | 5e-06 | N
12-07-18 | 09:05 | 532:83309 | URBAN | Planned |  | 14 | 115 | 0.001065 | 9e-06 | N
12-07-18 | 09:05 | 528:83019 | SHORT RURAL | Planned |  | 1 | 155 | 0.000808 | 5e-06 | N
12-07-18 | 11:30 | 532:83309 | URBAN | Planned |  | 6 | 90 | 0.000357 | 4e-06 | N
12-07-18 | 12:55 | 528:83019 | SHORT RURAL | Planned |  | 1 | 125 | 0.000652 | 5e-06 | N
12-07-18 | 08:33 | 813:89061 | LONG RURAL | Planned |  | 3 | 97 | 0.10275 | 0.001059 | N
12-07-18 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000209 | 5e-06 | N
12-07-18 | 09:10 | 814:82283 | SHORT RURAL | Planned |  | 1 | 60 | 0.000313 | 5e-06 | N
12-07-18 | 09:35 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000209 | 5e-06 | N
12-07-18 | 10:30 | 807:74184 | SHORT RURAL | Planned |  | 1 | 50 | 0.000261 | 5e-06 | N
12-07-18 | 10:35 | 813:89061 | LONG RURAL | Planned |  | 3 | 80 | 0.084746 | 0.001059 | N
12-07-18 | 10:40 | 814:82283 | SHORT RURAL | Planned |  | 2 | 40 | 0.000417 | 1e-05 | N
12-07-18 | 08:45 | 813:89055 | SHORT RURAL | Planned |  | 3 | 190 | 0.002972 | 1.6e-05 | N
12-07-18 | 11:35 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000209 | 5e-06 | N
12-07-18 | 10:00 | 520:48172 | SHORT RURAL | Planned |  | 3 | 150 | 0.002347 | 1.6e-05 | N
12-07-18 | 12:20 | 813:89061 | LONG RURAL | Planned |  | 1 | 80 | 0.028249 | 0.000353 | N
12-07-18 | 13:30 | 812:19072 | SHORT RURAL | Planned |  | 1 | 70 | 0.000365 | 5e-06 | N
15-07-18 | 06:25 | 245:72 | URBAN | Planned |  | 1 | 554 | 0.000367 | 1e-06 | N
14-07-18 | 23:05 | 224:80341 | URBAN | Planned |  | 105 | 340 | 0.023627 | 6.9e-05 | N
13-07-18 | 08:00 | 528:83020 | SHORT RURAL | Planned |  | 85 | 450 | 0.19947 | 0.000443 | N
13-07-18 | 08:57 | 509:33395 | LONG RURAL | Planned |  | 3 | 79 | 0.083686 | 0.001059 | N
13-07-18 | 08:05 | 507:80914 | SHORT RURAL | Planned |  | 19 | 260 | 0.025761 | 9.9e-05 | N
13-07-18 | 12:30 | 511:29878 | SHORT RURAL | Planned |  | 1 | 40 | 0.000209 | 5e-06 | N
13-07-18 | 12:26 | 509:33395 | LONG RURAL | Planned |  | 2 | 64 | 0.045198 | 0.000706 | N
13-07-18 | 09:05 | 516:48066 | SHORT RURAL | Planned |  | 3 | 16 | 0.00025 | 1.6e-05 | N
13-07-18 | 08:46 | 813:89055 | SHORT RURAL | Planned |  | 1 | 34 | 0.000177 | 5e-06 | N
13-07-18 | 09:25 | 801:74123 | SHORT RURAL | Planned |  | 1 | 30 | 0.000156 | 5e-06 | N
13-07-18 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 2 | 30 | 0.000313 | 1e-05 | N
13-07-18 | 09:35 | 813:89055 | SHORT RURAL | Planned |  | 3 | 40 | 0.000626 | 1.6e-05 | N
13-07-18 | 10:25 | 813:89055 | SHORT RURAL | Planned |  | 1 | 55 | 0.000287 | 5e-06 | N
13-07-18 | 10:40 | 801:74123 | SHORT RURAL | Planned |  | 1 | 20 | 0.000104 | 5e-06 | N
13-07-18 | 10:05 | 801:74123 | SHORT RURAL | Planned |  | 1 | 30 | 0.000156 | 5e-06 | N
13-07-18 | 10:00 | 514:18156 | SHORT RURAL | Planned |  | 2 | 135 | 0.001408 | 1e-05 | N
13-07-18 | 09:40 | 514:18156 | SHORT RURAL | Planned |  | 2 | 210 | 0.00219 | 1e-05 | N
13-07-18 | 09:10 | 414:LD734 | SHORT RURAL | Planned |  | 1 | 267 | 0.001392 | 5e-06 | N
16-07-18 | 08:25 | 227:13018 | URBAN | Planned |  | 2 | 60 | 7.9e-05 | 1e-06 | N
16-07-18 | 23:10 | 202:34254 | URBAN | Planned |  | 104 | 350 | 0.02409 | 6.9e-05 | N
16-07-18 | 10:35 | 511:29878 | SHORT RURAL | Planned |  | 5 | 265 | 0.00691 | 2.6e-05 | N
16-07-18 | 09:40 | 813:89061 | LONG RURAL | Planned |  | 1 | 75 | 0.026483 | 0.000353 | N
16-07-18 | 11:10 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017655 | 0.000353 | N
16-07-18 | 13:15 | 813:89055 | SHORT RURAL | Planned |  | 1 | 35 | 0.000183 | 5e-06 | N
16-07-18 | 08:30 | 516:48067 | SHORT RURAL | Planned |  | 21 | 645 | 0.070635 | 0.00011 | N
16-07-18 | 08:30 | 812:19072 | SHORT RURAL | Planned |  | 5 | 645 | 0.016818 | 2.6e-05 | N
17-07-18 | 08:15 | 515:35192 | SHORT RURAL | Planned |  | 4 | 230 | 0.004798 | 2.1e-05 | N
17-07-18 | 14:15 | 511:29878 | SHORT RURAL | Planned |  | 2 | 50 | 0.000521 | 1e-05 | N
17-07-18 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 2 | 10 | 0.000104 | 1e-05 | N
17-07-18 | 03:30 | 238:34136 | URBAN | Planned |  | 48 | 175 | 0.005559 | 3.2e-05 | N
17-07-18 | 10:05 | 526:34639 | SHORT RURAL | Planned |  | 4 | 43 | 0.000897 | 2.1e-05 | N
17-07-18 | 08:45 | 511:29878 | SHORT RURAL | Planned |  | 1 | 217 | 0.001132 | 5e-06 | N
17-07-18 | 11:00 | 528:83014 | SHORT RURAL | Planned |  | 6 | 100 | 0.003129 | 3.1e-05 | N
17-07-18 | 08:35 | 502:48010 | SHORT RURAL | Planned |  | 50 | 295 | 0.076919 | 0.000261 | N
17-07-18 | 13:15 | 511:29877 | SHORT RURAL | Planned |  | 2 | 55 | 0.000574 | 1e-05 | N
17-07-18 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 1 | 40 | 0.000209 | 5e-06 | N
17-07-18 | 09:35 | 801:74123 | SHORT RURAL | Planned |  | 8 | 40 | 0.001669 | 4.2e-05 | N
17-07-18 | 09:40 | 813:89062 | SHORT RURAL | Planned |  | 1 | 60 | 0.000313 | 5e-06 | N
17-07-18 | 10:55 | 801:74123 | SHORT RURAL | Planned |  | 1 | 25 | 0.00013 | 5e-06 | N
17-07-18 | 10:50 | 813:89062 | SHORT RURAL | Planned |  | 2 | 50 | 0.000521 | 1e-05 | N
17-07-18 | 08:15 | 810:74054 | LONG RURAL | Planned |  | 1 | 285 | 0.10067 | 0.000353 | N
17-07-18 | 09:04 | 513:48050 | SHORT RURAL | Planned |  | 6 | 326 | 0.0102 | 3.1e-05 | N
18-07-18 | 08:50 | 508:82579 | SHORT RURAL | Planned |  | 1 | 265 | 0.001382 | 5e-06 | N
19-07-18 | 09:15 | 264:81240 | SHORT RURAL | Planned |  | 46 | 375 | 0.089909 | 0.00024 | N
20-07-18 | 08:35 | 523:33508 | SHORT RURAL | Planned |  | 15 | 95 | 0.007427 | 7.8e-05 | N
19-07-18 | 09:53 | 227:13018 | URBAN | Planned |  | 2 | 41 | 5.4e-05 | 1e-06 | N
20-07-18 | 07:45 | 216:10722 | SHORT RURAL | Planned |  | 102 | 125 | 0.066456 | 0.000532 | N
18-07-18 | 10:15 | 511:29876 | SHORT RURAL | Planned |  | 1 | 135 | 0.000704 | 5e-06 | N
18-07-18 | 13:45 | 511:29876 | SHORT RURAL | Planned |  | 6 | 40 | 0.001252 | 3.1e-05 | N
18-07-18 | 07:40 | 509:33399 | SHORT RURAL | Planned |  | 22 | 590 | 0.067689 | 0.000115 | N
19-07-18 | 09:20 | 511:29878 | SHORT RURAL | Planned |  | 5 | 167 | 0.004352 | 2.6e-05 | N
19-07-18 | 09:45 | 230:81438 | SHORT RURAL | Planned |  | 2 | 105 | 0.001095 | 1e-05 | N
19-07-18 | 09:45 | 264:81240 | SHORT RURAL | Planned |  | 2 | 215 | 0.002241 | 1e-05 | N
19-07-18 | 08:12 | 509:33395 | LONG RURAL | Planned |  | 45 | 393 | 6.2447 | 0.01589 | N
19-07-18 | 08:35 | 235:2123 | URBAN | Planned |  | 87 | 405 | 0.023311 | 5.8e-05 | N
20-07-18 | 03:45 | 238:34136 | URBAN | Planned |  | 48 | 155 | 0.004922 | 3.2e-05 | N
20-07-18 | 09:20 | 522:83132 | SHORT RURAL | Planned |  | 1 | 110 | 0.000573 | 5e-06 | N
20-07-18 | 11:37 | 522:83132 | SHORT RURAL | Planned |  | 1 | 33 | 0.000172 | 5e-06 | N
20-07-18 | 11:00 | 528:83011 | SHORT RURAL | Planned |  | 17 | 240 | 0.021266 | 8.9e-05 | N
23-07-18 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 3 | 340 | 0.35979 | 0.001058 | N
18-07-18 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 2 | 140 | 0.00146 | 1e-05 | N
18-07-18 | 09:30 | 813:89062 | SHORT RURAL | Planned |  | 10 | 335 | 0.01747 | 5.2e-05 | N
18-07-18 | 09:20 | 813:89062 | SHORT RURAL | Planned |  | 2 | 80 | 0.000834 | 1e-05 | N
18-07-18 | 10:50 | 813:89062 | SHORT RURAL | Planned |  | 1 | 60 | 0.000313 | 5e-06 | N
18-07-18 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 1 | 40 | 0.014129 | 0.000353 | N
18-07-18 | 10:10 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015895 | 0.000353 | N
18-07-18 | 10:55 | 806:82662 | SHORT RURAL | Planned |  | 1 | 50 | 0.000261 | 5e-06 | N
18-07-18 | 09:45 | 806:82662 | SHORT RURAL | Planned |  | 23 | 65 | 0.007796 | 0.00012 | N
18-07-18 | 08:45 | 802:82225 | SHORT RURAL | Planned |  | 1 | 225 | 0.001173 | 5e-06 | N
18-07-18 | 12:00 | 813:89062 | SHORT RURAL | Planned |  | 1 | 70 | 0.000365 | 5e-06 | N
18-07-18 | 12:05 | 806:82667 | SHORT RURAL | Planned |  | 2 | 55 | 0.000574 | 1e-05 | N
18-07-18 | 13:00 | 811:74234 | SHORT RURAL | Planned |  | 1 | 45 | 0.000235 | 5e-06 | N
18-07-18 | 13:30 | 516:48067 | SHORT RURAL | Planned |  | 3 | 45 | 0.000704 | 1.6e-05 | N
18-07-18 | 08:30 | 516:48065 | SHORT RURAL | Planned |  | 14 | 385 | 0.028108 | 7.3e-05 | N
19-07-18 | 08:10 | 801:74121 | LONG RURAL | Planned |  | 2 | 75 | 0.052966 | 0.000706 | N
19-07-18 | 09:50 | 801:74121 | LONG RURAL | Planned |  | 1 | 40 | 0.014124 | 0.000353 | N
19-07-18 | 10:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 40 | 0.014124 | 0.000353 | N
19-07-18 | 09:25 | 806:82662 | SHORT RURAL | Planned |  | 26 | 150 | 0.020327 | 0.000136 | N
19-07-18 | 08:55 | 802:82225 | SHORT RURAL | Planned |  | 1 | 70 | 0.000365 | 5e-06 | N
19-07-18 | 10:15 | 802:82225 | SHORT RURAL | Planned |  | 2 | 50 | 0.000521 | 1e-05 | N
19-07-18 | 12:10 | 801:74121 | LONG RURAL | Planned |  | 2 | 70 | 0.049435 | 0.000706 | N
19-07-18 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 14 | 415 | 0.030282 | 7.3e-05 | N
20-07-18 | 09:05 | 813:89062 | SHORT RURAL | Planned |  | 4 | 65 | 0.001355 | 2.1e-05 | N
20-07-18 | 10:20 | 813:89062 | SHORT RURAL | Planned |  | 1 | 50 | 0.000261 | 5e-06 | N
20-07-18 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 1 | 170 | 0.060028 | 0.000353 | N
20-07-18 | 11:20 | 813:89062 | SHORT RURAL | Planned |  | 1 | 50 | 0.000261 | 5e-06 | N
20-07-18 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 240 | 0.084746 | 0.000353 | N
23-07-18 | 10:20 | 813:89062 | SHORT RURAL | Planned |  | 2 | 30 | 0.000313 | 1e-05 | N
23-07-18 | 08:50 | 813:89055 | SHORT RURAL | Planned |  | 1 | 80 | 0.000417 | 5e-06 | N
23-07-18 | 09:25 | 813:89062 | SHORT RURAL | Planned |  | 3 | 45 | 0.000703 | 1.6e-05 | N
23-07-18 | 12:10 | 813:89062 | SHORT RURAL | Planned |  | 1 | 35 | 0.000182 | 5e-06 | N
23-07-18 | 10:50 | 811:74234 | SHORT RURAL | Planned |  | 1 | 40 | 0.000208 | 5e-06 | N
23-07-18 | 12:00 | 814:82285 | SHORT RURAL | Planned |  | 1 | 50 | 0.000261 | 5e-06 | N
23-07-18 | 10:30 | 811:74234 | SHORT RURAL | Planned |  | 1 | 75 | 0.000391 | 5e-06 | N
23-07-18 | 12:30 | 811:74234 | SHORT RURAL | Planned |  | 1 | 70 | 0.000365 | 5e-06 | N
23-07-18 | 13:40 | 814:82285 | SHORT RURAL | Planned |  | 2 | 50 | 0.000521 | 1e-05 | N
23-07-18 | 09:20 | 801:74123 | SHORT RURAL | Planned |  | 1 | 60 | 0.000313 | 5e-06 | N
23-07-18 | 09:30 | 513:48050 | SHORT RURAL | Planned |  | 6 | 275 | 0.008598 | 3.1e-05 | N
24-07-18 | 08:15 | 810:74058 | SHORT RURAL | Planned |  | 5 | 245 | 0.006383 | 2.6e-05 | N
24-07-18 | 13:15 | 526:34636 | SHORT RURAL | Planned |  | 1 | 80 | 0.000417 | 5e-06 | N
24-07-18 | 12:30 | 509:33397 | SHORT RURAL | Planned |  | 2 | 90 | 0.000938 | 1e-05 | N
24-07-18 | 10:50 | 229:34986 | SHORT RURAL | Planned |  | 18 | 220 | 0.020635 | 9.4e-05 | N
24-07-18 | 08:00 | 526:34640 | SHORT RURAL | Planned |  | 7 | 210 | 0.00766 | 3.6e-05 | N
24-07-18 | 08:40 | 532:83307 | SHORT RURAL | Planned |  | 1 | 130 | 0.000677 | 5e-06 | N
24-07-18 | 08:15 | 509:33397 | SHORT RURAL | Planned |  | 2 | 165 | 0.00172 | 1e-05 | N
24-07-18 | 09:10 | 806:82662 | SHORT RURAL | Planned |  | 1 | 50 | 0.000261 | 5e-06 | N
24-07-18 | 10:00 | 515:35197 | LONG RURAL | Planned |  | 1 | 60 | 0.021164 | 0.000353 | N
24-07-18 | 10:15 | 806:82662 | SHORT RURAL | Planned |  | 1 | 50 | 0.000261 | 5e-06 | N
24-07-18 | 11:30 | 806:82662 | SHORT RURAL | Planned |  | 1 | 60 | 0.000313 | 5e-06 | N
24-07-18 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 53 | 395 | 0.10909 | 0.000276 | N
28-07-18 | 11:00 | 240:34835 | SHORT RURAL | Planned |  | 1 | 61 | 0.000317 | 5e-06 | N
02-08-18 | 10:13 | 239:82133 | URBAN | Planned |  | 1 | 141 | 9.3e-05 | 1e-06 | N
24-07-18 | 09:45 | 227:13018 | URBAN | Planned |  | 1 | 4,335 | 0.002868 | 1e-06 | N
27-07-18 | 08:45 | 508:82580 | SHORT RURAL | Planned |  | 17 | 405 | 0.036066 | 8.9e-05 | N
28-07-18 | 08:00 | 515:35192 | SHORT RURAL | Planned |  | 12 | 255 | 0.015927 | 6.2e-05 | N
01-08-18 | 09:10 | 811:74234 | SHORT RURAL | Planned |  | 4 | 130 | 0.002706 | 2.1e-05 | N
26-07-18 | 10:15 | 243:80078 | URBAN | Planned |  | 352 | 475 | 0.11057 | 0.000233 | N
26-07-18 | 08:00 | 239:82129 | SHORT RURAL | Planned |  | 143 | 490 | 0.36469 | 0.000744 | N
26-07-18 | 08:10 | 227:13019 | SHORT RURAL | Planned |  | 9 | 485 | 0.022718 | 4.7e-05 | N
29-07-18 | 08:01 | 221:11898 | SHORT RURAL | Planned |  | 62 | 579 | 0.18684 | 0.000323 | N
05-08-18 | 08:30 | 227:13015 | SHORT RURAL | Planned |  | 69 | 545 | 0.19714 | 0.000362 | N
25-07-18 | 08:45 | 511:29878 | SHORT RURAL | Planned |  | 1 | 105 | 0.000547 | 5e-06 | N
25-07-18 | 09:20 | 232:33409 | SHORT RURAL | Planned |  | 1 | 113 | 0.000588 | 5e-06 | N
25-07-18 | 09:00 | 229:34995 | SHORT RURAL | Planned |  | 18 | 285 | 0.026702 | 9.4e-05 | N
25-07-18 | 12:40 | 232:11455 | SHORT RURAL | Planned |  | 1 | 100 | 0.000521 | 5e-06 | N
25-07-18 | 08:10 | 526:34636 | SHORT RURAL | Planned |  | 28 | 495 | 0.072143 | 0.000146 | N
26-07-18 | 08:35 | 509:33395 | LONG RURAL | Planned |  | 1 | 50 | 0.01763 | 0.000353 | N
26-07-18 | 08:40 | 229:34995 | SHORT RURAL | Planned |  | 4 | 60 | 0.001249 | 2.1e-05 | N
26-07-18 | 11:30 | 242:81541 | URBAN | Planned |  | 102 | 15 | 0.001012 | 6.7e-05 | N
26-07-18 | 12:10 | 229:34995 | SHORT RURAL | Planned |  | 1 | 70 | 0.000364 | 5e-06 | N
26-07-18 | 12:32 | 524:33572 | SHORT RURAL | Planned |  | 1 | 93 | 0.000484 | 5e-06 | N
26-07-18 | 13:20 | 509:33395 | LONG RURAL | Planned |  | 1 | 65 | 0.02292 | 0.000353 | N
26-07-18 | 08:25 | 522:83132 | SHORT RURAL | Planned |  | 8 | 385 | 0.01603 | 4.2e-05 | N
27-07-18 | 08:50 | 232:11455 | SHORT RURAL | Planned |  | 1 | 131 | 0.000686 | 5e-06 | N
27-07-18 | 12:30 | 232:11455 | SHORT RURAL | Planned |  | 3 | 102 | 0.001603 | 1.6e-05 | N
27-07-18 | 08:40 | 532:83312 | URBAN | Planned |  | 88 | 440 | 0.025605 | 5.8e-05 | N
30-07-18 | 09:25 | 524:33580 | SHORT RURAL | Planned |  | 4 | 100 | 0.002082 | 2.1e-05 | N
30-07-18 | 12:50 | 526:34639 | SHORT RURAL | Planned |  | 1 | 105 | 0.000547 | 5e-06 | N
31-07-18 | 08:40 | 511:29878 | SHORT RURAL | Planned |  | 2 | 140 | 0.001457 | 1e-05 | N
31-07-18 | 13:23 | 511:29877 | SHORT RURAL | Planned |  | 1 | 22 | 0.000114 | 5e-06 | N
31-07-18 | 11:30 | 511:29877 | SHORT RURAL | Planned |  | 2 | 145 | 0.001509 | 1e-05 | N
31-07-18 | 08:40 | 511:29878 | SHORT RURAL | Planned |  | 47 | 305 | 0.074585 | 0.000245 | N
01-08-18 | 08:50 | 526:34639 | SHORT RURAL | Planned |  | 3 | 30 | 0.000468 | 1.6e-05 | N
01-08-18 | 10:55 | 526:34639 | SHORT RURAL | Planned |  | 2 | 20 | 0.000208 | 1e-05 | N
01-08-18 | 08:35 | 509:33395 | LONG RURAL | Planned |  | 1 | 195 | 0.06871 | 0.000352 | N
01-08-18 | 20:15 | 528:83011 | SHORT RURAL | Planned |  | 2 | 540 | 0.005619 | 1e-05 | N
02-08-18 | 11:15 | 508:82578 | SHORT RURAL | Planned |  | 2 | 141 | 0.001467 | 1e-05 | N
02-08-18 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 310 | 0.21846 | 0.000705 | N
03-08-18 | 08:30 | 508:82578 | SHORT RURAL | Planned |  | 5 | 295 | 0.007674 | 2.6e-05 | N
03-08-18 | 09:05 | 509:33395 | LONG RURAL | Planned |  | 1 | 280 | 0.098661 | 0.000352 | N
25-07-18 | 08:25 | 810:74058 | SHORT RURAL | Planned |  | 3 | 260 | 0.00406 | 1.6e-05 | N
25-07-18 | 09:40 | 810:74050 | SHORT RURAL | Planned |  | 26 | 230 | 0.031127 | 0.000135 | N
25-07-18 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 18 | 340 | 0.031855 | 9.4e-05 | N
26-07-18 | 10:55 | 806:82662 | SHORT RURAL | Planned |  | 2 | 40 | 0.000416 | 1e-05 | N
26-07-18 | 08:01 | 810:74054 | LONG RURAL | Planned |  | 13 | 313 | 1.4348 | 0.004584 | N
26-07-18 | 08:55 | 807:74184 | SHORT RURAL | Planned |  | 9 | 265 | 0.012413 | 4.7e-05 | N
26-07-18 | 08:00 | 513:48059 | SHORT RURAL | Planned |  | 45 | 360 | 0.084315 | 0.000234 | N
26-07-18 | 12:30 | 806:82662 | SHORT RURAL | Planned |  | 1 | 90 | 0.000468 | 5e-06 | N
27-07-18 | 08:00 | 810:74058 | SHORT RURAL | Planned |  | 4 | 220 | 0.00461 | 2.1e-05 | N
27-07-18 | 09:20 | 807:74179 | SHORT RURAL | Planned |  | 7 | 160 | 0.005867 | 3.7e-05 | N
27-07-18 | 09:00 | 814:82289 | SHORT RURAL | Planned |  | 7 | 255 | 0.009351 | 3.7e-05 | N
27-07-18 | 08:20 | 814:82285 | SHORT RURAL | Planned |  | 4 | 280 | 0.005867 | 2.1e-05 | N
27-07-18 | 08:50 | 814:82283 | SHORT RURAL | Planned |  | 70 | 235 | 0.086172 | 0.000367 | N
27-07-18 | 09:04 | 520:48172 | SHORT RURAL | Planned |  | 1 | 45 | 0.000236 | 5e-06 | N
30-07-18 | 08:30 | 515:35192 | SHORT RURAL | Planned |  | 1 | 30 | 0.000156 | 5e-06 | N
30-07-18 | 10:00 | 515:35192 | SHORT RURAL | Planned |  | 1 | 45 | 0.000234 | 5e-06 | N
30-07-18 | 10:00 | 802:82225 | SHORT RURAL | Planned |  | 1 | 85 | 0.000442 | 5e-06 | N
30-07-18 | 09:50 | 806:82662 | SHORT RURAL | Planned |  | 1 | 40 | 0.000208 | 5e-06 | N
30-07-18 | 11:10 | 806:82662 | SHORT RURAL | Planned |  | 1 | 40 | 0.000208 | 5e-06 | N
30-07-18 | 08:50 | 806:82667 | SHORT RURAL | Planned |  | 1 | 80 | 0.000416 | 5e-06 | N
30-07-18 | 11:10 | 806:82662 | SHORT RURAL | Planned |  | 1 | 40 | 0.000208 | 5e-06 | N
30-07-18 | 13:00 | 515:35192 | SHORT RURAL | Planned |  | 2 | 60 | 0.000625 | 1e-05 | N
31-07-18 | 08:15 | 514:18137 | SHORT RURAL | Planned |  | 15 | 230 | 0.01795 | 7.8e-05 | N
31-07-18 | 08:15 | 810:74050 | SHORT RURAL | Planned |  | 3 | 310 | 0.004839 | 1.6e-05 | N
31-07-18 | 08:00 | 526:34640 | SHORT RURAL | Planned |  | 26 | 450 | 0.060875 | 0.000135 | N
01-08-18 | 08:05 | 520:48172 | SHORT RURAL | Planned |  | 2 | 60 | 0.000624 | 1e-05 | N
01-08-18 | 10:00 | 520:48172 | SHORT RURAL | Planned |  | 1 | 35 | 0.000182 | 5e-06 | N
01-08-18 | 08:10 | 812:19071 | SHORT RURAL | Planned |  | 72 | 70 | 0.026223 | 0.000375 | N
01-08-18 | 13:00 | 520:48172 | SHORT RURAL | Planned |  | 1 | 35 | 0.000182 | 5e-06 | N
02-08-18 | 09:18 | 812:19071 | SHORT RURAL | Planned |  | 1 | 222 | 0.001155 | 5e-06 | N
02-08-18 | 08:00 | 813:89061 | LONG RURAL | Planned |  | 12 | 320 | 1.3531 | 0.004228 | N
03-08-18 | 09:00 | 807:74180 | SHORT RURAL | Planned |  | 3 | 55 | 0.000859 | 1.6e-05 | N
03-08-18 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 6 | 150 | 0.004683 | 3.1e-05 | N
03-08-18 | 09:05 | 813:89061 | LONG RURAL | Planned |  | 1 | 120 | 0.042283 | 0.000352 | N
03-08-18 | 08:35 | 514:18137 | SHORT RURAL | Planned |  | 26 | 290 | 0.039231 | 0.000135 | N
03-08-18 | 08:45 | 812:19066 | SHORT RURAL | Planned |  | 34 | 265 | 0.046879 | 0.000177 | N
06-08-18 | 08:40 | 522:83132 | SHORT RURAL | Planned |  | 3 | 140 | 0.002181 | 1.6e-05 | N
06-08-18 | 07:30 | 258:80787 | URBAN | Planned |  | 80 | 260 | 0.01375 | 5.3e-05 | N
06-08-18 | 08:15 | 242:81541 | URBAN | Planned |  | 1 | 405 | 0.000268 | 1e-06 | N
06-08-18 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 7 | 60 | 0.002181 | 3.6e-05 | N
06-08-18 | 09:10 | 801:74121 | LONG RURAL | Planned |  | 4 | 55 | 0.077438 | 0.001408 | N
06-08-18 | 08:58 | 801:74121 | LONG RURAL | Planned |  | 33 | 117 | 1.359 | 0.011616 | N
06-08-18 | 10:20 | 801:74121 | LONG RURAL | Planned |  | 1 | 55 | 0.019359 | 0.000352 | N
06-08-18 | 08:35 | 516:48066 | SHORT RURAL | Planned |  | 5 | 190 | 0.004933 | 2.6e-05 | N
06-08-18 | 13:00 | 523:33501 | SHORT RURAL | Planned |  | 3 | 60 | 0.000935 | 1.6e-05 | N
07-08-18 | 08:25 | 802:82215 | SHORT RURAL | Planned |  | 5 | 275 | 0.00714 | 2.6e-05 | N
07-08-18 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 120 | 0.084477 | 0.000704 | N
07-08-18 | 11:10 | 509:33395 | LONG RURAL | Planned |  | 1 | 110 | 0.038719 | 0.000352 | N
07-08-18 | 08:35 | 264:81240 | SHORT RURAL | Planned |  | 10 | 355 | 0.018434 | 5.2e-05 | N
07-08-18 | 08:55 | 807:74179 | SHORT RURAL | Planned |  | 18 | 190 | 0.017759 | 9.3e-05 | N
07-08-18 | 08:50 | 813:89055 | SHORT RURAL | Planned |  | 1 | 85 | 0.000441 | 5e-06 | N
06-08-18 | 08:50 | 813:89055 | SHORT RURAL | Planned |  | 2 | 220 | 0.002285 | 1e-05 | N
07-08-18 | 08:10 | 526:34639 | SHORT RURAL | Planned |  | 37 | 350 | 0.067245 | 0.000192 | N
07-08-18 | 09:50 | 806:82667 | SHORT RURAL | Planned |  | 1 | 240 | 0.001246 | 5e-06 | N
08-08-18 | 09:00 | 221:11900 | URBAN | Planned |  | 51 | 330 | 0.011126 | 3.4e-05 | N
08-08-18 | 10:30 | 264:81244 | SHORT RURAL | Planned |  | 2 | 168 | 0.001745 | 1e-05 | N
08-08-18 | 08:12 | 264:81244 | SHORT RURAL | Planned |  | 7 | 423 | 0.015376 | 3.6e-05 | N
08-08-18 | 09:10 | 813:89062 | SHORT RURAL | Planned |  | 3 | 45 | 0.000701 | 1.6e-05 | N
08-08-18 | 10:15 | 813:89062 | SHORT RURAL | Planned |  | 1 | 55 | 0.000286 | 5e-06 | N
08-08-18 | 11:25 | 813:89062 | SHORT RURAL | Planned |  | 1 | 20 | 0.000104 | 5e-06 | N
09-08-18 | 10:48 | ZN10999:PA29 | URBAN | Planned |  | 48 | 7 | 0.000222 | 3.2e-05 | N
09-08-18 | 08:15 | 523:33501 | SHORT RURAL | Planned |  | 45 | 410 | 0.095806 | 0.000234 | N
09-08-18 | 08:00 | 532:83298 | SHORT RURAL | Planned |  | 157 | 462 | 0.37665 | 0.000815 | N
09-08-18 | 09:40 | 270:83590 | URBAN | Planned |  | 59 | 175 | 0.006826 | 3.9e-05 | N
09-08-18 | 08:20 | 515:35192 | SHORT RURAL | Planned |  | 2 | 60 | 0.000623 | 1e-05 | N
09-08-18 | 08:20 | 512:83743 | SHORT RURAL | Planned |  | 1 | 55 | 0.000286 | 5e-06 | N
09-08-18 | 08:20 | 811:74234 | SHORT RURAL | Planned |  | 2 | 220 | 0.002285 | 1e-05 | N
09-08-18 | 10:05 | 512:83743 | SHORT RURAL | Planned |  | 1 | 50 | 0.00026 | 5e-06 | N
09-08-18 | 10:00 | 515:35192 | SHORT RURAL | Planned |  | 2 | 55 | 0.000571 | 1e-05 | N
09-08-18 | 09:50 | 810:74058 | SHORT RURAL | Planned |  | 1 | 100 | 0.000519 | 5e-06 | N
09-08-18 | 12:05 | 807:74181 | SHORT RURAL | Planned |  | 4 | 60 | 0.001246 | 2.1e-05 | N
09-08-18 | 13:00 | 515:35192 | SHORT RURAL | Planned |  | 3 | 60 | 0.000935 | 1.6e-05 | N
09-08-18 | 13:10 | 512:83743 | SHORT RURAL | Planned |  | 3 | 50 | 0.000779 | 1.6e-05 | N
10-08-18 | 09:40 | 516:48067 | SHORT RURAL | Planned |  | 4 | 225 | 0.004718 | 2.1e-05 | N
10-08-18 | 08:20 | 520:48172 | SHORT RURAL | Planned |  | 18 | 340 | 0.032086 | 9.4e-05 | N
13-08-18 | 08:00 | 224:80340 | SHORT RURAL | Planned |  | 234 | 305 | 0.37406 | 0.001226 | N
13-08-18 | 10:35 | 217:33612 | URBAN | Planned |  | 7 | 65 | 0.0003 | 5e-06 | N
13-08-18 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 2 | 60 | 0.000629 | 1e-05 | N
13-08-18 | 09:45 | 813:89062 | SHORT RURAL | Planned |  | 6 | 215 | 0.006761 | 3.1e-05 | N
13-08-18 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 1 | 570 | 0.002987 | 5e-06 | N
01-07-18 | 08:00 | ZN4990:PA51 52DEF | CBD | Planned |  | 2 | 590 | 0.03811 | 6.5e-05 | N
01-07-18 | 20:00 | ZN10999:PA32 | URBAN | Planned |  | 41 | 960 | 0.026043 | 2.7e-05 | N
01-07-18 | 21:00 | ZN10999:PA12 | URBAN | Planned |  | 72 | 900 | 0.042876 | 4.8e-05 | N
01-07-18 | 23:00 | ZN36800:PA49 | URBAN | Planned |  | 124 | 270 | 0.022153 | 8.2e-05 | N
02-07-18 | 00:10 | ZN4990:PA51 52KLM | CBD | Planned |  | 15 | 350 | 0.16956 | 0.000484 | N
02-07-18 | 09:20 | ZN342:PA35 | URBAN | Planned |  | 62 | 475 | 0.019487 | 4.1e-05 | N
02-07-18 | 09:10 | ZN36200:PA1 | URBAN | Planned |  | 75 | 340 | 0.016874 | 5e-05 | N
02-07-18 | 09:00 | ZN35400:PA95 | URBAN | Planned |  | 28 | 300 | 0.005558 | 1.9e-05 | N
02-07-18 | 22:00 | ZN15009:PA9 | URBAN | Planned |  | 136 | 565 | 0.050846 | 9e-05 | N
02-07-18 | 23:00 | ZN901:PA20 | URBAN | Planned |  | 79 | 240 | 0.012546 | 5.2e-05 | N
03-07-18 | 07:30 | ZN36100:PA20 | URBAN | Planned |  | 45 | 480 | 0.014293 | 3e-05 | N
03-07-18 | 08:00 | ZN35400:PA110 | URBAN | Planned |  | 89 | 575 | 0.033864 | 5.9e-05 | N
03-07-18 | 08:00 | ZN3154:PA12 | URBAN | Planned |  | 80 | 480 | 0.02541 | 5.3e-05 | N
03-07-18 | 08:30 | ZN35400:PA110 | URBAN | Planned |  | 75 | 450 | 0.022333 | 5e-05 | N
03-07-18 | 08:30 | ZN35400:PA110 | URBAN | Planned |  | 67 | 450 | 0.019951 | 4.4e-05 | N
03-07-18 | 20:25 | ZN262:PA39 | URBAN | Planned |  | 41 | 455 | 0.012344 | 2.7e-05 | N
03-07-18 | 09:30 | ZN36800:PA58 | URBAN | Planned |  | 165 | 240 | 0.026204 | 0.000109 | N
03-07-18 | 09:55 | ZN36800:PA50 | URBAN | Planned |  | 82 | 215 | 0.011666 | 5.4e-05 | N
03-07-18 | 23:30 | ZN3288:PA41 42KLM | CBD | Planned |  | 4 | 1,185 | 0.15309 | 0.000129 | N
04-07-18 | 05:30 | ZN9118:PA16 | URBAN | Planned |  | 13 | 240 | 0.002065 | 9e-06 | N
04-07-18 | 07:15 | ZN14143:PA17 | SHORT RURAL | Planned |  | 163 | 555 | 0.47188 | 0.00085 | N
04-07-18 | 08:25 | ZN847:PA21 | URBAN | Planned |  | 39 | 695 | 0.01794 | 2.6e-05 | N
04-07-18 | 08:00 | ZN847:PA21 | URBAN | Planned |  | 5 | 720 | 0.002383 | 3e-06 | N
04-07-18 | 08:00 | ZN965:PA38 | URBAN | Planned |  | 48 | 540 | 0.017156 | 3.2e-05 | N
04-07-18 | 09:10 | ZN36800:PA33 | URBAN | Planned |  | 58 | 110 | 0.004223 | 3.8e-05 | N
04-07-18 | 09:02 | ZN36800:PA58 | URBAN | Planned |  | 164 | 118 | 0.012808 | 0.000109 | N
04-07-18 | 20:00 | ZN188:PA45 | SHORT RURAL | Planned |  | 5 | 300 | 0.007824 | 2.6e-05 | N
05-07-18 | 07:30 | ZN15006:PA2 | URBAN | Planned |  | 22 | 510 | 0.007426 | 1.5e-05 | N
05-07-18 | 08:14 | ZN36100:PA19 | URBAN | Planned |  | 96 | 436 | 0.027704 | 6.4e-05 | N
05-07-18 | 07:30 | ZN129:PA35 | URBAN | Planned |  | 21 | 420 | 0.005838 | 1.4e-05 | N
05-07-18 | 09:05 | ZN3155:PA17 | URBAN | Planned |  | 45 | 145 | 0.004319 | 3e-05 | N
05-07-18 | 21:00 | ZN15006:PA12 | URBAN | Planned |  | 15 | 265 | 0.002631 | 1e-05 | N
05-07-18 | 21:30 | ZN15014:PA9 | URBAN | Planned |  | 34 | 450 | 0.010127 | 2.3e-05 | N
06-07-18 | 08:30 | ZN14143:PA5 | URBAN | Planned |  | 6 | 180 | 0.000715 | 4e-06 | N
06-07-18 | 09:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 15 | 205 | 0.01604 | 7.8e-05 | N
07-07-18 | 06:40 | ZN35800:PA18 | URBAN | Planned |  | 1 | 800 | 0.00053 | 1e-06 | N
07-07-18 | 08:30 | ZN384:PA65 | URBAN | Planned |  | 1 | 2,070 | 0.00137 | 1e-06 | N
08-07-18 | 01:30 | ZN7481:PA13 | URBAN | Planned |  | 111 | 70 | 0.005142 | 7.3e-05 | N
08-07-18 | 07:50 | ZN12690:PA7 | SHORT RURAL | Planned |  | 6 | 40 | 0.001252 | 3.1e-05 | N
08-07-18 | 07:10 | ZN263:PA31 32ABC | CBD | Planned |  | 16 | 320 | 0.16534 | 0.000517 | N
08-07-18 | 19:45 | ZN116:PA87 | URBAN | Planned |  | 16 | 285 | 0.003018 | 1.1e-05 | N
08-07-18 | 20:30 | ZN5868:PA13 | URBAN | Planned |  | 17 | 540 | 0.006075 | 1.1e-05 | N
09-07-18 | 08:00 | ZN14144:PA5 | URBAN | Planned |  | 5 | 445 | 0.001472 | 3e-06 | N
09-07-18 | 09:52 | ZN15005:PA6 | URBAN | Planned |  | 38 | 368 | 0.009254 | 2.5e-05 | N
09-07-18 | 08:30 | ZN12570:PA33 | SHORT RURAL | Planned |  | 5 | 370 | 0.009647 | 2.6e-05 | N
09-07-18 | 08:05 | ZN12690:PA24 | SHORT RURAL | Planned |  | 3 | 430 | 0.006727 | 1.6e-05 | N
09-07-18 | 22:00 | ZN15006:PA9 | URBAN | Planned |  | 2 | 150 | 0.000199 | 1e-06 | N
10-07-18 | 07:15 | ZN12570:PA37 | SHORT RURAL | Planned |  | 5 | 490 | 0.012776 | 2.6e-05 | N
10-07-18 | 07:30 | ZN965:PA8 | URBAN | Planned |  | 84 | 420 | 0.023347 | 5.6e-05 | N
10-07-18 | 08:00 | ZN12630:PA11 | SHORT RURAL | Planned |  | 28 | 75 | 0.010951 | 0.000146 | N
10-07-18 | 09:05 | ZN12600:PA2 | SHORT RURAL | Planned |  | 4 | 340 | 0.007092 | 2.1e-05 | N
10-07-18 | 10:55 | ZN9245:PA3 | SHORT RURAL | Planned |  | 5 | 125 | 0.003259 | 2.6e-05 | N
11-07-18 | 07:30 | ZN9245:PA10 | URBAN | Planned |  | 48 | 450 | 0.014295 | 3.2e-05 | N
11-07-18 | 07:30 | ZN263:PA31 32GHJ | CBD | Planned |  | 1 | 480 | 0.015504 | 3.2e-05 | N
11-07-18 | 07:30 | ZN263:PA33 34ABC | CBD | Planned |  | 3 | 480 | 0.046513 | 9.7e-05 | N
11-07-18 | 07:30 | ZN263:PA31 32GHJ | CBD | Planned |  | 4 | 480 | 0.062018 | 0.000129 | N
11-07-18 | 10:15 | ZN35370:PA4 | SHORT RURAL | Planned |  | 13 | 255 | 0.017287 | 6.8e-05 | N
11-07-18 | 20:30 | ZN2602:PA36 | URBAN | Planned |  | 90 | 525 | 0.031269 | 6e-05 | N
12-07-18 | 05:00 | ZN931:PA13 | URBAN | Planned |  | 1 | 20 | 1.3e-05 | 1e-06 | N
12-07-18 | 07:04 | ZN711:PA4 | URBAN | Planned |  | 74 | 1 | 4.9e-05 | 4.9e-05 | N
12-07-18 | 09:30 | ZN129:PA55 | URBAN | Planned |  | 9 | 510 | 0.003038 | 6e-06 | N
12-07-18 | 08:45 | ZN10999:PA32 | URBAN | Planned |  | 54 | 495 | 0.01769 | 3.6e-05 | N
12-07-18 | 08:20 | ZN14891:PA20 | SHORT RURAL | Planned |  | 4 | 700 | 0.014601 | 2.1e-05 | N
12-07-18 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 4 | 415 | 0.008657 | 2.1e-05 | N
12-07-18 | 08:30 | ZN35400:PA64 | URBAN | Planned |  | 157 | 510 | 0.05299 | 0.000104 | N
12-07-18 | 10:00 | ZN36800:PA57 | URBAN | Planned |  | 81 | 240 | 0.012865 | 5.4e-05 | N
12-07-18 | 17:25 | ZN10999:PA24 | URBAN | Planned |  | 25 | 175 | 0.002895 | 1.7e-05 | N
13-07-18 | 09:10 | ZN35370:PA4 | SHORT RURAL | Planned |  | 6 | 350 | 0.010951 | 3.1e-05 | N
13-07-18 | 16:30 | ZN10993:PA35 | URBAN | Planned |  | 1 | 2,580 | 0.001707 | 1e-06 | N
14-07-18 | 07:45 | ZN847:PA21 | URBAN | Planned |  | 65 | 475 | 0.020434 | 4.3e-05 | N
14-07-18 | 09:30 | ZN12650:PA14 | URBAN | Planned |  | 17 | 487 | 0.005479 | 1.1e-05 | N
14-07-18 | 16:20 | ZN711:PA4 | URBAN | Planned |  | 2 | 40 | 5.3e-05 | 1e-06 | N
15-08-18 | 09:00 | 242:81535 | URBAN | Planned |  | 34 | 229 | 0.005154 | 2.2e-05 | N
14-08-18 | 08:15 | 413:753 | URBAN | Planned |  | 1 | 370 | 0.000244 | 1e-06 | N
14-08-18 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 6 | 280 | 0.59113 | 0.002111 | N
14-08-18 | 08:30 | 514:18156 | SHORT RURAL | Planned |  | 4 | 330 | 0.00693 | 2.1e-05 | N
14-08-18 | 07:55 | 221:11893 | URBAN | Planned |  | 49 | 560 | 0.018111 | 3.2e-05 | N
14-08-18 | 08:00 | 227:13015 | SHORT RURAL | Planned |  | 39 | 161 | 0.032964 | 0.000205 | N
15-08-18 | 08:00 | 206:34440 | URBAN | Planned |  | 158 | 405 | 0.042303 | 0.000104 | N
14-08-18 | 11:30 | 238:34148 | SHORT RURAL | Planned |  | 1 | 60 | 0.000315 | 5e-06 | N
14-08-18 | 08:35 | 528:83014 | SHORT RURAL | Planned |  | 8 | 160 | 0.00672 | 4.2e-05 | N
14-08-18 | 08:05 | 522:83123 | SHORT RURAL | Planned |  | 7 | 290 | 0.010657 | 3.7e-05 | N
14-08-18 | 08:45 | 511:29878 | SHORT RURAL | Planned |  | 16 | 295 | 0.02478 | 8.4e-05 | N
14-08-18 | 08:30 | 232:11453 | SHORT RURAL | Planned |  | 1 | 230 | 0.001207 | 5e-06 | N
14-08-18 | 08:10 | 524:33580 | SHORT RURAL | Planned |  | 4 | 400 | 0.0084 | 2.1e-05 | N
14-08-18 | 07:35 | 528:83017 | URBAN | Planned |  | 26 | 425 | 0.007293 | 1.7e-05 | N
14-08-18 | 10:00 | 242:81538 | URBAN | Planned |  | 115 | 75 | 0.005693 | 7.6e-05 | N
15-08-18 | 09:00 | 229:34983 | SHORT RURAL | Planned |  | 2 | 345 | 0.003622 | 1e-05 | N
15-08-18 | 08:35 | 511:29877 | SHORT RURAL | Planned |  | 36 | 355 | 0.067094 | 0.000189 | N
15-08-18 | 08:10 | 526:34636 | SHORT RURAL | Planned |  | 11 | 440 | 0.02541 | 5.8e-05 | N
14-08-18 | 08:30 | 513:48051 | URBAN | Planned |  | 46 | 230 | 0.006983 | 3e-05 | N
15-08-18 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015834 | 0.000352 | N
15-08-18 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 3 | 75 | 0.001181 | 1.6e-05 | N
15-08-18 | 08:30 | 516:48065 | SHORT RURAL | Planned |  | 2 | 65 | 0.000682 | 1e-05 | N
15-08-18 | 10:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 170 | 0.059817 | 0.000352 | N
16-07-18 | 02:00 | ZN3155:PA18 | URBAN | Planned |  | 38 | 180 | 0.004527 | 2.5e-05 | N
16-07-18 | 08:00 | ZN15006:PA9 | URBAN | Planned |  | 92 | 565 | 0.034401 | 6.1e-05 | N
16-07-18 | 07:23 | ZN12630:PA11 | SHORT RURAL | Planned |  | 6 | 455 | 0.014236 | 3.1e-05 | N
16-07-18 | 07:30 | ZN129:PA39 | URBAN | Planned |  | 36 | 570 | 0.013581 | 2.4e-05 | N
16-07-18 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 17 | 460 | 0.04078 | 8.9e-05 | N
16-07-18 | 09:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 49 | 407 | 0.104 | 0.000256 | N
17-07-18 | 04:30 | ZN931:PA18 | URBAN | Planned |  | 1 | 70 | 4.6e-05 | 1e-06 | N
17-07-18 | 07:05 | ZN12630:PA3 | SHORT RURAL | Planned |  | 46 | 550 | 0.13194 | 0.00024 | N
17-07-18 | 07:30 | ZN129:PA39 | URBAN | Planned |  | 36 | 570 | 0.01358 | 2.4e-05 | N
17-07-18 | 07:30 | ZN15005:PA2 | URBAN | Planned |  | 14 | 480 | 0.004447 | 9e-06 | N
17-07-18 | 08:05 | ZN35370:PA2 | SHORT RURAL | Planned |  | 18 | 535 | 0.050219 | 9.4e-05 | N
17-07-18 | 08:15 | ZN12690:PA24 | SHORT RURAL | Planned |  | 47 | 420 | 0.10294 | 0.000245 | N
17-07-18 | 09:20 | ZN12690:PA17 | URBAN | Planned |  | 50 | 450 | 0.01489 | 3.3e-05 | N
18-07-18 | 08:00 | ZN129:PA39 | URBAN | Planned |  | 36 | 540 | 0.012866 | 2.4e-05 | N
18-07-18 | 07:30 | ZN15005:PA2 | URBAN | Planned |  | 26 | 480 | 0.008259 | 1.7e-05 | N
18-07-18 | 08:00 | ZN965:PA38 | URBAN | Planned |  | 48 | 540 | 0.017154 | 3.2e-05 | N
18-07-18 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 17 | 525 | 0.046543 | 8.9e-05 | N
18-07-18 | 19:35 | ZN12630:PA8 | SHORT RURAL | Planned |  | 17 | 565 | 0.050089 | 8.9e-05 | N
18-07-18 | 20:44 | ZN711:PA5 | URBAN | Planned |  | 70 | 436 | 0.020198 | 4.6e-05 | N
18-07-18 | 23:29 | ZN15002:PA6 | URBAN | Planned |  | 5 | 2,940 | 0.009729 | 3e-06 | N
19-07-18 | 05:05 | ZN931:PA32 | URBAN | Planned |  | 1 | 45 | 3e-05 | 1e-06 | N
19-07-18 | 05:05 | ZN931:PA32 | URBAN | Planned |  | 1 | 45 | 3e-05 | 1e-06 | N
19-07-18 | 07:30 | ZN2835:PA15 | URBAN | Planned |  | 43 | 570 | 0.016215 | 2.8e-05 | N
19-07-18 | 09:15 | ZN35500:PA28 | URBAN | Planned |  | 14 | 165 | 0.001528 | 9e-06 | N
19-07-18 | 08:05 | ZN14891:PA5 | SHORT RURAL | Planned |  | 46 | 475 | 0.11389 | 0.00024 | N
19-07-18 | 09:00 | ZN180:PA7 | URBAN | Planned |  | 78 | 540 | 0.027866 | 5.2e-05 | N
19-07-18 | 08:00 | ZN12570:PA22 | SHORT RURAL | Planned |  | 5 | 60 | 0.001564 | 2.6e-05 | N
19-07-18 | 15:00 | ZN12570:PA22 | SHORT RURAL | Planned |  | 5 | 30 | 0.000782 | 2.6e-05 | N
19-07-18 | 09:30 | ZN12640:PA13 | SHORT RURAL | Planned |  | 71 | 425 | 0.15728 | 0.00037 | N
19-07-18 | 08:55 | ZN12690:PA24 | SHORT RURAL | Planned |  | 3 | 425 | 0.006645 | 1.6e-05 | N
19-07-18 | 08:00 | ZN15002:PA4 | SHORT RURAL | Planned |  | 23 | 315 | 0.037762 | 0.00012 | N
19-07-18 | 09:30 | ZN9900:PA8 | URBAN | Planned |  | 43 | 300 | 0.008534 | 2.8e-05 | N
19-07-18 | 19:45 | ZN80:PA32 | URBAN | Planned |  | 71 | 585 | 0.027479 | 4.7e-05 | N
19-07-18 | 19:40 | ZN1285:PA10 | URBAN | Planned |  | 24 | 710 | 0.011273 | 1.6e-05 | N
20-07-18 | 09:15 | ZN12610:PA2 | URBAN | Planned |  | 53 | 350 | 0.012273 | 3.5e-05 | N
21-07-18 | 07:30 | ZN263:PA33 34ABC | CBD | Planned |  | 68 | 660 | 1.4496 | 0.002196 | N
21-07-18 | 10:45 | ZN3288:PA41 42KLM | CBD | Planned |  | 21 | 125 | 0.084787 | 0.000678 | N
21-07-18 | 14:20 | ZN4990:PA55 56DEF | CBD | Planned |  | 1 | 375 | 0.012112 | 3.2e-05 | N
22-07-18 | 06:30 | ZN167:PA8 | URBAN | Planned |  | 10 | 725 | 0.004797 | 7e-06 | N
22-07-18 | 07:30 | ZN263:PA35 37KLM | CBD | Planned |  | 1 | 600 | 0.01938 | 3.2e-05 | N
22-07-18 | 07:30 | ZN8700:PA63 64KLM | CBD | Planned |  | 46 | 570 | 0.8469 | 0.001486 | N
22-07-18 | 22:30 | ZN901:PA20 | URBAN | Planned |  | 59 | 270 | 0.010539 | 3.9e-05 | N
23-07-18 | 09:00 | ZN3922:PA11 | URBAN | Planned |  | 5 | 420 | 0.001389 | 3e-06 | N
23-07-18 | 10:25 | ZN9252:PA25 | URBAN | Planned |  | 22 | 275 | 0.004002 | 1.5e-05 | N
23-07-18 | 08:00 | ZN180:PA42 | URBAN | Planned |  | 61 | 420 | 0.016947 | 4e-05 | N
23-07-18 | 08:30 | ZN965:PA3 | URBAN | Planned |  | 37 | 330 | 0.008077 | 2.4e-05 | N
23-07-18 | 21:50 | ZN690:PA35 | URBAN | Planned |  | 69 | 640 | 0.029211 | 4.6e-05 | N
24-07-18 | 07:10 | ZN12650:PA1 | SHORT RURAL | Planned |  | 85 | 585 | 0.25911 | 0.000443 | N
24-07-18 | 08:10 | ZN12650:PA1 | SHORT RURAL | Planned |  | 18 | 450 | 0.042209 | 9.4e-05 | N
24-07-18 | 07:30 | ZN8700:PA67 68G | URBAN | Planned |  | 3 | 10,540 | 0.020916 | 2e-06 | N
24-07-18 | 09:00 | ZN15009:PA11 | URBAN | Planned |  | 99 | 465 | 0.030451 | 6.5e-05 | N
24-07-18 | 08:40 | ZN180:PA30 | URBAN | Planned |  | 75 | 300 | 0.014883 | 5e-05 | N
24-07-18 | 09:30 | ZN2400:PA18 | SHORT RURAL | Planned |  | 36 | 360 | 0.067534 | 0.000188 | N
24-07-18 | 08:10 | ZN12610:PA20 | SHORT RURAL | Planned |  | 16 | 430 | 0.035851 | 8.3e-05 | N
24-07-18 | 10:00 | ZN342:PA16 | URBAN | Planned |  | 86 | 240 | 0.013653 | 5.7e-05 | N
25-07-18 | 07:00 | ZN15006:PA12 | URBAN | Planned |  | 4 | 660 | 0.001746 | 3e-06 | N
25-07-18 | 09:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 36 | 450 | 0.084323 | 0.000187 | N
25-07-18 | 08:05 | ZN12690:PA24 | SHORT RURAL | Planned |  | 51 | 475 | 0.12609 | 0.000265 | N
25-07-18 | 09:00 | ZN80:PA40 | URBAN | Planned |  | 67 | 425 | 0.018834 | 4.4e-05 | N
25-07-18 | 20:20 | ZN630:PA32 | URBAN | Planned |  | 18 | 450 | 0.005358 | 1.2e-05 | N
25-07-18 | 20:30 | ZN195:PA4 | URBAN | Planned |  | 26 | 720 | 0.012382 | 1.7e-05 | N
26-07-18 | 07:00 | ZN1287:PA5 | URBAN | Planned |  | 1 | 285 | 0.000188 | 1e-06 | N
26-07-18 | 07:30 | ZN10991:PA6 | URBAN | Planned |  | 115 | 510 | 0.038785 | 7.6e-05 | N
26-07-18 | 08:00 | ZN12630:PA11 | SHORT RURAL | Planned |  | 8 | 465 | 0.019361 | 4.2e-05 | N
26-07-18 | 08:10 | ZN14891:PA5 | SHORT RURAL | Planned |  | 9 | 470 | 0.022016 | 4.7e-05 | N
26-07-18 | 08:00 | ZN15005:PA6 | URBAN | Planned |  | 38 | 480 | 0.012062 | 2.5e-05 | N
26-07-18 | 19:30 | ZN36300:PA17 | URBAN | Planned |  | 109 | 510 | 0.036761 | 7.2e-05 | N
27-07-18 | 08:00 | ZN14891:PA20 | SHORT RURAL | Planned |  | 3 | 480 | 0.007543 | 1.6e-05 | N
27-07-18 | 22:00 | ZN3155:PA18 | URBAN | Planned |  | 239 | 360 | 0.056898 | 0.000158 | N
28-07-18 | 08:00 | ZN35500:PA24 | URBAN | Planned |  | 113 | 775 | 0.057913 | 7.5e-05 | N
28-07-18 | 07:30 | ZN129:PA49 | URBAN | Planned |  | 51 | 805 | 0.02715 | 3.4e-05 | N
28-07-18 | 10:00 | ZN4990:PA55 56DEF | CBD | Planned |  | 39 | 390 | 0.49107 | 0.001259 | N
28-07-18 | 10:25 | ZN14892:PA5 | URBAN | Planned |  | 1 | 490 | 0.000324 | 1e-06 | N
29-07-18 | 07:30 | ZN2635:PA59 | URBAN | Planned |  | 1 | 570 | 0.000377 | 1e-06 | N
29-07-18 | 20:00 | ZN5868:PA6 | URBAN | Planned |  | 3 | 625 | 0.00124 | 2e-06 | N
30-07-18 | 07:30 | ZN2835:PA16 | URBAN | Planned |  | 24 | 540 | 0.00857 | 1.6e-05 | N
30-07-18 | 07:15 | ZN14143:PA17 | SHORT RURAL | Planned |  | 238 | 570 | 0.70608 | 0.001239 | N
30-07-18 | 08:30 | ZN9252:PA21 | URBAN | Planned |  | 5 | 520 | 0.001719 | 3e-06 | N
30-07-18 | 08:30 | ZN9252:PA21 | URBAN | Planned |  | 44 | 520 | 0.015131 | 2.9e-05 | N
30-07-18 | 07:30 | ZN15012:PA8 | URBAN | Planned |  | 59 | 300 | 0.011705 | 3.9e-05 | N
30-07-18 | 07:30 | ZN129:PA52 | URBAN | Planned |  | 50 | 420 | 0.013887 | 3.3e-05 | N
30-07-18 | 08:15 | ZN14891:PA12 | SHORT RURAL | Planned |  | 10 | 450 | 0.023422 | 5.2e-05 | N
30-07-18 | 08:40 | ZN12690:PA17 | URBAN | Planned |  | 50 | 440 | 0.014549 | 3.3e-05 | N
30-07-18 | 10:00 | ZN8100:PA30 | URBAN | Planned |  | 1 | 15 | 1e-05 | 1e-06 | N
30-07-18 | 18:00 | ZN7481:PA21 | URBAN | Planned |  | 11 | 780 | 0.005674 | 7e-06 | N
29-07-18 | 19:00 | ZN5868:PA13 | URBAN | Planned |  | 17 | 685 | 0.007701 | 1.1e-05 | N
30-07-18 | 20:30 | ZN630:PA33 | URBAN | Planned |  | 2 | 710 | 0.000939 | 1e-06 | N
31-07-18 | 04:20 | ZN2466:PA16 | URBAN | Planned |  | 3 | 60 | 0.000119 | 2e-06 | N
31-07-18 | 08:10 | ZN12630:PA8 | SHORT RURAL | Planned |  | 7 | 455 | 0.016572 | 3.6e-05 | N
31-07-18 | 09:25 | ZN36200:PA1 | URBAN | Planned |  | 25 | 450 | 0.007442 | 1.7e-05 | N
31-07-18 | 09:00 | ZN129:PA56 | URBAN | Planned |  | 97 | 302 | 0.019378 | 6.4e-05 | N
17-08-18 | 08:00 | 813:89061 | LONG RURAL | Planned |  | 12 | 350 | 1.4778 | 0.004222 | N
18-08-18 | 08:00 | 239:82131 | SHORT RURAL | Planned |  | 5 | 645 | 0.016903 | 2.6e-05 | N
19-08-18 | 08:05 | 256:80632 | URBAN | Planned |  | 79 | 430 | 0.022421 | 5.2e-05 | N
16-08-18 | 08:00 | 524:33572 | SHORT RURAL | Planned |  | 5 | 45 | 0.00118 | 2.6e-05 | N
16-08-18 | 11:05 | 524:33572 | SHORT RURAL | Planned |  | 4 | 42 | 0.000881 | 2.1e-05 | N
16-08-18 | 10:50 | 522:83132 | SHORT RURAL | Planned |  | 4 | 38 | 0.000797 | 2.1e-05 | N
16-08-18 | 13:00 | 522:83132 | SHORT RURAL | Planned |  | 1 | 60 | 0.000315 | 5e-06 | N
17-08-18 | 08:30 | 526:34641 | SHORT RURAL | Planned |  | 4 | 214 | 0.004488 | 2.1e-05 | N
16-08-18 | 08:45 | 810:74058 | SHORT RURAL | Planned |  | 2 | 80 | 0.000839 | 1e-05 | N
16-08-18 | 13:15 | 802:82220 | SHORT RURAL | Planned |  | 1 | 60 | 0.000315 | 5e-06 | N
17-08-18 | 08:30 | 516:48067 | SHORT RURAL | Planned |  | 3 | 45 | 0.000708 | 1.6e-05 | N
17-08-18 | 08:15 | 513:48059 | SHORT RURAL | Planned |  | 1 | 30 | 0.000157 | 5e-06 | N
17-08-18 | 09:30 | 807:74181 | SHORT RURAL | Planned |  | 48 | 40 | 0.010066 | 0.000252 | N
17-08-18 | 10:00 | 523:33501 | SHORT RURAL | Planned |  | 11 | 70 | 0.004037 | 5.8e-05 | N
17-08-18 | 08:10 | 515:35197 | LONG RURAL | Planned |  | 74 | 215 | 5.5982 | 0.026038 | N
18-08-18 | 08:10 | 513:48057 | URBAN | Planned |  | 19 | 260 | 0.003261 | 1.3e-05 | N
01-08-18 | 08:05 | ZN2635:PA57 | URBAN | Planned |  | 29 | 210 | 0.004026 | 1.9e-05 | N
01-08-18 | 07:30 | ZN9252:PA22 | URBAN | Planned |  | 39 | 480 | 0.012376 | 2.6e-05 | N
01-08-18 | 10:00 | ZN3922:PA10 | URBAN | Planned |  | 67 | 200 | 0.008859 | 4.4e-05 | N
01-08-18 | 08:05 | ZN12630:PA11 | SHORT RURAL | Planned |  | 8 | 430 | 0.017898 | 4.2e-05 | N
20-08-18 | 09:00 | 204:82697 | URBAN | Planned |  | 106 | 370 | 0.025887 | 7e-05 | N
20-08-18 | 08:35 | 514:18137 | SHORT RURAL | Planned |  | 8 | 260 | 0.010901 | 4.2e-05 | N
20-08-18 | 08:35 | 523:33501 | SHORT RURAL | Planned |  | 3 | 260 | 0.004088 | 1.6e-05 | N
01-08-18 | 08:30 | ZN384:PA76 | URBAN | Planned |  | 140 | 360 | 0.033319 | 9.3e-05 | N
02-08-18 | 08:00 | ZN965:PA24 | URBAN | Planned |  | 48 | 540 | 0.017136 | 3.2e-05 | N
02-08-18 | 08:00 | ZN965:PA38 | URBAN | Planned |  | 48 | 540 | 0.017136 | 3.2e-05 | N
02-08-18 | 08:30 | ZN14143:PA17 | SHORT RURAL | Planned |  | 1 | 390 | 0.002029 | 5e-06 | N
02-08-18 | 09:10 | ZN36800:PA49 | URBAN | Planned |  | 39 | 65 | 0.001676 | 2.6e-05 | N
02-08-18 | 08:40 | ZN80:PA40 | URBAN | Planned |  | 31 | 375 | 0.007685 | 2e-05 | N
02-08-18 | 13:15 | ZN12690:PA16 | SHORT RURAL | Planned |  | 16 | 65 | 0.005411 | 8.3e-05 | N
03-08-18 | 08:00 | ZN2466:PA2 | URBAN | Planned |  | 1 | 600 | 0.000397 | 1e-06 | N
03-08-18 | 08:15 | ZN195:PA30 | SHORT RURAL | Planned |  | 49 | 325 | 0.082859 | 0.000255 | N
03-08-18 | 22:30 | ZN3155:PA18 | URBAN | Planned |  | 277 | 540 | 0.09889 | 0.000183 | N
04-08-18 | 09:30 | ZN35900:PA10 | URBAN | Planned |  | 1 | 1,795 | 0.001188 | 1e-06 | N
04-08-18 | 10:30 | ZN8700:PA65 66ABC | CBD | Planned |  | 3 | 1,500 | 0.14582 | 9.7e-05 | N
05-08-18 | 18:20 | ZN14891:PA3 | SHORT RURAL | Planned |  | 1 | 1,740 | 0.009122 | 5e-06 | N
06-08-18 | 08:00 | ZN874:PA16 | URBAN | Planned |  | 69 | 505 | 0.023034 | 4.6e-05 | N
06-08-18 | 08:00 | ZN12650:PA13 | SHORT RURAL | Planned |  | 54 | 480 | 0.13459 | 0.00028 | N
06-08-18 | 09:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 12 | 395 | 0.024613 | 6.2e-05 | N
06-08-18 | 10:15 | ZN384:PA70 | URBAN | Planned |  | 57 | 225 | 0.008478 | 3.8e-05 | N
06-08-18 | 09:30 | ZN10994:PA20 | URBAN | Planned |  | 29 | 300 | 0.005751 | 1.9e-05 | N
06-08-18 | 19:45 | ZN80:PA27 | URBAN | Planned |  | 1 | 940 | 0.000621 | 1e-06 | N
06-08-18 | 22:30 | ZN35370:PA10 | SHORT RURAL | Planned |  | 1 | 255 | 0.001324 | 5e-06 | N
07-08-18 | 07:50 | ZN12630:PA11 | SHORT RURAL | Planned |  | 28 | 470 | 0.068336 | 0.000145 | N
07-08-18 | 08:20 | ZN263:PA33 34KLM | CBD | Planned |  | 1 | 410 | 0.013306 | 3.2e-05 | N
07-08-18 | 09:00 | ZN12580:PA12 | SHORT RURAL | Planned |  | 42 | 370 | 0.080695 | 0.000218 | N
07-08-18 | 08:20 | ZN12690:PA16 | SHORT RURAL | Planned |  | 30 | 350 | 0.054523 | 0.000156 | N
07-08-18 | 08:05 | ZN12630:PA8 | SHORT RURAL | Planned |  | 20 | 475 | 0.049331 | 0.000104 | N
07-08-18 | 08:50 | ZN12650:PA17 | URBAN | Planned |  | 128 | 287 | 0.024285 | 8.5e-05 | N
07-08-18 | 09:20 | ZN12580:PA4 | URBAN | Planned |  | 23 | 180 | 0.002737 | 1.5e-05 | N
21-08-18 | 08:10 | 242:81541 | URBAN | Planned |  | 263 | 380 | 0.066009 | 0.000174 | N
21-08-18 | 09:52 | 526:34636 | SHORT RURAL | Planned |  | 2 | 63 | 0.00066 | 1e-05 | N
21-08-18 | 12:30 | 526:34636 | SHORT RURAL | Planned |  | 2 | 25 | 0.000262 | 1e-05 | N
21-08-18 | 08:00 | 522:83123 | SHORT RURAL | Planned |  | 2 | 320 | 0.003355 | 1e-05 | N
21-08-18 | 08:30 | 229:34986 | SHORT RURAL | Planned |  | 52 | 390 | 0.1063 | 0.000273 | N
21-08-18 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 9 | 110 | 0.005189 | 4.7e-05 | N
21-08-18 | 08:27 | 512:83743 | SHORT RURAL | Planned |  | 78 | 283 | 0.1157 | 0.000409 | N
21-08-18 | 08:15 | 813:89055 | SHORT RURAL | Planned |  | 37 | 385 | 0.074664 | 0.000194 | N
22-08-18 | 12:50 | 526:34640 | SHORT RURAL | Planned |  | 1 | 70 | 0.000367 | 5e-06 | N
22-08-18 | 08:35 | 512:83743 | SHORT RURAL | Planned |  | 9 | 335 | 0.015802 | 4.7e-05 | N
22-08-18 | 10:15 | 227:13014 | SHORT RURAL | Planned |  | 2 | 123 | 0.001289 | 1e-05 | N
22-08-18 | 08:00 | 524:33576 | SHORT RURAL | Planned |  | 8 | 250 | 0.010482 | 4.2e-05 | N
22-08-18 | 08:25 | 522:83123 | SHORT RURAL | Planned |  | 1 | 155 | 0.000812 | 5e-06 | N
22-08-18 | 12:30 | 526:34640 | SHORT RURAL | Planned |  | 3 | 90 | 0.001415 | 1.6e-05 | N
22-08-18 | 09:30 | 508:82574 | SHORT RURAL | Planned |  | 3 | 30 | 0.000472 | 1.6e-05 | N
22-08-18 | 09:05 | 526:34637 | SHORT RURAL | Planned |  | 2 | 300 | 0.003145 | 1e-05 | N
22-08-18 | 08:47 | 232:33407 | SHORT RURAL | Planned |  | 15 | 388 | 0.030504 | 7.9e-05 | N
22-08-18 | 09:10 | 813:89063 | SHORT RURAL | Planned |  | 74 | 295 | 0.11442 | 0.000388 | N
07-08-18 | 10:30 | ZN931:PA2 | URBAN | Planned |  | 64 | 215 | 0.009096 | 4.2e-05 | N
08-08-18 | 07:30 | ZN2568:PA14 | URBAN | Planned |  | 67 | 480 | 0.02126 | 4.4e-05 | N
08-08-18 | 09:00 | ZN12610:PA10 | URBAN | Planned |  | 5 | 315 | 0.001041 | 3e-06 | N
08-08-18 | 09:00 | ZN965:PA38 | URBAN | Planned |  | 48 | 225 | 0.007139 | 3.2e-05 | N
08-08-18 | 12:00 | ZN15005:PA12 | URBAN | Planned |  | 42 | 145 | 0.004026 | 2.8e-05 | N
08-08-18 | 08:05 | ZN12630:PA8 | SHORT RURAL | Planned |  | 7 | 460 | 0.016721 | 3.6e-05 | N
08-08-18 | 08:40 | ZN12660:PA10 | SHORT RURAL | Planned |  | 59 | 65 | 0.019914 | 0.000306 | N
08-08-18 | 08:30 | ZN36800:PA58 | URBAN | Planned |  | 71 | 420 | 0.019713 | 4.7e-05 | N
08-08-18 | 16:00 | ZN2602:PA35 | URBAN | Planned |  | 94 | 240 | 0.014914 | 6.2e-05 | N
09-08-18 | 06:30 | ZN4990:PA53 54GHJ | CBD | Planned |  | 3 | 1,815 | 0.17719 | 9.8e-05 | N
09-08-18 | 09:20 | ZN5868:PA30 | URBAN | Planned |  | 45 | 360 | 0.010709 | 3e-05 | N
09-08-18 | 08:00 | ZN12580:PA12 | SHORT RURAL | Planned |  | 13 | 30 | 0.002025 | 6.8e-05 | N
09-08-18 | 15:30 | ZN12580:PA12 | SHORT RURAL | Planned |  | 13 | 15 | 0.001013 | 6.8e-05 | N
09-08-18 | 09:40 | ZN847:PA45 | SHORT RURAL | Planned |  | 5 | 100 | 0.002596 | 2.6e-05 | N
09-08-18 | 08:30 | ZN36800:PA50 | URBAN | Planned |  | 82 | 420 | 0.022767 | 5.4e-05 | N
10-08-18 | 07:30 | ZN195:PA11 | URBAN | Planned |  | 92 | 570 | 0.034767 | 6.1e-05 | N
10-08-18 | 11:00 | ZN14891:PA17 | SHORT RURAL | Planned |  | 37 | 30 | 0.005819 | 0.000194 | N
10-08-18 | 09:00 | ZN36800:PA50 | URBAN | Planned |  | 82 | 300 | 0.01631 | 5.4e-05 | N
11-08-18 | 07:30 | ZN384:PA66 | SHORT RURAL | Planned |  | 2 | 615 | 0.006447 | 1e-05 | N
11-08-18 | 07:15 | ZN2635:PA57 | URBAN | Planned |  | 1 | 600 | 0.000396 | 1e-06 | N
11-08-18 | 09:00 | ZN2568:PA21 | URBAN | Planned |  | 1 | 300 | 0.000198 | 1e-06 | N
11-08-18 | 07:30 | ZN384:PA66 | SHORT RURAL | Planned |  | 2 | 615 | 0.006447 | 1e-05 | N
11-08-18 | 15:30 | ZN8700:PA61 62KLM | CBD | Planned |  | 22 | 1,470 | 1.0524 | 0.000716 | N
11-08-18 | 22:00 | ZN9700:PA11 | URBAN | Planned |  | 17 | 750 | 0.008417 | 1.1e-05 | N
12-08-18 | 11:30 | ZN4990:PA55 56KLM | CBD | Planned |  | 130 | 390 | 1.6498 | 0.00423 | N
12-08-18 | 18:00 | ZN14891:PA3 | SHORT RURAL | Planned |  | 1 | 420 | 0.002201 | 5e-06 | N
12-08-18 | 20:30 | ZN10994:PA20 | URBAN | Planned |  | 51 | 450 | 0.015151 | 3.4e-05 | N
12-08-18 | 22:30 | ZN2568:PA27 | URBAN | Planned |  | 17 | 210 | 0.002357 | 1.1e-05 | N
13-08-18 | 07:40 | ZN12690:PA16 | SHORT RURAL | Planned |  | 43 | 475 | 0.10705 | 0.000225 | N
13-08-18 | 08:05 | ZN14143:PA5 | URBAN | Planned |  | 1 | 310 | 0.000205 | 1e-06 | N
13-08-18 | 09:15 | ZN1287:PA4 | URBAN | Planned |  | 2 | 325 | 0.000429 | 1e-06 | N
14-08-18 | 07:45 | ZN1610:PA1 | URBAN | Planned |  | 1 | 405 | 0.000267 | 1e-06 | N
14-08-18 | 07:30 | ZN3154:PA22 | SHORT RURAL | Planned |  | 13 | 535 | 0.036513 | 6.8e-05 | N
14-08-18 | 10:32 | ZN2400:PA18 | SHORT RURAL | Planned |  | 98 | 328 | 0.16875 | 0.000514 | N
14-08-18 | 08:50 | ZN12640:PA8 | SHORT RURAL | Planned |  | 58 | 365 | 0.11114 | 0.000304 | N
14-08-18 | 09:00 | ZN15014:PA14 | URBAN | Planned |  | 63 | 300 | 0.012474 | 4.2e-05 | N
14-08-18 | 09:00 | ZN15014:PA22 | URBAN | Planned |  | 60 | 300 | 0.01188 | 4e-05 | N
14-08-18 | 09:30 | ZN9550:PA3 | URBAN | Planned |  | 44 | 330 | 0.009584 | 2.9e-05 | N
14-08-18 | 11:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 4 | 300 | 0.0063 | 2.1e-05 | N
14-08-18 | 10:32 | ZN2400:PA18 | SHORT RURAL | Planned |  | 37 | 328 | 0.063713 | 0.000194 | N
14-08-18 | 22:00 | ZN15001:PA18 | URBAN | Planned |  | 127 | 480 | 0.040235 | 8.4e-05 | N
15-08-18 | 07:00 | ZN12650:PA9 | URBAN | Planned |  | 2 | 1,965 | 0.002598 | 1e-06 | N
15-08-18 | 07:30 | ZN36300:PA5 | URBAN | Planned |  | 28 | 455 | 0.008422 | 1.9e-05 | N
15-08-18 | 08:10 | ZN931:PA2 | URBAN | Planned |  | 58 | 620 | 0.023773 | 3.8e-05 | N
15-08-18 | 08:45 | ZN12630:PA13 | SHORT RURAL | Planned |  | 9 | 350 | 0.016537 | 4.7e-05 | N
15-08-18 | 08:00 | ZN9118:PA17 | URBAN | Planned |  | 28 | 240 | 0.004442 | 1.9e-05 | N
15-08-18 | 09:50 | ZN9900:PA6 | URBAN | Planned |  | 5 | 340 | 0.001124 | 3e-06 | N
15-08-18 | 09:30 | ZN12650:PA9 | URBAN | Planned |  | 62 | 165 | 0.006763 | 4.1e-05 | N
15-08-18 | 11:00 | ZN2835:PA30 | URBAN | Planned |  | 91 | 240 | 0.014438 | 6e-05 | N
16-08-18 | 07:30 | ZN35500:PA31 | URBAN | Planned |  | 109 | 420 | 0.030222 | 7.2e-05 | N
16-08-18 | 08:05 | ZN12600:PA13 | SHORT RURAL | Planned |  | 6 | 390 | 0.012267 | 3.1e-05 | N
16-08-18 | 09:10 | ZN12600:PA2 | SHORT RURAL | Planned |  | 5 | 153 | 0.00401 | 2.6e-05 | N
16-08-18 | 21:50 | ZN15005:PA2 | URBAN | Planned |  | 107 | 205 | 0.014481 | 7.1e-05 | N
16-08-18 | 20:00 | ZN263:PA33 34KLM | CBD | Planned |  | 1 | 600 | 0.019592 | 3.3e-05 | N
16-08-18 | 19:30 | ZN263:PA33 34KLM | CBD | Planned |  | 8 | 435 | 0.11363 | 0.000261 | N
16-08-18 | 20:00 | ZN12610:PA16 | URBAN | Planned |  | 44 | 570 | 0.016557 | 2.9e-05 | N
17-08-18 | 07:30 | ZN129:PA55 | URBAN | Planned |  | 9 | 420 | 0.002495 | 6e-06 | N
17-08-18 | 07:30 | ZN2196:PA3 | URBAN | Planned |  | 49 | 420 | 0.013587 | 3.2e-05 | N
17-08-18 | 08:20 | ZN14144:PA10 | SHORT RURAL | Planned |  | 13 | 380 | 0.025899 | 6.8e-05 | N
23-08-18 | 09:04 | 516:48067 | SHORT RURAL | Planned |  | 6 | 234 | 0.007359 | 3.1e-05 | N
23-08-18 | 08:36 | 224:80340 | SHORT RURAL | Planned |  | 1 | 30 | 0.000157 | 5e-06 | N
23-08-18 | 08:30 | 216:10722 | SHORT RURAL | Planned |  | 133 | 555 | 0.38689 | 0.000697 | N
23-08-18 | 09:00 | 265:81648 | SHORT RURAL | Planned |  | 2 | 140 | 0.001468 | 1e-05 | N
23-08-18 | 08:25 | 524:33580 | SHORT RURAL | Planned |  | 2 | 199 | 0.002086 | 1e-05 | N
23-08-18 | 08:30 | 265:81651 | SHORT RURAL | Planned |  | 18 | 215 | 0.020284 | 9.4e-05 | N
23-08-18 | 13:15 | 526:34640 | SHORT RURAL | Planned |  | 1 | 15 | 7.9e-05 | 5e-06 | N
23-08-18 | 08:00 | 515:35192 | SHORT RURAL | Planned |  | 19 | 230 | 0.022905 | 0.0001 | N
24-08-18 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 11 | 85 | 0.32888 | 0.003869 | N
24-08-18 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 14 | 150 | 0.011007 | 7.3e-05 | N
24-08-18 | 12:30 | 512:83743 | SHORT RURAL | Planned |  | 12 | 65 | 0.004088 | 6.3e-05 | N
25-08-18 | 08:00 | 224:80340 | SHORT RURAL | Planned |  | 62 | 150 | 0.048728 | 0.000325 | N
26-08-18 | 08:00 | 221:11898 | SHORT RURAL | Planned |  | 22 | 460 | 0.053025 | 0.000115 | N
26-08-18 | 08:15 | 227:13015 | SHORT RURAL | Planned |  | 134 | 605 | 0.42478 | 0.000702 | N
24-08-18 | 08:00 | 235:2120 | SHORT RURAL | Planned |  | 16 | 500 | 0.04193 | 8.4e-05 | N
24-08-18 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 3 | 210 | 0.2216 | 0.001055 | N
24-08-18 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 2 | 40 | 0.028139 | 0.000703 | N
24-08-18 | 14:05 | 526:34640 | SHORT RURAL | Planned |  | 1 | 60 | 0.000314 | 5e-06 | N
26-08-18 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 1 | 75 | 0.026371 | 0.000352 | N
26-08-18 | 11:50 | 509:33395 | LONG RURAL | Planned |  | 1 | 50 | 0.017581 | 0.000352 | N
26-08-18 | 08:24 | 511:29882 | URBAN | Planned |  | 1 | 310 | 0.000205 | 1e-06 | N
26-08-18 | 14:30 | 509:33395 | LONG RURAL | Planned |  | 4 | 95 | 0.13362 | 0.001406 | N
24-08-18 | 08:00 | 801:74123 | SHORT RURAL | Planned |  | 4 | 67 | 0.001405 | 2.1e-05 | N
24-08-18 | 11:15 | 813:89062 | SHORT RURAL | Planned |  | 2 | 60 | 0.000629 | 1e-05 | N
24-08-18 | 09:00 | 813:89055 | SHORT RURAL | Planned |  | 2 | 220 | 0.002306 | 1e-05 | N
24-08-18 | 10:30 | 811:74234 | SHORT RURAL | Planned |  | 2 | 70 | 0.000734 | 1e-05 | N
24-08-18 | 09:30 | 801:74123 | SHORT RURAL | Planned |  | 2 | 45 | 0.000472 | 1e-05 | N
24-08-18 | 08:10 | 513:48056 | SHORT RURAL | Planned |  | 23 | 123 | 0.014827 | 0.000121 | N
24-08-18 | 13:00 | 523:33501 | SHORT RURAL | Planned |  | 6 | 60 | 0.001887 | 3.1e-05 | N
26-08-18 | 10:00 | 514:18137 | SHORT RURAL | Planned |  | 2 | 25 | 0.000262 | 1e-05 | N
26-08-18 | 08:35 | 409:6012 | URBAN | Planned |  | 1 | 172 | 0.000114 | 1e-06 | N
27-08-18 | 11:00 | 232:11455 | SHORT RURAL | Planned |  | 147 | 215 | 0.1656 | 0.00077 | N
27-08-18 | 08:20 | 239:82136 | URBAN | Planned |  | 103 | 230 | 0.015633 | 6.8e-05 | N
27-08-18 | 08:43 | 508:82579 | SHORT RURAL | Planned |  | 4 | 41 | 0.000859 | 2.1e-05 | N
27-08-18 | 09:08 | 508:82575 | SHORT RURAL | Planned |  | 4 | 22 | 0.000461 | 2.1e-05 | N
27-08-18 | 10:46 | 508:82579 | SHORT RURAL | Planned |  | 2 | 34 | 0.000356 | 1e-05 | N
27-08-18 | 11:28 | 508:82575 | SHORT RURAL | Planned |  | 5 | 22 | 0.000576 | 2.6e-05 | N
28-08-18 | 08:05 | 526:34639 | SHORT RURAL | Planned |  | 37 | 470 | 0.090248 | 0.000192 | N
28-08-18 | 08:30 | 509:33399 | SHORT RURAL | Planned |  | 186 | 340 | 0.32819 | 0.000965 | N
28-08-18 | 08:25 | 508:82580 | SHORT RURAL | Planned |  | 2 | 355 | 0.003685 | 1e-05 | N
28-08-18 | 08:10 | 807:74184 | SHORT RURAL | Planned |  | 2 | 120 | 0.001246 | 1e-05 | N
28-08-18 | 08:07 | 513:48056 | SHORT RURAL | Planned |  | 35 | 683 | 0.12406 | 0.000182 | N
29-08-18 | 08:00 | 516:48067 | SHORT RURAL | Planned |  | 2 | 315 | 0.00327 | 1e-05 | N
29-08-18 | 08:20 | 256:80632 | URBAN | Planned |  | 3 | 140 | 0.000277 | 2e-06 | N
29-08-18 | 08:55 | 515:35197 | LONG RURAL | Planned |  | 5 | 320 | 0.56279 | 0.001759 | N
29-08-18 | 10:00 | 532:83307 | SHORT RURAL | Planned |  | 1 | 70 | 0.000363 | 5e-06 | N
29-08-18 | 10:00 | 235:2120 | SHORT RURAL | Planned |  | 25 | 207 | 0.026858 | 0.00013 | N
29-08-18 | 08:40 | 801:74123 | SHORT RURAL | Planned |  | 2 | 110 | 0.001142 | 1e-05 | N
29-08-18 | 11:30 | 515:35197 | LONG RURAL | Planned |  | 1 | 190 | 0.066831 | 0.000352 | N
29-08-18 | 08:35 | 508:82579 | SHORT RURAL | Planned |  | 4 | 42 | 0.000872 | 2.1e-05 | N
29-08-18 | 10:34 | 508:82579 | SHORT RURAL | Planned |  | 1 | 64 | 0.000332 | 5e-06 | N
03-09-18 | 08:05 | ZN12610:PA6 | URBAN | Planned |  | 240 | 460 | 0.072947 | 0.000159 | N
30-08-18 | 08:30 | 522:83131 | URBAN | Planned |  | 1 | 253 | 0.000167 | 1e-06 | N
30-08-18 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 33 | 200 | 2.3223 | 0.011612 | N
30-08-18 | 08:15 | 813:89061 | LONG RURAL | Planned |  | 5 | 335 | 0.58937 | 0.001759 | N
30-08-18 | 08:12 | 523:33501 | SHORT RURAL | Planned |  | 13 | 373 | 0.025166 | 6.7e-05 | N
30-08-18 | 08:15 | 202:34261 | URBAN | Planned |  | 31 | 385 | 0.007886 | 2e-05 | N
31-08-18 | 08:30 | 256:80632 | URBAN | Planned |  | 36 | 330 | 0.00785 | 2.4e-05 | N
02-09-18 | 08:00 | 256:80632 | URBAN | Planned |  | 79 | 540 | 0.028188 | 5.2e-05 | N
02-09-18 | 08:00 | 256:80640 | URBAN | Planned |  | 147 | 540 | 0.052451 | 9.7e-05 | N
30-08-18 | 08:50 | 526:34640 | SHORT RURAL | Planned |  | 1 | 130 | 0.000675 | 5e-06 | N
31-08-18 | 08:30 | 508:82574 | SHORT RURAL | Planned |  | 41 | 220 | 0.046814 | 0.000213 | N
31-08-18 | 11:30 | 528:83019 | SHORT RURAL | Planned |  | 2 | 165 | 0.001713 | 1e-05 | N
31-08-18 | 08:02 | 512:83743 | SHORT RURAL | Planned |  | 1 | 118 | 0.000612 | 5e-06 | N
31-08-18 | 10:35 | 512:83743 | SHORT RURAL | Planned |  | 1 | 45 | 0.000234 | 5e-06 | N
31-08-18 | 08:15 | 801:74121 | LONG RURAL | Planned |  | 17 | 195 | 1.1664 | 0.005982 | N
31-08-18 | 09:15 | 813:89062 | SHORT RURAL | Planned |  | 16 | 155 | 0.012871 | 8.3e-05 | N
31-08-18 | 08:40 | 515:35197 | LONG RURAL | Planned |  | 1 | 250 | 0.087966 | 0.000352 | N
03-09-18 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 20 | 285 | 2.0056 | 0.007037 | N
03-09-18 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 36 | 405 | 5.1302 | 0.012667 | N
03-09-18 | 07:50 | 810:74050 | SHORT RURAL | Planned |  | 1 | 40 | 0.000208 | 5e-06 | N
03-09-18 | 08:10 | 515:35197 | LONG RURAL | Planned |  | 2 | 65 | 0.045742 | 0.000704 | N
03-09-18 | 10:00 | 810:74050 | SHORT RURAL | Planned |  | 1 | 55 | 0.000285 | 5e-06 | N
03-09-18 | 10:00 | 515:35197 | LONG RURAL | Planned |  | 5 | 60 | 0.10556 | 0.001759 | N
03-09-18 | 13:00 | 515:35197 | LONG RURAL | Planned |  | 2 | 50 | 0.035186 | 0.000704 | N
03-09-18 | 11:10 | 810:74050 | SHORT RURAL | Planned |  | 1 | 45 | 0.000234 | 5e-06 | N
04-09-18 | 08:00 | 522:83132 | SHORT RURAL | Planned |  | 123 | 460 | 0.29368 | 0.000638 | N
04-09-18 | 08:30 | 524:33580 | SHORT RURAL | Planned |  | 13 | 230 | 0.01552 | 6.7e-05 | N
04-09-18 | 10:00 | 516:48067 | SHORT RURAL | Planned |  | 1 | 38 | 0.000197 | 5e-06 | N
04-09-18 | 09:10 | 813:89061 | LONG RURAL | Planned |  | 1 | 75 | 0.02639 | 0.000352 | N
04-09-18 | 08:50 | 523:33508 | SHORT RURAL | Planned |  | 25 | 120 | 0.015572 | 0.00013 | N
04-09-18 | 10:45 | 813:89061 | LONG RURAL | Planned |  | 3 | 55 | 0.058058 | 0.001056 | N
04-09-18 | 11:20 | 516:48067 | SHORT RURAL | Planned |  | 1 | 40 | 0.000208 | 5e-06 | N
04-09-18 | 11:55 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017593 | 0.000352 | N
04-09-18 | 13:00 | 813:89061 | LONG RURAL | Planned |  | 2 | 60 | 0.042224 | 0.000704 | N
05-09-18 | 08:05 | 810:74050 | SHORT RURAL | Planned |  | 7 | 185 | 0.006722 | 3.6e-05 | N
05-09-18 | 08:40 | 512:83743 | SHORT RURAL | Planned |  | 9 | 175 | 0.008175 | 4.7e-05 | N
05-09-18 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 11 | 457 | 1.7688 | 0.003871 | N
05-09-18 | 20:30 | 507:80932 | SHORT RURAL | Planned |  | 25 | 90 | 0.011679 | 0.00013 | N
05-09-18 | 08:05 | 515:35193 | SHORT RURAL | Planned |  | 10 | 265 | 0.013755 | 5.2e-05 | N
05-09-18 | 08:17 | 514:18137 | SHORT RURAL | Planned |  | 1 | 55 | 0.000285 | 5e-06 | N
05-09-18 | 10:00 | 514:18137 | SHORT RURAL | Planned |  | 1 | 40 | 0.000208 | 5e-06 | N
05-09-18 | 11:55 | 515:35193 | SHORT RURAL | Planned |  | 4 | 105 | 0.00218 | 2.1e-05 | N
17-08-18 | 20:30 | ZN35800:PA16 | URBAN | Planned |  | 79 | 720 | 0.037551 | 5.2e-05 | N
18-08-18 | 02:00 | ZN12690:PA16 | SHORT RURAL | Planned |  | 3 | 360 | 0.00566 | 1.6e-05 | N
19-08-18 | 16:00 | ZN12690:PA16 | SHORT RURAL | Planned |  | 3 | 240 | 0.003774 | 1.6e-05 | N
18-08-18 | 02:55 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 140 | 0.006604 | 4.7e-05 | N
18-08-18 | 07:00 | ZN4990:PA53 54KLM | CBD | Planned |  | 10 | 585 | 0.19099 | 0.000326 | N
18-08-18 | 07:30 | ZN195:PA29 | URBAN | Planned |  | 29 | 690 | 0.013207 | 1.9e-05 | N
18-08-18 | 15:00 | ZN2466:PA22 | URBAN | Planned |  | 4 | 61 | 0.000161 | 3e-06 | N
18-08-18 | 18:00 | ZN7481:PA21 | URBAN | Planned |  | 7 | 765 | 0.003535 | 5e-06 | N
19-08-18 | 07:30 | ZN8000:PA4 | URBAN | Planned |  | 1 | 330 | 0.000218 | 1e-06 | N
19-08-18 | 08:20 | ZN35400:PA102 | URBAN | Planned |  | 5 | 420 | 0.001386 | 3e-06 | N
19-08-18 | 08:00 | ZN12650:PA19 | URBAN | Planned |  | 3 | 480 | 0.00095 | 2e-06 | N
19-08-18 | 08:00 | ZN12650:PA14 | URBAN | Planned |  | 29 | 480 | 0.009188 | 1.9e-05 | N
19-08-18 | 08:15 | ZN12660:PA10 | SHORT RURAL | Planned |  | 19 | 395 | 0.039334 | 0.0001 | N
19-08-18 | 08:15 | ZN12660:PA10 | SHORT RURAL | Planned |  | 9 | 395 | 0.018632 | 4.7e-05 | N
19-08-18 | 17:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 245 | 0.011557 | 4.7e-05 | N
19-08-18 | 19:30 | ZN8700:PA61 62GHJ | CBD | Planned |  | 14 | 705 | 0.32224 | 0.000457 | N
19-08-18 | 23:00 | ZN3155:PA35 | URBAN | Planned |  | 94 | 240 | 0.01489 | 6.2e-05 | N
20-08-18 | 07:30 | ZN3155:PA35 | URBAN | Planned |  | 118 | 510 | 0.039721 | 7.8e-05 | N
21-08-18 | 08:10 | ZN9118:PA8 | URBAN | Planned |  | 45 | 350 | 0.010403 | 3e-05 | N
21-08-18 | 08:35 | ZN12600:PA2 | SHORT RURAL | Planned |  | 4 | 420 | 0.008806 | 2.1e-05 | N
21-08-18 | 11:10 | ZN12620:PA11 | SHORT RURAL | Planned |  | 3 | 140 | 0.002201 | 1.6e-05 | N
22-08-18 | 04:00 | ZN931:PA3 | URBAN | Planned |  | 1 | 2 | 1e-06 | 1e-06 | N
22-08-18 | 04:00 | ZN931:PA3 | URBAN | Planned |  | 1 | 2 | 1e-06 | 1e-06 | N
22-08-18 | 07:30 | ZN3922:PA26 | URBAN | Planned |  | 63 | 330 | 0.013723 | 4.2e-05 | N
22-08-18 | 07:30 | ZN2602:PA20 | URBAN | Planned |  | 46 | 420 | 0.012753 | 3e-05 | N
22-08-18 | 08:02 | ZN12630:PA11 | SHORT RURAL | Planned |  | 9 | 418 | 0.019717 | 4.7e-05 | N
22-08-18 | 08:02 | ZN12630:PA11 | SHORT RURAL | Planned |  | 3 | 418 | 0.006572 | 1.6e-05 | N
22-08-18 | 09:00 | ZN12580:PA10 | URBAN | Planned |  | 40 | 360 | 0.009505 | 2.6e-05 | N
22-08-18 | 08:50 | ZN8700:PA61 62ABC | CBD | Planned |  | 154 | 220 | 1.1063 | 0.005029 | N
23-08-18 | 07:30 | ZN9245:PA19 | URBAN | Planned |  | 38 | 450 | 0.011287 | 2.5e-05 | N
23-08-18 | 08:45 | ZN2400:PA11 | SHORT RURAL | Planned |  | 10 | 570 | 0.029876 | 5.2e-05 | N
23-08-18 | 09:30 | ZN3922:PA10 | URBAN | Planned |  | 71 | 285 | 0.013357 | 4.7e-05 | N
23-08-18 | 08:00 | ZN1287:PA3 | URBAN | Planned |  | 58 | 420 | 0.016079 | 3.8e-05 | N
23-08-18 | 08:20 | ZN9118:PA8 | URBAN | Planned |  | 74 | 445 | 0.021736 | 4.9e-05 | N
23-08-18 | 20:00 | ZN2466:PA40 | URBAN | Planned |  | 1 | 150 | 9.9e-05 | 1e-06 | N
23-08-18 | 20:00 | ZN2466:PA40 | URBAN | Planned |  | 6 | 150 | 0.000594 | 4e-06 | N
24-08-18 | 08:15 | ZN36100:PA1 | URBAN | Planned |  | 100 | 405 | 0.026733 | 6.6e-05 | N
24-08-18 | 07:00 | ZN2568:PA14 | URBAN | Planned |  | 78 | 540 | 0.027802 | 5.1e-05 | N
24-08-18 | 07:30 | ZN690:PA10 | URBAN | Planned |  | 75 | 450 | 0.022278 | 5e-05 | N
24-08-18 | 09:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 5 | 315 | 0.008255 | 2.6e-05 | N
24-08-18 | 09:15 | ZN36200:PA1 | URBAN | Planned |  | 30 | 345 | 0.006832 | 2e-05 | N
24-08-18 | 09:15 | ZN36200:PA1 | URBAN | Planned |  | 45 | 345 | 0.010248 | 3e-05 | N
24-08-18 | 08:00 | ZN180:PA32 | URBAN | Planned |  | 82 | 520 | 0.028146 | 5.4e-05 | N
24-08-18 | 08:30 | ZN901:PA13 | URBAN | Planned |  | 95 | 240 | 0.01505 | 6.3e-05 | N
24-08-18 | 21:30 | ZN384:PA70 | URBAN | Planned |  | 39 | 360 | 0.009267 | 2.6e-05 | N
24-08-18 | 21:30 | ZN384:PA70 | URBAN | Planned |  | 13 | 360 | 0.003089 | 9e-06 | N
25-08-18 | 08:54 | ZN711:PA27 | URBAN | Planned |  | 2 | 566 | 0.000747 | 1e-06 | N
25-08-18 | 08:54 | ZN711:PA2 | URBAN | Planned |  | 1 | 566 | 0.000374 | 1e-06 | N
25-08-18 | 00:30 | ZN8700:PA63 64DEF | CBD | Planned |  | 30 | 1,745 | 1.7093 | 0.00098 | N
26-08-18 | 09:00 | ZN35400:PA72 | URBAN | Planned |  | 60 | 15 | 0.000594 | 4e-05 | N
26-08-18 | 07:30 | ZN2466:PA34 | URBAN | Planned |  | 1 | 280 | 0.000185 | 1e-06 | N
26-08-18 | 09:40 | ZN1287:PA21 | URBAN | Planned |  | 1 | 225 | 0.000148 | 1e-06 | N
26-08-18 | 13:00 | ZN8700:PA63 64KLM | CBD | Planned |  | 1 | 465 | 0.015183 | 3.3e-05 | N
26-08-18 | 22:30 | ZN3288:PA45 46KLM | CBD | Planned |  | 2 | 525 | 0.034283 | 6.5e-05 | N
27-08-18 | 08:10 | ZN847:PA36 | URBAN | Planned |  | 31 | 540 | 0.011047 | 2e-05 | N
27-08-18 | 08:10 | ZN847:PA36 | URBAN | Planned |  | 39 | 540 | 0.013897 | 2.6e-05 | N
27-08-18 | 07:30 | ZN15005:PA6 | URBAN | Planned |  | 34 | 480 | 0.01077 | 2.2e-05 | N
27-08-18 | 08:10 | ZN12570:PA24 | SHORT RURAL | Planned |  | 20 | 435 | 0.045585 | 0.000105 | N
27-08-18 | 08:30 | ZN1193:PA20 | SHORT RURAL | Planned |  | 1 | 120 | 0.000629 | 5e-06 | N
06-09-18 | 08:35 | 232:33407 | SHORT RURAL | Planned |  | 2 | 45 | 0.000467 | 1e-05 | N
06-09-18 | 08:05 | 509:33395 | LONG RURAL | Planned |  | 11 | 495 | 1.9146 | 0.003868 | N
06-09-18 | 08:00 | 813:89055 | SHORT RURAL | Planned |  | 38 | 405 | 0.079844 | 0.000197 | N
06-09-18 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 9 | 550 | 0.025681 | 4.7e-05 | N
07-09-18 | 08:05 | 235:2120 | SHORT RURAL | Planned |  | 2 | 235 | 0.002439 | 1e-05 | N
10-09-18 | 07:30 | 257:81999 | URBAN | Planned |  | 2 | 268 | 0.000354 | 1e-06 | N
09-09-18 | 08:05 | 232:33407 | SHORT RURAL | Planned |  | 2 | 25 | 0.000259 | 1e-05 | N
09-09-18 | 09:35 | 232:11457 | SHORT RURAL | Planned |  | 81 | 15 | 0.006305 | 0.00042 | N
10-09-18 | 08:50 | 508:82579 | SHORT RURAL | Planned |  | 4 | 41 | 0.000851 | 2.1e-05 | N
10-09-18 | 11:30 | 508:82579 | SHORT RURAL | Planned |  | 3 | 38 | 0.000592 | 1.6e-05 | N
10-09-18 | 08:30 | 235:2124 | URBAN | Planned |  | 92 | 350 | 0.021268 | 6.1e-05 | N
07-09-18 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 15 | 145 | 0.011285 | 7.8e-05 | N
07-09-18 | 08:15 | 520:48172 | SHORT RURAL | Planned |  | 18 | 330 | 0.03082 | 9.3e-05 | N
07-09-18 | 08:25 | 814:82291 | SHORT RURAL | Planned |  | 15 | 245 | 0.019068 | 7.8e-05 | N
10-09-18 | 08:10 | 515:35200 | URBAN | Planned |  | 1 | 60 | 4e-05 | 1e-06 | N
10-09-18 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 8 | 85 | 0.003529 | 4.2e-05 | N
10-09-18 | 10:00 | 515:35192 | SHORT RURAL | Planned |  | 3 | 45 | 0.000701 | 1.6e-05 | N
10-09-18 | 10:22 | 523:33501 | SHORT RURAL | Planned |  | 1 | 63 | 0.000327 | 5e-06 | N
10-09-18 | 11:40 | 515:35192 | SHORT RURAL | Planned |  | 1 | 30 | 0.000156 | 5e-06 | N
10-09-18 | 13:16 | 523:33501 | SHORT RURAL | Planned |  | 2 | 14 | 0.000145 | 1e-05 | N
11-09-18 | 08:00 | 221:11893 | URBAN | Planned |  | 4 | 465 | 0.001266 | 3e-06 | N
11-09-18 | 08:30 | 526:34641 | SHORT RURAL | Planned |  | 62 | 300 | 0.078324 | 0.000261 | N
11-09-18 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 9 | 395 | 0.01497 | 3.8e-05 | N
11-09-18 | 08:00 | 810:74050 | SHORT RURAL | Planned |  | 9 | 275 | 0.010422 | 3.8e-05 | N
12-09-18 | 08:05 | 515:35193 | SHORT RURAL | Planned |  | 7 | 315 | 0.009284 | 2.9e-05 | N
12-09-18 | 08:20 | 233:82819 | SHORT RURAL | Planned |  | 36 | 379 | 0.057446 | 0.000152 | N
12-09-18 | 08:20 | 807:74179 | SHORT RURAL | Planned |  | 2 | 65 | 0.000547 | 8e-06 | N
12-09-18 | 09:35 | 807:74179 | SHORT RURAL | Planned |  | 2 | 50 | 0.000421 | 8e-06 | N
12-09-18 | 09:30 | 806:82667 | SHORT RURAL | Planned |  | 2 | 123 | 0.001036 | 8e-06 | N
12-09-18 | 08:10 | 802:82220 | SHORT RURAL | Planned |  | 18 | 155 | 0.011747 | 7.6e-05 | N
12-09-18 | 11:00 | 802:82220 | SHORT RURAL | Planned |  | 1 | 100 | 0.000421 | 4e-06 | N
12-09-18 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 3 | 260 | 0.27436 | 0.001055 | N
12-09-18 | 10:45 | 807:74183 | SHORT RURAL | Planned |  | 2 | 50 | 0.000421 | 8e-06 | N
12-09-18 | 11:50 | 807:74183 | SHORT RURAL | Planned |  | 1 | 75 | 0.000316 | 4e-06 | N
13-09-18 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 2 | 265 | 0.18642 | 0.000703 | N
16-09-18 | 08:00 | 409:6012 | URBAN | Planned |  | 1 | 75 | 5.1e-05 | 1e-06 | N
16-09-18 | 07:30 | 417:80507 | URBAN | Planned |  | 3 | 225 | 0.000459 | 2e-06 | N
16-09-18 | 09:00 | 513:48056 | SHORT RURAL | Planned |  | 9 | 135 | 0.005116 | 3.8e-05 | N
13-09-18 | 08:00 | 205:12206 | URBAN | Planned |  | 136 | 380 | 0.035167 | 9.3e-05 | N
13-09-18 | 22:15 | 240:34849 | URBAN | Planned |  | 1 | 830 | 0.000565 | 1e-06 | N
16-09-18 | 08:05 | 256:80640 | URBAN | Planned |  | 137 | 450 | 0.041954 | 9.3e-05 | N
16-09-18 | 09:20 | 202:34240 | URBAN | Planned |  | 6 | 310 | 0.001266 | 4e-06 | N
13-09-18 | 08:15 | 232:33409 | SHORT RURAL | Planned |  | 54 | 30 | 0.006821 | 0.000227 | N
13-09-18 | 08:22 | 232:33409 | SHORT RURAL | Planned |  | 44 | 114 | 0.021119 | 0.000185 | N
13-09-18 | 09:35 | 508:82578 | SHORT RURAL | Planned |  | 1 | 243 | 0.001023 | 4e-06 | N
14-09-18 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 70 | 0.024613 | 0.000352 | N
14-09-18 | 09:11 | 508:82578 | SHORT RURAL | Planned |  | 1 | 258 | 0.001086 | 4e-06 | N
14-09-18 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 12 | 355 | 0.017936 | 5.1e-05 | N
14-09-18 | 14:00 | 232:33409 | SHORT RURAL | Planned |  | 98 | 120 | 0.049512 | 0.000413 | N
13-09-18 | 10:00 | 813:89055 | SHORT RURAL | Planned |  | 2 | 75 | 0.000632 | 8e-06 | N
13-09-18 | 08:30 | 807:74181 | SHORT RURAL | Planned |  | 39 | 390 | 0.06404 | 0.000164 | N
13-09-18 | 08:10 | 807:74184 | SHORT RURAL | Planned |  | 2 | 325 | 0.002737 | 8e-06 | N
17-09-18 | 08:43 | 807:74184 | SHORT RURAL | Planned |  | 13 | 282 | 0.015435 | 5.5e-05 | N
17-09-18 | 08:40 | 235:2124 | URBAN | Planned |  | 2 | 250 | 0.00034 | 1e-06 | N
17-09-18 | 08:00 | 523:33508 | SHORT RURAL | Planned |  | 3 | 42 | 0.00053 | 1.3e-05 | N
17-09-18 | 10:00 | 523:33501 | SHORT RURAL | Planned |  | 12 | 42 | 0.002122 | 5.1e-05 | N
17-09-18 | 13:00 | 523:33501 | SHORT RURAL | Planned |  | 15 | 65 | 0.004105 | 6.3e-05 | N
18-09-18 | 09:10 | 205:12210 | URBAN | Planned |  | 101 | 215 | 0.014787 | 6.9e-05 | N
18-09-18 | 08:30 | 213:33771 | URBAN | Planned |  | 98 | 360 | 0.024024 | 6.7e-05 | N
18-09-18 | 08:05 | 238:34141 | SHORT RURAL | Planned |  | 71 | 385 | 0.11505 | 0.000299 | N
18-09-18 | 08:05 | 233:82819 | SHORT RURAL | Planned |  | 5 | 295 | 0.006208 | 2.1e-05 | N
18-09-18 | 08:30 | 238:34144 | URBAN | Planned |  | 60 | 290 | 0.011849 | 4.1e-05 | N
18-09-18 | 09:25 | 524:33580 | SHORT RURAL | Planned |  | 7 | 235 | 0.006924 | 2.9e-05 | N
18-09-18 | 08:25 | 807:74184 | SHORT RURAL | Planned |  | 2 | 255 | 0.002147 | 8e-06 | N
19-09-18 | 09:15 | 261:81879 | URBAN | Planned |  | 101 | 245 | 0.016835 | 6.9e-05 | N
19-09-18 | 09:03 | 522:83126 | SHORT RURAL | Planned |  | 1 | 31 | 0.00013 | 4e-06 | N
19-09-18 | 10:00 | 522:83126 | SHORT RURAL | Planned |  | 7 | 29 | 0.000854 | 2.9e-05 | N
19-09-18 | 08:47 | 232:33409 | SHORT RURAL | Planned |  | 44 | 196 | 0.0363 | 0.000185 | N
19-09-18 | 08:40 | 812:19071 | SHORT RURAL | Planned |  | 4 | 92 | 0.001549 | 1.7e-05 | N
19-09-18 | 08:10 | 813:89061 | LONG RURAL | Planned |  | 12 | 265 | 1.1181 | 0.004219 | N
19-09-18 | 07:40 | 514:18156 | SHORT RURAL | Planned |  | 1 | 555 | 0.002336 | 4e-06 | N
27-08-18 | 11:00 | ZN2310:PA55 | URBAN | Planned |  | 68 | 360 | 0.016154 | 4.5e-05 | N
27-08-18 | 20:30 | ZN2602:PA36 | URBAN | Planned |  | 91 | 790 | 0.04744 | 6e-05 | N
28-08-18 | 07:00 | ZN1600:PA23ABC | CBD | Planned |  | 2 | 270 | 0.017635 | 6.5e-05 | N
28-08-18 | 08:00 | ZN9245:PA13 | URBAN | Planned |  | 1 | 330 | 0.000218 | 1e-06 | N
28-08-18 | 08:00 | ZN9118:PA17 | URBAN | Planned |  | 27 | 430 | 0.007671 | 1.8e-05 | N
28-08-18 | 08:05 | ZN12600:PA2 | SHORT RURAL | Planned |  | 4 | 490 | 0.010172 | 2.1e-05 | N
28-08-18 | 08:30 | ZN3155:PA18 | URBAN | Planned |  | 23 | 300 | 0.004559 | 1.5e-05 | N
29-08-18 | 01:00 | ZN4990:PA51 52KLM | CBD | Planned |  | 3 | 180 | 0.017635 | 9.8e-05 | N
29-08-18 | 06:30 | ZN35400:PA79 | URBAN | Planned |  | 35 | 835 | 0.019309 | 2.3e-05 | N
29-08-18 | 07:45 | ZN14891:PA12 | SHORT RURAL | Planned |  | 161 | 555 | 0.46374 | 0.000836 | N
29-08-18 | 08:00 | ZN965:PA26 | URBAN | Planned |  | 1 | 460 | 0.000304 | 1e-06 | N
29-08-18 | 08:10 | ZN12600:PA2 | SHORT RURAL | Planned |  | 7 | 425 | 0.01544 | 3.6e-05 | N
29-08-18 | 20:00 | ZN2602:PA36 | URBAN | Planned |  | 74 | 600 | 0.029335 | 4.9e-05 | N
29-08-18 | 20:40 | ZN35600:PA20 | URBAN | Planned |  | 6 | 605 | 0.002398 | 4e-06 | N
30-08-18 | 08:15 | ZN2635:PA52 | URBAN | Planned |  | 49 | 255 | 0.008256 | 3.2e-05 | N
30-08-18 | 08:15 | ZN2635:PA52 | URBAN | Planned |  | 86 | 265 | 0.015058 | 5.7e-05 | N
30-08-18 | 07:35 | ZN35370:PA2 | SHORT RURAL | Planned |  | 50 | 475 | 0.12326 | 0.000259 | N
30-08-18 | 08:20 | ZN36800:PA33 | URBAN | Planned |  | 74 | 310 | 0.015157 | 4.9e-05 | N
30-08-18 | 08:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 50 | 450 | 0.11677 | 0.000259 | N
30-08-18 | 08:00 | ZN15013:PA4 | SHORT RURAL | Planned |  | 32 | 480 | 0.079717 | 0.000166 | N
30-08-18 | 08:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 26 | 450 | 0.060722 | 0.000135 | N
30-08-18 | 08:00 | ZN3155:PA21 | URBAN | Planned |  | 36 | 420 | 0.00999 | 2.4e-05 | N
30-08-18 | 09:10 | ZN35370:PA10 | SHORT RURAL | Planned |  | 2 | 305 | 0.003166 | 1e-05 | N
30-08-18 | 21:30 | ZN35500:PA31 | URBAN | Planned |  | 1 | 300 | 0.000198 | 1e-06 | N
31-08-18 | 09:55 | ZN847:PA39 | URBAN | Planned |  | 53 | 455 | 0.015934 | 3.5e-05 | N
31-08-18 | 08:00 | ZN12640:PA13 | SHORT RURAL | Planned |  | 67 | 455 | 0.15822 | 0.000348 | N
01-09-18 | 07:44 | ZN8700:PA63 64DEF | CBD | Planned |  | 18 | 437 | 0.25691 | 0.000588 | N
01-09-18 | 07:00 | ZN262:PA42 | URBAN | Planned |  | 1 | 810 | 0.000535 | 1e-06 | N
01-09-18 | 08:00 | ZN15015:PA15 | SHORT RURAL | Planned |  | 1 | 420 | 0.00218 | 5e-06 | N
01-09-18 | 17:00 | ZN35400:PA106 | URBAN | Planned |  | 9 | 300 | 0.001784 | 6e-06 | N
02-09-18 | 20:30 | ZN10994:PA20 | URBAN | Planned |  | 50 | 420 | 0.013876 | 3.3e-05 | N
03-09-18 | 09:30 | ZN9037:PA2 | URBAN | Planned |  | 80 | 305 | 0.016122 | 5.3e-05 | N
04-09-18 | 08:30 | ZN10991:PA13 | URBAN | Planned |  | 2 | 300 | 0.000396 | 1e-06 | N
04-09-18 | 10:10 | ZN195:PA10 | URBAN | Planned |  | 34 | 100 | 0.002247 | 2.2e-05 | N
05-09-18 | 08:20 | ZN3154:PA10 | URBAN | Planned |  | 40 | 430 | 0.011366 | 2.6e-05 | N
05-09-18 | 08:10 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 470 | 0.021956 | 4.7e-05 | N
05-09-18 | 09:20 | ZN9900:PA2 | URBAN | Planned |  | 31 | 330 | 0.00676 | 2e-05 | N
05-09-18 | 20:00 | ZN180:PA7 | URBAN | Planned |  | 7 | 270 | 0.001249 | 5e-06 | N
06-09-18 | 08:20 | ZN874:PA17 | URBAN | Planned |  | 72 | 190 | 0.009042 | 4.8e-05 | N
06-09-18 | 08:18 | ZN35500:PA27 | URBAN | Planned |  | 20 | 342 | 0.004521 | 1.3e-05 | N
06-09-18 | 08:00 | ZN2466:PA45 | URBAN | Planned |  | 48 | 255 | 0.00809 | 3.2e-05 | N
06-09-18 | 22:05 | ZN3155:PA18 | URBAN | Planned |  | 1 | 190 | 0.000126 | 1e-06 | N
07-09-18 | 10:30 | ZN35800:PA1 | URBAN | Planned |  | 38 | 480 | 0.01205 | 2.5e-05 | N
07-09-18 | 08:30 | ZN3155:PA17 | URBAN | Planned |  | 103 | 180 | 0.012248 | 6.8e-05 | N
08-09-18 | 07:30 | ZN35700:PA1 | URBAN | Planned |  | 1 | 345 | 0.000228 | 1e-06 | N
08-09-18 | 08:47 | ZN3155:PA21 | URBAN | Planned |  | 36 | 285 | 0.006777 | 2.4e-05 | N
09-09-18 | 00:01 | ZN4990:PA51 52KLM | CBD | Planned |  | 21 | 359 | 0.24628 | 0.000686 | N
09-09-18 | 08:15 | ZN1285:PA27 | URBAN | Planned |  | 7 | 495 | 0.002289 | 5e-06 | N
09-09-18 | 08:00 | ZN8700:PA61 62KLM | CBD | Planned |  | 5 | 420 | 0.068601 | 0.000163 | N
09-09-18 | 09:50 | ZN35900:PA22 | URBAN | Planned |  | 1 | 330 | 0.000218 | 1e-06 | N
09-09-18 | 16:30 | ZN1600:PA22ABC | CBD | Planned |  | 5 | 780 | 0.1274 | 0.000163 | N
09-09-18 | 21:50 | ZN7900:PA16 | URBAN | Planned |  | 22 | 400 | 0.005812 | 1.5e-05 | N
09-09-18 | 22:30 | ZN263:PA35 37ABC | CBD | Planned |  | 1 | 200 | 0.006533 | 3.3e-05 | N
10-09-18 | 02:10 | ZN4990:PA51 52KLM | CBD | Planned |  | 95 | 140 | 0.43447 | 0.003103 | N
10-09-18 | 07:00 | ZN35900:PA24 | URBAN | Planned |  | 94 | 334 | 0.020737 | 6.2e-05 | N
10-09-18 | 08:45 | ZN12630:PA6 | SHORT RURAL | Planned |  | 6 | 225 | 0.007005 | 3.1e-05 | N
10-09-18 | 08:00 | ZN36100:PA16 | URBAN | Planned |  | 92 | 120 | 0.007292 | 6.1e-05 | N
10-09-18 | 08:05 | ZN14144:PA8 | URBAN | Planned |  | 40 | 405 | 0.0107 | 2.6e-05 | N
11-09-18 | 07:30 | ZN35500:PA27 | URBAN | Planned |  | 5 | 480 | 0.001634 | 3e-06 | N
11-09-18 | 08:05 | ZN262:PA7 | URBAN | Planned |  | 64 | 403 | 0.017559 | 4.4e-05 | N
11-09-18 | 08:05 | ZN2400:PA11 | SHORT RURAL | Planned |  | 43 | 445 | 0.080577 | 0.000181 | N
11-09-18 | 08:00 | ZN15008:PA7 | URBAN | Planned |  | 84 | 490 | 0.028021 | 5.7e-05 | N
11-09-18 | 08:26 | ZN12650:PA12 | URBAN | Planned |  | 54 | 429 | 0.015771 | 3.7e-05 | N
11-09-18 | 09:25 | ZN8700:PA65 66ABC | CBD | Planned |  | 51 | 355 | 0.59147 | 0.001666 | N
11-09-18 | 10:00 | ZN9118:PA26 | URBAN | Planned |  | 25 | 360 | 0.006127 | 1.7e-05 | N
11-09-18 | 22:00 | ZN2602:PA42 | URBAN | Planned |  | 68 | 134 | 0.006203 | 4.6e-05 | N
12-09-18 | 07:25 | ZN12630:PA3 | SHORT RURAL | Planned |  | 6 | 505 | 0.012757 | 2.5e-05 | N
12-09-18 | 08:10 | ZN15014:PA5 | URBAN | Planned |  | 18 | 540 | 0.006624 | 1.2e-05 | N
12-09-18 | 07:30 | ZN35500:PA27 | URBAN | Planned |  | 25 | 480 | 0.008178 | 1.7e-05 | N
12-09-18 | 08:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 36 | 330 | 0.050019 | 0.000152 | N
12-09-18 | 08:17 | ZN12630:PA8 | SHORT RURAL | Planned |  | 68 | 423 | 0.12111 | 0.000286 | N
12-09-18 | 20:00 | ZN262:PA39 | URBAN | Planned |  | 41 | 480 | 0.013411 | 2.8e-05 | N
12-09-18 | 08:00 | ZN180:PA41 | URBAN | Planned |  | 31 | 450 | 0.009507 | 2.1e-05 | N
12-09-18 | 21:20 | ZN3288:PA43 44ABC | CBD | Planned |  | 25 | 400 | 0.32665 | 0.000817 | N
13-09-18 | 06:30 | ZN262:PA7 | URBAN | Planned |  | 1 | 240 | 0.000163 | 1e-06 | N
13-09-18 | 07:10 | ZN14143:PA17 | SHORT RURAL | Planned |  | 12 | 470 | 0.023747 | 5.1e-05 | N
13-09-18 | 07:30 | ZN2835:PA9 | URBAN | Planned |  | 22 | 600 | 0.008982 | 1.5e-05 | N
13-09-18 | 08:05 | ZN35370:PA2 | SHORT RURAL | Planned |  | 21 | 415 | 0.036694 | 8.8e-05 | N
13-09-18 | 08:00 | ZN180:PA41 | URBAN | Planned |  | 31 | 450 | 0.009493 | 2.1e-05 | N
13-09-18 | 08:50 | ZN14891:PA12 | SHORT RURAL | Planned |  | 6 | 170 | 0.004295 | 2.5e-05 | N
13-09-18 | 08:07 | ZN14891:PA5 | SHORT RURAL | Planned |  | 2 | 443 | 0.00373 | 8e-06 | N
13-09-18 | 08:05 | ZN12570:PA24 | SHORT RURAL | Planned |  | 104 | 455 | 0.19924 | 0.000438 | N
13-09-18 | 10:31 | ZN262:PA5 | URBAN | Planned |  | 1 | 299 | 0.000203 | 1e-06 | N
13-09-18 | 23:00 | ZN1193:PA26 | URBAN | Planned |  | 32 | 180 | 0.003919 | 2.2e-05 | N
14-09-18 | 07:30 | ZN2635:PA39 | URBAN | Planned |  | 66 | 390 | 0.017528 | 4.5e-05 | N
14-09-18 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 4 | 460 | 0.007747 | 1.7e-05 | N
14-09-18 | 09:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 1 | 300 | 0.001263 | 4e-06 | N
23-09-18 | 11:02 | ZN3155:PA35 | URBAN | Planned |  | 1 | 10 | 7e-06 | 1e-06 | N
20-09-18 | 08:40 | 810:74058 | SHORT RURAL | Planned |  | 8 | 305 | 0.01027 | 3.4e-05 | N
20-09-18 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 15 | 450 | 0.028412 | 6.3e-05 | N
23-09-18 | 07:30 | 409:6012 | URBAN | Planned |  | 1 | 106 | 7.2e-05 | 1e-06 | N
23-09-18 | 08:02 | 205:12206 | URBAN | Planned |  | 1 | 538 | 0.000366 | 1e-06 | N
23-09-18 | 08:02 | 256:80640 | URBAN | Planned |  | 137 | 538 | 0.050148 | 9.3e-05 | N
23-09-18 | 08:00 | 213:33773 | URBAN | Planned |  | 1 | 670 | 0.000456 | 1e-06 | N
20-09-18 | 10:45 | 508:82579 | SHORT RURAL | Planned |  | 2 | 40 | 0.000337 | 8e-06 | N
21-09-18 | 08:30 | 512:83732 | SHORT RURAL | Planned |  | 47 | 465 | 0.091995 | 0.000198 | N
21-09-18 | 08:30 | 232:11455 | SHORT RURAL | Planned |  | 1 | 46 | 0.000194 | 4e-06 | N
21-09-18 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 2 | 240 | 0.16878 | 0.000703 | N
20-09-18 | 08:30 | 516:48066 | SHORT RURAL | Planned |  | 4 | 81 | 0.001364 | 1.7e-05 | N
20-09-18 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 45 | 310 | 0.058718 | 0.000189 | N
20-09-18 | 13:00 | 516:48067 | SHORT RURAL | Planned |  | 3 | 50 | 0.000631 | 1.3e-05 | N
21-09-18 | 08:05 | 516:48067 | SHORT RURAL | Planned |  | 23 | 181 | 0.017524 | 9.7e-05 | N
21-09-18 | 08:35 | 813:89055 | SHORT RURAL | Planned |  | 38 | 210 | 0.033591 | 0.00016 | N
17-09-18 | 07:30 | 507:80914 | SHORT RURAL | Planned |  | 1 | 5,970 | 0.025135 | 4e-06 | N
24-09-18 | 10:00 | 258:80793 | URBAN | Planned |  | 153 | 11 | 0.001145 | 0.000104 | N
24-09-18 | 08:30 | 522:83123 | SHORT RURAL | Planned |  | 11 | 150 | 0.006946 | 4.6e-05 | N
24-09-18 | 08:30 | 242:81539 | URBAN | Planned |  | 44 | 405 | 0.012124 | 3e-05 | N
24-09-18 | 09:00 | 810:74050 | SHORT RURAL | Planned |  | 2 | 50 | 0.000421 | 8e-06 | N
24-09-18 | 10:10 | 810:74050 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
24-09-18 | 09:05 | 810:74050 | SHORT RURAL | Planned |  | 3 | 60 | 0.000758 | 1.3e-05 | N
24-09-18 | 10:25 | 810:74050 | SHORT RURAL | Planned |  | 2 | 55 | 0.000463 | 8e-06 | N
25-09-18 | 08:00 | 522:83132 | SHORT RURAL | Planned |  | 21 | 215 | 0.018999 | 8.8e-05 | N
25-09-18 | 09:20 | 214:8667 | URBAN | Planned |  | 37 | 390 | 0.009816 | 2.5e-05 | N
25-09-18 | 08:30 | 507:80914 | SHORT RURAL | Planned |  | 139 | 460 | 0.26905 | 0.000585 | N
25-09-18 | 08:30 | 512:83743 | SHORT RURAL | Planned |  | 3 | 47 | 0.000593 | 1.3e-05 | N
25-09-18 | 08:05 | 523:33501 | SHORT RURAL | Planned |  | 14 | 260 | 0.015317 | 5.9e-05 | N
25-09-18 | 08:10 | 515:35192 | SHORT RURAL | Planned |  | 14 | 380 | 0.022386 | 5.9e-05 | N
14-09-18 | 23:40 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 195 | 0.007389 | 3.8e-05 | N
15-09-18 | 01:00 | ZN12690:PA16 | SHORT RURAL | Planned |  | 42 | 360 | 0.063659 | 0.000177 | N
16-09-18 | 23:00 | ZN12690:PA16 | SHORT RURAL | Planned |  | 42 | 300 | 0.05305 | 0.000177 | N
16-09-18 | 00:15 | ZN1600:PA23ABC | CBD | Planned |  | 39 | 435 | 0.55416 | 0.001274 | N
16-09-18 | 02:00 | ZN263:PA31 32ABC | CBD | Planned |  | 69 | 470 | 1.0593 | 0.002254 | N
16-09-18 | 05:00 | ZN931:PA18 | URBAN | Planned |  | 57 | 15 | 0.000582 | 3.9e-05 | N
16-09-18 | 09:23 | ZN340:PA11 | URBAN | Planned |  | 2 | 291 | 0.000396 | 1e-06 | N
17-09-18 | 09:55 | ZN36100:PA16 | URBAN | Planned |  | 92 | 155 | 0.009704 | 6.3e-05 | N
17-09-18 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 27 | 460 | 0.052292 | 0.000114 | N
17-09-18 | 10:30 | ZN167:PA10 | URBAN | Planned |  | 127 | 200 | 0.017285 | 8.6e-05 | N
18-09-18 | 02:05 | ZN4990:PA51 52ABC | CBD | Planned |  | 10 | 275 | 0.089784 | 0.000326 | N
18-09-18 | 08:30 | ZN10991:PA6 | URBAN | Planned |  | 8 | 360 | 0.001961 | 5e-06 | N
18-09-18 | 09:00 | ZN874:PA17 | URBAN | Planned |  | 28 | 495 | 0.009438 | 1.9e-05 | N
18-09-18 | 08:45 | ZN80:PA30 | URBAN | Planned |  | 37 | 130 | 0.003275 | 2.5e-05 | N
18-09-18 | 11:00 | ZN80:PA30 | URBAN | Planned |  | 44 | 110 | 0.003296 | 3e-05 | N
18-09-18 | 08:00 | ZN35500:PA28 | URBAN | Planned |  | 49 | 480 | 0.016016 | 3.3e-05 | N
18-09-18 | 08:15 | ZN12690:PA24 | SHORT RURAL | Planned |  | 4 | 430 | 0.00724 | 1.7e-05 | N
18-09-18 | 08:00 | ZN9118:PA17 | URBAN | Planned |  | 52 | 450 | 0.015934 | 3.5e-05 | N
19-09-18 | 00:30 | ZN3288:PA43 44ABC | CBD | Planned |  | 18 | 225 | 0.13223 | 0.000588 | N
19-09-18 | 08:10 | ZN15008:PA7 | URBAN | Planned |  | 8 | 208 | 0.001132 | 5e-06 | N
19-09-18 | 08:10 | ZN12600:PA1 | SHORT RURAL | Planned |  | 77 | 245 | 0.079407 | 0.000324 | N
19-09-18 | 07:30 | ZN3425:PA43 | URBAN | Planned |  | 94 | 480 | 0.030697 | 6.4e-05 | N
19-09-18 | 07:30 | ZN35370:PA4 | SHORT RURAL | Planned |  | 18 | 415 | 0.031443 | 7.6e-05 | N
19-09-18 | 08:10 | ZN9118:PA3 | SHORT RURAL | Planned |  | 200 | 260 | 0.21888 | 0.000842 | N
19-09-18 | 08:10 | ZN12690:PA16 | SHORT RURAL | Planned |  | 10 | 445 | 0.018731 | 4.2e-05 | N
19-09-18 | 08:00 | ZN14143:PA12 | SHORT RURAL | Planned |  | 28 | 300 | 0.035357 | 0.000118 | N
26-09-18 | 08:35 | 242:81541 | URBAN | Planned |  | 1 | 75 | 5.1e-05 | 1e-06 | N
26-09-18 | 08:58 | 520:48172 | SHORT RURAL | Planned |  | 1 | 112 | 0.000471 | 4e-06 | N
26-09-18 | 09:25 | 513:48056 | SHORT RURAL | Planned |  | 3 | 155 | 0.001957 | 1.3e-05 | N
26-09-18 | 13:26 | 520:48172 | SHORT RURAL | Planned |  | 1 | 34 | 0.000143 | 4e-06 | N
26-09-18 | 08:20 | 513:48056 | SHORT RURAL | Planned |  | 25 | 415 | 0.043657 | 0.000105 | N
20-09-18 | 00:05 | ZN3288:PA41 42DEF | CBD | Planned |  | 15 | 175 | 0.085706 | 0.00049 | N
20-09-18 | 09:30 | ZN1788:PA16 | URBAN | Planned |  | 45 | 375 | 0.011504 | 3.1e-05 | N
20-09-18 | 07:35 | ZN3154:PA10 | URBAN | Planned |  | 32 | 235 | 0.005127 | 2.2e-05 | N
20-09-18 | 07:30 | ZN3425:PA15 | URBAN | Planned |  | 61 | 220 | 0.009149 | 4.2e-05 | N
20-09-18 | 07:30 | ZN3425:PA43 | URBAN | Planned |  | 56 | 435 | 0.016607 | 3.8e-05 | N
20-09-18 | 07:30 | ZN188:PA17 | URBAN | Planned |  | 98 | 360 | 0.024052 | 6.7e-05 | N
20-09-18 | 08:00 | ZN12630:PA11 | SHORT RURAL | Planned |  | 5 | 530 | 0.011154 | 2.1e-05 | N
20-09-18 | 11:10 | ZN36100:PA19 | URBAN | Planned |  | 87 | 125 | 0.007414 | 5.9e-05 | N
21-09-18 | 09:30 | ZN630:PA32 | URBAN | Planned |  | 1 | 1,770 | 0.001204 | 1e-06 | N
22-09-18 | 17:00 | ZN8700:PA65 66ABC | CBD | Planned |  | 56 | 240 | 0.43884 | 0.001829 | N
27-09-18 | 08:30 | 526:34633 | SHORT RURAL | Planned |  | 7 | 480 | 0.014139 | 2.9e-05 | N
27-09-18 | 08:20 | 229:34995 | SHORT RURAL | Planned |  | 61 | 280 | 0.071873 | 0.000257 | N
27-09-18 | 08:00 | 528:83011 | SHORT RURAL | Planned |  | 2 | 240 | 0.00202 | 8e-06 | N
28-09-18 | 08:00 | 523:33508 | SHORT RURAL | Planned |  | 15 | 300 | 0.018936 | 6.3e-05 | N
01-10-18 | 02:40 | 222:33602 | URBAN | Planned |  | 83 | 20 | 0.001129 | 5.6e-05 | N
02-10-18 | 02:50 | 222:33602 | URBAN | Planned |  | 83 | 20 | 0.001129 | 5.6e-05 | N
27-09-18 | 08:45 | 509:33395 | LONG RURAL | Planned |  | 4 | 335 | 0.471 | 0.001406 | N
28-09-18 | 08:00 | 509:33399 | SHORT RURAL | Planned |  | 22 | 400 | 0.03703 | 9.3e-05 | N
27-09-18 | 08:36 | 514:18137 | SHORT RURAL | Planned |  | 2 | 59 | 0.000497 | 8e-06 | N
27-09-18 | 08:25 | 813:89061 | LONG RURAL | Planned |  | 5 | 380 | 0.66784 | 0.001757 | N
28-09-18 | 10:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 30 | 0.010545 | 0.000351 | N
28-09-18 | 08:10 | 814:82291 | SHORT RURAL | Planned |  | 6 | 335 | 0.008458 | 2.5e-05 | N
02-10-18 | 17:00 | 532:83298 | SHORT RURAL | Planned |  | 2 | 270 | 0.002272 | 8e-06 | N
02-10-18 | 08:35 | 813:89061 | LONG RURAL | Planned |  | 9 | 195 | 0.61644 | 0.003161 | N
02-10-18 | 12:00 | 814:82285 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
02-10-18 | 13:12 | 515:35197 | LONG RURAL | Planned |  | 1 | 23 | 0.008079 | 0.000351 | N
11-09-18 | 09:30 | ZN262:PA7 | URBAN | Planned |  | 48 | 8,700 | 0.2843 | 3.3e-05 | N
17-09-18 | 16:20 | ZN12610:PA2 | URBAN | Planned |  | 108 | 5,200 | 0.38218 | 7.3e-05 | N
21-09-18 | 07:00 | ZN398:PA25 | URBAN | Planned |  | 1 | 225 | 0.000153 | 1e-06 | N
21-09-18 | 09:45 | ZN398:PA25 | URBAN | Planned |  | 1 | 255 | 0.000173 | 1e-06 | N
21-09-18 | 08:10 | ZN12570:PA22 | SHORT RURAL | Planned |  | 1 | 400 | 0.001684 | 4e-06 | N
21-09-18 | 11:05 | ZN2466:PA41 | URBAN | Planned |  | 32 | 115 | 0.002504 | 2.2e-05 | N
21-09-18 | 22:15 | ZN874:PA9 | URBAN | Planned |  | 1 | 2,250 | 0.001531 | 1e-06 | N
21-09-18 | 22:30 | ZN874:PA9 | URBAN | Planned |  | 2 | 2,235 | 0.003041 | 1e-06 | N
23-09-18 | 01:51 | ZN263:PA31 32ABC | CBD | Planned |  | 34 | 429 | 0.47626 | 0.00111 | N
22-09-18 | 08:30 | ZN8700:PA61 62KLM | CBD | Planned |  | 23 | 1,530 | 1.149 | 0.000751 | N
23-09-18 | 08:04 | ZN14891:PA3 | SHORT RURAL | Planned |  | 16 | 536 | 0.0361 | 6.7e-05 | N
23-09-18 | 07:50 | ZN35700:PA10 | URBAN | Planned |  | 20 | 310 | 0.004218 | 1.4e-05 | N
23-09-18 | 09:30 | ZN3155:PA44 | URBAN | Planned |  | 139 | 390 | 0.036883 | 9.5e-05 | N
23-09-18 | 09:00 | ZN3155:PA29 | URBAN | Planned |  | 32 | 420 | 0.009144 | 2.2e-05 | N
23-09-18 | 22:00 | ZN2310:PA55 | URBAN | Planned |  | 38 | 420 | 0.010859 | 2.6e-05 | N
24-09-18 | 08:30 | ZN35500:PA27 | URBAN | Planned |  | 63 | 345 | 0.014788 | 4.3e-05 | N
24-09-18 | 09:15 | ZN3425:PA15 | URBAN | Planned |  | 48 | 260 | 0.008491 | 3.3e-05 | N
24-09-18 | 08:30 | ZN10999:PA24 | URBAN | Planned |  | 45 | 300 | 0.009185 | 3.1e-05 | N
24-09-18 | 09:00 | ZN9900:PA8 | URBAN | Planned |  | 36 | 300 | 0.007348 | 2.4e-05 | N
24-09-18 | 20:30 | ZN8700:PA67 68ABC | CBD | Planned |  | 1 | 712 | 0.023248 | 3.3e-05 | N
25-09-18 | 07:30 | ZN3425:PA15 | URBAN | Planned |  | 39 | 435 | 0.011541 | 2.7e-05 | N
25-09-18 | 08:00 | ZN36100:PA16 | URBAN | Planned |  | 92 | 480 | 0.03004 | 6.3e-05 | N
25-09-18 | 08:20 | ZN12580:PA12 | SHORT RURAL | Planned |  | 11 | 415 | 0.019209 | 4.6e-05 | N
25-09-18 | 08:20 | ZN12580:PA12 | SHORT RURAL | Planned |  | 13 | 415 | 0.022702 | 5.5e-05 | N
25-09-18 | 08:15 | ZN14143:PA12 | SHORT RURAL | Planned |  | 1 | 180 | 0.000757 | 4e-06 | N
25-09-18 | 08:15 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 405 | 0.015338 | 3.8e-05 | N
25-09-18 | 08:15 | ZN12690:PA24 | SHORT RURAL | Planned |  | 3 | 405 | 0.005113 | 1.3e-05 | N
25-09-18 | 08:30 | ZN10990:PA8 | URBAN | Planned |  | 68 | 540 | 0.024979 | 4.6e-05 | N
25-09-18 | 08:30 | ZN15008:PA1 | URBAN | Planned |  | 59 | 420 | 0.016857 | 4e-05 | N
03-10-18 | 08:05 | 243:80083 | SHORT RURAL | Planned |  | 143 | 678 | 0.40787 | 0.000602 | N
03-10-18 | 08:20 | 507:80923 | SHORT RURAL | Planned |  | 1 | 180 | 0.000757 | 4e-06 | N
03-10-18 | 09:00 | 528:83019 | SHORT RURAL | Planned |  | 3 | 520 | 0.006563 | 1.3e-05 | N
03-10-18 | 08:20 | 807:74184 | SHORT RURAL | Planned |  | 6 | 305 | 0.007699 | 2.5e-05 | N
03-10-18 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 2 | 360 | 0.2529 | 0.000702 | N
26-09-18 | 00:10 | ZN188:PA41 | URBAN | Planned |  | 2 | 5 | 7e-06 | 1e-06 | N
26-09-18 | 08:30 | ZN10999:PA7 | URBAN | Planned |  | 44 | 380 | 0.011374 | 3e-05 | N
26-09-18 | 07:30 | ZN35600:PA14 | URBAN | Planned |  | 22 | 570 | 0.008531 | 1.5e-05 | N
26-09-18 | 08:00 | ZN1193:PA28 | URBAN | Planned |  | 70 | 420 | 0.02 | 4.8e-05 | N
26-09-18 | 08:00 | ZN180:PA34 | URBAN | Planned |  | 19 | 420 | 0.005429 | 1.3e-05 | N
26-09-18 | 08:00 | ZN9534:PA17 | URBAN | Planned |  | 116 | 480 | 0.037877 | 7.9e-05 | N
26-09-18 | 08:15 | ZN36200:PA8 | SHORT RURAL | Planned |  | 53 | 340 | 0.075826 | 0.000223 | N
26-09-18 | 08:45 | ZN14143:PA5 | URBAN | Planned |  | 85 | 435 | 0.025153 | 5.8e-05 | N
26-09-18 | 08:00 | ZN15008:PA1 | URBAN | Planned |  | 93 | 420 | 0.026571 | 6.3e-05 | N
26-09-18 | 10:50 | ZN36000:PA12 | URBAN | Planned |  | 2 | 518 | 0.000705 | 1e-06 | N
27-09-18 | 08:25 | ZN15008:PA1 | URBAN | Planned |  | 76 | 245 | 0.012667 | 5.2e-05 | N
27-09-18 | 08:02 | ZN12610:PA11 | URBAN | Planned |  | 83 | 508 | 0.028683 | 5.6e-05 | N
27-09-18 | 10:00 | ZN36000:PA12 | URBAN | Planned |  | 2 | 555 | 0.000755 | 1e-06 | N
26-09-18 | 20:30 | ZN9700:PA11 | URBAN | Planned |  | 67 | 570 | 0.025979 | 4.6e-05 | N
13-09-18 | 06:30 | ZN35600:PA14 | URBAN | Planned |  | 22 | 570 | 0.008533 | 1.5e-05 | N
04-10-18 | 08:00 | 524:33578 | URBAN | Planned |  | 157 | 345 | 0.036841 | 0.000107 | N
04-10-18 | 08:00 | 532:83298 | SHORT RURAL | Planned |  | 4 | 397 | 0.006681 | 1.7e-05 | N
04-10-18 | 08:10 | 813:89062 | SHORT RURAL | Planned |  | 75 | 395 | 0.12463 | 0.000316 | N
05-10-18 | 09:30 | 810:74054 | LONG RURAL | Planned |  | 18 | 118 | 0.74605 | 0.006322 | N
07-10-18 | 08:50 | 204:82689 | URBAN | Planned |  | 183 | 490 | 0.060991 | 0.000124 | N
07-10-18 | 08:10 | 205:12206 | URBAN | Planned |  | 175 | 515 | 0.0613 | 0.000119 | N
05-10-18 | 09:00 | 814:82283 | SHORT RURAL | Planned |  | 3 | 35 | 0.000442 | 1.3e-05 | N
05-10-18 | 13:10 | 512:83743 | SHORT RURAL | Planned |  | 4 | 25 | 0.000421 | 1.7e-05 | N
04-10-18 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 225 | 435 | 0.41176 | 0.000947 | N
04-10-18 | 08:00 | 806:82667 | SHORT RURAL | Planned |  | 40 | 435 | 0.073202 | 0.000168 | N
08-10-18 | 13:00 | 526:34637 | SHORT RURAL | Planned |  | 1 | 38 | 0.00016 | 4e-06 | N
08-10-18 | 08:00 | 261:81870 | URBAN | Planned |  | 351 | 420 | 0.10027 | 0.000239 | N
08-10-18 | 08:55 | 256:80646 | URBAN | Planned |  | 124 | 375 | 0.031628 | 8.4e-05 | N
08-10-18 | 09:08 | 256:80646 | URBAN | Planned |  | 178 | 87 | 0.010533 | 0.000121 | N
08-10-18 | 09:00 | 513:48059 | SHORT RURAL | Planned |  | 2 | 60 | 0.000505 | 8e-06 | N
08-10-18 | 08:55 | 813:89061 | LONG RURAL | Planned |  | 1 | 365 | 0.12821 | 0.000351 | N
08-10-18 | 10:00 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015806 | 0.000351 | N
08-10-18 | 11:40 | 813:89061 | LONG RURAL | Planned |  | 1 | 35 | 0.012294 | 0.000351 | N
10-10-18 | 07:35 | ZN2400:PA21 | URBAN | Planned |  | 148 | 505 | 0.050837 | 0.000101 | N
09-10-18 | 09:30 | 508:82579 | SHORT RURAL | Planned |  | 1 | 63 | 0.000265 | 4e-06 | N
09-10-18 | 11:10 | 508:82579 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
09-10-18 | 13:10 | 508:82579 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
09-10-18 | 08:20 | 516:48067 | SHORT RURAL | Planned |  | 30 | 375 | 0.047329 | 0.000126 | N
10-10-18 | 11:00 | ZN711:PA22 | SHORT RURAL | Planned |  | 232 | 140 | 0.13665 | 0.000976 | N
10-10-18 | 08:15 | 509:33395 | LONG RURAL | Planned |  | 751 | 460 | 121.3418 | 0.26379 | N
10-10-18 | 09:50 | 806:82662 | SHORT RURAL | Planned |  | 4 | 250 | 0.004207 | 1.7e-05 | N
10-10-18 | 11:25 | 806:82662 | SHORT RURAL | Planned |  | 140 | 278 | 0.16374 | 0.000589 | N
11-10-18 | 08:02 | 202:34245 | URBAN | Planned |  | 2 | 145 | 0.000197 | 1e-06 | N
11-10-18 | 08:35 | 258:80781 | URBAN | Planned |  | 70 | 425 | 0.020236 | 4.8e-05 | N
13-10-18 | 08:35 | 202:34261 | URBAN | Planned |  | 30 | 680 | 0.013876 | 2e-05 | N
13-10-18 | 08:35 | 202:34249 | URBAN | Planned |  | 1 | 680 | 0.000463 | 1e-06 | N
11-10-18 | 08:30 | 233:82812 | SHORT RURAL | Planned |  | 69 | 355 | 0.10305 | 0.00029 | N
12-10-18 | 08:40 | 522:83126 | SHORT RURAL | Planned |  | 15 | 180 | 0.011344 | 6.3e-05 | N
12-10-18 | 08:30 | 233:82819 | SHORT RURAL | Planned |  | 46 | 390 | 0.075378 | 0.000193 | N
14-10-18 | 09:00 | 526:34639 | SHORT RURAL | Planned |  | 2 | 30 | 0.000252 | 8e-06 | N
15-10-18 | 08:35 | 229:34983 | SHORT RURAL | Planned |  | 31 | 380 | 0.049481 | 0.00013 | N
15-10-18 | 08:50 | 217:33610 | URBAN | Planned |  | 94 | 485 | 0.031027 | 6.4e-05 | N
15-10-18 | 19:00 | 205:12210 | URBAN | Planned |  | 17 | 65 | 0.000752 | 1.2e-05 | N
16-10-18 | 08:00 | ZN2400:PA21 | URBAN | Planned |  | 150 | 990 | 0.10106 | 0.000102 | N
17-10-18 | 08:30 | 513:48050 | SHORT RURAL | Planned |  | 5 | 185 | 0.003886 | 2.1e-05 | N
17-10-18 | 10:00 | 515:35197 | LONG RURAL | Planned |  | 1 | 80 | 0.0281 | 0.000351 | N
16-10-18 | 08:05 | 812:19072 | SHORT RURAL | Planned |  | 2 | 230 | 0.001932 | 8e-06 | N
16-10-18 | 08:10 | 523:33508 | SHORT RURAL | Planned |  | 21 | 325 | 0.028668 | 8.8e-05 | N
16-10-18 | 08:20 | 801:74121 | LONG RURAL | Planned |  | 7 | 500 | 1.2294 | 0.002459 | N
16-10-18 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 3 | 73 | 0.00092 | 1.3e-05 | N
16-10-18 | 08:45 | 801:74123 | SHORT RURAL | Planned |  | 1 | 115 | 0.000483 | 4e-06 | N
16-10-18 | 11:10 | 801:74123 | SHORT RURAL | Planned |  | 1 | 55 | 0.000231 | 4e-06 | N
16-10-18 | 08:30 | 235:2120 | SHORT RURAL | Planned |  | 2 | 210 | 0.001764 | 8e-06 | N
17-10-18 | 08:00 | 238:34141 | SHORT RURAL | Planned |  | 15 | 450 | 0.028354 | 6.3e-05 | N
16-10-18 | 09:20 | 202:34259 | URBAN | Planned |  | 134 | 440 | 0.040126 | 9.1e-05 | N
19-10-18 | 11:15 | 813:89062 | SHORT RURAL | Planned |  | 5 | 140 | 0.00294 | 2.1e-05 | N
18-10-18 | 08:38 | 261:81870 | URBAN | Planned |  | 98 | 427 | 0.028479 | 6.7e-05 | N
20-10-18 | 08:45 | 238:34150 | SHORT RURAL | Planned |  | 4 | 365 | 0.006133 | 1.7e-05 | N
20-10-18 | 08:00 | 240:34843 | URBAN | Planned |  | 13 | 465 | 0.004114 | 9e-06 | N
19-10-18 | 08:00 | 238:34141 | SHORT RURAL | Planned |  | 14 | 575 | 0.033815 | 5.9e-05 | N
18-10-18 | 09:20 | 515:35197 | LONG RURAL | Planned |  | 1 | 72 | 0.02529 | 0.000351 | N
18-10-18 | 12:30 | 515:35197 | LONG RURAL | Planned |  | 1 | 70 | 0.024587 | 0.000351 | N
19-10-18 | 08:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 60 | 0.021112 | 0.000352 | N
19-10-18 | 10:15 | 801:74121 | LONG RURAL | Planned |  | 1 | 40 | 0.014075 | 0.000352 | N
19-10-18 | 09:00 | 806:82667 | SHORT RURAL | Planned |  | 2 | 110 | 0.000924 | 8e-06 | N
19-10-18 | 11:20 | 801:74121 | LONG RURAL | Planned |  | 4 | 45 | 0.063336 | 0.001407 | N
21-10-18 | 08:04 | 812:19065 | SHORT RURAL | Planned |  | 2 | 436 | 0.003663 | 8e-06 | N
22-10-18 | 07:30 | 258:80781 | URBAN | Planned |  | 4 | 490 | 0.001334 | 3e-06 | N
23-10-18 | 09:15 | 811:74234 | SHORT RURAL | Planned |  | 14 | 280 | 0.016466 | 5.9e-05 | N
23-10-18 | 10:33 | 520:48172 | SHORT RURAL | Planned |  | 8 | 143 | 0.004805 | 3.4e-05 | N
23-10-18 | 08:30 | 232:11455 | SHORT RURAL | Planned |  | 199 | 460 | 0.38452 | 0.000836 | N
23-10-18 | 08:25 | 243:80083 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
23-10-18 | 08:59 | 227:13015 | SHORT RURAL | Planned |  | 1 | 386 | 0.001621 | 4e-06 | N
23-10-18 | 10:00 | 243:80083 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
23-10-18 | 08:00 | 243:80083 | SHORT RURAL | Planned |  | 31 | 440 | 0.057296 | 0.00013 | N
23-10-18 | 11:20 | 243:80083 | SHORT RURAL | Planned |  | 1 | 55 | 0.000231 | 4e-06 | N
23-10-18 | 13:15 | 243:80083 | SHORT RURAL | Planned |  | 2 | 75 | 0.00063 | 8e-06 | N
23-10-18 | 08:30 | 238:34137 | SHORT RURAL | Planned |  | 44 | 100 | 0.018483 | 0.000185 | N
23-10-18 | 08:30 | 238:34147 | URBAN | Planned |  | 60 | 100 | 0.004084 | 4.1e-05 | N
23-10-18 | 12:00 | 238:34137 | SHORT RURAL | Planned |  | 85 | 50 | 0.017853 | 0.000357 | N
23-10-18 | 08:06 | 516:48066 | SHORT RURAL | Planned |  | 23 | 434 | 0.04193 | 9.7e-05 | N
23-10-18 | 08:40 | 523:33507 | URBAN | Planned |  | 23 | 275 | 0.004305 | 1.6e-05 | N
24-10-18 | 08:00 | 205:12210 | URBAN | Planned |  | 97 | 420 | 0.027728 | 6.6e-05 | N
24-10-18 | 08:00 | 509:33399 | SHORT RURAL | Planned |  | 40 | 420 | 0.07057 | 0.000168 | N
24-10-18 | 08:34 | 502:48010 | SHORT RURAL | Planned |  | 52 | 266 | 0.058103 | 0.000218 | N
24-10-18 | 09:35 | 232:11453 | SHORT RURAL | Planned |  | 147 | 220 | 0.13585 | 0.000617 | N
24-10-18 | 08:10 | 807:74184 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
24-10-18 | 09:15 | 807:74184 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
24-10-18 | 11:20 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
24-10-18 | 09:25 | 807:74184 | SHORT RURAL | Planned |  | 2 | 205 | 0.001722 | 8e-06 | N
24-10-18 | 08:20 | 523:33503 | URBAN | Planned |  | 52 | 355 | 0.012564 | 3.5e-05 | N
27-10-18 | 08:05 | 264:81236 | URBAN | Planned |  | 364 | 115 | 0.028461 | 0.000247 | N
27-10-18 | 08:05 | 264:81241 | URBAN | Planned |  | 391 | 115 | 0.030572 | 0.000266 | N
25-10-18 | 08:00 | 515:35192 | SHORT RURAL | Planned |  | 11 | 420 | 0.0194 | 4.6e-05 | N
25-10-18 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 36 | 510 | 6.458 | 0.012663 | N
26-10-18 | 08:00 | 522:83132 | SHORT RURAL | Planned |  | 21 | 400 | 0.035272 | 8.8e-05 | N
28-10-18 | 08:30 | 224:80332 | URBAN | Planned |  | 131 | 549 | 0.048898 | 8.9e-05 | N
28-10-18 | 08:30 | 224:80337 | URBAN | Planned |  | 50 | 549 | 0.018663 | 3.4e-05 | N
25-10-18 | 09:45 | 526:34640 | SHORT RURAL | Planned |  | 1 | 75 | 0.000315 | 4e-06 | N
25-10-18 | 08:50 | 532:83301 | URBAN | Planned |  | 114 | 270 | 0.020943 | 7.8e-05 | N
25-10-18 | 08:35 | 508:82579 | SHORT RURAL | Planned |  | 6 | 235 | 0.005921 | 2.5e-05 | N
27-10-18 | 07:20 | 264:81241 | URBAN | Planned |  | 15 | 30 | 0.000306 | 1e-05 | N
28-10-18 | 08:05 | 232:33407 | SHORT RURAL | Planned |  | 137 | 425 | 0.24449 | 0.000575 | N
25-10-18 | 10:25 | 813:89061 | LONG RURAL | Planned |  | 1 | 40 | 0.01407 | 0.000352 | N
25-10-18 | 11:15 | 813:89061 | LONG RURAL | Planned |  | 1 | 40 | 0.01407 | 0.000352 | N
25-10-18 | 09:35 | 813:89061 | LONG RURAL | Planned |  | 1 | 40 | 0.01407 | 0.000352 | N
25-10-18 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015828 | 0.000352 | N
26-10-18 | 09:00 | 512:83743 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
26-10-18 | 10:55 | 515:35197 | LONG RURAL | Planned |  | 1 | 50 | 0.017587 | 0.000352 | N
28-10-18 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 95 | 310 | 0.12366 | 0.000399 | N
28-10-18 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 137 | 321 | 0.18466 | 0.000575 | N
28-10-18 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 316 | 321 | 35.6667 | 0.11111 | N
28-10-18 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 573 | 321 | 0.77235 | 0.002406 | N
27-09-18 | 20:47 | ZN2602:PA8 | URBAN | Planned |  | 7 | 148 | 0.000705 | 5e-06 | N
27-09-18 | 21:20 | ZN35400:PA83 | URBAN | Planned |  | 17 | 450 | 0.005204 | 1.2e-05 | N
28-09-18 | 10:15 | ZN12690:PA19 | URBAN | Planned |  | 70 | 395 | 0.018809 | 4.8e-05 | N
29-09-18 | 00:30 | ZN8700:PA61 62DEF | CBD | Planned |  | 18 | 3,870 | 2.2883 | 0.000591 | N
29-09-18 | 07:00 | ZN7900:PA9 | URBAN | Planned |  | 1 | 1,920 | 0.001306 | 1e-06 | N
29-09-18 | 07:30 | ZN187:PA28 | URBAN | Planned |  | 1 | 510 | 0.000347 | 1e-06 | N
29-09-18 | 07:50 | ZN4990:PA51 52DEF | CBD | Planned |  | 27 | 595 | 0.52772 | 0.000887 | N
29-09-18 | 08:00 | ZN8700:PA65 66GHJ | CBD | Planned |  | 8 | 360 | 0.094606 | 0.000263 | N
19-09-18 | 10:08 | ZN35800:PA21 | URBAN | Planned |  | 1 | 212 | 0.000144 | 1e-06 | N
27-09-18 | 07:30 | ZN874:PA7 | URBAN | Planned |  | 32 | 420 | 0.009143 | 2.2e-05 | N
01-10-18 | 08:15 | ZN36000:PA12 | URBAN | Planned |  | 1 | 495 | 0.000337 | 1e-06 | N
02-10-18 | 08:00 | ZN9118:PA17 | URBAN | Planned |  | 40 | 420 | 0.011426 | 2.7e-05 | N
02-10-18 | 08:00 | ZN9252:PA28 | URBAN | Planned |  | 48 | 450 | 0.014691 | 3.3e-05 | N
02-10-18 | 08:00 | ZN10994:PA19 | URBAN | Planned |  | 40 | 450 | 0.012242 | 2.7e-05 | N
02-10-18 | 08:00 | ZN847:PA5 | URBAN | Planned |  | 12 | 360 | 0.002938 | 8e-06 | N
02-10-18 | 11:40 | ZN10998:PA16 | SHORT RURAL | Planned |  | 73 | 40 | 0.012284 | 0.000307 | N
02-10-18 | 09:30 | ZN4545:PA29 | URBAN | Planned |  | 47 | 300 | 0.00959 | 3.2e-05 | N
03-10-18 | 07:30 | ZN129:PA43 | URBAN | Planned |  | 3 | 400 | 0.000816 | 2e-06 | N
04-10-18 | 08:00 | ZN14892:PA14 | SHORT RURAL | Planned |  | 2 | 445 | 0.003744 | 8e-06 | N
14-10-18 | 08:00 | ZN847:PA5 | URBAN | Planned |  | 13 | 470 | 0.004158 | 9e-06 | N
04-10-18 | 08:30 | ZN2635:PA44 | URBAN | Planned |  | 105 | 150 | 0.010712 | 7.1e-05 | N
04-10-18 | 08:00 | ZN14892:PA14 | SHORT RURAL | Planned |  | 1 | 445 | 0.001872 | 4e-06 | N
04-10-18 | 08:00 | ZN36800:PA58 | URBAN | Planned |  | 10 | 295 | 0.002006 | 7e-06 | N
04-10-18 | 08:00 | ZN15010:PA24 | URBAN | Planned |  | 43 | 420 | 0.012284 | 2.9e-05 | N
04-10-18 | 20:30 | ZN35600:PA1 | URBAN | Planned |  | 18 | 405 | 0.004958 | 1.2e-05 | N
05-10-18 | 07:30 | ZN9700:PA23 | URBAN | Planned |  | 61 | 570 | 0.023649 | 4.1e-05 | N
05-10-18 | 07:50 | ZN80:PA40 | URBAN | Planned |  | 2 | 420 | 0.000571 | 1e-06 | N
05-10-18 | 07:30 | ZN35500:PA27 | URBAN | Planned |  | 38 | 480 | 0.012406 | 2.6e-05 | N
06-10-18 | 06:30 | ZN263:PA35 37DEF | CBD | Planned |  | 39 | 2,022 | 2.5901 | 0.001281 | N
06-10-18 | 08:05 | ZN12690:PA12 | SHORT RURAL | Planned |  | 2 | 790 | 0.006647 | 8e-06 | N
06-10-18 | 07:30 | ZN188:PA31 | URBAN | Planned |  | 33 | 390 | 0.008754 | 2.2e-05 | N
06-10-18 | 08:05 | ZN263:PA33 34KLM | CBD | Planned |  | 1 | 2,125 | 0.069812 | 3.3e-05 | N
06-10-18 | 12:30 | ZN2196:PA14 | URBAN | Planned |  | 2 | 120 | 0.000163 | 1e-06 | N
29-10-18 | 09:00 | 508:82579 | SHORT RURAL | Planned |  | 10 | 60 | 0.002519 | 4.2e-05 | N
29-10-18 | 12:30 | 508:82579 | SHORT RURAL | Planned |  | 3 | 65 | 0.000819 | 1.3e-05 | N
29-10-18 | 23:30 | 524:33578 | URBAN | Planned |  | 14 | 275 | 0.002617 | 1e-05 | N
29-10-18 | 09:10 | 515:35197 | LONG RURAL | Planned |  | 1 | 125 | 0.043952 | 0.000352 | N
29-10-18 | 12:30 | 515:35197 | LONG RURAL | Planned |  | 1 | 40 | 0.014065 | 0.000352 | N
29-10-18 | 08:45 | 807:74184 | SHORT RURAL | Planned |  | 2 | 195 | 0.001637 | 8e-06 | N
30-10-18 | 09:00 | 502:48010 | SHORT RURAL | Planned |  | 5 | 260 | 0.005457 | 2.1e-05 | N
30-10-18 | 09:00 | 502:48010 | SHORT RURAL | Planned |  | 18 | 260 | 0.019645 | 7.6e-05 | N
30-10-18 | 08:15 | 258:80793 | URBAN | Planned |  | 158 | 300 | 0.032217 | 0.000107 | N
30-10-18 | 08:00 | 526:34636 | SHORT RURAL | Planned |  | 15 | 380 | 0.023927 | 6.3e-05 | N
30-10-18 | 08:03 | 246:62 | URBAN | Planned |  | 1 | 449 | 0.000305 | 1e-06 | N
30-10-18 | 15:50 | 224:80340 | SHORT RURAL | Planned |  | 6 | 300 | 0.007556 | 2.5e-05 | N
30-10-18 | 09:00 | 511:29877 | SHORT RURAL | Planned |  | 5 | 56 | 0.001175 | 2.1e-05 | N
30-10-18 | 12:30 | 511:29877 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
30-10-18 | 09:00 | 523:33501 | SHORT RURAL | Planned |  | 2 | 60 | 0.000504 | 8e-06 | N
30-10-18 | 10:00 | 813:89061 | LONG RURAL | Planned |  | 4 | 295 | 0.41491 | 0.001406 | N
31-10-18 | 08:00 | 513:48056 | SHORT RURAL | Planned |  | 2 | 165 | 0.001385 | 8e-06 | N
31-10-18 | 12:35 | 516:48065 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
31-10-18 | 08:00 | 523:33507 | URBAN | Planned |  | 23 | 430 | 0.006722 | 1.6e-05 | N
31-10-18 | 08:45 | 807:74181 | SHORT RURAL | Planned |  | 39 | 340 | 0.055663 | 0.000164 | N
01-11-18 | 08:00 | 532:83307 | SHORT RURAL | Planned |  | 49 | 585 | 0.12033 | 0.000206 | N
01-11-18 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 4 | 560 | 0.009403 | 1.7e-05 | N
01-11-18 | 12:10 | 242:81541 | URBAN | Planned |  | 102 | 65 | 0.004506 | 6.9e-05 | N
01-11-18 | 08:10 | 507:80922 | SHORT RURAL | Planned |  | 23 | 415 | 0.040068 | 9.7e-05 | N
01-11-18 | 07:30 | 509:33395 | LONG RURAL | Planned |  | 33 | 469 | 5.4458 | 0.011612 | N
01-11-18 | 18:10 | 509:33395 | LONG RURAL | Planned |  | 2 | 20 | 0.014075 | 0.000704 | N
01-11-18 | 08:05 | 516:48067 | SHORT RURAL | Planned |  | 23 | 392 | 0.037847 | 9.7e-05 | N
02-11-18 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 7 | 300 | 0.73892 | 0.002463 | N
04-11-18 | 09:50 | 232:33407 | SHORT RURAL | Planned |  | 130 | 365 | 0.19915 | 0.000546 | N
02-11-18 | 08:30 | 523:33508 | SHORT RURAL | Planned |  | 6 | 40 | 0.001007 | 2.5e-05 | N
02-11-18 | 08:05 | 513:48059 | SHORT RURAL | Planned |  | 45 | 350 | 0.066115 | 0.000189 | N
04-11-18 | 08:03 | 523:33508 | SHORT RURAL | Planned |  | 174 | 204 | 0.14898 | 0.00073 | N
05-11-18 | 08:00 | 238:34141 | SHORT RURAL | Planned |  | 37 | 470 | 0.072987 | 0.000155 | N
05-11-18 | 08:35 | 526:34640 | SHORT RURAL | Planned |  | 1 | 65 | 0.000273 | 4e-06 | N
05-11-18 | 08:50 | 238:34137 | SHORT RURAL | Planned |  | 39 | 370 | 0.060563 | 0.000164 | N
05-11-18 | 10:30 | 526:34637 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
06-11-18 | 08:05 | 513:48059 | SHORT RURAL | Planned |  | 15 | 110 | 0.006925 | 6.3e-05 | N
06-11-18 | 08:25 | 511:29878 | SHORT RURAL | Planned |  | 17 | 615 | 0.04388 | 7.1e-05 | N
06-11-18 | 08:30 | 511:29876 | SHORT RURAL | Planned |  | 65 | 340 | 0.092755 | 0.000273 | N
06-11-18 | 08:45 | 532:83309 | URBAN | Planned |  | 6 | 103 | 0.00042 | 4e-06 | N
06-11-18 | 12:45 | 532:83307 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
06-11-18 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 15 | 200 | 0.012591 | 6.3e-05 | N
06-11-18 | 09:25 | 810:74054 | LONG RURAL | Planned |  | 2 | 245 | 0.17229 | 0.000703 | N
07-11-18 | 08:30 | 524:33572 | SHORT RURAL | Planned |  | 308 | 430 | 0.55587 | 0.001293 | N
07-11-18 | 09:55 | 243:80075 | SHORT RURAL | Planned |  | 12 | 51 | 0.002569 | 5e-05 | N
07-11-18 | 09:30 | 508:82579 | SHORT RURAL | Planned |  | 6 | 35 | 0.000881 | 2.5e-05 | N
07-11-18 | 08:31 | 233:82819 | SHORT RURAL | Planned |  | 20 | 288 | 0.024175 | 8.4e-05 | N
07-11-18 | 08:37 | 522:83132 | SHORT RURAL | Planned |  | 44 | 313 | 0.057803 | 0.000185 | N
07-11-18 | 08:30 | 524:33578 | URBAN | Planned |  | 159 | 430 | 0.046458 | 0.000108 | N
07-11-18 | 08:30 | 813:89062 | SHORT RURAL | Planned |  | 4 | 105 | 0.001763 | 1.7e-05 | N
07-11-18 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 3 | 77 | 0.00097 | 1.3e-05 | N
07-11-18 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 2 | 220 | 0.15471 | 0.000703 | N
07-11-18 | 09:45 | 806:82662 | SHORT RURAL | Planned |  | 2 | 400 | 0.003358 | 8e-06 | N
07-11-18 | 09:15 | 813:89062 | SHORT RURAL | Planned |  | 5 | 105 | 0.002203 | 2.1e-05 | N
07-11-18 | 08:40 | 813:89062 | SHORT RURAL | Planned |  | 4 | 275 | 0.004617 | 1.7e-05 | N
10-11-18 | 06:55 | 417:80507 | URBAN | Planned |  | 1 | 666 | 0.000452 | 1e-06 | N
08-11-18 | 07:30 | 509:33395 | LONG RURAL | Planned |  | 33 | 501 | 5.8133 | 0.011603 | N
08-11-18 | 17:00 | 522:83126 | SHORT RURAL | Planned |  | 15 | 50 | 0.003148 | 6.3e-05 | N
09-11-18 | 08:30 | 509:33397 | SHORT RURAL | Planned |  | 12 | 155 | 0.007841 | 5.1e-05 | N
09-11-18 | 08:30 | 230:81438 | SHORT RURAL | Planned |  | 39 | 405 | 0.066587 | 0.000164 | N
09-11-18 | 08:00 | 238:34150 | SHORT RURAL | Planned |  | 52 | 425 | 0.093167 | 0.000219 | N
08-11-18 | 09:35 | 515:35197 | LONG RURAL | Planned |  | 1 | 60 | 0.021097 | 0.000352 | N
08-11-18 | 13:00 | 515:35193 | SHORT RURAL | Planned |  | 3 | 40 | 0.000504 | 1.3e-05 | N
09-11-18 | 09:10 | 513:48056 | SHORT RURAL | Planned |  | 6 | 155 | 0.003921 | 2.5e-05 | N
09-11-18 | 09:02 | 516:48065 | SHORT RURAL | Planned |  | 2 | 145 | 0.001223 | 8e-06 | N
09-11-18 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 1 | 170 | 0.000717 | 4e-06 | N
09-11-18 | 08:25 | 810:74054 | LONG RURAL | Planned |  | 4 | 250 | 0.35162 | 0.001406 | N
11-11-18 | 06:45 | 813:89059 | URBAN | Planned |  | 41 | 95 | 0.002645 | 2.8e-05 | N
11-11-18 | 06:50 | 813:89063 | SHORT RURAL | Planned |  | 26 | 100 | 0.010961 | 0.00011 | N
11-11-18 | 08:00 | 812:19065 | SHORT RURAL | Planned |  | 2 | 160 | 0.001349 | 8e-06 | N
13-11-18 | 08:00 | ZN2635:PA57 | URBAN | Planned |  | 287 | 480 | 0.093549 | 0.000195 | N
12-11-18 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 11 | 246 | 0.95148 | 0.003868 | N
12-11-18 | 14:00 | 512:83733 | SHORT RURAL | Planned |  | 2 | 40 | 0.000337 | 8e-06 | N
12-11-18 | 07:56 | 220:8691 | URBAN | Planned |  | 1 | 309 | 0.00021 | 1e-06 | N
12-11-18 | 08:33 | 526:34633 | SHORT RURAL | Planned |  | 1 | 387 | 0.001632 | 4e-06 | N
12-11-18 | 08:40 | 265:81651 | SHORT RURAL | Planned |  | 18 | 355 | 0.02694 | 7.6e-05 | N
12-11-18 | 10:33 | 526:34633 | SHORT RURAL | Planned |  | 1 | 45 | 0.00019 | 4e-06 | N
12-11-18 | 08:03 | 528:83019 | SHORT RURAL | Planned |  | 32 | 427 | 0.057606 | 0.000135 | N
12-11-18 | 08:03 | 528:83014 | SHORT RURAL | Planned |  | 19 | 427 | 0.034203 | 8e-05 | N
18-11-18 | 08:40 | 228:7490 | URBAN | Planned |  | 34 | 505 | 0.011676 | 2.3e-05 | N
13-11-18 | 08:25 | 415:33884 | URBAN | Planned |  | 1 | 305 | 0.000207 | 1e-06 | N
13-11-18 | 08:10 | 813:89061 | LONG RURAL | Planned |  | 5 | 335 | 0.58896 | 0.001758 | N
13-11-18 | 08:00 | 515:35192 | SHORT RURAL | Planned |  | 11 | 375 | 0.01739 | 4.6e-05 | N
13-11-18 | 08:10 | 528:83020 | SHORT RURAL | Planned |  | 33 | 440 | 0.061214 | 0.000139 | N
14-11-18 | 08:42 | 227:13019 | SHORT RURAL | Planned |  | 49 | 418 | 0.086352 | 0.000207 | N
15-11-18 | 08:35 | 813:89061 | LONG RURAL | Planned |  | 5 | 300 | 0.52761 | 0.001759 | N
15-11-18 | 08:30 | 227:13020 | SHORT RURAL | Planned |  | 3 | 450 | 0.005692 | 1.3e-05 | N
13-11-18 | 08:37 | 227:13019 | SHORT RURAL | Planned |  | 1 | 113 | 0.000476 | 4e-06 | N
13-11-18 | 11:30 | 227:13019 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
13-11-18 | 08:45 | 258:80781 | URBAN | Planned |  | 4 | 430 | 0.001168 | 3e-06 | N
14-11-18 | 08:50 | 216:10722 | SHORT RURAL | Planned |  | 141 | 345 | 0.20509 | 0.000594 | N
13-11-18 | 09:00 | 511:29878 | SHORT RURAL | Planned |  | 9 | 118 | 0.004477 | 3.8e-05 | N
13-11-18 | 09:45 | 232:11455 | SHORT RURAL | Planned |  | 103 | 280 | 0.12159 | 0.000434 | N
13-11-18 | 08:07 | 509:33395 | LONG RURAL | Planned |  | 33 | 431 | 5.0011 | 0.011603 | N
13-11-18 | 08:00 | 528:83019 | SHORT RURAL | Planned |  | 28 | 510 | 0.060203 | 0.000118 | N
14-11-18 | 08:10 | 264:81240 | SHORT RURAL | Planned |  | 1 | 340 | 0.001433 | 4e-06 | N
14-11-18 | 08:05 | 532:83298 | SHORT RURAL | Planned |  | 156 | 460 | 0.30254 | 0.000658 | N
15-11-18 | 08:00 | 524:33574 | SHORT RURAL | Planned |  | 2 | 150 | 0.001265 | 8e-06 | N
15-11-18 | 11:20 | 508:82579 | SHORT RURAL | Planned |  | 8 | 40 | 0.001349 | 3.4e-05 | N
14-11-18 | 08:00 | 813:89065 | SHORT RURAL | Planned |  | 41 | 145 | 0.025064 | 0.000173 | N
14-11-18 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 5 | 290 | 0.51002 | 0.001759 | N
14-11-18 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 5 | 265 | 0.005586 | 2.1e-05 | N
14-11-18 | 09:00 | 514:18137 | SHORT RURAL | Planned |  | 1 | 50 | 0.000211 | 4e-06 | N
14-11-18 | 12:00 | 813:89061 | LONG RURAL | Planned |  | 5 | 145 | 0.25501 | 0.001759 | N
15-11-18 | 08:05 | 813:89065 | SHORT RURAL | Planned |  | 11 | 185 | 0.00858 | 4.6e-05 | N
15-11-18 | 12:00 | 813:89063 | SHORT RURAL | Planned |  | 130 | 150 | 0.082212 | 0.000548 | N
18-11-18 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 137 | 288 | 0.16618 | 0.000577 | N
18-11-18 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 316 | 288 | 32.0225 | 0.11119 | N
18-11-18 | 08:30 | 810:74058 | SHORT RURAL | Planned |  | 196 | 288 | 0.23775 | 0.000826 | N
18-11-18 | 08:30 | 810:74062 | SHORT RURAL | Planned |  | 572 | 288 | 0.69384 | 0.002409 | N
16-11-18 | 10:05 | 216:10728 | URBAN | Planned |  | 52 | 230 | 0.008122 | 3.5e-05 | N
17-11-18 | 08:00 | 204:82689 | URBAN | Planned |  | 169 | 470 | 0.054074 | 0.000115 | N
16-11-18 | 08:35 | 507:80914 | SHORT RURAL | Planned |  | 97 | 290 | 0.1186 | 0.000409 | N
16-11-18 | 08:55 | 233:82819 | SHORT RURAL | Planned |  | 20 | 353 | 0.029766 | 8.4e-05 | N
16-11-18 | 08:55 | 508:82580 | SHORT RURAL | Planned |  | 5 | 265 | 0.005586 | 2.1e-05 | N
17-11-18 | 07:40 | 264:81232 | SHORT RURAL | Planned |  | 1 | 525 | 0.002211 | 4e-06 | N
18-11-18 | 18:45 | 524:33570 | SHORT RURAL | Planned |  | 66 | 595 | 0.1654 | 0.000278 | N
16-11-18 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 3 | 80 | 0.001012 | 1.3e-05 | N
16-11-18 | 09:55 | 516:48067 | SHORT RURAL | Planned |  | 1 | 47 | 0.000198 | 4e-06 | N
16-11-18 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 5 | 130 | 0.22863 | 0.001759 | N
16-11-18 | 10:25 | 514:18137 | SHORT RURAL | Planned |  | 1 | 50 | 0.000211 | 4e-06 | N
16-11-18 | 10:48 | 516:48067 | SHORT RURAL | Planned |  | 1 | 52 | 0.000219 | 4e-06 | N
16-11-18 | 09:00 | 516:48067 | SHORT RURAL | Planned |  | 1 | 20 | 8.4e-05 | 4e-06 | N
16-11-18 | 13:40 | 514:18137 | SHORT RURAL | Planned |  | 1 | 40 | 0.000169 | 4e-06 | N
16-11-18 | 08:40 | 811:74234 | SHORT RURAL | Planned |  | 6 | 460 | 0.011636 | 2.5e-05 | N
18-11-18 | 08:00 | 513:48056 | SHORT RURAL | Planned |  | 6 | 480 | 0.01213 | 2.5e-05 | N
19-11-18 | 08:31 | 528:83014 | SHORT RURAL | Planned |  | 223 | 494 | 0.46393 | 0.000939 | N
20-11-18 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 10 | 350 | 1.2315 | 0.003519 | N
20-11-18 | 08:40 | 516:48067 | SHORT RURAL | Planned |  | 22 | 425 | 0.039377 | 9.3e-05 | N
20-11-18 | 08:50 | 239:82131 | SHORT RURAL | Planned |  | 3 | 210 | 0.002653 | 1.3e-05 | N
19-11-18 | 22:00 | 522:83129 | URBAN | Planned |  | 141 | 540 | 0.051776 | 9.6e-05 | N
20-11-18 | 08:35 | 507:80914 | SHORT RURAL | Planned |  | 19 | 460 | 0.036808 | 8e-05 | N
20-11-18 | 08:00 | 508:82579 | SHORT RURAL | Planned |  | 32 | 495 | 0.066708 | 0.000135 | N
20-11-18 | 08:30 | 524:33572 | SHORT RURAL | Planned |  | 132 | 430 | 0.23904 | 0.000556 | N
20-11-18 | 08:00 | 508:82579 | SHORT RURAL | Planned |  | 3 | 495 | 0.006254 | 1.3e-05 | N
20-11-18 | 10:00 | 514:18137 | SHORT RURAL | Planned |  | 1 | 70 | 0.000295 | 4e-06 | N
20-11-18 | 08:05 | 514:18137 | SHORT RURAL | Planned |  | 6 | 73 | 0.001845 | 2.5e-05 | N
20-11-18 | 13:05 | 514:18137 | SHORT RURAL | Planned |  | 1 | 55 | 0.000232 | 4e-06 | N
22-11-18 | 07:10 | 409:60200 | URBAN | Planned |  | 1 | 480 | 0.000326 | 1e-06 | N
22-11-18 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 11 | 285 | 0.013203 | 4.6e-05 | N
22-11-18 | 09:30 | 524:33572 | SHORT RURAL | Planned |  | 3 | 375 | 0.004738 | 1.3e-05 | N
23-11-18 | 08:30 | 508:82578 | SHORT RURAL | Planned |  | 8 | 415 | 0.013982 | 3.4e-05 | N
21-11-18 | 10:20 | 214:8670 | URBAN | Planned |  | 24 | 220 | 0.00359 | 1.6e-05 | N
21-11-18 | 10:10 | 526:34640 | SHORT RURAL | Planned |  | 1 | 71 | 0.000299 | 4e-06 | N
21-11-18 | 08:20 | 508:82579 | SHORT RURAL | Planned |  | 12 | 415 | 0.020973 | 5.1e-05 | N
22-11-18 | 09:15 | 511:29878 | SHORT RURAL | Planned |  | 1 | 15 | 6.3e-05 | 4e-06 | N
22-11-18 | 08:30 | 238:34138 | SHORT RURAL | Planned |  | 40 | 310 | 0.052222 | 0.000168 | N
22-11-18 | 08:10 | 508:82579 | SHORT RURAL | Planned |  | 12 | 405 | 0.020468 | 5.1e-05 | N
21-11-18 | 10:05 | 813:89055 | SHORT RURAL | Planned |  | 10 | 27 | 0.001137 | 4.2e-05 | N
21-11-18 | 09:30 | 513:48059 | SHORT RURAL | Planned |  | 2 | 110 | 0.000927 | 8e-06 | N
22-11-18 | 09:15 | 802:82225 | SHORT RURAL | Planned |  | 9 | 220 | 0.008339 | 3.8e-05 | N
23-11-18 | 08:45 | 814:82291 | SHORT RURAL | Planned |  | 39 | 385 | 0.063236 | 0.000164 | N
23-11-18 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 5 | 275 | 0.48398 | 0.00176 | N
26-11-18 | 08:00 | 238:34141 | SHORT RURAL | Planned |  | 108 | 420 | 0.19104 | 0.000455 | N
26-11-18 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 18 | 340 | 2.1542 | 0.006336 | N
26-11-18 | 09:14 | 813:89062 | SHORT RURAL | Planned |  | 5 | 316 | 0.006654 | 2.1e-05 | N
26-11-18 | 08:00 | 261:81865 | URBAN | Planned |  | 103 | 320 | 0.02237 | 7e-05 | N
26-11-18 | 10:15 | 813:89062 | SHORT RURAL | Planned |  | 1 | 235 | 0.00099 | 4e-06 | N
27-11-18 | 09:00 | 224:80329 | SHORT RURAL | Planned |  | 26 | 475 | 0.052012 | 0.000109 | N
27-11-18 | 09:26 | 511:29880 | URBAN | Planned |  | 15 | 304 | 0.003095 | 1e-05 | N
27-11-18 | 08:15 | 508:82579 | SHORT RURAL | Planned |  | 12 | 420 | 0.021226 | 5.1e-05 | N
27-11-18 | 08:30 | 508:82579 | SHORT RURAL | Planned |  | 16 | 445 | 0.029986 | 6.7e-05 | N
27-11-18 | 08:05 | 532:83307 | SHORT RURAL | Planned |  | 49 | 595 | 0.12279 | 0.000206 | N
27-11-18 | 17:25 | 511:29878 | SHORT RURAL | Planned |  | 1 | 50 | 0.000211 | 4e-06 | N
27-11-18 | 08:30 | 515:35198 | SHORT RURAL | Planned |  | 1 | 160 | 0.000674 | 4e-06 | N
27-11-18 | 08:10 | 520:48172 | SHORT RURAL | Planned |  | 34 | 335 | 0.047969 | 0.000143 | N
28-11-18 | 08:10 | 511:29878 | SHORT RURAL | Planned |  | 12 | 180 | 0.009097 | 5.1e-05 | N
28-11-18 | 06:25 | 406:6028 | URBAN | Planned |  | 1 | 735 | 0.000499 | 1e-06 | N
29-11-18 | 21:30 | 257:81985 | URBAN | Planned |  | 319 | 295 | 0.063874 | 0.000217 | N
29-11-18 | 08:30 | 511:29877 | SHORT RURAL | Planned |  | 7 | 275 | 0.008107 | 2.9e-05 | N
29-11-18 | 08:10 | 528:83014 | SHORT RURAL | Planned |  | 19 | 460 | 0.03681 | 8e-05 | N
29-11-18 | 08:15 | 227:13019 | SHORT RURAL | Planned |  | 11 | 340 | 0.015752 | 4.6e-05 | N
29-11-18 | 09:18 | 233:82812 | SHORT RURAL | Planned |  | 9 | 122 | 0.004624 | 3.8e-05 | N
29-11-18 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 52 | 278 | 0.060884 | 0.000219 | N
29-11-18 | 08:00 | 813:89065 | SHORT RURAL | Planned |  | 41 | 305 | 0.052667 | 0.000173 | N
29-11-18 | 08:00 | 515:35192 | SHORT RURAL | Planned |  | 11 | 435 | 0.020153 | 4.6e-05 | N
29-11-18 | 13:40 | 813:89061 | LONG RURAL | Planned |  | 5 | 210 | 0.36959 | 0.00176 | N
02-12-18 | 17:36 | ZN14892:PA19 | URBAN | Planned |  | 82 | 83 | 0.00464 | 5.6e-05 | N
30-11-18 | 08:15 | 516:48066 | SHORT RURAL | Planned |  | 5 | 185 | 0.003897 | 2.1e-05 | N
01-12-18 | 08:00 | 417:80504 | URBAN | Planned |  | 2 | 515 | 0.000699 | 1e-06 | N
01-12-18 | 08:00 | 258:80781 | URBAN | Planned |  | 4 | 495 | 0.001343 | 3e-06 | N
02-12-18 | 08:00 | 202:34238 43 48 | URBAN | Planned |  | 17 | 620 | 0.00715 | 1.2e-05 | N
30-11-18 | 12:00 | 522:83132 | SHORT RURAL | Planned |  | 1 | 50 | 0.000211 | 4e-06 | N
30-11-18 | 08:00 | 526:34635 | SHORT RURAL | Planned |  | 2 | 120 | 0.001011 | 8e-06 | N
30-11-18 | 00:45 | 813:89065 | SHORT RURAL | Planned |  | 11 | 690 | 0.031979 | 4.6e-05 | N
30-11-18 | 12:43 | 813:89063 | SHORT RURAL | Planned |  | 133 | 87 | 0.048752 | 0.00056 | N
03-12-18 | 12:45 | 528:83014 | SHORT RURAL | Planned |  | 1 | 70 | 0.000295 | 4e-06 | N
03-12-18 | 08:15 | 528:83013 | URBAN | Planned |  | 86 | 60 | 0.003501 | 5.8e-05 | N
03-12-18 | 08:30 | 802:82215 | SHORT RURAL | Planned |  | 5 | 265 | 0.005583 | 2.1e-05 | N
04-12-18 | 08:18 | 508:82575 | SHORT RURAL | Planned |  | 92 | 432 | 0.16746 | 0.000388 | N
04-12-18 | 08:15 | 216:10727 | URBAN | Planned |  | 33 | 555 | 0.012425 | 2.2e-05 | N
04-12-18 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 1 | 90 | 0.000379 | 4e-06 | N
04-12-18 | 08:30 | 507:80932 | SHORT RURAL | Planned |  | 25 | 440 | 0.046347 | 0.000105 | N
04-12-18 | 17:10 | 238:34144 | URBAN | Planned |  | 1 | 195 | 0.000132 | 1e-06 | N
04-12-18 | 08:05 | 810:74054 | LONG RURAL | Planned |  | 16 | 295 | 1.6614 | 0.005632 | N
05-12-18 | 08:35 | 509:33395 | LONG RURAL | Planned |  | 751 | 445 | 117.6329 | 0.26434 | N
05-12-18 | 08:00 | 515:35193 | SHORT RURAL | Planned |  | 9 | 405 | 0.015351 | 3.8e-05 | N
05-12-18 | 08:30 | 814:82285 | SHORT RURAL | Planned |  | 26 | 260 | 0.02847 | 0.000109 | N
05-12-18 | 08:32 | 801:74121 | LONG RURAL | Planned |  | 12 | 249 | 1.0517 | 0.004224 | N
06-12-18 | 08:00 | 508:82576 | SHORT RURAL | Planned |  | 112 | 450 | 0.21226 | 0.000472 | N
07-12-18 | 09:30 | 813:89059 | URBAN | Planned |  | 75 | 260 | 0.013223 | 5.1e-05 | N
07-12-18 | 08:00 | 264:81244 | SHORT RURAL | Planned |  | 244 | 365 | 0.37509 | 0.001028 | N
07-12-18 | 08:10 | 801:74121 | LONG RURAL | Planned |  | 7 | 475 | 1.1704 | 0.002464 | N
06-12-18 | 08:30 | 227:13015 | SHORT RURAL | Planned |  | 157 | 420 | 0.27771 | 0.000661 | N
06-12-18 | 07:45 | 217:33612 | URBAN | Planned |  | 147 | 455 | 0.045355 | 0.0001 | N
06-12-18 | 10:20 | 202:34238 43 48 | URBAN | Planned |  | 18 | 640 | 0.007812 | 1.2e-05 | N
08-12-18 | 08:15 | 202:34238 43 48 | URBAN | Planned |  | 18 | 435 | 0.005311 | 1.2e-05 | N
08-12-18 | 08:15 | 202:34249 | URBAN | Planned |  | 60 | 435 | 0.017704 | 4.1e-05 | N
09-12-18 | 08:20 | 256:80640 | URBAN | Planned |  | 65 | 370 | 0.016314 | 4.4e-05 | N
09-12-18 | 08:00 | 243:80075 | SHORT RURAL | Planned |  | 16 | 630 | 0.042439 | 6.7e-05 | N
09-12-18 | 08:00 | 243:80077 | SHORT RURAL | Planned |  | 52 | 630 | 0.13793 | 0.000219 | N
06-12-18 | 09:05 | 507:80932 | SHORT RURAL | Planned |  | 62 | 315 | 0.082251 | 0.000261 | N
06-12-18 | 08:00 | 238:34148 | SHORT RURAL | Planned |  | 101 | 450 | 0.19141 | 0.000425 | N
08-12-18 | 08:13 | 532:83298 | SHORT RURAL | Planned |  | 6 | 377 | 0.009524 | 2.5e-05 | N
08-12-18 | 08:13 | 532:83298 | SHORT RURAL | Planned |  | 102 | 377 | 0.1619 | 0.000429 | N
06-12-18 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 8 | 360 | 1.0137 | 0.002816 | N
06-12-18 | 08:15 | 812:19072 | SHORT RURAL | Planned |  | 2 | 312 | 0.002628 | 8e-06 | N
06-12-18 | 08:15 | 516:48067 | SHORT RURAL | Planned |  | 14 | 360 | 0.021226 | 5.9e-05 | N
07-12-18 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 8 | 280 | 0.78846 | 0.002816 | N
07-12-18 | 09:10 | 515:35197 | LONG RURAL | Planned |  | 9 | 40 | 0.12672 | 0.003168 | N
10-12-18 | 08:00 | 511:29877 | SHORT RURAL | Planned |  | 25 | 435 | 0.045786 | 0.000105 | N
10-12-18 | 08:00 | 242:81535 | URBAN | Planned |  | 17 | 55 | 0.000634 | 1.2e-05 | N
10-12-18 | 09:40 | 810:74054 | LONG RURAL | Planned |  | 1 | 155 | 0.05452 | 0.000352 | N
10-12-18 | 08:00 | 242:81535 | URBAN | Planned |  | 78 | 207 | 0.010952 | 5.3e-05 | N
11-12-18 | 08:30 | 227:13015 | SHORT RURAL | Planned |  | 157 | 400 | 0.2644 | 0.000661 | N
11-12-18 | 08:00 | 522:83126 | SHORT RURAL | Planned |  | 4 | 180 | 0.003031 | 1.7e-05 | N
11-12-18 | 08:20 | 528:83014 | SHORT RURAL | Planned |  | 6 | 445 | 0.011241 | 2.5e-05 | N
11-12-18 | 08:30 | 512:83732 | SHORT RURAL | Planned |  | 1 | 345 | 0.001453 | 4e-06 | N
11-12-18 | 08:35 | 812:19072 | SHORT RURAL | Planned |  | 3 | 395 | 0.004989 | 1.3e-05 | N
12-12-18 | 08:30 | 224:80329 | SHORT RURAL | Planned |  | 40 | 460 | 0.077466 | 0.000168 | N
12-12-18 | 08:00 | 204:82703 | URBAN | Planned |  | 46 | 435 | 0.013566 | 3.1e-05 | N
12-12-18 | 08:30 | 232:33407 | SHORT RURAL | Planned |  | 13 | 400 | 0.021893 | 5.5e-05 | N
12-12-18 | 08:33 | 507:80932 | SHORT RURAL | Planned |  | 25 | 357 | 0.037575 | 0.000105 | N
12-12-18 | 08:00 | 515:35193 | SHORT RURAL | Planned |  | 3 | 335 | 0.004231 | 1.3e-05 | N
12-12-18 | 10:20 | 514:18137 | SHORT RURAL | Planned |  | 4 | 60 | 0.00101 | 1.7e-05 | N
12-12-18 | 08:00 | 205:12213 | SHORT RURAL | Planned |  | 8 | 285 | 0.009599 | 3.4e-05 | N
12-12-18 | 13:20 | 514:18137 | SHORT RURAL | Planned |  | 3 | 60 | 0.000758 | 1.3e-05 | N
13-12-18 | 08:35 | 511:29878 | SHORT RURAL | Planned |  | 10 | 405 | 0.017051 | 4.2e-05 | N
13-12-18 | 08:35 | 532:83307 | SHORT RURAL | Planned |  | 2 | 325 | 0.002737 | 8e-06 | N
13-12-18 | 08:00 | 508:82578 | SHORT RURAL | Planned |  | 30 | 430 | 0.05431 | 0.000126 | N
13-12-18 | 08:30 | 813:89061 | LONG RURAL | Planned |  | 4 | 355 | 0.49947 | 0.001407 | N
15-12-18 | 08:00 | 264:81236 | URBAN | Planned |  | 366 | 680 | 0.16867 | 0.000248 | N
15-12-18 | 08:00 | 264:81241 | URBAN | Planned |  | 389 | 680 | 0.17927 | 0.000264 | N
17-12-18 | 19:21 | ZN12600:PA2 | SHORT RURAL | Planned |  | 115 | 133 | 0.064411 | 0.000484 | N
19-12-18 | 19:25 | 502:48004 | URBAN | Planned |  | 65 | 5 | 0.00022 | 4.4e-05 | N
06-01-19 | 06:42 | 511:29873 | URBAN | Planned |  | 62 | 128 | 0.005377 | 4.2e-05 | N
14-12-18 | 08:05 | 264:81244 | SHORT RURAL | Planned |  | 13 | 245 | 0.013409 | 5.5e-05 | N
14-12-18 | 08:30 | 528:83019 | SHORT RURAL | Planned |  | 35 | 315 | 0.046417 | 0.000147 | N
14-12-18 | 07:00 | 204:82708 | URBAN | Planned |  | 4 | 350 | 0.000949 | 3e-06 | N
14-12-18 | 09:10 | 511:29878 | SHORT RURAL | Planned |  | 4 | 80 | 0.001347 | 1.7e-05 | N
14-12-18 | 08:30 | 522:83132 | SHORT RURAL | Planned |  | 1 | 62 | 0.000261 | 4e-06 | N
14-12-18 | 10:30 | 522:83132 | SHORT RURAL | Planned |  | 1 | 60 | 0.000253 | 4e-06 | N
14-12-18 | 09:10 | 508:82578 | SHORT RURAL | Planned |  | 1 | 184 | 0.000775 | 4e-06 | N
14-12-18 | 11:45 | 522:83126 | SHORT RURAL | Planned |  | 15 | 55 | 0.003473 | 6.3e-05 | N
16-12-18 | 08:00 | 507:80926 | URBAN | Planned |  | 10 | 460 | 0.003118 | 7e-06 | N
14-12-18 | 09:00 | 814:82285 | SHORT RURAL | Planned |  | 1 | 85 | 0.000358 | 4e-06 | N
14-12-18 | 11:25 | 814:82285 | SHORT RURAL | Planned |  | 1 | 10 | 4.2e-05 | 4e-06 | N
14-12-18 | 09:15 | 813:89059 | URBAN | Planned |  | 75 | 210 | 0.010678 | 5.1e-05 | N
17-12-18 | 08:10 | 223:14395 | SHORT RURAL | Planned |  | 425 | 585 | 1.0465 | 0.001789 | N
18-12-18 | 09:30 | 812:19072 | SHORT RURAL | Planned |  | 19 | 210 | 0.016794 | 8e-05 | N
19-12-18 | 10:20 | 807:74179 | SHORT RURAL | Planned |  | 12 | 110 | 0.005556 | 5.1e-05 | N
21-12-18 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 19 | 485 | 0.038785 | 8e-05 | N
19-12-18 | 08:00 | 216:10726 | URBAN | Planned |  | 63 | 505 | 0.02156 | 4.3e-05 | N
20-12-18 | 07:05 | 227:13015 | SHORT RURAL | Planned |  | 67 | 345 | 0.097289 | 0.000282 | N
18-12-18 | 10:00 | 528:83019 | SHORT RURAL | Planned |  | 1 | 70 | 0.000295 | 4e-06 | N
18-12-18 | 13:00 | 528:83019 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
18-12-18 | 14:05 | 511:29873 | URBAN | Planned |  | 1 | 25 | 1.7e-05 | 1e-06 | N
18-12-18 | 17:05 | 522:83132 | SHORT RURAL | Planned |  | 2 | 35 | 0.000295 | 8e-06 | N
19-12-18 | 11:06 | 507:80925 | SHORT RURAL | Planned |  | 54 | 194 | 0.044092 | 0.000227 | N
19-12-18 | 14:15 | 265:81651 | SHORT RURAL | Planned |  | 20 | 85 | 0.007155 | 8.4e-05 | N
20-12-18 | 10:27 | 508:82578 | SHORT RURAL | Planned |  | 2 | 183 | 0.00154 | 8e-06 | N
20-12-18 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 29 | 485 | 0.059198 | 0.000122 | N
21-12-18 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 10 | 485 | 0.020413 | 4.2e-05 | N
17-12-18 | 09:05 | 813:89055 | SHORT RURAL | Planned |  | 3 | 160 | 0.00202 | 1.3e-05 | N
18-12-18 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 6 | 475 | 0.011995 | 2.5e-05 | N
18-12-18 | 08:45 | 813:89055 | SHORT RURAL | Planned |  | 1 | 60 | 0.000253 | 4e-06 | N
18-12-18 | 08:35 | 813:89055 | SHORT RURAL | Planned |  | 1 | 70 | 0.000295 | 4e-06 | N
18-12-18 | 09:05 | 802:82215 | SHORT RURAL | Planned |  | 4 | 170 | 0.002862 | 1.7e-05 | N
18-12-18 | 10:00 | 813:89055 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
18-12-18 | 09:50 | 813:89055 | SHORT RURAL | Planned |  | 2 | 45 | 0.000379 | 8e-06 | N
18-12-18 | 10:53 | 813:89055 | SHORT RURAL | Planned |  | 1 | 42 | 0.000177 | 4e-06 | N
18-12-18 | 11:50 | 813:89055 | SHORT RURAL | Planned |  | 1 | 35 | 0.000147 | 4e-06 | N
18-12-18 | 11:15 | 813:89055 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
18-12-18 | 08:15 | 526:34639 | SHORT RURAL | Planned |  | 37 | 415 | 0.064628 | 0.000156 | N
19-12-18 | 09:05 | 801:74121 | LONG RURAL | Planned |  | 1 | 29 | 0.0102 | 0.000352 | N
19-12-18 | 09:00 | 807:74184 | SHORT RURAL | Planned |  | 2 | 30 | 0.000253 | 8e-06 | N
19-12-18 | 09:45 | 807:74184 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
19-12-18 | 08:35 | 801:74123 | SHORT RURAL | Planned |  | 59 | 135 | 0.033524 | 0.000248 | N
19-12-18 | 10:30 | 801:74121 | LONG RURAL | Planned |  | 1 | 30 | 0.010552 | 0.000352 | N
19-12-18 | 10:00 | 514:18137 | SHORT RURAL | Planned |  | 1 | 70 | 0.000295 | 4e-06 | N
19-12-18 | 10:40 | 810:74058 | SHORT RURAL | Planned |  | 1 | 65 | 0.000274 | 4e-06 | N
19-12-18 | 11:25 | 801:74121 | LONG RURAL | Planned |  | 2 | 55 | 0.038692 | 0.000703 | N
19-12-18 | 12:50 | 807:74179 | SHORT RURAL | Planned |  | 10 | 60 | 0.002525 | 4.2e-05 | N
19-12-18 | 13:25 | 514:18137 | SHORT RURAL | Planned |  | 2 | 55 | 0.000463 | 8e-06 | N
20-12-18 | 10:05 | 514:18137 | SHORT RURAL | Planned |  | 7 | 55 | 0.00162 | 2.9e-05 | N
20-12-18 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
31-12-18 | 06:55 | 265:81641 | URBAN | Planned |  | 1 | 515 | 0.000349 | 1e-06 | N
27-12-18 | 07:30 | 523:33508 | SHORT RURAL | Planned |  | 13 | 65 | 0.003556 | 5.5e-05 | N
27-12-18 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
27-12-18 | 09:40 | 807:74184 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
27-12-18 | 10:30 | 807:74184 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
27-12-18 | 11:10 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
28-12-18 | 08:00 | 806:82667 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
28-12-18 | 09:30 | 806:82667 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
28-12-18 | 11:35 | 806:82667 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
28-12-18 | 10:30 | 806:82667 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
02-01-19 | 07:33 | 243:80077 | SHORT RURAL | Planned |  | 17 | 22 | 0.001574 | 7.2e-05 | N
02-01-19 | 14:35 | 243:80077 | SHORT RURAL | Planned |  | 17 | 3 | 0.000215 | 7.2e-05 | N
02-01-19 | 11:25 | 802:82225 | SHORT RURAL | Planned |  | 1 | 85 | 0.000358 | 4e-06 | N
02-01-19 | 08:45 | 802:82225 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
02-01-19 | 10:00 | 802:82225 | SHORT RURAL | Planned |  | 1 | 95 | 0.0004 | 4e-06 | N
03-01-19 | 07:40 | 221:11898 | SHORT RURAL | Planned |  | 1 | 360 | 0.001515 | 4e-06 | N
03-01-19 | 08:35 | 814:82285 | SHORT RURAL | Planned |  | 2 | 55 | 0.000463 | 8e-06 | N
03-01-19 | 09:35 | 814:82285 | SHORT RURAL | Planned |  | 1 | 55 | 0.000231 | 4e-06 | N
03-01-19 | 09:05 | 814:82285 | SHORT RURAL | Planned |  | 3 | 85 | 0.001073 | 1.3e-05 | N
03-01-19 | 09:00 | 512:83743 | SHORT RURAL | Planned |  | 3 | 155 | 0.001957 | 1.3e-05 | N
04-01-19 | 08:48 | 223:14395 | SHORT RURAL | Planned |  | 5 | 392 | 0.008248 | 2.1e-05 | N
04-01-19 | 09:05 | 813:89062 | SHORT RURAL | Planned |  | 1 | 70 | 0.000295 | 4e-06 | N
04-01-19 | 08:50 | 813:89062 | SHORT RURAL | Planned |  | 1 | 70 | 0.000295 | 4e-06 | N
07-01-19 | 08:05 | 242:81539 | URBAN | Planned |  | 94 | 185 | 0.011782 | 6.4e-05 | N
07-01-19 | 08:05 | 232:33409 | SHORT RURAL | Planned |  | 101 | 185 | 0.078621 | 0.000425 | N
07-01-19 | 11:20 | 242:81539 | URBAN | Planned |  | 68 | 175 | 0.008062 | 4.6e-05 | N
07-01-19 | 08:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 35 | 0.012294 | 0.000351 | N
07-01-19 | 09:15 | 811:74234 | SHORT RURAL | Planned |  | 1 | 35 | 0.000147 | 4e-06 | N
07-01-19 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 65 | 0.022831 | 0.000351 | N
07-01-19 | 09:10 | 812:19072 | SHORT RURAL | Planned |  | 1 | 72 | 0.000303 | 4e-06 | N
07-01-19 | 10:40 | 811:74234 | SHORT RURAL | Planned |  | 1 | 25 | 0.000105 | 4e-06 | N
07-01-19 | 10:30 | 812:19072 | SHORT RURAL | Planned |  | 1 | 70 | 0.000295 | 4e-06 | N
07-01-19 | 11:30 | 813:89061 | LONG RURAL | Planned |  | 5 | 70 | 0.12294 | 0.001756 | N
07-01-19 | 10:20 | 813:89061 | LONG RURAL | Planned |  | 3 | 60 | 0.063224 | 0.001054 | N
07-01-19 | 12:15 | 811:74234 | SHORT RURAL | Planned |  | 1 | 25 | 0.000105 | 4e-06 | N
07-01-19 | 12:50 | 811:74234 | SHORT RURAL | Planned |  | 1 | 20 | 8.4e-05 | 4e-06 | N
07-01-19 | 12:00 | 812:19072 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
08-01-19 | 08:00 | 512:83733 | SHORT RURAL | Planned |  | 99 | 315 | 0.13122 | 0.000417 | N
08-01-19 | 08:00 | 801:74119 | URBAN | Planned |  | 33 | 180 | 0.004024 | 2.2e-05 | N
09-01-19 | 08:38 | 502:48010 | SHORT RURAL | Planned |  | 3 | 362 | 0.00457 | 1.3e-05 | N
09-01-19 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 34 | 425 | 0.060802 | 0.000143 | N
11-01-19 | 07:45 | 243:80083 | SHORT RURAL | Planned |  | 6 | 295 | 0.007448 | 2.5e-05 | N
11-01-19 | 07:00 | 243:80083 | SHORT RURAL | Planned |  | 12 | 387 | 0.019541 | 5e-05 | N
12-01-19 | 07:44 | 224:80328 | URBAN | Planned |  | 10 | 301 | 0.002039 | 7e-06 | N
11-01-19 | 11:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 60 | 0.021075 | 0.000351 | N
10-01-19 | 08:00 | 515:35197 | LONG RURAL | Planned |  | 21 | 390 | 2.8767 | 0.007376 | N
10-01-19 | 08:10 | 806:82662 | SHORT RURAL | Planned |  | 52 | 430 | 0.094086 | 0.000219 | N
11-01-19 | 08:00 | 515:35193 | SHORT RURAL | Planned |  | 3 | 345 | 0.004355 | 1.3e-05 | N
11-01-19 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 43 | 275 | 4.1535 | 0.015104 | N
11-01-19 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 65 | 0.022831 | 0.000351 | N
11-01-19 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 2 | 90 | 0.063224 | 0.000702 | N
11-01-19 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 1 | 90 | 0.031612 | 0.000351 | N
11-01-19 | 09:55 | 813:89061 | LONG RURAL | Planned |  | 1 | 35 | 0.012294 | 0.000351 | N
11-01-19 | 09:40 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015806 | 0.000351 | N
11-01-19 | 10:30 | 813:89061 | LONG RURAL | Planned |  | 2 | 30 | 0.021075 | 0.000702 | N
11-01-19 | 10:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 60 | 0.021075 | 0.000351 | N
11-01-19 | 11:10 | 813:89061 | LONG RURAL | Planned |  | 2 | 35 | 0.024587 | 0.000702 | N
11-01-19 | 10:35 | 813:89061 | LONG RURAL | Planned |  | 2 | 35 | 0.024587 | 0.000702 | N
11-01-19 | 11:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 55 | 0.019319 | 0.000351 | N
11-01-19 | 12:00 | 813:89061 | LONG RURAL | Planned |  | 1 | 35 | 0.012294 | 0.000351 | N
11-01-19 | 13:25 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015806 | 0.000351 | N
14-01-19 | 08:10 | 227:13020 | SHORT RURAL | Planned |  | 8 | 305 | 0.010264 | 3.4e-05 | N
14-01-19 | 08:50 | 511:29873 | URBAN | Planned |  | 2 | 100 | 0.000136 | 1e-06 | N
14-01-19 | 09:00 | 511:29873 | URBAN | Planned |  | 4 | 90 | 0.000244 | 3e-06 | N
14-01-19 | 11:05 | 511:29873 | URBAN | Planned |  | 2 | 50 | 6.8e-05 | 1e-06 | N
14-01-19 | 12:31 | 511:29873 | URBAN | Planned |  | 99 | 39 | 0.002617 | 6.7e-05 | N
14-01-19 | 13:00 | 528:83019 | SHORT RURAL | Planned |  | 3 | 15 | 0.000189 | 1.3e-05 | N
14-01-19 | 08:40 | 813:89055 | SHORT RURAL | Planned |  | 1 | 85 | 0.000358 | 4e-06 | N
14-01-19 | 10:25 | 512:83743 | SHORT RURAL | Planned |  | 2 | 25 | 0.00021 | 8e-06 | N
14-01-19 | 10:20 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
14-01-19 | 11:30 | 807:74184 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
14-01-19 | 09:30 | 807:74184 | SHORT RURAL | Planned |  | 3 | 30 | 0.000379 | 1.3e-05 | N
14-01-19 | 08:30 | 807:74184 | SHORT RURAL | Planned |  | 2 | 45 | 0.000379 | 8e-06 | N
14-01-19 | 08:50 | 813:89055 | SHORT RURAL | Planned |  | 10 | 165 | 0.006941 | 4.2e-05 | N
15-01-19 | 08:00 | 813:89061 | LONG RURAL | Planned |  | 5 | 245 | 0.42997 | 0.001755 | N
15-01-19 | 08:40 | 513:48059 | SHORT RURAL | Planned |  | 24 | 220 | 0.022212 | 0.000101 | N
14-01-19 | 19:15 | 224:80341 | URBAN | Planned |  | 1 | 675 | 0.000457 | 1e-06 | N
15-01-19 | 08:15 | 270:83586 | URBAN | Planned |  | 92 | 353 | 0.022034 | 6.2e-05 | N
15-01-19 | 10:05 | 222:33597 | URBAN | Planned |  | 76 | 257 | 0.013252 | 5.2e-05 | N
15-01-19 | 08:30 | 508:82580 | SHORT RURAL | Planned |  | 65 | 305 | 0.083399 | 0.000273 | N
15-01-19 | 08:25 | 512:83743 | SHORT RURAL | Planned |  | 2 | 96 | 0.000808 | 8e-06 | N
15-01-19 | 10:10 | 512:83743 | SHORT RURAL | Planned |  | 3 | 64 | 0.000808 | 1.3e-05 | N
15-01-19 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 3 | 170 | 0.002145 | 1.3e-05 | N
15-01-19 | 08:30 | 814:82289 | SHORT RURAL | Planned |  | 4 | 210 | 0.003534 | 1.7e-05 | N
15-01-19 | 12:05 | 811:74234 | SHORT RURAL | Planned |  | 1 | 135 | 0.000568 | 4e-06 | N
16-01-19 | 08:00 | 502:48010 | SHORT RURAL | Planned |  | 5 | 220 | 0.004627 | 2.1e-05 | N
16-01-19 | 08:15 | 813:89061 | LONG RURAL | Planned |  | 2 | 75 | 0.05265 | 0.000702 | N
16-01-19 | 08:00 | 807:74179 | SHORT RURAL | Planned |  | 1 | 65 | 0.000273 | 4e-06 | N
16-01-19 | 09:10 | 807:74179 | SHORT RURAL | Planned |  | 1 | 80 | 0.000337 | 4e-06 | N
16-01-19 | 08:00 | 813:89061 | LONG RURAL | Planned |  | 5 | 190 | 0.33345 | 0.001755 | N
16-01-19 | 09:45 | 813:89055 | SHORT RURAL | Planned |  | 2 | 55 | 0.000463 | 8e-06 | N
16-01-19 | 10:45 | 813:89055 | SHORT RURAL | Planned |  | 1 | 55 | 0.000231 | 4e-06 | N
18-01-19 | 13:10 | ZN10998:PA10 | URBAN | Planned |  | 257 | 206 | 0.035955 | 0.000175 | N
18-01-19 | 20:00 | 235:8684 | SHORT RURAL | Planned |  | 2 | 430 | 0.003619 | 8e-06 | N
17-01-19 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 11 | 220 | 0.01018 | 4.6e-05 | N
18-01-19 | 08:20 | 232:11455 | SHORT RURAL | Planned |  | 14 | 550 | 0.032398 | 5.9e-05 | N
17-01-19 | 10:35 | 810:74058 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
17-01-19 | 09:45 | 810:74058 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
17-01-19 | 08:50 | 810:74058 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
17-01-19 | 07:45 | 810:74058 | SHORT RURAL | Planned |  | 1 | 55 | 0.000231 | 4e-06 | N
17-01-19 | 09:55 | 813:89061 | LONG RURAL | Planned |  | 1 | 25 | 0.008775 | 0.000351 | N
17-01-19 | 09:20 | 813:89061 | LONG RURAL | Planned |  | 1 | 25 | 0.008775 | 0.000351 | N
17-01-19 | 08:47 | 813:89061 | LONG RURAL | Planned |  | 2 | 28 | 0.019656 | 0.000702 | N
18-01-19 | 08:14 | 523:33509 | URBAN | Planned |  | 68 | 21 | 0.00097 | 4.6e-05 | N
18-01-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 5 | 210 | 0.36855 | 0.001755 | N
18-01-19 | 08:35 | 801:74121 | LONG RURAL | Planned |  | 7 | 525 | 1.2899 | 0.002457 | N
22-01-19 | 08:30 | 522:83124 | URBAN | Planned |  | 33 | 420 | 0.009402 | 2.2e-05 | N
21-01-19 | 10:00 | 243:80075 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
21-01-19 | 09:10 | 810:74050 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
21-01-19 | 10:00 | 813:89062 | SHORT RURAL | Planned |  | 3 | 30 | 0.000379 | 1.3e-05 | N
21-01-19 | 09:15 | 515:35192 | SHORT RURAL | Planned |  | 1 | 65 | 0.000273 | 4e-06 | N
21-01-19 | 10:20 | 810:74050 | SHORT RURAL | Planned |  | 1 | 50 | 0.00021 | 4e-06 | N
21-01-19 | 10:30 | 515:35192 | SHORT RURAL | Planned |  | 1 | 55 | 0.000231 | 4e-06 | N
21-01-19 | 09:50 | 801:74121 | LONG RURAL | Planned |  | 1 | 115 | 0.040365 | 0.000351 | N
21-01-19 | 11:25 | 810:74050 | SHORT RURAL | Planned |  | 1 | 35 | 0.000147 | 4e-06 | N
21-01-19 | 12:22 | 813:89062 | SHORT RURAL | Planned |  | 2 | 38 | 0.00032 | 8e-06 | N
21-01-19 | 11:41 | 813:89062 | SHORT RURAL | Planned |  | 1 | 31 | 0.00013 | 4e-06 | N
21-01-19 | 11:01 | 813:89062 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
21-01-19 | 12:00 | 801:74121 | LONG RURAL | Planned |  | 4 | 65 | 0.09126 | 0.001404 | N
21-01-19 | 13:05 | 810:74050 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
22-01-19 | 16:53 | ZN12630:PA3 | SHORT RURAL | Planned |  | 71 | 182 | 0.054448 | 0.000299 | N
22-01-19 | 11:05 | 528:83019 | SHORT RURAL | Planned |  | 2 | 65 | 0.000547 | 8e-06 | N
22-01-19 | 08:45 | 511:29873 | URBAN | Planned |  | 3 | 65 | 0.000132 | 2e-06 | N
22-01-19 | 08:40 | 511:29873 | URBAN | Planned |  | 3 | 95 | 0.000193 | 2e-06 | N
22-01-19 | 08:43 | 511:29873 | URBAN | Planned |  | 1 | 52 | 3.5e-05 | 1e-06 | N
22-01-19 | 10:15 | 511:29878 | SHORT RURAL | Planned |  | 1 | 53 | 0.000223 | 4e-06 | N
22-01-19 | 10:30 | 511:29873 | URBAN | Planned |  | 1 | 65 | 4.4e-05 | 1e-06 | N
22-01-19 | 12:34 | 511:29878 | SHORT RURAL | Planned |  | 1 | 61 | 0.000257 | 4e-06 | N
22-01-19 | 08:45 | 507:80923 | SHORT RURAL | Planned |  | 47 | 510 | 0.10081 | 0.000198 | N
22-01-19 | 07:35 | 807:74180 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
22-01-19 | 08:30 | 807:74180 | SHORT RURAL | Planned |  | 1 | 35 | 0.000147 | 4e-06 | N
22-01-19 | 09:20 | 807:74180 | SHORT RURAL | Planned |  | 1 | 40 | 0.000168 | 4e-06 | N
22-01-19 | 08:10 | 801:74121 | LONG RURAL | Planned |  | 1 | 100 | 0.0351 | 0.000351 | N
22-01-19 | 11:15 | 801:74121 | LONG RURAL | Planned |  | 1 | 60 | 0.02106 | 0.000351 | N
22-01-19 | 10:15 | 801:74121 | LONG RURAL | Planned |  | 1 | 45 | 0.015795 | 0.000351 | N
22-01-19 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 207 | 345 | 0.30036 | 0.000871 | N
23-01-19 | 08:35 | 515:35197 | LONG RURAL | Planned |  | 33 | 419 | 4.855 | 0.011587 | N
23-01-19 | 08:30 | 243:80077 | SHORT RURAL | Planned |  | 17 | 420 | 0.03003 | 7.2e-05 | N
23-01-19 | 08:40 | 522:83126 | SHORT RURAL | Planned |  | 10 | 40 | 0.001682 | 4.2e-05 | N
23-01-19 | 08:20 | 511:29878 | SHORT RURAL | Planned |  | 2 | 40 | 0.000336 | 8e-06 | N
23-01-19 | 09:20 | 511:29873 | URBAN | Planned |  | 3 | 35 | 7.1e-05 | 2e-06 | N
23-01-19 | 10:15 | 511:29873 | URBAN | Planned |  | 3 | 43 | 8.7e-05 | 2e-06 | N
23-01-19 | 08:45 | 526:34641 | SHORT RURAL | Planned |  | 50 | 160 | 0.033647 | 0.00021 | N
23-01-19 | 10:55 | 522:83126 | SHORT RURAL | Planned |  | 1 | 45 | 0.000189 | 4e-06 | N
23-01-19 | 08:35 | 233:82819 | SHORT RURAL | Planned |  | 20 | 210 | 0.017665 | 8.4e-05 | N
23-01-19 | 10:15 | 511:29878 | SHORT RURAL | Planned |  | 1 | 60 | 0.000252 | 4e-06 | N
23-01-19 | 12:00 | 522:83126 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
23-01-19 | 12:30 | 511:29878 | SHORT RURAL | Planned |  | 2 | 45 | 0.000379 | 8e-06 | N
23-01-19 | 12:40 | 511:29878 | SHORT RURAL | Planned |  | 6 | 38 | 0.000959 | 2.5e-05 | N
23-01-19 | 08:55 | 810:74054 | LONG RURAL | Planned |  | 16 | 220 | 1.236 | 0.005618 | N
24-01-19 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 24 | 405 | 0.040878 | 0.000101 | N
24-01-19 | 08:35 | 508:82580 | SHORT RURAL | Planned |  | 57 | 389 | 0.09325 | 0.00024 | N
24-01-19 | 08:00 | 526:34639 | SHORT RURAL | Planned |  | 25 | 530 | 0.055724 | 0.000105 | N
31-01-19 | 10:20 | 238:34140 | SHORT RURAL | Planned |  | 39 | 490 | 0.079961 | 0.000163 | N
25-01-19 | 08:13 | 515:35193 | SHORT RURAL | Planned |  | 5 | 156 | 0.00328 | 2.1e-05 | N
25-01-19 | 08:00 | 227:13020 | SHORT RURAL | Planned |  | 16 | 420 | 0.028261 | 6.7e-05 | N
28-01-19 | 17:10 | 202:34259 | URBAN | Planned |  | 5 | 104 | 0.000352 | 3e-06 | N
25-01-19 | 08:40 | 415:33884 | URBAN | Planned |  | 1 | 98 | 6.6e-05 | 1e-06 | N
25-01-19 | 08:06 | 514:18137 | SHORT RURAL | Planned |  | 4 | 64 | 0.001077 | 1.7e-05 | N
25-01-19 | 08:40 | 814:82291 | SHORT RURAL | Planned |  | 40 | 230 | 0.038691 | 0.000168 | N
25-01-19 | 09:05 | 813:89055 | SHORT RURAL | Planned |  | 1 | 195 | 0.00082 | 4e-06 | N
25-01-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 5 | 265 | 0.46524 | 0.001756 | N
25-01-19 | 08:00 | 515:35197 | LONG RURAL | Planned |  | 21 | 390 | 2.8757 | 0.007374 | N
25-01-19 | 10:00 | 514:18137 | SHORT RURAL | Planned |  | 2 | 50 | 0.000421 | 8e-06 | N
25-01-19 | 10:35 | 812:19071 | SHORT RURAL | Planned |  | 1 | 65 | 0.000273 | 4e-06 | N
29-01-19 | 08:55 | 813:89055 | SHORT RURAL | Planned |  | 7 | 75 | 0.002196 | 2.9e-05 | N
29-01-19 | 08:30 | 512:83743 | SHORT RURAL | Planned |  | 7 | 112 | 0.00328 | 2.9e-05 | N
29-01-19 | 10:25 | 813:89055 | SHORT RURAL | Planned |  | 3 | 55 | 0.00069 | 1.3e-05 | N
29-01-19 | 11:30 | 813:89055 | SHORT RURAL | Planned |  | 2 | 50 | 0.000418 | 8e-06 | N
30-01-19 | 08:12 | 220:8692 | URBAN | Planned |  | 76 | 132 | 0.006799 | 5.2e-05 | N
30-01-19 | 07:25 | 227:13015 | SHORT RURAL | Planned |  | 5 | 290 | 0.006066 | 2.1e-05 | N
30-01-19 | 08:30 | 270:83584 | URBAN | Planned |  | 66 | 420 | 0.018788 | 4.5e-05 | N
30-01-19 | 09:20 | 242:81533 | SHORT RURAL | Planned |  | 1 | 110 | 0.00046 | 4e-06 | N
30-01-19 | 08:00 | 522:83124 | URBAN | Planned |  | 11 | 475 | 0.003541 | 7e-06 | N
30-01-19 | 10:00 | 813:89062 | SHORT RURAL | Planned |  | 1 | 71 | 0.000297 | 4e-06 | N
30-01-19 | 08:25 | 813:89062 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
30-01-19 | 09:20 | 813:89062 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
30-01-19 | 07:45 | 810:74054 | LONG RURAL | Planned |  | 2 | 305 | 0.21404 | 0.000702 | N
30-01-19 | 09:40 | 814:82289 | SHORT RURAL | Planned |  | 3 | 55 | 0.00069 | 1.3e-05 | N
30-01-19 | 11:10 | 814:82289 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
30-01-19 | 08:00 | 515:35193 | SHORT RURAL | Planned |  | 12 | 390 | 0.019579 | 5e-05 | N
31-01-19 | 09:08 | 229:34983 | SHORT RURAL | Planned |  | 3 | 169 | 0.002121 | 1.3e-05 | N
31-01-19 | 08:20 | 238:34141 | SHORT RURAL | Planned |  | 15 | 265 | 0.016632 | 6.3e-05 | N
31-01-19 | 08:31 | 233:82812 | SHORT RURAL | Planned |  | 2 | 279 | 0.002335 | 8e-06 | N
31-01-19 | 08:05 | 801:74121 | LONG RURAL | Planned |  | 1 | 75 | 0.026316 | 0.000351 | N
31-01-19 | 08:33 | 807:74180 | SHORT RURAL | Planned |  | 2 | 47 | 0.000393 | 8e-06 | N
31-01-19 | 08:50 | 801:74123 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
31-01-19 | 08:45 | 801:74121 | LONG RURAL | Planned |  | 3 | 60 | 0.063158 | 0.001053 | N
31-01-19 | 09:30 | 807:74180 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
31-01-19 | 09:25 | 813:89062 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
31-01-19 | 09:40 | 801:74121 | LONG RURAL | Planned |  | 2 | 30 | 0.021053 | 0.000702 | N
31-01-19 | 10:00 | 801:74123 | SHORT RURAL | Planned |  | 1 | 30 | 0.000126 | 4e-06 | N
31-01-19 | 10:25 | 807:74180 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
31-01-19 | 10:20 | 814:82285 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
31-01-19 | 10:55 | 801:74123 | SHORT RURAL | Planned |  | 1 | 25 | 0.000105 | 4e-06 | N
31-01-19 | 10:30 | 812:19072 | SHORT RURAL | Planned |  | 3 | 40 | 0.000502 | 1.3e-05 | N
31-01-19 | 10:35 | 814:82289 | SHORT RURAL | Planned |  | 2 | 55 | 0.00046 | 8e-06 | N
31-01-19 | 11:20 | 814:82285 | SHORT RURAL | Planned |  | 2 | 50 | 0.000418 | 8e-06 | N
31-01-19 | 12:25 | 814:82285 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
31-01-19 | 12:00 | 813:89062 | SHORT RURAL | Planned |  | 1 | 60 | 0.000251 | 4e-06 | N
01-02-19 | 08:50 | 512:83743 | SHORT RURAL | Planned |  | 19 | 405 | 0.032198 | 8e-05 | N
01-02-19 | 08:00 | 515:35193 | SHORT RURAL | Planned |  | 26 | 420 | 0.045692 | 0.000109 | N
01-02-19 | 10:40 | 233:82812 | SHORT RURAL | Planned |  | 2 | 145 | 0.001213 | 8e-06 | N
01-02-19 | 08:00 | 508:82579 | SHORT RURAL | Planned |  | 38 | 470 | 0.074731 | 0.000159 | N
01-02-19 | 08:15 | 512:83743 | SHORT RURAL | Planned |  | 9 | 344 | 0.012955 | 3.8e-05 | N
01-02-19 | 08:10 | 801:74121 | LONG RURAL | Planned |  | 1 | 50 | 0.017544 | 0.000351 | N
01-02-19 | 10:25 | 811:74234 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
01-02-19 | 09:40 | 811:74234 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
01-02-19 | 08:35 | 811:74234 | SHORT RURAL | Planned |  | 4 | 55 | 0.000921 | 1.7e-05 | N
01-02-19 | 11:10 | 811:74234 | SHORT RURAL | Planned |  | 2 | 40 | 0.000335 | 8e-06 | N
01-02-19 | 09:45 | 806:82662 | SHORT RURAL | Planned |  | 4 | 75 | 0.001255 | 1.7e-05 | N
01-02-19 | 11:10 | 801:74121 | LONG RURAL | Planned |  | 2 | 60 | 0.042105 | 0.000702 | N
01-02-19 | 10:00 | 801:74121 | LONG RURAL | Planned |  | 4 | 55 | 0.077193 | 0.001404 | N
06-02-19 | 07:00 | ZN35400:PA73 | URBAN | Planned |  | 74 | 840 | 0.042122 | 5e-05 | N
04-02-19 | 08:22 | 239:82129 | SHORT RURAL | Planned |  | 111 | 338 | 0.15695 | 0.000464 | N
04-02-19 | 08:35 | 513:48059 | SHORT RURAL | Planned |  | 60 | 270 | 0.06777 | 0.000251 | N
04-02-19 | 09:48 | 508:82579 | SHORT RURAL | Planned |  | 4 | 75 | 0.001255 | 1.7e-05 | N
04-02-19 | 13:01 | 508:82579 | SHORT RURAL | Planned |  | 2 | 56 | 0.000469 | 8e-06 | N
04-02-19 | 08:00 | 801:74121 | LONG RURAL | Planned |  | 1 | 45 | 0.015795 | 0.000351 | N
04-02-19 | 10:35 | 801:74121 | LONG RURAL | Planned |  | 1 | 35 | 0.012285 | 0.000351 | N
04-02-19 | 10:35 | 810:74054 | LONG RURAL | Planned |  | 1 | 35 | 0.012285 | 0.000351 | N
04-02-19 | 09:50 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.01404 | 0.000351 | N
04-02-19 | 08:50 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.01404 | 0.000351 | N
04-02-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.01404 | 0.000351 | N
04-02-19 | 09:30 | 812:19072 | SHORT RURAL | Planned |  | 2 | 210 | 0.001757 | 8e-06 | N
05-02-19 | 08:00 | 526:34639 | SHORT RURAL | Planned |  | 31 | 486 | 0.063026 | 0.00013 | N
05-02-19 | 23:05 | 813:89065 | SHORT RURAL | Planned |  | 22 | 319 | 0.029359 | 9.2e-05 | N
05-02-19 | 07:40 | 509:33395 | LONG RURAL | Planned |  | 33 | 467 | 5.4112 | 0.011587 | N
05-02-19 | 09:15 | 233:82819 | SHORT RURAL | Planned |  | 100 | 550 | 0.23008 | 0.000418 | N
05-02-19 | 08:00 | 528:83019 | SHORT RURAL | Planned |  | 42 | 165 | 0.028991 | 0.000176 | N
05-02-19 | 08:30 | 513:48056 | SHORT RURAL | Planned |  | 6 | 145 | 0.00364 | 2.5e-05 | N
05-02-19 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 49 | 387 | 0.079329 | 0.000205 | N
05-02-19 | 08:30 | 806:82662 | SHORT RURAL | Planned |  | 58 | 405 | 0.098267 | 0.000243 | N
05-02-19 | 08:30 | 806:82662 | SHORT RURAL | Planned |  | 24 | 405 | 0.040662 | 0.0001 | N
06-02-19 | 08:55 | 224:80340 | SHORT RURAL | Planned |  | 92 | 330 | 0.12701 | 0.000385 | N
06-02-19 | 08:00 | 256:80632 | URBAN | Planned |  | 116 | 565 | 0.044413 | 7.9e-05 | N
06-02-19 | 09:11 | 522:83132 | SHORT RURAL | Planned |  | 53 | 379 | 0.084035 | 0.000222 | N
06-02-19 | 08:00 | 508:82580 | SHORT RURAL | Planned |  | 57 | 475 | 0.11327 | 0.000238 | N
06-02-19 | 08:40 | 520:48172 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
06-02-19 | 08:45 | 515:35198 | SHORT RURAL | Planned |  | 4 | 75 | 0.001255 | 1.7e-05 | N
06-02-19 | 08:30 | 802:82220 | SHORT RURAL | Planned |  | 41 | 330 | 0.056604 | 0.000172 | N
06-02-19 | 08:07 | 520:48172 | SHORT RURAL | Planned |  | 45 | 408 | 0.07681 | 0.000188 | N
06-02-19 | 10:20 | 520:48172 | SHORT RURAL | Planned |  | 5 | 55 | 0.00115 | 2.1e-05 | N
06-02-19 | 11:30 | 515:35197 | LONG RURAL | Planned |  | 3 | 40 | 0.042135 | 0.001053 | N
06-02-19 | 13:15 | 512:83743 | SHORT RURAL | Planned |  | 1 | 60 | 0.000251 | 4e-06 | N
06-02-19 | 08:10 | 509:33395 | LONG RURAL | Planned |  | 18 | 490 | 3.0969 | 0.00632 | N
07-02-19 | 08:00 | 243:80084 | SHORT RURAL | Planned |  | 40 | 495 | 0.082835 | 0.000167 | N
08-02-19 | 08:00 | 243:80083 | SHORT RURAL | Planned |  | 14 | 480 | 0.028116 | 5.9e-05 | N
08-02-19 | 21:40 | 205:12208 | URBAN | Planned |  | 3 | 115 | 0.000234 | 2e-06 | N
09-02-19 | 10:00 | 240:34843 | URBAN | Planned |  | 12 | 240 | 0.001952 | 8e-06 | N
10-02-19 | 08:10 | 243:80077 | SHORT RURAL | Planned |  | 125 | 410 | 0.21441 | 0.000523 | N
07-02-19 | 07:35 | 509:33399 | SHORT RURAL | Planned |  | 40 | 465 | 0.077815 | 0.000167 | N
08-02-19 | 09:35 | 232:33407 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
08-02-19 | 11:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 305 | 0.10709 | 0.000351 | N
07-02-19 | 08:10 | 516:48067 | SHORT RURAL | Planned |  | 8 | 170 | 0.00569 | 3.3e-05 | N
07-02-19 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 13 | 295 | 0.016044 | 5.4e-05 | N
07-02-19 | 13:00 | 520:48172 | SHORT RURAL | Planned |  | 2 | 118 | 0.000987 | 8e-06 | N
08-02-19 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 84 | 245 | 0.086106 | 0.000351 | N
08-02-19 | 08:00 | 515:35192 | SHORT RURAL | Planned |  | 5 | 450 | 0.009414 | 2.1e-05 | N
11-02-19 | 10:20 | 801:74121 | LONG RURAL | Planned |  | 1 | 35 | 0.012289 | 0.000351 | N
11-02-19 | 08:40 | 801:74121 | LONG RURAL | Planned |  | 4 | 90 | 0.1264 | 0.001404 | N
11-02-19 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 6 | 340 | 0.71629 | 0.002107 | N
12-02-19 | 09:30 | 810:74054 | LONG RURAL | Planned |  | 1 | 30 | 0.010537 | 0.000351 | N
12-02-19 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 1 | 75 | 0.026344 | 0.000351 | N
12-02-19 | 08:35 | 235:2120 | SHORT RURAL | Planned |  | 21 | 215 | 0.018889 | 8.8e-05 | N
12-02-19 | 08:05 | 810:74054 | LONG RURAL | Planned |  | 1 | 33 | 0.011591 | 0.000351 | N
12-02-19 | 08:45 | 810:74054 | LONG RURAL | Planned |  | 1 | 35 | 0.012294 | 0.000351 | N
12-02-19 | 08:20 | 813:89055 | SHORT RURAL | Planned |  | 1 | 15 | 6.3e-05 | 4e-06 | N
12-02-19 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 60 | 0.021075 | 0.000351 | N
12-02-19 | 10:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015806 | 0.000351 | N
12-02-19 | 10:20 | 812:19071 | SHORT RURAL | Planned |  | 18 | 85 | 0.006401 | 7.5e-05 | N
12-02-19 | 11:00 | 813:89055 | SHORT RURAL | Planned |  | 1 | 70 | 0.000293 | 4e-06 | N
12-02-19 | 10:00 | 813:89055 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
12-02-19 | 11:40 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017562 | 0.000351 | N
12-02-19 | 08:40 | 520:48172 | SHORT RURAL | Planned |  | 24 | 275 | 0.027613 | 0.0001 | N
12-02-19 | 09:00 | 515:35197 | LONG RURAL | Planned |  | 5 | 125 | 0.21953 | 0.001756 | N
07-10-18 | 06:00 | ZN263:PA33 34KLM | CBD | Planned |  | 11 | 810 | 0.29272 | 0.000361 | N
07-10-18 | 07:42 | ZN263:PA33 34KLM | CBD | Planned |  | 2 | 708 | 0.046519 | 6.6e-05 | N
07-10-18 | 07:40 | ZN263:PA33 34KLM | CBD | Planned |  | 19 | 710 | 0.44318 | 0.000624 | N
07-10-18 | 06:00 | ZN263:PA33 34KLM | CBD | Planned |  | 1 | 810 | 0.026611 | 3.3e-05 | N
07-10-18 | 06:00 | ZN263:PA33 34KLM | CBD | Planned |  | 8 | 810 | 0.21288 | 0.000263 | N
07-10-18 | 07:44 | ZN263:PA33 34KLM | CBD | Planned |  | 7 | 706 | 0.16236 | 0.00023 | N
07-10-18 | 06:00 | ZN263:PA33 34KLM | CBD | Planned |  | 8 | 720 | 0.18923 | 0.000263 | N
07-10-18 | 07:30 | ZN14143:PA12 | SHORT RURAL | Planned |  | 1 | 650 | 0.002735 | 4e-06 | N
07-10-18 | 09:50 | ZN1290:PA13 | URBAN | Planned |  | 2 | 220 | 0.000299 | 1e-06 | N
08-10-18 | 07:40 | ZN5868:PA14 | URBAN | Planned |  | 48 | 520 | 0.016977 | 3.3e-05 | N
08-10-18 | 08:00 | ZN80:PA37 | URBAN | Planned |  | 35 | 420 | 0.009999 | 2.4e-05 | N
08-10-18 | 08:00 | ZN2310:PA54 | URBAN | Planned |  | 74 | 420 | 0.02114 | 5e-05 | N
08-10-18 | 08:00 | ZN2310:PA55 | URBAN | Planned |  | 41 | 420 | 0.011713 | 2.8e-05 | N
09-10-18 | 01:00 | ZN8700:PA65 66GHJ | CBD | Planned |  | 14 | 230 | 0.10579 | 0.00046 | N
09-10-18 | 07:00 | ZN35600:PA14 | URBAN | Planned |  | 22 | 630 | 0.009427 | 1.5e-05 | N
09-10-18 | 07:30 | ZN262:PA14 | URBAN | Planned |  | 2 | 15 | 2e-05 | 1e-06 | N
09-10-18 | 08:00 | ZN2466:PA5 | URBAN | Planned |  | 99 | 735 | 0.049494 | 6.7e-05 | N
09-10-18 | 08:15 | ZN2568:PA14 | URBAN | Planned |  | 64 | 345 | 0.015018 | 4.4e-05 | N
09-10-18 | 08:30 | ZN36100:PA16 | URBAN | Planned |  | 57 | 380 | 0.014733 | 3.9e-05 | N
09-10-18 | 08:05 | ZN2400:PA18 | SHORT RURAL | Planned |  | 46 | 555 | 0.10741 | 0.000194 | N
10-10-18 | 07:45 | ZN2835:PA35 | URBAN | Planned |  | 72 | 615 | 0.030119 | 4.9e-05 | N
10-10-18 | 08:45 | ZN3672:PA6 | URBAN | Planned |  | 98 | 355 | 0.023664 | 6.7e-05 | N
11-10-18 | 08:00 | ZN36100:PA1 | URBAN | Planned |  | 91 | 540 | 0.033425 | 6.2e-05 | N
11-10-18 | 08:00 | ZN36100:PA16 | URBAN | Planned |  | 57 | 480 | 0.01861 | 3.9e-05 | N
11-10-18 | 08:00 | ZN36100:PA13 | URBAN | Planned |  | 32 | 450 | 0.009795 | 2.2e-05 | N
11-10-18 | 09:00 | ZN36800:PA43 | URBAN | Planned |  | 69 | 155 | 0.007275 | 4.7e-05 | N
12-10-18 | 07:30 | ZN12650:PA3 | URBAN | Planned |  | 11 | 600 | 0.00449 | 7e-06 | N
12-10-18 | 07:30 | ZN35500:PA27 | URBAN | Planned |  | 38 | 480 | 0.012409 | 2.6e-05 | N
12-10-18 | 21:30 | ZN847:PA15 | URBAN | Planned |  | 45 | 330 | 0.010102 | 3.1e-05 | N
13-10-18 | 08:30 | ZN263:PA33 34ABC | CBD | Planned |  | 67 | 575 | 1.2655 | 0.002201 | N
13-10-18 | 09:30 | ZN262:PA7 | URBAN | Planned |  | 28 | 315 | 0.005999 | 1.9e-05 | N
13-10-18 | 10:08 | ZN35800:PA21 | URBAN | Planned |  | 2 | 212 | 0.000288 | 1e-06 | N
14-10-18 | 07:30 | ZN8100:PA17 | URBAN | Planned |  | 2 | 480 | 0.000653 | 1e-06 | N
14-10-18 | 07:30 | ZN8100:PA9 | URBAN | Planned |  | 6 | 480 | 0.00196 | 4e-06 | N
14-10-18 | 07:30 | ZN2568:PA25 | URBAN | Planned |  | 1 | 480 | 0.000327 | 1e-06 | N
14-10-18 | 07:30 | ZN2568:PA25 | URBAN | Planned |  | 6 | 480 | 0.00196 | 4e-06 | N
14-10-18 | 07:30 | ZN8100:PA2 | URBAN | Planned |  | 4 | 480 | 0.001307 | 3e-06 | N
14-10-18 | 08:45 | ZN3288:PA45 46GHJ | CBD | Planned |  | 5 | 165 | 0.027093 | 0.000164 | N
14-10-18 | 10:30 | ZN262:PA14 | URBAN | Planned |  | 2 | 21 | 2.9e-05 | 1e-06 | N
15-10-18 | 08:00 | ZN10995:PA1 | URBAN | Planned |  | 90 | 450 | 0.027563 | 6.1e-05 | N
15-10-18 | 20:55 | ZN7900:PA11 | URBAN | Planned |  | 47 | 425 | 0.013594 | 3.2e-05 | N
15-10-18 | 21:00 | ZN630:PA31 | URBAN | Planned |  | 4 | 420 | 0.001143 | 3e-06 | N
15-10-18 | 21:30 | ZN8700:PA61 62GHJ | CBD | Planned |  | 13 | 195 | 0.083248 | 0.000427 | N
16-10-18 | 07:30 | ZN10993:PA26 | URBAN | Planned |  | 38 | 180 | 0.004655 | 2.6e-05 | N
16-10-18 | 08:00 | ZN2400:PA26 | URBAN | Planned |  | 31 | 540 | 0.011393 | 2.1e-05 | N
16-10-18 | 08:00 | ZN9252:PA31 | URBAN | Planned |  | 83 | 450 | 0.025419 | 5.6e-05 | N
16-10-18 | 16:25 | ZN3672:PA37 | URBAN | Planned |  | 178 | 50 | 0.006057 | 0.000121 | N
16-10-18 | 21:30 | ZN36100:PA1 | URBAN | Planned |  | 35 | 450 | 0.010719 | 2.4e-05 | N
16-10-18 | 21:30 | ZN36100:PA16 | URBAN | Planned |  | 56 | 450 | 0.01715 | 3.8e-05 | N
17-10-18 | 09:00 | ZN8000:PA38 | URBAN | Planned |  | 68 | 480 | 0.022214 | 4.6e-05 | N
17-10-18 | 07:35 | ZN36000:PA12 | URBAN | Planned |  | 2 | 685 | 0.000932 | 1e-06 | N
18-10-18 | 10:30 | ZN15008:PA1 | URBAN | Planned |  | 94 | 225 | 0.014394 | 6.4e-05 | N
18-10-18 | 09:10 | ZN36800:PA49 | URBAN | Planned |  | 70 | 140 | 0.00667 | 4.8e-05 | N
18-10-18 | 10:00 | ZN10999:PA25 | URBAN | Planned |  | 5 | 1,050 | 0.003573 | 3e-06 | N
18-10-18 | 19:30 | ZN180:PA33 | URBAN | Planned |  | 80 | 390 | 0.021234 | 5.4e-05 | N
18-10-18 | 19:30 | ZN180:PA33 | URBAN | Planned |  | 64 | 390 | 0.016987 | 4.4e-05 | N
18-10-18 | 22:30 | ZN965:PA3 | URBAN | Planned |  | 43 | 390 | 0.011413 | 2.9e-05 | N
18-10-18 | 23:02 | ZN9900:PA14 | URBAN | Planned |  | 56 | 8 | 0.000305 | 3.8e-05 | N
19-10-18 | 10:30 | ZN4545:PA21 | URBAN | Planned |  | 26 | 280 | 0.004955 | 1.8e-05 | N
19-10-18 | 11:10 | ZN1610:PA26 | URBAN | Planned |  | 1 | 320 | 0.000218 | 1e-06 | N
19-10-18 | 22:00 | ZN2635:PA43 | SHORT RURAL | Planned |  | 2 | 360 | 0.003024 | 8e-06 | N
20-10-18 | 07:15 | ZN4990:PA53 54GHJ | CBD | Planned |  | 42 | 435 | 0.6 | 0.001379 | N
20-10-18 | 10:35 | ZN3672:PA42 | URBAN | Planned |  | 2 | 15 | 2e-05 | 1e-06 | N
21-10-18 | 07:30 | ZN3922:PA29 | URBAN | Planned |  | 1 | 745 | 0.000507 | 1e-06 | N
21-10-18 | 08:50 | ZN3672:PA42 | URBAN | Planned |  | 13 | 265 | 0.002345 | 9e-06 | N
22-10-18 | 07:50 | ZN35900:PA2 | URBAN | Planned |  | 44 | 355 | 0.010631 | 3e-05 | N
22-10-18 | 07:30 | ZN15008:PA1 | URBAN | Planned |  | 21 | 480 | 0.00686 | 1.4e-05 | N
22-10-18 | 10:00 | ZN9700:PA18 | URBAN | Planned |  | 15 | 120 | 0.001225 | 1e-05 | N
22-10-18 | 10:40 | ZN36100:PA19 | URBAN | Planned |  | 76 | 225 | 0.011638 | 5.2e-05 | N
22-10-18 | 10:40 | ZN36100:PA19 | URBAN | Planned |  | 64 | 225 | 0.009801 | 4.4e-05 | N
23-10-18 | 09:30 | ZN188:PA26 | URBAN | Planned |  | 119 | 2 | 0.000162 | 8.1e-05 | N
23-10-18 | 09:45 | ZN2568:PA39 | URBAN | Planned |  | 89 | 465 | 0.028167 | 6.1e-05 | N
23-10-18 | 08:06 | ZN9245:PA13 | URBAN | Planned |  | 53 | 459 | 0.016557 | 3.6e-05 | N
23-10-18 | 10:30 | ZN10999:PA7 | URBAN | Planned |  | 127 | 10 | 0.000864 | 8.6e-05 | N
24-10-18 | 09:30 | ZN2196:PA25 | URBAN | Planned |  | 68 | 240 | 0.011107 | 4.6e-05 | N
24-10-18 | 08:00 | ZN630:PA34 | URBAN | Planned |  | 5 | 450 | 0.001531 | 3e-06 | N
24-10-18 | 08:30 | ZN9245:PA3 | SHORT RURAL | Planned |  | 9 | 405 | 0.015311 | 3.8e-05 | N
24-10-18 | 07:45 | ZN2835:PA21 | SHORT RURAL | Planned |  | 128 | 360 | 0.19356 | 0.000538 | N
24-10-18 | 10:00 | ZN2196:PA21 | URBAN | Planned |  | 24 | 360 | 0.00588 | 1.6e-05 | N
24-10-18 | 21:00 | ZN36100:PA16 | URBAN | Planned |  | 56 | 480 | 0.018295 | 3.8e-05 | N
24-10-18 | 21:00 | ZN36100:PA1 | URBAN | Planned |  | 35 | 480 | 0.011434 | 2.4e-05 | N
24-10-18 | 21:00 | ZN3155:PA24 | URBAN | Planned |  | 13 | 420 | 0.003716 | 9e-06 | N
24-10-18 | 21:30 | ZN1600:PA24ABC | CBD | Planned |  | 2 | 255 | 0.016749 | 6.6e-05 | N
25-10-18 | 07:00 | ZN2568:PA27 | URBAN | Planned |  | 109 | 510 | 0.037824 | 7.4e-05 | N
25-10-18 | 09:45 | ZN116:PA14 | URBAN | Planned |  | 1 | 225 | 0.000153 | 1e-06 | N
25-10-18 | 08:00 | ZN180:PA34 | URBAN | Planned |  | 19 | 420 | 0.00543 | 1.3e-05 | N
25-10-18 | 08:00 | ZN847:PA18 | SHORT RURAL | Planned |  | 64 | 450 | 0.12093 | 0.000269 | N
25-10-18 | 08:00 | ZN847:PA18 | SHORT RURAL | Planned |  | 26 | 450 | 0.049129 | 0.000109 | N
25-10-18 | 09:40 | ZN9245:PA9 | URBAN | Planned |  | 35 | 212 | 0.005049 | 2.4e-05 | N
25-10-18 | 08:45 | ZN9900:PA12 | URBAN | Planned |  | 37 | 375 | 0.009441 | 2.5e-05 | N
25-10-18 | 09:05 | ZN3155:PA19 | URBAN | Planned |  | 54 | 455 | 0.016718 | 3.7e-05 | N
25-10-18 | 10:24 | ZN8100:PA28 | SHORT RURAL | Planned |  | 68 | 636 | 0.1816 | 0.000286 | N
26-10-18 | 08:10 | ZN1850:PA40 | URBAN | Planned |  | 1 | 425 | 0.000289 | 1e-06 | N
26-10-18 | 08:00 | ZN3155:PA35 | URBAN | Planned |  | 88 | 500 | 0.029938 | 6e-05 | N
26-10-18 | 09:30 | ZN9700:PA11 | URBAN | Planned |  | 32 | 310 | 0.00675 | 2.2e-05 | N
26-10-18 | 15:15 | ZN187:PA14 | URBAN | Planned |  | 1 | 2,955 | 0.002011 | 1e-06 | N
26-10-18 | 17:00 | ZN3288:PA43 44KLM | CBD | Planned |  | 1 | 1,560 | 0.051218 | 3.3e-05 | N
26-10-18 | 18:30 | ZN1290:PA13 | URBAN | Planned |  | 1 | 2,745 | 0.001868 | 1e-06 | N
27-10-18 | 07:30 | ZN1610:PA2 | URBAN | Planned |  | 5 | 420 | 0.001428 | 3e-06 | N
27-10-18 | 09:15 | ZN7481:PA14 | URBAN | Planned |  | 1 | 375 | 0.000255 | 1e-06 | N
27-10-18 | 09:30 | ZN3472:PA34 | URBAN | Planned |  | 1 | 1,785 | 0.001214 | 1e-06 | N
28-10-18 | 20:30 | ZN35600:PA1 | URBAN | Planned |  | 58 | 250 | 0.009859 | 3.9e-05 | N
29-10-18 | 07:07 | ZN340:PA44 | URBAN | Planned |  | 2 | 348 | 0.000473 | 1e-06 | N
29-10-18 | 08:00 | ZN3472:PA17 | URBAN | Planned |  | 41 | 550 | 0.015327 | 2.8e-05 | N
29-10-18 | 09:00 | ZN3472:PA33 | URBAN | Planned |  | 55 | 375 | 0.014018 | 3.7e-05 | N
29-10-18 | 08:00 | ZN15010:PA24 | URBAN | Planned |  | 41 | 420 | 0.011704 | 2.8e-05 | N
31-10-18 | 09:10 | ZN36100:PA2 | URBAN | Planned |  | 63 | 350 | 0.014987 | 4.3e-05 | N
01-11-18 | 09:30 | ZN9700:PA21 | URBAN | Planned |  | 2 | 225 | 0.000306 | 1e-06 | N
01-11-18 | 21:00 | ZN36100:PA1 | URBAN | Planned |  | 51 | 420 | 0.014559 | 3.5e-05 | N
01-11-18 | 23:31 | ZN2835:PA41 | URBAN | Planned |  | 1 | 164 | 0.000111 | 1e-06 | N
02-11-18 | 10:45 | ZN10991:PA1 | URBAN | Planned |  | 90 | 30 | 0.001835 | 6.1e-05 | N
03-11-18 | 09:30 | ZN3288:PA43 44GHJ | CBD | Planned |  | 9 | 390 | 0.11517 | 0.000295 | N
03-11-18 | 07:30 | ZN35900:PA4 | SHORT RURAL | Planned |  | 30 | 439 | 0.055274 | 0.000126 | N
04-11-18 | 07:30 | ZN8700:PA63 64ABC | CBD | Planned |  | 44 | 570 | 0.82294 | 0.001444 | N
05-11-18 | 07:50 | ZN398:PA29 | URBAN | Planned |  | 94 | 520 | 0.033214 | 6.4e-05 | N
05-11-18 | 10:00 | ZN36800:PA58 | URBAN | Planned |  | 110 | 165 | 0.012333 | 7.5e-05 | N
07-11-18 | 11:40 | ZN1610:PA19 | URBAN | Planned |  | 139 | 90 | 0.008501 | 9.4e-05 | N
08-11-18 | 07:30 | ZN10993:PA35 | URBAN | Planned |  | 91 | 520 | 0.032155 | 6.2e-05 | N
09-11-18 | 07:00 | ZN630:PA41 | URBAN | Planned |  | 1 | 720 | 0.000489 | 1e-06 | N
10-11-18 | 07:30 | ZN9252:PA31 | URBAN | Planned |  | 52 | 510 | 0.018009 | 3.5e-05 | N
10-11-18 | 08:40 | ZN1610:PA16 | URBAN | Planned |  | 1 | 211 | 0.000143 | 1e-06 | N
10-11-18 | 08:30 | ZN3288:PA43 44KLM | CBD | Planned |  | 1 | 300 | 0.009845 | 3.3e-05 | N
11-11-18 | 08:15 | ZN8700:PA61 62KLM | CBD | Planned |  | 10 | 405 | 0.13292 | 0.000328 | N
11-11-18 | 13:00 | ZN36100:PA27 | URBAN | Planned |  | 69 | 240 | 0.011245 | 4.7e-05 | N
11-11-18 | 20:30 | ZN35600:PA3 | URBAN | Planned |  | 43 | 1,530 | 0.044676 | 2.9e-05 | N
11-11-18 | 23:00 | ZN10999:PA4 | URBAN | Planned |  | 14 | 390 | 0.003708 | 1e-05 | N
12-11-18 | 00:00 | ZN690:PA36 | URBAN | Planned |  | 7 | 330 | 0.001569 | 5e-06 | N
12-11-18 | 09:00 | ZN9900:PA20 | URBAN | Planned |  | 27 | 60 | 0.0011 | 1.8e-05 | N
14-11-18 | 06:30 | ZN3672:PA36 | URBAN | Planned |  | 2 | 570 | 0.000774 | 1e-06 | N
14-11-18 | 08:00 | ZN3155:PA23 | URBAN | Planned |  | 31 | 320 | 0.006737 | 2.1e-05 | N
15-11-18 | 08:30 | ZN3155:PA22 | URBAN | Planned |  | 38 | 375 | 0.009677 | 2.6e-05 | N
15-11-18 | 08:30 | ZN1610:PA19 | URBAN | Planned |  | 61 | 150 | 0.006214 | 4.1e-05 | N
15-11-18 | 21:00 | ZN263:PA35 37DEF | CBD | Planned |  | 29 | 185 | 0.17608 | 0.000952 | N
17-11-18 | 06:45 | ZN630:PA41 | URBAN | Planned |  | 10 | 2,190 | 0.014909 | 7e-06 | N
17-11-18 | 10:00 | ZN3288:PA45 46GHJ | CBD | Planned |  | 5 | 440 | 0.072178 | 0.000164 | N
17-11-18 | 10:00 | ZN3288:PA45 46KLM | CBD | Planned |  | 1 | 440 | 0.014436 | 3.3e-05 | N
18-11-18 | 06:30 | ZN342:PA15 | URBAN | Planned |  | 1 | 780 | 0.00053 | 1e-06 | N
18-11-18 | 08:15 | ZN263:PA33 34KLM | CBD | Planned |  | 8 | 165 | 0.043371 | 0.000263 | N
19-11-18 | 08:00 | ZN10999:PA1 | URBAN | Planned |  | 59 | 660 | 0.02648 | 4e-05 | N
20-11-18 | 08:01 | ZN901:PA13 | URBAN | Planned |  | 175 | 267 | 0.031775 | 0.000119 | N
20-11-18 | 08:00 | ZN10995:PA1 | URBAN | Planned |  | 90 | 450 | 0.027541 | 6.1e-05 | N
21-11-18 | 07:30 | ZN188:PA44 | URBAN | Planned |  | 110 | 480 | 0.035904 | 7.5e-05 | N
21-11-18 | 08:00 | ZN36100:PA13 | URBAN | Planned |  | 32 | 480 | 0.010445 | 2.2e-05 | N
21-11-18 | 08:00 | ZN36100:PA16 | URBAN | Planned |  | 55 | 480 | 0.017952 | 3.7e-05 | N
21-11-18 | 10:50 | ZN9900:PA21 | URBAN | Planned |  | 24 | 190 | 0.003101 | 1.6e-05 | N
22-11-18 | 07:30 | ZN10999:PA39 | URBAN | Planned |  | 2 | 60 | 8.2e-05 | 1e-06 | N
22-11-18 | 08:00 | ZN3155:PA17 | URBAN | Planned |  | 42 | 480 | 0.013709 | 2.9e-05 | N
22-11-18 | 07:30 | ZN901:PA11 | URBAN | Planned |  | 174 | 480 | 0.056795 | 0.000118 | N
23-11-18 | 08:40 | ZN1788:PA21 | URBAN | Planned |  | 1 | 4,805 | 0.003268 | 1e-06 | N
24-11-18 | 06:34 | ZN1600:PA24DEF | CBD | Planned |  | 18 | 1,466 | 0.86714 | 0.000592 | N
24-11-18 | 08:00 | ZN262:PA28 | URBAN | Planned |  | 4 | 330 | 0.000898 | 3e-06 | N
26-11-18 | 07:30 | ZN9245:PA1 | URBAN | Planned |  | 3 | 205 | 0.000417 | 2e-06 | N
26-11-18 | 08:30 | ZN36100:PA19 | URBAN | Planned |  | 52 | 430 | 0.015176 | 3.5e-05 | N
26-11-18 | 09:20 | ZN9900:PA2 | URBAN | Planned |  | 29 | 290 | 0.005708 | 2e-05 | N
27-11-18 | 07:30 | ZN262:PA42 | URBAN | Planned |  | 105 | 450 | 0.032069 | 7.1e-05 | N
27-11-18 | 07:30 | ZN262:PA42 | URBAN | Planned |  | 87 | 450 | 0.026572 | 5.9e-05 | N
27-11-18 | 07:30 | ZN262:PA41 | URBAN | Planned |  | 93 | 450 | 0.028404 | 6.3e-05 | N
27-11-18 | 08:55 | ZN384:PA70 | URBAN | Planned |  | 7 | 625 | 0.002969 | 5e-06 | N
28-11-18 | 07:30 | ZN262:PA42 | URBAN | Planned |  | 105 | 450 | 0.032071 | 7.1e-05 | N
28-11-18 | 07:30 | ZN262:PA42 | URBAN | Planned |  | 37 | 450 | 0.011301 | 2.5e-05 | N
28-11-18 | 07:30 | ZN262:PA42 | URBAN | Planned |  | 50 | 450 | 0.015272 | 3.4e-05 | N
28-11-18 | 07:30 | ZN262:PA41 | URBAN | Planned |  | 93 | 450 | 0.028406 | 6.3e-05 | N
28-11-18 | 08:00 | ZN10999:PA36 | URBAN | Planned |  | 23 | 180 | 0.00281 | 1.6e-05 | N
29-11-18 | 07:30 | ZN398:PA3 | URBAN | Planned |  | 76 | 720 | 0.037141 | 5.2e-05 | N
29-11-18 | 08:00 | ZN9252:PA28 | URBAN | Planned |  | 32 | 540 | 0.011729 | 2.2e-05 | N
29-11-18 | 08:55 | ZN262:PA42 | URBAN | Planned |  | 50 | 235 | 0.007975 | 3.4e-05 | N
29-11-18 | 21:30 | ZN35600:PA9 | URBAN | Planned |  | 60 | 240 | 0.009774 | 4.1e-05 | N
29-11-18 | 22:32 | ZN36100:PA1 | URBAN | Planned |  | 51 | 263 | 0.009104 | 3.5e-05 | N
30-11-18 | 08:30 | ZN2602:PA27 | URBAN | Planned |  | 105 | 240 | 0.017096 | 7.1e-05 | N
30-11-18 | 08:30 | ZN2602:PA27 | URBAN | Planned |  | 40 | 240 | 0.006513 | 2.7e-05 | N
30-11-18 | 10:30 | ZN36800:PA43 | URBAN | Planned |  | 100 | 240 | 0.016282 | 6.8e-05 | N
02-12-18 | 07:40 | ZN1600:PA22ABC | CBD | Planned |  | 20 | 290 | 0.19054 | 0.000657 | N
02-12-18 | 08:15 | ZN8700:PA65 66DEF | CBD | Planned |  | 16 | 255 | 0.13404 | 0.000526 | N
02-12-18 | 12:40 | ZN4990:PA55 56GHJ | CBD | Planned |  | 10 | 260 | 0.085417 | 0.000329 | N
03-12-18 | 09:03 | ZN3155:PA36 | URBAN | Planned |  | 47 | 207 | 0.0066 | 3.2e-05 | N
04-12-18 | 10:03 | ZN36100:PA19 | URBAN | Planned |  | 97 | 342 | 0.022506 | 6.6e-05 | N
04-12-18 | 13:10 | ZN2602:PA32 | URBAN | Planned |  | 62 | 70 | 0.002944 | 4.2e-05 | N
08-12-18 | 06:45 | ZN8100:PA7 | URBAN | Planned |  | 1 | 465 | 0.000315 | 1e-06 | N
09-12-18 | 01:30 | ZN263:PA31 32ABC | CBD | Planned |  | 27 | 360 | 0.31893 | 0.000886 | N
09-12-18 | 08:00 | ZN3155:PA35 | URBAN | Planned |  | 21 | 365 | 0.005199 | 1.4e-05 | N
11-12-18 | 06:55 | ZN342:PA15 | URBAN | Planned |  | 2 | 847 | 0.001148 | 1e-06 | N
11-12-18 | 08:00 | ZN36100:PA19 | URBAN | Planned |  | 87 | 480 | 0.028311 | 5.9e-05 | N
13-12-18 | 08:00 | ZN8100:PA28 | SHORT RURAL | Planned |  | 15 | 465 | 0.029365 | 6.3e-05 | N
15-12-18 | 21:30 | ZN4990:PA55ABC | CBD | Planned |  | 105 | 586 | 2.018 | 0.003444 | N
16-12-18 | 07:30 | ZN4990:PA55ABC | CBD | Planned |  | 87 | 300 | 0.85602 | 0.002853 | N
19-02-19 | 10:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 47 | 360 | 0.070768 | 0.000197 | N
12-10-18 | 09:20 | ZN12630:PA8 | SHORT RURAL | Planned |  | 10 | 520 | 0.021849 | 4.2e-05 | N
15-10-18 | 07:00 | ZN12610:PA2 | URBAN | Planned |  | 1 | 240 | 0.000163 | 1e-06 | N
15-10-18 | 07:30 | ZN3425:PA39 | URBAN | Planned |  | 42 | 510 | 0.014578 | 2.9e-05 | N
16-10-18 | 08:00 | ZN12610:PA10 | URBAN | Planned |  | 67 | 480 | 0.021887 | 4.6e-05 | N
16-10-18 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 34 | 480 | 0.068551 | 0.000143 | N
17-10-18 | 08:00 | ZN14144:PA5 | URBAN | Planned |  | 16 | 360 | 0.00392 | 1.1e-05 | N
17-10-18 | 08:30 | ZN12580:PA4 | URBAN | Planned |  | 71 | 450 | 0.021744 | 4.8e-05 | N
18-10-18 | 07:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 7 | 600 | 0.017642 | 2.9e-05 | N
18-02-19 | 14:39 | ZN12600:PA2 | SHORT RURAL | Planned |  | 271 | 1 | 0.001134 | 0.001134 | N
21-02-19 | 08:30 | 526:34636 | SHORT RURAL | Planned |  | 2 | 205 | 0.001715 | 8e-06 | N
13-02-19 | 08:50 | 515:35197 | LONG RURAL | Planned |  | 25 | 280 | 2.4587 | 0.008781 | N
14-02-19 | 10:25 | 216:10724 | SHORT RURAL | Planned |  | 4 | 50 | 0.000837 | 1.7e-05 | N
18-02-19 | 07:45 | 223:14395 | SHORT RURAL | Planned |  | 82 | 170 | 0.058309 | 0.000343 | N
19-02-19 | 08:15 | 515:35200 | URBAN | Planned |  | 1 | 360 | 0.000244 | 1e-06 | N
20-02-19 | 08:30 | 528:83020 | SHORT RURAL | Planned |  | 21 | 345 | 0.030303 | 8.8e-05 | N
20-02-19 | 08:25 | 807:74179 | SHORT RURAL | Planned |  | 23 | 270 | 0.025974 | 9.6e-05 | N
20-02-19 | 08:15 | 515:35197 | LONG RURAL | Planned |  | 15 | 285 | 1.4984 | 0.005258 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 29 | 385 | 0.046699 | 0.000121 | N
13-02-19 | 08:15 | 526:34640 | SHORT RURAL | Planned |  | 4 | 315 | 0.00527 | 1.7e-05 | N
13-02-19 | 10:35 | 532:83293 | URBAN | Planned |  | 89 | 265 | 0.01598 | 6e-05 | N
14-02-19 | 11:17 | 233:82812 | SHORT RURAL | Planned |  | 17 | 90 | 0.0064 | 7.1e-05 | N
14-02-19 | 08:00 | 508:82580 | SHORT RURAL | Planned |  | 57 | 404 | 0.09632 | 0.000238 | N
14-02-19 | 15:00 | 522:83131 | URBAN | Planned |  | 30 | 628 | 0.012766 | 2e-05 | N
18-02-19 | 07:49 | 415:33904 | URBAN | Planned |  | 1 | 467 | 0.000316 | 1e-06 | N
19-02-19 | 08:40 | 528:83011 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
19-02-19 | 09:05 | 511:29878 | SHORT RURAL | Planned |  | 6 | 68 | 0.001706 | 2.5e-05 | N
19-02-19 | 08:30 | 524:33580 | SHORT RURAL | Planned |  | 17 | 265 | 0.018842 | 7.1e-05 | N
19-02-19 | 11:00 | 511:29878 | SHORT RURAL | Planned |  | 5 | 65 | 0.001359 | 2.1e-05 | N
19-02-19 | 11:10 | 511:29878 | SHORT RURAL | Planned |  | 7 | 40 | 0.001171 | 2.9e-05 | N
19-02-19 | 12:05 | 511:29878 | SHORT RURAL | Planned |  | 2 | 55 | 0.00046 | 8e-06 | N
19-02-19 | 08:30 | 511:29873 | URBAN | Planned |  | 9 | 230 | 0.001403 | 6e-06 | N
19-02-19 | 13:20 | 528:83011 | SHORT RURAL | Planned |  | 11 | 44 | 0.002024 | 4.6e-05 | N
19-02-19 | 08:10 | 509:33395 | LONG RURAL | Planned |  | 27 | 345 | 3.265 | 0.009464 | N
19-02-19 | 08:05 | 265:81648 | SHORT RURAL | Planned |  | 15 | 400 | 0.025095 | 6.3e-05 | N
13-02-19 | 09:00 | 515:35193 | SHORT RURAL | Planned |  | 3 | 60 | 0.000753 | 1.3e-05 | N
13-02-19 | 08:00 | 810:74058 | SHORT RURAL | Planned |  | 14 | 260 | 0.015225 | 5.9e-05 | N
13-02-19 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 7 | 230 | 0.006734 | 2.9e-05 | N
13-02-19 | 08:30 | 814:82283 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
13-02-19 | 09:20 | 814:82283 | SHORT RURAL | Planned |  | 2 | 40 | 0.000335 | 8e-06 | N
13-02-19 | 10:20 | 814:82283 | SHORT RURAL | Planned |  | 2 | 50 | 0.000418 | 8e-06 | N
13-02-19 | 10:45 | 515:35193 | SHORT RURAL | Planned |  | 2 | 45 | 0.000376 | 8e-06 | N
13-02-19 | 11:30 | 814:82283 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
14-02-19 | 08:20 | 515:35198 | SHORT RURAL | Planned |  | 7 | 280 | 0.008198 | 2.9e-05 | N
14-02-19 | 08:20 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
14-02-19 | 08:08 | 516:48067 | SHORT RURAL | Planned |  | 1 | 62 | 0.000259 | 4e-06 | N
14-02-19 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 8 | 240 | 0.008031 | 3.3e-05 | N
14-02-19 | 09:15 | 807:74184 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
14-02-19 | 10:05 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
14-02-19 | 10:00 | 813:89061 | LONG RURAL | Planned |  | 1 | 40 | 0.01405 | 0.000351 | N
14-02-19 | 10:00 | 516:48067 | SHORT RURAL | Planned |  | 2 | 62 | 0.000519 | 8e-06 | N
14-02-19 | 10:50 | 813:89061 | LONG RURAL | Planned |  | 4 | 45 | 0.063224 | 0.001405 | N
14-02-19 | 11:45 | 813:89061 | LONG RURAL | Planned |  | 10 | 45 | 0.15806 | 0.003512 | N
14-02-19 | 12:20 | 807:74184 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
14-02-19 | 13:00 | 516:48067 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
15-02-19 | 08:20 | 513:48059 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
15-02-19 | 10:05 | 520:48172 | SHORT RURAL | Planned |  | 5 | 45 | 0.000941 | 2.1e-05 | N
15-02-19 | 11:15 | 813:89055 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
15-02-19 | 09:10 | 813:89055 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
15-02-19 | 10:05 | 813:89055 | SHORT RURAL | Planned |  | 3 | 45 | 0.000565 | 1.3e-05 | N
15-02-19 | 08:30 | 811:74234 | SHORT RURAL | Planned |  | 8 | 235 | 0.007864 | 3.3e-05 | N
15-02-19 | 08:30 | 516:48066 | SHORT RURAL | Planned |  | 22 | 255 | 0.023465 | 9.2e-05 | N
15-02-19 | 13:00 | 520:48172 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
18-02-19 | 08:10 | 813:89061 | LONG RURAL | Planned |  | 4 | 55 | 0.077274 | 0.001405 | N
18-02-19 | 08:12 | 515:35197 | LONG RURAL | Planned |  | 2 | 63 | 0.044257 | 0.000702 | N
18-02-19 | 08:55 | 807:74179 | SHORT RURAL | Planned |  | 1 | 60 | 0.000251 | 4e-06 | N
18-02-19 | 10:00 | 807:74179 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
18-02-19 | 09:15 | 813:89061 | LONG RURAL | Planned |  | 2 | 40 | 0.0281 | 0.000702 | N
18-02-19 | 08:35 | 801:74121 | LONG RURAL | Planned |  | 1 | 95 | 0.033368 | 0.000351 | N
18-02-19 | 10:00 | 515:35197 | LONG RURAL | Planned |  | 1 | 10 | 0.003512 | 0.000351 | N
18-02-19 | 11:20 | 807:74179 | SHORT RURAL | Planned |  | 1 | 55 | 0.00023 | 4e-06 | N
18-02-19 | 10:30 | 801:74121 | LONG RURAL | Planned |  | 1 | 60 | 0.021075 | 0.000351 | N
18-02-19 | 13:00 | 515:35197 | LONG RURAL | Planned |  | 1 | 40 | 0.01405 | 0.000351 | N
18-02-19 | 08:00 | 812:19072 | SHORT RURAL | Planned |  | 5 | 515 | 0.010771 | 2.1e-05 | N
19-02-19 | 09:00 | 512:83743 | SHORT RURAL | Planned |  | 3 | 50 | 0.000627 | 1.3e-05 | N
19-02-19 | 08:10 | 810:74054 | LONG RURAL | Planned |  | 47 | 320 | 5.2716 | 0.016474 | N
19-02-19 | 08:48 | 806:82662 | SHORT RURAL | Planned |  | 17 | 312 | 0.022184 | 7.1e-05 | N
20-02-19 | 09:00 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.01402 | 0.000351 | N
20-02-19 | 09:50 | 810:74054 | LONG RURAL | Planned |  | 1 | 35 | 0.012268 | 0.000351 | N
20-02-19 | 10:35 | 810:74054 | LONG RURAL | Planned |  | 1 | 30 | 0.010515 | 0.000351 | N
20-02-19 | 11:50 | 810:74054 | LONG RURAL | Planned |  | 1 | 30 | 0.010515 | 0.000351 | N
20-02-19 | 08:55 | 806:82662 | SHORT RURAL | Planned |  | 1 | 100 | 0.000418 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 10:50 | 806:82662 | SHORT RURAL | Planned |  | 1 | 80 | 0.000335 | 4e-06 | N
20-02-19 | 13:00 | 806:82662 | SHORT RURAL | Planned |  | 4 | 45 | 0.000753 | 1.7e-05 | N
20-02-19 | 14:00 | 806:82662 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 2 | 385 | 0.003221 | 8e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 3 | 385 | 0.004831 | 1.3e-05 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 14 | 385 | 0.022544 | 5.9e-05 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 3 | 385 | 0.004831 | 1.3e-05 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 2 | 385 | 0.003221 | 8e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
20-02-19 | 08:05 | 806:82662 | SHORT RURAL | Planned |  | 1 | 385 | 0.00161 | 4e-06 | N
21-02-19 | 08:15 | 508:82579 | SHORT RURAL | Planned |  | 14 | 380 | 0.022252 | 5.9e-05 | N
21-02-19 | 08:35 | 512:83743 | SHORT RURAL | Planned |  | 27 | 265 | 0.029927 | 0.000113 | N
22-02-19 | 08:10 | 523:33501 | SHORT RURAL | Planned |  | 49 | 385 | 0.078906 | 0.000205 | N
23-02-19 | 08:00 | 224:80341 | URBAN | Planned |  | 91 | 327 | 0.020156 | 6.2e-05 | N
24-02-19 | 08:20 | 238:34150 | SHORT RURAL | Planned |  | 4 | 495 | 0.008278 | 1.7e-05 | N
21-02-19 | 09:40 | 229:34995 | SHORT RURAL | Planned |  | 12 | 30 | 0.001506 | 5e-05 | N
21-02-19 | 09:05 | 508:82579 | SHORT RURAL | Planned |  | 7 | 18 | 0.000527 | 2.9e-05 | N
21-02-19 | 11:10 | 508:82579 | SHORT RURAL | Planned |  | 1 | 28 | 0.000117 | 4e-06 | N
21-02-19 | 11:10 | 229:34995 | SHORT RURAL | Planned |  | 2 | 50 | 0.000418 | 8e-06 | N
21-02-19 | 08:55 | 233:82815 | SHORT RURAL | Planned |  | 112 | 435 | 0.20378 | 0.000468 | N
22-02-19 | 09:10 | 232:33409 | SHORT RURAL | Planned |  | 1 | 137 | 0.000573 | 4e-06 | N
22-02-19 | 11:50 | 522:83126 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
22-02-19 | 08:00 | 528:83011 | SHORT RURAL | Planned |  | 103 | 255 | 0.10986 | 0.000431 | N
22-02-19 | 09:20 | 528:83011 | SHORT RURAL | Planned |  | 20 | 310 | 0.025933 | 8.4e-05 | N
22-02-19 | 08:30 | 233:82815 | SHORT RURAL | Planned |  | 183 | 430 | 0.32913 | 0.000765 | N
23-02-19 | 08:30 | 264:81232 | SHORT RURAL | Planned |  | 41 | 390 | 0.06686 | 0.000171 | N
21-02-19 | 08:00 | 811:74234 | SHORT RURAL | Planned |  | 8 | 340 | 0.011377 | 3.3e-05 | N
22-02-19 | 08:05 | 811:74234 | SHORT RURAL | Planned |  | 8 | 165 | 0.005521 | 3.3e-05 | N
22-02-19 | 10:05 | 806:82662 | SHORT RURAL | Planned |  | 2 | 45 | 0.000376 | 8e-06 | N
22-02-19 | 09:30 | 801:74121 | LONG RURAL | Planned |  | 4 | 60 | 0.084122 | 0.001402 | N
22-02-19 | 08:10 | 801:74121 | LONG RURAL | Planned |  | 1 | 55 | 0.019278 | 0.000351 | N
22-02-19 | 10:45 | 801:74121 | LONG RURAL | Planned |  | 1 | 45 | 0.015773 | 0.000351 | N
22-02-19 | 11:45 | 801:74121 | LONG RURAL | Planned |  | 2 | 50 | 0.035051 | 0.000701 | N
22-02-19 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 2 | 270 | 0.002259 | 8e-06 | N
22-02-19 | 08:05 | 801:74117 | SHORT RURAL | Planned |  | 214 | 265 | 0.2372 | 0.000895 | N
22-02-19 | 08:10 | 806:82662 | SHORT RURAL | Planned |  | 4 | 320 | 0.005354 | 1.7e-05 | N
23-02-19 | 08:20 | 812:19065 | SHORT RURAL | Planned |  | 10 | 160 | 0.00669 | 4.2e-05 | N
25-02-19 | 08:00 | 256:80647 | URBAN | Planned |  | 27 | 520 | 0.00951 | 1.8e-05 | N
25-02-19 | 08:55 | 511:29878 | SHORT RURAL | Planned |  | 4 | 120 | 0.002007 | 1.7e-05 | N
25-02-19 | 11:55 | 511:29878 | SHORT RURAL | Planned |  | 1 | 95 | 0.000397 | 4e-06 | N
25-02-19 | 09:50 | 812:19071 | SHORT RURAL | Planned |  | 5 | 45 | 0.000941 | 2.1e-05 | N
25-02-19 | 10:36 | 515:35197 | LONG RURAL | Planned |  | 1 | 39 | 0.01367 | 0.000351 | N
25-02-19 | 10:45 | 812:19071 | SHORT RURAL | Planned |  | 2 | 50 | 0.000418 | 8e-06 | N
25-02-19 | 11:45 | 814:82289 | SHORT RURAL | Planned |  | 2 | 60 | 0.000502 | 8e-06 | N
25-02-19 | 09:25 | 813:89055 | SHORT RURAL | Planned |  | 29 | 395 | 0.047889 | 0.000121 | N
26-02-19 | 08:15 | 240:34852 | URBAN | Planned |  | 20 | 335 | 0.004538 | 1.4e-05 | N
26-02-19 | 09:20 | 243:80074 | SHORT RURAL | Planned |  | 18 | 540 | 0.040637 | 7.5e-05 | N
26-02-19 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 60 | 420 | 0.10536 | 0.000251 | N
26-02-19 | 08:20 | 522:83124 | URBAN | Planned |  | 1 | 209 | 0.000142 | 1e-06 | N
26-02-19 | 07:40 | 235:2120 | SHORT RURAL | Planned |  | 15 | 460 | 0.028847 | 6.3e-05 | N
26-02-19 | 08:00 | 508:82580 | SHORT RURAL | Planned |  | 15 | 360 | 0.022576 | 6.3e-05 | N
26-02-19 | 08:20 | 813:89061 | LONG RURAL | Planned |  | 5 | 380 | 0.66597 | 0.001753 | N
26-02-19 | 09:25 | 512:83732 | SHORT RURAL | Planned |  | 2 | 40 | 0.000334 | 8e-06 | N
26-02-19 | 09:25 | 813:89061 | LONG RURAL | Planned |  | 3 | 65 | 0.068349 | 0.001052 | N
26-02-19 | 09:10 | 514:18137 | SHORT RURAL | Planned |  | 1 | 108 | 0.000452 | 4e-06 | N
26-02-19 | 10:45 | 512:83732 | SHORT RURAL | Planned |  | 1 | 30 | 0.000125 | 4e-06 | N
26-02-19 | 10:35 | 813:89061 | LONG RURAL | Planned |  | 1 | 40 | 0.01402 | 0.000351 | N
26-02-19 | 11:35 | 512:83732 | SHORT RURAL | Planned |  | 3 | 25 | 0.000314 | 1.3e-05 | N
26-02-19 | 12:10 | 512:83732 | SHORT RURAL | Planned |  | 2 | 20 | 0.000167 | 8e-06 | N
26-02-19 | 11:25 | 813:89061 | LONG RURAL | Planned |  | 1 | 65 | 0.022783 | 0.000351 | N
26-02-19 | 12:45 | 520:48172 | SHORT RURAL | Planned |  | 1 | 89 | 0.000372 | 4e-06 | N
27-02-19 | 07:00 | 258:80775 | URBAN | Planned |  | 87 | 185 | 0.010902 | 5.9e-05 | N
27-02-19 | 11:20 | 206:34440 | URBAN | Planned |  | 82 | 185 | 0.010276 | 5.6e-05 | N
27-02-19 | 11:10 | 524:33570 | SHORT RURAL | Planned |  | 2 | 161 | 0.001346 | 8e-06 | N
27-02-19 | 09:18 | 508:82576 | SHORT RURAL | Planned |  | 8 | 57 | 0.001906 | 3.3e-05 | N
27-02-19 | 08:05 | 509:33395 | LONG RURAL | Planned |  | 2 | 145 | 0.10165 | 0.000701 | N
27-02-19 | 13:13 | 508:82580 | SHORT RURAL | Planned |  | 4 | 57 | 0.000953 | 1.7e-05 | N
27-02-19 | 12:35 | 509:33399 | SHORT RURAL | Planned |  | 26 | 55 | 0.005979 | 0.000109 | N
27-02-19 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 10 | 445 | 1.5598 | 0.003505 | N
27-02-19 | 09:18 | 512:83743 | SHORT RURAL | Planned |  | 1 | 15 | 6.3e-05 | 4e-06 | N
27-02-19 | 10:00 | 512:83743 | SHORT RURAL | Planned |  | 2 | 45 | 0.000376 | 8e-06 | N
27-02-19 | 09:35 | 512:83743 | SHORT RURAL | Planned |  | 5 | 40 | 0.000836 | 2.1e-05 | N
27-02-19 | 10:00 | 813:89055 | SHORT RURAL | Planned |  | 5 | 95 | 0.001986 | 2.1e-05 | N
27-02-19 | 10:30 | 512:83743 | SHORT RURAL | Planned |  | 2 | 65 | 0.000544 | 8e-06 | N
27-02-19 | 11:50 | 813:89055 | SHORT RURAL | Planned |  | 3 | 35 | 0.000439 | 1.3e-05 | N
27-02-19 | 08:15 | 512:83733 | SHORT RURAL | Planned |  | 24 | 435 | 0.043648 | 0.0001 | N
02-03-19 | 08:00 | 264:81241 | URBAN | Planned |  | 550 | 520 | 0.19374 | 0.000373 | N
28-02-19 | 08:15 | 243:80084 | SHORT RURAL | Planned |  | 40 | 555 | 0.092815 | 0.000167 | N
28-02-19 | 08:10 | 520:48172 | SHORT RURAL | Planned |  | 18 | 345 | 0.025963 | 7.5e-05 | N
28-02-19 | 08:25 | 813:89058 | SHORT RURAL | Planned |  | 2 | 295 | 0.002467 | 8e-06 | N
06-03-19 | 08:30 | ZN12570:PA22 | SHORT RURAL | Planned |  | 16 | 420 | 0.028093 | 6.7e-05 | N
28-02-19 | 08:30 | 224:80346 | URBAN | Planned |  | 47 | 510 | 0.016237 | 3.2e-05 | N
02-03-19 | 23:00 | 224:80344 | URBAN | Planned |  | 10 | 146 | 0.000989 | 7e-06 | N
28-02-19 | 09:20 | 232:33407 | SHORT RURAL | Planned |  | 13 | 343 | 0.018642 | 5.4e-05 | N
28-02-19 | 07:30 | 509:33395 | LONG RURAL | Planned |  | 17 | 570 | 3.3964 | 0.005959 | N
01-03-19 | 11:00 | 526:34636 | SHORT RURAL | Planned |  | 8 | 290 | 0.0097 | 3.3e-05 | N
28-02-19 | 08:50 | 515:35193 | SHORT RURAL | Planned |  | 1 | 43 | 0.00018 | 4e-06 | N
28-02-19 | 08:00 | 810:74058 | SHORT RURAL | Planned |  | 14 | 370 | 0.021657 | 5.9e-05 | N
28-02-19 | 08:30 | 512:83743 | SHORT RURAL | Planned |  | 28 | 450 | 0.052679 | 0.000117 | N
28-02-19 | 08:25 | 813:89061 | LONG RURAL | Planned |  | 4 | 295 | 0.4136 | 0.001402 | N
01-03-19 | 09:10 | 813:89062 | SHORT RURAL | Planned |  | 1 | 55 | 0.00023 | 4e-06 | N
01-03-19 | 09:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 45 | 0.015778 | 0.000351 | N
01-03-19 | 10:10 | 512:83743 | SHORT RURAL | Planned |  | 2 | 15 | 0.000125 | 8e-06 | N
01-03-19 | 09:30 | 810:74054 | LONG RURAL | Planned |  | 1 | 35 | 0.012272 | 0.000351 | N
01-03-19 | 09:55 | 807:74184 | SHORT RURAL | Planned |  | 1 | 55 | 0.00023 | 4e-06 | N
01-03-19 | 10:05 | 813:89061 | LONG RURAL | Planned |  | 2 | 35 | 0.024544 | 0.000701 | N
01-03-19 | 09:40 | 512:83743 | SHORT RURAL | Planned |  | 1 | 14 | 5.9e-05 | 4e-06 | N
01-03-19 | 09:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 25 | 0.008766 | 0.000351 | N
01-03-19 | 08:35 | 807:74184 | SHORT RURAL | Planned |  | 1 | 55 | 0.00023 | 4e-06 | N
01-03-19 | 10:15 | 813:89062 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
01-03-19 | 10:15 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.014025 | 0.000351 | N
01-03-19 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 30 | 0.010519 | 0.000351 | N
01-03-19 | 08:34 | 814:82285 | SHORT RURAL | Planned |  | 1 | 46 | 0.000192 | 4e-06 | N
01-03-19 | 08:45 | 512:83743 | SHORT RURAL | Planned |  | 3 | 15 | 0.000188 | 1.3e-05 | N
01-03-19 | 08:45 | 810:74054 | LONG RURAL | Planned |  | 1 | 35 | 0.012272 | 0.000351 | N
01-03-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 3 | 35 | 0.036816 | 0.001052 | N
01-03-19 | 08:05 | 512:83743 | SHORT RURAL | Planned |  | 5 | 380 | 0.007944 | 2.1e-05 | N
01-03-19 | 12:20 | 811:74234 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
01-03-19 | 08:35 | 515:35192 | SHORT RURAL | Planned |  | 2 | 290 | 0.002425 | 8e-06 | N
01-03-19 | 12:20 | 515:35197 | LONG RURAL | Planned |  | 4 | 50 | 0.070126 | 0.001403 | N
01-03-19 | 12:05 | 801:74121 | LONG RURAL | Planned |  | 2 | 37 | 0.025947 | 0.000701 | N
01-03-19 | 11:10 | 813:89062 | SHORT RURAL | Planned |  | 1 | 55 | 0.00023 | 4e-06 | N
01-03-19 | 11:05 | 801:74121 | LONG RURAL | Planned |  | 1 | 45 | 0.015778 | 0.000351 | N
01-03-19 | 11:00 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017532 | 0.000351 | N
01-03-19 | 09:40 | 811:74234 | SHORT RURAL | Planned |  | 1 | 130 | 0.000544 | 4e-06 | N
01-03-19 | 11:00 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
05-03-19 | 09:00 | 224:80329 | SHORT RURAL | Planned |  | 67 | 540 | 0.15125 | 0.00028 | N
05-03-19 | 08:15 | 227:13015 | SHORT RURAL | Planned |  | 16 | 540 | 0.036119 | 6.7e-05 | N
05-03-19 | 08:06 | 526:34640 | SHORT RURAL | Planned |  | 4 | 344 | 0.005752 | 1.7e-05 | N
05-03-19 | 10:00 | 238:34141 | SHORT RURAL | Planned |  | 3 | 250 | 0.003135 | 1.3e-05 | N
04-03-19 | 09:20 | 524:33580 | SHORT RURAL | Planned |  | 1 | 51 | 0.000213 | 4e-06 | N
04-03-19 | 09:00 | 512:83733 | SHORT RURAL | Planned |  | 2 | 38 | 0.000318 | 8e-06 | N
04-03-19 | 10:40 | 526:34633 | SHORT RURAL | Planned |  | 2 | 36 | 0.000301 | 8e-06 | N
04-03-19 | 09:54 | 233:82812 | SHORT RURAL | Planned |  | 13 | 135 | 0.007336 | 5.4e-05 | N
04-03-19 | 09:07 | 229:34983 | SHORT RURAL | Planned |  | 63 | 218 | 0.057412 | 0.000263 | N
04-03-19 | 09:30 | 264:81236 | URBAN | Planned |  | 77 | 235 | 0.012252 | 5.2e-05 | N
04-03-19 | 08:30 | 526:34639 | SHORT RURAL | Planned |  | 77 | 360 | 0.11588 | 0.000322 | N
05-03-19 | 09:05 | 526:34636 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
05-03-19 | 08:45 | 522:83132 | SHORT RURAL | Planned |  | 2 | 255 | 0.002132 | 8e-06 | N
05-03-19 | 08:25 | 232:11454 | SHORT RURAL | Planned |  | 84 | 350 | 0.12291 | 0.000351 | N
05-03-19 | 08:35 | 528:83011 | SHORT RURAL | Planned |  | 15 | 380 | 0.023828 | 6.3e-05 | N
05-03-19 | 08:25 | 528:83020 | SHORT RURAL | Planned |  | 11 | 395 | 0.018164 | 4.6e-05 | N
04-03-19 | 10:35 | 812:19072 | SHORT RURAL | Planned |  | 2 | 20 | 0.000167 | 8e-06 | N
04-03-19 | 09:40 | 812:19072 | SHORT RURAL | Planned |  | 1 | 30 | 0.000125 | 4e-06 | N
04-03-19 | 08:35 | 801:74123 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
04-03-19 | 08:35 | 807:74184 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
04-03-19 | 11:45 | 812:19072 | SHORT RURAL | Planned |  | 1 | 20 | 8.4e-05 | 4e-06 | N
05-03-19 | 11:45 | 813:89061 | LONG RURAL | Planned |  | 3 | 55 | 0.057854 | 0.001052 | N
05-03-19 | 10:50 | 810:74054 | LONG RURAL | Planned |  | 1 | 50 | 0.017532 | 0.000351 | N
05-03-19 | 09:50 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.014025 | 0.000351 | N
05-03-19 | 09:00 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.014025 | 0.000351 | N
05-03-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 1 | 50 | 0.017532 | 0.000351 | N
05-03-19 | 09:05 | 802:82220 | SHORT RURAL | Planned |  | 41 | 330 | 0.056561 | 0.000171 | N
05-03-19 | 10:40 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017532 | 0.000351 | N
05-03-19 | 10:35 | 520:48172 | SHORT RURAL | Planned |  | 4 | 40 | 0.000669 | 1.7e-05 | N
05-03-19 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 2 | 85 | 0.059607 | 0.000701 | N
05-03-19 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 3 | 60 | 0.000752 | 1.3e-05 | N
05-03-19 | 11:30 | 520:48172 | SHORT RURAL | Planned |  | 2 | 30 | 0.000251 | 8e-06 | N
05-03-19 | 09:00 | 810:74054 | LONG RURAL | Planned |  | 47 | 285 | 4.6967 | 0.01648 | N
05-03-19 | 08:30 | 513:48050 | SHORT RURAL | Planned |  | 15 | 335 | 0.021007 | 6.3e-05 | N
05-03-19 | 08:10 | 801:74121 | LONG RURAL | Planned |  | 7 | 421 | 1.0333 | 0.002454 | N
05-03-19 | 08:30 | 515:35198 | SHORT RURAL | Planned |  | 5 | 335 | 0.007002 | 2.1e-05 | N
06-03-19 | 08:00 | 216:10726 | URBAN | Planned |  | 202 | 490 | 0.06702 | 0.000137 | N
06-03-19 | 08:45 | 807:74183 | SHORT RURAL | Planned |  | 7 | 215 | 0.006292 | 2.9e-05 | N
06-03-19 | 09:05 | 813:89061 | LONG RURAL | Planned |  | 8 | 280 | 0.78541 | 0.002805 | N
06-03-19 | 08:30 | 814:82289 | SHORT RURAL | Planned |  | 3 | 10 | 0.000125 | 1.3e-05 | N
06-03-19 | 08:12 | 514:18137 | SHORT RURAL | Planned |  | 1 | 44 | 0.000184 | 4e-06 | N
06-03-19 | 08:40 | 813:89058 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
06-03-19 | 09:10 | 814:82289 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
06-03-19 | 08:35 | 814:82283 | SHORT RURAL | Planned |  | 1 | 65 | 0.000272 | 4e-06 | N
06-03-19 | 09:35 | 813:89058 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
06-03-19 | 09:50 | 814:82289 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
06-03-19 | 10:40 | 814:82289 | SHORT RURAL | Planned |  | 5 | 35 | 0.000732 | 2.1e-05 | N
06-03-19 | 09:42 | 813:89065 | SHORT RURAL | Planned |  | 25 | 40 | 0.00418 | 0.000105 | N
06-03-19 | 11:00 | 813:89061 | LONG RURAL | Planned |  | 1 | 35 | 0.012272 | 0.000351 | N
06-03-19 | 10:15 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015778 | 0.000351 | N
06-03-19 | 11:00 | 523:33501 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
06-03-19 | 09:40 | 523:33501 | SHORT RURAL | Planned |  | 2 | 30 | 0.000251 | 8e-06 | N
06-03-19 | 11:45 | 813:89061 | LONG RURAL | Planned |  | 2 | 40 | 0.02805 | 0.000701 | N
06-03-19 | 11:33 | 813:89061 | LONG RURAL | Planned |  | 3 | 24 | 0.025245 | 0.001052 | N
06-03-19 | 12:20 | 813:89061 | LONG RURAL | Planned |  | 1 | 32 | 0.01122 | 0.000351 | N
06-03-19 | 12:35 | 807:74183 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
06-03-19 | 11:15 | 813:89061 | LONG RURAL | Planned |  | 2 | 110 | 0.077139 | 0.000701 | N
06-03-19 | 09:00 | 802:82225 | SHORT RURAL | Planned |  | 7 | 245 | 0.007169 | 2.9e-05 | N
07-03-19 | 08:30 | 532:83307 | SHORT RURAL | Planned |  | 48 | 430 | 0.086285 | 0.000201 | N
07-03-19 | 08:30 | 509:33399 | SHORT RURAL | Planned |  | 1 | 70 | 0.000293 | 4e-06 | N
07-03-19 | 10:10 | 511:29878 | SHORT RURAL | Planned |  | 1 | 90 | 0.000376 | 4e-06 | N
07-03-19 | 10:30 | 509:33399 | SHORT RURAL | Planned |  | 2 | 60 | 0.000502 | 8e-06 | N
07-03-19 | 13:10 | 509:33399 | SHORT RURAL | Planned |  | 1 | 30 | 0.000125 | 4e-06 | N
07-03-19 | 08:00 | 264:81236 | URBAN | Planned |  | 136 | 470 | 0.043281 | 9.2e-05 | N
07-03-19 | 08:00 | 264:81241 | URBAN | Planned |  | 202 | 470 | 0.064285 | 0.000137 | N
07-03-19 | 08:05 | 513:48059 | SHORT RURAL | Planned |  | 45 | 310 | 0.058317 | 0.000188 | N
07-03-19 | 08:55 | 810:74058 | SHORT RURAL | Planned |  | 7 | 285 | 0.00834 | 2.9e-05 | N
08-03-19 | 08:00 | 264:81240 | SHORT RURAL | Planned |  | 10 | 500 | 0.020905 | 4.2e-05 | N
08-03-19 | 08:10 | 511:29877 | SHORT RURAL | Planned |  | 1 | 305 | 0.001275 | 4e-06 | N
08-03-19 | 08:45 | 238:34140 | SHORT RURAL | Planned |  | 63 | 425 | 0.11195 | 0.000263 | N
10-03-19 | 08:30 | 235:2728 | URBAN | Planned |  | 150 | 500 | 0.050776 | 0.000102 | N
10-03-19 | 08:30 | 235:8685 | URBAN | Planned |  | 114 | 80 | 0.006174 | 7.7e-05 | N
08-03-19 | 08:32 | 512:83743 | SHORT RURAL | Planned |  | 50 | 88 | 0.018396 | 0.000209 | N
08-03-19 | 08:30 | 512:83743 | SHORT RURAL | Planned |  | 55 | 245 | 0.056339 | 0.00023 | N
08-03-19 | 08:30 | 806:82662 | SHORT RURAL | Planned |  | 58 | 410 | 0.099424 | 0.000242 | N
08-03-19 | 08:35 | 806:82662 | SHORT RURAL | Planned |  | 24 | 415 | 0.041643 | 0.0001 | N
11-03-19 | 08:15 | 801:74121 | LONG RURAL | Planned |  | 1 | 60 | 0.021038 | 0.000351 | N
11-03-19 | 09:45 | 801:74121 | LONG RURAL | Planned |  | 3 | 30 | 0.031557 | 0.001052 | N
11-03-19 | 08:40 | 814:82283 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
12-03-19 | 09:00 | 202:34262 | URBAN | Planned |  | 65 | 25 | 0.0011 | 4.4e-05 | N
12-03-19 | 08:19 | 528:83011 | SHORT RURAL | Planned |  | 50 | 286 | 0.059775 | 0.000209 | N
12-03-19 | 07:45 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.014025 | 0.000351 | N
12-03-19 | 09:20 | 802:82215 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
12-03-19 | 09:39 | 807:74179 | SHORT RURAL | Planned |  | 3 | 24 | 0.000301 | 1.3e-05 | N
12-03-19 | 08:50 | 807:74179 | SHORT RURAL | Planned |  | 1 | 38 | 0.000159 | 4e-06 | N
12-03-19 | 08:31 | 512:83743 | SHORT RURAL | Planned |  | 9 | 114 | 0.004289 | 3.8e-05 | N
12-03-19 | 10:16 | 807:74180 | SHORT RURAL | Planned |  | 1 | 23 | 9.6e-05 | 4e-06 | N
12-03-19 | 08:25 | 512:83743 | SHORT RURAL | Planned |  | 11 | 946 | 0.043498 | 4.6e-05 | N
12-03-19 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 1 | 165 | 0.057854 | 0.000351 | N
12-03-19 | 09:15 | 811:74234 | SHORT RURAL | Planned |  | 1 | 85 | 0.000355 | 4e-06 | N
12-03-19 | 10:55 | 811:74234 | SHORT RURAL | Planned |  | 1 | 70 | 0.000293 | 4e-06 | N
12-03-19 | 11:30 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.014025 | 0.000351 | N
12-03-19 | 08:15 | 512:83743 | SHORT RURAL | Planned |  | 25 | 255 | 0.026648 | 0.000105 | N
12-03-19 | 09:15 | 813:89061 | LONG RURAL | Planned |  | 5 | 230 | 0.40323 | 0.001753 | N
13-03-19 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 15 | 195 | 0.012227 | 6.3e-05 | N
13-03-19 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 13 | 155 | 0.70652 | 0.004558 | N
13-03-19 | 08:20 | 814:82285 | SHORT RURAL | Planned |  | 1 | 125 | 0.000523 | 4e-06 | N
13-03-19 | 08:33 | 229:34995 | SHORT RURAL | Planned |  | 6 | 382 | 0.009581 | 2.5e-05 | N
13-03-19 | 07:50 | 232:11453 | SHORT RURAL | Planned |  | 1 | 435 | 0.001818 | 4e-06 | N
13-03-19 | 08:03 | 511:29878 | SHORT RURAL | Planned |  | 133 | 437 | 0.24295 | 0.000556 | N
13-03-19 | 07:03 | 415:33904 | URBAN | Planned |  | 1 | 577 | 0.000391 | 1e-06 | N
13-03-19 | 08:08 | 801:74119 | URBAN | Planned |  | 33 | 297 | 0.006635 | 2.2e-05 | N
13-03-19 | 11:20 | 813:89061 | LONG RURAL | Planned |  | 1 | 55 | 0.019285 | 0.000351 | N
13-03-19 | 12:00 | 814:82285 | SHORT RURAL | Planned |  | 2 | 55 | 0.00046 | 8e-06 | N
13-03-19 | 09:10 | 807:74184 | SHORT RURAL | Planned |  | 1 | 220 | 0.00092 | 4e-06 | N
13-03-19 | 12:05 | 813:89061 | LONG RURAL | Planned |  | 1 | 40 | 0.014025 | 0.000351 | N
13-03-19 | 10:45 | 814:82285 | SHORT RURAL | Planned |  | 2 | 45 | 0.000376 | 8e-06 | N
13-03-19 | 11:20 | 813:89061 | LONG RURAL | Planned |  | 4 | 35 | 0.049088 | 0.001403 | N
13-03-19 | 10:45 | 802:82225 | SHORT RURAL | Planned |  | 1 | 60 | 0.000251 | 4e-06 | N
13-03-19 | 09:15 | 814:82289 | SHORT RURAL | Planned |  | 2 | 135 | 0.001129 | 8e-06 | N
13-03-19 | 09:25 | 813:89061 | LONG RURAL | Planned |  | 4 | 100 | 0.14025 | 0.001403 | N
13-03-19 | 08:30 | 802:82225 | SHORT RURAL | Planned |  | 2 | 70 | 0.000585 | 8e-06 | N
13-03-19 | 10:05 | 802:82225 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
13-03-19 | 08:25 | 813:89055 | SHORT RURAL | Planned |  | 29 | 530 | 0.064248 | 0.000121 | N
14-03-19 | 08:35 | 801:74121 | LONG RURAL | Planned |  | 7 | 225 | 0.55224 | 0.002454 | N
14-03-19 | 12:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 40 | 0.014025 | 0.000351 | N
15-03-19 | 08:10 | 511:29877 | SHORT RURAL | Planned |  | 6 | 410 | 0.010284 | 2.5e-05 | N
15-03-19 | 09:00 | 261:81879 | URBAN | Planned |  | 141 | 285 | 0.027207 | 9.5e-05 | N
15-03-19 | 08:20 | 512:83743 | SHORT RURAL | Planned |  | 32 | 370 | 0.049496 | 0.000134 | N
14-03-19 | 09:25 | 802:82215 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
14-03-19 | 09:20 | 512:83733 | SHORT RURAL | Planned |  | 27 | 400 | 0.045148 | 0.000113 | N
14-03-19 | 08:50 | 509:33399 | SHORT RURAL | Planned |  | 24 | 275 | 0.02759 | 0.0001 | N
14-03-19 | 09:19 | 232:11457 | SHORT RURAL | Planned |  | 208 | 241 | 0.20955 | 0.00087 | N
14-03-19 | 08:35 | 511:29878 | SHORT RURAL | Planned |  | 30 | 325 | 0.040759 | 0.000125 | N
15-03-19 | 08:13 | 233:82821 | SHORT RURAL | Planned |  | 30 | 97 | 0.012165 | 0.000125 | N
15-03-19 | 09:45 | 232:33407 | SHORT RURAL | Planned |  | 3 | 210 | 0.002634 | 1.3e-05 | N
15-03-19 | 08:30 | 522:83132 | SHORT RURAL | Planned |  | 2 | 335 | 0.002801 | 8e-06 | N
15-03-19 | 19:58 | 415:33904 | URBAN | Planned |  | 1 | 656 | 0.000444 | 1e-06 | N
14-03-19 | 08:40 | 512:83743 | SHORT RURAL | Planned |  | 3 | 170 | 0.002132 | 1.3e-05 | N
14-03-19 | 08:20 | 802:82215 | SHORT RURAL | Planned |  | 2 | 40 | 0.000334 | 8e-06 | N
14-03-19 | 08:35 | 813:89055 | SHORT RURAL | Planned |  | 4 | 55 | 0.00092 | 1.7e-05 | N
14-03-19 | 09:20 | 807:74184 | SHORT RURAL | Planned |  | 2 | 85 | 0.000711 | 8e-06 | N
14-03-19 | 09:08 | 811:74234 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
14-03-19 | 09:20 | 806:82662 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
14-03-19 | 09:45 | 813:89055 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
14-03-19 | 10:04 | 801:74121 | LONG RURAL | Planned |  | 13 | 36 | 0.16409 | 0.004558 | N
14-03-19 | 10:20 | 806:82662 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
14-03-19 | 10:40 | 810:74058 | SHORT RURAL | Planned |  | 2 | 35 | 0.000293 | 8e-06 | N
14-03-19 | 10:15 | 813:89061 | LONG RURAL | Planned |  | 1 | 65 | 0.022791 | 0.000351 | N
14-03-19 | 10:55 | 811:74234 | SHORT RURAL | Planned |  | 1 | 29 | 0.000121 | 4e-06 | N
14-03-19 | 10:50 | 813:89055 | SHORT RURAL | Planned |  | 2 | 45 | 0.000376 | 8e-06 | N
14-03-19 | 11:10 | 806:82662 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
14-03-19 | 11:33 | 811:74234 | SHORT RURAL | Planned |  | 1 | 25 | 0.000105 | 4e-06 | N
14-03-19 | 11:05 | 807:74184 | SHORT RURAL | Planned |  | 1 | 65 | 0.000272 | 4e-06 | N
14-03-19 | 11:30 | 810:74058 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
14-03-19 | 11:50 | 813:89055 | SHORT RURAL | Planned |  | 3 | 45 | 0.000564 | 1.3e-05 | N
14-03-19 | 11:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017532 | 0.000351 | N
14-03-19 | 12:55 | 807:74184 | SHORT RURAL | Planned |  | 1 | 70 | 0.000293 | 4e-06 | N
15-03-19 | 08:45 | 813:89055 | SHORT RURAL | Planned |  | 11 | 110 | 0.005058 | 4.6e-05 | N
15-03-19 | 08:00 | 810:74050 | SHORT RURAL | Planned |  | 3 | 160 | 0.002007 | 1.3e-05 | N
15-03-19 | 09:15 | 801:74121 | LONG RURAL | Planned |  | 5 | 140 | 0.24544 | 0.001753 | N
15-03-19 | 11:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 40 | 0.014025 | 0.000351 | N
15-03-19 | 09:05 | 813:89055 | SHORT RURAL | Planned |  | 17 | 225 | 0.01599 | 7.1e-05 | N
15-03-19 | 12:00 | 810:74062 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
15-03-19 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 4 | 270 | 0.37868 | 0.001403 | N
15-03-19 | 11:00 | 813:89055 | SHORT RURAL | Planned |  | 5 | 120 | 0.002508 | 2.1e-05 | N
15-03-19 | 13:05 | 810:74062 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
15-03-19 | 11:55 | 806:82667 | SHORT RURAL | Planned |  | 3 | 45 | 0.000564 | 1.3e-05 | N
15-03-19 | 09:30 | 806:82667 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
15-03-19 | 10:40 | 806:82667 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
15-03-19 | 08:35 | 801:74119 | URBAN | Planned |  | 33 | 430 | 0.009607 | 2.2e-05 | N
21-03-19 | 22:00 | ZN180:PA19 | URBAN | Planned |  | 61 | 360 | 0.014866 | 4.1e-05 | N
16-10-18 | 08:00 | ZN12610:PA2 | URBAN | Planned |  | 5 | 480 | 0.001633 | 3e-06 | N
18-10-18 | 07:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 67 | 600 | 0.16886 | 0.000281 | N
18-10-18 | 17:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 2 | 1,320 | 0.01109 | 8e-06 | N
21-10-18 | 07:30 | ZN12630:PA3 | SHORT RURAL | Planned |  | 5 | 600 | 0.012602 | 2.1e-05 | N
24-10-18 | 08:00 | ZN12570:PA29 | SHORT RURAL | Planned |  | 57 | 480 | 0.11493 | 0.000239 | N
24-10-18 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 20 | 480 | 0.040326 | 8.4e-05 | N
24-10-18 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 87 | 480 | 0.17542 | 0.000365 | N
25-10-18 | 07:00 | ZN12630:PA10 | SHORT RURAL | Planned |  | 14 | 540 | 0.031745 | 5.9e-05 | N
25-10-18 | 08:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 91 | 420 | 0.16049 | 0.000382 | N
26-10-18 | 02:30 | ZN12650:PA20 | URBAN | Planned |  | 38 | 210 | 0.00543 | 2.6e-05 | N
27-10-18 | 08:00 | ZN12690:PA16 | SHORT RURAL | Planned |  | 15 | 2,100 | 0.13227 | 6.3e-05 | N
29-10-18 | 08:00 | ZN12630:PA10 | SHORT RURAL | Planned |  | 9 | 480 | 0.018134 | 3.8e-05 | N
30-10-18 | 08:00 | ZN12690:PA26 | URBAN | Planned |  | 3 | 480 | 0.000979 | 2e-06 | N
30-10-18 | 09:00 | ZN12570:PA39 | URBAN | Planned |  | 34 | 360 | 0.008319 | 2.3e-05 | N
31-10-18 | 08:00 | ZN12570:PA29 | SHORT RURAL | Planned |  | 31 | 480 | 0.062464 | 0.00013 | N
31-10-18 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 7 | 480 | 0.014105 | 2.9e-05 | N
01-11-18 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 19 | 480 | 0.038284 | 8e-05 | N
01-11-18 | 08:00 | ZN14891:PA8 | SHORT RURAL | Planned |  | 11 | 480 | 0.022164 | 4.6e-05 | N
01-11-18 | 08:00 | ZN8000:PA19 | URBAN | Planned |  | 120 | 420 | 0.034257 | 8.2e-05 | N
01-11-18 | 09:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 84 | 420 | 0.1481 | 0.000353 | N
05-11-18 | 08:00 | ZN35370:PA2 | SHORT RURAL | Planned |  | 86 | 540 | 0.19491 | 0.000361 | N
05-11-18 | 08:00 | ZN12640:PA13 | SHORT RURAL | Planned |  | 53 | 480 | 0.10677 | 0.000222 | N
05-11-18 | 08:00 | ZN12640:PA7 | URBAN | Planned |  | 68 | 480 | 0.022179 | 4.6e-05 | N
06-11-18 | 08:00 | ZN12640:PA8 | SHORT RURAL | Planned |  | 14 | 540 | 0.03173 | 5.9e-05 | N
06-11-18 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 36 | 480 | 0.072525 | 0.000151 | N
06-11-18 | 08:00 | ZN12610:PA13 | SHORT RURAL | Planned |  | 46 | 480 | 0.092671 | 0.000193 | N
06-11-18 | 09:00 | ZN36200:PA4 | SHORT RURAL | Planned |  | 87 | 180 | 0.065726 | 0.000365 | N
07-11-18 | 08:00 | ZN3425:PA43 | URBAN | Planned |  | 195 | 480 | 0.063602 | 0.000133 | N
07-11-18 | 08:00 | ZN12620:PA11 | SHORT RURAL | Planned |  | 1 | 480 | 0.002015 | 4e-06 | N
08-11-18 | 07:00 | ZN80:PA24 | URBAN | Planned |  | 54 | 540 | 0.019815 | 3.7e-05 | N
08-11-18 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 83 | 480 | 0.16721 | 0.000348 | N
09-11-18 | 08:30 | ZN14892:PA21 | URBAN | Planned |  | 57 | 270 | 0.010451 | 3.9e-05 | N
12-11-18 | 08:00 | ZN965:PA4 | URBAN | Planned |  | 137 | 360 | 0.033492 | 9.3e-05 | N
12-11-18 | 08:30 | ZN3154:PA12 | URBAN | Planned |  | 29 | 420 | 0.008271 | 2e-05 | N
12-11-18 | 10:00 | ZN35335:PA9 | URBAN | Planned |  | 1 | 5,820 | 0.003952 | 1e-06 | N
02-11-18 | 07:30 | ZN15008:PA1 | URBAN | Planned |  | 21 | 480 | 0.006851 | 1.4e-05 | N
13-11-18 | 08:00 | ZN12660:PA10 | SHORT RURAL | Planned |  | 101 | 480 | 0.20439 | 0.000426 | N
13-11-18 | 20:30 | ZN15009:PA1 | URBAN | Planned |  | 5 | 300 | 0.001019 | 3e-06 | N
06-11-18 | 21:00 | ZN15009:PA1 | URBAN | Planned |  | 5 | 480 | 0.001631 | 3e-06 | N
14-11-18 | 08:00 | ZN12640:PA4 | URBAN | Planned |  | 318 | 480 | 0.10366 | 0.000216 | N
15-11-18 | 07:30 | ZN2400:PA11 | SHORT RURAL | Planned |  | 144 | 390 | 0.23677 | 0.000607 | N
15-11-18 | 07:00 | ZN12640:PA10 | URBAN | Planned |  | 132 | 600 | 0.053785 | 9e-05 | N
15-11-18 | 07:30 | ZN3425:PA39 | URBAN | Planned |  | 48 | 510 | 0.016625 | 3.3e-05 | N
15-11-18 | 07:30 | ZN3425:PA39 | URBAN | Planned |  | 42 | 510 | 0.014547 | 2.9e-05 | N
16-11-18 | 08:00 | ZN847:PA21 | URBAN | Planned |  | 125 | 420 | 0.035654 | 8.5e-05 | N
17-11-18 | 08:00 | ZN80:PA37 | URBAN | Planned |  | 162 | 420 | 0.04632 | 0.00011 | N
17-11-18 | 08:00 | ZN12690:PA12 | SHORT RURAL | Planned |  | 2 | 480 | 0.004043 | 8e-06 | N
19-11-18 | 07:00 | ZN12600:PA13 | SHORT RURAL | Planned |  | 9 | 600 | 0.022741 | 3.8e-05 | N
19-11-18 | 08:00 | ZN12660:PA16 | URBAN | Planned |  | 137 | 480 | 0.044718 | 9.3e-05 | N
19-11-18 | 09:00 | ZN965:PA42 | URBAN | Planned |  | 23 | 420 | 0.006569 | 1.6e-05 | N
19-11-18 | 09:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 2 | 360 | 0.003032 | 8e-06 | N
20-11-18 | 05:00 | ZN5868:PA24 | URBAN | Planned |  | 19 | 60 | 0.000775 | 1.3e-05 | N
20-11-18 | 05:00 | ZN5868:PA24 | URBAN | Planned |  | 9 | 60 | 0.000367 | 6e-06 | N
20-11-18 | 07:30 | ZN2400:PA22 | SHORT RURAL | Planned |  | 45 | 480 | 0.090966 | 0.00019 | N
20-11-18 | 07:30 | ZN15008:PA1 | URBAN | Planned |  | 87 | 510 | 0.030173 | 5.9e-05 | N
20-11-18 | 08:30 | ZN14892:PA14 | SHORT RURAL | Planned |  | 30 | 150 | 0.018951 | 0.000126 | N
20-11-18 | 08:00 | ZN4545:PA17 | URBAN | Planned |  | 175 | 480 | 0.057123 | 0.000119 | N
20-11-18 | 08:00 | ZN4545:PA21 | URBAN | Planned |  | 103 | 480 | 0.033621 | 7e-05 | N
21-11-18 | 08:30 | ZN14891:PA1 | URBAN | Planned |  | 2 | 420 | 0.000571 | 1e-06 | N
20-11-18 | 21:00 | ZN36300:PA11 | URBAN | Planned |  | 58 | 480 | 0.018932 | 3.9e-05 | N
21-11-18 | 07:30 | ZN2400:PA15 | SHORT RURAL | Planned |  | 45 | 480 | 0.090966 | 0.00019 | N
21-11-18 | 07:00 | ZN13000:PA8 | SHORT RURAL | Planned |  | 98 | 510 | 0.21049 | 0.000413 | N
21-11-18 | 07:00 | ZN1287:PA17 | URBAN | Planned |  | 5 | 570 | 0.001938 | 3e-06 | N
21-11-18 | 08:00 | ZN12570:PA22 | SHORT RURAL | Planned |  | 140 | 240 | 0.1415 | 0.00059 | N
21-11-18 | 09:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 31 | 420 | 0.054832 | 0.000131 | N
21-11-18 | 11:00 | ZN14144:PA10 | SHORT RURAL | Planned |  | 10 | 270 | 0.011371 | 4.2e-05 | N
21-11-18 | 07:30 | ZN2400:PA15 | SHORT RURAL | Planned |  | 34 | 480 | 0.06873 | 0.000143 | N
22-11-18 | 08:00 | ZN965:PA8 | URBAN | Planned |  | 10 | 480 | 0.003264 | 7e-06 | N
22-11-18 | 09:00 | ZN35370:PA2 | SHORT RURAL | Planned |  | 50 | 360 | 0.075806 | 0.000211 | N
23-11-18 | 08:00 | ZN35400:PA101 | URBAN | Planned |  | 92 | 420 | 0.026276 | 6.3e-05 | N
23-11-18 | 08:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 92 | 420 | 0.16273 | 0.000387 | N
24-11-18 | 07:30 | ZN2466:PA27 | URBAN | Planned |  | 29 | 630 | 0.012424 | 2e-05 | N
25-11-18 | 07:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 1 | 600 | 0.002527 | 4e-06 | N
26-11-18 | 19:00 | ZN1285:PA23 | URBAN | Planned |  | 3 | 780 | 0.001588 | 2e-06 | N
27-11-18 | 08:00 | ZN12570:PA40 | SHORT RURAL | Planned |  | 1 | 480 | 0.002022 | 4e-06 | N
27-11-18 | 08:30 | ZN12600:PA9 | SHORT RURAL | Planned |  | 77 | 420 | 0.1362 | 0.000324 | N
27-11-18 | 08:30 | ZN12650:PA6 | URBAN | Planned |  | 72 | 420 | 0.020524 | 4.9e-05 | N
29-11-18 | 07:00 | ZN15009:PA12 | URBAN | Planned |  | 24 | 600 | 0.009774 | 1.6e-05 | N
29-11-18 | 07:30 | ZN690:PA18 | URBAN | Planned |  | 24 | 750 | 0.012218 | 1.6e-05 | N
29-11-18 | 08:00 | ZN15012:PA6 | URBAN | Planned |  | 3 | 420 | 0.000855 | 2e-06 | N
29-11-18 | 18:30 | ZN2310:PA10 | URBAN | Planned |  | 40 | 630 | 0.017105 | 2.7e-05 | N
30-11-18 | 07:30 | ZN35800:PA3 | URBAN | Planned |  | 1 | 240 | 0.000163 | 1e-06 | N
30-11-18 | 08:00 | ZN12660:PA14 | SHORT RURAL | Planned |  | 126 | 480 | 0.25482 | 0.000531 | N
30-11-18 | 08:00 | ZN12610:PA9 | URBAN | Planned |  | 36 | 480 | 0.011723 | 2.4e-05 | N
01-12-18 | 07:00 | ZN2635:PA62 | URBAN | Planned |  | 1 | 360 | 0.000244 | 1e-06 | N
01-12-18 | 12:30 | ZN1193:PA28 | URBAN | Planned |  | 4 | 480 | 0.001303 | 3e-06 | N
03-12-18 | 11:00 | ZN2196:PA21 | URBAN | Planned |  | 237 | 270 | 0.043412 | 0.000161 | N
03-12-18 | 07:00 | ZN15004:PA9 | URBAN | Planned |  | 168 | 600 | 0.068384 | 0.000114 | N
03-12-18 | 08:00 | ZN15011:PA2 | URBAN | Planned |  | 80 | 420 | 0.022795 | 5.4e-05 | N
03-12-18 | 08:00 | ZN35370:PA8 | SHORT RURAL | Planned |  | 1 | 480 | 0.002022 | 4e-06 | N
03-12-18 | 08:00 | ZN12570:PA29 | SHORT RURAL | Planned |  | 3 | 540 | 0.006826 | 1.3e-05 | N
04-12-18 | 07:00 | ZN2400:PA15 | SHORT RURAL | Planned |  | 13 | 540 | 0.029578 | 5.5e-05 | N
04-12-18 | 08:00 | ZN9035:PA11 | URBAN | Planned |  | 14 | 450 | 0.004274 | 9e-06 | N
04-12-18 | 08:00 | ZN180:PA30 | URBAN | Planned |  | 112 | 240 | 0.018236 | 7.6e-05 | N
07-12-18 | 08:00 | ZN14144:PA1 | URBAN | Planned |  | 59 | 540 | 0.021605 | 4e-05 | N
04-12-18 | 11:45 | ZN3922:PA26 | URBAN | Planned |  | 147 | 180 | 0.017951 | 0.0001 | N
05-12-18 | 08:00 | ZN9700:PA23 | URBAN | Planned |  | 13 | 450 | 0.003967 | 9e-06 | N
05-12-18 | 08:00 | ZN10994:PA10 | URBAN | Planned |  | 35 | 540 | 0.012816 | 2.4e-05 | N
05-12-18 | 08:30 | ZN129:PA57 | URBAN | Planned |  | 205 | 450 | 0.062553 | 0.000139 | N
05-12-18 | 08:00 | ZN14891:PA8 | SHORT RURAL | Planned |  | 15 | 480 | 0.030323 | 6.3e-05 | N
06-12-18 | 07:00 | ZN2400:PA15 | SHORT RURAL | Planned |  | 45 | 660 | 0.12508 | 0.00019 | N
06-12-18 | 09:00 | ZN2400:PA11 | SHORT RURAL | Planned |  | 2 | 360 | 0.003032 | 8e-06 | N
06-12-18 | 08:30 | ZN2400:PA11 | SHORT RURAL | Planned |  | 1 | 360 | 0.001516 | 4e-06 | N
06-12-18 | 08:30 | ZN9900:PA2 | URBAN | Planned |  | 17 | 360 | 0.00415 | 1.2e-05 | N
06-12-18 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 38 | 480 | 0.076818 | 0.00016 | N
06-12-18 | 08:00 | ZN14891:PA8 | SHORT RURAL | Planned |  | 12 | 480 | 0.024258 | 5.1e-05 | N
06-12-18 | 21:00 | ZN5868:PA2 | URBAN | Planned |  | 58 | 390 | 0.015339 | 3.9e-05 | N
06-12-18 | 22:00 | ZN15001:PA15 | URBAN | Planned |  | 58 | 480 | 0.018878 | 3.9e-05 | N
06-12-18 | 23:30 | ZN9037:PA15 | URBAN | Planned |  | 21 | 450 | 0.006408 | 1.4e-05 | N
07-12-18 | 08:00 | ZN14891:PA8 | SHORT RURAL | Planned |  | 30 | 480 | 0.060647 | 0.000126 | N
07-12-18 | 08:00 | ZN12570:PA39 | URBAN | Planned |  | 55 | 480 | 0.017902 | 3.7e-05 | N
07-12-18 | 21:00 | ZN5868:PA2 | URBAN | Planned |  | 58 | 390 | 0.015339 | 3.9e-05 | N
22-12-18 | 05:30 | ZN3425:PA43 | URBAN | Planned |  | 38 | 300 | 0.007724 | 2.6e-05 | N
08-12-18 | 10:00 | TS7150:745SRA | URBAN | Planned |  | 1 | 2,880 | 0.001954 | 1e-06 | N
09-12-18 | 08:00 | ZN14892:PA5 | URBAN | Planned |  | 2 | 540 | 0.000733 | 1e-06 | N
09-12-18 | 16:00 | ZN1290:PA11 | URBAN | Planned |  | 1 | 540 | 0.000366 | 1e-06 | N
10-12-18 | 07:30 | ZN15014:PA22 | URBAN | Planned |  | 14 | 540 | 0.005128 | 9e-06 | N
10-12-18 | 07:30 | ZN3155:PA24 | URBAN | Planned |  | 1 | 450 | 0.000305 | 1e-06 | N
10-12-18 | 08:00 | ZN12610:PA7 | URBAN | Planned |  | 64 | 480 | 0.020838 | 4.3e-05 | N
10-12-18 | 08:30 | ZN9900:PA19 | URBAN | Planned |  | 7 | 360 | 0.001709 | 5e-06 | N
10-12-18 | 21:00 | ZN1285:PA31 | URBAN | Planned |  | 4 | 480 | 0.001302 | 3e-06 | N
11-12-18 | 05:00 | ZN187:PA23 | URBAN | Planned |  | 109 | 60 | 0.004434 | 7.4e-05 | N
11-12-18 | 08:00 | ZN12650:PA6 | URBAN | Planned |  | 76 | 570 | 0.029369 | 5.2e-05 | N
11-12-18 | 08:00 | ZN10994:PA19 | URBAN | Planned |  | 3 | 450 | 0.000915 | 2e-06 | N
11-12-18 | 08:00 | ZN15008:PA7 | URBAN | Planned |  | 47 | 420 | 0.013383 | 3.2e-05 | N
11-12-18 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 2 | 480 | 0.004042 | 8e-06 | N
11-12-18 | 20:30 | ZN4545:PA21 | URBAN | Planned |  | 26 | 450 | 0.007932 | 1.8e-05 | N
12-12-18 | 07:00 | ZN15010:PA28 | SHORT RURAL | Planned |  | 169 | 540 | 0.38421 | 0.000712 | N
12-12-18 | 08:00 | ZN9245:PA19 | URBAN | Planned |  | 4 | 450 | 0.00122 | 3e-06 | N
12-12-18 | 07:00 | ZN847:PA18 | SHORT RURAL | Planned |  | 64 | 480 | 0.12933 | 0.000269 | N
12-12-18 | 07:30 | ZN3155:PA24 | URBAN | Planned |  | 1 | 450 | 0.000305 | 1e-06 | N
12-12-18 | 07:30 | ZN262:PA41 | URBAN | Planned |  | 22 | 450 | 0.006712 | 1.5e-05 | N
12-12-18 | 07:30 | ZN262:PA42 | URBAN | Planned |  | 120 | 450 | 0.036609 | 8.1e-05 | N
12-12-18 | 08:00 | ZN15005:PA2 | URBAN | Planned |  | 8 | 540 | 0.002929 | 5e-06 | N
12-12-18 | 09:00 | ZN15006:PA12 | URBAN | Planned |  | 28 | 360 | 0.006834 | 1.9e-05 | N
12-12-18 | 07:30 | ZN3472:PA28 | URBAN | Planned |  | 2 | 450 | 0.00061 | 1e-06 | N
12-12-18 | 19:00 | ZN15001:PA11 | URBAN | Planned |  | 15 | 660 | 0.006712 | 1e-05 | N
12-12-18 | 21:00 | ZN2466:PA27 | URBAN | Planned |  | 1 | 870 | 0.00059 | 1e-06 | N
13-12-18 | 07:30 | ZN9252:PA31 | URBAN | Planned |  | 18 | 570 | 0.006956 | 1.2e-05 | N
13-12-18 | 08:00 | ZN180:PA9 | URBAN | Planned |  | 1 | 360 | 0.000244 | 1e-06 | N
13-12-18 | 08:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 36 | 540 | 0.081844 | 0.000152 | N
13-12-18 | 08:00 | ZN12570:PA29 | SHORT RURAL | Planned |  | 15 | 540 | 0.034102 | 6.3e-05 | N
13-12-18 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 38 | 480 | 0.076792 | 0.00016 | N
13-12-18 | 08:30 | ZN9900:PA2 | URBAN | Planned |  | 40 | 360 | 0.009763 | 2.7e-05 | N
13-12-18 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 1 | 480 | 0.002021 | 4e-06 | N
13-12-18 | 19:00 | ZN80:PA27 | URBAN | Planned |  | 1 | 840 | 0.000569 | 1e-06 | N
13-12-18 | 21:00 | ZN8000:PA38 | URBAN | Planned |  | 25 | 540 | 0.009152 | 1.7e-05 | N
14-12-18 | 06:30 | ZN15001:PA2 | URBAN | Planned |  | 71 | 570 | 0.027438 | 4.8e-05 | N
20-03-19 | 08:20 | 227:13019 | SHORT RURAL | Planned |  | 7 | 418 | 0.012228 | 2.9e-05 | N
20-03-19 | 08:30 | 814:82283 | SHORT RURAL | Planned |  | 24 | 240 | 0.024072 | 0.0001 | N
21-03-19 | 08:30 | 216:10728 | URBAN | Planned |  | 293 | 45 | 0.008926 | 0.000198 | N
21-03-19 | 09:00 | 213:33774 | URBAN | Planned |  | 104 | 192 | 0.013518 | 7e-05 | N
22-03-19 | 09:35 | 807:74179 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
23-03-19 | 10:00 | 224:80341 | URBAN | Planned |  | 91 | 360 | 0.022174 | 6.2e-05 | N
20-03-19 | 08:00 | 235:2123 | URBAN | Planned |  | 87 | 455 | 0.026797 | 5.9e-05 | N
20-03-19 | 08:50 | 232:11453 | SHORT RURAL | Planned |  | 1 | 310 | 0.001296 | 4e-06 | N
20-03-19 | 09:10 | 229:34995 | SHORT RURAL | Planned |  | 15 | 105 | 0.006582 | 6.3e-05 | N
20-03-19 | 09:30 | 528:83020 | SHORT RURAL | Planned |  | 2 | 240 | 0.002006 | 8e-06 | N
21-03-19 | 08:30 | 502:48010 | SHORT RURAL | Planned |  | 3 | 365 | 0.004576 | 1.3e-05 | N
21-03-19 | 08:30 | 233:82819 | SHORT RURAL | Planned |  | 108 | 540 | 0.24373 | 0.000451 | N
21-03-19 | 09:30 | 242:81535 | URBAN | Planned |  | 76 | 240 | 0.012348 | 5.1e-05 | N
21-03-19 | 08:00 | 242:81535 | URBAN | Planned |  | 16 | 40 | 0.000433 | 1.1e-05 | N
21-03-19 | 17:00 | 242:81535 | URBAN | Planned |  | 16 | 25 | 0.000271 | 1.1e-05 | N
22-03-19 | 08:00 | 238:34136 | URBAN | Planned |  | 91 | 255 | 0.015709 | 6.2e-05 | N
22-03-19 | 08:45 | 508:82578 | SHORT RURAL | Planned |  | 5 | 225 | 0.004701 | 2.1e-05 | N
20-03-19 | 08:15 | 801:74121 | LONG RURAL | Planned |  | 2 | 145 | 0.10161 | 0.000701 | N
20-03-19 | 10:38 | 512:83743 | SHORT RURAL | Planned |  | 2 | 50 | 0.000418 | 8e-06 | N
20-03-19 | 08:45 | 807:74184 | SHORT RURAL | Planned |  | 4 | 205 | 0.003427 | 1.7e-05 | N
20-03-19 | 08:05 | 810:74058 | SHORT RURAL | Planned |  | 46 | 275 | 0.052867 | 0.000192 | N
20-03-19 | 08:06 | 523:33509 | URBAN | Planned |  | 47 | 389 | 0.012377 | 3.2e-05 | N
21-03-19 | 08:45 | 523:33501 | SHORT RURAL | Planned |  | 21 | 375 | 0.032911 | 8.8e-05 | N
21-03-19 | 08:58 | 523:33501 | SHORT RURAL | Planned |  | 236 | 417 | 0.41128 | 0.000986 | N
21-03-19 | 08:10 | 523:33501 | SHORT RURAL | Planned |  | 49 | 445 | 0.091127 | 0.000205 | N
22-03-19 | 08:50 | 814:82285 | SHORT RURAL | Planned |  | 3 | 68 | 0.000852 | 1.3e-05 | N
22-03-19 | 08:25 | 812:19072 | SHORT RURAL | Planned |  | 5 | 75 | 0.001567 | 2.1e-05 | N
22-03-19 | 10:05 | 812:19072 | SHORT RURAL | Planned |  | 9 | 45 | 0.001692 | 3.8e-05 | N
22-03-19 | 10:00 | 814:82285 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
22-03-19 | 10:52 | 814:82285 | SHORT RURAL | Planned |  | 1 | 48 | 0.000201 | 4e-06 | N
22-03-19 | 10:40 | 807:74179 | SHORT RURAL | Planned |  | 9 | 60 | 0.002257 | 3.8e-05 | N
22-03-19 | 11:05 | 812:19072 | SHORT RURAL | Planned |  | 6 | 55 | 0.001379 | 2.5e-05 | N
22-03-19 | 11:45 | 814:82285 | SHORT RURAL | Planned |  | 1 | 60 | 0.000251 | 4e-06 | N
22-03-19 | 10:10 | 806:82662 | SHORT RURAL | Planned |  | 3 | 130 | 0.00163 | 1.3e-05 | N
22-03-19 | 12:30 | 806:82662 | SHORT RURAL | Planned |  | 2 | 30 | 0.000251 | 8e-06 | N
22-03-19 | 12:00 | 807:74179 | SHORT RURAL | Planned |  | 1 | 55 | 0.00023 | 4e-06 | N
25-03-19 | 10:40 | 813:89062 | SHORT RURAL | Planned |  | 2 | 50 | 0.000418 | 8e-06 | N
25-03-19 | 09:20 | 813:89062 | SHORT RURAL | Planned |  | 2 | 70 | 0.000585 | 8e-06 | N
26-03-19 | 08:45 | 202:34239 | SHORT RURAL | Planned |  | 1 | 360 | 0.001504 | 4e-06 | N
26-03-19 | 08:25 | 812:19072 | SHORT RURAL | Planned |  | 5 | 505 | 0.010549 | 2.1e-05 | N
27-03-19 | 06:35 | 270:83586 | URBAN | Planned |  | 1 | 215 | 0.000146 | 1e-06 | N
27-03-19 | 11:15 | 814:82285 | SHORT RURAL | Planned |  | 3 | 325 | 0.004073 | 1.3e-05 | N
27-03-19 | 07:00 | 235:2120 | SHORT RURAL | Planned |  | 15 | 580 | 0.036347 | 6.3e-05 | N
26-03-19 | 09:24 | 511:29878 | SHORT RURAL | Planned |  | 28 | 27 | 0.003158 | 0.000117 | N
26-03-19 | 09:13 | 233:82815 | SHORT RURAL | Planned |  | 57 | 357 | 0.085012 | 0.000238 | N
26-03-19 | 08:30 | 511:29877 | SHORT RURAL | Planned |  | 6 | 360 | 0.009024 | 2.5e-05 | N
26-03-19 | 08:30 | 507:80914 | SHORT RURAL | Planned |  | 147 | 435 | 0.26714 | 0.000614 | N
26-03-19 | 08:30 | 522:83126 | SHORT RURAL | Planned |  | 49 | 430 | 0.088025 | 0.000205 | N
26-03-19 | 08:10 | 528:83011 | SHORT RURAL | Planned |  | 68 | 402 | 0.1142 | 0.000284 | N
27-03-19 | 09:00 | 511:29878 | SHORT RURAL | Planned |  | 13 | 50 | 0.002716 | 5.4e-05 | N
27-03-19 | 09:30 | 528:83020 | SHORT RURAL | Planned |  | 13 | 188 | 0.01021 | 5.4e-05 | N
27-03-19 | 11:30 | 511:29878 | SHORT RURAL | Planned |  | 1 | 120 | 0.000501 | 4e-06 | N
27-03-19 | 08:15 | 512:83741 | SHORT RURAL | Planned |  | 148 | 355 | 0.2195 | 0.000618 | N
27-03-19 | 08:00 | 235:2120 | SHORT RURAL | Planned |  | 99 | 450 | 0.18612 | 0.000414 | N
27-03-19 | 11:00 | 528:83014 | SHORT RURAL | Planned |  | 3 | 140 | 0.001755 | 1.3e-05 | N
26-03-19 | 08:50 | 807:74179 | SHORT RURAL | Planned |  | 10 | 210 | 0.008773 | 4.2e-05 | N
26-03-19 | 08:50 | 515:35197 | LONG RURAL | Planned |  | 5 | 185 | 0.32399 | 0.001751 | N
27-03-19 | 08:25 | 814:82285 | SHORT RURAL | Planned |  | 2 | 60 | 0.000501 | 8e-06 | N
27-03-19 | 09:25 | 515:35197 | LONG RURAL | Planned |  | 5 | 310 | 0.54291 | 0.001751 | N
27-03-19 | 09:15 | 814:82283 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
27-03-19 | 09:55 | 814:82285 | SHORT RURAL | Planned |  | 3 | 55 | 0.000689 | 1.3e-05 | N
27-03-19 | 10:35 | 814:82283 | SHORT RURAL | Planned |  | 2 | 60 | 0.000501 | 8e-06 | N
27-03-19 | 11:20 | 814:82285 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
27-03-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 4 | 375 | 0.52539 | 0.001401 | N
28-03-19 | 08:00 | 264:81232 | SHORT RURAL | Planned |  | 178 | 420 | 0.31233 | 0.000744 | N
28-03-19 | 09:15 | 813:89055 | SHORT RURAL | Planned |  | 31 | 440 | 0.056986 | 0.00013 | N
28-03-19 | 11:00 | 528:83014 | SHORT RURAL | Planned |  | 6 | 155 | 0.003885 | 2.5e-05 | N
28-03-19 | 08:20 | 511:29878 | SHORT RURAL | Planned |  | 2 | 421 | 0.003518 | 8e-06 | N
28-03-19 | 08:45 | 524:33574 | SHORT RURAL | Planned |  | 23 | 270 | 0.025944 | 9.6e-05 | N
28-03-19 | 08:55 | 516:48067 | SHORT RURAL | Planned |  | 45 | 20 | 0.00376 | 0.000188 | N
28-03-19 | 08:40 | 520:48172 | SHORT RURAL | Planned |  | 2 | 70 | 0.000585 | 8e-06 | N
28-03-19 | 11:20 | 801:74121 | LONG RURAL | Planned |  | 5 | 45 | 0.078809 | 0.001751 | N
28-03-19 | 12:28 | 801:74121 | LONG RURAL | Planned |  | 7 | 22 | 0.05394 | 0.002452 | N
28-03-19 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 3 | 265 | 0.27846 | 0.001051 | N
28-03-19 | 13:15 | 814:82285 | SHORT RURAL | Planned |  | 1 | 25 | 0.000104 | 4e-06 | N
28-03-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 4 | 360 | 0.50438 | 0.001401 | N
28-03-19 | 15:40 | 414:LD1 | URBAN | Planned |  | 1 | 45 | 3e-05 | 1e-06 | N
28-03-19 | 09:15 | 813:89061 | LONG RURAL | Planned |  | 4 | 440 | 0.61646 | 0.001401 | N
29-03-19 | 08:25 | 507:80922 | SHORT RURAL | Planned |  | 19 | 335 | 0.02659 | 7.9e-05 | N
31-03-19 | 07:35 | 229:34983 | SHORT RURAL | Planned |  | 1 | 490 | 0.002047 | 4e-06 | N
29-03-19 | 10:57 | 807:74184 | SHORT RURAL | Planned |  | 3 | 20 | 0.000251 | 1.3e-05 | N
29-03-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 4 | 285 | 0.3993 | 0.001401 | N
29-03-19 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 6 | 280 | 0.58844 | 0.002102 | N
29-03-19 | 11:30 | 807:74184 | SHORT RURAL | Planned |  | 1 | 80 | 0.000334 | 4e-06 | N
01-04-19 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 1 | 140 | 0.000585 | 4e-06 | N
01-04-19 | 09:00 | 813:89062 | SHORT RURAL | Planned |  | 4 | 440 | 0.007349 | 1.7e-05 | N
02-04-19 | 08:20 | 807:74179 | SHORT RURAL | Planned |  | 11 | 305 | 0.014009 | 4.6e-05 | N
02-04-19 | 08:40 | 507:80932 | SHORT RURAL | Planned |  | 53 | 410 | 0.090735 | 0.000221 | N
03-04-19 | 09:55 | 526:34633 | SHORT RURAL | Planned |  | 2 | 35 | 0.000292 | 8e-06 | N
03-04-19 | 10:10 | 508:82579 | SHORT RURAL | Planned |  | 4 | 120 | 0.002004 | 1.7e-05 | N
03-04-19 | 10:49 | 229:34995 | SHORT RURAL | Planned |  | 166 | 102 | 0.070702 | 0.000693 | N
03-04-19 | 11:30 | 511:29878 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
03-04-19 | 09:35 | 523:33501 | SHORT RURAL | Planned |  | 2 | 170 | 0.00142 | 8e-06 | N
04-04-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 2 | 30 | 0.021001 | 0.0007 | N
04-04-19 | 08:52 | 802:82215 | SHORT RURAL | Planned |  | 36 | 4 | 0.000601 | 0.00015 | N
04-04-19 | 08:52 | 802:82220 | SHORT RURAL | Planned |  | 63 | 4 | 0.001052 | 0.000263 | N
04-04-19 | 08:52 | 802:82225 | SHORT RURAL | Planned |  | 106 | 4 | 0.001771 | 0.000443 | N
04-04-19 | 09:17 | 811:74234 | SHORT RURAL | Planned |  | 1 | 88 | 0.000367 | 4e-06 | N
04-04-19 | 09:20 | 807:74184 | SHORT RURAL | Planned |  | 5 | 215 | 0.004489 | 2.1e-05 | N
04-04-19 | 09:00 | 810:74062 | SHORT RURAL | Planned |  | 22 | 300 | 0.02756 | 9.2e-05 | N
04-04-19 | 08:20 | 812:19065 | SHORT RURAL | Planned |  | 5 | 480 | 0.010022 | 2.1e-05 | N
06-04-19 | 17:37 | 516:48067 | SHORT RURAL | Planned |  | 70 | 1 | 0.000292 | 0.000292 | N
06-04-19 | 08:30 | 507:80926 | URBAN | Planned |  | 2 | 320 | 0.000433 | 1e-06 | N
07-04-19 | 07:00 | 525:34589 | URBAN | Planned |  | 1 | 305 | 0.000206 | 1e-06 | N
05-04-19 | 08:30 | 511:29878 | SHORT RURAL | Planned |  | 1 | 45 | 0.000188 | 4e-06 | N
05-04-19 | 08:55 | 511:29878 | SHORT RURAL | Planned |  | 1 | 25 | 0.000104 | 4e-06 | N
05-04-19 | 10:30 | 511:29878 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
05-04-19 | 11:00 | 511:29878 | SHORT RURAL | Planned |  | 1 | 100 | 0.000418 | 4e-06 | N
07-04-19 | 07:00 | 525:34586 | SHORT RURAL | Planned |  | 2 | 305 | 0.002547 | 8e-06 | N
05-04-19 | 09:25 | 812:19072 | SHORT RURAL | Planned |  | 6 | 201 | 0.005036 | 2.5e-05 | N
09-04-19 | 21:00 | ZN36800:PA56 | URBAN | Planned |  | 158 | 480 | 0.051321 | 0.000107 | N
10-04-19 | 09:18 | ZN847:PA22 | URBAN | Planned |  | 100 | 432 | 0.029202 | 6.8e-05 | N
08-04-19 | 08:15 | 227:13019 | SHORT RURAL | Planned |  | 7 | 465 | 0.013592 | 2.9e-05 | N
08-04-19 | 08:10 | 532:83307 | SHORT RURAL | Planned |  | 13 | 460 | 0.024971 | 5.4e-05 | N
09-04-19 | 08:30 | 213:33773 | URBAN | Planned |  | 98 | 430 | 0.028516 | 6.6e-05 | N
09-04-19 | 08:50 | 509:33395 | LONG RURAL | Planned |  | 184 | 380 | 24.4732 | 0.064403 | N
10-04-19 | 09:50 | 508:82578 | SHORT RURAL | Planned |  | 34 | 330 | 0.046836 | 0.000142 | N
10-04-19 | 07:00 | 235:2120 | SHORT RURAL | Planned |  | 16 | 596 | 0.039807 | 6.7e-05 | N
10-04-19 | 07:00 | 235:2120 | SHORT RURAL | Planned |  | 22 | 596 | 0.054734 | 9.2e-05 | N
08-04-19 | 08:45 | 811:74234 | SHORT RURAL | Planned |  | 3 | 110 | 0.001378 | 1.3e-05 | N
09-04-19 | 09:30 | 515:35197 | LONG RURAL | Planned |  | 2 | 165 | 0.11551 | 0.0007 | N
09-04-19 | 10:55 | 512:83743 | SHORT RURAL | Planned |  | 5 | 90 | 0.001878 | 2.1e-05 | N
09-04-19 | 09:10 | 801:74121 | LONG RURAL | Planned |  | 7 | 275 | 0.67378 | 0.00245 | N
09-04-19 | 08:40 | 814:82291 | SHORT RURAL | Planned |  | 40 | 320 | 0.053432 | 0.000167 | N
09-04-19 | 08:10 | 812:19072 | SHORT RURAL | Planned |  | 68 | 390 | 0.1107 | 0.000284 | N
10-04-19 | 08:00 | 810:74054 | LONG RURAL | Planned |  | 6 | 195 | 0.40952 | 0.0021 | N
10-04-19 | 11:00 | 813:89055 | SHORT RURAL | Planned |  | 2 | 70 | 0.000584 | 8e-06 | N
12-04-19 | 15:15 | ZN4990:PA55ABC | CBD | Planned |  | 21 | 1,695 | 1.1649 | 0.000687 | N
12-04-19 | 21:30 | ZN2835:PA31 | URBAN | Planned |  | 62 | 240 | 0.01007 | 4.2e-05 | N
11-04-19 | 07:00 | 235:2120 | SHORT RURAL | Planned |  | 22 | 510 | 0.046838 | 9.2e-05 | N
12-04-19 | 07:10 | 235:2120 | SHORT RURAL | Planned |  | 22 | 502 | 0.046103 | 9.2e-05 | N
14-04-19 | 07:00 | 216:10728 | URBAN | Planned |  | 1 | 520 | 0.000352 | 1e-06 | N
13-04-19 | 10:45 | 238:34138 | SHORT RURAL | Planned |  | 14 | 40 | 0.002338 | 5.8e-05 | N
14-04-19 | 22:00 | 522:83129 | URBAN | Planned |  | 93 | 467 | 0.029392 | 6.3e-05 | N
14-04-19 | 22:00 | 522:83124 | URBAN | Planned |  | 54 | 467 | 0.017066 | 3.7e-05 | N
11-04-19 | 08:15 | 516:48067 | SHORT RURAL | Planned |  | 14 | 375 | 0.021916 | 5.8e-05 | N
12-04-19 | 09:45 | 813:89055 | SHORT RURAL | Planned |  | 2 | 70 | 0.000584 | 8e-06 | N
12-04-19 | 09:45 | 806:82662 | SHORT RURAL | Planned |  | 26 | 135 | 0.014653 | 0.000109 | N
12-04-19 | 10:10 | 806:82662 | SHORT RURAL | Planned |  | 6 | 115 | 0.00288 | 2.5e-05 | N
12-04-19 | 11:20 | 813:89055 | SHORT RURAL | Planned |  | 1 | 50 | 0.000209 | 4e-06 | N
12-04-19 | 11:15 | 520:48172 | SHORT RURAL | Planned |  | 2 | 110 | 0.000918 | 8e-06 | N
15-04-19 | 20:30 | ZN3472:PA28 | URBAN | Planned |  | 28 | 210 | 0.003979 | 1.9e-05 | N
16-04-19 | 08:45 | 224:80326 | URBAN | Planned |  | 76 | 520 | 0.026745 | 5.1e-05 | N
15-04-19 | 08:30 | 807:74179 | SHORT RURAL | Planned |  | 48 | 300 | 0.060114 | 0.0002 | N
15-04-19 | 10:10 | 806:82662 | SHORT RURAL | Planned |  | 2 | 120 | 0.001002 | 8e-06 | N
15-04-19 | 08:30 | 513:48057 | URBAN | Planned |  | 19 | 315 | 0.00405 | 1.3e-05 | N
16-04-19 | 08:00 | ZN4545:PA36 | URBAN | Planned |  | 85 | 450 | 0.025886 | 5.8e-05 | N
15-04-19 | 08:10 | 512:83741 | SHORT RURAL | Planned |  | 2 | 477 | 0.003983 | 8e-06 | N
16-04-19 | 08:30 | 216:10722 | SHORT RURAL | Planned |  | 56 | 360 | 0.08416 | 0.000234 | N
16-04-19 | 07:20 | 216:10722 | SHORT RURAL | Planned |  | 3 | 400 | 0.00501 | 1.3e-05 | N
16-04-19 | 08:30 | 217:33612 | URBAN | Planned |  | 215 | 420 | 0.061111 | 0.000146 | N
17-04-19 | 11:00 | ZN690:PA30 | URBAN | Planned |  | 39 | 270 | 0.007128 | 2.6e-05 | N
16-04-19 | 08:13 | 256:80650 | URBAN | Planned |  | 168 | 649 | 0.073788 | 0.000114 | N
17-04-19 | 08:53 | 507:80932 | SHORT RURAL | Planned |  | 242 | 427 | 0.43034 | 0.001008 | N
17-04-19 | 09:16 | 223:14397 | URBAN | Planned |  | 337 | 195 | 0.044484 | 0.000228 | N
17-04-19 | 10:12 | 214:8665 | URBAN | Planned |  | 17 | 135 | 0.001554 | 1.2e-05 | N
17-04-19 | 08:30 | 515:35197 | LONG RURAL | Planned |  | 2 | 375 | 0.26242 | 0.0007 | N
17-04-19 | 08:40 | 508:82580 | SHORT RURAL | Planned |  | 65 | 430 | 0.1164 | 0.000271 | N
17-04-19 | 11:45 | 813:89058 | SHORT RURAL | Planned |  | 3 | 55 | 0.000687 | 1.2e-05 | N
17-04-19 | 10:10 | 802:82225 | SHORT RURAL | Planned |  | 4 | 130 | 0.002166 | 1.7e-05 | N
17-04-19 | 10:35 | 814:82283 | SHORT RURAL | Planned |  | 2 | 65 | 0.000541 | 8e-06 | N
17-04-19 | 08:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.017495 | 0.00035 | N
17-04-19 | 09:42 | 813:89061 | LONG RURAL | Planned |  | 1 | 48 | 0.016795 | 0.00035 | N
28-04-19 | 10:36 | ZN931:PA2 | URBAN | Planned |  | 1 | 278 | 0.000188 | 1e-06 | N
18-04-19 | 08:00 | 216:10722 | SHORT RURAL | Planned |  | 92 | 88 | 0.033745 | 0.000383 | N
23-04-19 | 08:00 | 227:13014 | SHORT RURAL | Planned |  | 3 | 435 | 0.005437 | 1.2e-05 | N
23-04-19 | 07:02 | 402:3710 | URBAN | Planned |  | 1 | 580 | 0.000392 | 1e-06 | N
24-04-19 | 09:00 | 216:10722 | SHORT RURAL | Planned |  | 22 | 395 | 0.036204 | 9.2e-05 | N
24-04-19 | 08:15 | 224:80340 | SHORT RURAL | Planned |  | 189 | 445 | 0.3504 | 0.000787 | N
24-04-19 | 07:45 | 217:33610 | URBAN | Planned |  | 87 | 465 | 0.027375 | 5.9e-05 | N
26-04-19 | 08:30 | 220:8691 | URBAN | Planned |  | 141 | 30 | 0.002862 | 9.5e-05 | N
28-04-19 | 07:00 | 810:74050 | SHORT RURAL | Planned |  | 136 | 670 | 0.37952 | 0.000566 | N
28-04-19 | 07:00 | 810:74054 | LONG RURAL | Planned |  | 317 | 670 | 74.3142 | 0.11092 | N
28-04-19 | 07:00 | 810:74058 | SHORT RURAL | Planned |  | 196 | 670 | 0.54695 | 0.000816 | N
28-04-19 | 07:00 | 810:74062 | SHORT RURAL | Planned |  | 580 | 670 | 1.6185 | 0.002416 | N
29-04-19 | 09:10 | 814:82289 | SHORT RURAL | Planned |  | 54 | 170 | 0.038235 | 0.000225 | N
18-04-19 | 08:00 | 509:33399 | SHORT RURAL | Planned |  | 52 | 485 | 0.10512 | 0.000217 | N
18-04-19 | 08:40 | 509:33399 | SHORT RURAL | Planned |  | 100 | 480 | 0.20007 | 0.000417 | N
18-04-19 | 09:00 | 515:35192 | SHORT RURAL | Planned |  | 2 | 125 | 0.001042 | 8e-06 | N
18-04-19 | 08:20 | 812:19071 | SHORT RURAL | Planned |  | 19 | 275 | 0.021778 | 7.9e-05 | N
18-04-19 | 08:40 | 810:74054 | LONG RURAL | Planned |  | 1 | 60 | 0.020994 | 0.00035 | N
18-04-19 | 08:45 | 807:74184 | SHORT RURAL | Planned |  | 42 | 225 | 0.039389 | 0.000175 | N
18-04-19 | 10:15 | 810:74054 | LONG RURAL | Planned |  | 2 | 45 | 0.031491 | 0.0007 | N
18-04-19 | 11:10 | 810:74054 | LONG RURAL | Planned |  | 1 | 50 | 0.017495 | 0.00035 | N
18-04-19 | 13:20 | 523:33501 | SHORT RURAL | Planned |  | 1 | 60 | 0.00025 | 4e-06 | N
24-04-19 | 08:30 | 812:19071 | SHORT RURAL | Planned |  | 19 | 195 | 0.015436 | 7.9e-05 | N
24-04-19 | 08:33 | 513:48056 | SHORT RURAL | Planned |  | 2 | 60 | 0.0005 | 8e-06 | N
26-04-19 | 05:10 | 810:74062 | SHORT RURAL | Planned |  | 50 | 30 | 0.00625 | 0.000208 | N
26-04-19 | 13:03 | 516:48067 | SHORT RURAL | Planned |  | 1 | 72 | 0.0003 | 4e-06 | N
29-04-19 | 08:45 | 811:74234 | SHORT RURAL | Planned |  | 1 | 68 | 0.000283 | 4e-06 | N
29-04-19 | 08:20 | 261:81879 | URBAN | Planned |  | 101 | 325 | 0.022207 | 6.8e-05 | N
29-04-19 | 08:45 | 812:19072 | SHORT RURAL | Planned |  | 2 | 40 | 0.000333 | 8e-06 | N
29-04-19 | 09:00 | 811:74234 | SHORT RURAL | Planned |  | 32 | 155 | 0.020659 | 0.000133 | N
29-04-19 | 09:35 | 812:19072 | SHORT RURAL | Planned |  | 3 | 45 | 0.000562 | 1.2e-05 | N
29-04-19 | 09:55 | 811:74234 | SHORT RURAL | Planned |  | 3 | 45 | 0.000562 | 1.2e-05 | N
29-04-19 | 10:25 | 812:19072 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
29-04-19 | 10:50 | 811:74234 | SHORT RURAL | Planned |  | 1 | 55 | 0.000229 | 4e-06 | N
30-04-19 | 08:30 | 221:11900 | URBAN | Planned |  | 204 | 370 | 0.051065 | 0.000138 | N
30-04-19 | 08:40 | 522:83123 | SHORT RURAL | Planned |  | 14 | 275 | 0.016035 | 5.8e-05 | N
30-04-19 | 08:10 | 508:82578 | SHORT RURAL | Planned |  | 34 | 410 | 0.058061 | 0.000142 | N
30-04-19 | 08:45 | 512:83743 | SHORT RURAL | Planned |  | 5 | 80 | 0.001666 | 2.1e-05 | N
30-04-19 | 08:50 | 814:82289 | SHORT RURAL | Planned |  | 1 | 65 | 0.000271 | 4e-06 | N
30-04-19 | 08:20 | 813:89059 | URBAN | Planned |  | 82 | 370 | 0.020526 | 5.5e-05 | N
30-04-19 | 10:10 | 814:82289 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
30-04-19 | 11:15 | 814:82289 | SHORT RURAL | Planned |  | 1 | 65 | 0.000271 | 4e-06 | N
30-04-19 | 18:20 | 202:34254 | URBAN | Planned |  | 87 | 245 | 0.014421 | 5.9e-05 | N
02-05-19 | 21:00 | ZN9700:PA22 | URBAN | Planned |  | 7 | 660 | 0.003126 | 5e-06 | N
01-05-19 | 08:00 | 508:82578 | SHORT RURAL | Planned |  | 8 | 375 | 0.012495 | 3.3e-05 | N
01-05-19 | 20:15 | 240:34849 | URBAN | Planned |  | 162 | 85 | 0.009316 | 0.00011 | N
01-05-19 | 08:40 | 813:89061 | LONG RURAL | Planned |  | 4 | 40 | 0.055983 | 0.0014 | N
01-05-19 | 08:35 | 807:74179 | SHORT RURAL | Planned |  | 1 | 60 | 0.00025 | 4e-06 | N
01-05-19 | 08:30 | 523:33501 | SHORT RURAL | Planned |  | 8 | 100 | 0.003332 | 3.3e-05 | N
01-05-19 | 08:05 | 512:83732 | SHORT RURAL | Planned |  | 4 | 105 | 0.001749 | 1.7e-05 | N
01-05-19 | 09:45 | 807:74179 | SHORT RURAL | Planned |  | 2 | 45 | 0.000375 | 8e-06 | N
01-05-19 | 10:40 | 807:74179 | SHORT RURAL | Planned |  | 2 | 40 | 0.000333 | 8e-06 | N
01-05-19 | 08:35 | 801:74123 | SHORT RURAL | Planned |  | 1 | 200 | 0.000833 | 4e-06 | N
01-05-19 | 11:30 | 807:74179 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
01-05-19 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 1 | 370 | 0.001541 | 4e-06 | N
01-05-19 | 08:05 | 407:MS4 | URBAN | Planned |  | 1 | 415 | 0.000281 | 1e-06 | N
02-05-19 | 08:05 | 223:14397 | URBAN | Planned |  | 122 | 429 | 0.03541 | 8.3e-05 | N
02-05-19 | 09:00 | 514:18137 | SHORT RURAL | Planned |  | 56 | 215 | 0.050148 | 0.000233 | N
02-05-19 | 12:00 | 258:80785 | URBAN | Planned |  | 89 | 125 | 0.007527 | 6e-05 | N
02-05-19 | 08:05 | 509:33399 | SHORT RURAL | Planned |  | 43 | 395 | 0.070745 | 0.000179 | N
02-05-19 | 10:00 | 508:82574 | SHORT RURAL | Planned |  | 42 | 245 | 0.042859 | 0.000175 | N
02-05-19 | 08:30 | 229:34995 | SHORT RURAL | Planned |  | 65 | 465 | 0.12589 | 0.000271 | N
02-05-19 | 09:00 | 242:81538 | URBAN | Planned |  | 124 | 300 | 0.025168 | 8.4e-05 | N
02-05-19 | 08:20 | 810:74054 | LONG RURAL | Planned |  | 5 | 270 | 0.47236 | 0.001749 | N
05-05-19 | 07:30 | ZN80:PA32 | URBAN | Planned |  | 38 | 480 | 0.012338 | 2.6e-05 | N
02-05-19 | 22:20 | 261:81867 | URBAN | Planned |  | 5 | 485 | 0.001641 | 3e-06 | N
02-05-19 | 22:20 | 261:81867 | URBAN | Planned |  | 56 | 485 | 0.018375 | 3.8e-05 | N
03-05-19 | 08:14 | 526:34633 | SHORT RURAL | Planned |  | 14 | 386 | 0.022508 | 5.8e-05 | N
03-05-19 | 21:00 | 261:81867 | URBAN | Planned |  | 56 | 550 | 0.020838 | 3.8e-05 | N
05-05-19 | 08:00 | 224:80340 | SHORT RURAL | Planned |  | 60 | 120 | 0.02998 | 0.00025 | N
05-05-19 | 08:00 | 224:80329 | SHORT RURAL | Planned |  | 4 | 120 | 0.001999 | 1.7e-05 | N
04-05-19 | 08:00 | 524:33570 | SHORT RURAL | Planned |  | 149 | 220 | 0.1365 | 0.00062 | N
03-05-19 | 08:30 | 513:48050 | SHORT RURAL | Planned |  | 15 | 300 | 0.018743 | 6.2e-05 | N
09-05-19 | 07:30 | ZN2835:PA30 | URBAN | Planned |  | 43 | 480 | 0.013962 | 2.9e-05 | N
05-05-19 | 21:00 | 261:81867 | URBAN | Planned |  | 56 | 535 | 0.020267 | 3.8e-05 | N
07-05-19 | 08:30 | 221:11900 | URBAN | Planned |  | 320 | 455 | 0.098494 | 0.000216 | N
07-05-19 | 08:30 | 224:80329 | SHORT RURAL | Planned |  | 27 | 270 | 0.030355 | 0.000112 | N
07-05-19 | 08:30 | 224:80332 | URBAN | Planned |  | 53 | 270 | 0.00968 | 3.6e-05 | N
07-05-19 | 07:15 | 257:82003 | URBAN | Planned |  | 92 | 464 | 0.028877 | 6.2e-05 | N
07-05-19 | 08:30 | 522:83123 | SHORT RURAL | Planned |  | 138 | 405 | 0.23272 | 0.000575 | N
07-05-19 | 08:30 | 502:48010 | SHORT RURAL | Planned |  | 13 | 345 | 0.018675 | 5.4e-05 | N
07-05-19 | 08:00 | 229:34983 | SHORT RURAL | Planned |  | 48 | 440 | 0.087942 | 0.0002 | N
08-05-19 | 08:35 | 243:80080 | SHORT RURAL | Planned |  | 8 | 300 | 0.009993 | 3.3e-05 | N
08-05-19 | 08:00 | 204:82699 | URBAN | Planned |  | 101 | 360 | 0.024596 | 6.8e-05 | N
08-05-19 | 09:04 | 217:33612 | URBAN | Planned |  | 102 | 401 | 0.027669 | 6.9e-05 | N
06-05-19 | 10:55 | 264:81244 | SHORT RURAL | Planned |  | 79 | 60 | 0.019737 | 0.000329 | N
06-05-19 | 08:30 | 522:83131 | URBAN | Planned |  | 56 | 375 | 0.014205 | 3.8e-05 | N
07-05-19 | 08:55 | 508:82574 | SHORT RURAL | Planned |  | 2 | 20 | 0.000167 | 8e-06 | N
07-05-19 | 08:35 | 232:11457 | SHORT RURAL | Planned |  | 152 | 380 | 0.24051 | 0.000633 | N
07-05-19 | 08:06 | 509:33395 | LONG RURAL | Planned |  | 46 | 430 | 6.9137 | 0.016078 | N
07-05-19 | 08:30 | 522:83132 | SHORT RURAL | Planned |  | 45 | 414 | 0.077574 | 0.000187 | N
08-05-19 | 09:25 | 524:33580 | SHORT RURAL | Planned |  | 8 | 165 | 0.005496 | 3.3e-05 | N
07-05-19 | 08:45 | 516:48067 | SHORT RURAL | Planned |  | 21 | 195 | 0.017051 | 8.7e-05 | N
07-05-19 | 08:20 | 513:48051 | URBAN | Planned |  | 26 | 355 | 0.006244 | 1.8e-05 | N
10-05-19 | 13:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 49 | 300 | 0.06121 | 0.000204 | N
10-05-19 | 22:33 | ZN195:PA11 | URBAN | Planned |  | 41 | 254 | 0.007048 | 2.8e-05 | N
12-05-19 | 22:15 | ZN2466:PA41 | URBAN | Planned |  | 142 | 471 | 0.045252 | 9.6e-05 | N
09-05-19 | 09:05 | 258:80784 | URBAN | Planned |  | 55 | 195 | 0.007255 | 3.7e-05 | N
09-05-19 | 08:20 | 511:29878 | SHORT RURAL | Planned |  | 109 | 420 | 0.19062 | 0.000454 | N
10-05-19 | 08:46 | 256:80646 | URBAN | Planned |  | 223 | 414 | 0.062453 | 0.000151 | N
12-05-19 | 07:45 | 235:2123 | URBAN | Planned |  | 45 | 315 | 0.009589 | 3e-05 | N
12-05-19 | 19:00 | 216:10728 | URBAN | Planned |  | 1 | 630 | 0.000426 | 1e-06 | N
12-05-19 | 20:50 | 261:81867 | URBAN | Planned |  | 57 | 555 | 0.0214 | 3.9e-05 | N
09-05-19 | 08:30 | 232:33407 | SHORT RURAL | Planned |  | 24 | 520 | 0.051966 | 0.0001 | N
09-05-19 | 21:00 | 240:34849 | URBAN | Planned |  | 90 | 130 | 0.007915 | 6.1e-05 | N
10-05-19 | 08:50 | 532:83309 | URBAN | Planned |  | 51 | 80 | 0.00276 | 3.4e-05 | N
10-05-19 | 10:25 | 233:82821 | SHORT RURAL | Planned |  | 94 | 290 | 0.11351 | 0.000391 | N
11-05-19 | 08:10 | 524:33570 | SHORT RURAL | Planned |  | 149 | 560 | 0.34744 | 0.00062 | N
12-05-19 | 08:30 | 238:34144 | URBAN | Planned |  | 9 | 280 | 0.001705 | 6e-06 | N
12-05-19 | 08:00 | 511:29869 | SHORT RURAL | Planned |  | 14 | 430 | 0.025067 | 5.8e-05 | N
09-05-19 | 09:10 | 807:74179 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
09-05-19 | 10:05 | 807:74179 | SHORT RURAL | Planned |  | 2 | 45 | 0.000375 | 8e-06 | N
09-05-19 | 10:55 | 807:74179 | SHORT RURAL | Planned |  | 6 | 60 | 0.001499 | 2.5e-05 | N
09-05-19 | 13:20 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.013981 | 0.00035 | N
13-05-19 | 08:05 | 243:80074 | SHORT RURAL | Planned |  | 50 | 475 | 0.098919 | 0.000208 | N
13-05-19 | 20:50 | 261:81867 | URBAN | Planned |  | 57 | 550 | 0.021204 | 3.9e-05 | N
15-05-19 | 08:00 | ZN15002:PA2 | URBAN | Planned |  | 75 | 480 | 0.024349 | 5.1e-05 | N
14-05-19 | 08:50 | 814:82289 | SHORT RURAL | Planned |  | 15 | 435 | 0.027177 | 6.2e-05 | N
14-05-19 | 07:45 | 202:34260 | URBAN | Planned |  | 181 | 84 | 0.010284 | 0.000122 | N
14-05-19 | 08:10 | 213:33773 | URBAN | Planned |  | 11 | 563 | 0.004189 | 7e-06 | N
14-05-19 | 08:00 | 270:83586 | URBAN | Planned |  | 93 | 510 | 0.03208 | 6.3e-05 | N
14-05-19 | 08:25 | 509:33395 | LONG RURAL | Planned |  | 3 | 55 | 0.057733 | 0.00105 | N
14-05-19 | 08:00 | 229:34983 | SHORT RURAL | Planned |  | 48 | 460 | 0.091964 | 0.0002 | N
14-05-19 | 08:50 | 523:33501 | SHORT RURAL | Planned |  | 49 | 367 | 0.0749 | 0.000204 | N
14-05-19 | 09:10 | 516:48067 | SHORT RURAL | Planned |  | 3 | 280 | 0.003499 | 1.2e-05 | N
15-05-19 | 21:00 | ZN384:PA76 | URBAN | Planned |  | 139 | 420 | 0.039487 | 9.4e-05 | N
15-05-19 | 08:00 | 217:33612 | URBAN | Planned |  | 102 | 435 | 0.030011 | 6.9e-05 | N
15-05-19 | 08:50 | 807:74184 | SHORT RURAL | Planned |  | 4 | 135 | 0.002249 | 1.7e-05 | N
15-05-19 | 08:25 | 507:80925 | SHORT RURAL | Planned |  | 196 | 395 | 0.32243 | 0.000816 | N
15-05-19 | 11:00 | 807:74184 | SHORT RURAL | Planned |  | 2 | 60 | 0.0005 | 8e-06 | N
15-05-19 | 10:40 | 807:74180 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
15-05-19 | 09:55 | 807:74184 | SHORT RURAL | Planned |  | 1 | 55 | 0.000229 | 4e-06 | N
15-05-19 | 08:10 | 801:74121 | LONG RURAL | Planned |  | 3 | 135 | 0.14171 | 0.00105 | N
15-05-19 | 11:50 | 801:74121 | LONG RURAL | Planned |  | 1 | 45 | 0.015745 | 0.00035 | N
15-05-19 | 10:10 | 814:82289 | SHORT RURAL | Planned |  | 5 | 150 | 0.003123 | 2.1e-05 | N
15-05-19 | 08:40 | 807:74184 | SHORT RURAL | Planned |  | 1 | 60 | 0.00025 | 4e-06 | N
15-05-19 | 12:40 | 801:74121 | LONG RURAL | Planned |  | 1 | 55 | 0.019244 | 0.00035 | N
16-05-19 | 09:00 | 807:74179 | SHORT RURAL | Planned |  | 19 | 137 | 0.010841 | 7.9e-05 | N
16-05-19 | 08:10 | 204:82705 | URBAN | Planned |  | 151 | 357 | 0.036459 | 0.000102 | N
16-05-19 | 09:52 | 220:8691 | URBAN | Planned |  | 83 | 498 | 0.027955 | 5.6e-05 | N
16-05-19 | 12:00 | 807:74183 | SHORT RURAL | Planned |  | 3 | 135 | 0.001687 | 1.2e-05 | N
16-05-19 | 06:55 | 409:6011 | URBAN | Planned |  | 1 | 620 | 0.000419 | 1e-06 | N
16-05-19 | 08:00 | 522:83132 | SHORT RURAL | Planned |  | 1 | 365 | 0.00152 | 4e-06 | N
16-05-19 | 08:20 | 502:48010 | SHORT RURAL | Planned |  | 91 | 365 | 0.13833 | 0.000379 | N
16-05-19 | 08:15 | 502:48004 | URBAN | Planned |  | 127 | 420 | 0.036075 | 8.6e-05 | N
16-05-19 | 09:55 | 814:82289 | SHORT RURAL | Planned |  | 1 | 55 | 0.000229 | 4e-06 | N
16-05-19 | 11:15 | 810:74054 | LONG RURAL | Planned |  | 1 | 50 | 0.017495 | 0.00035 | N
16-05-19 | 11:10 | 814:82289 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
16-05-19 | 12:10 | 814:82289 | SHORT RURAL | Planned |  | 1 | 45 | 0.000187 | 4e-06 | N
16-05-19 | 09:55 | 513:48059 | SHORT RURAL | Planned |  | 7 | 55 | 0.001603 | 2.9e-05 | N
19-05-19 | 08:00 | ZN4545:PA2 | URBAN | Planned |  | 109 | 480 | 0.035386 | 7.4e-05 | N
17-05-19 | 08:05 | 232:11454 | SHORT RURAL | Planned |  | 300 | 95 | 0.11869 | 0.001249 | N
17-05-19 | 08:30 | 802:82220 | SHORT RURAL | Planned |  | 59 | 390 | 0.095829 | 0.000246 | N
17-05-19 | 08:20 | 257:81985 | URBAN | Planned |  | 122 | 380 | 0.031355 | 8.3e-05 | N
17-05-19 | 09:05 | 205:12206 | URBAN | Planned |  | 124 | 365 | 0.030611 | 8.4e-05 | N
17-05-19 | 09:05 | 256:80632 | URBAN | Planned |  | 36 | 365 | 0.008887 | 2.4e-05 | N
17-05-19 | 09:30 | 229:34983 | SHORT RURAL | Planned |  | 31 | 320 | 0.041313 | 0.000129 | N
17-05-19 | 08:00 | 507:80923 | SHORT RURAL | Planned |  | 27 | 480 | 0.053974 | 0.000112 | N
18-05-19 | 07:35 | 235:2120 | SHORT RURAL | Planned |  | 15 | 350 | 0.021864 | 6.2e-05 | N
19-05-19 | 08:30 | 258:80785 | URBAN | Planned |  | 211 | 540 | 0.077063 | 0.000143 | N
17-05-19 | 12:00 | 232:11453 | SHORT RURAL | Planned |  | 2 | 75 | 0.000625 | 8e-06 | N
17-05-19 | 08:30 | 233:82819 | SHORT RURAL | Planned |  | 5 | 345 | 0.007184 | 2.1e-05 | N
17-05-19 | 08:30 | 515:35193 | SHORT RURAL | Planned |  | 3 | 135 | 0.001687 | 1.2e-05 | N
17-05-19 | 08:30 | 802:82225 | SHORT RURAL | Planned |  | 106 | 376 | 0.16599 | 0.000441 | N
20-05-19 | 21:03 | ZN4545:PA32 | URBAN | Planned |  | 90 | 402 | 0.024467 | 6.1e-05 | N
20-05-19 | 19:00 | ZN4545:PA32 | URBAN | Planned |  | 85 | 660 | 0.037943 | 5.7e-05 | N
17-05-19 | 16:15 | 261:81864 | URBAN | Planned |  | 15 | 65 | 0.000659 | 1e-05 | N
20-05-19 | 07:20 | 228:7486 | URBAN | Planned |  | 1 | 610 | 0.000413 | 1e-06 | N
20-05-19 | 08:25 | 243:80084 | SHORT RURAL | Planned |  | 15 | 575 | 0.03592 | 6.2e-05 | N
21-05-19 | 05:00 | 261:81877 | URBAN | Planned |  | 3 | 100 | 0.000203 | 2e-06 | N
20-05-19 | 09:38 | 507:80922 | SHORT RURAL | Planned |  | 4 | 59 | 0.000983 | 1.7e-05 | N
20-05-19 | 08:55 | 526:34640 | SHORT RURAL | Planned |  | 1 | 25 | 0.000104 | 4e-06 | N
20-05-19 | 12:00 | 507:80922 | SHORT RURAL | Planned |  | 5 | 65 | 0.001354 | 2.1e-05 | N
20-05-19 | 13:20 | 515:35197 | LONG RURAL | Planned |  | 2 | 40 | 0.027992 | 0.0007 | N
21-05-19 | 09:00 | 227:13015 | SHORT RURAL | Planned |  | 55 | 455 | 0.10422 | 0.000229 | N
21-05-19 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 75 | 220 | 0.068718 | 0.000312 | N
21-05-19 | 07:15 | 813:89061 | LONG RURAL | Planned |  | 4 | 540 | 0.75577 | 0.0014 | N
21-05-19 | 07:35 | 216:10722 | SHORT RURAL | Planned |  | 31 | 535 | 0.069072 | 0.000129 | N
21-05-19 | 09:30 | 242:81539 | URBAN | Planned |  | 126 | 100 | 0.008522 | 8.5e-05 | N
21-05-19 | 08:30 | 233:82819 | SHORT RURAL | Planned |  | 5 | 320 | 0.006664 | 2.1e-05 | N
21-05-19 | 08:00 | 229:34992 | SHORT RURAL | Planned |  | 9 | 446 | 0.016717 | 3.7e-05 | N
21-05-19 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 46 | 492 | 7.9188 | 0.016095 | N
21-05-19 | 09:50 | 511:29880 | URBAN | Planned |  | 73 | 340 | 0.016787 | 4.9e-05 | N
21-05-19 | 08:30 | 522:83123 | SHORT RURAL | Planned |  | 138 | 695 | 0.39944 | 0.000575 | N
22-05-19 | 08:00 | 204:82705 | URBAN | Planned |  | 151 | 290 | 0.029618 | 0.000102 | N
22-05-19 | 08:40 | 204:82691 | URBAN | Planned |  | 147 | 250 | 0.024856 | 9.9e-05 | N
22-05-19 | 13:15 | 210:83474 | URBAN | Planned |  | 51 | 80 | 0.00276 | 3.4e-05 | N
22-05-19 | 08:50 | 216:10722 | SHORT RURAL | Planned |  | 31 | 25 | 0.003228 | 0.000129 | N
22-05-19 | 22:10 | 221:11895 | URBAN | Planned |  | 9 | 10 | 6.1e-05 | 6e-06 | N
22-05-19 | 08:20 | 233:82819 | SHORT RURAL | Planned |  | 5 | 425 | 0.00885 | 2.1e-05 | N
22-05-19 | 08:05 | 508:82580 | SHORT RURAL | Planned |  | 15 | 390 | 0.024364 | 6.2e-05 | N
22-05-19 | 08:30 | 810:74054 | LONG RURAL | Planned |  | 2 | 40 | 0.027992 | 0.0007 | N
22-05-19 | 09:20 | 810:74054 | LONG RURAL | Planned |  | 2 | 55 | 0.038488 | 0.0007 | N
22-05-19 | 08:47 | 515:35197 | LONG RURAL | Planned |  | 3 | 48 | 0.050385 | 0.00105 | N
22-05-19 | 09:00 | 810:74058 | SHORT RURAL | Planned |  | 1 | 90 | 0.000375 | 4e-06 | N
22-05-19 | 10:08 | 515:35197 | LONG RURAL | Planned |  | 1 | 33 | 0.011547 | 0.00035 | N
22-05-19 | 10:25 | 810:74054 | LONG RURAL | Planned |  | 1 | 35 | 0.012246 | 0.00035 | N
22-05-19 | 10:55 | 515:35197 | LONG RURAL | Planned |  | 3 | 37 | 0.038838 | 0.00105 | N
22-05-19 | 11:15 | 810:74054 | LONG RURAL | Planned |  | 1 | 35 | 0.012246 | 0.00035 | N
22-05-19 | 10:45 | 810:74058 | SHORT RURAL | Planned |  | 2 | 120 | 0.001 | 8e-06 | N
22-05-19 | 08:20 | 812:19072 | SHORT RURAL | Planned |  | 34 | 260 | 0.036816 | 0.000142 | N
28-05-19 | 12:00 | ZN342:PA18 | URBAN | Planned |  | 34 | 120 | 0.002766 | 2.3e-05 | N
23-05-19 | 05:17 | 221:11895 | URBAN | Planned |  | 18 | 38 | 0.000463 | 1.2e-05 | N
23-05-19 | 08:30 | 221:11895 | URBAN | Planned |  | 124 | 155 | 0.013 | 8.4e-05 | N
23-05-19 | 08:15 | 243:80084 | SHORT RURAL | Planned |  | 40 | 500 | 0.083296 | 0.000167 | N
23-05-19 | 10:00 | 810:74050 | SHORT RURAL | Planned |  | 1 | 90 | 0.000375 | 4e-06 | N
23-05-19 | 08:50 | 813:89062 | SHORT RURAL | Planned |  | 1 | 70 | 0.000292 | 4e-06 | N
23-05-19 | 18:23 | 221:11895 | URBAN | Planned |  | 18 | 17 | 0.000207 | 1.2e-05 | N
24-05-19 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 25 | 80 | 0.00833 | 0.000104 | N
27-05-19 | 08:00 | ZN15011:PA10 | URBAN | Planned |  | 56 | 480 | 0.01822 | 3.8e-05 | N
27-05-19 | 08:00 | ZN15011:PA2 | URBAN | Planned |  | 76 | 480 | 0.024727 | 5.2e-05 | N
24-05-19 | 08:10 | 508:82574 | SHORT RURAL | Planned |  | 178 | 395 | 0.29283 | 0.000741 | N
23-05-19 | 08:00 | 509:33399 | SHORT RURAL | Planned |  | 41 | 300 | 0.051227 | 0.000171 | N
23-05-19 | 08:30 | 511:29873 | URBAN | Planned |  | 45 | 510 | 0.015523 | 3e-05 | N
24-05-19 | 07:30 | 233:82819 | SHORT RURAL | Planned |  | 5 | 290 | 0.006039 | 2.1e-05 | N
24-05-19 | 08:00 | 233:82812 | SHORT RURAL | Planned |  | 69 | 65 | 0.018679 | 0.000287 | N
24-05-19 | 08:45 | 238:34150 | SHORT RURAL | Planned |  | 19 | 160 | 0.012661 | 7.9e-05 | N
23-05-19 | 09:10 | 516:48067 | SHORT RURAL | Planned |  | 2 | 45 | 0.000375 | 8e-06 | N
23-05-19 | 08:50 | 810:74050 | SHORT RURAL | Planned |  | 2 | 55 | 0.000458 | 8e-06 | N
23-05-19 | 08:00 | 810:74050 | SHORT RURAL | Planned |  | 2 | 45 | 0.000375 | 8e-06 | N
23-05-19 | 11:10 | 813:89055 | SHORT RURAL | Planned |  | 2 | 55 | 0.000458 | 8e-06 | N
23-05-19 | 11:40 | 813:89062 | SHORT RURAL | Planned |  | 1 | 65 | 0.000271 | 4e-06 | N
23-05-19 | 11:00 | 516:48067 | SHORT RURAL | Planned |  | 1 | 30 | 0.000125 | 4e-06 | N
28-05-19 | 09:20 | 806:82662 | SHORT RURAL | Planned |  | 226 | 350 | 0.32917 | 0.00094 | N
28-05-19 | 09:20 | 806:82667 | SHORT RURAL | Planned |  | 40 | 350 | 0.058261 | 0.000166 | N
23-05-19 | 12:25 | 813:89055 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
23-05-19 | 10:32 | 813:89062 | SHORT RURAL | Planned |  | 1 | 53 | 0.000221 | 4e-06 | N
23-05-19 | 08:55 | 813:89055 | SHORT RURAL | Planned |  | 3 | 120 | 0.001499 | 1.2e-05 | N
23-05-19 | 10:05 | 516:48067 | SHORT RURAL | Planned |  | 1 | 30 | 0.000125 | 4e-06 | N
23-05-19 | 08:00 | 523:33508 | SHORT RURAL | Planned |  | 58 | 570 | 0.13769 | 0.000242 | N
24-05-19 | 08:25 | 801:74123 | SHORT RURAL | Planned |  | 1 | 30 | 0.000125 | 4e-06 | N
24-05-19 | 08:30 | 512:83743 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
24-05-19 | 08:40 | 810:74054 | LONG RURAL | Planned |  | 1 | 53 | 0.018544 | 0.00035 | N
24-05-19 | 08:50 | 807:74184 | SHORT RURAL | Planned |  | 1 | 68 | 0.000283 | 4e-06 | N
24-05-19 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 70 | 0.024493 | 0.00035 | N
24-05-19 | 09:20 | 801:74123 | SHORT RURAL | Planned |  | 1 | 25 | 0.000104 | 4e-06 | N
24-05-19 | 10:10 | 801:74123 | SHORT RURAL | Planned |  | 1 | 25 | 0.000104 | 4e-06 | N
24-05-19 | 10:00 | 807:74184 | SHORT RURAL | Planned |  | 1 | 55 | 0.000229 | 4e-06 | N
24-05-19 | 10:15 | 813:89061 | LONG RURAL | Planned |  | 3 | 60 | 0.062981 | 0.00105 | N
24-05-19 | 10:40 | 810:74054 | LONG RURAL | Planned |  | 1 | 77 | 0.026942 | 0.00035 | N
24-05-19 | 09:40 | 512:83743 | SHORT RURAL | Planned |  | 1 | 130 | 0.000541 | 4e-06 | N
24-05-19 | 11:15 | 801:74123 | SHORT RURAL | Planned |  | 1 | 25 | 0.000104 | 4e-06 | N
24-05-19 | 11:25 | 813:89061 | LONG RURAL | Planned |  | 1 | 105 | 0.036739 | 0.00035 | N
24-05-19 | 11:25 | 812:19072 | SHORT RURAL | Planned |  | 1 | 65 | 0.000271 | 4e-06 | N
24-05-19 | 12:00 | 512:83743 | SHORT RURAL | Planned |  | 1 | 40 | 0.000167 | 4e-06 | N
24-05-19 | 08:00 | 523:33501 | SHORT RURAL | Planned |  | 3 | 375 | 0.004685 | 1.2e-05 | N
26-05-19 | 08:00 | 515:35200 | URBAN | Planned |  | 6 | 320 | 0.001301 | 4e-06 | N
27-05-19 | 10:40 | 814:82283 | SHORT RURAL | Planned |  | 1 | 45 | 0.000187 | 4e-06 | N
27-05-19 | 12:15 | 813:89061 | LONG RURAL | Planned |  | 1 | 20 | 0.006993 | 0.00035 | N
27-05-19 | 08:10 | 508:82579 | SHORT RURAL | Planned |  | 38 | 410 | 0.064836 | 0.000158 | N
27-05-19 | 10:00 | 806:82662 | SHORT RURAL | Planned |  | 6 | 50 | 0.001248 | 2.5e-05 | N
27-05-19 | 08:55 | 513:48059 | SHORT RURAL | Planned |  | 10 | 87 | 0.00362 | 4.2e-05 | N
27-05-19 | 10:28 | 810:74050 | SHORT RURAL | Planned |  | 1 | 37 | 0.000154 | 4e-06 | N
27-05-19 | 09:25 | 813:89055 | SHORT RURAL | Planned |  | 1 | 65 | 0.00027 | 4e-06 | N
27-05-19 | 09:39 | 810:74050 | SHORT RURAL | Planned |  | 1 | 31 | 0.000129 | 4e-06 | N
27-05-19 | 10:40 | 813:89055 | SHORT RURAL | Planned |  | 1 | 45 | 0.000187 | 4e-06 | N
27-05-19 | 08:50 | 814:82283 | SHORT RURAL | Planned |  | 1 | 30 | 0.000125 | 4e-06 | N
27-05-19 | 08:48 | 810:74050 | SHORT RURAL | Planned |  | 1 | 42 | 0.000175 | 4e-06 | N
27-05-19 | 08:15 | 512:83743 | SHORT RURAL | Planned |  | 4 | 230 | 0.003829 | 1.7e-05 | N
27-05-19 | 11:20 | 810:74050 | SHORT RURAL | Planned |  | 1 | 32 | 0.000133 | 4e-06 | N
27-05-19 | 11:35 | 813:89055 | SHORT RURAL | Planned |  | 2 | 45 | 0.000375 | 8e-06 | N
28-05-19 | 08:35 | 515:35192 | SHORT RURAL | Planned |  | 1 | 60 | 0.00025 | 4e-06 | N
28-05-19 | 07:50 | 220:8691 | URBAN | Planned |  | 141 | 305 | 0.02915 | 9.6e-05 | N
28-05-19 | 10:00 | 257:81994 | URBAN | Planned |  | 117 | 395 | 0.031325 | 7.9e-05 | N
28-05-19 | 08:30 | 813:89062 | SHORT RURAL | Planned |  | 4 | 430 | 0.007158 | 1.7e-05 | N
28-05-19 | 21:10 | 202:34254 | URBAN | Planned |  | 86 | 65 | 0.003789 | 5.8e-05 | N
28-05-19 | 21:55 | 528:83022 | URBAN | Planned |  | 13 | 100 | 0.000881 | 9e-06 | N
28-05-19 | 08:15 | 232:11454 | SHORT RURAL | Planned |  | 86 | 415 | 0.14852 | 0.000358 | N
28-05-19 | 08:05 | 526:34639 | SHORT RURAL | Planned |  | 25 | 460 | 0.047857 | 0.000104 | N
28-05-19 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 46 | 542 | 8.7175 | 0.016084 | N
28-05-19 | 23:00 | 507:80931 | URBAN | Planned |  | 105 | 92 | 0.006548 | 7.1e-05 | N
28-05-19 | 12:05 | 814:82283 | SHORT RURAL | Planned |  | 2 | 85 | 0.000707 | 8e-06 | N
28-05-19 | 11:40 | 515:35192 | SHORT RURAL | Planned |  | 1 | 80 | 0.000333 | 4e-06 | N
28-05-19 | 10:15 | 515:35192 | SHORT RURAL | Planned |  | 1 | 65 | 0.00027 | 4e-06 | N
28-05-19 | 08:40 | 523:33508 | SHORT RURAL | Planned |  | 25 | 100 | 0.010404 | 0.000104 | N
28-05-19 | 08:30 | 814:82285 | SHORT RURAL | Planned |  | 1 | 65 | 0.00027 | 4e-06 | N
28-05-19 | 08:30 | 813:89062 | SHORT RURAL | Planned |  | 1 | 430 | 0.001789 | 4e-06 | N
29-05-19 | 05:10 | 202:34231 37 42 | URBAN | Planned |  | 2 | 80 | 0.000108 | 1e-06 | N
29-05-19 | 12:30 | 807:74183 | SHORT RURAL | Planned |  | 5 | 70 | 0.001456 | 2.1e-05 | N
29-05-19 | 08:00 | 507:80917 | URBAN | Planned |  | 69 | 135 | 0.006312 | 4.7e-05 | N
29-05-19 | 12:35 | 507:80917 | URBAN | Planned |  | 83 | 35 | 0.001969 | 5.6e-05 | N
29-05-19 | 07:55 | 233:82819 | SHORT RURAL | Planned |  | 5 | 380 | 0.007904 | 2.1e-05 | N
29-05-19 | 08:17 | 229:34983 | SHORT RURAL | Planned |  | 2 | 338 | 0.002812 | 8e-06 | N
29-05-19 | 09:15 | 264:81244 | SHORT RURAL | Planned |  | 50 | 370 | 0.076961 | 0.000208 | N
29-05-19 | 09:15 | 238:34137 | SHORT RURAL | Planned |  | 2 | 361 | 0.003004 | 8e-06 | N
29-05-19 | 08:50 | 513:48059 | SHORT RURAL | Planned |  | 1 | 60 | 0.00025 | 4e-06 | N
29-05-19 | 09:00 | 801:74121 | LONG RURAL | Planned |  | 2 | 210 | 0.14685 | 0.000699 | N
29-05-19 | 08:00 | 513:48050 | SHORT RURAL | Planned |  | 6 | 220 | 0.005491 | 2.5e-05 | N
29-05-19 | 08:45 | 811:74234 | SHORT RURAL | Planned |  | 8 | 145 | 0.004826 | 3.3e-05 | N
29-05-19 | 09:15 | 807:74183 | SHORT RURAL | Planned |  | 1 | 65 | 0.00027 | 4e-06 | N
29-05-19 | 08:40 | 807:74183 | SHORT RURAL | Planned |  | 24 | 97 | 0.009685 | 0.0001 | N
29-05-19 | 09:45 | 813:89055 | SHORT RURAL | Planned |  | 1 | 55 | 0.000229 | 4e-06 | N
29-05-19 | 10:10 | 513:48059 | SHORT RURAL | Planned |  | 2 | 40 | 0.000333 | 8e-06 | N
29-05-19 | 10:25 | 807:74183 | SHORT RURAL | Planned |  | 1 | 40 | 0.000166 | 4e-06 | N
29-05-19 | 10:40 | 807:74184 | SHORT RURAL | Planned |  | 3 | 20 | 0.00025 | 1.2e-05 | N
29-05-19 | 10:00 | 810:74054 | LONG RURAL | Planned |  | 1 | 70 | 0.024476 | 0.00035 | N
29-05-19 | 10:50 | 813:89055 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
29-05-19 | 11:35 | 807:74184 | SHORT RURAL | Planned |  | 3 | 40 | 0.000499 | 1.2e-05 | N
29-05-19 | 11:20 | 807:74183 | SHORT RURAL | Planned |  | 3 | 60 | 0.000749 | 1.2e-05 | N
29-05-19 | 11:05 | 513:48059 | SHORT RURAL | Planned |  | 2 | 45 | 0.000374 | 8e-06 | N
29-05-19 | 11:10 | 813:89055 | SHORT RURAL | Planned |  | 2 | 85 | 0.000707 | 8e-06 | N
29-05-19 | 11:50 | 813:89055 | SHORT RURAL | Planned |  | 2 | 55 | 0.000458 | 8e-06 | N
30-05-19 | 08:00 | 807:74179 | SHORT RURAL | Planned |  | 4 | 130 | 0.002163 | 1.7e-05 | N
30-05-19 | 09:00 | 206:34441 | URBAN | Planned |  | 101 | 70 | 0.004791 | 6.8e-05 | N
30-05-19 | 07:00 | 261:81885 | URBAN | Planned |  | 119 | 285 | 0.022983 | 8.1e-05 | N
30-05-19 | 08:55 | 810:74058 | SHORT RURAL | Planned |  | 9 | 150 | 0.005616 | 3.7e-05 | N
30-05-19 | 09:15 | 528:83014 | SHORT RURAL | Planned |  | 1 | 40 | 0.000166 | 4e-06 | N
30-05-19 | 12:17 | 238:34148 | SHORT RURAL | Planned |  | 1 | 5 | 2.1e-05 | 4e-06 | N
30-05-19 | 08:10 | 507:80931 | URBAN | Planned |  | 157 | 405 | 0.04309 | 0.000106 | N
30-05-19 | 08:00 | 229:34983 | SHORT RURAL | Planned |  | 47 | 440 | 0.08603 | 0.000196 | N
30-05-19 | 08:00 | 512:83733 | SHORT RURAL | Planned |  | 212 | 420 | 0.37041 | 0.000882 | N
30-05-19 | 12:40 | 507:80917 | URBAN | Planned |  | 128 | 240 | 0.020818 | 8.7e-05 | N
30-05-19 | 08:40 | 814:82289 | SHORT RURAL | Planned |  | 8 | 65 | 0.002163 | 3.3e-05 | N
30-05-19 | 08:40 | 813:89055 | SHORT RURAL | Planned |  | 1 | 85 | 0.000354 | 4e-06 | N
30-05-19 | 08:35 | 806:82662 | SHORT RURAL | Planned |  | 5 | 220 | 0.004576 | 2.1e-05 | N
30-05-19 | 11:40 | 813:89055 | SHORT RURAL | Planned |  | 3 | 90 | 0.001123 | 1.2e-05 | N
30-05-19 | 10:15 | 814:82283 | SHORT RURAL | Planned |  | 4 | 55 | 0.000915 | 1.7e-05 | N
30-05-19 | 10:30 | 813:89055 | SHORT RURAL | Planned |  | 2 | 55 | 0.000458 | 8e-06 | N
31-05-19 | 08:35 | 528:83019 | SHORT RURAL | Planned |  | 183 | 445 | 0.33899 | 0.000762 | N
01-06-19 | 08:35 | 417:80504 | URBAN | Planned |  | 1 | 355 | 0.000241 | 1e-06 | N
31-05-19 | 08:37 | 507:80925 | SHORT RURAL | Planned |  | 2 | 33 | 0.000275 | 8e-06 | N
31-05-19 | 08:55 | 507:80914 | SHORT RURAL | Planned |  | 2 | 55 | 0.000458 | 8e-06 | N
31-05-19 | 08:00 | 242:81539 | URBAN | Planned |  | 259 | 255 | 0.044752 | 0.000175 | N
31-05-19 | 10:00 | 507:80925 | SHORT RURAL | Planned |  | 5 | 55 | 0.001145 | 2.1e-05 | N
31-05-19 | 11:15 | 507:80925 | SHORT RURAL | Planned |  | 1 | 60 | 0.00025 | 4e-06 | N
02-06-19 | 08:30 | 238:34150 | SHORT RURAL | Planned |  | 2 | 450 | 0.003746 | 8e-06 | N
02-06-19 | 09:10 | 235:8685 | URBAN | Planned |  | 114 | 385 | 0.02974 | 7.7e-05 | N
02-06-19 | 09:10 | 235:2728 | URBAN | Planned |  | 149 | 385 | 0.038871 | 0.000101 | N
31-05-19 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 8 | 45 | 0.12587 | 0.002797 | N
31-05-19 | 08:05 | 520:48172 | SHORT RURAL | Planned |  | 4 | 380 | 0.006327 | 1.7e-05 | N
31-05-19 | 08:50 | 812:19072 | SHORT RURAL | Planned |  | 1 | 60 | 0.00025 | 4e-06 | N
31-05-19 | 10:25 | 812:19072 | SHORT RURAL | Planned |  | 2 | 240 | 0.001998 | 8e-06 | N
31-05-19 | 08:30 | 810:74050 | SHORT RURAL | Planned |  | 2 | 120 | 0.000999 | 8e-06 | N
31-05-19 | 09:50 | 807:74180 | SHORT RURAL | Planned |  | 1 | 45 | 0.000187 | 4e-06 | N
31-05-19 | 09:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 60 | 0.020979 | 0.00035 | N
31-05-19 | 10:49 | 810:74050 | SHORT RURAL | Planned |  | 16 | 241 | 0.016051 | 6.7e-05 | N
31-05-19 | 11:05 | 801:74121 | LONG RURAL | Planned |  | 1 | 40 | 0.013986 | 0.00035 | N
31-05-19 | 12:30 | 801:74121 | LONG RURAL | Planned |  | 1 | 55 | 0.019231 | 0.00035 | N
02-06-19 | 07:00 | 513:48057 | URBAN | Planned |  | 22 | 480 | 0.007156 | 1.5e-05 | N
03-06-19 | 08:00 | 235:2120 | SHORT RURAL | Planned |  | 2 | 400 | 0.00333 | 8e-06 | N
03-06-19 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 1 | 65 | 0.000271 | 4e-06 | N
04-06-19 | 08:35 | 813:89062 | SHORT RURAL | Planned |  | 9 | 15 | 0.000562 | 3.7e-05 | N
04-06-19 | 08:00 | 520:48172 | SHORT RURAL | Planned |  | 12 | 50 | 0.002497 | 5e-05 | N
04-06-19 | 08:40 | 523:33501 | SHORT RURAL | Planned |  | 6 | 120 | 0.002996 | 2.5e-05 | N
04-06-19 | 09:00 | 814:82291 | SHORT RURAL | Planned |  | 4 | 120 | 0.001997 | 1.7e-05 | N
04-06-19 | 08:15 | 813:89047 | SHORT RURAL | Planned |  | 1 | 405 | 0.001685 | 4e-06 | N
04-06-19 | 08:30 | 520:48172 | SHORT RURAL | Planned |  | 1 | 70 | 0.000291 | 4e-06 | N
04-06-19 | 09:25 | 813:89062 | SHORT RURAL | Planned |  | 3 | 60 | 0.000749 | 1.2e-05 | N
05-06-19 | 10:25 | 243:80081 | SHORT RURAL | Planned |  | 53 | 40 | 0.008822 | 0.000221 | N
05-06-19 | 08:55 | 514:18137 | SHORT RURAL | Planned |  | 14 | 95 | 0.005534 | 5.8e-05 | N
05-06-19 | 08:55 | 814:82289 | SHORT RURAL | Planned |  | 5 | 95 | 0.001977 | 2.1e-05 | N
05-06-19 | 08:35 | 511:29878 | SHORT RURAL | Planned |  | 195 | 330 | 0.26778 | 0.000811 | N
05-06-19 | 08:25 | 813:89062 | SHORT RURAL | Planned |  | 1 | 75 | 0.000312 | 4e-06 | N
05-06-19 | 10:15 | 813:89062 | SHORT RURAL | Planned |  | 2 | 50 | 0.000416 | 8e-06 | N
05-06-19 | 11:20 | 813:89062 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
07-06-19 | 08:30 | ZN36100:PA21 | URBAN | Planned |  | 42 | 390 | 0.011098 | 2.8e-05 | N
12-06-19 | 09:00 | ZN4545:PA40 | URBAN | Planned |  | 118 | 300 | 0.023979 | 8e-05 | N
18-06-19 | 08:00 | 509:33399 | SHORT RURAL | Planned |  | 24 | 535 | 0.053394 | 0.0001 | N
18-06-19 | 10:09 | 515:35197 | LONG RURAL | Planned |  | 1 | 109 | 0.037931 | 0.000349 | N
18-06-19 | 08:30 | 216:10728 | URBAN | Planned |  | 294 | 506 | 0.10076 | 0.000199 | N
18-06-19 | 10:00 | ZN1788:PA15 | URBAN | Planned |  | 67 | 240 | 0.010891 | 4.5e-05 | N
18-06-19 | 20:30 | ZN15012:PA6 | URBAN | Planned |  | 52 | 197 | 0.006938 | 3.5e-05 | N
19-06-19 | 21:30 | ZN262:PA15 | URBAN | Planned |  | 111 | 240 | 0.018057 | 7.5e-05 | N
06-06-19 | 08:00 | 264:81236 | URBAN | Planned |  | 224 | 365 | 0.055394 | 0.000152 | N
07-06-19 | 00:00 | 224:80346 | URBAN | Planned |  | 387 | 115 | 0.030154 | 0.000262 | N
07-06-19 | 10:15 | 520:48172 | SHORT RURAL | Planned |  | 1 | 30 | 0.000125 | 4e-06 | N
07-06-19 | 08:10 | 232:11454 | SHORT RURAL | Planned |  | 2 | 195 | 0.001623 | 8e-06 | N
07-06-19 | 08:30 | 526:34633 | SHORT RURAL | Planned |  | 3 | 198 | 0.002472 | 1.2e-05 | N
07-06-19 | 08:00 | 240:34849 | URBAN | Planned |  | 162 | 435 | 0.047746 | 0.00011 | N
07-06-19 | 19:00 | 205:12206 | URBAN | Planned |  | 45 | 80 | 0.002439 | 3e-05 | N
11-06-19 | 07:00 | 532:83302 | URBAN | Planned |  | 6 | 50 | 0.000203 | 4e-06 | N
11-06-19 | 08:05 | 238:34141 | SHORT RURAL | Planned |  | 15 | 435 | 0.027144 | 6.2e-05 | N
11-06-19 | 08:30 | 221:11899 | SHORT RURAL | Planned |  | 93 | 380 | 0.14702 | 0.000387 | N
12-06-19 | 08:40 | 204:82689 | URBAN | Planned |  | 143 | 265 | 0.025669 | 9.7e-05 | N
12-06-19 | 10:08 | 520:48172 | SHORT RURAL | Planned |  | 1 | 22 | 9.2e-05 | 4e-06 | N
12-06-19 | 09:00 | 813:89061 | LONG RURAL | Planned |  | 24 | 120 | 1.0059 | 0.008383 | N
12-06-19 | 22:30 | 270:83590 | URBAN | Planned |  | 128 | 40 | 0.003468 | 8.7e-05 | N
13-06-19 | 09:00 | 217:33611 | URBAN | Planned |  | 39 | 40 | 0.001057 | 2.6e-05 | N
13-06-19 | 08:05 | 810:74054 | LONG RURAL | Planned |  | 5 | 268 | 0.4682 | 0.001747 | N
13-06-19 | 08:15 | 227:13020 | SHORT RURAL | Planned |  | 84 | 371 | 0.12965 | 0.000349 | N
13-06-19 | 08:05 | 520:48172 | SHORT RURAL | Planned |  | 4 | 380 | 0.006323 | 1.7e-05 | N
14-06-19 | 08:35 | 515:35197 | LONG RURAL | Planned |  | 18 | 190 | 1.1954 | 0.006292 | N
17-06-19 | 08:00 | 502:48010 | SHORT RURAL | Planned |  | 13 | 420 | 0.022714 | 5.4e-05 | N
18-06-19 | 08:20 | 515:35197 | LONG RURAL | Planned |  | 32 | 437 | 4.8827 | 0.011173 | N
06-06-19 | 12:29 | 509:33399 | SHORT RURAL | Planned |  | 3 | 5 | 6.2e-05 | 1.2e-05 | N
06-06-19 | 09:15 | 238:34144 | URBAN | Planned |  | 117 | 225 | 0.017836 | 7.9e-05 | N
06-06-19 | 08:40 | 509:33399 | SHORT RURAL | Planned |  | 43 | 336 | 0.060122 | 0.000179 | N
07-06-19 | 09:15 | 509:33395 | LONG RURAL | Planned |  | 1 | 85 | 0.0297 | 0.000349 | N
07-06-19 | 12:10 | 230:81440 | URBAN | Planned |  | 76 | 65 | 0.003347 | 5.1e-05 | N
07-06-19 | 08:14 | 233:82819 | SHORT RURAL | Planned |  | 20 | 426 | 0.035453 | 8.3e-05 | N
11-06-19 | 08:20 | 511:29878 | SHORT RURAL | Planned |  | 1 | 140 | 0.000582 | 4e-06 | N
11-06-19 | 09:30 | 509:33395 | LONG RURAL | Planned |  | 3 | 190 | 0.19909 | 0.001048 | N
12-06-19 | 09:00 | 509:33395 | LONG RURAL | Planned |  | 33 | 215 | 2.4782 | 0.011526 | N
12-06-19 | 08:00 | 507:80932 | SHORT RURAL | Planned |  | 198 | 280 | 0.23063 | 0.000824 | N
12-06-19 | 08:10 | 229:34983 | SHORT RURAL | Planned |  | 47 | 400 | 0.078209 | 0.000196 | N
13-06-19 | 08:40 | 509:33395 | LONG RURAL | Planned |  | 11 | 185 | 0.71104 | 0.003843 | N
13-06-19 | 08:00 | 511:29877 | SHORT RURAL | Planned |  | 105 | 30 | 0.013104 | 0.000437 | N
13-06-19 | 08:20 | 508:82579 | SHORT RURAL | Planned |  | 7 | 420 | 0.012231 | 2.9e-05 | N
14-06-19 | 10:00 | 230:81440 | URBAN | Planned |  | 162 | 110 | 0.012071 | 0.00011 | N
14-06-19 | 08:30 | 509:33395 | LONG RURAL | Planned |  | 1 | 150 | 0.052429 | 0.00035 | N
14-06-19 | 08:45 | 233:82815 | SHORT RURAL | Planned |  | 22 | 160 | 0.014643 | 9.2e-05 | N
17-06-19 | 08:35 | 528:83024 | URBAN | Planned |  | 2 | 20 | 2.7e-05 | 1e-06 | N
17-06-19 | 08:40 | 512:83732 | SHORT RURAL | Planned |  | 42 | 80 | 0.013978 | 0.000175 | N
17-06-19 | 10:00 | 532:83298 | SHORT RURAL | Planned |  | 2 | 56 | 0.000466 | 8e-06 | N
18-06-19 | 12:00 | 507:80932 | SHORT RURAL | Planned |  | 4 | 65 | 0.001081 | 1.7e-05 | N
18-06-19 | 11:05 | 522:83124 | URBAN | Planned |  | 82 | 45 | 0.002499 | 5.6e-05 | N
18-06-19 | 08:45 | 507:80932 | SHORT RURAL | Planned |  | 106 | 80 | 0.035263 | 0.000441 | N
18-06-19 | 09:00 | 507:80923 | SHORT RURAL | Planned |  | 85 | 35 | 0.012371 | 0.000353 | N
18-06-19 | 13:05 | 526:34643 | SHORT RURAL | Planned |  | 52 | 45 | 0.009731 | 0.000216 | N
20-06-19 | 17:00 | ZN3155:PA33 | URBAN | Planned |  | 52 | 180 | 0.006345 | 3.5e-05 | N
26-06-19 | 09:27 | ZN2835:PA32 | SHORT RURAL | Planned |  | 1 | 543 | 0.002259 | 4e-06 | N
26-06-19 | 08:00 | ZN12640:PA10 | URBAN | Planned |  | 224 | 540 | 0.081746 | 0.000151 | N
06-06-19 | 08:10 | 813:89058 | SHORT RURAL | Planned |  | 1 | 80 | 0.000333 | 4e-06 | N
06-06-19 | 10:45 | 813:89061 | LONG RURAL | Planned |  | 1 | 50 | 0.01747 | 0.000349 | N
06-06-19 | 08:40 | 807:74184 | SHORT RURAL | Planned |  | 9 | 185 | 0.006929 | 3.7e-05 | N
06-06-19 | 08:00 | 514:18137 | SHORT RURAL | Planned |  | 3 | 360 | 0.004494 | 1.2e-05 | N
06-06-19 | 09:10 | 801:74123 | SHORT RURAL | Planned |  | 58 | 275 | 0.066372 | 0.000241 | N
06-06-19 | 08:40 | 813:89055 | SHORT RURAL | Planned |  | 21 | 385 | 0.033644 | 8.7e-05 | N
06-06-19 | 08:40 | 813:89063 | SHORT RURAL | Planned |  | 19 | 390 | 0.030835 | 7.9e-05 | N
07-06-19 | 09:30 | 814:82289 | SHORT RURAL | Planned |  | 3 | 60 | 0.000749 | 1.2e-05 | N
07-06-19 | 08:15 | 520:48172 | SHORT RURAL | Planned |  | 1 | 65 | 0.00027 | 4e-06 | N
07-06-19 | 12:10 | 811:74234 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
07-06-19 | 11:25 | 814:82283 | SHORT RURAL | Planned |  | 1 | 70 | 0.000291 | 4e-06 | N
07-06-19 | 11:35 | 807:74184 | SHORT RURAL | Planned |  | 2 | 45 | 0.000375 | 8e-06 | N
07-06-19 | 09:30 | 520:48172 | SHORT RURAL | Planned |  | 3 | 145 | 0.00181 | 1.2e-05 | N
07-06-19 | 10:10 | 811:74234 | SHORT RURAL | Planned |  | 1 | 95 | 0.000395 | 4e-06 | N
07-06-19 | 11:00 | 520:48172 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
07-06-19 | 09:50 | 807:74184 | SHORT RURAL | Planned |  | 1 | 85 | 0.000354 | 4e-06 | N
07-06-19 | 08:45 | 807:74184 | SHORT RURAL | Planned |  | 3 | 50 | 0.000624 | 1.2e-05 | N
07-06-19 | 13:25 | 811:74234 | SHORT RURAL | Planned |  | 4 | 45 | 0.000749 | 1.7e-05 | N
09-06-19 | 07:25 | 513:48056 | SHORT RURAL | Planned |  | 5 | 320 | 0.006656 | 2.1e-05 | N
11-06-19 | 08:45 | 515:35197 | LONG RURAL | Planned |  | 3 | 50 | 0.052393 | 0.001048 | N
11-06-19 | 09:20 | 801:74123 | SHORT RURAL | Planned |  | 1 | 40 | 0.000166 | 4e-06 | N
11-06-19 | 08:20 | 810:74050 | SHORT RURAL | Planned |  | 2 | 91 | 0.000757 | 8e-06 | N
11-06-19 | 09:55 | 515:35197 | LONG RURAL | Planned |  | 1 | 35 | 0.012225 | 0.000349 | N
11-06-19 | 09:20 | 514:18137 | SHORT RURAL | Planned |  | 36 | 100 | 0.014976 | 0.00015 | N
11-06-19 | 11:10 | 515:35197 | LONG RURAL | Planned |  | 1 | 40 | 0.013971 | 0.000349 | N
11-06-19 | 09:30 | 813:89061 | LONG RURAL | Planned |  | 1 | 60 | 0.020957 | 0.000349 | N
11-06-19 | 10:32 | 813:89061 | LONG RURAL | Planned |  | 1 | 53 | 0.018512 | 0.000349 | N
11-06-19 | 10:20 | 801:74123 | SHORT RURAL | Planned |  | 1 | 55 | 0.000229 | 4e-06 | N
11-06-19 | 11:30 | 810:74050 | SHORT RURAL | Planned |  | 1 | 57 | 0.000237 | 4e-06 | N
11-06-19 | 08:45 | 814:82289 | SHORT RURAL | Planned |  | 8 | 240 | 0.007987 | 3.3e-05 | N
11-06-19 | 11:50 | 813:89061 | LONG RURAL | Planned |  | 1 | 55 | 0.019211 | 0.000349 | N
12-06-19 | 08:55 | 520:48172 | SHORT RURAL | Planned |  | 1 | 35 | 0.000146 | 4e-06 | N
12-06-19 | 09:35 | 810:74054 | LONG RURAL | Planned |  | 1 | 70 | 0.02445 | 0.000349 | N
12-06-19 | 10:40 | 520:48172 | SHORT RURAL | Planned |  | 4 | 350 | 0.005824 | 1.7e-05 | N
12-06-19 | 08:50 | 515:35197 | LONG RURAL | Planned |  | 74 | 420 | 10.8557 | 0.025847 | N
12-06-19 | 09:25 | 813:89061 | LONG RURAL | Planned |  | 125 | 160 | 6.9857 | 0.04366 | N
12-06-19 | 09:25 | 813:89061 | LONG RURAL | Planned |  | 18 | 185 | 1.1631 | 0.006287 | N
12-06-19 | 09:25 | 813:89061 | LONG RURAL | Planned |  | 1 | 160 | 0.055885 | 0.000349 | N
12-06-19 | 09:15 | 813:89061 | LONG RURAL | Planned |  | 1 | 170 | 0.059378 | 0.000349 | N
13-06-19 | 08:30 | 801:74123 | SHORT RURAL | Planned |  | 1 | 145 | 0.000603 | 4e-06 | N
13-06-19 | 07:50 | 812:19065 | SHORT RURAL | Planned |  | 5 | 255 | 0.005304 | 2.1e-05 | N
13-06-19 | 10:25 | 810:74054 | LONG RURAL | Planned |  | 2 | 25 | 0.01747 | 0.000699 | N
13-06-19 | 09:25 | 810:74054 | LONG RURAL | Planned |  | 13 | 185 | 0.84032 | 0.004542 | N
13-06-19 | 09:25 | 810:74054 | LONG RURAL | Planned |  | 1 | 55 | 0.019217 | 0.000349 | N
14-06-19 | 08:35 | 813:89061 | LONG RURAL | Planned |  | 3 | 65 | 0.068158 | 0.001049 | N
14-06-19 | 08:40 | 807:74181 | SHORT RURAL | Planned |  | 1 | 55 | 0.000229 | 4e-06 | N
14-06-19 | 09:00 | 814:82283 | SHORT RURAL | Planned |  | 4 | 150 | 0.002496 | 1.7e-05 | N
14-06-19 | 09:55 | 813:89061 | LONG RURAL | Planned |  | 1 | 45 | 0.015729 | 0.00035 | N
16-06-19 | 07:00 | 515:35200 | URBAN | Planned |  | 10 | 450 | 0.003048 | 7e-06 | N
17-06-19 | 08:20 | 813:89063 | SHORT RURAL | Planned |  | 136 | 110 | 0.062234 | 0.000566 | N
18-06-19 | 08:25 | 810:74054 | LONG RURAL | Planned |  | 1 | 25 | 0.008729 | 0.000349 | N
18-06-19 | 09:15 | 810:74054 | LONG RURAL | Planned |  | 1 | 35 | 0.012221 | 0.000349 | N
18-06-19 | 10:00 | 810:74054 | LONG RURAL | Planned |  | 1 | 40 | 0.013966 | 0.000349 | N
18-06-19 | 09:45 | 813:89062 | SHORT RURAL | Planned |  | 1 | 80 | 0.000333 | 4e-06 | N
18-06-19 | 11:00 | 512:83743 | SHORT RURAL | Planned |  | 4 | 40 | 0.000665 | 1.7e-05 | N
18-06-19 | 11:55 | 512:83743 | SHORT RURAL | Planned |  | 3 | 45 | 0.000561 | 1.2e-05 | N
18-06-19 | 08:30 | 526:34637 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
19-06-19 | 08:30 | 528:83024 | URBAN | Planned |  | 21 | 40 | 0.000569 | 1.4e-05 | N
19-06-19 | 08:25 | 528:83019 | SHORT RURAL | Planned |  | 14 | 50 | 0.002911 | 5.8e-05 | N
19-06-19 | 11:05 | 511:29880 | URBAN | Planned |  | 6 | 50 | 0.000203 | 4e-06 | N
19-06-19 | 11:50 | 242:81541 | URBAN | Planned |  | 150 | 50 | 0.005084 | 0.000102 | N
19-06-19 | 08:34 | 513:48059 | SHORT RURAL | Planned |  | 4 | 51 | 0.000848 | 1.7e-05 | N
19-06-19 | 08:35 | 813:89061 | LONG RURAL | Planned |  | 50 | 295 | 5.1555 | 0.017476 | N
20-06-19 | 08:20 | 812:19072 | SHORT RURAL | Planned |  | 12 | 395 | 0.019712 | 5e-05 | N
20-06-19 | 09:30 | 813:89061 | LONG RURAL | Planned |  | 22 | 200 | 1.5379 | 0.00769 | N
20-06-19 | 07:18 | 227:13015 | SHORT RURAL | Planned |  | 18 | 392 | 0.029343 | 7.5e-05 | N
20-06-19 | 08:00 | 227:13015 | SHORT RURAL | Planned |  | 10 | 390 | 0.016218 | 4.2e-05 | N
20-06-19 | 09:00 | 524:33576 | SHORT RURAL | Planned |  | 6 | 420 | 0.01048 | 2.5e-05 | N
20-06-19 | 10:20 | 202:34254 | URBAN | Planned |  | 107 | 365 | 0.026473 | 7.3e-05 | N
21-06-19 | 08:10 | 256:80650 | URBAN | Planned |  | 48 | 140 | 0.004555 | 3.3e-05 | N
21-06-19 | 11:00 | 202:34254 | URBAN | Planned |  | 171 | 105 | 0.012171 | 0.000116 | N
22-06-19 | 08:43 | 270:83593 | SHORT RURAL | Planned |  | 107 | 582 | 0.25897 | 0.000445 | N
20-06-19 | 09:20 | 508:82574 | SHORT RURAL | Planned |  | 4 | 215 | 0.003576 | 1.7e-05 | N
20-06-19 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 42 | 550 | 8.0741 | 0.01468 | N
21-06-19 | 10:00 | 522:83126 | SHORT RURAL | Planned |  | 2 | 55 | 0.000457 | 8e-06 | N
21-06-19 | 10:00 | 522:83126 | SHORT RURAL | Planned |  | 1 | 210 | 0.000873 | 4e-06 | N
21-06-19 | 09:25 | 230:81432 | SHORT RURAL | Planned |  | 174 | 265 | 0.19175 | 0.000724 | N
20-06-19 | 08:30 | 801:74121 | LONG RURAL | Planned |  | 4 | 320 | 0.4474 | 0.001398 | N
20-06-19 | 08:20 | 813:89059 | URBAN | Planned |  | 82 | 485 | 0.026957 | 5.6e-05 | N
20-06-19 | 09:00 | 814:82291 | SHORT RURAL | Planned |  | 6 | 125 | 0.003119 | 2.5e-05 | N
21-06-19 | 08:40 | 807:74184 | SHORT RURAL | Planned |  | 1 | 40 | 0.000166 | 4e-06 | N
21-06-19 | 09:15 | 811:74234 | SHORT RURAL | Planned |  | 3 | 75 | 0.000936 | 1.2e-05 | N
21-06-19 | 08:55 | 523:33501 | SHORT RURAL | Planned |  | 6 | 70 | 0.001747 | 2.5e-05 | N
21-06-19 | 11:00 | 811:74234 | SHORT RURAL | Planned |  | 2 | 100 | 0.000832 | 8e-06 | N
24-06-19 | 07:15 | 417:80504 | URBAN | Planned |  | 1 | 315 | 0.000214 | 1e-06 | N
24-06-19 | 08:45 | 202:34262 | URBAN | Planned |  | 174 | 220 | 0.025948 | 0.000118 | N
24-06-19 | 08:45 | 202:34261 | URBAN | Planned |  | 65 | 220 | 0.009693 | 4.4e-05 | N
24-06-19 | 09:15 | 258:80781 | URBAN | Planned |  | 93 | 165 | 0.010402 | 6.3e-05 | N
25-06-19 | 08:00 | 526:34640 | SHORT RURAL | Planned |  | 15 | 455 | 0.028383 | 6.2e-05 | N
25-06-19 | 10:10 | 233:82819 | SHORT RURAL | Planned |  | 91 | 223 | 0.084391 | 0.000378 | N
25-06-19 | 08:30 | 224:80337 | URBAN | Planned |  | 202 | 210 | 0.028755 | 0.000137 | N
25-06-19 | 08:30 | 513:48059 | SHORT RURAL | Planned |  | 86 | 350 | 0.12518 | 0.000358 | N
25-06-19 | 08:00 | 239:82133 | URBAN | Planned |  | 176 | 420 | 0.050108 | 0.000119 | N
26-06-19 | 08:30 | 514:18137 | SHORT RURAL | Planned |  | 8 | 60 | 0.001996 | 3.3e-05 | N
26-06-19 | 08:30 | 524:33572 | SHORT RURAL | Planned |  | 35 | 490 | 0.071321 | 0.000146 | N
26-06-19 | 11:50 | 526:34633 | SHORT RURAL | Planned |  | 4 | 47 | 0.000782 | 1.7e-05 | N
26-06-19 | 08:33 | 217:33610 | URBAN | Planned |  | 86 | 252 | 0.014646 | 5.8e-05 | N
26-06-19 | 08:30 | 227:13014 | SHORT RURAL | Planned |  | 52 | 380 | 0.082175 | 0.000216 | N
26-06-19 | 08:00 | 202:34260 | URBAN | Planned |  | 223 | 475 | 0.071585 | 0.000151 | N
26-06-19 | 08:00 | 256:80650 | URBAN | Planned |  | 85 | 475 | 0.027286 | 5.7e-05 | N
24-06-19 | 11:10 | 230:81432 | SHORT RURAL | Planned |  | 35 | 50 | 0.007278 | 0.000146 | N
24-06-19 | 08:45 | 264:81244 | SHORT RURAL | Planned |  | 8 | 375 | 0.012476 | 3.3e-05 | N
25-06-19 | 08:15 | 526:34640 | SHORT RURAL | Planned |  | 7 | 410 | 0.011935 | 2.9e-05 | N
25-06-19 | 12:40 | 230:81432 | SHORT RURAL | Planned |  | 15 | 165 | 0.010293 | 6.2e-05 | N
26-06-19 | 08:50 | 526:34635 | SHORT RURAL | Planned |  | 1 | 75 | 0.000312 | 4e-06 | N
26-06-19 | 09:04 | 232:11455 | SHORT RURAL | Planned |  | 87 | 62 | 0.022432 | 0.000362 | N
24-06-19 | 09:00 | 813:89055 | SHORT RURAL | Planned |  | 1 | 60 | 0.00025 | 4e-06 | N
24-06-19 | 08:45 | 813:89061 | LONG RURAL | Planned |  | 17 | 285 | 1.6935 | 0.005942 | N
25-06-19 | 09:00 | 520:48172 | SHORT RURAL | Planned |  | 3 | 105 | 0.00131 | 1.2e-05 | N
25-06-19 | 09:00 | 806:82667 | SHORT RURAL | Planned |  | 8 | 210 | 0.006987 | 3.3e-05 | N
25-06-19 | 09:55 | 520:48172 | SHORT RURAL | Planned |  | 2 | 190 | 0.00158 | 8e-06 | N
27-06-19 | 08:45 | 204:82701 | URBAN | Planned |  | 3 | 495 | 0.001003 | 2e-06 | N
27-06-19 | 08:30 | 258:80791 | URBAN | Planned |  | 63 | 260 | 0.011067 | 4.3e-05 | N
27-06-19 | 09:45 | 221:11898 | SHORT RURAL | Planned |  | 140 | 125 | 0.072751 | 0.000582 | N
27-06-19 | 21:40 | 204:82691 | URBAN | Planned |  | 197 | 256 | 0.034074 | 0.000133 | N
27-06-19 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 20 | 435 | 3.0398 | 0.006988 | N
27-06-19 | 09:00 | 512:83732 | SHORT RURAL | Planned |  | 2 | 75 | 0.000624 | 8e-06 | N
27-06-19 | 09:10 | 802:82225 | SHORT RURAL | Planned |  | 9 | 275 | 0.010289 | 3.7e-05 | N
29-06-19 | 09:00 | 258:80781 | URBAN | Planned |  | 86 | 275 | 0.015979 | 5.8e-05 | N
29-06-19 | 18:10 | 221:11898 | SHORT RURAL | Planned |  | 90 | 610 | 0.22823 | 0.000374 | N
28-06-19 | 08:00 | 509:33395 | LONG RURAL | Planned |  | 33 | 300 | 3.4591 | 0.01153 | N
29-06-19 | 08:00 | 229:34983 | SHORT RURAL | Planned |  | 1 | 505 | 0.002099 | 4e-06 | N
28-06-19 | 08:10 | 514:18141 | SHORT RURAL | Planned |  | 1 | 50 | 0.000208 | 4e-06 | N
28-06-19 | 08:00 | 806:82662 | SHORT RURAL | Planned |  | 52 | 385 | 0.083228 | 0.000216 | N
29-06-19 | 08:00 | ZN129:PA47 | URBAN | Planned |  | 34 | 540 | 0.012405 | 2.3e-05 | N
29-06-19 | 08:00 | ZN195:PA9 | SHORT RURAL | Planned |  | 11 | 360 | 0.016463 | 4.6e-05 | N
29-06-19 | 07:00 | ZN15009:PA11 | URBAN | Planned |  | 135 | 480 | 0.043783 | 9.1e-05 | N
29-06-19 | 06:00 | ZN12650:PA6 | URBAN | Planned |  | 1 | 600 | 0.000405 | 1e-06 | N
28-06-19 | 20:00 | ZN12580:PA16 | URBAN | Planned |  | 49 | 660 | 0.02185 | 3.3e-05 | N
28-06-19 | 07:00 | TS7140:326 | URBAN | Planned |  | 1 | 4,380 | 0.002959 | 1e-06 | N
30-06-19 | 07:00 | ZN195:PA30 | SHORT RURAL | Planned |  | 9 | 480 | 0.017963 | 3.7e-05 | N
26-06-19 | 09:00 | ZN9550:PA1 | URBAN | Planned |  | 1 | 240 | 0.000162 | 1e-06 | N
26-06-19 | 08:30 | ZN35555:PA6 | URBAN | Planned |  | 143 | 480 | 0.046388 | 9.7e-05 | N
26-06-19 | 08:00 | ZN3425:PA15 | URBAN | Planned |  | 30 | 420 | 0.008515 | 2e-05 | N
26-06-19 | 08:00 | ZN15013:PA6 | SHORT RURAL | Planned |  | 13 | 420 | 0.022706 | 5.4e-05 | N
26-06-19 | 08:00 | ZN15013:PA6 | SHORT RURAL | Planned |  | 1 | 420 | 0.001747 | 4e-06 | N
26-06-19 | 08:00 | ZN35500:PA28 | URBAN | Planned |  | 97 | 480 | 0.031466 | 6.6e-05 | N
26-06-19 | 07:00 | ZN1673:PA13 | URBAN | Planned |  | 91 | 660 | 0.040589 | 6.1e-05 | N
26-06-19 | 08:00 | ZN12570:PA41 | URBAN | Planned |  | 100 | 480 | 0.032439 | 6.8e-05 | N
26-06-19 | 07:30 | ZN7900:PA1 | URBAN | Planned |  | 22 | 300 | 0.00446 | 1.5e-05 | N
26-06-19 | 07:30 | ZN7900:PA3 | URBAN | Planned |  | 29 | 300 | 0.00588 | 2e-05 | N
26-06-19 | 08:00 | ZN10993:PA35 | URBAN | Planned |  | 86 | 360 | 0.020923 | 5.8e-05 | N
19-06-19 | 06:45 | ZN8100:PA17 | URBAN | Planned |  | 35 | 15 | 0.000356 | 2.4e-05 | N
26-06-19 | 05:00 | ZN14892:PA20 | URBAN | Planned |  | 4 | 90 | 0.000243 | 3e-06 | N
25-06-19 | 21:30 | ZN12570:PA22 | SHORT RURAL | Planned |  | 10 | 180 | 0.007486 | 4.2e-05 | N
25-06-19 | 21:30 | ZN12580:PA1 | URBAN | Planned |  | 20 | 180 | 0.00244 | 1.4e-05 | N
25-06-19 | 22:30 | ZN180:PA19 | URBAN | Planned |  | 61 | 60 | 0.002481 | 4.1e-05 | N
25-06-19 | 20:00 | ZN35600:PA16 | URBAN | Planned |  | 52 | 330 | 0.011632 | 3.5e-05 | N
25-06-19 | 16:00 | ZN12660:PA14 | SHORT RURAL | Planned |  | 3 | 420 | 0.00524 | 1.2e-05 | N
25-06-19 | 09:00 | ZN965:PA20 | URBAN | Planned |  | 119 | 300 | 0.0242 | 8.1e-05 | N
25-06-19 | 09:00 | ZN188:PA32 | URBAN | Planned |  | 7 | 540 | 0.002562 | 5e-06 | N
25-06-19 | 09:00 | ZN187:PA13 | URBAN | Planned |  | 133 | 210 | 0.018933 | 9e-05 | N
25-06-19 | 08:00 | ZN12610:PA13 | SHORT RURAL | Planned |  | 131 | 480 | 0.2615 | 0.000545 | N
25-06-19 | 08:00 | ZN965:PA43 | URBAN | Planned |  | 19 | 480 | 0.006182 | 1.3e-05 | N
25-06-19 | 08:00 | ZN965:PA43 | URBAN | Planned |  | 41 | 480 | 0.01334 | 2.8e-05 | N
25-06-19 | 08:00 | ZN965:PA43 | URBAN | Planned |  | 39 | 480 | 0.01269 | 2.6e-05 | N
25-06-19 | 08:00 | ZN2602:PA20 | URBAN | Planned |  | 47 | 420 | 0.013381 | 3.2e-05 | N
25-06-19 | 08:00 | ZN2602:PA30 | URBAN | Planned |  | 41 | 420 | 0.011673 | 2.8e-05 | N
25-06-19 | 07:30 | ZN3425:PA28 | SHORT RURAL | Planned |  | 37 | 450 | 0.069241 | 0.000154 | N
25-06-19 | 07:30 | ZN36800:PA31 | URBAN | Planned |  | 33 | 330 | 0.007382 | 2.2e-05 | N
25-06-19 | 07:30 | ZN2602:PA30 | URBAN | Planned |  | 89 | 330 | 0.019909 | 6e-05 | N
25-06-19 | 01:00 | ZN15009:PA5 | URBAN | Planned |  | 24 | 180 | 0.002928 | 1.6e-05 | N
24-06-19 | 23:00 | ZN14892:PA20 | URBAN | Planned |  | 4 | 120 | 0.000325 | 3e-06 | N
25-06-19 | 05:00 | ZN2602:PA36 | URBAN | Planned |  | 21 | 240 | 0.003416 | 1.4e-05 | N
24-06-19 | 11:00 | ZN2400:PA15 | SHORT RURAL | Planned |  | 34 | 240 | 0.033934 | 0.000141 | N
24-06-19 | 10:00 | ZN965:PA24 | URBAN | Planned |  | 33 | 240 | 0.005369 | 2.2e-05 | N
24-06-19 | 10:00 | ZN2196:PA26 | URBAN | Planned |  | 44 | 360 | 0.010737 | 3e-05 | N
24-06-19 | 10:00 | ZN2196:PA26 | URBAN | Planned |  | 29 | 360 | 0.007077 | 2e-05 | N
24-06-19 | 10:00 | ZN2196:PA26 | URBAN | Planned |  | 70 | 360 | 0.017082 | 4.7e-05 | N
24-06-19 | 09:00 | ZN14891:PA1 | URBAN | Planned |  | 90 | 240 | 0.014642 | 6.1e-05 | N
24-06-19 | 09:00 | ZN10999:PA12 | URBAN | Planned |  | 181 | 420 | 0.051531 | 0.000123 | N
24-06-19 | 08:00 | ZN14144:PA2 | SHORT RURAL | Planned |  | 103 | 480 | 0.2056 | 0.000428 | N
24-06-19 | 08:00 | ZN3425:PA28 | SHORT RURAL | Planned |  | 24 | 330 | 0.032936 | 0.0001 | N
24-06-19 | 08:00 | ZN15005:PA2 | URBAN | Planned |  | 32 | 390 | 0.00846 | 2.2e-05 | N
24-06-19 | 08:00 | ZN9900:PA13 | URBAN | Planned |  | 38 | 510 | 0.013137 | 2.6e-05 | N
24-06-19 | 08:00 | ZN9900:PA3 | URBAN | Planned |  | 36 | 480 | 0.011713 | 2.4e-05 | N
24-06-19 | 07:00 | ZN195:PA22 | URBAN | Planned |  | 93 | 660 | 0.041607 | 6.3e-05 | N
24-06-19 | 08:00 | ZN2400:PA26 | URBAN | Planned |  | 30 | 180 | 0.00366 | 2e-05 | N
24-06-19 | 07:00 | ZN931:PA9 | URBAN | Planned |  | 114 | 480 | 0.037092 | 7.7e-05 | N
23-06-19 | 22:00 | ZN188:PA44 | URBAN | Planned |  | 16 | 480 | 0.005206 | 1.1e-05 | N
23-06-19 | 21:00 | ZN3288:PA45 46GHJ | CBD | Planned |  | 40 | 360 | 0.47478 | 0.001319 | N
23-06-19 | 20:30 | ZN690:PA35 | URBAN | Planned |  | 72 | 330 | 0.016106 | 4.9e-05 | N
23-06-19 | 08:00 | ZN4545:PA25 | URBAN | Planned |  | 43 | 480 | 0.013991 | 2.9e-05 | N
23-06-19 | 08:00 | ZN4545:PA25 | URBAN | Planned |  | 33 | 480 | 0.010737 | 2.2e-05 | N
23-06-19 | 08:00 | ZN15002:PA6 | URBAN | Planned |  | 12 | 600 | 0.004881 | 8e-06 | N
23-06-19 | 08:00 | ZN36800:PA46 | URBAN | Planned |  | 261 | 480 | 0.084922 | 0.000177 | N
23-06-19 | 08:00 | ZN36800:PA57 | URBAN | Planned |  | 1 | 480 | 0.000325 | 1e-06 | N
23-06-19 | 08:00 | ZN1193:PA12 | URBAN | Planned |  | 28 | 360 | 0.006833 | 1.9e-05 | N
23-06-19 | 08:00 | ZN13000:PA5 | SHORT RURAL | Planned |  | 16 | 360 | 0.023954 | 6.7e-05 | N
23-06-19 | 08:00 | ZN15001:PA16 | URBAN | Planned |  | 15 | 420 | 0.00427 | 1e-05 | N
23-06-19 | 07:00 | ZN3472:PA35 | URBAN | Planned |  | 7 | 420 | 0.001993 | 5e-06 | N
21-06-19 | 20:00 | TS7150:745SRA | URBAN | Planned |  | 1 | 2,880 | 0.001952 | 1e-06 | N
22-06-19 | 10:00 | ZN2196:PA11 | URBAN | Planned |  | 1 | 420 | 0.000285 | 1e-06 | N
22-06-19 | 08:00 | ZN116:PA12 | URBAN | Planned |  | 1 | 540 | 0.000366 | 1e-06 | N
22-06-19 | 07:00 | ZN3154:PA24 | URBAN | Planned |  | 311 | 660 | 0.13914 | 0.000211 | N
22-06-19 | 07:30 | ZN3288:PA41 42GHJ | CBD | Planned |  | 28 | 240 | 0.22156 | 0.000923 | N
22-06-19 | 07:30 | ZN8700:PA61 62GHJ | CBD | Planned |  | 4 | 480 | 0.063304 | 0.000132 | N
21-06-19 | 09:00 | ZN965:PA4 | URBAN | Planned |  | 92 | 240 | 0.014967 | 6.2e-05 | N
21-06-19 | 08:30 | ZN35370:PA8 | SHORT RURAL | Planned |  | 15 | 330 | 0.020585 | 6.2e-05 | N
21-06-19 | 08:00 | ZN12620:PA2 | SHORT RURAL | Planned |  | 56 | 420 | 0.09781 | 0.000233 | N
21-06-19 | 08:00 | ZN12620:PA8 | SHORT RURAL | Planned |  | 50 | 510 | 0.10604 | 0.000208 | N
21-06-19 | 08:00 | ZN15002:PA8 | URBAN | Planned |  | 85 | 450 | 0.025928 | 5.8e-05 | N
21-06-19 | 08:00 | ZN12660:PA14 | SHORT RURAL | Planned |  | 305 | 480 | 0.60882 | 0.001268 | N
21-06-19 | 08:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 29 | 480 | 0.057888 | 0.000121 | N
21-06-19 | 08:00 | ZN9700:PA24 | URBAN | Planned |  | 79 | 480 | 0.025704 | 5.4e-05 | N
21-06-19 | 08:00 | ZN9700:PA24 | URBAN | Planned |  | 134 | 480 | 0.043599 | 9.1e-05 | N
21-06-19 | 07:00 | ZN2310:PA15 | URBAN | Planned |  | 129 | 600 | 0.052465 | 8.7e-05 | N
21-06-19 | 07:00 | ZN2310:PA15 | URBAN | Planned |  | 154 | 600 | 0.062633 | 0.000104 | N
20-06-19 | 22:00 | ZN15009:PA5 | URBAN | Planned |  | 24 | 480 | 0.007809 | 1.6e-05 | N
20-06-19 | 21:00 | ZN3154:PA22 | SHORT RURAL | Planned |  | 38 | 480 | 0.075852 | 0.000158 | N
20-06-19 | 20:00 | ZN10994:PA8 | URBAN | Planned |  | 7 | 239 | 0.001134 | 5e-06 | N
20-06-19 | 19:00 | ZN9700:PA11 | URBAN | Planned |  | 10 | 180 | 0.00122 | 7e-06 | N
20-06-19 | 20:00 | ZN4545:PA31 | URBAN | Planned |  | 197 | 720 | 0.096144 | 0.000134 | N
20-06-19 | 09:00 | ZN9118:PA6 | URBAN | Planned |  | 31 | 300 | 0.006304 | 2.1e-05 | N
20-06-19 | 08:00 | ZN12620:PA8 | SHORT RURAL | Planned |  | 71 | 360 | 0.10629 | 0.000295 | N
20-06-19 | 08:00 | ZN847:PA46 | URBAN | Planned |  | 25 | 480 | 0.008134 | 1.7e-05 | N
20-06-19 | 08:00 | ZN129:PA41 | URBAN | Planned |  | 41 | 420 | 0.011672 | 2.8e-05 | N
20-06-19 | 07:00 | ZN10999:PA10 | URBAN | Planned |  | 51 | 540 | 0.018668 | 3.5e-05 | N
20-06-19 | 08:00 | ZN36100:PA27 | URBAN | Planned |  | 34 | 240 | 0.005531 | 2.3e-05 | N
20-06-19 | 07:00 | ZN180:PA30 | URBAN | Planned |  | 47 | 540 | 0.017203 | 3.2e-05 | N
20-06-19 | 07:30 | ZN3155:PA16 | URBAN | Planned |  | 217 | 480 | 0.070603 | 0.000147 | N
20-06-19 | 07:30 | ZN3155:PA32 | URBAN | Planned |  | 29 | 480 | 0.009435 | 2e-05 | N
20-06-19 | 07:00 | ZN35900:PA11 | URBAN | Planned |  | 5 | 600 | 0.002034 | 3e-06 | N
19-06-19 | 22:30 | ZN3155:PA12 | URBAN | Planned |  | 92 | 330 | 0.020579 | 6.2e-05 | N
19-06-19 | 22:30 | ZN3155:PA32 | URBAN | Planned |  | 66 | 330 | 0.014763 | 4.5e-05 | N
19-06-19 | 21:30 | ZN10999:PA12 | URBAN | Planned |  | 30 | 180 | 0.00366 | 2e-05 | N
19-06-19 | 21:00 | ZN15014:PA19 | URBAN | Planned |  | 99 | 630 | 0.042276 | 6.7e-05 | N
19-06-19 | 09:30 | ZN9118:PA22 | URBAN | Planned |  | 32 | 180 | 0.003904 | 2.2e-05 | N
19-06-19 | 08:00 | ZN12610:PA2 | URBAN | Planned |  | 37 | 480 | 0.012038 | 2.5e-05 | N
18-06-19 | 09:30 | ZN10999:PA4 | URBAN | Planned |  | 52 | 330 | 0.011623 | 3.5e-05 | N
18-06-19 | 09:30 | ZN10999:PA4 | URBAN | Planned |  | 49 | 120 | 0.003983 | 3.3e-05 | N
18-06-19 | 09:00 | ZN9118:PA7 | URBAN | Planned |  | 38 | 300 | 0.007721 | 2.6e-05 | N
18-06-19 | 08:00 | ZN3425:PA33 | URBAN | Planned |  | 11 | 420 | 0.003129 | 7e-06 | N
18-06-19 | 08:00 | ZN3425:PA33 | URBAN | Planned |  | 32 | 420 | 0.009103 | 2.2e-05 | N
18-06-19 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 38 | 540 | 0.085331 | 0.000158 | N
18-06-19 | 09:00 | ZN10991:PA5 | URBAN | Planned |  | 84 | 330 | 0.018775 | 5.7e-05 | N
18-06-19 | 09:00 | ZN10994:PA9 | URBAN | Planned |  | 104 | 330 | 0.023246 | 7e-05 | N
18-06-19 | 08:00 | ZN9900:PA13 | URBAN | Planned |  | 4 | 510 | 0.001382 | 3e-06 | N
18-06-19 | 08:00 | ZN35600:PA19 | URBAN | Planned |  | 2 | 240 | 0.000325 | 1e-06 | N
18-06-19 | 07:00 | ZN35400:PA85 | URBAN | Planned |  | 26 | 30 | 0.000528 | 1.8e-05 | N
18-06-19 | 07:00 | ZN1850:PA41 | URBAN | Planned |  | 583 | 630 | 0.24877 | 0.000395 | N
17-06-19 | 20:00 | ZN35600:PA4 | URBAN | Planned |  | 134 | 600 | 0.054462 | 9.1e-05 | N
17-06-19 | 09:00 | ZN1673:PA7 | URBAN | Planned |  | 25 | 240 | 0.004064 | 1.7e-05 | N
17-06-19 | 09:00 | ZN3154:PA13 | SHORT RURAL | Planned |  | 45 | 240 | 0.044928 | 0.000187 | N
17-06-19 | 08:00 | ZN35370:PA2 | SHORT RURAL | Planned |  | 19 | 360 | 0.028455 | 7.9e-05 | N
17-06-19 | 08:00 | ZN262:PA20 | URBAN | Planned |  | 85 | 480 | 0.027637 | 5.8e-05 | N
17-06-19 | 08:00 | ZN12690:PA10 | SHORT RURAL | Planned |  | 1 | 240 | 0.000998 | 4e-06 | N
17-06-19 | 08:00 | ZN116:PA2 | URBAN | Planned |  | 42 | 420 | 0.011949 | 2.8e-05 | N
17-06-19 | 08:00 | ZN180:PA20 | URBAN | Planned |  | 31 | 420 | 0.00882 | 2.1e-05 | N
01-02-19 | 10:00 | ZN711:PA33 | URBAN | Planned |  | 36 | 60 | 0.001464 | 2.4e-05 | N
01-02-19 | 09:30 | ZN3155:PA44 | URBAN | Planned |  | 60 | 360 | 0.01464 | 4.1e-05 | N
08-02-19 | 09:00 | ZN711:PA32 | URBAN | Planned |  | 380 | 180 | 0.04635 | 0.000258 | N
01-02-19 | 14:00 | ZN965:PA26 | URBAN | Planned |  | 1 | 360 | 0.000244 | 1e-06 | N
02-02-19 | 06:30 | ZN1610:PA2 | URBAN | Planned |  | 4 | 570 | 0.001546 | 3e-06 | N
08-01-19 | 08:00 | ZN12640:PA8 | SHORT RURAL | Planned |  | 6 | 480 | 0.012118 | 2.5e-05 | N
08-01-19 | 08:00 | ZN12640:PA12 | URBAN | Planned |  | 19 | 480 | 0.006179 | 1.3e-05 | N
17-01-19 | 19:00 | ZN188:PA45 | SHORT RURAL | Planned |  | 9 | 900 | 0.034074 | 3.8e-05 | N
22-01-19 | 07:30 | ZN3472:PA30 | URBAN | Planned |  | 90 | 510 | 0.031138 | 6.1e-05 | N
02-02-19 | 07:00 | ZN4990:PA53 54GHJ | CBD | Planned |  | 8 | 420 | 0.1098 | 0.000261 | N
02-02-19 | 07:30 | ZN630:PA33 | URBAN | Planned |  | 6 | 570 | 0.002319 | 4e-06 | N
02-02-19 | 08:30 | ZN1610:PA18 | URBAN | Planned |  | 9 | 300 | 0.001831 | 6e-06 | N
03-02-19 | 07:00 | ZN4990:PA53 54GHJ | CBD | Planned |  | 9 | 420 | 0.12352 | 0.000294 | N
03-02-19 | 20:30 | ZN263:PA31 32ABC | CBD | Planned |  | 19 | 480 | 0.29802 | 0.000621 | N
04-02-19 | 08:00 | ZN10999:PA10 | URBAN | Planned |  | 53 | 420 | 0.015084 | 3.6e-05 | N
04-02-19 | 08:00 | ZN80:PA40 | URBAN | Planned |  | 21 | 420 | 0.005977 | 1.4e-05 | N
04-02-19 | 08:00 | ZN12570:PA25 | SHORT RURAL | Planned |  | 31 | 480 | 0.062248 | 0.00013 | N
04-02-19 | 08:00 | ZN12570:PA26 | URBAN | Planned |  | 54 | 480 | 0.017564 | 3.7e-05 | N
04-02-19 | 20:00 | ZN10993:PA33 | URBAN | Planned |  | 68 | 540 | 0.024882 | 4.6e-05 | N
05-02-19 | 07:00 | ZN965:PA4 | URBAN | Planned |  | 2 | 720 | 0.000976 | 1e-06 | N
05-02-19 | 07:00 | ZN36100:PA13 | URBAN | Planned |  | 20 | 600 | 0.008132 | 1.4e-05 | N
05-02-19 | 08:00 | ZN3472:PA30 | URBAN | Planned |  | 27 | 60 | 0.001098 | 1.8e-05 | N
05-02-19 | 08:30 | ZN188:PA45 | SHORT RURAL | Planned |  | 9 | 330 | 0.012425 | 3.8e-05 | N
05-02-19 | 09:00 | ZN10999:PA7 | URBAN | Planned |  | 142 | 420 | 0.040414 | 9.6e-05 | N
05-02-19 | 18:00 | ZN180:PA30 | URBAN | Planned |  | 36 | 330 | 0.00805 | 2.4e-05 | N
06-02-19 | 07:00 | ZN965:PA8 | URBAN | Planned |  | 10 | 600 | 0.004066 | 7e-06 | N
06-02-19 | 07:30 | ZN901:PA10 | URBAN | Planned |  | 85 | 480 | 0.027648 | 5.8e-05 | N
06-02-19 | 08:00 | ZN10995:PA13 | URBAN | Planned |  | 55 | 480 | 0.01789 | 3.7e-05 | N
06-02-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 8 | 240 | 0.008032 | 3.3e-05 | N
06-02-19 | 08:30 | ZN9118:PA24 | URBAN | Planned |  | 48 | 420 | 0.013661 | 3.3e-05 | N
06-02-19 | 11:00 | ZN9252:PA21 | URBAN | Planned |  | 2 | 240 | 0.000325 | 1e-06 | N
07-02-19 | 07:00 | ZN2466:PA17 | SHORT RURAL | Planned |  | 62 | 660 | 0.17119 | 0.000259 | N
07-02-19 | 07:30 | ZN901:PA20 | URBAN | Planned |  | 44 | 480 | 0.014312 | 3e-05 | N
07-02-19 | 08:00 | ZN9700:PA17 | URBAN | Planned |  | 21 | 420 | 0.005977 | 1.4e-05 | N
07-02-19 | 08:00 | ZN9245:PA10 | URBAN | Planned |  | 42 | 480 | 0.013661 | 2.8e-05 | N
07-02-19 | 08:00 | ZN35600:PA22 | URBAN | Planned |  | 98 | 390 | 0.0259 | 6.6e-05 | N
07-02-19 | 09:00 | ZN12580:PA4 | URBAN | Planned |  | 33 | 420 | 0.009392 | 2.2e-05 | N
07-02-19 | 20:00 | ZN167:PA20 | URBAN | Planned |  | 4 | 600 | 0.001626 | 3e-06 | N
07-02-19 | 20:00 | ZN2466:PA2 | URBAN | Planned |  | 12 | 600 | 0.004879 | 8e-06 | N
08-02-19 | 07:00 | ZN9118:PA6 | URBAN | Planned |  | 27 | 540 | 0.00988 | 1.8e-05 | N
08-02-19 | 20:00 | ZN2466:PA2 | URBAN | Planned |  | 12 | 600 | 0.004879 | 8e-06 | N
08-02-19 | 20:00 | ZN167:PA20 | URBAN | Planned |  | 4 | 600 | 0.001626 | 3e-06 | N
09-02-19 | 06:00 | ZN8700:PA65 66ABC | CBD | Planned |  | 35 | 480 | 0.54857 | 0.001143 | N
09-02-19 | 07:00 | ZN187:PA26 | URBAN | Planned |  | 1 | 3,060 | 0.002074 | 1e-06 | N
09-02-19 | 07:00 | ZN3155:PA23 | URBAN | Planned |  | 13 | 600 | 0.005286 | 9e-06 | N
09-02-19 | 07:30 | ZN901:PA10 | URBAN | Planned |  | 85 | 480 | 0.027648 | 5.8e-05 | N
10-02-19 | 20:00 | ZN7900:PA23 | URBAN | Planned |  | 8 | 600 | 0.003253 | 5e-06 | N
10-02-19 | 23:00 | ZN3288:PA45 46GHJ | CBD | Planned |  | 12 | 300 | 0.11755 | 0.000392 | N
11-02-19 | 08:00 | ZN847:PA47 | SHORT RURAL | Planned |  | 134 | 480 | 0.26909 | 0.000561 | N
11-02-19 | 21:30 | ZN1600:PA21ABC | CBD | Planned |  | 2 | 270 | 0.017633 | 6.5e-05 | N
12-02-19 | 08:00 | ZN10999:PA17 | URBAN | Planned |  | 32 | 398 | 0.00862 | 2.2e-05 | N
12-02-19 | 08:00 | ZN10999:PA29 | URBAN | Planned |  | 13 | 420 | 0.0037 | 9e-06 | N
12-02-19 | 08:00 | ZN12600:PA13 | SHORT RURAL | Planned |  | 4 | 480 | 0.008033 | 1.7e-05 | N
12-02-19 | 08:00 | ZN9037:PA10 | URBAN | Planned |  | 35 | 480 | 0.011385 | 2.4e-05 | N
17-06-19 | 07:00 | ZN180:PA20 | URBAN | Planned |  | 42 | 600 | 0.01707 | 2.8e-05 | N
17-06-19 | 07:00 | ZN35800:PA22 | URBAN | Planned |  | 47 | 150 | 0.004776 | 3.2e-05 | N
17-06-19 | 07:00 | ZN35800:PA22 | URBAN | Planned |  | 201 | 540 | 0.073523 | 0.000136 | N
16-06-19 | 10:00 | ZN1287:PA11 | URBAN | Planned |  | 69 | 420 | 0.019631 | 4.7e-05 | N
16-06-19 | 08:00 | ZN263:PA33 34DEF | CBD | Planned |  | 4 | 480 | 0.063306 | 0.000132 | N
16-06-19 | 07:30 | ZN167:PA19 | URBAN | Planned |  | 2 | 210 | 0.000285 | 1e-06 | N
16-06-19 | 05:00 | ZN8000:PA3 | URBAN | Planned |  | 2 | 720 | 0.000975 | 1e-06 | N
27-02-19 | 09:00 | ZN711:PA33 | URBAN | Planned |  | 112 | 180 | 0.013656 | 7.6e-05 | N
15-06-19 | 08:00 | ZN263:PA33 34DEF | CBD | Planned |  | 4 | 300 | 0.039565 | 0.000132 | N
13-02-19 | 07:00 | ZN2835:PA33 | URBAN | Planned |  | 29 | 750 | 0.014737 | 2e-05 | N
15-06-19 | 07:00 | ZN5868:PA14 | URBAN | Planned |  | 4 | 540 | 0.001463 | 3e-06 | N
15-06-19 | 08:00 | ZN263:PA33 34ABC | CBD | Planned |  | 40 | 180 | 0.23739 | 0.001319 | N
15-06-19 | 07:15 | ZN8100:PA24 | URBAN | Planned |  | 1 | 15 | 1e-05 | 1e-06 | N
15-06-19 | 07:00 | ZN8100:PA11 | URBAN | Planned |  | 1 | 15 | 1e-05 | 1e-06 | N
14-06-19 | 16:00 | ZN188:PA1 | URBAN | Planned |  | 1 | 60 | 4.1e-05 | 1e-06 | N
13-02-19 | 08:00 | ZN12580:PA14 | URBAN | Planned |  | 1 | 480 | 0.000325 | 1e-06 | N
13-02-19 | 09:30 | ZN711:PA9 | URBAN | Planned |  | 50 | 90 | 0.003049 | 3.4e-05 | N
13-02-19 | 10:30 | ZN7481:PA9 | URBAN | Planned |  | 268 | 70 | 0.012711 | 0.000182 | N
13-02-19 | 20:00 | ZN35555:PA20 | URBAN | Planned |  | 20 | 600 | 0.008131 | 1.4e-05 | N
14-06-19 | 10:00 | ZN180:PA30 | URBAN | Planned |  | 28 | 210 | 0.003983 | 1.9e-05 | N
14-02-19 | 07:30 | ZN7900:PA24 | URBAN | Planned |  | 39 | 480 | 0.012684 | 2.6e-05 | N
14-02-19 | 07:30 | ZN7900:PA12 | URBAN | Planned |  | 14 | 480 | 0.004553 | 9e-06 | N
14-06-19 | 08:00 | ZN847:PA15 | URBAN | Planned |  | 37 | 480 | 0.01203 | 2.5e-05 | N
14-06-19 | 08:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 4 | 420 | 0.006989 | 1.7e-05 | N
14-06-19 | 08:00 | ZN35600:PA9 | URBAN | Planned |  | 148 | 180 | 0.018045 | 0.0001 | N
14-02-19 | 08:00 | ZN9037:PA10 | URBAN | Planned |  | 12 | 480 | 0.003903 | 8e-06 | N
14-06-19 | 07:00 | ZN9035:PA2 | URBAN | Planned |  | 40 | 540 | 0.014631 | 2.7e-05 | N
14-06-19 | 06:00 | ZN7481:PA12 | URBAN | Planned |  | 1 | 540 | 0.000366 | 1e-06 | N
14-02-19 | 08:00 | ZN9700:PA17 | URBAN | Planned |  | 36 | 480 | 0.011709 | 2.4e-05 | N
15-06-19 | 13:00 | ZN9037:PA8 | URBAN | Planned |  | 62 | 300 | 0.012599 | 4.2e-05 | N
15-06-19 | 13:00 | ZN9700:PA19 | URBAN | Planned |  | 15 | 300 | 0.003048 | 1e-05 | N
14-02-19 | 08:00 | ZN14891:PA20 | SHORT RURAL | Planned |  | 3 | 480 | 0.006023 | 1.3e-05 | N
13-06-19 | 22:30 | ZN129:PA46 | URBAN | Planned |  | 10 | 510 | 0.003455 | 7e-06 | N
13-06-19 | 22:30 | ZN129:PA49 | URBAN | Planned |  | 52 | 510 | 0.017964 | 3.5e-05 | N
14-02-19 | 08:00 | ZN13000:PA7 | SHORT RURAL | Planned |  | 122 | 360 | 0.18371 | 0.00051 | N
13-06-19 | 21:00 | ZN15014:PA8 | URBAN | Planned |  | 76 | 540 | 0.0278 | 5.1e-05 | N
13-06-19 | 10:00 | ZN9252:PA31 | URBAN | Planned |  | 1 | 210 | 0.000142 | 1e-06 | N
13-06-19 | 09:00 | ZN3154:PA24 | URBAN | Planned |  | 6 | 360 | 0.001463 | 4e-06 | N
13-06-19 | 08:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 50 | 450 | 0.093603 | 0.000208 | N
13-06-19 | 08:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 6 | 180 | 0.004493 | 2.5e-05 | N
13-06-19 | 08:30 | ZN35800:PA3 | URBAN | Planned |  | 16 | 240 | 0.002601 | 1.1e-05 | N
13-06-19 | 08:00 | ZN35370:PA8 | SHORT RURAL | Planned |  | 17 | 480 | 0.033947 | 7.1e-05 | N
13-06-19 | 08:00 | ZN847:PA45 | SHORT RURAL | Planned |  | 25 | 480 | 0.049921 | 0.000104 | N
13-06-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 4 | 420 | 0.006989 | 1.7e-05 | N
13-06-19 | 08:00 | ZN116:PA25 | URBAN | Planned |  | 62 | 420 | 0.017639 | 4.2e-05 | N
13-06-19 | 07:30 | ZN3922:PA12 | URBAN | Planned |  | 77 | 480 | 0.025036 | 5.2e-05 | N
13-06-19 | 07:30 | ZN630:PA19 | URBAN | Planned |  | 3 | 390 | 0.000793 | 2e-06 | N
12-06-19 | 20:00 | ZN187:PA17 | URBAN | Planned |  | 86 | 480 | 0.027962 | 5.8e-05 | N
14-02-19 | 10:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 13 | 180 | 0.009788 | 5.4e-05 | N
12-06-19 | 20:00 | ZN187:PA17 | URBAN | Planned |  | 16 | 480 | 0.005202 | 1.1e-05 | N
14-02-19 | 19:00 | ZN12570:PA26 | URBAN | Planned |  | 8 | 720 | 0.003903 | 5e-06 | N
12-06-19 | 09:30 | ZN5868:PA7 | URBAN | Planned |  | 27 | 360 | 0.006584 | 1.8e-05 | N
12-06-19 | 08:30 | ZN342:PA17 | URBAN | Planned |  | 20 | 390 | 0.005284 | 1.4e-05 | N
14-02-19 | 20:00 | ZN2196:PA2 | URBAN | Planned |  | 4 | 690 | 0.00187 | 3e-06 | N
12-06-19 | 07:30 | ZN3922:PA23 | URBAN | Planned |  | 112 | 270 | 0.020484 | 7.6e-05 | N
12-06-19 | 07:00 | ZN9900:PA1 | URBAN | Planned |  | 45 | 480 | 0.014631 | 3e-05 | N
12-06-19 | 07:00 | ZN3472:PA28 | URBAN | Planned |  | 60 | 600 | 0.024385 | 4.1e-05 | N
12-06-19 | 07:00 | ZN3472:PA28 | URBAN | Planned |  | 33 | 600 | 0.013412 | 2.2e-05 | N
14-02-19 | 20:00 | ZN9035:PA4 | URBAN | Planned |  | 3 | 720 | 0.001464 | 2e-06 | N
11-06-19 | 22:00 | ZN2835:PA17 | URBAN | Planned |  | 4 | 450 | 0.001219 | 3e-06 | N
15-02-19 | 07:00 | ZN3922:PA26 | URBAN | Planned |  | 7 | 420 | 0.001992 | 5e-06 | N
15-02-19 | 07:00 | ZN1788:PA44 | URBAN | Planned |  | 75 | 480 | 0.024393 | 5.1e-05 | N
15-02-19 | 07:30 | ZN7900:PA12 | URBAN | Planned |  | 6 | 480 | 0.001951 | 4e-06 | N
11-06-19 | 08:00 | ZN13000:PA7 | SHORT RURAL | Planned |  | 11 | 480 | 0.021965 | 4.6e-05 | N
11-06-19 | 08:00 | ZN15004:PA9 | URBAN | Planned |  | 40 | 600 | 0.016257 | 2.7e-05 | N
15-02-19 | 08:00 | ZN12690:PA16 | SHORT RURAL | Planned |  | 27 | 480 | 0.054209 | 0.000113 | N
11-06-19 | 08:00 | ZN180:PA24 | URBAN | Planned |  | 27 | 420 | 0.007681 | 1.8e-05 | N
11-06-19 | 08:30 | ZN2400:PA11 | SHORT RURAL | Planned |  | 169 | 195 | 0.13709 | 0.000703 | N
11-06-19 | 07:00 | ZN3155:PA32 | URBAN | Planned |  | 21 | 540 | 0.007681 | 1.4e-05 | N
11-06-19 | 08:00 | ZN12600:PA13 | SHORT RURAL | Planned |  | 12 | 420 | 0.020966 | 5e-05 | N
15-02-19 | 09:00 | ZN340:PA32 | URBAN | Planned |  | 16 | 420 | 0.004553 | 1.1e-05 | N
11-06-19 | 07:00 | ZN35800:PA7 | URBAN | Planned |  | 1 | 270 | 0.000183 | 1e-06 | N
11-06-19 | 07:00 | ZN35800:PA4 | URBAN | Planned |  | 74 | 270 | 0.013534 | 5e-05 | N
15-02-19 | 10:00 | ZN14891:PA8 | SHORT RURAL | Planned |  | 24 | 180 | 0.01807 | 0.0001 | N
15-02-19 | 10:00 | ZN965:PA8 | URBAN | Planned |  | 16 | 240 | 0.002602 | 1.1e-05 | N
16-02-19 | 06:00 | ZN8100:PA17 | URBAN | Planned |  | 53 | 2,160 | 0.077571 | 3.6e-05 | N
09-06-19 | 06:00 | ZN3155:PA30 | URBAN | Planned |  | 1 | 300 | 0.000203 | 1e-06 | N
09-06-19 | 07:00 | ZN2400:PA11 | SHORT RURAL | Planned |  | 3 | 540 | 0.006739 | 1.2e-05 | N
16-02-19 | 07:30 | ZN3155:PA20 | URBAN | Planned |  | 41 | 600 | 0.016669 | 2.8e-05 | N
08-06-19 | 07:00 | ZN12600:PA5 | URBAN | Planned |  | 3 | 660 | 0.001341 | 2e-06 | N
08-06-19 | 07:00 | ZN2400:PA11 | SHORT RURAL | Planned |  | 3 | 540 | 0.006739 | 1.2e-05 | N
08-06-19 | 08:00 | ZN2196:PA17 | URBAN | Planned |  | 1 | 15 | 1e-05 | 1e-06 | N
16-02-19 | 07:30 | ZN3155:PA20 | URBAN | Planned |  | 19 | 600 | 0.007725 | 1.3e-05 | N
08-06-19 | 06:00 | ZN12660:PA14 | SHORT RURAL | Planned |  | 6 | 720 | 0.017971 | 2.5e-05 | N
08-06-19 | 07:30 | ZN7481:PA1 | URBAN | Planned |  | 1 | 510 | 0.000345 | 1e-06 | N
07-06-19 | 20:00 | ZN1600:PA21ABC | CBD | Planned |  | 30 | 235 | 0.23221 | 0.000988 | N
07-06-19 | 16:00 | ZN15006:PA1 | SHORT RURAL | Planned |  | 1 | 1,380 | 0.005742 | 4e-06 | N
16-02-19 | 09:00 | ZN14891:PA20 | SHORT RURAL | Planned |  | 16 | 360 | 0.024093 | 6.7e-05 | N
07-06-19 | 12:45 | ZN2400:PA11 | SHORT RURAL | Planned |  | 41 | 195 | 0.033269 | 0.000171 | N
07-06-19 | 08:30 | ZN2400:PA11 | SHORT RURAL | Planned |  | 169 | 285 | 0.20042 | 0.000703 | N
07-06-19 | 09:00 | ZN9118:PA11 | URBAN | Planned |  | 27 | 360 | 0.006586 | 1.8e-05 | N
18-02-19 | 08:00 | ZN9252:PA21 | URBAN | Planned |  | 1 | 420 | 0.000285 | 1e-06 | N
18-02-19 | 08:00 | ZN9252:PA21 | URBAN | Planned |  | 1 | 420 | 0.000285 | 1e-06 | N
18-02-19 | 08:00 | ZN9252:PA21 | URBAN | Planned |  | 1 | 420 | 0.000285 | 1e-06 | N
07-06-19 | 08:00 | ZN1193:PA28 | URBAN | Planned |  | 60 | 480 | 0.019513 | 4.1e-05 | N
07-06-19 | 08:00 | ZN14144:PA8 | URBAN | Planned |  | 15 | 480 | 0.004878 | 1e-05 | N
18-02-19 | 08:00 | ZN36300:PA7 | URBAN | Planned |  | 12 | 240 | 0.001951 | 8e-06 | N
18-02-19 | 08:00 | ZN188:PA10 | URBAN | Planned |  | 210 | 450 | 0.064033 | 0.000142 | N
07-06-19 | 15:00 | ZN2568:PA6 | URBAN | Planned |  | 2 | 180 | 0.000244 | 1e-06 | N
07-06-19 | 08:30 | ZN9252:PA22 | URBAN | Planned |  | 113 | 330 | 0.025265 | 7.7e-05 | N
19-02-19 | 08:00 | ZN15008:PA7 | URBAN | Planned |  | 6 | 420 | 0.001707 | 4e-06 | N
19-02-19 | 08:00 | ZN9037:PA8 | URBAN | Planned |  | 28 | 480 | 0.009106 | 1.9e-05 | N
19-02-19 | 08:00 | TS14450:757 | URBAN | Planned |  | 1 | 480 | 0.000325 | 1e-06 | N
19-02-19 | 08:00 | ZN1673:PA7 | URBAN | Planned |  | 48 | 540 | 0.017562 | 3.3e-05 | N
19-02-19 | 08:00 | ZN1673:PA7 | URBAN | Planned |  | 33 | 540 | 0.012074 | 2.2e-05 | N
19-02-19 | 08:00 | ZN14892:PA21 | URBAN | Planned |  | 2 | 420 | 0.000569 | 1e-06 | N
19-02-19 | 21:00 | ZN2602:PA27 | URBAN | Planned |  | 24 | 480 | 0.007806 | 1.6e-05 | N
20-02-19 | 06:00 | ZN12580:PA2 | URBAN | Planned |  | 1 | 2,370 | 0.001606 | 1e-06 | N
20-02-19 | 07:00 | ZN12650:PA12 | URBAN | Planned |  | 76 | 600 | 0.030894 | 5.1e-05 | N
20-02-19 | 07:00 | ZN12650:PA12 | URBAN | Planned |  | 49 | 600 | 0.019918 | 3.3e-05 | N
20-02-19 | 08:00 | ZN15008:PA7 | URBAN | Planned |  | 4 | 420 | 0.001138 | 3e-06 | N
20-02-19 | 08:00 | ZN9252:PA22 | URBAN | Planned |  | 2 | 420 | 0.000569 | 1e-06 | N
20-02-19 | 08:00 | ZN9037:PA8 | URBAN | Planned |  | 28 | 480 | 0.009105 | 1.9e-05 | N
20-02-19 | 10:30 | ZN9035:PA11 | URBAN | Planned |  | 49 | 360 | 0.011951 | 3.3e-05 | N
20-02-19 | 20:00 | ZN35800:PA14 | URBAN | Planned |  | 45 | 660 | 0.020121 | 3e-05 | N
21-02-19 | 07:00 | ZN35555:PA6 | URBAN | Planned |  | 22 | 540 | 0.008049 | 1.5e-05 | N
21-02-19 | 07:30 | ZN7900:PA24 | URBAN | Planned |  | 27 | 480 | 0.008781 | 1.8e-05 | N
21-02-19 | 08:00 | ZN15008:PA7 | URBAN | Planned |  | 6 | 420 | 0.001707 | 4e-06 | N
21-02-19 | 08:00 | ZN9118:PA20 | URBAN | Planned |  | 2 | 420 | 0.000569 | 1e-06 | N
21-02-19 | 08:00 | ZN9035:PA1 | URBAN | Planned |  | 2 | 420 | 0.000569 | 1e-06 | N
21-02-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 23 | 540 | 0.051949 | 9.6e-05 | N
21-02-19 | 08:00 | ZN9037:PA8 | URBAN | Planned |  | 38 | 480 | 0.012358 | 2.6e-05 | N
21-02-19 | 08:00 | ZN195:PA23 | URBAN | Planned |  | 35 | 210 | 0.00498 | 2.4e-05 | N
07-06-19 | 08:00 | ZN15001:PA18 | URBAN | Planned |  | 16 | 360 | 0.003903 | 1.1e-05 | N
06-06-19 | 21:00 | ZN847:PA46 | URBAN | Planned |  | 59 | 240 | 0.009594 | 4e-05 | N
06-06-19 | 21:00 | ZN847:PA46 | URBAN | Planned |  | 52 | 240 | 0.008455 | 3.5e-05 | N
08-06-19 | 06:30 | ZN847:PA44 | URBAN | Planned |  | 14 | 240 | 0.002276 | 9e-06 | N
08-06-19 | 21:30 | ZN847:PA46 | URBAN | Planned |  | 25 | 600 | 0.010161 | 1.7e-05 | N
09-06-19 | 10:30 | ZN847:PA46 | URBAN | Planned |  | 79 | 360 | 0.019264 | 5.4e-05 | N
09-06-19 | 21:30 | ZN847:PA46 | URBAN | Planned |  | 79 | 600 | 0.032107 | 5.4e-05 | N
06-06-19 | 20:00 | ZN2835:PA20 | URBAN | Planned |  | 2 | 780 | 0.001057 | 1e-06 | N
06-06-19 | 18:00 | ZN3425:PA15 | URBAN | Planned |  | 2 | 240 | 0.000325 | 1e-06 | N
06-06-19 | 09:00 | ZN15015:PA5 | URBAN | Planned |  | 18 | 180 | 0.002195 | 1.2e-05 | N
06-06-19 | 08:30 | ZN2568:PA32 | URBAN | Planned |  | 123 | 420 | 0.035001 | 8.3e-05 | N
06-06-19 | 08:30 | ZN2568:PA32 | URBAN | Planned |  | 59 | 420 | 0.016789 | 4e-05 | N
06-06-19 | 08:00 | ZN2400:PA11 | SHORT RURAL | Planned |  | 20 | 300 | 0.024968 | 8.3e-05 | N
06-06-19 | 08:00 | ZN36200:PA4 | SHORT RURAL | Planned |  | 18 | 480 | 0.035953 | 7.5e-05 | N
06-06-19 | 08:00 | ZN12570:PA34 | SHORT RURAL | Planned |  | 44 | 480 | 0.087886 | 0.000183 | N
06-06-19 | 08:00 | ZN12570:PA34 | SHORT RURAL | Planned |  | 85 | 480 | 0.16978 | 0.000354 | N
06-06-19 | 08:00 | ZN965:PA11 | URBAN | Planned |  | 78 | 480 | 0.025366 | 5.3e-05 | N
06-06-19 | 08:00 | ZN965:PA15 | URBAN | Planned |  | 64 | 480 | 0.020813 | 4.3e-05 | N
06-06-19 | 07:30 | ZN4545:PA29 | URBAN | Planned |  | 125 | 480 | 0.040651 | 8.5e-05 | N
06-06-19 | 07:00 | ZN15009:PA11 | URBAN | Planned |  | 107 | 600 | 0.043497 | 7.2e-05 | N
06-06-19 | 07:30 | ZN9245:PA19 | URBAN | Planned |  | 90 | 570 | 0.034757 | 6.1e-05 | N
06-06-19 | 07:30 | ZN9245:PA21 | URBAN | Planned |  | 42 | 240 | 0.006829 | 2.8e-05 | N
06-06-19 | 07:00 | ZN7481:PA12 | URBAN | Planned |  | 109 | 600 | 0.04431 | 7.4e-05 | N
05-06-19 | 20:00 | ZN10998:PA31 | URBAN | Planned |  | 16 | 300 | 0.003252 | 1.1e-05 | N
05-06-19 | 20:00 | ZN10998:PA8 | URBAN | Planned |  | 18 | 300 | 0.003659 | 1.2e-05 | N
21-02-19 | 20:00 | ZN35555:PA20 | URBAN | Planned |  | 11 | 660 | 0.004919 | 7e-06 | N
05-06-19 | 08:00 | ZN12610:PA22 | URBAN | Planned |  | 48 | 480 | 0.01561 | 3.3e-05 | N
05-06-19 | 08:00 | ZN847:PA10 | URBAN | Planned |  | 88 | 480 | 0.028618 | 6e-05 | N
05-06-19 | 08:00 | ZN1193:PA12 | URBAN | Planned |  | 20 | 480 | 0.006504 | 1.4e-05 | N
22-02-19 | 08:00 | ZN9245:PA3 | SHORT RURAL | Planned |  | 7 | 420 | 0.012297 | 2.9e-05 | N
05-06-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 12 | 480 | 0.023969 | 5e-05 | N
01-05-19 | 08:00 | ZN12650:PA17 | URBAN | Planned |  | 78 | 540 | 0.028496 | 5.3e-05 | N
05-06-19 | 07:00 | ZN15012:PA8 | URBAN | Planned |  | 85 | 510 | 0.02937 | 5.8e-05 | N
04-06-19 | 10:30 | ZN10998:PA10 | URBAN | Planned |  | 62 | 270 | 0.011341 | 4.2e-05 | N
22-02-19 | 08:00 | ZN9037:PA8 | URBAN | Planned |  | 20 | 480 | 0.006504 | 1.4e-05 | N
04-06-19 | 08:45 | ZN847:PA28 | URBAN | Planned |  | 26 | 375 | 0.006606 | 1.8e-05 | N
04-06-19 | 07:00 | ZN3425:PA16 | URBAN | Planned |  | 19 | 30 | 0.000386 | 1.3e-05 | N
03-06-19 | 16:00 | ZN36800:PA43 | URBAN | Planned |  | 139 | 60 | 0.005651 | 9.4e-05 | N
22-02-19 | 08:00 | ZN12570:PA34 | SHORT RURAL | Planned |  | 15 | 540 | 0.03388 | 6.3e-05 | N
22-02-19 | 08:00 | ZN12570:PA34 | SHORT RURAL | Planned |  | 29 | 540 | 0.065501 | 0.000121 | N
03-06-19 | 09:30 | ZN3922:PA19 | URBAN | Planned |  | 108 | 360 | 0.026345 | 7.3e-05 | N
03-06-19 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 3 | 510 | 0.006369 | 1.2e-05 | N
03-06-19 | 08:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 1 | 480 | 0.001998 | 4e-06 | N
03-06-19 | 08:00 | ZN10993:PA35 | URBAN | Planned |  | 87 | 480 | 0.028297 | 5.9e-05 | N
22-02-19 | 08:00 | ZN12660:PA14 | SHORT RURAL | Planned |  | 66 | 420 | 0.11594 | 0.000276 | N
23-02-19 | 06:00 | ZN35500:PA23 | URBAN | Planned |  | 19 | 180 | 0.002317 | 1.3e-05 | N
03-06-19 | 08:00 | ZN2568:PA29 | URBAN | Planned |  | 208 | 420 | 0.059196 | 0.000141 | N
03-06-19 | 07:00 | ZN4545:PA44 | URBAN | Planned |  | 196 | 540 | 0.071718 | 0.000133 | N
23-02-19 | 07:00 | ZN1068:PA26 | URBAN | Planned |  | 1 | 660 | 0.000447 | 1e-06 | N
03-06-19 | 07:00 | ZN2196:PA2 | URBAN | Planned |  | 2 | 300 | 0.000407 | 1e-06 | N
24-02-19 | 07:00 | ZN8100:PA20 | URBAN | Planned |  | 13 | 360 | 0.00317 | 9e-06 | N
03-06-19 | 08:00 | ZN9900:PA13 | URBAN | Planned |  | 28 | 510 | 0.009676 | 1.9e-05 | N
24-02-19 | 07:00 | ZN12650:PA2 | URBAN | Planned |  | 13 | 600 | 0.005283 | 9e-06 | N
02-06-19 | 09:00 | ZN9700:PA18 | URBAN | Planned |  | 29 | 270 | 0.005306 | 2e-05 | N
02-06-19 | 08:00 | ZN36300:PA11 | URBAN | Planned |  | 114 | 330 | 0.025492 | 7.7e-05 | N
02-06-19 | 08:00 | ZN36300:PA3 | URBAN | Planned |  | 79 | 330 | 0.017665 | 5.4e-05 | N
22-02-19 | 22:00 | ZN7900:PA23 | URBAN | Planned |  | 8 | 3,180 | 0.017236 | 5e-06 | N
02-06-19 | 07:00 | ZN3288:PA45 46GHJ | CBD | Planned |  | 5 | 480 | 0.079064 | 0.000165 | N
25-02-19 | 07:00 | ZN36000:PA12 | URBAN | Planned |  | 5 | 540 | 0.001829 | 3e-06 | N
01-06-19 | 18:00 | ZN15013:PA8 | URBAN | Planned |  | 1 | 300 | 0.000203 | 1e-06 | N
01-06-19 | 09:00 | ZN384:PA63 | SHORT RURAL | Planned |  | 1 | 180 | 0.000749 | 4e-06 | N
25-02-19 | 08:00 | ZN10999:PA36 | URBAN | Planned |  | 3 | 480 | 0.000975 | 2e-06 | N
01-06-19 | 09:00 | ZN3472:PA34 | URBAN | Planned |  | 29 | 330 | 0.006485 | 2e-05 | N
01-06-19 | 09:30 | ZN2196:PA13 | URBAN | Planned |  | 1 | 1,620 | 0.001098 | 1e-06 | N
25-02-19 | 08:00 | ZN12570:PA22 | SHORT RURAL | Planned |  | 140 | 540 | 0.31605 | 0.000585 | N
01-06-19 | 07:00 | ZN2196:PA11 | URBAN | Planned |  | 1 | 630 | 0.000427 | 1e-06 | N
01-06-19 | 07:30 | ZN2466:PA15 | URBAN | Planned |  | 1 | 210 | 0.000142 | 1e-06 | N
31-05-19 | 21:00 | ZN931:PA3 | URBAN | Planned |  | 36 | 360 | 0.008782 | 2.4e-05 | N
30-05-19 | 16:00 | ZN187:PA30 | URBAN | Planned |  | 37 | 420 | 0.010531 | 2.5e-05 | N
25-02-19 | 08:30 | ZN10994:PA11 | URBAN | Planned |  | 5 | 450 | 0.001524 | 3e-06 | N
30-05-19 | 22:30 | ZN180:PA19 | URBAN | Planned |  | 61 | 60 | 0.00248 | 4.1e-05 | N
25-02-19 | 19:00 | ZN3425:PA36 | URBAN | Planned |  | 3 | 750 | 0.001524 | 2e-06 | N
25-02-19 | 20:00 | ZN36100:PA1 | URBAN | Planned |  | 80 | 420 | 0.02276 | 5.4e-05 | N
25-02-19 | 20:30 | ZN847:PA21 | URBAN | Planned |  | 12 | 570 | 0.004633 | 8e-06 | N
25-02-19 | 22:00 | ZN3155:PA23 | URBAN | Planned |  | 27 | 420 | 0.007681 | 1.8e-05 | N
26-02-19 | 07:00 | ZN188:PA4 | SHORT RURAL | Planned |  | 1 | 600 | 0.002508 | 4e-06 | N
26-02-19 | 08:00 | ZN15008:PA5 | URBAN | Planned |  | 22 | 420 | 0.006259 | 1.5e-05 | N
26-02-19 | 08:00 | ZN10991:PA8 | URBAN | Planned |  | 30 | 420 | 0.008535 | 2e-05 | N
26-02-19 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 24 | 480 | 0.048162 | 0.0001 | N
26-02-19 | 09:45 | ZN690:PA28 | URBAN | Planned |  | 114 | 345 | 0.026641 | 7.7e-05 | N
26-02-19 | 18:30 | ZN8700:PA67A 68A | URBAN | Planned |  | 2 | 810 | 0.001097 | 1e-06 | N
27-02-19 | 00:30 | ZN12580:PA2 | URBAN | Planned |  | 1 | 2,700 | 0.001829 | 1e-06 | N
27-02-19 | 07:00 | ZN15014:PA19 | URBAN | Planned |  | 43 | 540 | 0.015729 | 2.9e-05 | N
27-02-19 | 07:30 | ZN690:PA35 | URBAN | Planned |  | 51 | 450 | 0.015546 | 3.5e-05 | N
27-02-19 | 07:30 | ZN901:PA20 | URBAN | Planned |  | 1 | 480 | 0.000325 | 1e-06 | N
27-02-19 | 08:00 | ZN847:PA23 | URBAN | Planned |  | 1 | 300 | 0.000203 | 1e-06 | N
27-02-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 12 | 480 | 0.024081 | 5e-05 | N
27-02-19 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 12 | 480 | 0.024081 | 5e-05 | N
27-02-19 | 08:00 | ZN9252:PA22 | URBAN | Planned |  | 39 | 480 | 0.012681 | 2.6e-05 | N
27-02-19 | 08:30 | ZN14892:PA21 | URBAN | Planned |  | 57 | 390 | 0.015058 | 3.9e-05 | N
27-02-19 | 18:30 | ZN8700:PA67 68ABC | CBD | Planned |  | 1 | 810 | 0.026453 | 3.3e-05 | N
28-02-19 | 05:00 | ZN12580:PA4 | URBAN | Planned |  | 1 | 720 | 0.000488 | 1e-06 | N
28-02-19 | 07:00 | ZN36800:PA43 | URBAN | Planned |  | 32 | 540 | 0.011705 | 2.2e-05 | N
28-02-19 | 07:00 | ZN36800:PA40 | URBAN | Planned |  | 43 | 300 | 0.008738 | 2.9e-05 | N
28-02-19 | 08:00 | ZN15008:PA5 | URBAN | Planned |  | 22 | 420 | 0.006259 | 1.5e-05 | N
28-02-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 1 | 480 | 0.002007 | 4e-06 | N
28-02-19 | 08:00 | ZN10997:PA12 | URBAN | Planned |  | 36 | 480 | 0.011705 | 2.4e-05 | N
28-02-19 | 18:30 | ZN8700:PA67 68ABC | CBD | Planned |  | 1 | 810 | 0.026455 | 3.3e-05 | N
28-02-19 | 19:00 | ZN195:PA22 | URBAN | Planned |  | 1 | 720 | 0.000488 | 1e-06 | N
14-02-19 | 08:00 | ZN4545:PA28 | URBAN | Planned |  | 195 | 480 | 0.063422 | 0.000132 | N
14-03-19 | 08:00 | ZN2602:PA4 | URBAN | Planned |  | 62 | 480 | 0.020149 | 4.2e-05 | N
28-03-19 | 06:00 | ZN2568:PA17 | URBAN | Planned |  | 1 | 10,260 | 0.006945 | 1e-06 | N
01-04-19 | 07:00 | ZN15014:PA10 | SHORT RURAL | Planned |  | 53 | 630 | 0.13942 | 0.000221 | N
02-04-19 | 07:30 | ZN35600:PA9 | URBAN | Planned |  | 30 | 540 | 0.010964 | 2e-05 | N
02-04-19 | 08:00 | ZN15009:PA7 | URBAN | Planned |  | 25 | 420 | 0.007107 | 1.7e-05 | N
02-04-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 32 | 480 | 0.064137 | 0.000134 | N
02-04-19 | 08:00 | ZN14891:PA21 | SHORT RURAL | Planned |  | 6 | 480 | 0.012026 | 2.5e-05 | N
02-04-19 | 08:30 | ZN12630:PA8 | SHORT RURAL | Planned |  | 2 | 180 | 0.001503 | 8e-06 | N
02-04-19 | 22:00 | ZN931:PA26 | URBAN | Planned |  | 22 | 300 | 0.004467 | 1.5e-05 | N
03-04-19 | 07:00 | ZN3922:PA18 | URBAN | Planned |  | 127 | 540 | 0.046416 | 8.6e-05 | N
03-04-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 13 | 480 | 0.026056 | 5.4e-05 | N
03-04-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 10 | 480 | 0.020043 | 4.2e-05 | N
03-04-19 | 08:30 | ZN3155:PA17 | URBAN | Planned |  | 33 | 210 | 0.00469 | 2.2e-05 | N
04-04-19 | 06:00 | ZN10995:PA5 | URBAN | Planned |  | 4 | 840 | 0.002274 | 3e-06 | N
04-04-19 | 07:00 | ZN384:PA73 | URBAN | Planned |  | 1 | 540 | 0.000365 | 1e-06 | N
04-04-19 | 07:00 | ZN384:PA70 | URBAN | Planned |  | 1 | 540 | 0.000365 | 1e-06 | N
04-04-19 | 08:00 | ZN35400:PA73 | URBAN | Planned |  | 2 | 540 | 0.000731 | 1e-06 | N
04-04-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 19 | 480 | 0.038083 | 7.9e-05 | N
04-04-19 | 08:30 | ZN3155:PA44 | URBAN | Planned |  | 64 | 450 | 0.019493 | 4.3e-05 | N
04-04-19 | 08:30 | ZN36200:PA4 | SHORT RURAL | Planned |  | 76 | 390 | 0.12377 | 0.000317 | N
04-04-19 | 19:00 | ZN15001:PA18 | URBAN | Planned |  | 140 | 210 | 0.019899 | 9.5e-05 | N
05-04-19 | 02:00 | ZN1610:PA17 | URBAN | Planned |  | 8 | 30 | 0.000162 | 5e-06 | N
05-04-19 | 20:00 | ZN15014:PA10 | SHORT RURAL | Planned |  | 53 | 2,400 | 0.53117 | 0.000221 | N
05-04-19 | 20:00 | ZN35500:PA23 | URBAN | Planned |  | 19 | 2,400 | 0.030864 | 1.3e-05 | N
07-04-19 | 20:00 | ZN3288:PA41 42ABC | CBD | Planned |  | 2 | 60 | 0.003928 | 6.5e-05 | N
07-04-19 | 21:00 | ZN7900:PA11 | URBAN | Planned |  | 48 | 480 | 0.015594 | 3.2e-05 | N
08-04-19 | 08:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 117 | 480 | 0.23452 | 0.000489 | N
18-04-19 | 07:00 | ZN10999:PA39 | URBAN | Planned |  | 2 | 30,600 | 0.041422 | 1e-06 | N
30-04-19 | 22:00 | ZN35400:PA88 | URBAN | Planned |  | 13 | 570 | 0.005013 | 9e-06 | N
01-05-19 | 00:00 | ZN35400:PA101 | URBAN | Planned |  | 40 | 180 | 0.004871 | 2.7e-05 | N
01-05-19 | 07:00 | ZN9900:PA8 | URBAN | Planned |  | 126 | 540 | 0.046032 | 8.5e-05 | N
01-05-19 | 07:30 | ZN35800:PA10 | URBAN | Planned |  | 19 | 450 | 0.005784 | 1.3e-05 | N
01-05-19 | 08:00 | ZN129:PA38 | URBAN | Planned |  | 32 | 480 | 0.010392 | 2.2e-05 | N
01-05-19 | 07:30 | ZN14891:PA12 | SHORT RURAL | Planned |  | 2 | 180 | 0.001499 | 8e-06 | N
01-05-19 | 08:00 | ZN36100:PA27 | URBAN | Planned |  | 85 | 420 | 0.024153 | 5.8e-05 | N
01-05-19 | 08:00 | ZN35370:PA4 | SHORT RURAL | Planned |  | 47 | 480 | 0.093965 | 0.000196 | N
02-05-19 | 07:00 | ZN15005:PA2 | URBAN | Planned |  | 79 | 390 | 0.020845 | 5.3e-05 | N
02-05-19 | 08:00 | ZN36100:PA19 | URBAN | Planned |  | 52 | 480 | 0.016887 | 3.5e-05 | N
02-05-19 | 07:30 | ZN2635:PA38 | URBAN | Planned |  | 72 | 570 | 0.027766 | 4.9e-05 | N
02-05-19 | 07:30 | ZN965:PA11 | URBAN | Planned |  | 75 | 570 | 0.028923 | 5.1e-05 | N
03-05-19 | 08:00 | ZN10998:PA26 | URBAN | Planned |  | 2 | 480 | 0.000649 | 1e-06 | N
08-04-19 | 08:00 | ZN12620:PA1 | SHORT RURAL | Planned |  | 62 | 450 | 0.11651 | 0.000259 | N
08-04-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 2 | 480 | 0.004009 | 8e-06 | N
08-04-19 | 12:00 | ZN12640:PA10 | URBAN | Planned |  | 132 | 300 | 0.026803 | 8.9e-05 | N
08-04-19 | 21:00 | ZN188:PA4 | SHORT RURAL | Planned |  | 174 | 240 | 0.17438 | 0.000727 | N
03-05-19 | 09:30 | ZN8000:PA38 | URBAN | Planned |  | 3 | 480 | 0.000974 | 2e-06 | N
03-05-19 | 09:00 | ZN12640:PA5 | URBAN | Planned |  | 49 | 420 | 0.013924 | 3.3e-05 | N
03-05-19 | 21:00 | ZN187:PA28 | URBAN | Planned |  | 1 | 120 | 8.1e-05 | 1e-06 | N
09-04-19 | 07:30 | ZN2835:PA24 | URBAN | Planned |  | 60 | 480 | 0.019489 | 4.1e-05 | N
04-05-19 | 06:00 | ZN1673:PA19 | URBAN | Planned |  | 1 | 600 | 0.000406 | 1e-06 | N
04-05-19 | 06:00 | ZN4990:PA53 54GHJ | CBD | Planned |  | 26 | 600 | 0.51372 | 0.000856 | N
09-04-19 | 07:30 | ZN180:PA7 | URBAN | Planned |  | 89 | 480 | 0.028909 | 6e-05 | N
04-05-19 | 08:00 | ZN5868:PA27 | URBAN | Planned |  | 18 | 60 | 0.000731 | 1.2e-05 | N
04-05-19 | 12:00 | ZN2196:PA14 | URBAN | Planned |  | 1 | 300 | 0.000203 | 1e-06 | N
09-04-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 14 | 480 | 0.028052 | 5.8e-05 | N
09-04-19 | 08:00 | ZN35600:PA3 | URBAN | Planned |  | 25 | 360 | 0.00609 | 1.7e-05 | N
05-05-19 | 08:00 | ZN12630:PA11 | SHORT RURAL | Planned |  | 20 | 540 | 0.04497 | 8.3e-05 | N
09-04-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 10 | 480 | 0.020037 | 4.2e-05 | N
05-05-19 | 08:00 | ZN9900:PA2 | URBAN | Planned |  | 30 | 510 | 0.01035 | 2e-05 | N
06-05-19 | 07:30 | ZN15014:PA10 | SHORT RURAL | Planned |  | 34 | 540 | 0.076449 | 0.000142 | N
06-05-19 | 08:00 | ZN12640:PA10 | URBAN | Planned |  | 86 | 360 | 0.020943 | 5.8e-05 | N
06-05-19 | 09:00 | ZN965:PA20 | URBAN | Planned |  | 74 | 360 | 0.018021 | 5e-05 | N
09-04-19 | 08:00 | ZN965:PA29 | URBAN | Planned |  | 20 | 480 | 0.006496 | 1.4e-05 | N
07-05-19 | 08:00 | ZN36200:PA8 | SHORT RURAL | Planned |  | 92 | 510 | 0.19537 | 0.000383 | N
09-04-19 | 08:30 | ZN12650:PA12 | URBAN | Planned |  | 148 | 300 | 0.030046 | 0.0001 | N
07-05-19 | 08:00 | ZN12660:PA14 | SHORT RURAL | Planned |  | 38 | 480 | 0.07595 | 0.000158 | N
09-04-19 | 18:00 | ZN8700:PA67A 68A | URBAN | Planned |  | 1 | 840 | 0.000568 | 1e-06 | N
07-05-19 | 09:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 78 | 300 | 0.097436 | 0.000325 | N
07-05-19 | 09:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 30 | 300 | 0.037475 | 0.000125 | N
07-05-19 | 20:30 | ZN2466:PA41 | URBAN | Planned |  | 242 | 660 | 0.10805 | 0.000164 | N
08-05-19 | 21:00 | ZN187:PA28 | URBAN | Planned |  | 1 | 120 | 8.1e-05 | 1e-06 | N
08-05-19 | 07:00 | ZN965:PA20 | URBAN | Planned |  | 20 | 360 | 0.004871 | 1.4e-05 | N
10-04-19 | 06:00 | ZN630:PA6 | URBAN | Planned |  | 1 | 720 | 0.000487 | 1e-06 | N
08-05-19 | 07:00 | ZN167:PA11 | URBAN | Planned |  | 2 | 510 | 0.00069 | 1e-06 | N
10-04-19 | 07:30 | ZN3472:PA17 | URBAN | Planned |  | 95 | 450 | 0.028929 | 6.4e-05 | N
08-05-19 | 07:30 | ZN15014:PA10 | SHORT RURAL | Planned |  | 34 | 540 | 0.07645 | 0.000142 | N
08-05-19 | 08:00 | ZN12610:PA17 | URBAN | Planned |  | 19 | 480 | 0.006169 | 1.3e-05 | N
08-05-19 | 08:30 | ZN3155:PA44 | URBAN | Planned |  | 65 | 450 | 0.019787 | 4.4e-05 | N
10-04-19 | 07:30 | ZN3472:PA27 | URBAN | Planned |  | 35 | 450 | 0.010658 | 2.4e-05 | N
08-05-19 | 13:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 6 | 240 | 0.005996 | 2.5e-05 | N
10-04-19 | 07:00 | ZN8100:PA1 | URBAN | Planned |  | 1 | 420 | 0.000284 | 1e-06 | N
09-05-19 | 07:00 | ZN2568:PA27 | URBAN | Planned |  | 116 | 480 | 0.037666 | 7.8e-05 | N
09-05-19 | 07:00 | ZN3154:PA18 | URBAN | Planned |  | 37 | 360 | 0.009011 | 2.5e-05 | N
09-05-19 | 07:30 | ZN15014:PA10 | SHORT RURAL | Planned |  | 34 | 540 | 0.07645 | 0.000142 | N
09-05-19 | 08:00 | ZN12610:PA7 | URBAN | Planned |  | 30 | 480 | 0.009741 | 2e-05 | N
09-05-19 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 9 | 240 | 0.008994 | 3.7e-05 | N
10-05-19 | 07:00 | ZN3155:PA20 | URBAN | Planned |  | 171 | 420 | 0.048584 | 0.000116 | N
10-05-19 | 07:30 | ZN1287:PA16 | URBAN | Planned |  | 1 | 360 | 0.000244 | 1e-06 | N
10-05-19 | 08:00 | ZN9900:PA19 | URBAN | Planned |  | 65 | 480 | 0.021106 | 4.4e-05 | N
10-05-19 | 07:00 | ZN80:PA21 | URBAN | Planned |  | 11 | 540 | 0.004018 | 7e-06 | N
10-05-19 | 07:00 | ZN15004:PA3 | SHORT RURAL | Planned |  | 33 | 600 | 0.082446 | 0.000137 | N
10-05-19 | 09:00 | ZN690:PA34 | URBAN | Planned |  | 98 | 240 | 0.015911 | 6.6e-05 | N
10-05-19 | 09:00 | ZN14144:PA4 | URBAN | Planned |  | 21 | 390 | 0.00554 | 1.4e-05 | N
10-05-19 | 09:00 | ZN13000:PA7 | SHORT RURAL | Planned |  | 49 | 390 | 0.079573 | 0.000204 | N
10-05-19 | 18:00 | ZN5868:PA10 | URBAN | Planned |  | 13 | 810 | 0.007123 | 9e-06 | N
11-05-19 | 07:00 | ZN630:PA30 | URBAN | Planned |  | 1 | 30 | 2e-05 | 1e-06 | N
11-05-19 | 08:30 | ZN263:PA33 34ABC | CBD | Planned |  | 40 | 180 | 0.23714 | 0.001317 | N
11-05-19 | 07:00 | ZN15011:PA8 | URBAN | Planned |  | 28 | 660 | 0.012501 | 1.9e-05 | N
11-05-19 | 09:30 | ZN2568:PA17 | URBAN | Planned |  | 1 | 390 | 0.000264 | 1e-06 | N
12-05-19 | 06:00 | ZN5868:PA25 | URBAN | Planned |  | 2 | 480 | 0.000649 | 1e-06 | N
12-05-19 | 07:00 | ZN4545:PA26 | URBAN | Planned |  | 7 | 540 | 0.002557 | 5e-06 | N
12-05-19 | 14:00 | ZN3155:PA15 | URBAN | Planned |  | 34 | 840 | 0.01932 | 2.3e-05 | N
12-05-19 | 18:00 | ZN9015:PA1 | SHORT RURAL | Planned |  | 2 | 720 | 0.005996 | 8e-06 | N
13-05-19 | 07:00 | ZN15004:PA3 | SHORT RURAL | Planned |  | 47 | 600 | 0.11745 | 0.000196 | N
13-05-19 | 07:00 | ZN15004:PA5 | URBAN | Planned |  | 48 | 600 | 0.019479 | 3.2e-05 | N
13-05-19 | 08:00 | ZN3154:PA22 | SHORT RURAL | Planned |  | 39 | 420 | 0.068223 | 0.000162 | N
13-05-19 | 09:00 | ZN35600:PA20 | URBAN | Planned |  | 21 | 360 | 0.005113 | 1.4e-05 | N
14-05-19 | 14:30 | ZN1285:PA22 | URBAN | Planned |  | 53 | 210 | 0.007528 | 3.6e-05 | N
14-05-19 | 15:00 | ZN2835:PA36 | URBAN | Planned |  | 74 | 180 | 0.009009 | 5e-05 | N
14-05-19 | 07:00 | ZN3154:PA5 | URBAN | Planned |  | 145 | 480 | 0.047075 | 9.8e-05 | N
14-05-19 | 08:30 | ZN2568:PA22 | URBAN | Planned |  | 66 | 390 | 0.01741 | 4.5e-05 | N
14-05-19 | 08:00 | ZN12620:PA11 | SHORT RURAL | Planned |  | 43 | 510 | 0.091339 | 0.000179 | N
14-05-19 | 08:00 | ZN36200:PA8 | SHORT RURAL | Planned |  | 20 | 510 | 0.042483 | 8.3e-05 | N
14-05-19 | 08:00 | ZN1673:PA6 | URBAN | Planned |  | 18 | 420 | 0.005113 | 1.2e-05 | N
14-05-19 | 09:00 | ZN195:PA28 | URBAN | Planned |  | 27 | 240 | 0.004383 | 1.8e-05 | N
14-05-19 | 19:00 | ZN2635:PA39 | URBAN | Planned |  | 54 | 660 | 0.024106 | 3.7e-05 | N
15-05-19 | 07:00 | ZN342:PA33 | URBAN | Planned |  | 41 | 180 | 0.004992 | 2.8e-05 | N
15-05-19 | 07:00 | ZN195:PA3 | URBAN | Planned |  | 41 | 600 | 0.016639 | 2.8e-05 | N
15-05-19 | 08:00 | ZN4545:PA40 | URBAN | Planned |  | 56 | 210 | 0.007954 | 3.8e-05 | N
15-05-19 | 12:00 | ZN342:PA33 | URBAN | Planned |  | 41 | 180 | 0.004992 | 2.8e-05 | N
15-05-19 | 08:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 10 | 480 | 0.01999 | 4.2e-05 | N
15-05-19 | 08:00 | ZN965:PA47 | URBAN | Planned |  | 51 | 420 | 0.014488 | 3.4e-05 | N
15-05-19 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 5 | 240 | 0.004998 | 2.1e-05 | N
15-05-19 | 09:30 | ZN15008:PA5 | URBAN | Planned |  | 73 | 120 | 0.005925 | 4.9e-05 | N
15-05-19 | 21:00 | ZN1673:PA21 | SHORT RURAL | Planned |  | 15 | 240 | 0.014993 | 6.2e-05 | N
16-05-19 | 22:30 | ZN10995:PA5 | URBAN | Planned |  | 24 | 300 | 0.00487 | 1.6e-05 | N
15-05-19 | 22:30 | ZN15011:PA4 | URBAN | Planned |  | 38 | 390 | 0.010024 | 2.6e-05 | N
16-05-19 | 07:30 | ZN1788:PA20 | URBAN | Planned |  | 51 | 180 | 0.006209 | 3.4e-05 | N
16-05-19 | 07:30 | ZN847:PA15 | URBAN | Planned |  | 56 | 480 | 0.01818 | 3.8e-05 | N
16-05-19 | 07:30 | ZN15012:PA6 | URBAN | Planned |  | 3 | 330 | 0.00067 | 2e-06 | N
16-05-19 | 08:00 | ZN12610:PA24 | URBAN | Planned |  | 59 | 540 | 0.021548 | 4e-05 | N
16-05-19 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 5 | 540 | 0.011245 | 2.1e-05 | N
16-05-19 | 08:00 | ZN180:PA17 | URBAN | Planned |  | 57 | 420 | 0.016191 | 3.9e-05 | N
16-05-19 | 08:00 | ZN15008:PA1 | URBAN | Planned |  | 62 | 420 | 0.017612 | 4.2e-05 | N
09-05-19 | 08:00 | ZN12580:PA16 | URBAN | Planned |  | 15 | 10,560 | 0.10715 | 1e-05 | N
16-05-19 | 09:00 | ZN195:PA10 | URBAN | Planned |  | 28 | 360 | 0.006817 | 1.9e-05 | N
16-05-19 | 19:00 | ZN35500:PA31 | URBAN | Planned |  | 102 | 660 | 0.045531 | 6.9e-05 | N
16-05-19 | 21:00 | ZN630:PA14 | URBAN | Planned |  | 5 | 240 | 0.000812 | 3e-06 | N
16-05-19 | 22:00 | ZN3425:PA24 | URBAN | Planned |  | 42 | 480 | 0.013635 | 2.8e-05 | N
17-05-19 | 06:00 | ZN8000:PA12 | URBAN | Planned |  | 1 | 60 | 4.1e-05 | 1e-06 | N
17-05-19 | 08:00 | ZN2835:PA24 | URBAN | Planned |  | 59 | 420 | 0.01676 | 4e-05 | N
17-05-19 | 08:00 | ZN12660:PA8 | URBAN | Planned |  | 69 | 480 | 0.0224 | 4.7e-05 | N
17-05-19 | 09:00 | ZN12570:PA41 | URBAN | Planned |  | 9 | 360 | 0.002191 | 6e-06 | N
17-05-19 | 09:00 | ZN965:PA4 | URBAN | Planned |  | 45 | 360 | 0.010957 | 3e-05 | N
17-05-19 | 20:30 | ZN12580:PA16 | URBAN | Planned |  | 4 | 420 | 0.001136 | 3e-06 | N
18-05-19 | 06:00 | ZN2466:PA27 | URBAN | Planned |  | 2 | 720 | 0.000974 | 1e-06 | N
18-05-19 | 07:30 | ZN8700:PA65 66ABC | CBD | Planned |  | 64 | 30 | 0.063279 | 0.002109 | N
18-05-19 | 18:00 | ZN15013:PA8 | URBAN | Planned |  | 1 | 300 | 0.000203 | 1e-06 | N
19-05-19 | 06:30 | ZN10999:PA14 | URBAN | Planned |  | 1 | 15 | 1e-05 | 1e-06 | N
19-05-19 | 07:00 | ZN847:PA31 | URBAN | Planned |  | 115 | 600 | 0.046668 | 7.8e-05 | N
19-05-19 | 04:30 | ZN9700:PA17 | URBAN | Planned |  | 22 | 210 | 0.003125 | 1.5e-05 | N
19-05-19 | 07:00 | ZN35800:PA10 | URBAN | Planned |  | 19 | 540 | 0.006939 | 1.3e-05 | N
20-05-19 | 08:00 | ZN9245:PA1 | URBAN | Planned |  | 31 | 540 | 0.011322 | 2.1e-05 | N
20-05-19 | 07:00 | ZN1648:PA1 | SHORT RURAL | Planned |  | 4 | 600 | 0.009995 | 1.7e-05 | N
20-05-19 | 07:00 | ZN15014:PA10 | SHORT RURAL | Planned |  | 40 | 600 | 0.099952 | 0.000167 | N
22-05-19 | 07:00 | ZN711:PA18 | SHORT RURAL | Planned |  | 151 | 600 | 0.37732 | 0.000629 | N
22-05-19 | 08:00 | ZN12630:PA13 | SHORT RURAL | Planned |  | 8 | 480 | 0.015993 | 3.3e-05 | N
20-05-19 | 07:00 | ZN10998:PA9 | URBAN | Planned |  | 1 | 420 | 0.000284 | 1e-06 | N
20-05-19 | 08:00 | ZN12620:PA1 | SHORT RURAL | Planned |  | 62 | 450 | 0.11619 | 0.000258 | N
20-05-19 | 08:00 | ZN847:PA21 | URBAN | Planned |  | 131 | 360 | 0.031896 | 8.9e-05 | N
20-05-19 | 08:00 | ZN847:PA21 | URBAN | Planned |  | 50 | 360 | 0.012174 | 3.4e-05 | N
20-05-19 | 09:00 | ZN15005:PA8 | URBAN | Planned |  | 116 | 240 | 0.018829 | 7.8e-05 | N
20-05-19 | 09:00 | ZN129:PA41 | URBAN | Planned |  | 29 | 420 | 0.008238 | 2e-05 | N
20-05-19 | 19:00 | ZN12690:PA11 | URBAN | Planned |  | 5 | 660 | 0.002232 | 3e-06 | N
21-05-19 | 23:30 | ZN12690:PA4 | URBAN | Planned |  | 5 | 120 | 0.000406 | 3e-06 | N
21-05-19 | 07:00 | ZN36100:PA2 | URBAN | Planned |  | 238 | 540 | 0.086925 | 0.000161 | N
21-05-19 | 08:00 | ZN9900:PA5 | URBAN | Planned |  | 40 | 480 | 0.012986 | 2.7e-05 | N
21-05-19 | 08:00 | ZN36200:PA8 | SHORT RURAL | Planned |  | 228 | 510 | 0.48427 | 0.00095 | N
21-05-19 | 08:00 | ZN14143:PA14 | URBAN | Planned |  | 4 | 330 | 0.000893 | 3e-06 | N
21-05-19 | 09:00 | ZN14144:PA1 | URBAN | Planned |  | 31 | 300 | 0.00629 | 2.1e-05 | N
21-05-19 | 12:30 | ZN14144:PA4 | URBAN | Planned |  | 95 | 180 | 0.011566 | 6.4e-05 | N
22-05-19 | 07:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 123 | 60 | 0.030736 | 0.000512 | N
22-05-19 | 16:30 | ZN12630:PA1 | SHORT RURAL | Planned |  | 123 | 60 | 0.030736 | 0.000512 | N
22-05-19 | 07:30 | ZN384:PA70 | URBAN | Planned |  | 74 | 180 | 0.009009 | 5e-05 | N
22-05-19 | 07:30 | ZN9118:PA26 | URBAN | Planned |  | 104 | 510 | 0.035874 | 7e-05 | N
21-05-19 | 08:00 | ZN35370:PA4 | SHORT RURAL | Planned |  | 7 | 480 | 0.013993 | 2.9e-05 | N
22-05-19 | 08:00 | ZN12620:PA1 | SHORT RURAL | Planned |  | 34 | 450 | 0.06372 | 0.000142 | N
22-05-19 | 08:30 | ZN35600:PA3 | URBAN | Planned |  | 25 | 360 | 0.006087 | 1.7e-05 | N
22-05-19 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 24 | 420 | 0.04198 | 0.0001 | N
22-05-19 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 44 | 480 | 0.087959 | 0.000183 | N
22-05-19 | 08:00 | ZN965:PA35 | URBAN | Planned |  | 67 | 420 | 0.019033 | 4.5e-05 | N
22-05-19 | 09:30 | ZN9900:PA21 | URBAN | Planned |  | 1 | 330 | 0.000223 | 1e-06 | N
22-05-19 | 09:30 | ZN9900:PA8 | URBAN | Planned |  | 5 | 330 | 0.001116 | 3e-06 | N
22-05-19 | 21:00 | ZN2568:PA21 | URBAN | Planned |  | 3 | 120 | 0.000243 | 2e-06 | N
23-05-19 | 07:00 | ZN15001:PA15 | URBAN | Planned |  | 56 | 600 | 0.022726 | 3.8e-05 | N
23-05-19 | 07:00 | ZN965:PA42 | URBAN | Planned |  | 113 | 540 | 0.041273 | 7.6e-05 | N
23-05-19 | 07:00 | ZN187:PA22 | URBAN | Planned |  | 60 | 390 | 0.015827 | 4.1e-05 | N
23-05-19 | 07:00 | ZN36100:PA8 | URBAN | Planned |  | 52 | 480 | 0.016882 | 3.5e-05 | N
23-05-19 | 07:00 | ZN2835:PA24 | URBAN | Planned |  | 6 | 300 | 0.001217 | 4e-06 | N
23-05-19 | 08:00 | ZN9900:PA2 | URBAN | Planned |  | 27 | 180 | 0.003287 | 1.8e-05 | N
23-05-19 | 08:00 | ZN4990:PA53 54DEF | CBD | Planned |  | 121 | 360 | 1.4357 | 0.003988 | N
23-05-19 | 08:00 | ZN12620:PA11 | SHORT RURAL | Planned |  | 80 | 510 | 0.16992 | 0.000333 | N
23-05-19 | 09:00 | ZN3672:PA13 | URBAN | Planned |  | 84 | 360 | 0.020454 | 5.7e-05 | N
23-05-19 | 08:30 | ZN8000:PA6 | URBAN | Planned |  | 14 | 390 | 0.003693 | 9e-06 | N
23-05-19 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 30 | 420 | 0.052476 | 0.000125 | N
23-05-19 | 09:30 | ZN15008:PA5 | URBAN | Planned |  | 73 | 120 | 0.005925 | 4.9e-05 | N
23-05-19 | 10:00 | ZN13000:PA2 | SHORT RURAL | Planned |  | 2 | 180 | 0.001499 | 8e-06 | N
23-05-19 | 20:00 | ZN3922:PA2 | SHORT RURAL | Planned |  | 44 | 480 | 0.08796 | 0.000183 | N
24-05-19 | 08:00 | ZN901:PA9 | URBAN | Planned |  | 136 | 480 | 0.044154 | 9.2e-05 | N
24-05-19 | 06:00 | ZN3025:PA30251 | URBAN | Planned |  | 1 | 720 | 0.000487 | 1e-06 | N
24-05-19 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 7 | 240 | 0.006997 | 2.9e-05 | N
24-05-19 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 69 | 480 | 0.13794 | 0.000287 | N
24-05-19 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 78 | 510 | 0.16567 | 0.000325 | N
24-05-19 | 09:00 | ZN9118:PA21 | URBAN | Planned |  | 49 | 360 | 0.011931 | 3.3e-05 | N
24-05-19 | 09:00 | ZN195:PA10 | URBAN | Planned |  | 43 | 360 | 0.01047 | 2.9e-05 | N
24-05-19 | 18:00 | ZN12650:PA2 | URBAN | Planned |  | 28 | 180 | 0.003409 | 1.9e-05 | N
24-05-19 | 20:00 | ZN262:PA7 | URBAN | Planned |  | 31 | 720 | 0.015097 | 2.1e-05 | N
24-05-19 | 22:00 | ZN965:PA3 | URBAN | Planned |  | 41 | 420 | 0.011647 | 2.8e-05 | N
25-05-19 | 08:00 | ZN9700:PA19 | URBAN | Planned |  | 44 | 390 | 0.011631 | 3e-05 | N
25-05-19 | 07:00 | ZN630:PA23 | URBAN | Planned |  | 1 | 30 | 2e-05 | 1e-06 | N
25-05-19 | 08:00 | ZN35900:PA25 | SHORT RURAL | Planned |  | 1 | 600 | 0.002497 | 4e-06 | N
25-05-19 | 08:00 | ZN12570:PA22 | SHORT RURAL | Planned |  | 235 | 480 | 0.46942 | 0.000978 | N
25-05-19 | 13:00 | ZN9700:PA12 | URBAN | Planned |  | 56 | 15 | 0.000569 | 3.8e-05 | N
26-05-19 | 07:00 | ZN2568:PA39 | URBAN | Planned |  | 37 | 660 | 0.016552 | 2.5e-05 | N
26-05-19 | 07:00 | ZN14891:PA6 | URBAN | Planned |  | 1 | 600 | 0.000407 | 1e-06 | N
26-05-19 | 07:00 | ZN14891:PA6 | URBAN | Planned |  | 29 | 600 | 0.011794 | 2e-05 | N
26-05-19 | 07:00 | ZN2835:PA9 | URBAN | Planned |  | 113 | 480 | 0.036765 | 7.7e-05 | N
26-05-19 | 09:00 | ZN2568:PA21 | URBAN | Planned |  | 3 | 60 | 0.000122 | 2e-06 | N
26-05-19 | 20:00 | ZN2635:PA58 | URBAN | Planned |  | 68 | 600 | 0.027655 | 4.6e-05 | N
27-05-19 | 07:00 | ZN4545:PA19 | URBAN | Planned |  | 45 | 600 | 0.018301 | 3.1e-05 | N
27-05-19 | 07:30 | ZN3922:PA10 | URBAN | Planned |  | 51 | 450 | 0.015556 | 3.5e-05 | N
27-05-19 | 08:00 | ZN10999:PA10 | URBAN | Planned |  | 74 | 360 | 0.018057 | 5e-05 | N
27-05-19 | 08:00 | ZN3425:PA12 | URBAN | Planned |  | 67 | 480 | 0.021799 | 4.5e-05 | N
27-05-19 | 08:00 | ZN12640:PA12 | URBAN | Planned |  | 139 | 300 | 0.028265 | 9.4e-05 | N
27-05-19 | 08:30 | ZN15015:PA5 | URBAN | Planned |  | 157 | 120 | 0.01277 | 0.000106 | N
27-05-19 | 13:30 | ZN15015:PA5 | URBAN | Planned |  | 157 | 120 | 0.01277 | 0.000106 | N
27-05-19 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 71 | 510 | 0.15069 | 0.000295 | N
27-05-19 | 08:00 | ZN12570:PA37 | SHORT RURAL | Planned |  | 32 | 480 | 0.06392 | 0.000133 | N
27-05-19 | 12:00 | ZN2635:PA31 | URBAN | Planned |  | 29 | 240 | 0.004718 | 2e-05 | N
27-05-19 | 22:00 | ZN7900:PA11 | URBAN | Planned |  | 48 | 420 | 0.013665 | 3.3e-05 | N
27-05-19 | 22:00 | ZN2835:PA42 | URBAN | Planned |  | 7 | 450 | 0.002135 | 5e-06 | N
28-05-19 | 08:00 | ZN9252:PA21 | URBAN | Planned |  | 69 | 540 | 0.025256 | 4.7e-05 | N
28-05-19 | 07:30 | ZN80:PA31 | URBAN | Planned |  | 60 | 540 | 0.021961 | 4.1e-05 | N
28-05-19 | 08:00 | ZN15006:PA8 | URBAN | Planned |  | 100 | 480 | 0.032535 | 6.8e-05 | N
28-05-19 | 08:00 | ZN3672:PA44 | URBAN | Planned |  | 50 | 420 | 0.014234 | 3.4e-05 | N
28-05-19 | 08:00 | ZN10999:PA17 | URBAN | Planned |  | 55 | 240 | 0.008947 | 3.7e-05 | N
28-05-19 | 08:00 | ZN7481:PA10 | URBAN | Planned |  | 24 | 420 | 0.006832 | 1.6e-05 | N
28-05-19 | 08:00 | ZN7481:PA2 | URBAN | Planned |  | 10 | 420 | 0.002847 | 7e-06 | N
28-05-19 | 08:00 | ZN7481:PA5 | URBAN | Planned |  | 8 | 420 | 0.002277 | 5e-06 | N
28-05-19 | 08:00 | ZN7481:PA8 | URBAN | Planned |  | 1 | 420 | 0.000285 | 1e-06 | N
28-05-19 | 07:30 | ZN2635:PA38 | URBAN | Planned |  | 33 | 570 | 0.01275 | 2.2e-05 | N
28-05-19 | 08:00 | ZN14144:PA1 | URBAN | Planned |  | 46 | 420 | 0.013095 | 3.1e-05 | N
28-05-19 | 08:30 | ZN9900:PA2 | URBAN | Planned |  | 38 | 420 | 0.010818 | 2.6e-05 | N
29-05-19 | 07:00 | ZN1068:PA21 | URBAN | Planned |  | 72 | 270 | 0.013174 | 4.9e-05 | N
29-05-19 | 07:00 | ZN1068:PA21 | URBAN | Planned |  | 2 | 570 | 0.000773 | 1e-06 | N
29-05-19 | 08:00 | ZN1193:PA11 | URBAN | Planned |  | 46 | 480 | 0.014963 | 3.1e-05 | N
29-05-19 | 07:00 | ZN15015:PA5 | URBAN | Planned |  | 92 | 480 | 0.029926 | 6.2e-05 | N
29-05-19 | 08:00 | ZN9700:PA20 | URBAN | Planned |  | 46 | 480 | 0.014963 | 3.1e-05 | N
29-05-19 | 07:30 | ZN1673:PA13 | URBAN | Planned |  | 77 | 480 | 0.025047 | 5.2e-05 | N
29-05-19 | 07:30 | ZN847:PA15 | URBAN | Planned |  | 51 | 480 | 0.016589 | 3.5e-05 | N
29-05-19 | 08:00 | ZN3154:PA23 | URBAN | Planned |  | 122 | 480 | 0.039684 | 8.3e-05 | N
29-05-19 | 08:00 | ZN14891:PA17 | SHORT RURAL | Planned |  | 21 | 540 | 0.047175 | 8.7e-05 | N
29-05-19 | 08:00 | ZN14891:PA21 | SHORT RURAL | Planned |  | 82 | 540 | 0.18421 | 0.000341 | N
29-05-19 | 09:00 | ZN3672:PA13 | URBAN | Planned |  | 71 | 360 | 0.017321 | 4.8e-05 | N
29-05-19 | 09:30 | ZN9118:PA13 | URBAN | Planned |  | 82 | 330 | 0.018338 | 5.6e-05 | N
29-05-19 | 10:00 | ZN874:PA17 | URBAN | Planned |  | 38 | 180 | 0.004635 | 2.6e-05 | N
30-05-19 | 07:00 | ZN10998:PA5 | URBAN | Planned |  | 34 | 600 | 0.013825 | 2.3e-05 | N
30-05-19 | 07:00 | ZN847:PA46 | URBAN | Planned |  | 94 | 660 | 0.042043 | 6.4e-05 | N
30-05-19 | 08:00 | ZN9900:PA13 | URBAN | Planned |  | 49 | 510 | 0.016935 | 3.3e-05 | N
30-05-19 | 14:00 | ZN2466:PA17 | SHORT RURAL | Planned |  | 59 | 240 | 0.058906 | 0.000245 | N
30-05-19 | 07:00 | ZN15001:PA3 | URBAN | Planned |  | 3 | 600 | 0.00122 | 2e-06 | N
30-05-19 | 08:00 | ZN2400:PA18 | SHORT RURAL | Planned |  | 59 | 480 | 0.11781 | 0.000245 | N
30-05-19 | 07:00 | ZN35600:PA16 | URBAN | Planned |  | 33 | 480 | 0.010734 | 2.2e-05 | N
30-05-19 | 07:30 | ZN35800:PA15 | URBAN | Planned |  | 1 | 630 | 0.000427 | 1e-06 | N
30-05-19 | 07:30 | ZN35800:PA15 | URBAN | Planned |  | 20 | 570 | 0.007725 | 1.4e-05 | N
30-05-19 | 08:30 | ZN3155:PA44 | URBAN | Planned |  | 65 | 450 | 0.019822 | 4.4e-05 | N
30-05-19 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 163 | 480 | 0.32548 | 0.000678 | N
30-05-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 10 | 420 | 0.017472 | 4.2e-05 | N
30-05-19 | 09:00 | ZN12580:PA8 | URBAN | Planned |  | 3 | 420 | 0.000854 | 2e-06 | N
30-05-19 | 16:00 | ZN187:PA30 | URBAN | Planned |  | 52 | 420 | 0.0148 | 3.5e-05 | N
30-05-19 | 19:00 | ZN129:PA49 | URBAN | Planned |  | 62 | 720 | 0.030251 | 4.2e-05 | N
31-05-19 | 05:00 | ZN1648:PA1 | SHORT RURAL | Planned |  | 1 | 1,740 | 0.007243 | 4e-06 | N
30-05-19 | 22:00 | ZN10993:PA26 | URBAN | Planned |  | 38 | 180 | 0.004635 | 2.6e-05 | N
30-05-19 | 23:30 | ZN10999:PA19 | URBAN | Planned |  | 391 | 210 | 0.055644 | 0.000265 | N
31-05-19 | 07:00 | ZN35800:PA1 | URBAN | Planned |  | 100 | 540 | 0.036591 | 6.8e-05 | N
31-05-19 | 08:30 | ZN36100:PA19 | URBAN | Planned |  | 64 | 450 | 0.019515 | 4.3e-05 | N
31-05-19 | 08:00 | ZN12570:PA25 | SHORT RURAL | Planned |  | 45 | 420 | 0.078675 | 0.000187 | N
31-05-19 | 08:00 | ZN195:PA11 | URBAN | Planned |  | 20 | 540 | 0.007318 | 1.4e-05 | N
31-05-19 | 08:00 | ZN3154:PA18 | URBAN | Planned |  | 19 | 540 | 0.006952 | 1.3e-05 | N
31-05-19 | 08:00 | ZN3154:PA16 | URBAN | Planned |  | 25 | 480 | 0.008131 | 1.7e-05 | N
31-05-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 29 | 480 | 0.057945 | 0.000121 | N
31-05-19 | 09:00 | ZN36300:PA13 | URBAN | Planned |  | 130 | 180 | 0.015856 | 8.8e-05 | N
10-04-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 22 | 480 | 0.044081 | 9.2e-05 | N
11-04-19 | 07:30 | ZN2310:PA2 | URBAN | Planned |  | 88 | 450 | 0.026798 | 6e-05 | N
11-04-19 | 08:30 | ZN14891:PA17 | SHORT RURAL | Planned |  | 51 | 270 | 0.057483 | 0.000213 | N
11-04-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 24 | 390 | 0.039073 | 0.0001 | N
11-04-19 | 21:00 | ZN36100:PA27 | URBAN | Planned |  | 85 | 480 | 0.02761 | 5.8e-05 | N
12-04-19 | 08:00 | ZN116:PA14 | URBAN | Planned |  | 57 | 480 | 0.018516 | 3.9e-05 | N
12-04-19 | 08:00 | ZN12570:PA35 | URBAN | Planned |  | 18 | 480 | 0.005847 | 1.2e-05 | N
12-04-19 | 08:00 | ZN12600:PA13 | SHORT RURAL | Planned |  | 1 | 480 | 0.002004 | 4e-06 | N
12-04-19 | 21:30 | ZN2835:PA10 | URBAN | Planned |  | 53 | 240 | 0.008608 | 3.6e-05 | N
12-04-19 | 21:30 | ZN2835:PA10 | URBAN | Planned |  | 32 | 240 | 0.005197 | 2.2e-05 | N
13-04-19 | 07:00 | ZN187:PA12 | URBAN | Planned |  | 2 | 60 | 8.1e-05 | 1e-06 | N
13-04-19 | 07:00 | ZN931:PA1 | URBAN | Planned |  | 1 | 30 | 2e-05 | 1e-06 | N
13-04-19 | 07:00 | ZN931:PA1 | URBAN | Planned |  | 7 | 480 | 0.002274 | 5e-06 | N
13-04-19 | 07:00 | ZN931:PA25 | URBAN | Planned |  | 36 | 660 | 0.01608 | 2.4e-05 | N
13-04-19 | 08:00 | ZN12620:PA8 | SHORT RURAL | Planned |  | 99 | 540 | 0.22317 | 0.000413 | N
15-04-19 | 08:00 | ZN80:PA37 | URBAN | Planned |  | 46 | 1,920 | 0.059771 | 3.1e-05 | N
15-04-19 | 08:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 16 | 480 | 0.032061 | 6.7e-05 | N
15-04-19 | 08:00 | ZN14144:PA7 | SHORT RURAL | Planned |  | 162 | 480 | 0.32461 | 0.000676 | N
15-04-19 | 08:00 | ZN12620:PA8 | SHORT RURAL | Planned |  | 42 | 510 | 0.089419 | 0.000175 | N
15-04-19 | 08:00 | ZN3154:PA4 | URBAN | Planned |  | 16 | 420 | 0.004548 | 1.1e-05 | N
15-04-19 | 08:00 | ZN847:PA39 | URBAN | Planned |  | 32 | 480 | 0.010395 | 2.2e-05 | N
15-04-19 | 10:00 | ZN9550:PA9 | URBAN | Planned |  | 1 | 60 | 4.1e-05 | 1e-06 | N
15-04-19 | 21:00 | ZN3154:PA24 | URBAN | Planned |  | 32 | 240 | 0.005197 | 2.2e-05 | N
16-04-19 | 06:30 | ZN8000:PA1 | URBAN | Planned |  | 3 | 30 | 6.1e-05 | 2e-06 | N
16-04-19 | 08:00 | ZN4545:PA44 | URBAN | Planned |  | 6 | 480 | 0.001949 | 4e-06 | N
16-04-19 | 07:00 | ZN847:PA19 | URBAN | Planned |  | 2 | 540 | 0.000731 | 1e-06 | N
17-04-19 | 08:30 | ZN2568:PA22 | URBAN | Planned |  | 46 | 390 | 0.012144 | 3.1e-05 | N
17-04-19 | 07:30 | ZN3154:PA22 | SHORT RURAL | Planned |  | 50 | 480 | 0.099949 | 0.000208 | N
17-04-19 | 08:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 15 | 480 | 0.029985 | 6.2e-05 | N
17-04-19 | 08:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 4 | 480 | 0.007996 | 1.7e-05 | N
17-04-19 | 08:00 | ZN2635:PA46 | URBAN | Planned |  | 64 | 480 | 0.020795 | 4.3e-05 | N
17-04-19 | 08:00 | ZN4545:PA29 | URBAN | Planned |  | 27 | 480 | 0.008773 | 1.8e-05 | N
17-04-19 | 20:30 | ZN2568:PA25 | URBAN | Planned |  | 4 | 600 | 0.001625 | 3e-06 | N
17-04-19 | 21:30 | ZN187:PA20 | URBAN | Planned |  | 28 | 300 | 0.005686 | 1.9e-05 | N
18-04-19 | 08:00 | ZN3672:PA44 | URBAN | Planned |  | 49 | 420 | 0.013929 | 3.3e-05 | N
18-04-19 | 08:30 | ZN12650:PA13 | SHORT RURAL | Planned |  | 36 | 390 | 0.05852 | 0.00015 | N
18-04-19 | 10:00 | ZN14891:PA10 | SHORT RURAL | Planned |  | 25 | 300 | 0.031261 | 0.000104 | N
18-04-19 | 18:00 | ZN13000:PA8 | SHORT RURAL | Planned |  | 1 | 2,880 | 0.012004 | 4e-06 | N
18-04-19 | 18:00 | ZN3288:PA45 46KLM | CBD | Planned |  | 42 | 5,520 | 7.607 | 0.001378 | N
23-04-19 | 16:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 6 | 120 | 0.003 | 2.5e-05 | N
26-04-19 | 07:00 | ZN2400:PA15 | SHORT RURAL | Planned |  | 45 | 660 | 0.12374 | 0.000187 | N
28-04-19 | 07:00 | ZN2568:PA28 | URBAN | Planned |  | 3 | 780 | 0.001583 | 2e-06 | N
28-04-19 | 09:00 | ZN931:PA9 | URBAN | Planned |  | 8 | 420 | 0.002273 | 5e-06 | N
28-04-19 | 08:00 | ZN5868:PA3 | URBAN | Planned |  | 10 | 540 | 0.003653 | 7e-06 | N
28-04-19 | 08:00 | ZN5868:PA17 | URBAN | Planned |  | 1 | 540 | 0.000365 | 1e-06 | N
28-04-19 | 19:00 | ZN8100:PA1 | URBAN | Planned |  | 5 | 660 | 0.002233 | 3e-06 | N
29-04-19 | 07:00 | ZN187:PA30 | URBAN | Planned |  | 71 | 240 | 0.011528 | 4.8e-05 | N
15-04-19 | 08:30 | ZN187:PA30 | URBAN | Planned |  | 79 | 390 | 0.020851 | 5.3e-05 | N
29-04-19 | 07:00 | ZN901:PA20 | URBAN | Planned |  | 151 | 660 | 0.067423 | 0.000102 | N
29-04-19 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 5 | 540 | 0.011246 | 2.1e-05 | N
29-04-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 49 | 480 | 0.097962 | 0.000204 | N
29-04-19 | 08:00 | ZN847:PA18 | SHORT RURAL | Planned |  | 50 | 450 | 0.093714 | 0.000208 | N
29-04-19 | 09:00 | ZN3672:PA6 | URBAN | Planned |  | 2 | 150 | 0.000203 | 1e-06 | N
29-04-19 | 07:30 | ZN35555:PA17 | URBAN | Planned |  | 65 | 450 | 0.019789 | 4.4e-05 | N
29-04-19 | 11:00 | ZN2602:PA30 | URBAN | Planned |  | 99 | 240 | 0.016074 | 6.7e-05 | N
29-04-19 | 12:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 1 | 150 | 0.000625 | 4e-06 | N
30-04-19 | 07:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 318 | 630 | 0.83443 | 0.001324 | N
30-04-19 | 06:30 | ZN3472:PA17 | URBAN | Planned |  | 83 | 240 | 0.013477 | 5.6e-05 | N
30-04-19 | 07:30 | ZN1648:PA4 | URBAN | Planned |  | 46 | 450 | 0.014004 | 3.1e-05 | N
30-04-19 | 08:00 | ZN9900:PA5 | URBAN | Planned |  | 31 | 480 | 0.010067 | 2.1e-05 | N
30-04-19 | 19:30 | ZN1290:PA12 | URBAN | Planned |  | 12 | 150 | 0.001218 | 8e-06 | N
14-12-18 | 08:00 | ZN10993:PA39 | URBAN | Planned |  | 1 | 450 | 0.000305 | 1e-06 | N
14-12-18 | 08:00 | ZN10999:PA32 | URBAN | Planned |  | 1 | 450 | 0.000305 | 1e-06 | N
14-12-18 | 07:30 | ZN35555:PA6 | URBAN | Planned |  | 21 | 450 | 0.006407 | 1.4e-05 | N
14-12-18 | 07:30 | ZN2635:PA31 | URBAN | Planned |  | 12 | 540 | 0.004393 | 8e-06 | N
14-12-18 | 07:30 | ZN2635:PA57 | URBAN | Planned |  | 90 | 540 | 0.032949 | 6.1e-05 | N
14-12-18 | 08:30 | ZN36100:PA19 | URBAN | Planned |  | 87 | 330 | 0.019465 | 5.9e-05 | N
14-12-18 | 08:30 | ZN36100:PA19 | URBAN | Planned |  | 85 | 330 | 0.019017 | 5.8e-05 | N
14-12-18 | 08:00 | ZN12640:PA8 | SHORT RURAL | Planned |  | 57 | 480 | 0.11519 | 0.00024 | N
14-12-18 | 08:00 | ZN15002:PA4 | SHORT RURAL | Planned |  | 6 | 480 | 0.012125 | 2.5e-05 | N
14-12-18 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 16 | 480 | 0.032334 | 6.7e-05 | N
14-12-18 | 10:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 13 | 180 | 0.009852 | 5.5e-05 | N
15-12-18 | 06:00 | ZN7481:PA12 | URBAN | Planned |  | 5 | 660 | 0.002237 | 3e-06 | N
15-12-18 | 07:00 | ZN1610:PA18 | URBAN | Planned |  | 9 | 360 | 0.002196 | 6e-06 | N
15-12-18 | 09:00 | ZN15012:PA6 | URBAN | Planned |  | 4 | 240 | 0.000651 | 3e-06 | N
15-12-18 | 13:00 | ZN9245:PA3 | SHORT RURAL | Planned |  | 4 | 180 | 0.003031 | 1.7e-05 | N
16-12-18 | 20:00 | ZN263:PA33 34DEF | CBD | Planned |  | 5 | 600 | 0.098393 | 0.000164 | N
16-12-18 | 20:30 | ZN3288:PA45 46GHJ | CBD | Planned |  | 6 | 360 | 0.070843 | 0.000197 | N
17-12-18 | 07:00 | ZN2568:PA38 | URBAN | Planned |  | 72 | 420 | 0.020495 | 4.9e-05 | N
17-12-18 | 07:00 | ZN36100:PA7 | URBAN | Planned |  | 46 | 600 | 0.018706 | 3.1e-05 | N
17-12-18 | 21:00 | ZN263:PA31 32GHJ | CBD | Planned |  | 1 | 420 | 0.013775 | 3.3e-05 | N
18-12-18 | 07:00 | ZN3472:PA17 | URBAN | Planned |  | 16 | 510 | 0.00553 | 1.1e-05 | N
18-12-18 | 08:00 | ZN12570:PA29 | SHORT RURAL | Planned |  | 32 | 480 | 0.064649 | 0.000135 | N
18-12-18 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 20 | 480 | 0.040406 | 8.4e-05 | N
18-12-18 | 07:00 | ZN342:PA18 | URBAN | Planned |  | 214 | 540 | 0.07832 | 0.000145 | N
18-12-18 | 19:30 | ZN3155:PA24 | URBAN | Planned |  | 1 | 540 | 0.000366 | 1e-06 | N
19-12-18 | 08:00 | ZN129:PA38 | URBAN | Planned |  | 33 | 360 | 0.008051 | 2.2e-05 | N
19-12-18 | 07:00 | ZN2466:PA26 | URBAN | Planned |  | 1 | 570 | 0.000386 | 1e-06 | N
19-12-18 | 07:30 | ZN3155:PA24 | URBAN | Planned |  | 1 | 450 | 0.000305 | 1e-06 | N
10-12-18 | 07:00 | ZN188:PA26 | URBAN | Planned |  | 87 | 510 | 0.030097 | 5.9e-05 | N
19-12-18 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 13 | 480 | 0.026264 | 5.5e-05 | N
19-12-18 | 19:00 | ZN15009:PA1 | URBAN | Planned |  | 9 | 660 | 0.004025 | 6e-06 | N
19-12-18 | 19:00 | ZN15009:PA1 | URBAN | Planned |  | 11 | 660 | 0.00492 | 7e-06 | N
20-12-18 | 07:30 | ZN398:PA3 | URBAN | Planned |  | 75 | 720 | 0.036595 | 5.1e-05 | N
22-12-18 | 07:00 | ZN1290:PA11 | URBAN | Planned |  | 1 | 780 | 0.000528 | 1e-06 | N
20-12-18 | 08:00 | ZN2196:PA3 | URBAN | Planned |  | 45 | 420 | 0.012808 | 3e-05 | N
20-12-18 | 08:00 | ZN10993:PA35 | URBAN | Planned |  | 92 | 480 | 0.029926 | 6.2e-05 | N
20-12-18 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 7 | 480 | 0.014142 | 2.9e-05 | N
20-12-18 | 09:00 | ZN2835:PA35 | URBAN | Planned |  | 1 | 270 | 0.000183 | 1e-06 | N
20-12-18 | 13:00 | ZN2568:PA19 | URBAN | Planned |  | 4 | 300 | 0.000813 | 3e-06 | N
21-12-18 | 08:00 | ZN690:PA5 | URBAN | Planned |  | 44 | 450 | 0.013418 | 3e-05 | N
06-12-18 | 08:00 | ZN35400:PA110 | URBAN | Planned |  | 37 | 420 | 0.010538 | 2.5e-05 | N
22-12-18 | 07:30 | ZN10999:PA25 | URBAN | Planned |  | 9 | 330 | 0.002012 | 6e-06 | N
23-12-18 | 23:15 | ZN2835:PA22 | URBAN | Planned |  | 16 | 480 | 0.005203 | 1.1e-05 | N
19-12-18 | 08:30 | ZN2400:PA18 | SHORT RURAL | Planned |  | 14 | 300 | 0.017677 | 5.9e-05 | N
28-12-18 | 08:00 | ZN9118:PA21 | URBAN | Planned |  | 50 | 480 | 0.01626 | 3.4e-05 | N
30-12-18 | 16:00 | ZN3288:PA43 44KLM | CBD | Planned |  | 1 | 1,440 | 0.047229 | 3.3e-05 | N
02-01-19 | 07:00 | ZN9900:PA1 | URBAN | Planned |  | 2 | 600 | 0.000813 | 1e-06 | N
05-01-19 | 05:00 | ZN35400:PA90 | URBAN | Planned |  | 25 | 840 | 0.014228 | 1.7e-05 | N
05-01-19 | 07:00 | ZN1788:PA15 | URBAN | Planned |  | 1 | 60 | 4.1e-05 | 1e-06 | N
07-01-19 | 10:00 | ZN12620:PA11 | SHORT RURAL | Planned |  | 4 | 300 | 0.005049 | 1.7e-05 | N
08-01-19 | 08:00 | ZN9118:PA13 | URBAN | Planned |  | 56 | 480 | 0.018212 | 3.8e-05 | N
08-01-19 | 08:00 | ZN9118:PA8 | URBAN | Planned |  | 99 | 480 | 0.032196 | 6.7e-05 | N
14-12-18 | 07:00 | ZN690:PA35 | URBAN | Planned |  | 21 | 540 | 0.007688 | 1.4e-05 | N
09-01-19 | 07:00 | ZN630:PA26 | URBAN | Planned |  | 21 | 540 | 0.007683 | 1.4e-05 | N
09-01-19 | 08:30 | ZN36100:PA19 | URBAN | Planned |  | 76 | 450 | 0.023171 | 5.1e-05 | N
09-01-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 38 | 540 | 0.086343 | 0.00016 | N
09-01-19 | 08:00 | ZN15005:PA2 | URBAN | Planned |  | 108 | 480 | 0.035123 | 7.3e-05 | N
09-01-19 | 10:30 | ZN2835:PA30 | URBAN | Planned |  | 17 | 270 | 0.00311 | 1.2e-05 | N
10-01-19 | 21:30 | ZN36100:PA27 | URBAN | Planned |  | 115 | 480 | 0.0374 | 7.8e-05 | N
12-01-19 | 06:00 | ZN630:PA25 | URBAN | Planned |  | 10 | 660 | 0.004472 | 7e-06 | N
13-01-19 | 07:00 | ZN15011:PA10 | URBAN | Planned |  | 10 | 420 | 0.002845 | 7e-06 | N
13-01-19 | 07:00 | ZN188:PA15 | URBAN | Planned |  | 22 | 720 | 0.010729 | 1.5e-05 | N
21-01-19 | 07:30 | ZN711:PA33 | URBAN | Planned |  | 316 | 600 | 0.12862 | 0.000214 | N
14-01-19 | 07:00 | ZN3922:PA11 | URBAN | Planned |  | 18 | 540 | 0.006588 | 1.2e-05 | N
14-01-19 | 08:30 | ZN14891:PA5 | SHORT RURAL | Planned |  | 2 | 360 | 0.003029 | 8e-06 | N
14-01-19 | 09:00 | ZN35400:PA73 | URBAN | Planned |  | 74 | 360 | 0.018055 | 5e-05 | N
14-01-19 | 19:30 | ZN15006:PA1 | SHORT RURAL | Planned |  | 7 | 240 | 0.007067 | 2.9e-05 | N
15-01-19 | 07:30 | ZN15014:PA22 | URBAN | Planned |  | 15 | 540 | 0.005496 | 1e-05 | N
15-01-19 | 07:00 | ZN35900:PA20 | URBAN | Planned |  | 126 | 510 | 0.043598 | 8.5e-05 | N
15-01-19 | 08:00 | ZN35400:PA101 | URBAN | Planned |  | 92 | 480 | 0.029961 | 6.2e-05 | N
15-01-19 | 08:00 | ZN14891:PA5 | SHORT RURAL | Planned |  | 3 | 300 | 0.003786 | 1.3e-05 | N
15-01-19 | 09:00 | ZN15010:PA28 | SHORT RURAL | Planned |  | 42 | 300 | 0.053005 | 0.000177 | N
15-01-19 | 17:00 | ZN15014:PA8 | URBAN | Planned |  | 1 | 540 | 0.000366 | 1e-06 | N
15-01-19 | 06:30 | ZN35555:PA8 | URBAN | Planned |  | 23 | 870 | 0.013576 | 1.6e-05 | N
16-01-19 | 07:00 | ZN3472:PA30 | URBAN | Planned |  | 27 | 540 | 0.009898 | 1.8e-05 | N
16-01-19 | 13:00 | ZN3154:PA5 | URBAN | Planned |  | 122 | 60 | 0.004969 | 8.3e-05 | N
16-01-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 38 | 540 | 0.086323 | 0.00016 | N
16-01-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 3 | 480 | 0.006058 | 1.3e-05 | N
16-01-19 | 10:30 | ZN2568:PA22 | URBAN | Planned |  | 171 | 300 | 0.034825 | 0.000116 | N
16-01-19 | 21:00 | ZN36800:PA42 | URBAN | Planned |  | 125 | 420 | 0.03564 | 8.5e-05 | N
17-01-19 | 07:00 | ZN3155:PA17 | URBAN | Planned |  | 42 | 540 | 0.015388 | 2.8e-05 | N
17-01-19 | 08:00 | ZN10999:PA29 | URBAN | Planned |  | 58 | 480 | 0.018889 | 3.9e-05 | N
17-01-19 | 07:30 | ZN1287:PA15 | URBAN | Planned |  | 80 | 420 | 0.022797 | 5.4e-05 | N
17-01-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 3 | 540 | 0.006815 | 1.3e-05 | N
17-01-19 | 09:00 | ZN167:PA10 | URBAN | Planned |  | 126 | 120 | 0.010259 | 8.5e-05 | N
17-01-19 | 20:00 | ZN2466:PA29 | URBAN | Planned |  | 7 | 120 | 0.00057 | 5e-06 | N
18-01-19 | 10:00 | ZN12630:PA10 | SHORT RURAL | Planned |  | 1 | 360 | 0.001515 | 4e-06 | N
19-01-19 | 09:00 | ZN188:PA21 | URBAN | Planned |  | 52 | 390 | 0.013758 | 3.5e-05 | N
19-01-19 | 07:00 | ZN14892:PA1 | SHORT RURAL | Planned |  | 1 | 660 | 0.002776 | 4e-06 | N
01-03-19 | 07:00 | ZN2196:PA9 | URBAN | Planned |  | 2 | 120 | 0.000163 | 1e-06 | N
03-03-19 | 08:00 | ZN342:PA24 | URBAN | Planned |  | 146 | 60 | 0.005932 | 9.9e-05 | N
01-03-19 | 08:00 | ZN10994:PA11 | URBAN | Planned |  | 104 | 420 | 0.029589 | 7e-05 | N
01-03-19 | 08:30 | ZN12620:PA7 | URBAN | Planned |  | 70 | 270 | 0.012803 | 4.7e-05 | N
01-03-19 | 20:30 | ZN847:PA5 | URBAN | Planned |  | 38 | 510 | 0.013128 | 2.6e-05 | N
02-03-19 | 06:45 | ZN116:PA29 | URBAN | Planned |  | 1 | 585 | 0.000396 | 1e-06 | N
02-03-19 | 06:45 | ZN116:PA1 | URBAN | Planned |  | 1 | 2,025 | 0.001372 | 1e-06 | N
03-03-19 | 07:00 | ZN15011:PA10 | URBAN | Planned |  | 4 | 600 | 0.001625 | 3e-06 | N
03-03-19 | 07:30 | ZN3155:PA15 | URBAN | Planned |  | 48 | 660 | 0.021452 | 3.3e-05 | N
03-03-19 | 20:00 | ZN3288:PA41 42ABC | CBD | Planned |  | 2 | 60 | 0.003918 | 6.5e-05 | N
03-03-19 | 19:00 | ZN398:PA25 | URBAN | Planned |  | 8 | 780 | 0.004225 | 5e-06 | N
03-03-19 | 20:00 | ZN15001:PA2 | URBAN | Planned |  | 3 | 600 | 0.001219 | 2e-06 | N
04-03-19 | 06:00 | ZN3288:PA41 42KLM | CBD | Planned |  | 8 | 3,240 | 0.84623 | 0.000261 | N
04-03-19 | 08:00 | ZN931:PA2 | URBAN | Planned |  | 120 | 540 | 0.043876 | 8.1e-05 | N
04-03-19 | 19:30 | ZN398:PA25 | URBAN | Planned |  | 70 | 660 | 0.031282 | 4.7e-05 | N
04-03-19 | 22:00 | ZN1285:PA30 | URBAN | Planned |  | 1 | 420 | 0.000284 | 1e-06 | N
04-03-19 | 22:00 | ZN35900:PA3 | URBAN | Planned |  | 1 | 420 | 0.000284 | 1e-06 | N
05-03-19 | 07:00 | ZN3922:PA18 | URBAN | Planned |  | 45 | 600 | 0.018282 | 3e-05 | N
05-03-19 | 08:00 | ZN9037:PA8 | URBAN | Planned |  | 32 | 480 | 0.0104 | 2.2e-05 | N
05-03-19 | 08:00 | ZN14144:PA10 | SHORT RURAL | Planned |  | 44 | 450 | 0.082772 | 0.000184 | N
05-03-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 97 | 480 | 0.19464 | 0.000406 | N
05-03-19 | 16:30 | ZN263:PA31 32GHJ | CBD | Planned |  | 1 | 360 | 0.011753 | 3.3e-05 | N
06-03-19 | 07:30 | ZN2835:PA31 | URBAN | Planned |  | 15 | 450 | 0.00457 | 1e-05 | N
06-03-19 | 07:00 | ZN931:PA2 | URBAN | Planned |  | 72 | 600 | 0.029251 | 4.9e-05 | N
06-03-19 | 08:00 | ZN9037:PA8 | URBAN | Planned |  | 43 | 480 | 0.013976 | 2.9e-05 | N
06-03-19 | 07:30 | ZN1850:PA45 | URBAN | Planned |  | 59 | 510 | 0.020374 | 4e-05 | N
06-03-19 | 08:30 | ZN12570:PA22 | SHORT RURAL | Planned |  | 15 | 420 | 0.026337 | 6.3e-05 | N
06-03-19 | 11:00 | ZN15011:PA2 | URBAN | Planned |  | 13 | 60 | 0.000528 | 9e-06 | N
06-03-19 | 14:00 | ZN10999:PA39 | URBAN | Planned |  | 2 | 120 | 0.000163 | 1e-06 | N
07-03-19 | 08:00 | ZN9700:PA23 | URBAN | Planned |  | 27 | 480 | 0.008775 | 1.8e-05 | N
07-03-19 | 08:00 | ZN12580:PA10 | URBAN | Planned |  | 24 | 420 | 0.006825 | 1.6e-05 | N
07-03-19 | 10:30 | ZN9900:PA1 | URBAN | Planned |  | 40 | 300 | 0.008125 | 2.7e-05 | N
07-03-19 | 10:30 | ZN9900:PA8 | URBAN | Planned |  | 99 | 300 | 0.02011 | 6.7e-05 | N
09-03-19 | 07:00 | ZN847:PA44 | URBAN | Planned |  | 41 | 540 | 0.014989 | 2.8e-05 | N
09-03-19 | 10:00 | ZN2400:PA15 | SHORT RURAL | Planned |  | 42 | 540 | 0.094803 | 0.000176 | N
10-03-19 | 11:30 | ZN2400:PA15 | SHORT RURAL | Planned |  | 14 | 390 | 0.022823 | 5.9e-05 | N
10-03-19 | 22:00 | ZN188:PA15 | URBAN | Planned |  | 61 | 420 | 0.017345 | 4.1e-05 | N
14-03-19 | 07:30 | ZN35370:PA10 | SHORT RURAL | Planned |  | 23 | 450 | 0.043267 | 9.6e-05 | N
18-03-19 | 07:30 | ZN35370:PA10 | SHORT RURAL | Planned |  | 23 | 450 | 0.043245 | 9.6e-05 | N
11-03-19 | 07:00 | ZN7481:PA12 | URBAN | Planned |  | 1 | 480 | 0.000325 | 1e-06 | N
12-03-19 | 08:00 | ZN14144:PA5 | URBAN | Planned |  | 11 | 480 | 0.003575 | 7e-06 | N
13-03-19 | 08:00 | ZN12580:PA12 | SHORT RURAL | Planned |  | 14 | 480 | 0.02809 | 5.9e-05 | N
11-03-19 | 07:30 | ZN3472:PA30 | URBAN | Planned |  | 22 | 510 | 0.007596 | 1.5e-05 | N
11-03-19 | 07:30 | ZN342:PA26 | URBAN | Planned |  | 68 | 450 | 0.020717 | 4.6e-05 | N
11-03-19 | 08:00 | ZN12650:PA6 | URBAN | Planned |  | 76 | 570 | 0.029328 | 5.1e-05 | N
11-03-19 | 08:00 | ZN35370:PA8 | SHORT RURAL | Planned |  | 12 | 480 | 0.024077 | 5e-05 | N
11-03-19 | 08:00 | ZN15002:PA2 | URBAN | Planned |  | 69 | 450 | 0.021021 | 4.7e-05 | N
11-03-19 | 10:00 | ZN12620:PA11 | SHORT RURAL | Planned |  | 4 | 330 | 0.005518 | 1.7e-05 | N
11-03-19 | 22:00 | ZN263:PA35 37DEF | CBD | Planned |  | 5 | 360 | 0.058747 | 0.000163 | N
12-03-19 | 07:00 | ZN3155:PA21 | URBAN | Planned |  | 9 | 540 | 0.00329 | 6e-06 | N
12-03-19 | 08:00 | ZN9700:PA23 | URBAN | Planned |  | 35 | 480 | 0.011374 | 2.4e-05 | N
12-03-19 | 08:00 | ZN9252:PA22 | URBAN | Planned |  | 86 | 420 | 0.024454 | 5.8e-05 | N
12-03-19 | 07:30 | ZN3472:PA30 | URBAN | Planned |  | 22 | 510 | 0.007596 | 1.5e-05 | N
12-03-19 | 07:30 | ZN342:PA24 | URBAN | Planned |  | 63 | 390 | 0.016634 | 4.3e-05 | N
12-03-19 | 08:00 | ZN12570:PA34 | SHORT RURAL | Planned |  | 31 | 540 | 0.069974 | 0.00013 | N
12-03-19 | 08:00 | ZN12630:PA11 | SHORT RURAL | Planned |  | 2 | 540 | 0.004514 | 8e-06 | N
12-03-19 | 20:00 | ZN262:PA16 | URBAN | Planned |  | 43 | 600 | 0.017467 | 2.9e-05 | N
12-03-19 | 20:00 | ZN35555:PA13 | URBAN | Planned |  | 11 | 600 | 0.004468 | 7e-06 | N
12-03-19 | 20:00 | ZN35555:PA5 | SHORT RURAL | Planned |  | 43 | 600 | 0.10784 | 0.00018 | N
12-03-19 | 22:30 | ZN263:PA33 34DEF | CBD | Planned |  | 4 | 300 | 0.039208 | 0.000131 | N
13-03-19 | 07:00 | ZN187:PA20 | URBAN | Planned |  | 15 | 540 | 0.005484 | 1e-05 | N
13-03-19 | 07:00 | ZN36800:PA49 | URBAN | Planned |  | 32 | 450 | 0.009749 | 2.2e-05 | N
13-03-19 | 08:00 | ZN9037:PA16 | URBAN | Planned |  | 43 | 480 | 0.013974 | 2.9e-05 | N
13-03-19 | 07:00 | ZN2568:PA33 | URBAN | Planned |  | 8 | 540 | 0.002925 | 5e-06 | N
13-03-19 | 08:00 | ZN12570:PA34 | SHORT RURAL | Planned |  | 23 | 480 | 0.046148 | 9.6e-05 | N
13-03-19 | 08:30 | ZN9900:PA12 | URBAN | Planned |  | 30 | 390 | 0.007921 | 2e-05 | N
13-03-19 | 08:00 | ZN8700:PA61 62GHJ | CBD | Planned |  | 3 | 240 | 0.023569 | 9.8e-05 | N
13-03-19 | 12:00 | ZN9900:PA19 | URBAN | Planned |  | 74 | 180 | 0.009018 | 5e-05 | N
13-03-19 | 12:00 | ZN9900:PA13 | URBAN | Planned |  | 63 | 180 | 0.007677 | 4.3e-05 | N
13-03-19 | 22:30 | ZN4990:PA55ABC | CBD | Planned |  | 33 | 300 | 0.32408 | 0.00108 | N
14-03-19 | 08:00 | ZN12600:PA2 | SHORT RURAL | Planned |  | 20 | 480 | 0.040132 | 8.4e-05 | N
14-03-19 | 08:00 | ZN9037:PA8 | URBAN | Planned |  | 65 | 540 | 0.023764 | 4.4e-05 | N
14-03-19 | 08:00 | ZN965:PA42 | URBAN | Planned |  | 75 | 480 | 0.024374 | 5.1e-05 | N
14-03-19 | 08:00 | ZN14892:PA17 | URBAN | Planned |  | 30 | 510 | 0.010359 | 2e-05 | N
14-03-19 | 08:00 | ZN36800:PA43 | URBAN | Planned |  | 45 | 480 | 0.014624 | 3e-05 | N
15-03-19 | 07:30 | ZN901:PA20 | URBAN | Planned |  | 44 | 480 | 0.014299 | 3e-05 | N
15-03-19 | 07:00 | ZN3472:PA28 | URBAN | Planned |  | 3 | 660 | 0.001341 | 2e-06 | N
15-03-19 | 07:00 | ZN3472:PA28 | URBAN | Planned |  | 56 | 660 | 0.025024 | 3.8e-05 | N
15-03-19 | 08:00 | ZN9037:PA8 | URBAN | Planned |  | 36 | 480 | 0.0117 | 2.4e-05 | N
15-03-19 | 08:30 | ZN847:PA18 | SHORT RURAL | Planned |  | 41 | 390 | 0.066845 | 0.000171 | N
15-03-19 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 12 | 450 | 0.022574 | 5e-05 | N
16-03-19 | 08:00 | ZN12650:PA17 | URBAN | Planned |  | 88 | 300 | 0.01787 | 6e-05 | N
17-03-19 | 08:00 | ZN263:PA35 37GHJ | CBD | Planned |  | 61 | 360 | 0.71887 | 0.001997 | N
17-03-19 | 08:00 | ZN263:PA31 32DEF | CBD | Planned |  | 16 | 360 | 0.18856 | 0.000524 | N
17-03-19 | 19:00 | ZN188:PA22 | URBAN | Planned |  | 30 | 600 | 0.012185 | 2e-05 | N
18-03-19 | 07:00 | ZN398:PA11 | URBAN | Planned |  | 32 | 600 | 0.012997 | 2.2e-05 | N
18-03-19 | 08:00 | ZN965:PA2 | SHORT RURAL | Planned |  | 14 | 480 | 0.028078 | 5.8e-05 | N
18-03-19 | 08:00 | ZN15008:PA7 | URBAN | Planned |  | 4 | 420 | 0.001137 | 3e-06 | N
18-03-19 | 08:00 | ZN3154:PA24 | URBAN | Planned |  | 20 | 450 | 0.006092 | 1.4e-05 | N
18-03-19 | 08:00 | ZN2635:PA57 | URBAN | Planned |  | 260 | 480 | 0.084479 | 0.000176 | N
18-03-19 | 08:00 | ZN80:PA31 | URBAN | Planned |  | 73 | 540 | 0.026684 | 4.9e-05 | N
18-03-19 | 08:00 | ZN3672:PA46 | URBAN | Planned |  | 86 | 540 | 0.031436 | 5.8e-05 | N
18-03-19 | 20:00 | ZN1285:PA17 | URBAN | Planned |  | 102 | 690 | 0.047642 | 6.9e-05 | N
19-03-19 | 07:30 | ZN10993:PA26 | URBAN | Planned |  | 23 | 60 | 0.000934 | 1.6e-05 | N
19-03-19 | 07:00 | ZN2466:PA20 | URBAN | Planned |  | 2 | 120 | 0.000162 | 1e-06 | N
19-03-19 | 08:00 | ZN13000:PA7 | SHORT RURAL | Planned |  | 3 | 540 | 0.006769 | 1.3e-05 | N
19-03-19 | 09:00 | ZN14144:PA10 | SHORT RURAL | Planned |  | 40 | 420 | 0.070195 | 0.000167 | N
19-03-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 4 | 480 | 0.008022 | 1.7e-05 | N
19-03-19 | 08:00 | ZN847:PA45 | SHORT RURAL | Planned |  | 10 | 450 | 0.018802 | 4.2e-05 | N
19-03-19 | 08:00 | ZN965:PA29 | URBAN | Planned |  | 65 | 480 | 0.021121 | 4.4e-05 | N
19-03-19 | 09:00 | ZN2400:PA15 | SHORT RURAL | Planned |  | 6 | 300 | 0.007521 | 2.5e-05 | N
19-03-19 | 20:00 | ZN35800:PA14 | URBAN | Planned |  | 25 | 780 | 0.0132 | 1.7e-05 | N
20-03-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 15 | 480 | 0.03009 | 6.3e-05 | N
20-03-19 | 08:00 | ZN13000:PA5 | SHORT RURAL | Planned |  | 40 | 540 | 0.09027 | 0.000167 | N
20-03-19 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 37 | 540 | 0.0835 | 0.000155 | N
20-03-19 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 20 | 540 | 0.045135 | 8.4e-05 | N
20-03-19 | 08:00 | ZN9700:PA16 | URBAN | Planned |  | 50 | 480 | 0.016247 | 3.4e-05 | N
20-03-19 | 08:00 | ZN12630:PA8 | SHORT RURAL | Planned |  | 1 | 540 | 0.002257 | 4e-06 | N
21-03-19 | 07:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 71 | 600 | 0.17803 | 0.000297 | N
21-03-19 | 08:00 | ZN10993:PA23 | URBAN | Planned |  | 214 | 420 | 0.060846 | 0.000145 | N
21-03-19 | 08:00 | ZN10993:PA35 | URBAN | Planned |  | 206 | 420 | 0.058572 | 0.000139 | N
21-03-19 | 08:00 | ZN9118:PA8 | URBAN | Planned |  | 39 | 300 | 0.007921 | 2.6e-05 | N
21-03-19 | 08:30 | ZN9900:PA13 | URBAN | Planned |  | 32 | 450 | 0.009748 | 2.2e-05 | N
21-03-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 9 | 480 | 0.018054 | 3.8e-05 | N
21-03-19 | 08:00 | ZN12570:PA40 | SHORT RURAL | Planned |  | 98 | 300 | 0.12287 | 0.00041 | N
21-03-19 | 10:00 | ZN10997:PA7 | URBAN | Planned |  | 76 | 120 | 0.006174 | 5.1e-05 | N
21-03-19 | 12:00 | ZN12570:PA40 | SHORT RURAL | Planned |  | 46 | 270 | 0.051905 | 0.000192 | N
21-03-19 | 20:00 | ZN965:PA2 | SHORT RURAL | Planned |  | 14 | 540 | 0.031595 | 5.9e-05 | N
21-03-19 | 20:30 | ZN3922:PA13 | SHORT RURAL | Planned |  | 4 | 510 | 0.008526 | 1.7e-05 | N
22-03-19 | 08:00 | ZN9252:PA31 | URBAN | Planned |  | 62 | 420 | 0.017628 | 4.2e-05 | N
22-03-19 | 08:00 | ZN14143:PA17 | SHORT RURAL | Planned |  | 67 | 360 | 0.10079 | 0.00028 | N
22-03-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 5 | 480 | 0.010029 | 2.1e-05 | N
22-03-19 | 09:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 15 | 420 | 0.026327 | 6.3e-05 | N
23-03-19 | 07:00 | ZN901:PA19 | URBAN | Planned |  | 1 | 600 | 0.000406 | 1e-06 | N
23-03-19 | 08:00 | ZN384:PA2 | URBAN | Planned |  | 99 | 360 | 0.024123 | 6.7e-05 | N
24-03-19 | 00:01 | ZN10999:PA9 | URBAN | Planned |  | 77 | 59 | 0.003075 | 5.2e-05 | N
24-03-19 | 07:30 | ZN9118:PA7 | URBAN | Planned |  | 1 | 570 | 0.000386 | 1e-06 | N
24-03-19 | 20:00 | ZN35600:PA9 | URBAN | Planned |  | 51 | 420 | 0.014499 | 3.5e-05 | N
24-03-19 | 21:00 | ZN3288:PA45 46DEF | CBD | Planned |  | 1 | 270 | 0.008839 | 3.3e-05 | N
25-03-19 | 07:00 | ZN3922:PA26 | URBAN | Planned |  | 18 | 480 | 0.005848 | 1.2e-05 | N
25-03-19 | 07:30 | ZN3472:PA30 | URBAN | Planned |  | 27 | 510 | 0.00932 | 1.8e-05 | N
25-03-19 | 08:00 | ZN12600:PA13 | SHORT RURAL | Planned |  | 8 | 480 | 0.016042 | 3.3e-05 | N
26-03-19 | 05:00 | ZN12690:PA11 | URBAN | Planned |  | 1 | 60 | 4.1e-05 | 1e-06 | N
25-03-19 | 08:00 | ZN12620:PA1 | SHORT RURAL | Planned |  | 27 | 480 | 0.054143 | 0.000113 | N
26-03-19 | 08:30 | ZN3155:PA44 | URBAN | Planned |  | 61 | 450 | 0.01858 | 4.1e-05 | N
26-03-19 | 08:00 | ZN12600:PA13 | SHORT RURAL | Planned |  | 2 | 480 | 0.004011 | 8e-06 | N
26-03-19 | 08:00 | ZN35370:PA10 | SHORT RURAL | Planned |  | 5 | 480 | 0.010027 | 2.1e-05 | N
26-03-19 | 21:00 | ZN9037:PA10 | URBAN | Planned |  | 37 | 420 | 0.010519 | 2.5e-05 | N
26-03-19 | 20:00 | ZN7900:PA23 | URBAN | Planned |  | 8 | 600 | 0.003249 | 5e-06 | N
26-03-19 | 21:00 | ZN901:PA9 | URBAN | Planned |  | 30 | 480 | 0.009747 | 2e-05 | N
27-03-19 | 07:30 | ZN35370:PA10 | SHORT RURAL | Planned |  | 23 | 510 | 0.049005 | 9.6e-05 | N
27-03-19 | 07:00 | ZN2568:PA39 | URBAN | Planned |  | 5 | 600 | 0.002031 | 3e-06 | N
27-03-19 | 07:00 | ZN2568:PA39 | URBAN | Planned |  | 1 | 600 | 0.000406 | 1e-06 | N
27-03-19 | 08:00 | ZN12640:PA8 | SHORT RURAL | Planned |  | 57 | 390 | 0.092872 | 0.000238 | N
27-03-19 | 07:30 | ZN3472:PA30 | URBAN | Planned |  | 27 | 510 | 0.009321 | 1.8e-05 | N
27-03-19 | 08:00 | ZN931:PA2 | URBAN | Planned |  | 151 | 480 | 0.049061 | 0.000102 | N
27-03-19 | 08:00 | ZN12620:PA8 | SHORT RURAL | Planned |  | 83 | 510 | 0.17685 | 0.000347 | N
27-03-19 | 08:00 | ZN15009:PA11 | URBAN | Planned |  | 53 | 450 | 0.016144 | 3.6e-05 | N
25-03-19 | 09:00 | ZN847:PA39 | URBAN | Planned |  | 241 | 390 | 0.063619 | 0.000163 | N
27-03-19 | 20:00 | ZN35800:PA14 | URBAN | Planned |  | 4 | 720 | 0.001949 | 3e-06 | N
27-03-19 | 22:30 | ZN116:PA12 | URBAN | Planned |  | 1 | 2,250 | 0.001523 | 1e-06 | N
28-03-19 | 07:00 | ZN180:PA21 | URBAN | Planned |  | 29 | 480 | 0.009422 | 2e-05 | N
28-03-19 | 08:00 | ZN9118:PA17 | URBAN | Planned |  | 40 | 540 | 0.014621 | 2.7e-05 | N
28-03-19 | 07:00 | ZN711:PA15 | URBAN | Planned |  | 20 | 540 | 0.007311 | 1.4e-05 | N
28-03-19 | 07:00 | ZN15014:PA19 | URBAN | Planned |  | 43 | 510 | 0.014844 | 2.9e-05 | N
28-03-19 | 08:00 | ZN10991:PA8 | URBAN | Planned |  | 58 | 540 | 0.021201 | 3.9e-05 | N
19-01-19 | 23:00 | ZN1673:PA9 | URBAN | Planned |  | 1 | 540 | 0.000366 | 1e-06 | N
28-03-19 | 07:00 | ZN2835:PA30 | URBAN | Planned |  | 29 | 510 | 0.010011 | 2e-05 | N
28-03-19 | 08:30 | ZN3155:PA44 | URBAN | Planned |  | 36 | 210 | 0.005117 | 2.4e-05 | N
28-03-19 | 08:00 | ZN12570:PA33 | SHORT RURAL | Planned |  | 8 | 450 | 0.01504 | 3.3e-05 | N
28-03-19 | 08:00 | ZN931:PA2 | URBAN | Planned |  | 168 | 480 | 0.054586 | 0.000114 | N
28-03-19 | 08:00 | ZN12570:PA24 | SHORT RURAL | Planned |  | 78 | 480 | 0.15642 | 0.000326 | N
28-03-19 | 08:00 | ZN14891:PA12 | SHORT RURAL | Planned |  | 10 | 480 | 0.020054 | 4.2e-05 | N
28-03-19 | 19:00 | ZN2635:PA57 | URBAN | Planned |  | 33 | 660 | 0.014743 | 2.2e-05 | N
28-03-19 | 20:00 | ZN35555:PA16 | URBAN | Planned |  | 57 | 600 | 0.02315 | 3.9e-05 | N
28-03-19 | 21:30 | ZN180:PA32 | URBAN | Planned |  | 50 | 390 | 0.0132 | 3.4e-05 | N
28-03-19 | 21:30 | ZN180:PA9 | URBAN | Planned |  | 40 | 390 | 0.01056 | 2.7e-05 | N
29-03-19 | 08:00 | ZN12650:PA1 | SHORT RURAL | Planned |  | 44 | 480 | 0.088229 | 0.000184 | N
29-03-19 | 08:00 | ZN12570:PA37 | SHORT RURAL | Planned |  | 99 | 480 | 0.19852 | 0.000414 | N
29-03-19 | 16:30 | ZN35900:PA3 | URBAN | Planned |  | 1 | 80 | 5.4e-05 | 1e-06 | N
30-03-19 | 06:00 | ZN262:PA17 | URBAN | Planned |  | 1 | 540 | 0.000366 | 1e-06 | N
30-03-19 | 08:00 | ZN14891:PA21 | SHORT RURAL | Planned |  | 1 | 480 | 0.002005 | 4e-06 | N
31-03-19 | 06:00 | ZN8700:PA67 68G | URBAN | Planned |  | 5 | 720 | 0.002437 | 3e-06 | N
20-01-19 | 07:30 | ZN35555:PA14 | URBAN | Planned |  | 65 | 600 | 0.026457 | 4.4e-05 | N
22-01-19 | 06:00 | ZN262:PA26 | URBAN | Planned |  | 1 | 840 | 0.00057 | 1e-06 | N
22-01-19 | 08:00 | ZN36100:PA27 | URBAN | Planned |  | 115 | 480 | 0.037447 | 7.8e-05 | N
22-01-19 | 12:00 | ZN12630:PA3 | SHORT RURAL | Planned |  | 56 | 180 | 0.042395 | 0.000236 | N
23-01-19 | 07:30 | ZN2196:PA5 | URBAN | Planned |  | 2 | 1,860 | 0.00252 | 1e-06 | N
23-01-19 | 08:00 | ZN36100:PA27 | URBAN | Planned |  | 115 | 480 | 0.037387 | 7.8e-05 | N
23-01-19 | 08:00 | ZN12690:PA24 | SHORT RURAL | Planned |  | 31 | 480 | 0.062584 | 0.00013 | N
23-01-19 | 08:00 | ZN12640:PA8 | SHORT RURAL | Planned |  | 57 | 420 | 0.10069 | 0.00024 | N
23-01-19 | 13:00 | ZN12630:PA1 | SHORT RURAL | Planned |  | 4 | 180 | 0.003028 | 1.7e-05 | N
24-01-19 | 07:30 | ZN3472:PA30 | URBAN | Planned |  | 27 | 510 | 0.009327 | 1.8e-05 | N
24-01-19 | 07:00 | ZN1788:PA30 | URBAN | Planned |  | 75 | 480 | 0.024383 | 5.1e-05 | N
24-01-19 | 07:30 | ZN262:PA31 | URBAN | Planned |  | 77 | 450 | 0.023469 | 5.2e-05 | N
24-01-19 | 08:00 | ZN14892:PA17 | URBAN | Planned |  | 2 | 480 | 0.00065 | 1e-06 | N
24-01-19 | 08:00 | ZN35400:PA101 | URBAN | Planned |  | 92 | 420 | 0.026172 | 6.2e-05 | N
24-01-19 | 20:00 | ZN263:PA35 37DEF | CBD | Planned |  | 29 | 360 | 0.34124 | 0.000948 | N
26-01-19 | 22:00 | ZN2568:PA38 | URBAN | Planned |  | 55 | 540 | 0.020115 | 3.7e-05 | N
27-01-19 | 12:30 | ZN847:PA44 | URBAN | Planned |  | 41 | 480 | 0.013329 | 2.8e-05 | N
29-01-19 | 07:00 | ZN2835:PA10 | URBAN | Planned |  | 40 | 540 | 0.01464 | 2.7e-05 | N
29-01-19 | 07:00 | ZN9534:PA18 | SHORT RURAL | Planned |  | 2 | 540 | 0.004518 | 8e-06 | N
29-01-19 | 08:00 | ZN129:PA38 | URBAN | Planned |  | 33 | 480 | 0.010736 | 2.2e-05 | N
29-01-19 | 07:30 | ZN3472:PA30 | URBAN | Planned |  | 22 | 510 | 0.007605 | 1.5e-05 | N
29-01-19 | 08:00 | ZN12600:PA13 | SHORT RURAL | Planned |  | 2 | 480 | 0.004016 | 8e-06 | N
29-01-19 | 08:30 | ZN3155:PA44 | URBAN | Planned |  | 9 | 420 | 0.002562 | 6e-06 | N
30-01-19 | 07:30 | ZN3472:PA30 | URBAN | Planned |  | 27 | 510 | 0.009333 | 1.8e-05 | N
30-01-19 | 07:00 | ZN1788:PA44 | URBAN | Planned |  | 54 | 480 | 0.017568 | 3.7e-05 | N
30-01-19 | 19:30 | ZN15005:PA2 | URBAN | Planned |  | 29 | 450 | 0.008845 | 2e-05 | N
31-01-19 | 07:30 | ZN901:PA20 | URBAN | Planned |  | 44 | 480 | 0.014315 | 3e-05 | N
31-01-19 | 07:00 | ZN1788:PA44 | URBAN | Planned |  | 77 | 480 | 0.025051 | 5.2e-05 | N
31-01-19 | 07:00 | ZN901:PA19 | URBAN | Planned |  | 142 | 480 | 0.046198 | 9.6e-05 | N
31-01-19 | 08:00 | ZN9245:PA13 | URBAN | Planned |  | 27 | 540 | 0.009882 | 1.8e-05 | N
31-01-19 | 08:00 | ZN12690:PA12 | SHORT RURAL | Planned |  | 5 | 480 | 0.010042 | 2.1e-05 | N
31-01-19 | 08:00 | ZN180:PA7 | URBAN | Planned |  | 52 | 480 | 0.016918 | 3.5e-05 | N
31-01-19 | 08:00 | ZN13000:PA11 | SHORT RURAL | Planned |  | 1 | 540 | 0.002259 | 4e-06 | N
31-01-19 | 09:00 | ZN35800:PA10 | URBAN | Planned |  | 20 | 420 | 0.005693 | 1.4e-05 | N
25-08-18 | 13:11 | ZN1068:PA15 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 4 | 93 | 0.000245 | 3e-06 | N
25-08-18 | 13:11 | ZN1068:PA16 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 679 | 93 | 0.041671 | 0.000448 | N
25-08-18 | 13:11 | ZN1068:PA17 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 896 | 93 | 0.054988 | 0.000591 | N
25-08-18 | 13:11 | ZN1068:PA18 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 544 | 93 | 0.033386 | 0.000359 | N
25-08-18 | 13:11 | ZN1068:PA22 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 169 | 94 | 0.010483 | 0.000112 | N
25-08-18 | 13:11 | ZN167:PA1 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 173 | 88 | 0.010046 | 0.000114 | N
25-08-18 | 13:11 | ZN167:PA10 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,041 | 88 | 0.060452 | 0.000687 | N
25-08-18 | 13:11 | ZN167:PA11 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 137 | 88 | 0.007956 | 9e-05 | N
25-08-18 | 13:11 | ZN167:PA12 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 142 | 89 | 0.00834 | 9.4e-05 | N
25-08-18 | 13:11 | ZN167:PA17 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 5 | 89 | 0.000294 | 3e-06 | N
25-08-18 | 13:11 | ZN167:PA19 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 75 | 89 | 0.004405 | 4.9e-05 | N
25-08-18 | 13:11 | ZN167:PA2 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 120 | 88 | 0.006969 | 7.9e-05 | N
25-08-18 | 13:11 | ZN167:PA20 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 388 | 89 | 0.022788 | 0.000256 | N
25-08-18 | 13:11 | ZN167:PA21 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 981 | 89 | 0.057615 | 0.000647 | N
25-08-18 | 13:11 | ZN167:PA4 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 247 | 88 | 0.014344 | 0.000163 | N
25-08-18 | 13:11 | ZN167:PA7 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 38 | 88 | 0.017521 | 0.000199 | N
25-08-18 | 13:11 | ZN167:PA8 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 13 | 88 | 0.000755 | 9e-06 | N
25-08-18 | 13:11 | ZN72:PA10 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 238 | 99 | 0.015549 | 0.000157 | N
25-08-18 | 13:11 | ZN72:PA15 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,261 | 99 | 0.082381 | 0.000832 | N
25-08-18 | 13:11 | ZN72:PA22 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 67 | 96 | 0.004244 | 4.4e-05 | N
25-08-18 | 13:11 | ZN72:PA24 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 770 | 98 | 0.049796 | 0.000508 | N
25-08-18 | 13:11 | ZN72:PA25 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 490 | 96 | 0.031042 | 0.000323 | N
25-08-18 | 13:11 | ZN874:PA10 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 212 | 91 | 0.10108 | 0.001111 | N
25-08-18 | 13:11 | ZN874:PA11 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 126 | 91 | 0.007566 | 8.3e-05 | N
25-08-18 | 13:11 | ZN874:PA12 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 96 | 91 | 0.005765 | 6.3e-05 | N
25-08-18 | 13:11 | ZN874:PA15 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 535 | 91 | 0.032127 | 0.000353 | N
25-08-18 | 13:11 | ZN874:PA16 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 507 | 91 | 0.030446 | 0.000335 | N
25-08-18 | 13:11 | ZN874:PA17 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 915 | 93 | 0.056154 | 0.000604 | N
25-08-18 | 13:11 | ZN874:PA18 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,862 | 93 | 0.11427 | 0.001229 | N
25-08-18 | 13:11 | ZN874:PA22 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,511 | 93 | 0.092731 | 0.000997 | N
25-08-18 | 13:11 | ZN874:PA24 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 39 | 93 | 0.002393 | 2.6e-05 | N
25-08-18 | 13:11 | ZN874:PA25 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 320 | 93 | 0.15593 | 0.001677 | N
25-08-18 | 13:11 | ZN874:PA26 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 636 | 93 | 0.039032 | 0.00042 | N
25-08-18 | 13:11 | ZN874:PA9 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 370 | 91 | 0.022219 | 0.000244 | N
25-08-18 | 13:11 | 233:82812 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 756 | 57 | 0.22579 | 0.003961 | N
25-08-18 | 13:11 | 233:82813 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 351 | 57 | 0.10483 | 0.001839 | N
25-08-18 | 13:11 | 233:82815 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 1,333 | 57 | 0.39811 | 0.006984 | N
25-08-18 | 13:11 | 233:82819 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 995 | 57 | 0.29716 | 0.005213 | N
25-08-18 | 13:11 | 233:82821 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 266 | 57 | 0.079443 | 0.001394 | N
25-08-18 | 13:11 | ZN2835:PA19 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1 | 58 | 3.8e-05 | 1e-06 | N
25-08-18 | 13:11 | ZN35555:PA13 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 2,785 | 57 | 0.10476 | 0.001838 | N
25-08-18 | 13:11 | ZN35555:PA14 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 242 | 58 | 0.009262 | 0.00016 | N
25-08-18 | 13:11 | ZN35555:PA16 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,574 | 58 | 0.060244 | 0.001039 | N
25-08-18 | 13:11 | ZN35555:PA17 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,072 | 55 | 0.038908 | 0.000707 | N
25-08-18 | 13:11 | ZN35555:PA2 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,353 | 53 | 0.047321 | 0.000893 | N
25-08-18 | 13:11 | ZN35555:PA20 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,663 | 53 | 0.058163 | 0.001097 | N
25-08-18 | 13:11 | ZN35555:PA6 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 932 | 54 | 0.033211 | 0.000615 | N
25-08-18 | 13:11 | ZN35555:PA8 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 458 | 56 | 0.016925 | 0.000302 | N
25-08-18 | 13:11 | ZN35555:PA9 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1,711 | 57 | 0.064358 | 0.001129 | N
25-08-18 | 13:11 | ZN3922:PA17 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 1 | 58 | 0.000304 | 5e-06 | N
25-08-18 | 13:11 | ZN398:PA16 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1 | 58 | 3.8e-05 | 1e-06 | N
25-08-18 | 13:11 | ZN36200:PA4 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 931 | 49 | 0.23903 | 0.004878 | N
25-08-18 | 13:11 | ZN36200:PA8 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 1,375 | 49 | 0.35302 | 0.007204 | N
25-08-18 | 13:11 | ZN2635:PA47 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 3 | 369 | 0.000731 | 2e-06 | N
25-08-18 | 13:11 | TS9200:732 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1 | 80 | 5.3e-05 | 1e-06 | N
25-08-18 | 13:11 | TS9200:749 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 2 | 79 | 0.000104 | 1e-06 | N
25-08-18 | 13:11 | ZN2466:PA21 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 1 | 177 | 0.000117 | 1e-06 | N
17-10-18 | 22:09 | ZN10994:PA12 | URBAN | 4 - STPIS Exclusion (3.3)(a) |  | 1 | 140 | 9.5e-05 | 1e-06 | N
13-12-18 | 23:38 | 813:89063 | SHORT RURAL | 4 - STPIS Exclusion (3.3)(a) |  | 1 | 331 | 0.001393 | 4e-06 | N
12-01-19 | 09:40 | 414:LD2 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 2 | 47 | 6.4e-05 | 1e-06 | N
21-01-19 | 14:20 | ZN2602:PA36 | URBAN | 4 - STPIS Exclusion (3.3)(a) |  | 5 | 139 | 0.000471 | 3e-06 | N
23-01-19 | 11:00 | ZN195:PA29 | URBAN | 4 - STPIS Exclusion (3.3)(a) |  | 35 | 70 | 0.001649 | 2.4e-05 | N
17-02-19 | 05:30 | ZN35500:PA28 | URBAN | 4 - STPIS Exclusion (3.3)(a) |  | 1 | 139 | 9.4e-05 | 1e-06 | N
17-02-19 | 21:38 | ZN2466:PA7 | URBAN | 4 - STPIS Exclusion (3.3)(a) |  | 1 | 172 | 0.000117 | 1e-06 | N
28-03-19 | 08:29 | ZN15001:PA13 | URBAN | 4 - STPIS Exclusion (3.3)(a) |  | 13 | 175 | 0.001544 | 9e-06 | N
28-03-19 | 08:29 | ZN15001:PA2 | URBAN | 4 - STPIS Exclusion (3.3)(a) |  | 6 | 1,590 | 0.006458 | 4e-06 | N
29-05-19 | 10:38 | ZN2400:PA18 | SHORT RURAL | 4 - STPIS Exclusion (3.3)(a) |  | 1 | 188 | 0.000783 | 4e-06 | N
02-06-19 | 03:20 | 814:82291 | SHORT RURAL | 4 - STPIS Exclusion (3.3)(a) |  | 1 | 1,023 | 0.00426 | 4e-06 | N
26-06-19 | 03:38 | 513:48056 | SHORT RURAL | 4 - STPIS Exclusion (3.3)(a) |  | 1 | 73 | 0.000303 | 4e-06 | N
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## Amendments
This sheet may be used to identify amendments made to data resubmitted to the AER.
NSP data amendments
Worksheet | Table | Comments
Contents
Instructions