## Cover
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | CitiPower Pty
DNSP - Australian business number: |  | ACN 064 651 056
Reporting year: |  | 2013
Business address | Address |  | 40 Market Street
| Suburb |  | Melbourne
|  | State | VIC | Postcode | 3000
Postal address | Address |  | Locked Bag 14090
| Suburb |  | Melbourne
|  | State | VIC | Postcode | 8001
Contact name/s | Hannah Williams
Contact phone/s | 9683 4088
Contact email address/s | hwilliams@powercor.com.au

## Contents
Electricity Distribution Network Service Provider Annual Reporting Template
Table of contents
Cover Sheet
1. Service Target Performance Incentive Scheme |  | 2. Demand |  | 6. Outages
3. Asset Installation
4. Customer Service
5. General Information
Cover sheet
1a. STPIS - Reliability
1b. STPIS - Customer Service
1d. STPIS - MED Threshold
1c. STPIS - Daily Performance
6a. Planned Outages
1e. STPIS - Exclusions
2. Demand
6b. Annual Feeder Reliability
6c. Cause of Outages
3. Asset Installation
4. Customer Services
5. General Information

## 1a. STPIS Reliability
CitiPower Pty
STPIS Data Reporting
2013
Reliability
Table 1: SAIDI (System Average Interruption Duration Index)
Network categorisation
Unplanned SAIDI 1 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | 8.0091 | 103.1128 | 0 | 0 | 86.0572
Total (after removing excluded events and MED) | 8.0091 | 31.0572 | 0 | 0 | 26.9238
Table 2: SAIFI (System Average Interruption Frequency Index)
Network categorisation
Unplanned SAIFI 2 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | 0.17407 | 0.82114 | 0 | 0 | 0.70509
Total (after removing excluded events and MED) | 0.17407 | 0.4427 | 0 | 0 | 0.39453
Table 3: MAIFI (Momentary Average Interruption Frequency Index)
Network categorisation
MAIFI 3 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | 0.025044 | 0.13438 | 0 | 0 | 0.11477
Total (after removing excluded events and MED) | 0.025044 | 0.12728 | 0 | 0 | 0.10895
Table 4: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI | 8.7969 | 19.0692 | 0 | 0 | 17.227
SAIFI | 0.040974 | 0.061996 | 0 | 0 | 0.058226
Table 5: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers at the start of period | 56922 | 261135 | 0 | 0 | 318057
Customer numbers at the end of period | 57718 | 263849 | 0 | 0 | 321567
Average distribution customer numbers | 57320 | 262492 | 0 | 0 | 319812
Note - the AER's Electricity distribution network service providers, Service target performance incentive scheme, November 2009, p. 22, defines SAIDI and SAIFI as follows;
1) Unplanned SAIDI - The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less).
2) Unplanned SAIFI - The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
The AER will apply the ESCV's definition of MAIFI for transitional reasons. The ESCV's Information specification (Service performance) for Victorian Electricity Distributors, 1 January 2009, p. 30, defines MAIFI as follows:
3) MAIFI - The total number of momentary interruptions divided by the total number of distribution customers (where the distribution customers are network or per feeder based, as appropriate).
4) Total includes the impact of excluded events and MED.
Contents
Contents

## 1b. STPIS Customer Service
CitiPower Pty
STPIS Data Reporting - AER Definitions
2013
Customer service
Table 1: Telephone answering
Telephone answering | Total | Total after removing MED
Number of calls received | 53696 | 49087
Number of calls answered within 30 seconds | 39862 | 38293
Percentage of calls answered within 30 seconds | 74.24% | 78.01%
Note:
Telephone answering has the same meaning as defined in the Electricity DNSPs' STPIS, November 2009.
Table 2: New connections
Note: This is for newly energised properties only
New connections | Total
Number of new connections | 5979
Number of new connections not provided on or before the agreed date | 0
Percentage of new connections not provided on or before the agreed date | 0%
Table 3: Streetlight repair
Note:
Streetlight repair has the same meaning as defined in the Electricity DNSPs' STPIS, November 2009
Streetlight repair | Total
Total number of streetlights | 52164
Total number of streetlight faults | 3093
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business | 635
Faulty streetlights not repaired within 5 business days of fault report or agreed date | 7
Percentage of faulty streetlights not repaired within 5 business days of fault report or agreed date | 0.2263%
Table 4 Guaranteed service levels - jurisdictional GSL scheme
Appointments
Customer arranged appointments Central - number |  |  | 18852
Appointments not met within 15 minutes of agreed time - number |  |  | 3213
Appointments - GSL payments - number |  |  | 0
Appointments - GSL payments - ($) |  |  | 0
Connections
Connections made |  |  | 45034
Connections not made on agreed date |  |  | 52
Connections - GSL payments - 1-4 day delay - number |  |  | 41
Connections - GSL payments - 1-4 day delay - ($) |  |  | 6700
Connections - GSL payments - 5+ day delay - number |  |  | 9
Connections - GSL payments - 5+ day delay - ($) |  |  | 4500
Reliability of supply
Low reliability payments - 20 hours - number |  |  | 84
Low reliability payments - 20 hours - ($) |  |  | 8400
Low reliability payments - 30 hours - number |  |  | 30
Low reliability payments - 30 hours - ($) |  |  | 4500
Low reliability payments - 60 hours - number |  |  | 0
Low reliability payments - 60 hours - ($) |  |  | 0
Low reliability payments - 10 events - number |  |  | 0
Low reliability payments - 10 events - ($) |  |  | 0
Low reliability payments - 15 events - number |  |  | 0
Low reliability payments - 15 events - ($) |  |  | 0
Low reliability payments - 30 events - number |  |  | 0
Low reliability payments - 30 events - ($) |  |  | 0
Low reliability payments - 24 momentary events - number |  |  | 0
Low reliability payments - 24 momentary events - ($) |  |  | 0
Low reliability payments - 36 momentary events - number |  |  | 0
Low reliability payments - 36 momentary events - ($) |  |  | 0
Street lights
Street lights |  |  | 52164
Street lights "out" during period |  |  | 3093
Street lights not repaired by "fix by" date |  |  | 8
Street lights not repaired in 2 business days |  |  | 11
Street lights – number of business days to repair |  |  | 2.24
Street lights - GSL payments - number |  |  | 11
Street lights - GSL payments - ($) |  |  | 440
Planned interruptions
Planned interruptions - 4 business days notice not given |  |  | 70
Total GSL payments made ($) |  |  | 24540
Contents

## 1c. STPIS Daily Performance
CitiPower Pty
STPIS Data Reporting
2013
Daily Performance Data
Instruction This regulatory template requires the input of historical daily performance recorded for the calculation of the parameters under the STPIS, such as MED day boundary and performance targets. STPIS definitions apply to SAIDI and Calls not answered within 30 seconds. Please note: The AER's definition of calls answered within 30 seconds is as follows: Calls to the fault line answered in 30 seconds where the time to answer a call is measured from when the call enters the telephone system of the call centre (including that time when it may be ringing unanswered by any response) and the caller speaks with a human operator, but excluding the time that the caller is connected to an automated interactive service that provides substantive information. This measure does not apply to: - calls to payment lines and automated interactive services; - calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator. Where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned. Note: Being placed in a queuing system (automated or otherwise) does not constitute a response. 'Calls answered within 30 seconds' and 'Calls received' should be calculated excluding calls abandoned within 30 seconds of being queued for a human operator; and calls to payment lines and automated interactive services. Exclusions refer to the exclusions listed in Section 3.3(a) of the STPIS.
Table 1 Daily Performance Data (unplanned)
Customer service
Date | CBD SAIDI All events | CBD SAIDI (after removing excluded events) | Urban SAIDI All events | Urban SAIDI (after removing excluded events) | Long Rural SAIDI All events | Long Rural SAIDI (after removing excluded events) | Short Rural SAIDI All events | Short Rural SAIDI (after removing excluded events) | Network SAIDI All events | Network SAIDI (after removing excluded events) | CBD SAIFI All events | CBD SAIFI (after removing excluded events) | Urban SAIFI All events | Urban SAIFI (after removing excluded events) | Long Rural SAIFI All events | Long Rural SAIFI (after removing excluded events) | Short Rural SAIFI All events | Short Rural SAIFI (after removing excluded events) | Network SAIFI All events | Network SAIFI (after removing excluded events) | CBD MAIFI All events | CBD MAIFI (after removing excluded events) | Urban MAIFI All events | Urban MAIFI (after removing excluded events) | Long Rural MAIFI All events | Long Rural MAIFI (after removing excluded events) | Short Rural MAIFI All events | Short Rural MAIFI (after removing excluded events) | Network MAIFI All events | Network MAIFI (after removing excluded events) | Number of calls received | Calls not answered in 30 seconds | MED | Comments / basis for exclusion - refer to category of exclusion under 3.3(a) of STPIS
1/01/2013 | 0 | 0 | 0.00024756 | 0.00024756 | 0 | 0 | 0 | 0 | 0.00020316 | 0.00020316 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1 | NO
2/01/2013 | 0 | 0 | 0.0025517 | 0.0025517 | 0 | 0 | 0 | 0 | 0.0020941 | 0.0020941 | 0 | 0 | 2.666e-05 | 2.666e-05 | 0 | 0 | 0 | 0 | 2.1879e-05 | 2.1879e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 25 | NO
3/01/2013 | 0 | 0 | 0.019275 | 0.019275 | 0 | 0 | 0 | 0 | 0.015818 | 0.015818 | 0 | 0 | 0.00012949 | 0.00012949 | 0 | 0 | 0 | 0 | 0.00010627 | 0.00010627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 21 | NO
4/01/2013 | 0.0026491 | 0.0026491 | 0.8554 | 0.8554 | 0 | 0 | 0 | 0 | 0.70247 | 0.70247 | 1.7428e-05 | 1.7428e-05 | 0.013802 | 0.013802 | 0 | 0 | 0 | 0 | 0.01133 | 0.01133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 265 | NO
5/01/2013 | 0 | 0 | 0.0017519 | 0.0017519 | 0 | 0 | 0 | 0 | 0.0014377 | 0.0014377 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | NO
6/01/2013 | 0 | 0 | 0.00068173 | 0.00068173 | 0 | 0 | 0 | 0 | 0.00055947 | 0.00055947 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 2 | NO
7/01/2013 | 0 | 0 | 0.024946 | 0.024946 | 0 | 0 | 0 | 0 | 0.020472 | 0.020472 | 0 | 0 | 0.00029326 | 0.00029326 | 0 | 0 | 0 | 0 | 0.00024067 | 0.00024067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 25 | NO
8/01/2013 | 0.0022657 | 0.0022657 | 0.001531 | 0.001531 | 0 | 0 | 0 | 0 | 0.0016628 | 0.0016628 | 1.7428e-05 | 1.7428e-05 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 41 | NO
9/01/2013 | 0 | 0 | 0.015128 | 0.015128 | 0 | 0 | 0 | 0 | 0.012415 | 0.012415 | 0 | 0 | 0.00012187 | 0.00012187 | 0 | 0 | 0 | 0 | 0.00010002 | 0.00010002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 34 | NO
10/01/2013 | 0 | 0 | 0.0015691 | 0.0015691 | 0 | 0 | 0 | 0 | 0.0012877 | 0.0012877 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 11 | NO
11/01/2013 | 0 | 0 | 0.20108 | 0.20108 | 0 | 0 | 0 | 0 | 0.16502 | 0.16502 | 0 | 0 | 0.0030697 | 0.0030697 | 0 | 0 | 0 | 0 | 0.0025192 | 0.0025192 | 0 | 0 | 0.0099898 | 0.0099898 | 0 | 0 | 0 | 0 | 0.0081983 | 0.0081983 | 229 | 72 | NO
12/01/2013 | 0 | 0 | 0.13554 | 0.13554 | 0 | 0 | 0 | 0 | 0.11123 | 0.11123 | 0 | 0 | 0.00047226 | 0.00047226 | 0 | 0 | 0 | 0 | 0.00038757 | 0.00038757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | NO
13/01/2013 | 0 | 0 | 0.00077314 | 0.00077314 | 0 | 0 | 0 | 0 | 0.00063448 | 0.00063448 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 6 | NO
14/01/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 22 | NO
15/01/2013 | 0 | 0 | 0.0019347 | 0.0019347 | 0 | 0 | 0 | 0 | 0.0015878 | 0.0015878 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 8 | NO
16/01/2013 | 0.0094113 | 0.0094113 | 0.0017938 | 0.0017938 | 0 | 0 | 0 | 0 | 0.0031599 | 0.0031599 | 3.4857e-05 | 3.4857e-05 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 13 | NO
17/01/2013 | 0.029802 | 0.029802 | 0.071308 | 0.071308 | 0 | 0 | 0 | 0 | 0.063864 | 0.063864 | 0.00013943 | 0.00013943 | 0.00023613 | 0.00023613 | 0 | 0 | 0 | 0 | 0.00021879 | 0.00021879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 82 | NO
18/01/2013 | 0 | 0 | 0.0032715 | 0.0032715 | 0 | 0 | 0 | 0 | 0.0026848 | 0.0026848 | 0 | 0 | 2.2851e-05 | 2.2851e-05 | 0 | 0 | 0 | 0 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 25 | NO
19/01/2013 | 0.00064485 | 0.00064485 | 0.00043798 | 0.00043798 | 0 | 0 | 0 | 0 | 0.00047508 | 0.00047508 | 1.7428e-05 | 1.7428e-05 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 8 | NO
20/01/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1 | NO
21/01/2013 | 0.0021611 | 0.0021611 | 0.00091024 | 0.00091024 | 0 | 0 | 0 | 0 | 0.0011346 | 0.0011346 | 1.7428e-05 | 1.7428e-05 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 23 | NO
22/01/2013 | 0 | 0 | 0.0010283 | 0.0010283 | 0 | 0 | 0 | 0 | 0.0008439 | 0.0008439 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 9 | NO
23/01/2013 | 0 | 0 | 0.51449 | 0.51449 | 0 | 0 | 0 | 0 | 0.42222 | 0.42222 | 0 | 0 | 0.0050844 | 0.0050844 | 0 | 0 | 0 | 0 | 0.0041726 | 0.0041726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 30 | NO
24/01/2013 | 0 | 0 | 0.010969 | 0.010969 | 0 | 0 | 0 | 0 | 0.0090015 | 0.0090015 | 0 | 0 | 6.4745e-05 | 6.4745e-05 | 0 | 0 | 0 | 0 | 5.3134e-05 | 5.3134e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 38 | NO
25/01/2013 | 0 | 0 | 0.0016301 | 0.0016301 | 0 | 0 | 0 | 0 | 0.0013377 | 0.0013377 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0.0024337 | 0.0024337 | 0 | 0 | 0 | 0 | 0.0019972 | 0.0019972 | 175 | 48 | NO
26/01/2013 | 0 | 0 | 0.00030468 | 0.00030468 | 0 | 0 | 0 | 0 | 0.00025004 | 0.00025004 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 11 | NO
27/01/2013 | 0 | 0 | 0.0030735 | 0.0030735 | 0 | 0 | 0 | 0 | 0.0025223 | 0.0025223 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 142 | NO
28/01/2013 | 0.00076684 | 0.00076684 | 0.0089425 | 0.0089425 | 0 | 0 | 0 | 0 | 0.0074763 | 0.0074763 | 1.7428e-05 | 1.7428e-05 | 7.998e-05 | 7.998e-05 | 0 | 0 | 0 | 0 | 6.8762e-05 | 6.8762e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 4 | NO
29/01/2013 | 0 | 0 | 0.27526 | 0.27526 | 0 | 0 | 0 | 0 | 0.22589 | 0.22589 | 0 | 0 | 0.014773 | 0.014773 | 0 | 0 | 0 | 0 | 0.012124 | 0.012124 | 0 | 0 | 0.0063527 | 0.0063527 | 0 | 0 | 0 | 0 | 0.0052134 | 0.0052134 | 285 | 75 | NO
30/01/2013 | 0 | 0 | 0.0018433 | 0.0018433 | 0 | 0 | 0 | 0 | 0.0015128 | 0.0015128 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 72 | NO
31/01/2013 | 0 | 0 | 0.059916 | 0.059916 | 0 | 0 | 0 | 0 | 0.049171 | 0.049171 | 0 | 0 | 0.00030088 | 0.00030088 | 0 | 0 | 0 | 0 | 0.00024692 | 0.00024692 | 0 | 0 | 0.0017672 | 0.0017672 | 0 | 0 | 0 | 0 | 0.0014502 | 0.0014502 | 293 | 112 | NO
1/02/2013 | 0 | 0 | 0.18805 | 0.18805 | 0 | 0 | 0 | 0 | 0.15433 | 0.15433 | 0 | 0 | 0.00075409 | 0.00075409 | 0 | 0 | 0 | 0 | 0.00061886 | 0.00061886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 55 | NO
2/02/2013 | 0 | 0 | 0.0025403 | 0.0025403 | 0 | 0 | 0 | 0 | 0.0020847 | 0.0020847 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 7 | NO
3/02/2013 | 0 | 0 | 0.023362 | 0.023362 | 0 | 0 | 0 | 0 | 0.019172 | 0.019172 | 0 | 0 | 0.00022851 | 0.00022851 | 0 | 0 | 0 | 0 | 0.00018753 | 0.00018753 | 0 | 0 | 0.0084321 | 0.0084321 | 0 | 0 | 0 | 0 | 0.0069199 | 0.0069199 | 62 | 4 | NO
4/02/2013 | 0 | 0 | 0.051415 | 0.051415 | 0 | 0 | 0 | 0 | 0.042195 | 0.042195 | 0 | 0 | 0.00012568 | 0.00012568 | 0 | 0 | 0 | 0 | 0.00010314 | 0.00010314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 17 | NO
5/02/2013 | 0 | 0 | 0.00029707 | 0.00029707 | 0 | 0 | 0 | 0 | 0.00024379 | 0.00024379 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 36 | NO
6/02/2013 | 0 | 0 | 0.33523 | 0.33523 | 0 | 0 | 0 | 0 | 0.27511 | 0.27511 | 0 | 0 | 0.0066954 | 0.0066954 | 0 | 0 | 0 | 0 | 0.0054947 | 0.0054947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 55 | NO
7/02/2013 | 0 | 0 | 0.081012 | 0.081012 | 0 | 0 | 0 | 0 | 0.066483 | 0.066483 | 0 | 0 | 0.00046464 | 0.00046464 | 0 | 0 | 0 | 0 | 0.00038132 | 0.00038132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 28 | NO
8/02/2013 | 0 | 0 | 0.0045322 | 0.0045322 | 0 | 0 | 0 | 0 | 0.0037194 | 0.0037194 | 0 | 0 | 7.6171e-05 | 7.6171e-05 | 0 | 0 | 0 | 0 | 6.2511e-05 | 6.2511e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 12 | NO
9/02/2013 | 0 | 0 | 0.0099632 | 0.0099632 | 0 | 0 | 0 | 0 | 0.0081764 | 0.0081764 | 0 | 0 | 3.0468e-05 | 3.0468e-05 | 0 | 0 | 0 | 0 | 2.5004e-05 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 2 | NO
10/02/2013 | 0 | 0 | 0.025209 | 0.025209 | 0 | 0 | 0 | 0 | 0.020688 | 0.020688 | 0 | 0 | 0.00014853 | 0.00014853 | 0 | 0 | 0 | 0 | 0.0001219 | 0.0001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 2 | NO
11/02/2013 | 0.00062742 | 0.00062742 | 0.51515 | 0.51515 | 0 | 0 | 0 | 0 | 0.42288 | 0.42288 | 1.7428e-05 | 1.7428e-05 | 0.0086759 | 0.0086759 | 0 | 0 | 0 | 0 | 0.0071231 | 0.0071231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 31 | NO
12/02/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 14 | NO
13/02/2013 | 0.0027362 | 0.0027362 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00049071 | 0.00049071 | 1.7428e-05 | 1.7428e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 33 | NO
14/02/2013 | 0 | 0 | 0.0039647 | 0.0039647 | 0 | 0 | 0 | 0 | 0.0032537 | 0.0032537 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0.0029897 | 0.0029897 | 0 | 0 | 0 | 0 | 0.0024535 | 0.0024535 | 179 | 53 | NO
15/02/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 117 | NO
16/02/2013 | 0.0010631 | 0.0010631 | 0.01715 | 0.01715 | 0 | 0 | 0 | 0 | 0.014265 | 0.014265 | 1.7428e-05 | 1.7428e-05 | 0.00037324 | 0.00037324 | 0 | 0 | 0 | 0 | 0.00030943 | 0.00030943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 37 | NO
17/02/2013 | 0.010283 | 0.010283 | 0.0043037 | 0.0043037 | 0 | 0 | 0 | 0 | 0.0053759 | 0.0053759 | 0.00017428 | 0.00017428 | 2.2851e-05 | 2.2851e-05 | 0 | 0 | 0 | 0 | 5.0009e-05 | 5.0009e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 13 | NO
18/02/2013 | 0.69623 | 0.69623 | 0.93706 | 0.93706 | 0 | 0 | 0 | 0 | 0.89387 | 0.89387 | 0.0096553 | 0.0096553 | 0.011205 | 0.011205 | 0 | 0 | 0 | 0 | 0.010927 | 0.010927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 311 | NO
19/02/2013 | 0.40808 | 0.40808 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073184 | 0.073184 | 0.0099864 | 0.0099864 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017909 | 0.0017909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 132 | NO
20/02/2013 | 0 | 0 | 0.27366 | 0.27366 | 0 | 0 | 0 | 0 | 0.22458 | 0.22458 | 0 | 0 | 0.0050882 | 0.0050882 | 0 | 0 | 0 | 0 | 0.0041757 | 0.0041757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 53 | NO
21/02/2013 | 0.071107 | 0.071107 | 0.90097 | 0.90097 | 0 | 0 | 0 | 0 | 0.75215 | 0.75215 | 0.0011328 | 0.0011328 | 0.0059947 | 0.0059947 | 0 | 0 | 0 | 0 | 0.0051228 | 0.0051228 | 0 | 0 | 0.0080551 | 0.0080551 | 0 | 0 | 0 | 0 | 0.0066105 | 0.0066105 | 365 | 137 | NO
22/02/2013 | 0 | 0 | 0.00038086 | 0.00038086 | 0 | 0 | 0 | 0 | 0.00031255 | 0.00031255 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 67 | NO
23/02/2013 | 0 | 0 | 0.00023232 | 0.00023232 | 0 | 0 | 0 | 0 | 0.00019066 | 0.00019066 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 11 | NO
24/02/2013 | 0 | 0 | 0.026416 | 0.026416 | 0 | 0 | 0 | 0 | 0.021679 | 0.021679 | 0 | 0 | 0.00012949 | 0.00012949 | 0 | 0 | 0 | 0 | 0.00010627 | 0.00010627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 11 | NO
25/02/2013 | 0 | 0 | 0.012107 | 0.012107 | 0 | 0 | 0 | 0 | 0.0099361 | 0.0099361 | 0 | 0 | 5.332e-05 | 5.332e-05 | 0 | 0 | 0 | 0 | 4.3758e-05 | 4.3758e-05 | 0 | 0 | 0.0066383 | 0.0066383 | 0 | 0 | 0 | 0 | 0.0054478 | 0.0054478 | 269 | 123 | NO
26/02/2013 | 0.095646 | 0.095646 | 0.19549 | 0.19549 | 0 | 0 | 0 | 0 | 0.17758 | 0.17758 | 0.000122 | 0.000122 | 0.00060175 | 0.00060175 | 0 | 0 | 0 | 0 | 0.00051571 | 0.00051571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 213 | NO
27/02/2013 | 0 | 0 | 0.015653 | 0.015653 | 0 | 0 | 0 | 0 | 0.012846 | 0.012846 | 0 | 0 | 0.00011807 | 0.00011807 | 0 | 0 | 0 | 0 | 9.6892e-05 | 9.6892e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 150 | NO
28/02/2013 | 0 | 0 | 0.026591 | 0.026591 | 0 | 0 | 0 | 0 | 0.021823 | 0.021823 | 0 | 0 | 0.00011426 | 0.00011426 | 0 | 0 | 0 | 0 | 9.3766e-05 | 9.3766e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 77 | NO
1/03/2013 | 0 | 0 | 0.057319 | 0.057319 | 0 | 0 | 0 | 0 | 0.047039 | 0.047039 | 0 | 0 | 0.00082646 | 0.00082646 | 0 | 0 | 0 | 0 | 0.00067824 | 0.00067824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 84 | NO
2/03/2013 | 0 | 0 | 0.58713 | 0.58713 | 0 | 0 | 0 | 0 | 0.48183 | 0.48183 | 0 | 0 | 0.012679 | 0.012679 | 0 | 0 | 0 | 0 | 0.010405 | 0.010405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 70 | NO
3/03/2013 | 0 | 0 | 0.0023842 | 0.0023842 | 0 | 0 | 0 | 0 | 0.0019566 | 0.0019566 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 23 | NO
4/03/2013 | 0 | 0 | 0.0014587 | 0.0014587 | 0 | 0 | 0 | 0 | 0.0011971 | 0.0011971 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 79 | NO
5/03/2013 | 0 | 0 | 0.097887 | 0.097887 | 0 | 0 | 0 | 0 | 0.080333 | 0.080333 | 0 | 0 | 0.00067031 | 0.00067031 | 0 | 0 | 0 | 0 | 0.00055009 | 0.00055009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 77 | NO
6/03/2013 | 0.27043 | 0.27043 | 0.069453 | 0.069453 | 0 | 0 | 0 | 0 | 0.1055 | 0.1055 | 0.0043919 | 0.0043919 | 0.00067411 | 0.00067411 | 0 | 0 | 0 | 0 | 0.0013409 | 0.0013409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 123 | NO
7/03/2013 | 0 | 0 | 0.044492 | 0.044492 | 0 | 0 | 0 | 0 | 0.036513 | 0.036513 | 0 | 0 | 0.00036562 | 0.00036562 | 0 | 0 | 0 | 0 | 0.00030005 | 0.00030005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 113 | NO
8/03/2013 | 0 | 0 | 0.15139 | 0.15139 | 0 | 0 | 0 | 0 | 0.12424 | 0.12424 | 0 | 0 | 0.0024032 | 0.0024032 | 0 | 0 | 0 | 0 | 0.0019722 | 0.0019722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 83 | NO
9/03/2013 | 0 | 0 | 0.064178 | 0.064178 | 0 | 0 | 0 | 0 | 0.052668 | 0.052668 | 0 | 0 | 0.00030849 | 0.00030849 | 0 | 0 | 0 | 0 | 0.00025317 | 0.00025317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 45 | NO
10/03/2013 | 0.98144 | 0.98144 | 0.0026469 | 0.0026469 | 0 | 0 | 0 | 0 | 0.17818 | 0.17818 | 0.027362 | 0.027362 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 0.0049196 | 0.0049196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | NO
11/03/2013 | 0.0088884 | 0.0088884 | 0.26637 | 0.26637 | 0 | 0 | 0 | 0 | 0.2202 | 0.2202 | 0.00010457 | 0.00010457 | 0.001691 | 0.001691 | 0 | 0 | 0 | 0 | 0.0014065 | 0.0014065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 181 | NO
12/03/2013 | 0.59755 | 0.59755 | 0.50187 | 0.50187 | 0 | 0 | 0 | 0 | 0.51903 | 0.51903 | 0.0096378 | 0.0096378 | 0.0027193 | 0.0027193 | 0 | 0 | 0 | 0 | 0.0039601 | 0.0039601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684 | 528 | NO
13/03/2013 | 0 | 0 | 0.132 | 0.132 | 0 | 0 | 0 | 0 | 0.10833 | 0.10833 | 0 | 0 | 0.00088739 | 0.00088739 | 0 | 0 | 0 | 0 | 0.00072825 | 0.00072825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 93 | NO
14/03/2013 | 0.0013768 | 0.0013768 | 0.042363 | 0.042363 | 0 | 0 | 0 | 0 | 0.035012 | 0.035012 | 1.7428e-05 | 1.7428e-05 | 0.00039609 | 0.00039609 | 0 | 0 | 0 | 0 | 0.00032818 | 0.00032818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 56 | NO
15/03/2013 | 0 | 0 | 0.0019347 | 0.0019347 | 0 | 0 | 0 | 0 | 0.0015878 | 0.0015878 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 36 | NO
16/03/2013 | 0 | 0 | 3.3909 | 3.3909 | 0 | 0 | 0 | 0 | 2.7828 | 2.7828 | 0 | 0 | 0.091268 | 0.091268 | 0 | 0 | 0 | 0 | 0.0749 | 0.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866 | 746 | Yes | Exceeded Unplanned SAIDI Threshold
17/03/2013 | 0 | 0 | 0.18716 | 0.18716 | 0 | 0 | 0 | 0 | 0.1536 | 0.1536 | 0 | 0 | 0.0030583 | 0.0030583 | 0 | 0 | 0 | 0 | 0.0025098 | 0.0025098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 17 | NO
18/03/2013 | 0 | 0 | 0.66678 | 0.66678 | 0 | 0 | 0 | 0 | 0.5472 | 0.5472 | 0 | 0 | 0.011391 | 0.011391 | 0 | 0 | 0 | 0 | 0.0093485 | 0.0093485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 66 | NO
19/03/2013 | 0.0033637 | 0.0033637 | 0.0013406 | 0.0013406 | 0 | 0 | 0 | 0 | 0.0017034 | 0.0017034 | 1.7428e-05 | 1.7428e-05 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 13 | NO
20/03/2013 | 0 | 0 | 0.037705 | 0.037705 | 0 | 0 | 0 | 0 | 0.030943 | 0.030943 | 0 | 0 | 0.00038086 | 0.00038086 | 0 | 0 | 0 | 0 | 0.00031255 | 0.00031255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 12 | NO
21/03/2013 | 0 | 0 | 0.65406 | 0.65406 | 0 | 0 | 0 | 0 | 0.53676 | 0.53676 | 0 | 0 | 0.016023 | 0.016023 | 0 | 0 | 0 | 0 | 0.013149 | 0.013149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 254 | NO
22/03/2013 | 0.012322 | 0.012322 | 0.017675 | 0.017675 | 0 | 0 | 0 | 0 | 0.016715 | 0.016715 | 1.7428e-05 | 1.7428e-05 | 6.8554e-05 | 6.8554e-05 | 0 | 0 | 0 | 0 | 5.9385e-05 | 5.9385e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 50 | NO
23/03/2013 | 0 | 0 | 0.054462 | 0.054462 | 0 | 0 | 0 | 0 | 0.044695 | 0.044695 | 0 | 0 | 0.00028945 | 0.00028945 | 0 | 0 | 0 | 0 | 0.00023754 | 0.00023754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 27 | NO
24/03/2013 | 0 | 0 | 0.83996 | 0.83996 | 0 | 0 | 0 | 0 | 0.68933 | 0.68933 | 0 | 0 | 0.01397 | 0.01397 | 0 | 0 | 0 | 0 | 0.011464 | 0.011464 | 0 | 0 | 0.0041932 | 0.0041932 | 0 | 0 | 0 | 0 | 0.0034412 | 0.0034412 | 175 | 59 | NO
25/03/2013 | 0.0027537 | 0 | 0.0025517 | 0.0025517 | 0 | 0 | 0 | 0 | 0.0025879 | 0.0025879 | 1.7428e-05 | 1.7428e-05 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 63 | NO
26/03/2013 | 0.023424 | 0.023424 | 0.035679 | 0.035679 | 0 | 0 | 0 | 0 | 0.033481 | 0.033481 | 0.000122 | 0.000122 | 0.00063984 | 0.00063984 | 0 | 0 | 0 | 0 | 0.00054697 | 0.00054697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 42 | NO
27/03/2013 | 0.014884 | 0.014884 | 0.1432 | 0.1432 | 0 | 0 | 0 | 0 | 0.12019 | 0.12019 | 0.000244 | 0.000244 | 0.0030164 | 0.0030164 | 0 | 0 | 0 | 0 | 0.0025192 | 0.0025192 | 0 | 0 | 0.0029745 | 0.0029745 | 0 | 0 | 0 | 0 | 0.002441 | 0.002441 | 248 | 81 | NO
28/03/2013 | 0.0031894 | 0.0031894 | 0.54572 | 0.54572 | 0 | 0 | 0 | 0 | 0.44842 | 0.44842 | 1.7428e-05 | 1.7428e-05 | 0.011536 | 0.011536 | 0 | 0 | 0 | 0 | 0.0094704 | 0.0094704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 86 | NO
29/03/2013 | 0 | 0 | 0.00081122 | 0.00081122 | 0 | 0 | 0 | 0 | 0.00066574 | 0.00066574 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 3 | NO
30/03/2013 | 0 | 0 | 0.00024375 | 0.00024375 | 0 | 0 | 0 | 0 | 0.00020003 | 0.00020003 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | NO
31/03/2013 | 0 | 0 | 0.24943 | 0.24943 | 0 | 0 | 0 | 0 | 0.2047 | 0.2047 | 0 | 0 | 0.0002247 | 0.0002247 | 0 | 0 | 0 | 0 | 0.00018441 | 0.00018441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 7 | NO
1/04/2013 | 0.37927 | 0.37927 | 0.19787 | 0.19787 | 0 | 0 | 0 | 0 | 0.23041 | 0.23041 | 0.0061173 | 0.0061173 | 0.0035343 | 0.0035343 | 0 | 0 | 0 | 0 | 0.0039976 | 0.0039976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | NO
2/04/2013 | 0 | 0 | 0.0021328 | 0.0021328 | 0 | 0 | 0 | 0 | 0.0017503 | 0.0017503 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 22 | NO
3/04/2013 | 0.0029454 | 0.0029454 | 0.021038 | 0.021038 | 0 | 0 | 0 | 0 | 0.017794 | 0.017794 | 1.7428e-05 | 1.7428e-05 | 5.7128e-05 | 5.7128e-05 | 0 | 0 | 0 | 0 | 5.0009e-05 | 5.0009e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 32 | NO
4/04/2013 | 0 | 0 | 0.011715 | 0.011715 | 0 | 0 | 0 | 0 | 0.0096142 | 0.0096142 | 0 | 0 | 4.1894e-05 | 4.1894e-05 | 0 | 0 | 0 | 0 | 3.4381e-05 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 40 | NO
5/04/2013 | 0 | 0 | 0.0019347 | 0.0019347 | 0 | 0 | 0 | 0 | 0.0015878 | 0.0015878 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 43 | NO
6/04/2013 | 0 | 0 | 0.10174 | 0.10174 | 0 | 0 | 0 | 0 | 0.083492 | 0.083492 | 0 | 0 | 0.00015234 | 0.00015234 | 0 | 0 | 0 | 0 | 0.00012502 | 0.00012502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | NO
7/04/2013 | 0 | 0 | 0.07026 | 0.07026 | 0 | 0 | 0 | 0 | 0.05766 | 0.05766 | 0 | 0 | 0.00037705 | 0.00037705 | 0 | 0 | 0 | 0 | 0.00030943 | 0.00030943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 4 | NO
8/04/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | NO
9/04/2013 | 0.33717 | 0.33717 | 0.0071982 | 0.0071982 | 0 | 0 | 0 | 0 | 0.066374 | 0.066374 | 0.007651 | 0.007651 | 8.7597e-05 | 8.7597e-05 | 0 | 0 | 0 | 0 | 0.001444 | 0.001444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 35 | NO
10/04/2013 | 0.0014117 | 0.0014117 | 0.013456 | 0.013456 | 0 | 0 | 0 | 0 | 0.011296 | 0.011296 | 1.7428e-05 | 1.7428e-05 | 5.332e-05 | 5.332e-05 | 0 | 0 | 0 | 0 | 4.6883e-05 | 4.6883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 28 | NO
11/04/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 22 | NO
12/04/2013 | 0 | 0 | 0.0013178 | 0.0013178 | 0 | 0 | 0 | 0 | 0.0010814 | 0.0010814 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 20 | NO
13/04/2013 | 0.00087141 | 0.00087141 | 0.0011311 | 0.0011311 | 0 | 0 | 0 | 0 | 0.0010846 | 0.0010846 | 1.7428e-05 | 1.7428e-05 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 3 | NO
14/04/2013 | 0.0017777 | 0.0017777 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0003188 | 0.0003188 | 1.7428e-05 | 1.7428e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1 | NO
15/04/2013 | 0.0010457 | 0.0010457 | 0.28138 | 0.28138 | 0 | 0 | 0 | 0 | 0.23111 | 0.23111 | 1.7428e-05 | 1.7428e-05 | 0.0074838 | 0.0074838 | 0 | 0 | 0 | 0 | 0.0061448 | 0.0061448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 56 | NO
16/04/2013 | 0 | 0 | 0.025407 | 0.025407 | 0 | 0 | 0 | 0 | 0.02085 | 0.02085 | 0 | 0 | 0.0026888 | 0.0026888 | 0 | 0 | 0 | 0 | 0.0022066 | 0.0022066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 56 | NO
17/04/2013 | 0.011224 | 0.011224 | 0.003222 | 0.003222 | 0 | 0 | 0 | 0 | 0.0046571 | 0.0046571 | 0.000244 | 0.000244 | 4.9511e-05 | 4.9511e-05 | 0 | 0 | 0 | 0 | 8.439e-05 | 8.439e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 32 | NO
18/04/2013 | 0 | 0 | 0.036189 | 0.036189 | 0 | 0 | 0 | 0 | 0.029699 | 0.029699 | 0 | 0 | 0.00028183 | 0.00028183 | 0 | 0 | 0 | 0 | 0.00023129 | 0.00023129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 29 | NO
19/04/2013 | 0.00244 | 0.00244 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00043758 | 0.00043758 | 0.000122 | 0.000122 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1879e-05 | 2.1879e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 31 | NO
20/04/2013 | 0 | 0 | 0.023781 | 0.023781 | 0 | 0 | 0 | 0 | 0.019516 | 0.019516 | 0 | 0 | 0.00058652 | 0.00058652 | 0 | 0 | 0 | 0 | 0.00048133 | 0.00048133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 4 | NO
21/04/2013 | 0 | 0 | 0.00091786 | 0.00091786 | 0 | 0 | 0 | 0 | 0.00075325 | 0.00075325 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 20 | NO
22/04/2013 | 0.0075639 | 0.0075639 | 0.0062346 | 0.0062346 | 0 | 0 | 0 | 0 | 0.006473 | 0.006473 | 0.000122 | 0.000122 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 3.4381e-05 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 33 | NO
23/04/2013 | 0 | 0 | 0.015352 | 0.015352 | 0 | 0 | 0 | 0 | 0.012599 | 0.012599 | 0 | 0 | 0.00017519 | 0.00017519 | 0 | 0 | 0 | 0 | 0.00014377 | 0.00014377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 4 | NO
24/04/2013 | 0 | 0 | 0.00058652 | 0.00058652 | 0 | 0 | 0 | 0 | 0.00048133 | 0.00048133 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 10 | NO
25/04/2013 | 0 | 0 | 0.003363 | 0.003363 | 0 | 0 | 0 | 0 | 0.0027598 | 0.0027598 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1 | NO
26/04/2013 | 0 | 0 | 0.01587 | 0.01587 | 0 | 0 | 0 | 0 | 0.013024 | 0.013024 | 0 | 0 | 0.00017138 | 0.00017138 | 0 | 0 | 0 | 0 | 0.00014065 | 0.00014065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 3 | NO
27/04/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 1 | NO
28/04/2013 | 0 | 0 | 0.011163 | 0.011163 | 0 | 0 | 0 | 0 | 0.0091609 | 0.0091609 | 0 | 0 | 6.0937e-05 | 6.0937e-05 | 0 | 0 | 0 | 0 | 5.0009e-05 | 5.0009e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1 | NO
29/04/2013 | 0 | 0 | 0.0013635 | 0.0013635 | 0 | 0 | 0 | 0 | 0.0011189 | 0.0011189 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 4 | NO
30/04/2013 | 0 | 0 | 0.0019881 | 0.0019881 | 0 | 0 | 0 | 0 | 0.0016315 | 0.0016315 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 14 | NO
1/05/2013 | 0 | 0 | 0.018072 | 0.018072 | 0 | 0 | 0 | 0 | 0.014831 | 0.014831 | 0 | 0 | 0.00015234 | 0.00015234 | 0 | 0 | 0 | 0 | 0.00012502 | 0.00012502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 18 | NO
2/05/2013 | 0 | 0 | 0.0032792 | 0.0032792 | 0 | 0 | 0 | 0 | 0.0026911 | 0.0026911 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 11 | NO
3/05/2013 | 0 | 0 | 0.03649 | 0.03649 | 0 | 0 | 0 | 0 | 0.029946 | 0.029946 | 0 | 0 | 0.00037324 | 0.00037324 | 0 | 0 | 0 | 0 | 0.0003063 | 0.0003063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 12 | NO
4/05/2013 | 0.297 | 0.297 | 0.00078075 | 0.00078075 | 0 | 0 | 0 | 0 | 0.053903 | 0.053903 | 0.002074 | 0.002074 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 0.00037819 | 0.00037819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 10 | NO
5/05/2013 | 0 | 0 | 0.027376 | 0.027376 | 0 | 0 | 0 | 0 | 0.022466 | 0.022466 | 0 | 0 | 0.00018281 | 0.00018281 | 0 | 0 | 0 | 0 | 0.00015003 | 0.00015003 | 0.015337 | 0.015337 | 0.015337 | 0 | 0 | 0 | 0 | 0 | 0.0027505 | 0.0027505 | 55 | 3 | NO
6/05/2013 | 0.0013071 | 0.0013071 | 0.0017786 | 0.0017786 | 0 | 0 | 0 | 0 | 0.001694 | 0.001694 | 1.7428e-05 | 1.7428e-05 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 5 | NO
7/05/2013 | 0 | 0 | 0.0020642 | 0.0020642 | 0 | 0 | 0 | 0 | 0.001694 | 0.001694 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 13 | NO
8/05/2013 | 0 | 0 | 0.0022509 | 0.0022509 | 0 | 0 | 0 | 0 | 0.0018472 | 0.0018472 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 17 | NO
9/05/2013 | 0 | 0 | 0.0087254 | 0.0087254 | 0 | 0 | 0 | 0 | 0.0071606 | 0.0071606 | 0 | 0 | 0.00011045 | 0.00011045 | 0 | 0 | 0 | 0 | 9.0641e-05 | 9.0641e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 9 | NO
10/05/2013 | 0 | 0 | 0.0014472 | 0.0014472 | 0 | 0 | 0 | 0 | 0.0011877 | 0.0011877 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 11 | NO
11/05/2013 | 0.035501 | 0.035501 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0063667 | 0.0063667 | 0.00036599 | 0.00036599 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5636e-05 | 6.5636e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 2 | NO
12/05/2013 | 0 | 0 | 0.010435 | 0.010435 | 0 | 0 | 0 | 0 | 0.008564 | 0.008564 | 0 | 0 | 6.8554e-05 | 6.8554e-05 | 0 | 0 | 0 | 0 | 5.626e-05 | 5.626e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 2 | NO
13/05/2013 | 0 | 0 | 0.12826 | 0.12826 | 0 | 0 | 0 | 0 | 0.10526 | 0.10526 | 0 | 0 | 0.0008912 | 0.0008912 | 0 | 0 | 0 | 0 | 0.00073138 | 0.00073138 | 0 | 0 | 0.0066459 | 0.0066459 | 0 | 0 | 0 | 0 | 0.0054541 | 0.0054541 | 181 | 11 | NO
14/05/2013 | 0.16142 | 0.16142 | 0.053708 | 0.053708 | 0 | 0 | 0 | 0 | 0.073025 | 0.073025 | 0.0009237 | 0.0009237 | 0.00020185 | 0.00020185 | 0 | 0 | 0 | 0 | 0.00033131 | 0.00033131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 18 | NO
15/05/2013 | 0 | 0 | 0.39558 | 0.39558 | 0 | 0 | 0 | 0 | 0.32464 | 0.32464 | 0 | 0 | 0.0038695 | 0.0038695 | 0 | 0 | 0 | 0 | 0.0031755 | 0.0031755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 43 | NO
16/05/2013 | 0 | 0 | 0.013178 | 0.013178 | 0 | 0 | 0 | 0 | 0.010814 | 0.010814 | 0 | 0 | 5.7128e-05 | 5.7128e-05 | 0 | 0 | 0 | 0 | 4.6883e-05 | 4.6883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 44 | NO
17/05/2013 | 0 | 0 | 0.0019386 | 0.0019386 | 0 | 0 | 0 | 0 | 0.0015909 | 0.0015909 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 10 | NO
18/05/2013 | 0 | 0 | 0.00023613 | 0.00023613 | 0 | 0 | 0 | 0 | 0.00019378 | 0.00019378 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 4 | NO
19/05/2013 | 0 | 0 | 0.0013673 | 0.0013673 | 0 | 0 | 0 | 0 | 0.0011221 | 0.0011221 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 2 | NO
20/05/2013 | 0.0021437 | 0.0021437 | 0.033397 | 0.033397 | 0 | 0 | 0 | 0 | 0.027792 | 0.027792 | 1.7428e-05 | 1.7428e-05 | 0.00014853 | 0.00014853 | 0 | 0 | 0 | 0 | 0.00012502 | 0.00012502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 16 | NO
21/05/2013 | 0.036704 | 0.036704 | 0.016563 | 0.016563 | 0 | 0 | 0 | 0 | 0.020175 | 0.020175 | 0.00094113 | 0.00094113 | 0.00021328 | 0.00021328 | 0 | 0 | 0 | 0 | 0.00034381 | 0.00034381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 15 | NO
22/05/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 26 | NO
23/05/2013 | 0.00047056 | 0.00047056 | 0.054599 | 0.054599 | 0 | 0 | 0 | 0 | 0.044892 | 0.044892 | 1.7428e-05 | 1.7428e-05 | 0.00055224 | 0.00055224 | 0 | 0 | 0 | 0 | 0.00045633 | 0.00045633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 22 | NO
24/05/2013 | 0 | 0 | 0.0010588 | 0.0010588 | 0 | 0 | 0 | 0 | 0.0008689 | 0.0008689 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 14 | NO
25/05/2013 | 0 | 0 | 0.50473 | 0.50473 | 0 | 0 | 0 | 0 | 0.41421 | 0.41421 | 0 | 0 | 0.0085921 | 0.0085921 | 0 | 0 | 0 | 0 | 0.0070512 | 0.0070512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 1 | NO
26/05/2013 | 0 | 0 | 0.01699 | 0.01699 | 0 | 0 | 0 | 0 | 0.013943 | 0.013943 | 0 | 0 | 0.00023232 | 0.00023232 | 0 | 0 | 0 | 0 | 0.00019066 | 0.00019066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | NO
27/05/2013 | 0 | 0 | 0.0029669 | 0.0029669 | 0 | 0 | 0 | 0 | 0.0024348 | 0.0024348 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 36 | NO
28/05/2013 | 0.011067 | 0.011067 | 0.00058652 | 0.00058652 | 0 | 0 | 0 | 0 | 0.002466 | 0.002466 | 3.4857e-05 | 3.4857e-05 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 18 | NO
29/05/2013 | 0 | 0 | 0.00054462 | 0.00054462 | 0 | 0 | 0 | 0 | 0.00044695 | 0.00044695 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 11 | NO
30/05/2013 | 0 | 0 | 0.0022394 | 0.0022394 | 0 | 0 | 0 | 0 | 0.0018378 | 0.0018378 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 26 | NO
31/05/2013 | 0.0054376 | 0.0054376 | 0.15702 | 0.15702 | 0 | 0 | 0 | 0 | 0.12983 | 0.12983 | 3.4857e-05 | 3.4857e-05 | 0.00049892 | 0.00049892 | 0 | 0 | 0 | 0 | 0.0004157 | 0.0004157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 83 | NO
1/06/2013 | 0 | 0 | 0.027132 | 0.027132 | 0 | 0 | 0 | 0 | 0.022266 | 0.022266 | 0 | 0 | 0.00052939 | 0.00052939 | 0 | 0 | 0 | 0 | 0.00043445 | 0.00043445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 101 | NO
2/06/2013 | 0.002074 | 0.002074 | 0.013006 | 0.013006 | 0 | 0 | 0 | 0 | 0.011046 | 0.011046 | 1.7428e-05 | 1.7428e-05 | 9.5214e-05 | 9.5214e-05 | 0 | 0 | 0 | 0 | 8.1264e-05 | 8.1264e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 2 | NO
3/06/2013 | 0 | 0 | 0.006246 | 0.006246 | 0 | 0 | 0 | 0 | 0.0051259 | 0.0051259 | 0 | 0 | 2.666e-05 | 2.666e-05 | 0 | 0 | 0 | 0 | 2.1879e-05 | 2.1879e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 15 | NO
4/06/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 9 | NO
5/06/2013 | 0 | 0 | 0.0014587 | 0.0014587 | 0 | 0 | 0 | 0 | 0.0011971 | 0.0011971 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 34 | NO
6/06/2013 | 0 | 0 | 0.0074419 | 0.0074419 | 0 | 0 | 0 | 0 | 0.0061073 | 0.0061073 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 17 | NO
7/06/2013 | 0 | 0 | 0.38429 | 0.38429 | 0 | 0 | 0 | 0 | 0.31538 | 0.31538 | 0 | 0 | 0.0061775 | 0.0061775 | 0 | 0 | 0 | 0 | 0.0050696 | 0.0050696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 43 | NO
8/06/2013 | 0 | 0 | 0.00095214 | 0.00095214 | 0 | 0 | 0 | 0 | 0.00078138 | 0.00078138 | 0 | 0 | 4.1894e-05 | 4.1894e-05 | 0 | 0 | 0 | 0 | 3.4381e-05 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 5 | NO
9/06/2013 | 0 | 0 | 0.0226 | 0.0226 | 0 | 0 | 0 | 0 | 0.018547 | 0.018547 | 0 | 0 | 0.00012568 | 0.00012568 | 0 | 0 | 0 | 0 | 0.00010314 | 0.00010314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 4 | NO
10/06/2013 | 0 | 0 | 0.068325 | 0.068325 | 0 | 0 | 0 | 0 | 0.056072 | 0.056072 | 0 | 0 | 0.00027422 | 0.00027422 | 0 | 0 | 0 | 0 | 0.00022504 | 0.00022504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | NO
11/06/2013 | 0.00055771 | 0.00055771 | 0.010409 | 0.010409 | 0 | 0 | 0 | 0 | 0.0086421 | 0.0086421 | 1.7428e-05 | 1.7428e-05 | 0.00015615 | 0.00015615 | 0 | 0 | 0 | 0 | 0.00013127 | 0.00013127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 42 | NO
12/06/2013 | 0 | 0 | 0.053678 | 0.053678 | 0 | 0 | 0 | 0 | 0.044051 | 0.044051 | 0 | 0 | 0.00038847 | 0.00038847 | 0 | 0 | 0 | 0 | 0.0003188 | 0.0003188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 24 | NO
13/06/2013 | 0.2708 | 0.2708 | 0.028857 | 0.028857 | 0 | 0 | 0 | 0 | 0.072247 | 0.072247 | 0.0072502 | 0.0072502 | 0.00027802 | 0.00027802 | 0 | 0 | 0 | 0 | 0.0015284 | 0.0015284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 34 | NO
14/06/2013 | 0 | 0 | 0.0035153 | 0.0035153 | 0 | 0 | 0 | 0 | 0.0028849 | 0.0028849 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 17 | NO
15/06/2013 | 0 | 0 | 0.0043189 | 0.0043189 | 0 | 0 | 0 | 0 | 0.0035444 | 0.0035444 | 0 | 0 | 5.332e-05 | 5.332e-05 | 0 | 0 | 0 | 0 | 4.3758e-05 | 4.3758e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 9 | NO
16/06/2013 | 0 | 0 | 0.13092 | 0.13092 | 0 | 0 | 0 | 0 | 0.10744 | 0.10744 | 0 | 0 | 0.00063984 | 0.00063984 | 0 | 0 | 0 | 0 | 0.00052509 | 0.00052509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 2 | NO
17/06/2013 | 0 | 0 | 0.041151 | 0.041151 | 0 | 0 | 0 | 0 | 0.033771 | 0.033771 | 0 | 0 | 0.00027041 | 0.00027041 | 0 | 0 | 0 | 0 | 0.00022191 | 0.00022191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 60 | NO
18/06/2013 | 0 | 0 | 0.0096433 | 0.0096433 | 0 | 0 | 0 | 0 | 0.0079139 | 0.0079139 | 0 | 0 | 3.0468e-05 | 3.0468e-05 | 0 | 0 | 0 | 0 | 2.5004e-05 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 3 | NO
19/06/2013 | 0 | 0 | 0.0041323 | 0.0041323 | 0 | 0 | 0 | 0 | 0.0033912 | 0.0033912 | 0 | 0 | 0.00020566 | 0.00020566 | 0 | 0 | 0 | 0 | 0.00016878 | 0.00016878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 31 | NO
20/06/2013 | 0 | 0 | 0.0019424 | 0.0019424 | 0 | 0 | 0 | 0 | 0.001594 | 0.001594 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 15 | NO
21/06/2013 | 0 | 0 | 0.0070649 | 0.0070649 | 0 | 0 | 0 | 0 | 0.0057979 | 0.0057979 | 0 | 0 | 5.7128e-05 | 5.7128e-05 | 0 | 0 | 0 | 0 | 4.6883e-05 | 4.6883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 11 | NO
22/06/2013 | 0 | 0 | 0.0043265 | 0.0043265 | 0 | 0 | 0 | 0 | 0.0035506 | 0.0035506 | 0 | 0 | 4.1894e-05 | 4.1894e-05 | 0 | 0 | 0 | 0 | 3.4381e-05 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 7 | NO
23/06/2013 | 0 | 0 | 0.16472 | 0.16472 | 0 | 0 | 0 | 0 | 0.13518 | 0.13518 | 0 | 0 | 0.001314 | 0.001314 | 0 | 0 | 0 | 0 | 0.0010783 | 0.0010783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 44 | NO
24/06/2013 | 0 | 0 | 0.017797 | 0.017797 | 0 | 0 | 0 | 0 | 0.014606 | 0.014606 | 0 | 0 | 0.0002247 | 0.0002247 | 0 | 0 | 0 | 0 | 0.00018441 | 0.00018441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 30 | NO
25/06/2013 | 0 | 0 | 0.010603 | 0.010603 | 0 | 0 | 0 | 0 | 0.0087015 | 0.0087015 | 0 | 0 | 9.1405e-05 | 9.1405e-05 | 0 | 0 | 0 | 0 | 7.5013e-05 | 7.5013e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 14 | NO
26/06/2013 | 0 | 0 | 0.11107 | 0.11107 | 0 | 0 | 0 | 0 | 0.09115 | 0.09115 | 0 | 0 | 0.0012911 | 0.0012911 | 0 | 0 | 0 | 0 | 0.0010596 | 0.0010596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 22 | NO
27/06/2013 | 0 | 0 | 0.0037133 | 0.0037133 | 0 | 0 | 0 | 0 | 0.0030474 | 0.0030474 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 18 | NO
28/06/2013 | 0 | 0 | 0.0010055 | 0.0010055 | 0 | 0 | 0 | 0 | 0.00082514 | 0.00082514 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 16 | NO
29/06/2013 | 0.019084 | 0.019084 | 0.0028564 | 0.0028564 | 0 | 0 | 0 | 0 | 0.0057666 | 0.0057666 | 8.7141e-05 | 8.7141e-05 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 2.813e-05 | 2.813e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 2 | NO
30/06/2013 | 0.0029628 | 0.0029628 | 0.053209 | 0.053209 | 0 | 0 | 0 | 0 | 0.044198 | 0.044198 | 1.7428e-05 | 1.7428e-05 | 0.00023613 | 0.00023613 | 0 | 0 | 0 | 0 | 0.00019691 | 0.00019691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 9 | NO
1/07/2013 | 0 | 0 | 0.007998 | 0.007998 | 0 | 0 | 0 | 0 | 0.0065636 | 0.0065636 | 0 | 0 | 4.9511e-05 | 4.9511e-05 | 0 | 0 | 0 | 0 | 4.0632e-05 | 4.0632e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 49 | NO
2/07/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 18 | NO
3/07/2013 | 0 | 0 | 0.017218 | 0.017218 | 0 | 0 | 0 | 0 | 0.014131 | 0.014131 | 0 | 0 | 4.1894e-05 | 4.1894e-05 | 0 | 0 | 0 | 0 | 3.4381e-05 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 11 | NO
4/07/2013 | 0 | 0 | 0.011304 | 0.011304 | 0 | 0 | 0 | 0 | 0.0092766 | 0.0092766 | 0 | 0 | 6.4745e-05 | 6.4745e-05 | 0 | 0 | 0 | 0 | 5.3134e-05 | 5.3134e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 22 | NO
5/07/2013 | 0 | 0 | 0.0024032 | 0.0024032 | 0 | 0 | 0 | 0 | 0.0019722 | 0.0019722 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 14 | NO
6/07/2013 | 0 | 0 | 0.019942 | 0.019942 | 0 | 0 | 0 | 0 | 0.016365 | 0.016365 | 0 | 0 | 0.00025898 | 0.00025898 | 0 | 0 | 0 | 0 | 0.00021254 | 0.00021254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 12 | NO
7/07/2013 | 0 | 0 | 0.051434 | 0.051434 | 0 | 0 | 0 | 0 | 0.04221 | 0.04221 | 0 | 0 | 0.0002247 | 0.0002247 | 0 | 0 | 0 | 0 | 0.00018441 | 0.00018441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 2 | NO
8/07/2013 | 0 | 0 | 40.3102 | 40.3102 | 0 | 0 | 0 | 0 | 33.0811 | 33.0811 | 0 | 0 | 0.11595 | 0.11595 | 0 | 0 | 0 | 0 | 0.095154 | 0.095154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1448 | 785 | Yes | Exceeded Unplanned SAIDI Threshold
9/07/2013 | 0 | 0 | 0.13034 | 0.13034 | 0 | 0 | 0 | 0 | 0.10697 | 0.10697 | 0 | 0 | 0.00070839 | 0.00070839 | 0 | 0 | 0 | 0 | 0.00058135 | 0.00058135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 68 | NO
10/07/2013 | 0 | 0 | 0.22534 | 0.22534 | 0 | 0 | 0 | 0 | 0.18493 | 0.18493 | 0 | 0 | 0.0038314 | 0.0038314 | 0 | 0 | 0 | 0 | 0.0031443 | 0.0031443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 28 | NO
11/07/2013 | 0 | 0 | 0.00020947 | 0.00020947 | 0 | 0 | 0 | 0 | 0.0001719 | 0.0001719 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 18 | NO
12/07/2013 | 0.0018648 | 0.0018648 | 0.027403 | 0.027403 | 0 | 0 | 0 | 0 | 0.022823 | 0.022823 | 1.7428e-05 | 1.7428e-05 | 0.00027041 | 0.00027041 | 0 | 0 | 0 | 0 | 0.00022504 | 0.00022504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 6 | NO
13/07/2013 | 0.08932 | 0.08932 | 0.0096204 | 0.0096204 | 0 | 0 | 0 | 0 | 0.023913 | 0.023913 | 0.00043571 | 0.00043571 | 2.2851e-05 | 2.2851e-05 | 0 | 0 | 0 | 0 | 9.6892e-05 | 9.6892e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 17 | NO
14/07/2013 | 0 | 0 | 0.99317 | 0.99317 | 0 | 0 | 0 | 0 | 0.81506 | 0.81506 | 0 | 0 | 0.0085845 | 0.0085845 | 0 | 0 | 0 | 0 | 0.007045 | 0.007045 | 0 | 0 | 0.0011654 | 0.0011654 | 0 | 0 | 0 | 0 | 0.00095641 | 0.00095641 | 350 | 178 | NO
15/07/2013 | 0 | 0 | 0.0020719 | 0.0020719 | 0 | 0 | 0 | 0 | 0.0017003 | 0.0017003 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 34 | NO
16/07/2013 | 0 | 0 | 0.029711 | 0.029711 | 0 | 0 | 0 | 0 | 0.024382 | 0.024382 | 0 | 0 | 0.000358 | 0.000358 | 0 | 0 | 0 | 0 | 0.0002938 | 0.0002938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | NO
17/07/2013 | 0 | 0 | 0.017596 | 0.017596 | 0 | 0 | 0 | 0 | 0.01444 | 0.01444 | 0 | 0 | 0.00029326 | 0.00029326 | 0 | 0 | 0 | 0 | 0.00024067 | 0.00024067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 6 | NO
18/07/2013 | 0 | 0 | 0.35387 | 0.35387 | 0 | 0 | 0 | 0 | 0.29041 | 0.29041 | 0 | 0 | 0.0037667 | 0.0037667 | 0 | 0 | 0 | 0 | 0.0030912 | 0.0030912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 93 | NO
19/07/2013 | 0 | 0 | 0.074937 | 0.074937 | 0 | 0 | 0 | 0 | 0.061498 | 0.061498 | 0 | 0 | 0.00056747 | 0.00056747 | 0 | 0 | 0 | 0 | 0.00046571 | 0.00046571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 19 | NO
20/07/2013 | 0 | 0 | 0.022691 | 0.022691 | 0 | 0 | 0 | 0 | 0.018622 | 0.018622 | 0 | 0 | 0.00017138 | 0.00017138 | 0 | 0 | 0 | 0 | 0.00014065 | 0.00014065 | 0.0097076 | 0.0097076 | 0.0097076 | 0 | 0 | 0 | 0 | 0 | 0.0017409 | 0.0017409 | 99 | 23 | NO
21/07/2013 | 0 | 0 | 0.0094681 | 0.0094681 | 0 | 0 | 0 | 0 | 0.0077701 | 0.0077701 | 0 | 0 | 0.00020185 | 0.00020185 | 0 | 0 | 0 | 0 | 0.00016565 | 0.00016565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 6 | NO
22/07/2013 | 0.074506 | 0.074506 | 0.0042046 | 0.0042046 | 0 | 0 | 0 | 0 | 0.016812 | 0.016812 | 0.00036599 | 0.00036599 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 8.1264e-05 | 8.1264e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 48 | NO
23/07/2013 | 0 | 0 | 0.015585 | 0.015585 | 0 | 0 | 0 | 0 | 0.01279 | 0.01279 | 0 | 0 | 0.00011807 | 0.00011807 | 0 | 0 | 0 | 0 | 9.6892e-05 | 9.6892e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 38 | NO
24/07/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 49 | NO
25/07/2013 | 0 | 0 | 1.0923 | 1.0923 | 0 | 0 | 0 | 0 | 0.89645 | 0.89645 | 0 | 0 | 0.01827 | 0.01827 | 0 | 0 | 0 | 0 | 0.014993 | 0.014993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | NO
26/07/2013 | 0.0074942 | 0.0074942 | 0.019747 | 0.019747 | 0 | 0 | 0 | 0 | 0.01755 | 0.01755 | 0.0074942 | 0.0074942 | 0.00024756 | 0.00024756 | 0 | 0 | 0 | 0 | 0.0015471 | 0.0015471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 12 | NO
27/07/2013 | 0 | 0 | 0.085064 | 0.085064 | 0 | 0 | 0 | 0 | 0.069809 | 0.069809 | 0 | 0 | 0.00091024 | 0.00091024 | 0 | 0 | 0 | 0 | 0.000747 | 0.000747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 5 | NO
28/07/2013 | 0 | 0 | 0.0010892 | 0.0010892 | 0 | 0 | 0 | 0 | 0.0008939 | 0.0008939 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | NO
29/07/2013 | 0 | 0 | 0.044716 | 0.044716 | 0 | 0 | 0 | 0 | 0.036697 | 0.036697 | 0 | 0 | 0.00011807 | 0.00011807 | 0 | 0 | 0 | 0 | 9.6892e-05 | 9.6892e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 12 | NO
30/07/2013 | 0 | 0 | 0.0033363 | 0.0033363 | 0 | 0 | 0 | 0 | 0.002738 | 0.002738 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 19 | NO
31/07/2013 | 0 | 0 | 0.0016072 | 0.0016072 | 0 | 0 | 0 | 0 | 0.001319 | 0.001319 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 38 | NO
1/08/2013 | 0 | 0 | 0.00020566 | 0.00020566 | 0 | 0 | 0 | 0 | 0.00016878 | 0.00016878 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 13 | NO
2/08/2013 | 0.045383 | 0.045383 | 0.00019424 | 0.00019424 | 0 | 0 | 0 | 0 | 0.0082983 | 0.0082983 | 0.0010806 | 0.0010806 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 0.00019691 | 0.00019691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 17 | NO
3/08/2013 | 0 | 0 | 0.012736 | 0.012736 | 0 | 0 | 0 | 0 | 0.010452 | 0.010452 | 0 | 0 | 0.00011426 | 0.00011426 | 0 | 0 | 0 | 0 | 9.3766e-05 | 9.3766e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 17 | NO
4/08/2013 | 0 | 0 | 0.010336 | 0.010336 | 0 | 0 | 0 | 0 | 0.0084827 | 0.0084827 | 0 | 0 | 7.6171e-05 | 7.6171e-05 | 0 | 0 | 0 | 0 | 6.2511e-05 | 6.2511e-05 | 0 | 0 | 0.0013901 | 0.0013901 | 0 | 0 | 0 | 0 | 0.0011408 | 0.0011408 | 69 | 6 | NO
5/08/2013 | 0 | 0 | 0.35959 | 0.35959 | 0 | 0 | 0 | 0 | 0.2951 | 0.2951 | 0 | 0 | 0.0068592 | 0.0068592 | 0 | 0 | 0 | 0 | 0.0056291 | 0.0056291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 40 | NO
6/08/2013 | 0 | 0 | 0.021103 | 0.021103 | 0 | 0 | 0 | 0 | 0.017319 | 0.017319 | 0 | 0 | 0.00013711 | 0.00013711 | 0 | 0 | 0 | 0 | 0.00011252 | 0.00011252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 11 | NO
7/08/2013 | 0 | 0 | 0.0022394 | 0.0022394 | 0 | 0 | 0 | 0 | 0.0018378 | 0.0018378 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 32 | NO
8/08/2013 | 0 | 0 | 0.028915 | 0.028915 | 0 | 0 | 0 | 0 | 0.023729 | 0.023729 | 0 | 0 | 0.00028945 | 0.00028945 | 0 | 0 | 0 | 0 | 0.00023754 | 0.00023754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 10 | NO
9/08/2013 | 0 | 0 | 0.091836 | 0.091836 | 0 | 0 | 0 | 0 | 0.075366 | 0.075366 | 0 | 0 | 0.0048635 | 0.0048635 | 0 | 0 | 0 | 0 | 0.0039913 | 0.0039913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 12 | NO
10/08/2013 | 0 | 0 | 0.076742 | 0.076742 | 0 | 0 | 0 | 0 | 0.06298 | 0.06298 | 0 | 0 | 0.00020947 | 0.00020947 | 0 | 0 | 0 | 0 | 0.0001719 | 0.0001719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 3 | NO
11/08/2013 | 0.022116 | 0.022116 | 0.028324 | 0.028324 | 0 | 0 | 0 | 0 | 0.027211 | 0.027211 | 0.00047056 | 0.00047056 | 0.00027422 | 0.00027422 | 0 | 0 | 0 | 0 | 0.00030943 | 0.00030943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | NO
12/08/2013 | 0 | 0 | 6.2582 | 6.2582 | 0 | 0 | 0 | 0 | 5.1359 | 5.1359 | 0 | 0 | 0.040409 | 0.040409 | 0 | 0 | 0 | 0 | 0.033162 | 0.033162 | 0 | 0 | 0.0070953 | 0.0070953 | 0 | 0 | 0 | 0 | 0.0058229 | 0.0058229 | 719 | 217 | Yes | Exceeded Unplanned SAIDI Threshold
13/08/2013 | 0.0096901 | 0.0096901 | 0.0011121 | 0.0011121 | 0 | 0 | 0 | 0 | 0.0026505 | 0.0026505 | 1.7428e-05 | 1.7428e-05 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 46 | NO
14/08/2013 | 0 | 0 | 0.04141 | 0.04141 | 0 | 0 | 0 | 0 | 0.033984 | 0.033984 | 0 | 0 | 0.0002666 | 0.0002666 | 0 | 0 | 0 | 0 | 0.00021879 | 0.00021879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 12 | NO
15/08/2013 | 0 | 0 | 0.02068 | 0.02068 | 0 | 0 | 0 | 0 | 0.016972 | 0.016972 | 0 | 0 | 7.6171e-05 | 7.6171e-05 | 0 | 0 | 0 | 0 | 6.2511e-05 | 6.2511e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 14 | NO
16/08/2013 | 0.13103 | 0.13103 | 0.073707 | 0.073707 | 0 | 0 | 0 | 0 | 0.083986 | 0.083986 | 0.00047056 | 0.00047056 | 0.0005332 | 0.0005332 | 0 | 0 | 0 | 0 | 0.00052196 | 0.00052196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 73 | NO
17/08/2013 | 0 | 0 | 0.0091938 | 0.0091938 | 0 | 0 | 0 | 0 | 0.007545 | 0.007545 | 0 | 0 | 0.000179 | 0.000179 | 0 | 0 | 0 | 0 | 0.0001469 | 0.0001469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | NO
18/08/2013 | 0 | 0 | 0.011959 | 0.011959 | 0 | 0 | 0 | 0 | 0.0098142 | 0.0098142 | 0 | 0 | 0.00010283 | 0.00010283 | 0 | 0 | 0 | 0 | 8.439e-05 | 8.439e-05 | 0 | 0 | 4.5703e-05 | 4.5703e-05 | 0 | 0 | 0 | 0 | 3.7506e-05 | 3.7506e-05 | 76 | 18 | NO
19/08/2013 | 0.024783 | 0.024783 | 0.060903 | 0.060903 | 0 | 0 | 0 | 0 | 0.054425 | 0.054425 | 6.9713e-05 | 6.9713e-05 | 0.00033515 | 0.00033515 | 0 | 0 | 0 | 0 | 0.00028755 | 0.00028755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 26 | NO
20/08/2013 | 0 | 0 | 0.044412 | 0.044412 | 0 | 0 | 0 | 0 | 0.036447 | 0.036447 | 0 | 0 | 0.00043037 | 0.00043037 | 0 | 0 | 0 | 0 | 0.00035319 | 0.00035319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 14 | NO
21/08/2013 | 0 | 0 | 0.10791 | 0.10791 | 0 | 0 | 0 | 0 | 0.088559 | 0.088559 | 0 | 0 | 0.00059413 | 0.00059413 | 0 | 0 | 0 | 0 | 0.00048758 | 0.00048758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 10 | NO
22/08/2013 | 0 | 0 | 0.024451 | 0.024451 | 0 | 0 | 0 | 0 | 0.020066 | 0.020066 | 0 | 0 | 0.00024756 | 0.00024756 | 0 | 0 | 0 | 0 | 0.00020316 | 0.00020316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 8 | NO
23/08/2013 | 0.034613 | 0.034613 | 0.00083788 | 0.00083788 | 0 | 0 | 0 | 0 | 0.0068949 | 0.0068949 | 0.00036599 | 0.00036599 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 7.1887e-05 | 7.1887e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 12 | NO
24/08/2013 | 0.57733 | 0.57733 | 0.081526 | 0.081526 | 0 | 0 | 0 | 0 | 0.17044 | 0.17044 | 0.0010457 | 0.0010457 | 0.00058652 | 0.00058652 | 0 | 0 | 0 | 0 | 0.00066886 | 0.00066886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 8 | NO
25/08/2013 | 0 | 0 | 0.00033134 | 0.00033134 | 0 | 0 | 0 | 0 | 0.00027192 | 0.00027192 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 1 | NO
26/08/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 6 | NO
27/08/2013 | 0 | 0 | 0.00011426 | 0.00011426 | 0 | 0 | 0 | 0 | 9.3766e-05 | 9.3766e-05 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 13 | NO
28/08/2013 | 0.0063265 | 0.0063265 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011346 | 0.0011346 | 5.2285e-05 | 5.2285e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 18 | NO
29/08/2013 | 1.0414 | 1.0414 | 0.42664 | 0.42664 | 0 | 0 | 0 | 0 | 0.53689 | 0.53689 | 0.010962 | 0.010962 | 0.0050121 | 0.0050121 | 0 | 0 | 0 | 0 | 0.0060792 | 0.0060792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 76 | NO
30/08/2013 | 0 | 0 | 0.069278 | 0.069278 | 0 | 0 | 0 | 0 | 0.056854 | 0.056854 | 0 | 0 | 0.0019881 | 0.0019881 | 0 | 0 | 0 | 0 | 0.0016315 | 0.0016315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 16 | NO
31/08/2013 | 0 | 0 | 0.036893 | 0.036893 | 0 | 0 | 0 | 0 | 0.030277 | 0.030277 | 0 | 0 | 0.00022851 | 0.00022851 | 0 | 0 | 0 | 0 | 0.00018753 | 0.00018753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 2 | NO
1/09/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | NO
2/09/2013 | 0.22958 | 0.22958 | 0.00054843 | 0.00054843 | 0 | 0 | 0 | 0 | 0.041623 | 0.041623 | 0.00020914 | 0.00020914 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 4.0632e-05 | 4.0632e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 1 | NO
3/09/2013 | 0 | 0 | 0.00049892 | 0.00049892 | 0 | 0 | 0 | 0 | 0.00040945 | 0.00040945 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 5 | NO
4/09/2013 | 0 | 0 | 0.0027117 | 0.0027117 | 0 | 0 | 0 | 0 | 0.0022254 | 0.0022254 | 0 | 0 | 3.0468e-05 | 3.0468e-05 | 0 | 0 | 0 | 0 | 2.5004e-05 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | NO
5/09/2013 | 0 | 0 | 0.0005789 | 0.0005789 | 0 | 0 | 0 | 0 | 0.00047508 | 0.00047508 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 20 | NO
6/09/2013 | 0.0024922 | 0.0024922 | 0.000358 | 0.000358 | 0 | 0 | 0 | 0 | 0.00074075 | 0.00074075 | 1.7428e-05 | 1.7428e-05 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | NO
7/09/2013 | 0 | 0 | 0.00076552 | 0.00076552 | 0 | 0 | 0 | 0 | 0.00062823 | 0.00062823 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 7 | NO
8/09/2013 | 0 | 0 | 0.12452 | 0.12452 | 0 | 0 | 0 | 0 | 0.10219 | 0.10219 | 0 | 0 | 0.00096737 | 0.00096737 | 0 | 0 | 0 | 0 | 0.00079389 | 0.00079389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 12 | NO
9/09/2013 | 0 | 0 | 0.85612 | 0 | 0 | 0 | 0 | 0 | 0.70259 | 0 | 0 | 0 | 0.045059 | 0 | 0 | 0 | 0 | 0 | 0.036978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 337 | NO | Transmission Outage
10/09/2013 | 0 | 0 | 0.001691 | 0.001691 | 0 | 0 | 0 | 0 | 0.0013877 | 0.0013877 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 7 | NO
11/09/2013 | 0 | 0 | 0.085849 | 0.085849 | 0 | 0 | 0 | 0 | 0.070453 | 0.070453 | 0 | 0 | 0.0029897 | 0.0029897 | 0 | 0 | 0 | 0 | 0.0024535 | 0.0024535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 31 | NO
12/09/2013 | 0.00034857 | 0.00034857 | 0.17274 | 0.17274 | 0 | 0 | 0 | 0 | 0.14183 | 0.14183 | 1.7428e-05 | 1.7428e-05 | 0.008634 | 0.008634 | 0 | 0 | 0 | 0 | 0.0070887 | 0.0070887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 52 | NO
13/09/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 6 | NO
14/09/2013 | 0 | 0 | 0.028122 | 0.028122 | 0 | 0 | 0 | 0 | 0.023079 | 0.023079 | 0 | 0 | 0.00037324 | 0.00037324 | 0 | 0 | 0 | 0 | 0.0003063 | 0.0003063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 6 | NO
15/09/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 12 | NO
16/09/2013 | 0 | 0 | 0.42164 | 0.42164 | 0 | 0 | 0 | 0 | 0.34602 | 0.34602 | 0 | 0 | 0.0073238 | 0.0073238 | 0 | 0 | 0 | 0 | 0.0060104 | 0.0060104 | 0 | 0 | 0.0033782 | 0.0033782 | 0 | 0 | 0 | 0 | 0.0027724 | 0.0027724 | 214 | 80 | NO
17/09/2013 | 0 | 0 | 0.0047188 | 0.0047188 | 0 | 0 | 0 | 0 | 0.0038725 | 0.0038725 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 11 | NO
18/09/2013 | 0.0068842 | 0.0068842 | 0.021339 | 0.021339 | 0 | 0 | 0 | 0 | 0.018747 | 0.018747 | 1.7428e-05 | 1.7428e-05 | 0.00051035 | 0.00051035 | 0 | 0 | 0 | 0 | 0.00042195 | 0.00042195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 8 | NO
19/09/2013 | 0.15131 | 0.15131 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027136 | 0.027136 | 0.0023528 | 0.0023528 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00042195 | 0.00042195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 16 | NO
20/09/2013 | 0 | 0 | 0.0044179 | 0.0044179 | 0 | 0 | 0 | 0 | 0.0036256 | 0.0036256 | 0 | 0 | 2.2851e-05 | 2.2851e-05 | 0 | 0 | 0 | 0 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 12 | NO
21/09/2013 | 0 | 0 | 0.0027498 | 0.0027498 | 0 | 0 | 0 | 0 | 0.0022566 | 0.0022566 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 5 | NO
22/09/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1 | NO
23/09/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 2 | NO
24/09/2013 | 0 | 0 | 0.0026012 | 0.0026012 | 0 | 0 | 0 | 0 | 0.0021347 | 0.0021347 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 5 | NO
25/09/2013 | 0 | 0 | 0.00065507 | 0.00065507 | 0 | 0 | 0 | 0 | 0.00053759 | 0.00053759 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 2 | NO
26/09/2013 | 0 | 0 | 1.2284 | 1.2284 | 0 | 0 | 0 | 0 | 1.0081 | 1.0081 | 0 | 0 | 0.014073 | 0.014073 | 0 | 0 | 0 | 0 | 0.011549 | 0.011549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 174 | NO
27/09/2013 | 0 | 0 | 0.0013178 | 0.0013178 | 0 | 0 | 0 | 0 | 0.0010814 | 0.0010814 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 24 | NO
28/09/2013 | 0 | 0 | 0.043791 | 0.043791 | 0 | 0 | 0 | 0 | 0.035937 | 0.035937 | 0 | 0 | 0.00034658 | 0.00034658 | 0 | 0 | 0 | 0 | 0.00028442 | 0.00028442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 4 | NO
29/09/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | NO
30/09/2013 | 0 | 0 | 0.0037057 | 0.0037057 | 0 | 0 | 0 | 0 | 0.0030411 | 0.0030411 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 75 | NO
1/10/2013 | 0 | 0 | 21.2402 | 21.2402 | 0 | 0 | 0 | 0 | 17.4311 | 17.4311 | 0 | 0 | 0.08575 | 0.08575 | 0 | 0 | 0 | 0 | 0.070371 | 0.070371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1121 | 955 | Yes | Exceeded Unplanned SAIDI Threshold
2/10/2013 | 0 | 0 | 0.085376 | 0.085376 | 0 | 0 | 0 | 0 | 0.070065 | 0.070065 | 0 | 0 | 0.00028564 | 0.00028564 | 0 | 0 | 0 | 0 | 0.00023442 | 0.00023442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 77 | NO
3/10/2013 | 0 | 0 | 0.0086759 | 0.0086759 | 0 | 0 | 0 | 0 | 0.00712 | 0.00712 | 0 | 0 | 3.0468e-05 | 3.0468e-05 | 0 | 0 | 0 | 0 | 2.5004e-05 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 5 | NO
4/10/2013 | 0 | 0 | 0.010976 | 0.010976 | 0 | 0 | 0 | 0 | 0.0090078 | 0.0090078 | 0 | 0 | 8.3788e-05 | 8.3788e-05 | 0 | 0 | 0 | 0 | 6.8762e-05 | 6.8762e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 9 | NO
5/10/2013 | 0 | 0 | 0.0035001 | 0.0035001 | 0 | 0 | 0 | 0 | 0.0028724 | 0.0028724 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | NO
6/10/2013 | 0 | 0 | 0.0078151 | 0.0078151 | 0 | 0 | 0 | 0 | 0.0064136 | 0.0064136 | 0 | 0 | 0.000179 | 0.000179 | 0 | 0 | 0 | 0 | 0.0001469 | 0.0001469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 1 | NO
7/10/2013 | 0 | 0 | 0.0020604 | 0.0020604 | 0 | 0 | 0 | 0 | 0.0016909 | 0.0016909 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 3 | NO
8/10/2013 | 0.0037645 | 0.0037645 | 0.95196 | 0.95196 | 0 | 0 | 0 | 0 | 0.78191 | 0.78191 | 5.2285e-05 | 5.2285e-05 | 0.0187 | 0.0187 | 0 | 0 | 0 | 0 | 0.015356 | 0.015356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 96 | NO
9/10/2013 | 0 | 0 | 0.0021899 | 0.0021899 | 0 | 0 | 0 | 0 | 0.0017972 | 0.0017972 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 14 | NO
10/10/2013 | 0.0017777 | 0.0017777 | 0.0050349 | 0.0050349 | 0 | 0 | 0 | 0 | 0.0044508 | 0.0044508 | 1.7428e-05 | 1.7428e-05 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 26 | NO
11/10/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 11 | NO
12/10/2013 | 0 | 0 | 0.037872 | 0.037872 | 0 | 0 | 0 | 0 | 0.03108 | 0.03108 | 0 | 0 | 0.0002209 | 0.0002209 | 0 | 0 | 0 | 0 | 0.00018128 | 0.00018128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1 | NO
13/10/2013 | 0 | 0 | 0.042222 | 0.042222 | 0 | 0 | 0 | 0 | 0.03465 | 0.03465 | 0 | 0 | 9.5214e-05 | 9.5214e-05 | 0 | 0 | 0 | 0 | 7.8138e-05 | 7.8138e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 11 | NO
14/10/2013 | 0 | 0 | 0.0018548 | 0.0018548 | 0 | 0 | 0 | 0 | 0.0015221 | 0.0015221 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 19 | NO
15/10/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 47 | NO
16/10/2013 | 0 | 0 | 0.14121 | 0.14121 | 0 | 0 | 0 | 0 | 0.11588 | 0.11588 | 0 | 0 | 0.0041894 | 0.0041894 | 0 | 0 | 0 | 0 | 0.0034381 | 0.0034381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 77 | NO
17/10/2013 | 0.12956 | 0.12956 | 0.53746 | 0.53746 | 0 | 0 | 0 | 0 | 0.46431 | 0.46431 | 0.00073199 | 0.00073199 | 0.0066231 | 0.0066231 | 0 | 0 | 0 | 0 | 0.0055666 | 0.0055666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 155 | NO
18/10/2013 | 0 | 0 | 0.019016 | 0.019016 | 0 | 0 | 0 | 0 | 0.015606 | 0.015606 | 0 | 0 | 6.8554e-05 | 6.8554e-05 | 0 | 0 | 0 | 0 | 5.626e-05 | 5.626e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 17 | NO
19/10/2013 | 0 | 0 | 0.00070077 | 0.00070077 | 0 | 0 | 0 | 0 | 0.0005751 | 0.0005751 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 1 | NO
20/10/2013 | 0.044094 | 0.044094 | 0.033393 | 0.033393 | 0 | 0 | 0 | 0 | 0.035312 | 0.035312 | 0.044094 | 0.044094 | 0.0003542 | 0.0003542 | 0 | 0 | 0 | 0 | 0.0081983 | 0.0081983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | NO
21/10/2013 | 0 | 0 | 0.00096356 | 0.00096356 | 0 | 0 | 0 | 0 | 0.00079076 | 0.00079076 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 5 | NO
22/10/2013 | 0 | 0 | 0.03035 | 0.03035 | 0 | 0 | 0 | 0 | 0.024907 | 0.024907 | 0 | 0 | 0.00017519 | 0.00017519 | 0 | 0 | 0 | 0 | 0.00014377 | 0.00014377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 64 | NO
23/10/2013 | 0 | 0 | 0.027943 | 0.027943 | 0 | 0 | 0 | 0 | 0.022932 | 0.022932 | 0 | 0 | 9.5214e-05 | 9.5214e-05 | 0 | 0 | 0 | 0 | 7.8138e-05 | 7.8138e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 9 | NO
24/10/2013 | 0 | 0 | 0.0048788 | 0.0048788 | 0 | 0 | 0 | 0 | 0.0040038 | 0.0040038 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 1 | NO
25/10/2013 | 0.0013594 | 0.0013594 | 0.037301 | 0.037301 | 0 | 0 | 0 | 0 | 0.030855 | 0.030855 | 1.7428e-05 | 1.7428e-05 | 0.00031992 | 0.00031992 | 0 | 0 | 0 | 0 | 0.00026567 | 0.00026567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 5 | NO
26/10/2013 | 0 | 0 | 0.0012987 | 0.0012987 | 0 | 0 | 0 | 0 | 0.0010658 | 0.0010658 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 8 | NO
27/10/2013 | 0 | 0 | 0.014179 | 0.014179 | 0 | 0 | 0 | 0 | 0.011636 | 0.011636 | 0 | 0 | 0.00011807 | 0.00011807 | 0 | 0 | 0 | 0 | 9.6892e-05 | 9.6892e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 6 | NO
28/10/2013 | 0 | 0 | 0.83647 | 0.83647 | 0 | 0 | 0 | 0 | 0.68646 | 0.68646 | 0 | 0 | 0.015729 | 0.015729 | 0 | 0 | 0 | 0 | 0.012908 | 0.012908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 20 | NO
29/10/2013 | 0.0031545 | 0.0031545 | 0.01723 | 0.01723 | 0 | 0 | 0 | 0 | 0.014706 | 0.014706 | 3.4857e-05 | 3.4857e-05 | 0.00014472 | 0.00014472 | 0 | 0 | 0 | 0 | 0.00012502 | 0.00012502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 4 | NO
30/10/2013 | 0 | 0 | 0.015687 | 0.015687 | 0 | 0 | 0 | 0 | 0.012874 | 0.012874 | 0 | 0 | 0.00016758 | 0.00016758 | 0 | 0 | 0 | 0 | 0.00013752 | 0.00013752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 3 | NO
31/10/2013 | 0 | 0 | 0.073532 | 0.073532 | 0 | 0 | 0 | 0 | 0.060345 | 0.060345 | 0 | 0 | 0.0028374 | 0.0028374 | 0 | 0 | 0 | 0 | 0.0023285 | 0.0023285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 5 | NO
1/11/2013 | 0 | 0 | 0.00012187 | 0.00012187 | 0 | 0 | 0 | 0 | 0.00010002 | 0.00010002 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 33 | NO
2/11/2013 | 0 | 0 | 0.29187 | 0.29187 | 0 | 0 | 0 | 0 | 0.23953 | 0.23953 | 0 | 0 | 0.0050692 | 0.0050692 | 0 | 0 | 0 | 0 | 0.0041601 | 0.0041601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 6 | NO
3/11/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1 | NO
4/11/2013 | 0 | 0 | 0.21253 | 0.21253 | 0 | 0 | 0 | 0 | 0.17441 | 0.17441 | 0 | 0 | 0.00067411 | 0.00067411 | 0 | 0 | 0 | 0 | 0.00055322 | 0.00055322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 1 | NO
5/11/2013 | 0 | 0 | 0.0015729 | 0.0015729 | 0 | 0 | 0 | 0 | 0.0012908 | 0.0012908 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | NO
6/11/2013 | 0.0023702 | 0.0023702 | 0.00096737 | 0.00096737 | 0 | 0 | 0 | 0 | 0.001219 | 0.001219 | 1.7428e-05 | 1.7428e-05 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 24 | NO
7/11/2013 | 0 | 0 | 0.055887 | 0.055887 | 0 | 0 | 0 | 0 | 0.045864 | 0.045864 | 0 | 0 | 0.00081884 | 0.00081884 | 0 | 0 | 0 | 0 | 0.00067199 | 0.00067199 | 0 | 0 | 0.005073 | 0.005073 | 0 | 0 | 0 | 0 | 0.0041632 | 0.0041632 | 137 | 15 | NO
8/11/2013 | 0 | 0 | 0.012953 | 0.012953 | 0 | 0 | 0 | 0 | 0.01063 | 0.01063 | 0 | 0 | 4.5703e-05 | 4.5703e-05 | 0 | 0 | 0 | 0 | 3.7506e-05 | 3.7506e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 7 | NO
9/11/2013 | 0 | 0 | 0.025609 | 0.025609 | 0 | 0 | 0 | 0 | 0.021016 | 0.021016 | 0 | 0 | 0.00018281 | 0.00018281 | 0 | 0 | 0 | 0 | 0.00015003 | 0.00015003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 2 | NO
10/11/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 7 | NO
11/11/2013 | 0 | 0 | 0.0080894 | 0.0080894 | 0 | 0 | 0 | 0 | 0.0066386 | 0.0066386 | 0 | 0 | 6.8554e-05 | 6.8554e-05 | 0 | 0 | 0 | 0 | 5.626e-05 | 5.626e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 9 | NO
12/11/2013 | 0 | 0 | 0.042595 | 0.042595 | 0 | 0 | 0 | 0 | 0.034956 | 0.034956 | 0 | 0 | 0.00047226 | 0.00047226 | 0 | 0 | 0 | 0 | 0.00038757 | 0.00038757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 5 | NO
13/11/2013 | 0 | 0 | 0.46975 | 0.46975 | 0 | 0 | 0 | 0 | 0.38551 | 0.38551 | 0 | 0 | 0.0069087 | 0.0069087 | 0 | 0 | 0 | 0 | 0.0056697 | 0.0056697 | 0 | 0 | 0.0061889 | 0.0061889 | 0 | 0 | 0 | 0 | 0.005079 | 0.005079 | 227 | 23 | NO
14/11/2013 | 6.9713e-05 | 6.9713e-05 | 0.0021404 | 0.0021404 | 0 | 0 | 0 | 0 | 0.0017691 | 0.0017691 | 3.4857e-05 | 3.4857e-05 | 0.0003123 | 0.0003123 | 0 | 0 | 0 | 0 | 0.00026255 | 0.00026255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 4 | NO
15/11/2013 | 0 | 0 | 0.0026241 | 0.0026241 | 0 | 0 | 0 | 0 | 0.0021535 | 0.0021535 | 0 | 0 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 3 | NO
16/11/2013 | 0 | 0 | 0.00030468 | 0.00030468 | 0 | 0 | 0 | 0 | 0.00025004 | 0.00025004 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 1 | NO
17/11/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | NO
18/11/2013 | 0 | 0 | 0.012496 | 0.012496 | 0 | 0 | 0 | 0 | 0.010255 | 0.010255 | 0 | 0 | 0.00020185 | 0.00020185 | 0 | 0 | 0 | 0 | 0.00016565 | 0.00016565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 16 | NO
19/11/2013 | 0 | 0 | 0.0080094 | 0.0080094 | 0 | 0 | 0 | 0 | 0.006573 | 0.006573 | 0 | 0 | 0.00010283 | 0.00010283 | 0 | 0 | 0 | 0 | 8.439e-05 | 8.439e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 30 | NO
20/11/2013 | 0 | 0 | 0.00064365 | 0.00064365 | 0 | 0 | 0 | 0 | 0.00052822 | 0.00052822 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 36 | NO
21/11/2013 | 0 | 0 | 0.022714 | 0.022714 | 0 | 0 | 0 | 0 | 0.018641 | 0.018641 | 0 | 0 | 0.00021709 | 0.00021709 | 0 | 0 | 0 | 0 | 0.00017816 | 0.00017816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 38 | NO
22/11/2013 | 0 | 0 | 0.00081884 | 0.00081884 | 0 | 0 | 0 | 0 | 0.00067199 | 0.00067199 | 0 | 0 | 7.6171e-06 | 7.6171e-06 | 0 | 0 | 0 | 0 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 2 | NO
23/11/2013 | 0 | 0 | 0.55259 | 0.55259 | 0 | 0 | 0 | 0 | 0.45349 | 0.45349 | 0 | 0 | 0.010854 | 0.010854 | 0 | 0 | 0 | 0 | 0.0089078 | 0.0089078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 5 | NO
24/11/2013 | 0 | 0 | 0.89969 | 0.89969 | 0 | 0 | 0 | 0 | 0.73834 | 0.73834 | 0 | 0 | 0.0079713 | 0.0079713 | 0 | 0 | 0 | 0 | 0.0065417 | 0.0065417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 12 | NO
25/11/2013 | 0 | 0 | 0.0020376 | 0.0020376 | 0 | 0 | 0 | 0 | 0.0016722 | 0.0016722 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 11 | NO
26/11/2013 | 0 | 0 | 0.0010664 | 0.0010664 | 0 | 0 | 0 | 0 | 0.00087515 | 0.00087515 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0.0043951 | 0.0043951 | 0 | 0 | 0 | 0 | 0.0036069 | 0.0036069 | 96 | 13 | NO
27/11/2013 | 0 | 0 | 0.45593 | 0.45593 | 0 | 0 | 0 | 0 | 0.37416 | 0.37416 | 0 | 0 | 0.0069811 | 0.0069811 | 0 | 0 | 0 | 0 | 0.0057291 | 0.0057291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 61 | NO
28/11/2013 | 0 | 0 | 0.0041399 | 0.0041399 | 0 | 0 | 0 | 0 | 0.0033975 | 0.0033975 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 16 | NO
29/11/2013 | 0 | 0 | 0.0078151 | 0.0078151 | 0 | 0 | 0 | 0 | 0.0064136 | 0.0064136 | 0 | 0 | 2.2851e-05 | 2.2851e-05 | 0 | 0 | 0 | 0 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 8 | NO
30/11/2013 | 0 | 0 | 0.010721 | 0.010721 | 0 | 0 | 0 | 0 | 0.0087984 | 0.0087984 | 0 | 0 | 0.00030849 | 0.00030849 | 0 | 0 | 0 | 0 | 0.00025317 | 0.00025317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 2 | NO
1/12/2013 | 0 | 0 | 0.040984 | 0.040984 | 0 | 0 | 0 | 0 | 0.033634 | 0.033634 | 0 | 0 | 0.00051035 | 0.00051035 | 0 | 0 | 0 | 0 | 0.00041882 | 0.00041882 | 0 | 0 | 0.0074495 | 0.0074495 | 0 | 0 | 0 | 0 | 0.0061136 | 0.0061136 | 40 | 5 | NO
2/12/2013 | 0 | 0 | 0.111 | 0.111 | 0 | 0 | 0 | 0 | 0.091091 | 0.091091 | 0 | 0 | 0.0045017 | 0.0045017 | 0 | 0 | 0 | 0 | 0.0036944 | 0.0036944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 30 | NO
3/12/2013 | 0 | 0 | 0.0067031 | 0.0067031 | 0 | 0 | 0 | 0 | 0.0055009 | 0.0055009 | 0 | 0 | 3.8086e-05 | 3.8086e-05 | 0 | 0 | 0 | 0 | 3.1255e-05 | 3.1255e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 39 | NO
4/12/2013 | 0 | 0 | 0.57268 | 0.57268 | 0 | 0 | 0 | 0 | 0.46998 | 0.46998 | 0 | 0 | 0.0065926 | 0.0065926 | 0 | 0 | 0 | 0 | 0.0054103 | 0.0054103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 45 | NO
5/12/2013 | 0 | 0 | 0.25578 | 0.25578 | 0 | 0 | 0 | 0 | 0.20991 | 0.20991 | 0 | 0 | 0.0034963 | 0.0034963 | 0 | 0 | 0 | 0 | 0.0028692 | 0.0028692 | 0 | 0 | 0.025552 | 0.025552 | 0 | 0 | 0 | 0 | 0.020969 | 0.020969 | 137 | 24 | NO
6/12/2013 | 0 | 0 | 0.00044941 | 0.00044941 | 0 | 0 | 0 | 0 | 0.00036881 | 0.00036881 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 11 | NO
7/12/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 9 | NO
8/12/2013 | 0 | 0 | 0.0056024 | 0.0056024 | 0 | 0 | 0 | 0 | 0.0045977 | 0.0045977 | 0 | 0 | 4.9511e-05 | 4.9511e-05 | 0 | 0 | 0 | 0 | 4.0632e-05 | 4.0632e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 4 | NO
9/12/2013 | 0 | 0 | 0.14994 | 0.14994 | 0 | 0 | 0 | 0 | 0.12305 | 0.12305 | 0 | 0 | 0.0047569 | 0.0047569 | 0 | 0 | 0 | 0 | 0.0039038 | 0.0039038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 41 | NO
10/12/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 9 | NO
11/12/2013 | 0 | 0 | 0.0019804 | 0.0019804 | 0 | 0 | 0 | 0 | 0.0016253 | 0.0016253 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 8 | NO
12/12/2013 | 0 | 0 | 0.81614 | 0.81614 | 0 | 0 | 0 | 0 | 0.66978 | 0.66978 | 0 | 0 | 0.0084398 | 0.0084398 | 0 | 0 | 0 | 0 | 0.0069262 | 0.0069262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 11 | NO
13/12/2013 | 0 | 0 | 0.0015425 | 0.0015425 | 0 | 0 | 0 | 0 | 0.0012658 | 0.0012658 | 0 | 0 | 2.2851e-05 | 2.2851e-05 | 0 | 0 | 0 | 0 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | NO
14/12/2013 | 0 | 0 | 0.0015691 | 0.0015691 | 0 | 0 | 0 | 0 | 0.0012877 | 0.0012877 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 2 | NO
15/12/2013 | 0 | 0 | 0.0039 | 0.0039 | 0 | 0 | 0 | 0 | 0.0032006 | 0.0032006 | 0 | 0 | 4.9511e-05 | 4.9511e-05 | 0 | 0 | 0 | 0 | 4.0632e-05 | 4.0632e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | NO
16/12/2013 | 0.0028408 | 0.0028408 | 0.00036181 | 0.00036181 | 0 | 0 | 0 | 0 | 0.00080639 | 0.00080639 | 3.4857e-05 | 3.4857e-05 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | NO
17/12/2013 | 0 | 0 | 0.0065012 | 0.0065012 | 0 | 0 | 0 | 0 | 0.0053353 | 0.0053353 | 0 | 0 | 1.1426e-05 | 1.1426e-05 | 0 | 0 | 0 | 0 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 3 | NO
18/12/2013 | 0 | 0 | 0.00068173 | 0.00068173 | 0 | 0 | 0 | 0 | 0.00055947 | 0.00055947 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 2 | NO
19/12/2013 | 0 | 0 | 0.075139 | 0.075139 | 0 | 0 | 0 | 0 | 0.061664 | 0.061664 | 0 | 0 | 0.00036181 | 0.00036181 | 0 | 0 | 0 | 0 | 0.00029693 | 0.00029693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 45 | NO
20/12/2013 | 0 | 0 | 0.011845 | 0.011845 | 0 | 0 | 0 | 0 | 0.0097204 | 0.0097204 | 0 | 0 | 4.1894e-05 | 4.1894e-05 | 0 | 0 | 0 | 0 | 3.4381e-05 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 25 | NO
21/12/2013 | 0 | 0 | 0.00037324 | 0.00037324 | 0 | 0 | 0 | 0 | 0.0003063 | 0.0003063 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 23 | NO
22/12/2013 | 0 | 0 | 0.76553 | 0.76553 | 0 | 0 | 0 | 0 | 0.62824 | 0.62824 | 0 | 0 | 0.012633 | 0.012633 | 0 | 0 | 0 | 0 | 0.010367 | 0.010367 | 0 | 0 | 0.012172 | 0.012172 | 0 | 0 | 0 | 0 | 0.0099892 | 0.0099892 | 162 | 105 | NO
23/12/2013 | 0 | 0 | 0.051244 | 0.051244 | 0 | 0 | 0 | 0 | 0.042054 | 0.042054 | 0 | 0 | 0.00037324 | 0.00037324 | 0 | 0 | 0 | 0 | 0.0003063 | 0.0003063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 5 | NO
24/12/2013 | 0 | 0 | 0.06876 | 0.06876 | 0 | 0 | 0 | 0 | 0.056428 | 0.056428 | 0 | 0 | 0.0013749 | 0.0013749 | 0 | 0 | 0 | 0 | 0.0011283 | 0.0011283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1 | NO
25/12/2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1 | NO
26/12/2013 | 0 | 0 | 0.00041132 | 0.00041132 | 0 | 0 | 0 | 0 | 0.00033756 | 0.00033756 | 0 | 0 | 3.8086e-06 | 3.8086e-06 | 0 | 0 | 0 | 0 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 1 | NO
27/12/2013 | 0.14779 | 0.14779 | 0.0080437 | 0.0080437 | 0 | 0 | 0 | 0 | 0.033106 | 0.033106 | 0.0036948 | 0.0036948 | 3.8086e-05 | 3.8086e-05 | 0 | 0 | 0 | 0 | 0.00069387 | 0.00069387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | NO
28/12/2013 | 0 | 0 | 0.044385 | 0.044385 | 0 | 0 | 0 | 0 | 0.036425 | 0.036425 | 0 | 0 | 0.00034658 | 0.00034658 | 0 | 0 | 0 | 0 | 0.00028442 | 0.00028442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 14 | NO
29/12/2013 | 0 | 0 | 0.0051187 | 0.0051187 | 0 | 0 | 0 | 0 | 0.0042007 | 0.0042007 | 0 | 0 | 1.9043e-05 | 1.9043e-05 | 0 | 0 | 0 | 0 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | NO
30/12/2013 | 0 | 0 | 0.041928 | 0.041928 | 0 | 0 | 0 | 0 | 0.034409 | 0.034409 | 0 | 0 | 0.00054462 | 0.00054462 | 0 | 0 | 0 | 0 | 0.00044695 | 0.00044695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | NO
31/12/2013 | 0.37046 | 0.37046 | 0.0013977 | 0.0013977 | 0 | 0 | 0 | 0 | 0.067583 | 0.067583 | 0.010387 | 0.010387 | 1.5234e-05 | 1.5234e-05 | 0 | 0 | 0 | 0 | 0.0018753 | 0.0018753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 1 | NO
Contents
Contents

## 1d. STPIS MED Threshold
CitiPower Pty
STPIS Data Reporting
2013
MED Threshold
Table 1 MED Threshold
MED Threshold (Timed) year ending 31 December | 2.0175
Alpha - average of Ln(SAIDI) | -4.6863
Beta - Standard deviation of Ln(SAIDI) | 2.1553
X Beta from the mean | 2.5
Table 2 MED Calculation
Date | Network SAIDI All Events | Network SAIDI (after removing excluded events) | Ln (SAIDI)
1/01/2008 | 0.0020164 | 0.0020164 | -6.2065
2/01/2008 | 0.0016759 | 0.0016759 | -6.3914
3/01/2008 | 0.021562 | 0.021562 | -3.8368
4/01/2008 | 0.0039501 | 0.0039501 | -5.534
5/01/2008 | 0.021218 | 0.021218 | -3.8529
6/01/2008 | 0.0014577 | 0.0014577 | -6.5309
7/01/2008 | 0.0029221 | 0.0029221 | -5.8355
8/01/2008 | 0.0011636 | 0.0011636 | -6.7563
9/01/2008 | 0.033416 | 0.033416 | -3.3987
10/01/2008 | 0.40876 | 0.40876 | -0.89463
11/01/2008 | 0.06309 | 0.06309 | -2.7632
12/01/2008 | 0.005074 | 0.005074 | -5.2836
13/01/2008 | 0.00072061 | 0.00072061 | -7.2354
14/01/2008 | 0.00064458 | 0.00064458 | -7.3469
15/01/2008 | 0.11766 | 0.11766 | -2.14
16/01/2008 | 0.0012991 | 0.0012991 | -6.6461
17/01/2008 | 0.002261 | 0.002261 | -6.092
18/01/2008 | 0.0017123 | 0.0017123 | -6.3699
19/01/2008 | 0.16001 | 0.16001 | -1.8325
20/01/2008 | 0.0051467 | 0.0051467 | -5.2694
21/01/2008 | 0.0037353 | 0.0037353 | -5.5899
22/01/2008 | 0.0015933 | 0.0015933 | -6.442
23/01/2008 | 0.011692 | 0.011692 | -4.4489
24/01/2008 | 0.00056525 | 0.00056525 | -7.4782
25/01/2008 | 0.0016032 | 0.0016032 | -6.4358
26/01/2008 | 0.0019304 | 0.0019304 | -6.25
27/01/2008 | 0.00036691 | 0.00036691 | -7.9104
28/01/2008 | 0.0022808 | 0.0022808 | -6.0832
29/01/2008 | 0.0040989 | 0.0040989 | -5.497
30/01/2008 | 0.12988 | 0.12988 | -2.0411
31/01/2008 | 0.20028 | 0.20028 | -1.608
1/02/2008 | 0.003484 | 0.003484 | -5.6596
2/02/2008 | 0.0022412 | 0.0022412 | -6.1008
3/02/2008 | 0.0011305 | 0.0011305 | -6.7851
4/02/2008 | 0.053441 | 0.053441 | -2.9292
5/02/2008 | 0.0010611 | 0.0010611 | -6.8485
6/02/2008 | 0.069185 | 0.069185 | -2.671
7/02/2008 | 0.0030213 | 0.0030213 | -5.8021
8/02/2008 | 0.0014677 | 0.0014677 | -6.5241
9/02/2008 | 0.011136 | 0.011136 | -4.4975
10/02/2008 | 0.007411 | 0.007411 | -4.9048
11/02/2008 | 0.0095762 | 0.0095762 | -4.6485
12/02/2008 | 0.0016759 | 0.0016759 | -6.3914
13/02/2008 | 0.0020263 | 0.0020263 | -6.2015
14/02/2008 | 0.0029915 | 0.0029915 | -5.812
15/02/2008 | 0.00082639 | 0.00082639 | -7.0984
16/02/2008 | 0.0039865 | 0.0039865 | -5.5248
17/02/2008 | 0.57418 | 0.57418 | -0.55481
18/02/2008 | 0.0030279 | 0.0030279 | -5.7999
19/02/2008 | 0.0086539 | 0.0086539 | -4.7497
20/02/2008 | 0.019714 | 0.019714 | -3.9264
21/02/2008 | 0.011345 | 0.011345 | -4.479
22/02/2008 | 0.0011569 | 0.0011569 | -6.762
23/02/2008 | 0.0010875 | 0.0010875 | -6.8239
24/02/2008 | 0.0008363 | 0.0008363 | -7.0865
25/02/2008 | 0.0005983 | 0.0005983 | -7.4214
26/02/2008 | 0.0020263 | 0.0020263 | -6.2015
27/02/2008 | 0.0010016 | 0.0010016 | -6.9062
28/02/2008 | 0.0025717 | 0.0025717 | -5.9632
29/02/2008 | 0.0015999 | 0.0015999 | -6.4378
1/03/2008 | 0.0018048 | 0.0018048 | -6.3173
2/03/2008 | 0.28848 | 0.28848 | -1.2431
3/03/2008 | 0.0075598 | 0.0075598 | -4.8849
4/03/2008 | 0.016055 | 0.016055 | -4.1317
5/03/2008 | 0.29479 | 0.29479 | -1.2215
6/03/2008 | 0.0080259 | 0.0080259 | -4.8251
7/03/2008 | 0.0014313 | 0.0014313 | -6.5492
8/03/2008 | 0.0014016 | 0.0014016 | -6.5702
9/03/2008 | 0.10661 | 0.10661 | -2.2386
10/03/2008 | 0.015034 | 0.015034 | -4.1975
11/03/2008 | 0.014921 | 0.014921 | -4.205
12/03/2008 | 0.0012958 | 0.0012958 | -6.6486
13/03/2008 | 0.0028428 | 0.0028428 | -5.863
14/03/2008 | 0.072296 | 0.072296 | -2.627
15/03/2008 | 0.38791 | 0.38791 | -0.94699
16/03/2008 | 0.056003 | 0.056003 | -2.8824
17/03/2008 | 0.24968 | 0.24968 | -1.3876
18/03/2008 | 0.011427 | 0.011427 | -4.4718
19/03/2008 | 0.27676 | 0.27676 | -1.2846
20/03/2008 | 0.0060392 | 0.0060392 | -5.1095
21/03/2008 | 0.00027767 | 0.00027767 | -8.1891
22/03/2008 | 0.0007173 | 0.0007173 | -7.24
23/03/2008 | 0.00049253 | 0.00049253 | -7.616
24/03/2008 | 0.0038609 | 0.0038609 | -5.5569
25/03/2008 | 0.0069317 | 0.0069317 | -4.9716
26/03/2008 | 0.0010446 | 0.0010446 | -6.8642
27/03/2008 | 0.49526 | 0.49526 | -0.70268
28/03/2008 | 0.0050079 | 0.0050079 | -5.2967
29/03/2008 | 0.0012726 | 0.0012726 | -6.6667
30/03/2008 | 0.038182 | 0.038182 | -3.2654
31/03/2008 | 0.016058 | 0.016058 | -4.1315
1/04/2008 | 0.0045683 | 0.0045683 | -5.3886
2/04/2008 | 23.1001 | 23.1001 | 3.1398
3/04/2008 | 0.98901 | 0.98901 | -0.011052
4/04/2008 | 0.02342 | 0.02342 | -3.7542
5/04/2008 | 0.0093249 | 0.0093249 | -4.6751
6/04/2008 | 0.00046608 | 0.00046608 | -7.6711
7/04/2008 | 0.32881 | 0.32881 | -1.1123
8/04/2008 | 0.0014016 | 0.0014016 | -6.5702
9/04/2008 | 0.0028064 | 0.0028064 | -5.8759
10/04/2008 | 0.0047203 | 0.0047203 | -5.3559
11/04/2008 | 0.0055103 | 0.0055103 | -5.2011
12/04/2008 | 0.014075 | 0.014075 | -4.2634
13/04/2008 | 0.0012759 | 0.0012759 | -6.6641
14/04/2008 | 0.0010214 | 0.0010214 | -6.8866
15/04/2008 | 0.0019106 | 0.0019106 | -6.2603
16/04/2008 | 0.0096886 | 0.0096886 | -4.6368
17/04/2008 | 0.030173 | 0.030173 | -3.5008
18/04/2008 | 0.0015668 | 0.0015668 | -6.4587
19/04/2008 | 0.00084952 | 0.00084952 | -7.0708
20/04/2008 | 0.0011867 | 0.0011867 | -6.7366
21/04/2008 | 0.06698 | 0.06698 | -2.7034
22/04/2008 | 0.085862 | 0.085862 | -2.455
23/04/2008 | 0.28493 | 0.28493 | -1.2555
24/04/2008 | 0.0020263 | 0.0020263 | -6.2015
25/04/2008 | 0.0064524 | 0.0064524 | -5.0433
26/04/2008 | 0.0011007 | 0.0011007 | -6.8118
27/04/2008 | 0.0017519 | 0.0017519 | -6.347
28/04/2008 | 0.0091927 | 0.0091927 | -4.6893
29/04/2008 | 0.0016263 | 0.0016263 | -6.4214
30/04/2008 | 0.0078275 | 0.0078275 | -4.8501
1/05/2008 | 0.0086704 | 0.0086704 | -4.7478
2/05/2008 | 0.0013321 | 0.0013321 | -6.621
3/05/2008 | 0.016306 | 0.016306 | -4.1162
4/05/2008 | 0.0045782 | 0.0045782 | -5.3865
5/05/2008 | 0.01586 | 0.01586 | -4.144
6/05/2008 | 0.036146 | 0.036146 | -3.3202
7/05/2008 | 0.25008 | 0.25008 | -1.386
8/05/2008 | 0.0016197 | 0.0016197 | -6.4255
9/05/2008 | 0.0018445 | 0.0018445 | -6.2956
10/05/2008 | 0.0019437 | 0.0019437 | -6.2432
11/05/2008 | 0.0083399 | 0.0083399 | -4.7867
12/05/2008 | 0.0021056 | 0.0021056 | -6.1631
13/05/2008 | 0.0018247 | 0.0018247 | -6.3064
14/05/2008 | 0.2311 | 0.2311 | -1.4649
15/05/2008 | 0.015533 | 0.015533 | -4.1648
16/05/2008 | 0.014164 | 0.014164 | -4.257
17/05/2008 | 0.0037287 | 0.0037287 | -5.5917
18/05/2008 | 0.0010479 | 0.0010479 | -6.861
19/05/2008 | 0.026041 | 0.026041 | -3.6481
20/05/2008 | 0.0098076 | 0.0098076 | -4.6246
21/05/2008 | 0.22114 | 0.22114 | -1.5089
22/05/2008 | 0.0061153 | 0.0061153 | -5.097
23/05/2008 | 0.024494 | 0.024494 | -3.7093
24/05/2008 | 0.10324 | 0.10324 | -2.2707
25/05/2008 | 0.10972 | 0.10972 | -2.2098
26/05/2008 | 0.0015503 | 0.0015503 | -6.4693
27/05/2008 | 0.0021817 | 0.0021817 | -6.1277
28/05/2008 | 0.0032328 | 0.0032328 | -5.7344
29/05/2008 | 0.0041551 | 0.0041551 | -5.4834
30/05/2008 | 0.24443 | 0.24443 | -1.4088
31/05/2008 | 0.000833 | 0.000833 | -7.0905
1/06/2008 | 0.035776 | 0.035776 | -3.3305
2/06/2008 | 0.0040691 | 0.0040691 | -5.5043
3/06/2008 | 0.012951 | 0.012951 | -4.3466
4/06/2008 | 0.0026742 | 0.0026742 | -5.9241
5/06/2008 | 0.0023833 | 0.0023833 | -6.0393
6/06/2008 | 0.0010875 | 0.0010875 | -6.8239
7/06/2008 | 0.00076358 | 0.00076358 | -7.1775
8/06/2008 | 0.002889 | 0.002889 | -5.8468
9/06/2008 | 0.0013487 | 0.0013487 | -6.6086
10/06/2008 | 0.0086043 | 0.0086043 | -4.7555
11/06/2008 | 0.0060624 | 0.0060624 | -5.1057
12/06/2008 | 0.0093448 | 0.0093448 | -4.6729
13/06/2008 | 0.0035997 | 0.0035997 | -5.6269
14/06/2008 | 0.001385 | 0.001385 | -6.582
15/06/2008 | 0.0012594 | 0.0012594 | -6.6771
16/06/2008 | 0.0012264 | 0.0012264 | -6.7037
17/06/2008 | 0.0063632 | 0.0063632 | -5.0572
18/06/2008 | 0.049821 | 0.049821 | -2.9993
19/06/2008 | 0.051259 | 0.051259 | -2.9709
20/06/2008 | 0.0076424 | 0.0076424 | -4.874
21/06/2008 | 0.0029221 | 0.0029221 | -5.8355
22/06/2008 | 0.012935 | 0.012935 | -4.3478
23/06/2008 | 0.0032857 | 0.0032857 | -5.7182
24/06/2008 | 0.0074738 | 0.0074738 | -4.8963
25/06/2008 | 0.12499 | 0.12499 | -2.0795
26/06/2008 | 0.0031899 | 0.0031899 | -5.7478
27/06/2008 | 0.0015239 | 0.0015239 | -6.4865
28/06/2008 | 0.00119 | 0.00119 | -6.7338
29/06/2008 | 0.0028031 | 0.0028031 | -5.877
30/06/2008 | 0.0034708 | 0.0034708 | -5.6634
1/07/2008 | 0.0065747 | 0.0065747 | -5.0245
2/07/2008 | 0.0052128 | 0.0052128 | -5.2566
3/07/2008 | 0.0021155 | 0.0021155 | -6.1584
4/07/2008 | 0.0027667 | 0.0027667 | -5.8901
5/07/2008 | 0.0016594 | 0.0016594 | -6.4013
6/07/2008 | 0.0016065 | 0.0016065 | -6.4337
7/07/2008 | 0.0019337 | 0.0019337 | -6.2483
8/07/2008 | 0.0055136 | 0.0055136 | -5.2005
9/07/2008 | 0.37364 | 0.37364 | -0.98447
10/07/2008 | 0.52619 | 0.52619 | -0.64209
11/07/2008 | 0.0015503 | 0.0015503 | -6.4693
12/07/2008 | 0.00091894 | 0.00091894 | -6.9923
13/07/2008 | 0.0038047 | 0.0038047 | -5.5715
14/07/2008 | 0.023869 | 0.023869 | -3.7352
15/07/2008 | 0.0012264 | 0.0012264 | -6.7037
16/07/2008 | 0.012954 | 0.012954 | -4.3463
17/07/2008 | 0.0027634 | 0.0027634 | -5.8913
18/07/2008 | 0.013946 | 0.013946 | -4.2726
19/07/2008 | 0.0083531 | 0.0083531 | -4.7851
20/07/2008 | 2.403 | 2.403 | 0.87673
21/07/2008 | 0.019509 | 0.019509 | -3.9369
22/07/2008 | 0.0033981 | 0.0033981 | -5.6845
23/07/2008 | 0.0018048 | 0.0018048 | -6.3173
24/07/2008 | 0.11613 | 0.11613 | -2.1531
25/07/2008 | 0.090175 | 0.090175 | -2.406
26/07/2008 | 0.0099794 | 0.0099794 | -4.6072
27/07/2008 | 0.021595 | 0.021595 | -3.8353
28/07/2008 | 0.010092 | 0.010092 | -4.596
29/07/2008 | 0.0068061 | 0.0068061 | -4.9899
30/07/2008 | 0.01352 | 0.01352 | -4.3036
31/07/2008 | 0.011745 | 0.011745 | -4.4444
1/08/2008 | 0.0013784 | 0.0013784 | -6.5868
2/08/2008 | 0.008092 | 0.008092 | -4.8169
3/08/2008 | 0.0024957 | 0.0024957 | -5.9932
4/08/2008 | 0.026282 | 0.026282 | -3.6389
5/08/2008 | 0.0025122 | 0.0025122 | -5.9866
6/08/2008 | 0.049679 | 0.049679 | -3.0022
7/08/2008 | 0.31867 | 0.31867 | -1.1436
8/08/2008 | 0.0073978 | 0.0073978 | -4.9066
9/08/2008 | 0.0027304 | 0.0027304 | -5.9033
10/08/2008 | 0.87074 | 0.87074 | -0.13842
11/08/2008 | 0.44443 | 0.44443 | -0.81097
12/08/2008 | 0.0051434 | 0.0051434 | -5.27
13/08/2008 | 0.08608 | 0.08608 | -2.4525
14/08/2008 | 0.001623 | 0.001623 | -6.4235
15/08/2008 | 0.0018775 | 0.0018775 | -6.2778
16/08/2008 | 0.0056029 | 0.0056029 | -5.1845
17/08/2008 | 0.051831 | 0.051831 | -2.9598
18/08/2008 | 0.03257 | 0.03257 | -3.4244
19/08/2008 | 0.026464 | 0.026464 | -3.632
20/08/2008 | 0.064299 | 0.064299 | -2.7442
21/08/2008 | 0.0092258 | 0.0092258 | -4.6858
22/08/2008 | 0.0024494 | 0.0024494 | -6.0119
23/08/2008 | 0.013077 | 0.013077 | -4.3369
24/08/2008 | 0.0010875 | 0.0010875 | -6.8239
25/08/2008 | 0.053031 | 0.053031 | -2.9369
26/08/2008 | 0.0017619 | 0.0017619 | -6.3414
27/08/2008 | 0.0025684 | 0.0025684 | -5.9645
28/08/2008 | 0.00058178 | 0.00058178 | -7.4494
29/08/2008 | 0.0012363 | 0.0012363 | -6.6957
30/08/2008 | 0.00058178 | 0.00058178 | -7.4494
31/08/2008 | 0.43095 | 0.43095 | -0.84176
1/09/2008 | 0.0019271 | 0.0019271 | -6.2517
2/09/2008 | 0.002099 | 0.002099 | -6.1663
3/09/2008 | 0.0012528 | 0.0012528 | -6.6824
4/09/2008 | 0.0012098 | 0.0012098 | -6.7173
5/09/2008 | 0.028342 | 0.028342 | -3.5634
6/09/2008 | 0.0012098 | 0.0012098 | -6.7173
7/09/2008 | 0.0015668 | 0.0015668 | -6.4587
8/09/2008 | 0.0024692 | 0.0024692 | -6.0038
9/09/2008 | 0.0014247 | 0.0014247 | -6.5538
10/09/2008 | 0.0080193 | 0.0080193 | -4.8259
11/09/2008 | 0.19235 | 0.19235 | -1.6484
12/09/2008 | 0.0027271 | 0.0027271 | -5.9045
13/09/2008 | 0.0017354 | 0.0017354 | -6.3565
14/09/2008 | 0.00057186 | 0.00057186 | -7.4666
15/09/2008 | 0.0016891 | 0.0016891 | -6.3835
16/09/2008 | 0.0051765 | 0.0051765 | -5.2636
17/09/2008 | 0.0015007 | 0.0015007 | -6.5018
18/09/2008 | 0.0019635 | 0.0019635 | -6.233
19/09/2008 | 0.00066111 | 0.00066111 | -7.3216
20/09/2008 | 0.0059004 | 0.0059004 | -5.1327
21/09/2008 | 0.023036 | 0.023036 | -3.7707
22/09/2008 | 0.066025 | 0.066025 | -2.7177
23/09/2008 | 0.0012892 | 0.0012892 | -6.6538
24/09/2008 | 0.0021387 | 0.0021387 | -6.1476
25/09/2008 | 0.0015272 | 0.0015272 | -6.4843
26/09/2008 | 0.006588 | 0.006588 | -5.0225
27/09/2008 | 0.0041022 | 0.0041022 | -5.4962
28/09/2008 | 0.40893 | 0.40893 | -0.89422
29/09/2008 | 0.0016594 | 0.0016594 | -6.4013
30/09/2008 | 0.031218 | 0.031218 | -3.4668
1/10/2008 | 0.0025552 | 0.0025552 | -5.9696
2/10/2008 | 0.0015338 | 0.0015338 | -6.48
3/10/2008 | 0.020151 | 0.020151 | -3.9045
4/10/2008 | 0.00092886 | 0.00092886 | -6.9816
5/10/2008 | 0.0010512 | 0.0010512 | -6.8579
6/10/2008 | 0.019509 | 0.019509 | -3.9369
7/10/2008 | 0.0012958 | 0.0012958 | -6.6486
8/10/2008 | 0.001233 | 0.001233 | -6.6983
9/10/2008 | 0.0010412 | 0.0010412 | -6.8673
10/10/2008 | 0.0011437 | 0.0011437 | -6.7735
11/10/2008 | 0.0081449 | 0.0081449 | -4.8104
12/10/2008 | 0.33207 | 0.33207 | -1.1024
13/10/2008 | 0.0011702 | 0.0011702 | -6.7506
14/10/2008 | 0.0091365 | 0.0091365 | -4.6955
15/10/2008 | 0.0013189 | 0.0013189 | -6.6309
16/10/2008 | 0.005236 | 0.005236 | -5.2522
17/10/2008 | 0.0041088 | 0.0041088 | -5.4946
18/10/2008 | 2.5713 | 2.5713 | 0.94442
19/10/2008 | 0.00039997 | 0.00039997 | -7.8241
20/10/2008 | 0.0024725 | 0.0024725 | -6.0025
21/10/2008 | 0.26736 | 0.26736 | -1.3192
22/10/2008 | 0.0014346 | 0.0014346 | -6.5469
23/10/2008 | 0.0014412 | 0.0014412 | -6.5423
24/10/2008 | 0.0026676 | 0.0026676 | -5.9266
25/10/2008 | 0.20586 | 0.20586 | -1.5806
26/10/2008 | 0.0017387 | 0.0017387 | -6.3546
27/10/2008 | 0.0038708 | 0.0038708 | -5.5543
28/10/2008 | 0.0015602 | 0.0015602 | -6.4629
29/10/2008 | 0.035333 | 0.035333 | -3.3429
30/10/2008 | 0.17502 | 0.17502 | -1.7429
31/10/2008 | 0.00042972 | 0.00042972 | -7.7524
1/11/2008 | 0.00080655 | 0.00080655 | -7.1227
2/11/2008 | 0.0057186 | 0.0057186 | -5.164
3/11/2008 | 0.0031436 | 0.0031436 | -5.7624
4/11/2008 | 0.00084952 | 0.00084952 | -7.0708
5/11/2008 | 0.0015437 | 0.0015437 | -6.4736
6/11/2008 | 0.0076226 | 0.0076226 | -4.8766
7/11/2008 | 0.2317 | 0.2317 | -1.4623
8/11/2008 | 0.21511 | 0.21511 | -1.5366
9/11/2008 | 0.00078672 | 0.00078672 | -7.1476
10/11/2008 | 0.025506 | 0.025506 | -3.6689
11/11/2008 | 0.12822 | 0.12822 | -2.054
12/11/2008 | 0.002423 | 0.002423 | -6.0228
13/11/2008 | 0.214 | 0.214 | -1.5418
14/11/2008 | 0.017549 | 0.017549 | -4.0428
15/11/2008 | 0.00042641 | 0.00042641 | -7.7601
16/11/2008 | 0.012231 | 0.012231 | -4.4038
17/11/2008 | 0.010948 | 0.010948 | -4.5146
18/11/2008 | 0.00070408 | 0.00070408 | -7.2586
19/11/2008 | 0.019536 | 0.019536 | -3.9355
20/11/2008 | 0.0023172 | 0.0023172 | -6.0674
21/11/2008 | 0.0012693 | 0.0012693 | -6.6693
22/11/2008 | 0.0057021 | 0.0057021 | -5.1669
23/11/2008 | 0.0046178 | 0.0046178 | -5.3778
24/11/2008 | 0.0024527 | 0.0024527 | -6.0106
25/11/2008 | 0.0026411 | 0.0026411 | -5.9365
26/11/2008 | 0.00053219 | 0.00053219 | -7.5385
27/11/2008 | 0.0078606 | 0.0078606 | -4.8459
28/11/2008 | 0.00048261 | 0.00048261 | -7.6363
29/11/2008 | 0.0099827 | 0.0099827 | -4.6069
30/11/2008 | 0.00025783 | 0.00025783 | -8.2632
1/12/2008 | 0.017308 | 0.017308 | -4.0566
2/12/2008 | 0.0065681 | 0.0065681 | -5.0255
3/12/2008 | 0.0063533 | 0.0063533 | -5.0588
4/12/2008 | 0.0073019 | 0.0073019 | -4.9196
5/12/2008 | 0.0034874 | 0.0034874 | -5.6586
6/12/2008 | 0.0018544 | 0.0018544 | -6.2902
7/12/2008 | 0.1137 | 0.1137 | -2.1742
8/12/2008 | 0.0059665 | 0.0059665 | -5.1216
9/12/2008 | 0.002975 | 0.002975 | -5.8175
10/12/2008 | 0.0010875 | 0.0010875 | -6.8239
11/12/2008 | 0.38264 | 0.38264 | -0.96065
12/12/2008 | 0.0091828 | 0.0091828 | -4.6904
13/12/2008 | 0.32802 | 0.32802 | -1.1147
14/12/2008 | 0.088265 | 0.088265 | -2.4274
15/12/2008 | 0.042959 | 0.042959 | -3.1475
16/12/2008 | 0.0041584 | 0.0041584 | -5.4826
17/12/2008 | 0.0016627 | 0.0016627 | -6.3993
18/12/2008 | 0.00069416 | 0.00069416 | -7.2728
19/12/2008 | 0.036675 | 0.036675 | -3.3057
20/12/2008 | 0.001147 | 0.001147 | -6.7706
21/12/2008 | 0.15647 | 0.15647 | -1.8549
22/12/2008 | 0.4929 | 0.4929 | -0.70746
23/12/2008 | 0.0021089 | 0.0021089 | -6.1616
24/12/2008 | 0.0014049 | 0.0014049 | -6.5678
25/12/2008 | 0.00066772 | 0.00066772 | -7.3116
26/12/2008 | 0.0031105 | 0.0031105 | -5.773
27/12/2008 | 0.025324 | 0.025324 | -3.676
28/12/2008 | 0.0018445 | 0.0018445 | -6.2956
29/12/2008 | 0.00068755 | 0.00068755 | -7.2824
30/12/2008 | 0.11529 | 0.11529 | -2.1603
31/12/2008 | 0.0003603 | 0.0003603 | -7.9286
1/01/2009 | 0.00046573 | 0.00046573 | -7.6719
2/01/2009 | 0.0029879 | 0.0029879 | -5.8132
3/01/2009 | 0.00039685 | 0.00039685 | -7.8319
4/01/2009 | 0.00096426 | 0.00096426 | -6.9442
5/01/2009 | 0.00017383 | 0.00017383 | -8.6574
6/01/2009 | 0.00075107 | 0.00075107 | -7.194
7/01/2009 | 0.0072877 | 0.0072877 | -4.9216
8/01/2009 | 0.0091834 | 0.0091834 | -4.6904
9/01/2009 | 0 | 0
10/01/2009 | 0.00035422 | 0.00035422 | -7.9456
11/01/2009 | 0.0017744 | 0.0017744 | -6.3343
12/01/2009 | 0.00068548 | 0.00068548 | -7.2854
13/01/2009 | 0.017186 | 0.017186 | -4.0637
14/01/2009 | 1.2086 | 1.2086 | 0.18945
15/01/2009 | 0.011269 | 0.011269 | -4.4857
16/01/2009 | 0.067377 | 0.067377 | -2.6975
17/01/2009 | 0.00066252 | 0.00066252 | -7.3195
18/01/2009 | 0.00066908 | 0.00066908 | -7.3096
19/01/2009 | 0.0096688 | 0.0096688 | -4.6389
20/01/2009 | 0.1322 | 0.1322 | -2.0235
21/01/2009 | 0.0049623 | 0.0049623 | -5.3059
22/01/2009 | 0.33886 | 0.33886 | -1.0822
23/01/2009 | 0.001243 | 0.001243 | -6.6902
24/01/2009 | 0.0092916 | 0.0092916 | -4.6786
25/01/2009 | 0.0012463 | 0.0012463 | -6.6876
26/01/2009 | 0.15158 | 0.15158 | -1.8867
27/01/2009 | 0.05042 | 0.05042 | -2.9874
28/01/2009 | 2.9618 | 2.9618 | 1.0858
29/01/2009 | 6.8527 | 1.8066 | 0.59143
30/01/2009 | 26.2502 | 1.1634 | 0.15137
31/01/2009 | 0.11653 | 0.11653 | -2.1496
1/02/2009 | 0.014375 | 0.014375 | -4.2422
2/02/2009 | 0.088249 | 0.088249 | -2.4276
3/02/2009 | 0.032316 | 0.032316 | -3.4322
4/02/2009 | 0.34582 | 0.34582 | -1.0618
5/02/2009 | 0.046147 | 0.046147 | -3.0759
6/02/2009 | 0.016602 | 0.016602 | -4.0982
7/02/2009 | 0.28703 | 0.28703 | -1.2482
8/02/2009 | 0.1498 | 0.1498 | -1.8985
9/02/2009 | 0.0045031 | 0.0045031 | -5.403
10/02/2009 | 0.0051066 | 0.0051066 | -5.2772
11/02/2009 | 0.28716 | 0.28716 | -1.2477
12/02/2009 | 0.13124 | 0.13124 | -2.0307
13/02/2009 | 0.0015579 | 0.0015579 | -6.4644
14/02/2009 | 0.0021811 | 0.0021811 | -6.1279
15/02/2009 | 0.011853 | 0.011853 | -4.4352
16/02/2009 | 0.010197 | 0.010197 | -4.5857
17/02/2009 | 0.001489 | 0.001489 | -6.5096
18/02/2009 | 0.16972 | 0.16972 | -1.7736
19/02/2009 | 0.27519 | 0.27519 | -1.2903
20/02/2009 | 0.029981 | 0.029981 | -3.5072
21/02/2009 | 0.28893 | 0.28893 | -1.2416
22/02/2009 | 0.0015317 | 0.0015317 | -6.4814
23/02/2009 | 0.008921 | 0.008921 | -4.7193
24/02/2009 | 0.025477 | 0.025477 | -3.67
25/02/2009 | 0.34767 | 0.34767 | -1.0565
26/02/2009 | 0.0036537 | 0.0036537 | -5.612
27/02/2009 | 0.0091801 | 0.0091801 | -4.6907
28/02/2009 | 0.39658 | 0.39658 | -0.92489
1/03/2009 | 0.033697 | 0.033697 | -3.3904
2/03/2009 | 0.14107 | 0.14107 | -1.9585
3/03/2009 | 0.24816 | 0.24816 | -1.3937
4/03/2009 | 0.018636 | 0.018636 | -3.9827
5/03/2009 | 0.0231 | 0.0231 | -3.7679
6/03/2009 | 0.00092162 | 0.00092162 | -6.9894
7/03/2009 | 0.24051 | 0.24051 | -1.425
8/03/2009 | 0.0025878 | 0.0025878 | -5.957
9/03/2009 | 0.12439 | 0.12439 | -2.0843
10/03/2009 | 0.011214 | 0.011214 | -4.4906
11/03/2009 | 0.0049459 | 0.0049459 | -5.3092
12/03/2009 | 0.018619 | 0.018619 | -3.9836
13/03/2009 | 0.054379 | 0.054379 | -2.9118
14/03/2009 | 0.55121 | 0.55121 | -0.59563
15/03/2009 | 0.0022467 | 0.0022467 | -6.0983
16/03/2009 | 0.070164 | 0.070164 | -2.6569
17/03/2009 | 0.003939 | 0.003939 | -5.5368
18/03/2009 | 0.0019088 | 0.0019088 | -6.2613
19/03/2009 | 0.28901 | 0.28901 | -1.2413
20/03/2009 | 0.0066383 | 0.0066383 | -5.0149
21/03/2009 | 0.03777 | 0.03777 | -3.2762
22/03/2009 | 0.0025582 | 0.0025582 | -5.9684
23/03/2009 | 0.0020302 | 0.0020302 | -6.1996
24/03/2009 | 0.0012266 | 0.0012266 | -6.7035
25/03/2009 | 0.0033618 | 0.0033618 | -5.6953
26/03/2009 | 0.0016858 | 0.0016858 | -6.3855
27/03/2009 | 0.574 | 0.574 | -0.55513
28/03/2009 | 0.0021351 | 0.0021351 | -6.1492
29/03/2009 | 0.0027288 | 0.0027288 | -5.9039
30/03/2009 | 0.003306 | 0.003306 | -5.712
31/03/2009 | 0.0006166 | 0.0006166 | -7.3913
1/04/2009 | 0.0016825 | 0.0016825 | -6.3875
2/04/2009 | 0.0046934 | 0.0046934 | -5.3616
3/04/2009 | 0.62363 | 0.62363 | -0.4722
4/04/2009 | 0.17977 | 0.17977 | -1.7161
5/04/2009 | 0.3197 | 0.3197 | -1.1404
6/04/2009 | 0.02963 | 0.02963 | -3.519
7/04/2009 | 0.00067892 | 0.00067892 | -7.295
8/04/2009 | 0.011007 | 0.011007 | -4.5092
9/04/2009 | 0.000551 | 0.000551 | -7.5038
10/04/2009 | 0.0022401 | 0.0022401 | -6.1012
11/04/2009 | 0.017094 | 0.017094 | -4.069
12/04/2009 | 0.00082651 | 0.00082651 | -7.0983
13/04/2009 | 0.021148 | 0.021148 | -3.8562
14/04/2009 | 0.028459 | 0.028459 | -3.5593
15/04/2009 | 0.97335 | 0.97335 | -0.02701
16/04/2009 | 0.0015513 | 0.0015513 | -6.4686
17/04/2009 | 0.025097 | 0.025097 | -3.685
18/04/2009 | 0.0073894 | 0.0073894 | -4.9077
19/04/2009 | 0.0045687 | 0.0045687 | -5.3885
20/04/2009 | 0.011765 | 0.011765 | -4.4427
21/04/2009 | 0.0027583 | 0.0027583 | -5.8931
22/04/2009 | 0.0014693 | 0.0014693 | -6.5229
23/04/2009 | 0.18286 | 0.18286 | -1.699
24/04/2009 | 0.0010331 | 0.0010331 | -6.8752
25/04/2009 | 0.0015841 | 0.0015841 | -6.4477
26/04/2009 | 0.011319 | 0.011319 | -4.4813
27/04/2009 | 0.0011709 | 0.0011709 | -6.75
28/04/2009 | 0.0034503 | 0.0034503 | -5.6693
29/04/2009 | 0.012716 | 0.012716 | -4.3649
30/04/2009 | 0.002942 | 0.002942 | -5.8287
1/05/2009 | 0.0034766 | 0.0034766 | -5.6617
2/05/2009 | 0.27181 | 0.27181 | -1.3027
3/05/2009 | 0.0013939 | 0.0013939 | -6.5756
4/05/2009 | 0.0099312 | 0.0099312 | -4.6121
5/05/2009 | 0.00044277 | 0.00044277 | -7.7225
6/05/2009 | 0.0005674 | 0.0005674 | -7.4744
7/05/2009 | 0.11793 | 0.11793 | -2.1377
8/05/2009 | 0.0054051 | 0.0054051 | -5.2204
9/05/2009 | 0.002696 | 0.002696 | -5.916
10/05/2009 | 0.0015054 | 0.0015054 | -6.4987
11/05/2009 | 0.057872 | 0.057872 | -2.8495
12/05/2009 | 0.0020499 | 0.0020499 | -6.19
13/05/2009 | 0.0018432 | 0.0018432 | -6.2962
14/05/2009 | 0.097524 | 0.097524 | -2.3277
15/05/2009 | 0.0021483 | 0.0021483 | -6.1431
16/05/2009 | 0.00016727 | 0.00016727 | -8.6959
17/05/2009 | 0.0028075 | 0.0028075 | -5.8755
18/05/2009 | 0.0054772 | 0.0054772 | -5.2072
19/05/2009 | 0.00096754 | 0.00096754 | -6.9408
20/05/2009 | 0.010187 | 0.010187 | -4.5866
21/05/2009 | 0.0015284 | 0.0015284 | -6.4835
22/05/2009 | 0.0099804 | 0.0099804 | -4.6071
23/05/2009 | 0.00090522 | 0.00090522 | -7.0073
24/05/2009 | 0.0023713 | 0.0023713 | -6.0443
25/05/2009 | 0.014333 | 0.014333 | -4.2452
26/05/2009 | 0.0024041 | 0.0024041 | -6.0306
27/05/2009 | 0.013093 | 0.013093 | -4.3357
28/05/2009 | 0.0011643 | 0.0011643 | -6.7556
29/05/2009 | 0.011653 | 0.011653 | -4.4522
30/05/2009 | 0.016707 | 0.016707 | -4.0919
31/05/2009 | 0.17477 | 0.17477 | -1.7443
1/06/2009 | 0.0071434 | 0.0071434 | -4.9416
2/06/2009 | 0.00070187 | 0.00070187 | -7.2618
3/06/2009 | 0.0020499 | 0.0020499 | -6.19
4/06/2009 | 0.00057068 | 0.00057068 | -7.4687
5/06/2009 | 0.48726 | 0.48726 | -0.71895
6/06/2009 | 0.0016891 | 0.0016891 | -6.3836
7/06/2009 | 0.031768 | 0.031768 | -3.4493
8/06/2009 | 0.0066284 | 0.0066284 | -5.0164
9/06/2009 | 0.0036078 | 0.0036078 | -5.6247
10/06/2009 | 0.17847 | 0.17847 | -1.7233
11/06/2009 | 0.030358 | 0.030358 | -3.4947
12/06/2009 | 0.031184 | 0.031184 | -3.4678
13/06/2009 | 0.037763 | 0.037763 | -3.2764
14/06/2009 | 0.023608 | 0.023608 | -3.7462
15/06/2009 | 0.013831 | 0.013831 | -4.2809
16/06/2009 | 0.0032601 | 0.0032601 | -5.726
17/06/2009 | 0.0041948 | 0.0041948 | -5.4739
18/06/2009 | 0.0050345 | 0.0050345 | -5.2914
19/06/2009 | 0.00060348 | 0.00060348 | -7.4128
20/06/2009 | 0.0017612 | 0.0017612 | -6.3417
21/06/2009 | 0.004513 | 0.004513 | -5.4008
22/06/2009 | 0.00056084 | 0.00056084 | -7.4861
23/06/2009 | 0.025438 | 0.025438 | -3.6715
24/06/2009 | 0.0034995 | 0.0034995 | -5.6551
25/06/2009 | 0.041037 | 0.041037 | -3.1933
26/06/2009 | 0.002614 | 0.002614 | -5.9469
27/06/2009 | 0.18134 | 0.18134 | -1.7074
28/06/2009 | 0.018688 | 0.018688 | -3.9799
29/06/2009 | 0.028134 | 0.028134 | -3.5708
30/06/2009 | 0.0015284 | 0.0015284 | -6.4835
1/07/2009 | 0.0021679 | 0.0021679 | -6.134
2/07/2009 | 0.0028239 | 0.0028239 | -5.8696
3/07/2009 | 0.0020171 | 0.0020171 | -6.2061
4/07/2009 | 0.20772 | 0.20772 | -1.5716
5/07/2009 | 0.0044605 | 0.0044605 | -5.4125
6/07/2009 | 0.020335 | 0.020335 | -3.8954
7/07/2009 | 0.024359 | 0.024359 | -3.7149
8/07/2009 | 0.0053592 | 0.0053592 | -5.2289
9/07/2009 | 0.011401 | 0.011401 | -4.4741
10/07/2009 | 0.9244 | 0.9244 | -0.078606
11/07/2009 | 0.012024 | 0.012024 | -4.4209
12/07/2009 | 0.001817 | 0.001817 | -6.3106
13/07/2009 | 0.0047295 | 0.0047295 | -5.3539
14/07/2009 | 0.0085865 | 0.0085865 | -4.7576
15/07/2009 | 0.017619 | 0.017619 | -4.0388
16/07/2009 | 0.011325 | 0.011325 | -4.4807
17/07/2009 | 0.16232 | 0.16232 | -1.8182
18/07/2009 | 0.8743 | 0.8743 | -0.13433
19/07/2009 | 0.03535 | 0.03535 | -3.3425
20/07/2009 | 0.0010167 | 0.0010167 | -6.8912
21/07/2009 | 0.0034536 | 0.0034536 | -5.6683
22/07/2009 | 0.063428 | 0.063428 | -2.7579
23/07/2009 | 0.0052641 | 0.0052641 | -5.2469
24/07/2009 | 0.021082 | 0.021082 | -3.8593
25/07/2009 | 0.0033027 | 0.0033027 | -5.713
26/07/2009 | 0.0048574 | 0.0048574 | -5.3273
27/07/2009 | 0.00036734 | 0.00036734 | -7.9092
28/07/2009 | 0.015894 | 0.015894 | -4.1418
29/07/2009 | 0.00037718 | 0.00037718 | -7.8828
30/07/2009 | 0.0072844 | 0.0072844 | -4.922
31/07/2009 | 0.0009413 | 0.0009413 | -6.9683
1/08/2009 | 0.0008429 | 0.0008429 | -7.0787
2/08/2009 | 0.043247 | 0.043247 | -3.1408
3/08/2009 | 0.028983 | 0.028983 | -3.541
4/08/2009 | 0.0010167 | 0.0010167 | -6.8912
5/08/2009 | 0.004126 | 0.004126 | -5.4905
6/08/2009 | 0.0021023 | 0.0021023 | -6.1647
7/08/2009 | 0.017691 | 0.017691 | -4.0347
8/08/2009 | 0.22528 | 0.22528 | -1.4904
9/08/2009 | 0.0075468 | 0.0075468 | -4.8866
10/08/2009 | 0.0025878 | 0.0025878 | -5.957
11/08/2009 | 0.27816 | 0.27816 | -1.2796
12/08/2009 | 0.0066481 | 0.0066481 | -5.0134
13/08/2009 | 0.0014825 | 0.0014825 | -6.5141
14/08/2009 | 0.0052313 | 0.0052313 | -5.2531
15/08/2009 | 0.14083 | 0.14083 | -1.9602
16/08/2009 | 0.24884 | 0.24884 | -1.3909
17/08/2009 | 0.0024894 | 0.0024894 | -5.9957
18/08/2009 | 0.0013775 | 0.0013775 | -6.5875
19/08/2009 | 0.050837 | 0.050837 | -2.9791
20/08/2009 | 8.8554e-05 | 8.8554e-05 | -9.3319
21/08/2009 | 0.33682 | 0.33682 | -1.0882
22/08/2009 | 0.018203 | 0.018203 | -4.0062
23/08/2009 | 0.0065661 | 0.0065661 | -5.0258
24/08/2009 | 0.072116 | 0.072116 | -2.6295
25/08/2009 | 0.036711 | 0.036711 | -3.3047
26/08/2009 | 0.0087177 | 0.0087177 | -4.7424
27/08/2009 | 0.0093933 | 0.0093933 | -4.6678
28/08/2009 | 0.047764 | 0.047764 | -3.0415
29/08/2009 | 0.011696 | 0.011696 | -4.4485
30/08/2009 | 0.0049754 | 0.0049754 | -5.3032
31/08/2009 | 0.0012463 | 0.0012463 | -6.6876
1/09/2009 | 0.26368 | 0.26368 | -1.333
2/09/2009 | 0.0034307 | 0.0034307 | -5.675
3/09/2009 | 0.0017416 | 0.0017416 | -6.353
4/09/2009 | 0.0021581 | 0.0021581 | -6.1385
5/09/2009 | 0.06939 | 0.06939 | -2.668
6/09/2009 | 0.011427 | 0.011427 | -4.4718
7/09/2009 | 0.0032273 | 0.0032273 | -5.7361
8/09/2009 | 0.00066908 | 0.00066908 | -7.3096
9/09/2009 | 0.0045458 | 0.0045458 | -5.3936
10/09/2009 | 0.00080355 | 0.00080355 | -7.1265
11/09/2009 | 0.0012234 | 0.0012234 | -6.7062
12/09/2009 | 0.22584 | 0.22584 | -1.4879
13/09/2009 | 0.0028042 | 0.0028042 | -5.8766
14/09/2009 | 0.00039685 | 0.00039685 | -7.8319
15/09/2009 | 0.0053231 | 0.0053231 | -5.2357
16/09/2009 | 0.0018432 | 0.0018432 | -6.2962
17/09/2009 | 0.013385 | 0.013385 | -4.3136
18/09/2009 | 0.05572 | 0.05572 | -2.8874
19/09/2009 | 0.001348 | 0.001348 | -6.6091
20/09/2009 | 0.0013119 | 0.0013119 | -6.6363
21/09/2009 | 0.0019712 | 0.0019712 | -6.2291
22/09/2009 | 0.013896 | 0.013896 | -4.2761
23/09/2009 | 0.0048082 | 0.0048082 | -5.3374
24/09/2009 | 0.021919 | 0.021919 | -3.8204
25/09/2009 | 0.015307 | 0.015307 | -4.1795
26/09/2009 | 0.24202 | 0.24202 | -1.4188
27/09/2009 | 0.57173 | 0.57173 | -0.55908
28/09/2009 | 0.026884 | 0.026884 | -3.6162
29/09/2009 | 0.011361 | 0.011361 | -4.4776
30/09/2009 | 0.1751 | 0.1751 | -1.7424
1/10/2009 | 0.0015021 | 0.0015021 | -6.5009
2/10/2009 | 0.00059036 | 0.00059036 | -7.4348
3/10/2009 | 0.00086586 | 0.00086586 | -7.0518
4/10/2009 | 0.00060348 | 0.00060348 | -7.4128
5/10/2009 | 0.001594 | 0.001594 | -6.4415
6/10/2009 | 0.0041588 | 0.0041588 | -5.4825
7/10/2009 | 0.0026599 | 0.0026599 | -5.9295
8/10/2009 | 0.00026566 | 0.00026566 | -8.2333
9/10/2009 | 0.15325 | 0.15325 | -1.8757
10/10/2009 | 0.006694 | 0.006694 | -5.0065
11/10/2009 | 0.00026238 | 0.00026238 | -8.2457
12/10/2009 | 0.00086586 | 0.00086586 | -7.0518
13/10/2009 | 0.0011315 | 0.0011315 | -6.7842
14/10/2009 | 0.0039423 | 0.0039423 | -5.536
15/10/2009 | 0.044533 | 0.044533 | -3.1115
16/10/2009 | 0.00010167 | 0.00010167 | -9.1937
17/10/2009 | 0.019649 | 0.019649 | -3.9297
18/10/2009 | 0.0012398 | 0.0012398 | -6.6928
19/10/2009 | 0.083002 | 0.083002 | -2.4889
20/10/2009 | 0.0015546 | 0.0015546 | -6.4665
21/10/2009 | 0.0048508 | 0.0048508 | -5.3286
22/10/2009 | 0.0030305 | 0.0030305 | -5.799
23/10/2009 | 0.19735 | 0.19735 | -1.6228
24/10/2009 | 0.016438 | 0.016438 | -4.1081
25/10/2009 | 0.0022893 | 0.0022893 | -6.0795
26/10/2009 | 0.021758 | 0.021758 | -3.8278
27/10/2009 | 0.22138 | 0.22138 | -1.5079
28/10/2009 | 0.0015513 | 0.0015513 | -6.4686
29/10/2009 | 0.49335 | 0.49335 | -0.70655
30/10/2009 | 0.27094 | 0.27094 | -1.3059
31/10/2009 | 0.23513 | 0.23513 | -1.4476
1/11/2009 | 0.00038046 | 0.00038046 | -7.8741
2/11/2009 | 0.0027386 | 0.0027386 | -5.9003
3/11/2009 | 0.0018301 | 0.0018301 | -6.3034
4/11/2009 | 0.030741 | 0.030741 | -3.4821
5/11/2009 | 0.10555 | 0.10555 | -2.2486
6/11/2009 | 0.0010299 | 0.0010299 | -6.8783
7/11/2009 | 0.0013382 | 0.0013382 | -6.6165
8/11/2009 | 0.13981 | 0.13981 | -1.9675
9/11/2009 | 0.15856 | 0.15856 | -1.8416
10/11/2009 | 0.071365 | 0.071365 | -2.6399
11/11/2009 | 0.031463 | 0.031463 | -3.4589
12/11/2009 | 0.0012988 | 0.0012988 | -6.6463
13/11/2009 | 0.017337 | 0.017337 | -4.0549
14/11/2009 | 0.0076452 | 0.0076452 | -4.8737
15/11/2009 | 0.34649 | 0.34649 | -1.0599
16/11/2009 | 0.0070089 | 0.0070089 | -4.9606
17/11/2009 | 0.0035618 | 0.0035618 | -5.6375
18/11/2009 | 0.00083635 | 0.00083635 | -7.0865
19/11/2009 | 0.026064 | 0.026064 | -3.6472
20/11/2009 | 0.016497 | 0.016497 | -4.1046
21/11/2009 | 0.31766 | 0.31766 | -1.1468
22/11/2009 | 0.014369 | 0.014369 | -4.2427
23/11/2009 | 0.013847 | 0.013847 | -4.2797
24/11/2009 | 0.00061988 | 0.00061988 | -7.386
25/11/2009 | 0.013054 | 0.013054 | -4.3387
26/11/2009 | 0.43229 | 0.43229 | -0.83866
27/11/2009 | 0.00010823 | 0.00010823 | -9.1312
28/11/2009 | 0.0028731 | 0.0028731 | -5.8524
29/11/2009 | 1.1293 | 1.1293 | 0.12159
30/11/2009 | 0.0022926 | 0.0022926 | -6.0781
1/12/2009 | 0.0013382 | 0.0013382 | -6.6165
2/12/2009 | 0.0080683 | 0.0080683 | -4.8198
3/12/2009 | 1.9166 | 1.9166 | 0.65056
4/12/2009 | 0.0015251 | 0.0015251 | -6.4857
5/12/2009 | 0.0058282 | 0.0058282 | -5.1451
6/12/2009 | 0 | 0
7/12/2009 | 0.0014989 | 0.0014989 | -6.503
8/12/2009 | 0.43194 | 0.43194 | -0.83947
9/12/2009 | 0.0088357 | 0.0088357 | -4.729
10/12/2009 | 0.0011545 | 0.0011545 | -6.7641
11/12/2009 | 0.0019154 | 0.0019154 | -6.2578
12/12/2009 | 0.0013513 | 0.0013513 | -6.6067
13/12/2009 | 0.042335 | 0.042335 | -3.1621
14/12/2009 | 0.00012463 | 0.00012463 | -8.9901
15/12/2009 | 0.0091768 | 0.0091768 | -4.6911
16/12/2009 | 0.0096196 | 0.0096196 | -4.644
17/12/2009 | 0.0097869 | 0.0097869 | -4.6267
18/12/2009 | 0.001371 | 0.001371 | -6.5923
19/12/2009 | 0.0052969 | 0.0052969 | -5.2406
20/12/2009 | 0.019498 | 0.019498 | -3.9374
21/12/2009 | 0.0005674 | 0.0005674 | -7.4744
22/12/2009 | 0.034936 | 0.034936 | -3.3542
23/12/2009 | 0.25835 | 0.25835 | -1.3535
24/12/2009 | 0.003611 | 0.003611 | -5.6238
25/12/2009 | 0.003165 | 0.003165 | -5.7556
26/12/2009 | 0.014113 | 0.014113 | -4.2607
27/12/2009 | 0.001243 | 0.001243 | -6.6902
28/12/2009 | 0.0040997 | 0.0040997 | -5.4968
29/12/2009 | 0.029915 | 0.029915 | -3.5094
30/12/2009 | 0.0068121 | 0.0068121 | -4.9891
31/12/2009 | 1.1528 | 1.1528 | 0.1422
1/01/2010 | 0.34459 | 0.34459 | -1.0654
2/01/2010 | 0.045765 | 0.045765 | -3.0842
3/01/2010 | 0.065871 | 0.065871 | -2.7201
4/01/2010 | 0.0010839 | 0.0010839 | -6.8272
5/01/2010 | 0.015495 | 0.015495 | -4.1673
6/01/2010 | 0.30898 | 0.30898 | -1.1745
7/01/2010 | 0.037418 | 0.037418 | -3.2856
8/01/2010 | 0.0060762 | 0.0060762 | -5.1034
9/01/2010 | 0.2469 | 0.2469 | -1.3988
10/01/2010 | 0.0029378 | 0.0029378 | -5.8301
11/01/2010 | 0.35268 | 0.35268 | -1.0422
12/01/2010 | 0.083701 | 0.083701 | -2.4805
13/01/2010 | 0.52173 | 0.52173 | -0.65061
14/01/2010 | 0.0012748 | 0.0012748 | -6.665
15/01/2010 | 0.0015886 | 0.0015886 | -6.4449
16/01/2010 | 0.011233 | 0.011233 | -4.4889
17/01/2010 | 0.027213 | 0.027213 | -3.604
18/01/2010 | 0.17767 | 0.17767 | -1.7279
19/01/2010 | 0.38523 | 0.38523 | -0.95393
20/01/2010 | 0.00014236 | 0.00014236 | -8.8572
21/01/2010 | 0.0018798 | 0.0018798 | -6.2766
22/01/2010 | 0.0012974 | 0.0012974 | -6.6474
23/01/2010 | 0.0013751 | 0.0013751 | -6.5893
24/01/2010 | 0.011272 | 0.011272 | -4.4854
25/01/2010 | 0.040514 | 0.040514 | -3.2061
26/01/2010 | 0.0204 | 0.0204 | -3.8922
27/01/2010 | 0.0010062 | 0.0010062 | -6.9015
28/01/2010 | 0.30962 | 0.30962 | -1.1724
29/01/2010 | 0.00562 | 0.00562 | -5.1814
30/01/2010 | 0.10263 | 0.10263 | -2.2766
31/01/2010 | 1.0214 | 1.0214 | 0.021174
1/02/2010 | 0.77305 | 0.77305 | -0.25741
2/02/2010 | 0.0337 | 0.0337 | -3.3902
3/02/2010 | 0.017591 | 0.017591 | -4.0404
4/02/2010 | 0.013961 | 0.013961 | -4.2715
5/02/2010 | 0.019241 | 0.019241 | -3.9507
6/02/2010 | 0.011292 | 0.011292 | -4.4837
7/02/2010 | 0.0015174 | 0.0015174 | -6.4907
8/02/2010 | 0.35185 | 0.35185 | -1.0446
9/02/2010 | 0.016378 | 0.016378 | -4.1118
10/02/2010 | 0.0089201 | 0.0089201 | -4.7194
11/02/2010 | 1.0052 | 1.0052 | 0.0052116
12/02/2010 | 0.008176 | 0.008176 | -4.8066
13/02/2010 | 0.0082245 | 0.0082245 | -4.8006
14/02/2010 | 0.0035655 | 0.0035655 | -5.6365
15/02/2010 | 0.0012521 | 0.0012521 | -6.6829
16/02/2010 | 0.031872 | 0.031872 | -3.446
17/02/2010 | 0.00067621 | 0.00067621 | -7.299
18/02/2010 | 0.014158 | 0.014158 | -4.2575
19/02/2010 | 0.52119 | 0.52119 | -0.65164
20/02/2010 | 0.089256 | 0.089256 | -2.4162
21/02/2010 | 0.10994 | 0.10994 | -2.2078
22/02/2010 | 0.0018119 | 0.0018119 | -6.3134
23/02/2010 | 0.2156 | 0.2156 | -1.5343
24/02/2010 | 0.00039472 | 0.00039472 | -7.8373
25/02/2010 | 0.0049729 | 0.0049729 | -5.3038
26/02/2010 | 0.49488 | 0.49488 | -0.70344
27/02/2010 | 0.0024622 | 0.0024622 | -6.0067
28/02/2010 | 0.023127 | 0.023127 | -3.7668
1/03/2010 | 0.00094152 | 0.00094152 | -6.968
2/03/2010 | 0.012974 | 0.012974 | -4.3448
3/03/2010 | 0.0014624 | 0.0014624 | -6.5277
4/03/2010 | 0.047183 | 0.047183 | -3.0537
5/03/2010 | 0.032105 | 0.032105 | -3.4387
6/03/2010 | 8.1857 | 8.1857 | 2.1024
7/03/2010 | 0.089952 | 0.089952 | -2.4085
8/03/2010 | 0.22051 | 0.22051 | -1.5118
9/03/2010 | 0.098542 | 0.098542 | -2.3173
10/03/2010 | 0.0008671 | 0.0008671 | -7.0504
11/03/2010 | 0.028009 | 0.028009 | -3.5752
12/03/2010 | 0 | 0
13/03/2010 | 0.011143 | 0.011143 | -4.497
14/03/2010 | 0.0022098 | 0.0022098 | -6.1148
15/03/2010 | 0.0034263 | 0.0034263 | -5.6763
16/03/2010 | 0.082517 | 0.082517 | -2.4948
17/03/2010 | 0.0013265 | 0.0013265 | -6.6252
18/03/2010 | 0.0095316 | 0.0095316 | -4.6531
19/03/2010 | 0.065071 | 0.065071 | -2.7323
20/03/2010 | 0.00093828 | 0.00093828 | -6.9715
21/03/2010 | 0.17425 | 0.17425 | -1.7473
22/03/2010 | 0.00052414 | 0.00052414 | -7.5537
23/03/2010 | 4.199 | 4.199 | 1.4348
24/03/2010 | 0.00043031 | 0.00043031 | -7.751
25/03/2010 | 0.0042773 | 0.0042773 | -5.4544
26/03/2010 | 0.015423 | 0.015423 | -4.1719
27/03/2010 | 0.0020513 | 0.0020513 | -6.1893
28/03/2010 | 0.75674 | 0.75674 | -0.27874
29/03/2010 | 0.0035816 | 0.0035816 | -5.6319
30/03/2010 | 0.0016371 | 0.0016371 | -6.4148
31/03/2010 | 0.0093828 | 0.0093828 | -4.6689
1/04/2010 | 0.00093505 | 0.00093505 | -6.9749
2/04/2010 | 0.058038 | 0.058038 | -2.8467
3/04/2010 | 0.011809 | 0.011809 | -4.4389
4/04/2010 | 0.00062768 | 0.00062768 | -7.3735
5/04/2010 | 0.0011001 | 0.0011001 | -6.8124
6/04/2010 | 0 | 0
7/04/2010 | 0.011958 | 0.011958 | -4.4263
8/04/2010 | 0.00017795 | 0.00017795 | -8.634
9/04/2010 | 0.0074836 | 0.0074836 | -4.895
10/04/2010 | 0.0082795 | 0.0082795 | -4.794
11/04/2010 | 0.16906 | 0.16906 | -1.7775
12/04/2010 | 0.00081533 | 0.00081533 | -7.1119
13/04/2010 | 0.0011356 | 0.0011356 | -6.7806
14/04/2010 | 0.020801 | 0.020801 | -3.8728
15/04/2010 | 0.00063738 | 0.00063738 | -7.3581
16/04/2010 | 0.00024589 | 0.00024589 | -8.3106
17/04/2010 | 0.00072798 | 0.00072798 | -7.2252
18/04/2010 | 0.74025 | 0.74025 | -0.30077
19/04/2010 | 0 | 0
20/04/2010 | 0.022224 | 0.022224 | -3.8066
21/04/2010 | 0.00083151 | 0.00083151 | -7.0923
22/04/2010 | 0.14055 | 0.14055 | -1.9622
23/04/2010 | 0.0039796 | 0.0039796 | -5.5266
24/04/2010 | 0.0026531 | 0.0026531 | -5.932
25/04/2010 | 0.0025301 | 0.0025301 | -5.9795
26/04/2010 | 0.00012618 | 0.00012618 | -8.9778
27/04/2010 | 0.036716 | 0.036716 | -3.3045
28/04/2010 | 0.0075742 | 0.0075742 | -4.883
29/04/2010 | 0.0011098 | 0.0011098 | -6.8036
30/04/2010 | 0.00063415 | 0.00063415 | -7.3632
1/05/2010 | 0.050227 | 0.050227 | -2.9912
2/05/2010 | 0.0012942 | 0.0012942 | -6.6499
3/05/2010 | 0.1258 | 0.1258 | -2.0731
4/05/2010 | 0.0020804 | 0.0020804 | -6.1752
5/05/2010 | 0.0023554 | 0.0023554 | -6.051
6/05/2010 | 0.092427 | 0.092427 | -2.3813
7/05/2010 | 0.0043193 | 0.0043193 | -5.4447
8/05/2010 | 0.018157 | 0.018157 | -4.0087
9/05/2010 | 0.002158 | 0.002158 | -6.1386
10/05/2010 | 0.0012456 | 0.0012456 | -6.6881
11/05/2010 | 0.0069271 | 0.0069271 | -4.9723
12/05/2010 | 0.0019542 | 0.0019542 | -6.2378
13/05/2010 | 0.00022325 | 0.00022325 | -8.4072
14/05/2010 | 0.024259 | 0.024259 | -3.719
15/05/2010 | 0.014757 | 0.014757 | -4.216
16/05/2010 | 0.0023263 | 0.0023263 | -6.0635
17/05/2010 | 0.021237 | 0.021237 | -3.852
18/05/2010 | 0.038932 | 0.038932 | -3.2459
19/05/2010 | 0.020522 | 0.020522 | -3.8862
20/05/2010 | 0.00042708 | 0.00042708 | -7.7585
21/05/2010 | 0.0004012 | 0.0004012 | -7.8211
22/05/2010 | 0.013582 | 0.013582 | -4.299
23/05/2010 | 0.015355 | 0.015355 | -4.1763
24/05/2010 | 0.013324 | 0.013324 | -4.3182
25/05/2010 | 0.0026854 | 0.0026854 | -5.9199
26/05/2010 | 0.33057 | 0.33057 | -1.1069
27/05/2010 | 0.0015918 | 0.0015918 | -6.4429
28/05/2010 | 0.0010451 | 0.0010451 | -6.8637
29/05/2010 | 0.064253 | 0.064253 | -2.7449
30/05/2010 | 0.014835 | 0.014835 | -4.2108
31/05/2010 | 0.014893 | 0.014893 | -4.2069
1/06/2010 | 0.00059532 | 0.00059532 | -7.4264
2/06/2010 | 0.19272 | 0.19272 | -1.6465
3/06/2010 | 0.49728 | 0.49728 | -0.69861
4/06/2010 | 0.0021289 | 0.0021289 | -6.1521
5/06/2010 | 0.0080886 | 0.0080886 | -4.8173
6/06/2010 | 0.028679 | 0.028679 | -3.5516
7/06/2010 | 0.015271 | 0.015271 | -4.1818
8/06/2010 | 0.012104 | 0.012104 | -4.4142
9/06/2010 | 0.002721 | 0.002721 | -5.9068
10/06/2010 | 0.021127 | 0.021127 | -3.8572
11/06/2010 | 0.0019089 | 0.0019089 | -6.2612
12/06/2010 | 0.022787 | 0.022787 | -3.7816
13/06/2010 | 0.021095 | 0.021095 | -3.8587
14/06/2010 | 0.047393 | 0.047393 | -3.0493
15/06/2010 | 0.016656 | 0.016656 | -4.095
16/06/2010 | 0.022706 | 0.022706 | -3.7851
17/06/2010 | 0.11622 | 0.11622 | -2.1523
18/06/2010 | 0.090078 | 0.090078 | -2.4071
19/06/2010 | 0.0025722 | 0.0025722 | -5.963
20/06/2010 | 0.025182 | 0.025182 | -3.6816
21/06/2010 | 0.016562 | 0.016562 | -4.1006
22/06/2010 | 0.022053 | 0.022053 | -3.8143
23/06/2010 | 0.12859 | 0.12859 | -2.0511
24/06/2010 | 0.0018733 | 0.0018733 | -6.28
25/06/2010 | 0.76268 | 0.76268 | -0.27091
26/06/2010 | 0.0036334 | 0.0036334 | -5.6176
27/06/2010 | 0.017222 | 0.017222 | -4.0616
28/06/2010 | 0.035202 | 0.035202 | -3.3467
29/06/2010 | 0.021817 | 0.021817 | -3.8251
30/06/2010 | 0.05717 | 0.05717 | -2.8617
1/07/2010 | 0.058827 | 0.058827 | -2.8332
2/07/2010 | 0.0007571 | 0.0007571 | -7.186
3/07/2010 | 0.0027728 | 0.0027728 | -5.8879
4/07/2010 | 0.00672 | 0.00672 | -5.0027
5/07/2010 | 0.019607 | 0.019607 | -3.9319
6/07/2010 | 0.0021807 | 0.0021807 | -6.1281
7/07/2010 | 0.0022842 | 0.0022842 | -6.0817
8/07/2010 | 0.0032322 | 0.0032322 | -5.7346
9/07/2010 | 0.0010159 | 0.0010159 | -6.8919
10/07/2010 | 0.44532 | 0.44532 | -0.80895
11/07/2010 | 0 | 0
12/07/2010 | 0.0051638 | 0.0051638 | -5.2661
13/07/2010 | 0.0021225 | 0.0021225 | -6.1552
14/07/2010 | 0.025424 | 0.025424 | -3.6721
15/07/2010 | 0.00030737 | 0.00030737 | -8.0875
16/07/2010 | 0.0048855 | 0.0048855 | -5.3215
17/07/2010 | 0.02049 | 0.02049 | -3.8878
18/07/2010 | 1.1384 | 1.1384 | 0.12959
19/07/2010 | 0.07713 | 0.07713 | -2.5623
20/07/2010 | 0.049302 | 0.049302 | -3.0098
21/07/2010 | 0.014048 | 0.014048 | -4.2653
22/07/2010 | 0.0092275 | 0.0092275 | -4.6856
23/07/2010 | 0.00694 | 0.00694 | -4.9704
24/07/2010 | 0.037081 | 0.037081 | -3.2946
25/07/2010 | 0.45283 | 0.45283 | -0.79223
26/07/2010 | 0.013142 | 0.013142 | -4.3319
27/07/2010 | 0.071888 | 0.071888 | -2.6326
28/07/2010 | 0.023444 | 0.023444 | -3.7531
29/07/2010 | 0.0040314 | 0.0040314 | -5.5136
30/07/2010 | 0.00029119 | 0.00029119 | -8.1415
31/07/2010 | 0 | 0
1/08/2010 | 0.020616 | 0.020616 | -3.8817
2/08/2010 | 0.011153 | 0.011153 | -4.4961
3/08/2010 | 0.55303 | 0.55303 | -0.59234
4/08/2010 | 0.007791 | 0.007791 | -4.8548
5/08/2010 | 0.19115 | 0.19115 | -1.6547
6/08/2010 | 0.0017148 | 0.0017148 | -6.3685
7/08/2010 | 0.0049632 | 0.0049632 | -5.3057
8/08/2010 | 0 | 0
9/08/2010 | 0.0015789 | 0.0015789 | -6.451
10/08/2010 | 0.020846 | 0.020846 | -3.8706
11/08/2010 | 0.0093213 | 0.0093213 | -4.6754
12/08/2010 | 0.17621 | 0.17621 | -1.7361
13/08/2010 | 0.028349 | 0.028349 | -3.5632
14/08/2010 | 0.13151 | 0.13151 | -2.0286
15/08/2010 | 0.0031125 | 0.0031125 | -5.7723
16/08/2010 | 0.010781 | 0.010781 | -4.53
17/08/2010 | 0.0029507 | 0.0029507 | -5.8257
18/08/2010 | 0.012621 | 0.012621 | -4.3724
19/08/2010 | 0.17066 | 0.17066 | -1.7681
20/08/2010 | 0.022457 | 0.022457 | -3.7961
21/08/2010 | 0.28094 | 0.28094 | -1.2696
22/08/2010 | 0.0035266 | 0.0035266 | -5.6474
23/08/2010 | 0.2483 | 0.2483 | -1.3931
24/08/2010 | 0.019173 | 0.019173 | -3.9542
25/08/2010 | 0.0094346 | 0.0094346 | -4.6634
26/08/2010 | 0.0018119 | 0.0018119 | -6.3134
27/08/2010 | 0.0045555 | 0.0045555 | -5.3914
28/08/2010 | 0.013899 | 0.013899 | -4.2759
29/08/2010 | 0.00072474 | 0.00072474 | -7.2297
30/08/2010 | 0.7858 | 0.7858 | -0.24106
31/08/2010 | 0.00037531 | 0.00037531 | -7.8878
1/09/2010 | 0.0099975 | 0.0099975 | -4.6054
2/09/2010 | 0.0017666 | 0.0017666 | -6.3387
3/09/2010 | 0.0010321 | 0.0010321 | -6.8762
4/09/2010 | 0.60797 | 0.60797 | -0.49762
5/09/2010 | 0.25941 | 0.25941 | -1.3493
6/09/2010 | 0.0067427 | 0.0067427 | -4.9993
7/09/2010 | 0.0087195 | 0.0087195 | -4.7422
8/09/2010 | 0.0061797 | 0.0061797 | -5.0865
9/09/2010 | 0.0009221 | 0.0009221 | -6.9889
10/09/2010 | 0.018591 | 0.018591 | -3.9851
11/09/2010 | 0.18021 | 0.18021 | -1.7136
12/09/2010 | 0.013654 | 0.013654 | -4.2938
13/09/2010 | 0.0010839 | 0.0010839 | -6.8272
14/09/2010 | 0.0019251 | 0.0019251 | -6.2528
15/09/2010 | 0.2449 | 0.2449 | -1.4069
16/09/2010 | 0.012298 | 0.012298 | -4.3983
17/09/2010 | 0.042909 | 0.042909 | -3.1487
18/09/2010 | 0.0014948 | 0.0014948 | -6.5058
19/09/2010 | 0.029611 | 0.029611 | -3.5196
20/09/2010 | 0.002171 | 0.002171 | -6.1326
21/09/2010 | 0.00029119 | 0.00029119 | -8.1415
22/09/2010 | 0.011693 | 0.011693 | -4.4488
23/09/2010 | 0.074687 | 0.074687 | -2.5944
24/09/2010 | 0.0010192 | 0.0010192 | -6.8888
25/09/2010 | 0.00032355 | 0.00032355 | -8.0362
26/09/2010 | 0.00088004 | 0.00088004 | -7.0355
27/09/2010 | 0.20773 | 0.20773 | -1.5715
28/09/2010 | 0.0010224 | 0.0010224 | -6.8856
29/09/2010 | 0.00087034 | 0.00087034 | -7.0466
30/09/2010 | 0.55869 | 0.55869 | -0.58216
1/10/2010 | 0.00038178 | 0.00038178 | -7.8707
2/10/2010 | 0.0039408 | 0.0039408 | -5.5364
3/10/2010 | 0.014482 | 0.014482 | -4.2349
4/10/2010 | 0.010428 | 0.010428 | -4.5633
5/10/2010 | 0.0011162 | 0.0011162 | -6.7978
6/10/2010 | 0.42168 | 0.42168 | -0.86351
7/10/2010 | 0.0027695 | 0.0027695 | -5.8891
8/10/2010 | 0.0016242 | 0.0016242 | -6.4227
9/10/2010 | 0.00036237 | 0.00036237 | -7.9228
10/10/2010 | 0.00053385 | 0.00053385 | -7.5354
11/10/2010 | 0.001718 | 0.001718 | -6.3666
12/10/2010 | 0.079459 | 0.079459 | -2.5325
13/10/2010 | 0.028909 | 0.028909 | -3.5436
14/10/2010 | 0.00051767 | 0.00051767 | -7.5662
15/10/2010 | 2.0453 | 2.0453 | 0.71555
16/10/2010 | 0.063425 | 0.063425 | -2.7579
17/10/2010 | 0 | 0
18/10/2010 | 0.55629 | 0.55629 | -0.58647
19/10/2010 | 0.02072 | 0.02072 | -3.8767
20/10/2010 | 0.0019219 | 0.0019219 | -6.2545
21/10/2010 | 0.0015304 | 0.0015304 | -6.4822
22/10/2010 | 0.090298 | 0.090298 | -2.4046
23/10/2010 | 0.013935 | 0.013935 | -4.2733
24/10/2010 | 0.0014624 | 0.0014624 | -6.5277
25/10/2010 | 0.0026822 | 0.0026822 | -5.9211
26/10/2010 | 0.00066003 | 0.00066003 | -7.3232
27/10/2010 | 0.0044423 | 0.0044423 | -5.4166
28/10/2010 | 0.0040961 | 0.0040961 | -5.4977
29/10/2010 | 0.011224 | 0.011224 | -4.4897
30/10/2010 | 0.014505 | 0.014505 | -4.2333
31/10/2010 | 0.46666 | 0.46666 | -0.76216
1/11/2010 | 0.068579 | 0.068579 | -2.6798
2/11/2010 | 0.0095834 | 0.0095834 | -4.6477
3/11/2010 | 0.036606 | 0.036606 | -3.3075
4/11/2010 | 0.00097387 | 0.00097387 | -6.9342
5/11/2010 | 0.00010353 | 0.00010353 | -9.1756
6/11/2010 | 0.00052414 | 0.00052414 | -7.5537
7/11/2010 | 0.0068624 | 0.0068624 | -4.9817
8/11/2010 | 0.037732 | 0.037732 | -3.2773
9/11/2010 | 0.00056297 | 0.00056297 | -7.4823
10/11/2010 | 0 | 0
11/11/2010 | 0.0034975 | 0.0034975 | -5.6557
12/11/2010 | 0.002281 | 0.002281 | -6.0831
13/11/2010 | 0.1264 | 0.1264 | -2.0683
14/11/2010 | 1.8449 | 1.8449 | 0.61243
15/11/2010 | 0.00089298 | 0.00089298 | -7.0209
16/11/2010 | 0.0044099 | 0.0044099 | -5.4239
17/11/2010 | 0.0011615 | 0.0011615 | -6.758
18/11/2010 | 0.00057591 | 0.00057591 | -7.4596
19/11/2010 | 0.00057591 | 0.00057591 | -7.4596
20/11/2010 | 0.019144 | 0.019144 | -3.9558
21/11/2010 | 0 | 0
22/11/2010 | 0.0032581 | 0.0032581 | -5.7266
23/11/2010 | 0.25548 | 0.25548 | -1.3646
24/11/2010 | 0.17789 | 0.17789 | -1.7266
25/11/2010 | 0.017177 | 0.017177 | -4.0642
26/11/2010 | 0.015818 | 0.015818 | -4.1466
27/11/2010 | 0.11282 | 0.11282 | -2.1819
28/11/2010 | 0.0026692 | 0.0026692 | -5.926
29/11/2010 | 0.0026142 | 0.0026142 | -5.9468
30/11/2010 | 0.44393 | 0.44393 | -0.8121
1/12/2010 | 0.00059209 | 0.00059209 | -7.4319
2/12/2010 | 0.012398 | 0.012398 | -4.3902
3/12/2010 | 0.0030413 | 0.0030413 | -5.7955
4/12/2010 | 0.0048952 | 0.0048952 | -5.3195
5/12/2010 | 0.01443 | 0.01443 | -4.2384
6/12/2010 | 0.0023683 | 0.0023683 | -6.0456
7/12/2010 | 0.035367 | 0.035367 | -3.342
8/12/2010 | 0.081896 | 0.081896 | -2.5023
9/12/2010 | 0.0069368 | 0.0069368 | -4.9709
10/12/2010 | 0.018377 | 0.018377 | -3.9966
11/12/2010 | 1.6571 | 1.6571 | 0.50504
12/12/2010 | 0.043274 | 0.043274 | -3.1402
13/12/2010 | 0.0032872 | 0.0032872 | -5.7177
14/12/2010 | 0.0027566 | 0.0027566 | -5.8938
15/12/2010 | 0.00080563 | 0.00080563 | -7.1239
16/12/2010 | 0.077761 | 0.077761 | -2.5541
17/12/2010 | 0.00074415 | 0.00074415 | -7.2033
18/12/2010 | 0.053081 | 0.053081 | -2.9359
19/12/2010 | 0.031458 | 0.031458 | -3.4591
20/12/2010 | 0.0013427 | 0.0013427 | -6.6131
21/12/2010 | 0.0010418 | 0.0010418 | -6.8668
22/12/2010 | 0.0069368 | 0.0069368 | -4.9709
23/12/2010 | 0.0015595 | 0.0015595 | -6.4634
24/12/2010 | 0.0036755 | 0.0036755 | -5.6061
25/12/2010 | 0 | 0
26/12/2010 | 0.44973 | 0.44973 | -0.79911
27/12/2010 | 0.00057267 | 0.00057267 | -7.4652
28/12/2010 | 0 | 0
29/12/2010 | 0.20564 | 0.20564 | -1.5816
30/12/2010 | 0.36403 | 0.36403 | -1.0105
31/12/2010 | 0.37318 | 0.37318 | -0.98569
1/01/2011 | 0.0047631 | 0.0047631 | -5.3469
2/01/2011 | 0.0017942 | 0.0017942 | -6.3232
3/01/2011 | 0.67177 | 0.67177 | -0.39783
4/01/2011 | 0.00043009 | 0.00043009 | -7.7515
5/01/2011 | 0 | 0
6/01/2011 | 0.0055783 | 0.0055783 | -5.1889
7/01/2011 | 0.00039478 | 0.00039478 | -7.8372
8/01/2011 | 0.1321 | 0.1321 | -2.0242
9/01/2011 | 0.017274 | 0.017274 | -4.0585
10/01/2011 | 0.0025099 | 0.0025099 | -5.9875
11/01/2011 | 0.0056842 | 0.0056842 | -5.1701
12/01/2011 | 0.0038708 | 0.0038708 | -5.5543
13/01/2011 | 0.041093 | 0.041093 | -3.1919
14/01/2011 | 0.059763 | 0.059763 | -2.8174
15/01/2011 | 0.017274 | 0.017274 | -4.0585
16/01/2011 | 0.014832 | 0.014832 | -4.211
17/01/2011 | 0.0031454 | 0.0031454 | -5.7618
18/01/2011 | 0.0015182 | 0.0015182 | -6.4903
19/01/2011 | 0.1941 | 0.1941 | -1.6394
20/01/2011 | 0.0010816 | 0.0010816 | -6.8293
21/01/2011 | 0.012315 | 0.012315 | -4.3969
22/01/2011 | 0.013991 | 0.013991 | -4.2694
23/01/2011 | 0.011571 | 0.011571 | -4.4593
24/01/2011 | 0.00091474 | 0.00091474 | -6.9969
25/01/2011 | 0.0027539 | 0.0027539 | -5.8948
26/01/2011 | 0.0052253 | 0.0052253 | -5.2542
27/01/2011 | 0.0053023 | 0.0053023 | -5.2396
28/01/2011 | 0.00078957 | 0.00078957 | -7.144
29/01/2011 | 0.0037521 | 0.0037521 | -5.5855
30/01/2011 | 0.039786 | 0.039786 | -3.2242
31/01/2011 | 0.063233 | 0.063233 | -2.7609
1/02/2011 | 2.4018 | 2.4018 | 0.87623
2/02/2011 | 0.23255 | 0.23255 | -1.4587
3/02/2011 | 0.27469 | 0.27469 | -1.2921
4/02/2011 | 4.5643 | 4.5643 | 1.5183
5/02/2011 | 0.61151 | 0.61151 | -0.49182
6/02/2011 | 0.0027282 | 0.0027282 | -5.9041
7/02/2011 | 0.020275 | 0.020275 | -3.8984
8/02/2011 | 0.00080241 | 0.00080241 | -7.1279
9/02/2011 | 0.00268 | 0.00268 | -5.9219
10/02/2011 | 0.0071061 | 0.0071061 | -4.9468
11/02/2011 | 0.0039864 | 0.0039864 | -5.5249
12/02/2011 | 0.0010752 | 0.0010752 | -6.8352
13/02/2011 | 0.015339 | 0.015339 | -4.1774
14/02/2011 | 0.063268 | 0.00078315 | -7.1522
15/02/2011 | 0.0014122 | 0.0014122 | -6.5626
16/02/2011 | 0.0093111 | 0.0093111 | -4.6765
17/02/2011 | 0.0072634 | 0.0072634 | -4.9249
18/02/2011 | 0.14648 | 0.14648 | -1.9209
19/02/2011 | 0.1293 | 0.1293 | -2.0456
20/02/2011 | 0.034028 | 0.034028 | -3.3806
21/02/2011 | 0.055896 | 0.055896 | -2.8843
22/02/2011 | 0.0014347 | 0.0014347 | -6.5468
23/02/2011 | 0 | 0
24/02/2011 | 0.000934 | 0.000934 | -6.976
25/02/2011 | 0.1321 | 0.1321 | -2.0242
26/02/2011 | 0.0032963 | 0.0032963 | -5.715
27/02/2011 | 0.00074784 | 0.00074784 | -7.1983
28/02/2011 | 0.012351 | 0.012351 | -4.394
1/03/2011 | 0.0021825 | 0.0021825 | -6.1273
2/03/2011 | 0.0019322 | 0.0019322 | -6.2491
3/03/2011 | 0 | 0
4/03/2011 | 0.024595 | 0.024595 | -3.7052
5/03/2011 | 0.00065797 | 0.00065797 | -7.3263
6/03/2011 | 0.00054243 | 0.00054243 | -7.5195
7/03/2011 | 0.0023783 | 0.0023783 | -6.0414
8/03/2011 | 0.25704 | 0.25704 | -1.3585
9/03/2011 | 0.7761 | 0.7761 | -0.25348
10/03/2011 | 0.31483 | 0.31483 | -1.1557
11/03/2011 | 0.00021825 | 0.00021825 | -8.4298
12/03/2011 | 0.035572 | 0.035572 | -3.3362
13/03/2011 | 0.00056489 | 0.00056489 | -7.4789
14/03/2011 | 0.00088586 | 0.00088586 | -7.029
15/03/2011 | 0.007992 | 0.007992 | -4.8293
16/03/2011 | 0.00017332 | 0.00017332 | -8.6604
17/03/2011 | 0.00051996 | 0.00051996 | -7.5618
18/03/2011 | 0 | 0
19/03/2011 | 0.017897 | 0.017897 | -4.0231
20/03/2011 | 0.003322 | 0.003322 | -5.7072
21/03/2011 | 0.0085986 | 0.0085986 | -4.7562
22/03/2011 | 0.032392 | 0.032392 | -3.4299
23/03/2011 | 0.00075747 | 0.00075747 | -7.1855
24/03/2011 | 0.39355 | 0.39355 | -0.93254
25/03/2011 | 0.0025581 | 0.0025581 | -5.9685
26/03/2011 | 0.00074784 | 0.00074784 | -7.1983
27/03/2011 | 0.010858 | 0.010858 | -4.5228
28/03/2011 | 0.035553 | 0.035553 | -3.3367
29/03/2011 | 0.00023751 | 0.00023751 | -8.3453
30/03/2011 | 0.0035627 | 0.0035627 | -5.6372
31/03/2011 | 0.0050776 | 0.0050776 | -5.2829
1/04/2011 | 0.0026319 | 0.0026319 | -5.9401
2/04/2011 | 0.023876 | 0.023876 | -3.7349
3/04/2011 | 0.0087238 | 0.0087238 | -4.7417
4/04/2011 | 0.0027731 | 0.0027731 | -5.8878
5/04/2011 | 0.0067755 | 0.0067755 | -4.9944
6/04/2011 | 0.0016048 | 0.0016048 | -6.4347
7/04/2011 | 0.0011169 | 0.0011169 | -6.7972
8/04/2011 | 0.00069649 | 0.00069649 | -7.2695
9/04/2011 | 0.12342 | 0.12342 | -2.0922
10/04/2011 | 0.0016177 | 0.0016177 | -6.4268
11/04/2011 | 0.00034985 | 0.00034985 | -7.958
12/04/2011 | 0.22957 | 0.22957 | -1.4716
13/04/2011 | 0.0021472 | 0.0021472 | -6.1436
14/04/2011 | 0.0073212 | 0.0073212 | -4.917
15/04/2011 | 0.0016497 | 0.0016497 | -6.4071
16/04/2011 | 0.0014251 | 0.0014251 | -6.5535
17/04/2011 | 0.0032513 | 0.0032513 | -5.7287
18/04/2011 | 0.0010784 | 0.0010784 | -6.8322
19/04/2011 | 0.00054243 | 0.00054243 | -7.5195
20/04/2011 | 0.0026479 | 0.0026479 | -5.934
21/04/2011 | 0.00034985 | 0.00034985 | -7.958
22/04/2011 | 0.00057452 | 0.00057452 | -7.462
23/04/2011 | 0.0094684 | 0.0094684 | -4.6598
24/04/2011 | 8.9869e-05 | 8.9869e-05 | -9.3172
25/04/2011 | 0.0002664 | 0.0002664 | -8.2305
26/04/2011 | 0.0027603 | 0.0027603 | -5.8924
27/04/2011 | 0.0039222 | 0.0039222 | -5.5411
28/04/2011 | 0.033781 | 0.033781 | -3.3878
29/04/2011 | 0.0011587 | 0.0011587 | -6.7605
30/04/2011 | 0.37145 | 0.37145 | -0.99033
1/05/2011 | 0.00017011 | 0.00017011 | -8.6791
2/05/2011 | 0.13879 | 0.13879 | -1.9748
3/05/2011 | 0.00065476 | 0.00065476 | -7.3312
4/05/2011 | 0.0017621 | 0.0017621 | -6.3413
5/05/2011 | 0.29574 | 0.29574 | -1.2183
6/05/2011 | 0.0018487 | 0.0018487 | -6.2932
7/05/2011 | 0.0011298 | 0.0011298 | -6.7857
8/05/2011 | 0.0012197 | 0.0012197 | -6.7092
9/05/2011 | 0.00077994 | 0.00077994 | -7.1563
10/05/2011 | 0.0029657 | 0.0029657 | -5.8206
11/05/2011 | 0.16746 | 0.16746 | -1.787
12/05/2011 | 0.42887 | 0.42887 | -0.8466
13/05/2011 | 0.015804 | 0.015804 | -4.1475
14/05/2011 | 0.037935 | 0.037935 | -3.2719
15/05/2011 | 0.040785 | 0.040785 | -3.1994
16/05/2011 | 0.00042046 | 0.00042046 | -7.7742
17/05/2011 | 0.0022082 | 0.0022082 | -6.1156
18/05/2011 | 0.0029689 | 0.0029689 | -5.8196
19/05/2011 | 0.013525 | 0.013525 | -4.3032
20/05/2011 | 0.00013801 | 0.00013801 | -8.8882
21/05/2011 | 0.00019258 | 0.00019258 | -8.555
22/05/2011 | 0.42436 | 0.42436 | -0.85717
23/05/2011 | 0.51461 | 0.51461 | -0.66434
24/05/2011 | 0.0019129 | 0.0019129 | -6.2591
25/05/2011 | 0.012261 | 0.012261 | -4.4014
26/05/2011 | 0.022455 | 0.022455 | -3.7963
27/05/2011 | 0.0012614 | 0.0012614 | -6.6755
28/05/2011 | 0.0095197 | 0.0095197 | -4.6544
29/05/2011 | 0.0087494 | 0.0087494 | -4.7388
30/05/2011 | 0.034934 | 0.034934 | -3.3543
31/05/2011 | 0.0011073 | 0.0011073 | -6.8058
1/06/2011 | 0.0084606 | 0.0084606 | -4.7723
2/06/2011 | 0.0018776 | 0.0018776 | -6.2777
3/06/2011 | 0.0015663 | 0.0015663 | -6.459
4/06/2011 | 0.00081203 | 0.00081203 | -7.116
5/06/2011 | 0.0057645 | 0.0057645 | -5.156
6/06/2011 | 0.0006323 | 0.0006323 | -7.3662
7/06/2011 | 0.084339 | 0.084339 | -2.4729
8/06/2011 | 0.016873 | 0.016873 | -4.082
9/06/2011 | 0.057651 | 0.057651 | -2.8533
10/06/2011 | 0.028049 | 0.028049 | -3.5738
11/06/2011 | 0.00095326 | 0.00095326 | -6.9556
12/06/2011 | 0.0006323 | 0.0006323 | -7.3662
13/06/2011 | 0.050481 | 0.050481 | -2.9862
14/06/2011 | 0.046016 | 0.046016 | -3.0788
15/06/2011 | 0.0054339 | 0.0054339 | -5.2151
16/06/2011 | 0.003996 | 0.003996 | -5.5225
17/06/2011 | 0.0089677 | 0.0089677 | -4.7141
18/06/2011 | 0.07014 | 0.07014 | -2.6573
19/06/2011 | 0.060222 | 0.060222 | -2.8097
20/06/2011 | 0.003476 | 0.003476 | -5.6619
21/06/2011 | 0.072483 | 0.072483 | -2.6244
22/06/2011 | 0.0022339 | 0.0022339 | -6.104
23/06/2011 | 0.053148 | 0.053148 | -2.9347
24/06/2011 | 0.00063551 | 0.00063551 | -7.3611
25/06/2011 | 0.00020542 | 0.00020542 | -8.4905
26/06/2011 | 0.0017749 | 0.0017749 | -6.334
27/06/2011 | 0.013801 | 0.013801 | -4.283
28/06/2011 | 0.015409 | 0.015409 | -4.1728
29/06/2011 | 0.00021184 | 0.00021184 | -8.4597
30/06/2011 | 0.37501 | 0.37501 | -0.9808
1/07/2011 | 0.0075041 | 0.0075041 | -4.8923
2/07/2011 | 0.015284 | 0.015284 | -4.1809
3/07/2011 | 0.076341 | 0.076341 | -2.5725
4/07/2011 | 0.0016497 | 0.0016497 | -6.4071
5/07/2011 | 0.0041853 | 0.0041853 | -5.4762
6/07/2011 | 0.023064 | 0.023064 | -3.7695
7/07/2011 | 0.00062588 | 0.00062588 | -7.3764
8/07/2011 | 0.0029978 | 0.0029978 | -5.8099
9/07/2011 | 0.3278 | 0.3278 | -1.1154
10/07/2011 | 0.036859 | 0.036859 | -3.3006
11/07/2011 | 0.00075426 | 0.00075426 | -7.1898
12/07/2011 | 0.0049845 | 0.0049845 | -5.3014
13/07/2011 | 0.42215 | 0.42215 | -0.8624
14/07/2011 | 0.011648 | 0.011648 | -4.4526
15/07/2011 | 0.00091153 | 0.00091153 | -7.0004
16/07/2011 | 0.0014668 | 0.0014668 | -6.5247
17/07/2011 | 0.0040345 | 0.0040345 | -5.5129
18/07/2011 | 0.098645 | 0.098645 | -2.3162
19/07/2011 | 0.012341 | 0.012341 | -4.3948
20/07/2011 | 0.017412 | 0.017412 | -4.0506
21/07/2011 | 0.016979 | 0.016979 | -4.0758
22/07/2011 | 0.22184 | 0.22184 | -1.5058
23/07/2011 | 0.0035531 | 0.0035531 | -5.6399
24/07/2011 | 0.011741 | 0.011741 | -4.4447
25/07/2011 | 0.01852 | 0.01852 | -3.9889
26/07/2011 | 0.0063518 | 0.0063518 | -5.059
27/07/2011 | 0.0093432 | 0.0093432 | -4.6731
28/07/2011 | 0.011632 | 0.011632 | -4.454
29/07/2011 | 0.018487 | 0.018487 | -3.9907
30/07/2011 | 0.0030106 | 0.0030106 | -5.8056
31/07/2011 | 0.00031454 | 0.00031454 | -8.0644
1/08/2011 | 0.0056008 | 0.0056008 | -5.1848
2/08/2011 | 0.012752 | 0.012752 | -4.3621
3/08/2011 | 0.83171 | 0.83171 | -0.18427
4/08/2011 | 0.0033508 | 0.0033508 | -5.6985
5/08/2011 | 0 | 0
6/08/2011 | 0.29199 | 0.29199 | -1.231
7/08/2011 | 0.048969 | 0.048969 | -3.0166
8/08/2011 | 0.0014026 | 0.0014026 | -6.5694
9/08/2011 | 0.0052734 | 0.0052734 | -5.2451
10/08/2011 | 0.011105 | 0.011105 | -4.5003
11/08/2011 | 0.13563 | 0.13563 | -1.9979
12/08/2011 | 0.0019226 | 0.0019226 | -6.2541
13/08/2011 | 0.0041115 | 0.0041115 | -5.494
14/08/2011 | 0.0014058 | 0.0014058 | -6.5671
15/08/2011 | 0.00020863 | 0.00020863 | -8.475
16/08/2011 | 0 | 0
17/08/2011 | 0.72669 | 0.72669 | -0.31925
18/08/2011 | 0.0069841 | 0.0069841 | -4.9641
19/08/2011 | 0.0019771 | 0.0019771 | -6.2261
20/08/2011 | 0.0068493 | 0.0068493 | -4.9836
21/08/2011 | 0.0018808 | 0.0018808 | -6.276
22/08/2011 | 0 | 0
23/08/2011 | 0.00039157 | 0.00039157 | -7.8453
24/08/2011 | 0.0012389 | 0.0012389 | -6.6935
25/08/2011 | 0.00882 | 0.00882 | -4.7307
26/08/2011 | 0.0025998 | 0.0025998 | -5.9523
27/08/2011 | 0.14562 | 0.14562 | -1.9268
28/08/2011 | 0 | 0
29/08/2011 | 0.00075426 | 0.00075426 | -7.1898
30/08/2011 | 0.03069 | 0.03069 | -3.4838
31/08/2011 | 0.11699 | 0.11699 | -2.1456
1/09/2011 | 0.0021665 | 0.0021665 | -6.1346
2/09/2011 | 0.21423 | 0.21423 | -1.5407
3/09/2011 | 0.16506 | 0.16506 | -1.8014
4/09/2011 | 0.00030812 | 0.00030812 | -8.085
5/09/2011 | 0 | 0
6/09/2011 | 0.021893 | 0.021893 | -3.8216
7/09/2011 | 0.0012132 | 0.0012132 | -6.7145
8/09/2011 | 0.001531 | 0.001531 | -6.4818
9/09/2011 | 0.0092726 | 0.0092726 | -4.6807
10/09/2011 | 0.012697 | 0.012697 | -4.3664
11/09/2011 | 0.022358 | 0.022358 | -3.8006
12/09/2011 | 0.002863 | 0.002863 | -5.8559
13/09/2011 | 0.00033059 | 0.00033059 | -8.0146
14/09/2011 | 0.017345 | 0.017345 | -4.0545
15/09/2011 | 0.00052317 | 0.00052317 | -7.5556
16/09/2011 | 0.019973 | 0.019973 | -3.9133
17/09/2011 | 0.13345 | 0.13345 | -2.0141
18/09/2011 | 0.0024136 | 0.0024136 | -6.0266
19/09/2011 | 0.083303 | 0.083303 | -2.4853
20/09/2011 | 0.024942 | 0.024942 | -3.6912
21/09/2011 | 0.00044614 | 0.00044614 | -7.7149
22/09/2011 | 0.020712 | 0.020712 | -3.8771
23/09/2011 | 0.33174 | 0.33174 | -1.1034
24/09/2011 | 0 | 0
25/09/2011 | 0.062636 | 0.062636 | -2.7704
26/09/2011 | 0.00082487 | 0.00082487 | -7.1003
27/09/2011 | 0.013561 | 0.013561 | -4.3006
28/09/2011 | 3.4012 | 3.4012 | 1.2241
29/09/2011 | 0.28284 | 0.28284 | -1.2629
30/09/2011 | 0.092922 | 0.092922 | -2.376
1/10/2011 | 0.0032417 | 0.0032417 | -5.7317
2/10/2011 | 0.0025581 | 0.0025581 | -5.9685
3/10/2011 | 0.24205 | 0.24205 | -1.4186
4/10/2011 | 0.1722 | 0.1722 | -1.7591
5/10/2011 | 0.00072858 | 0.00072858 | -7.2244
6/10/2011 | 0.0093015 | 0.0093015 | -4.6776
7/10/2011 | 0.0014251 | 0.0014251 | -6.5535
8/10/2011 | 0 | 0
9/10/2011 | 0.017223 | 0.017223 | -4.0615
10/10/2011 | 0.0015374 | 0.0015374 | -6.4777
11/10/2011 | 0.0017942 | 0.0017942 | -6.3232
12/10/2011 | 0.0015856 | 0.0015856 | -6.4468
13/10/2011 | 0.014212 | 0.014212 | -4.2537
14/10/2011 | 0.4057 | 0.4057 | -0.90215
15/10/2011 | 0.005206 | 0.005206 | -5.2579
16/10/2011 | 0.04091 | 0.04091 | -3.1964
17/10/2011 | 0.0044261 | 0.0044261 | -5.4202
18/10/2011 | 0.0027539 | 0.0027539 | -5.8948
19/10/2011 | 0.14357 | 0.14357 | -1.941
20/10/2011 | 0.13902 | 0.13902 | -1.9731
21/10/2011 | 0.051187 | 0.051187 | -2.9723
22/10/2011 | 0.00040762 | 0.00040762 | -7.8052
23/10/2011 | 0.0014283 | 0.0014283 | -6.5513
24/10/2011 | 0.0053857 | 0.0053857 | -5.224
25/10/2011 | 0.0044325 | 0.0044325 | -5.4188
26/10/2011 | 0.006615 | 0.006615 | -5.0184
27/10/2011 | 0.15 | 0.15 | -1.8971
28/10/2011 | 0.55608 | 0.55608 | -0.58685
29/10/2011 | 0.0061593 | 0.0061593 | -5.0898
30/10/2011 | 0.1462 | 0.1462 | -1.9228
31/10/2011 | 0.0046347 | 0.0046347 | -5.3742
1/11/2011 | 0.0030909 | 0.0030909 | -5.7793
2/11/2011 | 0.10513 | 0.10513 | -2.2526
3/11/2011 | 0.00026961 | 0.00026961 | -8.2185
4/11/2011 | 0 | 0
5/11/2011 | 0.032546 | 0.032546 | -3.4251
6/11/2011 | 0.00018295 | 0.00018295 | -8.6063
7/11/2011 | 0.0057195 | 0.0057195 | -5.1639
8/11/2011 | 0.015605 | 0.015605 | -4.1602
9/11/2011 | 0.0026832 | 0.0026832 | -5.9207
10/11/2011 | 0.03512 | 0.03512 | -3.349
11/11/2011 | 0.00075426 | 0.00075426 | -7.1898
12/11/2011 | 0.005344 | 0.005344 | -5.2318
13/11/2011 | 0.00048465 | 0.00048465 | -7.6321
14/11/2011 | 0.20109 | 0.20109 | -1.604
15/11/2011 | 0.019774 | 0.019774 | -3.9234
16/11/2011 | 0.0021537 | 0.0021537 | -6.1406
17/11/2011 | 0.036689 | 0.036689 | -3.3053
18/11/2011 | 1.2059 | 1.2059 | 0.1872
19/11/2011 | 0.05897 | 0.05897 | -2.8307
20/11/2011 | 0.0011844 | 0.0011844 | -6.7386
21/11/2011 | 0.073767 | 0.073767 | -2.6068
22/11/2011 | 0.0015502 | 0.0015502 | -6.4693
23/11/2011 | 0.0065541 | 0.0065541 | -5.0277
24/11/2011 | 0.0027378 | 0.0027378 | -5.9006
25/11/2011 | 0.010595 | 0.010595 | -4.5474
26/11/2011 | 0.010839 | 0.010839 | -4.5246
27/11/2011 | 0.00072217 | 0.00072217 | -7.2333
28/11/2011 | 0.0095936 | 0.0095936 | -4.6467
29/11/2011 | 0.055279 | 0.055279 | -2.8954
30/11/2011 | 0.002327 | 0.002327 | -6.0632
1/12/2011 | 0.00010271 | 0.00010271 | -9.1836
2/12/2011 | 0.0013416 | 0.0013416 | -6.6139
3/12/2011 | 0.017348 | 0.017348 | -4.0543
4/12/2011 | 0.0017396 | 0.0017396 | -6.3541
5/12/2011 | 0.00087623 | 0.00087623 | -7.0399
6/12/2011 | 0.0026736 | 0.0026736 | -5.9243
7/12/2011 | 0.0026319 | 0.0026319 | -5.9401
8/12/2011 | 0.049133 | 0.049133 | -3.0132
9/12/2011 | 0.024727 | 0.024727 | -3.6999
10/12/2011 | 0.71742 | 0.71742 | -0.3321
11/12/2011 | 0.037874 | 0.037874 | -3.2735
12/12/2011 | 0.0093336 | 0.0093336 | -4.6741
13/12/2011 | 0.0066375 | 0.0066375 | -5.015
14/12/2011 | 0.0033027 | 0.0033027 | -5.713
15/12/2011 | 0.11943 | 0.11943 | -2.1251
16/12/2011 | 0.00086339 | 0.00086339 | -7.0546
17/12/2011 | 0.16864 | 0.16864 | -1.78
18/12/2011 | 0.0016818 | 0.0016818 | -6.3879
19/12/2011 | 0.56436 | 0.56436 | -0.57206
20/12/2011 | 0.0024136 | 0.0024136 | -6.0266
21/12/2011 | 0.0029561 | 0.0029561 | -5.8239
22/12/2011 | 0.10913 | 0.10913 | -2.2152
23/12/2011 | 0.001332 | 0.001332 | -6.6211
24/12/2011 | 0.74687 | 0.74687 | -0.29186
25/12/2011 | 0.88583 | 0.88583 | -0.12123
26/12/2011 | 0.014918 | 0.014918 | -4.2052
27/12/2011 | 0.55038 | 0.55038 | -0.59715
28/12/2011 | 0.0018776 | 0.0018776 | -6.2777
29/12/2011 | 0.043404 | 0.043404 | -3.1372
30/12/2011 | 0.0035081 | 0.0035081 | -5.6527
31/12/2011 | 0.21542 | 0.21542 | -1.5352
1/01/2012 | 0.002207 | 0.002207 | -6.1161
2/01/2012 | 0.50502 | 0.50502 | -0.68317
3/01/2012 | 0.0066177 | 0.0066177 | -5.018
4/01/2012 | 0.058844 | 0.058844 | -2.8329
5/01/2012 | 0.0010259 | 0.0010259 | -6.8822
6/01/2012 | 0.0006491 | 0.0006491 | -7.3399
7/01/2012 | 0.012412 | 0.012412 | -4.3891
8/01/2012 | 0.0073808 | 0.0073808 | -4.9089
9/01/2012 | 0.00097841 | 0.00097841 | -6.9296
10/01/2012 | 0.0016338 | 0.0016338 | -6.4168
11/01/2012 | 0.93091 | 0.93091 | -0.071593
12/01/2012 | 0.0019188 | 0.0019188 | -6.256
13/01/2012 | 0.092569 | 0.092569 | -2.3798
14/01/2012 | 0.00082009 | 0.00082009 | -7.1061
15/01/2012 | 0.00043063 | 0.00043063 | -7.7503
16/01/2012 | 0.0067823 | 0.0067823 | -4.9934
17/01/2012 | 0.041172 | 0.041172 | -3.19
18/01/2012 | 0.0020771 | 0.0020771 | -6.1768
19/01/2012 | 0.015382 | 0.015382 | -4.1745
20/01/2012 | 0.00032297 | 0.00032297 | -8.038
21/01/2012 | 0.0017542 | 0.0017542 | -6.3458
22/01/2012 | 0.011399 | 0.011399 | -4.4742
23/01/2012 | 0.2871 | 0.2871 | -1.2479
24/01/2012 | 0.0090653 | 0.0090653 | -4.7033
25/01/2012 | 0.0013362 | 0.0013362 | -6.6179
26/01/2012 | 0.0024888 | 0.0024888 | -5.996
27/01/2012 | 0.016722 | 0.016722 | -4.0911
28/01/2012 | 0.0039864 | 0.0039864 | -5.5249
29/01/2012 | 0.29253 | 0.29253 | -1.2292
30/01/2012 | 1.0913 | 1.0913 | 0.087363
31/01/2012 | 0.080213 | 0.080213 | -2.5231
1/02/2012 | 0.27725 | 0.27725 | -1.2828
2/02/2012 | 0.0019758 | 0.0019758 | -6.2268
3/02/2012 | 0.00060477 | 0.00060477 | -7.4107
4/02/2012 | 0.0013077 | 0.0013077 | -6.6395
5/02/2012 | 4.6549 | 4.6549 | 1.5379
6/02/2012 | 0.018381 | 0.018381 | -3.9965
7/02/2012 | 0.18218 | 0.18218 | -1.7028
8/02/2012 | 0.33122 | 0.33122 | -1.105
9/02/2012 | 0.075701 | 0.075701 | -2.581
10/02/2012 | 0.11018 | 0.11018 | -2.2056
11/02/2012 | 0.0021436 | 0.0021436 | -6.1453
12/02/2012 | 0.052688 | 0.052688 | -2.9434
13/02/2012 | 0.0020455 | 0.0020455 | -6.1921
14/02/2012 | 0.006529 | 0.006529 | -5.0315
15/02/2012 | 0.014812 | 0.014812 | -4.2123
16/02/2012 | 3.4343 | 3.4343 | 1.2338
17/02/2012 | 0.35101 | 0.35101 | -1.0469
18/02/2012 | 0 | 0
19/02/2012 | 0.014838 | 0.014838 | -4.2106
20/02/2012 | 0.62151 | 0.62151 | -0.4756
21/02/2012 | 0.071797 | 0.071797 | -2.6339
22/02/2012 | 0.0006586 | 0.0006586 | -7.3254
23/02/2012 | 0.0014534 | 0.0014534 | -6.5339
24/02/2012 | 0.27168 | 0.27168 | -1.3031
25/02/2012 | 0.016468 | 0.016468 | -4.1063
26/02/2012 | 0.1962 | 0.1962 | -1.6286
27/02/2012 | 0.012412 | 0.012412 | -4.3891
28/02/2012 | 0.025404 | 0.025404 | -3.6729
29/02/2012 | 0.069942 | 0.069942 | -2.6601
1/03/2012 | 0.043195 | 0.043195 | -3.142
2/03/2012 | 0.0064309 | 0.0064309 | -5.0466
3/03/2012 | 0.38325 | 0.38325 | -0.95908
4/03/2012 | 0.022111 | 0.022111 | -3.8117
5/03/2012 | 0.017133 | 0.017133 | -4.0667
6/03/2012 | 0.0029795 | 0.0029795 | -5.816
7/03/2012 | 0.25363 | 0.25363 | -1.3719
8/03/2012 | 0.0093598 | 0.0093598 | -4.6713
9/03/2012 | 0.0010132 | 0.0010132 | -6.8946
10/03/2012 | 0.0042683 | 0.0042683 | -5.4566
11/03/2012 | 0.001371 | 0.001371 | -6.5922
12/03/2012 | 0.0094611 | 0.0094611 | -4.6606
13/03/2012 | 0.00095941 | 0.00095941 | -6.9492
14/03/2012 | 0.0069153 | 0.0069153 | -4.974
15/03/2012 | 1.133 | 1.133 | 0.1249
16/03/2012 | 0.091416 | 0.091416 | -2.3923
17/03/2012 | 0.0018587 | 0.0018587 | -6.2879
18/03/2012 | 0.0016718 | 0.0016718 | -6.3938
19/03/2012 | 0.0012254 | 0.0012254 | -6.7045
20/03/2012 | 0.027915 | 0.027915 | -3.5786
21/03/2012 | 0.0034798 | 0.0034798 | -5.6608
22/03/2012 | 0.030141 | 0.030141 | -3.5019
23/03/2012 | 0.04274 | 0.04274 | -3.1526
24/03/2012 | 0.00071876 | 0.00071876 | -7.238
25/03/2012 | 0.00091508 | 0.00091508 | -6.9965
26/03/2012 | 0.70996 | 0.70996 | -0.34255
27/03/2012 | 0.18893 | 0.18893 | -1.6664
28/03/2012 | 0.0010069 | 0.0010069 | -6.9009
29/03/2012 | 0.18102 | 0.18102 | -1.7091
30/03/2012 | 0.26342 | 0.26342 | -1.334
31/03/2012 | 0.042037 | 0.042037 | -3.1692
1/04/2012 | 0 | 0
2/04/2012 | 0.16107 | 0.16107 | -1.8259
3/04/2012 | 0.037233 | 0.037233 | -3.2906
4/04/2012 | 0.00078209 | 0.00078209 | -7.1535
5/04/2012 | 0.022912 | 0.022912 | -3.7761
6/04/2012 | 0.21822 | 0.21822 | -1.5223
7/04/2012 | 0.056377 | 0.056377 | -2.8757
8/04/2012 | 0.017963 | 0.017963 | -4.0195
9/04/2012 | 0.00090241 | 0.00090241 | -7.0104
10/04/2012 | 0.0054335 | 0.0054335 | -5.2152
11/04/2012 | 0.0021975 | 0.0021975 | -6.1205
12/04/2012 | 0.0015958 | 0.0015958 | -6.4404
13/04/2012 | 0.003863 | 0.003863 | -5.5563
14/04/2012 | 0 | 0
15/04/2012 | 0.39777 | 0.39777 | -0.92188
16/04/2012 | 0.0064815 | 0.0064815 | -5.0388
17/04/2012 | 0.0022766 | 0.0022766 | -6.0851
18/04/2012 | 0.0086315 | 0.0086315 | -4.7523
19/04/2012 | 0.032116 | 0.032116 | -3.4384
20/04/2012 | 0.00080742 | 0.00080742 | -7.1217
21/04/2012 | 0.00027231 | 0.00027231 | -8.2086
22/04/2012 | 0.1823 | 0.1823 | -1.7021
23/04/2012 | 0.047717 | 0.047717 | -3.0425
24/04/2012 | 0.28607 | 0.28607 | -1.2515
25/04/2012 | 0.0063929 | 0.0063929 | -5.0526
26/04/2012 | 0.0019441 | 0.0019441 | -6.2429
27/04/2012 | 0.012314 | 0.012314 | -4.397
28/04/2012 | 0.024777 | 0.024777 | -3.6978
29/04/2012 | 0.012358 | 0.012358 | -4.3934
30/04/2012 | 0.010129 | 0.010129 | -4.5923
1/05/2012 | 0.062475 | 0.062475 | -2.773
2/05/2012 | 0.0011652 | 0.0011652 | -6.7548
3/05/2012 | 0.0023019 | 0.0023019 | -6.074
4/05/2012 | 0.0059306 | 0.0059306 | -5.1276
5/05/2012 | 0.0045121 | 0.0045121 | -5.401
6/05/2012 | 0.016661 | 0.016661 | -4.0947
7/05/2012 | 0.022757 | 0.022757 | -3.7829
8/05/2012 | 0.0043696 | 0.0043696 | -5.4331
9/05/2012 | 0.15161 | 0.15161 | -1.8864
10/05/2012 | 0.0087772 | 0.0087772 | -4.7356
11/05/2012 | 0.19654 | 0.19654 | -1.6269
12/05/2012 | 0.046074 | 0.046074 | -3.0775
13/05/2012 | 0.075755 | 0.075755 | -2.5802
14/05/2012 | 0.028969 | 0.028969 | -3.5415
15/05/2012 | 0.0057216 | 0.0057216 | -5.1635
16/05/2012 | 0.45406 | 0.45406 | -0.78953
17/05/2012 | 0.0015009 | 0.0015009 | -6.5017
18/05/2012 | 0.00083275 | 0.00083275 | -7.0908
19/05/2012 | 0.016551 | 0.016551 | -4.1013
20/05/2012 | 0.00090558 | 0.00090558 | -7.0069
21/05/2012 | 0.019701 | 0.019701 | -3.9271
22/05/2012 | 0.0097904 | 0.0097904 | -4.6264
23/05/2012 | 0.00095941 | 0.00095941 | -6.9492
24/05/2012 | 0.0010987 | 0.0010987 | -6.8136
25/05/2012 | 0.013837 | 0.013837 | -4.2804
26/05/2012 | 0.0013109 | 0.0013109 | -6.6371
27/05/2012 | 0.0071053 | 0.0071053 | -4.9469
28/05/2012 | 0.01676 | 0.01676 | -4.0888
29/05/2012 | 0.010994 | 0.010994 | -4.5104
30/05/2012 | 0.047416 | 0.047416 | -3.0488
31/05/2012 | 0.068948 | 0.068948 | -2.6744
1/06/2012 | 0.00039896 | 0.00039896 | -7.8266
2/06/2012 | 0.0011336 | 0.0011336 | -6.7824
3/06/2012 | 0.0017953 | 0.0017953 | -6.3226
4/06/2012 | 0.38007 | 0.38007 | -0.96739
5/06/2012 | 0.0013109 | 0.0013109 | -6.6371
6/06/2012 | 0.012874 | 0.012874 | -4.3525
7/06/2012 | 0.011114 | 0.011114 | -4.4996
8/06/2012 | 0.17664 | 0.17664 | -1.7336
9/06/2012 | 0.0023209 | 0.0023209 | -6.0658
10/06/2012 | 0.0003768 | 0.0003768 | -7.8838
11/06/2012 | 0.059103 | 0.059103 | -2.8285
12/06/2012 | 0.0044741 | 0.0044741 | -5.4095
13/06/2012 | 0.051143 | 0.051143 | -2.9731
14/06/2012 | 0.0014407 | 0.0014407 | -6.5426
15/06/2012 | 0.023716 | 0.023716 | -3.7416
16/06/2012 | 0.010794 | 0.010794 | -4.5288
17/06/2012 | 0.00065544 | 0.00065544 | -7.3302
18/06/2012 | 0.043724 | 0.043724 | -3.1299
19/06/2012 | 0.0013552 | 0.0013552 | -6.6038
20/06/2012 | 0.0021563 | 0.0021563 | -6.1394
21/06/2012 | 0.10079 | 0.10079 | -2.2947
22/06/2012 | 0.028896 | 0.028896 | -3.544
23/06/2012 | 0.061127 | 0.061127 | -2.7948
24/06/2012 | 0.03325 | 0.03325 | -3.4037
25/06/2012 | 0.041264 | 0.041264 | -3.1878
26/06/2012 | 0.010762 | 0.010762 | -4.5317
27/06/2012 | 0.22727 | 0.22727 | -1.4816
28/06/2012 | 0.0011019 | 0.0011019 | -6.8107
29/06/2012 | 0.01662 | 0.01662 | -4.0971
30/06/2012 | 0.14026 | 0.14026 | -1.9642
1/07/2012 | 0.015389 | 0.015389 | -4.1741
2/07/2012 | 0.021262 | 0.021262 | -3.8508
3/07/2012 | 0.079859 | 0.079859 | -2.5275
4/07/2012 | 0.025939 | 0.025939 | -3.652
5/07/2012 | 0.0031379 | 0.0031379 | -5.7642
6/07/2012 | 0.10249 | 0.10249 | -2.278
7/07/2012 | 0.021297 | 0.021297 | -3.8492
8/07/2012 | 0.047632 | 0.047632 | -3.0443
9/07/2012 | 0.0010259 | 0.0010259 | -6.8822
10/07/2012 | 0.00016782 | 0.00016782 | -8.6926
11/07/2012 | 0.041938 | 0.041938 | -3.1716
12/07/2012 | 0.011443 | 0.011443 | -4.4704
13/07/2012 | 0.0013774 | 0.0013774 | -6.5876
14/07/2012 | 0.0092743 | 0.0092743 | -4.6805
15/07/2012 | 0.046204 | 0.046204 | -3.0747
16/07/2012 | 0.0029415 | 0.0029415 | -5.8288
17/07/2012 | 0.18764 | 0.18764 | -1.6732
18/07/2012 | 0.00078526 | 0.00078526 | -7.1495
19/07/2012 | 0.029086 | 0.029086 | -3.5375
20/07/2012 | 0.0098474 | 0.0098474 | -4.6205
21/07/2012 | 7.5993e-05 | 7.5993e-05 | -9.4849
22/07/2012 | 9.1824e-05 | 9.1824e-05 | -9.2956
23/07/2012 | 0.54308 | 0.54308 | -0.6105
24/07/2012 | 0.0026502 | 0.0026502 | -5.9331
25/07/2012 | 0.48757 | 0.48757 | -0.71832
26/07/2012 | 0.0026882 | 0.0026882 | -5.9189
27/07/2012 | 0.0023969 | 0.0023969 | -6.0336
28/07/2012 | 0.010348 | 0.010348 | -4.571
29/07/2012 | 0.0094389 | 0.0094389 | -4.6629
30/07/2012 | 0.0028877 | 0.0028877 | -5.8473
31/07/2012 | 0.00158 | 0.00158 | -6.4503
1/08/2012 | 0.31676 | 0.31676 | -1.1496
2/08/2012 | 0.0051137 | 0.0051137 | -5.2758
3/08/2012 | 0.00058578 | 0.00058578 | -7.4426
4/08/2012 | 0.0059686 | 0.0059686 | -5.1212
5/08/2012 | 0.0003103 | 0.0003103 | -8.078
6/08/2012 | 0.0031157 | 0.0031157 | -5.7713
7/08/2012 | 0.00019948 | 0.00019948 | -8.5198
8/08/2012 | 0.037376 | 0.037376 | -3.2867
9/08/2012 | 0.010797 | 0.010797 | -4.5285
10/08/2012 | 0.023776 | 0.023776 | -3.7391
11/08/2012 | 0.0034798 | 0.0034798 | -5.6608
12/08/2012 | 0.002112 | 0.002112 | -6.1601
13/08/2012 | 0.00727 | 0.00727 | -4.924
14/08/2012 | 0.023662 | 0.023662 | -3.7439
15/08/2012 | 0.0039959 | 0.0039959 | -5.5225
16/08/2012 | 0.061006 | 0.061006 | -2.7968
17/08/2012 | 0.011738 | 0.011738 | -4.4449
18/08/2012 | 0.0017352 | 0.0017352 | -6.3567
19/08/2012 | 0.0006491 | 0.0006491 | -7.3399
20/08/2012 | 0.14739 | 0.14739 | -1.9146
21/08/2012 | 0.0014122 | 0.0014122 | -6.5626
22/08/2012 | 0.0022228 | 0.0022228 | -6.109
23/08/2012 | 0.0010037 | 0.0010037 | -6.904
24/08/2012 | 0.0046292 | 0.0046292 | -5.3754
25/08/2012 | 0 | 0
26/08/2012 | 0.013672 | 0.013672 | -4.2924
27/08/2012 | 0 | 0
28/08/2012 | 0 | 0
29/08/2012 | 0.0024033 | 0.0024033 | -6.0309
30/08/2012 | 0.00071876 | 0.00071876 | -7.238
31/08/2012 | 0.00056045 | 0.00056045 | -7.4868
1/09/2012 | 0.0015895 | 0.0015895 | -6.4443
2/09/2012 | 0.17455 | 0.17455 | -1.7456
3/09/2012 | 0.0025901 | 0.0025901 | -5.9561
4/09/2012 | 0.005386 | 0.005386 | -5.224
5/09/2012 | 0.91527 | 0.91527 | -0.088542
6/09/2012 | 0.18161 | 0.18161 | -1.7059
7/09/2012 | 0 | 0
8/09/2012 | 0.0022038 | 0.0022038 | -6.1176
9/09/2012 | 0.00061744 | 0.00061744 | -7.3899
10/09/2012 | 0.53963 | 0.53963 | -0.61687
11/09/2012 | 0.003103 | 0.003103 | -5.7754
12/09/2012 | 0 | 0
13/09/2012 | 0.36767 | 0.36767 | -1.0006
14/09/2012 | 0.00074093 | 0.00074093 | -7.2076
15/09/2012 | 0.00057311 | 0.00057311 | -7.4644
16/09/2012 | 0.0022228 | 0.0022228 | -6.109
17/09/2012 | 0.13873 | 0.13873 | -1.9752
18/09/2012 | 0 | 0
19/09/2012 | 0.0010797 | 0.0010797 | -6.831
20/09/2012 | 0.022662 | 0.022662 | -3.7871
21/09/2012 | 0.011858 | 0.011858 | -4.4348
22/09/2012 | 0.0056741 | 0.0056741 | -5.1718
23/09/2012 | 0 | 0
24/09/2012 | 0.015591 | 0.015591 | -4.1611
25/09/2012 | 0.30967 | 0.30967 | -1.1722
26/09/2012 | 0 | 0
27/09/2012 | 0.0095339 | 0.0095339 | -4.6529
28/09/2012 | 0.10053 | 0.10053 | -2.2973
29/09/2012 | 0.010984 | 0.010984 | -4.5113
30/09/2012 | 0.0039896 | 0.0039896 | -5.5241
1/10/2012 | 0.061887 | 0.061887 | -2.7825
2/10/2012 | 0.030375 | 0.030375 | -3.4941
3/10/2012 | 0.0033342 | 0.0033342 | -5.7035
4/10/2012 | 0.23746 | 0.23746 | -1.4377
5/10/2012 | 0.0039485 | 0.0039485 | -5.5344
6/10/2012 | 0.00094358 | 0.00094358 | -6.9658
7/10/2012 | 0.006529 | 0.006529 | -5.0315
8/10/2012 | 0.0006966 | 0.0006966 | -7.2693
9/10/2012 | 0.030578 | 0.030578 | -3.4875
10/10/2012 | 0.023323 | 0.023323 | -3.7583
11/10/2012 | 0.00015515 | 0.00015515 | -8.7711
12/10/2012 | 0.0014692 | 0.0014692 | -6.523
13/10/2012 | 0.0013235 | 0.0013235 | -6.6274
14/10/2012 | 0.0018112 | 0.0018112 | -6.3138
15/10/2012 | 0.085105 | 0.085105 | -2.4639
16/10/2012 | 0 | 0
17/10/2012 | 0.0010006 | 0.0010006 | -6.9072
18/10/2012 | 0.0014217 | 0.0014217 | -6.5559
19/10/2012 | 0.00099107 | 0.00099107 | -6.9167
20/10/2012 | 0.00080426 | 0.00080426 | -7.1256
21/10/2012 | 0.2436 | 0.2436 | -1.4122
22/10/2012 | 0.0014597 | 0.0014597 | -6.5295
23/10/2012 | 0.22065 | 0.22065 | -1.5112
24/10/2012 | 0.0010734 | 0.0010734 | -6.8369
25/10/2012 | 0.099769 | 0.099769 | -2.3049
26/10/2012 | 0.0007346 | 0.0007346 | -7.2162
27/10/2012 | 0.3751 | 0.3751 | -0.98057
28/10/2012 | 0.00075993 | 0.00075993 | -7.1823
29/10/2012 | 0.0016117 | 0.0016117 | -6.4305
30/10/2012 | 0.28857 | 0.28857 | -1.2428
31/10/2012 | 0.81725 | 0.81725 | -0.20181
1/11/2012 | 0.015458 | 0.015458 | -4.1696
2/11/2012 | 0.0006491 | 0.0006491 | -7.3399
3/11/2012 | 0 | 0
4/11/2012 | 0.00089291 | 0.00089291 | -7.021
5/11/2012 | 0.010503 | 0.010503 | -4.5561
6/11/2012 | 0.0043601 | 0.0043601 | -5.4353
7/11/2012 | 0.0036571 | 0.0036571 | -5.6111
8/11/2012 | 0.0010639 | 0.0010639 | -6.8458
9/11/2012 | 0.032886 | 0.032886 | -3.4147
10/11/2012 | 0.0003293 | 0.0003293 | -8.0185
11/11/2012 | 0.017694 | 0.017694 | -4.0346
12/11/2012 | 0.0015199 | 0.0015199 | -6.4891
13/11/2012 | 0.0056425 | 0.0056425 | -5.1774
14/11/2012 | 0 | 0
15/11/2012 | 0.0029447 | 0.0029447 | -5.8277
16/11/2012 | 0.011399 | 0.011399 | -4.4742
17/11/2012 | 0.0096257 | 0.0096257 | -4.6433
18/11/2012 | 0.0003483 | 0.0003483 | -7.9624
19/11/2012 | 0.029517 | 0.029517 | -3.5228
20/11/2012 | 0.0027452 | 0.0027452 | -5.8979
21/11/2012 | 0.32022 | 0.32022 | -1.1387
22/11/2012 | 0.081553 | 0.081553 | -2.5065
23/11/2012 | 0.012333 | 0.012333 | -4.3955
24/11/2012 | 0.20352 | 0.20352 | -1.592
25/11/2012 | 0.71724 | 0.71724 | -0.33234
26/11/2012 | 0.31921 | 0.31921 | -1.1419
27/11/2012 | 0.90026 | 0.90026 | -0.10507
28/11/2012 | 0.00063327 | 0.00063327 | -7.3646
29/11/2012 | 1.271 | 1.271 | 0.23982
30/11/2012 | 0.027133 | 0.027133 | -3.607
1/12/2012 | 0.52701 | 0.52701 | -0.64054
2/12/2012 | 0.0015262 | 0.0015262 | -6.485
3/12/2012 | 0.0065227 | 0.0065227 | -5.0325
4/12/2012 | 0.34614 | 0.34614 | -1.0609
5/12/2012 | 0.013951 | 0.013951 | -4.2722
6/12/2012 | 0.008736 | 0.008736 | -4.7403
7/12/2012 | 0.0069248 | 0.0069248 | -4.9726
8/12/2012 | 0.18252 | 0.18252 | -1.7009
9/12/2012 | 0.021762 | 0.021762 | -3.8276
10/12/2012 | 0.00056361 | 0.00056361 | -7.4811
11/12/2012 | 0.00030397 | 0.00030397 | -8.0986
12/12/2012 | 0.29139 | 0.29139 | -1.2331
13/12/2012 | 1.1317 | 1.1317 | 0.12375
14/12/2012 | 0.078187 | 0.078187 | -2.5487
15/12/2012 | 0.036445 | 0.036445 | -3.312
16/12/2012 | 0.30444 | 0.30444 | -1.1893
17/12/2012 | 0.0028877 | 0.0028877 | -5.8473
18/12/2012 | 0.0043981 | 0.0043981 | -5.4266
19/12/2012 | 0.0017637 | 0.0017637 | -6.3404
20/12/2012 | 0.0010544 | 0.0010544 | -6.8548
21/12/2012 | 0.00098474 | 0.00098474 | -6.9231
22/12/2012 | 0.00088658 | 0.00088658 | -7.0281
23/12/2012 | 0.32991 | 0.32991 | -1.1089
24/12/2012 | 0.015085 | 0.015085 | -4.1941
25/12/2012 | 0.00082642 | 0.00082642 | -7.0984
26/12/2012 | 0.00016782 | 0.00016782 | -8.6926
27/12/2012 | 0.0013995 | 0.0013995 | -6.5716
28/12/2012 | 0.014407 | 0.014407 | -4.24
29/12/2012 | 0.0062377 | 0.0062377 | -5.0771
30/12/2012 | 0.00019315 | 0.00019315 | -8.5521
31/12/2012 | 0.00019631 | 0.00019631 | -8.5358
Note:
Exclusions refer to upstream events only and do not refer MED exclusions.
MED calculation starts from 5 years prior to the relevant regulatory reporting year (e.g. 2013 requires data from 1 January 2008 to 31 December 2012).
Contents

## 1e. STPIS Exclusions
CitiPower Pty
STPIS Data Reporting
2013
Exclusions
Table 1: Exclusions
Date of event (DD/MM/YYYY) | Feeder ID / name | Feeder classification | Number of interruptions (unplanned) | Duration of interruption (unplanned) (mins) | Total unplanned minutes off supply | Event category (use Exclusion categories listed in section 3.3 (a) of the AER's STPIS) | Effect on unplanned SAIDI | Effect on unplanned SAIFI | Effect on unplanned MAIFI | Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning | Cause of event (Use categories listed in table 1, Template 6C)
16/03/2013 | AR002 | Urban | 491 | 57 | 27987 | 3.3 (b) | 0.087474 | 0.0015346 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR003 | Urban | 1150 | 57 | 65550 | 3.3 (b) | 0.20488 | 0.0035944 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR004 | Urban | 2325 | 57 | 132525 | 3.3 (b) | 0.41421 | 0.0072669 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR005 | Urban | 888 | 57 | 50616 | 3.3 (b) | 0.1582 | 0.0027755 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR006 | Urban | 332 | 57 | 18924 | 3.3 (b) | 0.059148 | 0.0010377 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR007 | Urban | 1611 | 57 | 91827 | 3.3 (b) | 0.28701 | 0.0050352 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR009 | Urban | 1024 | 57 | 58368 | 3.3 (b) | 0.18243 | 0.0032006 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR010 | Urban | 2363 | 57 | 134691 | 3.3 (b) | 0.42098 | 0.0073856 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR011 | Urban | 1376 | 57 | 78432 | 3.3 (b) | 0.24514 | 0.0043007 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR012 | Urban | 498 | 57 | 28386 | 3.3 (b) | 0.088721 | 0.0015565 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | AR013 | Urban | 370 | 57 | 21090 | 3.3 (b) | 0.065918 | 0.0011564 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC006 | Urban | 50 | 93 | 4650 | 3.3 (b) | 0.014534 | 0.00015628 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
16/03/2013 | BC006 | Urban | 1279 | 15 | 19185 | 3.3 (b) | 0.059963 | 0.0039976 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC011 | Urban | 266 | 15 | 3990 | 3.3 (b) | 0.012471 | 0.00083139 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC012 | Urban | 1741 | 15 | 26115 | 3.3 (b) | 0.081623 | 0.0054416 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC013 | Urban | 2118 | 15 | 31770 | 3.3 (b) | 0.099298 | 0.0066199 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC014 | Urban | 450 | 15 | 6750 | 3.3 (b) | 0.021097 | 0.0014065 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC015 | Urban | 3102 | 15 | 46530 | 3.3 (b) | 0.14543 | 0.0096954 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC020 | Urban | 162 | 15 | 2430 | 3.3 (b) | 0.0075951 | 0.00050634 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC020 | Urban | 1724 | 15 | 25860 | 3.3 (b) | 0.080826 | 0.0053884 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | BC022 | Urban | 396 | 15 | 5940 | 3.3 (b) | 0.018566 | 0.0012377 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
16/03/2013 | NC001 | Urban | 247 | 35 | 8645 | 3.3 (b) | 0.02702 | 0.00077201 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
16/03/2013 | TK009 | Urban | 1 | 76 | 76 | 3.3 (b) | 0.00023754 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
8/07/2013 | BK002 | Urban | 3 | 346 | 1038 | 3.3 (b) | 0.0032443 | 9.3766e-06 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | BK004 | Urban | 1 | 346 | 346 | 3.3 (b) | 0.0010814 | 3.1255e-06 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | C023 | Urban | 60 | 400 | 24000 | 3.3 (b) | 0.075013 | 0.00018753 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | C023 | Urban | 66 | 400 | 26400 | 3.3 (b) | 0.082514 | 0.00020629 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | C023 | Urban | 128 | 400 | 51200 | 3.3 (b) | 0.16003 | 0.00040007 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | F037 | Urban | 1 | 114 | 114 | 3.3 (b) | 0.00035631 | 3.1255e-06 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC001 | Urban | 63 | 344 | 21672 | 3.3 (b) | 0.067737 | 0.00019691 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC001 | Urban | 1395 | 343 | 478485 | 3.3 (b) | 1.4955 | 0.0043601 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC002 | Urban | 3197 | 343 | 1096571 | 3.3 (b) | 3.4274 | 0.0099923 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC004 | Urban | 3248 | 343 | 1114064 | 3.3 (b) | 3.482 | 0.010152 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC005 | Urban | 1183 | 343 | 405769 | 3.3 (b) | 1.2682 | 0.0036975 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC006 | Urban | 1 | 247 | 247 | 3.3 (b) | 0.00077201 | 3.1255e-06 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC006 | Urban | 935 | 343 | 320705 | 3.3 (b) | 1.0024 | 0.0029224 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC009 | Urban | 1697 | 344 | 583768 | 3.3 (b) | 1.8246 | 0.005304 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC010 | Urban | 944 | 344 | 324736 | 3.3 (b) | 1.015 | 0.0029505 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC013 | Urban | 1868 | 344 | 642592 | 3.3 (b) | 2.0084 | 0.0058385 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC014 | Urban | 1255 | 344 | 431720 | 3.3 (b) | 1.3494 | 0.0039225 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | NC015 | Urban | 2312 | 344 | 795328 | 3.3 (b) | 2.4858 | 0.0072262 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | SK025 | Urban | 1 | 41 | 41 | 3.3 (b) | 0.00012815 | 3.1255e-06 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Third party impacts
8/07/2013 | WB001 | Urban | 876 | 347 | 303972 | 3.3 (b) | 0.95008 | 0.002738 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB002 | Urban | 3447 | 347 | 1196109 | 3.3 (b) | 3.7385 | 0.010774 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB004 | Urban | 399 | 347 | 138453 | 3.3 (b) | 0.43274 | 0.0012471 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB005 | Urban | 740 | 347 | 256780 | 3.3 (b) | 0.80258 | 0.0023129 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB009 | Urban | 1094 | 346 | 378524 | 3.3 (b) | 1.1831 | 0.0034193 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB010 | Urban | 659 | 346 | 228014 | 3.3 (b) | 0.71267 | 0.0020597 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB011 | Urban | 1675 | 346 | 579550 | 3.3 (b) | 1.8114 | 0.0052353 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB013 | Urban | 2211 | 360.3704 | 796779 | 3.3 (b) | 2.4904 | 0.0069106 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB014 | Urban | 122 | 346 | 42212 | 3.3 (b) | 0.13194 | 0.00038132 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
8/07/2013 | WB015 | Urban | 863 | 399.6918 | 344934 | 3.3 (b) | 1.0781 | 0.0026973 | 0 | Threshold Exceeded due to Equipment failure in Brunswick/Nor | Equipment failure
12/08/2013 | AP008 | Urban | 1 | 157 | 157 | 3.3 (b) | 0.00049071 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | C023 | Urban | 1 | 546 | 546 | 3.3 (b) | 0.0017065 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | C023 | Urban | 3 | 732 | 2196 | 3.3 (b) | 0.0068637 | 9.3766e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | CW009 | Urban | 108 | 440 | 47520 | 3.3 (b) | 0.14853 | 0.00033756 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | CW013 | Urban | 21 | 643 | 13503 | 3.3 (b) | 0.042204 | 6.5636e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Third party impacts
12/08/2013 | F035 | Urban | 9 | 295 | 2655 | 3.3 (b) | 0.0082983 | 2.813e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | L002 | Urban | 1863 | 0 | 0 | 3.3 (b) | 0 | 0 | 0.0058229 | Threshold Exceeded due to Storms acrosss network | Vegetation
12/08/2013 | L014 | Urban | 8 | 788 | 6304 | 3.3 (b) | 0.019703 | 2.5004e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | L018 | Urban | 39 | 1011 | 39429 | 3.3 (b) | 0.12324 | 0.0001219 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
12/08/2013 | NC001 | Urban | 1 | 145 | 145 | 3.3 (b) | 0.0004532 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | NC002 | Urban | 1 | 418 | 418 | 3.3 (b) | 0.0013065 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
12/08/2013 | NC002 | Urban | 43 | 618 | 26574 | 3.3 (b) | 0.083058 | 0.0001344 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | NC002 | Urban | 3074 | 112.2521 | 345063 | 3.3 (b) | 1.0785 | 0.0096079 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | NC005 | Urban | 1134 | 124.7434 | 141459 | 3.3 (b) | 0.44214 | 0.0035444 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | NC009 | Urban | 3 | 333 | 999 | 3.3 (b) | 0.0031224 | 9.3766e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | NC013 | Urban | 1 | 359 | 359 | 3.3 (b) | 0.0011221 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | NC014 | Urban | 139 | 411 | 57129 | 3.3 (b) | 0.17856 | 0.00043445 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | Q002 | Urban | 1717 | 225.187 | 386646 | 3.3 (b) | 1.2085 | 0.0053665 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
12/08/2013 | Q019 | Urban | 9 | 601 | 5409 | 3.3 (b) | 0.016906 | 2.813e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | Q019 | Urban | 2266 | 149.7502 | 339334 | 3.3 (b) | 1.0606 | 0.0070825 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
12/08/2013 | SK005 | Urban | 9 | 698 | 6282 | 3.3 (b) | 0.019635 | 2.813e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | WB002 | Urban | 1 | 159 | 159 | 3.3 (b) | 0.00049696 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
12/08/2013 | WB002 | Urban | 3 | 264 | 792 | 3.3 (b) | 0.0024754 | 9.3766e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | WD013 | Urban | 1 | 23 | 23 | 3.3 (b) | 7.1887e-05 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
12/08/2013 | WD013 | Urban | 2 | 409 | 818 | 3.3 (b) | 0.0025567 | 6.2511e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
12/08/2013 | WD031 | Urban | 13 | 624 | 8112 | 3.3 (b) | 0.025354 | 4.0632e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | WD031 | Urban | 2002 | 105.0629 | 210336 | 3.3 (b) | 0.65741 | 0.0062573 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
12/08/2013 | WD032 | Urban | 1 | 831 | 831 | 3.3 (b) | 0.0025973 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
9/09/2013 | RD001 | Urban | 1662 | 19 | 31578 | 3.3 (a) (6 | 0.098698 | 0.0051946 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD002 | Urban | 1815 | 19 | 34485 | 3.3 (a) (6 | 0.10778 | 0.0056729 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD004 | Urban | 256 | 19 | 4864 | 3.3 (a) (6 | 0.015203 | 0.00080014 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD005 | Urban | 1745 | 19 | 33155 | 3.3 (a) (6 | 0.10363 | 0.0054541 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD006 | Urban | 1320 | 19 | 25080 | 3.3 (a) (6 | 0.078388 | 0.0041257 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD009 | Urban | 457 | 19 | 8683 | 3.3 (a) (6 | 0.027139 | 0.0014284 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD010 | Urban | 236 | 19 | 4484 | 3.3 (a) (6 | 0.014015 | 0.00073763 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD013 | Urban | 1670 | 19 | 31730 | 3.3 (a) (6 | 0.099173 | 0.0052196 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD014 | Urban | 1661 | 19 | 31559 | 3.3 (a) (6 | 0.098639 | 0.0051915 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
9/09/2013 | RD015 | Urban | 1009 | 19 | 19171 | 3.3 (a) (6 | 0.05992 | 0.0031537 | 0 | Failure of transmission connection assets at Springvale term | Transmission failure
1/10/2013 | AP005 | Urban | 1 | 692 | 692 | 3.3 (b) | 0.0021629 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
1/10/2013 | BC006 | Urban | 1283 | 89 | 114187 | 3.3 (b) | 0.3569 | 0.0040101 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BC011 | Urban | 264 | 90 | 23760 | 3.3 (b) | 0.074263 | 0.00082514 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BC012 | Urban | 1769 | 90 | 159210 | 3.3 (b) | 0.49762 | 0.0055291 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BC013 | Urban | 121 | 327 | 39567 | 3.3 (b) | 0.12367 | 0.00037819 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BC013 | Urban | 2106 | 173 | 364338 | 3.3 (b) | 1.1388 | 0.0065824 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BC014 | Urban | 445 | 91 | 40495 | 3.3 (b) | 0.12657 | 0.0013909 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BC015 | Urban | 60 | 181 | 10860 | 3.3 (b) | 0.033943 | 0.00018753 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
1/10/2013 | BC015 | Urban | 3093 | 91 | 281463 | 3.3 (b) | 0.87972 | 0.0096673 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BC020 | Urban | 1887 | 92 | 173604 | 3.3 (b) | 0.54261 | 0.0058979 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BC022 | Urban | 400 | 92 | 36800 | 3.3 (b) | 0.11502 | 0.0012502 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | BK009 | Urban | 1 | 71 | 71 | 3.3 (b) | 0.00022191 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
1/10/2013 | BK009 | Urban | 7 | 40 | 280 | 3.3 (b) | 0.00087515 | 2.1879e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | BK009 | Urban | 34 | 443 | 15062 | 3.3 (b) | 0.047077 | 0.00010627 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
1/10/2013 | C022 | Urban | 1485 | 380.5185 | 565070 | 3.3 (b) | 1.7661 | 0.0046414 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | C023 | Urban | 37 | 353 | 13061 | 3.3 (b) | 0.040823 | 0.00011564 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | C028 | Urban | 55 | 318 | 17490 | 3.3 (b) | 0.054666 | 0.0001719 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | C029 | Urban | 66 | 796 | 52536 | 3.3 (b) | 0.1642 | 0.00020629 | 0 | Threshold Exceeded due to Storms acrosss network | Animals
1/10/2013 | CL022 | Urban | 21 | 500 | 10500 | 3.3 (b) | 0.032818 | 6.5636e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | CL036 | Urban | 1 | 485 | 485 | 3.3 (b) | 0.0015159 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | CL036 | Urban | 1638 | 496 | 812448 | 3.3 (b) | 2.5393 | 0.0051196 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | DA008 | Urban | 1 | 351 | 351 | 3.3 (b) | 0.0010971 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | F028 | Urban | 39 | 883 | 34437 | 3.3 (b) | 0.10763 | 0.0001219 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | FF084 | Urban | 1 | 241 | 241 | 3.3 (b) | 0.00075325 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
1/10/2013 | L001 | Urban | 1202 | 48.6106 | 58430 | 3.3 (b) | 0.18263 | 0.0037569 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | L009 | Urban | 13 | 137 | 1781 | 3.3 (b) | 0.0055666 | 4.0632e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | L020 | Urban | 32 | 200 | 6400 | 3.3 (b) | 0.020003 | 0.00010002 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | NC002 | Urban | 3187 | 443 | 1411841 | 3.3 (b) | 4.4128 | 0.0099611 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
1/10/2013 | NC009 | Urban | 312 | 525 | 163800 | 3.3 (b) | 0.51196 | 0.00097517 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | NC013 | Urban | 1 | 310 | 310 | 3.3 (b) | 0.00096892 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | NS013 | Urban | 20 | 1152 | 23040 | 3.3 (b) | 0.072012 | 6.2511e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | R024 | Urban | 9 | 167 | 1503 | 3.3 (b) | 0.0046977 | 2.813e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | RD004 | Urban | 257 | 471 | 121047 | 3.3 (b) | 0.37834 | 0.00080326 | 0 | Threshold Exceeded due to Storms acrosss network | Inter-distributor connection
1/10/2013 | RD014 | Urban | 1661 | 447.9175 | 743991 | 3.3 (b) | 2.3254 | 0.0051915 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | RD015 | Urban | 95 | 633 | 60135 | 3.3 (b) | 0.18795 | 0.00029693 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | SK005 | Urban | 63 | 368 | 23184 | 3.3 (b) | 0.072462 | 0.00019691 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | SK023 | Urban | 1 | 252 | 252 | 3.3 (b) | 0.00078764 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
1/10/2013 | TK005 | Urban | 18 | 562 | 10116 | 3.3 (b) | 0.031618 | 5.626e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | TK006 | Urban | 1 | 569 | 569 | 3.3 (b) | 0.0017784 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | TK006 | Urban | 1 | 754 | 754 | 3.3 (b) | 0.0023567 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | TK014 | Urban | 4 | 156 | 624 | 3.3 (b) | 0.0019503 | 1.2502e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Weather
1/10/2013 | WB013 | Urban | 1 | 349 | 349 | 3.3 (b) | 0.0010908 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | WB013 | Urban | 1 | 488 | 488 | 3.3 (b) | 0.0015253 | 3.1255e-06 | 0 | Threshold Exceeded due to Storms acrosss network | Equipment failure
1/10/2013 | WD013 | Urban | 22 | 597 | 13134 | 3.3 (b) | 0.041051 | 6.8762e-05 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
1/10/2013 | WD022 | Urban | 799 | 210.5444 | 168225 | 3.3 (b) | 0.52579 | 0.0024973 | 0 | Threshold Exceeded due to Storms acrosss network | Vegetation
Note:
The AER's Electricity distribution network service providers, Service target performance incentive scheme, November 2009, p. 22, defines SAIDI and SAIFI.
The AER will apply the ESCV's definition of MAIFI for transitional reasons. The ESCV's Information specification (Service performance) for Victorian Electricity Distributors, 1 January 2009, p. 30, defines MAIFI as follows:
MAIFI - The total number of momentary interruptions divided by the average number of distribution customers over the regulatory reporting period. (where the distribution customers are network or per feeder based, as appropriate).
Contents

## 2. Demand
CitiPower Pty
Demand | THIS TEMPLATE IS NOT REQUIRED
2013 | AS PER AER EMAIL 18/12/13
Table 1 Customer Numbers by Voltage Level
Customer numbers by voltage level
Subtransmission
High Voltage
Low Voltage Residential
Low Voltage Non-Residential
Total - all customers | 0
Table 2 New Customer Connections
Note: 'Total customer numbers' is the total average of end of prior year customers and end of current year customers
New connections
Total new connections
New customer connections as a % of total customers | #DIV/0!
Table 3 Customer Disconnections
Note: 'Total customer numbers' is the total average of end of prior year customers and end of current year customers
Disconnections
Total disconnections
Disconnections as a % of total customers | #DIV/0!
Table 4 Electricity Consumption
Electricity consumption by voltage level (MWh)
Subtransmission
High Voltage
Low Voltage Residential
Low Voltage Non-Residential
Controlled load
Total consumption | 0
Table 5 Maximum Coincident Demand at the Network Level
Note: a) Maximum Coincident Demand at the Network Level is calculated as the sum of all maximum coincident demand for zone substations and all feeders from terminal stations.
b) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
c) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
d) The PoE level only applies to the forecasts
Network coincident maximum demand |  |  |  |  | t+1 forecast
| Forecast | Actual: raw | Actual: weather normalised | Variation %
90% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
50% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
10% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
Table 6 Summer or winter non-coincident maximum demand by zone substation
Note: a) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
b) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
c) The PoE level only applies to the forecasts
Summer and winter maximum demand - ZS | [12 empty] | t+1 forecast |  |  |  | Nameplate rating (MVA)
POE level = 50% | Forecast |  |  |  | Actual: raw |  |  |  | Actual: weather normalised
Location | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF
<ZS 1> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 1> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 2> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 2> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 3> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 3> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS n> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS n> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
Contents

## 3. Asset Installation
CitiPower Pty
Asset Installation |  | THIS TEMPLATE IS NOT REQUIRED
2013 |  | AS PER AER EMAIL 18/12/13
Instructions
Insert rows for each of its asset types under each high level asset group. Additional groups may be added if a particular asset is not encompassed by the asset groups in the table.
Develop a set of asset types under the high level asset groups that represent its network asset base.
In determining whether a new asset type is required, whether asset types should be aggregated or whether asset types should be disaggregated, the DNSP should consider:
- the proportion of the overall replacement expenditure forecast for the assets
- the differentiation of unit replacement costs into clear and distinguishable distributions
- the differentiation of replacement lives into clear and distinguishable distributions
- multiple 'end of life' actions such as 'replacement' or 'life extension' (eg pole staking) - in the case of 'life extension', the DNSP should appropriately account for this in defining the replacement life and unit cost for the asset category.
Table 1 For each asset type, provide:
a) the mean replacement asset life (years)
b) the standard deviation of the mean replacement asset life
c) the replacement unit cost ($ nominal).
d) the total number of asset failures during the regulatory year
e) the total quantity (number) of each asset type that was commissioned in the relevant regulatory reporting year.
Table 1 Asset age profile for distribution system assets
Statutory Account code or reference to account code | Asset group | Replacement life (years) |  | Replacement unit cost | Number of asset failures | Total quantity replaced | Total quantity installed | Year Commissioned (number of assets commissioned in each year)
|  | Mean | Standard Deviation |  |  |  |  | 1910 | 1911 | 1912 | 1913 | 1914 | 1915 | 1916 | 1917 | 1918 | 1919 | 1920 | 1921 | 1922 | 1923 | 1924 | 1925 | 1926 | 1927 | 1928 | 1929 | 1930 | 1931 | 1932 | 1933 | 1934 | 1935 | 1936 | 1937 | 1938 | 1939 | 1940 | 1941 | 1942 | 1943 | 1944 | 1945 | 1946 | 1947 | 1948 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012
Poles
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Pole top structures
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Conductors
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Underground cables
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Services (incl. LV pillars and LV service pits)
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution transformers
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution switchgear
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution 'other assets'
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone transformers
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone switchgear
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone 'other assets'
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
SCADA and protection
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Other
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Contents

## 4. Customer Service
CitiPower Pty
Customer Service
2013
Table 1 Quality of supply
Over voltage events - due to high voltage injection | 0
Customers receiving over-voltage - due to high voltage injection | 39
Over voltage events - due to lightning | 0
Customers receiving over-voltage - due to lightning | 17
Over voltage events - due to voltage regulation or other cause | 4
Customers receiving over-voltage - due to voltage regulation or other cause | 287
Voltage variations - steady state (zone sub) | 732
Voltage variations - one minute (zone sub) | 2913
Voltage variations - 10 seconds (zone sub) Min<0.7 | 540
Voltage variations - 10 seconds (zone sub) Min<0.8 | 653
Voltage variations - 10 seconds (zone sub) Min<0.9 | 967
Voltage variations - steady state (feeder) | 19631
Voltage variations - % zone subs monitored | 97
Voltage variations - % feeders monitored | 87
Table 2 Complaints - technical quality of supply
Complaints - technical quality of supply - number | 4
Complaints by category (%)
Low voltage supply | 25%
Voltage dips | 0%
Voltage swell | 25%
Voltage spike (impulsive transient) | 50%
TV or radio interference | 0%
Noise from appliances | 0%
Other | 0%
Complaints by Likely Cause (%)
Network equipment faulty | 0%
Network interference by NSP equipment | 0%
Network interference by another customer | 25%
Network limitation | 50%
Customer internal problem | 0%
No problem identified | 25%
Environmental | 0%
Other | 0%
Table 3 Customer service
Timely provision of services
Connections made | 45034
Connections not made on agreed date | 52
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 257.8
Streetlights - not repaired by "fix by" date | 17
Streetlights - average number of days to repair | 6.3
Total streetlights | 52164
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 106184
Calls to fault line not answered within 30 seconds | 13834
Calls to fault line - average waiting time before call answered | 21.8908
Calls abandoned - percentage | 2.406%
Call centre - number of overload events | 2
Customer complaints (number)
Complaint - reliability of supply | 23
Complaint - technical quality of supply | 4
Complaint - administrative process or customer service | 81
Complaint - connection or augmentation | 15
Complaint - other | 14
Total complaints | 137
Note: for Table 3 Calls to Call Centre Fault Line means the total number of calls to the fault line to be reported, including any answered by an automated response service and terminated without being answered by an operator. Excludes missed calls where the fault line is overloaded.
Contents

## 5. General Information
CitiPower Pty
General Information
2013
Table 1 General Information
Number of metered supply points | Total no. | By type of customer |  | By supply voltage
|  | Domestic | Non-Domestic | ST | HV | LV
CBD | 58479.5359 | 39604.6567 | 18874.8792 | 0 | 28 | 58451.5359
Urban | 263040.4641 | 227772.3433 | 35268.1208 | 7 | 47 | 262986.4641
Rural Short | 0 | 0 | 0 | 0 | 0 | 0
Rural Long | 0 | 0 | 0 | 0 | 0 | 0
Total number of metered supply points | 321520 | 267377 | 54143 | 7 | 75 | 321438
Number of unmetered supply points | CBD | Urban | Short Rural | Long Rural
Total no. | 226.9101 | 927.0899 | 0 | 0
Energy delivered (GWh) | Total GWh | By type of customer |  | By supply voltage
|  | Domestic | Non-Domestic | ST | HV | LV
CBD | 2666.8772 | 192.3029 | 2474.5743 | 0 | 294.2338 | 2372.6434
Urban | 3314.4768 | 1077.2763 | 2237.2005 | 115.046 | 269.0422 | 2930.3886
Rural Short | 0.00096835 | 0 | 0.00096835 | 0 | 0 | 0.00096835
Rural Long | 0 | 0 | 0 | 0 | 0 | 0
Total energy | 5981.3549 | 1269.5792 | 4711.7758 | 115.046 | 563.276 | 5303.033
Line length (km) | Total km | Underground |  |  | Overhead
|  | ST | HV | LV | ST | HV | LV
CBD | 1425 | n/a | 613 | 582 | n/a | 2 | 228
Urban | 5516 | n/a | 712 | 851 | n/a | 455 | 3498
Rural Short | 0 | n/a | n/a | n/a | n/a | n/a | n/a
Rural Long | 0 | n/a | n/a | n/a | n/a | n/a | n/a
Not categorised | 383 | 132 | 2 | 86 | 153 | 0 | 10
Total line length | 7324 | 132 | 1327 | 1519 | 153 | 457 | 3736
Number and total capacity of transformers | Total no. | Capacity (MVA)
Distribution | 4621 | 3999
Zone substations | 106 | 2740
Total | 4727 | 6739
Customer numbers
Subtransmission | 7
High voltage | 75
Low voltage - residential | 267377
Low voltage - non-residential | 54061
Total customer numbers | 321520
Number of poles
Subtransmission | 3088
Distribution | 46144
Total | 49232
Other information
Distribution losses (% of purchases) | 2.98
Network Service area (sq.km) | 157
Peak Coincident Demand (MW) | 1442
Note: Distribution Loss factors are to be reported on a financial year basis
Contents
Contents

## 6a. Planned Outages
CitiPower Pty
Planned Outages
2013
Table 1 Planned Outages
Date (DD/MM/YYYY) | Feeder ID / name | Feeder Classification | Reason for planned outage | Number of customers interrupted | Duration of interruption (mins) | Total minutes off supply (planned) | Effect on planned SAIDI | Effect on planned SAIFI | Effect on planned MAIFI
20/01/2013 | AP001 | Urban | Network augmentation/maintenanace | 16 | 435 | 6960 | 0.021754 | 5.0009e-05 | 0
25/08/2013 | AP003 | Urban | Network augmentation/maintenanace | 1 | 280 | 280 | 0.00087515 | 3.1255e-06 | 0
7/10/2013 | AP003 | Urban | Network augmentation/maintenanace | 12 | 30 | 360 | 0.0011252 | 3.7506e-05 | 0
7/10/2013 | AP003 | Urban | Network augmentation/maintenanace | 6 | 195 | 1170 | 0.0036569 | 1.8753e-05 | 0
22/02/2013 | AP003 | Urban | Network augmentation/maintenanace | 19 | 285 | 5415 | 0.016925 | 5.9385e-05 | 0
25/08/2013 | AP003 | Urban | Network augmentation/maintenanace | 42 | 294 | 12348 | 0.038594 | 0.00013127 | 0
3/12/2013 | AP003 | Urban | Network augmentation/maintenanace | 151 | 147 | 22197 | 0.069378 | 0.00047196 | 0
25/08/2013 | AP003 | Urban | Network augmentation/maintenanace | 141 | 294 | 41454 | 0.12957 | 0.0004407 | 0
16/07/2013 | AP005 | Urban | Network augmentation/maintenanace | 14 | 397 | 5558 | 0.017372 | 4.3758e-05 | 0
25/06/2013 | AP005 | Urban | Network augmentation/maintenanace | 14 | 499 | 6986 | 0.021835 | 4.3758e-05 | 0
26/09/2013 | AP005 | Urban | Network augmentation/maintenanace | 38 | 355 | 13490 | 0.042163 | 0.00011877 | 0
24/09/2013 | AP005 | Urban | Network augmentation/maintenanace | 38 | 360 | 13680 | 0.042757 | 0.00011877 | 0
21/07/2013 | AP005 | Urban | Network augmentation/maintenanace | 49 | 405 | 19845 | 0.062026 | 0.00015315 | 0
18/05/2013 | AP006 | Urban | Network augmentation/maintenanace | 2 | 156 | 312 | 0.00097517 | 6.2511e-06 | 0
13/10/2013 | AP006 | Urban | Network augmentation/maintenanace | 16 | 481 | 7696 | 0.024054 | 5.0009e-05 | 0
13/10/2013 | AP006 | Urban | Network augmentation/maintenanace | 49 | 480 | 23520 | 0.073513 | 0.00015315 | 0
18/12/2013 | AP007 | Urban | Network augmentation/maintenanace | 2 | 435 | 870 | 0.0027192 | 6.2511e-06 | 0
11/10/2013 | AP007 | Urban | Network augmentation/maintenanace | 28 | 130 | 3640 | 0.011377 | 8.7515e-05 | 0
19/09/2013 | AP007 | Urban | Network augmentation/maintenanace | 14 | 330 | 4620 | 0.01444 | 4.3758e-05 | 0
2/07/2013 | AP008 | Urban | Network augmentation/maintenanace | 1 | 170 | 170 | 0.00053134 | 3.1255e-06 | 0
14/06/2013 | AP008 | Urban | Network augmentation/maintenanace | 7 | 180 | 1260 | 0.0039382 | 2.1879e-05 | 0
20/07/2013 | AP008 | Urban | Network augmentation/maintenanace | 19 | 205 | 3895 | 0.012174 | 5.9385e-05 | 0
20/06/2013 | AP008 | Urban | Network augmentation/maintenanace | 17 | 300 | 5100 | 0.01594 | 5.3134e-05 | 0
23/09/2013 | AP008 | Urban | Network augmentation/maintenanace | 24 | 255 | 6120 | 0.019128 | 7.5013e-05 | 0
24/06/2013 | AP008 | Urban | Network augmentation/maintenanace | 37 | 209 | 7733 | 0.02417 | 0.00011564 | 0
11/08/2013 | AP009 | Urban | Network augmentation/maintenanace | 19 | 335 | 6365 | 0.019894 | 5.9385e-05 | 0
7/07/2013 | AP011 | Urban | Network augmentation/maintenanace | 24 | 146.6667 | 3520 | 0.011002 | 7.5013e-05 | 0
4/03/2013 | AP014 | Urban | Network augmentation/maintenanace | 3 | 100 | 300 | 0.00093766 | 9.3766e-06 | 0
10/03/2013 | AP014 | Urban | Network augmentation/maintenanace | 4 | 330 | 1320 | 0.0041257 | 1.2502e-05 | 0
5/03/2013 | AP015 | Urban | Network augmentation/maintenanace | 1 | 390 | 390 | 0.001219 | 3.1255e-06 | 0
21/06/2013 | AP015 | Urban | Network augmentation/maintenanace | 4 | 240 | 960 | 0.0030005 | 1.2502e-05 | 0
7/10/2013 | AP019 | Urban | Network augmentation/maintenanace | 1 | 143 | 143 | 0.00044695 | 3.1255e-06 | 0
18/07/2013 | AP019 | Urban | Network augmentation/maintenanace | 12 | 205 | 2460 | 0.0076888 | 3.7506e-05 | 0
6/10/2013 | AP019 | Urban | Network augmentation/maintenanace | 43 | 463.8372 | 19945 | 0.062339 | 0.0001344 | 0
16/10/2013 | AR003 | Urban | Network augmentation/maintenanace | 57 | 24 | 1368 | 0.0042757 | 0.00017816 | 0
21/04/2013 | AR004 | Urban | Network augmentation/maintenanace | 1 | 12 | 12 | 3.7506e-05 | 3.1255e-06 | 0
6/11/2013 | AR004 | Urban | Network augmentation/maintenanace | 3 | 190 | 570 | 0.0017816 | 9.3766e-06 | 0
6/11/2013 | AR004 | Urban | Network augmentation/maintenanace | 2 | 335 | 670 | 0.0020941 | 6.2511e-06 | 0
8/11/2013 | AR004 | Urban | Network augmentation/maintenanace | 86 | 400.1163 | 34410 | 0.10755 | 0.0002688 | 0
18/06/2013 | AR006 | Urban | Network augmentation/maintenanace | 83 | 710 | 58930 | 0.18419 | 0.00025942 | 0
19/10/2013 | AR009 | Urban | Network augmentation/maintenanace | 116 | 50 | 5800 | 0.018128 | 0.00036256 | 0
18/08/2013 | AR010 | Urban | Network augmentation/maintenanace | 7 | 30 | 210 | 0.00065636 | 2.1879e-05 | 0
13/09/2013 | AR010 | Urban | Network augmentation/maintenanace | 48 | 278 | 13344 | 0.041707 | 0.00015003 | 0
22/01/2013 | AR011 | Urban | Network augmentation/maintenanace | 37 | 350 | 12950 | 0.040476 | 0.00011564 | 0
9/01/2013 | AR013 | Urban | Network augmentation/maintenanace | 33 | 310 | 10230 | 0.031974 | 0.00010314 | 0
21/04/2013 | B002 | Urban | Network augmentation/maintenanace | 6 | 370 | 2220 | 0.0069387 | 1.8753e-05 | 0
21/04/2013 | B003 | Urban | Network augmentation/maintenanace | 4 | 170 | 680 | 0.0021254 | 1.2502e-05 | 0
21/04/2013 | B003 | Urban | Network augmentation/maintenanace | 12 | 360 | 4320 | 0.013502 | 3.7506e-05 | 0
1/12/2013 | B003 | Urban | Network augmentation/maintenanace | 13 | 355 | 4615 | 0.014424 | 4.0632e-05 | 0
21/04/2013 | B003 | Urban | Network augmentation/maintenanace | 40 | 165 | 6600 | 0.020629 | 0.00012502 | 0
15/09/2013 | B004 | Urban | Network augmentation/maintenanace | 102 | 60 | 6120 | 0.019128 | 0.0003188 | 0
17/02/2013 | B004 | Urban | Network augmentation/maintenanace | 10 | 615 | 6150 | 0.019222 | 3.1255e-05 | 0
14/04/2013 | B004 | Urban | Network augmentation/maintenanace | 16 | 400 | 6400 | 0.020003 | 5.0009e-05 | 0
17/11/2013 | B011 | Urban | Network augmentation/maintenanace | 1 | 231 | 231 | 0.000722 | 3.1255e-06 | 0
7/03/2013 | B011 | Urban | Network augmentation/maintenanace | 12 | 385 | 4620 | 0.01444 | 3.7506e-05 | 0
7/04/2013 | B011 | Urban | Network augmentation/maintenanace | 19 | 245 | 4655 | 0.014549 | 5.9385e-05 | 0
5/04/2013 | B012 | Urban | Network augmentation/maintenanace | 4 | 85 | 340 | 0.0010627 | 1.2502e-05 | 0
28/07/2013 | B012 | Urban | Network augmentation/maintenanace | 3 | 195 | 585 | 0.0018284 | 9.3766e-06 | 0
3/02/2013 | B014 | Urban | Network augmentation/maintenanace | 2 | 295 | 590 | 0.0018441 | 6.2511e-06 | 0
6/10/2013 | B014 | Urban | Network augmentation/maintenanace | 14 | 255 | 3570 | 0.011158 | 4.3758e-05 | 0
21/04/2013 | B014 | Urban | Network augmentation/maintenanace | 32 | 380 | 12160 | 0.038007 | 0.00010002 | 0
7/03/2013 | B016 | Urban | Network augmentation/maintenanace | 5 | 385 | 1925 | 0.0060167 | 1.5628e-05 | 0
12/04/2013 | B016 | Urban | Network augmentation/maintenanace | 12 | 195 | 2340 | 0.0073138 | 3.7506e-05 | 0
12/02/2013 | B021 | Urban | Network augmentation/maintenanace | 13 | 2 | 26 | 8.1264e-05 | 4.0632e-05 | 0
25/08/2013 | B021 | Urban | Network augmentation/maintenanace | 45 | 520 | 23400 | 0.073138 | 0.00014065 | 0
14/04/2013 | B023 | Urban | Network augmentation/maintenanace | 13 | 400 | 5200 | 0.016253 | 4.0632e-05 | 0
21/08/2013 | BC006 | Urban | Network augmentation/maintenanace | 12 | 440 | 5280 | 0.016503 | 3.7506e-05 | 0
9/01/2013 | BC012 | Urban | Network augmentation/maintenanace | 51 | 423 | 21573 | 0.067427 | 0.0001594 | 0
10/09/2013 | BC012 | Urban | Network augmentation/maintenanace | 59 | 443 | 26137 | 0.081692 | 0.00018441 | 0
19/11/2013 | BC013 | Urban | Network augmentation/maintenanace | 13 | 320 | 4160 | 0.013002 | 4.0632e-05 | 0
7/06/2013 | BC013 | Urban | Network augmentation/maintenanace | 26 | 310 | 8060 | 0.025192 | 8.1264e-05 | 0
18/08/2013 | BC015 | Urban | Network augmentation/maintenanace | 2 | 320 | 640 | 0.0020003 | 6.2511e-06 | 0
24/03/2013 | BC015 | Urban | Network augmentation/maintenanace | 17 | 480 | 8160 | 0.025504 | 5.3134e-05 | 0
18/07/2013 | BC015 | Urban | Network augmentation/maintenanace | 71 | 455 | 32305 | 0.10097 | 0.00022191 | 0
19/11/2013 | BC015 | Urban | Network augmentation/maintenanace | 182 | 490 | 89180 | 0.27874 | 0.00056885 | 0
18/12/2013 | BC020 | Urban | Network augmentation/maintenanace | 30 | 10 | 300 | 0.00093766 | 9.3766e-05 | 0
18/11/2013 | BC020 | Urban | Network augmentation/maintenanace | 12 | 128 | 1536 | 0.0048008 | 3.7506e-05 | 0
18/11/2013 | BC020 | Urban | Network augmentation/maintenanace | 20 | 376 | 7520 | 0.023504 | 6.2511e-05 | 0
18/10/2013 | BK002 | Urban | Network augmentation/maintenanace | 73 | 127 | 9271 | 0.028977 | 0.00022816 | 0
1/12/2013 | BK002 | Urban | Network augmentation/maintenanace | 21 | 455 | 9555 | 0.029865 | 6.5636e-05 | 0
14/07/2013 | BK004 | Urban | Network augmentation/maintenanace | 16 | 555 | 8880 | 0.027755 | 5.0009e-05 | 0
4/08/2013 | BK004 | Urban | Network augmentation/maintenanace | 42 | 214.2857 | 9000 | 0.02813 | 0.00013127 | 0
2/06/2013 | BK004 | Urban | Network augmentation/maintenanace | 34 | 282.9412 | 9620 | 0.030068 | 0.00010627 | 0
30/06/2013 | BK007 | Urban | Network augmentation/maintenanace | 10 | 247 | 2470 | 0.0077201 | 3.1255e-05 | 0
5/06/2013 | BK009 | Urban | Network augmentation/maintenanace | 195 | 94 | 18330 | 0.057291 | 0.00060948 | 0
5/06/2013 | BK009 | Urban | Network augmentation/maintenanace | 77 | 470.6883 | 36243 | 0.11328 | 0.00024067 | 0
23/06/2013 | BK011 | Urban | Network augmentation/maintenanace | 2 | 162 | 324 | 0.0010127 | 6.2511e-06 | 0
2/06/2013 | BK011 | Urban | Network augmentation/maintenanace | 7 | 56 | 392 | 0.0012252 | 2.1879e-05 | 0
2/06/2013 | BK011 | Urban | Network augmentation/maintenanace | 7 | 65 | 455 | 0.0014221 | 2.1879e-05 | 0
11/08/2013 | BQ001 | CBD | Network augmentation/maintenanace | 2 | 240 | 480 | 0.0015003 | 6.2511e-06 | 0
26/05/2013 | BQ001 | CBD | Network augmentation/maintenanace | 10 | 312 | 3120 | 0.0097517 | 3.1255e-05 | 0
30/10/2013 | BQ003 | Urban | Network augmentation/maintenanace | 9 | 203 | 1827 | 0.0057104 | 2.813e-05 | 0
28/07/2013 | BQ020 | CBD | Network augmentation/maintenanace | 3 | 125 | 375 | 0.0011721 | 9.3766e-06 | 0
17/05/2013 | BQ028 | Urban | Network augmentation/maintenanace | 3 | 240 | 720 | 0.0022504 | 9.3766e-06 | 0
24/11/2013 | BQ028 | Urban | Network augmentation/maintenanace | 54 | 164 | 8856 | 0.02768 | 0.00016878 | 0
15/12/2013 | BQ030 | CBD | Network augmentation/maintenanace | 1 | 628 | 628 | 0.0019628 | 3.1255e-06 | 0
20/01/2013 | BQ043 | CBD | Network augmentation/maintenanace | 8 | 245 | 1960 | 0.0061261 | 2.5004e-05 | 0
26/03/2013 | BQ047 | CBD | Network augmentation/maintenanace | 84 | 342 | 28728 | 0.08979 | 0.00026255 | 0
19/10/2013 | BQ051 | Urban | Network augmentation/maintenanace | 165 | 360 | 59400 | 0.18566 | 0.00051571 | 0
3/12/2013 | BQ053 | Urban | Network augmentation/maintenanace | 1 | 72 | 72 | 0.00022504 | 3.1255e-06 | 0
30/06/2013 | C020 | Urban | Network augmentation/maintenanace | 51 | 265 | 13515 | 0.042242 | 0.0001594 | 0
17/03/2013 | C023 | Urban | Network augmentation/maintenanace | 1 | 155 | 155 | 0.00048446 | 3.1255e-06 | 0
16/11/2013 | C023 | Urban | Network augmentation/maintenanace | 1 | 410 | 410 | 0.0012815 | 3.1255e-06 | 0
30/05/2013 | C023 | Urban | Network augmentation/maintenanace | 21 | 265 | 5565 | 0.017394 | 6.5636e-05 | 0
31/07/2013 | C023 | Urban | Network augmentation/maintenanace | 21 | 290 | 6090 | 0.019035 | 6.5636e-05 | 0
16/11/2013 | C023 | Urban | Network augmentation/maintenanace | 31 | 340 | 10540 | 0.032943 | 9.6892e-05 | 0
23/09/2013 | C023 | Urban | Network augmentation/maintenanace | 92 | 360 | 33120 | 0.10352 | 0.00028755 | 0
23/04/2013 | C027 | Urban | Network augmentation/maintenanace | 1 | 225 | 225 | 0.00070325 | 3.1255e-06 | 0
24/03/2013 | C028 | Urban | Network augmentation/maintenanace | 1 | 465 | 465 | 0.0014534 | 3.1255e-06 | 0
31/07/2013 | C028 | Urban | Network augmentation/maintenanace | 17 | 290 | 4930 | 0.015409 | 5.3134e-05 | 0
25/09/2013 | C028 | Urban | Network augmentation/maintenanace | 38 | 355 | 13490 | 0.042163 | 0.00011877 | 0
25/06/2013 | C028 | Urban | Network augmentation/maintenanace | 54 | 309 | 16686 | 0.052153 | 0.00016878 | 0
24/03/2013 | C029 | Urban | Network augmentation/maintenanace | 1 | 18 | 18 | 5.626e-05 | 3.1255e-06 | 0
2/05/2013 | C029 | Urban | Network augmentation/maintenanace | 47 | 350 | 16450 | 0.051415 | 0.0001469 | 0
24/03/2013 | C029 | Urban | Network augmentation/maintenanace | 52 | 418 | 21736 | 0.067937 | 0.00016253 | 0
16/12/2013 | CL011 | Urban | Network augmentation/maintenanace | 23 | 410 | 9430 | 0.029474 | 7.1887e-05 | 0
10/12/2013 | CL011 | Urban | Network augmentation/maintenanace | 30 | 400 | 12000 | 0.037506 | 9.3766e-05 | 0
13/12/2013 | CL011 | Urban | Network augmentation/maintenanace | 38 | 400 | 15200 | 0.047508 | 0.00011877 | 0
16/05/2013 | CL013 | Urban | Network augmentation/maintenanace | 1 | 2 | 2 | 6.2511e-06 | 3.1255e-06 | 0
10/03/2013 | CL013 | Urban | Network augmentation/maintenanace | 3 | 160 | 480 | 0.0015003 | 9.3766e-06 | 0
30/06/2013 | CL013 | Urban | Network augmentation/maintenanace | 20 | 273 | 5460 | 0.017065 | 6.2511e-05 | 0
20/01/2013 | CL013 | Urban | Network augmentation/maintenanace | 17 | 561.1765 | 9540 | 0.029818 | 5.3134e-05 | 0
6/03/2013 | CL013 | Urban | Network augmentation/maintenanace | 59 | 310 | 18290 | 0.057166 | 0.00018441 | 0
20/08/2013 | CL013 | Urban | Network augmentation/maintenanace | 80 | 450 | 36000 | 0.11252 | 0.00025004 | 0
1/12/2013 | CL014 | Urban | Network augmentation/maintenanace | 1 | 200 | 200 | 0.00062511 | 3.1255e-06 | 0
11/09/2013 | CL022 | Urban | Network augmentation/maintenanace | 1 | 111 | 111 | 0.00034693 | 3.1255e-06 | 0
18/10/2013 | CL022 | Urban | Network augmentation/maintenanace | 1 | 111 | 111 | 0.00034693 | 3.1255e-06 | 0
18/10/2013 | CL022 | Urban | Network augmentation/maintenanace | 12 | 50 | 600 | 0.0018753 | 3.7506e-05 | 0
7/11/2013 | CL022 | Urban | Network augmentation/maintenanace | 3 | 450 | 1350 | 0.0042195 | 9.3766e-06 | 0
8/10/2013 | CL022 | Urban | Network augmentation/maintenanace | 14 | 225 | 3150 | 0.0098454 | 4.3758e-05 | 0
12/09/2013 | CL022 | Urban | Network augmentation/maintenanace | 47 | 220 | 10340 | 0.032318 | 0.0001469 | 0
18/09/2013 | CL022 | Urban | Network augmentation/maintenanace | 49 | 295 | 14455 | 0.04518 | 0.00015315 | 0
17/09/2013 | CL022 | Urban | Network augmentation/maintenanace | 49 | 385 | 18865 | 0.058963 | 0.00015315 | 0
11/09/2013 | CL022 | Urban | Network augmentation/maintenanace | 47 | 440 | 20680 | 0.064636 | 0.0001469 | 0
19/02/2013 | CL023 | Urban | Network augmentation/maintenanace | 6 | 155 | 930 | 0.0029067 | 1.8753e-05 | 0
16/11/2013 | CL023 | Urban | Network augmentation/maintenanace | 24 | 310 | 7440 | 0.023254 | 7.5013e-05 | 0
8/03/2013 | CL023 | Urban | Network augmentation/maintenanace | 32 | 350 | 11200 | 0.035006 | 0.00010002 | 0
10/02/2013 | CL023 | Urban | Network augmentation/maintenanace | 42 | 310 | 13020 | 0.040694 | 0.00013127 | 0
27/11/2013 | CL026 | Urban | Network augmentation/maintenanace | 32 | 217 | 6944 | 0.021704 | 0.00010002 | 0
27/10/2013 | CL026 | Urban | Network augmentation/maintenanace | 40 | 385 | 15400 | 0.048133 | 0.00012502 | 0
30/07/2013 | CL035 | Urban | Network augmentation/maintenanace | 1 | 251 | 251 | 0.00078451 | 3.1255e-06 | 0
20/10/2013 | CL036 | Urban | Network augmentation/maintenanace | 2 | 439 | 878 | 0.0027442 | 6.2511e-06 | 0
6/03/2013 | CL036 | Urban | Network augmentation/maintenanace | 26 | 438 | 11388 | 0.035594 | 8.1264e-05 | 0
14/09/2013 | CL037 | Urban | Network augmentation/maintenanace | 3 | 242 | 726 | 0.0022691 | 9.3766e-06 | 0
1/09/2013 | CL037 | Urban | Network augmentation/maintenanace | 2 | 365 | 730 | 0.0022816 | 6.2511e-06 | 0
22/09/2013 | CL037 | Urban | Network augmentation/maintenanace | 68 | 385 | 26180 | 0.081827 | 0.00021254 | 0
10/10/2013 | CL037 | Urban | Network augmentation/maintenanace | 81 | 351.5432 | 28475 | 0.089 | 0.00025317 | 0
15/06/2013 | CL038 | Urban | Network augmentation/maintenanace | 2 | 195 | 390 | 0.001219 | 6.2511e-06 | 0
7/06/2013 | CL038 | Urban | Network augmentation/maintenanace | 5 | 150 | 750 | 0.0023442 | 1.5628e-05 | 0
24/11/2013 | CL038 | Urban | Network augmentation/maintenanace | 3 | 300 | 900 | 0.002813 | 9.3766e-06 | 0
10/03/2013 | CL038 | Urban | Network augmentation/maintenanace | 7 | 145 | 1015 | 0.0031724 | 2.1879e-05 | 0
21/07/2013 | CL038 | Urban | Network augmentation/maintenanace | 53 | 45 | 2385 | 0.0074544 | 0.00016565 | 0
4/02/2013 | CW004 | Urban | Network augmentation/maintenanace | 6 | 210 | 1260 | 0.0039382 | 1.8753e-05 | 0
3/03/2013 | CW004 | Urban | Network augmentation/maintenanace | 8 | 340 | 2720 | 0.0085015 | 2.5004e-05 | 0
1/03/2013 | CW004 | Urban | Network augmentation/maintenanace | 21 | 135 | 2835 | 0.0088609 | 6.5636e-05 | 0
7/02/2013 | CW004 | Urban | Network augmentation/maintenanace | 31 | 200 | 6200 | 0.019378 | 9.6892e-05 | 0
25/08/2013 | CW005 | Urban | Network augmentation/maintenanace | 4 | 266 | 1064 | 0.0033256 | 1.2502e-05 | 0
19/02/2013 | CW005 | Urban | Network augmentation/maintenanace | 17 | 195 | 3315 | 0.010361 | 5.3134e-05 | 0
10/11/2013 | CW005 | Urban | Network augmentation/maintenanace | 37 | 240 | 8880 | 0.027755 | 0.00011564 | 0
24/03/2013 | CW005 | Urban | Network augmentation/maintenanace | 26 | 400 | 10400 | 0.032506 | 8.1264e-05 | 0
13/08/2013 | CW005 | Urban | Network augmentation/maintenanace | 29 | 470 | 13630 | 0.042601 | 9.0641e-05 | 0
24/02/2013 | CW006 | Urban | Network augmentation/maintenanace | 1 | 187 | 187 | 0.00058448 | 3.1255e-06 | 0
31/01/2013 | CW006 | Urban | Network augmentation/maintenanace | 31 | 295 | 9145 | 0.028583 | 9.6892e-05 | 0
13/02/2013 | CW007 | Urban | Network augmentation/maintenanace | 9 | 5 | 45 | 0.00014065 | 2.813e-05 | 0
7/02/2013 | CW008 | Urban | Network augmentation/maintenanace | 3 | 170 | 510 | 0.001594 | 9.3766e-06 | 0
8/05/2013 | CW008 | Urban | Network augmentation/maintenanace | 21 | 435 | 9135 | 0.028552 | 6.5636e-05 | 0
24/02/2013 | CW009 | Urban | Network augmentation/maintenanace | 3 | 187 | 561 | 0.0017534 | 9.3766e-06 | 0
10/02/2013 | CW009 | Urban | Network augmentation/maintenanace | 15 | 88 | 1320 | 0.0041257 | 4.6883e-05 | 0
5/08/2013 | CW009 | Urban | Network augmentation/maintenanace | 6 | 410 | 2460 | 0.0076888 | 1.8753e-05 | 0
10/02/2013 | CW009 | Urban | Network augmentation/maintenanace | 33 | 430 | 14190 | 0.044351 | 0.00010314 | 0
18/12/2013 | CW009 | Urban | Network augmentation/maintenanace | 62 | 305 | 18910 | 0.059104 | 0.00019378 | 0
7/03/2013 | CW009 | Urban | Network augmentation/maintenanace | 40 | 535 | 21400 | 0.066886 | 0.00012502 | 0
6/02/2013 | CW009 | Urban | Network augmentation/maintenanace | 102 | 310 | 31620 | 0.098829 | 0.0003188 | 0
15/09/2013 | CW011 | Urban | Network augmentation/maintenanace | 4 | 330 | 1320 | 0.0041257 | 1.2502e-05 | 0
17/03/2013 | CW011 | Urban | Network augmentation/maintenanace | 58 | 445 | 25810 | 0.08067 | 0.00018128 | 0
22/03/2013 | CW012 | Urban | Network augmentation/maintenanace | 1 | 195 | 195 | 0.00060948 | 3.1255e-06 | 0
5/05/2013 | CW012 | Urban | Network augmentation/maintenanace | 4 | 225 | 900 | 0.002813 | 1.2502e-05 | 0
26/03/2013 | CW012 | Urban | Network augmentation/maintenanace | 5 | 180 | 900 | 0.002813 | 1.5628e-05 | 0
1/03/2013 | CW012 | Urban | Network augmentation/maintenanace | 7 | 135 | 945 | 0.0029536 | 2.1879e-05 | 0
13/01/2013 | CW012 | Urban | Network augmentation/maintenanace | 11 | 240 | 2640 | 0.0082514 | 3.4381e-05 | 0
21/07/2013 | CW012 | Urban | Network augmentation/maintenanace | 6 | 455 | 2730 | 0.0085327 | 1.8753e-05 | 0
25/08/2013 | CW012 | Urban | Network augmentation/maintenanace | 36 | 400 | 14400 | 0.045008 | 0.00011252 | 0
10/02/2013 | CW013 | Urban | Network augmentation/maintenanace | 3 | 180 | 540 | 0.0016878 | 9.3766e-06 | 0
19/06/2013 | CW013 | Urban | Network augmentation/maintenanace | 28 | 154.8214 | 4335 | 0.013549 | 8.7515e-05 | 0
8/01/2013 | CW013 | Urban | Network augmentation/maintenanace | 16 | 380 | 6080 | 0.019003 | 5.0009e-05 | 0
10/02/2013 | CW013 | Urban | Network augmentation/maintenanace | 19 | 350.5263 | 6660 | 0.020816 | 5.9385e-05 | 0
21/07/2013 | CW014 | Urban | Network augmentation/maintenanace | 8 | 450 | 3600 | 0.011252 | 2.5004e-05 | 0
23/01/2013 | CW014 | Urban | Network augmentation/maintenanace | 17 | 320 | 5440 | 0.017003 | 5.3134e-05 | 0
13/04/2013 | CW015 | Urban | Network augmentation/maintenanace | 1 | 270 | 270 | 0.0008439 | 3.1255e-06 | 0
4/06/2013 | CW015 | Urban | Network augmentation/maintenanace | 4 | 85 | 340 | 0.0010627 | 1.2502e-05 | 0
9/04/2013 | CW015 | Urban | Network augmentation/maintenanace | 6 | 240 | 1440 | 0.0045008 | 1.8753e-05 | 0
10/04/2013 | CW015 | Urban | Network augmentation/maintenanace | 6 | 270 | 1620 | 0.0050634 | 1.8753e-05 | 0
5/04/2013 | CW015 | Urban | Network augmentation/maintenanace | 39 | 205 | 7995 | 0.024989 | 0.0001219 | 0
10/03/2013 | DA004 | Urban | Network augmentation/maintenanace | 1 | 65 | 65 | 0.00020316 | 3.1255e-06 | 0
10/03/2013 | DA016 | Urban | Network augmentation/maintenanace | 13 | 540 | 7020 | 0.021941 | 4.0632e-05 | 0
24/11/2013 | DA020 | Urban | Network augmentation/maintenanace | 22 | 210 | 4620 | 0.01444 | 6.8762e-05 | 0
6/10/2013 | DA026 | Urban | Network augmentation/maintenanace | 25 | 11 | 275 | 0.00085952 | 7.8138e-05 | 0
21/06/2013 | DA028 | Urban | Network augmentation/maintenanace | 1 | 285 | 285 | 0.00089078 | 3.1255e-06 | 0
14/08/2013 | EL011 | Urban | Network augmentation/maintenanace | 39 | 189 | 7371 | 0.023038 | 0.0001219 | 0
18/09/2013 | F027 | Urban | Network augmentation/maintenanace | 40 | 155 | 6200 | 0.019378 | 0.00012502 | 0
14/02/2013 | F027 | Urban | Network augmentation/maintenanace | 26 | 285 | 7410 | 0.02316 | 8.1264e-05 | 0
8/02/2013 | F029 | Urban | Network augmentation/maintenanace | 2 | 325 | 650 | 0.0020316 | 6.2511e-06 | 0
21/01/2013 | F032 | Urban | Network augmentation/maintenanace | 1 | 112 | 112 | 0.00035006 | 3.1255e-06 | 0
7/04/2013 | F032 | Urban | Network augmentation/maintenanace | 7 | 480 | 3360 | 0.010502 | 2.1879e-05 | 0
3/04/2013 | F032 | Urban | Network augmentation/maintenanace | 49 | 260 | 12740 | 0.039819 | 0.00015315 | 0
18/07/2013 | F032 | Urban | Network augmentation/maintenanace | 38 | 407.9474 | 15502 | 0.048452 | 0.00011877 | 0
24/03/2013 | F034 | Urban | Network augmentation/maintenanace | 5 | 300 | 1500 | 0.0046883 | 1.5628e-05 | 0
3/04/2013 | F034 | Urban | Network augmentation/maintenanace | 19 | 255 | 4845 | 0.015143 | 5.9385e-05 | 0
24/03/2013 | F034 | Urban | Network augmentation/maintenanace | 19 | 400 | 7600 | 0.023754 | 5.9385e-05 | 0
24/03/2013 | F034 | Urban | Network augmentation/maintenanace | 23 | 360 | 8280 | 0.025879 | 7.1887e-05 | 0
6/03/2013 | F034 | Urban | Network augmentation/maintenanace | 67 | 260 | 17420 | 0.054447 | 0.00020941 | 0
19/03/2013 | F034 | Urban | Network augmentation/maintenanace | 68 | 300 | 20400 | 0.063761 | 0.00021254 | 0
6/10/2013 | F034 | Urban | Network augmentation/maintenanace | 76 | 335 | 25460 | 0.079576 | 0.00023754 | 0
27/09/2013 | F035 | Urban | Network augmentation/maintenanace | 9 | 110 | 990 | 0.0030943 | 2.813e-05 | 0
24/03/2013 | F037 | Urban | Network augmentation/maintenanace | 7 | 415 | 2905 | 0.0090797 | 2.1879e-05 | 0
14/11/2013 | F037 | Urban | Network augmentation/maintenanace | 21 | 400 | 8400 | 0.026255 | 6.5636e-05 | 0
8/03/2013 | F037 | Urban | Network augmentation/maintenanace | 39 | 295 | 11505 | 0.035959 | 0.0001219 | 0
17/07/2013 | FB005 | Urban | Network augmentation/maintenanace | 2 | 225 | 450 | 0.0014065 | 6.2511e-06 | 0
4/11/2013 | FB023 | Urban | Network augmentation/maintenanace | 6 | 245 | 1470 | 0.0045945 | 1.8753e-05 | 0
3/07/2013 | FF084 | Urban | Network augmentation/maintenanace | 7 | 20 | 140 | 0.00043758 | 2.1879e-05 | 0
10/11/2013 | FF084 | Urban | Network augmentation/maintenanace | 15 | 305 | 4575 | 0.014299 | 4.6883e-05 | 0
16/01/2013 | FF084 | Urban | Network augmentation/maintenanace | 24 | 250 | 6000 | 0.018753 | 7.5013e-05 | 0
15/09/2013 | FF084 | Urban | Network augmentation/maintenanace | 67 | 129.5672 | 8681 | 0.027133 | 0.00020941 | 0
7/05/2013 | FF084 | Urban | Network augmentation/maintenanace | 67 | 305 | 20435 | 0.06387 | 0.00020941 | 0
19/10/2013 | FF085 | Urban | Network augmentation/maintenanace | 4 | 25 | 100 | 0.00031255 | 1.2502e-05 | 0
20/10/2013 | FF085 | Urban | Network augmentation/maintenanace | 1 | 645 | 645 | 0.002016 | 3.1255e-06 | 0
16/03/2013 | FF086 | Urban | Network augmentation/maintenanace | 16 | 18.25 | 292 | 0.00091266 | 5.0009e-05 | 0
2/06/2013 | FF086 | Urban | Network augmentation/maintenanace | 3 | 155 | 465 | 0.0014534 | 9.3766e-06 | 0
21/03/2013 | FF086 | Urban | Network augmentation/maintenanace | 5 | 315 | 1575 | 0.0049227 | 1.5628e-05 | 0
2/06/2013 | FF086 | Urban | Network augmentation/maintenanace | 31 | 130.9677 | 4060 | 0.01269 | 9.6892e-05 | 0
17/08/2013 | FF092 | Urban | Network augmentation/maintenanace | 20 | 535 | 10700 | 0.033443 | 6.2511e-05 | 0
11/11/2013 | FF097 | Urban | Network augmentation/maintenanace | 4 | 90 | 360 | 0.0011252 | 1.2502e-05 | 0
18/08/2013 | FF097 | Urban | Network augmentation/maintenanace | 9 | 245 | 2205 | 0.0068918 | 2.813e-05 | 0
9/06/2013 | FF097 | Urban | Network augmentation/maintenanace | 38 | 406 | 15428 | 0.048221 | 0.00011877 | 0
24/03/2013 | FR007 | CBD | Network augmentation/maintenanace | 15 | 165 | 2475 | 0.0077357 | 4.6883e-05 | 0
9/09/2013 | FR008 | CBD | Network augmentation/maintenanace | 1 | 645 | 645 | 0.002016 | 3.1255e-06 | 0
20/05/2013 | FR018 | CBD | Network augmentation/maintenanace | 5 | 220 | 1100 | 0.0034381 | 1.5628e-05 | 0
6/05/2013 | FR018 | CBD | Network augmentation/maintenanace | 5 | 230 | 1150 | 0.0035944 | 1.5628e-05 | 0
8/02/2013 | FR020 | CBD | Network augmentation/maintenanace | 16 | 44 | 704 | 0.0022004 | 5.0009e-05 | 0
5/08/2013 | FR029 | CBD | Network augmentation/maintenanace | 1 | 225 | 225 | 0.00070325 | 3.1255e-06 | 0
19/08/2013 | FR029 | CBD | Network augmentation/maintenanace | 1 | 240 | 240 | 0.00075013 | 3.1255e-06 | 0
16/09/2013 | JA001 | CBD | Network augmentation/maintenanace | 1 | 110 | 110 | 0.00034381 | 3.1255e-06 | 0
30/07/2013 | JA001 | CBD | Network augmentation/maintenanace | 1 | 165 | 165 | 0.00051571 | 3.1255e-06 | 0
7/08/2013 | JA001 | CBD | Network augmentation/maintenanace | 1 | 240 | 240 | 0.00075013 | 3.1255e-06 | 0
22/09/2013 | JA018 | CBD | Network augmentation/maintenanace | 14 | 400 | 5600 | 0.017503 | 4.3758e-05 | 0
22/09/2013 | JA025 | CBD | Network augmentation/maintenanace | 16 | 223 | 3568 | 0.011152 | 5.0009e-05 | 0
22/06/2013 | JA027 | CBD | Network augmentation/maintenanace | 34 | 497 | 16898 | 0.052815 | 0.00010627 | 0
2/08/2013 | L001 | Urban | Network augmentation/maintenanace | 9 | 150 | 1350 | 0.0042195 | 2.813e-05 | 0
16/07/2013 | L002 | Urban | Network augmentation/maintenanace | 4 | 80 | 320 | 0.0010002 | 1.2502e-05 | 0
24/09/2013 | L002 | Urban | Network augmentation/maintenanace | 41 | 335 | 13735 | 0.042929 | 0.00012815 | 0
30/04/2013 | L004 | Urban | Network augmentation/maintenanace | 1 | 241 | 241 | 0.00075325 | 3.1255e-06 | 0
11/08/2013 | L004 | Urban | Network augmentation/maintenanace | 1 | 344 | 344 | 0.0010752 | 3.1255e-06 | 0
5/12/2013 | L004 | Urban | Network augmentation/maintenanace | 39 | 395 | 15405 | 0.048149 | 0.0001219 | 0
30/04/2013 | L004 | Urban | Network augmentation/maintenanace | 51 | 405 | 20655 | 0.064558 | 0.0001594 | 0
4/12/2013 | L004 | Urban | Network augmentation/maintenanace | 54 | 444.5556 | 24006 | 0.075032 | 0.00016878 | 0
26/11/2013 | L005 | Urban | Network augmentation/maintenanace | 6 | 295 | 1770 | 0.0055322 | 1.8753e-05 | 0
2/07/2013 | L005 | Urban | Network augmentation/maintenanace | 5 | 360 | 1800 | 0.005626 | 1.5628e-05 | 0
7/06/2013 | L005 | Urban | Network augmentation/maintenanace | 26 | 150 | 3900 | 0.01219 | 8.1264e-05 | 0
28/05/2013 | L005 | Urban | Network augmentation/maintenanace | 17 | 435 | 7395 | 0.023113 | 5.3134e-05 | 0
26/05/2013 | L005 | Urban | Network augmentation/maintenanace | 33 | 350 | 11550 | 0.0361 | 0.00010314 | 0
19/02/2013 | L006 | Urban | Network augmentation/maintenanace | 12 | 345 | 4140 | 0.01294 | 3.7506e-05 | 0
21/01/2013 | L009 | Urban | Network augmentation/maintenanace | 2 | 70 | 140 | 0.00043758 | 6.2511e-06 | 0
13/08/2013 | L010 | Urban | Network augmentation/maintenanace | 2 | 30 | 60 | 0.00018753 | 6.2511e-06 | 0
3/07/2013 | L010 | Urban | Network augmentation/maintenanace | 56 | 25.8929 | 1450 | 0.004532 | 0.00017503 | 0
2/07/2013 | L010 | Urban | Network augmentation/maintenanace | 7 | 315 | 2205 | 0.0068918 | 2.1879e-05 | 0
3/07/2013 | L010 | Urban | Network augmentation/maintenanace | 20 | 118 | 2360 | 0.0073763 | 6.2511e-05 | 0
3/04/2013 | L010 | Urban | Network augmentation/maintenanace | 6 | 405 | 2430 | 0.0075951 | 1.8753e-05 | 0
11/08/2013 | L010 | Urban | Network augmentation/maintenanace | 29 | 320 | 9280 | 0.029005 | 9.0641e-05 | 0
17/05/2013 | L013 | Urban | Network augmentation/maintenanace | 28 | 300 | 8400 | 0.026255 | 8.7515e-05 | 0
15/05/2013 | L013 | Urban | Network augmentation/maintenanace | 34 | 278 | 9452 | 0.029543 | 0.00010627 | 0
16/10/2013 | L013 | Urban | Network augmentation/maintenanace | 33 | 355 | 11715 | 0.036616 | 0.00010314 | 0
31/10/2013 | L013 | Urban | Network augmentation/maintenanace | 34 | 365 | 12410 | 0.038788 | 0.00010627 | 0
3/04/2013 | L013 | Urban | Network augmentation/maintenanace | 35 | 415 | 14525 | 0.045398 | 0.00010939 | 0
8/09/2013 | L013 | Urban | Network augmentation/maintenanace | 112 | 445 | 49840 | 0.15578 | 0.00035006 | 0
11/08/2013 | L013 | Urban | Network augmentation/maintenanace | 143 | 360 | 51480 | 0.1609 | 0.00044695 | 0
17/10/2013 | L018 | Urban | Network augmentation/maintenanace | 27 | 85 | 2295 | 0.0071731 | 8.439e-05 | 0
14/08/2013 | L018 | Urban | Network augmentation/maintenanace | 39 | 151 | 5889 | 0.018406 | 0.0001219 | 0
14/12/2013 | LQ007 | CBD | Network augmentation/maintenanace | 4 | 100 | 400 | 0.0012502 | 1.2502e-05 | 0
15/12/2013 | LQ007 | CBD | Network augmentation/maintenanace | 4 | 228 | 912 | 0.0028505 | 1.2502e-05 | 0
6/07/2013 | LQ014 | CBD | Network augmentation/maintenanace | 37 | 190 | 7030 | 0.021973 | 0.00011564 | 0
13/06/2013 | LQ014 | CBD | Network augmentation/maintenanace | 41 | 275 | 11275 | 0.03524 | 0.00012815 | 0
6/07/2013 | LQ028 | CBD | Network augmentation/maintenanace | 20 | 190 | 3800 | 0.011877 | 6.2511e-05 | 0
13/06/2013 | LQ028 | CBD | Network augmentation/maintenanace | 35 | 275 | 9625 | 0.030083 | 0.00010939 | 0
21/12/2013 | LQ035 | CBD | Network augmentation/maintenanace | 4 | 80 | 320 | 0.0010002 | 1.2502e-05 | 0
22/12/2013 | LQ035 | CBD | Network augmentation/maintenanace | 4 | 215 | 860 | 0.002688 | 1.2502e-05 | 0
28/07/2013 | LS006 | Urban | Network augmentation/maintenanace | 4 | 59 | 236 | 0.00073763 | 1.2502e-05 | 0
2/06/2013 | LS006 | Urban | Network augmentation/maintenanace | 2 | 520 | 1040 | 0.0032506 | 6.2511e-06 | 0
17/12/2013 | LS006 | Urban | Network augmentation/maintenanace | 7 | 390 | 2730 | 0.0085327 | 2.1879e-05 | 0
14/06/2013 | LS006 | Urban | Network augmentation/maintenanace | 27 | 255 | 6885 | 0.021519 | 8.439e-05 | 0
18/05/2013 | LS007 | Urban | Network augmentation/maintenanace | 1 | 430 | 430 | 0.001344 | 3.1255e-06 | 0
23/11/2013 | LS009 | Urban | Network augmentation/maintenanace | 1 | 85 | 85 | 0.00026567 | 3.1255e-06 | 0
13/08/2013 | LS012 | Urban | Network augmentation/maintenanace | 3 | 223 | 669 | 0.002091 | 9.3766e-06 | 0
28/07/2013 | LS012 | Urban | Network augmentation/maintenanace | 38 | 65 | 2470 | 0.0077201 | 0.00011877 | 0
28/07/2013 | LS012 | Urban | Network augmentation/maintenanace | 188 | 53 | 9964 | 0.031143 | 0.0005876 | 0
12/04/2013 | LS012 | Urban | Network augmentation/maintenanace | 91 | 115 | 10465 | 0.032709 | 0.00028442 | 0
17/12/2013 | LS016 | CBD | Network augmentation/maintenanace | 1 | 230 | 230 | 0.00071887 | 3.1255e-06 | 0
17/12/2013 | LS016 | CBD | Network augmentation/maintenanace | 1 | 237 | 237 | 0.00074075 | 3.1255e-06 | 0
17/12/2013 | LS016 | CBD | Network augmentation/maintenanace | 1 | 247 | 247 | 0.00077201 | 3.1255e-06 | 0
26/07/2013 | LS016 | CBD | Network augmentation/maintenanace | 23 | 159 | 3657 | 0.01143 | 7.1887e-05 | 0
22/12/2013 | LS020 | Urban | Network augmentation/maintenanace | 11 | 166 | 1826 | 0.0057072 | 3.4381e-05 | 0
26/05/2013 | LS025 | CBD | Network augmentation/maintenanace | 1 | 97 | 97 | 0.00030318 | 3.1255e-06 | 0
26/05/2013 | LS025 | CBD | Network augmentation/maintenanace | 5 | 255 | 1275 | 0.0039851 | 1.5628e-05 | 0
23/11/2013 | LS025 | CBD | Network augmentation/maintenanace | 16 | 264 | 4224 | 0.013202 | 5.0009e-05 | 0
23/11/2013 | LS025 | CBD | Network augmentation/maintenanace | 79 | 80 | 6320 | 0.019753 | 0.00024692 | 0
16/12/2013 | MG001 | Urban | Network augmentation/maintenanace | 2 | 45 | 90 | 0.0002813 | 6.2511e-06 | 0
24/09/2013 | MG009 | Urban | Network augmentation/maintenanace | 5 | 27 | 135 | 0.00042195 | 1.5628e-05 | 0
28/07/2013 | MG014 | Urban | Network augmentation/maintenanace | 1 | 90 | 90 | 0.0002813 | 3.1255e-06 | 0
1/12/2013 | MP008 | CBD | Network augmentation/maintenanace | 8 | 465 | 3720 | 0.011627 | 2.5004e-05 | 0
22/03/2013 | MP030 | CBD | Network augmentation/maintenanace | 1 | 235 | 235 | 0.0007345 | 3.1255e-06 | 0
17/12/2013 | MP030 | CBD | Network augmentation/maintenanace | 4 | 307 | 1228 | 0.0038382 | 1.2502e-05 | 0
15/10/2013 | MP030 | CBD | Network augmentation/maintenanace | 68 | 280 | 19040 | 0.05951 | 0.00021254 | 0
22/03/2013 | MP030 | CBD | Network augmentation/maintenanace | 121 | 221 | 26741 | 0.08358 | 0.00037819 | 0
21/11/2013 | MP030 | CBD | Network augmentation/maintenanace | 137 | 410 | 56170 | 0.17556 | 0.0004282 | 0
9/09/2013 | MP033 | CBD | Network augmentation/maintenanace | 1 | 220 | 220 | 0.00068762 | 3.1255e-06 | 0
24/06/2013 | MP033 | CBD | Network augmentation/maintenanace | 4 | 73 | 292 | 0.00091266 | 1.2502e-05 | 0
26/07/2013 | MP033 | CBD | Network augmentation/maintenanace | 4 | 216 | 864 | 0.0027005 | 1.2502e-05 | 0
22/07/2013 | MP033 | CBD | Network augmentation/maintenanace | 4 | 280 | 1120 | 0.0035006 | 1.2502e-05 | 0
8/12/2013 | MP050 | CBD | Network augmentation/maintenanace | 6 | 319 | 1914 | 0.0059823 | 1.8753e-05 | 0
26/02/2013 | MP053 | CBD | Network augmentation/maintenanace | 1 | 28 | 28 | 8.7515e-05 | 3.1255e-06 | 0
26/02/2013 | MP053 | CBD | Network augmentation/maintenanace | 92 | 40 | 3680 | 0.011502 | 0.00028755 | 0
26/02/2013 | MP062 | CBD | Network augmentation/maintenanace | 1 | 21 | 21 | 6.5636e-05 | 3.1255e-06 | 0
5/05/2013 | MP062 | CBD | Network augmentation/maintenanace | 10 | 25 | 250 | 0.00078138 | 3.1255e-05 | 0
5/07/2013 | NC001 | Urban | Network augmentation/maintenanace | 63 | 9 | 567 | 0.0017722 | 0.00019691 | 0
1/08/2013 | NC001 | Urban | Network augmentation/maintenanace | 8 | 345 | 2760 | 0.0086265 | 2.5004e-05 | 0
21/08/2013 | NC001 | Urban | Network augmentation/maintenanace | 26 | 250 | 6500 | 0.020316 | 8.1264e-05 | 0
18/09/2013 | NC001 | Urban | Network augmentation/maintenanace | 32 | 300 | 9600 | 0.030005 | 0.00010002 | 0
21/08/2013 | NC001 | Urban | Network augmentation/maintenanace | 273 | 760 | 207480 | 0.64849 | 0.00085327 | 0
25/09/2013 | NC002 | Urban | Network augmentation/maintenanace | 1 | 63 | 63 | 0.00019691 | 3.1255e-06 | 0
26/09/2013 | NC002 | Urban | Network augmentation/maintenanace | 9 | 149 | 1341 | 0.0041913 | 2.813e-05 | 0
9/10/2013 | NC002 | Urban | Network augmentation/maintenanace | 16 | 220 | 3520 | 0.011002 | 5.0009e-05 | 0
9/10/2013 | NC002 | Urban | Network augmentation/maintenanace | 14 | 329 | 4606 | 0.014396 | 4.3758e-05 | 0
27/08/2013 | NC002 | Urban | Network augmentation/maintenanace | 11 | 505 | 5555 | 0.017362 | 3.4381e-05 | 0
10/09/2013 | NC002 | Urban | Network augmentation/maintenanace | 15 | 412 | 6180 | 0.019316 | 4.6883e-05 | 0
26/11/2013 | NC002 | Urban | Network augmentation/maintenanace | 49 | 210 | 10290 | 0.032162 | 0.00015315 | 0
4/07/2013 | NC002 | Urban | Network augmentation/maintenanace | 68 | 255 | 17340 | 0.054197 | 0.00021254 | 0
23/10/2013 | NC002 | Urban | Network augmentation/maintenanace | 46 | 385 | 17710 | 0.055353 | 0.00014377 | 0
12/09/2013 | NC002 | Urban | Network augmentation/maintenanace | 99 | 263 | 26037 | 0.08138 | 0.00030943 | 0
13/04/2013 | NC002 | Urban | Network augmentation/maintenanace | 61 | 435 | 26535 | 0.082936 | 0.00019066 | 0
25/09/2013 | NC002 | Urban | Network augmentation/maintenanace | 169 | 250 | 42250 | 0.13205 | 0.00052822 | 0
16/10/2013 | NC004 | Urban | Network augmentation/maintenanace | 1 | 6 | 6 | 1.8753e-05 | 3.1255e-06 | 0
16/10/2013 | NC004 | Urban | Network augmentation/maintenanace | 1 | 19 | 19 | 5.9385e-05 | 3.1255e-06 | 0
26/05/2013 | NC004 | Urban | Network augmentation/maintenanace | 2 | 75 | 150 | 0.00046883 | 6.2511e-06 | 0
11/10/2013 | NC004 | Urban | Network augmentation/maintenanace | 13 | 195 | 2535 | 0.0079232 | 4.0632e-05 | 0
23/10/2013 | NC004 | Urban | Network augmentation/maintenanace | 13 | 205 | 2665 | 0.0083296 | 4.0632e-05 | 0
9/10/2013 | NC004 | Urban | Network augmentation/maintenanace | 16 | 190 | 3040 | 0.0095016 | 5.0009e-05 | 0
27/09/2013 | NC004 | Urban | Network augmentation/maintenanace | 73 | 147 | 10731 | 0.03354 | 0.00022816 | 0
17/10/2013 | NC004 | Urban | Network augmentation/maintenanace | 125 | 90 | 11250 | 0.035162 | 0.00039069 | 0
26/05/2013 | NC004 | Urban | Network augmentation/maintenanace | 37 | 498.6486 | 18450 | 0.057666 | 0.00011564 | 0
23/05/2013 | NC004 | Urban | Network augmentation/maintenanace | 66 | 393.6364 | 25980 | 0.081201 | 0.00020629 | 0
1/12/2013 | NC005 | Urban | Network augmentation/maintenanace | 1 | 10 | 10 | 3.1255e-05 | 3.1255e-06 | 0
1/12/2013 | NC005 | Urban | Network augmentation/maintenanace | 6 | 10 | 60 | 0.00018753 | 1.8753e-05 | 0
26/06/2013 | NC005 | Urban | Network augmentation/maintenanace | 6 | 16.6667 | 100 | 0.00031255 | 1.8753e-05 | 0
24/09/2013 | NC005 | Urban | Network augmentation/maintenanace | 9 | 84 | 756 | 0.0023629 | 2.813e-05 | 0
22/09/2013 | NC005 | Urban | Network augmentation/maintenanace | 3 | 425 | 1275 | 0.0039851 | 9.3766e-06 | 0
31/05/2013 | NC005 | Urban | Network augmentation/maintenanace | 9 | 230 | 2070 | 0.0064699 | 2.813e-05 | 0
29/05/2013 | NC005 | Urban | Network augmentation/maintenanace | 11 | 295 | 3245 | 0.010142 | 3.4381e-05 | 0
4/08/2013 | NC005 | Urban | Network augmentation/maintenanace | 48 | 355 | 17040 | 0.053259 | 0.00015003 | 0
23/09/2013 | NC006 | Urban | Network augmentation/maintenanace | 9 | 230 | 2070 | 0.0064699 | 2.813e-05 | 0
15/05/2013 | NC006 | Urban | Network augmentation/maintenanace | 10 | 330 | 3300 | 0.010314 | 3.1255e-05 | 0
9/07/2013 | NC006 | Urban | Network augmentation/maintenanace | 15 | 345 | 5175 | 0.016175 | 4.6883e-05 | 0
6/10/2013 | NC006 | Urban | Network augmentation/maintenanace | 24 | 395 | 9480 | 0.02963 | 7.5013e-05 | 0
3/10/2013 | NC006 | Urban | Network augmentation/maintenanace | 57 | 208 | 11856 | 0.037056 | 0.00017816 | 0
1/12/2013 | NC009 | Urban | Network augmentation/maintenanace | 4 | 10 | 40 | 0.00012502 | 1.2502e-05 | 0
1/12/2013 | NC009 | Urban | Network augmentation/maintenanace | 4 | 10 | 40 | 0.00012502 | 1.2502e-05 | 0
24/09/2013 | NC009 | Urban | Network augmentation/maintenanace | 2 | 84 | 168 | 0.00052509 | 6.2511e-06 | 0
8/03/2013 | NC009 | Urban | Network augmentation/maintenanace | 20 | 220 | 4400 | 0.013752 | 6.2511e-05 | 0
25/10/2013 | NC009 | Urban | Network augmentation/maintenanace | 19 | 260 | 4940 | 0.01544 | 5.9385e-05 | 0
21/10/2013 | NC009 | Urban | Network augmentation/maintenanace | 30 | 180 | 5400 | 0.016878 | 9.3766e-05 | 0
29/10/2013 | NC009 | Urban | Network augmentation/maintenanace | 30 | 228 | 6840 | 0.021379 | 9.3766e-05 | 0
24/09/2013 | NC009 | Urban | Network augmentation/maintenanace | 24 | 450 | 10800 | 0.033756 | 7.5013e-05 | 0
29/01/2013 | NC009 | Urban | Network augmentation/maintenanace | 36 | 330 | 11880 | 0.037131 | 0.00011252 | 0
1/11/2013 | NC009 | Urban | Network augmentation/maintenanace | 49 | 311.6327 | 15270 | 0.047727 | 0.00015315 | 0
3/10/2013 | NC009 | Urban | Network augmentation/maintenanace | 27 | 601 | 16227 | 0.050718 | 8.439e-05 | 0
1/12/2013 | NC010 | Urban | Network augmentation/maintenanace | 11 | 10 | 110 | 0.00034381 | 3.4381e-05 | 0
1/12/2013 | NC010 | Urban | Network augmentation/maintenanace | 14 | 10 | 140 | 0.00043758 | 4.3758e-05 | 0
4/08/2013 | NC010 | Urban | Network augmentation/maintenanace | 1 | 355 | 355 | 0.0011096 | 3.1255e-06 | 0
20/09/2013 | NC010 | Urban | Network augmentation/maintenanace | 4 | 240 | 960 | 0.0030005 | 1.2502e-05 | 0
5/07/2013 | NC010 | Urban | Network augmentation/maintenanace | 169 | 9 | 1521 | 0.0047539 | 0.00052822 | 0
29/08/2013 | NC010 | Urban | Network augmentation/maintenanace | 15 | 280 | 4200 | 0.013127 | 4.6883e-05 | 0
29/05/2013 | NC010 | Urban | Network augmentation/maintenanace | 17 | 335 | 5695 | 0.0178 | 5.3134e-05 | 0
9/10/2013 | NC010 | Urban | Network augmentation/maintenanace | 22 | 366 | 8052 | 0.025167 | 6.8762e-05 | 0
16/04/2013 | NC010 | Urban | Network augmentation/maintenanace | 34 | 299 | 10166 | 0.031774 | 0.00010627 | 0
12/11/2013 | NC010 | Urban | Network augmentation/maintenanace | 20 | 510 | 10200 | 0.03188 | 6.2511e-05 | 0
8/10/2013 | NC010 | Urban | Network augmentation/maintenanace | 22 | 560 | 12320 | 0.038507 | 6.8762e-05 | 0
6/08/2013 | NC010 | Urban | Network augmentation/maintenanace | 43 | 375 | 16125 | 0.050399 | 0.0001344 | 0
27/09/2013 | NC013 | Urban | Network augmentation/maintenanace | 3 | 270 | 810 | 0.0025317 | 9.3766e-06 | 0
24/09/2013 | NC013 | Urban | Network augmentation/maintenanace | 5 | 305 | 1525 | 0.0047664 | 1.5628e-05 | 0
25/09/2013 | NC013 | Urban | Network augmentation/maintenanace | 15 | 165 | 2475 | 0.0077357 | 4.6883e-05 | 0
20/09/2013 | NC013 | Urban | Network augmentation/maintenanace | 13 | 240 | 3120 | 0.0097517 | 4.0632e-05 | 0
15/11/2013 | NC013 | Urban | Network augmentation/maintenanace | 162 | 477 | 77274 | 0.24152 | 0.00050634 | 0
9/11/2013 | NC014 | Urban | Network augmentation/maintenanace | 1 | 135 | 135 | 0.00042195 | 3.1255e-06 | 0
10/10/2013 | NC014 | Urban | Network augmentation/maintenanace | 1 | 180 | 180 | 0.0005626 | 3.1255e-06 | 0
11/10/2013 | NC014 | Urban | Network augmentation/maintenanace | 1 | 220 | 220 | 0.00068762 | 3.1255e-06 | 0
17/12/2013 | NC014 | Urban | Network augmentation/maintenanace | 4 | 59 | 236 | 0.00073763 | 1.2502e-05 | 0
10/10/2013 | NC014 | Urban | Network augmentation/maintenanace | 3 | 180 | 540 | 0.0016878 | 9.3766e-06 | 0
24/09/2013 | NC014 | Urban | Network augmentation/maintenanace | 80 | 400 | 32000 | 0.10002 | 0.00025004 | 0
21/08/2013 | NC014 | Urban | Network augmentation/maintenanace | 129 | 320 | 41280 | 0.12902 | 0.00040319 | 0
31/10/2013 | NC015 | Urban | Network augmentation/maintenanace | 2 | 310 | 620 | 0.0019378 | 6.2511e-06 | 0
20/11/2013 | NC015 | Urban | Network augmentation/maintenanace | 5 | 155 | 775 | 0.0024223 | 1.5628e-05 | 0
18/11/2013 | NC015 | Urban | Network augmentation/maintenanace | 26 | 240 | 6240 | 0.019503 | 8.1264e-05 | 0
20/11/2013 | NC015 | Urban | Network augmentation/maintenanace | 29 | 220 | 6380 | 0.019941 | 9.0641e-05 | 0
15/10/2013 | NC015 | Urban | Network augmentation/maintenanace | 91 | 120 | 10920 | 0.034131 | 0.00028442 | 0
17/12/2013 | NC015 | Urban | Network augmentation/maintenanace | 103 | 311.9806 | 32134 | 0.10044 | 0.00032193 | 0
9/05/2013 | NR002 | Urban | Network augmentation/maintenanace | 3 | 260 | 780 | 0.0024379 | 9.3766e-06 | 0
13/06/2013 | NR002 | Urban | Network augmentation/maintenanace | 4 | 230 | 920 | 0.0028755 | 1.2502e-05 | 0
20/02/2013 | NR002 | Urban | Network augmentation/maintenanace | 6 | 370 | 2220 | 0.0069387 | 1.8753e-05 | 0
5/07/2013 | NR002 | Urban | Network augmentation/maintenanace | 30 | 125 | 3750 | 0.011721 | 9.3766e-05 | 0
5/07/2013 | NR002 | Urban | Network augmentation/maintenanace | 17 | 440 | 7480 | 0.023379 | 5.3134e-05 | 0
5/08/2013 | NR002 | Urban | Network augmentation/maintenanace | 44 | 484 | 21296 | 0.066561 | 0.00013752 | 0
2/07/2013 | NR002 | Urban | Network augmentation/maintenanace | 107 | 400 | 42800 | 0.13377 | 0.00033443 | 0
26/06/2013 | NR002 | Urban | Network augmentation/maintenanace | 94 | 463 | 43522 | 0.13603 | 0.0002938 | 0
19/01/2013 | NR003 | Urban | Network augmentation/maintenanace | 1 | 95 | 95 | 0.00029693 | 3.1255e-06 | 0
8/02/2013 | NR003 | Urban | Network augmentation/maintenanace | 2 | 67 | 134 | 0.00041882 | 6.2511e-06 | 0
10/08/2013 | NR003 | Urban | Network augmentation/maintenanace | 1 | 375 | 375 | 0.0011721 | 3.1255e-06 | 0
20/03/2013 | NR003 | Urban | Network augmentation/maintenanace | 5 | 75 | 375 | 0.0011721 | 1.5628e-05 | 0
19/01/2013 | NR003 | Urban | Network augmentation/maintenanace | 11 | 100 | 1100 | 0.0034381 | 3.4381e-05 | 0
21/03/2013 | NR003 | Urban | Network augmentation/maintenanace | 16 | 70 | 1120 | 0.0035006 | 5.0009e-05 | 0
26/03/2013 | NR003 | Urban | Network augmentation/maintenanace | 14 | 385 | 5390 | 0.016847 | 4.3758e-05 | 0
23/05/2013 | NR003 | Urban | Network augmentation/maintenanace | 70 | 347 | 24290 | 0.075919 | 0.00021879 | 0
10/02/2013 | NR003 | Urban | Network augmentation/maintenanace | 106 | 435 | 46110 | 0.14412 | 0.00033131 | 0
11/12/2013 | NR006 | Urban | Network augmentation/maintenanace | 17 | 150 | 2550 | 0.0079701 | 5.3134e-05 | 0
11/05/2013 | NR006 | Urban | Network augmentation/maintenanace | 16 | 160 | 2560 | 0.0080014 | 5.0009e-05 | 0
23/01/2013 | NR006 | Urban | Network augmentation/maintenanace | 17 | 280 | 4760 | 0.014878 | 5.3134e-05 | 0
15/08/2013 | NR006 | Urban | Network augmentation/maintenanace | 18 | 302 | 5436 | 0.01699 | 5.626e-05 | 0
13/06/2013 | NR007 | Urban | Network augmentation/maintenanace | 6 | 230 | 1380 | 0.0043132 | 1.8753e-05 | 0
26/07/2013 | NR007 | Urban | Network augmentation/maintenanace | 12 | 159 | 1908 | 0.0059635 | 3.7506e-05 | 0
10/07/2013 | NR007 | Urban | Network augmentation/maintenanace | 44 | 305 | 13420 | 0.041945 | 0.00013752 | 0
21/09/2013 | NR015 | Urban | Network augmentation/maintenanace | 1 | 395 | 395 | 0.0012346 | 3.1255e-06 | 0
5/09/2013 | NR015 | Urban | Network augmentation/maintenanace | 16 | 335 | 5360 | 0.016753 | 5.0009e-05 | 0
13/10/2013 | NR015 | Urban | Network augmentation/maintenanace | 97 | 480 | 46560 | 0.14553 | 0.00030318 | 0
8/09/2013 | NR016 | Urban | Network augmentation/maintenanace | 1 | 250 | 250 | 0.00078138 | 3.1255e-06 | 0
24/05/2013 | NR021 | Urban | Network augmentation/maintenanace | 7 | 145 | 1015 | 0.0031724 | 2.1879e-05 | 0
24/11/2013 | NR022 | Urban | Network augmentation/maintenanace | 9 | 20 | 180 | 0.0005626 | 2.813e-05 | 0
16/11/2013 | NR022 | Urban | Network augmentation/maintenanace | 12 | 360 | 4320 | 0.013502 | 3.7506e-05 | 0
16/10/2013 | NR022 | Urban | Network augmentation/maintenanace | 103 | 370 | 38110 | 0.11911 | 0.00032193 | 0
2/12/2013 | NS013 | Urban | Network augmentation/maintenanace | 1 | 45 | 45 | 0.00014065 | 3.1255e-06 | 0
10/07/2013 | PM002 | Urban | Network augmentation/maintenanace | 1 | 285 | 285 | 0.00089078 | 3.1255e-06 | 0
22/02/2013 | PM006 | Urban | Network augmentation/maintenanace | 2 | 88 | 176 | 0.00055009 | 6.2511e-06 | 0
28/05/2013 | PM006 | Urban | Network augmentation/maintenanace | 1 | 550 | 550 | 0.001719 | 3.1255e-06 | 0
8/03/2013 | PM009 | Urban | Network augmentation/maintenanace | 1 | 96 | 96 | 0.00030005 | 3.1255e-06 | 0
8/03/2013 | PM009 | Urban | Network augmentation/maintenanace | 9 | 255 | 2295 | 0.0071731 | 2.813e-05 | 0
30/06/2013 | PR018 | Urban | Network augmentation/maintenanace | 14 | 350 | 4900 | 0.015315 | 4.3758e-05 | 0
15/09/2013 | PR018 | Urban | Network augmentation/maintenanace | 32 | 715 | 22880 | 0.071512 | 0.00010002 | 0
7/05/2013 | PR019 | Urban | Network augmentation/maintenanace | 1 | 45 | 45 | 0.00014065 | 3.1255e-06 | 0
17/11/2013 | PR019 | Urban | Network augmentation/maintenanace | 7 | 485 | 3395 | 0.010611 | 2.1879e-05 | 0
30/05/2013 | PR020 | Urban | Network augmentation/maintenanace | 1 | 57 | 57 | 0.00017816 | 3.1255e-06 | 0
15/04/2013 | PR020 | Urban | Network augmentation/maintenanace | 1 | 178 | 178 | 0.00055635 | 3.1255e-06 | 0
12/04/2013 | PR020 | Urban | Network augmentation/maintenanace | 40 | 35 | 1400 | 0.0043758 | 0.00012502 | 0
16/09/2013 | PR020 | Urban | Network augmentation/maintenanace | 6 | 475 | 2850 | 0.0089078 | 1.8753e-05 | 0
8/10/2013 | PR020 | Urban | Network augmentation/maintenanace | 21 | 385 | 8085 | 0.02527 | 6.5636e-05 | 0
20/10/2013 | PR020 | Urban | Network augmentation/maintenanace | 42 | 540 | 22680 | 0.070887 | 0.00013127 | 0
30/05/2013 | PR023 | Urban | Network augmentation/maintenanace | 39 | 57 | 2223 | 0.0069481 | 0.0001219 | 0
28/11/2013 | PR023 | Urban | Network augmentation/maintenanace | 89 | 100 | 8900 | 0.027817 | 0.00027817 | 0
11/08/2013 | PR023 | Urban | Network augmentation/maintenanace | 22 | 670 | 14740 | 0.04607 | 6.8762e-05 | 0
7/11/2013 | PR025 | Urban | Network augmentation/maintenanace | 12 | 345 | 4140 | 0.01294 | 3.7506e-05 | 0
29/01/2013 | PR026 | Urban | Network augmentation/maintenanace | 56 | 300 | 16800 | 0.052509 | 0.00017503 | 0
24/11/2013 | PR026 | Urban | Network augmentation/maintenanace | 81 | 234 | 18954 | 0.059241 | 0.00025317 | 0
16/06/2013 | Q001 | Urban | Network augmentation/maintenanace | 12 | 390 | 4680 | 0.014628 | 3.7506e-05 | 0
3/05/2013 | Q001 | Urban | Network augmentation/maintenanace | 40 | 286 | 11440 | 0.035756 | 0.00012502 | 0
3/05/2013 | Q001 | Urban | Network augmentation/maintenanace | 95 | 295 | 28025 | 0.087593 | 0.00029693 | 0
14/05/2013 | Q002 | Urban | Network augmentation/maintenanace | 1 | 300 | 300 | 0.00093766 | 3.1255e-06 | 0
16/07/2013 | Q002 | Urban | Network augmentation/maintenanace | 1 | 375 | 375 | 0.0011721 | 3.1255e-06 | 0
18/04/2013 | Q002 | Urban | Network augmentation/maintenanace | 25 | 175 | 4375 | 0.013674 | 7.8138e-05 | 0
1/09/2013 | Q004 | Urban | Network augmentation/maintenanace | 5 | 148 | 740 | 0.0023129 | 1.5628e-05 | 0
12/04/2013 | Q005 | Urban | Network augmentation/maintenanace | 2 | 150 | 300 | 0.00093766 | 6.2511e-06 | 0
8/01/2013 | Q005 | Urban | Network augmentation/maintenanace | 2 | 170 | 340 | 0.0010627 | 6.2511e-06 | 0
25/02/2013 | Q005 | Urban | Network augmentation/maintenanace | 21 | 185 | 3885 | 0.012143 | 6.5636e-05 | 0
5/05/2013 | Q005 | Urban | Network augmentation/maintenanace | 39 | 465 | 18135 | 0.056682 | 0.0001219 | 0
24/08/2013 | Q005 | Urban | Network augmentation/maintenanace | 134 | 273 | 36582 | 0.11434 | 0.00041882 | 0
15/04/2013 | Q009 | Urban | Network augmentation/maintenanace | 21 | 210 | 4410 | 0.013784 | 6.5636e-05 | 0
28/04/2013 | Q010 | Urban | Network augmentation/maintenanace | 31 | 235 | 7285 | 0.02277 | 9.6892e-05 | 0
28/07/2013 | Q013 | Urban | Network augmentation/maintenanace | 1 | 67 | 67 | 0.00020941 | 3.1255e-06 | 0
28/06/2013 | Q013 | Urban | Network augmentation/maintenanace | 3 | 160 | 480 | 0.0015003 | 9.3766e-06 | 0
28/07/2013 | Q013 | Urban | Network augmentation/maintenanace | 7 | 333 | 2331 | 0.0072856 | 2.1879e-05 | 0
23/07/2013 | Q013 | Urban | Network augmentation/maintenanace | 40 | 180 | 7200 | 0.022504 | 0.00012502 | 0
28/07/2013 | Q013 | Urban | Network augmentation/maintenanace | 71 | 287.7465 | 20430 | 0.063855 | 0.00022191 | 0
28/07/2013 | Q013 | Urban | Network augmentation/maintenanace | 76 | 442 | 33592 | 0.10499 | 0.00023754 | 0
28/02/2013 | Q014 | Urban | Network augmentation/maintenanace | 1 | 1 | 1 | 3.1255e-06 | 3.1255e-06 | 0
28/02/2013 | Q014 | Urban | Network augmentation/maintenanace | 1 | 13 | 13 | 4.0632e-05 | 3.1255e-06 | 0
28/02/2013 | Q014 | Urban | Network augmentation/maintenanace | 1 | 28 | 28 | 8.7515e-05 | 3.1255e-06 | 0
16/01/2013 | Q014 | Urban | Network augmentation/maintenanace | 1 | 155 | 155 | 0.00048446 | 3.1255e-06 | 0
8/02/2013 | Q014 | Urban | Network augmentation/maintenanace | 2 | 120 | 240 | 0.00075013 | 6.2511e-06 | 0
5/02/2013 | Q014 | Urban | Network augmentation/maintenanace | 15 | 190 | 2850 | 0.0089078 | 4.6883e-05 | 0
25/01/2013 | Q014 | Urban | Network augmentation/maintenanace | 36 | 230 | 8280 | 0.025879 | 0.00011252 | 0
14/01/2013 | Q014 | Urban | Network augmentation/maintenanace | 31 | 290 | 8990 | 0.028099 | 9.6892e-05 | 0
25/01/2013 | Q014 | Urban | Network augmentation/maintenanace | 25 | 380 | 9500 | 0.029693 | 7.8138e-05 | 0
24/01/2013 | Q014 | Urban | Network augmentation/maintenanace | 54 | 257 | 13878 | 0.043376 | 0.00016878 | 0
28/02/2013 | Q014 | Urban | Network augmentation/maintenanace | 39 | 460.5128 | 17960 | 0.056135 | 0.0001219 | 0
30/01/2013 | Q014 | Urban | Network augmentation/maintenanace | 60 | 305 | 18300 | 0.057197 | 0.00018753 | 0
30/12/2013 | Q015 | Urban | Network augmentation/maintenanace | 5 | 365 | 1825 | 0.0057041 | 1.5628e-05 | 0
21/03/2013 | Q018 | Urban | Network augmentation/maintenanace | 36 | 8 | 288 | 0.00090015 | 0.00011252 | 0
11/04/2013 | Q018 | Urban | Network augmentation/maintenanace | 36 | 213 | 7668 | 0.023967 | 0.00011252 | 0
28/06/2013 | Q019 | Urban | Network augmentation/maintenanace | 1 | 270 | 270 | 0.0008439 | 3.1255e-06 | 0
28/05/2013 | Q019 | Urban | Network augmentation/maintenanace | 1 | 338 | 338 | 0.0010564 | 3.1255e-06 | 0
17/08/2013 | Q019 | Urban | Network augmentation/maintenanace | 2 | 433 | 866 | 0.0027067 | 6.2511e-06 | 0
13/01/2013 | Q019 | Urban | Network augmentation/maintenanace | 10 | 240 | 2400 | 0.0075013 | 3.1255e-05 | 0
16/07/2013 | Q019 | Urban | Network augmentation/maintenanace | 12 | 375 | 4500 | 0.014065 | 3.7506e-05 | 0
11/04/2013 | Q019 | Urban | Network augmentation/maintenanace | 66 | 315 | 20790 | 0.06498 | 0.00020629 | 0
30/07/2013 | Q019 | Urban | Network augmentation/maintenanace | 84 | 665 | 55860 | 0.17459 | 0.00026255 | 0
28/04/2013 | R022 | Urban | Network augmentation/maintenanace | 1 | 65 | 65 | 0.00020316 | 3.1255e-06 | 0
4/11/2013 | R022 | Urban | Network augmentation/maintenanace | 2 | 240 | 480 | 0.0015003 | 6.2511e-06 | 0
28/03/2013 | R022 | Urban | Network augmentation/maintenanace | 6 | 135 | 810 | 0.0025317 | 1.8753e-05 | 0
27/03/2013 | R022 | Urban | Network augmentation/maintenanace | 17 | 275 | 4675 | 0.014612 | 5.3134e-05 | 0
8/12/2013 | R022 | Urban | Network augmentation/maintenanace | 18 | 480 | 8640 | 0.027005 | 5.626e-05 | 0
5/05/2013 | R022 | Urban | Network augmentation/maintenanace | 46 | 240 | 11040 | 0.034506 | 0.00014377 | 0
7/07/2013 | R022 | Urban | Network augmentation/maintenanace | 26 | 453 | 11778 | 0.036813 | 8.1264e-05 | 0
28/11/2013 | R022 | Urban | Network augmentation/maintenanace | 58 | 238 | 13804 | 0.043145 | 0.00018128 | 0
28/03/2013 | R022 | Urban | Network augmentation/maintenanace | 107 | 132 | 14124 | 0.044145 | 0.00033443 | 0
6/12/2013 | R023 | Urban | Network augmentation/maintenanace | 9 | 205 | 1845 | 0.0057666 | 2.813e-05 | 0
7/04/2013 | R023 | Urban | Network augmentation/maintenanace | 22 | 149 | 3278 | 0.010246 | 6.8762e-05 | 0
17/12/2013 | R023 | Urban | Network augmentation/maintenanace | 70 | 350 | 24500 | 0.076576 | 0.00021879 | 0
2/06/2013 | R024 | Urban | Network augmentation/maintenanace | 6 | 106 | 636 | 0.0019878 | 1.8753e-05 | 0
5/05/2013 | R024 | Urban | Network augmentation/maintenanace | 16 | 350 | 5600 | 0.017503 | 5.0009e-05 | 0
12/06/2013 | R031 | Urban | Network augmentation/maintenanace | 10 | 45 | 450 | 0.0014065 | 3.1255e-05 | 0
18/04/2013 | R031 | Urban | Network augmentation/maintenanace | 22 | 110 | 2420 | 0.0075638 | 6.8762e-05 | 0
2/06/2013 | R031 | Urban | Network augmentation/maintenanace | 13 | 330 | 4290 | 0.013409 | 4.0632e-05 | 0
5/05/2013 | R031 | Urban | Network augmentation/maintenanace | 26 | 295 | 7670 | 0.023973 | 8.1264e-05 | 0
28/04/2013 | R033 | Urban | Network augmentation/maintenanace | 28 | 210 | 5880 | 0.018378 | 8.7515e-05 | 0
8/12/2013 | R033 | Urban | Network augmentation/maintenanace | 28 | 500 | 14000 | 0.043758 | 8.7515e-05 | 0
22/05/2013 | R034 | Urban | Network augmentation/maintenanace | 39 | 290 | 11310 | 0.03535 | 0.0001219 | 0
24/03/2013 | R035 | Urban | Network augmentation/maintenanace | 1 | 351 | 351 | 0.0010971 | 3.1255e-06 | 0
11/04/2013 | R035 | Urban | Network augmentation/maintenanace | 2 | 275 | 550 | 0.001719 | 6.2511e-06 | 0
14/04/2013 | R035 | Urban | Network augmentation/maintenanace | 2 | 475 | 950 | 0.0029693 | 6.2511e-06 | 0
24/03/2013 | R035 | Urban | Network augmentation/maintenanace | 6 | 403 | 2418 | 0.0075575 | 1.8753e-05 | 0
5/05/2013 | R035 | Urban | Network augmentation/maintenanace | 22 | 240 | 5280 | 0.016503 | 6.8762e-05 | 0
5/05/2013 | R035 | Urban | Network augmentation/maintenanace | 21 | 305 | 6405 | 0.020019 | 6.5636e-05 | 0
24/03/2013 | R035 | Urban | Network augmentation/maintenanace | 22 | 362 | 7964 | 0.024892 | 6.8762e-05 | 0
5/05/2013 | R035 | Urban | Network augmentation/maintenanace | 42 | 595 | 24990 | 0.078107 | 0.00013127 | 0
31/10/2013 | RD001 | Urban | Network augmentation/maintenanace | 53 | 325 | 17225 | 0.053837 | 0.00016565 | 0
10/01/2013 | RD002 | Urban | Network augmentation/maintenanace | 3 | 240 | 720 | 0.0022504 | 9.3766e-06 | 0
8/02/2013 | RD002 | Urban | Network augmentation/maintenanace | 13 | 265 | 3445 | 0.010767 | 4.0632e-05 | 0
10/02/2013 | RD002 | Urban | Network augmentation/maintenanace | 19 | 190 | 3610 | 0.011283 | 5.9385e-05 | 0
2013-02-01 | RD002 | Urban | Network augmentation/maintenanace | 19 | 360 | 6840 | 0.021379 | 5.9385e-05 | 0
7/02/2013 | RD002 | Urban | Network augmentation/maintenanace | 50 | 470 | 23500 | 0.07345 | 0.00015628 | 0
4/07/2013 | RD005 | Urban | Network augmentation/maintenanace | 72 | 120 | 8640 | 0.027005 | 0.00022504 | 0
4/07/2013 | RD006 | Urban | Network augmentation/maintenanace | 1 | 2 | 2 | 6.2511e-06 | 3.1255e-06 | 0
28/02/2013 | RD009 | Urban | Network augmentation/maintenanace | 1 | 136 | 136 | 0.00042507 | 3.1255e-06 | 0
22/02/2013 | RD009 | Urban | Network augmentation/maintenanace | 4 | 68 | 272 | 0.00085015 | 1.2502e-05 | 0
10/02/2013 | RD009 | Urban | Network augmentation/maintenanace | 35 | 148.2 | 5187 | 0.016212 | 0.00010939 | 0
28/02/2013 | RD009 | Urban | Network augmentation/maintenanace | 13 | 425 | 5525 | 0.017269 | 4.0632e-05 | 0
14/03/2013 | RD009 | Urban | Network augmentation/maintenanace | 22 | 345 | 7590 | 0.023723 | 6.8762e-05 | 0
11/01/2013 | RD013 | Urban | Network augmentation/maintenanace | 2 | 150 | 300 | 0.00093766 | 6.2511e-06 | 0
6/11/2013 | RD013 | Urban | Network augmentation/maintenanace | 8 | 200 | 1600 | 0.0050009 | 2.5004e-05 | 0
11/10/2013 | RD013 | Urban | Network augmentation/maintenanace | 8 | 290 | 2320 | 0.0072512 | 2.5004e-05 | 0
1/02/2013 | RD013 | Urban | Network augmentation/maintenanace | 28 | 270 | 7560 | 0.023629 | 8.7515e-05 | 0
12/02/2013 | RD014 | Urban | Network augmentation/maintenanace | 33 | 172 | 5676 | 0.017741 | 0.00010314 | 0
8/12/2013 | RD014 | Urban | Network augmentation/maintenanace | 18 | 440 | 7920 | 0.024754 | 5.626e-05 | 0
11/02/2013 | RD014 | Urban | Network augmentation/maintenanace | 25 | 320 | 8000 | 0.025004 | 7.8138e-05 | 0
11/01/2013 | RD015 | Urban | Network augmentation/maintenanace | 8 | 165 | 1320 | 0.0041257 | 2.5004e-05 | 0
25/08/2013 | SB012 | CBD | Network augmentation/maintenanace | 6 | 170 | 1020 | 0.003188 | 1.8753e-05 | 0
13/10/2013 | SB012 | CBD | Network augmentation/maintenanace | 26 | 318 | 8268 | 0.025842 | 8.1264e-05 | 0
25/11/2013 | SB012 | CBD | Network augmentation/maintenanace | 130 | 100 | 13000 | 0.040632 | 0.00040632 | 0
19/10/2013 | SB012 | CBD | Network augmentation/maintenanace | 8 | 1797 | 14376 | 0.044933 | 2.5004e-05 | 0
20/01/2013 | SB015 | CBD | Network augmentation/maintenanace | 4 | 420 | 1680 | 0.0052509 | 1.2502e-05 | 0
10/09/2013 | SK001 | Urban | Network augmentation/maintenanace | 77 | 250 | 19250 | 0.060167 | 0.00024067 | 0
12/06/2013 | SK002 | CBD | Network augmentation/maintenanace | 2 | 120 | 240 | 0.00075013 | 6.2511e-06 | 0
16/07/2013 | SK005 | Urban | Network augmentation/maintenanace | 7 | 150 | 1050 | 0.0032818 | 2.1879e-05 | 0
5/06/2013 | SK005 | Urban | Network augmentation/maintenanace | 24 | 210 | 5040 | 0.015753 | 7.5013e-05 | 0
1/09/2013 | SK005 | Urban | Network augmentation/maintenanace | 188 | 135 | 25380 | 0.079326 | 0.0005876 | 0
24/03/2013 | SK005 | Urban | Network augmentation/maintenanace | 59 | 480 | 28320 | 0.088515 | 0.00018441 | 0
22/05/2013 | SK006 | Urban | Network augmentation/maintenanace | 17 | 290 | 4930 | 0.015409 | 5.3134e-05 | 0
28/08/2013 | SK013 | Urban | Network augmentation/maintenanace | 43 | 380 | 16340 | 0.051071 | 0.0001344 | 0
24/11/2013 | SK014 | CBD | Network augmentation/maintenanace | 114 | 65 | 7410 | 0.02316 | 0.00035631 | 0
16/01/2013 | SK015 | CBD | Network augmentation/maintenanace | 1 | 430 | 430 | 0.001344 | 3.1255e-06 | 0
18/08/2013 | SK015 | CBD | Network augmentation/maintenanace | 10 | 595 | 5950 | 0.018597 | 3.1255e-05 | 0
18/08/2013 | SK019 | CBD | Network augmentation/maintenanace | 80 | 128 | 10240 | 0.032006 | 0.00025004 | 0
25/08/2013 | SK022 | CBD | Network augmentation/maintenanace | 12 | 633 | 7596 | 0.023742 | 3.7506e-05 | 0
15/09/2013 | SK025 | Urban | Network augmentation/maintenanace | 2 | 715 | 1430 | 0.0044695 | 6.2511e-06 | 0
13/07/2013 | SK025 | Urban | Network augmentation/maintenanace | 47 | 48 | 2256 | 0.0070512 | 0.0001469 | 0
7/07/2013 | SK025 | Urban | Network augmentation/maintenanace | 47 | 110 | 5170 | 0.016159 | 0.0001469 | 0
6/10/2013 | SO001 | CBD | Network augmentation/maintenanace | 1 | 625 | 625 | 0.0019535 | 3.1255e-06 | 0
15/05/2013 | SO010 | CBD | Network augmentation/maintenanace | 22 | 120 | 2640 | 0.0082514 | 6.8762e-05 | 0
6/10/2013 | SO010 | CBD | Network augmentation/maintenanace | 107 | 570 | 60990 | 0.19063 | 0.00033443 | 0
24/02/2013 | SO018 | Urban | Network augmentation/maintenanace | 6 | 245 | 1470 | 0.0045945 | 1.8753e-05 | 0
7/05/2013 | TK001 | Urban | Network augmentation/maintenanace | 1 | 300 | 300 | 0.00093766 | 3.1255e-06 | 0
21/04/2013 | TK001 | Urban | Network augmentation/maintenanace | 2 | 390 | 780 | 0.0024379 | 6.2511e-06 | 0
7/05/2013 | TK001 | Urban | Network augmentation/maintenanace | 8 | 320 | 2560 | 0.0080014 | 2.5004e-05 | 0
18/07/2013 | TK004 | Urban | Network augmentation/maintenanace | 5 | 355 | 1775 | 0.0055478 | 1.5628e-05 | 0
2/12/2013 | TK004 | Urban | Network augmentation/maintenanace | 28 | 228 | 6384 | 0.019953 | 8.7515e-05 | 0
22/10/2013 | TK004 | Urban | Network augmentation/maintenanace | 17 | 410 | 6970 | 0.021785 | 5.3134e-05 | 0
30/07/2013 | TK004 | Urban | Network augmentation/maintenanace | 68 | 345 | 23460 | 0.073325 | 0.00021254 | 0
2/10/2013 | TK004 | Urban | Network augmentation/maintenanace | 157 | 430 | 67510 | 0.21101 | 0.00049071 | 0
22/10/2013 | TK005 | Urban | Network augmentation/maintenanace | 2 | 410 | 820 | 0.0025629 | 6.2511e-06 | 0
5/03/2013 | TK005 | Urban | Network augmentation/maintenanace | 58 | 200 | 11600 | 0.036256 | 0.00018128 | 0
12/07/2013 | TK006 | Urban | Network augmentation/maintenanace | 2 | 315 | 630 | 0.0019691 | 6.2511e-06 | 0
5/09/2013 | TK006 | Urban | Network augmentation/maintenanace | 5 | 295 | 1475 | 0.0046102 | 1.5628e-05 | 0
10/09/2013 | TK006 | Urban | Network augmentation/maintenanace | 18 | 125 | 2250 | 0.0070325 | 5.626e-05 | 0
24/04/2013 | TK006 | Urban | Network augmentation/maintenanace | 30 | 90 | 2700 | 0.008439 | 9.3766e-05 | 0
29/10/2013 | TK006 | Urban | Network augmentation/maintenanace | 18 | 530 | 9540 | 0.029818 | 5.626e-05 | 0
12/11/2013 | TK006 | Urban | Network augmentation/maintenanace | 33 | 325 | 10725 | 0.033521 | 0.00010314 | 0
26/11/2013 | TK006 | Urban | Network augmentation/maintenanace | 26 | 450.9231 | 11724 | 0.036644 | 8.1264e-05 | 0
12/12/2013 | TK006 | Urban | Network augmentation/maintenanace | 61 | 425 | 25925 | 0.08103 | 0.00019066 | 0
25/06/2013 | TK006 | Urban | Network augmentation/maintenanace | 92 | 540.8261 | 49756 | 0.15551 | 0.00028755 | 0
15/06/2013 | TK006 | Urban | Network augmentation/maintenanace | 98 | 604 | 59192 | 0.18501 | 0.0003063 | 0
27/05/2013 | TK009 | Urban | Network augmentation/maintenanace | 98 | 443 | 43414 | 0.13569 | 0.0003063 | 0
17/06/2013 | TK011 | Urban | Network augmentation/maintenanace | 3 | 40 | 120 | 0.00037506 | 9.3766e-06 | 0
15/06/2013 | TK011 | Urban | Network augmentation/maintenanace | 10 | 604 | 6040 | 0.018878 | 3.1255e-05 | 0
10/09/2013 | TK014 | Urban | Network augmentation/maintenanace | 52 | 125 | 6500 | 0.020316 | 0.00016253 | 0
8/10/2013 | TK014 | Urban | Network augmentation/maintenanace | 66 | 400 | 26400 | 0.082514 | 0.00020629 | 0
15/08/2013 | TK015 | Urban | Network augmentation/maintenanace | 33 | 380 | 12540 | 0.039194 | 0.00010314 | 0
11/12/2013 | TK022 | Urban | Network augmentation/maintenanace | 10 | 360 | 3600 | 0.011252 | 3.1255e-05 | 0
10/12/2013 | TK022 | Urban | Network augmentation/maintenanace | 108 | 390 | 42120 | 0.13165 | 0.00033756 | 0
30/09/2013 | TK025 | Urban | Network augmentation/maintenanace | 1 | 150 | 150 | 0.00046883 | 3.1255e-06 | 0
22/05/2013 | VM004 | Urban | Network augmentation/maintenanace | 2 | 39 | 78 | 0.00024379 | 6.2511e-06 | 0
17/03/2013 | VM004 | Urban | Network augmentation/maintenanace | 15 | 320 | 4800 | 0.015003 | 4.6883e-05 | 0
16/06/2013 | VM004 | Urban | Network augmentation/maintenanace | 23 | 252 | 5796 | 0.018116 | 7.1887e-05 | 0
19/05/2013 | VM008 | Urban | Network augmentation/maintenanace | 10 | 431 | 4310 | 0.013471 | 3.1255e-05 | 0
17/12/2013 | VM014 | CBD | Network augmentation/maintenanace | 13 | 225 | 2925 | 0.0091422 | 4.0632e-05 | 0
7/10/2013 | VM014 | CBD | Network augmentation/maintenanace | 10 | 320 | 3200 | 0.010002 | 3.1255e-05 | 0
17/12/2013 | VM020 | CBD | Network augmentation/maintenanace | 1 | 210 | 210 | 0.00065636 | 3.1255e-06 | 0
2/07/2013 | VM026 | CBD | Network augmentation/maintenanace | 7 | 280 | 1960 | 0.0061261 | 2.1879e-05 | 0
24/11/2013 | VM026 | CBD | Network augmentation/maintenanace | 6 | 400 | 2400 | 0.0075013 | 1.8753e-05 | 0
6/06/2013 | VM026 | CBD | Network augmentation/maintenanace | 7 | 387 | 2709 | 0.0084671 | 2.1879e-05 | 0
30/06/2013 | VM026 | CBD | Network augmentation/maintenanace | 9 | 305 | 2745 | 0.0085796 | 2.813e-05 | 0
21/07/2013 | VM026 | CBD | Network augmentation/maintenanace | 10 | 350 | 3500 | 0.010939 | 3.1255e-05 | 0
24/07/2013 | VM035 | CBD | Network augmentation/maintenanace | 1 | 42 | 42 | 0.00013127 | 3.1255e-06 | 0
24/07/2013 | VM035 | CBD | Network augmentation/maintenanace | 18 | 250 | 4500 | 0.014065 | 5.626e-05 | 0
29/05/2013 | VM040 | Urban | Network augmentation/maintenanace | 5 | 250 | 1250 | 0.0039069 | 1.5628e-05 | 0
15/03/2013 | VM040 | Urban | Network augmentation/maintenanace | 39 | 245 | 9555 | 0.029865 | 0.0001219 | 0
17/03/2013 | VM040 | Urban | Network augmentation/maintenanace | 33 | 320 | 10560 | 0.033006 | 0.00010314 | 0
7/11/2013 | VM041 | CBD | Network augmentation/maintenanace | 45 | 325 | 14625 | 0.045711 | 0.00014065 | 0
2/02/2013 | WA009 | CBD | Network augmentation/maintenanace | 110 | 120 | 13200 | 0.041257 | 0.00034381 | 0
3/02/2013 | WA009 | CBD | Network augmentation/maintenanace | 110 | 182 | 20020 | 0.062573 | 0.00034381 | 0
6/05/2013 | WA014 | CBD | Network augmentation/maintenanace | 5 | 195 | 975 | 0.0030474 | 1.5628e-05 | 0
29/04/2013 | WA014 | CBD | Network augmentation/maintenanace | 6 | 165 | 990 | 0.0030943 | 1.8753e-05 | 0
9/05/2013 | WA014 | CBD | Network augmentation/maintenanace | 11 | 134 | 1474 | 0.004607 | 3.4381e-05 | 0
15/10/2013 | WA015 | CBD | Network augmentation/maintenanace | 201 | 39 | 7839 | 0.024501 | 0.00062823 | 0
16/05/2013 | WA024 | CBD | Network augmentation/maintenanace | 4 | 166 | 664 | 0.0020754 | 1.2502e-05 | 0
30/04/2013 | WA024 | CBD | Network augmentation/maintenanace | 5 | 155 | 775 | 0.0024223 | 1.5628e-05 | 0
9/02/2013 | WA024 | CBD | Network augmentation/maintenanace | 130 | 130 | 16900 | 0.052822 | 0.00040632 | 0
10/02/2013 | WA024 | CBD | Network augmentation/maintenanace | 130 | 230 | 29900 | 0.093454 | 0.00040632 | 0
29/04/2013 | WA033 | CBD | Network augmentation/maintenanace | 3 | 158 | 474 | 0.0014815 | 9.3766e-06 | 0
1/05/2013 | WA033 | CBD | Network augmentation/maintenanace | 9 | 148 | 1332 | 0.0041632 | 2.813e-05 | 0
22/04/2013 | WA033 | CBD | Network augmentation/maintenanace | 20 | 124 | 2480 | 0.0077513 | 6.2511e-05 | 0
5/12/2013 | WB002 | Urban | Network augmentation/maintenanace | 18 | 315 | 5670 | 0.017722 | 5.626e-05 | 0
5/07/2013 | WB002 | Urban | Network augmentation/maintenanace | 152 | 312 | 47424 | 0.14823 | 0.00047508 | 0
4/08/2013 | WB009 | Urban | Network augmentation/maintenanace | 20 | 450 | 9000 | 0.02813 | 6.2511e-05 | 0
18/12/2013 | WB010 | Urban | Network augmentation/maintenanace | 26 | 3 | 78 | 0.00024379 | 8.1264e-05 | 0
17/06/2013 | WB010 | Urban | Network augmentation/maintenanace | 1 | 104 | 104 | 0.00032506 | 3.1255e-06 | 0
4/08/2013 | WB010 | Urban | Network augmentation/maintenanace | 3 | 155 | 465 | 0.0014534 | 9.3766e-06 | 0
18/10/2013 | WB010 | Urban | Network augmentation/maintenanace | 25 | 60 | 1500 | 0.0046883 | 7.8138e-05 | 0
18/12/2013 | WB010 | Urban | Network augmentation/maintenanace | 26 | 200 | 5200 | 0.016253 | 8.1264e-05 | 0
16/06/2013 | WB010 | Urban | Network augmentation/maintenanace | 32 | 385 | 12320 | 0.038507 | 0.00010002 | 0
28/05/2013 | WB015 | Urban | Network augmentation/maintenanace | 7 | 230 | 1610 | 0.0050321 | 2.1879e-05 | 0
30/06/2013 | WB015 | Urban | Network augmentation/maintenanace | 30 | 255 | 7650 | 0.02391 | 9.3766e-05 | 0
19/05/2013 | WB015 | Urban | Network augmentation/maintenanace | 105 | 723 | 75915 | 0.23728 | 0.00032818 | 0
19/02/2013 | WD004 | Urban | Network augmentation/maintenanace | 7 | 285 | 1995 | 0.0062354 | 2.1879e-05 | 0
1/02/2013 | WD006 | Urban | Network augmentation/maintenanace | 1 | 365 | 365 | 0.0011408 | 3.1255e-06 | 0
11/09/2013 | WD011 | Urban | Network augmentation/maintenanace | 8 | 375 | 3000 | 0.0093766 | 2.5004e-05 | 0
16/10/2013 | WD011 | Urban | Network augmentation/maintenanace | 39 | 105 | 4095 | 0.012799 | 0.0001219 | 0
26/05/2013 | WD012 | Urban | Network augmentation/maintenanace | 54 | 170 | 9180 | 0.028692 | 0.00016878 | 0
10/11/2013 | WD013 | Urban | Network augmentation/maintenanace | 14 | 600 | 8400 | 0.026255 | 4.3758e-05 | 0
22/08/2013 | WD013 | Urban | Network augmentation/maintenanace | 61 | 315 | 19215 | 0.060057 | 0.00019066 | 0
31/07/2013 | WD021 | Urban | Network augmentation/maintenanace | 42 | 300 | 12600 | 0.039382 | 0.00013127 | 0
24/08/2013 | WD022 | Urban | Network augmentation/maintenanace | 14 | 211 | 2954 | 0.0092328 | 4.3758e-05 | 0
2/07/2013 | WD022 | Urban | Network augmentation/maintenanace | 9 | 335 | 3015 | 0.0094235 | 2.813e-05 | 0
20/06/2013 | WD031 | Urban | Network augmentation/maintenanace | 24 | 260 | 6240 | 0.019503 | 7.5013e-05 | 0
28/07/2013 | WD032 | Urban | Network augmentation/maintenanace | 35 | 435 | 15225 | 0.047586 | 0.00010939 | 0
15/09/2013 | WG024 | Urban | Network augmentation/maintenanace | 6 | 55 | 330 | 0.0010314 | 1.8753e-05 | 0
23/06/2013 | WG024 | Urban | Network augmentation/maintenanace | 14 | 383 | 5362 | 0.016759 | 4.3758e-05 | 0
28/07/2013 | WG028 | Urban | Network augmentation/maintenanace | 1 | 220 | 220 | 0.00068762 | 3.1255e-06 | 0
Contents

## 6b. Annual Feeder Reliability
CitiPower Pty
Annual Feeder Reliability
2013
Table 1 Annual Feeder Reliability Data
Feeder ID / name | Description of the service area for the feeder | Feeder classification | Number of distribution customers | Length of high voltage distribution lines (overhead) | Length of high voltage distribution lines (underground) | Maximum demand (MVA) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Total number of unplanned outages | Total unplanned minutes off-supply | Unplanned minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) | Unplanned interruptions (SAIFI) (after removing excluded events) | Total number of planned outages | Total planned minutes off-supply | Planned interruptions (SAIFI) | Total number of momentary feeder outages | Total number of momentary feeder section outages | Momentary interruptions due to feeder outages (MAIFI) | Momentary interruptions due to feeder outages (MAIFI) (after removing excluded events) | Momentary interruptions due to feeder section outages (MAIFI) | Monetary interruptions due to feeder section outages (MAIFI) (after removing excluded events) | Low Reliability Feeder (SAIDI) | Low Reliability Feeder (MAIFI)
AP001 | Citipower | Urban | 205 | 0 | 2.417 | 3.054 | 1.422 | 0.673 | 2 | 14702 | 14702 | 0.0004532 | 0.0004532 | 1 | 6960 | 5.0009e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP002 | Citipower | CBD | 20 | 0 | 1.917 | 6.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP003 | Citipower | Urban | 2686 | 2.11 | 2.594 | 5.103 | 2.232 | 1.026 | 6 | 180978 | 180978 | 0.010014 | 0.010014 | 7 | 83224 | 0.0011627 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP005 | Citipower | Urban | 2104 | 3.523 | 3.048 | 3.996 | 0.447 | 0.734 | 2 | 36220 | 35528 | 0.00050009 | 0.00049696 | 5 | 59559 | 0.00047821 | 1 | 0 | 0.0066105 | 0.0066105 | 0 | 0 | NO | NO
AP006 | Citipower | Urban | 666 | 0.745 | 1.865 | 4.155 | 0.344 | 1.277 | 2 | 8502 | 8502 | 0.00016565 | 0.00016565 | 3 | 31528 | 0.00020941 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP007 | Citipower | Urban | 1362 | 2.448 | 0.716 | 2.273 | 1.485 | 0.099 | 1 | 137020 | 137020 | 0.0041945 | 0.0041945 | 3 | 9130 | 0.00013752 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP008 | Citipower | Urban | 2631 | 4.299 | 1.582 | 5.362 | 0.556 | 0.321 | 7 | 42000 | 41843 | 0.00065949 | 0.00065636 | 6 | 24278 | 0.00032818 | 1 | 0 | 0.0081983 | 0.0081983 | 0 | 0 | NO | NO
AP009 | Citipower | Urban | 897 | 1.552 | 3.031 | 8.886 | 0.167 | 0.409 | 2 | 2592 | 2592 | 0.00010627 | 0.00010627 | 1 | 6365 | 5.9385e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP011 | Citipower | Urban | 279 | 0.459 | 2.744 | 5.362 | 0.075 | 0.439 | 0 | 599 | 599 | 6.2511e-06 | 6.2511e-06 | 1 | 3520 | 7.5013e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP012 | Citipower | Urban | 120 | 0.017 | 0.99 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP013 | Citipower | Urban | 432 | 0 | 2.736 | 2.583 | 0.014 | 0 | 0 | 366 | 366 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP014 | Citipower | Urban | 1865 | 3.176 | 1.88 | 4.962 | 0.275 | 0.028 | 2 | 15924 | 15924 | 0.00016878 | 0.00016878 | 2 | 1620 | 2.1879e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP015 | Citipower | Urban | 1366 | 3.219 | 1.052 | 2.889 | 3.149 | 0.019 | 1 | 229415 | 229415 | 0.0042757 | 0.0042757 | 2 | 1350 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP017 | Citipower | Urban | 1011 | 0.672 | 6.944 | 5.263 | 1.38 | 0 | 3 | 40850 | 40850 | 0.0025348 | 0.0025348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP018 | Citipower | Urban | 529 | 0.893 | 1.402 | 5.571 | 0.284 | 0 | 1 | 4153 | 4153 | 7.5013e-05 | 7.5013e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AP019 | Citipower | Urban | 878 | 1.075 | 1.802 | 4.343 | 0.152 | 0.724 | 1 | 4736 | 4736 | 0.00010002 | 0.00010002 | 2 | 22548 | 0.00017503 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR002 | Citipower | Urban | 496 | 0.329 | 1.504 | 4.387 | 2.409 | 0 | 4 | 41966 | 13979 | 0.0018066 | 0.00027192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR003 | Citipower | Urban | 1155 | 2.54 | 3.269 | 5.877 | 7.305 | 0.045 | 7 | 221151 | 155601 | 0.0074513 | 0.0038569 | 1 | 1368 | 0.00017816 | 2 | 0 | 0.0045633 | 0.0045633 | 0 | 0 | NO | NO
AR004 | Citipower | Urban | 2333 | 2.017 | 2.455 | 3.49 | 1.782 | 0.346 | 3 | 183489 | 50964 | 0.0078732 | 0.00060635 | 3 | 35662 | 0.00028755 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR005 | Citipower | Urban | 887 | 2.789 | 1.413 | 3.616 | 3.94 | 0 | 4 | 148897 | 98281 | 0.0057416 | 0.0029661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR006 | Citipower | Urban | 340 | 0.098 | 1.98 | 3.946 | 2.724 | 4.44 | 3 | 36157 | 17233 | 0.0021472 | 0.0011096 | 1 | 58930 | 0.00025942 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
AR007 | Citipower | Urban | 1656 | 3.126 | 0.588 | 3.901 | 1.889 | 0 | 6 | 123535 | 31708 | 0.0055728 | 0.00053759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR009 | Citipower | Urban | 1022 | 1.943 | 0.443 | 2.411 | 1.417 | 0.089 | 3 | 92515 | 34147 | 0.0039225 | 0.000722 | 1 | 5800 | 0.00036256 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR010 | Citipower | Urban | 2385 | 2.912 | 1.106 | 3.688 | 1.492 | 0.136 | 5 | 148596 | 13905 | 0.0075826 | 0.00019691 | 2 | 13554 | 0.0001719 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR011 | Citipower | Urban | 1341 | 2.937 | 1.111 | 4.452 | 1.798 | 0.279 | 4 | 83421 | 4989 | 0.0044383 | 0.00013752 | 1 | 12950 | 0.00011564 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR012 | Citipower | Urban | 492 | 1.185 | 0.335 | 4.877 | 3.57 | 0 | 2 | 55478 | 27092 | 0.0031224 | 0.0015659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
AR013 | Citipower | Urban | 384 | 0.602 | 0.661 | 2.232 | 1.139 | 0.386 | 2 | 30201 | 9111 | 0.0013471 | 0.00019066 | 1 | 10230 | 0.00010314 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B001 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B002 | Citipower | Urban | 226 | 0 | 2.03 | 2.451 | 0 | 0.156 | 0 | 0 | 0 | 0 | 0 | 1 | 2220 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B003 | Citipower | Urban | 251 | 0.103 | 1.411 | 2.163 | 0.014 | 0.907 | 0 | 250 | 250 | 3.1255e-06 | 3.1255e-06 | 4 | 16215 | 0.00021566 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B004 | Citipower | Urban | 1075 | 0.212 | 3.794 | 4.178 | 0.904 | 0.471 | 2 | 35820 | 35820 | 0.0033975 | 0.0033975 | 3 | 18670 | 0.00040007 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B011 | Citipower | Urban | 893 | 0.234 | 2.527 | 4.174 | 0.013 | 0.288 | 0 | 428 | 428 | 1.8753e-05 | 1.8753e-05 | 3 | 9506 | 0.00010002 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B012 | Citipower | Urban | 469 | 0.859 | 2.327 | 4.604 | 0.052 | 0.059 | 1 | 812 | 812 | 2.5004e-05 | 2.5004e-05 | 2 | 925 | 2.1879e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B014 | Citipower | Urban | 722 | 0.176 | 1.77 | 2.373 | 0.357 | 0.348 | 2 | 16730 | 16730 | 0.00032818 | 0.00032818 | 3 | 16320 | 0.00015003 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B015 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B016 | Citipower | Urban | 686 | 0 | 2.151 | 1.557 | 0.065 | 0.063 | 1 | 4396 | 4396 | 3.1255e-05 | 3.1255e-05 | 2 | 4265 | 5.3134e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B021 | Citipower | Urban | 891 | 0.001 | 2.099 | 2.88 | 0.9 | 0.492 | 2 | 42870 | 42870 | 0.0027692 | 0.0027692 | 2 | 23426 | 0.00018128 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B023 | Citipower | Urban | 700 | 0.493 | 1.531 | 4.389 | 0.014 | 0.212 | 0 | 336 | 336 | 6.2511e-06 | 6.2511e-06 | 1 | 5200 | 4.0632e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B024 | Citipower | Urban | 99 | 0 | 2.143 | 1.827 | 0.884 | 0 | 1 | 7384 | 7384 | 0.0003063 | 0.0003063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B025 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B026 | Citipower | Urban | 3 | 0 | 1.597 | 2.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
B027 | Citipower | Urban | 0 | 0 | 1.269 | 2.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BC006 | Citipower | Urban | 1267 | 0.007 | 2.108 | 2.445 | 1.843 | 0.066 | 5 | 147133 | 9111 | 0.0083514 | 0.00018753 | 1 | 5280 | 3.7506e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BC011 | Citipower | Urban | 264 | 0.224 | 0.401 | 2.612 | 1.782 | 0 | 2 | 27750 | 0 | 0.0016565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BC012 | Citipower | Urban | 1765 | 3.417 | 1.003 | 4.647 | 3.846 | 0.815 | 8 | 225023 | 39698 | 0.011911 | 0.00094079 | 2 | 47710 | 0.00034381 | 2 | 0 | 0.010902 | 0.010902 | 0 | 0 | NO | NO
BC013 | Citipower | Urban | 2098 | 1.492 | 2.382 | 2.946 | 4.007 | 0.111 | 6 | 439572 | 3897 | 0.013674 | 9.3766e-05 | 2 | 12220 | 0.0001219 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BC014 | Citipower | Urban | 445 | 0.762 | 0.594 | 2.669 | 2.266 | 0 | 3 | 58190 | 10945 | 0.0028724 | 7.5013e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BC015 | Citipower | Urban | 3079 | 2.93 | 1.514 | 3.255 | 2.537 | 0.894 | 6 | 369633 | 30780 | 0.020078 | 0.00052822 | 4 | 130285 | 0.00085015 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BC020 | Citipower | Urban | 1885 | 0.499 | 2.729 | 3.342 | 2.394 | 0.108 | 8 | 208016 | 6122 | 0.011974 | 0.00018128 | 3 | 9356 | 0.00019378 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BC022 | Citipower | Urban | 398 | 0.025 | 0.876 | 1.914 | 1.382 | 0 | 3 | 44271 | 1531 | 0.0025129 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BC023 | Citipower | Urban | 0 | 0 | 0.836 | 5.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BK002 | Citipower | Urban | 1462 | 2.592 | 1.833 | 2.455 | 0.109 | 0.205 | 4 | 10005 | 8967 | 0.00024067 | 0.00023129 | 2 | 18826 | 0.0002938 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BK003 | Citipower | Urban | 427 | 1.586 | 0.645 | 2.202 | 0.761 | 0 | 3 | 22734 | 22734 | 0.00087202 | 0.00087202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BK004 | Citipower | Urban | 1303 | 2.984 | 0.574 | 2.387 | 1.557 | 0.327 | 3 | 130954 | 130608 | 0.0046727 | 0.0046696 | 3 | 27500 | 0.00028755 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BK006 | Citipower | Urban | 129 | 0 | 0.716 | 0.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BK007 | Citipower | Urban | 1277 | 2.591 | 1.4 | 2.527 | 0.303 | 0.032 | 2 | 23611 | 23611 | 0.00055009 | 0.00055009 | 1 | 2470 | 3.1255e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BK009 | Citipower | Urban | 717 | 2.68 | 0.725 | 1.46 | 0.575 | 0.721 | 3 | 43524 | 28111 | 0.00054072 | 0.00040945 | 2 | 54573 | 0.00085015 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BK011 | Citipower | Urban | 1342 | 2.15 | 0.776 | 2.187 | 0.764 | 0.012 | 1 | 72215 | 72215 | 0.0041757 | 0.0041757 | 3 | 1171 | 5.0009e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ001 | Citipower | CBD | 97 | 0 | 0.075 | 0.365 | 0 | 0.088 | 0 | 0 | 0 | 0 | 0 | 2 | 3600 | 3.7506e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ002 | Citipower | CBD | 0 | 0 | 1.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ003 | Citipower | Urban | 846 | 0 | 5.494 | 2.514 | 0.033 | 0.035 | 2 | 1691 | 1691 | 2.1879e-05 | 2.1879e-05 | 1 | 1827 | 2.813e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ005 | Citipower | CBD | 0 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ007 | Citipower | Urban | 12 | 0 | 1.519 | 3.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ009 | Citipower | CBD | 202 | 0 | 1.904 | 5.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ012 | Citipower | CBD | 0 | 0 | 5.163 | 3.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ014 | Citipower | CBD | 22 | 0 | 1.133 | 1.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ015 | Citipower | Urban | 56 | 0 | 0.755 | 1.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ020 | Citipower | CBD | 80 | 0 | 0.089 | 0.3 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 1 | 375 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ024 | Citipower | CBD | 4 | 0 | 1.432 | 4.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ026 | Citipower | CBD | 1 | 0 | 2.093 | 4.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ028 | Citipower | Urban | 2015 | 0 | 5.638 | 3.125 | 0.002 | 0.096 | 0 | 155 | 155 | 3.1255e-06 | 3.1255e-06 | 2 | 9576 | 0.00017816 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ030 | Citipower | CBD | 302 | 0 | 1.477 | 3.522 | 0.045 | 0.048 | 1 | 590 | 590 | 3.1255e-05 | 3.1255e-05 | 1 | 628 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ032 | Citipower | CBD | 0 | 0 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ033 | Citipower | CBD | 395 | 0 | 1.632 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ041 | Citipower | Urban | 2351 | 0 | 5.234 | 4.527 | 0.03 | 0 | 2 | 2436 | 2436 | 4.6883e-05 | 4.6883e-05 | 0 | 0 | 0 | 1 | 0 | 0.0019972 | 0.0019972 | 0 | 0 | NO | NO
BQ043 | Citipower | CBD | 308 | 0 | 2.963 | 3.74 | 0 | 0.154 | 0 | 0 | 0 | 0 | 0 | 1 | 1960 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ047 | Citipower | CBD | 1172 | 0 | 3.481 | 3.966 | 0.012 | 0.631 | 1 | 549 | 549 | 1.2502e-05 | 1.2502e-05 | 1 | 28728 | 0.00026255 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ051 | Citipower | Urban | 2991 | 0 | 8.616 | 4.76 | 0.01 | 0.614 | 0 | 953 | 953 | 2.813e-05 | 2.813e-05 | 1 | 59400 | 0.00051571 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ052 | Citipower | CBD | 117 | 0 | 4.299 | 5.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ053 | Citipower | Urban | 877 | 0 | 4.567 | 4.045 | 0.054 | 0.002 | 1 | 1795 | 1795 | 6.2511e-05 | 6.2511e-05 | 1 | 72 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ056 | Citipower | CBD | 735 | 0 | 2.69 | 3.73 | 0.016 | 0 | 1 | 487 | 487 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ057 | Citipower | Urban | 424 | 0 | 1.702 | 1.583 | 0.005 | 0 | 0 | 224 | 224 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ061 | Citipower | CBD | 62 | 0 | 4.351 | 4.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BQ062 | Citipower | Urban | 100 | 0 | 4.379 | 4.33 | 3.095 | 0 | 1 | 11009 | 11009 | 0.00044695 | 0.00044695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BTS-RUS177 | Citipower | Urban | 1 | 4.281 | 0.745 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BTS-VP180 | Citipower | Urban | 2 | 0.921 | 7.213 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
BW005 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
C020 | Citipower | Urban | 780 | 4.516 | 1.021 | 0 | 0 | 0 | 0 | 320 | 320 | 3.1255e-06 | 3.1255e-06 | 1 | 13515 | 0.0001594 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
C021 | Citipower | Urban | 1 | 0 | 1.007 | 0.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
C022 | Citipower | Urban | 1375 | 3.463 | 0.914 | 2.559 | 6.96 | 0 | 3 | 576160 | 11090 | 0.004804 | 0.00016253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
C023 | Citipower | Urban | 1250 | 3.053 | 1.8 | 2.935 | 2.959 | 0.852 | 15 | 194139 | 76736 | 0.002391 | 0.001469 | 6 | 55880 | 0.00052196 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
C024 | Citipower | Urban | 0 | 1.803 | 1.63 | 1.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
C027 | Citipower | Urban | 98 | 0 | 0.959 | 1.269 | 0 | 0.019 | 0 | 0 | 0 | 0 | 0 | 1 | 225 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
C028 | Citipower | Urban | 1130 | 2.538 | 0.666 | 2.48 | 0.368 | 0.507 | 2 | 25859 | 8369 | 0.00037819 | 0.00020629 | 4 | 35571 | 0.00034381 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
C029 | Citipower | Urban | 907 | 0.851 | 0.785 | 2.904 | 1.657 | 0.794 | 5 | 79707 | 27171 | 0.00054697 | 0.00034068 | 2 | 38204 | 0.00031255 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CFD021 | Citipower | Urban | 105 | 0 | 0.004 | 0 | 0 | 0 | 0 | 350 | 350 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CFD022 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CFD023 | Citipower | Urban | 368 | 0.889 | 0.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.0011408 | 0.0011408 | 0 | 0 | NO | NO
CL011 | Citipower | Urban | 1166 | 8.305 | 0.883 | 0 | 0 | 0 | 0 | 1002 | 1002 | 9.3766e-06 | 9.3766e-06 | 3 | 36630 | 0.00028442 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL013 | Citipower | Urban | 518 | 1.031 | 3.785 | 3.375 | 0.235 | 2.951 | 2 | 5564 | 5564 | 0.00010627 | 0.00010627 | 6 | 69772 | 0.0005626 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL014 | Citipower | Urban | 416 | 0 | 1.908 | 3.404 | 0.03 | 0.011 | 0 | 559 | 559 | 3.1255e-06 | 3.1255e-06 | 1 | 200 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL016 | Citipower | Urban | 284 | 0.325 | 2.955 | 4.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL021 | Citipower | Urban | 1091 | 1.016 | 1.953 | 4.547 | 0.19 | 0 | 3 | 7008 | 7008 | 0.00016878 | 0.00016878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL022 | Citipower | Urban | 1090 | 3.629 | 0.647 | 4.775 | 1.088 | 1.981 | 4 | 38266 | 27766 | 0.00061261 | 0.00054697 | 7 | 69662 | 0.00069699 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL023 | Citipower | Urban | 1288 | 2.796 | 2.521 | 4.795 | 2.311 | 0.788 | 4 | 95629 | 95629 | 0.002713 | 0.002713 | 4 | 32590 | 0.00032506 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL026 | Citipower | Urban | 581 | 0.312 | 1.155 | 4.387 | 1.295 | 1.095 | 3 | 26418 | 26418 | 0.00039069 | 0.00039069 | 2 | 22344 | 0.00022504 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL027 | Citipower | Urban | 188 | 0 | 1.499 | 2.261 | 0.258 | 0 | 4 | 3303 | 3303 | 0.00022816 | 0.00022816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL028 | Citipower | Urban | 118 | 0 | 3.994 | 3.022 | 0.115 | 0 | 1 | 690 | 690 | 3.1255e-05 | 3.1255e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL033 | Citipower | Urban | 1758 | 1.758 | 1.324 | 3.628 | 2.649 | 0 | 6 | 197735 | 197735 | 0.0065011 | 0.0065011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL034 | Citipower | Urban | 506 | 0 | 0 | 0 | 0 | 0 | 0 | 1158 | 1158 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL035 | Citipower | Urban | 240 | 0.282 | 1.188 | 3.705 | 0 | 0.025 | 0 | 0 | 0 | 0 | 0 | 1 | 251 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL036 | Citipower | Urban | 1550 | 4.514 | 4.084 | 5.162 | 19.425 | 0.265 | 3 | 898507 | 85574 | 0.014937 | 0.0098142 | 2 | 12266 | 8.7515e-05 | 1 | 0 | 0.005079 | 0.005079 | 0 | 0 | YES | NO
CL037 | Citipower | Urban | 1491 | 1.953 | 2.422 | 3.661 | 0.058 | 0.894 | 1 | 3612 | 3612 | 5.626e-05 | 5.626e-05 | 4 | 56111 | 0.00048133 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CL038 | Citipower | Urban | 1282 | 2.52 | 5.252 | 7.214 | 6.121 | 0.199 | 9 | 167545 | 167545 | 0.0046102 | 0.0046102 | 5 | 5440 | 0.00021879 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW004 | Citipower | Urban | 588 | 0 | 1.413 | 1.8 | 0.001 | 0.259 | 0 | 59 | 59 | 3.1255e-06 | 3.1255e-06 | 4 | 13015 | 0.00020629 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW005 | Citipower | Urban | 1502 | 0.267 | 2.757 | 4.307 | 0.983 | 0.694 | 3 | 52830 | 52830 | 0.0048321 | 0.0048321 | 5 | 37289 | 0.00035319 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW006 | Citipower | Urban | 304 | 0 | 2.233 | 1.86 | 0.404 | 0.371 | 3 | 10159 | 10159 | 0.00019378 | 0.00019378 | 2 | 9332 | 0.00010002 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW007 | Citipower | Urban | 624 | 0.767 | 2.158 | 4.4 | 0.003 | 0.002 | 0 | 65 | 65 | 3.1255e-06 | 3.1255e-06 | 1 | 45 | 2.813e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW008 | Citipower | Urban | 360 | 0.268 | 0.735 | 1.551 | 0.012 | 0.27 | 0 | 443 | 443 | 6.2511e-06 | 6.2511e-06 | 2 | 9645 | 7.5013e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW009 | Citipower | Urban | 1179 | 1.92 | 5.023 | 4.697 | 1.308 | 2.34 | 2 | 50584 | 3064 | 0.00037506 | 3.7506e-05 | 7 | 90461 | 0.00081577 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW011 | Citipower | Urban | 1243 | 0.004 | 3.498 | 2.473 | 0.497 | 0.35 | 1 | 38484 | 38484 | 0.0038975 | 0.0038975 | 2 | 27130 | 0.00019378 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW012 | Citipower | Urban | 716 | 0 | 3.041 | 3.383 | 0.566 | 0.697 | 1 | 18443 | 18443 | 0.002266 | 0.002266 | 7 | 22710 | 0.00021879 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW013 | Citipower | Urban | 826 | 0.421 | 1.79 | 3.945 | 0.653 | 0.546 | 5 | 21076 | 7573 | 0.00024692 | 0.00018128 | 4 | 17615 | 0.00020629 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW014 | Citipower | Urban | 1536 | 0.177 | 3.255 | 2.359 | 0.066 | 0.09 | 2 | 6636 | 6636 | 0.00013752 | 0.00013752 | 2 | 9040 | 7.8138e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
CW015 | Citipower | Urban | 903 | 0 | 3.19 | 4.049 | 0.038 | 0.339 | 0 | 1314 | 1314 | 9.3766e-06 | 9.3766e-06 | 5 | 11665 | 0.00017503 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA004 | Citipower | Urban | 11 | 0.943 | 3.761 | 2.117 | 0 | 0.081 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA006 | Citipower | Urban | 304 | 0 | 3.027 | 1.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA007 | Citipower | Urban | 711 | 0 | 2.98 | 3.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA008 | Citipower | Urban | 1167 | 0 | 8.767 | 3.332 | 0.007 | 0 | 1 | 351 | 0 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA009 | Citipower | Urban | 59 | 0 | 2.558 | 3.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA013 | Citipower | Urban | 4 | 0 | 1.663 | 0.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA015 | Citipower | Urban | 2 | 0 | 4.374 | 2.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA016 | Citipower | Urban | 35 | 0 | 5.812 | 3.526 | 0 | 4.591 | 0 | 0 | 0 | 0 | 0 | 1 | 7020 | 4.0632e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA020 | Citipower | Urban | 91 | 0 | 5.552 | 2.987 | 0.363 | 0.985 | 1 | 1702 | 1702 | 0.00014377 | 0.00014377 | 1 | 4620 | 6.8762e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA021 | Citipower | Urban | 45 | 0 | 4.317 | 3.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA022 | Citipower | Urban | 447 | 0.003 | 3.161 | 2.767 | 0.006 | 0 | 0 | 145 | 145 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA026 | Citipower | Urban | 75 | 0 | 4.373 | 3.647 | 0 | 0.087 | 0 | 0 | 0 | 0 | 0 | 1 | 275 | 7.8138e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA027 | Citipower | Urban | 1 | 0 | 1.652 | 2.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA028 | Citipower | Urban | 35 | 0 | 5.305 | 1.675 | 0 | 0.089 | 0 | 0 | 0 | 0 | 0 | 1 | 285 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA029 | Citipower | Urban | 191 | 0 | 3.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DA030 | Citipower | Urban | 63 | 0 | 3.197 | 3.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DLF002 | Citipower | CBD | 13 | 0 | 6.075 | 6.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DLF003 | Citipower | Urban | 1 | 0 | 4.695 | 2.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DLF005 | Citipower | CBD | 0 | 0 | 0 | 3.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
DLF063 | Citipower | CBD | 22 | 0 | 5.287 | 2.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E021 | Citipower | Urban | 5 | 0 | 0.815 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E022 | Citipower | Urban | 0 | 0.341 | 0.597 | 0.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E023 | Citipower | Urban | 0 | 0 | 0.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E024 | Citipower | Urban | 1 | 0 | 0.485 | 2.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E027 | Citipower | Urban | 1 | 0 | 0.949 | 0.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E029 | Citipower | Urban | 9 | 0 | 1.291 | 1.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E032 | Citipower | Urban | 8 | 0.421 | 2.573 | 0.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E033 | Citipower | Urban | 50 | 0.447 | 0.728 | 1.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
E035 | Citipower | Urban | 0 | 0.09 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
EL005 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
EL009 | Citipower | Urban | 73 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
EL011 | Citipower | Urban | 967 | 1.375 | 0.239 | 0 | 0 | 0 | 0 | 226 | 226 | 3.1255e-06 | 3.1255e-06 | 1 | 7371 | 0.0001219 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
EW001 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
EW009 | Citipower | Urban | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
EW012 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F026 | Citipower | Urban | 436 | 0.154 | 1.707 | 1.187 | 0.002 | 0 | 0 | 93 | 93 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F027 | Citipower | Urban | 1147 | 0 | 3.89 | 1.818 | 0.971 | 0.14 | 8 | 94375 | 94375 | 0.00075013 | 0.00075013 | 2 | 13610 | 0.00020629 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F028 | Citipower | Urban | 1210 | 1.872 | 0.921 | 1.866 | 0.353 | 0 | 1 | 35233 | 796 | 0.00014065 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F029 | Citipower | Urban | 557 | 2.097 | 0.467 | 0.863 | 0.03 | 0.007 | 1 | 2995 | 2995 | 1.5628e-05 | 1.5628e-05 | 1 | 650 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F030 | Citipower | Urban | 1 | 0 | 0.619 | 0.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F032 | Citipower | Urban | 377 | 1.509 | 0.173 | 0.72 | 0.001 | 0.393 | 0 | 82 | 82 | 3.1255e-06 | 3.1255e-06 | 3 | 31714 | 0.00029693 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F033 | Citipower | Urban | 1306 | 0.324 | 3.97 | 2.419 | 0.053 | 0 | 1 | 4384 | 4384 | 0.00015628 | 0.00015628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F034 | Citipower | Urban | 1224 | 1.128 | 1.742 | 1.62 | 0.042 | 0.735 | 2 | 4922 | 4922 | 0.00019066 | 0.00019066 | 7 | 85505 | 0.00086577 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F035 | Citipower | Urban | 569 | 0.908 | 2.533 | 1.477 | 0.051 | 0.017 | 1 | 3040 | 385 | 3.4381e-05 | 6.2511e-06 | 1 | 990 | 2.813e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
F037 | Citipower | Urban | 1396 | 1.566 | 1.012 | 2.656 | 0.242 | 0.282 | 4 | 19562 | 19448 | 0.00042507 | 0.00042195 | 3 | 22810 | 0.00020941 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB001 | Citipower | CBD | 2 | 0 | 0.156 | 2.542 | 0.033 | 0 | 1 | 4 | 4 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB002 | Citipower | Urban | 3 | 0 | 0.85 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB004 | Citipower | Urban | 1 | 0.017 | 1.179 | 2.178 | 2.927 | 0 | 2 | 207 | 207 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB005 | Citipower | Urban | 80 | 0 | 1.973 | 2.004 | 0.026 | 0.073 | 1 | 158 | 158 | 0.00024692 | 0.00024692 | 1 | 450 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB006 | Citipower | Urban | 1 | 0 | 0.293 | 2.36 | 0.031 | 0 | 1 | 2 | 2 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB009 | Citipower | Urban | 1 | 0 | 0.177 | 2.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB010 | Citipower | CBD | 2 | 0 | 0.636 | 1.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB011 | Citipower | Urban | 55 | 0 | 2.023 | 1.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB013 | Citipower | CBD | 0 | 0 | 0.901 | 0.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB014 | Citipower | Urban | 41 | 0.119 | 2.549 | 1.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB015 | Citipower | CBD | 1 | 0.914 | 0.401 | 3.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB018 | Citipower | CBD | 0 | 0 | 0.926 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB019 | Citipower | CBD | 2 | 0 | 1.036 | 0.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB020 | Citipower | Urban | 58 | 1.101 | 4.148 | 3.923 | 0.105 | 0 | 0 | 240 | 240 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB022 | Citipower | Urban | 0 | 0.003 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FB023 | Citipower | Urban | 110 | 2.304 | 4.725 | 5.644 | 3.929 | 0.49 | 1 | 11796 | 11796 | 0.00033131 | 0.00033131 | 1 | 1470 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FF084 | Citipower | Urban | 2007 | 5.119 | 0.172 | 2.504 | 0.167 | 0.323 | 5 | 20571 | 20330 | 0.00040945 | 0.00040632 | 5 | 39831 | 0.0005626 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FF085 | Citipower | Urban | 93 | 1.563 | 0.392 | 1.257 | 0 | 0.065 | 0 | 0 | 0 | 0 | 0 | 2 | 745 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FF086 | Citipower | Urban | 237 | 3.143 | 0.845 | 1.715 | 1.46 | 0.3 | 2 | 31089 | 31089 | 0.0010814 | 0.0010814 | 4 | 6392 | 0.0001719 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FF091 | Citipower | Urban | 79 | 3.74 | 0.915 | 0.8 | 0.197 | 0 | 1 | 2997 | 2997 | 0.00025317 | 0.00025317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FF092 | Citipower | Urban | 100 | 1.168 | 0.286 | 1.543 | 2.412 | 1.072 | 2 | 24078 | 24078 | 0.00034693 | 0.00034693 | 1 | 10700 | 6.2511e-05 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
FF097 | Citipower | Urban | 778 | 5.152 | 0.551 | 2.286 | 0.24 | 0.343 | 2 | 12589 | 12589 | 0.00023442 | 0.00023442 | 3 | 17993 | 0.0001594 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR001 | Citipower | CBD | 351 | 0 | 1.185 | 3.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.0010814 | 0.0010814 | 0 | 0 | NO | NO
FR002 | Citipower | CBD | 0 | 0 | 2.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR003 | Citipower | CBD | 29 | 0 | 0.774 | 2.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 9.0641e-05 | 9.0641e-05 | 0 | 0 | NO | NO
FR004 | Citipower | CBD | 299 | 0 | 0.775 | 3.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.00093454 | 0.00093454 | 0 | 0 | NO | NO
FR005 | Citipower | CBD | 6 | 0 | 0.358 | 4.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | NO | NO
FR006 | Citipower | CBD | 6 | 0 | 0.709 | 2.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | NO | NO
FR007 | Citipower | CBD | 153 | 0 | 1.075 | 4.319 | 0 | 0.454 | 0 | 0 | 0 | 0 | 0 | 1 | 2475 | 4.6883e-05 | 1 | 0 | 0.00047821 | 0.00047821 | 0 | 0 | NO | NO
FR008 | Citipower | CBD | 37 | 0 | 3.576 | 2.21 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 645 | 3.1255e-06 | 1 | 0 | 0.00011564 | 0.00011564 | 0 | 0 | NO | NO
FR009 | Citipower | CBD | 4 | 0 | 0.541 | 0.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | NO | NO
FR013 | Citipower | CBD | 25 | 0 | 1.128 | 0.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR014 | Citipower | CBD | 766 | 0 | 4.082 | 3.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR015 | Citipower | CBD | 69 | 0 | 0.868 | 2.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR016 | Citipower | CBD | 296 | 0 | 7.068 | 3.274 | 0.668 | 0 | 1 | 9300 | 9300 | 0.0001594 | 0.0001594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR018 | Citipower | CBD | 109 | 0 | 0.721 | 3.121 | 0.6 | 0.418 | 1 | 3228 | 3228 | 3.7506e-05 | 3.7506e-05 | 2 | 2250 | 3.1255e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR019 | Citipower | CBD | 82 | 0 | 1.187 | 3.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR020 | Citipower | CBD | 799 | 0 | 1.535 | 2.772 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 1 | 704 | 5.0009e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR021 | Citipower | CBD | 0 | 0 | 0.394 | 1.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR024 | Citipower | CBD | 263 | 0 | 1.585 | 3.234 | 0.273 | 0 | 7 | 3416 | 3416 | 0.00015315 | 0.00015315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR026 | Citipower | CBD | 113 | 0 | 0.701 | 1.776 | 0.886 | 0 | 1 | 8682 | 8682 | 0.00042195 | 0.00042195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
FR027 | Citipower | CBD | 554 | 0 | 1.158 | 3.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR028 | Citipower | CBD | 149 | 0 | 1.218 | 2.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR029 | Citipower | CBD | 22 | 0 | 0.671 | 3.892 | 0 | 0.534 | 0 | 0 | 0 | 0 | 0 | 2 | 465 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR030 | Citipower | CBD | 37 | 0 | 1.017 | 2.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR031 | Citipower | CBD | 669 | 0 | 5.913 | 4.91 | 0.004 | 0 | 0 | 89 | 89 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FR032 | Citipower | CBD | 13 | 0 | 1.876 | 4.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FT009 | Citipower | Urban | 184 | 0 | 0.056 | 0 | 0 | 0 | 1 | 1430 | 1430 | 3.4381e-05 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
FT013 | Citipower | Urban | 221 | 0.325 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J047 | Citipower | CBD | 74 | 0 | 1.821 | 1.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J048 | Citipower | CBD | 38 | 0 | 3.236 | 2.126 | 4.762 | 0 | 1 | 13112 | 13112 | 3.4381e-05 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J052 | Citipower | CBD | 127 | 0 | 1.186 | 1.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J055 | Citipower | CBD | 37 | 0 | 1.328 | 1.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J057 | Citipower | CBD | 326 | 0 | 2.175 | 1.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J059 | Citipower | CBD | 89 | 0 | 2.581 | 2.068 | 0.537 | 0 | 1 | 3560 | 3560 | 0.00027817 | 0.00027817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J062 | Citipower | CBD | 56 | 0 | 1.745 | 2.665 | 0.816 | 0 | 1 | 2640 | 2640 | 0.0001719 | 0.0001719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J063 | Citipower | CBD | 131 | 0 | 1.017 | 1.289 | 0.476 | 0 | 1 | 7448 | 7448 | 0.0004157 | 0.0004157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J064 | Citipower | CBD | 0 | 0 | 0.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J067 | Citipower | CBD | 3 | 0 | 0.489 | 0 | 0 | 0 | 1 | 330 | 330 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
J068 | Citipower | CBD | 129 | 0 | 0.999 | 0.726 | 0.255 | 0 | 1 | 6985 | 6985 | 0.00039694 | 0.00039694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
J070 | Citipower | CBD | 82 | 0 | 0 | 2.354 | 0.457 | 0 | 1 | 2452 | 2452 | 0.00051259 | 0.00051259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA001 | Citipower | CBD | 303 | 0 | 5.174 | 6.931 | 0 | 0.076 | 0 | 0 | 0 | 0 | 0 | 3 | 515 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA002 | Citipower | CBD | 67 | 0 | 3.117 | 6.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA003 | Citipower | CBD | 2 | 0 | 0.323 | 0.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA005 | Citipower | CBD | 264 | 0 | 5.493 | 6.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA006 | Citipower | CBD | 379 | 0 | 1.749 | 2.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA009 | Citipower | CBD | 482 | 0 | 2.983 | 6.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA010 | Citipower | CBD | 1 | 0 | 1.329 | 4.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA011 | Citipower | CBD | 418 | 0 | 4.824 | 7.738 | 1.885 | 0 | 1 | 15689 | 15689 | 0.0013065 | 0.0013065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA013 | Citipower | CBD | 6 | 0 | 1.472 | 7.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA014 | Citipower | CBD | 1 | 0 | 1.323 | 0.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA017 | Citipower | CBD | 65 | 0 | 2.616 | 3.798 | 0.988 | 0 | 1 | 2604 | 2604 | 0.00019378 | 0.00019378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA018 | Citipower | CBD | 305 | 0 | 2.413 | 4.636 | 0 | 0.553 | 0 | 0 | 0 | 0 | 0 | 1 | 5600 | 4.3758e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA019 | Citipower | CBD | 795 | 0 | 2.224 | 5.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA021 | Citipower | CBD | 88 | 0 | 0.904 | 2.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA022 | Citipower | CBD | 59 | 0 | 1.426 | 2.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA025 | Citipower | CBD | 619 | 0 | 3.877 | 3.1 | 1.943 | 0.116 | 1 | 59754 | 59754 | 0.001966 | 0.001966 | 1 | 3568 | 5.0009e-05 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
JA026 | Citipower | CBD | 195 | 0 | 5.2 | 7.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA027 | Citipower | CBD | 132 | 0 | 1.357 | 2.803 | 0 | 2.329 | 0 | 0 | 0 | 0 | 0 | 1 | 16898 | 0.00010627 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA029 | Citipower | CBD | 359 | 0 | 3.621 | 5.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA030 | Citipower | CBD | 0 | 0 | 1.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA033 | Citipower | CBD | 185 | 0 | 4.272 | 4.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA034 | Citipower | CBD | 543 | 0 | 2.356 | 2.497 | 0.001 | 0 | 0 | 37 | 37 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA035 | Citipower | CBD | 698 | 0 | 6.064 | 7.003 | 0.004 | 0 | 0 | 67 | 67 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA037 | Citipower | CBD | 540 | 0 | 5.85 | 5.794 | 1.481 | 0 | 1 | 21256 | 21256 | 0.0018628 | 0.0018628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA038 | Citipower | CBD | 19 | 0 | 1.403 | 3.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA041 | Citipower | CBD | 124 | 0.079 | 2.773 | 0.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA042 | Citipower | CBD | 1005 | 0 | 6.709 | 6.091 | 0.003 | 0 | 0 | 75 | 75 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA043 | Citipower | CBD | 41 | 0 | 0.997 | 3.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA045 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
JA046 | Citipower | CBD | 107 | 0 | 3.235 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
K003 | Citipower | Urban | 125 | 0 | 1.022 | 0 | 0 | 0 | 0 | 298 | 298 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
K004 | Citipower | Urban | 397 | 0.303 | 0 | 3.02 | 0.688 | 0 | 1 | 13938 | 13938 | 0.00021566 | 0.00021566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
K005 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
K007 | Citipower | Urban | 12 | 0.063 | 0 | 3.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3.7506e-05 | 3.7506e-05 | 0 | 0 | NO | NO
K008 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
K011 | Citipower | Urban | 544 | 2.127 | 0.884 | 5.501 | 6.812 | 0 | 6 | 103771 | 103771 | 0.0027036 | 0.0027036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
K012 | Citipower | Urban | 0 | 0 | 0.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L001 | Citipower | Urban | 1194 | 5.226 | 1.424 | 3.762 | 3.349 | 0.028 | 4 | 163742 | 105312 | 0.0071387 | 0.0033818 | 1 | 1350 | 2.813e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L002 | Citipower | Urban | 1852 | 4.701 | 1.917 | 4.394 | 0.415 | 0.216 | 6 | 26959 | 26959 | 0.00067199 | 0.00067199 | 2 | 14055 | 0.00014065 | 1 | 0 | 0.0058229 | 0 | 0 | 0 | NO | NO
L004 | Citipower | Urban | 1329 | 3.841 | 1.146 | 5.286 | 0.927 | 1.566 | 4 | 35922 | 35922 | 0.0012908 | 0.0012908 | 3 | 60651 | 0.00045633 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L005 | Citipower | Urban | 1330 | 5.186 | 1.218 | 4.657 | 0.86 | 0.6 | 3 | 37817 | 37817 | 0.004407 | 0.004407 | 5 | 26415 | 0.00027192 | 1 | 0 | 0.0041632 | 0.0041632 | 0 | 0 | NO | NO
L006 | Citipower | Urban | 434 | 0.069 | 1.307 | 2.03 | 0.005 | 0.126 | 0 | 154 | 154 | 3.1255e-06 | 3.1255e-06 | 1 | 4140 | 3.7506e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L009 | Citipower | Urban | 1007 | 2.759 | 0.308 | 2.763 | 0.182 | 0.002 | 4 | 10219 | 8438 | 0.00071575 | 0.00067512 | 1 | 140 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L010 | Citipower | Urban | 675 | 3.296 | 1.543 | 0.549 | 0.65 | 0.094 | 4 | 122956 | 122956 | 0.0067355 | 0.0067355 | 6 | 17785 | 0.00037506 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L013 | Citipower | Urban | 801 | 1.963 | 0.704 | 4.848 | 0.048 | 6.2 | 1 | 1223 | 1223 | 1.8753e-05 | 1.8753e-05 | 7 | 157822 | 0.0013096 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L014 | Citipower | Urban | 648 | 0.656 | 3.296 | 3.358 | 0.259 | 0 | 2 | 7691 | 1387 | 8.439e-05 | 5.9385e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L015 | Citipower | Urban | 134 | 1.154 | 0.632 | 0.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L018 | Citipower | Urban | 1771 | 5.972 | 0.659 | 4.802 | 0.774 | 0.144 | 3 | 43957 | 4528 | 0.00021566 | 9.3766e-05 | 2 | 8184 | 0.00020629 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L019 | Citipower | Urban | 1912 | 3.145 | 3.337 | 4.628 | 1.676 | 0 | 3 | 106673 | 106673 | 0.0064886 | 0.0064886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L020 | Citipower | Urban | 951 | 1.263 | 2.326 | 4.456 | 0.208 | 0 | 2 | 6835 | 435 | 0.00011564 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L022 | Citipower | Urban | 98 | 0.33 | 0.045 | 0.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
L023 | Citipower | Urban | 1 | 0 | 0.119 | 0.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ001 | Citipower | CBD | 26 | 0 | 0.623 | 3.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ002 | Citipower | CBD | 367 | 0 | 1.521 | 2.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ003 | Citipower | CBD | 280 | 0 | 1.452 | 3.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ004 | Citipower | CBD | 206 | 0 | 1.826 | 3.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ007 | Citipower | CBD | 5 | 0 | 0.32 | 2.343 | 0 | 3.991 | 0 | 0 | 0 | 0 | 0 | 2 | 1312 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
LQ008 | Citipower | CBD | 1 | 0 | 0.282 | 0.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ009 | Citipower | CBD | 140 | 0 | 0.865 | 1.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ010 | Citipower | CBD | 35 | 0 | 0.566 | 1.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ011 | Citipower | CBD | 61 | 0 | 1.772 | 4.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ012 | Citipower | CBD | 92 | 0 | 1.269 | 4.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ014 | Citipower | CBD | 273 | 0 | 2.149 | 4.237 | 0.011 | 1.844 | 0 | 110 | 110 | 6.2511e-06 | 6.2511e-06 | 2 | 18305 | 0.00024379 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ015 | Citipower | CBD | 220 | 0 | 2.234 | 5.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ016 | Citipower | CBD | 57 | 0 | 1.026 | 2.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ017 | Citipower | CBD | 432 | 0 | 3.286 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ021 | Citipower | CBD | 114 | 0 | 2.013 | 3.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ022 | Citipower | CBD | 43 | 0 | 0.901 | 4.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ023 | Citipower | CBD | 233 | 0 | 1.509 | 3.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ024 | Citipower | CBD | 235 | 0 | 1.968 | 4.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ027 | Citipower | CBD | 37 | 0 | 0.297 | 0.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ028 | Citipower | CBD | 246 | 0 | 1.834 | 4.73 | 0.158 | 1.676 | 1 | 1265 | 1265 | 1.8753e-05 | 1.8753e-05 | 2 | 13425 | 0.0001719 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ029 | Citipower | CBD | 61 | 0 | 0.795 | 3.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ030 | Citipower | CBD | 129 | 0 | 1.202 | 2.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ031 | Citipower | CBD | 0 | 0 | 0.559 | 2.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ033 | Citipower | CBD | 53 | 0 | 0.723 | 1.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ034 | Citipower | CBD | 92 | 0 | 3.568 | 6.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ035 | Citipower | CBD | 12 | 0 | 0.326 | 2.013 | 0 | 1.285 | 0 | 0 | 0 | 0 | 0 | 2 | 1180 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ036 | Citipower | CBD | 0 | 0 | 0.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ040 | Citipower | CBD | 126 | 0 | 0.952 | 4.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ041 | Citipower | CBD | 224 | 0 | 1.375 | 2.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ042 | Citipower | CBD | 63 | 0 | 1.306 | 2.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ043 | Citipower | CBD | 55 | 0 | 1.329 | 1.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ045 | Citipower | CBD | 3 | 0 | 0.272 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ046 | Citipower | CBD | 45 | 0 | 1.384 | 5.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ047 | Citipower | CBD | 150 | 0 | 0.978 | 3.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ048 | Citipower | CBD | 103 | 0 | 1.951 | 2.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ049 | Citipower | CBD | 119 | 0 | 1.868 | 4.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ050 | Citipower | CBD | 56 | 0 | 1.321 | 3.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ052 | Citipower | CBD | 95 | 0 | 1.829 | 2.774 | 0.03 | 0 | 0 | 157 | 157 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ054 | Citipower | CBD | 167 | 0 | 1.607 | 3.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ055 | Citipower | CBD | 285 | 0 | 2.509 | 5.728 | 2.013 | 0 | 1 | 15429 | 15429 | 0.00078451 | 0.00078451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LQ056 | Citipower | CBD | 65 | 0 | 1.722 | 3.722 | 1.516 | 0 | 1 | 4080 | 4080 | 0.00020316 | 0.00020316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS003 | Citipower | Urban | 137 | 0 | 5.553 | 3.606 | 0.107 | 0 | 0 | 627 | 627 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS004 | Citipower | Urban | 86 | 0 | 0.973 | 1.376 | 0.035 | 0 | 1 | 333 | 333 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS005 | Citipower | Urban | 39 | 0 | 2.025 | 0.963 | 0.02 | 0 | 1 | 125 | 125 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS006 | Citipower | Urban | 2271 | 0 | 3.44 | 2.349 | 1.006 | 0.073 | 3 | 149734 | 149734 | 0.0074513 | 0.0074513 | 4 | 10891 | 0.00012502 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS007 | Citipower | Urban | 8 | 0.009 | 1.051 | 0.514 | 0.185 | 0.179 | 1 | 444 | 444 | 3.1255e-06 | 3.1255e-06 | 1 | 430 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS009 | Citipower | Urban | 414 | 0 | 2.437 | 1.53 | 0.002 | 0.002 | 0 | 100 | 100 | 3.1255e-06 | 3.1255e-06 | 1 | 85 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS010 | Citipower | Urban | 94 | 0 | 0.017 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS012 | Citipower | Urban | 1104 | 0 | 9.617 | 2.191 | 0.609 | 0.304 | 2 | 47279 | 47279 | 0.0034756 | 0.0034756 | 4 | 23568 | 0.0010002 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS016 | Citipower | CBD | 409 | 0 | 2.203 | 1.86 | 0.004 | 0.129 | 0 | 130 | 130 | 3.1255e-06 | 3.1255e-06 | 1 | 4371 | 8.1264e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS017 | Citipower | Urban | 56 | 0 | 0.03 | 0.17 | 0.006 | 0 | 0 | 311 | 311 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS019 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS020 | Citipower | Urban | 268 | 0 | 3.55 | 1.413 | 0.002 | 0.063 | 0 | 57 | 57 | 3.1255e-06 | 3.1255e-06 | 1 | 1826 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS021 | Citipower | Urban | 0 | 0 | 0.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS023 | Citipower | Urban | 33 | 0 | 4.842 | 2.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS024 | Citipower | Urban | 88 | 0 | 1.7 | 1.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS025 | Citipower | CBD | 209 | 0 | 1.612 | 2.497 | 0.821 | 0.924 | 2 | 10586 | 10586 | 0.00083139 | 0.00083139 | 3 | 11916 | 0.00031568 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
LS026 | Citipower | Urban | 0 | 0 | 2.043 | 2.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
LS027 | Citipower | Urban | 309 | 0 | 4.702 | 3.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG001 | Citipower | Urban | 1225 | 2.105 | 1.738 | 4.13 | 0.253 | 0.002 | 2 | 11561 | 11561 | 0.00011252 | 0.00011252 | 1 | 90 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG002 | Citipower | CBD | 6 | 0 | 7.835 | 1.985 | 0.238 | 0 | 1 | 111 | 111 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG004 | Citipower | CBD | 693 | 0.485 | 4.101 | 3.068 | 0.012 | 0 | 0 | 401 | 401 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG005 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG006 | Citipower | Urban | 1404 | 1.509 | 4.299 | 3.738 | 0.344 | 0 | 2 | 19912 | 19912 | 0.0002938 | 0.0002938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG009 | Citipower | Urban | 501 | 1.388 | 2.159 | 2.894 | 1.365 | 0.005 | 1 | 36403 | 36403 | 0.001569 | 0.001569 | 1 | 135 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG010 | Citipower | CBD | 2 | 0 | 0.159 | 0.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG013 | Citipower | Urban | 5 | 0 | 1.711 | 2.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG014 | Citipower | Urban | 899 | 4.707 | 1.145 | 3.761 | 2.701 | 0.002 | 3 | 99450 | 99450 | 0.0030193 | 0.0030193 | 1 | 90 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG015 | Citipower | CBD | 7 | 0.194 | 3.394 | 0.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG018 | Citipower | Urban | 94 | 0.129 | 3.55 | 2.625 | 0.159 | 0 | 0 | 875 | 875 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG019 | Citipower | Urban | 913 | 0.222 | 5.083 | 5.726 | 0.008 | 0 | 1 | 206 | 206 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG020 | Citipower | CBD | 11 | 0 | 3.502 | 6.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG022 | Citipower | Urban | 52 | 1.117 | 1.11 | 2.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG023 | Citipower | CBD | 54 | 0 | 8.182 | 1.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MG024 | Citipower | Urban | 60 | 0 | 2.817 | 1.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP001 | Citipower | CBD | 186 | 0 | 2.607 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP003 | Citipower | CBD | 27 | 0 | 0.689 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP005 | Citipower | CBD | 445 | 0 | 3.49 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP006 | Citipower | CBD | 4 | 0 | 2.29 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP007 | Citipower | CBD | 2 | 0 | 0.675 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP008 | Citipower | CBD | 117 | 0 | 1.631 | 3.5 | 0 | 0.722 | 0 | 0 | 0 | 0 | 0 | 1 | 3720 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP009 | Citipower | CBD | 61 | 0 | 1.072 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP015 | Citipower | CBD | 113 | 0 | 4.109 | 3.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP016 | Citipower | CBD | 355 | 0 | 1.971 | 1.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP017 | Citipower | CBD | 36 | 0 | 2.054 | 3.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP018 | Citipower | CBD | 46 | 0 | 0.598 | 2.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP020 | Citipower | CBD | 136 | 0 | 0.817 | 4.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP021 | Citipower | CBD | 955 | 0 | 7.428 | 4.394 | 0.001 | 0 | 0 | 35 | 35 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP024 | Citipower | CBD | 0 | 0 | 2.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP026 | Citipower | CBD | 270 | 0 | 2.38 | 4.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP028 | Citipower | CBD | 0 | 0 | 0.661 | 3.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP029 | Citipower | CBD | 60 | 0 | 0.899 | 3.439 | 0.053 | 0 | 0 | 143 | 143 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP030 | Citipower | CBD | 1620 | 0 | 9.621 | 4.513 | 0.004 | 1.87 | 1 | 195 | 195 | 1.5628e-05 | 1.5628e-05 | 5 | 103414 | 0.0010346 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP031 | Citipower | CBD | 37 | 0 | 0.4 | 2.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP032 | Citipower | CBD | 1 | 0 | 1.037 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP033 | Citipower | CBD | 332 | 0 | 2.724 | 5.428 | 0 | 0.265 | 0 | 0 | 0 | 0 | 0 | 4 | 2496 | 4.0632e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP035 | Citipower | CBD | 96 | 0 | 1.844 | 1.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP036 | Citipower | CBD | 447 | 0 | 8.042 | 4.909 | 1.379 | 0 | 1 | 19346 | 19346 | 0.0013721 | 0.0013721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP037 | Citipower | CBD | 79 | 0 | 2.223 | 4.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP038 | Citipower | CBD | 43 | 0 | 1.693 | 1.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP039 | Citipower | CBD | 0 | 0 | 0.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP040 | Citipower | CBD | 7 | 0 | 1.214 | 3.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP041 | Citipower | CBD | 40 | 0 | 1.078 | 4.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP044 | Citipower | CBD | 10 | 0 | 3.222 | 3.224 | 1.48 | 0 | 0 | 707 | 707 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP047 | Citipower | CBD | 292 | 0 | 2.053 | 3.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP049 | Citipower | CBD | 285 | 0 | 3.289 | 5.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP050 | Citipower | CBD | 420 | 0 | 2.704 | 3.451 | 0 | 0.102 | 0 | 0 | 0 | 0 | 0 | 1 | 1914 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP051 | Citipower | CBD | 172 | 0 | 1.539 | 3.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP053 | Citipower | CBD | 183 | 0 | 1.199 | 4.641 | 2.208 | 0.61 | 1 | 13414 | 13414 | 0.00029067 | 0.00029067 | 1 | 3708 | 0.00029067 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
MP054 | Citipower | CBD | 6 | 0 | 0.46 | 2.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP055 | Citipower | CBD | 1495 | 0 | 6.766 | 4.061 | 0.1 | 0 | 2 | 5678 | 5678 | 0.0001344 | 0.0001344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP058 | Citipower | CBD | 591 | 0 | 4.413 | 4.151 | 0.023 | 0 | 0 | 511 | 511 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP059 | Citipower | CBD | 189 | 0 | 2.352 | 4.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP060 | Citipower | CBD | 0 | 0 | 6.601 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP062 | Citipower | CBD | 355 | 0 | 1.644 | 5.4 | 0.365 | 0.027 | 1 | 3701 | 3701 | 8.439e-05 | 8.439e-05 | 1 | 271 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP063 | Citipower | CBD | 0 | 0 | 0.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP064 | Citipower | CBD | 43 | 0 | 0.584 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP066 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
MP067 | Citipower | CBD | 122 | 0 | 3.094 | 4.4 | 0.13 | 0 | 0 | 556 | 556 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NC001 | Citipower | Urban | 1422 | 1.082 | 2.746 | 2.699 | 7.036 | 2.796 | 9 | 571067 | 62120 | 0.0069387 | 0.0016065 | 5 | 226907 | 0.0012565 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NC002 | Citipower | Urban | 3185 | 7.186 | 0.837 | 4.56 | 30.183 | 1.5 | 15 | 3247781 | 367314 | 0.050581 | 0.020882 | 12 | 161427 | 0.001744 | 1 | 0 | 0.0099892 | 0.0099892 | 0 | 0 | YES | NO
NC004 | Citipower | Urban | 3234 | 7.841 | 1.129 | 4.435 | 11.417 | 0.666 | 6 | 1282442 | 168378 | 0.020479 | 0.010327 | 8 | 74826 | 0.0010846 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NC005 | Citipower | Urban | 1146 | 2.575 | 1.686 | 2.03 | 6.364 | 0.282 | 4 | 553489 | 6261 | 0.0075669 | 0.00032506 | 8 | 24556 | 0.00029067 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NC006 | Citipower | Urban | 936 | 4.411 | 0.368 | 2.434 | 6.642 | 0.538 | 6 | 393507 | 72555 | 0.0065386 | 0.0036131 | 5 | 31881 | 0.00035944 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NC009 | Citipower | Urban | 1703 | 3.088 | 1.992 | 3 | 11.443 | 0.869 | 13 | 1000593 | 252026 | 0.018153 | 0.011865 | 11 | 76005 | 0.00076576 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NC010 | Citipower | Urban | 1010 | 4.019 | 0.915 | 1.422 | 4.1 | 0.638 | 9 | 448713 | 123977 | 0.0074075 | 0.004457 | 12 | 69844 | 0.0011627 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NC013 | Citipower | Urban | 1859 | 5.279 | 1.839 | 2.695 | 6.14 | 0.802 | 2 | 652525 | 9264 | 0.0059291 | 8.439e-05 | 5 | 85204 | 0.00061886 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NC014 | Citipower | Urban | 1257 | 1.574 | 2.294 | 4.307 | 12.552 | 1.659 | 5 | 564288 | 75439 | 0.0084421 | 0.0040851 | 7 | 74591 | 0.00068449 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NC015 | Citipower | Urban | 2320 | 4.811 | 1.385 | 3.194 | 7.235 | 0.51 | 3 | 809479 | 14151 | 0.0074857 | 0.00025942 | 6 | 57069 | 0.00080014 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
NR002 | Citipower | Urban | 1341 | 3.141 | 6.595 | 6.109 | 0.096 | 3.63 | 2 | 3237 | 3237 | 5.9385e-05 | 5.9385e-05 | 8 | 122768 | 0.00095329 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR003 | Citipower | Urban | 2811 | 0.452 | 6.464 | 7.789 | 0.43 | 1.421 | 6 | 23878 | 23878 | 0.00028442 | 0.00028442 | 9 | 78989 | 0.00070637 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR004 | Citipower | Urban | 69 | 0 | 2.674 | 2.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR006 | Citipower | Urban | 2184 | 1.455 | 3.559 | 7.243 | 0.19 | 0.33 | 4 | 8828 | 8828 | 0.00017816 | 0.00017816 | 4 | 15306 | 0.00021254 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR007 | Citipower | Urban | 1396 | 1.541 | 4.297 | 5.654 | 0.033 | 0.439 | 1 | 1242 | 1242 | 4.3758e-05 | 4.3758e-05 | 3 | 16708 | 0.00019378 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR011 | Citipower | Urban | 42 | 0 | 0.934 | 1.683 | 0.032 | 0 | 0 | 123 | 123 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR012 | Citipower | Urban | 31 | 0 | 0.929 | 1.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR013 | Citipower | Urban | 165 | 0 | 3.825 | 3.501 | 0.017 | 0 | 1 | 127 | 127 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR015 | Citipower | Urban | 1800 | 0.591 | 3.399 | 3.81 | 0.004 | 0.719 | 0 | 318 | 318 | 6.2511e-06 | 6.2511e-06 | 3 | 52315 | 0.00035631 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR016 | Citipower | Urban | 775 | 2.409 | 4.875 | 3.081 | 0.675 | 0.006 | 1 | 26170 | 26170 | 0.0020347 | 0.0020347 | 1 | 250 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR020 | Citipower | Urban | 1271 | 2.257 | 5.171 | 3.027 | 0.013 | 0 | 0 | 812 | 812 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR021 | Citipower | Urban | 819 | 0.612 | 3.536 | 4.313 | 0.001 | 0.035 | 1 | 28 | 28 | 3.1255e-06 | 3.1255e-06 | 1 | 1015 | 2.1879e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR022 | Citipower | Urban | 1489 | 0.282 | 2.906 | 4.749 | 0.177 | 0.882 | 7 | 8541 | 8541 | 0.00049071 | 0.00049071 | 3 | 42610 | 0.00038757 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR024 | Citipower | Urban | 526 | 0 | 3.259 | 3.464 | 0.001 | 0 | 0 | 14 | 14 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NR025 | Citipower | Urban | 406 | 0.766 | 3.42 | 3.849 | 0.019 | 0 | 0 | 305 | 305 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NS010 | Citipower | Urban | 645 | 1.799 | 0.253 | 1.2 | 0.045 | 0 | 1 | 3748 | 3748 | 0.00010002 | 0.00010002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
NS013 | Citipower | Urban | 1042 | 2.618 | 0.741 | 1.5 | 0.223 | 0 | 1 | 23906 | 866 | 6.8762e-05 | 6.2511e-06 | 1 | 45 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
P056 | Citipower | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM001 | Citipower | Urban | 45 | 0.658 | 1.952 | 2.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM002 | Citipower | Urban | 45 | 0.794 | 0.365 | 2.471 | 3.278 | 0.102 | 2 | 9196 | 9196 | 0.0002813 | 0.0002813 | 1 | 285 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM003 | Citipower | Urban | 896 | 1.341 | 3.68 | 3.088 | 1.054 | 0 | 3 | 47121 | 47121 | 0.0031505 | 0.0031505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM004 | Citipower | Urban | 62 | 0.478 | 1.201 | 2.34 | 1.362 | 0 | 1 | 5560 | 5560 | 0.00019378 | 0.00019378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM005 | Citipower | Urban | 773 | 2.682 | 0.937 | 2.661 | 0.274 | 0 | 2 | 12258 | 12258 | 0.0002813 | 0.0002813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM006 | Citipower | Urban | 45 | 3.849 | 2.724 | 1.179 | 0.044 | 0.123 | 1 | 260 | 260 | 3.1255e-06 | 3.1255e-06 | 2 | 726 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM007 | Citipower | Urban | 15 | 0.95 | 0.252 | 0.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM008 | Citipower | Urban | 179 | 0.73 | 0.799 | 1.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM009 | Citipower | Urban | 558 | 1.945 | 0.625 | 1.912 | 0.03 | 0.053 | 1 | 1363 | 1363 | 2.813e-05 | 2.813e-05 | 1 | 2391 | 3.1255e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM010 | Citipower | Urban | 72 | 0.264 | 0.44 | 0.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM011 | Citipower | Urban | 1 | 0 | 0.025 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PM012 | Citipower | Urban | 257 | 0.8 | 1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PR018 | Citipower | Urban | 617 | 0.339 | 1.355 | 2.175 | 1.054 | 0.636 | 2 | 46050 | 46050 | 0.0020253 | 0.0020253 | 2 | 27780 | 0.00014377 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PR019 | Citipower | Urban | 1440 | 0.692 | 2.588 | 3.864 | 3.384 | 0.06 | 4 | 194282 | 194282 | 0.010461 | 0.010461 | 2 | 3440 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PR020 | Citipower | Urban | 2050 | 0.002 | 4.202 | 4.246 | 1.437 | 0.474 | 4 | 106915 | 106915 | 0.0062542 | 0.0062542 | 5 | 35250 | 0.00034693 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PR021 | Citipower | Urban | 462 | 0 | 0.646 | 4.919 | 1.725 | 0 | 1 | 24954 | 24954 | 0.001444 | 0.001444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PR022 | Citipower | Urban | 629 | 0 | 1.971 | 4.485 | 0.042 | 0 | 1 | 899 | 899 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PR023 | Citipower | Urban | 1710 | 2.671 | 2.914 | 1.293 | 0.001 | 0.127 | 0 | 227 | 227 | 1.2502e-05 | 1.2502e-05 | 3 | 25863 | 0.00046883 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PR025 | Citipower | Urban | 350 | 0.222 | 1.649 | 2.533 | 0.811 | 0.195 | 2 | 17249 | 17249 | 0.0011189 | 0.0011189 | 1 | 4140 | 3.7506e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
PR026 | Citipower | Urban | 725 | 0 | 2.621 | 4.291 | 1.235 | 1.374 | 5 | 32139 | 32139 | 0.00055322 | 0.00055322 | 2 | 35754 | 0.0004282 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q001 | Citipower | Urban | 693 | 1.023 | 1.638 | 4.291 | 0.149 | 1.774 | 2 | 3695 | 3695 | 0.00028755 | 0.00028755 | 3 | 44145 | 0.00045945 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q002 | Citipower | Urban | 1723 | 4.624 | 2.587 | 2.894 | 4.484 | 0.055 | 3 | 411260 | 24614 | 0.0055916 | 0.00022504 | 3 | 5050 | 8.439e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q004 | Citipower | Urban | 468 | 1.391 | 1.983 | 4.994 | 1.884 | 0.051 | 3 | 27203 | 27203 | 0.001694 | 0.001694 | 1 | 740 | 1.5628e-05 | 1 | 0 | 0.0014502 | 0.0014502 | 0 | 0 | NO | NO
Q005 | Citipower | Urban | 2048 | 5.598 | 0.819 | 4.539 | 2.05 | 0.852 | 7 | 142469 | 142469 | 0.014215 | 0.014215 | 5 | 59242 | 0.00061886 | 1 | 0 | 0.0069199 | 0.0069199 | 0 | 0 | NO | NO
Q006 | Citipower | Urban | 694 | 3.481 | 1.673 | 0 | 0 | 0 | 0 | 678 | 678 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q009 | Citipower | Urban | 1843 | 4.734 | 2.49 | 5.359 | 1.471 | 0.083 | 3 | 77934 | 77934 | 0.0058729 | 0.0058729 | 1 | 4410 | 6.5636e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q010 | Citipower | Urban | 893 | 2.988 | 1.128 | 4.605 | 1.892 | 0.244 | 3 | 56532 | 56532 | 0.0029693 | 0.0029693 | 1 | 7285 | 9.6892e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q013 | Citipower | Urban | 1493 | 0.764 | 1.691 | 4.334 | 0.195 | 1.208 | 3 | 10369 | 10369 | 0.00019378 | 0.00019378 | 5 | 64100 | 0.00061886 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q014 | Citipower | Urban | 1955 | 6.485 | 1.973 | 5.687 | 0.439 | 1.514 | 3 | 23259 | 23259 | 0.00061573 | 0.00061573 | 9 | 80195 | 0.00083139 | 1 | 0 | 0.0061136 | 0.0061136 | 0 | 0 | NO | NO
Q015 | Citipower | Urban | 65 | 1.227 | 4.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1825 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q018 | Citipower | Urban | 58 | 0 | 0 | 1.1 | 0 | 0.98 | 0 | 0 | 0 | 0 | 0 | 2 | 7956 | 0.00022504 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Q019 | Citipower | Urban | 2260 | 5.069 | 7.031 | 4 | 6.857 | 0.977 | 7 | 596784 | 252041 | 0.028508 | 0.021397 | 7 | 85024 | 0.00055009 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
R-CRE013 | Citipower | Urban | 3 | 0 | 0.21 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R-CRE022 | Citipower | Urban | 0 | 0 | 0.211 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R021 | Citipower | Urban | 71 | 0 | 2.003 | 2.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R022 | Citipower | Urban | 271 | 0 | 1.541 | 1.895 | 2.057 | 2.969 | 2 | 45336 | 45336 | 0.00092516 | 0.00092516 | 9 | 65416 | 0.00087828 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
R023 | Citipower | Urban | 744 | 0.645 | 3.918 | 5.152 | 11.309 | 1.332 | 6 | 251564 | 251564 | 0.0098048 | 0.0098048 | 3 | 29623 | 0.00031568 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
R024 | Citipower | Urban | 642 | 0.399 | 3.212 | 5.357 | 0.817 | 0.338 | 5 | 15076 | 13573 | 0.00037194 | 0.00034381 | 2 | 6236 | 6.8762e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R031 | Citipower | Urban | 766 | 0 | 2.569 | 4.578 | 1.545 | 0.575 | 1 | 39824 | 39824 | 0.0024129 | 0.0024129 | 4 | 14830 | 0.00022191 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R032 | Citipower | Urban | 991 | 0.196 | 1.953 | 3.371 | 1.261 | 0 | 3 | 57136 | 57136 | 0.0031818 | 0.0031818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R033 | Citipower | Urban | 563 | 0.328 | 2.61 | 3.5 | 1.188 | 0.802 | 1 | 29432 | 29432 | 0.0017691 | 0.0017691 | 2 | 19880 | 0.00017503 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R034 | Citipower | Urban | 327 | 0 | 1.431 | 3.682 | 2.452 | 0.827 | 1 | 33540 | 33540 | 0.002016 | 0.002016 | 1 | 11310 | 0.0001219 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R035 | Citipower | Urban | 251 | 0.341 | 3.676 | 5.926 | 2.934 | 7.495 | 2 | 19148 | 19148 | 0.00096579 | 0.00096579 | 8 | 48908 | 0.00036881 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
R083_R090 | Citipower | Urban | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R084_R096 | Citipower | Urban | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R091_R092 | Citipower | Urban | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
R093_R095 | Citipower | Urban | 1056 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 369 | 6.2511e-06 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RD001 | Citipower | Urban | 1668 | 5.123 | 2.035 | 4.73 | 0.69 | 0.317 | 3 | 37483 | 5905 | 0.0052978 | 0.00010314 | 1 | 17225 | 0.00016565 | 1 | 0 | 0.0052134 | 0.0052134 | 0 | 0 | NO | NO
RD002 | Citipower | Urban | 1137 | 1.241 | 0.315 | 5.783 | 5.304 | 1.259 | 6 | 160643 | 126158 | 0.011343 | 0.0056697 | 5 | 38115 | 0.00032506 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RD004 | Citipower | Urban | 255 | 0.817 | 0.326 | 6.282 | 20.196 | 0 | 2 | 126295 | 384 | 0.0016065 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
RD005 | Citipower | Urban | 1745 | 4.513 | 2.151 | 4.619 | 1.072 | 0.148 | 6 | 62422 | 29267 | 0.0060667 | 0.00061261 | 1 | 8640 | 0.00022504 | 0 | 1 | 0 | 0 | 0.0034412 | 0.0034412 | NO | NO
RD006 | Citipower | Urban | 1310 | 3.763 | 1.789 | 5.066 | 1.133 | 0 | 6 | 45156 | 20076 | 0.0043445 | 0.00021879 | 0 | 2 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RD009 | Citipower | Urban | 457 | 2.669 | 0.313 | 2.063 | 0.404 | 0.548 | 3 | 13783 | 5100 | 0.0016815 | 0.00025317 | 4 | 18710 | 0.00023442 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RD010 | Citipower | Urban | 238 | 0.543 | 0.257 | 2.711 | 2.948 | 0 | 3 | 39873 | 35389 | 0.0019035 | 0.0011658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RD013 | Citipower | Urban | 1662 | 4.789 | 0.685 | 5.37 | 2.636 | 0.247 | 2 | 125694 | 93964 | 0.010452 | 0.0052321 | 4 | 11780 | 0.00014377 | 0 | 2 | 0 | 0 | 0.0048946 | 0.0048946 | NO | NO
RD014 | Citipower | Urban | 1663 | 6.692 | 1.386 | 4.85 | 14.777 | 0.409 | 4 | 780589 | 5039 | 0.010442 | 5.9385e-05 | 3 | 21596 | 0.00023754 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
RD015 | Citipower | Urban | 1008 | 2.688 | 0.316 | 2.516 | 2.236 | 0.021 | 4 | 138002 | 58696 | 0.0067949 | 0.0033443 | 1 | 1320 | 2.5004e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP001 | Citipower | CBD | 131 | 0 | 0.788 | 1.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP002 | Citipower | CBD | 97 | 0 | 0.116 | 0.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP003 | Citipower | CBD | 140 | 0 | 0.823 | 1.374 | 0.012 | 0 | 0 | 183 | 183 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP007 | Citipower | CBD | 7 | 0 | 0.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP009 | Citipower | CBD | 0 | 0 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP018 | Citipower | CBD | 180 | 0 | 0.95 | 0.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP019 | Citipower | CBD | 32 | 0 | 0.82 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP022 | Citipower | CBD | 125 | 0 | 0.108 | 0.627 | 0.003 | 0 | 0 | 102 | 102 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP023 | Citipower | CBD | 0 | 0 | 0.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP026 | Citipower | CBD | 56 | 0 | 1.374 | 2.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP027 | Citipower | CBD | 0 | 0 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RP030 | Citipower | CBD | 251 | 0 | 1.096 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RTS-BUR137 | Citipower | Urban | 1 | 0.566 | 0.812 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RTS-BUR151 | Citipower | Urban | 1 | 0.792 | 1.098 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RTS-CIT150 | Citipower | Urban | 1 | 0 | 0.397 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RTS152 | Citipower | CBD | 0 | 0 | 0.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
RTS153 | Citipower | CBD | 0 | 0.003 | 19.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB011 | Citipower | CBD | 0 | 0 | 0 | 5.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB012 | Citipower | CBD | 1556 | 0 | 2.641 | 4.648 | 1.088 | 0.711 | 1 | 56116 | 56116 | 0.0049071 | 0.0049071 | 4 | 36664 | 0.00053134 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB013 | Citipower | CBD | 0 | 0 | 0 | 4.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB015 | Citipower | CBD | 72 | 0 | 2.839 | 3.378 | 0 | 0.512 | 0 | 0 | 0 | 0 | 0 | 1 | 1680 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB016 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB021 | Citipower | CBD | 138 | 0 | 2.277 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB022 | Citipower | CBD | 18 | 0 | 1.67 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB023 | Citipower | CBD | 349 | 0 | 4.608 | 3.307 | 1.339 | 0 | 1 | 21762 | 21762 | 0.0010971 | 0.0010971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB025 | Citipower | CBD | 173 | 0 | 0.816 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB026 | Citipower | CBD | 24 | 0 | 1.241 | 9.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB041 | Citipower | CBD | 250 | 0 | 8.943 | 3.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB042 | Citipower | CBD | 1 | 0 | 0.603 | 0.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB043 | Citipower | CBD | 0 | 0 | 0.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB045 | Citipower | CBD | 237 | 0 | 0.829 | 3.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB046 | Citipower | CBD | 1 | 0 | 0.756 | 0.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB051 | Citipower | CBD | 612 | 0 | 5.843 | 5.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB052 | Citipower | CBD | 33 | 0.001 | 0.873 | 0.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB053 | Citipower | CBD | 1 | 0 | 0.615 | 0.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB055 | Citipower | CBD | 16 | 0 | 0.776 | 1.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SB056 | Citipower | CBD | 145 | 0 | 1.903 | 0.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK001 | Citipower | Urban | 1764 | 0.374 | 4.256 | 4.858 | 0.05 | 0.344 | 2 | 2784 | 2784 | 2.813e-05 | 2.813e-05 | 1 | 19250 | 0.00024067 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK002 | Citipower | CBD | 56 | 0 | 5.008 | 3.463 | 2.203 | 0.096 | 1 | 5488 | 5488 | 2.1879e-05 | 2.1879e-05 | 1 | 240 | 6.2511e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK004 | Citipower | CBD | 556 | 0 | 3.74 | 4.04 | 1.884 | 0 | 1 | 39948 | 39948 | 0.0017315 | 0.0017315 | 0 | 0 | 0 | 1 | 0 | 0.0017409 | 0.0017409 | 0 | 0 | NO | NO
SK005 | Citipower | Urban | 2928 | 0.88 | 5.794 | 6.207 | 0.42 | 0.823 | 4 | 30524 | 1058 | 0.00026567 | 4.0632e-05 | 4 | 59790 | 0.0008689 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK006 | Citipower | Urban | 976 | 0.228 | 2.295 | 3.949 | 0.401 | 0.129 | 5 | 15280 | 15280 | 0.00066574 | 0.00066574 | 1 | 4930 | 5.3134e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK009 | Citipower | Urban | 577 | 0.728 | 1.718 | 0.99 | 0.071 | 0 | 1 | 6342 | 6342 | 4.3758e-05 | 4.3758e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK010 | Citipower | CBD | 20 | 0 | 2.681 | 3.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK013 | Citipower | Urban | 2103 | 0.964 | 2.804 | 4.522 | 0.008 | 0.228 | 0 | 559 | 559 | 1.5628e-05 | 1.5628e-05 | 1 | 16340 | 0.0001344 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK014 | Citipower | CBD | 667 | 0 | 2.888 | 4.501 | 0 | 0.325 | 0 | 0 | 0 | 0 | 0 | 1 | 7410 | 0.00035631 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK015 | Citipower | CBD | 842 | 0 | 1.849 | 3.914 | 0 | 0.192 | 0 | 0 | 0 | 0 | 0 | 1 | 6380 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK018 | Citipower | CBD | 174 | 0 | 3.515 | 3.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK019 | Citipower | CBD | 395 | 0 | 3.595 | 3.261 | 0 | 0.549 | 0 | 0 | 0 | 0 | 0 | 1 | 10240 | 0.00025004 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK020 | Citipower | CBD | 305 | 0 | 3.808 | 5.182 | 0.468 | 0 | 1 | 4240 | 4240 | 6.2511e-05 | 6.2511e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK022 | Citipower | CBD | 399 | 0 | 2.298 | 3.455 | 0 | 0.427 | 0 | 0 | 0 | 0 | 0 | 1 | 7596 | 3.7506e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK023 | Citipower | Urban | 687 | 0.249 | 1.407 | 3.794 | 0.009 | 0 | 0 | 252 | 0 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK024 | Citipower | Urban | 574 | 0.52 | 4.301 | 4.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SK025 | Citipower | Urban | 430 | 0 | 2.318 | 1.244 | 0.001 | 0.166 | 0 | 41 | 0 | 3.1255e-06 | 0 | 3 | 8856 | 0.00030005 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO001 | Citipower | CBD | 380 | 0 | 1.962 | 3.673 | 0.024 | 0.039 | 1 | 381 | 381 | 0.0011908 | 0.0011908 | 1 | 625 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO002 | Citipower | CBD | 661 | 0 | 4.906 | 7.093 | 0.046 | 0 | 1 | 657 | 657 | 0.0020535 | 0.0020535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO004 | Citipower | CBD | 0 | 0 | 0.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO005 | Citipower | CBD | 1037 | 0 | 1.531 | 3.853 | 0.028 | 0 | 1 | 1167 | 1167 | 0.0032256 | 0.0032256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO006 | Citipower | CBD | 463 | 0 | 1.956 | 3.776 | 0.024 | 0 | 1 | 461 | 461 | 0.0014409 | 0.0014409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO009 | Citipower | Urban | 220 | 0 | 1.507 | 3.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO010 | Citipower | CBD | 973 | 0 | 2.971 | 5.861 | 1.341 | 2.488 | 1 | 34286 | 34286 | 0.0017284 | 0.0017284 | 2 | 63630 | 0.00040319 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO013 | Citipower | CBD | 353 | 0 | 1.69 | 6.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO014 | Citipower | CBD | 110 | 0 | 3.299 | 5.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO015 | Citipower | CBD | 73 | 0 | 0.763 | 1.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO018 | Citipower | Urban | 270 | 0.183 | 2.121 | 2.755 | 0 | 0.097 | 0 | 0 | 0 | 0 | 0 | 1 | 1470 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO019 | Citipower | CBD | 299 | 0 | 0.34 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO020 | Citipower | CBD | 377 | 0 | 1.688 | 2.86 | 0.006 | 0 | 0 | 114 | 114 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO022 | Citipower | CBD | 549 | 0 | 4.423 | 4.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO023 | Citipower | CBD | 7 | 0 | 1.098 | 1.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
SO024 | Citipower | CBD | 127 | 0 | 1.777 | 2.332 | 0.004 | 0 | 0 | 36 | 36 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK001 | Citipower | Urban | 1224 | 2.839 | 2.852 | 4.123 | 0.989 | 0.08 | 7 | 45206 | 45206 | 0.0010064 | 0.0010064 | 2 | 3640 | 3.4381e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK002 | Citipower | Urban | 942 | 0.323 | 2.378 | 2.871 | 1.012 | 0 | 1 | 51121 | 51121 | 0.00032193 | 0.00032193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK004 | Citipower | Urban | 1533 | 0.868 | 2.853 | 5.548 | 0.075 | 2.492 | 1 | 3191 | 3191 | 8.439e-05 | 8.439e-05 | 5 | 106099 | 0.00085952 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK005 | Citipower | Urban | 690 | 0.287 | 1.994 | 2.619 | 0.256 | 0.306 | 1 | 10390 | 274 | 5.9385e-05 | 3.1255e-06 | 2 | 12420 | 0.00018753 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK006 | Citipower | Urban | 944 | 2.743 | 2.505 | 3.476 | 1.046 | 4.158 | 5 | 43763 | 42440 | 0.0028192 | 0.002813 | 10 | 173917 | 0.0011971 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK009 | Citipower | Urban | 1810 | 0.368 | 3.242 | 3.393 | 1.166 | 0.528 | 1 | 95855 | 95779 | 0.0056353 | 0.0056322 | 1 | 43414 | 0.0003063 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK010 | Citipower | Urban | 891 | 2.721 | 2.153 | 3.088 | 2.34 | 0 | 3 | 104017 | 104017 | 0.0055822 | 0.0055822 | 0 | 0 | 0 | 1 | 0 | 0.0027724 | 0.0027724 | 0 | 0 | NO | NO
TK011 | Citipower | Urban | 655 | 0 | 1.885 | 4.302 | 0.036 | 0.263 | 1 | 852 | 852 | 3.7506e-05 | 3.7506e-05 | 2 | 6160 | 4.0632e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK013 | Citipower | Urban | 121 | 0 | 1.597 | 4.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK014 | Citipower | Urban | 1038 | 0.718 | 1.722 | 2.588 | 0.013 | 0.533 | 1 | 813 | 189 | 1.5628e-05 | 3.1255e-06 | 2 | 32900 | 0.00036881 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK015 | Citipower | Urban | 1936 | 1.392 | 0.647 | 4.801 | 0.231 | 0.202 | 6 | 14374 | 14374 | 0.00051259 | 0.00051259 | 1 | 12540 | 0.00010314 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK017 | Citipower | Urban | 437 | 0 | 2.388 | 4.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK020 | Citipower | Urban | 17 | 0 | 1.946 | 1.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK022 | Citipower | Urban | 898 | 0.724 | 2.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 45720 | 0.00036881 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TK025 | Citipower | Urban | 1217 | 3.247 | 1.479 | 5.57 | 0.154 | 0.004 | 2 | 5184 | 5184 | 0.0001344 | 0.0001344 | 1 | 150 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP002 | Citipower | CBD | 164 | 0 | 0.634 | 1.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP003 | Citipower | CBD | 27 | 0 | 0.027 | 0.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP006 | Citipower | CBD | 4 | 0 | 0.112 | 0.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP007 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP008 | Citipower | CBD | 17 | 0 | 0.059 | 0.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP013 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP014 | Citipower | CBD | 119 | 0 | 0.546 | 1.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP027 | Citipower | CBD | 3 | 0 | 0.52 | 1.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP029 | Citipower | CBD | 1 | 0 | 0.036 | 2.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP031 | Citipower | CBD | 27 | 0 | 1.162 | 0.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
TP034 | Citipower | CBD | 19 | 0 | 0.078 | 1.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM002 | Citipower | CBD | 147 | 0 | 1.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM003 | Citipower | CBD | 180 | 0 | 1.644 | 1.861 | 0.013 | 0 | 2 | 193 | 193 | 0.00060323 | 0.00060323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM004 | Citipower | Urban | 1176 | 0 | 6.108 | 2.743 | 1.536 | 0.162 | 4 | 101483 | 101483 | 0.00044383 | 0.00044383 | 3 | 10674 | 0.00012502 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM005 | Citipower | CBD | 1 | 0 | 0.058 | 0.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM006 | Citipower | Urban | 0 | 0 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM007 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM008 | Citipower | Urban | 176 | 0 | 2.726 | 2.786 | 0.018 | 0.443 | 1 | 180 | 180 | 3.1255e-06 | 3.1255e-06 | 1 | 4310 | 3.1255e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM009 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM010 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM011 | Citipower | CBD | 433 | 0 | 2.395 | 2.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM014 | Citipower | CBD | 427 | 0 | 3.88 | 2.121 | 0.011 | 0.198 | 0 | 348 | 348 | 3.1255e-06 | 3.1255e-06 | 2 | 6125 | 7.1887e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM018 | Citipower | CBD | 188 | 0 | 3.044 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM019 | Citipower | Urban | 0 | 0 | 0.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM020 | Citipower | CBD | 673 | 0 | 4.437 | 3.055 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM022 | Citipower | CBD | 1 | 0 | 0.723 | 1.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM025 | Citipower | CBD | 299 | 0 | 1.067 | 1.593 | 0.44 | 0 | 2 | 12731 | 12731 | 0.00021566 | 0.00021566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM026 | Citipower | CBD | 274 | 0 | 1.76 | 1.681 | 0.004 | 0.53 | 0 | 102 | 102 | 3.1255e-06 | 3.1255e-06 | 5 | 13314 | 0.0001219 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM027 | Citipower | CBD | 246 | 0 | 1.605 | 1.862 | 0.012 | 0 | 1 | 237 | 237 | 0.00074075 | 0.00074075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM028 | Citipower | CBD | 1 | 0 | 1.987 | 1.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM029 | Citipower | CBD | 12 | 0 | 0.055 | 1.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM030 | Citipower | Urban | 1209 | 0 | 6.19 | 4.597 | 0.022 | 0 | 1 | 876 | 876 | 1.8753e-05 | 1.8753e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM034 | Citipower | CBD | 239 | 0 | 3.776 | 3.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM035 | Citipower | CBD | 211 | 0 | 3.104 | 2.934 | 0.184 | 0.41 | 1 | 2037 | 2037 | 6.5636e-05 | 6.5636e-05 | 1 | 4542 | 5.9385e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM037 | Citipower | CBD | 7 | 0 | 2.968 | 4.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM038 | Citipower | Urban | 412 | 0 | 2.069 | 0.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM039 | Citipower | Urban | 1 | 0 | 4.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM040 | Citipower | Urban | 912 | 0 | 2.724 | 2.366 | 0.06 | 0.36 | 1 | 3563 | 3563 | 4.6883e-05 | 4.6883e-05 | 3 | 21365 | 0.00024067 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM041 | Citipower | CBD | 113 | 0 | 2.255 | 2.65 | 5.328 | 2.226 | 3 | 35001 | 35001 | 0.00023442 | 0.00023442 | 1 | 14625 | 0.00014065 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
VM042 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
VM043 | Citipower | CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA002 | Citipower | CBD | 22 | 0 | 0.927 | 4.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA003 | Citipower | CBD | 72 | 0 | 1.332 | 2.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA004 | Citipower | CBD | 0 | 0 | 0.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA005 | Citipower | CBD | 641 | 0 | 0.361 | 3.017 | 0.006 | 0 | 0 | 200 | 200 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA006 | Citipower | CBD | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA007 | Citipower | CBD | 0 | 0 | 0.441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA008 | Citipower | CBD | 316 | 0 | 2.153 | 3.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA009 | Citipower | CBD | 650 | 0 | 2.382 | 6.252 | 0.019 | 2.074 | 1 | 304 | 304 | 1.2502e-05 | 1.2502e-05 | 2 | 33220 | 0.00068762 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA011 | Citipower | CBD | 85 | 0 | 1.449 | 1.837 | 0.009 | 0 | 0 | 61 | 61 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA014 | Citipower | CBD | 93 | 0 | 0.874 | 1.337 | 0.195 | 0.321 | 2 | 2092 | 2092 | 4.0632e-05 | 4.0632e-05 | 3 | 3439 | 6.8762e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA015 | Citipower | CBD | 142 | 0 | 0.997 | 5.162 | 0 | 1.85 | 0 | 0 | 0 | 0 | 0 | 1 | 7839 | 0.00062823 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA019 | Citipower | CBD | 0 | 0 | 0.705 | 1.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA020 | Citipower | CBD | 389 | 0 | 2.216 | 4.53 | 0.031 | 0 | 0 | 406 | 406 | 9.3766e-06 | 9.3766e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA021 | Citipower | CBD | 466 | 0 | 1.174 | 3.169 | 0.007 | 0 | 0 | 165 | 165 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA022 | Citipower | CBD | 713 | 0 | 1.653 | 4.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA023 | Citipower | CBD | 401 | 0 | 2.649 | 1.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA024 | Citipower | CBD | 180 | 0 | 1.339 | 3.002 | 0 | 5.222 | 0 | 0 | 0 | 0 | 0 | 4 | 48239 | 0.00084077 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
WA027 | Citipower | CBD | 1 | 0 | 1.5 | 4.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA030 | Citipower | CBD | 230 | 0 | 1.187 | 4.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA031 | Citipower | CBD | 171 | 0 | 1.384 | 2.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA032 | Citipower | CBD | 25 | 0 | 0.356 | 1.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA033 | Citipower | CBD | 51 | 0 | 0.665 | 0.59 | 0 | 0.322 | 0 | 0 | 0 | 0 | 0 | 3 | 4286 | 0.00010002 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA034 | Citipower | CBD | 925 | 0 | 3.917 | 3.317 | 0.033 | 0 | 1 | 1422 | 1422 | 1.2502e-05 | 1.2502e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WA035 | Citipower | CBD | 337 | 0 | 1.422 | 3.274 | 0.025 | 0 | 0 | 395 | 395 | 3.1255e-06 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WB001 | Citipower | Urban | 854 | 1.059 | 0.65 | 1.894 | 4.375 | 0 | 1 | 303972 | 0 | 0.002738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
WB002 | Citipower | Urban | 3440 | 8.464 | 0.559 | 5.202 | 13.788 | 0.521 | 5 | 1404664 | 207604 | 0.021638 | 0.010852 | 2 | 53094 | 0.00053134 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
WB004 | Citipower | Urban | 400 | 1.151 | 0.832 | 2.584 | 7.598 | 0 | 10 | 181151 | 42698 | 0.0023317 | 0.0010846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
WB005 | Citipower | Urban | 756 | 1.677 | 0.382 | 1.9 | 4.393 | 0 | 5 | 269346 | 12566 | 0.0045914 | 0.0022785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO
WB009 | Citipower | Urban | 1113 | 2.806 | 1.355 | 2.393 | 5.343 | 0.126 | 2 | 382888 | 4364 | 0.0035662 | 0.0001469 | 1 | 9000 | 6.2511e-05 | 1 | 0 | 0.0035631 | 0.0035631 | 0 | 0 | YES | NO
WB010 | Citipower | Urban | 627 | 0.184 | 4 | 1.921 | 4.536 | 0.391 | 1 | 228014 | 0 | 0.0020597 | 0 | 5 | 19667 | 0.00035319 | 1 | 0 | 0.0020535 | 0.0020535 | 0 | 0 | YES | NO
WB011 | Citipower | Urban | 1681 | 4.578 | 0.179 | 2.482 | 5.62 | 0 | 3 | 586383 | 6833 | 0.0052915 | 5.626e-05 | 0 | 0 | 0 | 1 | 0 | 0.0052447 | 0.0052447 | 0 | 0 | YES | NO
WB013 | Citipower | Urban | 2199 | 4.572 | 1.129 | 3.548 | 10.633 | 0 | 4 | 1015235 | 217619 | 0.013874 | 0.0069574 | 0 | 0 | 0 | 1 | 0 | 0.0069231 | 0.0069231 | 0 | 0 | YES | NO
WB014 | Citipower | Urban | 138 | 0.357 | 1.121 | 2.004 | 3.979 | 0 | 1 | 42212 | 0 | 0.00038132 | 0 | 0 | 0 | 0 | 1 | 0 | 0.00048758 | 0.00048758 | 0 | 0 | YES | NO
WB015 | Citipower | Urban | 864 | 1.522 | 2.008 | 2.72 | 7.057 | 1.741 | 1 | 345302 | 368 | 0.0027098 | 1.2502e-05 | 3 | 85175 | 0.00044383 | 1 | 0 | 0.0026973 | 0.0026973 | 0 | 0 | YES | NO
WD002 | Citipower | Urban | 429 | 0 | 0 | 2.451 | 0.042 | 0 | 0 | 1144 | 1144 | 1.5628e-05 | 1.5628e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD004 | Citipower | Urban | 829 | 0 | 0 | 4.616 | 0.004 | 0.072 | 0 | 102 | 102 | 6.2511e-06 | 6.2511e-06 | 1 | 1995 | 2.1879e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD006 | Citipower | Urban | 1002 | 0 | 0 | 4.81 | 0.071 | 0.011 | 1 | 2291 | 2291 | 9.0641e-05 | 9.0641e-05 | 1 | 365 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD007 | Citipower | Urban | 1547 | 0 | 0 | 8.438 | 4.316 | 0 | 7 | 121875 | 121875 | 0.0039132 | 0.0039132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD011 | Citipower | Urban | 704 | 6.144 | 0.789 | 0 | 0 | 0 | 1 | 2749 | 2749 | 0.0025129 | 0.0025129 | 2 | 7095 | 0.0001469 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD012 | Citipower | Urban | 702 | 0 | 0 | 4.192 | 2.074 | 0.356 | 2 | 53499 | 53499 | 0.0025223 | 0.0025223 | 1 | 9180 | 0.00016878 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD013 | Citipower | Urban | 834 | 7.215 | 0.884 | 0 | 0 | 0 | 4 | 18527 | 4552 | 0.00021566 | 0.00013752 | 2 | 27615 | 0.00023442 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD021 | Citipower | Urban | 435 | 4.5 | 0.212 | 0 | 0 | 0 | 1 | 3268 | 3268 | 0.00019066 | 0.00019066 | 1 | 12600 | 0.00013127 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD022 | Citipower | Urban | 753 | 6.518 | 0.314 | 0 | 0 | 0 | 2 | 169222 | 997 | 0.0025098 | 1.2502e-05 | 2 | 5969 | 7.1887e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD031 | Citipower | Urban | 1002 | 6.576 | 0.292 | 0 | 0 | 0 | 3 | 223806 | 5358 | 0.0065449 | 0.00024692 | 1 | 6240 | 7.5013e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WD032 | Citipower | Urban | 787 | 5.376 | 0.847 | 0 | 0 | 0 | 1 | 2019 | 1188 | 4.0632e-05 | 3.7506e-05 | 1 | 15225 | 0.00010939 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG011 | Citipower | CBD | 1 | 0 | 0 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG012 | Citipower | CBD | 176 | 0 | 5.089 | 5.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG013 | Citipower | CBD | 306 | 0 | 6.969 | 3.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG014 | Citipower | Urban | 155 | 1.441 | 0.875 | 3.191 | 0.758 | 0 | 1 | 5674 | 5674 | 0.00048446 | 0.00048446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG016 | Citipower | Urban | 1 | 0 | 0.054 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG017 | Citipower | Urban | 1 | 0 | 1.739 | 3.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG018 | Citipower | CBD | 0 | 0 | 0 | 0.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG021 | Citipower | CBD | 189 | 0 | 6.671 | 0.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG022 | Citipower | CBD | 1 | 0 | 4.08 | 2.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG023 | Citipower | Urban | 1 | 0 | 1.735 | 3.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG024 | Citipower | Urban | 138 | 2.735 | 5.316 | 5.96 | 0 | 1.596 | 0 | 0 | 0 | 0 | 0 | 2 | 5692 | 6.2511e-05 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG026 | Citipower | Urban | 1 | 0 | 6.813 | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG027 | Citipower | Urban | 0 | 0 | 0.46 | 0.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG028 | Citipower | Urban | 11 | 0 | 0.782 | 1.353 | 0 | 0.176 | 0 | 0 | 0 | 0 | 0 | 1 | 220 | 3.1255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG032 | Citipower | Urban | 133 | 0 | 6.873 | 4.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG033 | Citipower | Urban | 0 | 0 | 1.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG034 | Citipower | CBD | 112 | 0 | 1.415 | 4.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WG036 | Citipower | CBD | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WMTS-NM011 | Citipower | Urban | 1 | 0.123 | 0.009 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
WMTS-NM035 | Citipower | Urban | 0 | 0.123 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO
Contents
Contents

## 6c. Causes of Outages and Worst
CitiPower Pty
Cause of Outages and Worst Served 15 per cent customers
2013
Table 1 Causes of Unplanned Sustained Outages
Cause of outage | Number of outages
Weather | 37075
Equipment failure | 94595
Operational error | 9887
Vegetation | 45922
Animals | 10485
Third party impacts | 8999
Transmission failure | 11831
Load shedding | 0
Inter-distributor connection failure | 257
Other | 6540
Table 2 Minutes off Supply for Worst Served 15 per cent customers
Minutes off supply (worst 15%) | 439.8234
The AER will use the ESCV's definition of minutes of supply for worst served 15% of customers. This is defined as the total annual minutes off supply (SAIDI for planned and unplanned sustained interruptions) experienced by the 15% of customers in the distribution business area connected by those feeders experiencing the longest time off supply.
Contents