## Instructions
Electricity Distribution Network Service Provider
Category Analysis RIN
This template is to be used by Endeavour Energy to fulfil its reporting obligations to the AER.
INSTRUCTIONS
GENERAL | Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting.
CONFIDENTIAL INFORMATION | Please use the macro at the top of each worksheet to identify confidential information in the confidential workbook.
-Do this by selecting the cell or cells that contain confidential information and then run the Mark selection as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential. -To reverse this, select the cell or cells and run the Return selection to NON-CONFIDENTIAL macro.
RESPONSES | Please return four (4) files to the AER: 1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 2. An actual and an estimate version with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response. Use the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public.
AMENDMENTS | If an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. NSPs must identify the reason for the amendments in the Amendment Reason box on the Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. .
NSP may use Amended Data macro to highlight cells that contain amended data. NB: if data is also CONFIDENTIAL, re-apply the Confidentiality macro after applying the Amended macro
Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER
UNITS OF MEASURE | All amounts are to be unrounded and reported on a one for one basis: that is 1000 is to be entered as '1000'. Applicable units of measure may be identified in the table column headings or row descriptors.
INPUT / NON-INPUT CELLS
Yellow = Input cell (mandatory)
Darker yellow = input cell (mandatory)
Orange = input cell (if data available)
Grey = Not applicable/No inputs required
PLEASE DO NOT ENTER TEXT into cells that are to contain numeric data.
NAVIGATION | Many tables in the worksheets have been "grouped" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin (for Row groupings) or above the columns (for column groupings).

## CONTENTS
CATEGORY ANALYSIS
Endeavour Energy
2019-20
CONTENTS
| TEMPLATE DATED | 2020-06-01
| SUBMISSION | Business & other details
| EXPENDITURE | 2.1 Expenditure summary
2.2 Repex
2.3(a) Augex
2.3(b) Augex
2.5 Connections
2.6 Non-network
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency Response
2.10 Overheads
2.10(A) Overheads
2.11 Labour
2.12 Input tables
| SERVICE | 6.3 Sustained interruptions
| ALTERNATIVE CONTROL | 4.1 Public lighting
4.2 Metering
4.3 Fee-based services
4.4 Quoted services
| NETWORK | 5.2 Asset Age Profile
5.3 MD - Network level
5.4 MD & utilisation-Spatial

## Business & other details
CATEGORY ANALYSIS
Endeavour Energy
2019-20
BUSINESS & OTHER DETAILS
INSTRUCTIONS
Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells.
SUBMISSION PARTICULARS INPUT SHEET
ENTITY DETAILS
Business Name
| Short name |  |  | Endeavour Energy
| ACN/ABN |  |  | 11247365823
| Business Address | [6 empty] | Postal Address
| Address 1 |  |  | 51 Huntingwood Drive |  |  | Address 1 | PO Box 811
| Address 2 | [5 empty] | Address 2
| Suburb |  |  | HUNTINGWOOD |  |  | Suburb | SEVEN HILLS
| State |  |  | NSW | Post code |  | State | NSW | Post code
`
Contact Names
Name
Phone
Email
REGULATORY CONTROL PERIODS
|  |  | Commencing year | 2019-20
ANNUAL RINS
|  |  | Final year | 2023-24
SUBMISSION DETAILS
|  |  | RIN type | Category Analysis
|  |  | Source | Reporting
|  | THIS FILE | Data Quality | Consolidated
|  |  | Confidentiality Status | Public
|  |  | Amended RIN Amendment Reason | 31032023 - #15,086,532 - Endeavour Energy reported Type 5 meter data as Type 4 in tables 4.2.1 and 4.2.2. The classification has been amended.
|  |  | Submission Date | 2023-03-03
Contents
Instructions

## 2.1 Expenditure summary
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.1 EXPENDITURE SUMMARY & RECONCILIATION
There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.1.1 - STANDARD CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2019-20
Replacement expenditure | 110221356
Connections | 35155359
Augmentation Expenditure | 35850850.581
Non-network | 62580402.54
Capitalised network overheads | 51899095.2453
Capitalised corporate overheads | 33197368.9877
Metering | 0
Public Lighting | 0
balancing item | 94604121.805
capcons (included in the above) | 94604121.805
TOTAL GROSS CAPEX (including capcons) | 423508554.159
2.1.2 - STANDARD CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2019-20
Vegetation management | 38003487
Maintenance | 40679530.2136
Emergency response | 27276019.8015
Non-network | 66584940.7728
Network overheads | 47899457.6113
Corporate overheads | 6329358.9221
Metering | 0
Public Lighting | 0
balancing item
TOTAL OPEX | 226772794.3214
2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2019-20
Connections | 0
Capitalised network overheads | 1362889
Capitalised corporate overheads | 0
Metering | 0
Public lighting | 2903174.6394
Fee and quoted | 0
balancing item
TOTAL CAPEX | 4266063.6394
2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2019-20
Connections | 0
Network overheads | 8752144.5027
Corporate overheads | 20807086.4675
Metering | 18440614.5425
Public lighting | 20953997.118
Fee and quoted | 27696466.9489
balancing item | -29559230.9703
TOTAL OPEX | 67091078.6094
2.1.5 - DUAL FUNCTION ASSETS CAPEX
EXPENDITURE ($0's)
2019-20
Replacement expenditure | 0
Connections | 0
Augmentation Expenditure | 0
Non-network | 0
Capitalised network overheads | 0
Capitalised corporate overheads | 0
balancing item | 0
capcons (included in the above) | 0
TOTAL GROSS CAPEX (including capcons) | 0
2.1.6 - DUAL FUNCTION ASSETS OPEX
EXPENDITURE ($0's)
2019-20
Vegetation management | 0
Maintenance | 0
Emergency response | 0
Non-network | 0
Network overheads | 0
Corporate overheads | 0
balancing item | 0
TOTAL OPEX | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.2 Repex
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.2 REPEX
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY
|  |  | EXPENDITURE ($0's) | ASSET REPLACEMENTS (0's) | ASSET FAILURES (0's)
ASSET GROUP | ASSET CATEGORY |  | 2019-20 | 2019-20 | 2019-20
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole |  | 234474.4 | 277 | 4
| ˂ = 1 kV; Wood |  | 4722534.5906 | 590 | 106
| > 1 kV & < = 11 kV; Wood |  | 6671353.45 | 834 | 98
| ˃ 11 kV & < = 22 kV; Wood |  | 118578.9253 | 15 | 0
| > 22 kV & < = 66 kV; Wood |  | 2397616.5796 | 193 | 1
| > 66 kV & < = 132 kV; Wood |  | 605583.5691 | 49 | 0
| > 132 kV; Wood |  | 0 | 0 | 0
| ˂ = 1 kV; Concrete |  | 116258.9029 | 14 | 1
| > 1 kV & < = 11 kV; Concrete |  | 561477.6558 | 55 | 6
| ˃ 11 kV & < = 22 kV; Concrete |  | 31706.9735 | 3 | 0
| > 22 kV & < = 66 kV; Concrete |  | 407617.7422 | 19 | 0
| > 66 kV & < = 132 kV; Concrete |  | 0 | 0 | 0
| > 132 kV; Concrete |  | 0 |  | 0
| ˂ = 1 kV; Steel |  | 194205.2127 | 27 | 1
| > 1 kV & < = 11 kV; Steel |  | 487494.7177 | 53 | 0
| ˃ 11 kV & < = 22 kV; Steel |  | 43597.0886 | 4 | 0
| > 22 kV & < = 66 kV; Steel |  | 85814.2615 | 4 | 0
| > 66 kV & < = 132 kV; Steel |  | 51079.9176 | 2 | 0
| > 132 kV; Steel |  | 0 | 0 | 0
| Other |  | 167122.1729 | 15 | 0
POLE TOP STRUCTURES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 0 | 0 | 90
| > 1 kV & < = 11 kV |  | 0 | 0 | 74
| ˃ 11 kV & < = 22 kV |  | 0 | 0 | 0
| > 22 kV & < = 66 kV |  | 0 | 0 | 1
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV |  | 2035972.9702 | 27.5131 | 346
| > 1 kV & < = 11 kV |  | 2662757.0891 | 35.9832 | 682
| ˃ 11 kV & < = 22 kV ; SWER |  | 111000.1463 | 2.7073 | 0
| ˃ 11 kV & < = 22 kV ; Single-Phase |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase |  | 225970.8198 | 3.0537 | 0
| > 22 kV & < = 66 kV |  | 10920457.7792 | 17.1463 | 8
| > 66 kV & < = 132 kV |  | 2381870.7154 | 3.8098 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 3425671.76 | 7.4269 | 262
| > 1 kV & < = 11 kV |  | 0 | 0 | 148
| > 11 kV & < = 22 kV |  | 0 | 0 | 6
| > 22 kV & < = 33 kV |  | 0 | 0 | 2
| > 33 kV & < = 66 kV |  | 0 | 0 | 0
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type |  | 2279250.4 | 4221 | 1611
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type |  | 0 | 0 | 0
| ˂ = 11 kV ; Residential ; Complex Type |  | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type |  | 0 | 0 | 0
| ˂ = 11 kV ; Subdivision ; Complex Type |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision |  | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 132 kV ; Subdivision |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 111778.2715 | 11 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 59176.732 | 4 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 874500.5948 | 24 | 184
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 517796.4048 | 14 | 32
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 994497.8569 | 19 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA |  | 2483146.23 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA |  | 17411.42 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA |  | 2355942.63 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; FUSE |  | 420705.18 | 137 | 616
| ˂ = 11 kV ; Switch |  | 8306361.84 | 565 | 490
| ˂ = 11 kV ; Circuit Breaker |  | 5976624.7686 | 17 | 42
| > 11 kV & < = 22 kV ; Switch |  | 8681.3524 | 2 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Switch |  | 21640.9035 | 1 | 2
| > 22 kV & < = 33 kV ; Circuit Breaker |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Switch |  | 43281.8071 | 2 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker |  | 152664.816 | 1 | 4
| > 66 kV & < = 132 kV ; Switch |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Circuit Breaker |  | 338390.8024 | 2 | 0
| > 132 kV ; Switch |  | 0 | 0 | 0
| > 132 kV ; Circuit Breaker |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road |  | 0 | 0 | 0
| Luminaires ; Minor Road |  | 0 | 0 | 0
| Brackets ; Major Road |  | 0 | 0 | 0
| Brackets ; Minor Road |  | 0 | 0 | 0
| Lamps ; Major Road |  | 0 | 0 | 0
| Lamps ; Minor Road |  | 0 | 0 | 0
| Poles / Columns ; Major Road |  | 0 | 0 | 0
| Poles / Columns ; Minor Road |  | 0 | 0 | 0
| Other |  | 2281685.79 | 636 | 544
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices |  | 486342.43 | 95 | 29
| Local Network Wiring Assets |  | 0 | 0 | 47
| Communications Network Assets |  | 4958774.99 | 242 | 163
| Master Station Assets |  | 0 | 0 | 0
| Communications Site Infrastructure |  | 657618.49 | 0 | 5
| Communications Linear Assets |  | 0 | 0 | 0
| AFLC |  | 0 | 0 | 50
| Other |  | 0 | 0 | 0
OTHER BY: DNSP DEFINED | Substation Establishment: Major Indoor |  | 73405.77 | 0 | 0
| Substation Establishment: Major Outdoor |  | 8056730.8484 | 0 | 0
| Substation Establishment: Medium Indoor |  | 3063547.0386 | 0 | 0
| Substation Establishment: Medium Outdoor |  | 5291581.2486 | 0 | 0
| Substation Establishment: Small Indoor |  | 563639.6067 | 0 | 0
| Substation Establishment: Small Outdoor |  | 1763860.4162 | 0 | 0
| Substation Establishment: Type A |  | 848774.9371 | 0 | 0
| Substation Establishment: Type B |  | 3262478.6645 | 0 | 0
| Distribution Sub - Chamber Type |  | 333279.6173 | 6 | 0
| Distribution OH Sub < 64KVA |  | 220250.2126 | 2 | 0
| Distribution OH Sub >= 64KVA |  | 44486.6274 | 2 | 0
| 11/22 - kiosk and pad mount <=500kVA Substn |  | 78098.8934 | 3 | 0
| 11/22 - kiosk and pad mount >500kVA Substn |  | 104003.7766 | 2 | 0
| 11/22 Switching Station |  | 398804.9027 | 7 | 0
| Capacitor Banks |  | 0 | 0 | 0
| Metering & Relays |  | 755969.08 | 0 | 0
| Reliability |  | 2803802.37 | 0 | 0
| Technology |  | 12647343.96 | 0 | 0
| Essential Spares |  | 186492.89 | 0 | 0
| Tower |  | 0 | 0 | 0
2.2.2 - SELECTED ASSET CHARACTERISTICS
|  |  | ASSET VOLUMES CURRENTLY IN COMMISSION | ASSET REPLACEMENTS (0's)
ASSET GROUP | METRIC | UNITS | 2019-20 | 2019-20
TOTAL POLES BY: FEEDER TYPE | Total CBD poles | Number | 0 | 0
| Total urban poles | Number | 79463.6167 | 548.0637
| Total rural long poles | Number | 5973.712 | 34.1548
| Total rural short poles | Number | 221816.6713 | 1294.7816
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH BY FEEDER TYPE | Conductors CBD | KM | 0 | 0
| Conductors urban | KM | 7700.3443 | 30.9566
| Conductors rural long | KM | 530.875 | 1.4692
| Conductors rural short | KM | 19893.3378 | 57.7876
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH MATERIAL TYPE | OH conductor LV ABC | KM | 2110.2599 | 0
| OH conductor steel | KM | 657.5209 | 15.2387
| OH conductor ACSR | KM | 6055.8716 | 16.3793
| OH conductor AAAC | KM | 1382.3499 | 1.2829
| OH conductor AAC | KM | 11578.0659 | 28.6421
| OH conductor HDBC | KM | 6340.489 | 28.6704
| Other | KM | 0 | 0
UNDERGROUND CABLES BY: CABLE LENGTH BY FEEDER TYPE | Cable CBD | KM | 0 | 0
| Cable urban | KM | 13614.4266 | 5.1426
| Cable rural long | KM | 1.2629 | 0.00049183
| Cable rural short | KM | 5886.2464 | 2.2838
TRANSFORMERS BY: TOTAL MVA | Total MVA replaced | MVA | 0 | 26.97
| Total MVA disposed of | MVA | 0 | 26.97
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(a) Augex
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.3 AUGEX PROJECT DATA
There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped. See the Instructions sheet on how to group or ungroup tables.
2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
SUBSTATION ID | SUBSTATION TYPE (drop down) | PROJECT ID | PROJECT TYPE (drop down) | PROJECT TRIGGER (drop down) | VOLTAGE (KV) | SUBSTATION RATING NORMAL CYCLIC (MVA) |  | SUBSTATION RATING N-1 EMERGENCY (MVA) |  | TRANSFORMERS |  |  | SWITCHGEAR |  | CAPACITORS |  |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | PRE | POST | PRE | POST | UNITS ADDED | MVA ADDED | EXPENDITURE ($0's) | UNITS ADDED | EXPENDITURE ($0's) | MVAR ADDED | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
Edmondson Park ZS | Zone substation | PR110 | New substation establishment | Demand growth | 33/11 | 0 | 70 | 0 | 35 | 2 | 70 | 1343470 | 23 | 787843.42 | 0 | 0 |  |  | 1889088.26 | 27854.5077 | 2699183.56 | 10317336.08 | 178562.9 | 17215484.22 | 2011/12, 2012/13, 2013/14, 2014/15, 2015/16, 2016/17, 2017/18, 2018/19, 2019/20, | 0 | 1375831.61 | 0 | 0 | 0
Liverpool ZS | Zone substation | PR673 | Other | Demand growth | 33/11 | 105 | 105 | 70 | 70 | 0 | 0 | 0 | 6 | 692408.37 | 0 | 0 |  |  | 1342260.74 | 22947.6605 | 1920512.18 | 1707125.58 | 225634.88 | 5887941.75 | 2014/15, 2015/16, 2016/17, 2017/18, 2018/19, 2019/20, | 0 | 1574898.75 | 0 | 0 | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
|  | Non material projects - [actual] | [21 empty] | 433711.69 | 2015/16
AUG232_1 | AUG232_2 | AUG232_3 | AUG232_4 | AUG232_5 | AUG232_6 | ED_AUG232_00001 | ED_AUG232_00002 | ED_AUG232_00003 | ED_AUG232_00004 | ED_AUG232_00005 | ED_AUG232_00006 | ED_AUG232_00007 | ED_AUG232_00008 | ED_AUG232_00009 | ED_AUG232_00010 | ED_AUG232_00011 | ED_AUG232_00012 | ED_AUG232_00013 | ED_AUG232_00014 | ED_AUG232_00015 | ED_AUG232_00016 | ED_AUG232_00017 | ED_AUG232_00018 | ED_AUG232_00019 | ED_AUG232_00020 | ED_AUG232_00021
2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
LINE ID | PROJECT ID | PROJECT TYPE | PROJECT TRIGGER |  | VOLTAGE (KV) | ROUTE LINE LENGTH ADDED |  |  |  | POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS) |  |  | OVERHEAD LINES |  |  | UNDERGROUND CABLES |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | KM ADDED |  |  |  | POLES/TOWERS ADDED | POLES/TOWERS UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
625, 626, | PR110 | New line on new route - single circuit | Demand growth | Demand growth | Other |  | 6.035 |  |  | 0 | 0 | 0 | 0 | 0 | 181884.46 | 0 | 0 | 204011.68 | 0 | 5890.75 | 384260.93 | 0 | 132569.58 | 902726.65 | 2011/12, 2012/13, 2013/14, 2014/15, 2015/16, 2016/17, 2017/18, 2018/19, 2019/20, | 0 | 291979.02 | 0 | 0 | 0 | New line on new route - single circuit
[24 empty] | 0 | [6 empty] | New line on new route - dual circuit
[24 empty] | 0 | [6 empty] | New line on new route - other
[24 empty] | 0 | [6 empty] | Line rebuild over existing route - single circuit
[24 empty] | 0 | [6 empty] | Line rebuild over existing route - dual circuit
[24 empty] | 0 | [6 empty] | Reconductor - Single circuit
[24 empty] | 0 | [6 empty] | Reconductor - Dual circuit
[24 empty] | 0 | [6 empty] | Reconductor - Other
[24 empty] | 0 | [6 empty] | Line upgrade - raising/retensoring
[24 empty] | 0 | [6 empty] | Line upgrade - voltage upgrade
[24 empty] | 0 | [6 empty] | Line upgrade - capacity
[24 empty] | 0 | [6 empty] | String spare circuit
[24 empty] | 0 | [6 empty] | Other
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Non material projects - [actual]
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(b) Augex
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.3 AUGEX DATA
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS.
DESCRIPTOR METRICS
PROJECT TYPE |  | UNITS ADDED (0's) | UNITS UPGRADED (0's)
| UNITS | 2019-20 | 2019-20
HV Feeder Augmentations - Overhead Lines | Circuit line length in km | 12.395 | 18.914
HV Feeder Augmentations - Underground Cables | Circuit line length in km | 26.435 | 0.1
LV Feeder Augmentations - Overhead Lines | Circuit line length in km | 0.50239 | 0.33492
LV Feeder Augmentations - Underground Cables | Circuit line length in km | 0.7566 | 0.068781
Distribution Substation Augmentations - Pole Mounted | Number | 1.0429 | 8.1715
Distribution Substation Augmentations - Ground Mounted | Number | 0.71794 | 5.8409
Distribution Substation Augmentations - Indoor | Number | 0 | 0.17417
COST METRICS
TOTAL DIRECT EXPENDITURE - Project Type |  | EXPENDITURE ($0's)
2019-20
HV Feeder Augmentations - Overhead Lines |  | 2827918.5013
HV Feeder Augmentations - Underground Cables |  | 4664734.5887
HV Feeder Non-Material Projects |  | 0
LV Feeder Augmentations - Overhead Lines |  | 83982.189
LV Feeder Augmentations - Underground Cables |  | 335928.756
LV Feeder Non-Material Projects |  | 84244.189
Distribution Substation Augmentations - Pole Mounted |  | 188545.172
Distribution Substation Augmentations - Ground Mounted |  | 280305.6894
Distribution Substation Augmentations - Indoor |  | 6983.1545
2.3.4 - AUGEX DATA - TOTAL EXPENDITURE
AUGMENTATION CAPEX (As incurred) |  | EXPENDITURE ($0's)
2019-20
Subtransmission Substations, Switching Stations, Zone Substations |  | 14115090.6488
Subtransmission Lines |  | 13251117.6922
HV Feeders |  | 7492653.09
HV Feeders - Land Purchases and Easements |  | 0
Distribution Substations |  | 475834.016
Distribution Substations - Land Purchases And Easements |  | 12000
LV Feeders |  | 504155.134
LV Feeders - Land Purchases And Easements |  | 0
Other Assets |  | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.5 Connections
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.5 CONNECTIONS
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.5.1 - DESCRIPTOR METRICS
<<<GROUP-ROW>>>
VOLUMES AND EXPENDITURE
CONNECTION SUBCATEGORY | DESCRIPTOR METRIC | UNITS | 2019-20
RESIDENTIAL | Underground connections | 0's | 6973
| Overhead connections | 0's | 955
| Distribution substation installed | MVA added | 34.543
| Distribution substations installed | 0's | 67
| Distribution substation installed | total spend $0s | 3646184
| Augmentation HV | net circuit km added | 12.28
| Augmentation HV | total spend $0s | 1823432
| Augmentation LV | net circuit km added | 6.16
| Augmentation LV | total spend $0s | 794201
| Mean days to connect residential customer with LV single phase connection | 0's | 0
| Volume of GSL breaches for residential customers | 0's | 0
| Volume of customer complaints relating to connection services | 0's | 0
| GSL payments | $0s | 0
COMMERCIAL/INDUSTRIAL | Underground connections | 0's | 3195
| Overhead connections | 0's | 908
| Distribution substation installed | MVA added | 109.361
| Distribution substations installed | 0's | 127
| Distribution substation installed | total spend $0s | 8711029
| Augmentation HV | net circuit km added | 27.85
| Augmentation HV | total spend $0s | 3673879
| Augmentation LV | net circuit km added | 5.9
| Augmentation LV | total spend $0s | 646762
SUBDIVISION | Underground connections | 0's | 11621
| Overhead connections | 0's | 365
| Distribution substation installed | MVA added | 36.752
| Distribution substations installed | 0's | 91
| Distribution substation installed | total spend $0s | 6966496
| Augmentation HV | net circuit km added | 44.8
| Augmentation HV | total spend $0s | 8162749
| Augmentation LV | net circuit km added | 3.76
| Augmentation LV | total spend $0s | 551732
| Cost per lot ($) | $0s | 1308.2744
EMBEDDED GENERATION | Underground connections | 0's | 5498
| Overhead connections | 0's | 8955
| Distribution substation installed | MVA added | 0
| Distribution substations installed | 0's | 0
| Distribution substation installed | total spend $0s | 0
| Augmentation HV | net circuit km added | 0
| Augmentation HV | total spend $0s | 0
| Augmentation LV | net circuit km added | 0
| Augmentation LV | total spend $0s | 0
2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION
|  | EXPENDITURE ($0's) | VOLUMES (0's)
CONNECTION SUBCATEGORY | CONNECTION CLASSIFICATION | 2019-20 | 2019-20
RESIDENTIAL | Simple connection LV | 6263817 | 7928
| Complex connection LV | 0 | 0
| Complex connection HV | 0 | 0
COMMERCIAL/INDUSTRIAL | Simple connection LV | 0 | 0
| Complex connection HV (customer connected at LV, minor HV works) | 13031670 | 4103
| Complex connection HV (customer connected at LV, upstream asset works) | 0 | 0
| Complex connection HV (customer connected at HV) | 0 | 0
| Complex connection sub-transmission | 0 | 0
SUBDIVISION | Complex connection LV | 0 | 0
| Complex connection HV (no upstream asset works) | 0 | 0
| Complex connection HV (with upstream asset works) | 15680977 | 11986
EMBEDDED GENERATION | Simple connection LV | 0 | 14453
| Complex connection HV (small capacity) | 0 | 0
| Complex connection HV (large capacity) | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.6 Non-network
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.6 NON NETWORK EXPENDITURE
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.6.1 - NON-NETWORK EXPENDITURE
EXPENDITURE ($0's)
SERVICE SUBCATEGORY | ASSET CATEGORY |  |  | 2019-20
OPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 2725542.7609
| Recurrent expenditure |  |  | 33866301.8986
| Non-recurrent expenditure |  |  | 3213245.8352
MOTOR VEHICLES | Car |  |  | 247477.0247
| Light commercial vehicle |  |  | 2693992.6455
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 3424123.316
| Heavy commercial vehicle |  |  | 4964978.8082
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 15449278.4838
OTHER | Other expenditure |  |  | 0
OTHER - DNSP nominated
CAPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 18369.7465
| Recurrent expenditure |  |  | 3811317.1001
| Non-recurrent expenditure |  |  | 45592093.3334
MOTOR VEHICLES | Car |  |  | 0
| Light commercial vehicle |  |  | 0
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 0
| Heavy commercial vehicle |  |  | 7520163.15
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 3400628.38
OTHER | Other expenditure |  |  | 2237830.83
OTHER - DNSP nominated
2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE
VOLUMES (0's)
NON-NETWORK CATEGORY | DESCRIPTOR METRIC |  |  | 2019-20
IT & COMMUNICATIONS | Employee numbers |  |  | 1707
| User numbers |  |  | 3113
| Number of devices |  |  | 4736
2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES
VOLUMES / %
NON-NETWORK CATEGORY | ASSET CATEGORY | DESCRIPTOR METRIC | UNITS | 2019-20
MOTOR VEHICLES | CAR | Average kilometres travelled | 0's | 21366.48
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 50
|  | Number in fleet | 0's | 50
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 93.88%
| LIGHT COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 20436.2174
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 345
|  | Number in fleet | 0's | 345
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 93.88%
| ELEVATED WORK PLATFORM (LCV) | Average kilometres travelled | 0's | 0
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 0
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 0%
| ELEVATED WORK PLATFORM (HCV) | Average kilometres travelled | 0's | 16740.6125
|  | Number purchased | 0's | 9
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 80
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 93.88%
| HEAVY COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 28835.7414
|  | Number purchased | 0's | 5
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 216
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 93.88%
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.7 Vegetation management
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.7 VEGETATION MANAGEMENT
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Please enter a description for each Zone in table 2.7.1 - Urban and CBD. The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2.
` | 2.7.1 - DESCRIPTOR METRICS BY ZONE
URBAN AND CBD
2019-20
| ZONES | ASSET | UNITS
| Bowenfels | Route line length within zone | km | 198.9514
|  | Number of maintenance spans | 0's | 702
|  | Total length of maintenance spans | km | 39.1958
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 17.4392
|  | Average frequency of cutting cycle | years | 1.3182
| Bowral | Route line length within zone | km | 1342.6755
|  | Number of maintenance spans | 0's | 2219
|  | Total length of maintenance spans | km | 135.6694
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 22.2242
|  | Average frequency of cutting cycle | years | 1.2159
| Hills | Route line length within zone | km | 1742.6756
|  | Number of maintenance spans | 0's | 20478
|  | Total length of maintenance spans | km | 963.1496
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 17.8646
|  | Average frequency of cutting cycle | years | 1.1996
| Hoxton Park | Route line length within zone | km | 1342.6755
|  | Number of maintenance spans | 0's | 11474
|  | Total length of maintenance spans | km | 571.995
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 17.9158
|  | Average frequency of cutting cycle | years | 1.217
| Katoomba | Route line length within zone | km | 401.7668
|  | Number of maintenance spans | 0's | 8548
|  | Total length of maintenance spans | km | 403.2728
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 24.8894
|  | Average frequency of cutting cycle | years | 1.0893
| Narellan | Route line length within zone | km | 895.8374
|  | Number of maintenance spans | 0's | 4154
|  | Total length of maintenance spans | km | 259.9015
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 18.2358
|  | Average frequency of cutting cycle | years | 1.1389
| Nowra | Route line length within zone | km | 753.147
|  | Number of maintenance spans | 0's | 4646
|  | Total length of maintenance spans | km | 258.4976
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 15.2761
|  | Average frequency of cutting cycle | years | 1.2122
| Penrith | Route line length within zone | km | 893.8701
|  | Number of maintenance spans | 0's | 8191
|  | Total length of maintenance spans | km | 404.2341
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 16.4427
|  | Average frequency of cutting cycle | years | 1.1059
| Shellharbour | Route line length within zone | km | 522.8281
|  | Number of maintenance spans | 0's | 3225
|  | Total length of maintenance spans | km | 153.4642
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 14.197
|  | Average frequency of cutting cycle | years | 1.24
| Springhill | Route line length within zone | km | 736.3657
|  | Number of maintenance spans | 0's | 5908
|  | Total length of maintenance spans | km | 264.0112
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 15.7842
|  | Average frequency of cutting cycle | years | 1.2329
| Windsor | Route line length within zone | km | 309.7247
|  | Number of maintenance spans | 0's | 1884
|  | Total length of maintenance spans | km | 122.7359
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 17.3075
|  | Average frequency of cutting cycle | years | 1.0833
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
RURAL
2019-20
| ZONES | ASSET | UNITS
| Bowenfels | Route line length within zone | km | 2182.7001
|  | Number of maintenance spans | 0's | 5271
|  | Total length of maintenance spans | km | 543.6024
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 25.0916
|  | Average frequency of cutting cycle | years | 1.9786
| Bowral | Route line length within zone | km | 182.0178
|  | Number of maintenance spans | 0's | 5263
|  | Total length of maintenance spans | km | 611.6418
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 21.6321
|  | Average frequency of cutting cycle | years | 1.8117
| Hills | Route line length within zone | km | 250.1743
|  | Number of maintenance spans | 0's | 2793
|  | Total length of maintenance spans | km | 197.7842
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 21.2629
|  | Average frequency of cutting cycle | years | 1
| Hoxton Park | Route line length within zone | km | 182.0178
|  | Number of maintenance spans | 0's | 1681
|  | Total length of maintenance spans | km | 134.5473
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 16.5342
|  | Average frequency of cutting cycle | years | 1.15
| Katoomba | Route line length within zone | km | 232.127
|  | Number of maintenance spans | 0's | 3158
|  | Total length of maintenance spans | km | 219.79
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 36.801
|  | Average frequency of cutting cycle | years | 1.3333
| Narellan | Route line length within zone | km | 1722.2973
|  | Number of maintenance spans | 0's | 6043
|  | Total length of maintenance spans | km | 531.3981
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 20.7274
|  | Average frequency of cutting cycle | years | 1.6468
| Nowra | Route line length within zone | km | 1680.2314
|  | Number of maintenance spans | 0's | 8197
|  | Total length of maintenance spans | km | 723.0091
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 22.9735
|  | Average frequency of cutting cycle | years | 1.7401
| Penrith | Route line length within zone | km | 264.3786
|  | Number of maintenance spans | 0's | 2514
|  | Total length of maintenance spans | km | 178.1878
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 23.6049
|  | Average frequency of cutting cycle | years | 1.0667
| Shellharbour | Route line length within zone | km | 473.4425
|  | Number of maintenance spans | 0's | 2404
|  | Total length of maintenance spans | km | 221.7125
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 20.7247
|  | Average frequency of cutting cycle | years | 1.9375
| Springhill | Route line length within zone | km | 260.1107
|  | Number of maintenance spans | 0's | 4202
|  | Total length of maintenance spans | km | 270.8004
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 30.0715
|  | Average frequency of cutting cycle | years | 1.6508
| Windsor | Route line length within zone | km | 1198.2043
|  | Number of maintenance spans | 0's | 10151
|  | Total length of maintenance spans | km | 824.2319
|  | Length of vegetation corridors | km | 0
|  | Average number of trees per maintenance span | 0's | 23.1188
|  | Average frequency of cutting cycle | years | 1.3244
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
2.7.2 - EXPENDITURE METRICS BY ZONE
EXPENDITURE ($0's)
| ZONES | SERVICE SUBCATEGORY |  | 2019-20
| Bowenfels | Tree trimming (excluding hazard trees) |  | 1822875.58
|  | Hazard tree cutting |  | 1802488.36
|  | Ground clearance |  | 227859.45
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 227859.45
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 36487
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Bowral | Tree trimming (excluding hazard trees) |  | 2094155.69
|  | Hazard tree cutting |  | 201507.19
|  | Ground clearance |  | 261769.46
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 261769.46
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 965.4
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Hills | Tree trimming (excluding hazard trees) |  | 3306962.32
|  | Hazard tree cutting |  | 160526.68
|  | Ground clearance |  | 413370.29
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 413370.29
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Hoxton Park | Tree trimming (excluding hazard trees) |  | 1156132.05
|  | Hazard tree cutting |  | 176605.88
|  | Ground clearance |  | 144516.51
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 144516.51
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Katoomba | Tree trimming (excluding hazard trees) |  | 2648908.57
|  | Hazard tree cutting |  | 703325.88
|  | Ground clearance |  | 331113.57
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 331113.57
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Narellan | Tree trimming (excluding hazard trees) |  | 1502303.96
|  | Hazard tree cutting |  | 432670.73
|  | Ground clearance |  | 187787.99
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 187787.99
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Nowra | Tree trimming (excluding hazard trees) |  | 4341508.13
|  | Hazard tree cutting |  | 517792.76
|  | Ground clearance |  | 542688.52
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 542688.52
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 53885.15
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Penrith | Tree trimming (excluding hazard trees) |  | 1554212.77
|  | Hazard tree cutting |  | 154853.36
|  | Ground clearance |  | 194276.6
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 194276.6
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Shellharbour | Tree trimming (excluding hazard trees) |  | 1599818.82
|  | Hazard tree cutting |  | 166082.66
|  | Ground clearance |  | 199977.35
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 199977.35
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Springhill | Tree trimming (excluding hazard trees) |  | 1542313.49
|  | Hazard tree cutting |  | 139353.73
|  | Ground clearance |  | 192789.19
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 192789.19
|  | Audit |  | 113418.73
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 113168.45
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| Windsor | Tree trimming (excluding hazard trees) |  | 2526297.75
|  | Hazard tree cutting |  | 559270.36
|  | Ground clearance |  | 315787.22
|  | Vegetation corridor clearance |  | 0
|  | Inspection |  | 315787.22
|  | Audit |  | 114193.36
|  | Contractor liaison expenditure |  | 0
|  | Tree replacement program costs |  | 0
|  | Other vegetation management costs not specified in sheet |  | 128796.49
| ZONE 12 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 13 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 14 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 15 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 16 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 17 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 18 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS
VOLUMES (0's)
| DESCRIPTOR METRIC |  |  | 2019-20
| Number of fire starts caused by vegetation grow-ins (NSP responsibility) |  |  | 1
| Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility) |  |  | 0
| Number of fire starts caused by vegetation grow-ins (other party responsibility) |  |  | 0
| Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility) |  |  | 47
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.8 Maintenance
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.8 MAINTENANCE
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
|  |  |  | ASSET QUANTITY (0's) |  | AVERAGE AGE OF ASSET GROUP | INSPECTION CYCLE (YEARS) | MAINTENANCE CYCLE (YEARS)
|  |  |  | AT YEAR END | INSPECTED / MAINTAINED
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2019-20 | 2019-20 | 2019-20
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 427576 | 78534 | 29.1026 | 5.5 | 0
| Service lines | Number of customers | Number | 800818 | 0 | 24.2632 | 0 | 0
Pole inspection and treatment | All poles | Number of poles | Number | 427576 | 78534 | 29.1026 | 5.5 | 0
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 36484.0748 | 393.7 | 28.524 | 1 to 12 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 24999.9086 | 0 | 19.3533 | 0 | 0
| 33 KV and above | Length (KM) | KM | 407.4979 | 8827.0085 | 18.4223 | 1 week to 1 year | 0
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 0 | 0 | 0 | 0 | 0
| Non-CBD | Length (KM) | KM | 25407.4065 | 8827.0085 | 19.2875 | 1 week to 1 year | 0
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 32382 | 1 | 22.6349 | 0 | 0
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 81447 | 825 | 0 | 1 to 5 | 3 to 10
| Distribution substation - other equipment | Earth mat | Number | 0 | 0 | 0 | 0 | 0
| Distribution substation - property | Number of distribution substation properties maintained | Number | 33638 | 3856 | 29.9159 | 1 to 3 | 0
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 453 | 260 | 27.1764 | 0.5 | 7
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 278 | 39 | 0 | 0.5 | 6
| Transformers - HV | Number of HV transformers | Number | 0 | 0 | 0 | 0 | 0
| Zone substation - other equipment | <DNSP to nominate> | Number | 0 | 0 | 0 | 0 | 0
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 202 | 2159 | 33.5049 | 0.5 to 2 | 0
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 224993 | 14460 | 25.3408 | 0 | 3 to 6
| Major roads | Number of public lights maintained | Number | 0 | 0 | 0 | 0 | 0
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 366 | 30 | 24.0443 | 0.5 | 4
Protection systems maintenance | Protection systems | Number of systems | Number | 6539 | 2377 | 0 | 0 | 0.5 to 6
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets | <DNSP to nominate> | Number | 0 | 0 | 0 | 0 | 0
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 0 | 0 |  | 0 | 0
Ground clearance - access tracks | Access tracks | Number | Number | 0 | 0 |  | 0 | 0
Other | Nil | Nil
2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
EXPENDITURE ($0'S)
|  |  |  | ROUTINE MAINTENANCE | NON-ROUTINE MAINTENANCE
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2019-20 | 2019-20
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 0 | 0
| Service lines | Number of customers | Number | 0 | 0
Pole inspection and treatment | All poles | Number of poles | Number | 8884576.07 | 425796.94
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 1079179.31 | 8113798.3767
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 2519.06 | 891087.15
| 33 KV and above | Length (KM) | KM | 697598.93 | 992575.57
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 0 | 0
| Non-CBD | Length (KM) | KM | 700117.99 | 1883662.72
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 0 | 104481.0121
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 610702.1845 | 38509.1824
| Distribution substation - other equipment | Earth mat | Number | 167894.8455 | 651614.1055
| Distribution substation - property | Number of distribution substation properties maintained | Number | 0 | 0
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 201497.6357 | 177762.3364
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 42974.451 | 6128.8882
| Transformers - HV | Number of HV transformers | Number | 0 | 0
| Zone substation - other equipment | <DNSP to nominate> | Number | 5230326.3632 | 2928320.0554
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 0 | 374498.61
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 0 | 0
| Major roads | Number of public lights maintained | Number | 0 | 0
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 0 | 0
Protection systems maintenance | Protection systems | Number of systems | Number | 466311.2 | 252370.13
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets | <DNSP to nominate> | Number | 0 | 0
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 0 | 0
Ground clearance - access tracks | Access tracks | Number | Number | 0 | 0
Other | Nil | Nil |  | 450463.79 | 7888544.0169
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.9 Emergency Response
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.9 EMERGENCY RESPONSE
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)
EXPENDITURE ($0's)
2019-20
(A) TOTAL EMERGENCY RESPONSE EXPENDITURE
Total Expenditure | 27276019.8015
(B) MAJOR EVENTS O&M EXPENDITURE
WIND STORM 9TH AUGUST 2019 | 248001.12
WIND STORM 6TH-7TH SEPTEMBER 2019 | 1021343.1
STORMS 26TH NOVEMBER 2019 | 230043.26
STORMS 9TH FEBRUARY 2020 | 1516879.96
STORMS 18TH FEBRUARY 2020 | 843507.54
(C) MAJOR EVENT DAYS O&M EXPENDITURE
2019-08-09 | 248001.12
2019-09-06 | 1021343.1
2019-11-26 | 230043.26
2020-02-09 | 1516879.96
2020-02-18 | 843507.54
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10 Overheads
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.10 OVERHEADS
Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. Endeavour Energy is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If Endeavour Energy is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. Endeavour Energy is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN. |  | Choose Response drop down selection
Worksheet 2.10A
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Instructions Please enter a description for each expenditure category as currently reported under Endeavour Energy's annual RIN.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2019-20
NETWORK OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED NETWORK OVERHEADS
Standard Control Services
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2019-20
CORPORATE OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED CORPORATE OVERHEADS
Standard Control Services
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10(A) Overheads
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.10(A) OVERHEADS
This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options.
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2019-20
OPEX
Standard Control Services | Total | 47899458
Alternative Control Services | Total | 8752145
CAPEX
Standard Control Services | Total | 51899095.2453
Alternative Control Services | Total | 1362889
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total | 0
Unregulated Services | Total | 1059506
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2019-20
OPEX
Standard Control Services | Total | 6329358.9221
Alternative Control Services | Total | 20807086
CAPEX
Standard Control Services | Total | 33197369
Alternative Control Services | Total | 0
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total | 0
Unregulated Services | Total | 6076677
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.11 Labour
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.11 LABOUR
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.11.1 - COST METRICS PER ANNUM
|  | ASL (0's) | TOTAL LABOUR EXPENDITURE ($0's) | AVERAGE PRODUCTIVE WORK HOURS PER ASL (0's) | STAND-DOWN OCCURENCES PER ASL (0's)
|  | 2019-20 | 2019-20 | 2019-20 | 2019-20
INTERNAL LABOUR EXPENDITURE
CORPORATE OVERHEADS | Executive manager | 4.283 | 2497055.9893 | 1695.6762 | 0
| Senior manager | 13.4694 | 2079180.4195 | 1698.4655 | 0
| Manager | 94.5506 | 13110151.3479 | 1679.151 | 0
| Professional | 104.77 | 14249542.6223 | 1675.6638 | 0
| Semi professional | 60.6476 | 5699236.0137 | 1574.6786 | 0
| Support staff | 33.357 | 4346228.6283 | 1583.5278 | 0
| Intern, junior staff, apprentice | 3.2368 | 181314.3784 | 1553.2052 | 0
NETWORK OVERHEADS | Executive manager | 1.0388 | 388646.1402 | 1621.4436 | 0
| Senior manager | 4.5436 | 1053492.1635 | 1692.2327 | 0
| Manager | 144.4213 | 20660790.5132 | 1682.2438 | 1.1856
| Professional | 132.4696 | 20624006.6644 | 1638.9431 | 0.15316
| Semi professional | 98.336 | 14013969.4225 | 1603.4128 | 1.5885
| Support staff | 73.2447 | 10352198.7317 | 1540.036 | 0.01383
| Intern, junior staff, apprentice | 0 | 0 | 0 | 0
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker | 458.6025 | 60895655.281 | 1644.9071 | 8.3324
| Skilled non electical worker | 93.6115 | 11647287.3959 | 1594.9733 | 8.0448
| Apprentice | 20.4007 | 1774605.388 | 1625.3269 | 2.3529
| Unskilled worker | 37.5441 | 4090180.4625 | 1584.5388 | 8.0549
2.11.2 - DESCRIPTOR METRICS
|  | ORDINARY TIME (0's) |  | OVERTIME (0's)
|  | PER ASL | HOURLY RATE PER ASL | PER ASL | HOURLY RATE PER ASL
|  | 2019-20 | 2019-20 | 2019-20 | 2019-20
AVERAGE PRODUCTIVE WORK HOURS PER ASL
CORPORATE OVERHEADS | Executive manager | 1695.6762 | 425.5351 | 0 | 421.0869
| Senior manager | 1698.4655 | 187.3934 | 0 | 183.9417
| Manager | 1679.151 | 121.0641 | 3.7145 | 122.0862
| Professional | 1675.6638 | 101.7809 | 3.6498 | 103.4548
| Semi professional | 1574.6786 | 78.1734 | 12.7665 | 80.9454
| Support staff | 1583.5278 | 71.4283 | 1.241 | 74.3803
| Intern, junior staff, apprentice | 1553.2052 | 68.5452 | 0 | 71.4077
NETWORK OVERHEADS | Executive manager | 1621.4436 | 332.8831 | 0 | 326.369
| Senior manager | 1692.2327 | 206.8929 | 7.3871 | 202.3388
| Manager | 1682.2438 | 115.7309 | 94.1973 | 118.4008
| Professional | 1638.9431 | 98.0646 | 26.0255 | 102.656
| Semi professional | 1603.4128 | 85.5215 | 113.3403 | 89.0566
| Support staff | 1540.036 | 68.326 | 81.1159 | 70.9412
| Intern, junior staff, apprentice | 0 | 0 | 0 | 0
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker | 1644.9071 | 77.9856 | 279.4455 | 80.5604
| Skilled non electical worker | 1594.9733 | 73.3062 | 265.2617 | 76.088
| Apprentice | 1625.3269 | 49.3317 | 1.7635 | 51.3917
| Unskilled worker | 1584.5388 | 57.586 | 286.8531 | 59.6297
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.12 Input tables
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
2.12 INPUT TABLES
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.12.1 - INPUT TABLES
|  | DIRECT MATERIAL EXPENDITURE | DIRECT LABOUR EXPENDITURE | CONTRACT EXPENDITURE | OTHER EXPENDITURE | RELATED PARTY CONTRACT EXPENDITURE | RELATED PARTY CONTRACT MARGIN EXPENDITURE
EXPENDITURE ($0's)
|  | 2019-20 | 2019-20 | 2019-20 | 2019-20 | 2019-20 | 2019-20
VEGETATION MANAGEMENT | Bowenfels | 6028.5108 | 757899.5177 | 3149979.1286 | 445877.9028 | 0 | 0
| Bowral | 4234.522 | 532360.6846 | 2212595.4776 | 313191.7359 | 0 | 0
| Hills | 6272.7878 | 788609.8234 | 3277617.1856 | 463945.0032 | 0 | 0
| Hoxton Park | 2577.4346 | 324032.997 | 1346744.725 | 190631.0134 | 0 | 0
| Katoomba | 5885.9375 | 739975.31 | 3075482.6039 | 435332.9586 | 0 | 0
| Narellan | 3529.8476 | 443769.5919 | 1844393.5109 | 261072.9395 | 0 | 0
| Nowra | 8629.462 | 1084889.0023 | 4509011.596 | 638248.2398 | 0 | 0
| Penrith | 3235.4159 | 406753.8772 | 1690548.9366 | 239296.3203 | 0 | 0
| Shellharbour | 3329.7707 | 418616.0849 | 1739850.5995 | 246274.945 | 0 | 0
| Springhill | 3349.9006 | 421146.8066 | 1750368.7755 | 247763.7873 | 0 | 0
| Windsor | 5475.8894 | 688424.4051 | 2861226.9263 | 405005.1792 | 0 | 0
ZONE 12
ZONE 13
ZONE 14
ZONE 15
ZONE 16
ZONE 17
ZONE 18
ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 0 | 0 | 0 | 0 | 0 | 0
| Pole inspection and treatment | 338839.3335 | 4230965.7778 | 2221700.4834 | 2093070.4753 | 0 | 0
| Overhead asset inspection | 41157.6642 | 513921.0574 | 269862.4195 | 254238.1689 | 0 | 0
| Network underground cable maintenance | 26701.0504 | 333406.4825 | 175073.3479 | 164937.1093 | 0 | 0
| Distribution substation equipment & property maintenance | 29694.0784 | 370779.3554 | 194698.0232 | 183425.5729 | 0 | 0
| Zone substation equipment maintenance | 208797.4759 | 2607179.5322 | 1369042.5145 | 1289778.9274 | 0 | 0
| Zone substation property maintenance | 0 | 0 | 0 | 0 | 0 | 0
| Public lighting maintenance | 0 | 0 | 0 | 0 | 0 | 0
| Scada & network control maintenance | 0 | 0 | 0 | 0 | 0 | 0
| Protection systems maintenance | 17784.1436 | 222064.2508 | 116607.0064 | 109855.7992 | 0 | 0
| Subtransmission asset maintenance - for dnsps with dual function assets | 0 | 0 | 0 | 0 | 0 | 0
| Other | 17179.7561 | 214517.4812 | 112644.1613 | 106122.3914 | 0 | 0
NON-ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 0 | 0 | 0 | 0 | 0 | 0
| Pole inspection and treatment | 16239.0136 | 202770.7644 | 106475.9039 | 100311.2581 | 0 | 0
| Overhead asset inspection | 309443.4684 | 3863910.1055 | 2028957.7841 | 1911487.0187 | 0 | 0
| Network underground cable maintenance | 71838.9955 | 897027.8877 | 471033.6591 | 443762.1777 | 0 | 0
| Distribution substation equipment & property maintenance | 30304.5626 | 378402.2528 | 198700.8433 | 187196.6413 | 0 | 0
| Zone substation equipment maintenance | 118693.2936 | 1482080.7786 | 778247.7465 | 733189.4613 | 0 | 0
| Zone substation property maintenance | 14282.6015 | 178341.7453 | 93648.1084 | 88226.1548 | 0 | 0
| Public lighting maintenance | 0 | 0 | 0 | 0 | 0 | 0
| SCADA & network control maintenance | 0 | 0 | 0 | 0 | 0 | 0
| Protection systems maintenance | 9624.8742 | 120182.3672 | 63108.3391 | 59454.5495 | 0 | 0
| Subtransmission asset maintenance - for DNSP with dual function assets | 0 | 0 | 0 | 0 | 0 | 0
| Other | 300852.7335 | 3756640.6668 | 1972630.0859 | 1858420.5307 | 0 | 0
OVERHEADS | Network overheads | 8618129.779 | 51207486.5939 | 28476392.5691 | 22671083.0766 | 0 | 0
| Corporate overheads | 5157414.4674 | 30644494.6842 | 17041349.2001 | 13567232.6653 | 0 | 0
AUGMENTATION | Subtransmission substations, switching stations, zone substations | 3270036.0534 | 2066256.2333 | 8028556.7057 | 750241.6564 | 0 | 0
| Subtransmission lines | 3069879.8668 | 1939782.4081 | 7537135.4286 | 704319.9887 | 0 | 0
| HV feeders | 1767853.0766 | 2541437.5984 | 2588801.2292 | 594561.1858 | 0 | 0
| Distribution substations | 111020.565 | 360861.5486 | 0 | 15951.9024 | 0 | 0
| LV feeders | 61212.9782 | 122707.4198 | 306556.7858 | 13677.9501 | 0 | 0
| Other assets | 0 | 0 | 0 | 0 | 0 | 0
CONNECTIONS | Simple and complex customer connections | 690786.9871 | 2947737.4602 | 31281286.3364 | 235548.2164 | 0 | 0
EMERGENCY RESPONSE | Major storms | 3755129.4613 | 10239807.1 | 5068961.7899 | 5195854.0103 | 0 | 0
| Major event days | 466883.3613 | 1273137.3465 | 630234.9741 | 646011.7581 | 0 | 0
PUBLIC LIGHTING | All public lighting services | 9250770.0892 | 10020172.2564 | 4284819.7509 | 1664298.9035 | 0 | 0
METERING | All metering services | 3010103.9594 | 10257285.2072 | 4018479.7371 | 1154746.0963 | 0 | 0
FEE-BASED SERVICES | All fee-based services | 288197.9954 | 13646161.6412 | 3243270.8238 | 4381954.1611 | 0 | 0
QUOTED SERVICES | All quoted services | 82034.8425 | 3884345.9676 | 923188.9727 | 1247312.3523 | 0 | 0
REPLACEMENT | Poles | 4512358.4671 | 6921785.5081 | 3776298.7759 | 1686073.4089 | 0 | 0
| Pole top structures | 0 | 0 | 0 | 0 | 0 | 0
| Overhead conductors | 4897326.8803 | 7512312.3476 | 4098470.8193 | 1829919.4729 | 0 | 0
| Underground cables | 914854.8035 | 1403352.3195 | 765622.922 | 341841.715 | 0 | 0
| Service lines | 608693.2208 | 933712.1474 | 509402.673 | 227442.3588 | 0 | 0
| Transformers | 1980038.6115 | 3037303.5889 | 1657053.0554 | 739854.8842 | 0 | 0
| Switchgear | 4077543.2274 | 6254795.5411 | 3412410.9621 | 1523601.7394 | 0 | 0
| Public lighting | 609343.6124 | 934709.8234 | 509946.9722 | 227685.3821 | 0 | 0
| SCADA network control and protection systems | 1629787.5725 | 2500031.8753 | 1363935.2591 | 608981.2031 | 0 | 0
| Other | 7039562.9445 | 13411416.4516 | 16437071.5443 | 3608499.9196 | 0 | 0
NON-NETWORK EXPENDITURE | IT and communications | 149815.4212 | 18153766.946 | 11011650.2054 | 20106547.4273 | 0 | 0
| Motor vehicles | 3289979.8551 | 1472650.532 | 291656.6857 | 2465875.9273 | 0 | 0
| Buildings and property | 29495.9761 | 609570.9034 | 651090.7715 | 2110470.3491 | 0 | 0
| Other | 2223824.1426 | 12692.6004 | 0 | 1315.257 | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.1 Public lighting
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
4.1 PUBLIC LIGHTING
There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.1.1 - DESCRIPTOR METRICS OVER YEAR
VOLUME (0's)
| LIGHT TYPE |  | 2019-20
POPULATION OF LIGHTS | Fluorescent |  | 38380
| Incandescent |  | 1
| Metal Halide |  | 11482
| High Pressure Sodium |  | 52037
| Mercury |  | 44105
| Low Pressure Sodium |  | 23
| LED |  | 74064
4.1.2 - DESCRIPTOR METRICS ANNUALLY
VOLUMES & EXPENDITURE
SERVICE/SERVICE QUALITY | DESCRIPTOR METRIC | UNITS | 2019-20
LIGHT INSTALLATION | Major road light installation | 0's | 593.8977
| Minor road light installation | 0's | 1527.1656
| Number of poles installed | 0's | 1625
| Total cost | $0s | 4266064
LIGHT REPLACEMENT | Major road light replacement | 0's | 753
| Minor road light replacement | 0's | 25833
| Number of poles replaced | 0's | 594
| Total cost | $0s | 9557333.8352
LIGHT MAINTENANCE | Major road light maintenance | 0's | 11142
| Minor road light maintenance | 0's | 28651
| Number of poles installed | 0's | 31029
| Total cost | $0s | 11396663.2828
QUALITY OF SUPPLY | Mean days to rectify/replace public lighting assets | days | 5
| GSO breaches | 0's | 1078
| GSL payments | $0s | 26950
| Customer complaints | 0's | 16022
4.1.3 - COST METRICS
AVERAGE UNIT COST ($)
ACTIVITY TYPE | LIGHT TYPE |  | 2019-20
LIGHT INSTALLATION | Minor Road 17W LED Luminair Install |  | 364.0499
| Minor Road 42W LED Luminair Install |  | 397.2256
| Major Road 82W LED Luminair Install |  | 628.0207
| Major Road 100W LED Luminair Install |  | 628.0207
| Major Road 198W LED Luminair Install |  | 734.0396
LIGHT REPLACEMENT | Major Road 250W HPS luminaire |  | 349.2933
| Major Road 150W HPS luminaire |  | 375.6033
| Minor Road 42W CFL luminaire |  | 266.5833
| Minor Road 2x24W T5 luminaire |  | 362.8633
LIGHT MAINTENANCE | Major Road 250W HPS lamp |  | 104.1033
| Major Road 150W HPS lamp |  | 105.8633
| Minor Road 42W CFL lamp |  | 102.3633
| Minor Road 2x24W T5 lamp |  | 98.8133
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.2 Metering
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
4.2 METERING
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.2.1 - METERING DESCRIPTOR METRIC
VOLUMES (0's)
Asset Category | Asset Subcategory | 2019-20
Meter Type 4 | Single phase meter population | 0
| Multi phase meter population | 0
| Current transformer connected meter population | 0
| Direct connect meter population | 0
Meter Type 5 | Single phase meter population | 48
| Multi phase meter population | 556
| Current transformer connected meter population | 185
| Direct connect meter population | 419
Meter Type 6 | Single phase meter population | 1276150
| Multi phase meter population | 128908
| Current transformer connected meter population | 3212
| Direct connect meter population | 1401846
4.2.2 - COST METRICS
|  | VOLUMES (0's) | EXPENDITURE ($0's)
Service Subcategory | Meter Type | 2019-20 | 2019-20
Meter purchase | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter testing | Meter Type 4 | 0 | 0
| Meter Type 5 | 30 | 15895.0508
| Meter Type 6 | 704 | 373003.8598
Meter investigation | Meter Type 4 | 0 | 0
| Meter Type 5 | 8 | 1525.0077
| Meter Type 6 | 1070 | 203969.7846
Scheduled meter reading | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 3284930 | 11603498.7956
Special meter reading | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
New meter installation | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter replacement | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter maintenance | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 3874073.1767
Remote meter reading | Meter Type 4 | 0 | 0
Remote meter re-configuration | Meter Type 4 | 0 | 0
Other metering | Meter Type 4 |  | 0
| Meter Type 5 |  | 1036.6726
| Meter Type 6 |  | 2411564.8334
| Meter Type 7 |  | 0
IT infrastructure capex | Meter Type 4 |  | 0
IT infrastructure opex | Meter Type 4 |  | 0
Communications infrastructure capex | Meter Type 4 |  | 0
Communications infrastructure opex | Meter Type 4 |  | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.3 Fee-based services
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
4.3 ANCILLARY SERVICES - FEE BASED SERVICES
4.3.1 - COST METRICS FOR FEE-BASED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2019-20 |  | 2019-20
Common Fee-Based Services | Energisation | 0 | ED_FEE431_00001 | 0
| De-energisation | 0 | ED_FEE431_00002 | 0
| Re-energisation | 0 | ED_FEE431_00003 | 0
Miscellaneous Fee-Based Services | Administration Fee - Subdivision - URD - Underground - 1-5 lots | 96346.8193 | ED_FEE431_00004 | 148
| Administration Fee - Subdivision - URD - Underground - 6-10 lots | 40704.6572 | ED_FEE431_00004 | 51
| Administration Fee - Subdivision - URD - Underground - 11-40 lots | 103242.748 | ED_FEE431_00004 | 92
| Administration Fee - Subdivision - URD - Underground - 41+ lots | 92242.6179 | ED_FEE431_00004 | 74
| Administration Fee - Subdivision - Non Urban - Underground - 1-5 lots | 9236.1982 | ED_FEE431_00004 | 15
| Administration Fee - Subdivision - Non Urban - Underground - 6-10 lots | 746.9777 | ED_FEE431_00004 | 1
| Administration Fee - Subdivision - Non Urban - Underground - 11-40 lots | 4911.4837 | ED_FEE431_00004 | 6
| Administration Fee - Subdivision - Non Urban - Overhead - 1-5 poles | 654.8582 | ED_FEE431_00004 | 1
| Administration Fee - Connection of Load - Non Urban - Overhead - 1-5 poles | 5075.2061 | ED_FEE431_00004 | 8
| Design Information Fee - Subdivision - URD - Underground - 1-5 lots | 101136.7407 | ED_FEE431_00004 | 150
| Design Information Fee - Subdivision - URD - Underground - 6-10 lots | 44863.1731 | ED_FEE431_00004 | 52
| Design Information Fee - Subdivision - URD - Underground - 11-40 lots | 140110.9495 | ED_FEE431_00004 | 94
| Design Information Fee - Subdivision - URD - Underground - 41+ lots | 141381.6101 | ED_FEE431_00004 | 75
| Design Certification Fee - Subdivision - URD - Underground - 1-5 lots | 328157.2749 | ED_FEE431_00004 | 347
| Design Certification Fee - Subdivision - URD - Underground - 6-10 lots | 5482.4279 | ED_FEE431_00004 | 7
| Design Certification Fee - Subdivision - URD - Underground - 11-40 lots | 7777.0752 | ED_FEE431_00004 | 6
| Design Certification Fee - Subdivision - URD - Underground - 41+ lots | 3116.6005 | ED_FEE431_00004 | 2
| Design Certification Fee - Subdivision - Non Urban - Underground - 1-5 lots | 14516.8556 | ED_FEE431_00004 | 23
| Design Certification Fee - Subdivision - Non Urban - Overhead - 1-5 poles | 514.5211 | ED_FEE431_00004 | 1
| Design Certification Fee - Subdivision - Industrial & Commercial - Underground - 1-10 lots | 12986.0974 | ED_FEE431_00004 | 16
| Design Certification Fee - Subdivision - Industrial & Commercial - Overhead - 1-5 poles | 771.7816 | ED_FEE431_00004 | 1
| Design Certification Fee - Connection of Load - Non Urban - Overhead - 1-5 poles | 8232.3368 | ED_FEE431_00004 | 8
| Notification of Arrangement - Subdivision - Industrial & Commercial - Per NOA | 91.8788 | ED_FEE431_00004 | 40
| Notification of Arrangement - Subdivision - Non Urban - Per NOA | 114.4189 | ED_FEE431_00004 | 50
| Notification of Arrangement - Subdivision - URD - Per NOA | 2932.2146 | ED_FEE431_00004 | 1277
| Compliance Certificate - Connection of Load - Industrial & Commercial - Per Compliance Cert | 11.5522 | ED_FEE431_00004 | 5
| Compliance Certificate - Connection of Load - URD - Per Compliance Cert | 378.1109 | ED_FEE431_00004 | 162.3194
| Inspection of Service Work (Level 1) - Subdivision - URD - Underground - Per Lot (1 - 10) - Grade A | 18627.9239 | ED_FEE431_00004 | 101
| Inspection of Service Work (Level 1) - Subdivision - URD - Underground - Per Lot (11 - 50) - Grade A | 88516.125 | ED_FEE431_00004 | 121
| Inspection of Service Work (Level 1) - Subdivision - URD - Underground - Per Lot (51 +) - Grade A | 75632.2337 | ED_FEE431_00004 | 55
| Inspection of Service Work (Level 1) - Subdivision - URD - Underground - Per Lot (1 - 10) - Grade B | 13652.3957 | ED_FEE431_00004 | 63
| Inspection of Service Work (Level 1) - Subdivision - URD - Underground - Per Lot (11 - 50) - Grade B | 25985.3445 | ED_FEE431_00004 | 16
| Inspection of Service Work (Level 1) - Subdivision - URD - Underground - Per Lot (51 +) - Grade B | 13869.1601 | ED_FEE431_00004 | 4
| Inspection of Service Work (Level 1) - Subdivision - URD - Underground - Per Lot (1 - 10) - Grade C | 2200.6023 | ED_FEE431_00004 | 4
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Underground - Per Lot (1 - 10) - Grade A | 1063.0661 | ED_FEE431_00004 | 3
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Underground - Per Lot (11 - 50) - Grade A | 927.5942 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Underground - Per Lot (1 - 10) - Grade B | 1367.7776 | ED_FEE431_00004 | 4
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Underground - Per Lot (1 - 10) - Grade C | 270.8489 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Underground - Per Lot (11 - 50) - Grade C | 2234.4908 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Overhead - Per Pole (1 - 5) - Grade A | 534.9271 | ED_FEE431_00004 | 2
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Overhead - Per Pole Sub - Grade A | 0 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Overhead - Per Pole (1 - 5) - Grade B | 3890.2792 | ED_FEE431_00004 | 5
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Overhead - Per Pole (6 - 10) - Grade B | 621.1114 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Non Urban - Overhead - Per Pole Sub - Grade B | 0 | ED_FEE431_00004 | 4
| Inspection of Service Work (Level 1) - Subdivision - Industrial & Commercial - Overhead - Per Pole (1 - 5) - Grade A | 2065.1951 | ED_FEE431_00004 | 2
| Inspection of Service Work (Level 1) - Subdivision - Industrial & Commercial - Overhead - Per Pole (1 - 5) - Grade B | 82.814 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Industrial & Commercial - Overhead - Per Pole (1 - 5) - Grade C | 297.9278 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Industrial & Commercial - Overhead - Per Pole (11 +) - Grade C | 3047.0074 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Industrial & Commercial - Underground - Per Lot (1 - 10) - Grade A | 812.4951 | ED_FEE431_00004 | 7
| Inspection of Service Work (Level 1) - Subdivision - Industrial & Commercial - Underground - Per Lot (1 - 10) - Grade B | 4279.3735 | ED_FEE431_00004 | 4
| Inspection of Service Work (Level 1) - Subdivision - Industrial & Commercial - Underground - Per Lot (11 - 50) - Grade B | 575.5518 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Subdivision - Industrial & Commercial - Underground - Per Lot (1 - 10) - Grade C | 507.8353 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Connection of Load - Non Urban - Overhead - Per Pole (1 - 5) - Grade A | 1043.5554 | ED_FEE431_00004 | 5
| Inspection of Service Work (Level 1) - Connection of Load - Non Urban - Overhead - Per Pole (1 - 5) - Grade B | 3613.1939 | ED_FEE431_00004 | 14
| Inspection of Service Work (Level 1) - Connection of Load - Non Urban - Overhead - Per Pole (1 - 5) - Grade C | 303.6297 | ED_FEE431_00004 | 2
| Inspection of Service Work (Level 1) - Connection of Load - Non Urban - Overhead - Per Pole Sub - Grade B | 0 | ED_FEE431_00004 | 4
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Overhead - Per Pole (1 - 5) - Grade A | 21689.9943 | ED_FEE431_00004 | 29
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Overhead - Per Pole (1 - 5) - Grade B | 3600.3893 | ED_FEE431_00004 | 4
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Overhead - Per Pole (1 - 5) - Grade C | 1364.6573 | ED_FEE431_00004 | 2
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Overhead - Per Pole (6 - 10) - Grade A | 1231.8317 | ED_FEE431_00004 | 4
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Overhead - Per Pole (6 - 10) - Grade B | 552.1105 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Overhead - Per Pole (6 - 10) - Grade C | 947.9713 | ED_FEE431_00004 | 1
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Overhead - Per Pole (11+) - Grade A | 13077.4903 | ED_FEE431_00004 | 13
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Overhead - Per Pole (11+) - Grade B | 5890.96 | ED_FEE431_00004 | 5
| Access Permits - Subdivision - URD - Per Lot | 468166.4456 | ED_FEE431_00004 | 156
| Access Permits - All Other - Industrial & Commercial | 1032761.6456 | ED_FEE431_00004 | 291.4207
| Access Permits - All Other - Non Urban | 186260.0808 | ED_FEE431_00004 | 61.3817
| Access Permits - All Other - URD | 234911.8822 | ED_FEE431_00004 | 77.4148
| Access Permits - All Other - Asset Relocation | 495609.4944 | ED_FEE431_00004 | 163.3272
| Access Permits - All Other - Public Lighting | 34609.3684 | ED_FEE431_00004 | 11.4055
| Substation Commissioning Fee - Subdivision - URD - Per Lot | 173266.7163 | ED_FEE431_00004 | 125
| Substation Commissioning Fee - All Other - Industrial & Commercial | 167765.414 | ED_FEE431_00004 | 212.61
| Substation Commissioning Fee - All Other - Non Urban | 46538.7359 | ED_FEE431_00004 | 58.92
| Substation Commissioning Fee - All Other - URD | 55741.4121 | ED_FEE431_00004 | 70.64
| Substation Commissioning Fee - All Other - Asset Relocation | 12499.2511 | ED_FEE431_00004 | 15.8
| Substation Commissioning Fee - All Other - Public Lighting | 791.1104 | ED_FEE431_00004 | 1
| Connection Offer (Basic) | 127147.5713 | ED_FEE431_00004 | 50093
| Connection Offer (Standard) | 1559139.4214 | ED_FEE431_00004 | 1806
| Clearance to Work | 515278.6321 | ED_FEE431_00004 | 566.3704
| Excluded Distribution Services - Connect & disconnect generator to LV OH mains - One generator | 11368.6621 | ED_FEE431_00004 | 3
| Excluded Distribution Services - Install & remove HV live line links - one set | 25577.0553 | ED_FEE431_00004 | 4
| Excluded Distribution Services - Testing cable prior to commissioning | 769339.3837 | ED_FEE431_00004 | 181
| Excluded Distribution Services - Protection setting | 324084.3917 | ED_FEE431_00004 | 105
| Labour Rates - quoted service charges | 0 | ED_FEE431_00004 | 470
| Provision of Access Fee (Standby) - Normal Time - 1 x Visit - Open / Close - 1 hour | 95934.2443 | ED_FEE431_00004 | 353
| Provision of Access Fee (Standby) - Normal Time - 1 x Visit - Open / Isolate & CSO to close - 1 hour | 16856.422 | ED_FEE431_00004 | 39
| Provision of Access Fee (Standby) - Normal Time - 2 x Visit - Open / Close & no isolation - 2 hours | 18599.1984 | ED_FEE431_00004 | 30
| Provision of Access Fee (Standby) - Normal Time - 2 x Visit - Open / Isolate / Close - 2 hours | 4338.826 | ED_FEE431_00004 | 6
| Provision of Access Fee (Standby) - Overtime - 1 x Visit - Open / Close - 1 hour | 25581.8671 | ED_FEE431_00004 | 42
| Provision of Access Fee (Standby) - Overtime - 1 x Visit - Open / Isolate & CSO to close - 1 hour | 7414.9019 | ED_FEE431_00004 | 11
| Provision of Access Fee (Standby) - Overtime - 2 x Visit - Open / Close & no isolation - 2 hours | 25372.6492 | ED_FEE431_00004 | 18
| Provision of Access Fee (Standby) - Overtime - 2 x Visit - Open / Isolate / Close - 2 hours | 6623.4275 | ED_FEE431_00004 | 6
| Inspection Of Service Work (Level 2) - Grade A | 312763.1318 | ED_FEE431_00004 | 13184
| Inspection Of Service Work (Level 2) - Grade B | 151601.5761 | ED_FEE431_00004 | 3724
| Inspection Of Service Work (Level 2) - Grade C | 2440.235 | ED_FEE431_00004 | 18
| Site Establishment | 397826.0648 | ED_FEE431_00004 | 21333
| Site Establishment fee | 0 | ED_FEE431_00004 | 102
| Rectification Works - Rectification of illegal connections | 2515.4519 | ED_FEE431_00004 | 166
| Disconnections / Reconnections (Meter Box) | 2355627.1261 | ED_FEE431_00004 | 18103
| Disconnections / Reconnections (Meter Load Tail) | 1803073.0317 | ED_FEE431_00004 | 720
| Disconnections / Reconnections (Site Visit) | 172478.8643 | ED_FEE431_00004 | 18688
| Disconnections / Reconnections (Pole Top / Pillar Box) | 631996.7755 | ED_FEE431_00004 | 370
| Off Peak Conversions | 68724.1461 | ED_FEE431_00004 | 404
| Meter Test | 102576.0249 | ED_FEE431_00004 | 512
| Special Meter Reads | 3259495.2316 | ED_FEE431_00004 | 39179
| Special Meter Reads - Site Visits | 554649.2274 | ED_FEE431_00004 | 8332
| Move In Meter Reads | 237647.4193 | ED_FEE431_00004 | 64522
| Move Out Meter Read | 248254.768 | ED_FEE431_00004 | 67382
| Authorisation - Renewal | 0 | ED_FEE431_00004 | 1650
| Authorisation - Old Fee | 0 | ED_FEE431_00004 | 719
| Conveyancing Information | 108996.3579 | ED_FEE431_00004 | 2803
| Excluded Distribution Services - Break & remake LV bonds - One set | 39884.3196 | ED_FEE431_00004 | 1
| Excluded Distribution Services - Install & remove LV live line links - One set | 19269.3465 | ED_FEE431_00004 | 3
| Excluded Distribution Services - Zone substation access and supervision for installation of cable(s) for one feeder | 50855.9773 | ED_FEE431_00004 | 10
| Excluded Distribution Services - 11kV Zone substation circuit breaker cable termination | 23239.9381 | ED_FEE431_00004 | 3
| Excluded Distribution Services - 11kV Straight through joint | 209693.434 | ED_FEE431_00004 | 32
| Excluded Distribution Services - Traffic Management to install & remove, break & remake, connect & disconnect excluded distribution services | 18988.0317 | ED_FEE431_00004 | 2
| Excluded Distribution Services - Traffic Management to test, terminate and joint excluded distribution services | 34013.4155 | ED_FEE431_00004 | 5
| Nightwatch Rental Minor - Per light/month | 75822.0005 | ED_FEE431_00004 | 3384
| Nightwatch Rental Small - Per light/month | 62225.6617 | ED_FEE431_00004 | 905
| Nightwatch Rental Medium - Per light/month | 501737.2751 | ED_FEE431_00004 | 5947
| Nightwatch Rental Large - Per light/month | 1400285.94 | ED_FEE431_00004 | 13550
| Nightwatch Rental X-Large - Per light/month | 764913.5874 | ED_FEE431_00004 | 5389
| Nightwatch Installation - Per light | 26297 | ED_FEE431_00004 | 64
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00164
ED_FEE431_00165
ED_FEE431_00166
ED_FEE431_00167
ED_FEE431_00168
ED_FEE431_00169
ED_FEE431_00170
ED_FEE431_00171
ED_FEE431_00172
ED_FEE431_00173
ED_FEE431_00174
ED_FEE431_00175
ED_FEE431_00176
ED_FEE431_00177
ED_FEE431_00178
ED_FEE431_00179
ED_FEE431_00180
ED_FEE431_00181
ED_FEE431_00182
ED_FEE431_00183
ED_FEE431_00184
ED_FEE431_00185
ED_FEE431_00186
ED_FEE431_00187
ED_FEE431_00188
ED_FEE431_00189
ED_FEE431_00190
ED_FEE431_00191
ED_FEE431_00192
ED_FEE431_00193
ED_FEE431_00194
ED_FEE431_00195
ED_FEE431_00196
ED_FEE431_00197
ED_FEE431_00198
ED_FEE431_00199
ED_FEE431_00200
ED_FEE431_00201
ED_FEE431_00202
ED_FEE431_00203
ED_FEE431_00204
ED_FEE431_00205
ED_FEE431_00206
ED_FEE431_00207
ED_FEE431_00208
ED_FEE431_00209
ED_FEE431_00210
ED_FEE431_00211
ED_FEE431_00212
ED_FEE431_00213
ED_FEE431_00214
ED_FEE431_00215
ED_FEE431_00216
ED_FEE431_00217
ED_FEE431_00218
ED_FEE431_00219
ED_FEE431_00220
ED_FEE431_00221
ED_FEE431_00222
ED_FEE431_00223
ED_FEE431_00224
ED_FEE431_00225
ED_FEE431_00226
ED_FEE431_00227
ED_FEE431_00228
ED_FEE431_00229
ED_FEE431_00230
ED_FEE431_00231
ED_FEE431_00232
ED_FEE431_00233
ED_FEE431_00234
ED_FEE431_00235
ED_FEE431_00236
ED_FEE431_00237
ED_FEE431_00238
ED_FEE431_00239
ED_FEE431_00240
ED_FEE431_00241
ED_FEE431_00242
ED_FEE431_00243
ED_FEE431_00244
ED_FEE431_00245
ED_FEE431_00246
ED_FEE431_00247
ED_FEE431_00248
ED_FEE431_00249
ED_FEE431_00250
ED_FEE431_00251
ED_FEE431_00252
ED_FEE431_00253
ED_FEE431_00254
ED_FEE431_00255
ED_FEE431_00256
ED_FEE431_00257
ED_FEE431_00258
ED_FEE431_00259
ED_FEE431_00260
ED_FEE431_00261
ED_FEE431_00262
ED_FEE431_00263
ED_FEE431_00264
ED_FEE431_00265
ED_FEE431_00266
ED_FEE431_00267
ED_FEE431_00268
ED_FEE431_00269
ED_FEE431_00270
ED_FEE431_00271
ED_FEE431_00272
ED_FEE431_00273
ED_FEE431_00274
ED_FEE431_00275
ED_FEE431_00276
ED_FEE431_00277
ED_FEE431_00278
ED_FEE431_00279
ED_FEE431_00280
ED_FEE431_00281
ED_FEE431_00282
ED_FEE431_00283
ED_FEE431_00284
ED_FEE431_00285
ED_FEE431_00286
ED_FEE431_00287
ED_FEE431_00288
ED_FEE431_00289
ED_FEE431_00290
ED_FEE431_00291
ED_FEE431_00292
ED_FEE431_00293
ED_FEE431_00294
ED_FEE431_00295
ED_FEE431_00296
ED_FEE431_00297
ED_FEE431_00298
ED_FEE431_00299
ED_FEE431_00300
ED_FEE431_00301
ED_FEE431_00302
ED_FEE431_00303
ED_FEE431_00304
ED_FEE431_00305
ED_FEE431_00306
ED_FEE431_00307
ED_FEE431_00308
ED_FEE431_00309
ED_FEE431_00310
ED_FEE431_00311
ED_FEE431_00312
ED_FEE431_00313
ED_FEE431_00314
ED_FEE431_00315
ED_FEE431_00316
ED_FEE431_00317
ED_FEE431_00318
ED_FEE431_00319
ED_FEE431_00320
ED_FEE431_00321
ED_FEE431_00322
ED_FEE431_00323
ED_FEE431_00324
ED_FEE431_00325
ED_FEE431_00326
ED_FEE431_00327
ED_FEE431_00328
ED_FEE431_00329
ED_FEE431_00330
ED_FEE431_00331
ED_FEE431_00332
ED_FEE431_00333
ED_FEE431_00334
ED_FEE431_00335
ED_FEE431_00336
ED_FEE431_00337
ED_FEE431_00338
ED_FEE431_00339
ED_FEE431_00340
ED_FEE431_00341
ED_FEE431_00342
ED_FEE431_00343
ED_FEE431_00344
ED_FEE431_00345
ED_FEE431_00346
ED_FEE431_00347
ED_FEE431_00348
ED_FEE431_00349
ED_FEE431_00350
ED_FEE431_00351
ED_FEE431_00352
ED_FEE431_00353
ED_FEE431_00354
ED_FEE431_00355
ED_FEE431_00356
ED_FEE431_00357
ED_FEE431_00358
ED_FEE431_00359
ED_FEE431_00360
ED_FEE431_00361
ED_FEE431_00362
ED_FEE431_00363
ED_FEE431_00364
ED_FEE431_00365
ED_FEE431_00366
ED_FEE431_00367
ED_FEE431_00368
ED_FEE431_00369
ED_FEE431_00370
ED_FEE431_00371
ED_FEE431_00372
ED_FEE431_00373
ED_FEE431_00374
ED_FEE431_00375
ED_FEE431_00376
ED_FEE431_00377
ED_FEE431_00378
ED_FEE431_00379
ED_FEE431_00380
ED_FEE431_00381
ED_FEE431_00382
ED_FEE431_00383
ED_FEE431_00384
ED_FEE431_00385
ED_FEE431_00386
ED_FEE431_00387
ED_FEE431_00388
ED_FEE431_00389
ED_FEE431_00390
ED_FEE431_00391
ED_FEE431_00392
ED_FEE431_00393
ED_FEE431_00394
ED_FEE431_00395
ED_FEE431_00396
ED_FEE431_00397
ED_FEE431_00398
ED_FEE431_00399
ED_FEE431_00400
ED_FEE431_00401
ED_FEE431_00402
ED_FEE431_00403
ED_FEE431_00404
ED_FEE431_00405
ED_FEE431_00406
ED_FEE431_00407
ED_FEE431_00408
ED_FEE431_00409
ED_FEE431_00410
ED_FEE431_00411
ED_FEE431_00412
ED_FEE431_00413
ED_FEE431_00414
ED_FEE431_00415
ED_FEE431_00416
ED_FEE431_00417
ED_FEE431_00418
ED_FEE431_00419
ED_FEE431_00420
ED_FEE431_00421
ED_FEE431_00422
ED_FEE431_00423
ED_FEE431_00424
ED_FEE431_00425
ED_FEE431_00426
ED_FEE431_00427
ED_FEE431_00428
ED_FEE431_00429
ED_FEE431_00430
ED_FEE431_00431
ED_FEE431_00432
ED_FEE431_00433
ED_FEE431_00434
ED_FEE431_00435
ED_FEE431_00436
ED_FEE431_00437
ED_FEE431_00438
ED_FEE431_00439
ED_FEE431_00440
ED_FEE431_00441
ED_FEE431_00442
ED_FEE431_00443
ED_FEE431_00444
ED_FEE431_00445
ED_FEE431_00446
ED_FEE431_00447
ED_FEE431_00448
ED_FEE431_00449
ED_FEE431_00450
ED_FEE431_00451
ED_FEE431_00452
ED_FEE431_00453
ED_FEE431_00454
ED_FEE431_00455
ED_FEE431_00456
ED_FEE431_00457
ED_FEE431_00458
ED_FEE431_00459
ED_FEE431_00460
ED_FEE431_00461
ED_FEE431_00462
ED_FEE431_00463
ED_FEE431_00464
ED_FEE431_00465
ED_FEE431_00466
ED_FEE431_00467
ED_FEE431_00468
ED_FEE431_00469
ED_FEE431_00470
ED_FEE431_00471
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.4 Quoted services
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
4.4 ANCILLARY SERVICES - QUOTED SERVICES
4.4.1 - COST METRICS FOR QUOTED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2019-20 |  | 2019-20
Quoted Services | Administration Fee - Subdivision - Industrial & Commercial - Per Hour | 11060.7184 | ED_QUO441_00001 | 21
| Administration Fee - Connection of Load - URD - Per Hour | 45859.8809 | ED_QUO441_00002 | 93
| Administration Fee - Connection of Load - Industrial & Commercial - Per Hour | 132694.112 | ED_QUO441_00003 | 268
| Administration Fee - Connection of Load - Non Urban - Underground - Per Hour | 43772.6958 | ED_QUO441_00004 | 68
| Administration Fee - Other - Asset Relocation - Per Hour | 97529.245 | ED_QUO441_00005 | 205
| Administration Fee - Other - Public Lighting - Per Hour | 44208.2226 | ED_QUO441_00006 | 92
| Administration Fee - Other - Generator - Per Hour | 491.1673 | ED_QUO441_00007 | 1
| Design Information Fee - Subdivision - Non Urban - Per Hour | 25654.9865 | ED_QUO441_00008 | 24
| Design Information Fee - Subdivision - Industrial & Commercial - Per Hour | 31499.0412 | ED_QUO441_00009 | 21
| Design Information Fee - Connection of Load - Industrial & Commercial - <= 200A/Phase (LV) | 416304.617 | ED_QUO441_00010 | 157
| Design Information Fee - Connection of Load - Industrial & Commercial - <= 700A/Phase (LV) | 88124.3551 | ED_QUO441_00011 | 35
| Design Information Fee - Connection of Load - Industrial & Commercial - > 700A/Phase (LV) | 202137.5906 | ED_QUO441_00012 | 54
| Design Information Fee - Connection of Load - Industrial & Commercial - HV Customer | 31924.6636 | ED_QUO441_00013 | 5
| Design Information Fee - Connection of Load - Multi-Dwelling - <= 5 units | 5390.3108 | ED_QUO441_00014 | 4
| Design Information Fee - Connection of Load - Multi-Dwelling - <= 20 units | 19774.0745 | ED_QUO441_00015 | 15
| Design Information Fee - Connection of Load - Multi-Dwelling - <= 40 units | 38909.3257 | ED_QUO441_00016 | 17
| Design Information Fee - Connection of Load - Multi-Dwelling - > 40 units | 129450.0321 | ED_QUO441_00017 | 30
| Design Information Fee - Connection of Load - Non Urban - Single Residential - Per Hour | 113688.7954 | ED_QUO441_00018 | 76
| Design Information Fee - Asset Relocation | 320040.7632 | ED_QUO441_00019 | 204
| Design Information Fee - Public Lighting | 80769.354 | ED_QUO441_00020 | 92
| Design Certification Fee - Connection of Load - Industrial & Commercial - <= 200A/Phase (LV) | 80640.5557 | ED_QUO441_00021 | 46
| Design Certification Fee - Connection of Load - Industrial & Commercial - <= 700A/Phase (LV) | 396478.3903 | ED_QUO441_00022 | 158
| Design Certification Fee - Connection of Load - Industrial & Commercial - > 700A/Phase (LV) | 150547.4478 | ED_QUO441_00023 | 41
| Design Certification Fee - Connection of Load - Industrial & Commercial - HV Customer | 30871.263 | ED_QUO441_00024 | 5
| Design Certification Fee - Connection of Load - Multi-Dwelling - <= 5 units | 6456.2387 | ED_QUO441_00025 | 4
| Design Certification Fee - Connection of Load - Multi-Dwelling - <= 20 units | 80732.1713 | ED_QUO441_00026 | 40
| Design Certification Fee - Connection of Load - Multi-Dwelling - <= 40 units | 62113.4095 | ED_QUO441_00027 | 23
| Design Certification Fee - Connection of Load - Multi-Dwelling - > 40 units | 136807.8592 | ED_QUO441_00028 | 27
| Design Certification Fee - Connection of Load - Non Urban - Underground - Per Hour | 48154.2383 | ED_QUO441_00029 | 63
| Design Certification Fee - Asset Relocation | 592614.6506 | ED_QUO441_00030 | 314
| Design Certification Fee - Public Lighting | 111474.9432 | ED_QUO441_00031 | 92
| Design Re-certification Fee - Subdivision - Industrial & Commercial - Per Hour | 16207.4131 | ED_QUO441_00032 | 13
| Design Re-certification Fee - Subdivision - Non Urban - Per Hour | 4373.4289 | ED_QUO441_00033 | 6
| Design Re-certification Fee - Subdivision - URD - Per Hour | 122215.0257 | ED_QUO441_00034 | 137
| Design Re-certification Fee - Connection of Load - Industrial & Commercial - Per Hour | 71928.8049 | ED_QUO441_00035 | 76
| Design Re-certification Fee - Connection of Load - Non Urban - Per Hour | 11072.0601 | ED_QUO441_00036 | 13
| Design Re-certification Fee - Connection of Load - URD - Per Hour | 52589.8741 | ED_QUO441_00037 | 55
| Design Re-certification Fee - Asset Relocation | 81848.2605 | ED_QUO441_00038 | 77
| Design Re-certification Fee - Public Lighting | 13669.3909 | ED_QUO441_00039 | 12
| Early NOA Fee - Subdivision - Industrial & Commercial - Per hour for early notification | 8.0866 | ED_QUO441_00040 | 2
| Early NOA Fee - Subdivision - Non Urban - Per hour for early notification | 4.6478 | ED_QUO441_00041 | 1
| Early NOA Fee - Subdivision - URD - Per hour for early notification | 233.8349 | ED_QUO441_00042 | 48
| Inspection of Service Work (Level 1) - Subdivision - URD - Underground - Per Hour + travel time | 828.1614 | ED_QUO441_00043 | 0
| Inspection of Service Work (Level 1) - Connection of Load - URD - Underground - Per hour + travel time | 99063.1836 | ED_QUO441_00044 | 105
| Inspection of Service Work (Level 1) - Connection of Load - Non Urban - Underground - Per hour + travel time | 18468.9374 | ED_QUO441_00045 | 33
| Inspection of Service Work (Level 1) - Connection of Load - Industrial & Commercial - Underground - Per Hour + travel time | 207663.3364 | ED_QUO441_00046 | 176
| Inspection of Service Work (Level 1) - Other - Asset Relocation - Underground - Per Hour + travel time | 210034.5039 | ED_QUO441_00047 | 195
| Inspection of Service Work (Level 1) - Other - Public Lighting - Underground - Per Hour + travel time | 31814.833 | ED_QUO441_00048 | 47
| Inspection of Service Work (Level 1) - Other - Public Lighting - Overhead - Per Hour + travel time | 2513.1535 | ED_QUO441_00049 | 5
| Inspection of Service Work (Level 1) - Other - Asset Relocation - Overhead - Per Hour + travel time | 18207.4777 | ED_QUO441_00050 | 21
| Planning Studies (Simple) | 16345.497 | ED_QUO441_00051 | 25
| Planning Studies (Complex) | 334410.2467 | ED_QUO441_00052 | 104
| Investigation, review & implementation of remedial actions associated with ASP's connection work. | -28447.5132 | ED_QUO441_00053 | 1
| Customer Interface Co-ordination | 406344.6126 | ED_QUO441_00054 | 63
| Preliminary Enquiry (Simple) | 123945.803 | ED_QUO441_00055 | 110
| Preliminary Enquiry (Complex) | 371351.5393 | ED_QUO441_00056 | 0
| Reinspection (Level 1 & Level 2 work) | 24689.263 | ED_QUO441_00057 | 6
| Inspection of works outside normal working hours | 133687.7618 | ED_QUO441_00058 | 312
| Reinspection Fee | 0 | ED_QUO441_00059 | 20
| Rectification Works - Tiger Tails | 179339.9689 | ED_QUO441_00060 | 71
| Rectification Works - High Load Escorts | 33.3353 | ED_QUO441_00061 | 1
| Rectification Works - Provision of service crew / additional crew (Additional person per crew) | 36262.0871 | ED_QUO441_00062 | 9
ED_QUO441_00063
ED_QUO441_00064
ED_QUO441_00065
ED_QUO441_00066
ED_QUO441_00067
ED_QUO441_00068
ED_QUO441_00069
ED_QUO441_00070
ED_QUO441_00071
ED_QUO441_00072
ED_QUO441_00073
ED_QUO441_00074
ED_QUO441_00075
ED_QUO441_00076
ED_QUO441_00077
ED_QUO441_00078
ED_QUO441_00079
ED_QUO441_00080
ED_QUO441_00081
ED_QUO441_00082
ED_QUO441_00083
ED_QUO441_00084
ED_QUO441_00085
ED_QUO441_00086
ED_QUO441_00087
ED_QUO441_00088
ED_QUO441_00089
ED_QUO441_00090
ED_QUO441_00091
ED_QUO441_00092
ED_QUO441_00093
ED_QUO441_00094
ED_QUO441_00095
ED_QUO441_00096
ED_QUO441_00097
ED_QUO441_00098
ED_QUO441_00099
ED_QUO441_00100
ED_QUO441_00101
ED_QUO441_00102
ED_QUO441_00103
ED_QUO441_00104
ED_QUO441_00105
ED_QUO441_00106
ED_QUO441_00107
ED_QUO441_00108
ED_QUO441_00109
ED_QUO441_00110
ED_QUO441_00111
ED_QUO441_00112
ED_QUO441_00113
ED_QUO441_00114
ED_QUO441_00115
ED_QUO441_00116
ED_QUO441_00117
ED_QUO441_00118
ED_QUO441_00119
ED_QUO441_00120
ED_QUO441_00121
ED_QUO441_00122
ED_QUO441_00123
ED_QUO441_00124
ED_QUO441_00125
ED_QUO441_00126
ED_QUO441_00127
ED_QUO441_00128
ED_QUO441_00129
ED_QUO441_00130
ED_QUO441_00131
ED_QUO441_00132
ED_QUO441_00133
ED_QUO441_00134
ED_QUO441_00135
ED_QUO441_00136
ED_QUO441_00137
ED_QUO441_00138
ED_QUO441_00139
ED_QUO441_00140
ED_QUO441_00141
ED_QUO441_00142
ED_QUO441_00143
ED_QUO441_00144
ED_QUO441_00145
ED_QUO441_00146
ED_QUO441_00147
ED_QUO441_00148
ED_QUO441_00149
ED_QUO441_00150
ED_QUO441_00151
ED_QUO441_00152
ED_QUO441_00153
ED_QUO441_00154
ED_QUO441_00155
ED_QUO441_00156
ED_QUO441_00157
ED_QUO441_00158
ED_QUO441_00159
ED_QUO441_00160
ED_QUO441_00161
ED_QUO441_00162
ED_QUO441_00163
ED_QUO441_00164
ED_QUO441_00165
ED_QUO441_00166
ED_QUO441_00167
ED_QUO441_00168
ED_QUO441_00169
ED_QUO441_00170
ED_QUO441_00171
ED_QUO441_00172
ED_QUO441_00173
ED_QUO441_00174
ED_QUO441_00175
ED_QUO441_00176
ED_QUO441_00177
ED_QUO441_00178
ED_QUO441_00179
ED_QUO441_00180
ED_QUO441_00181
ED_QUO441_00182
ED_QUO441_00183
ED_QUO441_00184
ED_QUO441_00185
ED_QUO441_00186
ED_QUO441_00187
ED_QUO441_00188
ED_QUO441_00189
ED_QUO441_00190
ED_QUO441_00191
ED_QUO441_00192
ED_QUO441_00193
ED_QUO441_00194
ED_QUO441_00195
ED_QUO441_00196
ED_QUO441_00197
ED_QUO441_00198
ED_QUO441_00199
ED_QUO441_00200
ED_QUO441_00201
ED_QUO441_00202
ED_QUO441_00203
ED_QUO441_00204
ED_QUO441_00205
ED_QUO441_00206
ED_QUO441_00207
ED_QUO441_00208
ED_QUO441_00209
ED_QUO441_00210
ED_QUO441_00211
ED_QUO441_00212
ED_QUO441_00213
ED_QUO441_00214
ED_QUO441_00215
ED_QUO441_00216
ED_QUO441_00217
ED_QUO441_00218
ED_QUO441_00219
ED_QUO441_00220
ED_QUO441_00221
ED_QUO441_00222
ED_QUO441_00223
ED_QUO441_00224
ED_QUO441_00225
ED_QUO441_00226
ED_QUO441_00227
ED_QUO441_00228
ED_QUO441_00229
ED_QUO441_00230
ED_QUO441_00231
ED_QUO441_00232
ED_QUO441_00233
ED_QUO441_00234
ED_QUO441_00235
ED_QUO441_00236
ED_QUO441_00237
ED_QUO441_00238
ED_QUO441_00239
ED_QUO441_00240
ED_QUO441_00241
ED_QUO441_00242
ED_QUO441_00243
ED_QUO441_00244
ED_QUO441_00245
ED_QUO441_00246
ED_QUO441_00247
ED_QUO441_00248
ED_QUO441_00249
ED_QUO441_00250
ED_QUO441_00251
ED_QUO441_00252
ED_QUO441_00253
ED_QUO441_00254
ED_QUO441_00255
ED_QUO441_00256
ED_QUO441_00257
ED_QUO441_00258
ED_QUO441_00259
ED_QUO441_00260
ED_QUO441_00261
ED_QUO441_00262
ED_QUO441_00263
ED_QUO441_00264
ED_QUO441_00265
ED_QUO441_00266
ED_QUO441_00267
ED_QUO441_00268
ED_QUO441_00269
ED_QUO441_00270
ED_QUO441_00271
ED_QUO441_00272
ED_QUO441_00273
ED_QUO441_00274
ED_QUO441_00275
ED_QUO441_00276
ED_QUO441_00277
ED_QUO441_00278
ED_QUO441_00279
ED_QUO441_00280
ED_QUO441_00281
ED_QUO441_00282
ED_QUO441_00283
ED_QUO441_00284
ED_QUO441_00285
ED_QUO441_00286
ED_QUO441_00287
ED_QUO441_00288
ED_QUO441_00289
ED_QUO441_00290
ED_QUO441_00291
ED_QUO441_00292
ED_QUO441_00293
ED_QUO441_00294
ED_QUO441_00295
ED_QUO441_00296
ED_QUO441_00297
ED_QUO441_00298
ED_QUO441_00299
ED_QUO441_00300
ED_QUO441_00301
ED_QUO441_00302
ED_QUO441_00303
ED_QUO441_00304
ED_QUO441_00305
ED_QUO441_00306
ED_QUO441_00307
ED_QUO441_00308
ED_QUO441_00309
ED_QUO441_00310
ED_QUO441_00311
ED_QUO441_00312
ED_QUO441_00313
ED_QUO441_00314
ED_QUO441_00315
ED_QUO441_00316
ED_QUO441_00317
ED_QUO441_00318
ED_QUO441_00319
ED_QUO441_00320
ED_QUO441_00321
ED_QUO441_00322
ED_QUO441_00323
ED_QUO441_00324
ED_QUO441_00325
ED_QUO441_00326
ED_QUO441_00327
ED_QUO441_00328
ED_QUO441_00329
ED_QUO441_00330
ED_QUO441_00331
ED_QUO441_00332
ED_QUO441_00333
ED_QUO441_00334
ED_QUO441_00335
ED_QUO441_00336
ED_QUO441_00337
ED_QUO441_00338
ED_QUO441_00339
ED_QUO441_00340
ED_QUO441_00341
ED_QUO441_00342
ED_QUO441_00343
ED_QUO441_00344
ED_QUO441_00345
ED_QUO441_00346
ED_QUO441_00347
ED_QUO441_00348
ED_QUO441_00349
ED_QUO441_00350
ED_QUO441_00351
ED_QUO441_00352
ED_QUO441_00353
ED_QUO441_00354
ED_QUO441_00355
ED_QUO441_00356
ED_QUO441_00357
ED_QUO441_00358
ED_QUO441_00359
ED_QUO441_00360
ED_QUO441_00361
ED_QUO441_00362
ED_QUO441_00363
ED_QUO441_00364
ED_QUO441_00365
ED_QUO441_00366
ED_QUO441_00367
ED_QUO441_00368
ED_QUO441_00369
ED_QUO441_00370
ED_QUO441_00371
ED_QUO441_00372
ED_QUO441_00373
ED_QUO441_00374
ED_QUO441_00375
ED_QUO441_00376
ED_QUO441_00377
ED_QUO441_00378
ED_QUO441_00379
ED_QUO441_00380
ED_QUO441_00381
ED_QUO441_00382
ED_QUO441_00383
ED_QUO441_00384
ED_QUO441_00385
ED_QUO441_00386
ED_QUO441_00387
ED_QUO441_00388
ED_QUO441_00389
ED_QUO441_00390
ED_QUO441_00391
ED_QUO441_00392
ED_QUO441_00393
ED_QUO441_00394
ED_QUO441_00395
ED_QUO441_00396
ED_QUO441_00397
ED_QUO441_00398
ED_QUO441_00399
ED_QUO441_00400
ED_QUO441_00401
ED_QUO441_00402
ED_QUO441_00403
ED_QUO441_00404
ED_QUO441_00405
ED_QUO441_00406
ED_QUO441_00407
ED_QUO441_00408
ED_QUO441_00409
ED_QUO441_00410
ED_QUO441_00411
ED_QUO441_00412
ED_QUO441_00413
ED_QUO441_00414
ED_QUO441_00415
ED_QUO441_00416
ED_QUO441_00417
ED_QUO441_00418
ED_QUO441_00419
ED_QUO441_00420
ED_QUO441_00421
ED_QUO441_00422
ED_QUO441_00423
ED_QUO441_00424
ED_QUO441_00425
ED_QUO441_00426
ED_QUO441_00427
ED_QUO441_00428
ED_QUO441_00429
ED_QUO441_00430
ED_QUO441_00431
ED_QUO441_00432
ED_QUO441_00433
ED_QUO441_00434
ED_QUO441_00435
ED_QUO441_00436
ED_QUO441_00437
ED_QUO441_00438
ED_QUO441_00439
ED_QUO441_00440
ED_QUO441_00441
ED_QUO441_00442
ED_QUO441_00443
ED_QUO441_00444
ED_QUO441_00445
ED_QUO441_00446
ED_QUO441_00447
ED_QUO441_00448
ED_QUO441_00449
ED_QUO441_00450
ED_QUO441_00451
ED_QUO441_00452
ED_QUO441_00453
ED_QUO441_00454
ED_QUO441_00455
ED_QUO441_00456
ED_QUO441_00457
ED_QUO441_00458
ED_QUO441_00459
ED_QUO441_00460
ED_QUO441_00461
ED_QUO441_00462
ED_QUO441_00463
ED_QUO441_00464
ED_QUO441_00465
ED_QUO441_00466
ED_QUO441_00467
ED_QUO441_00468
ED_QUO441_00469
ED_QUO441_00470
ED_QUO441_00471
ED_QUO441_00472
ED_QUO441_00473
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.2 Asset Age Profile
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
5.2 ASSET AGE PROFILE
There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data.
5.2.1 - ASSET AGE PROFILE
|  | ECONOMIC LIFE (YEARS) |  | INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR
ASSET GROUP | ASSET CATEGORY | MEAN | STANDARD DEVIATION | 2019-20 | 2018-19 | 2017-18 | 2016-17 | 2015-16 | 2014-15 | 2013-14 | 2012-13 | 2011-12 | 2010-11 | 2009-10 | 2008-09 | 2007-08 | 2006-07 | 2005-06 | 2004-05 | 2003-04 | 2002-03 | 2001-02 | 2000-01 | 1999-00 | 1998-99 | 1997-98 | 1996-97 | 1995-96 | 1994-95 | 1993-94 | 1992-93 | 1991-92 | 1990-91 | 1989-90 | 1988-89 | 1987-88 | 1986-87 | 1985-86 | 1984-85 | 1983-84 | 1982-83 | 1981-82 | 1980-81 | 1979-80 | 1978-79 | 1977-78 | 1976-77 | 1975-76 | 1974-75 | 1973-74 | 1972-73 | 1971-72 | 1970-71 | 1969-70 | 1968-69 | 1967-68 | 1966-67 | 1965-66 | 1964-65 | 1963-64 | 1962-63 | 1961-62 | 1960-61 | 1959-60 | 1958-59 | 1957-58 | 1956-57 | 1955-56 | 1954-55 | 1953-54 | 1952-53 | 1951-52 | 1950-51 | 1949-50 | 1948-49 | 1947-48 | 1946-47 | 1945-46 | 1944-45 | 1943-44 | 1942-43 | 1941-42 | 1940-41 | 1939-40 | 1938-39 | 1937-38 | 1936-37 | 1935-36 | 1934-35 | 1933-34 | 1932-33 | 1931-32 | 1930-31 | 1929-30 | 1928-29 | 1927-28 | 1926-27 | 1925-26 | 1924-25 | 1923-24 | 1922-23 | 1921-22 | 1920-21 | 1919-20 | 1918-19 | 1917-18 | 1916-17 | 1915-16 | 1914-15 | 1913-14 | 1912-13 | 1911-12
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole | 0 | 0 | 275 | 295 | 176 | 346 | 281 | 273 | 162 | 241 | 319 | 409 | 233 | 328 | 165 | 204 | 175 | 281 | 426 | 553 | 461 | 784 | 55 | 17 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Wood | 55 | 7.4162 | 916 | 680 | 2415 | 2182 | 1974 | 2149 | 2698 | 2670 | 1995 | 1744 | 1605 | 1828 | 2262 | 2236 | 2223 | 2146 | 2154 | 2527 | 2139 | 1864 | 2560 | 1574 | 1382 | 2139 | 2371 | 1826 | 2711 | 2159 | 1806 | 2609 | 3025 | 3123 | 2637 | 2593 | 2326 | 3114 | 1777 | 1841 | 4024 | 4516 | 3239 | 2663 | 2539 | 2663 | 2431 | 2952 | 2304 | 3995 | 3355 | 3949 | 2969 | 4193 | 4314 | 1821 | 2317 | 2382 | 1541 | 1939 | 1517 | 800 | 176 | 26 | 48 | 37 | 3 | 0 | 0 | 5 | 0 | 29 | 42 | 26 | 31 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; Wood | 55 | 7.4162 | 1294 | 841 | 1875 | 1842 | 1787 | 2246 | 2651 | 3204 | 2673 | 2675 | 2147 | 1898 | 2048 | 2248 | 2182 | 2294 | 1982 | 2643 | 2421 | 2056 | 2172 | 1375 | 1242 | 1968 | 1938 | 1358 | 1891 | 1408 | 1543 | 1966 | 2675 | 2348 | 1791 | 2033 | 1733 | 2759 | 1729 | 1824 | 3153 | 2956 | 2328 | 1690 | 1757 | 1732 | 1547 | 1840 | 1263 | 2106 | 1725 | 2540 | 1917 | 2126 | 2588 | 1162 | 1486 | 1124 | 852 | 851 | 633 | 278 | 24 | 12 | 7 | 5 | 2 | 0 | 0 | 1 | 0 | 5 | 15 | 3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Wood | 55 | 7.4162 | 23 | 28 | 161 | 93 | 85 | 146 | 57 | 39 | 50 | 63 | 30 | 78 | 55 | 37 | 36 | 32 | 28 | 44 | 27 | 57 | 32 | 30 | 37 | 74 | 33 | 40 | 58 | 36 | 24 | 25 | 98 | 90 | 51 | 50 | 44 | 121 | 66 | 66 | 182 | 151 | 44 | 43 | 25 | 24 | 27 | 45 | 63 | 37 | 36 | 53 | 12 | 13 | 24 | 19 | 25 | 14 | 3 | 6 | 7 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Wood | 55 | 7.4162 | 194 | 267 | 271 | 261 | 268 | 236 | 329 | 434 | 340 | 283 | 505 | 228 | 242 | 170 | 224 | 267 | 194 | 207 | 339 | 203 | 186 | 116 | 164 | 158 | 862 | 127 | 373 | 164 | 134 | 288 | 289 | 182 | 183 | 111 | 221 | 272 | 104 | 172 | 331 | 394 | 262 | 321 | 425 | 361 | 338 | 336 | 229 | 531 | 453 | 553 | 365 | 313 | 443 | 123 | 331 | 478 | 267 | 118 | 35 | 28 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Wood | 55 | 7.4162 | 49 | 25 | 54 | 79 | 57 | 64 | 61 | 30 | 67 | 51 | 37 | 38 | 34 | 35 | 33 | 39 | 47 | 21 | 27 | 42 | 39 | 7 | 28 | 27 | 39 | 14 | 34 | 23 | 283 | 59 | 35 | 25 | 32 | 59 | 39 | 23 | 19 | 30 | 19 | 28 | 23 | 71 | 148 | 56 | 48 | 30 | 22 | 11 | 63 | 101 | 128 | 64 | 57 | 21 | 16 | 25 | 53 | 92 | 17 | 12 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Concrete | 55 | 7.4162 | 22 | 44 | 138 | 135 | 124 | 129 | 304 | 166 | 136 | 196 | 145 | 274 | 303 | 254 | 222 | 177 | 168 | 66 | 5 |  | 6 | 8 | 7 | 24 | 114 | 130 | 266 | 139 | 118 | 150 | 123 | 228 | 172 | 90 | 211 | 212 | 23 | 10 | 17 | 6 | 1 | 1 | 2 | 1 | 0 | 1 | 3 | 3 | 0 | 4 | 0 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; Concrete | 55 | 7.4162 | 85 | 140 | 193 | 257 | 174 | 317 | 390 | 392 | 393 | 444 | 456 | 809 | 1093 | 1130 | 861 | 399 | 515 | 215 | 10 | 1 | 8 | 6 | 3 | 25 | 111 | 47 | 192 | 213 | 173 | 199 | 156 | 200 | 242 | 138 | 259 | 160 | 21 | 3 | 4 | 7 | 4 | 2 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Concrete | 55 | 7.4162 | 4 | 31 | 26 | 17 | 5 | 26 | 1 | 8 | 12 | 17 | 7 | 31 | 96 | 28 | 16 | 30 | 19 | 7 |  | 1 | 3 | 11 | 0 | 26 | 24 | 59 | 80 | 22 | 34 | 90 | 83 | 117 | 82 | 84 | 41 | 41 | 2 |  | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Concrete | 55 | 7.4162 | 19 | 68 | 26 | 15 | 28 | 13 | 99 | 694 | 138 | 139 | 361 | 174 | 99 | 82 | 230 | 84 | 80 | 14 | 19 | 11 | 22 | 19 | 1 | 1 | 216 | 9 | 85 | 7 | 8 | 24 | 38 | 111 | 28 | 62 | 66 | 160 | 26 | 41 | 2 | 2 | 1 | 0 | 0 | 2 | 2 | 1 | 3 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Concrete | 55 | 7.4162 | 0 | 0 | 20 | 3 | 44 | 14 | 68 | 86 | 89 | 52 | 101 | 28 | 59 | 342 | 52 | 102 | 41 | 5 | 54 | 5 | 8 | 0 | 1 | 1 | 180 | 0 | 53 | 199 | 39 | 3 | 86 | 78 | 24 | 438 | 4 | 4 | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Steel | 55 | 7.4162 | 42 | 99 | 155 | 109 | 91 | 101 | 48 | 51 | 55 | 30 | 14 | 66 | 65 | 65 | 24 | 28 | 64 | 21 | 13 | 6 | 8 | 9 | 7 | 8 | 15 | 12 | 17 | 24 | 8 | 8 | 8 | 5 | 3 | 9 | 5 | 7 | 6 | 5 | 0 | 1 | 2 | 4 | 1 | 5 | 1 | 4 | 4 | 4 | 8 | 2 | 4 | 2 | 3 | 2 | 2 | 5 | 5 | 4 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; Steel | 55 | 7.4162 | 82 | 103 | 144 | 124 | 85 | 92 | 13 | 7 | 9 | 5 | 7 | 27 | 18 | 29 | 8 | 5 | 1 | 1 | 3 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Steel | 55 | 7.4162 | 6 | 19 | 19 | 8 | 94 | 133 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Steel | 55 | 7.4162 | 4 | 47 | 17 | 4 | 23 | 125 | 11 | 17 | 56 | 53 | 18 | 0 | 15 | 18 | 0 | 5 | 6 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Steel | 55 | 7.4162 | 2 | 0 | 4 | 0 | 3 | 21 | 0 | 12 | 0 | 0 | 3 | 0 | 95 | 40 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 55 | 7.42 | 23 | 11 | 25 | 7 | 1 | 5 | 5 | 0 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV | 50 | 7.0711 | 76.3118 | 247.0868 | 190.1444 | 153.9414 | 196.6327 | 207.2662 | 328.3964 | 234.8409 | 226.7828 | 181.5668 | 201.8628 | 253.4478 | 270.3214 | 220.9937 | 199 | 186.4158 | 279.5415 | 217.4275 | 148.7319 | 174.9644 | 123.5841 | 128.4073 | 199.6097 | 235.9218 | 156.3824 | 288.3038 | 231.4124 | 207.1654 | 307.1978 | 287.9384 | 259.7118 | 191.1935 | 186.4183 | 157.8518 | 314.6814 | 130.4295 | 145.958 | 375.513 | 395.4904 | 299.4852 | 217.1069 | 213.035 | 220.4684 | 198.814 | 279.335 | 166.1143 | 373.509 | 311.1475 | 456.8146 | 313.8587 | 434.0212 | 522.8652 | 171.3577 | 270.7041 | 271.57 | 161.0216 | 194.0111 | 116.7052 | 49.9779 | 2.8986 | 0.57481 | 0.22481 | 0.33717 | 0.13614 | 0 | 0 | 0.19737 | 0 | 0.46052 | 9.6203 | 1.1098 | 1.7987 | 0.0193 | 0.01336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 50 | 7.0711 | 99.8048 | 158.6549 | 155.2094 | 143.3817 | 224.4151 | 214.879 | 325.7262 | 226.4203 | 224.0137 | 178.8215 | 180.0345 | 238.6964 | 264.6318 | 218.3969 | 185.9165 | 182.5158 | 248.5083 | 204.1839 | 161.5008 | 179.9956 | 149.1718 | 140.2043 | 191.4894 | 274.5874 | 158.3554 | 253.8203 | 196.0929 | 190.8288 | 270.5578 | 271.3907 | 244.9151 | 199.1454 | 209.0901 | 158.4318 | 257.218 | 152.3341 | 141.6453 | 308.5077 | 262.0783 | 192.1432 | 121.048 | 133.4314 | 137.1887 | 124.052 | 157.7881 | 108.0155 | 202.9691 | 146.2391 | 199.609 | 136.0329 | 141.3867 | 170.6851 | 79.1018 | 112.8144 | 88.3098 | 58.7244 | 54.7037 | 36.0194 | 24.2941 | 0.85164 | 0.64277 | 0.45518 | 0.02884 | 0.09778 | 0 | 0 | 0.19737 | 0 | 0.46052 | 6.9543 | 0.02849 | 0.60532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; SWER | 50 | 7.0711 | 7.5092 | 35.6711 | 30.6378 | 35.9054 | 15.7843 | 27.4934 | 1.2415 | 2.4101 | 15.4457 | 1.7429 | 7.6587 | 8.7048 | 7.8939 | 14.3219 | 2.0485 | 5.5966 | 4.3259 | 3.3702 | 4.4043 | 4.4702 | 5.6387 | 0.72811 | 15.798 | 15.2528 | 8.657 | 11.6048 | 3.4041 | 7.4824 | 12.5637 | 14.1559 | 18.3775 | 5.1958 | 3.3781 | 7.1083 | 21.0169 | 12.0324 | 3.5497 | 26.8714 | 16.2119 | 1.5158 | 0.66746 | 0 | 2.6784 | 9.6804 | 1.5971 | 5.084 | 8.0357 | 0 | 0 | 0.4013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19737 | 0 | 0.46052 | 0.41427 | 0.02849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Single-Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19737 | 0 | 0.46052 | 0 | 0.02849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase | 50 | 7.0711 | 8.4698 | 7.8265 | 8.9874 | 7.8643 | 22.2766 | 3.0416 | 3.9574 | 3.6489 | 2.5607 | 2.6954 | 11.5753 | 17.488 | 3.6001 | 2.6716 | 0.74812 | 1.2222 | 4.1641 | 1.6216 | 2.8585 | 2.1349 | 1.001 | 0.74076 | 3.6238 | 2.7485 | 6.6522 | 7.9609 | 3.7056 | 7.7715 | 13.7597 | 6.2683 | 24.2345 | 5.1768 | 11.0284 | 4.751 | 14.3306 | 2.2806 | 1.2331 | 5.6815 | 10.2243 | 2.1595 | 5.2651 | 0.60333 | 0.51284 | 0.41859 | 3.4122 | 5.1433 | 2.2743 | 2.0482 | 3.0296 | 0.51097 | 1.0773 | 1.9763 | 0.25245 | 3.7375 | 0.75957 | 0.045341 | 0 | 0.22069 | 0.29278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19737 | 0 | 0.46052 | 4.559 | 0.02849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV | 55 | 7.4162 | 47.5577 | 16.7722 | 13.3688 | 14.9194 | 41.4384 | 20.8918 | 117.5216 | 35.2771 | 35.1856 | 80.1659 | 24.6784 | 48.019 | 28.1599 | 46.2462 | 29.6501 | 17.2937 | 19.5463 | 38.0204 | 24.0905 | 34.3843 | 13.6758 | 27.0705 | 27.7168 | 121.6345 | 36.6152 | 88.6158 | 20.6836 | 15.2863 | 28.6555 | 28.7795 | 17.0351 | 17.2678 | 12.0692 | 24.9892 | 44.1183 | 5.5414 | 16.7094 | 25.9113 | 28.2516 | 16.6801 | 36.087 | 35.3214 | 47.8612 | 36.2784 | 29.819 | 20.151 | 48.1845 | 51.562 | 54.4554 | 24.8118 | 25.5104 | 46.507 | 12.8384 | 34.0676 | 47.0058 | 37.9903 | 6.8285 | 1.1134 | 0.3689 | 0.0028944 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19737 | 0 | 0.46052 | 0 | 0.02849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 55 | 7.4162 | 10.567 | 19.3808 | 18.5022 | 25.3947 | 11.9471 | 16.0502 | 19.5297 | 16.0481 | 13.1515 | 19.32 | 11.7068 | 32.722 | 74.1484 | 6.6386 | 24.604 | 23.288 | 19.5595 | 15.0432 | 20.6158 | 12.0725 | 7.4214 | 3.0472 | 17.259 | 43.3782 | 57.4974 | 34.1475 | 43.2285 | 47.8196 | 10.1067 | 29.5575 | 17.904 | 13.8594 | 73.6156 | 5.1342 | 13.1348 | 2.6134 | 8.0187 | 12.535 | 15.4769 | 15.7366 | 11.2848 | 44.6774 | 8.6117 | 13.3942 | 7.2544 | 6.3494 | 9.7322 | 14.0679 | 25.1014 | 19.9582 | 29.1552 | 27.8972 | 6.3594 | 5.8551 | 4.0593 | 17.2657 | 16.0512 | 3.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19737 | 0 | 0.46052 | 0.69055 | 0.02849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19737 | 0 | 0.46052 | 0 | 0.02849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV | 60 | 7.746 | 378.9794 | 628.9906 | 574.7103 | 505.4581 | 477.6711 | 461.2435 | 357.9951 | 409.9856 | 303.0007 | 319.211 | 309.3647 | 274.2611 | 353.4587 | 237.0674 | 784.2969 | 275.2238 | 324.7609 | 171.3686 | 186.0897 | 187.1762 | 204.7604 | 205.9683 | 110.8862 | 157.3628 | 168.0602 | 201.7589 | 193.9798 | 178.2435 | 194.0631 | 288.6505 | 282.7316 | 244.184 | 209.4043 | 267.7051 | 307.7571 | 225.683 | 397.1488 | 457.2428 | 528.7267 | 292.0735 | 224.822 | 162.2568 | 141.1737 | 121.9002 | 176.4883 | 66.2421 | 58.8797 | 35.7441 | 24.9651 | 13.2157 | 11.8087 | 12.8198 | 2.7227 | 6.8968 | 6.9921 | 5.8794 | 4.8508 | 4.5291 | 2.0051 | 1.5289 | 0.56922 | 0 | 0.44666 | 0 | 0.59794 | 0 | 0.21082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 60 | 7.746 | 255.9122 | 319.7744 | 246.4314 | 198.9104 | 238.8445 | 211.7192 | 198.5276 | 220.1867 | 152.5238 | 138.0709 | 140.2278 | 119.3745 | 150.1396 | 132.5958 | 181.9779 | 139.8427 | 152.6811 | 43.4493 | 51.9775 | 57.8884 | 61.7492 | 65.4919 | 34.2936 | 52.7812 | 54.6592 | 68.8941 | 45.4523 | 45.7565 | 59.2704 | 80.2502 | 69.4706 | 61.4256 | 57.1874 | 67.9923 | 79.151 | 51.8044 | 90.6038 | 91.6499 | 108.2404 | 64.1938 | 55.2156 | 44.3355 | 31.0199 | 32.6892 | 48.7291 | 19.8057 | 16.4269 | 9.2985 | 8.3656 | 8.0464 | 6.9617 | 8.0078 | 1.3585 | 2.0968 | 2.0765 | 1.4999 | 0.77964 | 2.3954 | 0.2919 | 0.04418 | 0.68217 | 0 | 0.05881 | 0 | 0.24139 | 0 | 0.088648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV | 60 | 7.746 | 19.5914 | 32.6308 | 38.1514 | 16.5378 | 13.1515 | 13.1901 | 17.7165 | 13.4254 | 10.2934 | 15.0034 | 10.0877 | 8.3642 | 17.5154 | 13.6681 | 19.6163 | 18.0286 | 29.0118 | 9.7947 | 13.1312 | 12.8434 | 8.9016 | 11.0149 | 2.9359 | 5.2602 | 3.8365 | 2.9457 | 2.1274 | 0.1603 | 0.45552 | 0.28501 | 0.24638 | 0.29565 |  | 0.57478 | 1.1053 | 0.51859 |  | 0.68958 |  | 0.63787 | 0.04716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV | 45 | 6.7082 | 13.5505 | 8.8978 | 3.4331 | 8.5999 | 9.6022 | 8.4489 | 23.2638 | 11.3095 | 8.8257 | 11.4192 | 3.6282 | 21.9196 | 7.8828 | 3.1753 | 1.6462 | 5.2039 | 3.7891 | 0.30046 | 5.0115 | 0 | 0.02183 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.38718 | 0 | 0 |  |  |  |  | 5.9712 |  | 4.2593 |  |  | 0.59966 | 1.2229 | 0 | 11.4734 | 1.0681 | 3.765 | 0 | 2.1269 | 2.514 | 4.9709 | 2.2444 | 3.344 | 3.0543 | 0.57939 | 6.6591 | 4.7046 | 0.33043 | 0 | 0.8532 | 0 | 0.56797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV | 45 | 6.7082 | 1.175 | 4.3477 |  | 2.7915 | 0.89536 | 0.36584 | 7.823 | 7.0996 | 0.84781 | 0.56558 | 0.08508 | 0 | 0 | 0.44811 | 0 | 0 | 0 | 0 | 2.8219 | 0 | 0 | 0 | 0 | 1.1637 | 0 | 0 | 0 | 0 | 0 | 0.24188 | 3.8483 | 5.0029 |  | 0.097105 | 2.1355 | 0.67521 | 0.38217 | 0.23974 |  |  | 0.21529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.426 | 2.6195 | 0.33043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 45 | 6.7082 | 2.0944 | 10.1258 | 4.7715 | 16.7912 | 1.9958 | 2.8449 | 20.2868 | 19.2731 | 18.9012 | 11.6426 | 3.6712 | 2.3566 | 8.0953 | 0.0339 | 0 | 0.56804 | 0 | 0 | 0 | 1.5022 | 0 | 0 | 0 | 0 | 0 | 1.4842 | 0 | 0 | 0.92212 | 0 | 0 |  |  | 0.64507 |  |  |  |  | 5.0217 |  |  | 0 | 0 | 1.4842 | 0 | 0.64507 | 0 | 0 | 0 | 2.8584 |  | 0 | 0 | 0 | 15.8894 | 0.5145 | 0.33043 | 0 | 0 | 0 | 7.4866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type | 35 | 5.9161 | 37066 | 17789 | 13012 | 11708 | 8902 | 9053 | 9666 | 8724 | 13367 | 10758 | 10599 | 13201 | 13533 | 9822 | 5416 | 4422 | 7457 | 4237 | 3140 | 4053 | 2544 | 2397 | 3833 | 5008 | 3985 | 6323 | 4891 | 3926 | 5206 | 5818 | 5435 | 4775 | 4392 | 4379 | 5853 | 3091 | 3921 | 7427 | 7858 | 6033 | 5074 | 4991 | 4677 | 4214 | 5851 | 4440 | 7741 | 6757 | 8641 | 6348 | 8753 | 9612 | 4817 | 6319 | 5933 | 3546 | 6093 | 3758 | 1772 | 651 | 59 | 88 | 109 | 5 | 0 | 0 | 18 | 0 | 28 | 218 | 24 | 82 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Residential ; Complex Type | 60 | 7.746 | 21332 | 20667 | 19649 | 16688 | 13377 | 13245 | 10682 | 12145 | 12230 | 10482 | 8550 | 8483 | 9774 | 5688 | 9089 | 3294 | 9972 | 5426 | 6516 | 6638 | 7340 | 8079 | 3897 | 6155 | 6599 | 7365 | 6936 | 5784 | 6000 | 7881 | 7108 | 5361 | 4193 | 5344 | 6158 | 4403 | 7882 | 9276 | 10379 | 6129 | 4203 | 3203 | 2886 | 2780 | 4043 | 1746 | 1610 | 1123 | 468 | 303 | 320 | 347 | 48 | 95 | 139 | 120 | 111 | 76 | 43 | 22 | 10 | 0 | 121 | 0 | 12 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Subdivision ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 45 | 6.7082 | 68 | 43 | 59 | 34 | 30 | 71 | 50 | 69 | 44 | 65 | 58 | 45 | 54 | 61 | 86 | 65 | 47 | 51 | 47 | 42 | 37 | 53 | 62 | 14 | 31 | 41 | 38 | 45 | 39 | 32 | 72 | 112 | 93 | 72 | 44 | 58 | 38 | 38 | 83 | 52 | 32 | 12 | 17 | 6 | 14 | 11 | 10 | 8 | 27 | 10 | 19 | 5 | 9 | 6 | 2 | 9 | 5 | 10 | 4 |  | 1 | 1 | 3 | 3 | 4 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 45 | 6.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 3 | 5 | 3 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 45 | 6.7082 | 24 | 58 | 17 | 18 | 21 | 43 | 26 | 45 | 70 | 42 | 70 | 69 | 86 | 64 | 64 | 83 | 115 | 76 | 84 | 64 | 41 | 91 | 115 | 22 | 44 | 69 | 83 | 80 | 95 | 70 | 94 | 99 | 115 | 97 | 86 | 75 | 57 | 66 | 124 | 119 | 83 | 73 | 61 | 40 | 49 | 43 | 47 | 17 | 46 | 55 | 59 | 67 | 72 | 40 | 45 | 34 | 46 | 51 | 23 | 11 | 16 | 5 | 3 | 8 | 3 | 5 | 3 | 6 | 4 | 2 | 0 | 2 | 3 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 45 | 6.7082 | 152 | 217 | 242 | 199 | 142 | 199 | 187 | 233 | 175 | 260 | 354 | 433 | 465 | 454 | 506 | 451 | 672 | 360 | 448 | 476 | 189 | 158 | 255 | 39 | 172 | 181 | 93 | 76 | 167 | 147 | 204 | 190 | 210 | 109 | 184 | 145 | 259 | 317 | 266 | 421 | 318 | 256 | 137 | 94 | 126 | 98 | 78 | 90 | 175 | 112 | 202 | 155 | 174 | 133 | 148 | 110 | 93 | 102 | 54 | 54 | 119 | 13 | 5 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 |  | 1 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 45 | 6.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 45 | 6.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 45 | 6.7082 | 90 | 434 | 316 | 275 | 157 | 132 | 229 | 267 | 285 | 345 | 345 | 294 | 364 | 404 | 388 | 441 | 508 | 288 | 336 | 271 | 169 | 150 | 98 | 71 | 131 | 95 | 97 | 72 | 52 | 79 | 161 | 115 | 98 | 146 | 105 | 79 | 62 | 201 | 225 | 200 | 136 | 92 | 55 | 30 | 64 | 91 | 76 | 50 | 18 | 10 | 18 | 11 | 4 | 6 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 45 | 6.7082 | 121 | 172 | 153 | 87 | 54 | 48 | 75 | 77 | 64 | 95 | 79 | 137 | 178 | 117 | 190 | 108 | 157 | 123 | 77 | 83 | 51 | 158 | 74 | 48 | 38 | 70 | 51 | 22 | 22 | 18 | 29 | 20 | 39 | 30 | 24 | 17 | 11 | 34 | 15 | 13 | 3 | 5 | 8 | 2 | 3 | 1 | 1 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase | 45 | 6.7082 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 3 | 11 | 8 | 1 | 1 | 3 | 4 | 5 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 1 |  | 3 | 6 | 9 | 0 | 2 | 0 | 0 | 3 | 2 | 0 | 0 | 2 | 0 | 4 | 0 | 2 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 45 | 6.7082 | 0 | 5 | 3 | 1 | 5 | 1 | 2 | 6 | 4 | 7 | 4 | 5 | 1 | 7 | 6 | 7 | 0 | 7 | 0 | 4 | 0 | 6 | 10 |  | 3 | 8 | 13 | 8 | 10 | 14 | 5 | 4 | 7 | 6 | 7 | 3 | 10 | 9 | 7 | 8 | 7 | 7 | 6 | 14 | 18 | 8 | 7 | 1 | 6 | 12 | 17 | 13 | 5 | 9 | 4 | 6 | 8 | 9 | 3 | 4 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase | 45 | 6.7082 | 0 | 3 | 2 | 0 | 0 | 0 | 1 | 2 | 0 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 3 | 1 | 2 | 4 | 1 | 0 | 7 | 3 | 5 | 2 | 8 | 11 | 7 | 5 | 1 | 12 | 8 | 16 | 2 | 6 | 7 | 1 |  | 4 | 7 | 6 | 5 | 7 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA | 50 | 7.0711 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 2 | 2 | 1 | 3 | 5 | 2 | 0 | 0 | 3 | 2 | 2 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 4 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 4 | 1 | 1 | 2 | 0 | 1 | 3 | 1 | 8 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA | 50 | 7.0711 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 8 | 5 | 8 | 2 | 18 | 5 | 1 | 5 | 8 | 15 | 1 | 4 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 1 | 0 | 2 | 2 | 0 | 0 | 4 | 2 | 5 | 4 | 2 | 3 | 6 | 3 |  | 2 | 4 | 5 | 2 | 7 | 7 | 5 | 1 | 5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA | 50 | 7.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA | 50 | 7.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 4 | 0 | 0 | 2 | 4 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 5 | 0 | 2 | 3 | 2 | 0 | 0 | 2 |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA | 50 | 7.0711 | 0 | 0 | 2 | 0 | 0 | 1 | 1 | 4 | 4 | 4 | 0 | 10 | 9 | 0 | 7 | 10 | 1 | 8 | 1 | 3 | 2 | 0 | 0 | 2 | 2 | 1 |  | 2 | 2 | 1 | 0 | 0 | 5 | 0 | 3 | 2 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA | 50 | 7.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 0 | 0 | 3 | 0 | 10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 1 | 2 | 0 | 0 | 0 | 4 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 45 | 6.7082 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 6 | 3 | 9 |  |  | 12 | 5 | 2 | 2 | 1 | 2 | 0 | 0 | 0 | 2 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; Fuse | 35 | 5.9161 | 511 | 609 | 1026 | 1057 | 1224 | 951 | 1029 | 977 | 944 | 931 | 897 | 797 | 621 | 628 | 671 | 834 | 951 | 712 | 742 | 544 | 516 | 327 | 360 | 313 | 376 | 428 | 410 | 447 | 392 | 554 | 533 | 630 | 531 | 477 | 543 | 686 | 810 | 796 | 1853 | 959 | 710 | 507 | 502 | 384 | 435 | 238 | 119 | 103 | 122 | 91 | 132 | 101 | 93 | 82 | 65 | 95 | 76 | 46 | 42 | 39 | 172 | 21 | 12 | 27 | 3 | 11 | 20 | 26 | 9 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Switch | 35 | 5.9161 | 994 | 977 | 1294 | 932 | 968 | 972 | 1532 | 1413 | 1402 | 1203 | 1376 | 1447 | 1288 | 1381 | 1474 | 1285 | 1023 | 1042 | 969 | 943 | 853 | 623 | 377 | 343 | 358 | 366 | 390 | 389 | 330 | 554 | 599 | 507 | 576 | 508 | 618 | 423 | 480 | 567 | 645 | 490 | 498 | 414 | 344 | 253 | 336 | 296 | 263 | 226 | 270 | 183 | 194 | 216 | 112 | 101 | 157 | 73 | 62 | 43 | 27 | 6 | 61 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Circuit Breaker | 45 | 6.7082 | 18 | 24 | 160 | 27 | 46 | 134 | 70 | 187 | 234 | 152 | 173 | 210 | 133 | 162 | 197 | 174 | 193 | 96 | 47 | 82 | 28 | 39 | 42 | 28 | 12 | 27 | 26 | 4 | 10 | 39 | 27 | 43 | 35 | 42 | 36 | 116 | 135 | 64 | 81 | 32 | 11 | 12 | 1 | 23 | 11 | 4 | 2 |  | 3 | 6 | 4 | 1 | 5 | 12 | 10 | 2 | 14 | 5 | 14 | 0 | 2 | 3 | 0 | 0 | 0 | 10 | 0 | 3 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Switch | 35 | 5.9161 | 2 | 39 | 37 | 52 | 56 | 198 | 82 | 33 | 37 | 19 | 19 | 32 | 30 | 24 | 42 | 30 | 37 | 23 | 39 | 16 | 4 | 2 | 3 | 0 | 2 | 2 | 1 | 0 | 1 | 1 | 2 | 9 | 2 | 4 | 4 | 3 | 3 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker | 45 | 6.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 30 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Switch | 35 | 5.9161 | 1 | 0 | 4 | 14 | 9 | 0 | 13 | 8 | 4 | 3 | 2 | 2 | 1 | 4 | 5 | 6 | 5 | 9 | 4 | 0 | 8 | 2 | 0 | 1 | 0 | 1 | 3 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker | 45 | 6.7082 | 0 | 9 | 25 | 1 | 3 | 15 | 53 | 71 | 68 | 59 | 33 | 84 | 60 | 84 | 16 | 35 | 24 | 23 | 14 | 11 | 10 | 4 | 2 | 3 | 9 | 11 | 8 | 0 | 0 | 39 | 18 | 1 | 3 | 1 | 0 | 12 | 16 | 14 | 24 | 19 | 3 | 3 | 5 | 4 | 4 | 1 | 0 | 0 | 1 | 7 | 6 | 15 | 3 | 12 | 2 | 2 | 2 | 0 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Switch | 35 | 5.9161 | 2 | 0 | 0 | 2 | 3 | 4 | 12 | 3 | 5 | 4 | 3 | 1 | 4 | 2 | 1 | 2 | 4 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker | 45 | 6.7082 | 1 | 0 | 0 | 0 | 0 | 8 | 1 | 8 | 21 | 15 | 4 | 12 | 12 | 15 | 21 | 4 | 0 | 0 | 20 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 2 | 0 | 0 | 9 | 3 | 0 | 5 | 0 | 5 | 0 | 4 | 0 | 7 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Circuit Breaker | 45 | 6.7082 | 2 | 3 | 2 | 1 | 5 | 8 | 14 | 19 | 33 | 3 | 8 | 49 | 33 | 58 | 26 | 25 | 25 | 7 | 9 | 2 | 14 | 11 | 0 | 6 | 4 | 8 | 1 | 2 | 0 | 10 | 0 | 3 | 3 | 2 | 4 | 0 | 0 | 3 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 35 | 5.9161 | 11 | 0 | 16 | 12 | 5 | 24 | 16 | 22 | 7 | 6 | 0 | 2 |  | 2 |  | 7 |  | 1 |  | 1 | 3 | 1 | 2 | 6 | 5 | 11 | 8 | 9 | 10 | 22 | 13 | 21 | 18 | 9 | 33 | 152 | 158 | 11 | 2 | 47 | 1 | 3 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Luminaires ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamps ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamps ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 20 | 4.4721 | 1846 | 3194 | 3571 | 4100 | 3608 | 3687 | 3132 | 2666 | 1524 | 2583 | 1491 | 2747 | 2935 | 3952 | 4539 | 5422 | 8585 | 9100 | 9131 | 10211 | 9578 | 8315 | 8199 | 8082 | 4839 | 5054 | 4486 | 3906 | 3920 | 4571 | 4228 | 4262 | 4557 | 5029 | 4849 | 3424 | 3995 | 4368 | 4215 | 5293 | 5110 | 4928 | 3487 | 3732 | 2977 | 2634 | 2340 | 1521 | 1379 | 1825 | 1491 | 1197 | 904 | 340 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices | 10 | 3.1623 | 524 | 213 | 125 | 135 | 100 | 114 | 114 | 25 | 40 | 44 | 3 | 32 | 38 | 25 | 47 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Local Network Wiring Assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Network Assets | 10 | 3.1623 | 9 | 20 | 37 | 41 | 32 | 34 | 37 | 20 | 25 | 10 | 3 | 7 | 13 | 7 | 12 | 9 | 15 | 16 | 13 | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Master Station Assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Site Infrastructure | 50 | 7.0711 | 0 | 0 | 0 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 0 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Linear Assets | 50 | 7.0711 | 71.9478 | 27.0014 | 55.4884 | 148.9438 | 79.9514 | 93.4909 | 34.9125 | 75.279 | 149.0209 | 36.1284 | 11.0469 | 1.7369 | 0 | 63.1378 | 0 | 27.6174 | 0 | 0 | 0 | 0 | 10.0846 | 0 | 0 | 0 | 0 | 0 | 7.0803 | 0 | 0 | 15.182 | 0.13151 | 0 | 0 | 3.672 | 0.9226 | 2.637 | 2.2677 | 0 | 13.593 | 9.519 | 0 | 14.0741 | 18.8336 | 15.2938 | 17.2058 | 3.7579 | 6.9216 | 5.7748 | 21.0488 | 36.5402 | 32.5983 | 30.4295 | 22.9213 | 0.6589 | 31.7609 | 55.9346 | 57.0357 | 56.31 | 0 | 23.7451 | 15.7421 | 0 | 6.5924 | 7.528 | 10.9894 | 2.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AFLC | 50 | 7.0711 | 5 | 3 | 1 | 1 | 8 | 16 | 18 | 15 | 10 | 13 | 6 | 17 | 7 | 10 | 15 | 8 | 6 | 0 | 2 | 3 | 0 | 11 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 3 | 1 | 3 | 5 | 8 | 8 | 7 | 0 | 0 | 2 | 2 | 0 | 1 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BY: DNSP DEFINED | Substation Establishment: Major Indoor | 50 | 7.0711 | 0 | 0 | 0 | 0 | 1 | 2 | 4 | 6 | 5 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Establishment: Major Outdoor | 50 | 7.0711 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 2 | 2 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 3 | 0 | 3 | 2 | 2 | 2 | 4 | 1 | 1 | 3 | 3 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Establishment: Medium Indoor | 50 | 7.0711 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 4 | 3 | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Establishment: Medium Outdoor | 50 | 7.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 3 | 3 | 1 | 3 | 0 | 3 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Establishment: Small Indoor | 50 | 7.0711 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Establishment: Small Outdoor | 50 | 7.0711 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Establishment: Type A | 50 | 7.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Establishment: Type B | 50 | 7.0711 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Distribution Sub - Chamber Type | 45 | 6.7082 | 12 | 7 | 16 | 9 | 15 | 12 | 12 | 14 | 9 | 6 | 8 | 10 | 5 | 19 | 12 | 16 | 14 | 14 | 7 | 5 | 9 | 4 | 5 | 4 | 6 | 12 | 6 | 10 | 9 | 18 | 14 | 16 | 24 | 20 | 14 | 10 | 15 | 13 | 8 | 10 | 8 | 7 | 9 | 3 | 21 | 9 | 5 | 2 | 6 | 2 | 3 | 8 | 1 | 1 | 3 | 1 | 5 | 4 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Distribution OH Sub < 64KVA | 45 | 6.7082 | 45 | 43 | 61 | 109 | 98 | 73 | 71 | 69 | 118 | 69 | 78 | 78 | 73 | 111 | 100 | 113 | 137 | 156 | 138 | 131 | 165 | 146 | 141 | 130 | 133 | 182 | 167 | 194 | 168 | 201 | 225 | 228 | 176 | 172 | 246 | 443 | 535 | 323 | 529 | 238 | 192 | 126 | 87 | 81 | 92 | 72 | 47 | 68 | 49 | 35 | 63 | 57 | 102 | 50 | 58 | 64 | 52 | 39 | 44 | 45 | 27 | 32 | 23 | 41 | 18 | 23 | 32 | 34 | 24 | 15 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Distribution OH Sub >= 64KVA | 45 | 6.7082 | 41 | 30 | 27 | 11 | 17 | 41 | 49 | 56 | 93 | 91 | 116 | 104 | 121 | 138 | 93 | 162 | 211 | 203 | 163 | 146 | 112 | 88 | 70 | 57 | 104 | 119 | 130 | 139 | 114 | 207 | 165 | 179 | 172 | 95 | 121 | 176 | 269 | 215 | 903 | 807 | 526 | 389 | 361 | 328 | 329 | 201 | 95 | 93 | 133 | 115 | 158 | 149 | 215 | 196 | 198 | 182 | 165 | 119 | 111 | 116 | 162 | 89 | 87 | 87 | 81 | 86 | 92 | 86 | 81 | 83 | 81 | 80 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11/22 - kiosk and pad mount <=500kVA Substn | 45 | 6.7082 | 280 | 438 | 490 | 473 | 446 | 358 | 286 | 267 | 236 | 320 | 236 | 185 | 186 | 212 | 200 | 291 | 383 | 234 | 220 | 182 | 194 | 148 | 144 | 119 | 142 | 158 | 128 | 138 | 111 | 180 | 186 | 186 | 174 | 168 | 210 | 187 | 169 | 290 | 358 | 257 | 187 | 136 | 108 | 83 | 115 | 99 | 48 | 36 | 14 | 10 | 10 | 3 | 9 | 8 | 8 | 9 | 7 | 5 | 9 | 8 | 13 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11/22 - kiosk and pad mount >500kVA Substn | 45 | 6.7082 | 157 | 66 | 80 | 49 | 71 | 71 | 75 | 60 | 70 | 81 | 49 | 72 | 83 | 88 | 82 | 92 | 85 | 81 | 53 | 67 | 52 | 60 | 43 | 41 | 34 | 35 | 27 | 27 | 29 | 47 | 30 | 34 | 30 | 34 | 31 | 26 | 12 | 32 | 50 | 33 | 29 | 24 | 19 | 9 | 16 | 16 | 1 | 3 | 8 | 2 | 1 | 2 | 4 | 1 | 2 | 2 | 3 | 2 | 2 | 2 | 4 | 2 | 2 | 1 | 2 | 3 | 2 | 2 | 1 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11/22 Switching Station | 45 | 6.7082 | 15 | 9 | 7 | 3 | 6 | 30 | 23 | 23 | 17 | 5 | 7 | 6 | 8 | 7 | 9 | 14 | 14 | 7 | 1 | 3 | 8 | 4 | 10 | 2 | 4 | 8 | 7 | 14 | 7 | 3 | 5 | 1 | 5 | 7 | 6 | 3 | 8 | 22 | 3 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacitor Banks | 50 | 7.0711 | 0 | 1 | 3 | 0 | 4 | 0 | 6 | 4 | 3 | 11 | 1 | 2 | 6 | 1 | 0 | 7 | 36 | 35 | 11 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 13 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Towers | 60 | 7.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 38 | 37 | 72 | 4 | 6 | 0 | 74 | 109 | 1 | 0 | 0 | 23 | 56 | 0 | 0 | 12 | 0 | 105 | 81 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.3 MD - Network level
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
5.3 MAXIMUM DEMAND AT NETWORK LEVEL
5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL (Summed at transmission connection point)
| UNIT | 2019-20
Raw network coincident MD | MW | 4056
Date MD occurred |  | 2020-02-01
Half hour time period MD occurred |  | 17:30
Winter/summer peaking |  | Summer
Embedded generation | MW | 419.7103
Weather corrected (10% POE) network coincident MD | MW | 3998
Weather corrected (50% POE) network coincident MD | MW | 3622
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.4 MD & utilisation-Spatial
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL
There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data.
5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2019-20
SUBTRANSMISSION SUBSTATION | Dapto BSP | Substation Rating | MVA | Non-Coincident | 1125
|  |  |  | Coincident | 1125
|  | Raw Adjusted MD | MW | Non-Coincident | 556.5233
|  |  |  | Coincident | 202.3883
|  | Raw Adjusted MD | MVA | Non-Coincident | 563.493
|  |  |  | Coincident | 263.6902
|  | Date MD occurred |  | Non-Coincident | 2020-01-28
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 382.7382
|  |  |  | Coincident | 377.4531
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 666.85
|  |  |  | Coincident | 242.5103
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 669.82
|  |  |  | Coincident | 313.4466
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 666.85
|  |  |  | Coincident | 242.5103
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 669.82
|  |  |  | Coincident | 313.4466
| Holroyd BSP | Substation Rating | MVA | Non-Coincident | 375
|  |  |  | Coincident | 375
|  | Raw Adjusted MD | MW | Non-Coincident | 344.4839
|  |  |  | Coincident | 270.9254
|  | Raw Adjusted MD | MVA | Non-Coincident | 344.4909
|  |  |  | Coincident | 276.4841
|  | Date MD occurred |  | Non-Coincident | 2020-01-28
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 14:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.74046
|  |  |  | Coincident | 0.60735
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 366.78
|  |  |  | Coincident | 288.4606
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 366.7906
|  |  |  | Coincident | 294.3816
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 336.43
|  |  |  | Coincident | 264.5913
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 336.4398
|  |  |  | Coincident | 270.0224
| Ilford BSP | Substation Rating | MVA | Non-Coincident | 60
|  |  |  | Coincident | 60
|  | Raw Adjusted MD | MW | Non-Coincident | 5.1134
|  |  |  | Coincident | 4.4676
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.1135
|  |  |  | Coincident | 4.4702
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.184
|  |  |  | Coincident | 4.5293
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.1892
|  |  |  | Coincident | 4.5364
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.184
|  |  |  | Coincident | 4.5293
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.1892
|  |  |  | Coincident | 4.5364
| Ingleburn BSP | Substation Rating | MVA | Non-Coincident | 219
|  |  |  | Coincident | 219
|  | Raw Adjusted MD | MW | Non-Coincident | 130.4575
|  |  |  | Coincident | 120.187
|  | Raw Adjusted MD | MVA | Non-Coincident | 135.1904
|  |  |  | Coincident | 124.5755
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 137.89
|  |  |  | Coincident | 127.0344
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 142.8923
|  |  |  | Coincident | 131.6727
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 124.25
|  |  |  | Coincident | 114.4682
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 128.7575
|  |  |  | Coincident | 118.6477
| Liverpool BSP | Substation Rating | MVA | Non-Coincident | 750
|  |  |  | Coincident | 750
|  | Raw Adjusted MD | MW | Non-Coincident | 447.0994
|  |  |  | Coincident | 442.1727
|  | Raw Adjusted MD | MVA | Non-Coincident | 451.2862
|  |  |  | Coincident | 446.2706
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 430.59
|  |  |  | Coincident | 425.8452
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 434.6253
|  |  |  | Coincident | 429.7948
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 380.09
|  |  |  | Coincident | 375.9017
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 383.652
|  |  |  | Coincident | 379.3881
| Macarthur 66kV BSP | Substation Rating | MVA | Non-Coincident | 250
|  |  |  | Coincident | 250
|  | Raw Adjusted MD | MW | Non-Coincident | 146.6968
|  |  |  | Coincident | 146.3116
|  | Raw Adjusted MD | MVA | Non-Coincident | 147.1843
|  |  |  | Coincident | 146.8475
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 36.8517
|  |  |  | Coincident | 37.8537
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 160.253
|  |  |  | Coincident | 159.8322
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 160.7855
|  |  |  | Coincident | 160.4176
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 143.095
|  |  |  | Coincident | 142.7193
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 143.5705
|  |  |  | Coincident | 143.2419
| Macarthur 132kV BSP | Substation Rating | MVA | Non-Coincident | 375
|  |  |  | Coincident | 375
|  | Raw Adjusted MD | MW | Non-Coincident | 170.9885
|  |  |  | Coincident | 121.2965
|  | Raw Adjusted MD | MVA | Non-Coincident | 172.1373
|  |  |  | Coincident | 122.2827
|  | Date MD occurred |  | Non-Coincident | 2019-12-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 185.49
|  |  |  | Coincident | 131.5836
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 186.7375
|  |  |  | Coincident | 132.6544
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 166.19
|  |  |  | Coincident | 117.8925
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 167.3077
|  |  |  | Coincident | 118.8519
| Marulan BSP | Substation Rating | MVA | Non-Coincident | 160
|  |  |  | Coincident | 160
|  | Raw Adjusted MD | MW | Non-Coincident | 80.064
|  |  |  | Coincident | 74.892
|  | Raw Adjusted MD | MVA | Non-Coincident | 83.749
|  |  |  | Coincident | 78.3389
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 80.06
|  |  |  | Coincident | 74.8883
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 83.75
|  |  |  | Coincident | 78.3398
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 80.06
|  |  |  | Coincident | 74.8883
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 83.75
|  |  |  | Coincident | 78.3398
| Mount Piper BSP | Substation Rating | MVA | Non-Coincident | 120
|  |  |  | Coincident | 120
|  | Raw Adjusted MD | MW | Non-Coincident | 28.3866
|  |  |  | Coincident | 21.686
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.0426
|  |  |  | Coincident | 22.8857
|  | Date MD occurred |  | Non-Coincident | 2019-11-26
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.39
|  |  |  | Coincident | 21.6886
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.0459
|  |  |  | Coincident | 22.8882
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.39
|  |  |  | Coincident | 21.6886
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.0459
|  |  |  | Coincident | 22.8882
| Regentville BSP | Substation Rating | MVA | Non-Coincident | 375
|  |  |  | Coincident | 375
|  | Raw Adjusted MD | MW | Non-Coincident | 316.992
|  |  |  | Coincident | 306.528
|  | Raw Adjusted MD | MVA | Non-Coincident | 327.8097
|  |  |  | Coincident | 316.9886
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 329.26
|  |  |  | Coincident | 318.391
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 340.4988
|  |  |  | Coincident | 329.2588
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 293.01
|  |  |  | Coincident | 283.3377
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 303.0115
|  |  |  | Coincident | 293.009
| Sydney North BSP | Substation Rating | MVA | Non-Coincident | 75
|  |  |  | Coincident | 75
|  | Raw Adjusted MD | MW | Non-Coincident | 36.9436
|  |  |  | Coincident | 36.5987
|  | Raw Adjusted MD | MVA | Non-Coincident | 43.6239
|  |  |  | Coincident | 43.242
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 40.309
|  |  |  | Coincident | 39.9327
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 47.5995
|  |  |  | Coincident | 47.1828
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.681
|  |  |  | Coincident | 35.3479
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.1344
|  |  |  | Coincident | 41.7656
| Sydney West BSP | Substation Rating | MVA | Non-Coincident | 1500
|  |  |  | Coincident | 1500
|  | Raw Adjusted MD | MW | Non-Coincident | 1277.7561
|  |  |  | Coincident | 1220.7414
|  | Raw Adjusted MD | MVA | Non-Coincident | 1288.3073
|  |  |  | Coincident | 1235.9098
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 5.1174
|  |  |  | Coincident | 3.7962
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1199.7
|  |  |  | Coincident | 1146.1682
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1209.6055
|  |  |  | Coincident | 1160.4089
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1069.49
|  |  |  | Coincident | 1021.7683
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1078.3204
|  |  |  | Coincident | 1034.4634
| Vineyard BSP | Substation Rating | MVA | Non-Coincident | 750
|  |  |  | Coincident | 750
|  | Raw Adjusted MD | MW | Non-Coincident | 510.1656
|  |  |  | Coincident | 482.1929
|  | Raw Adjusted MD | MVA | Non-Coincident | 510.6271
|  |  |  | Coincident | 482.3106
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 497.97
|  |  |  | Coincident | 470.666
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 498.419
|  |  |  | Coincident | 470.7795
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 443.13
|  |  |  | Coincident | 418.8329
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 443.5296
|  |  |  | Coincident | 418.9339
| Wallerawang BSP 66kV | Substation Rating | MVA | Non-Coincident | 60
|  |  |  | Coincident | 60
|  | Raw Adjusted MD | MW | Non-Coincident | 33.6451
|  |  |  | Coincident | 18.622
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.1574
|  |  |  | Coincident | 19.2329
|  | Date MD occurred |  | Non-Coincident | 2019-11-22
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 13:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.9
|  |  |  | Coincident | 17.6561
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.529
|  |  |  | Coincident | 18.3421
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.9
|  |  |  | Coincident | 17.6561
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.529
|  |  |  | Coincident | 18.3421
| Wallerawang BSP 132kV | Substation Rating | MVA | Non-Coincident | 375
|  |  |  | Coincident | 375
|  | Raw Adjusted MD | MW | Non-Coincident | 66.258
|  |  |  | Coincident | 34.7662
|  | Raw Adjusted MD | MVA | Non-Coincident | 66.5497
|  |  |  | Coincident | 34.8345
|  | Date MD occurred |  | Non-Coincident | 2019-11-19
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 66.26
|  |  |  | Coincident | 34.7672
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 66.55
|  |  |  | Coincident | 34.8347
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 66.26
|  |  |  | Coincident | 34.7672
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 66.55
|  |  |  | Coincident | 34.8347
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2019-20
ZONE SUBSTATION | Abbotsbury | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 39.1625
|  |  |  | Coincident | 38.025
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.3279
|  |  |  | Coincident | 39.2335
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.163
|  |  |  | Coincident | 38.0255
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.328
|  |  |  | Coincident | 39.2336
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 39.163
|  |  |  | Coincident | 38.0255
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 40.328
|  |  |  | Coincident | 39.2336
| Albion Park | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 27.4833
|  |  |  | Coincident | 24.602
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.6112
|  |  |  | Coincident | 24.8602
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.9502
|  |  |  | Coincident | 23.2296
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.0711
|  |  |  | Coincident | 23.4735
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.13
|  |  |  | Coincident | 19.8099
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.2331
|  |  |  | Coincident | 20.0179
| Ambarvale | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 31.239
|  |  |  | Coincident | 29.6775
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.2493
|  |  |  | Coincident | 29.6848
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.468
|  |  |  | Coincident | 29.8951
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.4781
|  |  |  | Coincident | 29.9021
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.971
|  |  |  | Coincident | 25.6228
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.9796
|  |  |  | Coincident | 25.6289
| Anzac Village | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 27
|  |  |  | Coincident | 26.19
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.6849
|  |  |  | Coincident | 26.8955
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.283
|  |  |  | Coincident | 24.5245
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.9244
|  |  |  | Coincident | 25.1852
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.676
|  |  |  | Coincident | 21.0257
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.2259
|  |  |  | Coincident | 21.5922
| Appin | Substation Rating | MVA | Non-Coincident | 5
|  |  |  | Coincident | 5
|  | Raw Adjusted MD | MW | Non-Coincident | 6.5736
|  |  |  | Coincident | 6.1398
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.7746
|  |  |  | Coincident | 6.3399
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.033
|  |  |  | Coincident | 5.6349
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.2175
|  |  |  | Coincident | 5.8185
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.14
|  |  |  | Coincident | 4.8008
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.2972
|  |  |  | Coincident | 4.9573
| Arndell Park | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 28.8015
|  |  |  | Coincident | 23.391
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.9622
|  |  |  | Coincident | 23.4513
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.312
|  |  |  | Coincident | 24.6177
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.4804
|  |  |  | Coincident | 24.6806
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 27.87
|  |  |  | Coincident | 22.6345
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.0248
|  |  |  | Coincident | 22.6923
| Baulkham Hills 11kV | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 34.6125
|  |  |  | Coincident | 33.6
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.4078
|  |  |  | Coincident | 34.3706
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.321
|  |  |  | Coincident | 33.317
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.1439
|  |  |  | Coincident | 36.0559
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.105
|  |  |  | Coincident | 29.2244
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.5812
|  |  |  | Coincident | 31.6268
| Bella Vista | Substation Rating | MVA | Non-Coincident | 90
|  |  |  | Coincident | 90
|  | Raw Adjusted MD | MW | Non-Coincident | 52.6533
|  |  |  | Coincident | 48
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.8272
|  |  |  | Coincident | 48.5
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.656
|  |  |  | Coincident | 45.2676
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 48.8769
|  |  |  | Coincident | 45.7391
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.456
|  |  |  | Coincident | 40.5271
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 43.7585
|  |  |  | Coincident | 40.9493
| Berrima Junction | Substation Rating | MVA | Non-Coincident | 20
|  |  |  | Coincident | 20
|  | Raw Adjusted MD | MW | Non-Coincident | 1.6185
|  |  |  | Coincident | 0.012
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.6253
|  |  |  | Coincident | 0.0495
|  | Date MD occurred |  | Non-Coincident | 2020-02-05
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 12:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.619
|  |  |  | Coincident | 0.012004
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.625
|  |  |  | Coincident | 0.049491
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.619
|  |  |  | Coincident | 0.012004
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.625
|  |  |  | Coincident | 0.049491
| Berry | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 9.8784
|  |  |  | Coincident | 9.2844
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.8823
|  |  |  | Coincident | 9.2849
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.6184
|  |  |  | Coincident | 8.1002
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.6219
|  |  |  | Coincident | 8.1007
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.1098
|  |  |  | Coincident | 6.6823
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.1127
|  |  |  | Coincident | 6.6827
| Blackheath | Substation Rating | MVA | Non-Coincident | 7
|  |  |  | Coincident | 7
|  | Raw Adjusted MD | MW | Non-Coincident | 4.61
|  |  |  | Coincident | 3.995
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.6248
|  |  |  | Coincident | 4.0559
|  | Date MD occurred |  | Non-Coincident | 2020-03-14
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.61
|  |  |  | Coincident | 3.995
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.625
|  |  |  | Coincident | 4.0561
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.61
|  |  |  | Coincident | 3.995
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.625
|  |  |  | Coincident | 4.0561
| Blackmans Flat | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 5.406
|  |  |  | Coincident | 4.509
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.5422
|  |  |  | Coincident | 4.6101
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.406
|  |  |  | Coincident | 4.509
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.542
|  |  |  | Coincident | 4.6099
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.406
|  |  |  | Coincident | 4.509
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.542
|  |  |  | Coincident | 4.6099
| Blaxland | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 28.27
|  |  |  | Coincident | 26.79
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.293
|  |  |  | Coincident | 26.8076
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.081
|  |  |  | Coincident | 24.7156
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.1022
|  |  |  | Coincident | 24.7318
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.996
|  |  |  | Coincident | 20.8445
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.0139
|  |  |  | Coincident | 20.8582
| Bolong Road | Substation Rating | MVA | Non-Coincident | 12.5
|  |  |  | Coincident | 12.5
|  | Raw Adjusted MD | MW | Non-Coincident | 3.2124
|  |  |  | Coincident | 2.007
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.343
|  |  |  | Coincident | 2.0785
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.212
|  |  |  | Coincident | 2.0068
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.343
|  |  |  | Coincident | 2.0785
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.212
|  |  |  | Coincident | 2.0068
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.343
|  |  |  | Coincident | 2.0785
| Bomaderry | Substation Rating | MVA | Non-Coincident | 30
|  |  |  | Coincident | 30
|  | Raw Adjusted MD | MW | Non-Coincident | 22.176
|  |  |  | Coincident | 21.078
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.176
|  |  |  | Coincident | 21.3256
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.8505
|  |  |  | Coincident | 18.8676
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.8505
|  |  |  | Coincident | 19.0893
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.2975
|  |  |  | Coincident | 16.441
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.2975
|  |  |  | Coincident | 16.6342
| Bonnyrigg | Substation Rating | MVA | Non-Coincident | 70
|  |  |  | Coincident | 70
|  | Raw Adjusted MD | MW | Non-Coincident | 33.6285
|  |  |  | Coincident | 32.9805
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.6463
|  |  |  | Coincident | 32.9952
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.539
|  |  |  | Coincident | 31.912
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.5554
|  |  |  | Coincident | 31.9255
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.013
|  |  |  | Coincident | 27.4732
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.0272
|  |  |  | Coincident | 27.4848
| Bossley Park | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 32.352
|  |  |  | Coincident | 31.164
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.3661
|  |  |  | Coincident | 31.2177
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.923
|  |  |  | Coincident | 31.714
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.9372
|  |  |  | Coincident | 31.7686
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.584
|  |  |  | Coincident | 28.4976
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.5968
|  |  |  | Coincident | 28.5467
| Bow Bowing | Substation Rating | MVA | Non-Coincident | 70
|  |  |  | Coincident | 70
|  | Raw Adjusted MD | MW | Non-Coincident | 43.215
|  |  |  | Coincident | 32.69
|  | Raw Adjusted MD | MVA | Non-Coincident | 43.2517
|  |  |  | Coincident | 32.8833
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 43.215
|  |  |  | Coincident | 32.69
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 43.252
|  |  |  | Coincident | 32.8835
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.215
|  |  |  | Coincident | 32.69
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 43.252
|  |  |  | Coincident | 32.8835
| Bowral | Substation Rating | MVA | Non-Coincident | 20
|  |  |  | Coincident | 20
|  | Raw Adjusted MD | MW | Non-Coincident | 21.2508
|  |  |  | Coincident | 20.2194
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.6128
|  |  |  | Coincident | 20.5947
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.7018
|  |  |  | Coincident | 16.8426
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.9947
|  |  |  | Coincident | 17.147
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.1723
|  |  |  | Coincident | 14.4359
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.4233
|  |  |  | Coincident | 14.6968
| Bringelly | Substation Rating | MVA | Non-Coincident | 19
|  |  |  | Coincident | 19
|  | Raw Adjusted MD | MW | Non-Coincident | 11.7765
|  |  |  | Coincident | 11.1825
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.325
|  |  |  | Coincident | 11.6977
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.1367
|  |  |  | Coincident | 11.5245
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.7012
|  |  |  | Coincident | 12.0547
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.8063
|  |  |  | Coincident | 10.2612
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.3089
|  |  |  | Coincident | 10.7333
| Bulli | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 12.6
|  |  |  | Coincident | 10.475
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.6721
|  |  |  | Coincident | 10.5238
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.9867
|  |  |  | Coincident | 9.9651
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.0552
|  |  |  | Coincident | 10.0115
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.253
|  |  |  | Coincident | 8.5238
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.3116
|  |  |  | Coincident | 8.5635
| Bylong | Substation Rating | MVA | Non-Coincident | 1.5
|  |  |  | Coincident | 1.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.3542
|  |  |  | Coincident | 0.2766
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.3643
|  |  |  | Coincident | 0.279
|  | Date MD occurred |  | Non-Coincident | 2020-01-10
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.354
|  |  |  | Coincident | 0.27644
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.364
|  |  |  | Coincident | 0.27877
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.354
|  |  |  | Coincident | 0.27644
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.364
|  |  |  | Coincident | 0.27877
| Cabramatta | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 18.3333
|  |  |  | Coincident | 16.44
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.45
|  |  |  | Coincident | 16.6067
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.6611
|  |  |  | Coincident | 16.7339
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.7799
|  |  |  | Coincident | 16.9036
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.7407
|  |  |  | Coincident | 15.0119
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.8473
|  |  |  | Coincident | 15.1641
| Cambridge Park | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 26.478
|  |  |  | Coincident | 24.285
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.4784
|  |  |  | Coincident | 24.2907
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.421
|  |  |  | Coincident | 23.3155
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.421
|  |  |  | Coincident | 23.3207
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.144
|  |  |  | Coincident | 20.31
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.144
|  |  |  | Coincident | 20.3144
| Campbelltown | Substation Rating | MVA | Non-Coincident | 70
|  |  |  | Coincident | 70
|  | Raw Adjusted MD | MW | Non-Coincident | 49.425
|  |  |  | Coincident | 42.3375
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.4414
|  |  |  | Coincident | 42.3859
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.518
|  |  |  | Coincident | 43.2738
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.5344
|  |  |  | Coincident | 43.3229
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 46.367
|  |  |  | Coincident | 39.718
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.382
|  |  |  | Coincident | 39.7631
| Canley Vale | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 37.7625
|  |  |  | Coincident | 36.7875
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.8066
|  |  |  | Coincident | 36.8303
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.707
|  |  |  | Coincident | 32.8367
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.7463
|  |  |  | Coincident | 32.8748
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.139
|  |  |  | Coincident | 28.3867
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.173
|  |  |  | Coincident | 28.4196
| Carramar | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 16.4646
|  |  |  | Coincident | 16.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.6
|  |  |  | Coincident | 17.3
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.774
|  |  |  | Coincident | 16.4025
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.9307
|  |  |  | Coincident | 17.6251
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.134
|  |  |  | Coincident | 14.7989
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.1776
|  |  |  | Coincident | 15.9019
| Castle Hill | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 27.9083
|  |  |  | Coincident | 27.7333
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.4117
|  |  |  | Coincident | 28.2333
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.406
|  |  |  | Coincident | 24.253
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.8468
|  |  |  | Coincident | 24.6907
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.559
|  |  |  | Coincident | 21.4238
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.9483
|  |  |  | Coincident | 21.8105
| Casula | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 28.575
|  |  |  | Coincident | 28.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.1234
|  |  |  | Coincident | 28.6873
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.575
|  |  |  | Coincident | 28.1
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.123
|  |  |  | Coincident | 28.6869
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.575
|  |  |  | Coincident | 28.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.123
|  |  |  | Coincident | 28.6869
| Cattai | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 15.26
|  |  |  | Coincident | 14.75
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.89
|  |  |  | Coincident | 15.4596
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.221
|  |  |  | Coincident | 13.7457
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.8081
|  |  |  | Coincident | 14.407
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.444
|  |  |  | Coincident | 12.0281
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.9577
|  |  |  | Coincident | 12.6068
| Cawdor | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 30.4625
|  |  |  | Coincident | 29.15
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.3812
|  |  |  | Coincident | 30.035
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.463
|  |  |  | Coincident | 29.1505
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.381
|  |  |  | Coincident | 30.0348
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.463
|  |  |  | Coincident | 29.1505
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.381
|  |  |  | Coincident | 30.0348
| Cheriton Avenue | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 27.0375
|  |  |  | Coincident | 26.8375
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.2504
|  |  |  | Coincident | 27.0536
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.407
|  |  |  | Coincident | 25.2191
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.6062
|  |  |  | Coincident | 25.4213
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.583
|  |  |  | Coincident | 22.416
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.7601
|  |  |  | Coincident | 22.5957
| Chipping Norton | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 19.55
|  |  |  | Coincident | 18.9125
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.0753
|  |  |  | Coincident | 19.4007
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.55
|  |  |  | Coincident | 18.9125
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.0762
|  |  |  | Coincident | 19.4015
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.55
|  |  |  | Coincident | 18.9125
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.0762
|  |  |  | Coincident | 19.4015
| Claremont Meadows | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 26.825
|  |  |  | Coincident | 25.6375
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.2555
|  |  |  | Coincident | 26.0018
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.825
|  |  |  | Coincident | 25.6375
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.255
|  |  |  | Coincident | 26.0013
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.825
|  |  |  | Coincident | 25.6375
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 27.255
|  |  |  | Coincident | 26.0013
| Corrimal | Substation Rating | MVA | Non-Coincident | 19
|  |  |  | Coincident | 19
|  | Raw Adjusted MD | MW | Non-Coincident | 18.35
|  |  |  | Coincident | 15.5875
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.3602
|  |  |  | Coincident | 15.775
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.4915
|  |  |  | Coincident | 14.8582
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.501
|  |  |  | Coincident | 15.0368
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.0383
|  |  |  | Coincident | 12.7744
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.0465
|  |  |  | Coincident | 12.9279
| Cranebrook | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 29.9025
|  |  |  | Coincident | 29.7
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.9342
|  |  |  | Coincident | 29.7277
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.071
|  |  |  | Coincident | 30.8606
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.1032
|  |  |  | Coincident | 30.8886
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.552
|  |  |  | Coincident | 28.3586
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.5816
|  |  |  | Coincident | 28.3844
| Culburra | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 9.7699
|  |  |  | Coincident | 7.2183
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.0883
|  |  |  | Coincident | 7.4067
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.77
|  |  |  | Coincident | 7.2184
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.088
|  |  |  | Coincident | 7.4065
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.77
|  |  |  | Coincident | 7.2184
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.088
|  |  |  | Coincident | 7.4065
| Dapto | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 34.7391
|  |  |  | Coincident | 33.3561
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.9008
|  |  |  | Coincident | 33.5294
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.9259
|  |  |  | Coincident | 34.4957
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.0934
|  |  |  | Coincident | 34.6752
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.9931
|  |  |  | Coincident | 28.799
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.133
|  |  |  | Coincident | 28.9489
| Darkes Forest | Substation Rating | MVA | Non-Coincident | 5
|  |  |  | Coincident | 5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.9132
|  |  |  | Coincident | 0.177
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.9229
|  |  |  | Coincident | 0.1794
|  | Date MD occurred |  | Non-Coincident | 2020-02-09
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.913
|  |  |  | Coincident | 0.17696
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.923
|  |  |  | Coincident | 0.17942
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.913
|  |  |  | Coincident | 0.17696
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.923
|  |  |  | Coincident | 0.17942
| Doonside | Substation Rating | MVA | Non-Coincident | 90
|  |  |  | Coincident | 90
|  | Raw Adjusted MD | MW | Non-Coincident | 47.3625
|  |  |  | Coincident | 44.7625
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.1663
|  |  |  | Coincident | 45.5301
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.765
|  |  |  | Coincident | 42.3076
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.524
|  |  |  | Coincident | 43.0324
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 38.187
|  |  |  | Coincident | 36.0907
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 38.8344
|  |  |  | Coincident | 36.709
| Dundas | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 37.9917
|  |  |  | Coincident | 37.3233
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.4533
|  |  |  | Coincident | 37.7933
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.01
|  |  |  | Coincident | 36.3589
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.4591
|  |  |  | Coincident | 36.8161
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.977
|  |  |  | Coincident | 29.4496
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.3407
|  |  |  | Coincident | 29.82
| East Richmond | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 26.325
|  |  |  | Coincident | 23.9125
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.0029
|  |  |  | Coincident | 24.5595
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.012
|  |  |  | Coincident | 24.5365
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.7077
|  |  |  | Coincident | 25.2005
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.378
|  |  |  | Coincident | 22.1439
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.0059
|  |  |  | Coincident | 22.7432
| Eastern Creek | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 24.225
|  |  |  | Coincident | 15.975
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.4801
|  |  |  | Coincident | 16.0525
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.225
|  |  |  | Coincident | 15.975
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.48
|  |  |  | Coincident | 16.0524
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.225
|  |  |  | Coincident | 15.975
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.48
|  |  |  | Coincident | 16.0524
| Edmondson Park | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 5.0875
|  |  |  | Coincident | 4.5875
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.1354
|  |  |  | Coincident | 4.5973
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.088
|  |  |  | Coincident | 4.588
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.135
|  |  |  | Coincident | 4.5969
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.088
|  |  |  | Coincident | 4.588
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.135
|  |  |  | Coincident | 4.5969
| Emu Plains | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 39.8595
|  |  |  | Coincident | 33.8
|  | Raw Adjusted MD | MVA | Non-Coincident | 39.8595
|  |  |  | Coincident | 33.5
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.003
|  |  |  | Coincident | 31.3777
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.003
|  |  |  | Coincident | 31.0992
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.99
|  |  |  | Coincident | 27.9748
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.99
|  |  |  | Coincident | 27.7265
| Fairfield | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 26.9617
|  |  |  | Coincident | 22.555
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.9617
|  |  |  | Coincident | 22.555
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.962
|  |  |  | Coincident | 22.5553
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.962
|  |  |  | Coincident | 22.5553
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.962
|  |  |  | Coincident | 22.5553
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.962
|  |  |  | Coincident | 22.5553
| Figtree | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 24.1625
|  |  |  | Coincident | 23.2
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.5757
|  |  |  | Coincident | 23.6639
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.163
|  |  |  | Coincident | 23.2005
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.576
|  |  |  | Coincident | 23.6642
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.163
|  |  |  | Coincident | 23.2005
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.576
|  |  |  | Coincident | 23.6642
| Gerringong | Substation Rating | MVA | Non-Coincident | 5
|  |  |  | Coincident | 5
|  | Raw Adjusted MD | MW | Non-Coincident | 6.195
|  |  |  | Coincident | 5.0475
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.2285
|  |  |  | Coincident | 5.0813
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.195
|  |  |  | Coincident | 5.0475
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.228
|  |  |  | Coincident | 5.0809
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.195
|  |  |  | Coincident | 5.0475
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.228
|  |  |  | Coincident | 5.0809
| Glenmore Park | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 43.995
|  |  |  | Coincident | 42.3675
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.5504
|  |  |  | Coincident | 42.9078
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.271
|  |  |  | Coincident | 43.5963
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.8421
|  |  |  | Coincident | 44.1519
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 39.684
|  |  |  | Coincident | 38.216
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 40.1846
|  |  |  | Coincident | 38.703
| Glenorie | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 6.4
|  |  |  | Coincident | 5.975
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.5678
|  |  |  | Coincident | 6.1426
|  | Date MD occurred |  | Non-Coincident | 2020-01-04
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.4
|  |  |  | Coincident | 5.975
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.568
|  |  |  | Coincident | 6.1428
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.4
|  |  |  | Coincident | 5.975
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.568
|  |  |  | Coincident | 6.1428
| Glossodia | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 19.764
|  |  |  | Coincident | 17.754
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.6934
|  |  |  | Coincident | 18.5038
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.7314
|  |  |  | Coincident | 16.8264
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.6119
|  |  |  | Coincident | 17.5367
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.4159
|  |  |  | Coincident | 14.7464
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.1875
|  |  |  | Coincident | 15.3689
| Granville 132kV | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 30.875
|  |  |  | Coincident | 29.675
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.0277
|  |  |  | Coincident | 29.8092
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.6797
|  |  |  | Coincident | 28.5262
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.8268
|  |  |  | Coincident | 28.6554
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.986
|  |  |  | Coincident | 25.9372
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 27.1197
|  |  |  | Coincident | 26.0547
| Greystanes | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 25.2
|  |  |  | Coincident | 24.22
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.0046
|  |  |  | Coincident | 24.2917
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.2967
|  |  |  | Coincident | 24.3129
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.3014
|  |  |  | Coincident | 24.58
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.7732
|  |  |  | Coincident | 20.9265
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.7772
|  |  |  | Coincident | 21.1563
| Hartley Vale | Substation Rating | MVA | Non-Coincident | 2.5
|  |  |  | Coincident | 2.5
|  | Raw Adjusted MD | MW | Non-Coincident | 1.245
|  |  |  | Coincident | 0.2363
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.2511
|  |  |  | Coincident | 0.2381
|  | Date MD occurred |  | Non-Coincident | 2019-12-02
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 21:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.245
|  |  |  | Coincident | 0.2363
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.251
|  |  |  | Coincident | 0.23808
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.245
|  |  |  | Coincident | 0.2363
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.251
|  |  |  | Coincident | 0.23808
| Hazelbrook | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 9.972
|  |  |  | Coincident | 9.072
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.061
|  |  |  | Coincident | 9.1542
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.972
|  |  |  | Coincident | 9.072
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.061
|  |  |  | Coincident | 9.1542
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.972
|  |  |  | Coincident | 9.072
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.061
|  |  |  | Coincident | 9.1542
| Helensburgh | Substation Rating | MVA | Non-Coincident | 12.5
|  |  |  | Coincident | 12.5
|  | Raw Adjusted MD | MW | Non-Coincident | 9.2772
|  |  |  | Coincident | 9.0108
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.3062
|  |  |  | Coincident | 9.0401
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.277
|  |  |  | Coincident | 9.0106
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.306
|  |  |  | Coincident | 9.0399
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.277
|  |  |  | Coincident | 9.0106
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.306
|  |  |  | Coincident | 9.0399
| Hinchinbrook | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 49.56
|  |  |  | Coincident | 48.24
|  | Raw Adjusted MD | MVA | Non-Coincident | 50.7146
|  |  |  | Coincident | 49.3844
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 46.9412
|  |  |  | Coincident | 45.691
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 48.0352
|  |  |  | Coincident | 46.7752
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.9043
|  |  |  | Coincident | 39.8148
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.8576
|  |  |  | Coincident | 40.7597
| Holroyd | Substation Rating | MVA | Non-Coincident | 42.25
|  |  |  | Coincident | 42.25
|  | Raw Adjusted MD | MW | Non-Coincident | 40.3717
|  |  |  | Coincident | 40.087
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.8867
|  |  |  | Coincident | 40.64
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.2925
|  |  |  | Coincident | 36.0366
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.7555
|  |  |  | Coincident | 36.5337
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.4741
|  |  |  | Coincident | 31.2521
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.8756
|  |  |  | Coincident | 31.6833
| Homepride | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 34.4417
|  |  |  | Coincident | 28.9917
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.63
|  |  |  | Coincident | 28.9917
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 14:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.442
|  |  |  | Coincident | 28.992
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.63
|  |  |  | Coincident | 28.9917
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.442
|  |  |  | Coincident | 28.992
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.63
|  |  |  | Coincident | 28.9917
| Horsley Park | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 8.635
|  |  |  | Coincident | 7.6767
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.9317
|  |  |  | Coincident | 8.0033
|  | Date MD occurred |  | Non-Coincident | 2020-01-04
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.0759
|  |  |  | Coincident | 8.0687
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.3881
|  |  |  | Coincident | 8.4122
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.1785
|  |  |  | Coincident | 7.2709
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.4598
|  |  |  | Coincident | 7.5805
| Huntingwood | Substation Rating | MVA | Non-Coincident | 90
|  |  |  | Coincident | 90
|  | Raw Adjusted MD | MW | Non-Coincident | 32.4
|  |  |  | Coincident | 25.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.5912
|  |  |  | Coincident | 25.1136
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.4
|  |  |  | Coincident | 25.1
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.591
|  |  |  | Coincident | 25.1134
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.4
|  |  |  | Coincident | 25.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.591
|  |  |  | Coincident | 25.1134
| Huskisson | Substation Rating | MVA | Non-Coincident | 20
|  |  |  | Coincident | 20
|  | Raw Adjusted MD | MW | Non-Coincident | 14.865
|  |  |  | Coincident | 12.84
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.965
|  |  |  | Coincident | 12.925
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.865
|  |  |  | Coincident | 12.84
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.965
|  |  |  | Coincident | 12.925
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.865
|  |  |  | Coincident | 12.84
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.965
|  |  |  | Coincident | 12.925
| ilford Hall | Substation Rating | MVA | Non-Coincident | 2.5
|  |  |  | Coincident | 2.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.4404
|  |  |  | Coincident | 0.2952
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.4651
|  |  |  | Coincident | 0.3328
|  | Date MD occurred |  | Non-Coincident | 2019-12-20
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.44
|  |  |  | Coincident | 0.29493
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.465
|  |  |  | Coincident | 0.33273
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.44
|  |  |  | Coincident | 0.29493
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.465
|  |  |  | Coincident | 0.33273
| Inner Harbour | Substation Rating | MVA | Non-Coincident | 12.5
|  |  |  | Coincident | 12.5
|  | Raw Adjusted MD | MW | Non-Coincident | 8.8578
|  |  |  | Coincident | 3.8718
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.91
|  |  |  | Coincident | 3.9318
|  | Date MD occurred |  | Non-Coincident | 2020-03-17
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 6:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.858
|  |  |  | Coincident | 3.8719
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.91
|  |  |  | Coincident | 3.9318
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.858
|  |  |  | Coincident | 3.8719
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.91
|  |  |  | Coincident | 3.9318
| Jamberoo | Substation Rating | MVA | Non-Coincident | 3.75
|  |  |  | Coincident | 3.75
|  | Raw Adjusted MD | MW | Non-Coincident | 2.955
|  |  |  | Coincident | 2.1421
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.1233
|  |  |  | Coincident | 2.155
|  | Date MD occurred |  | Non-Coincident | 2020-01-04
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.821
|  |  |  | Coincident | 2.045
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.9817
|  |  |  | Coincident | 2.0573
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.4781
|  |  |  | Coincident | 1.7964
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.6192
|  |  |  | Coincident | 1.8072
| Jasper Road | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 37.7375
|  |  |  | Coincident | 36.7
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.5352
|  |  |  | Coincident | 37.5249
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.908
|  |  |  | Coincident | 34.9208
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.6664
|  |  |  | Coincident | 35.705
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.895
|  |  |  | Coincident | 29.0731
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.5264
|  |  |  | Coincident | 29.726
| Jordan Springs | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 24.75
|  |  |  | Coincident | 22.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.0997
|  |  |  | Coincident | 22.75
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.75
|  |  |  | Coincident | 22.4
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.1
|  |  |  | Coincident | 22.7503
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.75
|  |  |  | Coincident | 22.4
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.1
|  |  |  | Coincident | 22.7503
| Kandos | Substation Rating | MVA | Non-Coincident | 5
|  |  |  | Coincident | 5
|  | Raw Adjusted MD | MW | Non-Coincident | 4.368
|  |  |  | Coincident | 3.8078
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.3881
|  |  |  | Coincident | 3.8283
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.368
|  |  |  | Coincident | 3.8078
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.388
|  |  |  | Coincident | 3.8282
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.368
|  |  |  | Coincident | 3.8078
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.388
|  |  |  | Coincident | 3.8282
| Kangaroo Valley | Substation Rating | MVA | Non-Coincident | 2.5
|  |  |  | Coincident | 2.5
|  | Raw Adjusted MD | MW | Non-Coincident | 2.298
|  |  |  | Coincident | 2.138
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.3266
|  |  |  | Coincident | 2.1684
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.2864
|  |  |  | Coincident | 2.1272
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.3153
|  |  |  | Coincident | 2.1578
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.935
|  |  |  | Coincident | 1.8003
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.9594
|  |  |  | Coincident | 1.8262
| Katoomba | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 12.897
|  |  |  | Coincident | 12.1905
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.9424
|  |  |  | Coincident | 12.3791
|  | Date MD occurred |  | Non-Coincident | 2020-03-25
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 10:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.897
|  |  |  | Coincident | 12.1905
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.942
|  |  |  | Coincident | 12.3787
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.897
|  |  |  | Coincident | 12.1905
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.942
|  |  |  | Coincident | 12.3787
| Kellyville | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 23.7015
|  |  |  | Coincident | 23.112
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.5193
|  |  |  | Coincident | 24.8074
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.407
|  |  |  | Coincident | 21.8497
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.1247
|  |  |  | Coincident | 23.4517
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.257
|  |  |  | Coincident | 18.778
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.7332
|  |  |  | Coincident | 20.1549
| Kembla Grange | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 4.734
|  |  |  | Coincident | 4.104
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.7545
|  |  |  | Coincident | 4.1248
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.734
|  |  |  | Coincident | 4.104
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.754
|  |  |  | Coincident | 4.1244
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.734
|  |  |  | Coincident | 4.104
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.754
|  |  |  | Coincident | 4.1244
| Kemps Creek | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 11.525
|  |  |  | Coincident | 11.35
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.5641
|  |  |  | Coincident | 11.3876
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.5225
|  |  |  | Coincident | 11.3475
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.5615
|  |  |  | Coincident | 11.385
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.2571
|  |  |  | Coincident | 10.1014
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.2918
|  |  |  | Coincident | 10.1347
| Kenny Street | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 16.569
|  |  |  | Coincident | 8.847
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.0462
|  |  |  | Coincident | 8.9508
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 14:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.3104
|  |  |  | Coincident | 9.2429
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.8087
|  |  |  | Coincident | 9.3512
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.0209
|  |  |  | Coincident | 8.5543
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.4821
|  |  |  | Coincident | 8.6546
| Kenthurst | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 24.0705
|  |  |  | Coincident | 22.7025
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.9369
|  |  |  | Coincident | 24.1792
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.5053
|  |  |  | Coincident | 20.2831
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 22.279
|  |  |  | Coincident | 21.6021
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.5939
|  |  |  | Coincident | 17.5372
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.2629
|  |  |  | Coincident | 18.6776
| Kentlyn | Substation Rating | MVA | Non-Coincident | 33
|  |  |  | Coincident | 33
|  | Raw Adjusted MD | MW | Non-Coincident | 36.2086
|  |  |  | Coincident | 35.0577
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.2406
|  |  |  | Coincident | 35.0954
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.1587
|  |  |  | Coincident | 33.073
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.189
|  |  |  | Coincident | 33.1086
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.4957
|  |  |  | Coincident | 28.5582
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.5218
|  |  |  | Coincident | 28.589
| Kiama | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 13.795
|  |  |  | Coincident | 10.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.8494
|  |  |  | Coincident | 10.6783
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.1679
|  |  |  | Coincident | 9.3762
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.2155
|  |  |  | Coincident | 9.4185
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.6765
|  |  |  | Coincident | 8.227
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.7183
|  |  |  | Coincident | 8.2641
| Kingswood | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 43.7502
|  |  |  | Coincident | 41.5474
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.0793
|  |  |  | Coincident | 41.7431
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.8221
|  |  |  | Coincident | 43.515
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.1667
|  |  |  | Coincident | 43.7199
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.3412
|  |  |  | Coincident | 39.2597
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.6521
|  |  |  | Coincident | 39.4445
| Kurrajong | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 15.7032
|  |  |  | Coincident | 14.706
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.2847
|  |  |  | Coincident | 15.2864
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.4421
|  |  |  | Coincident | 13.525
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.9774
|  |  |  | Coincident | 14.0592
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.3038
|  |  |  | Coincident | 11.5225
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.7598
|  |  |  | Coincident | 11.9776
| Leabons Lane | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 23.395
|  |  |  | Coincident | 23.205
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.7133
|  |  |  | Coincident | 23.5317
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.7438
|  |  |  | Coincident | 22.5591
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.0529
|  |  |  | Coincident | 22.8764
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.5173
|  |  |  | Coincident | 20.3507
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.7962
|  |  |  | Coincident | 20.6369
| Lennox | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 20.815
|  |  |  | Coincident | 20.815
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.93
|  |  |  | Coincident | 20.93
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.772
|  |  |  | Coincident | 20.772
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.8868
|  |  |  | Coincident | 20.8868
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.2185
|  |  |  | Coincident | 19.2185
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.3247
|  |  |  | Coincident | 19.3247
| Lithgow | Substation Rating | MVA | Non-Coincident | 30
|  |  |  | Coincident | 30
|  | Raw Adjusted MD | MW | Non-Coincident | 14.355
|  |  |  | Coincident | 13.41
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.5298
|  |  |  | Coincident | 13.5647
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.355
|  |  |  | Coincident | 13.41
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.53
|  |  |  | Coincident | 13.5649
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.355
|  |  |  | Coincident | 13.41
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.53
|  |  |  | Coincident | 13.5649
| Liverpool | Substation Rating | MVA | Non-Coincident | 70
|  |  |  | Coincident | 70
|  | Raw Adjusted MD | MW | Non-Coincident | 37.3875
|  |  |  | Coincident | 35.7375
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.5047
|  |  |  | Coincident | 35.7439
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.1381
|  |  |  | Coincident | 36.455
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.2574
|  |  |  | Coincident | 36.4613
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.7014
|  |  |  | Coincident | 33.1699
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.81
|  |  |  | Coincident | 33.1757
| Luddenham | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 7.764
|  |  |  | Coincident | 7.668
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.1229
|  |  |  | Coincident | 8.0348
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.7482
|  |  |  | Coincident | 7.6524
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.1065
|  |  |  | Coincident | 8.0185
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.8656
|  |  |  | Coincident | 6.7807
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.1831
|  |  |  | Coincident | 7.1052
| Macquarie Fields | Substation Rating | MVA | Non-Coincident | 33
|  |  |  | Coincident | 33
|  | Raw Adjusted MD | MW | Non-Coincident | 28.332
|  |  |  | Coincident | 27.693
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.7849
|  |  |  | Coincident | 30.0631
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.1402
|  |  |  | Coincident | 27.5055
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.5766
|  |  |  | Coincident | 29.8597
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.6733
|  |  |  | Coincident | 24.1168
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.8095
|  |  |  | Coincident | 26.1809
| Maldon | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 25.41
|  |  |  | Coincident | 24.24
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.6638
|  |  |  | Coincident | 24.4477
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.1281
|  |  |  | Coincident | 22.0632
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.3591
|  |  |  | Coincident | 22.2522
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.7812
|  |  |  | Coincident | 18.8704
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.9787
|  |  |  | Coincident | 19.032
| Mamre | Substation Rating | MVA | Non-Coincident | 90
|  |  |  | Coincident | 90
|  | Raw Adjusted MD | MW | Non-Coincident | 55.9125
|  |  |  | Coincident | 47.925
|  | Raw Adjusted MD | MVA | Non-Coincident | 56.186
|  |  |  | Coincident | 48.3117
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 57.0687
|  |  |  | Coincident | 48.916
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.3473
|  |  |  | Coincident | 49.3103
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 52.1333
|  |  |  | Coincident | 44.6857
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 52.3878
|  |  |  | Coincident | 45.0458
| Marayong | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 30.7492
|  |  |  | Coincident | 22.4655
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.7905
|  |  |  | Coincident | 22.4701
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.749
|  |  |  | Coincident | 22.4654
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.791
|  |  |  | Coincident | 22.4705
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.749
|  |  |  | Coincident | 22.4654
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.791
|  |  |  | Coincident | 22.4705
| Marsden_Park | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 10.1625
|  |  |  | Coincident | 9.425
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.2568
|  |  |  | Coincident | 9.5557
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.163
|  |  |  | Coincident | 9.4255
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.257
|  |  |  | Coincident | 9.5559
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.163
|  |  |  | Coincident | 9.4255
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.257
|  |  |  | Coincident | 9.5559
| Meadow Flat | Substation Rating | MVA | Non-Coincident | 2.5
|  |  |  | Coincident | 2.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.9213
|  |  |  | Coincident | 0.8034
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.9219
|  |  |  | Coincident | 0.8067
|  | Date MD occurred |  | Non-Coincident | 2019-12-02
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 20:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.921
|  |  |  | Coincident | 0.80314
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.922
|  |  |  | Coincident | 0.80679
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.921
|  |  |  | Coincident | 0.80314
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.922
|  |  |  | Coincident | 0.80679
| Minto | Substation Rating | MVA | Non-Coincident | 66
|  |  |  | Coincident | 66
|  | Raw Adjusted MD | MW | Non-Coincident | 61.2029
|  |  |  | Coincident | 58.2417
|  | Raw Adjusted MD | MVA | Non-Coincident | 61.7762
|  |  |  | Coincident | 58.9
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 63.1163
|  |  |  | Coincident | 60.0625
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 63.7072
|  |  |  | Coincident | 60.7411
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 56.6224
|  |  |  | Coincident | 53.8828
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 57.1525
|  |  |  | Coincident | 54.4916
| Mittagong | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 18.798
|  |  |  | Coincident | 17.5905
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.1098
|  |  |  | Coincident | 17.9111
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.1233
|  |  |  | Coincident | 15.0876
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.3909
|  |  |  | Coincident | 15.3628
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.0961
|  |  |  | Coincident | 13.1906
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.3301
|  |  |  | Coincident | 13.4312
| Moorebank | Substation Rating | MVA | Non-Coincident | 70
|  |  |  | Coincident | 70
|  | Raw Adjusted MD | MW | Non-Coincident | 23.6858
|  |  |  | Coincident | 17.7053
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.7285
|  |  |  | Coincident | 18.5951
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.686
|  |  |  | Coincident | 17.7054
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.729
|  |  |  | Coincident | 18.5955
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.686
|  |  |  | Coincident | 17.7054
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.729
|  |  |  | Coincident | 18.5955
| Moss Vale | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 18.108
|  |  |  | Coincident | 17.0856
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.4228
|  |  |  | Coincident | 17.4359
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.6906
|  |  |  | Coincident | 15.7482
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.9809
|  |  |  | Coincident | 16.0713
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.9103
|  |  |  | Coincident | 14.0684
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.1697
|  |  |  | Coincident | 14.357
| Mount Ousley | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 19.56
|  |  |  | Coincident | 15.78
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.6108
|  |  |  | Coincident | 15.854
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.9936
|  |  |  | Coincident | 15.3231
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.581
|  |  |  | Coincident | 15.8299
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.8034
|  |  |  | Coincident | 13.5561
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.3231
|  |  |  | Coincident | 14.0045
| Mungerie Park | Substation Rating | MVA | Non-Coincident | 90
|  |  |  | Coincident | 90
|  | Raw Adjusted MD | MW | Non-Coincident | 81.16
|  |  |  | Coincident | 79.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 82.6231
|  |  |  | Coincident | 81.436
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 81.16
|  |  |  | Coincident | 79.92
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 82.623
|  |  |  | Coincident | 81.4359
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 81.16
|  |  |  | Coincident | 79.92
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 82.623
|  |  |  | Coincident | 81.4359
| Narellan | Substation Rating | MVA | Non-Coincident | 70
|  |  |  | Coincident | 70
|  | Raw Adjusted MD | MW | Non-Coincident | 65.22
|  |  |  | Coincident | 64.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 65.7511
|  |  |  | Coincident | 64.5715
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 69.167
|  |  |  | Coincident | 67.9262
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 69.7301
|  |  |  | Coincident | 68.4791
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 60.9868
|  |  |  | Coincident | 59.8927
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 61.4833
|  |  |  | Coincident | 60.3803
| Nepean Zone | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 40.2875
|  |  |  | Coincident | 38.3625
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.3779
|  |  |  | Coincident | 38.4514
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.949
|  |  |  | Coincident | 38.0402
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.0382
|  |  |  | Coincident | 38.1279
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.7523
|  |  |  | Coincident | 32.1396
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.8277
|  |  |  | Coincident | 32.2137
| Newton | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 27.185
|  |  |  | Coincident | 0.9633
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.1533
|  |  |  | Coincident | 6.0567
|  | Date MD occurred |  | Non-Coincident | 2019-12-19
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.115
|  |  |  | Coincident | 0.99625
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.1161
|  |  |  | Coincident | 6.2638
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.9015
|  |  |  | Coincident | 0.91782
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.8238
|  |  |  | Coincident | 5.7707
| North Eastern Creek | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 13.65
|  |  |  | Coincident | 6.9
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.9145
|  |  |  | Coincident | 6.9001
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.65
|  |  |  | Coincident | 6.9
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.914
|  |  |  | Coincident | 6.8999
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.65
|  |  |  | Coincident | 6.9
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.914
|  |  |  | Coincident | 6.8999
| North Parramatta | Substation Rating | MVA | Non-Coincident | 55
|  |  |  | Coincident | 55
|  | Raw Adjusted MD | MW | Non-Coincident | 34.5917
|  |  |  | Coincident | 34.2336
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.6533
|  |  |  | Coincident | 34.2517
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.803
|  |  |  | Coincident | 32.4634
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.8608
|  |  |  | Coincident | 32.48
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.3445
|  |  |  | Coincident | 29.0407
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.3962
|  |  |  | Coincident | 29.0556
| North Richmond | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 16.68
|  |  |  | Coincident | 15.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.7395
|  |  |  | Coincident | 15.2298
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.68
|  |  |  | Coincident | 15.18
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.739
|  |  |  | Coincident | 15.2293
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.68
|  |  |  | Coincident | 15.18
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.739
|  |  |  | Coincident | 15.2293
| North Rocks | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 19.2
|  |  |  | Coincident | 16.99
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.6183
|  |  |  | Coincident | 18.1217
|  | Date MD occurred |  | Non-Coincident | 2020-01-04
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.517
|  |  |  | Coincident | 17.2705
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.9419
|  |  |  | Coincident | 18.4206
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.1037
|  |  |  | Coincident | 15.135
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.4761
|  |  |  | Coincident | 16.1429
| North Warragamba | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 12.6
|  |  |  | Coincident | 12.24
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.0478
|  |  |  | Coincident | 12.835
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.827
|  |  |  | Coincident | 11.4891
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.2475
|  |  |  | Coincident | 12.0478
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.4512
|  |  |  | Coincident | 10.1526
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.8228
|  |  |  | Coincident | 10.6463
| North Wollongong | Substation Rating | MVA | Non-Coincident | 19
|  |  |  | Coincident | 19
|  | Raw Adjusted MD | MW | Non-Coincident | 13.2408
|  |  |  | Coincident | 9.5112
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.4949
|  |  |  | Coincident | 9.604
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.241
|  |  |  | Coincident | 9.5113
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.495
|  |  |  | Coincident | 9.6041
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.241
|  |  |  | Coincident | 9.5113
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.495
|  |  |  | Coincident | 9.6041
| Northmead | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 27.6683
|  |  |  | Coincident | 26.87
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.675
|  |  |  | Coincident | 26.8833
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.504
|  |  |  | Coincident | 25.7393
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.5104
|  |  |  | Coincident | 25.752
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.3537
|  |  |  | Coincident | 22.6799
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.3594
|  |  |  | Coincident | 22.6911
| Nowra | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 24.2
|  |  |  | Coincident | 22.9
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.3163
|  |  |  | Coincident | 22.9567
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.2878
|  |  |  | Coincident | 22.9831
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.4042
|  |  |  | Coincident | 23.0397
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.9697
|  |  |  | Coincident | 19.8432
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.0702
|  |  |  | Coincident | 19.8921
| Oakdale | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 3.021
|  |  |  | Coincident | 2.208
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.0774
|  |  |  | Coincident | 2.2364
|  | Date MD occurred |  | Non-Coincident | 2020-03-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.187
|  |  |  | Coincident | 1.5984
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.2275
|  |  |  | Coincident | 1.6188
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.9334
|  |  |  | Coincident | 1.4131
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.9692
|  |  |  | Coincident | 1.4311
| Oran Park | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 39.1875
|  |  |  | Coincident | 38.1875
|  | Raw Adjusted MD | MVA | Non-Coincident | 39.9344
|  |  |  | Coincident | 38.9098
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.188
|  |  |  | Coincident | 38.188
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.934
|  |  |  | Coincident | 38.9094
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 39.188
|  |  |  | Coincident | 38.188
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 39.934
|  |  |  | Coincident | 38.9094
| Parklea | Substation Rating | MVA | Non-Coincident | 90
|  |  |  | Coincident | 90
|  | Raw Adjusted MD | MW | Non-Coincident | 84.3
|  |  |  | Coincident | 82.6833
|  | Raw Adjusted MD | MVA | Non-Coincident | 86.5
|  |  |  | Coincident | 85.7917
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 86.792
|  |  |  | Coincident | 85.1275
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 89.057
|  |  |  | Coincident | 88.3278
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 75.3539
|  |  |  | Coincident | 73.9088
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 77.3204
|  |  |  | Coincident | 76.6873
| Penrith 11kV | Substation Rating | MVA | Non-Coincident | 52
|  |  |  | Coincident | 52
|  | Raw Adjusted MD | MW | Non-Coincident | 42.5967
|  |  |  | Coincident | 33.12
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.9733
|  |  |  | Coincident | 33.155
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 43.77
|  |  |  | Coincident | 34.0323
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 44.1564
|  |  |  | Coincident | 34.0678
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.6278
|  |  |  | Coincident | 31.5891
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 40.9864
|  |  |  | Coincident | 31.6221
| Plumpton | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 36.216
|  |  |  | Coincident | 34.371
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.788
|  |  |  | Coincident | 34.7308
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.379
|  |  |  | Coincident | 33.5766
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.9378
|  |  |  | Coincident | 33.9281
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.3038
|  |  |  | Coincident | 29.709
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.7982
|  |  |  | Coincident | 30.02
| Port Central | Substation Rating | MVA | Non-Coincident | 19
|  |  |  | Coincident | 19
|  | Raw Adjusted MD | MW | Non-Coincident | 12.2331
|  |  |  | Coincident | 5.6772
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.8028
|  |  |  | Coincident | 5.8605
|  | Date MD occurred |  | Non-Coincident | 2020-01-08
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 10:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.233
|  |  |  | Coincident | 5.6772
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.803
|  |  |  | Coincident | 5.8606
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.233
|  |  |  | Coincident | 5.6772
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.803
|  |  |  | Coincident | 5.8606
| Port Kembla | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 12.7375
|  |  |  | Coincident | 10.225
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.9547
|  |  |  | Coincident | 10.3654
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.8386
|  |  |  | Coincident | 9.5034
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.0403
|  |  |  | Coincident | 9.6337
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.5228
|  |  |  | Coincident | 8.4472
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.7021
|  |  |  | Coincident | 8.563
| Portland | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 2.2845
|  |  |  | Coincident | 1.773
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.2884
|  |  |  | Coincident | 1.7754
|  | Date MD occurred |  | Non-Coincident | 2019-12-02
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 23:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.285
|  |  |  | Coincident | 1.7734
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.288
|  |  |  | Coincident | 1.7751
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.285
|  |  |  | Coincident | 1.7734
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.288
|  |  |  | Coincident | 1.7751
| Prestons | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 36.48
|  |  |  | Coincident | 36.15
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.4828
|  |  |  | Coincident | 36.151
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.258
|  |  |  | Coincident | 33.9481
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.2608
|  |  |  | Coincident | 33.9492
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.1584
|  |  |  | Coincident | 28.8946
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.1608
|  |  |  | Coincident | 28.8956
| Prospect | Substation Rating | MVA | Non-Coincident | 30
|  |  |  | Coincident | 30
|  | Raw Adjusted MD | MW | Non-Coincident | 25.3366
|  |  |  | Coincident | 23.6703
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.4069
|  |  |  | Coincident | 23.6776
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.106
|  |  |  | Coincident | 25.3233
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.1809
|  |  |  | Coincident | 25.3308
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.2599
|  |  |  | Coincident | 22.6644
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.3269
|  |  |  | Coincident | 22.6711
| Quakers Hill | Substation Rating | MVA | Non-Coincident | 95
|  |  |  | Coincident | 95
|  | Raw Adjusted MD | MW | Non-Coincident | 44.87
|  |  |  | Coincident | 42.6167
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.8083
|  |  |  | Coincident | 42.965
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 42.042
|  |  |  | Coincident | 39.9307
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.9842
|  |  |  | Coincident | 40.2571
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 36.4843
|  |  |  | Coincident | 34.6521
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.4341
|  |  |  | Coincident | 34.9353
| Quarries | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 25.84
|  |  |  | Coincident | 23.4083
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.83
|  |  |  | Coincident | 24.2083
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.512
|  |  |  | Coincident | 23.1112
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.4894
|  |  |  | Coincident | 23.901
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.3686
|  |  |  | Coincident | 21.1695
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.2639
|  |  |  | Coincident | 21.893
| Ringwood | Substation Rating | MVA | Non-Coincident | 12.5
|  |  |  | Coincident | 12.5
|  | Raw Adjusted MD | MW | Non-Coincident | 7.275
|  |  |  | Coincident | 6.425
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.388
|  |  |  | Coincident | 6.5227
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 20:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.419
|  |  |  | Coincident | 4.7859
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.5032
|  |  |  | Coincident | 4.8586
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.8832
|  |  |  | Coincident | 4.3127
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.959
|  |  |  | Coincident | 4.3782
| Riverstone | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 17.425
|  |  |  | Coincident | 16.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.9433
|  |  |  | Coincident | 16.45
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.781
|  |  |  | Coincident | 17.299
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.2788
|  |  |  | Coincident | 17.6744
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.7275
|  |  |  | Coincident | 15.4075
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.1709
|  |  |  | Coincident | 15.7419
| Robertson | Substation Rating | MVA | Non-Coincident | 3.5
|  |  |  | Coincident | 3.5
|  | Raw Adjusted MD | MW | Non-Coincident | 4.0001
|  |  |  | Coincident | 3.5838
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.2106
|  |  |  | Coincident | 3.7724
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.0001
|  |  |  | Coincident | 3.5838
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.2106
|  |  |  | Coincident | 3.7724
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.0001
|  |  |  | Coincident | 3.5838
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.2106
|  |  |  | Coincident | 3.7724
| Rooty Hill | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 35.6925
|  |  |  | Coincident | 33.165
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.8503
|  |  |  | Coincident | 33.3823
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.922
|  |  |  | Coincident | 34.3074
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.0844
|  |  |  | Coincident | 34.5314
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.9875
|  |  |  | Coincident | 30.6515
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.1326
|  |  |  | Coincident | 30.8517
| Rosehill | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 18.365
|  |  |  | Coincident | 14.1217
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.6367
|  |  |  | Coincident | 14.135
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.365
|  |  |  | Coincident | 14.1217
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.7574
|  |  |  | Coincident | 14.2266
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.365
|  |  |  | Coincident | 14.1217
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.7574
|  |  |  | Coincident | 14.2266
| Russell Vale | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 15.2767
|  |  |  | Coincident | 12.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.3767
|  |  |  | Coincident | 12.5983
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.277
|  |  |  | Coincident | 12.5002
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.377
|  |  |  | Coincident | 12.5985
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.277
|  |  |  | Coincident | 12.5002
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.377
|  |  |  | Coincident | 12.5985
| Rydalmere | Substation Rating | MVA | Non-Coincident | 58
|  |  |  | Coincident | 58
|  | Raw Adjusted MD | MW | Non-Coincident | 38.625
|  |  |  | Coincident | 35.175
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.6259
|  |  |  | Coincident | 35.2108
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.658
|  |  |  | Coincident | 36.1157
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.659
|  |  |  | Coincident | 36.1526
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.4625
|  |  |  | Coincident | 32.295
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.4634
|  |  |  | Coincident | 32.3279
| Schofields | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 32.1125
|  |  |  | Coincident | 30.4875
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.3395
|  |  |  | Coincident | 30.7754
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.375
|  |  |  | Coincident | 27.8885
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.5826
|  |  |  | Coincident | 28.1519
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.2538
|  |  |  | Coincident | 23.9759
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.4323
|  |  |  | Coincident | 24.2023
| Seven Hills | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 20.5085
|  |  |  | Coincident | 13.9001
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.5524
|  |  |  | Coincident | 14.1492
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.508
|  |  |  | Coincident | 13.8998
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.552
|  |  |  | Coincident | 14.1489
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.508
|  |  |  | Coincident | 13.8998
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.552
|  |  |  | Coincident | 14.1489
| Shellharbour | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 34.5033
|  |  |  | Coincident | 24.9367
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.4967
|  |  |  | Coincident | 25.0167
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.503
|  |  |  | Coincident | 24.9365
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.497
|  |  |  | Coincident | 25.0169
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.503
|  |  |  | Coincident | 24.9365
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.497
|  |  |  | Coincident | 25.0169
| Sherwood | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 27.018
|  |  |  | Coincident | 26.424
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.7613
|  |  |  | Coincident | 27.1636
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.095
|  |  |  | Coincident | 25.5213
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.8126
|  |  |  | Coincident | 26.2353
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.5191
|  |  |  | Coincident | 22.024
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.1384
|  |  |  | Coincident | 22.6402
| Smithfield | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 39.9825
|  |  |  | Coincident | 38.2275
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.0736
|  |  |  | Coincident | 38.3243
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.198
|  |  |  | Coincident | 34.6091
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.2804
|  |  |  | Coincident | 34.6967
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.0884
|  |  |  | Coincident | 30.6799
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.1614
|  |  |  | Coincident | 30.7575
| South Granville | Substation Rating | MVA | Non-Coincident | 20
|  |  |  | Coincident | 20
|  | Raw Adjusted MD | MW | Non-Coincident | 20.3
|  |  |  | Coincident | 19.5375
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.6689
|  |  |  | Coincident | 19.906
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.446
|  |  |  | Coincident | 19.678
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.8177
|  |  |  | Coincident | 20.0493
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.0491
|  |  |  | Coincident | 17.3711
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.3772
|  |  |  | Coincident | 17.6989
| South Leppington | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 13.64
|  |  |  | Coincident | 13.29
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.8227
|  |  |  | Coincident | 13.4676
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.64
|  |  |  | Coincident | 13.29
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.823
|  |  |  | Coincident | 13.4679
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.64
|  |  |  | Coincident | 13.29
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.823
|  |  |  | Coincident | 13.4679
| South_Marsden_Park | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 10.34
|  |  |  | Coincident | 8.81
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.6126
|  |  |  | Coincident | 9.0854
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.34
|  |  |  | Coincident | 8.81
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.613
|  |  |  | Coincident | 9.0857
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.34
|  |  |  | Coincident | 8.81
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.613
|  |  |  | Coincident | 9.0857
| South Nowra | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 9.85
|  |  |  | Coincident | 7.225
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.1531
|  |  |  | Coincident | 7.3455
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.4516
|  |  |  | Coincident | 6.9328
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.7423
|  |  |  | Coincident | 7.0483
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.4503
|  |  |  | Coincident | 6.1983
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.7102
|  |  |  | Coincident | 6.3016
| South Windsor | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 32.95
|  |  |  | Coincident | 30.375
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.8011
|  |  |  | Coincident | 31.0063
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.451
|  |  |  | Coincident | 32.6806
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.3666
|  |  |  | Coincident | 33.3597
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.0541
|  |  |  | Coincident | 29.5491
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.882
|  |  |  | Coincident | 30.1632
| South Wollongong | Substation Rating | MVA | Non-Coincident | 19
|  |  |  | Coincident | 19
|  | Raw Adjusted MD | MW | Non-Coincident | 14.508
|  |  |  | Coincident | 9.4104
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.5203
|  |  |  | Coincident | 9.4547
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.41
|  |  |  | Coincident | 8.6982
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.4211
|  |  |  | Coincident | 8.739
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.103
|  |  |  | Coincident | 7.8504
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.113
|  |  |  | Coincident | 7.8872
| Springwood | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 28.725
|  |  |  | Coincident | 27.78
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.169
|  |  |  | Coincident | 28.0028
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.665
|  |  |  | Coincident | 26.7549
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.0926
|  |  |  | Coincident | 26.9695
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.1774
|  |  |  | Coincident | 22.4149
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.5357
|  |  |  | Coincident | 22.5947
| St Marys | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 33.725
|  |  |  | Coincident | 32.2
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.7525
|  |  |  | Coincident | 32.2262
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.725
|  |  |  | Coincident | 32.2
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.753
|  |  |  | Coincident | 32.2267
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.725
|  |  |  | Coincident | 32.2
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.753
|  |  |  | Coincident | 32.2267
| Sussex Inlet | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 6.171
|  |  |  | Coincident | 5.526
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.2363
|  |  |  | Coincident | 5.5712
|  | Date MD occurred |  | Non-Coincident | 2020-01-26
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.171
|  |  |  | Coincident | 5.526
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.236
|  |  |  | Coincident | 5.5709
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.171
|  |  |  | Coincident | 5.526
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.236
|  |  |  | Coincident | 5.5709
| Tahmoor | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 18.72
|  |  |  | Coincident | 18.57
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.8122
|  |  |  | Coincident | 18.657
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.378
|  |  |  | Coincident | 18.2307
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.4683
|  |  |  | Coincident | 18.316
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.6514
|  |  |  | Coincident | 15.526
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.7283
|  |  |  | Coincident | 15.5986
| The Oaks | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 8.675
|  |  |  | Coincident | 8.1625
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.9435
|  |  |  | Coincident | 8.4221
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.675
|  |  |  | Coincident | 8.1625
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.944
|  |  |  | Coincident | 8.4226
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.675
|  |  |  | Coincident | 8.1625
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.944
|  |  |  | Coincident | 8.4226
| Tomerong Zone | Substation Rating | MVA | Non-Coincident | 15
|  |  |  | Coincident | 15
|  | Raw Adjusted MD | MW | Non-Coincident | 10.51
|  |  |  | Coincident | 9.98
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.6563
|  |  |  | Coincident | 10.1098
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.51
|  |  |  | Coincident | 9.98
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.656
|  |  |  | Coincident | 10.1095
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.51
|  |  |  | Coincident | 9.98
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.656
|  |  |  | Coincident | 10.1095
| Ulladulla | Substation Rating | MVA | Non-Coincident | 30
|  |  |  | Coincident | 30
|  | Raw Adjusted MD | MW | Non-Coincident | 25.854
|  |  |  | Coincident | 21.828
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.2386
|  |  |  | Coincident | 22.1875
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.854
|  |  |  | Coincident | 21.828
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.239
|  |  |  | Coincident | 22.1878
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.854
|  |  |  | Coincident | 21.828
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.239
|  |  |  | Coincident | 22.1878
| Unanderra | Substation Rating | MVA | Non-Coincident | 24
|  |  |  | Coincident | 24
|  | Raw Adjusted MD | MW | Non-Coincident | 13.5756
|  |  |  | Coincident | 6.8148
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.6624
|  |  |  | Coincident | 7.0165
|  | Date MD occurred |  | Non-Coincident | 2019-12-19
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.368
|  |  |  | Coincident | 7.2126
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.459
|  |  |  | Coincident | 7.4256
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.537
|  |  |  | Coincident | 6.7954
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.6228
|  |  |  | Coincident | 6.9961
| Warilla | Substation Rating | MVA | Non-Coincident | 20
|  |  |  | Coincident | 20
|  | Raw Adjusted MD | MW | Non-Coincident | 19.242
|  |  |  | Coincident | 15.876
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.6115
|  |  |  | Coincident | 16.2141
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.7144
|  |  |  | Coincident | 14.6156
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.055
|  |  |  | Coincident | 14.9273
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.6564
|  |  |  | Coincident | 12.9176
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.9575
|  |  |  | Coincident | 13.1931
| Wentworth Falls | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 5.7402
|  |  |  | Coincident | 5.1408
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.8114
|  |  |  | Coincident | 5.2126
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.74
|  |  |  | Coincident | 5.1406
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.811
|  |  |  | Coincident | 5.2122
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.74
|  |  |  | Coincident | 5.1406
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.811
|  |  |  | Coincident | 5.2122
| Werrington | Substation Rating | MVA | Non-Coincident | 70
|  |  |  | Coincident | 70
|  | Raw Adjusted MD | MW | Non-Coincident | 35.46
|  |  |  | Coincident | 31.08
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.5
|  |  |  | Coincident | 31.1147
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 13:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.339
|  |  |  | Coincident | 32.7269
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.339
|  |  |  | Coincident | 32.7265
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.205
|  |  |  | Coincident | 29.98
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.205
|  |  |  | Coincident | 29.9797
| West Castle Hill | Substation Rating | MVA | Non-Coincident | 65
|  |  |  | Coincident | 65
|  | Raw Adjusted MD | MW | Non-Coincident | 39.36
|  |  |  | Coincident | 36.6283
|  | Raw Adjusted MD | MVA | Non-Coincident | 39.3633
|  |  |  | Coincident | 36.6367
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 40.71
|  |  |  | Coincident | 37.8846
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.7134
|  |  |  | Coincident | 37.8933
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 36.0456
|  |  |  | Coincident | 33.5439
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.0486
|  |  |  | Coincident | 33.5516
| West Liverpool Zone | Substation Rating | MVA | Non-Coincident | 70
|  |  |  | Coincident | 70
|  | Raw Adjusted MD | MW | Non-Coincident | 35.175
|  |  |  | Coincident | 31.625
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.2114
|  |  |  | Coincident | 31.7307
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.987
|  |  |  | Coincident | 30.5569
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.0218
|  |  |  | Coincident | 30.6587
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.1583
|  |  |  | Coincident | 27.1146
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.1892
|  |  |  | Coincident | 27.2049
| West Parramatta | Substation Rating | MVA | Non-Coincident | 90
|  |  |  | Coincident | 90
|  | Raw Adjusted MD | MW | Non-Coincident | 51.6625
|  |  |  | Coincident | 32.0375
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.8897
|  |  |  | Coincident | 32.1438
|  | Date MD occurred |  | Non-Coincident | 2020-01-28
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 13:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.577
|  |  |  | Coincident | 31.9845
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.8036
|  |  |  | Coincident | 32.0905
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 48.4765
|  |  |  | Coincident | 30.0618
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 48.6895
|  |  |  | Coincident | 30.1614
| West Pennant Hills | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 26.76
|  |  |  | Coincident | 25.956
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.6746
|  |  |  | Coincident | 26.8714
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.023
|  |  |  | Coincident | 24.2712
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.8786
|  |  |  | Coincident | 25.1275
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.8092
|  |  |  | Coincident | 20.184
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.5207
|  |  |  | Coincident | 20.8961
| West Wetherill Park 11kV | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 23.4
|  |  |  | Coincident | 7.6125
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.2827
|  |  |  | Coincident | 7.6612
|  | Date MD occurred |  | Non-Coincident | 2020-01-28
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.4
|  |  |  | Coincident | 7.6125
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.283
|  |  |  | Coincident | 7.6613
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.4
|  |  |  | Coincident | 7.6125
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.283
|  |  |  | Coincident | 7.6613
| West Wollongong | Substation Rating | MVA | Non-Coincident | 22.5
|  |  |  | Coincident | 22.5
|  | Raw Adjusted MD | MW | Non-Coincident | 13.2
|  |  |  | Coincident | 11.8583
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.3
|  |  |  | Coincident | 11.9583
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.8789
|  |  |  | Coincident | 11.5698
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.9765
|  |  |  | Coincident | 11.6674
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.2126
|  |  |  | Coincident | 10.0729
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.2975
|  |  |  | Coincident | 10.1579
| Westmead | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 26.5375
|  |  |  | Coincident | 22.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.9615
|  |  |  | Coincident | 22.5743
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:15
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.559
|  |  |  | Coincident | 22.4181
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.9823
|  |  |  | Coincident | 22.5917
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.0206
|  |  |  | Coincident | 21.1196
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.4194
|  |  |  | Coincident | 21.2831
| Wetherill Park | Substation Rating | MVA | Non-Coincident | 45
|  |  |  | Coincident | 45
|  | Raw Adjusted MD | MW | Non-Coincident | 26.276
|  |  |  | Coincident | 9.8835
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.7704
|  |  |  | Coincident | 9.8889
|  | Date MD occurred |  | Non-Coincident | 2019-12-10
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.276
|  |  |  | Coincident | 9.8835
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.77
|  |  |  | Coincident | 9.8888
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.276
|  |  |  | Coincident | 9.8835
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.77
|  |  |  | Coincident | 9.8888
| Whalan | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 29.9025
|  |  |  | Coincident | 28.1475
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.954
|  |  |  | Coincident | 28.1519
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.326
|  |  |  | Coincident | 29.4875
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.3794
|  |  |  | Coincident | 29.4916
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.1774
|  |  |  | Coincident | 26.5236
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.2255
|  |  |  | Coincident | 26.5274
| Wilton | Substation Rating | MVA | Non-Coincident | 20
|  |  |  | Coincident | 20
|  | Raw Adjusted MD | MW | Non-Coincident | 4.8975
|  |  |  | Coincident | 4.515
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.9148
|  |  |  | Coincident | 4.5305
|  | Date MD occurred |  | Non-Coincident | 2020-02-01
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.898
|  |  |  | Coincident | 4.5155
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.915
|  |  |  | Coincident | 4.5307
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.898
|  |  |  | Coincident | 4.5155
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.915
|  |  |  | Coincident | 4.5307
| Windsor | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 23.5
|  |  |  | Coincident | 21.8125
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.3559
|  |  |  | Coincident | 22.4952
|  | Date MD occurred |  | Non-Coincident | 2020-01-31
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 17:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.041
|  |  |  | Coincident | 22.3147
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.9167
|  |  |  | Coincident | 23.0132
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.4409
|  |  |  | Coincident | 19.9013
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.2219
|  |  |  | Coincident | 20.5242
| Wisemans | Substation Rating | MVA | Non-Coincident | 12.5
|  |  |  | Coincident | 12.5
|  | Raw Adjusted MD | MW | Non-Coincident | 5.088
|  |  |  | Coincident | 3.258
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.209
|  |  |  | Coincident | 3.3029
|  | Date MD occurred |  | Non-Coincident | 2019-12-10
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 15:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.088
|  |  |  | Coincident | 3.258
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.209
|  |  |  | Coincident | 3.3029
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.088
|  |  |  | Coincident | 3.258
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.209
|  |  |  | Coincident | 3.3029
| Wombarra | Substation Rating | MVA | Non-Coincident | 5
|  |  |  | Coincident | 5
|  | Raw Adjusted MD | MW | Non-Coincident | 5.075
|  |  |  | Coincident | 4.115
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.0979
|  |  |  | Coincident | 4.1379
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.075
|  |  |  | Coincident | 4.115
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.098
|  |  |  | Coincident | 4.138
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.075
|  |  |  | Coincident | 4.115
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.098
|  |  |  | Coincident | 4.138
| Woodpark | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 19.37
|  |  |  | Coincident | 6.8583
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.4367
|  |  |  | Coincident | 6.8683
|  | Date MD occurred |  | Non-Coincident | 2020-03-17
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 14:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.37
|  |  |  | Coincident | 6.8583
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.437
|  |  |  | Coincident | 6.8684
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.37
|  |  |  | Coincident | 6.8583
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.437
|  |  |  | Coincident | 6.8684
| Yatte Yattah | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 3.3694
|  |  |  | Coincident | 2.9783
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.5717
|  |  |  | Coincident | 3.2367
|  | Date MD occurred |  | Non-Coincident | 2019-12-28
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.032
|  |  |  | Coincident | 3.564
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.4222
|  |  |  | Coincident | 4.0074
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.032
|  |  |  | Coincident | 3.564
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.4222
|  |  |  | Coincident | 4.0074
| Yennora | Substation Rating | MVA | Non-Coincident | 25
|  |  |  | Coincident | 25
|  | Raw Adjusted MD | MW | Non-Coincident | 19.4715
|  |  |  | Coincident | 16.362
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.4728
|  |  |  | Coincident | 16.3799
|  | Date MD occurred |  | Non-Coincident | 2020-01-23
|  |  |  | Coincident | 2020-02-01
|  | Half hour time period MD occurred |  | Non-Coincident | 16:45
|  |  |  | Coincident | 17:30
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.003
|  |  |  | Coincident | 16.8086
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.004
|  |  |  | Coincident | 16.8268
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.0797
|  |  |  | Coincident | 15.1925
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.0806
|  |  |  | Coincident | 15.2088
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 6.3 Sustained interruptions
REGULATORY REPORTING STATEMENT
Endeavour Energy
CATEGORY ANALYSIS 2019-20
6.3 SUSTAINED INTERRUPTIONS TO SUPPLY
6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2019-20)
There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data.
Definitions:
Feeder classification definitions (column E) |  |  |  |  | Average duration of sustained customer interruption (column I) |  | Effect on unplanned SAIDI (column J) |  | Effect on unplanned SAIFI (column K)
CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km. Short rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km. Long rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km. |  |  |  |  | The average duration of an interruption experienced by an affected customer. |  | The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less). |  | The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
Date of event | Time of interruption | Asset ID | Feeder classification | Reason for interruption | Detailed reason for interruption | Number of customers affected by the interruption | Average duration of sustained customer interruption | Effect on unplanned SAIDI | Effect on unplanned SAIFI | MED
(DD/MM/YYYY) | (HH:MM) | (eg. feeder ID) | (drop down) | (select from options in drop-down box) | (select from options in column 'O' that correspond with reason in column 'F') |  | (minutes)
2019-07-01 | 8:53 | 55870 | Urban | Asset Failure | Distribution substation | 1 | 183 | 0.0002442 | 1.3344e-06 | No
2019-07-01 | 10:48 | W120 | Short rural | Asset Failure | HV | 1163 | 40 | 0.15304 | 0.0038261 | No
2019-07-01 | 11:22 | J493 | Urban | Asset Failure | Distribution substation | 15 | 58 | 0.0011609 | 2.0016e-05 | No
2019-07-01 | 12:35 | HKC2 | Short rural | Other | Probable Accidental Damage - Vehicle High Load | 87 | 14.046 | 0.0040202 | 0.00028622 | No
2019-07-01 | 13:56 | 9020 | Urban | Asset Failure | Distribution substation | 1 | 198 | 0.00026421 | 1.3344e-06 | No
2019-07-01 | 14:35 | 35981 | Short rural | Unknown | Unknown | 3 | 121 | 0.0011942 | 9.8696e-06 | No
2019-07-01 | 14:48 | DFA2 | Short rural | Asset Failure | LV | 39 | 221.8718 | 0.028467 | 0.0001283 | No
2019-07-01 | 15:18 | L584 | Short rural | Asset Failure | Distribution substation | 1 | 67 | 0.00022042 | 3.2899e-06 | No
2019-07-01 | 17:39 | BL1251 | Urban | Third Party | Other | 13 | 229 | 0.0039725 | 1.7347e-05 | No
2019-07-01 | 17:47 | 87220 | Short rural | Unknown | Unknown | 17 | 121 | 0.0067672 | 5.5928e-05 | No
2019-07-01 | 18:57 | 35693 | Short rural | Unknown | Unknown | 25 | 73 | 0.006004 | 8.2247e-05 | No
2019-07-01 | 19:57 | CV1284 | Urban | Unknown | Unknown | 42 | 42 | 0.0023539 | 5.6045e-05 | No
2019-07-01 | 20:41 | TM1284 | Short rural | Unknown | Unknown | 2 | 111 | 0.00073035 | 6.5797e-06 | No
2019-07-02 | 3:02 | 10245 | Short rural | Asset Failure | Distribution substation | 38 | 203 | 0.025378 | 0.00012501 | No
2019-07-02 | 11:17 | CS1284 | Urban | Asset Failure | Distribution substation | 81 | 168.5926 | 0.018223 | 0.00010809 | No
2019-07-02 | 11:34 | PH1201 | Urban | Unknown | Unknown | 1 | 256 | 0.00034161 | 1.3344e-06 | No
2019-07-02 | 15:40 | X877 | Short rural | Third Party | Dig-in | 1205 | 74.1046 | 0.29377 | 0.0039643 | No
2019-07-02 | 16:27 | L947 | Short rural | Asset Failure | Distribution substation | 1 | 205 | 0.00067442 | 3.2899e-06 | No
2019-07-02 | 18:28 | WL1217 | Urban | Unknown | Unknown | 28 | 203 | 0.0075847 | 3.7363e-05 | No
2019-07-02 | 19:03 | KMD2 | Short rural | Asset Failure | Distribution substation | 32 | 89 | 0.0093695 | 0.00010528 | No
2019-07-03 | 7:38 | ULB2 | Short rural | Unknown | Unknown | 28 | 137 | 0.01262 | 9.2116e-05 | No
2019-07-03 | 9:50 | 49918 | Urban | Asset Failure | Distribution substation | 1 | 350 | 0.00046704 | 1.3344e-06 | No
2019-07-03 | 11:16 | CX1210 | Short rural | Asset Failure | Distribution substation | 9 | 107.1111 | 0.0031714 | 2.9609e-05 | No
2019-07-03 | 12:57 | J495 | Short rural | Asset Failure | Distribution substation | 19 | 141.1053 | 0.0088201 | 6.2507e-05 | No
2019-07-03 | 14:33 | L537 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 978 | 75.4509 | 0.098467 | 0.001305 | No
2019-07-03 | 16:34 | T868 | Short rural | Unknown | Unknown | 12 | 108 | 0.0042637 | 3.9478e-05 | No
2019-07-03 | 17:12 | CD1297 | Urban | Asset Failure | Distribution substation | 15 | 203.5333 | 0.0040739 | 2.0016e-05 | No
2019-07-03 | 17:24 | 48159 | Urban | Asset Failure | Distribution substation | 1 | 514 | 0.00068588 | 1.3344e-06 | No
2019-07-03 | 19:57 | BDA2 | Short rural | Asset Failure | Distribution substation | 1 | 82 | 0.00026977 | 3.2899e-06 | No
2019-07-03 | 20:11 | J459 | Short rural | Asset Failure | Distribution substation | 1 | 130 | 0.00042768 | 3.2899e-06 | No
2019-07-03 | 22:33 | MM1142 | Urban | Asset Failure | Distribution substation | 1 | 63 | 8.4067e-05 | 1.3344e-06 | No
2019-07-04 | 7:09 | ULD2 | Urban | Network business | Switching or protection error | 659 | 15 | 0.013191 | 0.00087937 | No
2019-07-04 | 8:03 | HR1250 | Urban | Asset Failure | Distribution substation | 254 | 91 | 0.030843 | 0.00033894 | No
2019-07-04 | 8:03 | HR1250 | Urban | Unknown | Unknown | 12 | 89.3333 | 0.0014305 | 1.6013e-05 | No
2019-07-04 | 8:27 | CJ1275 | Urban | Asset Failure | HV | 594.4797 | 102.1493 | 0.081032 | 0.00079327 | No
2019-07-04 | 8:27 | 55870 | Urban | Asset Failure | HV | 390.9224 | 102.1493 | 0.053286 | 0.00052165 | No
2019-07-04 | 8:27 | CJ1204 | Urban | Asset Failure | HV | 481.5979 | 102.1493 | 0.065646 | 0.00064264 | No
2019-07-04 | 10:57 | J516 | Urban | Asset Failure | Distribution substation | 1 | 43 | 5.7379e-05 | 1.3344e-06 | No
2019-07-04 | 12:30 | 68181 | Urban | Asset Failure | Distribution substation | 1 | 133 | 0.00017748 | 1.3344e-06 | No
2019-07-04 | 12:44 | 48198 | Urban | Asset Failure | Distribution substation | 16 | 27 | 0.00057646 | 2.135e-05 | No
2019-07-04 | 13:08 | ULL2 | Short rural | Vegetation | Grow-in - NSP responsibility | 81 | 64.963 | 0.017311 | 0.00026648 | No
2019-07-04 | 13:30 | DS1205 | Urban | Asset Failure | Distribution substation | 1 | 213 | 0.00028423 | 1.3344e-06 | No
2019-07-04 | 15:17 | KMF2 | Urban | Asset Failure | Distribution substation | 45 | 156 | 0.0093675 | 6.0048e-05 | No
2019-07-04 | 17:02 | 27187 | Urban | Unknown | Unknown | 16 | 86 | 0.0018361 | 2.135e-05 | No
2019-07-04 | 22:03 | C889 | Urban | Asset Failure | Distribution substation | 1 | 204 | 0.00027222 | 1.3344e-06 | No
2019-07-05 | 5:25 | KVA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 19 | 147 | 0.0091886 | 6.2507e-05 | No
2019-07-05 | 11:03 | HS1152 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 79 | 0.0010396 | 1.3159e-05 | No
2019-07-05 | 12:54 | J506 | Urban | Asset Failure | Distribution substation | 19 | 206.6316 | 0.0052389 | 2.5354e-05 | No
2019-07-05 | 14:14 | SHK2 | Urban | Asset Failure | Distribution substation | 1 | 213 | 0.00028423 | 1.3344e-06 | No
2019-07-05 | 16:44 | 7976 | Urban | Unknown | Unknown | 13 | 101 | 0.0017521 | 1.7347e-05 | No
2019-07-05 | 21:36 | FT1208 | Urban | Asset Failure | Distribution substation | 1 | 94 | 0.00012543 | 1.3344e-06 | No
2019-07-05 | 22:46 | SY1322 | Urban | Unknown | Unknown | 52 | 51 | 0.0035388 | 6.9389e-05 | No
2019-07-05 | 22:51 | 25744 | Short rural | Asset Failure | Distribution substation | 20 | 208.4 | 0.013712 | 6.5797e-05 | No
2019-07-06 | 2:31 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 364.4286 | 0.0083924 | 2.3029e-05 | No
2019-07-06 | 6:38 | TM1284 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 133 | 0.0052506 | 3.9478e-05 | No
2019-07-06 | 9:03 | 27187 | Urban | Unknown | Unknown | 7 | 95 | 0.00088738 | 9.3408e-06 | No
2019-07-06 | 10:19 | CS1280 | Short rural | Third Party | Dig-in | 941 | 76.9841 | 0.23832 | 0.0030958 | No
2019-07-06 | 16:47 | 27187 | Urban | Asset Failure | Distribution substation | 7 | 91 | 0.00085001 | 9.3408e-06 | No
2019-07-06 | 22:37 | 19857 | Urban | Asset Failure | HV | 1346 | 130.2801 | 0.234 | 0.0017961 | No
2019-07-07 | 5:59 | SN1230 | Short rural | Asset Failure | Distribution substation | 6 | 149 | 0.0029411 | 1.9739e-05 | No
2019-07-07 | 6:01 | HR1280 | Short rural | Unknown | Unknown | 22 | 180.0455 | 0.013031 | 7.2377e-05 | No
2019-07-07 | 16:03 | X870 | Urban | Asset Failure | Distribution substation | 3 | 324 | 0.001297 | 4.0032e-06 | No
2019-07-07 | 16:05 | L947 | Short rural | Unknown | Unknown | 10 | 156 | 0.0051322 | 3.2899e-05 | No
2019-07-08 | 8:43 | NG1299 | Short rural | Asset Failure | Distribution substation | 2 | 98 | 0.00064481 | 6.5797e-06 | No
2019-07-08 | 9:19 | 55875 | Urban | Other | Probable Equipment Failure | 955 | 93.7068 | 0.11942 | 0.0012744 | No
2019-07-08 | 9:19 | T831 | Short rural | Asset Failure | Distribution substation | 1 | 262 | 0.00086194 | 3.2899e-06 | No
2019-07-08 | 10:27 | 8801 | Short rural | Unknown | Unknown | 1 | 141 | 0.00046387 | 3.2899e-06 | No
2019-07-08 | 10:40 | 9025 | Urban | Asset Failure | Distribution substation | 362 | 102.6547 | 0.049588 | 0.00048305 | No
2019-07-08 | 10:46 | MVB2 | Short rural | Asset Failure | Distribution substation | 3 | 582 | 0.0057441 | 9.8696e-06 | No
2019-07-08 | 12:36 | 35981 | Short rural | Unknown | Unknown | 8 | 131 | 0.0034478 | 2.6319e-05 | No
2019-07-08 | 13:46 | BWF2 | Short rural | Asset Failure | Distribution substation | 3 | 210 | 0.0020726 | 9.8696e-06 | No
2019-07-08 | 14:42 | JBA2 | Short rural | Asset Failure | Distribution substation | 2 | 76 | 0.00050006 | 6.5797e-06 | No
2019-07-08 | 16:38 | J478 | Short rural | Asset Failure | Distribution substation | 1 | 58 | 0.00019081 | 3.2899e-06 | No
2019-07-08 | 17:34 | X877 | Short rural | Unknown | Unknown | 5 | 194 | 0.0031912 | 1.6449e-05 | No
2019-07-08 | 17:48 | S785 | Urban | Asset Failure | HV | 837 | 4 | 0.0044676 | 0.0011169 | No
2019-07-08 | 18:10 | WRA2 | Urban | Asset Failure | Distribution substation | 1 | 905 | 0.0012076 | 1.3344e-06 | No
2019-07-08 | 19:28 | 9025 | Urban | Asset Failure | HV | 204 | 5 | 0.0013611 | 0.00027222 | No
2019-07-08 | 19:57 | 2807 | Urban | Unknown | Unknown | 58 | 78 | 0.0060368 | 7.7395e-05 | No
2019-07-08 | 20:18 | GG1232 | Short rural | Asset Failure | Distribution substation | 1 | 64 | 0.00021055 | 3.2899e-06 | No
2019-07-09 | 6:08 | X871 | Urban | Asset Failure | Distribution substation | 1 | 86 | 0.00011476 | 1.3344e-06 | No
2019-07-09 | 8:42 | WWC2 | Short rural | Asset Failure | Distribution substation | 1 | 384 | 0.0012633 | 3.2899e-06 | No
2019-07-09 | 9:45 | RW1255 | Short rural | Unknown | Unknown | 3 | 127 | 0.0012534 | 9.8696e-06 | No
2019-07-09 | 11:47 | J506 | Urban | Asset Failure | Distribution substation | 27 | 72.1111 | 0.0025981 | 3.6029e-05 | No
2019-07-09 | 14:47 | CA1236 | Urban | Asset Failure | Distribution substation | 6 | 63.5 | 0.00050841 | 8.0064e-06 | No
2019-07-09 | 14:53 | CA1284 | Urban | Asset Failure | Distribution substation | 6 | 44.3333 | 0.00035495 | 8.0064e-06 | No
2019-07-09 | 22:28 | JS1222 | Short rural | Third Party | Unauthorised access | 72 | 70.2778 | 0.016647 | 0.00023687 | No
2019-07-10 | 5:36 | C833 | Urban | Asset Failure | Distribution substation | 10 | 300.2 | 0.0040059 | 1.3344e-05 | No
2019-07-10 | 5:40 | J481 | Urban | Asset Failure | Distribution substation | 58 | 34.8621 | 0.0026982 | 7.7395e-05 | No
2019-07-10 | 6:33 | NM1239 | Urban | Unknown | Unknown | 88 | 56 | 0.0065759 | 0.00011743 | No
2019-07-10 | 10:44 | 9015 | Urban | Network business | Network error | 4.3801 | 44 | 0.00025717 | 5.8449e-06 | No
2019-07-10 | 10:44 | 9016 | Urban | Network business | Network error | 575.5501 | 44 | 0.033793 | 0.00076801 | No
2019-07-10 | 10:44 | 9017 | Urban | Network business | Network error | 357.4193 | 44 | 0.020985 | 0.00047694 | No
2019-07-10 | 10:44 | 9019 | Urban | Network business | Network error | 961.8783 | 44 | 0.056475 | 0.0012835 | No
2019-07-10 | 10:44 | 9020 | Urban | Network business | Network error | 551.0214 | 44 | 0.032352 | 0.00073528 | No
2019-07-10 | 10:44 | 9022 | Urban | Network business | Network error | 836.6064 | 44 | 0.04912 | 0.0011164 | No
2019-07-10 | 10:44 | 9025 | Urban | Network business | Network error | 1943.9053 | 44 | 0.11413 | 0.0025939 | No
2019-07-10 | 10:44 | 9026 | Urban | Network business | Network error | 570.294 | 44 | 0.033484 | 0.000761 | No
2019-07-10 | 10:44 | 9027 | Urban | Network business | Network error | 770.9043 | 44 | 0.045263 | 0.0010287 | No
2019-07-10 | 10:44 | 9029 | Urban | Network business | Network error | 849.7468 | 44 | 0.049892 | 0.0011339 | No
2019-07-10 | 10:44 | 9030 | Urban | Network business | Network error | 897.9283 | 44 | 0.052721 | 0.0011982 | No
2019-07-10 | 10:44 | 9032 | Short rural | Network business | Network error | 604.4591 | 44 | 0.087498 | 0.0019886 | No
2019-07-10 | 10:44 | 9033 | Urban | Network business | Network error | 1127.4476 | 44 | 0.066196 | 0.0015045 | No
2019-07-10 | 10:44 | 9034 | Urban | Network business | Network error | 604.4591 | 44 | 0.03549 | 0.00080659 | No
2019-07-10 | 11:38 | L509 | Urban | Other | Probable Equipment Failure | 7 | 243.4286 | 0.0022738 | 9.3408e-06 | No
2019-07-10 | 12:05 | CT1206 | Urban | Asset Failure | Distribution substation | 1 | 98 | 0.00013077 | 1.3344e-06 | No
2019-07-10 | 15:02 | 35001 | Urban | Asset Failure | Distribution substation | 1 | 269 | 0.00035895 | 1.3344e-06 | No
2019-07-10 | 15:40 | MG1219 | Short rural | Asset Failure | Distribution substation | 1 | 228 | 0.00075009 | 3.2899e-06 | No
2019-07-10 | 19:59 | OA1244 | Short rural | Unknown | Unknown | 1 | 73 | 0.00024016 | 3.2899e-06 | No
2019-07-10 | 20:37 | NA1270 | Short rural | Asset Failure | Distribution substation | 1 | 73 | 0.00024016 | 3.2899e-06 | No
2019-07-11 | 2:53 | A095 | Short rural | Third Party | Other | 4 | 110 | 0.0014475 | 1.3159e-05 | No
2019-07-11 | 3:21 | W163 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 41 | 240.2439 | 0.032405 | 0.00013488 | No
2019-07-11 | 4:18 | W127 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 144 | 524.25 | 0.24836 | 0.00047374 | No
2019-07-11 | 4:30 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 626 | 461.0048 | 0.94942 | 0.0020595 | No
2019-07-11 | 4:30 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 562.7333 | 0.02777 | 4.9348e-05 | No
2019-07-11 | 5:20 | ULE2 | Short rural | Weather |  | 1 | 808 | 0.0026582 | 3.2899e-06 | No
2019-07-11 | 5:43 | W124 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 362 | 218.7928 | 0.26057 | 0.0011909 | No
2019-07-11 | 5:52 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1179 | 317.374 | 1.231 | 0.0038787 | No
2019-07-11 | 6:00 | BDH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1291 | 219.4593 | 0.93209 | 0.0042472 | No
2019-07-11 | 6:18 | YYB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1218 | 67.2997 | 0.26967 | 0.0040071 | No
2019-07-11 | 6:26 | 35990 | Short rural | Weather |  | 25 | 432 | 0.035531 | 8.2247e-05 | No
2019-07-11 | 6:35 | P608 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 7 | 351 | 0.0080832 | 2.3029e-05 | No
2019-07-11 | 6:35 | 35825 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 438 | 133.9132 | 0.19296 | 0.001441 | No
2019-07-11 | 6:37 | BYB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 199 | 63.4372 | 0.041531 | 0.00065468 | No
2019-07-11 | 6:38 | W123 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1024 | 112 | 0.37731 | 0.0033688 | No
2019-07-11 | 6:39 | 8686 | Short rural | Asset Failure | Distribution substation | 1 | 502 | 0.0016515 | 3.2899e-06 | No
2019-07-11 | 6:41 | BDG2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 3 | 616 | 0.0060797 | 9.8696e-06 | No
2019-07-11 | 6:49 | 35701 | Short rural | Weather |  | 18 | 207 | 0.012258 | 5.9218e-05 | No
2019-07-11 | 6:51 | 35693 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 323 | 134.8266 | 0.14327 | 0.0010626 | No
2019-07-11 | 6:53 | RW1281 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 140 | 0.00092116 | 6.5797e-06 | No
2019-07-11 | 6:58 | W124 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 206 | 490.6602 | 0.33253 | 0.00067771 | No
2019-07-11 | 7:02 | ULH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 797 | 293.7842 | 0.77031 | 0.002622 | No
2019-07-11 | 7:07 | 35818 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 528 | 0.019108 | 3.6188e-05 | No
2019-07-11 | 7:14 | 35824 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 756 | 188.6627 | 0.46923 | 0.0024871 | No
2019-07-11 | 7:24 | NA1225 | Short rural | Weather |  | 1 | 195 | 0.00064152 | 3.2899e-06 | No
2019-07-11 | 7:29 | RW1218 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 189 | 0.0012436 | 6.5797e-06 | No
2019-07-11 | 7:34 | KVD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 100 | 328.27 | 0.108 | 0.00032899 | No
2019-07-11 | 7:42 | W163 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 45 | 0.00014804 | 3.2899e-06 | No
2019-07-11 | 7:45 | W163 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 40 | 0.00013159 | 3.2899e-06 | No
2019-07-11 | 7:54 | W163 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 318 | 0.0010462 | 3.2899e-06 | No
2019-07-11 | 8:04 | W163 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 18 | 5.9218e-05 | 3.2899e-06 | No
2019-07-11 | 8:11 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 614 | 0.0404 | 6.5797e-05 | No
2019-07-11 | 8:14 | ULE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 26 | 74.6923 | 0.0063889 | 8.5536e-05 | No
2019-07-11 | 8:24 | W120 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 146 | 0.00048032 | 3.2899e-06 | No
2019-07-11 | 8:27 | KVA2 | Short rural | Weather |  | 1 | 365 | 0.0012008 | 3.2899e-06 | No
2019-07-11 | 8:33 | BDA2 | Short rural | Weather |  | 1 | 308 | 0.0010133 | 3.2899e-06 | No
2019-07-11 | 8:34 | RW1218 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 6 | 128 | 0.0025266 | 1.9739e-05 | No
2019-07-11 | 8:54 | APC2 | Short rural | Asset Failure | HV | 7 | 100.2857 | 0.0023095 | 2.3029e-05 | No
2019-07-11 | 9:00 | 35980 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 16 | 323 | 0.017002 | 5.2638e-05 | No
2019-07-11 | 9:27 | C851 | Urban | Asset Failure | Distribution substation | 50 | 400.76 | 0.026739 | 6.672e-05 | No
2019-07-11 | 9:36 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 48.5 | 0.00031912 | 6.5797e-06 | No
2019-07-11 | 9:39 | NG1247 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 12 | 116 | 0.0018575 | 1.6013e-05 | No
2019-07-11 | 9:43 | GV1282 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 136 | 135 | 0.060402 | 0.00044742 | No
2019-07-11 | 9:52 | 35816 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 42 | 0.0016581 | 3.9478e-05 | No
2019-07-11 | 9:55 | BDG2 | Short rural | Weather |  | 3 | 299 | 0.002951 | 9.8696e-06 | No
2019-07-11 | 10:00 | 35982 | Short rural | Unknown | Unknown | 37 | 171 | 0.020815 | 0.00012172 | No
2019-07-11 | 10:24 | RW1218 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 9 | 44 | 0.0013028 | 2.9609e-05 | No
2019-07-11 | 10:29 | KVA2 | Short rural | Weather |  | 71 | 99.6338 | 0.023272 | 0.00023358 | No
2019-07-11 | 10:34 | 35693 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 488 | 0.043347 | 8.8826e-05 | No
2019-07-11 | 11:01 | W123 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 16 | 268.125 | 0.014114 | 5.2638e-05 | No
2019-07-11 | 11:23 | RBD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 187 | 0.0043064 | 2.3029e-05 | No
2019-07-11 | 11:46 | BDH2 | Short rural | Weather |  | 97 | 176 | 0.056165 | 0.00031912 | No
2019-07-11 | 11:54 | MVC2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 78 | 0.00051322 | 6.5797e-06 | No
2019-07-11 | 12:40 | 8676 | Urban | Third Party | Vehicle impact | 45 | 104 | 0.006245 | 6.0048e-05 | No
2019-07-11 | 12:50 | ULE2 | Short rural | Weather |  | 6 | 381 | 0.0075206 | 1.9739e-05 | No
2019-07-11 | 12:51 | RW1281 | Short rural | Weather |  | 3 | 131 | 0.0012929 | 9.8696e-06 | No
2019-07-11 | 14:29 | YYA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 31 | 299.4194 | 0.030537 | 0.00010199 | No
2019-07-11 | 15:51 | KVA2 | Short rural | Weather |  | 1 | 78 | 0.00025661 | 3.2899e-06 | No
2019-07-11 | 16:07 | RW1292 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 334.3636 | 0.0121 | 3.6188e-05 | No
2019-07-11 | 16:18 | ULF2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1702 | 110 | 0.61593 | 0.0055993 | No
2019-07-11 | 16:51 | 55874 | Urban | Weather |  | 1 | 107 | 0.00014278 | 1.3344e-06 | No
2019-07-11 | 16:53 | BDH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 137 | 0.0036057 | 2.6319e-05 | No
2019-07-11 | 17:14 | 52237 | Urban | Asset Failure | Distribution substation | 1 | 94 | 0.00012543 | 1.3344e-06 | No
2019-07-11 | 17:20 | BWH2 | Short rural | Weather |  | 44 | 264 | 0.038215 | 0.00014475 | No
2019-07-11 | 17:30 | YYA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 1149 | 0.0037801 | 3.2899e-06 | No
2019-07-11 | 17:30 | MVF2 | Short rural | Asset Failure | Distribution substation | 11 | 55 | 0.0019904 | 3.6188e-05 | No
2019-07-11 | 18:43 | BK1236 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 68 | 120.5735 | 0.026974 | 0.00022371 | No
2019-07-11 | 19:01 | 10241 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 68 | 1040 | 0.23266 | 0.00022371 | No
2019-07-11 | 19:01 | R208 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1091.0853 | 13.2976 | 0.047732 | 0.0035895 | No
2019-07-11 | 19:01 | R210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1184.3824 | 13.2976 | 0.051813 | 0.0038965 | No
2019-07-11 | 19:01 | R211 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1340.5323 | 13.2976 | 0.058645 | 0.0044102 | No
2019-07-11 | 20:44 | 35824 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 2 | 156 | 0.0010264 | 6.5797e-06 | No
2019-07-11 | 22:36 | 10244 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 230 | 127 | 0.096097 | 0.00075667 | No
2019-07-12 | 9:52 | W163 | Short rural | Unknown | Unknown | 105 | 165 | 0.056997 | 0.00034544 | No
2019-07-12 | 11:17 | W120 | Short rural | Asset Failure | Distribution substation | 1 | 172 | 0.00056586 | 3.2899e-06 | No
2019-07-12 | 13:47 | ER1252 | Short rural | Other | Probable Accidental Damage - Vehicle Impact | 169 | 70.6509 | 0.039281 | 0.00055599 | No
2019-07-12 | 13:56 | ER1252 | Short rural | Other | Probable Accidental Damage - Vehicle Impact | 59 | 129 | 0.025039 | 0.0001941 | No
2019-07-12 | 14:11 | 10241 | Short rural | Asset Failure | Distribution substation | 26 | 79.2692 | 0.0067804 | 8.5536e-05 | No
2019-07-12 | 14:25 | BWE2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 31 | 147 | 0.014992 | 0.00010199 | No
2019-07-12 | 14:39 | W127 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 82 | 0.0013488 | 1.6449e-05 | No
2019-07-12 | 15:09 | CT1203 | Urban | Asset Failure | Distribution substation | 1 | 122 | 0.0001628 | 1.3344e-06 | No
2019-07-12 | 15:10 | R211 | Short rural | Asset Failure | Distribution substation | 1 | 1108 | 0.0036452 | 3.2899e-06 | No
2019-07-12 | 16:23 | 35818 | Short rural | Asset Failure | Distribution substation | 1 | 280 | 0.00092116 | 3.2899e-06 | No
2019-07-12 | 16:44 | RD1228 | Urban | Unknown | Unknown | 29 | 92 | 0.0035602 | 3.8698e-05 | No
2019-07-12 | 18:06 | RBD2 | Short rural | Asset Failure | Distribution substation | 2 | 304 | 0.0020002 | 6.5797e-06 | No
2019-07-12 | 18:44 | RW1292 | Short rural | Asset Failure | Distribution substation | 1 | 158 | 0.0005198 | 3.2899e-06 | No
2019-07-12 | 21:46 | RW1218 | Short rural | Asset Failure | LV | 9 | 177 | 0.0052408 | 2.9609e-05 | No
2019-07-13 | 0:26 | BWF2 | Short rural | Asset Failure | Distribution substation | 1 | 99 | 0.0003257 | 3.2899e-06 | No
2019-07-13 | 0:59 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 93 | 380.129 | 0.1163 | 0.00030596 | No
2019-07-13 | 1:21 | ULE2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 27 | 260 | 0.023095 | 8.8826e-05 | No
2019-07-13 | 5:23 | APC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 165.4038 | 0.028296 | 0.00017107 | No
2019-07-13 | 6:19 | RBB2 | Short rural | Asset Failure | Distribution substation | 1 | 228 | 0.00075009 | 3.2899e-06 | No
2019-07-13 | 7:02 | D852 | Urban | Unknown | Unknown | 37 | 163 | 0.0080478 | 4.9373e-05 | No
2019-07-13 | 7:43 | ULH2 | Short rural | Asset Failure | Distribution substation | 2 | 152 | 0.0010001 | 6.5797e-06 | No
2019-07-13 | 8:36 | 7092/3 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 586.875 | 0.015446 | 2.6319e-05 | No
2019-07-13 | 9:28 | DP1236 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 44 | 311 | 0.045018 | 0.00014475 | No
2019-07-13 | 11:38 | TM1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 74.1111 | 0.0021943 | 2.9609e-05 | No
2019-07-13 | 12:04 | L947 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 106 | 183 | 0.063817 | 0.00034873 | No
2019-07-13 | 12:09 | HR1213 | Urban | Other | FOREIGN MATTER ON SYSTEM | 571 | 38 | 0.028954 | 0.00076194 | No
2019-07-13 | 12:33 | 35693 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 23.3333 | 0.00092116 | 3.9478e-05 | No
2019-07-13 | 12:44 | APF2 | Short rural | Other | Probable Equipment Failure | 569 | 41.8805 | 0.078397 | 0.0018719 | No
2019-07-13 | 13:02 | FT1204 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 868 | 102.621 | 0.29304 | 0.0028556 | No
2019-07-13 | 13:28 | CR1228 | Urban | Asset Failure | Distribution substation | 108 | 126.8981 | 0.018288 | 0.00014412 | No
2019-07-13 | 13:31 | R210 | Short rural | Unknown | Unknown | 12 | 158 | 0.0062376 | 3.9478e-05 | No
2019-07-13 | 13:41 | KC1236 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 89 | 124.6966 | 0.036511 | 0.0002928 | No
2019-07-13 | 13:49 | A344 | Urban | Asset Failure | LV | 125 | 196.048 | 0.032701 | 0.0001668 | No
2019-07-13 | 14:02 | CD1234 | Short rural | Weather |  | 3 | 1099 | 0.010847 | 9.8696e-06 | No
2019-07-13 | 14:38 | YYA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1012 | 68 | 0.2264 | 0.0033293 | No
2019-07-13 | 15:23 | RV1206 | Short rural | Weather |  | 65 | 104.9538 | 0.022443 | 0.00021384 | No
2019-07-13 | 17:42 | CA1280 | Short rural | Asset Failure | Distribution substation | 28 | 298.8571 | 0.02753 | 9.2116e-05 | No
2019-07-14 | 0:07 | SHC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1350 | 185.297 | 0.82296 | 0.0044413 | No
2019-07-14 | 2:29 | MVF2 | Short rural | Weather |  | 16 | 178.25 | 0.0093827 | 5.2638e-05 | No
2019-07-14 | 6:33 | RW1218 | Short rural | Asset Failure | Distribution substation | 14 | 74 | 0.0034083 | 4.6058e-05 | No
2019-07-14 | 13:44 | BDC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 134 | 0.0030859 | 2.3029e-05 | No
2019-07-14 | 14:06 | DFA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 39 | 531.0256 | 0.068133 | 0.0001283 | No
2019-07-14 | 14:29 | BYC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 369 | 0.0048558 | 1.3159e-05 | No
2019-07-14 | 14:40 | BYB2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 3 | 483 | 0.004767 | 9.8696e-06 | No
2019-07-14 | 14:41 | W124 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1134 | 56 | 0.20892 | 0.0037307 | No
2019-07-14 | 14:49 | KVB2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 16 | 448 | 0.023582 | 5.2638e-05 | No
2019-07-14 | 15:19 | BYC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 81 | 166.1358 | 0.044272 | 0.00026648 | No
2019-07-14 | 15:44 | MG1219 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 551 | 61.9074 | 0.11222 | 0.0018127 | No
2019-07-14 | 17:08 | BDC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 348.5714 | 0.0080273 | 2.3029e-05 | No
2019-07-14 | 17:40 | BK1288 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 19.75 | 0.0007797 | 3.9478e-05 | No
2019-07-14 | 18:01 | BK1236 | Short rural | Asset Failure | Subtransmission | 970.2336 | 13 | 0.041495 | 0.0031919 | No
2019-07-14 | 18:01 | BK1251 | Short rural | Asset Failure | Subtransmission | 962.2316 | 13 | 0.041153 | 0.0031656 | No
2019-07-14 | 18:01 | BK1288 | Short rural | Asset Failure | Subtransmission | 1461.3518 | 13 | 0.062499 | 0.0048076 | No
2019-07-14 | 18:01 | BK1299 | Short rural | Asset Failure | Subtransmission | 760.183 | 13 | 0.032512 | 0.0025009 | No
2019-07-14 | 18:02 | L942 | Short rural | Unknown | Unknown | 1 | 78 | 0.00025661 | 3.2899e-06 | No
2019-07-14 | 18:08 | 10244 | Short rural | Asset Failure | Distribution substation | 1 | 259 | 0.00085207 | 3.2899e-06 | No
2019-07-14 | 18:23 | R260 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 294 | 402.1837 | 0.389 | 0.00096722 | No
2019-07-14 | 19:00 | 25449 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 23 | 122 | 0.0092314 | 7.5667e-05 | No
2019-07-14 | 19:16 | B201 | Urban | Unknown | Unknown | 24 | 49 | 0.0015693 | 3.2026e-05 | No
2019-07-14 | 19:27 | BWH2 | Short rural | Weather |  | 335 | 348.4119 | 0.38399 | 0.0011021 | No
2019-07-14 | 19:29 | T841 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 83 | 176.0241 | 0.048065 | 0.00027306 | No
2019-07-14 | 19:57 | GG1295 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 998 | 0.0197 | 1.9739e-05 | No
2019-07-14 | 20:03 | T828 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 269.9091 | 0.0097676 | 3.6188e-05 | No
2019-07-14 | 20:29 | RW1292 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 5 | 538 | 0.0088497 | 1.6449e-05 | No
2019-07-14 | 21:24 | RW1292 | Short rural | Unknown | Unknown | 1 | 653 | 0.0021483 | 3.2899e-06 | No
2019-07-14 | 23:39 | RW1292 | Short rural | Asset Failure | Distribution substation | 1 | 567 | 0.0018654 | 3.2899e-06 | No
2019-07-15 | 1:39 | T841 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 83 | 140.6265 | 0.038399 | 0.00027306 | No
2019-07-15 | 4:28 | T841 | Short rural | Weather |  | 2 | 53.5 | 0.00035202 | 6.5797e-06 | No
2019-07-15 | 8:38 | T834 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 41 | 193.9512 | 0.026161 | 0.00013488 | No
2019-07-15 | 8:59 | BK1288 | Short rural | Asset Failure | Distribution substation | 1 | 621 | 0.002043 | 3.2899e-06 | No
2019-07-15 | 9:09 | 35314 | Urban | Other | Isolation Request by EE | 52 | 10 | 0.00069389 | 6.9389e-05 | No
2019-07-15 | 9:39 | RW1292 | Short rural | Asset Failure | Distribution substation | 1 | 105 | 0.00034544 | 3.2899e-06 | No
2019-07-15 | 11:12 | 25744 | Short rural | Asset Failure | Distribution substation | 17 | 243.8824 | 0.01364 | 5.5928e-05 | No
2019-07-15 | 14:46 | L591 | Short rural | Asset Failure | HV | 5 | 38.2 | 0.00062836 | 1.6449e-05 | No
2019-07-15 | 15:01 | 53803 | Urban | Asset Failure | Distribution substation | 1 | 92 | 0.00012276 | 1.3344e-06 | No
2019-07-15 | 15:33 | JBA2 | Short rural | Unknown | Unknown | 1 | 205 | 0.00067442 | 3.2899e-06 | No
2019-07-15 | 17:40 | TM1258 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1907 | 74.2832 | 0.46604 | 0.0062738 | No
2019-07-15 | 18:26 | GV1208 | Urban | Other | Probable Equipment Failure | 102 | 15 | 0.0020416 | 0.00013611 | No
2019-07-15 | 19:29 | MG1282 | Short rural | Unknown | Unknown | 33 | 25.5455 | 0.0027734 | 0.00010857 | No
2019-07-16 | 6:39 | 35818 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 366 | 0.0012041 | 3.2899e-06 | No
2019-07-16 | 6:52 | 35818 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 80 | 0.00052638 | 6.5797e-06 | No
2019-07-16 | 10:07 | ULK2 | Short rural | Asset Failure | LV | 39 | 89.2564 | 0.011452 | 0.0001283 | No
2019-07-16 | 10:54 | 9052 | Urban | Unknown | Unknown | 1 | 113 | 0.00015079 | 1.3344e-06 | No
2019-07-16 | 15:07 | 9052 | Urban | Unknown | Unknown | 1 | 98 | 0.00013077 | 1.3344e-06 | No
2019-07-16 | 15:51 | 8802 | Short rural | Asset Failure | HV | 485.334 | 180.9978 | 0.289 | 0.0015967 | No
2019-07-16 | 15:51 | 8801 | Short rural | Asset Failure | HV | 415.666 | 180.9978 | 0.24751 | 0.0013675 | No
2019-07-16 | 15:52 | 8802 | Short rural | Asset Failure | HV | 149 | 130.6174 | 0.064027 | 0.00049019 | No
2019-07-16 | 16:31 | WD1210 | Short rural | Asset Failure | Distribution substation | 42 | 51.9524 | 0.0071785 | 0.00013817 | No
2019-07-16 | 18:03 | NA1225 | Short rural | Asset Failure | Distribution substation | 3 | 134 | 0.0013225 | 9.8696e-06 | No
2019-07-16 | 18:13 | MM1202 | Urban | Unknown | Unknown | 20 | 77.65 | 0.0020723 | 2.6688e-05 | No
2019-07-17 | 2:59 | 17067 | Urban | Asset Failure | Distribution substation | 40 | 596.8 | 0.031855 | 5.3376e-05 | No
2019-07-17 | 4:49 | MM1202 | Urban | Unknown | Unknown | 7 | 223 | 0.002083 | 9.3408e-06 | No
2019-07-17 | 5:37 | C896 | Urban | Asset Failure | Distribution substation | 37 | 457.5405 | 0.02259 | 4.9373e-05 | No
2019-07-17 | 5:57 | D813 | Short rural | Third Party | Vehicle impact | 6 | 603 | 0.011903 | 1.9739e-05 | No
2019-07-17 | 10:08 | CD1230 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 12 | 0.00015791 | 1.3159e-05 | No
2019-07-17 | 10:24 | OA1233 | Short rural | Third Party | Other | 1 | 459 | 0.00151 | 3.2899e-06 | No
2019-07-17 | 12:32 | J506 | Urban | Asset Failure | Distribution substation | 19 | 259 | 0.0065666 | 2.5354e-05 | No
2019-07-17 | 14:48 | X877 | Short rural | Asset Failure | Distribution substation | 1 | 154 | 0.00050664 | 3.2899e-06 | No
2019-07-17 | 15:30 | 35763 | Urban | Unknown | Unknown | 16 | 124 | 0.0026474 | 2.135e-05 | No
2019-07-17 | 15:51 | DP1210 | Short rural | Weather |  | 49 | 252.4694 | 0.040699 | 0.0001612 | No
2019-07-17 | 16:10 | TM1258 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1907 | 132.6848 | 0.83243 | 0.0062738 | No
2019-07-17 | 19:31 | WWD2 | Urban | Animal | Animal Impact | 48 | 84 | 0.0053803 | 6.4051e-05 | No
2019-07-17 | 19:33 | WRA2 | Urban | Asset Failure | HV | 96 | 38.7083 | 0.0049586 | 0.0001281 | No
2019-07-17 | 19:53 | CR1254 | Urban | Weather |  | 106 | 161.3962 | 0.022829 | 0.00014145 | No
2019-07-17 | 23:10 | R211 | Short rural | Unknown | Unknown | 9 | 81 | 0.0023983 | 2.9609e-05 | No
2019-07-18 | 0:07 | J478 | Short rural | Other | Probable Equipment Failure | 38 | 607.6579 | 0.075966 | 0.00012501 | No
2019-07-18 | 0:40 | 25450 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1059 | 103.2729 | 0.3598 | 0.003484 | No
2019-07-18 | 8:01 | CT1206 | Urban | Asset Failure | Distribution substation | 31 | 59 | 0.0024406 | 4.1366e-05 | No
2019-07-18 | 13:00 | L585 | Short rural | Asset Failure | Distribution substation | 2 | 145 | 0.00095406 | 6.5797e-06 | No
2019-07-18 | 13:25 | CT1206 | Urban | Asset Failure | Distribution substation | 31 | 58.5484 | 0.0024219 | 4.1366e-05 | No
2019-07-18 | 15:27 | CS1250 | Urban | Asset Failure | Distribution substation | 2 | 475.5 | 0.001269 | 2.6688e-06 | No
2019-07-18 | 15:48 | SXD2 | Short rural | Third Party | Unauthorised access | 1 | 10 | 3.2899e-05 | 3.2899e-06 | No
2019-07-18 | 16:27 | DP1284 | Short rural | Asset Failure | Distribution substation | 1 | 80 | 0.00026319 | 3.2899e-06 | No
2019-07-18 | 17:10 | RD1236 | Urban | Asset Failure | Distribution substation | 1 | 219 | 0.00029223 | 1.3344e-06 | No
2019-07-19 | 6:23 | 35326 | Urban | Other | Probable Equipment Failure | 489 | 69.8875 | 0.045603 | 0.00065252 | No
2019-07-19 | 8:29 | H745 | Short rural | Asset Failure | Distribution substation | 1 | 688 | 0.0022634 | 3.2899e-06 | No
2019-07-19 | 9:18 | W184 | Urban | Third Party | Dig-in | 14 | 52.9286 | 0.00098879 | 1.8682e-05 | No
2019-07-19 | 10:17 | X217 | Short rural | Asset Failure | HV | 23 | 100 | 0.0075667 | 7.5667e-05 | No
2019-07-19 | 10:31 | 55875 | Urban | Vegetation | Grow-in - NSP responsibility | 524 | 44.3664 | 0.031022 | 0.00069923 | No
2019-07-19 | 13:00 | C857 | Urban | Asset Failure | Distribution substation | 1 | 102 | 0.00013611 | 1.3344e-06 | No
2019-07-19 | 18:02 | JS1252 | Short rural | Asset Failure | Distribution substation | 1 | 85 | 0.00027964 | 3.2899e-06 | No
2019-07-19 | 19:20 | 55354 | Urban | Asset Failure | Distribution substation | 7 | 111 | 0.0010368 | 9.3408e-06 | No
2019-07-19 | 21:28 | CT1206 | Urban | Asset Failure | Distribution substation | 31 | 36.6774 | 0.0015172 | 4.1366e-05 | No
2019-07-20 | 8:05 | X867 | Urban | Asset Failure | Distribution substation | 50 | 132 | 0.008807 | 6.672e-05 | No
2019-07-20 | 8:33 | NM1221 | Urban | Asset Failure | Distribution substation | 1 | 113 | 0.00015079 | 1.3344e-06 | No
2019-07-20 | 9:07 | 9052 | Urban | Unknown | Unknown | 1 | 10 | 1.3344e-05 | 1.3344e-06 | No
2019-07-20 | 9:55 | 9052 | Urban | Asset Failure | Distribution substation | 42 | 13.1429 | 0.00073659 | 5.6045e-05 | No
2019-07-20 | 11:39 | L582 | Short rural | Unknown | Unknown | 1 | 121 | 0.00039807 | 3.2899e-06 | No
2019-07-20 | 14:30 | SHE2 | Urban | Asset Failure | HV | 1168 | 15.8022 | 0.024629 | 0.0015586 | No
2019-07-20 | 21:45 | 55870 | Urban | Asset Failure | Distribution substation | 42 | 286.1667 | 0.016038 | 5.6045e-05 | No
2019-07-20 | 22:24 | SY1112 | Urban | Third Party | Vehicle impact | 94 | 168.2766 | 0.021108 | 0.00012543 | No
2019-07-21 | 10:22 | 35765 | Urban | Asset Failure | Distribution substation | 69 | 160.3188 | 0.014761 | 9.2074e-05 | No
2019-07-21 | 10:48 | 55875 | Urban | Asset Failure | Distribution substation | 6 | 143 | 0.0011449 | 8.0064e-06 | No
2019-07-21 | 16:01 | ULK2 | Short rural | Asset Failure | Distribution substation | 26 | 321 | 0.027457 | 8.5536e-05 | No
2019-07-21 | 23:59 | C896 | Urban | Asset Failure | Distribution substation | 24 | 115 | 0.0036829 | 3.2026e-05 | No
2019-07-22 | 10:10 | X877 | Short rural | Unknown | Unknown | 2 | 68 | 0.00044742 | 6.5797e-06 | No
2019-07-22 | 10:56 | BDA2 | Short rural | Other | Probable Animals | 1 | 173 | 0.00056915 | 3.2899e-06 | No
2019-07-22 | 11:31 | OP1282 | Urban | Third Party | Dig-in | 4 | 86 | 0.00045903 | 5.3376e-06 | No
2019-07-22 | 13:05 | PCD2 | Urban | Asset Failure | Distribution substation | 21 | 29 | 0.00081265 | 2.8022e-05 | No
2019-07-22 | 14:46 | RW1255 | Short rural | Unknown | Unknown | 1 | 176 | 0.00057902 | 3.2899e-06 | No
2019-07-22 | 15:36 | S788 | Short rural | Third Party | Vehicle impact | 10 | 147.5 | 0.0048525 | 3.2899e-05 | No
2019-07-23 | 17:15 | B719 | Short rural | Asset Failure | Distribution substation | 1 | 108 | 0.00035531 | 3.2899e-06 | No
2019-07-23 | 19:14 | L948 | Short rural | Unknown | Unknown | 21 | 152 | 0.010501 | 6.9087e-05 | No
2019-07-23 | 23:12 | 17061 | Urban | Asset Failure | Distribution substation | 1 | 311 | 0.000415 | 1.3344e-06 | No
2019-07-24 | 6:56 | CX1232 | Short rural | Unknown | Unknown | 13 | 155 | 0.0066291 | 4.2768e-05 | No
2019-07-24 | 8:45 | HR1273 | Urban | Asset Failure | Distribution substation | 14 | 123 | 0.0022978 | 1.8682e-05 | No
2019-07-24 | 9:19 | ER1122 | Short rural | Unknown | Unknown | 7 | 166 | 0.0038228 | 2.3029e-05 | No
2019-07-24 | 16:14 | RV1246 | Short rural | Animal | Animal Impact | 139 | 77.8489 | 0.0356 | 0.00045729 | No
2019-07-24 | 19:01 | 35766 | Urban | Asset Failure | Distribution substation | 52 | 64 | 0.0044409 | 6.9389e-05 | No
2019-07-24 | 23:12 | NM1236 | Urban | Animal | Animal Impact | 396 | 147.0606 | 0.07771 | 0.00052842 | No
2019-07-25 | 3:21 | AZ1272 | Short rural | Unknown | Unknown | 16 | 80 | 0.004211 | 5.2638e-05 | No
2019-07-25 | 8:49 | RD1251 | Urban | Network business | Network error | 1081 | 27.9991 | 0.040388 | 0.0014425 | No
2019-07-25 | 9:46 | 10241 | Short rural | Network business | Switching or protection error | 40 | 62 | 0.0081589 | 0.00013159 | No
2019-07-25 | 12:37 | W124 | Short rural | Vegetation | Grow-in - NSP responsibility | 41 | 12 | 0.0016186 | 0.00013488 | No
2019-07-25 | 13:29 | NA1270 | Short rural | Vegetation | Grow-in - NSP responsibility | 39 | 146.3333 | 0.018775 | 0.0001283 | No
2019-07-25 | 16:51 | DS1241 | Urban | Asset Failure | Distribution substation | 2 | 205 | 0.0005471 | 2.6688e-06 | No
2019-07-25 | 19:00 | 8801 | Short rural | Asset Failure | Distribution substation | 4 | 123 | 0.0016186 | 1.3159e-05 | No
2019-07-25 | 20:01 | H745 | Short rural | Asset Failure | Distribution substation | 30 | 95 | 0.0093761 | 9.8696e-05 | No
2019-07-26 | 2:51 | MVB2 | Short rural | Unknown | Unknown | 9 | 315.6667 | 0.0093465 | 2.9609e-05 | No
2019-07-26 | 7:19 | DP1258 | Short rural | Asset Failure | LV | 178 | 33.6854 | 0.019726 | 0.0005856 | No
2019-07-26 | 8:40 | R208 | Short rural | Vegetation | Grow-in - NSP responsibility | 98 | 64 | 0.020634 | 0.00032241 | No
2019-07-26 | 9:24 | APD2 | Short rural | Unknown | Unknown | 450 | 50.5422 | 0.074825 | 0.0014804 | No
2019-07-26 | 11:55 | CA1254 | Urban | Asset Failure | HV | 704 | 73.1236 | 0.068694 | 0.00093942 | No
2019-07-26 | 17:55 | 8679 | Urban | Asset Failure | Distribution substation | 1 | 179 | 0.00023886 | 1.3344e-06 | No
2019-07-26 | 18:54 | 1962 | Urban | Asset Failure | Distribution substation | 104 | 80 | 0.011102 | 0.00013878 | No
2019-07-27 | 12:05 | 8694 | Urban | Unknown | Unknown | 1 | 164 | 0.00021884 | 1.3344e-06 | No
2019-07-27 | 12:14 | PK1288 | Short rural | Asset Failure | Distribution substation | 12 | 51 | 0.0020134 | 3.9478e-05 | No
2019-07-27 | 13:43 | WRE2 | Urban | Third Party | Vehicle impact | 26 | 104.0385 | 0.0036095 | 3.4694e-05 | No
2019-07-27 | 14:31 | L948 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 232.1667 | 0.0091656 | 3.9478e-05 | No
2019-07-27 | 17:45 | TM1217 | Short rural | Asset Failure | Distribution substation | 4 | 55 | 0.00072377 | 1.3159e-05 | No
2019-07-28 | 3:12 | BX1342 | Urban | Asset Failure | LV | 43 | 178.7209 | 0.010255 | 5.7379e-05 | No
2019-07-28 | 9:58 | RW1292 | Short rural | Asset Failure | HV | 10 | 254 | 0.0083563 | 3.2899e-05 | No
2019-07-28 | 12:08 | R210 | Short rural | Vegetation | Grow-in - NSP responsibility | 32 | 31.2812 | 0.0032932 | 0.00010528 | No
2019-07-28 | 15:07 | MG1286 | Short rural | Unknown | Unknown | 9 | 139 | 0.0041156 | 2.9609e-05 | No
2019-07-28 | 17:03 | J502 | Urban | Asset Failure | Distribution substation | 11 | 643.0909 | 0.0094395 | 1.4678e-05 | No
2019-07-28 | 19:19 | MYG2 | Urban | Third Party | Vehicle impact | 38 | 390.5526 | 0.019804 | 5.0707e-05 | No
2019-07-28 | 20:44 | 35001 | Urban | Unknown | Unknown | 923 | 12 | 0.01478 | 0.0012317 | No
2019-07-28 | 20:44 | 35004 | Urban | Unknown | Unknown | 711 | 12 | 0.011385 | 0.00094876 | No
2019-07-28 | 20:44 | 35005 | Urban | Unknown | Unknown | 766 | 12 | 0.012266 | 0.0010221 | No
2019-07-28 | 20:44 | 35006 | Urban | Unknown | Unknown | 7 | 12 | 0.00011209 | 9.3408e-06 | No
2019-07-28 | 20:44 | 35009 | Urban | Unknown | Unknown | 10 | 12 | 0.00016013 | 1.3344e-05 | No
2019-07-28 | 20:44 | 35010 | Urban | Unknown | Unknown | 660 | 12 | 0.010568 | 0.0008807 | No
2019-07-28 | 20:44 | 35011 | Urban | Unknown | Unknown | 70 | 12 | 0.0011209 | 9.3408e-05 | No
2019-07-28 | 20:44 | 35012 | Urban | Unknown | Unknown | 2 | 12 | 3.2026e-05 | 2.6688e-06 | No
2019-07-28 | 20:44 | 35013 | Short rural | Unknown | Unknown | 44 | 12 | 0.001737 | 0.00014475 | No
2019-07-28 | 20:44 | 35014 | Urban | Unknown | Unknown | 20 | 12 | 0.00032026 | 2.6688e-05 | No
2019-07-28 | 20:44 | 35015 | Urban | Unknown | Unknown | 11 | 12 | 0.00017614 | 1.4678e-05 | No
2019-07-29 | 2:56 | HR1269 | Urban | Unknown | Unknown | 2091 | 48.1014 | 0.13421 | 0.0027902 | No
2019-07-29 | 5:13 | HR1269 | Urban | Asset Failure | Distribution substation | 82 | 87 | 0.0095196 | 0.00010942 | No
2019-07-29 | 8:40 | A348 | Urban | Asset Failure | Distribution substation | 1 | 453 | 0.00060448 | 1.3344e-06 | No
2019-07-29 | 17:03 | HT1293 | Short rural | Third Party | Vehicle impact | 5 | 60 | 0.00098696 | 1.6449e-05 | No
2019-07-29 | 17:09 | T828 | Short rural | Unknown | Unknown | 2 | 80 | 0.00052638 | 6.5797e-06 | No
2019-07-30 | 3:30 | 35304 | Urban | Animal | Animal Impact | 37 | 77 | 0.0038017 | 4.9373e-05 | No
2019-07-30 | 9:25 | NN1262 | Urban | Asset Failure | Distribution substation | 27 | 37.6667 | 0.0013571 | 3.6029e-05 | No
2019-07-30 | 13:03 | RBB2 | Short rural | Asset Failure | Distribution substation | 1 | 191 | 0.00062836 | 3.2899e-06 | No
2019-07-30 | 14:12 | NN1262 | Urban | Asset Failure | Distribution substation | 58 | 146.7241 | 0.011356 | 7.7395e-05 | No
2019-07-30 | 16:56 | 8650 | Short rural | Asset Failure | Distribution substation | 5 | 89.8 | 0.0014771 | 1.6449e-05 | No
2019-07-30 | 17:56 | J510 | Urban | Asset Failure | Distribution substation | 1 | 169 | 0.00022551 | 1.3344e-06 | No
2019-07-31 | 6:30 | CD1234 | Short rural | Unknown | Unknown | 10 | 128 | 0.004211 | 3.2899e-05 | No
2019-07-31 | 8:33 | X213 | Short rural | Animal | Animal Impact | 84 | 91.6786 | 0.025335 | 0.00027635 | No
2019-07-31 | 8:56 | 87220 | Short rural | Other | Isolation Request by EE | 29 | 13.8276 | 0.0013192 | 9.5406e-05 | No
2019-07-31 | 14:43 | 2810 | Urban | Unknown | Unknown | 54 | 82 | 0.0059087 | 7.2058e-05 | No
2019-07-31 | 16:55 | DP1243 | Urban | Asset Failure | Distribution substation | 1 | 31 | 4.1366e-05 | 1.3344e-06 | No
2019-07-31 | 17:15 | JBA2 | Short rural | Asset Failure | Distribution substation | 1 | 108 | 0.00035531 | 3.2899e-06 | No
2019-07-31 | 18:41 | SZ1322 | Short rural | Unknown | Unknown | 6 | 122 | 0.0024082 | 1.9739e-05 | No
2019-07-31 | 19:36 | CV1213 | Urban | Asset Failure | Distribution substation | 50 | 87.76 | 0.0058553 | 6.672e-05 | No
2019-08-01 | 6:40 | WQ1212 | Urban | Third Party | Vehicle impact | 75 | 68.7333 | 0.0068788 | 0.00010008 | No
2019-08-01 | 8:36 | CS1213 | Urban | Overload |  | 1 | 176 | 0.00023485 | 1.3344e-06 | No
2019-08-01 | 8:44 | AB1280 | Urban | Asset Failure | Distribution substation | 26 | 34.8077 | 0.0012076 | 3.4694e-05 | No
2019-08-01 | 8:53 | BYD2 | Short rural | Unknown | Unknown | 1 | 242 | 0.00079615 | 3.2899e-06 | No
2019-08-01 | 14:46 | 9026 | Urban | Asset Failure | Distribution substation | 7 | 76 | 0.0007099 | 9.3408e-06 | No
2019-08-01 | 15:24 | BYB2 | Short rural | Unknown | Unknown | 859 | 146.2584 | 0.41333 | 0.002826 | No
2019-08-01 | 18:43 | CLD2 | Short rural | Asset Failure | Distribution substation | 25 | 269.64 | 0.022177 | 8.2247e-05 | No
2019-08-01 | 18:44 | 8686 | Short rural | Other | Probable Theft of EE Equipment | 48 | 143 | 0.022582 | 0.00015791 | No
2019-08-01 | 23:58 | 2815 | Urban | Asset Failure | Distribution substation | 32 | 106.5625 | 0.0045503 | 4.2701e-05 | No
2019-08-02 | 2:53 | MVB2 | Short rural | Unknown | Unknown | 1 | 382 | 0.0012567 | 3.2899e-06 | No
2019-08-02 | 6:38 | BWH2 | Short rural | Third Party | Unauthorised access | 6 | 203 | 0.0040071 | 1.9739e-05 | No
2019-08-02 | 8:06 | RW1255 | Short rural | Vegetation | Grow-in - NSP responsibility | 30 | 168.8333 | 0.016663 | 9.8696e-05 | No
2019-08-02 | 8:56 | YYB2 | Short rural | Asset Failure | Distribution substation | 1 | 136 | 0.00044742 | 3.2899e-06 | No
2019-08-02 | 12:24 | B217 | Urban | Unknown | Unknown | 22 | 170 | 0.0049907 | 2.9357e-05 | No
2019-08-02 | 13:08 | WH1287 | Urban | Asset Failure | Distribution substation | 14 | 616 | 0.011508 | 1.8682e-05 | No
2019-08-03 | 0:31 | WH1235 | Urban | Other | Fault within LV customers installation - Defective Equipment | 82 | 93 | 0.010176 | 0.00010942 | No
2019-08-03 | 20:21 | WD1247 | Short rural | Asset Failure | Distribution substation | 5 | 175 | 0.0028786 | 1.6449e-05 | No
2019-08-04 | 9:50 | 8685 | Urban | Asset Failure | Distribution substation | 1 | 65 | 8.6736e-05 | 1.3344e-06 | No
2019-08-04 | 14:37 | C812 | Short rural | Other | Probable Willful damage - damage/destruction of EE equipment | 3 | 82 | 0.00080931 | 9.8696e-06 | No
2019-08-05 | 5:44 | MM1352 | Short rural | Other | Probable Accidental Damage - Vehicle High Load | 32 | 62.1875 | 0.0065468 | 0.00010528 | No
2019-08-05 | 9:39 | ER1232 | Short rural | Asset Failure | HV | 8 | 169.375 | 0.0044578 | 2.6319e-05 | No
2019-08-05 | 10:48 | BWB2 | Urban | Asset Failure | Distribution substation | 28 | 215 | 0.0080331 | 3.7363e-05 | No
2019-08-05 | 11:19 | DS1290 | Urban | Third Party | Vehicle impact | 57 | 38.2807 | 0.0029117 | 7.6061e-05 | No
2019-08-05 | 11:51 | LP1312 | Urban | Third Party | Other | 11 | 74 | 0.0010862 | 1.4678e-05 | No
2019-08-05 | 16:36 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 271 | 349.6015 | 0.31169 | 0.00089155 | No
2019-08-05 | 18:50 | FF1243 | Urban | Other | Fire | 12 | 254.3333 | 0.0040726 | 1.6013e-05 | No
2019-08-05 | 19:18 | 35981 | Short rural | Third Party | Unauthorised access | 465 | 95.7634 | 0.1465 | 0.0015298 | No
2019-08-06 | 2:35 | HKC2 | Short rural | Unknown | Unknown | 825 | 113.0473 | 0.30683 | 0.0027141 | No
2019-08-06 | 7:30 | FF1243 | Urban | Other | Fire | 3 | 135 | 0.00054043 | 4.0032e-06 | No
2019-08-06 | 10:02 | C851 | Urban | Asset Failure | Distribution substation | 78 | 41.1795 | 0.0042861 | 0.00010408 | No
2019-08-06 | 11:31 | 7970 | Urban | Asset Failure | Distribution substation | 44 | 69.5227 | 0.0040819 | 5.8714e-05 | No
2019-08-06 | 12:44 | BYC2 | Short rural | Asset Failure | LV | 33 | 210.5758 | 0.022861 | 0.00010857 | No
2019-08-06 | 19:23 | SY1132 | Urban | Asset Failure | Distribution substation | 124 | 54.5806 | 0.0090312 | 0.00016547 | No
2019-08-07 | 5:47 | S743 | Short rural | Third Party | Unauthorised access | 282.1542 | 112.3011 | 0.10424 | 0.00092825 | No
2019-08-07 | 5:47 | GL1233 | Short rural | Third Party | Unauthorised access | 567.31 | 112.3011 | 0.2096 | 0.0018664 | No
2019-08-07 | 5:47 | GL1255 | Short rural | Third Party | Unauthorised access | 487.2663 | 112.3011 | 0.18002 | 0.001603 | No
2019-08-07 | 5:47 | S738 | Short rural | Third Party | Unauthorised access | 493.2695 | 112.3011 | 0.18224 | 0.0016228 | No
2019-08-07 | 6:07 | CN1243 | Urban | Third Party | Other | 25 | 162 | 0.0054043 | 3.336e-05 | No
2019-08-07 | 6:39 | RW1281 | Short rural | Weather |  | 10 | 157 | 0.0051651 | 3.2899e-05 | No
2019-08-07 | 6:47 | 6423 | Urban | Asset Failure | Distribution substation | 11 | 206 | 0.0030237 | 1.4678e-05 | No
2019-08-07 | 8:59 | T872 | Urban | Asset Failure | Distribution substation | 9 | 31 | 0.0003723 | 1.201e-05 | No
2019-08-07 | 15:06 | J474 | Short rural | Asset Failure | Distribution substation | 31 | 46 | 0.0046913 | 0.00010199 | No
2019-08-07 | 16:43 | KME2 | Short rural | Asset Failure | Distribution substation | 36 | 294.75 | 0.034909 | 0.00011844 | No
2019-08-07 | 18:24 | ER1252 | Short rural | Asset Failure | Distribution substation | 1 | 269 | 0.00088497 | 3.2899e-06 | No
2019-08-07 | 18:45 | SG1254 | Urban | Asset Failure | Distribution substation | 1 | 132 | 0.00017614 | 1.3344e-06 | No
2019-08-07 | 19:37 | KC1284 | Short rural | Unknown | Unknown | 14 | 123 | 0.0056651 | 4.6058e-05 | No
2019-08-08 | 2:43 | BYC2 | Short rural | Unknown | Unknown | 34 | 275.7059 | 0.030839 | 0.00011186 | No
2019-08-08 | 8:37 | J473 | Urban | Asset Failure | Distribution substation | 1 | 69 | 9.2074e-05 | 1.3344e-06 | No
2019-08-08 | 8:49 | W111 | Short rural | Asset Failure | Distribution substation | 15 | 196.5333 | 0.0096985 | 4.9348e-05 | No
2019-08-08 | 9:59 | ULF2 | Short rural | Asset Failure | Distribution substation | 60 | 31.3667 | 0.0061915 | 0.00019739 | No
2019-08-08 | 10:12 | 10290 | Short rural | Asset Failure | HV | 357 | 133.4566 | 0.15674 | 0.0011745 | No
2019-08-08 | 12:36 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 652 | 155.3298 | 0.33318 | 0.002145 | No
2019-08-08 | 12:47 | 35702 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 64 | 598 | 0.05107 | 8.5402e-05 | No
2019-08-08 | 13:15 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 166 | 252.5663 | 0.13793 | 0.00054612 | No
2019-08-08 | 13:40 | FF1284 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 60 | 169.3333 | 0.013557 | 8.0064e-05 | No
2019-08-08 | 14:00 | ULE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 9 | 36 | 0.0010659 | 2.9609e-05 | No
2019-08-08 | 15:47 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 207 | 59.3623 | 0.040426 | 0.000681 | No
2019-08-08 | 15:54 | PH1286 | Urban | Third Party | Other | 60 | 24.45 | 0.0019576 | 8.0064e-05 | No
2019-08-08 | 20:10 | S785 | Urban | Asset Failure | Distribution substation | 17 | 508 | 0.011524 | 2.2685e-05 | No
2019-08-08 | 20:16 | BX1212 | Urban | Vegetation | Grow-in - NSP responsibility | 1078 | 80.3998 | 0.11565 | 0.0014385 | No
2019-08-08 | 21:08 | BX1232 | Urban | Vegetation | Grow-in - NSP responsibility | 24 | 34 | 0.0010889 | 3.2026e-05 | No
2019-08-08 | 21:53 | NG1247 | Urban | Vegetation | Grow-in - NSP responsibility | 899 | 49.8331 | 0.059781 | 0.0011996 | No
2019-08-08 | 22:14 | ULH2 | Short rural | Asset Failure | LV | 7 | 160.2857 | 0.0036912 | 2.3029e-05 | No
2019-08-08 | 22:31 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 207 | 104.5314 | 0.071186 | 0.000681 | No
2019-08-08 | 22:55 | NG1299 | Short rural | Vegetation | Grow-in - NSP responsibility | 69 | 69 | 0.015663 | 0.000227 | No
2019-08-09 | 0:17 | BYB2 | Short rural | Weather |  | 75 | 239.2533 | 0.059033 | 0.00024674 | Yes
2019-08-09 | 0:22 | DP1210 | Short rural | Weather |  | 59 | 467.9661 | 0.090833 | 0.0001941 | Yes
2019-08-09 | 0:51 | CR1262 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2302 | 77 | 0.23653 | 0.0030718 | Yes
2019-08-09 | 0:59 | JBB2 | Short rural | Weather |  | 39 | 618.4103 | 0.079345 | 0.0001283 | Yes
2019-08-09 | 1:26 | 19856 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 494.8877 | 106.7728 | 0.07051 | 0.00066038 | Yes
2019-08-09 | 1:26 | 19857 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1081.1123 | 106.7728 | 0.15403 | 0.0014426 | Yes
2019-08-09 | 1:54 | 27454 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 361 | 0.0047506 | 1.3159e-05 | Yes
2019-08-09 | 2:09 | BYG2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 94 | 471.5 | 0.14581 | 0.00030925 | Yes
2019-08-09 | 2:09 | ULE2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 27 | 751 | 0.066709 | 8.8826e-05 | Yes
2019-08-09 | 2:21 | GV1278 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 217 | 197.1659 | 0.057092 | 0.00028956 | Yes
2019-08-09 | 2:31 | C896 | Urban | Asset Failure | HV | 451.0998 | 100.5395 | 0.060519 | 0.00060195 | Yes
2019-08-09 | 2:31 | C890 | Urban | Asset Failure | HV | 612.9002 | 100.5395 | 0.082227 | 0.00081785 | Yes
2019-08-09 | 2:34 | ULJ2 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1885 | 103 | 0.25908 | 0.0025153 | Yes
2019-08-09 | 2:40 | JBB2 | Short rural | Weather |  | 110 | 389.2727 | 0.14087 | 0.00036188 | Yes
2019-08-09 | 3:21 | BX1242 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 597 | 61 | 0.048595 | 0.00079664 | Yes
2019-08-09 | 3:29 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 73 | 187 | 0.04491 | 0.00024016 | Yes
2019-08-09 | 4:01 | SWJ2 | Urban | Weather |  | 351.0862 | 137.5461 | 0.064439 | 0.00046849 | Yes
2019-08-09 | 4:01 | SWE2 | Urban | Weather |  | 591.9138 | 137.5461 | 0.10864 | 0.00078985 | Yes
2019-08-09 | 4:05 | R210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 45 | 333.6889 | 0.049401 | 0.00014804 | Yes
2019-08-09 | 5:06 | PK1236 | Short rural | Weather |  | 3 | 79 | 0.0007797 | 9.8696e-06 | Yes
2019-08-09 | 5:41 | CLB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 584 | 201 | 0.38618 | 0.0019213 | Yes
2019-08-09 | 6:42 | PK1236 | Short rural | Weather |  | 1 | 94 | 0.00030925 | 3.2899e-06 | Yes
2019-08-09 | 6:43 | WRA2 | Urban | Weather |  | 32 | 214 | 0.009138 | 4.2701e-05 | Yes
2019-08-09 | 7:36 | JBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 278.5556 | 0.016495 | 5.9218e-05 | Yes
2019-08-09 | 7:37 | RBC2 | Short rural | Weather |  | 35 | 236 | 0.027174 | 0.00011515 | Yes
2019-08-09 | 7:38 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 887 | 90.5457 | 0.26422 | 0.0029181 | Yes
2019-08-09 | 8:32 | TM1258 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1609 | 78 | 0.41288 | 0.0052934 | Yes
2019-08-09 | 8:37 | SWG2 | Urban | Weather |  | 216.1842 | 83.3915 | 0.024056 | 0.00028848 | Yes
2019-08-09 | 8:37 | SWJ2 | Urban | Weather |  | 843.8158 | 83.3915 | 0.093898 | 0.001126 | Yes
2019-08-09 | 9:11 | TM1217 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1421 | 135 | 0.63111 | 0.0046749 | Yes
2019-08-09 | 9:25 | TM1284 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 840 | 71.9083 | 0.19872 | 0.0027635 | Yes
2019-08-09 | 9:33 | A096 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 464 | 96 | 0.14654 | 0.0015265 | Yes
2019-08-09 | 9:43 | 25744 | Short rural | Asset Failure | HV | 1089 | 78.1524 | 0.27999 | 0.0035827 | Yes
2019-08-09 | 9:46 | SY1122 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 405 | 0.010809 | 2.6688e-05 | Yes
2019-08-09 | 9:50 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 281 | 25 | 0.023111 | 0.00092445 | Yes
2019-08-09 | 10:06 | 8798 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 194 | 96 | 0.06127 | 0.00063823 | Yes
2019-08-09 | 10:14 | CLA2 | Short rural | Weather |  | 1 | 343 | 0.0011284 | 3.2899e-06 | Yes
2019-08-09 | 10:18 | WL1292 | Urban | Weather |  | 15 | 237 | 0.0047438 | 2.0016e-05 | Yes
2019-08-09 | 10:29 | T868 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 991 | 248.3966 | 0.80984 | 0.0032603 | Yes
2019-08-09 | 10:39 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 265 | 160.7245 | 0.14012 | 0.00087181 | Yes
2019-08-09 | 10:43 | L947 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 102 | 369.2059 | 0.12389 | 0.00033557 | Yes
2019-08-09 | 10:45 | BX1332 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 84 | 342.1667 | 0.038353 | 0.00011209 | Yes
2019-08-09 | 10:46 | NWA2 | Urban | Asset Failure | Distribution substation | 1 | 270 | 0.00036029 | 1.3344e-06 | Yes
2019-08-09 | 10:52 | S738 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 19 | 322.0526 | 0.020131 | 6.2507e-05 | Yes
2019-08-09 | 10:53 | 10290 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 357 | 177.5238 | 0.2085 | 0.0011745 | Yes
2019-08-09 | 10:59 | GL1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 109 | 418.055 | 0.14991 | 0.0003586 | Yes
2019-08-09 | 11:06 | D814 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 191.8667 | 0.0094682 | 4.9348e-05 | Yes
2019-08-09 | 11:09 | A096 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 85 | 163.1882 | 0.045634 | 0.00027964 | Yes
2019-08-09 | 11:11 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 428 | 0.0098564 | 2.3029e-05 | Yes
2019-08-09 | 11:12 | 46397 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 20 | 93 | 0.002482 | 2.6688e-05 | Yes
2019-08-09 | 11:12 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 46 | 123.6739 | 0.018716 | 0.00015133 | Yes
2019-08-09 | 11:19 | GL1233 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 185 | 256 | 0.15581 | 0.00060862 | Yes
2019-08-09 | 11:22 | D814 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 314 | 0.0041321 | 1.3159e-05 | Yes
2019-08-09 | 11:29 | LL1172 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1017 | 45 | 0.061069 | 0.0013571 | Yes
2019-08-09 | 11:30 | 25451 | Short rural | Weather |  | 29 | 132 | 0.012594 | 9.5406e-05 | Yes
2019-08-09 | 11:43 | SZ1122 | Short rural | Weather |  | 6 | 236 | 0.0046584 | 1.9739e-05 | Yes
2019-08-09 | 11:44 | JBA2 | Short rural | Weather |  | 35 | 68.0286 | 0.0078332 | 0.00011515 | Yes
2019-08-09 | 11:56 | 8802 | Short rural | Weather |  | 14 | 282.3571 | 0.013005 | 4.6058e-05 | Yes
2019-08-09 | 12:03 | 25450 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 1059 | 63.9726 | 0.22288 | 0.003484 | Yes
2019-08-09 | 12:13 | SC1204 | Short rural | Weather |  | 720 | 84 | 0.19897 | 0.0023687 | Yes
2019-08-09 | 12:34 | TM1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 238 | 107.7143 | 0.084339 | 0.00078299 | Yes
2019-08-09 | 12:37 | RBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 206 | 19.1602 | 0.012985 | 0.00067771 | Yes
2019-08-09 | 12:41 | RBE2 | Short rural | Asset Failure | Distribution substation | 11 | 43.7273 | 0.0015824 | 3.6188e-05 | Yes
2019-08-09 | 12:41 | PH1219 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 12 | 274 | 0.0043875 | 1.6013e-05 | Yes
2019-08-09 | 12:51 | J495 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 20 | 118 | 0.0077641 | 6.5797e-05 | Yes
2019-08-09 | 12:55 | APB2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 19 | 80 | 0.0050006 | 6.2507e-05 | Yes
2019-08-09 | 13:08 | W113 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 471.1299 | 63.0344 | 0.0977 | 0.00155 | Yes
2019-08-09 | 13:08 | T868 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 604.8701 | 63.0344 | 0.12543 | 0.0019899 | Yes
2019-08-09 | 13:14 | 55354 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 35 | 181 | 0.0084534 | 4.6704e-05 | Yes
2019-08-09 | 13:18 | 8798 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 1173.5 | 0.0077213 | 6.5797e-06 | Yes
2019-08-09 | 13:22 | YYA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 164 | 574.2378 | 0.30982 | 0.00053954 | Yes
2019-08-09 | 13:30 | ULH2 | Short rural | Weather |  | 6 | 60 | 0.0011844 | 1.9739e-05 | Yes
2019-08-09 | 13:32 | CD1234 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 526 | 278.2395 | 0.48148 | 0.0017305 | Yes
2019-08-09 | 13:38 | 8737 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 983 | 71 | 0.093132 | 0.0013117 | Yes
2019-08-09 | 13:52 | LP1422 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 96 | 46.625 | 0.0059728 | 0.0001281 | Yes
2019-08-09 | 13:52 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 464 | 80.556 | 0.12297 | 0.0015265 | Yes
2019-08-09 | 14:05 | RBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 28 | 64.3929 | 0.0059316 | 9.2116e-05 | Yes
2019-08-09 | 14:08 | NN1277 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 23 | 134 | 0.0041126 | 3.0691e-05 | Yes
2019-08-09 | 14:19 | LP1312 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 47 | 88 | 0.0055191 | 6.2717e-05 | Yes
2019-08-09 | 14:39 | S788 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 5 | 65 | 0.0010692 | 1.6449e-05 | Yes
2019-08-09 | 15:10 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 1259 | 0.033136 | 2.6319e-05 | Yes
2019-08-09 | 15:39 | 25744 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 226 | 0.001487 | 6.5797e-06 | Yes
2019-08-09 | 15:41 | 2815 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 97 | 26 | 0.0033654 | 0.00012944 | Yes
2019-08-09 | 15:42 | B211 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1153 | 77.9957 | 0.12 | 0.0015386 | Yes
2019-08-09 | 15:45 | 27335 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 513 | 65.2729 | 0.044682 | 0.00068455 | Yes
2019-08-09 | 15:46 | ULE2 | Short rural | Weather |  | 27 | 359 | 0.031889 | 8.8826e-05 | Yes
2019-08-09 | 16:31 | ULL2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 5 | 128 | 0.0021055 | 1.6449e-05 | Yes
2019-08-09 | 17:10 | 87220 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 17 | 162 | 0.0090603 | 5.5928e-05 | Yes
2019-08-09 | 17:15 | SY1122 | Urban | Asset Failure | Distribution substation | 30 | 260 | 0.010408 | 4.0032e-05 | Yes
2019-08-09 | 17:47 | HKF2 | Short rural | Asset Failure | Distribution substation | 1 | 279 | 0.00091787 | 3.2899e-06 | Yes
2019-08-09 | 17:51 | 25744 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 118 | 0.0023292 | 1.9739e-05 | Yes
2019-08-09 | 18:03 | C869 | Urban | Asset Failure | Distribution substation | 11 | 132 | 0.0019375 | 1.4678e-05 | Yes
2019-08-09 | 18:17 | TM1284 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 250 | 0.00082247 | 3.2899e-06 | Yes
2019-08-09 | 18:20 | W124 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 364 | 76.4451 | 0.091544 | 0.0011975 | Yes
2019-08-09 | 20:31 | PK1262 | Short rural | Weather |  | 138 | 8 | 0.003632 | 0.000454 | Yes
2019-08-09 | 20:49 | KME2 | Short rural | Weather |  | 1038 | 302.5058 | 1.033 | 0.0034149 | Yes
2019-08-09 | 20:56 | PK1262 | Short rural | Weather |  | 909 | 43.0781 | 0.12882 | 0.0029905 | Yes
2019-08-09 | 20:56 | SHD2 | Short rural | Weather |  | 1 | 524 | 0.0017239 | 3.2899e-06 | Yes
2019-08-09 | 21:07 | KMF2 | Urban | Weather |  | 1590 | 83.7893 | 0.17778 | 0.0021217 | Yes
2019-08-09 | 21:12 | 8799 | Short rural | Weather |  | 1 | 913 | 0.0030036 | 3.2899e-06 | Yes
2019-08-09 | 21:30 | SL1112 | Short rural | Asset Failure | Distribution substation | 2 | 959 | 0.00631 | 6.5797e-06 | Yes
2019-08-09 | 21:30 | BYF2 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 468 | 167 | 0.10429 | 0.0006245 | Yes
2019-08-09 | 22:51 | JBA2 | Short rural | Weather |  | 15 | 915 | 0.045153 | 4.9348e-05 | Yes
2019-08-09 | 23:09 | HKG2 | Short rural | Weather |  | 29 | 168 | 0.016028 | 9.5406e-05 | Yes
2019-08-09 | 23:21 | WWC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1661 | 104.9025 | 0.57324 | 0.0054645 | Yes
2019-08-09 | 23:48 | AB1287 | Urban | Asset Failure | Distribution substation | 1 | 66 | 8.807e-05 | 1.3344e-06 | Yes
2019-08-10 | 7:01 | 49001 | Short rural | Asset Failure | LV | 1066 | 90.3265 | 0.31677 | 0.003507 | No
2019-08-10 | 7:38 | X877 | Short rural | Unknown | Unknown | 1 | 174 | 0.00057244 | 3.2899e-06 | No
2019-08-10 | 7:59 | 8798 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 256 | 617 | 0.51964 | 0.0008422 | No
2019-08-10 | 8:34 | BK1251 | Short rural | Asset Failure | Distribution substation | 1 | 219 | 0.00072048 | 3.2899e-06 | No
2019-08-10 | 9:04 | BYG2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 131 | 0.00086194 | 6.5797e-06 | No
2019-08-10 | 9:12 | W112 | Short rural | Weather |  | 7 | 189.2857 | 0.0043591 | 2.3029e-05 | No
2019-08-10 | 9:26 | RD1265 | Urban | Asset Failure | Distribution substation | 1 | 513 | 0.00068455 | 1.3344e-06 | No
2019-08-10 | 10:38 | R210 | Short rural | Asset Failure | LV | 40 | 214.925 | 0.028283 | 0.00013159 | No
2019-08-10 | 10:59 | PH1286 | Urban | Vegetation | Grow-in - NSP responsibility | 1362 | 83.5242 | 0.1518 | 0.0018175 | No
2019-08-10 | 11:24 | FT1204 | Short rural | Asset Failure | LV | 868 | 45.8295 | 0.13087 | 0.0028556 | No
2019-08-10 | 11:26 | 8802 | Short rural | Other | Probable Equipment Failure | 1 | 151 | 0.00049677 | 3.2899e-06 | No
2019-08-10 | 11:42 | JBB2 | Short rural | Weather |  | 5 | 28.8 | 0.00047374 | 1.6449e-05 | No
2019-08-10 | 12:13 | 8798 | Short rural | Vegetation | Grow-in - NSP responsibility | 194 | 179 | 0.11424 | 0.00063823 | No
2019-08-10 | 13:14 | D810 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 192 | 0.001895 | 9.8696e-06 | No
2019-08-10 | 13:19 | 49001 | Short rural | Unknown | Unknown | 1 | 76 | 0.00025003 | 3.2899e-06 | No
2019-08-10 | 13:48 | 35818 | Short rural | Asset Failure | Distribution substation | 1 | 339 | 0.0011153 | 3.2899e-06 | No
2019-08-10 | 14:13 | W118 | Short rural | Vegetation | Grow-in - NSP responsibility | 70 | 230.4 | 0.053059 | 0.00023029 | No
2019-08-10 | 14:16 | ULH2 | Short rural | Asset Failure | HV | 25 | 166.64 | 0.013706 | 8.2247e-05 | No
2019-08-10 | 14:54 | WD1247 | Short rural | Weather |  | 1 | 164 | 0.00053954 | 3.2899e-06 | No
2019-08-10 | 16:46 | 35304 | Urban | Weather |  | 34 | 52 | 0.0023592 | 4.537e-05 | No
2019-08-10 | 17:27 | TM1258 | Short rural | Weather |  | 1 | 941 | 0.0030958 | 3.2899e-06 | No
2019-08-10 | 18:59 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 490 | 38.1184 | 0.061448 | 0.001612 | No
2019-08-10 | 19:42 | R208 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 715 | 143.6 | 0.33778 | 0.0023523 | No
2019-08-10 | 20:20 | NG1210 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 14 | 167 | 0.0076917 | 4.6058e-05 | No
2019-08-10 | 20:53 | BYB2 | Short rural | Asset Failure | HV | 75 | 314.32 | 0.077555 | 0.00024674 | No
2019-08-10 | 21:46 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 281 | 70 | 0.064712 | 0.00092445 | No
2019-08-10 | 22:04 | KME2 | Short rural | Asset Failure | HV | 1038 | 71.8189 | 0.24525 | 0.0034149 | No
2019-08-11 | 1:00 | 8801 | Short rural | Weather |  | 327 | 546.4924 | 0.58791 | 0.0010758 | No
2019-08-11 | 9:22 | R260 | Short rural | Weather |  | 298 | 9 | 0.0088234 | 0.00098038 | No
2019-08-11 | 9:50 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 365 | 4 | 0.0048032 | 0.0012008 | No
2019-08-11 | 9:59 | TM1210 | Short rural | Vegetation | Grow-in - NSP responsibility | 25 | 169.68 | 0.013956 | 8.2247e-05 | No
2019-08-11 | 10:10 | F602 | Urban | Asset Failure | HV | 1184 | 50.8666 | 0.080366 | 0.0015799 | No
2019-08-11 | 10:17 | GG1232 | Short rural | Asset Failure | HV | 14 | 120.0714 | 0.0055303 | 4.6058e-05 | No
2019-08-11 | 12:51 | W124 | Short rural | Vegetation | Grow-in - NSP responsibility | 21 | 57.4286 | 0.0039676 | 6.9087e-05 | No
2019-08-11 | 12:54 | 35818 | Short rural | Asset Failure | Distribution substation | 6 | 131 | 0.0025858 | 1.9739e-05 | No
2019-08-11 | 13:54 | CX1206 | Short rural | Third Party | Vehicle impact | 249 | 133.5221 | 0.10938 | 0.00081918 | No
2019-08-11 | 17:42 | DP1269 | Urban | Asset Failure | HV | 1161 | 28.2326 | 0.043739 | 0.0015492 | No
2019-08-11 | 17:59 | SY1232 | Urban | Asset Failure | Distribution substation | 27 | 152.037 | 0.0054777 | 3.6029e-05 | No
2019-08-11 | 20:23 | T889 | Urban | Asset Failure | Distribution substation | 29 | 46.7586 | 0.0018094 | 3.8698e-05 | No
2019-08-11 | 20:45 | WD1251 | Short rural | Third Party | Other | 6 | 284.5 | 0.0056158 | 1.9739e-05 | No
2019-08-11 | 21:58 | A350 | Urban | Asset Failure | Distribution substation | 17 | 183 | 0.0041513 | 2.2685e-05 | No
2019-08-12 | 3:35 | 48185 | Short rural | Other | Fire | 4 | 62 | 0.00081589 | 1.3159e-05 | No
2019-08-12 | 7:08 | MG1208 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 163 | 0.00053625 | 3.2899e-06 | No
2019-08-12 | 7:49 | 55888 | Urban | Vegetation | Grow-in - NSP responsibility | 228 | 77 | 0.023427 | 0.00030424 | No
2019-08-12 | 9:42 | 1962 | Urban | Unknown | Unknown | 6 | 26 | 0.00020817 | 8.0064e-06 | No
2019-08-12 | 10:57 | CT1273 | Urban | Other | Probable Birds | 17 | 204 | 0.0046277 | 2.2685e-05 | No
2019-08-12 | 11:43 | W111 | Short rural | Asset Failure | HV | 509 | 74.7171 | 0.12512 | 0.0016745 | No
2019-08-12 | 13:57 | M159 | Urban | Unknown | Unknown | 3 | 218 | 0.0008727 | 4.0032e-06 | No
2019-08-12 | 15:16 | 77674 | Short rural | Asset Failure | HV | 20 | 61 | 0.0040136 | 6.5797e-05 | No
2019-08-12 | 16:17 | J473 | Urban | Asset Failure | Distribution substation | 24 | 38 | 0.001217 | 3.2026e-05 | No
2019-08-12 | 16:30 | APA2 | Urban | Asset Failure | Zone substation | 1601.9753 | 188.8829 | 0.40377 | 0.0021377 | No
2019-08-12 | 16:30 | APB2 | Short rural | Asset Failure | Zone substation | 1499.6158 | 188.8829 | 0.93186 | 0.0049335 | No
2019-08-12 | 16:30 | APC2 | Short rural | Asset Failure | Zone substation | 1943.8361 | 188.8829 | 1.2079 | 0.006395 | No
2019-08-12 | 16:30 | APD2 | Short rural | Asset Failure | Zone substation | 447.2015 | 188.8829 | 0.27789 | 0.0014712 | No
2019-08-12 | 16:30 | APE2 | Short rural | Asset Failure | Zone substation | 761.2364 | 188.8829 | 0.47303 | 0.0025044 | No
2019-08-12 | 16:30 | APF2 | Short rural | Asset Failure | Zone substation | 572.418 | 188.8829 | 0.3557 | 0.0018832 | No
2019-08-12 | 16:30 | APG2 | Urban | Asset Failure | Zone substation | 1678.4965 | 188.8829 | 0.42306 | 0.0022398 | No
2019-08-12 | 16:30 | APH2 | Urban | Asset Failure | Zone substation | 2042.2204 | 188.8829 | 0.51473 | 0.0027251 | No
2019-08-12 | 16:49 | J459 | Short rural | Asset Failure | Distribution substation | 13 | 43.0769 | 0.0018423 | 4.2768e-05 | No
2019-08-12 | 17:15 | MYB2 | Urban | Asset Failure | HV | 6 | 261.6667 | 0.002095 | 8.0064e-06 | No
2019-08-12 | 19:15 | T869 | Urban | Asset Failure | Distribution substation | 1 | 222 | 0.00029624 | 1.3344e-06 | No
2019-08-12 | 19:20 | CR1280 | Urban | Unknown | Unknown | 49 | 187 | 0.012227 | 6.5386e-05 | No
2019-08-12 | 19:28 | MYF2 | Urban | Asset Failure | HV | 3 | 24 | 9.6077e-05 | 4.0032e-06 | No
2019-08-12 | 19:56 | SHC2 | Short rural | Other | Probable Overload | 1350 | 25 | 0.11103 | 0.0044413 | No
2019-08-12 | 19:56 | SHH2 | Short rural | Other | Probable Overload | 36 | 154 | 0.018239 | 0.00011844 | No
2019-08-12 | 22:54 | T869 | Urban | Asset Failure | Distribution substation | 78 | 3.9487 | 0.00041099 | 0.00010408 | No
2019-08-13 | 6:18 | W111 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 59.2 | 0.0009738 | 1.6449e-05 | No
2019-08-13 | 9:48 | APC2 | Short rural | Unknown | Unknown | 1272.0034 | 33 | 0.1381 | 0.0041847 | No
2019-08-13 | 9:48 | SHG2 | Short rural | Unknown | Unknown | 1046.9966 | 33 | 0.11367 | 0.0034445 | No
2019-08-13 | 16:09 | SG1257 | Urban | Third Party | Other | 86 | 489.2442 | 0.056145 | 0.00011476 | No
2019-08-13 | 17:24 | MVC2 | Short rural | Other | Probable Equipment Failure | 13 | 67 | 0.0028655 | 4.2768e-05 | No
2019-08-13 | 17:25 | APA2 | Urban | Unknown | Unknown | 149 | 137.4832 | 0.027335 | 0.00019883 | No
2019-08-13 | 18:03 | AZ1205 | Urban | Asset Failure | Distribution substation | 1 | 167 | 0.00022284 | 1.3344e-06 | No
2019-08-13 | 18:31 | D814 | Short rural | Other | Within Customer Installation | 9 | 190 | 0.0056257 | 2.9609e-05 | No
2019-08-13 | 18:51 | NN1255 | Urban | Asset Failure | Distribution substation | 20 | 97 | 0.0025887 | 2.6688e-05 | No
2019-08-14 | 7:02 | 1960 | Urban | Asset Failure | Distribution substation | 27 | 175.4074 | 0.0063197 | 3.6029e-05 | No
2019-08-14 | 15:33 | T828 | Short rural | Asset Failure | Distribution substation | 11 | 185.3636 | 0.006708 | 3.6188e-05 | No
2019-08-14 | 18:03 | SHH2 | Short rural | Asset Failure | LV | 278.6673 | 105.2736 | 0.096512 | 0.00091678 | No
2019-08-14 | 18:03 | APA2 | Urban | Asset Failure | LV | 1060.1187 | 105.2736 | 0.14892 | 0.0014146 | No
2019-08-14 | 18:03 | APH2 | Urban | Asset Failure | LV | 1541.2141 | 105.2736 | 0.21651 | 0.0020566 | No
2019-08-15 | 11:55 | X871 | Urban | Asset Failure | Distribution substation | 13 | 83.8462 | 0.0014545 | 1.7347e-05 | No
2019-08-15 | 13:23 | CX1232 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 1 | 178 | 0.0005856 | 3.2899e-06 | No
2019-08-15 | 15:23 | 61617 | Short rural | Asset Failure | Distribution substation | 13 | 110.5385 | 0.0047275 | 4.2768e-05 | No
2019-08-15 | 16:23 | BL1210 | Short rural | Asset Failure | Distribution substation | 22 | 158 | 0.011436 | 7.2377e-05 | No
2019-08-15 | 21:38 | PK1236 | Short rural | Other | Probable Overload | 1 | 105 | 0.00034544 | 3.2899e-06 | No
2019-08-16 | 8:25 | AZ1205 | Urban | Unknown | Unknown | 21 | 25 | 0.00070056 | 2.8022e-05 | No
2019-08-16 | 8:25 | AZ1205 | Urban | Unknown | Unknown | 19 | 157 | 0.0039805 | 2.5354e-05 | No
2019-08-16 | 9:48 | 55890 | Urban | Asset Failure | Distribution substation | 5 | 272 | 0.0018148 | 6.672e-06 | No
2019-08-16 | 10:23 | NN1240 | Urban | Asset Failure | Distribution substation | 18 | 292 | 0.0070136 | 2.4019e-05 | No
2019-08-16 | 10:29 | L946 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 265 | 4 | 0.0034873 | 0.00087181 | No
2019-08-16 | 10:54 | GV1249 | Urban | Third Party | Other | 77 | 42 | 0.0043154 | 0.00010275 | No
2019-08-16 | 10:57 | 8779 | Urban | Asset Failure | Distribution substation | 2 | 244 | 0.00065119 | 2.6688e-06 | No
2019-08-16 | 12:27 | KVB2 | Short rural | Asset Failure | Distribution substation | 1 | 323 | 0.0010626 | 3.2899e-06 | No
2019-08-16 | 14:15 | NM1243 | Urban | Asset Failure | HV | 1270 | 82.4976 | 0.13981 | 0.0016947 | No
2019-08-16 | 15:05 | S735 | Short rural | Unknown | Unknown | 9 | 143 | 0.0042341 | 2.9609e-05 | No
2019-08-16 | 15:14 | 87222 | Long rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 120 | 156.3667 | 59.758 | 0.38217 | No
2019-08-16 | 16:54 | AZ1205 | Urban | Asset Failure | Distribution substation | 1 | 366 | 0.00048839 | 1.3344e-06 | No
2019-08-16 | 19:03 | 35403 | Urban | Third Party | Other | 14 | 73 | 0.0013638 | 1.8682e-05 | No
2019-08-16 | 21:20 | MM1252 | Urban | Asset Failure | Distribution substation | 1 | 63 | 8.4067e-05 | 1.3344e-06 | No
2019-08-17 | 2:54 | J477 | Urban | Asset Failure | Distribution substation | 1 | 261 | 0.00034828 | 1.3344e-06 | No
2019-08-17 | 7:02 | DS1223 | Urban | Asset Failure | Distribution substation | 7 | 589 | 0.0055017 | 9.3408e-06 | No
2019-08-17 | 9:42 | MM1162 | Urban | Asset Failure | Distribution substation | 1 | 465 | 0.0006205 | 1.3344e-06 | No
2019-08-17 | 13:46 | 7501 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 14 | 0.00013817 | 9.8696e-06 | No
2019-08-17 | 16:49 | 25781 | Urban | Asset Failure | Distribution substation | 19 | 221 | 0.0056031 | 2.5354e-05 | No
2019-08-18 | 7:08 | RW1229 | Short rural | Unknown | Unknown | 8 | 173 | 0.0045532 | 2.6319e-05 | No
2019-08-18 | 8:18 | WRA2 | Urban | Asset Failure | Distribution substation | 51 | 210.9608 | 0.014357 | 6.8054e-05 | No
2019-08-18 | 11:08 | WH1224 | Urban | Asset Failure | Distribution substation | 1 | 166 | 0.00022151 | 1.3344e-06 | No
2019-08-18 | 13:40 | 49917 | Urban | Asset Failure | Distribution substation | 1 | 261 | 0.00034828 | 1.3344e-06 | No
2019-08-18 | 14:50 | 35702 | Urban | Asset Failure | Distribution substation | 19 | 467.8421 | 0.011861 | 2.5354e-05 | No
2019-08-18 | 17:09 | MM1142 | Urban | Asset Failure | Distribution substation | 1 | 78 | 0.00010408 | 1.3344e-06 | No
2019-08-18 | 17:48 | 35765 | Urban | Asset Failure | Distribution substation | 69 | 120.3043 | 0.011077 | 9.2074e-05 | No
2019-08-18 | 23:20 | J513 | Urban | Third Party | Unauthorised access | 399 | 155 | 0.082526 | 0.00053243 | No
2019-08-19 | 2:32 | 27459 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 317 | 0.0010429 | 3.2899e-06 | No
2019-08-19 | 3:29 | PK1262 | Short rural | Asset Failure | Distribution substation | 1 | 446 | 0.0014673 | 3.2899e-06 | No
2019-08-19 | 5:54 | 25450 | Short rural | Unknown | Unknown | 17 | 183 | 0.010235 | 5.5928e-05 | No
2019-08-19 | 7:20 | PK1262 | Short rural | Unknown | Unknown | 10 | 99 | 0.003257 | 3.2899e-05 | No
2019-08-19 | 8:31 | SC1289 | Short rural | Network business | Switching or protection error | 809 | 5.8158 | 0.015479 | 0.0026615 | No
2019-08-19 | 9:09 | FT1204 | Short rural | Asset Failure | Distribution substation | 1 | 82 | 0.00026977 | 3.2899e-06 | No
2019-08-19 | 9:18 | YYA2 | Short rural | Asset Failure | Distribution substation | 1 | 326 | 0.0010725 | 3.2899e-06 | No
2019-08-19 | 12:38 | X217 | Short rural | Unknown | Unknown | 1 | 116 | 0.00038162 | 3.2899e-06 | No
2019-08-19 | 12:39 | BWC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 27 | 128 | 0.01137 | 8.8826e-05 | No
2019-08-19 | 14:39 | CA1284 | Urban | Asset Failure | Distribution substation | 1 | 36 | 4.8038e-05 | 1.3344e-06 | No
2019-08-19 | 19:01 | CA1254 | Urban | Third Party | Vehicle impact | 26 | 57.3462 | 0.0019896 | 3.4694e-05 | No
2019-08-19 | 20:03 | J516 | Urban | Asset Failure | Distribution substation | 1 | 85 | 0.00011342 | 1.3344e-06 | No
2019-08-20 | 7:47 | APD2 | Short rural | Other | Probable Overload | 145 | 41.9241 | 0.019999 | 0.00047703 | No
2019-08-20 | 12:29 | NN1281 | Short rural | Unknown | Unknown | 1 | 190 | 0.00062507 | 3.2899e-06 | No
2019-08-20 | 14:53 | CR1228 | Urban | Third Party | Other | 1 | 1132 | 0.0015105 | 1.3344e-06 | No
2019-08-20 | 14:57 | J474 | Short rural | Asset Failure | Distribution substation | 1 | 208 | 0.00068429 | 3.2899e-06 | No
2019-08-20 | 17:38 | T874 | Short rural | Unknown | Unknown | 3 | 144 | 0.0014212 | 9.8696e-06 | No
2019-08-20 | 20:22 | FT1206 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 310.5 | 0.004086 | 1.3159e-05 | No
2019-08-20 | 22:02 | BDC2 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 7 | 148 | 0.0034083 | 2.3029e-05 | No
2019-08-20 | 22:18 | FT1206 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 392 | 254.4847 | 0.32819 | 0.0012896 | No
2019-08-20 | 23:58 | FT1210 | Urban | Weather |  | 1419 | 6.1783 | 0.011699 | 0.0018935 | No
2019-08-21 | 0:45 | W127 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 811 | 66.0691 | 0.17628 | 0.0026681 | No
2019-08-21 | 1:53 | 35816 | Short rural | Asset Failure | HV | 22.0648 | 126.1837 | 0.0091597 | 7.259e-05 | No
2019-08-21 | 1:53 | MG1267 | Short rural | Asset Failure | HV | 26.9352 | 126.1837 | 0.011182 | 8.8613e-05 | No
2019-08-21 | 2:26 | BYC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 292.5714 | 0.0067376 | 2.3029e-05 | No
2019-08-21 | 6:57 | CD1230 | Short rural | Unknown | Unknown | 2 | 83 | 0.00054612 | 6.5797e-06 | No
2019-08-21 | 7:04 | 25744 | Short rural | Third Party | Vehicle impact | 1 | 60 | 0.00019739 | 3.2899e-06 | No
2019-08-21 | 7:08 | 25744 | Short rural | Third Party | Vehicle impact | 9 | 57 | 0.0016877 | 2.9609e-05 | No
2019-08-21 | 7:12 | X863 | Urban | Asset Failure | Distribution substation | 23 | 130 | 0.0039899 | 3.0691e-05 | No
2019-08-21 | 7:14 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 262 | 0.0051717 | 1.9739e-05 | No
2019-08-21 | 7:19 | L582 | Short rural | Unknown | Unknown | 1 | 245 | 0.00080602 | 3.2899e-06 | No
2019-08-21 | 8:36 | 16660 | Urban | Third Party | Dig-in | 1115 | 78.3435 | 0.11656 | 0.0014879 | No
2019-08-21 | 9:12 | WM1142 | Urban | Asset Failure | Distribution substation | 40 | 57.45 | 0.0030664 | 5.3376e-05 | No
2019-08-21 | 12:26 | CD1230 | Short rural | Asset Failure | Distribution substation | 5 | 376.4 | 0.0061915 | 1.6449e-05 | No
2019-08-21 | 16:41 | X482 | Short rural | Asset Failure | HV | 31 | 63.1935 | 0.0064448 | 0.00010199 | No
2019-08-21 | 17:05 | 35818 | Short rural | Asset Failure | Distribution substation | 28 | 52.5 | 0.0048361 | 9.2116e-05 | No
2019-08-21 | 17:19 | L582 | Short rural | Asset Failure | Distribution substation | 6 | 54.8333 | 0.0010824 | 1.9739e-05 | No
2019-08-21 | 18:18 | W118 | Short rural | Animal | Animal Impact | 38 | 77 | 0.0096261 | 0.00012501 | No
2019-08-21 | 18:23 | WM1142 | Urban | Asset Failure | Distribution substation | 1 | 922 | 0.0012303 | 1.3344e-06 | No
2019-08-21 | 23:59 | APF2 | Short rural | Asset Failure | HV | 576 | 53.3993 | 0.10119 | 0.001895 | No
2019-08-22 | 0:32 | HBA2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 16 | 200 | 0.010528 | 5.2638e-05 | No
2019-08-22 | 0:47 | JBB2 | Short rural | Asset Failure | LV | 320 | 95.0875 | 0.1001 | 0.0010528 | No
2019-08-22 | 6:54 | 10245 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 13 | 290.1538 | 0.012409 | 4.2768e-05 | No
2019-08-22 | 9:07 | OA1233 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 24 | 251 | 0.019818 | 7.8957e-05 | No
2019-08-22 | 9:50 | AZ1227 | Urban | Other | Isolation Request by EE | 22 | 30 | 0.0008807 | 2.9357e-05 | No
2019-08-22 | 11:32 | X217 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 216 | 0.016344 | 7.5667e-05 | No
2019-08-22 | 12:08 | NN1214 | Short rural | Third Party | Dig-in | 6 | 126.5 | 0.002497 | 1.9739e-05 | No
2019-08-22 | 13:17 | D852 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 71 | 466.9577 | 0.044241 | 9.4742e-05 | No
2019-08-22 | 14:00 | 8679 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1131 | 57.2325 | 0.086376 | 0.0015092 | No
2019-08-22 | 14:00 | CX1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 238 | 143.4496 | 0.11232 | 0.00078299 | No
2019-08-22 | 15:02 | 35818 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 295 | 0.001941 | 6.5797e-06 | No
2019-08-22 | 15:43 | 6430 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 758 | 55.4499 | 0.056086 | 0.0010115 | No
2019-08-22 | 15:44 | B776 | Urban | Network business | Network error | 1 | 115 | 0.00015346 | 1.3344e-06 | No
2019-08-22 | 15:55 | 41535 | Urban | Unknown | Unknown | 1752 | 135.7255 | 0.31731 | 0.0023379 | No
2019-08-22 | 17:15 | M399 | Short rural | Asset Failure | Distribution substation | 1 | 126 | 0.00041452 | 3.2899e-06 | No
2019-08-23 | 8:26 | R260 | Short rural | Vegetation | Grow-in - NSP responsibility | 60 | 313 | 0.061784 | 0.00019739 | No
2019-08-23 | 11:12 | CV1251 | Urban | Unknown | Unknown | 14 | 70 | 0.0013077 | 1.8682e-05 | No
2019-08-23 | 13:20 | S738 | Short rural | Asset Failure | Distribution substation | 2 | 422 | 0.0027766 | 6.5797e-06 | No
2019-08-23 | 13:59 | FT1210 | Urban | Animal | Animal Impact | 1419 | 57.5229 | 0.10892 | 0.0018935 | No
2019-08-23 | 16:15 | R211 | Short rural | Other | Isolation Request by EE | 108 | 13 | 0.004619 | 0.00035531 | No
2019-08-23 | 17:08 | OA1233 | Short rural | Third Party | Vehicle impact | 688 | 47.8227 | 0.10824 | 0.0022634 | No
2019-08-24 | 2:47 | ER1252 | Short rural | Asset Failure | Distribution substation | 22 | 381.0909 | 0.027582 | 7.2377e-05 | No
2019-08-24 | 5:37 | C896 | Urban | Third Party | Unauthorised access | 38 | 286.9737 | 0.014552 | 5.0707e-05 | No
2019-08-24 | 8:59 | C852 | Urban | Asset Failure | Distribution substation | 86 | 271.8605 | 0.031198 | 0.00011476 | No
2019-08-24 | 10:26 | APC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 229.5 | 0.00151 | 6.5797e-06 | No
2019-08-24 | 14:55 | 87220 | Short rural | Asset Failure | Distribution substation | 3 | 26 | 0.00025661 | 9.8696e-06 | No
2019-08-25 | 8:42 | 55867 | Urban | Asset Failure | Distribution substation | 1 | 261 | 0.00034828 | 1.3344e-06 | No
2019-08-25 | 9:17 | 10242 | Short rural | Asset Failure | HV | 541 | 209.9002 | 0.37358 | 0.0017798 | No
2019-08-25 | 10:28 | CLA2 | Short rural | Asset Failure | HV | 10 | 35 | 0.0011515 | 3.2899e-05 | No
2019-08-25 | 10:34 | AZ1227 | Urban | Asset Failure | Distribution substation | 22 | 272 | 0.007985 | 2.9357e-05 | No
2019-08-25 | 12:42 | HKF2 | Short rural | Asset Failure | Distribution substation | 114 | 85 | 0.031879 | 0.00037504 | No
2019-08-25 | 14:35 | KVA2 | Short rural | Unknown | Unknown | 2 | 283 | 0.0018621 | 6.5797e-06 | No
2019-08-26 | 5:33 | BYC2 | Short rural | Asset Failure | HV | 81 | 196.1605 | 0.052273 | 0.00026648 | No
2019-08-26 | 7:24 | RBE2 | Short rural | Asset Failure | LV | 25 | 180.64 | 0.014857 | 8.2247e-05 | No
2019-08-26 | 8:07 | L590 | Short rural | Asset Failure | Distribution substation | 1 | 266 | 0.0008751 | 3.2899e-06 | No
2019-08-26 | 9:08 | JBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 16 | 70.25 | 0.0036978 | 5.2638e-05 | No
2019-08-26 | 9:56 | 27187 | Urban | Asset Failure | Distribution substation | 16 | 453.5 | 0.0096824 | 2.135e-05 | No
2019-08-26 | 10:17 | NM1239 | Urban | Third Party | Other | 6 | 186 | 0.0014892 | 8.0064e-06 | No
2019-08-26 | 11:04 | APB2 | Short rural | Asset Failure | Distribution substation | 1 | 175 | 0.00057573 | 3.2899e-06 | No
2019-08-26 | 14:04 | GG1295 | Short rural | Asset Failure | Distribution substation | 1 | 185 | 0.00060862 | 3.2899e-06 | No
2019-08-26 | 14:11 | M399 | Short rural | Asset Failure | Distribution substation | 1 | 106 | 0.00034873 | 3.2899e-06 | No
2019-08-26 | 15:15 | L584 | Short rural | Asset Failure | Distribution substation | 2 | 188 | 0.001237 | 6.5797e-06 | No
2019-08-26 | 19:54 | J489 | Urban | Unknown | Unknown | 1601 | 101.3354 | 0.21649 | 0.0021364 | No
2019-08-26 | 20:22 | HR1269 | Urban | Asset Failure | Distribution substation | 54 | 64 | 0.0046117 | 7.2058e-05 | No
2019-08-26 | 20:41 | 35818 | Short rural | Asset Failure | Distribution substation | 34 | 31.6176 | 0.0035366 | 0.00011186 | No
2019-08-27 | 0:14 | HR1250 | Urban | Unknown | Unknown | 272 | 72 | 0.026133 | 0.00036296 | No
2019-08-27 | 1:24 | 55890 | Urban | Asset Failure | Distribution substation | 1 | 539 | 0.00071924 | 1.3344e-06 | No
2019-08-27 | 4:02 | 19871 | Urban | Unknown | Unknown | 15 | 231 | 0.0046237 | 2.0016e-05 | No
2019-08-27 | 7:52 | CA1210 | Urban | Third Party | Other | 11 | 84.8182 | 0.001245 | 1.4678e-05 | No
2019-08-27 | 8:18 | B214 | Urban | Asset Failure | Distribution substation | 1 | 226 | 0.00030157 | 1.3344e-06 | No
2019-08-27 | 8:41 | 19871 | Urban | Asset Failure | Distribution substation | 9 | 332.2222 | 0.0039899 | 1.201e-05 | No
2019-08-27 | 13:10 | X877 | Short rural | Unknown | Unknown | 5 | 119 | 0.0019575 | 1.6449e-05 | No
2019-08-27 | 13:43 | RW1292 | Short rural | Vegetation | Grow-in - NSP responsibility | 22 | 69.7273 | 0.0050467 | 7.2377e-05 | No
2019-08-27 | 17:18 | JBA2 | Short rural | Asset Failure | Distribution substation | 4 | 40.5 | 0.00053296 | 1.3159e-05 | No
2019-08-27 | 17:46 | MR2225 | Urban | Unknown | Unknown | 19 | 191.7368 | 0.0048612 | 2.5354e-05 | No
2019-08-27 | 19:15 | BYF2 | Urban | Asset Failure | Distribution substation | 19 | 112 | 0.0028396 | 2.5354e-05 | No
2019-08-28 | 4:08 | 9019 | Urban | Unknown | Unknown | 12 | 151 | 0.0024179 | 1.6013e-05 | No
2019-08-28 | 10:24 | J468 | Urban | Asset Failure | Distribution substation | 3 | 162 | 0.00064852 | 4.0032e-06 | No
2019-08-28 | 11:09 | SN1230 | Short rural | Third Party | Unauthorised access | 16 | 55 | 0.0028951 | 5.2638e-05 | No
2019-08-28 | 11:53 | SN1230 | Short rural | Third Party | Unauthorised access | 8 | 31 | 0.00081589 | 2.6319e-05 | No
2019-08-28 | 17:26 | WM1112 | Urban | Asset Failure | Distribution substation | 1 | 119 | 0.00015879 | 1.3344e-06 | No
2019-08-28 | 17:33 | 76225 | Short rural | Asset Failure | LV | 12 | 84 | 0.0033162 | 3.9478e-05 | No
2019-08-28 | 22:58 | WBD2 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 2 | 155 | 0.0010199 | 6.5797e-06 | No
2019-08-29 | 0:45 | JBB2 | Short rural | Weather |  | 88 | 140.3523 | 0.040633 | 0.00028951 | No
2019-08-29 | 8:52 | ULK2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 39 | 0.0001283 | 3.2899e-06 | No
2019-08-29 | 12:22 | SZ1222 | Urban | Asset Failure | Distribution substation | 1 | 345 | 0.00046037 | 1.3344e-06 | No
2019-08-29 | 13:56 | 9025 | Urban | Asset Failure | Distribution substation | 1 | 63 | 8.4067e-05 | 1.3344e-06 | No
2019-08-29 | 14:16 | NN1240 | Urban | Asset Failure | Distribution substation | 18 | 93.8889 | 0.0022551 | 2.4019e-05 | No
2019-08-29 | 14:49 | GG1269 | Short rural | Weather |  | 61 | 205.5738 | 0.041255 | 0.00020068 | No
2019-08-29 | 15:29 | MM1252 | Urban | Asset Failure | Distribution substation | 105 | 263.019 | 0.036852 | 0.00014011 | No
2019-08-29 | 16:39 | MYQ2 | Short rural | Asset Failure | Distribution substation | 42 | 408 | 0.056375 | 0.00013817 | No
2019-08-29 | 17:30 | 8675 | Urban | Asset Failure | Distribution substation | 32 | 105.75 | 0.0045156 | 4.2701e-05 | No
2019-08-29 | 17:36 | HS1152 | Short rural | Vegetation | Grow-in - NSP responsibility | 346 | 53.0983 | 0.060441 | 0.0011383 | No
2019-08-29 | 17:55 | 55890 | Urban | Asset Failure | Distribution substation | 1 | 290 | 0.00038698 | 1.3344e-06 | No
2019-08-29 | 18:15 | A098 | Short rural | Asset Failure | Distribution substation | 19 | 22.7895 | 0.0014245 | 6.2507e-05 | No
2019-08-29 | 22:01 | GL1255 | Short rural | Vegetation | Grow-in - NSP responsibility | 487 | 57.6489 | 0.092363 | 0.0016022 | No
2019-08-30 | 1:56 | 41537 | Urban | Vegetation | Grow-in - NSP responsibility | 1412 | 60.1282 | 0.11329 | 0.0018842 | No
2019-08-30 | 1:58 | J492 | Urban | Unknown | Unknown | 110 | 353 | 0.051815 | 0.00014678 | No
2019-08-30 | 2:39 | C855 | Short rural | Vegetation | Grow-in - NSP responsibility | 62 | 103 | 0.021009 | 0.00020397 | No
2019-08-30 | 4:30 | CX1232 | Short rural | Asset Failure | HV | 271 | 220.7343 | 0.1968 | 0.00089155 | No
2019-08-30 | 6:43 | L946 | Short rural | Third Party | Other | 1 | 513 | 0.0016877 | 3.2899e-06 | No
2019-08-30 | 7:34 | 8741 | Urban | Unknown | Unknown | 570 | 78 | 0.059327 | 0.00076061 | No
2019-08-30 | 7:47 | RW1292 | Short rural | Unknown | Unknown | 3 | 133 | 0.0013127 | 9.8696e-06 | No
2019-08-30 | 9:26 | 9017 | Urban | Asset Failure | HV | 406 | 232.532 | 0.12598 | 0.00054177 | No
2019-08-30 | 9:40 | 49918 | Urban | Asset Failure | Distribution substation | 1 | 470 | 0.00062717 | 1.3344e-06 | No
2019-08-30 | 14:09 | 35981 | Short rural | Asset Failure | Distribution substation | 1 | 213 | 0.00070074 | 3.2899e-06 | No
2019-08-30 | 15:09 | MM1382 | Urban | Asset Failure | Distribution substation | 1 | 141 | 0.00018815 | 1.3344e-06 | No
2019-08-30 | 15:35 | J459 | Short rural | Asset Failure | Distribution substation | 5 | 147 | 0.002418 | 1.6449e-05 | No
2019-08-30 | 15:35 | J459 | Short rural | Asset Failure | Distribution substation | 18 | 140.5556 | 0.0083234 | 5.9218e-05 | No
2019-08-30 | 16:50 | T838 | Short rural | Other | Probable Willful damage - damage/destruction of EE equipment | 1 | 75 | 0.00024674 | 3.2899e-06 | No
2019-08-30 | 17:14 | 9017 | Urban | Unknown | Unknown | 53 | 84 | 0.0059407 | 7.0723e-05 | No
2019-08-30 | 18:50 | 19868 | Urban | Asset Failure | Distribution substation | 43 | 155 | 0.0088938 | 5.7379e-05 | No
2019-08-30 | 19:26 | A096 | Short rural | Third Party | Other | 2 | 167 | 0.0010988 | 6.5797e-06 | No
2019-08-30 | 19:45 | S765 | Urban | Unknown | Unknown | 10 | 79 | 0.0010542 | 1.3344e-05 | No
2019-08-30 | 20:27 | L588 | Short rural | Asset Failure | LV | 46 | 60 | 0.00908 | 0.00015133 | No
2019-08-31 | 7:00 | SWJ2 | Urban | Unknown | Unknown | 1 | 64 | 8.5402e-05 | 1.3344e-06 | No
2019-08-31 | 7:26 | DP1221 | Short rural | Unknown | Unknown | 3 | 5 | 4.9348e-05 | 9.8696e-06 | No
2019-08-31 | 14:50 | 8722 | Short rural | Third Party | Vehicle impact | 724 | 44.4779 | 0.10594 | 0.0023819 | No
2019-08-31 | 15:54 | T870 | Urban | Asset Failure | Distribution substation | 74 | 168 | 0.016589 | 9.8746e-05 | No
2019-08-31 | 16:39 | 8798 | Short rural | Asset Failure | Distribution substation | 1 | 99 | 0.0003257 | 3.2899e-06 | No
2019-09-01 | 4:16 | C900 | Urban | Unknown | Unknown | 61 | 139 | 0.011314 | 8.1398e-05 | No
2019-09-01 | 13:02 | WX1228 | Short rural | Asset Failure | Distribution substation | 3 | 382.3333 | 0.0037735 | 9.8696e-06 | No
2019-09-01 | 13:52 | S737 | Short rural | Asset Failure | Distribution substation | 1 | 191 | 0.00062836 | 3.2899e-06 | No
2019-09-01 | 13:56 | 76225 | Short rural | Asset Failure | HV | 10 | 313.4 | 0.01031 | 3.2899e-05 | No
2019-09-01 | 17:54 | 8675 | Urban | Unknown | Unknown | 35 | 48 | 0.0022418 | 4.6704e-05 | No
2019-09-02 | 5:35 | CA1269 | Urban | Third Party | Dig-in | 8 | 538.125 | 0.0057446 | 1.0675e-05 | No
2019-09-02 | 7:33 | RW1281 | Short rural | Unknown | Unknown | 2 | 447 | 0.0029411 | 6.5797e-06 | No
2019-09-02 | 13:14 | X217 | Short rural | Asset Failure | Distribution substation | 2 | 5718 | 0.037623 | 6.5797e-06 | No
2019-09-02 | 14:27 | GV1204 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 38 | 174.8684 | 0.0088671 | 5.0707e-05 | No
2019-09-02 | 14:34 | RBB2 | Short rural | Unknown | Unknown | 12 | 456.8333 | 0.018035 | 3.9478e-05 | No
2019-09-02 | 17:25 | ULB2 | Short rural | Asset Failure | Distribution substation | 25 | 976 | 0.080273 | 8.2247e-05 | No
2019-09-02 | 19:12 | 8675 | Urban | Asset Failure | Distribution substation | 1 | 174 | 0.00023219 | 1.3344e-06 | No
2019-09-03 | 5:03 | 35773 | Urban | Animal | Animal Impact | 378 | 83.0212 | 0.041876 | 0.0005044 | No
2019-09-03 | 7:34 | C852 | Urban | Asset Failure | Distribution substation | 1 | 271 | 0.00036162 | 1.3344e-06 | No
2019-09-03 | 7:39 | CX1210 | Short rural | Other | Isolation Request by EE | 5 | 14 | 0.00023029 | 1.6449e-05 | No
2019-09-03 | 7:40 | CX1232 | Short rural | Other | Isolation Request by EE | 14 | 20 | 0.00092116 | 4.6058e-05 | No
2019-09-03 | 9:48 | DP1206 | Urban | Unknown | Unknown | 80 | 40.5125 | 0.0043248 | 0.00010675 | No
2019-09-03 | 10:28 | P608 | Short rural | Unknown | Unknown | 23 | 95.6957 | 0.007241 | 7.5667e-05 | No
2019-09-03 | 10:44 | CR1262 | Urban | Asset Failure | Distribution substation | 136 | 489.9632 | 0.088918 | 0.00018148 | No
2019-09-03 | 12:01 | KVD2 | Short rural | Unknown | Unknown | 4 | 191.75 | 0.0025233 | 1.3159e-05 | No
2019-09-03 | 18:00 | T893 | Urban | Unknown | Unknown | 12 | 99 | 0.0015853 | 1.6013e-05 | No
2019-09-04 | 7:25 | 35818 | Short rural | Asset Failure | Distribution substation | 1 | 79 | 0.0002599 | 3.2899e-06 | No
2019-09-04 | 7:27 | 35990 | Short rural | Asset Failure | Distribution substation | 16 | 63 | 0.0033162 | 5.2638e-05 | No
2019-09-04 | 10:33 | L540 | Urban | Asset Failure | Distribution substation | 1 | 234 | 0.00031225 | 1.3344e-06 | No
2019-09-04 | 11:17 | FF1202 | Urban | Third Party | Other | 96 | 152.0312 | 0.019476 | 0.0001281 | No
2019-09-04 | 12:00 | TM1284 | Short rural | Third Party | Unauthorised access | 1 | 111 | 0.00036517 | 3.2899e-06 | No
2019-09-04 | 14:21 | CA1210 | Urban | Third Party | Vehicle impact | 45 | 85.0222 | 0.0051054 | 6.0048e-05 | No
2019-09-04 | 14:58 | KVB2 | Short rural | Asset Failure | Distribution substation | 1 | 120 | 0.00039478 | 3.2899e-06 | No
2019-09-04 | 15:12 | 49917 | Urban | Asset Failure | LV | 27 | 395.3704 | 0.014245 | 3.6029e-05 | No
2019-09-04 | 15:42 | WWB2 | Short rural | Unknown | Unknown | 38 | 28 | 0.0035004 | 0.00012501 | No
2019-09-04 | 17:44 | X213 | Short rural | Asset Failure | Distribution substation | 4 | 149.5 | 0.0019673 | 1.3159e-05 | No
2019-09-04 | 18:14 | YYB2 | Short rural | Asset Failure | Distribution substation | 1 | 144 | 0.00047374 | 3.2899e-06 | No
2019-09-04 | 19:22 | 10244 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 233 | 90.0472 | 0.069025 | 0.00076654 | No
2019-09-04 | 23:23 | 68188 | Urban | Third Party | Other | 786 | 27.6158 | 0.028964 | 0.0010488 | No
2019-09-05 | 1:37 | CLA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 35 | 60 | 0.0069087 | 0.00011515 | No
2019-09-05 | 2:24 | CV1221 | Urban | Unknown | Unknown | 9 | 239 | 0.0028703 | 1.201e-05 | No
2019-09-05 | 9:26 | FF1202 | Urban | Asset Failure | Distribution substation | 9 | 65 | 0.00078062 | 1.201e-05 | No
2019-09-05 | 12:34 | 2813 | Urban | Asset Failure | HV | 783 | 38.6641 | 0.040398 | 0.0010448 | No
2019-09-05 | 14:11 | L940 | Short rural | Unknown | Unknown | 11 | 154 | 0.005573 | 3.6188e-05 | No
2019-09-05 | 14:15 | HR1206 | Urban | Unknown | Unknown | 12 | 80 | 0.001281 | 1.6013e-05 | No
2019-09-05 | 16:30 | RV1280 | Urban | Third Party | Vehicle impact | 235 | 209.3234 | 0.06564 | 0.00031358 | No
2019-09-05 | 16:43 | LP1132 | Urban | Third Party | Vehicle impact | 136 | 497 | 0.090195 | 0.00018148 | No
2019-09-06 | 11:43 | T831 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 15 | 488.2 | 0.024092 | 4.9348e-05 | Yes
2019-09-06 | 11:43 | T831 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 141 | 290.227 | 0.13463 | 0.00046387 | Yes
2019-09-06 | 14:22 | BK1236 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 461 | 183.8416 | 0.27882 | 0.0015166 | Yes
2019-09-06 | 14:36 | A096 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 87 | 90.7931 | 0.025987 | 0.00028622 | Yes
2019-09-06 | 14:47 | A096 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 379 | 181.5831 | 0.22641 | 0.0012469 | Yes
2019-09-06 | 14:59 | BX1232 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1285 | 102.614 | 0.17595 | 0.0017147 | Yes
2019-09-06 | 15:10 | L579 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 16 | 66 | 0.0014091 | 2.135e-05 | Yes
2019-09-06 | 15:17 | C891 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 906 | 92.4415 | 0.11176 | 0.001209 | Yes
2019-09-06 | 15:18 | R260 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 298 | 1343.3826 | 1.317 | 0.00098038 | Yes
2019-09-06 | 15:18 | R260 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 82 | 1155.9756 | 0.31185 | 0.00026977 | Yes
2019-09-06 | 15:21 | NN1281 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 184 | 114.6141 | 0.06938 | 0.00060533 | Yes
2019-09-06 | 15:22 | OA1244 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 373 | 399.0536 | 0.48969 | 0.0012271 | Yes
2019-09-06 | 15:30 | A055 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1069 | 162.3573 | 0.57099 | 0.0035169 | Yes
2019-09-06 | 15:32 | MR2272 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 1004 | 165.25 | 0.54582 | 0.003303 | Yes
2019-09-06 | 15:38 | CD1271 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 765 | 440.7307 | 1.1092 | 0.0025167 | Yes
2019-09-06 | 15:45 | H745 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 483 | 0.006356 | 1.3159e-05 | Yes
2019-09-06 | 15:50 | J513 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 399 | 167.2155 | 0.08903 | 0.00053243 | Yes
2019-09-06 | 15:56 | 9052 | Urban | Weather |  | 65 | 2477 | 0.21484 | 8.6736e-05 | Yes
2019-09-06 | 15:58 | NL1322 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 206 | 224 | 0.061575 | 0.00027489 | Yes
2019-09-06 | 15:59 | CD1234 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 71 | 507.7887 | 0.11861 | 0.00023358 | Yes
2019-09-06 | 16:00 | R260 | Short rural | Weather |  | 67 | 450.6716 | 0.099337 | 0.00022042 | Yes
2019-09-06 | 16:02 | LP1422 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 685 | 1006.2321 | 0.91976 | 0.00091406 | Yes
2019-09-06 | 16:02 | SL1132 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 1042 | 340.9165 | 1.1687 | 0.003428 | Yes
2019-09-06 | 16:02 | NG1299 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 311.4092 | 366.7353 | 0.37572 | 0.0010245 | Yes
2019-09-06 | 16:02 | NG1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 387.5908 | 366.7353 | 0.46763 | 0.0012751 | Yes
2019-09-06 | 16:07 | C855 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 766 | 117.4739 | 0.29604 | 0.00252 | Yes
2019-09-06 | 16:12 | J482 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 604 | 208.9123 | 0.16838 | 0.00080598 | Yes
2019-09-06 | 16:12 | CD1234 | Short rural | Asset Failure | HV | 458 | 479.7489 | 0.72287 | 0.0015068 | Yes
2019-09-06 | 16:13 | OP1122 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 694 | 124.755 | 0.28484 | 0.0022832 | Yes
2019-09-06 | 16:14 | NL1182 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 360 | 277.55 | 0.13333 | 0.00048038 | Yes
2019-09-06 | 16:16 | SL1142 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 944 | 243.9333 | 0.75757 | 0.0031056 | Yes
2019-09-06 | 16:16 | NN1240 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 80 | 970 | 0.10355 | 0.00010675 | Yes
2019-09-06 | 16:16 | 19857 | Urban | Weather |  | 19 | 1571.3684 | 0.03984 | 2.5354e-05 | Yes
2019-09-06 | 16:17 | 6430 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 1366.8333 | 0.076604 | 5.6045e-05 | Yes
2019-09-06 | 16:21 | 27454 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 426 | 2120.5164 | 2.9719 | 0.0014015 | Yes
2019-09-06 | 16:21 | KC1262 | Short rural | Unknown | Unknown | 2 | 481 | 0.0031648 | 6.5797e-06 | Yes
2019-09-06 | 16:21 | KC1262 | Short rural | Unknown | Unknown | 115 | 408.5478 | 0.15457 | 0.00037833 | Yes
2019-09-06 | 16:21 | 8798 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 594 | 203.6145 | 0.3979 | 0.0019542 | Yes
2019-09-06 | 16:21 | 8798 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1367 | 636.4887 | 2.8624 | 0.0044972 | Yes
2019-09-06 | 16:22 | BX1342 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 1013 | 183.5597 | 0.24813 | 0.0013517 | Yes
2019-09-06 | 16:23 | ER1262 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 663 | 1493.8673 | 3.2584 | 0.0021812 | Yes
2019-09-06 | 16:25 | ER1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 532 | 1435.8985 | 2.5131 | 0.0017502 | Yes
2019-09-06 | 16:27 | 19857 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 1075 | 176.3805 | 0.25301 | 0.0014345 | Yes
2019-09-06 | 16:27 | A046 | Short rural | Weather |  | 1040 | 532.7808 | 1.8229 | 0.0034215 | Yes
2019-09-06 | 16:28 | SZ1122 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 159 | 2129 | 1.1137 | 0.00052309 | Yes
2019-09-06 | 16:28 | SZ1122 | Short rural | Weather |  | 448 | 285.7656 | 0.42118 | 0.0014739 | Yes
2019-09-06 | 16:28 | SZ1242 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 645 | 1029.7984 | 2.1852 | 0.002122 | Yes
2019-09-06 | 16:29 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1056 | 1202.6581 | 4.1781 | 0.0034741 | Yes
2019-09-06 | 16:30 | 9025 | Urban | Unknown | Unknown | 2219 | 154.0036 | 0.45601 | 0.002961 | Yes
2019-09-06 | 16:30 | KC1288 | Short rural | Weather |  | 554 | 259.8917 | 0.47367 | 0.0018226 | Yes
2019-09-06 | 16:32 | CD1260 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2489 | 279.6022 | 0.92865 | 0.0033213 | Yes
2019-09-06 | 16:33 | L941 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 110 | 1397.2091 | 0.50563 | 0.00036188 | Yes
2019-09-06 | 16:33 | MM1222 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 956 | 266.5659 | 0.34005 | 0.0012757 | Yes
2019-09-06 | 16:33 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 453 | 1666.7506 | 2.484 | 0.0014903 | Yes
2019-09-06 | 16:34 | JS1252 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 541 | 358.6266 | 0.63829 | 0.0017798 | Yes
2019-09-06 | 16:36 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 788 | 1621.3312 | 4.2032 | 0.0025924 | Yes
2019-09-06 | 16:36 | 8799 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 623 | 1314.0546 | 2.6933 | 0.0020496 | Yes
2019-09-06 | 16:38 | SZ1322 | Short rural | Weather |  | 77 | 2625.8182 | 0.66517 | 0.00025332 | Yes
2019-09-06 | 16:46 | L947 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 180 | 1322.0222 | 0.78287 | 0.00059218 | Yes
2019-09-06 | 16:46 | L947 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 307 | 1255.4658 | 1.268 | 0.00101 | Yes
2019-09-06 | 16:46 | 10290 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 357 | 1114.958 | 1.3095 | 0.0011745 | Yes
2019-09-06 | 16:47 | CX1273 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 140.2331 | 1328.8825 | 0.61308 | 0.00046135 | Yes
2019-09-06 | 16:47 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 276.7669 | 1328.8825 | 1.21 | 0.00091053 | Yes
2019-09-06 | 16:47 | 10287 | Urban | Weather |  | 959 | 386.4995 | 0.4946 | 0.0012797 | Yes
2019-09-06 | 16:47 | 35701 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 49 | 25.5714 | 0.0041222 | 0.0001612 | Yes
2019-09-06 | 16:48 | 35988 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 414 | 195.6691 | 0.2665 | 0.001362 | Yes
2019-09-06 | 16:49 | 8679 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 2761.8824 | 0.062653 | 2.2685e-05 | Yes
2019-09-06 | 16:52 | 9052 | Urban | Weather |  | 1263 | 238.5827 | 0.40209 | 0.0016853 | Yes
2019-09-06 | 16:55 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 2835.5476 | 0.3918 | 0.00013817 | Yes
2019-09-06 | 16:59 | CX1210 | Short rural | Weather |  | 815 | 382.1644 | 1.0247 | 0.0026812 | Yes
2019-09-06 | 16:59 | CX1210 | Short rural | Weather |  | 42 | 2757.6667 | 0.38104 | 0.00013817 | Yes
2019-09-06 | 17:00 | GL1207 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 369 | 1234.29 | 1.4984 | 0.001214 | Yes
2019-09-06 | 17:01 | 41533 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 726 | 404.2287 | 0.96548 | 0.0023884 | Yes
2019-09-06 | 17:02 | S735 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 541 | 904.3346 | 1.6095 | 0.0017798 | Yes
2019-09-06 | 17:03 | CX1206 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 741 | 1158.6289 | 2.8245 | 0.0024378 | Yes
2019-09-06 | 17:03 | CX1284 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 205 | 1534.2439 | 1.0347 | 0.00067442 | Yes
2019-09-06 | 17:03 | L940 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 359 | 1289.1421 | 1.5226 | 0.0011811 | Yes
2019-09-06 | 17:05 | ER1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 1273.8333 | 0.050289 | 3.9478e-05 | Yes
2019-09-06 | 17:06 | 41535 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 1060 | 0.0084868 | 8.0064e-06 | Yes
2019-09-06 | 17:06 | KC1221 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 14 | 173 | 0.007968 | 4.6058e-05 | Yes
2019-09-06 | 17:08 | L946 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 269 | 1368.8327 | 1.2114 | 0.00088497 | Yes
2019-09-06 | 17:08 | L946 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 176 | 1113.5057 | 0.64474 | 0.00057902 | Yes
2019-09-06 | 17:08 | 55875 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 126 | 266.4603 | 0.044801 | 0.00016813 | Yes
2019-09-06 | 17:11 | T889 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 14 | 954 | 0.017822 | 1.8682e-05 | Yes
2019-09-06 | 17:11 | YYA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 164 | 137.811 | 0.074354 | 0.00053954 | Yes
2019-09-06 | 17:11 | 19857 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 40 | 571.425 | 0.0305 | 5.3376e-05 | Yes
2019-09-06 | 17:13 | L942 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 802 | 856.7307 | 2.2605 | 0.0026385 | Yes
2019-09-06 | 17:14 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 127 | 2567.1496 | 1.0726 | 0.00041781 | Yes
2019-09-06 | 17:14 | S741 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 698 | 897.2436 | 2.0604 | 0.0022963 | Yes
2019-09-06 | 17:14 | CN1213 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 86 | 1198.9419 | 0.13759 | 0.00011476 | Yes
2019-09-06 | 17:16 | MR2232 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 388 | 613.4742 | 0.78308 | 0.0012765 | Yes
2019-09-06 | 17:17 | SZ1332 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 601 | 1055.9035 | 2.0877 | 0.0019772 | Yes
2019-09-06 | 17:20 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 482 | 1775.3942 | 2.8153 | 0.0015857 | Yes
2019-09-06 | 17:21 | M388 | Urban | Asset Failure | Distribution substation | 20 | 22.55 | 0.00060181 | 2.6688e-05 | Yes
2019-09-06 | 17:23 | S738 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 493 | 541.2596 | 0.87787 | 0.0016219 | Yes
2019-09-06 | 17:27 | S743 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 282 | 457.8369 | 0.42475 | 0.00092774 | Yes
2019-09-06 | 17:27 | 55880 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 261 | 341.3333 | 0.11888 | 0.00034828 | Yes
2019-09-06 | 17:28 | GL1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 487 | 631.5955 | 1.0119 | 0.0016022 | Yes
2019-09-06 | 17:29 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 259 | 808.3938 | 0.68881 | 0.00085207 | Yes
2019-09-06 | 17:31 | DS1204 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 30 | 984 | 0.039391 | 4.0032e-05 | Yes
2019-09-06 | 17:34 | 35980 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 399 | 296.4486 | 0.38913 | 0.0013127 | Yes
2019-09-06 | 17:48 | W112 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 308 | 480.3831 | 0.48676 | 0.0010133 | Yes
2019-09-06 | 17:48 | APC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 471.3846 | 0.080641 | 0.00017107 | Yes
2019-09-06 | 17:55 | 35305 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 58 | 1121.4655 | 0.086796 | 7.7395e-05 | Yes
2019-09-06 | 17:58 | APF2 | Short rural | Asset Failure | HV | 578 | 41.1159 | 0.078184 | 0.0019015 | Yes
2019-09-06 | 17:59 | S786 | Short rural | Vegetation | Grow-in - NSP responsibility | 1297 | 378.3292 | 1.6143 | 0.004267 | Yes
2019-09-06 | 18:05 | DP1210 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 1885 | 0.36658 | 0.0022733 | 0.0062014 | Yes
2019-09-06 | 18:05 | TM1217 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1422 | 71.3664 | 0.33387 | 0.0046782 | Yes
2019-09-06 | 18:05 | JBB2 | Short rural | Weather |  | 322 | 289.028 | 0.30618 | 0.0010593 | Yes
2019-09-06 | 18:08 | 6426 | Urban | Asset Failure | HV | 20 | 751.8 | 0.020064 | 2.6688e-05 | Yes
2019-09-06 | 18:11 | C891 | Urban | Asset Failure | Distribution substation | 19 | 1216 | 0.03083 | 2.5354e-05 | Yes
2019-09-06 | 18:14 | W185 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 462 | 312.5 | 0.47497 | 0.0015199 | Yes
2019-09-06 | 18:20 | 87222 | Long rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 22 | 303.1818 | 21.242 | 0.070064 | Yes
2019-09-06 | 18:28 | 7974 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 11 | 269 | 0.0039485 | 1.4678e-05 | Yes
2019-09-06 | 18:33 | KMF2 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 66 | 116.5909 | 0.010268 | 8.807e-05 | Yes
2019-09-06 | 18:37 | SZ1132 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 230 | 1089.0478 | 0.33424 | 0.00030691 | Yes
2019-09-06 | 18:40 | S744 | Urban | Weather |  | 1 | 1357 | 0.0018108 | 1.3344e-06 | Yes
2019-09-06 | 18:41 | A348 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 810 | 450.3074 | 0.48672 | 0.0010809 | Yes
2019-09-06 | 18:41 | 35307 | Urban | Weather |  | 17 | 188 | 0.0042647 | 2.2685e-05 | Yes
2019-09-06 | 18:45 | 9029 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 12 | 1365 | 0.021857 | 1.6013e-05 | Yes
2019-09-06 | 18:45 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 37 | 770.7838 | 0.093824 | 0.00012172 | Yes
2019-09-06 | 18:48 | 8686 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 2339 | 0.084645 | 3.6188e-05 | Yes
2019-09-06 | 18:49 | RW1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 252 | 110.75 | 0.091817 | 0.00082905 | Yes
2019-09-06 | 18:53 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 28 | 2419 | 0.22283 | 9.2116e-05 | Yes
2019-09-06 | 18:59 | MM1212 | Urban | Unknown | Unknown | 5 | 750 | 0.005004 | 6.672e-06 | Yes
2019-09-06 | 19:06 | X877 | Short rural | Unknown | Unknown | 2 | 2588 | 0.017028 | 6.5797e-06 | Yes
2019-09-06 | 19:08 | X877 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 1129 | 0.0037143 | 3.2899e-06 | Yes
2019-09-06 | 19:28 | NK1352 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 1085 | 0.0043435 | 4.0032e-06 | Yes
2019-09-06 | 19:44 | JBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 39 | 205.9487 | 0.026424 | 0.0001283 | Yes
2019-09-06 | 19:45 | GL1207 | Short rural | Weather |  | 7 | 1061.5714 | 0.024447 | 2.3029e-05 | Yes
2019-09-06 | 19:50 | ULE2 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 27 | 804.7037 | 0.071479 | 8.8826e-05 | Yes
2019-09-06 | 19:58 | GG1232 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 1 | 339 | 0.0011153 | 3.2899e-06 | Yes
2019-09-06 | 20:09 | NL1172 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 18 | 687 | 0.016501 | 2.4019e-05 | Yes
2019-09-06 | 20:09 | S765 | Urban | Asset Failure | Distribution substation | 1 | 1269 | 0.0016934 | 1.3344e-06 | Yes
2019-09-06 | 20:30 | ULK2 | Short rural | Third Party | Vehicle impact | 914 | 18.0799 | 0.054365 | 0.0030069 | Yes
2019-09-06 | 21:02 | 19857 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 26 | 2088 | 0.072442 | 3.4694e-05 | Yes
2019-09-06 | 21:15 | PK1236 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 3 | 122 | 0.0012041 | 9.8696e-06 | Yes
2019-09-06 | 21:16 | RBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 141 | 600.4043 | 0.27851 | 0.00046387 | Yes
2019-09-06 | 21:23 | CV1251 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 28 | 103.25 | 0.0038577 | 3.7363e-05 | Yes
2019-09-06 | 21:39 | NG1247 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 847.7778 | 0.010181 | 1.201e-05 | Yes
2019-09-06 | 22:25 | 9052 | Urban | Asset Failure | Distribution substation | 28 | 670 | 0.025033 | 3.7363e-05 | Yes
2019-09-06 | 22:36 | 8686 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 11 | 734 | 0.026562 | 3.6188e-05 | Yes
2019-09-06 | 22:50 | 48185 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 2 | 1095 | 0.0072048 | 6.5797e-06 | Yes
2019-09-06 | 22:58 | T874 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 462 | 160.0996 | 0.24334 | 0.0015199 | Yes
2019-09-06 | 23:14 | BDG2 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 2 | 576 | 0.0037899 | 6.5797e-06 | Yes
2019-09-06 | 23:40 | BYC2 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 78 | 667.5385 | 0.1713 | 0.00025661 | Yes
2019-09-06 | 23:48 | CX1210 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 238 | 754.1134 | 0.59046 | 0.00078299 | Yes
2019-09-07 | 1:11 | 35824 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 780 | 72.7167 | 0.1866 | 0.0025661 | Yes
2019-09-07 | 1:28 | D814 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 169 | 1453.9822 | 0.8084 | 0.00055599 | Yes
2019-09-07 | 1:49 | NA1207 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 39 | 603.6667 | 0.077453 | 0.0001283 | Yes
2019-09-07 | 2:12 | T874 | Short rural | Asset Failure | HV | 462 | 360.5108 | 0.54795 | 0.0015199 | Yes
2019-09-07 | 3:58 | BX1332 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 67 | 705.4328 | 0.063069 | 8.9405e-05 | Yes
2019-09-07 | 4:50 | RW1255 | Short rural | Weather |  | 1 | 189 | 0.00062178 | 3.2899e-06 | Yes
2019-09-07 | 5:14 | L582 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 35 | 366.5143 | 0.042202 | 0.00011515 | Yes
2019-09-07 | 5:54 | NWD2 | Urban | Weather |  | 610.6542 | 73.5468 | 0.05993 | 0.00081486 | Yes
2019-09-07 | 5:54 | NWA2 | Urban | Weather |  | 577.5714 | 73.5468 | 0.056683 | 0.00077071 | Yes
2019-09-07 | 5:54 | NWB2 | Urban | Weather |  | 583.7744 | 73.5468 | 0.057292 | 0.00077899 | Yes
2019-09-07 | 6:23 | CD1234 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 355 | 0.0046716 | 1.3159e-05 | Yes
2019-09-07 | 6:29 | 35693 | Short rural | Weather |  | 1 | 176 | 0.00057902 | 3.2899e-06 | Yes
2019-09-07 | 6:49 | FF1202 | Urban | Asset Failure | Distribution substation | 16 | 475.5 | 0.010152 | 2.135e-05 | Yes
2019-09-07 | 6:52 | FF1239 | Urban | Asset Failure | Distribution substation | 11 | 296 | 0.0043448 | 1.4678e-05 | Yes
2019-09-07 | 7:06 | C897 | Urban | Asset Failure | Distribution substation | 6 | 390 | 0.0031225 | 8.0064e-06 | Yes
2019-09-07 | 7:32 | BWH2 | Short rural | Weather |  | 21 | 90.1905 | 0.006231 | 6.9087e-05 | Yes
2019-09-07 | 7:39 | 35980 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 399 | 448.4185 | 0.58862 | 0.0013127 | Yes
2019-09-07 | 7:47 | S743 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 219.8 | 0.010847 | 4.9348e-05 | Yes
2019-09-07 | 8:01 | A045 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 1493.3 | 0.049128 | 3.2899e-05 | Yes
2019-09-07 | 8:15 | J495 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1586 | 244.4975 | 1.2757 | 0.0052177 | Yes
2019-09-07 | 8:17 | A096 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 504 | 0.011607 | 2.3029e-05 | Yes
2019-09-07 | 8:20 | 25449 | Short rural | Weather |  | 386 | 176.9741 | 0.22474 | 0.0012699 | Yes
2019-09-07 | 9:02 | S738 | Short rural | Weather |  | 1 | 208 | 0.00068429 | 3.2899e-06 | Yes
2019-09-07 | 9:13 | T841 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 83 | 466 | 0.12725 | 0.00027306 | Yes
2019-09-07 | 9:22 | S737 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 3 | 699 | 0.0068988 | 9.8696e-06 | Yes
2019-09-07 | 9:26 | A046 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 1559 | 0.015387 | 9.8696e-06 | Yes
2019-09-07 | 9:34 | A048 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 4 | 1653.5 | 0.0088257 | 5.3376e-06 | Yes
2019-09-07 | 9:38 | 41533 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 6 | 271 | 0.0053493 | 1.9739e-05 | Yes
2019-09-07 | 10:05 | WWB2 | Short rural | Weather |  | 4 | 7.5 | 9.8696e-05 | 1.3159e-05 | Yes
2019-09-07 | 10:10 | P608 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 12 | 239 | 0.0094353 | 3.9478e-05 | Yes
2019-09-07 | 10:16 | TM1258 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1616 | 98.9554 | 0.52609 | 0.0053164 | Yes
2019-09-07 | 10:33 | 10244 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 267.3333 | 0.023746 | 8.8826e-05 | Yes
2019-09-07 | 10:36 | NA1270 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 70 | 209.0571 | 0.048144 | 0.00023029 | Yes
2019-09-07 | 10:50 | RW1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 104 | 131.875 | 0.04512 | 0.00034215 | Yes
2019-09-07 | 10:53 | DP1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 43 | 67.7674 | 0.0095867 | 0.00014146 | Yes
2019-09-07 | 11:09 | BYD2 | Short rural | Weather |  | 24 | 54.9583 | 0.0043393 | 7.8957e-05 | Yes
2019-09-07 | 11:13 | L947 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 560 | 0.0018423 | 3.2899e-06 | Yes
2019-09-07 | 11:28 | MVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 305 | 514.5574 | 0.51631 | 0.0010034 | Yes
2019-09-07 | 11:28 | BYC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 22 | 201 | 0.014548 | 7.2377e-05 | Yes
2019-09-07 | 11:32 | HR1239 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 530 | 0.0014145 | 2.6688e-06 | Yes
2019-09-07 | 11:49 | PK1221 | Urban | Weather |  | 1 | 360 | 0.00048038 | 1.3344e-06 | Yes
2019-09-07 | 11:51 | ULE2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 35 | 104 | 0.011975 | 0.00011515 | Yes
2019-09-07 | 11:51 | NWD2 | Urban | Weather |  | 232 | 317.8664 | 0.098405 | 0.00030958 | Yes
2019-09-07 | 12:12 | WWF2 | Urban | Weather |  | 52 | 117.5769 | 0.0081585 | 6.9389e-05 | Yes
2019-09-07 | 12:15 | MVE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 2465 | 0.097314 | 3.9478e-05 | Yes
2019-09-07 | 13:17 | MG1286 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 28 | 1854.5714 | 0.17084 | 9.2116e-05 | Yes
2019-09-07 | 13:23 | L582 | Short rural | Weather |  | 35 | 233.0286 | 0.026832 | 0.00011515 | Yes
2019-09-07 | 13:35 | MG1286 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 391 | 99.4476 | 0.12792 | 0.0012863 | Yes
2019-09-07 | 13:39 | MVE2 | Short rural | Weather |  | 502 | 241.2729 | 0.39846 | 0.0016515 | Yes
2019-09-07 | 14:11 | BWE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 125 | 296.328 | 0.12186 | 0.00041123 | Yes
2019-09-07 | 14:18 | MG1267 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 870 | 717.808 | 2.0545 | 0.0028622 | Yes
2019-09-07 | 14:20 | KVC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 138 | 86.3333 | 0.039195 | 0.000454 | Yes
2019-09-07 | 14:28 | MVF2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 33 | 1059.2727 | 0.115 | 0.00010857 | Yes
2019-09-07 | 14:34 | RBE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 142 | 914.8732 | 0.42739 | 0.00046716 | Yes
2019-09-07 | 14:43 | WWB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 1422.25 | 0.018716 | 1.3159e-05 | Yes
2019-09-07 | 14:44 | MG1286 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 28 | 1772 | 0.16323 | 9.2116e-05 | Yes
2019-09-07 | 15:01 | KVD2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 100 | 158.81 | 0.052246 | 0.00032899 | Yes
2019-09-07 | 15:17 | MVF2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 152 | 1148.0987 | 0.57412 | 0.00050006 | Yes
2019-09-07 | 15:26 | W114 | Short rural | Weather |  | 35 | 178.4286 | 0.020545 | 0.00011515 | Yes
2019-09-07 | 15:31 | 35824 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 40.6522 | 0.003076 | 7.5667e-05 | Yes
2019-09-07 | 15:35 | BWB2 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 32 | 1534 | 0.065503 | 4.2701e-05 | Yes
2019-09-07 | 15:53 | HKF2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2339 | 172.1163 | 1.3244 | 0.007695 | Yes
2019-09-07 | 15:57 | MG1282 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 38 | 1579 | 0.1974 | 0.00012501 | Yes
2019-09-07 | 15:58 | RBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 1121.6667 | 0.066422 | 5.9218e-05 | Yes
2019-09-07 | 16:02 | RW1281 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 1743 | 0.017203 | 9.8696e-06 | Yes
2019-09-07 | 16:08 | TM1258 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 19 | 337 | 0.021065 | 6.2507e-05 | Yes
2019-09-07 | 16:14 | SZ1332 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 3 | 1198 | 0.011824 | 9.8696e-06 | Yes
2019-09-07 | 16:27 | 35816 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 578 | 499.6384 | 0.95008 | 0.0019015 | Yes
2019-09-07 | 16:55 | R210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1223 | 231.2453 | 0.93042 | 0.0040235 | Yes
2019-09-07 | 17:25 | T841 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 83 | 1305 | 0.35634 | 0.00027306 | Yes
2019-09-07 | 17:31 | DP1210 | Short rural | Asset Failure | Distribution substation | 21 | 79.5238 | 0.0054941 | 6.9087e-05 | Yes
2019-09-07 | 17:49 | BWF2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 113 | 172.2743 | 0.064044 | 0.00037175 | Yes
2019-09-07 | 18:26 | J489 | Urban | Asset Failure | Distribution substation | 1 | 924 | 0.001233 | 1.3344e-06 | Yes
2019-09-07 | 18:36 | 35990 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1263 | 160.3911 | 0.66644 | 0.0041551 | Yes
2019-09-07 | 18:55 | MG1282 | Short rural | Unknown | Unknown | 4 | 1219 | 0.016041 | 1.3159e-05 | Yes
2019-09-07 | 18:57 | KVD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 1128.5 | 0.01485 | 1.3159e-05 | Yes
2019-09-07 | 19:00 | 35824 | Short rural | Weather |  | 98 | 789 | 0.25438 | 0.00032241 | Yes
2019-09-07 | 19:19 | MG1282 | Short rural | Unknown | Unknown | 11 | 1425 | 0.051569 | 3.6188e-05 | Yes
2019-09-07 | 19:24 | KVB2 | Short rural | Unknown | Unknown | 3 | 89 | 0.00087839 | 9.8696e-06 | Yes
2019-09-07 | 19:31 | MG1208 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 1890 | 0.0062178 | 3.2899e-06 | Yes
2019-09-07 | 19:49 | MVD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1713 | 1253.8786 | 7.0663 | 0.0056355 | Yes
2019-09-07 | 19:55 | NG1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 749 | 0.0024641 | 3.2899e-06 | Yes
2019-09-07 | 20:02 | R211 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 30 | 1291 | 0.12742 | 9.8696e-05 | Yes
2019-09-07 | 20:13 | 35816 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 926 | 132.865 | 0.40476 | 0.0030464 | Yes
2019-09-07 | 20:22 | BDG2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 118 | 114 | 0.044255 | 0.0003882 | Yes
2019-09-07 | 20:39 | R211 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 16 | 1153 | 0.060691 | 5.2638e-05 | Yes
2019-09-07 | 20:45 | 1962 | Urban | Animal | Animal Impact | 1768 | 31.4163 | 0.074118 | 0.0023592 | Yes
2019-09-07 | 21:42 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 838 | 195.0155 | 0.53764 | 0.0027569 | Yes
2019-09-07 | 21:42 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 342 | 177.2807 | 0.19946 | 0.0011251 | Yes
2019-09-07 | 22:33 | CLC2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 97 | 0.00031912 | 3.2899e-06 | Yes
2019-09-08 | 5:03 | RBE2 | Short rural | Asset Failure | Distribution substation | 6 | 1020 | 0.020134 | 1.9739e-05 | No
2019-09-08 | 5:26 | J499 | Urban | Weather |  | 21 | 63.5238 | 0.0017801 | 2.8022e-05 | No
2019-09-08 | 6:19 | SHD2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 236 | 0.00077641 | 3.2899e-06 | No
2019-09-08 | 6:35 | T841 | Short rural | Weather |  | 4 | 115.75 | 0.0015232 | 1.3159e-05 | No
2019-09-08 | 6:46 | R210 | Short rural | Weather |  | 11 | 417 | 0.015091 | 3.6188e-05 | No
2019-09-08 | 7:34 | ER1262 | Short rural | Weather |  | 9 | 372.3333 | 0.011024 | 2.9609e-05 | No
2019-09-08 | 7:51 | MG1267 | Short rural | Weather |  | 15 | 651 | 0.032126 | 4.9348e-05 | No
2019-09-08 | 8:12 | RBD2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 792 | 0.0052111 | 6.5797e-06 | No
2019-09-08 | 8:34 | MVC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 1624 | 0.0053427 | 3.2899e-06 | No
2019-09-08 | 8:37 | ER1262 | Short rural | Weather |  | 24 | 323.1667 | 0.025516 | 7.8957e-05 | No
2019-09-08 | 9:02 | PCB2 | Short rural | Asset Failure | Distribution substation | 1 | 201 | 0.00066126 | 3.2899e-06 | No
2019-09-08 | 9:06 | BX1352 | Urban | Third Party | Other | 330 | 140.0667 | 0.061679 | 0.00044035 | No
2019-09-08 | 9:15 | CX1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 115 | 532.913 | 0.20162 | 0.00037833 | No
2019-09-08 | 9:28 | 35816 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 26 | 172 | 0.014712 | 8.5536e-05 | No
2019-09-08 | 9:31 | MG1286 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 7 | 442 | 0.010179 | 2.3029e-05 | No
2019-09-08 | 9:40 | 35825 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 22 | 184.0455 | 0.013321 | 7.2377e-05 | No
2019-09-08 | 9:44 | 35818 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 396 | 0.022147 | 5.5928e-05 | No
2019-09-08 | 9:59 | 35815 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 5 | 201 | 0.0033063 | 1.6449e-05 | No
2019-09-08 | 10:47 | 35816 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 185 | 0.0012172 | 6.5797e-06 | No
2019-09-08 | 11:08 | JBA2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 9 | 163.4444 | 0.0048394 | 2.9609e-05 | No
2019-09-08 | 11:21 | L941 | Short rural | Unknown | Unknown | 1 | 207 | 0.000681 | 3.2899e-06 | No
2019-09-08 | 11:27 | BWC2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 18 | 182 | 0.010778 | 5.9218e-05 | No
2019-09-08 | 11:33 | OA1233 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 144 | 551.4236 | 0.26123 | 0.00047374 | No
2019-09-08 | 11:56 | R208 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 93 | 319 | 0.0976 | 0.00030596 | No
2019-09-08 | 12:03 | CX1206 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 538 | 0.0053098 | 9.8696e-06 | No
2019-09-08 | 13:20 | T869 | Urban | Third Party | Unauthorised access | 1 | 489 | 0.00065252 | 1.3344e-06 | No
2019-09-08 | 13:21 | MVE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 459 | 0.00151 | 3.2899e-06 | No
2019-09-08 | 13:31 | T874 | Short rural | Asset Failure | Distribution substation | 1 | 278 | 0.00091458 | 3.2899e-06 | No
2019-09-08 | 14:39 | MG1286 | Short rural | Weather |  | 6 | 159 | 0.0031385 | 1.9739e-05 | No
2019-09-08 | 14:50 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 325 | 0.0010692 | 3.2899e-06 | No
2019-09-08 | 14:56 | MG1282 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 439 | 159.344 | 0.23013 | 0.0014442 | No
2019-09-08 | 15:00 | BK1251 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 1588 | 0.020897 | 1.3159e-05 | No
2019-09-08 | 15:02 | MVD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 120.8333 | 0.0023852 | 1.9739e-05 | No
2019-09-08 | 15:08 | BK1251 | Short rural | Weather |  | 1 | 315 | 0.0010363 | 3.2899e-06 | No
2019-09-08 | 15:37 | MG1286 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1146 | 28.9154 | 0.10902 | 0.0037702 | No
2019-09-08 | 15:47 | BWC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 19.85 | 0.0013061 | 6.5797e-05 | No
2019-09-08 | 16:19 | RBE2 | Short rural | Unknown | Unknown | 4 | 1278 | 0.016818 | 1.3159e-05 | No
2019-09-08 | 17:07 | CX1232 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 2 | 149 | 0.00098038 | 6.5797e-06 | No
2019-09-08 | 17:22 | R208 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 96 | 13 | 0.0041057 | 0.00031583 | No
2019-09-08 | 17:40 | 17067 | Urban | Asset Failure | Distribution substation | 1 | 81 | 0.00010809 | 1.3344e-06 | No
2019-09-08 | 18:45 | HKD2 | Short rural | Other | Fire | 18 | 86 | 0.0050927 | 5.9218e-05 | No
2019-09-08 | 19:34 | CX1232 | Short rural | Network business | Switching or protection error | 1 | 134 | 0.00044084 | 3.2899e-06 | No
2019-09-08 | 20:09 | L588 | Short rural | Weather |  | 46 | 58.6957 | 0.0088826 | 0.00015133 | No
2019-09-09 | 6:55 | B211 | Urban | Unknown | Unknown | 5 | 109 | 0.00072725 | 6.672e-06 | No
2019-09-09 | 7:44 | GV1245 | Urban | Other | Probable Overload | 53 | 588.3208 | 0.041608 | 7.0723e-05 | No
2019-09-09 | 7:52 | A347 | Urban | Asset Failure | Distribution substation | 7 | 196 | 0.0018308 | 9.3408e-06 | No
2019-09-09 | 7:59 | FT1208 | Urban | Asset Failure | Distribution substation | 1 | 105 | 0.00014011 | 1.3344e-06 | No
2019-09-09 | 8:09 | MVC2 | Short rural | Unknown | Unknown | 5 | 119 | 0.0019575 | 1.6449e-05 | No
2019-09-09 | 11:02 | MVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 47 | 0.00015462 | 3.2899e-06 | No
2019-09-09 | 15:15 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 651 | 162.5499 | 0.34813 | 0.0021417 | No
2019-09-09 | 15:46 | 10241 | Short rural | Asset Failure | Distribution substation | 4 | 4025.25 | 0.05297 | 1.3159e-05 | No
2019-09-09 | 16:42 | MVH2 | Short rural | Vegetation | Grow-in - NSP responsibility | 31 | 44.6452 | 0.0045532 | 0.00010199 | No
2019-09-10 | 7:20 | MVB2 | Short rural | Unknown | Unknown | 183 | 6.9672 | 0.0041946 | 0.00060204 | No
2019-09-10 | 8:57 | J491 | Urban | Asset Failure | Distribution substation | 1 | 91 | 0.00012143 | 1.3344e-06 | No
2019-09-10 | 10:14 | 1954 | Urban | Asset Failure | Distribution substation | 4 | 122.75 | 0.00065519 | 5.3376e-06 | No
2019-09-10 | 11:26 | KC1262 | Short rural | Asset Failure | Distribution substation | 1 | 60 | 0.00019739 | 3.2899e-06 | No
2019-09-10 | 13:55 | L591 | Short rural | Other | Probable Equipment Failure | 188 | 43.0053 | 0.026599 | 0.00061849 | No
2019-09-10 | 23:39 | S740 | Urban | Asset Failure | LV | 860 | 26.1919 | 0.030057 | 0.0011476 | No
2019-09-11 | 2:47 | WQ1275 | Urban | Asset Failure | HV | 32 | 152.1875 | 0.0064985 | 4.2701e-05 | No
2019-09-11 | 12:21 | 5494 | Urban | Third Party | Other | 36 | 182.4167 | 0.008763 | 4.8038e-05 | No
2019-09-11 | 12:49 | 27334 | Urban | Asset Failure | Distribution substation | 89 | 1128 | 0.13396 | 0.00011876 | No
2019-09-11 | 13:19 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 62 | 0.00061191 | 9.8696e-06 | No
2019-09-11 | 14:16 | X217 | Short rural | Unknown | Unknown | 1 | 1635 | 0.0053789 | 3.2899e-06 | No
2019-09-11 | 14:16 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 81 | 55.3457 | 0.014748 | 0.00026648 | No
2019-09-11 | 16:58 | BYC2 | Short rural | Asset Failure | Distribution substation | 1 | 1050 | 0.0034544 | 3.2899e-06 | No
2019-09-11 | 17:41 | BWF2 | Short rural | Third Party | Other | 4 | 244 | 0.0032109 | 1.3159e-05 | No
2019-09-11 | 18:20 | BWH2 | Short rural | Asset Failure | HV | 2 | 150 | 0.00098696 | 6.5797e-06 | No
2019-09-11 | 18:55 | 8770 | Urban | Asset Failure | Distribution substation | 1 | 242 | 0.00032292 | 1.3344e-06 | No
2019-09-11 | 19:08 | MVB2 | Short rural | Unknown | Unknown | 6 | 1321 | 0.026075 | 1.9739e-05 | No
2019-09-12 | 0:35 | FT1205 | Short rural | Animal | Animal Impact | 1183 | 95.1141 | 0.37018 | 0.0038919 | No
2019-09-12 | 5:00 | 9060 | Urban | Asset Failure | HV | 1270 | 20 | 0.033894 | 0.0016947 | No
2019-09-12 | 6:47 | 35771 | Urban | Unknown | Unknown | 35 | 76 | 0.0035495 | 4.6704e-05 | No
2019-09-12 | 7:36 | 87220 | Short rural | Asset Failure | Distribution substation | 1 | 81 | 0.00026648 | 3.2899e-06 | No
2019-09-12 | 8:22 | 9030 | Urban | Asset Failure | HV | 1032 | 103.938 | 0.14313 | 0.0013771 | No
2019-09-12 | 11:12 | 87220 | Short rural | Other | Isolation Request by EE | 40 | 27 | 0.0035531 | 0.00013159 | No
2019-09-12 | 14:45 | 1957 | Urban | Vegetation | Grow-in - NSP responsibility | 70 | 87.5429 | 0.0081772 | 9.3408e-05 | No
2019-09-12 | 15:09 | 35771 | Urban | Asset Failure | Distribution substation | 52 | 464.5385 | 0.032234 | 6.9389e-05 | No
2019-09-12 | 15:42 | GL1207 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 465 | 0.0076489 | 1.6449e-05 | No
2019-09-12 | 16:45 | APC2 | Short rural | Asset Failure | Distribution substation | 1 | 295 | 0.00097051 | 3.2899e-06 | No
2019-09-12 | 19:28 | R210 | Short rural | Asset Failure | Distribution substation | 1 | 70 | 0.00023029 | 3.2899e-06 | No
2019-09-12 | 21:27 | J489 | Urban | Animal | Animal Impact | 1601 | 43 | 0.091864 | 0.0021364 | No
2019-09-12 | 21:46 | J482 | Urban | Unknown | Unknown | 81 | 15 | 0.0016213 | 0.00010809 | No
2019-09-13 | 7:17 | SWJ2 | Urban | Asset Failure | Distribution substation | 1 | 218 | 0.0002909 | 1.3344e-06 | No
2019-09-13 | 7:59 | BDG2 | Short rural | Unknown | Unknown | 2 | 179 | 0.0011778 | 6.5797e-06 | No
2019-09-13 | 9:40 | L591 | Short rural | Asset Failure | HV | 7 | 569 | 0.013104 | 2.3029e-05 | No
2019-09-13 | 10:13 | SWJ2 | Urban | Asset Failure | Distribution substation | 93 | 41.9677 | 0.0052082 | 0.0001241 | No
2019-09-13 | 11:05 | DP1210 | Short rural | Asset Failure | HV | 76 | 79.3289 | 0.019835 | 0.00025003 | No
2019-09-13 | 14:37 | NK1332 | Urban | Asset Failure | Distribution substation | 1 | 125 | 0.0001668 | 1.3344e-06 | No
2019-09-13 | 14:42 | J459 | Short rural | Asset Failure | Distribution substation | 25 | 41.68 | 0.003428 | 8.2247e-05 | No
2019-09-13 | 15:38 | AB1246 | Urban | Asset Failure | Distribution substation | 15 | 79.2667 | 0.0015866 | 2.0016e-05 | No
2019-09-13 | 23:46 | BWF2 | Short rural | Asset Failure | HV | 113 | 178.9646 | 0.066531 | 0.00037175 | No
2019-09-14 | 4:30 | NL1182 | Urban | Third Party | Vehicle impact | 59 | 434.6441 | 0.034219 | 7.873e-05 | No
2019-09-14 | 7:56 | CD1297 | Urban | Asset Failure | Distribution substation | 1 | 334 | 0.00044569 | 1.3344e-06 | No
2019-09-14 | 10:14 | L582 | Short rural | Asset Failure | HV | 10 | 41.2 | 0.0013554 | 3.2899e-05 | No
2019-09-14 | 13:19 | D842 | Urban | Vegetation | Grow-in - NSP responsibility | 42 | 11 | 0.00061649 | 5.6045e-05 | No
2019-09-14 | 13:39 | C854 | Urban | Third Party | Vehicle impact | 2 | 132 | 0.00035228 | 2.6688e-06 | No
2019-09-14 | 18:53 | CX1210 | Short rural | Unknown | Unknown | 3 | 1080 | 0.010659 | 9.8696e-06 | No
2019-09-15 | 5:52 | B713 | Urban | Third Party | Vehicle impact | 44 | 195.8636 | 0.0115 | 5.8714e-05 | No
2019-09-15 | 7:10 | NK1352 | Urban | Asset Failure | Distribution substation | 19 | 206 | 0.0052228 | 2.5354e-05 | No
2019-09-15 | 10:42 | RV1298 | Urban | Asset Failure | HV | 1720 | 54.007 | 0.12395 | 0.0022952 | No
2019-09-15 | 15:59 | 10244 | Short rural | Unknown | Unknown | 1 | 116 | 0.00038162 | 3.2899e-06 | No
2019-09-16 | 8:20 | 8777 | Urban | Asset Failure | HV | 22.1632 | 54 | 0.001597 | 2.9575e-05 | No
2019-09-16 | 8:20 | 8766 | Urban | Asset Failure | HV | 40.8368 | 54 | 0.0029426 | 5.4493e-05 | No
2019-09-16 | 11:57 | T889 | Urban | Asset Failure | Distribution substation | 29 | 52.1034 | 0.0020163 | 3.8698e-05 | No
2019-09-16 | 13:34 | NN1233 | Short rural | Unknown | Unknown | 3 | 94 | 0.00092774 | 9.8696e-06 | No
2019-09-16 | 13:49 | FT1204 | Short rural | Vegetation | Grow-in - NSP responsibility | 199 | 42.8492 | 0.028053 | 0.00065468 | No
2019-09-16 | 13:49 | FT1209 | Urban | Asset Failure | HV | 170 | 34 | 0.0077128 | 0.00022685 | No
2019-09-16 | 14:10 | A048 | Urban | Third Party | Other | 6 | 147.8333 | 0.0011836 | 8.0064e-06 | No
2019-09-16 | 14:43 | 68197 | Urban | Vegetation | Grow-in - NSP responsibility | 706.3104 | 52.424 | 0.04941 | 0.0009425 | No
2019-09-16 | 14:43 | CV1284 | Urban | Vegetation | Grow-in - NSP responsibility | 866.6896 | 52.424 | 0.060629 | 0.0011565 | No
2019-09-16 | 14:55 | HT1203 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 78 | 172.2308 | 0.017926 | 0.00010408 | No
2019-09-16 | 15:03 | MR2291 | Urban | Third Party | Vehicle impact | 40 | 314.15 | 0.016768 | 5.3376e-05 | No
2019-09-16 | 15:23 | SZ1322 | Short rural | Vegetation | Grow-in - NSP responsibility | 405 | 49.8988 | 0.066485 | 0.0013324 | No
2019-09-16 | 15:55 | S735 | Short rural | Vegetation | Grow-in - NSP responsibility | 13 | 272 | 0.011633 | 4.2768e-05 | No
2019-09-16 | 21:54 | WBB2 | Short rural | Asset Failure | HV | 1055 | 75.236 | 0.26113 | 0.0034708 | No
2019-09-16 | 22:37 | 41537 | Urban | Asset Failure | HV | 1413 | 250.0651 | 0.4715 | 0.0018855 | No
2019-09-16 | 22:40 | S735 | Short rural | Asset Failure | HV | 15 | 30 | 0.0014804 | 4.9348e-05 | No
2019-09-16 | 23:14 | 35702 | Urban | Vegetation | Grow-in - NSP responsibility | 71.1759 | 586 | 0.055657 | 9.4977e-05 | No
2019-09-16 | 23:14 | 35695 | Short rural | Vegetation | Grow-in - NSP responsibility | 46.8241 | 586 | 0.09027 | 0.00015404 | No
2019-09-17 | 0:57 | SZ1242 | Short rural | Asset Failure | Distribution substation | 25 | 281 | 0.023111 | 8.2247e-05 | No
2019-09-17 | 1:23 | T841 | Short rural | Weather |  | 83 | 619 | 0.16902 | 0.00027306 | No
2019-09-17 | 1:39 | SG1250 | Urban | Third Party | Vehicle impact | 1340 | 137.4172 | 0.24571 | 0.0017881 | No
2019-09-17 | 3:27 | WQ1208 | Urban | Asset Failure | HV | 173 | 107.7168 | 0.024867 | 0.00023085 | No
2019-09-17 | 4:19 | S735 | Short rural | Asset Failure | Distribution substation | 10 | 111 | 0.0036517 | 3.2899e-05 | No
2019-09-17 | 5:35 | J489 | Urban | Asset Failure | Distribution substation | 1 | 434 | 0.00057913 | 1.3344e-06 | No
2019-09-17 | 5:48 | 1957 | Urban | Asset Failure | LV | 95 | 96.8526 | 0.012278 | 0.00012677 | No
2019-09-17 | 5:54 | L591 | Short rural | Weather |  | 71 | 340.7746 | 0.079598 | 0.00023358 | No
2019-09-17 | 6:13 | PH1267 | Urban | Asset Failure | Distribution substation | 6 | 215 | 0.0017214 | 8.0064e-06 | No
2019-09-17 | 7:51 | RBE2 | Short rural | Unknown | Unknown | 2 | 129 | 0.00084878 | 6.5797e-06 | No
2019-09-17 | 8:18 | X482 | Short rural | Weather |  | 4 | 29 | 0.00038162 | 1.3159e-05 | No
2019-09-17 | 9:51 | HS1142 | Short rural | Weather |  | 7 | 59 | 0.0013587 | 2.3029e-05 | No
2019-09-17 | 10:11 | SG1250 | Urban | Third Party | Vehicle impact | 136 | 11.1029 | 0.0020149 | 0.00018148 | No
2019-09-17 | 10:21 | 8610 | Urban | Vegetation | Grow-in - NSP responsibility | 104 | 105 | 0.014572 | 0.00013878 | No
2019-09-17 | 11:35 | 9046 | Urban | Asset Failure | Distribution substation | 46 | 285 | 0.017494 | 6.1382e-05 | No
2019-09-17 | 13:08 | 35418 | Short rural | Animal | Animal Impact | 192 | 169.1042 | 0.10682 | 0.00063165 | No
2019-09-17 | 14:58 | B217 | Urban | Vegetation | Grow-in - NSP responsibility | 178 | 390.7303 | 0.092807 | 0.00023752 | No
2019-09-17 | 18:10 | L582 | Short rural | Weather |  | 90 | 171.8222 | 0.050874 | 0.00029609 | No
2019-09-17 | 18:11 | RBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 193 | 120.4663 | 0.076489 | 0.00063494 | No
2019-09-17 | 18:27 | WBB2 | Short rural | Asset Failure | Distribution substation | 150 | 37.4 | 0.018456 | 0.00049348 | No
2019-09-17 | 19:20 | NG1299 | Short rural | Unknown | Unknown | 20 | 253 | 0.016647 | 6.5797e-05 | No
2019-09-17 | 19:47 | GG1295 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 3 | 365 | 0.0036024 | 9.8696e-06 | No
2019-09-17 | 20:39 | 7091/1 | Short rural | Unknown | Unknown | 12 | 233 | 0.0091985 | 3.9478e-05 | No
2019-09-17 | 20:40 | 7091 | Short rural | Unknown | Unknown | 1 | 222 | 0.00073035 | 3.2899e-06 | No
2019-09-17 | 22:50 | WQ1271 | Urban | Animal | Animal Impact | 1 | 248 | 0.00033093 | 1.3344e-06 | No
2019-09-17 | 23:23 | S765 | Urban | Asset Failure | Distribution substation | 23 | 154 | 0.0047264 | 3.0691e-05 | No
2019-09-17 | 23:37 | 35702 | Urban | Vegetation | Grow-in - NSP responsibility | 840.8407 | 25.67 | 0.028802 | 0.001122 | No
2019-09-17 | 23:37 | 35695 | Short rural | Vegetation | Grow-in - NSP responsibility | 553.1593 | 25.67 | 0.046715 | 0.0018198 | No
2019-09-18 | 3:27 | WBC2 | Short rural | Asset Failure | HV | 513 | 120.7856 | 0.20385 | 0.0016877 | No
2019-09-18 | 4:35 | GG1269 | Short rural | Asset Failure | Distribution substation | 56 | 595.6071 | 0.10973 | 0.00018423 | No
2019-09-18 | 4:53 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 288 | 267.3021 | 0.25326 | 0.00094748 | No
2019-09-18 | 4:55 | WH1287 | Urban | Asset Failure | Distribution substation | 14 | 232.6429 | 0.0043461 | 1.8682e-05 | No
2019-09-18 | 6:26 | 7966 | Urban | Unknown | Unknown | 40 | 158 | 0.0084334 | 5.3376e-05 | No
2019-09-18 | 7:30 | S786 | Short rural | Vegetation | Grow-in - NSP responsibility | 6 | 267 | 0.0052704 | 1.9739e-05 | No
2019-09-18 | 7:49 | MVH2 | Short rural | Asset Failure | LV | 1531 | 96.7446 | 0.48728 | 0.0050368 | No
2019-09-18 | 10:21 | WL1292 | Urban | Unknown | Unknown | 10 | 173 | 0.0023085 | 1.3344e-05 | No
2019-09-18 | 11:32 | 35010 | Urban | Third Party | Vehicle impact | 660 | 77.5318 | 0.068283 | 0.0008807 | No
2019-09-18 | 11:33 | 9055 | Urban | Unknown | Unknown | 28 | 95 | 0.0035495 | 3.7363e-05 | No
2019-09-18 | 11:37 | 55163 | Short rural | Asset Failure | Distribution substation | 1 | 69 | 0.000227 | 3.2899e-06 | No
2019-09-18 | 12:44 | 7966 | Urban | Other | Probable Overload | 40 | 109 | 0.005818 | 5.3376e-05 | No
2019-09-18 | 13:45 | GL1255 | Short rural | Vegetation | Grow-in - NSP responsibility | 487 | 104.6037 | 0.16759 | 0.0016022 | No
2019-09-18 | 14:42 | CV1236 | Urban | Other | Probable Overload | 17 | 90 | 0.0020416 | 2.2685e-05 | No
2019-09-18 | 15:20 | SY1332 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 205 | 0.0067442 | 3.2899e-05 | No
2019-09-18 | 16:29 | HT1268 | Short rural | Weather |  | 2 | 157 | 0.001033 | 6.5797e-06 | No
2019-09-18 | 16:42 | CV1236 | Urban | Asset Failure | Distribution substation | 1 | 470 | 0.00062717 | 1.3344e-06 | No
2019-09-18 | 18:28 | BGA2 | Short rural | Unknown | Unknown | 1 | 173 | 0.00056915 | 3.2899e-06 | No
2019-09-18 | 18:31 | J510 | Urban | Asset Failure | HV | 1997.6381 | 128.2935 | 0.34199 | 0.0026656 | No
2019-09-18 | 18:31 | M388 | Urban | Asset Failure | HV | 1528.3619 | 128.2935 | 0.26165 | 0.0020394 | No
2019-09-18 | 18:42 | J483 | Urban | Asset Failure | Distribution substation | 6 | 70.5 | 0.00056445 | 8.0064e-06 | No
2019-09-18 | 19:17 | AZ1205 | Urban | Asset Failure | Distribution substation | 7 | 393 | 0.0036709 | 9.3408e-06 | No
2019-09-18 | 19:54 | J493 | Urban | Asset Failure | Distribution substation | 23 | 64.3913 | 0.0019762 | 3.0691e-05 | No
2019-09-18 | 20:07 | 25780 | Urban | Asset Failure | Distribution substation | 1 | 254 | 0.00033894 | 1.3344e-06 | No
2019-09-18 | 21:13 | 49916 | Urban | Asset Failure | Distribution substation | 13 | 373.1538 | 0.0064732 | 1.7347e-05 | No
2019-09-18 | 22:01 | MR2292 | Urban | Unknown | Unknown | 8 | 271 | 0.002893 | 1.0675e-05 | No
2019-09-19 | 0:09 | 8686 | Short rural | Vegetation | Grow-in - NSP responsibility | 16 | 76 | 0.0040005 | 5.2638e-05 | No
2019-09-19 | 3:55 | C833 | Urban | Vegetation | Grow-in - NSP responsibility | 1029 | 464.1429 | 0.63731 | 0.0013731 | No
2019-09-19 | 4:56 | CA1210 | Urban | Unknown | Unknown | 11 | 112 | 0.001644 | 1.4678e-05 | No
2019-09-19 | 6:58 | 35701 | Short rural | Asset Failure | Distribution substation | 17 | 437 | 0.02444 | 5.5928e-05 | No
2019-09-19 | 8:16 | 16651 | Urban | Unknown | Unknown | 23 | 104 | 0.0031919 | 3.0691e-05 | No
2019-09-19 | 8:21 | KC1221 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 214 | 0.0084484 | 3.9478e-05 | No
2019-09-19 | 8:49 | WQ1271 | Urban | Asset Failure | HV | 1 | 672 | 0.00089672 | 1.3344e-06 | No
2019-09-19 | 10:34 | L946 | Short rural | Asset Failure | Distribution substation | 1 | 382 | 0.0012567 | 3.2899e-06 | No
2019-09-19 | 11:54 | OP1132 | Short rural | Third Party | Vehicle impact | 14 | 52 | 0.002395 | 4.6058e-05 | No
2019-09-19 | 11:57 | WBC2 | Short rural | Asset Failure | Distribution substation | 1 | 259 | 0.00085207 | 3.2899e-06 | No
2019-09-19 | 15:10 | KC1221 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 84 | 0.00027635 | 3.2899e-06 | No
2019-09-19 | 16:01 | C833 | Urban | Unknown | Unknown | 132 | 131 | 0.023074 | 0.00017614 | No
2019-09-19 | 17:46 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 83 | 0.00027306 | 3.2899e-06 | No
2019-09-19 | 23:59 | SHD2 | Short rural | Asset Failure | Distribution substation | 20 | 107 | 0.0070403 | 6.5797e-05 | No
2019-09-20 | 5:24 | PH1230 | Urban | Asset Failure | Distribution substation | 2 | 589 | 0.0015719 | 2.6688e-06 | No
2019-09-20 | 9:33 | WL1295 | Urban | Other | FOREIGN MATTER ON SYSTEM | 41 | 125 | 0.0068388 | 5.471e-05 | No
2019-09-20 | 10:30 | B743 | Urban | Asset Failure | HV | 1054 | 118.7903 | 0.16707 | 0.0014065 | No
2019-09-20 | 10:35 | B747 | Urban | Asset Failure | HV | 457 | 4 | 0.0024393 | 0.00060982 | No
2019-09-20 | 10:35 | B746 | Urban | Asset Failure | HV | 49 | 4 | 0.00026154 | 6.5386e-05 | No
2019-09-20 | 10:35 | B745 | Urban | Asset Failure | HV | 388 | 4 | 0.002071 | 0.00051775 | No
2019-09-20 | 13:14 | 1960 | Urban | Asset Failure | Distribution substation | 1 | 225 | 0.00030024 | 1.3344e-06 | No
2019-09-20 | 15:12 | 8611 | Urban | Other | Fault within LV customers installation - Defective Equipment | 7 | 147 | 0.0013731 | 9.3408e-06 | No
2019-09-20 | 15:55 | WH1209 | Urban | Vegetation | Grow-in - NSP responsibility | 998 | 76 | 0.10121 | 0.0013317 | No
2019-09-20 | 17:38 | CX1273 | Short rural | Unknown | Unknown | 1 | 95 | 0.00031254 | 3.2899e-06 | No
2019-09-20 | 18:58 | WL1236 | Urban | Vegetation | Grow-in - NSP responsibility | 23 | 14 | 0.00042968 | 3.0691e-05 | No
2019-09-20 | 19:39 | CJ1249 | Urban | Asset Failure | Distribution substation | 9 | 116 | 0.0013931 | 1.201e-05 | No
2019-09-20 | 20:33 | B743 | Urban | Asset Failure | HV | 91 | 98 | 0.0119 | 0.00012143 | No
2019-09-20 | 22:09 | 8686 | Short rural | Asset Failure | Distribution substation | 7 | 649 | 0.014946 | 2.3029e-05 | No
2019-09-21 | 6:19 | CA1210 | Urban | Asset Failure | Distribution substation | 1 | 102 | 0.00013611 | 1.3344e-06 | No
2019-09-21 | 9:11 | L582 | Short rural | Asset Failure | LV | 300 | 177 | 0.17469 | 0.00098696 | No
2019-09-21 | 10:06 | 1959 | Urban | Asset Failure | Distribution substation | 1 | 353 | 0.00047104 | 1.3344e-06 | No
2019-09-21 | 16:08 | CD1271 | Short rural | Unknown | Unknown | 8 | 144 | 0.0037899 | 2.6319e-05 | No
2019-09-21 | 16:12 | SY1232 | Urban | Asset Failure | Distribution substation | 1 | 141 | 0.00018815 | 1.3344e-06 | No
2019-09-21 | 16:17 | NA1270 | Short rural | Asset Failure | LV | 50 | 227 | 0.03734 | 0.00016449 | No
2019-09-21 | 17:06 | BDA2 | Short rural | Asset Failure | Distribution substation | 1 | 264 | 0.00086852 | 3.2899e-06 | No
2019-09-21 | 17:15 | BYB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 146 | 120.089 | 0.057681 | 0.00048032 | No
2019-09-21 | 21:07 | L516 | Urban | Asset Failure | Distribution substation | 1 | 293 | 0.00039098 | 1.3344e-06 | No
2019-09-22 | 11:24 | CLA2 | Short rural | Asset Failure | HV | 4 | 90 | 0.0011844 | 1.3159e-05 | No
2019-09-22 | 14:44 | WBB2 | Short rural | Asset Failure | Distribution substation | 1 | 180 | 0.00059218 | 3.2899e-06 | No
2019-09-22 | 15:54 | RS1203 | Urban | Asset Failure | Distribution substation | 16 | 112 | 0.0023912 | 2.135e-05 | No
2019-09-22 | 16:08 | L948 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 443 | 69 | 0.10056 | 0.0014574 | No
2019-09-22 | 20:58 | T890 | Urban | Asset Failure | Distribution substation | 1 | 53 | 7.0723e-05 | 1.3344e-06 | No
2019-09-23 | 10:00 | WD1247 | Short rural | Other | Isolation Request by EE | 6 | 31 | 0.00061191 | 1.9739e-05 | No
2019-09-23 | 12:15 | KC1262 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 7 | 122 | 0.0028095 | 2.3029e-05 | No
2019-09-23 | 14:00 | PCA2 | Short rural | Asset Failure | HV | 82 | 117.1463 | 0.031602 | 0.00026977 | No
2019-09-23 | 15:04 | T882 | Urban | Vegetation | Grow-in - NSP responsibility | 773 | 37 | 0.038165 | 0.0010315 | No
2019-09-23 | 23:05 | 8615 | Urban | Asset Failure | Distribution substation | 1 | 545 | 0.00072725 | 1.3344e-06 | No
2019-09-23 | 23:29 | 35418 | Short rural | Vegetation | Grow-in - NSP responsibility | 73 | 540.1918 | 0.12973 | 0.00024016 | No
2019-09-24 | 10:12 | 35333 | Urban | Asset Failure | Distribution substation | 1 | 344 | 0.00045903 | 1.3344e-06 | No
2019-09-24 | 14:38 | 35763 | Urban | Asset Failure | LV | 3 | 199 | 0.00079664 | 4.0032e-06 | No
2019-09-24 | 16:31 | R211 | Short rural | Asset Failure | Distribution substation | 1 | 208 | 0.00068429 | 3.2899e-06 | No
2019-09-24 | 18:16 | J514 | Urban | Unknown | Unknown | 1 | 763 | 0.0010181 | 1.3344e-06 | No
2019-09-25 | 1:37 | 27334 | Urban | Asset Failure | Distribution substation | 21 | 50.2381 | 0.0014078 | 2.8022e-05 | No
2019-09-25 | 12:38 | ULL2 | Short rural | Asset Failure | Distribution substation | 50 | 268 | 0.044084 | 0.00016449 | No
2019-09-25 | 13:59 | 7092/2 | Short rural | Asset Failure | HV | 6 | 844.1667 | 0.016663 | 1.9739e-05 | No
2019-09-25 | 14:22 | WWD2 | Urban | Third Party | Other | 591 | 164.2606 | 0.12954 | 0.00078863 | No
2019-09-25 | 14:26 | R260 | Short rural | Vegetation | Grow-in - NSP responsibility | 67 | 217.7015 | 0.047986 | 0.00022042 | No
2019-09-25 | 15:04 | T868 | Short rural | Asset Failure | LV | 204 | 22.8971 | 0.015367 | 0.00067113 | No
2019-09-25 | 15:26 | SXA2 | Short rural | Third Party | Unauthorised access | 165 | 38 | 0.020627 | 0.00054283 | No
2019-09-26 | 3:08 | CX1284 | Short rural | Third Party | Unauthorised access | 65 | 447.8615 | 0.095771 | 0.00021384 | No
2019-09-26 | 6:09 | SN1271 | Short rural | Unknown | Unknown | 8 | 325 | 0.0085536 | 2.6319e-05 | No
2019-09-26 | 7:21 | CR1262 | Urban | Asset Failure | Distribution substation | 1 | 446 | 0.00059514 | 1.3344e-06 | No
2019-09-26 | 10:04 | 6421 | Urban | Third Party | Other | 197 | 73 | 0.01919 | 0.00026288 | No
2019-09-26 | 18:02 | MM1392 | Urban | Asset Failure | Distribution substation | 1 | 87 | 0.00011609 | 1.3344e-06 | No
2019-09-27 | 4:09 | 35771 | Urban | Third Party | Unauthorised access | 19 | 54 | 0.0013691 | 2.5354e-05 | No
2019-09-27 | 5:46 | CA1210 | Urban | Third Party | Other | 30 | 76 | 0.0030424 | 4.0032e-05 | No
2019-09-27 | 7:11 | S776 | Urban | Asset Failure | Distribution substation | 1 | 218 | 0.0002909 | 1.3344e-06 | No
2019-09-27 | 7:47 | YYB2 | Short rural | Asset Failure | Distribution substation | 1 | 330 | 0.0010857 | 3.2899e-06 | No
2019-09-27 | 8:04 | BWH2 | Short rural | Asset Failure | Distribution substation | 1 | 405 | 0.0013324 | 3.2899e-06 | No
2019-09-27 | 9:03 | CA1284 | Urban | Third Party | Vehicle impact | 98 | 75.3878 | 0.0098585 | 0.00013077 | No
2019-09-27 | 10:00 | KVB2 | Short rural | Asset Failure | Distribution substation | 1 | 238 | 0.00078299 | 3.2899e-06 | No
2019-09-27 | 10:13 | PCA2 | Short rural | Animal | Animal Impact | 82 | 28.1463 | 0.007593 | 0.00026977 | No
2019-09-27 | 13:37 | SXA2 | Short rural | Third Party | Unauthorised access | 90 | 124 | 0.036715 | 0.00029609 | No
2019-09-27 | 13:41 | SXA2 | Short rural | Third Party | Unauthorised access | 118 | 49.7288 | 0.019305 | 0.0003882 | No
2019-09-27 | 14:15 | 8801 | Short rural | Other | Isolation Request by EE | 11 | 10.8182 | 0.00039149 | 3.6188e-05 | No
2019-09-27 | 15:24 | W111 | Short rural | Other | Isolation Request by EE | 21 | 27.1905 | 0.0018785 | 6.9087e-05 | No
2019-09-28 | 9:51 | WD1221 | Short rural | Asset Failure | Distribution substation | 4 | 210 | 0.0027635 | 1.3159e-05 | No
2019-09-28 | 13:07 | SXC2 | Short rural | Asset Failure | Distribution substation | 2 | 67.5 | 0.00044413 | 6.5797e-06 | No
2019-09-28 | 17:32 | SC1253 | Short rural | Asset Failure | Distribution substation | 1 | 161 | 0.00052967 | 3.2899e-06 | No
2019-09-28 | 18:39 | X881 | Short rural | Asset Failure | Distribution substation | 1 | 138 | 0.000454 | 3.2899e-06 | No
2019-09-29 | 0:28 | RW1255 | Short rural | Third Party | Vehicle impact | 104 | 97.7981 | 0.033461 | 0.00034215 | No
2019-09-29 | 6:47 | T868 | Short rural | Asset Failure | HV | 187 | 105.9733 | 0.065195 | 0.0006152 | No
2019-09-29 | 8:32 | RW1281 | Short rural | Unknown | Unknown | 1 | 341 | 0.0011218 | 3.2899e-06 | No
2019-09-29 | 12:51 | WL1218 | Urban | Asset Failure | Distribution substation | 1 | 488 | 0.00065119 | 1.3344e-06 | No
2019-09-29 | 16:27 | BX1242 | Urban | Vegetation | Grow-in - NSP responsibility | 64 | 185.2969 | 0.015825 | 8.5402e-05 | No
2019-09-30 | 8:09 | ER1142 | Urban | Third Party | Vehicle impact | 23 | 235.7826 | 0.0072364 | 3.0691e-05 | No
2019-09-30 | 10:36 | T888 | Urban | Asset Failure | Distribution substation | 12 | 80 | 0.001281 | 1.6013e-05 | No
2019-09-30 | 12:11 | CR1214 | Urban | Asset Failure | LV | 1289 | 26.6843 | 0.045898 | 0.00172 | No
2019-09-30 | 15:25 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 166.5 | 0.0010955 | 6.5797e-06 | No
2019-09-30 | 17:39 | LP1132 | Urban | Unknown | Unknown | 25 | 75 | 0.002502 | 3.336e-05 | No
2019-09-30 | 17:54 | J491 | Urban | Asset Failure | Distribution substation | 1 | 155 | 0.00020683 | 1.3344e-06 | No
2019-09-30 | 18:16 | D850 | Urban | Asset Failure | Distribution substation | 1 | 263 | 0.00035095 | 1.3344e-06 | No
2019-09-30 | 19:25 | LP1132 | Urban | Asset Failure | Distribution substation | 25 | 314.56 | 0.010494 | 3.336e-05 | No
2019-09-30 | 20:35 | DS1235 | Urban | Asset Failure | Distribution substation | 0.4765 | 724 | 0.00046034 | 6.3584e-07 | No
2019-09-30 | 20:35 | CA1210 | Urban | Asset Failure | Distribution substation | 0.5235 | 724 | 0.00050576 | 6.9856e-07 | No
2019-10-01 | 5:59 | CA1210 | Urban | Third Party | Other | 29 | 142 | 0.0054951 | 3.8698e-05 | No
2019-10-01 | 7:52 | PH1286 | Urban | Asset Failure | HV | 100 | 115 | 0.015346 | 0.00013344 | No
2019-10-01 | 7:56 | 1960 | Urban | Unknown | Unknown | 5 | 72 | 0.00048038 | 6.672e-06 | No
2019-10-01 | 9:53 | CLD2 | Short rural | Asset Failure | Distribution substation | 87 | 288 | 0.082431 | 0.00028622 | No
2019-10-01 | 11:29 | L509 | Urban | Asset Failure | Distribution substation | 11 | 134 | 0.0019669 | 1.4678e-05 | No
2019-10-01 | 13:08 | R293 | Short rural | Asset Failure | HV | 1 | 102 | 0.00033557 | 3.2899e-06 | No
2019-10-01 | 21:50 | MR2206 | Urban | Other | Probable Equipment Failure | 2070 | 87.4164 | 0.24146 | 0.0027622 | No
2019-10-02 | 4:02 | JBB2 | Short rural | Unknown | Unknown | 6 | 218 | 0.0043031 | 1.9739e-05 | No
2019-10-02 | 5:26 | CA1210 | Urban | Third Party | Other | 29 | 81 | 0.0031345 | 3.8698e-05 | No
2019-10-02 | 5:44 | BWH2 | Short rural | Animal | Animal Impact | 79 | 132 | 0.034307 | 0.0002599 | No
2019-10-02 | 8:27 | RD1236 | Urban | Third Party | Dig-in | 131 | 90.1145 | 0.015753 | 0.00017481 | No
2019-10-02 | 9:11 | SN1219 | Short rural | Asset Failure | Distribution substation | 1 | 153 | 0.00050335 | 3.2899e-06 | No
2019-10-02 | 15:52 | CX1206 | Short rural | Unknown | Unknown | 1 | 128 | 0.0004211 | 3.2899e-06 | No
2019-10-03 | 4:17 | KC1214 | Short rural | Asset Failure | Distribution substation | 3 | 115 | 0.001135 | 9.8696e-06 | No
2019-10-03 | 8:50 | 49916 | Urban | Unknown | Unknown | 13 | 85 | 0.0014745 | 1.7347e-05 | No
2019-10-03 | 12:20 | NA1236 | Short rural | Unknown | Unknown | 5 | 134 | 0.0022042 | 1.6449e-05 | No
2019-10-03 | 13:24 | TM1210 | Short rural | Third Party | Unauthorised access | 7 | 29 | 0.00066784 | 2.3029e-05 | No
2019-10-03 | 14:04 | 1952 | Urban | Asset Failure | Distribution substation | 59 | 70 | 0.0055111 | 7.873e-05 | No
2019-10-03 | 14:14 | 49916 | Urban | Other | Probable Equipment Failure | 13 | 494 | 0.0085695 | 1.7347e-05 | No
2019-10-03 | 15:36 | NM1210 | Urban | Asset Failure | HV | 337 | 44.3739 | 0.019955 | 0.00044969 | No
2019-10-03 | 23:51 | X482 | Short rural | Animal | Animal Impact | 8 | 679 | 0.017871 | 2.6319e-05 | No
2019-10-03 | 23:59 | 49006 | Short rural | Unknown | Unknown | 13 | 237 | 0.010136 | 4.2768e-05 | No
2019-10-04 | 5:18 | CA1210 | Urban | Third Party | Other | 10 | 57 | 0.00076061 | 1.3344e-05 | No
2019-10-04 | 5:39 | X482 | Short rural | Animal | Animal Impact | 8 | 313 | 0.0082378 | 2.6319e-05 | No
2019-10-04 | 8:48 | L582 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 26.1387 | 639.3478 | 0.054979 | 8.5993e-05 | No
2019-10-04 | 8:48 | BK1251 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 19.8613 | 639.3478 | 0.041776 | 6.5341e-05 | No
2019-10-04 | 9:03 | A350 | Urban | Third Party | Other | 42 | 188 | 0.010536 | 5.6045e-05 | No
2019-10-04 | 9:52 | 8801 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 198 | 0.00065139 | 3.2899e-06 | No
2019-10-04 | 10:31 | BL1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 170 | 11 | 0.006152 | 0.00055928 | No
2019-10-04 | 11:01 | 10251 | Urban | Asset Failure | LV | 154 | 138 | 0.028359 | 0.0002055 | No
2019-10-04 | 11:33 | 87222 | Long rural | Asset Failure | Distribution substation | 1 | 87 | 0.27707 | 0.0031847 | No
2019-10-04 | 12:14 | CX1210 | Short rural | Vegetation | Grow-in - NSP responsibility | 816 | 11.2892 | 0.030306 | 0.0026845 | No
2019-10-04 | 12:24 | BWE2 | Short rural | Third Party | Dig-in | 22 | 298 | 0.021568 | 7.2377e-05 | No
2019-10-04 | 12:43 | NG1262 | Short rural | Vegetation | Grow-in - NSP responsibility | 368 | 71.1821 | 0.086178 | 0.0012107 | No
2019-10-04 | 13:27 | X482 | Short rural | Asset Failure | Distribution substation | 1 | 63 | 0.00020726 | 3.2899e-06 | No
2019-10-04 | 14:49 | CR1214 | Urban | Asset Failure | HV | 84 | 24.2262 | 0.0027155 | 0.00011209 | No
2019-10-04 | 15:09 | 4871 | Urban | Unknown | Unknown | 165 | 222 | 0.048879 | 0.00022018 | No
2019-10-04 | 15:14 | RW1281 | Short rural | Asset Failure | Distribution substation | 3 | 291 | 0.0028721 | 9.8696e-06 | No
2019-10-04 | 18:29 | 9027 | Urban | Asset Failure | Distribution substation | 49 | 226.8163 | 0.014831 | 6.5386e-05 | No
2019-10-04 | 21:40 | JBB2 | Short rural | Animal | Animal Impact | 14 | 187 | 0.0086129 | 4.6058e-05 | No
2019-10-04 | 23:34 | MVC2 | Short rural | Animal | Animal Impact | 22 | 471 | 0.03409 | 7.2377e-05 | No
2019-10-04 | 23:44 | CR1210 | Urban | Unknown | Unknown | 15 | 327 | 0.0065452 | 2.0016e-05 | No
2019-10-05 | 1:26 | 7976 | Urban | Asset Failure | Distribution substation | 39 | 236.4872 | 0.012307 | 5.2042e-05 | No
2019-10-05 | 1:30 | AB1287 | Urban | Unknown | Unknown | 9 | 80 | 0.00096077 | 1.201e-05 | No
2019-10-05 | 5:50 | HR1250 | Urban | Asset Failure | Distribution substation | 289 | 528 | 0.20362 | 0.00038564 | No
2019-10-05 | 6:11 | CR1210 | Urban | Unknown | Unknown | 15 | 77 | 0.0015412 | 2.0016e-05 | No
2019-10-05 | 7:41 | WD1288 | Urban | Asset Failure | HV | 12 | 49.3333 | 0.00078996 | 1.6013e-05 | No
2019-10-05 | 8:35 | MR2292 | Urban | Asset Failure | Distribution substation | 8 | 358.75 | 0.0038297 | 1.0675e-05 | No
2019-10-05 | 11:24 | CJ1241 | Urban | Asset Failure | Distribution substation | 14 | 361 | 0.0067441 | 1.8682e-05 | No
2019-10-05 | 12:15 | WBC2 | Short rural | Asset Failure | LV | 34 | 67 | 0.0074943 | 0.00011186 | No
2019-10-05 | 13:40 | AB1287 | Urban | Unknown | Unknown | 1 | 178 | 0.00023752 | 1.3344e-06 | No
2019-10-05 | 14:17 | S735 | Short rural | Vegetation | Grow-in - NSP responsibility | 13 | 55.6923 | 0.0023819 | 4.2768e-05 | No
2019-10-05 | 15:02 | 25746 | Urban | Unknown | Unknown | 15 | 175 | 0.0035028 | 2.0016e-05 | No
2019-10-05 | 15:34 | 27334 | Urban | Asset Failure | Distribution substation | 21 | 52.4286 | 0.0014692 | 2.8022e-05 | No
2019-10-05 | 16:36 | WBC2 | Short rural | Unknown | Unknown | 2 | 115 | 0.00075667 | 6.5797e-06 | No
2019-10-05 | 16:56 | GL1255 | Short rural | Asset Failure | LV | 38 | 14.4474 | 0.0018061 | 0.00012501 | No
2019-10-05 | 23:18 | DS1223 | Urban | Unknown | Unknown | 23 | 44 | 0.0013504 | 3.0691e-05 | No
2019-10-06 | 3:22 | NA1281 | Urban | Asset Failure | Distribution substation | 10 | 456 | 0.0060849 | 1.3344e-05 | No
2019-10-06 | 8:00 | NN1277 | Urban | Unknown | Unknown | 1 | 116 | 0.00015479 | 1.3344e-06 | No
2019-10-06 | 12:09 | A095 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 121 | 0.00039807 | 3.2899e-06 | No
2019-10-06 | 13:33 | KMF2 | Urban | Asset Failure | HV | 127 | 130.748 | 0.022158 | 0.00016947 | No
2019-10-06 | 17:38 | DS1223 | Urban | Asset Failure | Distribution substation | 23 | 103.2609 | 0.0031692 | 3.0691e-05 | No
2019-10-06 | 23:04 | 1954 | Urban | Asset Failure | Distribution substation | 52 | 167.0192 | 0.011589 | 6.9389e-05 | No
2019-10-06 | 23:36 | TM1284 | Short rural | Asset Failure | Distribution substation | 72 | 70 | 0.016581 | 0.00023687 | No
2019-10-07 | 8:39 | 828/4 | Short rural | Other | Isolation Request by EE | 1 | 177 | 0.00058231 | 3.2899e-06 | No
2019-10-07 | 11:04 | T828 | Short rural | Asset Failure | Distribution substation | 1 | 214 | 0.00070403 | 3.2899e-06 | No
2019-10-07 | 12:47 | CD1260 | Urban | Unknown | Unknown | 66 | 111 | 0.0097758 | 8.807e-05 | No
2019-10-08 | 14:05 | 9055 | Urban | Asset Failure | Distribution substation | 41 | 70 | 0.0038297 | 5.471e-05 | No
2019-10-08 | 15:39 | 8770 | Urban | Vegetation | Grow-in - NSP responsibility | 1025 | 35.2166 | 0.048168 | 0.0013678 | No
2019-10-08 | 16:29 | A325 | Urban | Other | Probable Accidental Damage - Foreign Matter On System | 42 | 86 | 0.0048198 | 5.6045e-05 | No
2019-10-09 | 5:28 | WH1287 | Urban | Asset Failure | Distribution substation | 10 | 329.8 | 0.0044008 | 1.3344e-05 | No
2019-10-09 | 9:25 | WL1236 | Urban | Third Party | Vehicle impact | 105 | 477 | 0.066833 | 0.00014011 | No
2019-10-09 | 12:02 | 7981 | Urban | Animal | Animal Impact | 32 | 187 | 0.007985 | 4.2701e-05 | No
2019-10-09 | 12:31 | SZ1352 | Urban | Third Party | Vehicle impact | 19 | 53.8421 | 0.0013651 | 2.5354e-05 | No
2019-10-09 | 16:13 | KC1236 | Short rural | Asset Failure | Distribution substation | 1 | 59 | 0.0001941 | 3.2899e-06 | No
2019-10-10 | 7:02 | C868 | Urban | Unknown | Unknown | 1 | 79 | 0.00010542 | 1.3344e-06 | No
2019-10-10 | 7:20 | 35818 | Short rural | Third Party | Vehicle impact | 4 | 596.25 | 0.0078463 | 1.3159e-05 | No
2019-10-10 | 8:06 | D810 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 559 | 0.001839 | 3.2899e-06 | No
2019-10-10 | 14:01 | 16651 | Urban | Asset Failure | Distribution substation | 1 | 3324 | 0.0044355 | 1.3344e-06 | No
2019-10-10 | 17:56 | L591 | Short rural | Asset Failure | Distribution substation | 1 | 194 | 0.00063823 | 3.2899e-06 | No
2019-10-10 | 19:30 | SHH2 | Short rural | Asset Failure | LV | 1 | 262 | 0.00086194 | 3.2899e-06 | No
2019-10-10 | 19:40 | 49006 | Short rural | Unknown | Unknown | 13 | 234 | 0.010008 | 4.2768e-05 | No
2019-10-10 | 23:24 | S788 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 2 | 107 | 0.00070403 | 6.5797e-06 | No
2019-10-10 | 23:34 | LL1212 | Urban | Unknown | Unknown | 72 | 142 | 0.013643 | 9.6077e-05 | No
2019-10-11 | 2:24 | WRB2 | Urban | Third Party | Unauthorised access | 1370 | 84 | 0.15356 | 0.0018281 | No
2019-10-11 | 6:28 | 49006 | Short rural | Asset Failure | Distribution substation | 1 | 561 | 0.0018456 | 3.2899e-06 | No
2019-10-11 | 11:52 | L585 | Short rural | Third Party | Vehicle impact | 130 | 132 | 0.056454 | 0.00042768 | No
2019-10-11 | 13:45 | WQ1264 | Urban | Unknown | Unknown | 1 | 183 | 0.0002442 | 1.3344e-06 | No
2019-10-11 | 14:25 | HS1152 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 272.3208 | 64.7378 | 0.057998 | 0.0008959 | No
2019-10-11 | 14:25 | HS1142 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 566.6792 | 64.7378 | 0.12069 | 0.0018643 | No
2019-10-11 | 15:59 | X217 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 111 | 0.00073035 | 6.5797e-06 | No
2019-10-11 | 16:45 | CD1260 | Urban | Asset Failure | Distribution substation | 13 | 73 | 0.0012663 | 1.7347e-05 | No
2019-10-11 | 18:00 | MVB2 | Short rural | Unknown | Unknown | 26 | 45 | 0.0038491 | 8.5536e-05 | No
2019-10-11 | 18:46 | 35327 | Urban | Asset Failure | Distribution substation | 45 | 95 | 0.0057046 | 6.0048e-05 | No
2019-10-11 | 19:14 | 8694 | Urban | Third Party | Dig-in | 1 | 549 | 0.00073259 | 1.3344e-06 | No
2019-10-11 | 23:03 | WL1236 | Urban | Asset Failure | LV | 1396 | 153 | 0.28501 | 0.0018628 | No
2019-10-11 | 23:54 | BWE2 | Short rural | Asset Failure | Distribution substation | 1 | 664 | 0.0021845 | 3.2899e-06 | No
2019-10-12 | 1:26 | J497 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 407 | 0.001339 | 3.2899e-06 | No
2019-10-12 | 2:38 | 1962 | Urban | Unknown | Unknown | 79 | 132 | 0.013915 | 0.00010542 | No
2019-10-12 | 4:27 | WQ1275 | Urban | Asset Failure | HV | 35.0189 | 82.8621 | 0.0038721 | 4.6729e-05 | No
2019-10-12 | 4:27 | WQ1271 | Urban | Asset Failure | HV | 22.9811 | 82.8621 | 0.002541 | 3.0666e-05 | No
2019-10-12 | 6:55 | MVB2 | Short rural | Unknown | Unknown | 9 | 147 | 0.0043525 | 2.9609e-05 | No
2019-10-12 | 11:33 | 87222 | Long rural | Asset Failure | Distribution substation | 1 | 30 | 0.095541 | 0.0031847 | No
2019-10-12 | 11:43 | WL1236 | Urban | Asset Failure | Distribution substation | 1 | 177 | 0.00023619 | 1.3344e-06 | No
2019-10-12 | 13:50 | L585 | Short rural | Third Party | Unauthorised access | 7 | 35 | 0.00080602 | 2.3029e-05 | No
2019-10-12 | 15:40 | BX1232 | Urban | Asset Failure | Distribution substation | 16 | 368 | 0.0078569 | 2.135e-05 | No
2019-10-12 | 15:40 | L591 | Short rural | Asset Failure | HV | 184 | 171.038 | 0.10354 | 0.00060533 | No
2019-10-12 | 19:56 | 35982 | Short rural | Animal | Animal Impact | 1 | 279 | 0.00091787 | 3.2899e-06 | No
2019-10-12 | 22:22 | NG1210 | Short rural | Asset Failure | Distribution substation | 4 | 715 | 0.009409 | 1.3159e-05 | No
2019-10-13 | 3:27 | HR1239 | Urban | Third Party | Vehicle impact | 1047 | 113.2951 | 0.15829 | 0.0013971 | No
2019-10-13 | 7:43 | 35763 | Urban | Third Party | Vehicle impact | 38 | 180.3684 | 0.009146 | 5.0707e-05 | No
2019-10-13 | 8:46 | SHE2 | Urban | Asset Failure | HV | 928.7915 | 72.3649 | 0.089687 | 0.0012394 | No
2019-10-13 | 8:46 | SHA2 | Urban | Asset Failure | HV | 847.2085 | 72.3649 | 0.08181 | 0.0011305 | No
2019-10-13 | 15:11 | 27039 | Urban | Asset Failure | Distribution substation | 1 | 58 | 7.7395e-05 | 1.3344e-06 | No
2019-10-13 | 19:20 | BX1242 | Urban | Unknown | Unknown | 35 | 50 | 0.0023352 | 4.6704e-05 | No
2019-10-13 | 22:42 | MVB2 | Short rural | Unknown | Unknown | 3 | 471 | 0.0046486 | 9.8696e-06 | No
2019-10-14 | 6:49 | A048 | Urban | Asset Failure | Distribution substation | 4 | 90 | 0.00048038 | 5.3376e-06 | No
2019-10-14 | 12:36 | CT1265 | Urban | Third Party | Other | 30 | 153.0667 | 0.0061276 | 4.0032e-05 | No
2019-10-14 | 13:41 | SN1208 | Short rural | Asset Failure | LV | 6 | 98 | 0.0019344 | 1.9739e-05 | No
2019-10-14 | 14:32 | WBD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 133 | 91.9624 | 0.040238 | 0.00043755 | No
2019-10-14 | 14:54 | YYB2 | Short rural | Animal | Animal Impact | 2 | 152 | 0.0010001 | 6.5797e-06 | No
2019-10-15 | 18:17 | CLA2 | Short rural | Animal | Animal Impact | 1326 | 51.3778 | 0.22413 | 0.0043624 | No
2019-10-15 | 22:05 | 27341 | Urban | Other | Probable Equipment Failure | 18 | 253 | 0.0060769 | 2.4019e-05 | No
2019-10-16 | 6:00 | B743 | Urban | Third Party | Vehicle impact | 43 | 474 | 0.027198 | 5.7379e-05 | No
2019-10-16 | 11:50 | GL1233 | Short rural | Asset Failure | Distribution substation | 1 | 149 | 0.00049019 | 3.2899e-06 | No
2019-10-16 | 12:21 | RW1255 | Short rural | Third Party | Unauthorised access | 2 | 35 | 0.00023029 | 6.5797e-06 | No
2019-10-16 | 16:18 | WWC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1770 | 51.8757 | 0.30208 | 0.0058231 | No
2019-10-16 | 17:12 | J506 | Urban | Asset Failure | Distribution substation | 28 | 239.5357 | 0.0089498 | 3.7363e-05 | No
2019-10-16 | 18:24 | KVD2 | Short rural | Unknown | Unknown | 63 | 254 | 0.052644 | 0.00020726 | No
2019-10-16 | 19:16 | BYB2 | Short rural | Asset Failure | HV | 200 | 54.175 | 0.035646 | 0.00065797 | No
2019-10-16 | 19:39 | APA2 | Urban | Asset Failure | Distribution substation | 2 | 154 | 0.00041099 | 2.6688e-06 | No
2019-10-17 | 7:38 | M388 | Urban | Asset Failure | Distribution substation | 20 | 47.35 | 0.0012637 | 2.6688e-05 | No
2019-10-17 | 9:16 | A098 | Short rural | Third Party | Other | 5 | 182.6 | 0.0030036 | 1.6449e-05 | No
2019-10-17 | 9:56 | 4873 | Urban | Unknown | Unknown | 6 | 141 | 0.0011289 | 8.0064e-06 | No
2019-10-17 | 10:32 | S735 | Short rural | Other | Isolation Request by EE | 15 | 32 | 0.0015791 | 4.9348e-05 | No
2019-10-17 | 12:36 | MR2225 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2860 | 46 | 0.17555 | 0.0038164 | No
2019-10-17 | 13:07 | J489 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1602 | 109.8802 | 0.23489 | 0.0021377 | No
2019-10-17 | 13:07 | J491 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1607 | 109.8802 | 0.23562 | 0.0021444 | No
2019-10-17 | 13:07 | J492 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1528 | 109.8802 | 0.22404 | 0.002039 | No
2019-10-17 | 13:07 | J493 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 804 | 109.8802 | 0.11789 | 0.0010729 | No
2019-10-17 | 13:07 | J495 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1587 | 109.8802 | 0.57369 | 0.005221 | No
2019-10-17 | 13:07 | J496 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 919 | 109.8802 | 0.13475 | 0.0012263 | No
2019-10-17 | 13:07 | J497 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1021 | 109.8802 | 0.36908 | 0.003359 | No
2019-10-17 | 13:07 | J499 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1305 | 109.8802 | 0.19134 | 0.0017414 | No
2019-10-17 | 13:07 | J500 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 760 | 109.8802 | 0.11143 | 0.0010141 | No
2019-10-17 | 13:07 | J502 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 785 | 109.8802 | 0.1151 | 0.0010475 | No
2019-10-17 | 13:07 | J503 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 987 | 109.8802 | 0.14472 | 0.0013171 | No
2019-10-17 | 13:07 | J504 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1230 | 109.8802 | 0.18035 | 0.0016413 | No
2019-10-17 | 13:09 | L582 | Short rural | Asset Failure | LV | 24 | 137.6667 | 0.01087 | 7.8957e-05 | No
2019-10-17 | 13:24 | CD1234 | Short rural | Weather |  | 527 | 155.1461 | 0.26899 | 0.0017338 | No
2019-10-17 | 13:25 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 651 | 277.1951 | 0.59367 | 0.0021417 | No
2019-10-17 | 13:29 | CT1265 | Urban | Unknown | Unknown | 1 | 250 | 0.0003336 | 1.3344e-06 | No
2019-10-17 | 13:34 | J495 | Short rural | Asset Failure | Distribution substation | 36 | 533 | 0.063126 | 0.00011844 | No
2019-10-17 | 14:18 | WWC2 | Short rural | Asset Failure | HV | 1770 | 24.2836 | 0.1414 | 0.0058231 | No
2019-10-17 | 14:47 | BDA2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 31 | 121 | 0.01234 | 0.00010199 | No
2019-10-17 | 15:07 | CN1243 | Urban | Unknown | Unknown | 9 | 229 | 0.0027502 | 1.201e-05 | No
2019-10-17 | 15:10 | RW1218 | Short rural | Weather |  | 21 | 41.0952 | 0.0028392 | 6.9087e-05 | No
2019-10-17 | 15:16 | 35818 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1506 | 177.8433 | 0.88113 | 0.0049545 | No
2019-10-17 | 15:25 | 27454 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 425 | 44 | 0.06152 | 0.0013982 | No
2019-10-17 | 15:26 | BX1232 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1285 | 35.7518 | 0.061304 | 0.0017147 | No
2019-10-17 | 15:47 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1258.7024 | 85.6304 | 0.35459 | 0.004141 | No
2019-10-17 | 15:47 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 762.2976 | 85.6304 | 0.21475 | 0.0025079 | No
2019-10-17 | 15:55 | R208 | Short rural | Weather |  | 60 | 88.55 | 0.017479 | 0.00019739 | No
2019-10-17 | 16:04 | KVA2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 15 | 201 | 0.0099189 | 4.9348e-05 | No
2019-10-17 | 16:07 | NM1258 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1003.2773 | 94.4714 | 0.12648 | 0.0013388 | No
2019-10-17 | 16:07 | HR1236 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 956.7227 | 94.4714 | 0.12061 | 0.0012766 | No
2019-10-17 | 16:14 | DS1290 | Urban | Asset Failure | Distribution substation | 24 | 175.4167 | 0.0056178 | 3.2026e-05 | No
2019-10-17 | 16:28 | BYE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 22 | 363.2273 | 0.026289 | 7.2377e-05 | No
2019-10-17 | 17:00 | MG1286 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 210 | 0.00069087 | 3.2899e-06 | No
2019-10-17 | 17:06 | 35418 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 363 | 115.8595 | 0.13836 | 0.0011942 | No
2019-10-17 | 17:13 | JS1252 | Short rural | Asset Failure | Distribution substation | 2 | 191 | 0.0012567 | 6.5797e-06 | No
2019-10-17 | 17:23 | T868 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 175 | 0.0011515 | 6.5797e-06 | No
2019-10-17 | 19:04 | 35818 | Short rural | Weather |  | 222 | 24.464 | 0.017867 | 0.00073035 | No
2019-10-17 | 19:06 | BYE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 192 | 51.6823 | 0.032645 | 0.00063165 | No
2019-10-17 | 21:10 | GL1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 53 | 1067.3208 | 0.1861 | 0.00017436 | No
2019-10-17 | 23:07 | 35824 | Short rural | Asset Failure | Distribution substation | 1 | 674 | 0.0022174 | 3.2899e-06 | No
2019-10-18 | 6:31 | H745 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 4 | 73 | 0.00096064 | 1.3159e-05 | No
2019-10-18 | 7:18 | J478 | Short rural | Asset Failure | Distribution substation | 37 | 753 | 0.091659 | 0.00012172 | No
2019-10-18 | 7:43 | C832 | Urban | Third Party | Other | 1330 | 160.694 | 0.28519 | 0.0017748 | No
2019-10-18 | 11:14 | CD1230 | Short rural | Other | Isolation Request by EE | 6 | 30 | 0.00059218 | 1.9739e-05 | No
2019-10-18 | 12:17 | CA1210 | Urban | Third Party | Other | 29 | 231 | 0.0089391 | 3.8698e-05 | No
2019-10-18 | 12:42 | B205 | Urban | Asset Failure | HV | 673 | 113.4859 | 0.10192 | 0.00089805 | No
2019-10-18 | 12:49 | J499 | Urban | Asset Failure | Distribution substation | 13 | 600 | 0.010408 | 1.7347e-05 | No
2019-10-18 | 18:06 | MM1372 | Urban | Third Party | Dig-in | 68 | 164 | 0.014881 | 9.0739e-05 | No
2019-10-18 | 18:46 | OA1207 | Short rural | Asset Failure | LV | 34 | 227.4118 | 0.025437 | 0.00011186 | No
2019-10-19 | 6:50 | FT1206 | Short rural | Animal | Animal Impact | 22 | 79 | 0.0057178 | 7.2377e-05 | No
2019-10-19 | 6:54 | BX1242 | Urban | Vegetation | Grow-in - NSP responsibility | 19 | 66.8421 | 0.0016947 | 2.5354e-05 | No
2019-10-19 | 7:06 | BYB2 | Short rural | Asset Failure | HV | 583.1279 | 75.0333 | 0.14394 | 0.0019184 | No
2019-10-19 | 7:06 | BDC2 | Short rural | Asset Failure | HV | 286.8721 | 75.0333 | 0.070814 | 0.00094377 | No
2019-10-19 | 9:54 | X217 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 117 | 0.00038491 | 3.2899e-06 | No
2019-10-19 | 10:23 | WP1245 | Urban | Unknown | Unknown | 1 | 217 | 0.00028956 | 1.3344e-06 | No
2019-10-19 | 12:58 | CN1221 | Urban | Asset Failure | Distribution substation | 32 | 129.5312 | 0.0055311 | 4.2701e-05 | No
2019-10-19 | 13:22 | CD1234 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 527 | 275.334 | 0.47736 | 0.0017338 | No
2019-10-19 | 15:24 | 57448 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 146 | 134.1712 | 0.064445 | 0.00048032 | No
2019-10-19 | 15:42 | 49341 | Urban | Other | Probable Equipment Failure | 1 | 221 | 0.0002949 | 1.3344e-06 | No
2019-10-19 | 15:55 | CD1260 | Urban | Asset Failure | Distribution substation | 32 | 94 | 0.0040139 | 4.2701e-05 | No
2019-10-19 | 16:21 | 35695 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 255 | 117.7059 | 0.098745 | 0.00083892 | No
2019-10-19 | 16:26 | BX1222 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 521 | 54.8829 | 0.038156 | 0.00069522 | No
2019-10-19 | 16:40 | 35418 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 1277.5 | 0.0084056 | 6.5797e-06 | No
2019-10-19 | 16:53 | W196 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1065 | 35.8995 | 0.051018 | 0.0014211 | No
2019-10-19 | 16:56 | BWE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 876 | 150.4053 | 0.43346 | 0.0028819 | No
2019-10-19 | 16:58 | 27454 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 428 | 172.4463 | 0.24281 | 0.0014081 | No
2019-10-19 | 17:12 | SZ1242 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 325 | 0.0021384 | 6.5797e-06 | No
2019-10-19 | 17:14 | C851 | Urban | Unknown | Unknown | 20 | 132 | 0.0035228 | 2.6688e-05 | No
2019-10-19 | 17:30 | JS1252 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 178.1818 | 0.0064481 | 3.6188e-05 | No
2019-10-19 | 18:30 | 35990 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 11 | 146 | 0.0052835 | 3.6188e-05 | No
2019-10-19 | 19:22 | 1962 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 79 | 108 | 0.011385 | 0.00010542 | No
2019-10-20 | 5:17 | A046 | Short rural | Unknown | Unknown | 1 | 87 | 0.00028622 | 3.2899e-06 | No
2019-10-20 | 5:19 | MR2206 | Urban | Asset Failure | Distribution substation | 10 | 701 | 0.0093541 | 1.3344e-05 | No
2019-10-20 | 7:25 | CD1234 | Short rural | Animal | Animal Impact | 6 | 92 | 0.001816 | 1.9739e-05 | No
2019-10-20 | 11:30 | P608 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 38.4286 | 0.00088497 | 2.3029e-05 | No
2019-10-20 | 23:10 | 9033 | Urban | Asset Failure | Distribution substation | 1 | 245 | 0.00032693 | 1.3344e-06 | No
2019-10-21 | 11:52 | CA1210 | Urban | Third Party | Other | 30 | 106 | 0.0042434 | 4.0032e-05 | No
2019-10-21 | 16:20 | RBB2 | Short rural | Asset Failure | HV | 7 | 89.2857 | 0.0020562 | 2.3029e-05 | No
2019-10-22 | 7:12 | R293 | Short rural | Asset Failure | Distribution substation | 3 | 192 | 0.001895 | 9.8696e-06 | No
2019-10-22 | 10:49 | 19870 | Urban | Asset Failure | LV | 5 | 13 | 8.6736e-05 | 6.672e-06 | No
2019-10-22 | 13:41 | GG1269 | Short rural | Asset Failure | Distribution substation | 8 | 158 | 0.0041584 | 2.6319e-05 | No
2019-10-22 | 13:46 | 1950 | Urban | Third Party | Vehicle impact | 17 | 555.5882 | 0.012603 | 2.2685e-05 | No
2019-10-22 | 14:18 | CLC2 | Short rural | Asset Failure | Distribution substation | 72 | 127.1389 | 0.030115 | 0.00023687 | No
2019-10-22 | 14:53 | 55870 | Urban | Asset Failure | LV | 838 | 42.0823 | 0.047058 | 0.0011182 | No
2019-10-23 | 1:23 | WRD2 | Urban | Asset Failure | Distribution substation | 10 | 332 | 0.0044302 | 1.3344e-05 | No
2019-10-23 | 4:09 | WQ1219 | Urban | Asset Failure | LV | 26 | 64.3462 | 0.0022324 | 3.4694e-05 | No
2019-10-23 | 6:07 | SY1352 | Urban | Other | Fault within LV customers installation - Defective Equipment | 1 | 295 | 0.00039365 | 1.3344e-06 | No
2019-10-23 | 7:36 | FT1205 | Short rural | Asset Failure | Distribution substation | 41 | 222 | 0.029944 | 0.00013488 | No
2019-10-23 | 9:25 | ER1262 | Short rural | Unknown | Unknown | 1 | 87 | 0.00028622 | 3.2899e-06 | No
2019-10-23 | 10:36 | NL1172 | Urban | Third Party | Other | 18 | 204.5556 | 0.0049133 | 2.4019e-05 | No
2019-10-23 | 11:50 | PH1293 | Urban | Asset Failure | Distribution substation | 25 | 280.84 | 0.0093688 | 3.336e-05 | No
2019-10-23 | 14:23 | APF2 | Short rural | Third Party | Dig-in | 31 | 143 | 0.014584 | 0.00010199 | No
2019-10-23 | 15:50 | 2810 | Urban | Third Party | Other | 61 | 137.2459 | 0.011172 | 8.1398e-05 | No
2019-10-23 | 17:19 | APF2 | Short rural | Third Party | Dig-in | 31 | 88 | 0.0089747 | 0.00010199 | No
2019-10-24 | 2:06 | C855 | Short rural | Unknown | Unknown | 33 | 67 | 0.0072739 | 0.00010857 | No
2019-10-24 | 9:38 | S738 | Short rural | Other | Isolation Request by EE | 13.5965 | 5 | 0.00022365 | 4.4731e-05 | No
2019-10-24 | 9:38 | GL1255 | Short rural | Other | Isolation Request by EE | 13.4035 | 5 | 0.00022048 | 4.4096e-05 | No
2019-10-24 | 10:56 | OA1233 | Short rural | Other | Isolation Request by EE | 5 | 23 | 0.00037833 | 1.6449e-05 | No
2019-10-24 | 16:14 | F601 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1410 | 171.0504 | 0.32183 | 0.0018815 | No
2019-10-24 | 17:06 | A045 | Short rural | Weather |  | 16 | 65 | 0.0034215 | 5.2638e-05 | No
2019-10-24 | 22:04 | 68188 | Urban | Third Party | Other | 41 | 144 | 0.0078783 | 5.471e-05 | No
2019-10-25 | 8:08 | BWH2 | Short rural | Unknown | Unknown | 1 | 320 | 0.0010528 | 3.2899e-06 | No
2019-10-25 | 9:21 | H745 | Short rural | Third Party | Unauthorised access | 3 | 188 | 0.0018555 | 9.8696e-06 | No
2019-10-25 | 9:34 | RBA2 | Short rural | Animal | Animal Impact | 2 | 162 | 0.0010659 | 6.5797e-06 | No
2019-10-25 | 11:49 | NN1233 | Short rural | Other | Isolation Request by EE | 5 | 10 | 0.00016449 | 1.6449e-05 | No
2019-10-25 | 12:10 | 87222 | Long rural | Unknown | Unknown | 22 | 131.3636 | 9.2038 | 0.070064 | No
2019-10-25 | 14:27 | CT1265 | Urban | Third Party | Vehicle impact | 1104 | 56.1413 | 0.082706 | 0.0014732 | No
2019-10-25 | 14:44 | 35816 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 56 | 129 | 0.023766 | 0.00018423 | No
2019-10-25 | 15:06 | BK1251 | Short rural | Unknown | Unknown | 1 | 61 | 0.00020068 | 3.2899e-06 | No
2019-10-25 | 20:03 | 55867 | Urban | Asset Failure | Distribution substation | 1 | 84 | 0.00011209 | 1.3344e-06 | No
2019-10-25 | 23:30 | L940 | Short rural | Asset Failure | Distribution substation | 10 | 741 | 0.024378 | 3.2899e-05 | No
2019-10-26 | 4:15 | NN1233 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 448 | 510.4263 | 0.7523 | 0.0014739 | No
2019-10-26 | 4:18 | CD1234 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 527 | 208.074 | 0.36075 | 0.0017338 | No
2019-10-26 | 4:18 | A095 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 370 | 236.4973 | 0.28788 | 0.0012172 | No
2019-10-26 | 4:34 | DS1204 | Urban | Animal | Animal Impact | 30 | 177 | 0.0070857 | 4.0032e-05 | No
2019-10-26 | 6:32 | T842 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 314 | 0.001033 | 3.2899e-06 | No
2019-10-26 | 6:50 | SWC2 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 103 | 57 | 0.0078343 | 0.00013744 | No
2019-10-26 | 6:59 | J513 | Urban | Unknown | Unknown | 51 | 337.2941 | 0.022954 | 6.8054e-05 | No
2019-10-26 | 8:27 | B776 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 24 | 65 | 0.0020817 | 3.2026e-05 | No
2019-10-26 | 9:35 | 8798 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 421 | 0.0096952 | 2.3029e-05 | No
2019-10-26 | 10:40 | GG1232 | Short rural | Asset Failure | LV | 12 | 37 | 0.0014607 | 3.9478e-05 | No
2019-10-26 | 11:23 | L940 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 51 | 56 | 0.0093958 | 0.00016778 | No
2019-10-26 | 12:28 | 27454 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 426 | 323.8286 | 0.45384 | 0.0014015 | No
2019-10-26 | 12:45 | 9052 | Urban | Weather |  | 54 | 273 | 0.019672 | 7.2058e-05 | No
2019-10-26 | 13:05 | 49916 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 731.892 | 107 | 0.1045 | 0.00097664 | No
2019-10-26 | 13:05 | 49918 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 978.108 | 107 | 0.13965 | 0.0013052 | No
2019-10-26 | 13:16 | KVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 210 | 92.1429 | 0.063659 | 0.00069087 | No
2019-10-26 | 13:19 | D814 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 288 | 305.7222 | 0.28967 | 0.00094748 | No
2019-10-26 | 13:20 | L940 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 21 | 835 | 0.057688 | 6.9087e-05 | No
2019-10-26 | 13:21 | CD1234 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 526 | 104.135 | 0.1802 | 0.0017305 | No
2019-10-26 | 14:12 | T842 | Short rural | Weather |  | 4 | 169.25 | 0.0022272 | 1.3159e-05 | No
2019-10-26 | 14:54 | 35333 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 69 | 215.3188 | 0.019825 | 9.2074e-05 | No
2019-10-26 | 15:12 | L947 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 102 | 86 | 0.028859 | 0.00033557 | No
2019-10-26 | 15:14 | RW1292 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 4 | 92 | 0.0012107 | 1.3159e-05 | No
2019-10-26 | 15:15 | SC1238 | Urban | Weather |  | 14 | 115 | 0.0021484 | 1.8682e-05 | No
2019-10-26 | 16:28 | ULL2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1573 | 42.2422 | 0.2186 | 0.005175 | No
2019-10-26 | 16:34 | 9056 | Urban | Asset Failure | Distribution substation | 33 | 451 | 0.01986 | 4.4035e-05 | No
2019-10-26 | 16:45 | MVD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 16 | 24 | 0.0012633 | 5.2638e-05 | No
2019-10-26 | 16:45 | BX1232 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1284 | 132 | 0.22616 | 0.0017134 | No
2019-10-26 | 18:14 | 8801 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 198 | 0.0013028 | 6.5797e-06 | No
2019-10-26 | 18:41 | RBC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 503 | 154.9026 | 0.25633 | 0.0016548 | No
2019-10-26 | 18:57 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 29 | 604 | 0.057625 | 9.5406e-05 | No
2019-10-26 | 19:01 | BYC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 81 | 349 | 0.093001 | 0.00026648 | No
2019-10-27 | 9:47 | T842 | Short rural | Other | Isolation Request by EE | 2 | 74 | 0.0004869 | 6.5797e-06 | No
2019-10-27 | 11:28 | MR2232 | Short rural | Unknown | Unknown | 3 | 83 | 0.00081918 | 9.8696e-06 | No
2019-10-27 | 11:42 | T841 | Short rural | Asset Failure | Distribution substation | 12 | 120 | 0.0047374 | 3.9478e-05 | No
2019-10-27 | 11:46 | RW1281 | Short rural | Unknown | Unknown | 1 | 152 | 0.00050006 | 3.2899e-06 | No
2019-10-27 | 20:37 | BWA2 | Short rural | Animal | Animal Impact | 1518 | 118.1831 | 0.59021 | 0.004994 | No
2019-10-27 | 20:51 | A051 | Urban | Animal | Animal Impact | 15 | 89.7333 | 0.0017961 | 2.0016e-05 | No
2019-10-28 | 1:19 | SC1271 | Urban | Third Party | Vehicle impact | 7 | 198 | 0.0018495 | 9.3408e-06 | No
2019-10-28 | 5:37 | NM1221 | Urban | Animal | Animal Impact | 51 | 147 | 0.010004 | 6.8054e-05 | No
2019-10-28 | 7:09 | J503 | Urban | Asset Failure | Distribution substation | 19 | 36.1053 | 0.0009154 | 2.5354e-05 | No
2019-10-28 | 8:12 | X482 | Short rural | Unknown | Unknown | 7 | 34 | 0.00078299 | 2.3029e-05 | No
2019-10-28 | 9:32 | NA1225 | Short rural | Unknown | Unknown | 3 | 330 | 0.003257 | 9.8696e-06 | No
2019-10-28 | 10:57 | LP1312 | Urban | Unknown | Unknown | 58 | 166 | 0.012848 | 7.7395e-05 | No
2019-10-28 | 13:53 | MM1362 | Urban | Asset Failure | Distribution substation | 46 | 54 | 0.0033146 | 6.1382e-05 | No
2019-10-28 | 14:24 | OP1112 | Short rural | Unknown | Unknown | 5 | 171 | 0.0028128 | 1.6449e-05 | No
2019-10-28 | 14:32 | GG1269 | Short rural | Asset Failure | Distribution substation | 1 | 1217 | 0.0040038 | 3.2899e-06 | No
2019-10-28 | 15:08 | J497 | Short rural | Unknown | Unknown | 6 | 147 | 0.0029017 | 1.9739e-05 | No
2019-10-28 | 16:51 | 25781 | Urban | Asset Failure | Distribution substation | 1 | 589 | 0.00078596 | 1.3344e-06 | No
2019-10-28 | 16:54 | 17061 | Urban | Asset Failure | Distribution substation | 25 | 244.2 | 0.0081465 | 3.336e-05 | No
2019-10-28 | 21:03 | W127 | Short rural | Vegetation | Grow-in - NSP responsibility | 407 | 95.6511 | 0.12807 | 0.001339 | No
2019-10-28 | 21:08 | W127 | Short rural | Vegetation | Grow-in - NSP responsibility | 407 | 13.0025 | 0.01741 | 0.001339 | No
2019-10-28 | 23:15 | 35333 | Urban | Unknown | Unknown | 990 | 78.0909 | 0.10316 | 0.0013211 | No
2019-10-29 | 7:32 | 8799 | Short rural | Vegetation | Grow-in - NSP responsibility | 29 | 478 | 0.045604 | 9.5406e-05 | No
2019-10-29 | 7:36 | W123 | Short rural | Unknown | Unknown | 1 | 320 | 0.0010528 | 3.2899e-06 | No
2019-10-29 | 8:03 | A046 | Short rural | Asset Failure | LV | 2 | 160 | 0.0010528 | 6.5797e-06 | No
2019-10-29 | 8:06 | B798 | Urban | Network business | Network error | 4.6548 | 5 | 3.1057e-05 | 6.2114e-06 | No
2019-10-29 | 8:06 | CJ1286 | Urban | Network business | Network error | 213.3452 | 5 | 0.0014234 | 0.00028469 | No
2019-10-29 | 8:22 | BGA2 | Short rural | Asset Failure | LV | 28 | 130.7143 | 0.012041 | 9.2116e-05 | No
2019-10-29 | 9:00 | S788 | Short rural | Third Party | Vehicle impact | 10 | 1209.3 | 0.039784 | 3.2899e-05 | No
2019-10-29 | 9:29 | GG1295 | Short rural | Asset Failure | Distribution substation | 1 | 73 | 0.00024016 | 3.2899e-06 | No
2019-10-29 | 13:12 | BX1352 | Urban | Unknown | Unknown | 26 | 78 | 0.0027062 | 3.4694e-05 | No
2019-10-29 | 16:53 | A324 | Urban | Third Party | Other | 105 | 154.2952 | 0.021619 | 0.00014011 | No
2019-10-29 | 21:00 | 10290 | Short rural | Asset Failure | HV | 356 | 91.4916 | 0.10715 | 0.0011712 | No
2019-10-29 | 21:33 | BGA2 | Short rural | Asset Failure | Distribution substation | 6 | 120 | 0.0023687 | 1.9739e-05 | No
2019-10-29 | 22:54 | MR2232 | Short rural | Unknown | Unknown | 176 | 161 | 0.093222 | 0.00057902 | No
2019-10-29 | 23:15 | BDC2 | Short rural | Unknown | Unknown | 7 | 151 | 0.0034774 | 2.3029e-05 | No
2019-10-30 | 9:56 | TM1284 | Short rural | Vegetation | Grow-in - NSP responsibility | 324 | 6 | 0.0063955 | 0.0010659 | No
2019-10-30 | 11:13 | X881 | Short rural | Unknown | Unknown | 102 | 93.2647 | 0.031296 | 0.00033557 | No
2019-10-30 | 13:51 | H745 | Short rural | Vegetation | Grow-in - NSP responsibility | 8 | 48.375 | 0.0012732 | 2.6319e-05 | No
2019-10-30 | 16:53 | HR1276 | Urban | Third Party | Vehicle impact | 31 | 63.5484 | 0.0026288 | 4.1366e-05 | No
2019-10-30 | 19:28 | L940 | Short rural | Asset Failure | HV | 148 | 71.4797 | 0.034803 | 0.0004869 | No
2019-10-30 | 20:04 | 48203 | Urban | Asset Failure | Distribution substation | 132 | 140.0455 | 0.024668 | 0.00017614 | No
2019-10-31 | 5:49 | MM1202 | Urban | Asset Failure | Distribution substation | 18 | 757 | 0.018183 | 2.4019e-05 | No
2019-10-31 | 9:09 | X482 | Short rural | Network business | Switching or protection error | 40 | 9 | 0.0011844 | 0.00013159 | No
2019-10-31 | 18:05 | 55888 | Urban | Unknown | Unknown | 26 | 47 | 0.0016306 | 3.4694e-05 | No
2019-10-31 | 19:11 | 8802 | Short rural | Unknown | Unknown | 10 | 127 | 0.0041781 | 3.2899e-05 | No
2019-10-31 | 19:56 | 87220 | Short rural | Unknown | Unknown | 29 | 98 | 0.0093498 | 9.5406e-05 | No
2019-10-31 | 22:39 | 17058 | Urban | Third Party | Vehicle impact | 29 | 5 | 0.00019349 | 3.8698e-05 | No
2019-11-01 | 10:33 | TM1210 | Short rural | Other | Isolation Request by EE | 1 | 38 | 0.00012501 | 3.2899e-06 | No
2019-11-01 | 15:52 | SN1282 | Short rural | Third Party | Dig-in | 62 | 157.4032 | 0.032106 | 0.00020397 | No
2019-11-01 | 17:08 | 8686 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1392 | 76.4325 | 0.35002 | 0.0045795 | No
2019-11-01 | 17:14 | BK1288 | Short rural | Asset Failure | Distribution substation | 1 | 114 | 0.00037504 | 3.2899e-06 | No
2019-11-01 | 17:16 | 8648 | Urban | Unknown | Unknown | 2 | 179 | 0.00047771 | 2.6688e-06 | No
2019-11-02 | 14:33 | W164 | Short rural | Asset Failure | HV | 2 | 84 | 0.0005527 | 6.5797e-06 | No
2019-11-03 | 0:12 | ER1232 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 42 | 108 | 0.014923 | 0.00013817 | No
2019-11-03 | 6:52 | 8734 | Urban | Vegetation | Grow-in - NSP responsibility | 732 | 48 | 0.046885 | 0.00097678 | No
2019-11-03 | 7:37 | RW1292 | Short rural | Unknown | Unknown | 13 | 88 | 0.0037636 | 4.2768e-05 | No
2019-11-03 | 10:49 | NK1352 | Urban | Asset Failure | HV | 882 | 130.0998 | 0.15312 | 0.0011769 | No
2019-11-03 | 10:49 | NK1322 | Urban | Network business | Switching or protection error | 2 | 100.9924 | 0.00026953 | 2.6688e-06 | No
2019-11-03 | 10:49 | NK1342 | Urban | Network business | Switching or protection error | 2105 | 100.9924 | 0.28368 | 0.0028089 | No
2019-11-03 | 10:49 | NK1362 | Urban | Network business | Switching or protection error | 8 | 100.9924 | 0.0010781 | 1.0675e-05 | No
2019-11-03 | 13:07 | PH1264 | Urban | Other | Probable Equipment Failure | 279 | 53.7025 | 0.019993 | 0.0003723 | No
2019-11-03 | 16:12 | C811 | Urban | Third Party | Vehicle impact | 21 | 189 | 0.0052962 | 2.8022e-05 | No
2019-11-03 | 16:42 | T842 | Short rural | Asset Failure | Distribution substation | 1 | 191 | 0.00062836 | 3.2899e-06 | No
2019-11-03 | 16:44 | L591 | Short rural | Asset Failure | Distribution substation | 1 | 81 | 0.00026648 | 3.2899e-06 | No
2019-11-03 | 16:57 | CR1254 | Urban | Weather |  | 814.0432 | 54.2044 | 0.05888 | 0.0010863 | No
2019-11-03 | 16:57 | CR1214 | Urban | Weather |  | 721.9568 | 54.2044 | 0.052219 | 0.00096338 | No
2019-11-03 | 17:49 | MG1234 | Short rural | Asset Failure | Distribution substation | 1 | 517 | 0.0017009 | 3.2899e-06 | No
2019-11-03 | 19:04 | KVB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 80 | 0.0013159 | 1.6449e-05 | No
2019-11-03 | 20:31 | C832 | Urban | Asset Failure | Distribution substation | 11 | 250 | 0.0036696 | 1.4678e-05 | No
2019-11-03 | 21:57 | 68179 | Urban | Asset Failure | Distribution substation | 24 | 168 | 0.0053803 | 3.2026e-05 | No
2019-11-03 | 22:51 | 2809 | Urban | Vegetation | Grow-in - NSP responsibility | 614 | 11 | 0.0090125 | 0.00081932 | No
2019-11-03 | 22:57 | CX1206 | Short rural | Vegetation | Grow-in - NSP responsibility | 112 | 74 | 0.027266 | 0.00036846 | No
2019-11-03 | 23:02 | 7966 | Urban | Unknown | Unknown | 40 | 61 | 0.0032559 | 5.3376e-05 | No
2019-11-03 | 23:27 | 8780 | Urban | Unknown | Unknown | 6 | 615 | 0.0049239 | 8.0064e-06 | No
2019-11-04 | 0:51 | 7966 | Urban | Other | Probable Equipment Failure | 60 | 15 | 0.001201 | 8.0064e-05 | No
2019-11-04 | 6:18 | 35816 | Short rural | Unknown | Unknown | 4 | 191 | 0.0025135 | 1.3159e-05 | No
2019-11-04 | 7:40 | X877 | Short rural | Asset Failure | Distribution substation | 1 | 477 | 0.0015693 | 3.2899e-06 | No
2019-11-04 | 8:07 | KC1288 | Short rural | Asset Failure | Distribution substation | 2 | 332 | 0.0021845 | 6.5797e-06 | No
2019-11-04 | 8:57 | FF1239 | Urban | Third Party | Other | 40 | 151 | 0.0080598 | 5.3376e-05 | No
2019-11-04 | 9:31 | MVB2 | Short rural | Asset Failure | Distribution substation | 1 | 395 | 0.0012995 | 3.2899e-06 | No
2019-11-04 | 9:52 | BGA2 | Short rural | Asset Failure | Distribution substation | 1 | 126 | 0.00041452 | 3.2899e-06 | No
2019-11-04 | 10:04 | C889 | Urban | Asset Failure | Distribution substation | 72 | 445 | 0.042754 | 9.6077e-05 | No
2019-11-04 | 13:46 | 8780 | Urban | Asset Failure | Distribution substation | 18 | 135.8889 | 0.0032639 | 2.4019e-05 | No
2019-11-04 | 15:08 | GV1245 | Urban | Third Party | Other | 19 | 403 | 0.010217 | 2.5354e-05 | No
2019-11-04 | 17:04 | 6430 | Urban | Asset Failure | Distribution substation | 1 | 101 | 0.00013477 | 1.3344e-06 | No
2019-11-04 | 17:37 | T868 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 75.75 | 0.00099683 | 1.3159e-05 | No
2019-11-05 | 6:00 | CD1234 | Short rural | Asset Failure | LV | 16 | 102.375 | 0.0053888 | 5.2638e-05 | No
2019-11-05 | 9:13 | F602 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 21 | 121 | 0.0033907 | 2.8022e-05 | No
2019-11-05 | 14:03 | NN1233 | Short rural | Unknown | Unknown | 1 | 119 | 0.00039149 | 3.2899e-06 | No
2019-11-05 | 14:47 | KC1262 | Short rural | Third Party | Other | 117 | 124.0342 | 0.047742 | 0.00038491 | No
2019-11-05 | 22:05 | J483 | Urban | Asset Failure | Distribution substation | 26 | 481 | 0.016688 | 3.4694e-05 | No
2019-11-06 | 6:13 | J483 | Urban | Asset Failure | Distribution substation | 26 | 527 | 0.018284 | 3.4694e-05 | No
2019-11-06 | 8:59 | NK1342 | Urban | Vegetation | Grow-in - NSP responsibility | 1626.8635 | 38 | 0.082494 | 0.0021709 | No
2019-11-06 | 8:59 | NK1352 | Urban | Vegetation | Grow-in - NSP responsibility | 681.6597 | 38 | 0.034565 | 0.00090961 | No
2019-11-06 | 8:59 | NM1221 | Urban | Vegetation | Grow-in - NSP responsibility | 675.4768 | 38 | 0.034252 | 0.00090136 | No
2019-11-06 | 15:21 | L503 | Urban | Asset Failure | Distribution substation | 2 | 1811 | 0.0048332 | 2.6688e-06 | No
2019-11-06 | 19:33 | KC1221 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 17 | 15 | 0.00083892 | 5.5928e-05 | No
2019-11-06 | 20:41 | NN1233 | Short rural | Asset Failure | HV | 8 | 147.125 | 0.0038722 | 2.6319e-05 | No
2019-11-07 | 4:28 | W124 | Short rural | Unknown | Unknown | 1136 | 117.2632 | 0.43825 | 0.0037373 | No
2019-11-07 | 5:27 | W127 | Short rural | Weather |  | 407 | 157 | 0.21022 | 0.001339 | No
2019-11-07 | 5:30 | MYE2 | Short rural | Unknown | Unknown | 415 | 75.2843 | 0.10279 | 0.0013653 | No
2019-11-07 | 6:01 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 21 | 412.7143 | 0.028513 | 6.9087e-05 | No
2019-11-07 | 6:41 | NA1270 | Short rural | Unknown | Unknown | 9 | 164 | 0.0048558 | 2.9609e-05 | No
2019-11-07 | 7:23 | L591 | Short rural | Asset Failure | Distribution substation | 3 | 257 | 0.0025365 | 9.8696e-06 | No
2019-11-07 | 7:42 | OP1122 | Short rural | Unknown | Unknown | 1 | 231 | 0.00075996 | 3.2899e-06 | No
2019-11-07 | 8:03 | WWC2 | Short rural | Asset Failure | Distribution substation | 1 | 58 | 0.00019081 | 3.2899e-06 | No
2019-11-07 | 9:10 | 10244 | Short rural | Third Party | Vehicle impact | 962 | 88.8295 | 0.28113 | 0.0031648 | No
2019-11-07 | 10:16 | WD1221 | Short rural | Animal | Animal Impact | 6 | 147 | 0.0029017 | 1.9739e-05 | No
2019-11-07 | 10:43 | 87222 | Long rural | Unknown | Unknown | 209 | 116.3636 | 77.4522 | 0.66561 | No
2019-11-07 | 11:09 | CD1297 | Urban | Asset Failure | Distribution substation | 66 | 195 | 0.017174 | 8.807e-05 | No
2019-11-07 | 12:09 | 87222 | Long rural | Unknown | Unknown | 22 | 334.5909 | 23.4427 | 0.070064 | No
2019-11-07 | 13:52 | RBC2 | Short rural | Other | Probable Equipment Failure | 2 | 292 | 0.0019213 | 6.5797e-06 | No
2019-11-07 | 15:20 | S786 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 582.8358 | 102.3703 | 0.19629 | 0.0019175 | No
2019-11-07 | 15:20 | S788 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 716.1642 | 102.3703 | 0.24119 | 0.0023561 | No
2019-11-07 | 16:42 | 8801 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 198 | 0.0013028 | 6.5797e-06 | No
2019-11-08 | 3:24 | BGA2 | Short rural | Asset Failure | Distribution substation | 16 | 269 | 0.01416 | 5.2638e-05 | No
2019-11-08 | 6:27 | 49917 | Urban | Third Party | Other | 318.7187 | 134.9861 | 0.057409 | 0.0004253 | No
2019-11-08 | 6:27 | 68190 | Urban | Third Party | Other | 327.2813 | 134.9861 | 0.058952 | 0.00043672 | No
2019-11-08 | 7:14 | BYC2 | Short rural | Other | Probable Animals | 3 | 116 | 0.0011449 | 9.8696e-06 | No
2019-11-08 | 9:41 | BK1236 | Short rural | Vegetation | Grow-in - NSP responsibility | 33 | 468 | 0.050809 | 0.00010857 | No
2019-11-08 | 11:34 | S768 | Urban | Asset Failure | Distribution substation | 15 | 47 | 0.00094075 | 2.0016e-05 | No
2019-11-08 | 12:02 | SG1220 | Urban | Unknown | Unknown | 117 | 78 | 0.012178 | 0.00015612 | No
2019-11-08 | 12:40 | S786 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 582.8358 | 54.0454 | 0.10363 | 0.0019175 | No
2019-11-08 | 12:40 | S788 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 716.1642 | 54.0454 | 0.12734 | 0.0023561 | No
2019-11-08 | 13:58 | S786 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 123 | 0.001214 | 9.8696e-06 | No
2019-11-08 | 15:22 | 9059 | Urban | Unknown | Unknown | 18 | 87 | 0.0020897 | 2.4019e-05 | No
2019-11-08 | 16:00 | LL1212 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 67 | 125 | 0.011176 | 8.9405e-05 | No
2019-11-08 | 16:35 | TM1210 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 496 | 40.1673 | 0.065544 | 0.0016318 | No
2019-11-08 | 16:58 | HKD2 | Short rural | Asset Failure | Distribution substation | 6 | 97.5 | 0.0019246 | 1.9739e-05 | No
2019-11-08 | 17:19 | PK1262 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 75 | 133 | 0.032816 | 0.00024674 | No
2019-11-08 | 17:29 | TM1284 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 839 | 61 | 0.16837 | 0.0027602 | No
2019-11-09 | 6:53 | DP1236 | Short rural | Animal | Animal Impact | 2396 | 32.9971 | 0.2601 | 0.0078825 | No
2019-11-09 | 18:06 | J504 | Urban | Third Party | Vehicle impact | 119 | 639 | 0.10147 | 0.00015879 | No
2019-11-09 | 18:09 | BWF2 | Short rural | Asset Failure | Distribution substation | 1 | 98 | 0.00032241 | 3.2899e-06 | No
2019-11-09 | 20:03 | HKF2 | Short rural | Other | Probable Overload | 31 | 112 | 0.011422 | 0.00010199 | No
2019-11-09 | 20:22 | APD2 | Short rural | Asset Failure | Distribution substation | 2 | 79 | 0.0005198 | 6.5797e-06 | No
2019-11-10 | 2:39 | WWC2 | Short rural | Animal | Animal Impact | 29 | 212 | 0.020226 | 9.5406e-05 | No
2019-11-10 | 7:06 | WL1292 | Urban | Asset Failure | Distribution substation | 1 | 271 | 0.00036162 | 1.3344e-06 | No
2019-11-10 | 12:53 | 25775 | Urban | Asset Failure | Distribution substation | 1 | 76 | 0.00010141 | 1.3344e-06 | No
2019-11-10 | 16:01 | CX1232 | Short rural | Asset Failure | Distribution substation | 1 | 119 | 0.00039149 | 3.2899e-06 | No
2019-11-10 | 16:24 | KMB2 | Short rural | Asset Failure | Distribution substation | 4 | 115 | 0.0015133 | 1.3159e-05 | No
2019-11-11 | 5:31 | L584 | Short rural | Asset Failure | HV | 397 | 265.0151 | 0.34613 | 0.0013061 | No
2019-11-11 | 7:17 | WWB2 | Short rural | Asset Failure | Distribution substation | 27 | 208 | 0.018476 | 8.8826e-05 | No
2019-11-11 | 13:37 | CX1210 | Short rural | Vegetation | Grow-in - NSP responsibility | 10 | 15 | 0.00049348 | 3.2899e-05 | No
2019-11-11 | 15:40 | 25773 | Urban | Asset Failure | Zone substation | 774.3163 | 174.9297 | 0.18075 | 0.0010332 | No
2019-11-11 | 15:40 | 25774 | Urban | Asset Failure | Zone substation | 1731.7074 | 174.9297 | 0.40423 | 0.0023108 | No
2019-11-11 | 15:40 | 25775 | Urban | Asset Failure | Zone substation | 1078.4405 | 174.9297 | 0.25174 | 0.0014391 | No
2019-11-11 | 15:40 | 25776 | Urban | Asset Failure | Zone substation | 2.0008 | 174.9297 | 0.00046704 | 2.6699e-06 | No
2019-11-11 | 15:40 | 25777 | Urban | Asset Failure | Zone substation | 1309.5349 | 174.9297 | 0.30568 | 0.0017474 | No
2019-11-11 | 15:40 | 25780 | Urban | Vegetation | Grow-in - NSP responsibility | 1683 | 179 | 0.402 | 0.0022458 | No
2019-11-11 | 21:01 | 25739 | Short rural | Asset Failure | Distribution substation | 1 | 59 | 0.0001941 | 3.2899e-06 | No
2019-11-12 | 8:44 | HBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 25 | 0.00057573 | 2.3029e-05 | No
2019-11-12 | 12:49 | RW1281 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 49 | 161 | 0.025954 | 0.0001612 | No
2019-11-12 | 12:54 | 828 | Short rural | Unknown | Unknown | 2 | 226 | 0.001487 | 6.5797e-06 | No
2019-11-12 | 13:41 | L946 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 158 | 0.0036386 | 2.3029e-05 | No
2019-11-12 | 14:21 | JBA2 | Short rural | Weather |  | 2 | 14 | 9.2116e-05 | 6.5797e-06 | No
2019-11-12 | 14:40 | JS1252 | Short rural | Third Party | Other | 3 | 148 | 0.0014607 | 9.8696e-06 | No
2019-11-12 | 14:57 | BWH2 | Short rural | Unknown | Unknown | 50 | 264 | 0.043426 | 0.00016449 | No
2019-11-12 | 15:16 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 42 | 87.5714 | 0.0121 | 0.00013817 | No
2019-11-12 | 15:21 | H745 | Short rural | Weather |  | 1 | 91 | 0.00029938 | 3.2899e-06 | No
2019-11-12 | 15:29 | BK1299 | Short rural | Weather |  | 20 | 246 | 0.016186 | 6.5797e-05 | No
2019-11-12 | 15:32 | R211 | Short rural | Vegetation | Grow-in - NSP responsibility | 263 | 93 | 0.080467 | 0.00086523 | No
2019-11-12 | 15:38 | 9032 | Short rural | Vegetation | Grow-in - NSP responsibility | 711 | 50.0872 | 0.11716 | 0.0023391 | No
2019-11-12 | 15:42 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 20 | 285.15 | 0.018762 | 6.5797e-05 | No
2019-11-12 | 16:20 | KC1288 | Short rural | Asset Failure | HV | 138 | 201.2391 | 0.091363 | 0.000454 | No
2019-11-12 | 16:29 | CLB2 | Short rural | Other | Isolation Request by EE | 62 | 43 | 0.0087708 | 0.00020397 | No
2019-11-12 | 16:56 | CS1239 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 77 | 0.00025332 | 3.2899e-06 | No
2019-11-12 | 17:59 | 2812 | Urban | Asset Failure | HV | 1498 | 174.3024 | 0.34842 | 0.0019989 | No
2019-11-12 | 18:13 | C854 | Urban | Asset Failure | Distribution substation | 1 | 69 | 9.2074e-05 | 1.3344e-06 | No
2019-11-12 | 18:34 | 2806 | Urban | Overload |  | 128 | 250.5703 | 0.042798 | 0.0001708 | No
2019-11-12 | 18:58 | KVD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 100 | 306.42 | 0.10081 | 0.00032899 | No
2019-11-12 | 20:40 | S738 | Short rural | Unknown | Unknown | 2 | 53 | 0.00034873 | 6.5797e-06 | No
2019-11-13 | 7:42 | PH1286 | Urban | Asset Failure | Distribution substation | 34 | 39 | 0.0017694 | 4.537e-05 | No
2019-11-13 | 8:10 | MR2272 | Short rural | Animal | Animal Impact | 1 | 198 | 0.00065139 | 3.2899e-06 | No
2019-11-13 | 9:58 | L591 | Short rural | Vegetation | Grow-in - NSP responsibility | 221 | 297.8416 | 0.21655 | 0.00072706 | No
2019-11-13 | 13:11 | 35696 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 14 | 0.0010593 | 7.5667e-05 | No
2019-11-13 | 15:19 | 49010 | Short rural | Third Party | Vehicle impact | 82 | 158 | 0.042623 | 0.00026977 | No
2019-11-13 | 15:20 | 9025 | Urban | Asset Failure | Distribution substation | 2 | 143 | 0.00038164 | 2.6688e-06 | No
2019-11-13 | 16:40 | A347 | Urban | Asset Failure | HV | 108 | 56 | 0.0080704 | 0.00014412 | No
2019-11-13 | 19:47 | 87222 | Long rural | Vegetation | Grow-in - NSP responsibility | 307 | 313.4691 | 306.4809 | 0.97771 | No
2019-11-13 | 23:42 | JBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 34 | 49 | 0.0054809 | 0.00011186 | No
2019-11-14 | 7:20 | SN1230 | Short rural | Unknown | Unknown | 1 | 76 | 0.00025003 | 3.2899e-06 | No
2019-11-14 | 8:56 | T869 | Urban | Asset Failure | Distribution substation | 30 | 59 | 0.0023619 | 4.0032e-05 | No
2019-11-14 | 10:15 | 27194 | Urban | Asset Failure | Distribution substation | 30 | 91.3333 | 0.0036563 | 4.0032e-05 | No
2019-11-14 | 10:23 | 9059 | Urban | Asset Failure | Distribution substation | 17 | 208 | 0.0047184 | 2.2685e-05 | No
2019-11-14 | 12:41 | 8798 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 19 | 366.3158 | 0.022897 | 6.2507e-05 | No
2019-11-14 | 13:28 | JBA2 | Short rural | Asset Failure | Distribution substation | 1 | 140 | 0.00046058 | 3.2899e-06 | No
2019-11-14 | 14:36 | ER1242 | Urban | Overload |  | 23 | 74 | 0.0022711 | 3.0691e-05 | No
2019-11-14 | 14:49 | DS1235 | Urban | Asset Failure | Distribution substation | 1 | 272 | 0.00036296 | 1.3344e-06 | No
2019-11-14 | 14:59 | DS1290 | Urban | Third Party | Unauthorised access | 1372 | 170.5554 | 0.31225 | 0.0018308 | No
2019-11-14 | 15:21 | 9059 | Urban | Asset Failure | Distribution substation | 23 | 27 | 0.00082866 | 3.0691e-05 | No
2019-11-14 | 15:35 | CT1206 | Urban | Asset Failure | Distribution substation | 33 | 342.6667 | 0.015089 | 4.4035e-05 | No
2019-11-14 | 19:04 | ULL2 | Short rural | Asset Failure | Distribution substation | 1 | 106 | 0.00034873 | 3.2899e-06 | No
2019-11-14 | 21:12 | SN1230 | Short rural | Animal | Animal Impact | 34 | 84 | 0.0093958 | 0.00011186 | No
2019-11-14 | 23:35 | 55356 | Urban | Animal | Animal Impact | 34 | 8 | 0.00036296 | 4.537e-05 | No
2019-11-15 | 1:18 | 10248 | Urban | Unknown | Unknown | 60 | 261 | 0.020897 | 8.0064e-05 | No
2019-11-15 | 5:55 | 1953 | Urban | Animal | Animal Impact | 23 | 26 | 0.00079797 | 3.0691e-05 | No
2019-11-15 | 7:58 | 1953 | Urban | Asset Failure | HV | 23 | 83.1739 | 0.0025527 | 3.0691e-05 | No
2019-11-15 | 13:55 | S785 | Urban | Asset Failure | Distribution substation | 5 | 83 | 0.00055378 | 6.672e-06 | No
2019-11-15 | 14:13 | NA1270 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 50 | 139.16 | 0.022891 | 0.00016449 | No
2019-11-15 | 14:52 | 8686 | Short rural | Asset Failure | Distribution substation | 15 | 125 | 0.0061685 | 4.9348e-05 | No
2019-11-15 | 15:21 | 35001 | Urban | Third Party | Vehicle impact | 7 | 259 | 0.0024193 | 9.3408e-06 | No
2019-11-15 | 18:12 | KC1288 | Short rural | Unknown | Unknown | 138 | 115.9203 | 0.052628 | 0.000454 | No
2019-11-15 | 21:26 | 16653 | Urban | Vegetation | Grow-in - NSP responsibility | 1222.7227 | 141.3399 | 0.23061 | 0.0016316 | No
2019-11-15 | 21:26 | 16660 | Urban | Vegetation | Grow-in - NSP responsibility | 822.2773 | 141.3399 | 0.15508 | 0.0010972 | No
2019-11-15 | 22:22 | J473 | Urban | Asset Failure | Distribution substation | 24 | 63.125 | 0.0020216 | 3.2026e-05 | No
2019-11-15 | 22:28 | FT1207 | Urban | Asset Failure | HV | 925 | 63.6605 | 0.078577 | 0.0012343 | No
2019-11-15 | 22:30 | NN1251 | Short rural | Asset Failure | HV | 180 | 163 | 0.096525 | 0.00059218 | No
2019-11-16 | 6:31 | MM1352 | Short rural | Unknown | Unknown | 9 | 149 | 0.0044117 | 2.9609e-05 | No
2019-11-16 | 8:26 | W185 | Short rural | Unknown | Unknown | 2 | 194 | 0.0012765 | 6.5797e-06 | No
2019-11-16 | 10:01 | X879 | Short rural | Vegetation | Grow-in - NSP responsibility | 128 | 108.6719 | 0.045762 | 0.0004211 | No
2019-11-16 | 11:26 | NL1132 | Urban | Unknown | Unknown | 14 | 157 | 0.002933 | 1.8682e-05 | No
2019-11-16 | 13:35 | SY1232 | Urban | Asset Failure | Distribution substation | 31 | 168.6452 | 0.0069762 | 4.1366e-05 | No
2019-11-16 | 14:24 | AB1280 | Urban | Asset Failure | Distribution substation | 1 | 114 | 0.00015212 | 1.3344e-06 | No
2019-11-16 | 23:20 | CX1232 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 271 | 242.5018 | 0.2162 | 0.00089155 | No
2019-11-17 | 7:34 | WP1286 | Urban | Asset Failure | Distribution substation | 9 | 604.5556 | 0.0072605 | 1.201e-05 | No
2019-11-17 | 11:23 | J493 | Urban | Asset Failure | Distribution substation | 34 | 65.5 | 0.0029717 | 4.537e-05 | No
2019-11-17 | 18:24 | 8734 | Urban | Third Party | Vehicle impact | 488 | 55.666 | 0.036249 | 0.00065119 | No
2019-11-17 | 20:48 | J504 | Urban | Asset Failure | Distribution substation | 1 | 190 | 0.00025354 | 1.3344e-06 | No
2019-11-18 | 6:19 | 35771 | Urban | Third Party | Unauthorised access | 19 | 144.1053 | 0.0036536 | 2.5354e-05 | No
2019-11-18 | 8:54 | J495 | Short rural | Asset Failure | Distribution substation | 19 | 285 | 0.017815 | 6.2507e-05 | No
2019-11-18 | 12:20 | BWH2 | Short rural | Asset Failure | Distribution substation | 1 | 196 | 0.00064481 | 3.2899e-06 | No
2019-11-18 | 12:33 | SL1112 | Short rural | Asset Failure | Distribution substation | 22 | 202 | 0.01462 | 7.2377e-05 | No
2019-11-18 | 13:12 | WM1252 | Urban | Asset Failure | LV | 65 | 59 | 0.0051174 | 8.6736e-05 | No
2019-11-18 | 14:39 | WBC2 | Short rural | Asset Failure | Distribution substation | 54 | 14 | 0.0024871 | 0.00017765 | No
2019-11-18 | 15:17 | SQ1332 | Urban | Third Party | Unauthorised access | 9 | 462 | 0.0055484 | 1.201e-05 | No
2019-11-18 | 20:26 | RV1280 | Urban | Asset Failure | Distribution substation | 96 | 111.5625 | 0.014291 | 0.0001281 | No
2019-11-19 | 7:05 | J489 | Urban | Animal | Animal Impact | 1602 | 75.1829 | 0.16072 | 0.0021377 | No
2019-11-19 | 7:50 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 524 | 0.0034478 | 6.5797e-06 | No
2019-11-19 | 7:54 | J473 | Urban | Asset Failure | Distribution substation | 1 | 78 | 0.00010408 | 1.3344e-06 | No
2019-11-19 | 9:38 | 55361 | Urban | Asset Failure | Distribution substation | 1 | 448 | 0.00059781 | 1.3344e-06 | No
2019-11-19 | 10:13 | CN1213 | Urban | Asset Failure | Distribution substation | 7 | 80.1429 | 0.0007486 | 9.3408e-06 | No
2019-11-19 | 11:43 | 10290 | Short rural | Asset Failure | HV | 17 | 165.8824 | 0.0092774 | 5.5928e-05 | No
2019-11-19 | 13:24 | 35304 | Urban | Asset Failure | HV | 1143 | 120.028 | 0.18307 | 0.0015252 | No
2019-11-19 | 13:42 | NM1213 | Urban | Weather |  | 37 | 89 | 0.0043942 | 4.9373e-05 | No
2019-11-19 | 14:05 | SZ1352 | Urban | Vegetation | Grow-in - NSP responsibility | 1391 | 91.3825 | 0.16962 | 0.0018561 | No
2019-11-19 | 15:06 | B712 | Urban | Asset Failure | HV | 975 | 44.1877 | 0.05749 | 0.001301 | No
2019-11-19 | 16:20 | A055 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 2 | 246 | 0.0016186 | 6.5797e-06 | No
2019-11-19 | 16:47 | WWC2 | Short rural | Asset Failure | Distribution substation | 17 | 80.7059 | 0.0045137 | 5.5928e-05 | No
2019-11-19 | 17:01 | JS1222 | Short rural | Overload |  | 30 | 460.1 | 0.04541 | 9.8696e-05 | No
2019-11-19 | 17:22 | R293 | Short rural | Asset Failure | Distribution substation | 2 | 1342 | 0.00883 | 6.5797e-06 | No
2019-11-19 | 17:41 | KC1288 | Short rural | Unknown | Unknown | 138 | 125.3986 | 0.056931 | 0.000454 | No
2019-11-19 | 18:16 | CLA2 | Short rural | Unknown | Unknown | 1 | 108 | 0.00035531 | 3.2899e-06 | No
2019-11-19 | 18:30 | RV1280 | Urban | Third Party | Vehicle impact | 37 | 64.9459 | 0.0032066 | 4.9373e-05 | No
2019-11-19 | 18:54 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 127 | 994.8189 | 0.41565 | 0.00041781 | No
2019-11-19 | 18:54 | 55354 | Urban | Asset Failure | Distribution substation | 1 | 188 | 0.00025087 | 1.3344e-06 | No
2019-11-19 | 19:17 | WBD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 861 | 9.4019 | 0.026631 | 0.0028326 | No
2019-11-19 | 19:49 | KC1288 | Short rural | Unknown | Unknown | 138 | 44.3188 | 0.020121 | 0.000454 | No
2019-11-19 | 20:05 | M399 | Short rural | Asset Failure | Distribution substation | 1 | 154 | 0.00050664 | 3.2899e-06 | No
2019-11-20 | 3:46 | 19816 | Urban | Asset Failure | Distribution substation | 23 | 2227 | 0.068349 | 3.0691e-05 | No
2019-11-20 | 7:16 | X877 | Short rural | Unknown | Unknown | 4 | 109.25 | 0.0014377 | 1.3159e-05 | No
2019-11-20 | 10:19 | A347 | Urban | Asset Failure | HV | 137 | 96 | 0.01755 | 0.00018281 | No
2019-11-20 | 11:34 | SL1142 | Short rural | Unknown | Unknown | 1 | 82 | 0.00026977 | 3.2899e-06 | No
2019-11-20 | 13:43 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 37 | 178.8108 | 0.021766 | 0.00012172 | No
2019-11-20 | 14:04 | 8611 | Urban | Unknown | Unknown | 11 | 325 | 0.0047705 | 1.4678e-05 | No
2019-11-20 | 14:10 | JBA2 | Short rural | Asset Failure | LV | 15 | 60.6 | 0.0029905 | 4.9348e-05 | No
2019-11-20 | 15:54 | SC1216 | Urban | Asset Failure | Distribution substation | 1 | 126 | 0.00016813 | 1.3344e-06 | No
2019-11-20 | 17:10 | WRD2 | Urban | Unknown | Unknown | 10 | 198 | 0.0026421 | 1.3344e-05 | No
2019-11-20 | 20:31 | SY1232 | Urban | Third Party | Other | 43 | 88.8605 | 0.0050987 | 5.7379e-05 | No
2019-11-21 | 0:36 | 8677 | Urban | Other | Fire | 75 | 26.9333 | 0.0026955 | 0.00010008 | No
2019-11-21 | 5:56 | M160 | Urban | Unknown | Unknown | 62 | 100.3548 | 0.0083026 | 8.2733e-05 | No
2019-11-21 | 7:15 | 8767 | Urban | Overload |  | 96 | 165 | 0.021137 | 0.0001281 | No
2019-11-21 | 9:14 | OP1132 | Short rural | Third Party | Dig-in | 5 | 243 | 0.0039972 | 1.6449e-05 | No
2019-11-21 | 14:17 | J514 | Urban | Third Party | Unauthorised access | 85 | 282.5647 | 0.03205 | 0.00011342 | No
2019-11-21 | 18:00 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 169 | 210.1183 | 0.11682 | 0.00055599 | No
2019-11-21 | 20:51 | L511 | Urban | Weather |  | 5 | 67 | 0.00044702 | 6.672e-06 | No
2019-11-21 | 23:23 | 48185 | Short rural | Unknown | Unknown | 13 | 80 | 0.0034215 | 4.2768e-05 | No
2019-11-22 | 6:49 | HKG2 | Short rural | Asset Failure | Distribution substation | 1 | 216 | 0.00071061 | 3.2899e-06 | No
2019-11-22 | 8:18 | GG1232 | Short rural | Asset Failure | Distribution substation | 1 | 346 | 0.0011383 | 3.2899e-06 | No
2019-11-22 | 9:48 | C889 | Urban | Asset Failure | Distribution substation | 1 | 312 | 0.00041633 | 1.3344e-06 | No
2019-11-22 | 10:06 | APC2 | Short rural | Third Party | Other | 8 | 141 | 0.003711 | 2.6319e-05 | No
2019-11-22 | 10:08 | KC1236 | Short rural | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 81 | 0.00079944 | 9.8696e-06 | No
2019-11-22 | 13:27 | 10244 | Short rural | Unknown | Unknown | 27 | 103 | 0.0091491 | 8.8826e-05 | No
2019-11-22 | 14:08 | 6419 | Urban | Asset Failure | Distribution substation | 61 | 78.2295 | 0.0063678 | 8.1398e-05 | No
2019-11-22 | 16:05 | RW1281 | Short rural | Asset Failure | Distribution substation | 1 | 187 | 0.0006152 | 3.2899e-06 | No
2019-11-22 | 17:08 | 1958 | Urban | Unknown | Unknown | 19 | 163 | 0.0041326 | 2.5354e-05 | No
2019-11-22 | 17:37 | L511 | Urban | Asset Failure | Distribution substation | 14 | 481.7143 | 0.0089992 | 1.8682e-05 | No
2019-11-22 | 17:53 | 8798 | Short rural | Other | Probable Lightning/Electrical Storm | 30 | 328.2 | 0.032392 | 9.8696e-05 | No
2019-11-22 | 18:13 | J514 | Urban | Asset Failure | Distribution substation | 1 | 65 | 8.6736e-05 | 1.3344e-06 | No
2019-11-22 | 18:45 | 35818 | Short rural | Asset Failure | Distribution substation | 1 | 240 | 0.00078957 | 3.2899e-06 | No
2019-11-22 | 18:48 | J495 | Short rural | Other | Probable Lightning/Electrical Storm | 1587 | 71.0202 | 0.3708 | 0.005221 | No
2019-11-22 | 18:53 | 35988 | Short rural | Other | Probable Lightning/Electrical Storm | 12 | 191 | 0.0075404 | 3.9478e-05 | No
2019-11-22 | 18:53 | CLA2 | Short rural | Other | Probable Overload | 2 | 65 | 0.00042768 | 6.5797e-06 | No
2019-11-22 | 18:58 | HR1239 | Urban | Asset Failure | Distribution substation | 1 | 347 | 0.00046304 | 1.3344e-06 | No
2019-11-22 | 19:25 | OA1207 | Short rural | Weather |  | 4 | 239 | 0.0031451 | 1.3159e-05 | No
2019-11-22 | 20:13 | MM1142 | Urban | Asset Failure | Distribution substation | 23 | 53.0435 | 0.001628 | 3.0691e-05 | No
2019-11-22 | 22:44 | MG1286 | Short rural | Animal | Animal Impact | 128 | 89 | 0.037478 | 0.0004211 | No
2019-11-23 | 0:47 | CX1232 | Short rural | Other | Probable Lightning/Electrical Storm | 14 | 486 | 0.022384 | 4.6058e-05 | No
2019-11-23 | 7:45 | 35696 | Short rural | Other | Probable Accidental Damage Excavation | 2 | 318 | 0.0020924 | 6.5797e-06 | No
2019-11-23 | 14:06 | UNF2 | Urban | Asset Failure | HV | 585 | 38.0154 | 0.029676 | 0.00078062 | No
2019-11-23 | 14:46 | W123 | Short rural | Weather |  | 593 | 39.7336 | 0.077516 | 0.0019509 | No
2019-11-23 | 20:15 | J495 | Short rural | Asset Failure | Distribution substation | 1 | 78 | 0.00025661 | 3.2899e-06 | No
2019-11-23 | 22:47 | APC2 | Short rural | Asset Failure | Distribution substation | 8 | 179.5 | 0.0047242 | 2.6319e-05 | No
2019-11-24 | 2:09 | MVB2 | Short rural | Asset Failure | Distribution substation | 1 | 498 | 0.0016384 | 3.2899e-06 | No
2019-11-24 | 8:29 | 8679 | Urban | Animal | Animal Impact | 33 | 101 | 0.0044476 | 4.4035e-05 | No
2019-11-24 | 9:10 | RW1281 | Short rural | Animal | Animal Impact | 1 | 123 | 0.00040465 | 3.2899e-06 | No
2019-11-24 | 9:39 | 8779 | Urban | Third Party | Other | 9 | 320.4444 | 0.0038484 | 1.201e-05 | No
2019-11-24 | 11:13 | MM1112 | Urban | Asset Failure | Distribution substation | 1 | 102 | 0.00013611 | 1.3344e-06 | No
2019-11-24 | 15:39 | WWB2 | Short rural | Unknown | Unknown | 27 | 302 | 0.026826 | 8.8826e-05 | No
2019-11-24 | 17:00 | CJ1275 | Urban | Third Party | Vehicle impact | 721.4416 | 246.0391 | 0.23686 | 0.00096269 | No
2019-11-24 | 17:00 | CJ1204 | Urban | Third Party | Vehicle impact | 584.5584 | 246.0391 | 0.19192 | 0.00078003 | No
2019-11-24 | 17:06 | CJ1275 | Urban | Third Party | Vehicle impact | 550 | 83.04 | 0.060945 | 0.00073392 | No
2019-11-24 | 22:40 | C889 | Urban | Asset Failure | Distribution substation | 116 | 128.6034 | 0.019907 | 0.00015479 | No
2019-11-24 | 22:45 | 76225 | Short rural | Weather |  | 22.4071 | 9 | 0.00066345 | 7.3716e-05 | No
2019-11-24 | 22:45 | 77674 | Short rural | Weather |  | 18.6726 | 9 | 0.00055287 | 6.143e-05 | No
2019-11-24 | 22:45 | 87218 | Short rural | Weather |  | 236.2084 | 9 | 0.0069938 | 0.00077709 | No
2019-11-24 | 22:45 | 87220 | Short rural | Weather |  | 706.7579 | 9 | 0.020926 | 0.0023251 | No
2019-11-24 | 22:45 | 87221 | Short rural | Weather |  | 276.3545 | 9 | 0.0081825 | 0.00090917 | No
2019-11-24 | 22:45 | 87222 | Long rural | Weather |  | 292.2262 | 9 | 8.3759 | 0.93066 | No
2019-11-24 | 22:45 | 87223 | Short rural | Weather |  | 398.66 | 9 | 0.011804 | 0.0013115 | No
2019-11-24 | 22:45 | R290 | Short rural | Weather |  | 28.9425 | 9 | 0.00085695 | 9.5217e-05 | No
2019-11-24 | 22:45 | R293 | Short rural | Weather |  | 88.6948 | 9 | 0.0026261 | 0.00029179 | No
2019-11-24 | 22:45 | X213 | Short rural | Weather |  | 70.0222 | 9 | 0.0020733 | 0.00023036 | No
2019-11-24 | 22:45 | X217 | Short rural | Weather |  | 210.0667 | 9 | 0.0062198 | 0.00069109 | No
2019-11-24 | 22:45 | X482 | Short rural | Weather |  | 168.987 | 9 | 0.0050035 | 0.00055594 | No
2019-11-24 | 23:22 | X217 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 233 | 0.00076654 | 3.2899e-06 | No
2019-11-25 | 2:08 | BWH2 | Short rural | Asset Failure | HV | 1179 | 109.7235 | 0.42559 | 0.0038787 | No
2019-11-25 | 5:43 | 57448 | Short rural | Weather |  | 1 | 276 | 0.000908 | 3.2899e-06 | No
2019-11-25 | 7:02 | X213 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 294 | 0.0038689 | 1.3159e-05 | No
2019-11-25 | 7:38 | WX1254 | Urban | Unknown | Unknown | 3 | 39 | 0.00015612 | 4.0032e-06 | No
2019-11-25 | 12:33 | CT1262 | Short rural | Asset Failure | Distribution substation | 1 | 500 | 0.0016449 | 3.2899e-06 | No
2019-11-25 | 13:01 | R260 | Short rural | Vegetation | Grow-in - NSP responsibility | 60 | 137.8667 | 0.027214 | 0.00019739 | No
2019-11-25 | 13:47 | WL1292 | Urban | Asset Failure | Distribution substation | 16 | 2997 | 0.063987 | 2.135e-05 | No
2019-11-25 | 14:15 | S738 | Short rural | Third Party | Vehicle impact | 12 | 626 | 0.024713 | 3.9478e-05 | No
2019-11-25 | 16:15 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 895 | 118.1709 | 0.34795 | 0.0029444 | No
2019-11-25 | 16:57 | T868 | Short rural | Other | Probable Lightning/Electrical Storm | 9 | 309.8889 | 0.0091754 | 2.9609e-05 | No
2019-11-25 | 17:04 | WD1221 | Short rural | Weather |  | 7 | 177 | 0.0040761 | 2.3029e-05 | No
2019-11-25 | 17:44 | SZ1322 | Short rural | Other | Probable Lightning/Electrical Storm | 23 | 76 | 0.0057507 | 7.5667e-05 | No
2019-11-25 | 18:24 | S741 | Short rural | Other | Probable Lightning/Electrical Storm | 8 | 161 | 0.0042373 | 2.6319e-05 | No
2019-11-25 | 18:57 | J468 | Urban | Weather |  | 1187 | 58 | 0.091868 | 0.0015839 | No
2019-11-25 | 21:54 | 5498 | Urban | Weather |  | 838 | 69.4117 | 0.077618 | 0.0011182 | No
2019-11-25 | 22:02 | HR1280 | Short rural | Asset Failure | Distribution substation | 33 | 13.697 | 0.001487 | 0.00010857 | No
2019-11-26 | 3:31 | T874 | Short rural | Weather |  | 3 | 405.3333 | 0.0040005 | 9.8696e-06 | Yes
2019-11-26 | 5:34 | H745 | Short rural | Vegetation | Grow-in - NSP responsibility | 136 | 220.2059 | 0.098525 | 0.00044742 | Yes
2019-11-26 | 7:05 | 8683 | Urban | Unknown | Unknown | 124 | 95 | 0.015719 | 0.00016547 | Yes
2019-11-26 | 7:14 | OA1207 | Short rural | Weather |  | 15 | 202.8 | 0.010008 | 4.9348e-05 | Yes
2019-11-26 | 9:13 | CX1206 | Short rural | Vegetation | Grow-in - NSP responsibility | 95 | 72.9789 | 0.022809 | 0.00031254 | Yes
2019-11-26 | 9:22 | MM1142 | Urban | Asset Failure | Distribution substation | 1 | 129 | 0.00017214 | 1.3344e-06 | Yes
2019-11-26 | 10:45 | SC1289 | Short rural | Unknown | Unknown | 14 | 130 | 0.0059876 | 4.6058e-05 | Yes
2019-11-26 | 10:56 | H745 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 199 | 0.00065468 | 3.2899e-06 | Yes
2019-11-26 | 11:06 | RBB2 | Short rural | Unknown | Unknown | 1 | 61 | 0.00020068 | 3.2899e-06 | Yes
2019-11-26 | 11:12 | ULJ2 | Urban | Asset Failure | Distribution substation | 27 | 415.5185 | 0.014971 | 3.6029e-05 | Yes
2019-11-26 | 11:21 | 87220 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 560 | 0.0036846 | 6.5797e-06 | Yes
2019-11-26 | 11:22 | BYB2 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 162 | 0.0021318 | 1.3159e-05 | Yes
2019-11-26 | 11:23 | X217 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 192 | 85.8333 | 0.054217 | 0.00063165 | Yes
2019-11-26 | 12:00 | ER1252 | Short rural | Weather |  | 11 | 240 | 0.0086852 | 3.6188e-05 | Yes
2019-11-26 | 12:09 | B745 | Urban | Weather |  | 388 | 92.3866 | 0.047833 | 0.00051775 | Yes
2019-11-26 | 12:14 | X482 | Short rural | Weather |  | 108 | 364.6944 | 0.12958 | 0.00035531 | Yes
2019-11-26 | 12:25 | ER1262 | Short rural | Weather |  | 663 | 251.9955 | 0.54965 | 0.0021812 | Yes
2019-11-26 | 12:30 | JBA2 | Short rural | Weather |  | 7 | 99 | 0.0022799 | 2.3029e-05 | Yes
2019-11-26 | 12:32 | SC1208 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 223 | 66.0135 | 0.04843 | 0.00073364 | Yes
2019-11-26 | 12:33 | WT1215 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 92 | 0.00060533 | 6.5797e-06 | Yes
2019-11-26 | 12:36 | 8677 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 113.4714 | 77.6193 | 0.011753 | 0.00015142 | Yes
2019-11-26 | 12:36 | 8686 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 372.5286 | 77.6193 | 0.095128 | 0.0012256 | Yes
2019-11-26 | 12:37 | X877 | Short rural | Other | Probable Lightning/Electrical Storm | 178 | 427.9663 | 0.25062 | 0.0005856 | Yes
2019-11-26 | 12:37 | ER1262 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 14 | 1382 | 0.063652 | 4.6058e-05 | Yes
2019-11-26 | 12:39 | ER1252 | Short rural | Vegetation | Grow-in - NSP responsibility | 11 | 209.4545 | 0.0075798 | 3.6188e-05 | Yes
2019-11-26 | 12:39 | OP1112 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 173.3043 | 0.013113 | 7.5667e-05 | Yes
2019-11-26 | 12:40 | CX1273 | Short rural | Other | Probable Lightning/Electrical Storm | 375 | 757.2533 | 0.93422 | 0.0012337 | Yes
2019-11-26 | 12:40 | D810 | Short rural | Vegetation | Grow-in - NSP responsibility | 100 | 1460.25 | 0.4804 | 0.00032899 | Yes
2019-11-26 | 12:40 | 35418 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 330.6156 | 179.1006 | 0.1948 | 0.0010877 | Yes
2019-11-26 | 12:40 | D810 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 205.8378 | 179.1006 | 0.12128 | 0.00067718 | Yes
2019-11-26 | 12:40 | D813 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 285.0762 | 179.1006 | 0.16797 | 0.00093786 | Yes
2019-11-26 | 12:40 | D814 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 301.4704 | 179.1006 | 0.17763 | 0.0009918 | Yes
2019-11-26 | 12:40 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 650 | 90.5662 | 0.19367 | 0.0021384 | Yes
2019-11-26 | 12:41 | 25738 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1008 | 208.8284 | 0.28089 | 0.0013451 | Yes
2019-11-26 | 12:42 | 10287 | Urban | Vegetation | Grow-in - NSP responsibility | 10 | 114 | 0.0015212 | 1.3344e-05 | Yes
2019-11-26 | 12:42 | S737 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 356 | 184.6882 | 0.21631 | 0.0011712 | Yes
2019-11-26 | 12:43 | OP1262 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1094 | 231.5832 | 0.83349 | 0.0035991 | Yes
2019-11-26 | 12:44 | SV1142 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 842 | 274.285 | 0.30818 | 0.0011236 | Yes
2019-11-26 | 12:44 | SV1132 | Urban | Vegetation | Grow-in - NSP responsibility | 991 | 228.6831 | 0.30241 | 0.0013224 | Yes
2019-11-26 | 12:44 | KC1284 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 513 | 1655.8616 | 2.7946 | 0.0016877 | Yes
2019-11-26 | 12:45 | 87222 | Long rural | Weather |  | 1 | 428 | 1.3631 | 0.0031847 | Yes
2019-11-26 | 12:47 | SZ1322 | Short rural | Vegetation | Grow-in - NSP responsibility | 1013 | 102.8164 | 0.34265 | 0.0033326 | Yes
2019-11-26 | 12:49 | 27334 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1441 | 243.0625 | 0.46738 | 0.0019229 | Yes
2019-11-26 | 12:50 | 27341 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 628 | 143.699 | 0.12042 | 0.000838 | Yes
2019-11-26 | 12:50 | A324 | Urban | Vegetation | Grow-in - NSP responsibility | 20 | 667 | 0.017801 | 2.6688e-05 | Yes
2019-11-26 | 12:50 | J505 | Urban | Weather |  | 384.9179 | 172.0503 | 0.088371 | 0.00051363 | Yes
2019-11-26 | 12:50 | J506 | Urban | Weather |  | 1596.957 | 172.0503 | 0.36664 | 0.002131 | Yes
2019-11-26 | 12:50 | J507 | Short rural | Weather |  | 900.4868 | 172.0503 | 0.5097 | 0.0029625 | Yes
2019-11-26 | 12:50 | J509 | Urban | Weather |  | 265.322 | 172.0503 | 0.060914 | 0.00035405 | Yes
2019-11-26 | 12:50 | J510 | Urban | Weather |  | 1248.2194 | 172.0503 | 0.28657 | 0.0016656 | Yes
2019-11-26 | 12:50 | J512 | Urban | Weather |  | 887.4217 | 172.0503 | 0.20374 | 0.0011842 | Yes
2019-11-26 | 12:50 | J513 | Urban | Weather |  | 400.998 | 172.0503 | 0.092063 | 0.00053509 | Yes
2019-11-26 | 12:50 | J514 | Urban | Weather |  | 1958.7597 | 172.0503 | 0.4497 | 0.0026138 | Yes
2019-11-26 | 12:50 | J515 | Urban | Weather |  | 578.8844 | 172.0503 | 0.1329 | 0.00077246 | Yes
2019-11-26 | 12:50 | J516 | Urban | Weather |  | 1458.266 | 172.0503 | 0.33479 | 0.0019459 | Yes
2019-11-26 | 12:50 | M388 | Urban | Weather |  | 956.7672 | 172.0503 | 0.21966 | 0.0012767 | Yes
2019-11-26 | 12:51 | J478 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1774 | 285.7959 | 1.668 | 0.0058362 | Yes
2019-11-26 | 12:53 | J516 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1451 | 258.7161 | 0.50093 | 0.0019362 | Yes
2019-11-26 | 12:57 | S735 | Short rural | Vegetation | Grow-in - NSP responsibility | 42 | 581.2619 | 0.080315 | 0.00013817 | Yes
2019-11-26 | 12:59 | 5496 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 69 | 512 | 0.047142 | 9.2074e-05 | Yes
2019-11-26 | 13:03 | HS1152 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 6 | 673 | 0.013284 | 1.9739e-05 | Yes
2019-11-26 | 13:05 | ER1262 | Short rural | Vegetation | Grow-in - NSP responsibility | 100 | 155.03 | 0.051003 | 0.00032899 | Yes
2019-11-26 | 13:06 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 1127.6 | 0.018548 | 1.6449e-05 | Yes
2019-11-26 | 13:09 | 87222 | Long rural | Unknown | Unknown | 20 | 362 | 23.0573 | 0.063694 | Yes
2019-11-26 | 13:13 | NG1299 | Short rural | Other | Probable Lightning/Electrical Storm | 6 | 544.6667 | 0.010751 | 1.9739e-05 | Yes
2019-11-26 | 13:14 | H745 | Short rural | Weather |  | 1 | 336 | 0.0011054 | 3.2899e-06 | Yes
2019-11-26 | 13:15 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 60 | 568.8167 | 0.11228 | 0.00019739 | Yes
2019-11-26 | 13:25 | WL1236 | Urban | Weather |  | 10 | 304.2 | 0.0040592 | 1.3344e-05 | Yes
2019-11-26 | 13:32 | 8615 | Urban | Unknown | Unknown | 16 | 185.1875 | 0.0039538 | 2.135e-05 | Yes
2019-11-26 | 13:34 | BDA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 31 | 113.9677 | 0.011623 | 0.00010199 | Yes
2019-11-26 | 13:38 | GL1233 | Short rural | Unknown | Unknown | 2 | 395.5 | 0.0026023 | 6.5797e-06 | Yes
2019-11-26 | 13:58 | J495 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 1007 | 0.033129 | 3.2899e-05 | Yes
2019-11-26 | 13:59 | SG1247 | Urban | Weather |  | 130 | 420.5769 | 0.072958 | 0.00017347 | Yes
2019-11-26 | 14:07 | R260 | Short rural | Asset Failure | HV | 286 | 83 | 0.078095 | 0.0009409 | Yes
2019-11-26 | 14:17 | CX1273 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 22 | 1553 | 0.1124 | 7.2377e-05 | Yes
2019-11-26 | 14:30 | 35815 | Short rural | Asset Failure | Distribution substation | 1 | 143 | 0.00047045 | 3.2899e-06 | Yes
2019-11-26 | 15:40 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 93 | 347.9677 | 0.10646 | 0.00030596 | Yes
2019-11-26 | 15:57 | RBD2 | Short rural | Weather |  | 4 | 256 | 0.0033688 | 1.3159e-05 | Yes
2019-11-26 | 16:01 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 111.3333 | 0.0010988 | 9.8696e-06 | Yes
2019-11-26 | 16:08 | NA1266 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 476 | 40.2983 | 0.025596 | 0.00063517 | Yes
2019-11-26 | 16:18 | CN1206 | Urban | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 39 | 258.2308 | 0.013439 | 5.2042e-05 | Yes
2019-11-26 | 16:20 | S765 | Urban | Other | Fault within LV customers installation - Defective Equipment | 13 | 270 | 0.0046837 | 1.7347e-05 | Yes
2019-11-26 | 16:21 | 9059 | Urban | Asset Failure | Distribution substation | 57 | 461.193 | 0.035079 | 7.6061e-05 | Yes
2019-11-26 | 16:30 | SXD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 83.4062 | 0.0087806 | 0.00010528 | Yes
2019-11-26 | 16:36 | 27334 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 21 | 316.7143 | 0.0088751 | 2.8022e-05 | Yes
2019-11-26 | 16:36 | TM1258 | Short rural | Asset Failure | Distribution substation | 30 | 100.8333 | 0.0099518 | 9.8696e-05 | Yes
2019-11-26 | 16:39 | J469 | Urban | Asset Failure | Distribution substation | 30 | 317.2 | 0.012698 | 4.0032e-05 | Yes
2019-11-26 | 16:40 | KVC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 34 | 150.5588 | 0.016841 | 0.00011186 | Yes
2019-11-26 | 16:46 | SXD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 60 | 0.0021713 | 3.6188e-05 | Yes
2019-11-26 | 16:51 | S738 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 405 | 0.011992 | 2.9609e-05 | Yes
2019-11-26 | 16:54 | JBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 206 | 0.0027108 | 1.3159e-05 | Yes
2019-11-26 | 17:01 | X879 | Short rural | Weather |  | 12 | 243 | 0.0095932 | 3.9478e-05 | Yes
2019-11-26 | 17:01 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 28 | 1301.8571 | 0.11992 | 9.2116e-05 | Yes
2019-11-26 | 17:09 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 633 | 170.0948 | 0.35422 | 0.0020825 | Yes
2019-11-26 | 17:18 | B747 | Urban | Weather |  | 11 | 367 | 0.005387 | 1.4678e-05 | Yes
2019-11-26 | 17:21 | 2809 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 290 | 124.5586 | 0.048201 | 0.00038698 | Yes
2019-11-26 | 17:23 | J478 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1774 | 50.8929 | 0.29702 | 0.0058362 | Yes
2019-11-26 | 17:36 | T841 | Short rural | Asset Failure | Distribution substation | 8 | 78.25 | 0.0020595 | 2.6319e-05 | Yes
2019-11-26 | 17:44 | SY1322 | Urban | Other | Probable Lightning/Electrical Storm | 58 | 128 | 0.0099066 | 7.7395e-05 | Yes
2019-11-26 | 17:50 | NA1266 | Urban | Weather |  | 20 | 299.8 | 0.0080011 | 2.6688e-05 | Yes
2019-11-26 | 17:55 | W196 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 29 | 121 | 0.0046824 | 3.8698e-05 | Yes
2019-11-26 | 18:00 | BDH2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 16 | 222 | 0.011686 | 5.2638e-05 | Yes
2019-11-26 | 18:10 | R210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1319 | 122.0584 | 0.52965 | 0.0043393 | Yes
2019-11-26 | 18:15 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 1268 | 0.062573 | 4.9348e-05 | Yes
2019-11-26 | 18:17 | FT1206 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 19 | 150.4211 | 0.0094024 | 6.2507e-05 | Yes
2019-11-26 | 18:25 | TM1217 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 194 | 0.00063823 | 3.2899e-06 | Yes
2019-11-26 | 18:51 | 19857 | Urban | Asset Failure | Distribution substation | 1 | 357 | 0.00047638 | 1.3344e-06 | Yes
2019-11-26 | 19:37 | J478 | Short rural | Other | Probable Lightning/Electrical Storm | 1774 | 117.4098 | 0.68523 | 0.0058362 | Yes
2019-11-26 | 19:58 | CN1206 | Urban | Asset Failure | Distribution substation | 50 | 60.66 | 0.0040472 | 6.672e-05 | Yes
2019-11-26 | 20:39 | CN1206 | Urban | Asset Failure | HV | 235 | 17.3489 | 0.0054403 | 0.00031358 | Yes
2019-11-26 | 21:21 | 8799 | Short rural | Weather |  | 4 | 951 | 0.012515 | 1.3159e-05 | Yes
2019-11-26 | 21:37 | 48198 | Urban | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 1340 | 65.9694 | 0.11796 | 0.0017881 | Yes
2019-11-26 | 22:17 | SZ1322 | Short rural | Weather |  | 1 | 994 | 0.0032701 | 3.2899e-06 | Yes
2019-11-27 | 5:25 | 55885 | Urban | Other | Probable Animals | 48 | 194 | 0.012426 | 6.4051e-05 | No
2019-11-27 | 7:47 | J469 | Urban | Other | Probable Lightning/Electrical Storm | 34 | 423 | 0.019191 | 4.537e-05 | No
2019-11-27 | 8:04 | BDH2 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 97 | 0.0038294 | 3.9478e-05 | No
2019-11-27 | 8:33 | HS1152 | Short rural | Asset Failure | Distribution substation | 5 | 579 | 0.0095242 | 1.6449e-05 | No
2019-11-27 | 9:52 | CX1232 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 397 | 0.0013061 | 3.2899e-06 | No
2019-11-27 | 10:47 | OP1172 | Urban | Other | Isolation Request by EE | 11 | 20 | 0.00029357 | 1.4678e-05 | No
2019-11-27 | 10:58 | WRF2 | Short rural | Other | Isolation Request by EE | 82 | 15 | 0.0040465 | 0.00026977 | No
2019-11-27 | 13:54 | 8647 | Urban | Unknown | Unknown | 597 | 4 | 0.0031865 | 0.00079664 | No
2019-11-27 | 13:55 | L582 | Short rural | Asset Failure | HV | 35 | 177.6571 | 0.020456 | 0.00011515 | No
2019-11-27 | 14:18 | SC1289 | Short rural | Unknown | Unknown | 14 | 123 | 0.0056651 | 4.6058e-05 | No
2019-11-27 | 14:48 | PK1221 | Urban | Asset Failure | Distribution substation | 2 | 75 | 0.00020016 | 2.6688e-06 | No
2019-11-27 | 18:02 | 8769 | Urban | Asset Failure | Distribution substation | 1 | 485 | 0.00064718 | 1.3344e-06 | No
2019-11-27 | 18:09 | J495 | Short rural | Third Party | Other | 1 | 119 | 0.00039149 | 3.2899e-06 | No
2019-11-27 | 18:46 | 5494 | Urban | Asset Failure | HV | 85.2921 | 108 | 0.012292 | 0.00011381 | No
2019-11-27 | 18:46 | F601 | Urban | Asset Failure | HV | 386.7079 | 108 | 0.05573 | 0.00051602 | No
2019-11-28 | 8:43 | SZ1332 | Short rural | Asset Failure | Distribution substation | 10 | 208 | 0.0068429 | 3.2899e-05 | No
2019-11-28 | 9:34 | JBB2 | Short rural | Asset Failure | HV | 18 | 230 | 0.01362 | 5.9218e-05 | No
2019-11-28 | 9:49 | J491 | Urban | Asset Failure | Distribution substation | 6 | 101 | 0.00080865 | 8.0064e-06 | No
2019-11-28 | 10:02 | 87222 | Long rural | Asset Failure | LV | 8 | 201 | 5.121 | 0.025478 | No
2019-11-28 | 11:04 | CS1276 | Urban | Unknown | Unknown | 5 | 115 | 0.00076728 | 6.672e-06 | No
2019-11-28 | 11:08 | SC1289 | Short rural | Unknown | Unknown | 14 | 110 | 0.0050664 | 4.6058e-05 | No
2019-11-28 | 14:13 | RD1296 | Urban | Asset Failure | HV | 8 | 189 | 0.0020176 | 1.0675e-05 | No
2019-11-28 | 14:55 | D852 | Urban | Asset Failure | HV | 1397 | 4 | 0.0074566 | 0.0018642 | No
2019-11-28 | 17:37 | 19870 | Urban | Other | Probable Equipment Failure | 9 | 294 | 0.0035308 | 1.201e-05 | No
2019-11-28 | 20:47 | MVF2 | Short rural | Asset Failure | Distribution substation | 1 | 247 | 0.0008126 | 3.2899e-06 | No
2019-11-28 | 21:05 | JS1252 | Short rural | Asset Failure | Distribution substation | 12 | 18 | 0.00071061 | 3.9478e-05 | No
2019-11-29 | 1:41 | SG1209 | Urban | Unknown | Unknown | 13 | 70 | 0.0012143 | 1.7347e-05 | No
2019-11-29 | 7:01 | 35702 | Urban | Asset Failure | Distribution substation | 12 | 545 | 0.008727 | 1.6013e-05 | No
2019-11-29 | 8:17 | L582 | Short rural | Asset Failure | LV | 6 | 53.1667 | 0.0010495 | 1.9739e-05 | No
2019-11-29 | 10:13 | 8680 | Urban | Asset Failure | Distribution substation | 1 | 124 | 0.00016547 | 1.3344e-06 | No
2019-11-29 | 11:02 | X867 | Urban | Third Party | Dig-in | 21 | 69.381 | 0.0019442 | 2.8022e-05 | No
2019-11-29 | 11:15 | SC1289 | Short rural | Asset Failure | Distribution substation | 1 | 184 | 0.00060533 | 3.2899e-06 | No
2019-11-29 | 11:35 | 35769 | Urban | Unknown | Unknown | 2 | 85 | 0.00022685 | 2.6688e-06 | No
2019-11-29 | 13:13 | 35983 | Short rural | Asset Failure | Distribution substation | 11 | 173.6364 | 0.0062836 | 3.6188e-05 | No
2019-11-29 | 15:44 | 10242 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 166 | 0.00054612 | 3.2899e-06 | No
2019-11-29 | 15:53 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 169 | 1377.7515 | 0.76601 | 0.00055599 | No
2019-11-29 | 16:52 | OA1233 | Short rural | Overload |  | 144 | 4 | 0.001895 | 0.00047374 | No
2019-11-29 | 16:56 | NG1210 | Short rural | Overload |  | 237 | 3.1139 | 0.0024279 | 0.0007797 | No
2019-11-29 | 17:23 | T841 | Short rural | Other | Probable Lightning/Electrical Storm | 3 | 352 | 0.0034741 | 9.8696e-06 | No
2019-11-30 | 0:01 | PCE2 | Urban | Vegetation | Grow-in - NSP responsibility | 87 | 116 | 0.013467 | 0.00011609 | No
2019-11-30 | 0:18 | 41535 | Urban | Unknown | Unknown | 1755 | 84.2906 | 0.1974 | 0.0023419 | No
2019-11-30 | 1:08 | PCE2 | Urban | Vegetation | Grow-in - NSP responsibility | 907 | 40.8831 | 0.049481 | 0.0012103 | No
2019-11-30 | 4:01 | TM1284 | Short rural | Vegetation | Grow-in - NSP responsibility | 916 | 72.6496 | 0.21893 | 0.0030135 | No
2019-11-30 | 9:05 | 87222 | Long rural | Unknown | Unknown | 1 | 61 | 0.19427 | 0.0031847 | No
2019-11-30 | 11:46 | HKF2 | Short rural | Asset Failure | Distribution substation | 1 | 527 | 0.0017338 | 3.2899e-06 | No
2019-11-30 | 12:51 | MYG2 | Urban | Asset Failure | Distribution substation | 1 | 137 | 0.00018281 | 1.3344e-06 | No
2019-11-30 | 13:38 | FF1243 | Urban | Unknown | Unknown | 1 | 47 | 6.2717e-05 | 1.3344e-06 | No
2019-11-30 | 16:00 | MVF2 | Short rural | Vegetation | Grow-in - NSP responsibility | 152 | 123.6579 | 0.061836 | 0.00050006 | No
2019-11-30 | 18:18 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 476 | 0.0031319 | 6.5797e-06 | No
2019-11-30 | 20:28 | RW1218 | Short rural | Unknown | Unknown | 1 | 92 | 0.00030267 | 3.2899e-06 | No
2019-12-01 | 5:06 | BYC2 | Short rural | Unknown | Unknown | 4 | 378 | 0.0049743 | 1.3159e-05 | No
2019-12-01 | 6:42 | JBA2 | Short rural | Unknown | Unknown | 7 | 147 | 0.0033853 | 2.3029e-05 | No
2019-12-01 | 6:47 | S741 | Short rural | Animal | Animal Impact | 2 | 86 | 0.00056586 | 6.5797e-06 | No
2019-12-01 | 7:02 | 49319 | Urban | Asset Failure | Distribution substation | 1 | 198 | 0.00026421 | 1.3344e-06 | No
2019-12-01 | 7:44 | 35773 | Urban | Unknown | Unknown | 9 | 86 | 0.0010328 | 1.201e-05 | No
2019-12-01 | 15:26 | JBA2 | Short rural | Asset Failure | HV | 65 | 348.3385 | 0.074489 | 0.00021384 | No
2019-12-02 | 4:27 | 7972 | Urban | Unknown | Unknown | 8 | 106 | 0.0011316 | 1.0675e-05 | No
2019-12-02 | 4:47 | 55885 | Urban | Unknown | Unknown | 48 | 119 | 0.0076221 | 6.4051e-05 | No
2019-12-02 | 6:40 | JBA2 | Short rural | Unknown | Unknown | 5 | 41 | 0.00067442 | 1.6449e-05 | No
2019-12-02 | 7:44 | JBA2 | Short rural | Animal | Animal Impact | 4 | 60 | 0.00078957 | 1.3159e-05 | No
2019-12-02 | 8:14 | X482 | Short rural | Unknown | Unknown | 23 | 261.7391 | 0.019805 | 7.5667e-05 | No
2019-12-02 | 10:39 | J469 | Urban | Asset Failure | Distribution substation | 1 | 154 | 0.0002055 | 1.3344e-06 | No
2019-12-02 | 10:49 | B775 | Urban | Asset Failure | Distribution substation | 6 | 299 | 0.0023939 | 8.0064e-06 | No
2019-12-02 | 12:00 | NN1233 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 220 | 0.00072377 | 3.2899e-06 | No
2019-12-02 | 12:59 | 10250 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 247 | 40.6356 | 0.03302 | 0.0008126 | No
2019-12-02 | 13:34 | BX1352 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 575 | 92.5096 | 0.070981 | 0.00076728 | No
2019-12-02 | 14:08 | C855 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 722 | 0.054631 | 7.5667e-05 | No
2019-12-02 | 15:19 | HKG2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 177 | 18.1808 | 0.010587 | 0.00058231 | No
2019-12-02 | 15:32 | 7964 | Urban | Other | Fire | 33 | 109 | 0.0047998 | 4.4035e-05 | No
2019-12-02 | 15:39 | JS1122 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 217.5 | 0.0042933 | 1.9739e-05 | No
2019-12-02 | 15:42 | 9059 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 56 | 153.0536 | 0.011437 | 7.4726e-05 | No
2019-12-02 | 15:56 | BX1212 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 26 | 201 | 0.0069736 | 3.4694e-05 | No
2019-12-02 | 16:14 | SXC2 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 504 | 154.5139 | 0.2562 | 0.0016581 | No
2019-12-02 | 16:20 | 10290 | Short rural | Asset Failure | Distribution substation | 5 | 433.4 | 0.0071291 | 1.6449e-05 | No
2019-12-02 | 16:25 | D810 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 192.5 | 0.0012666 | 6.5797e-06 | No
2019-12-02 | 16:33 | TM1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 55 | 218.6545 | 0.039564 | 0.00018094 | No
2019-12-02 | 16:44 | 35818 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 39 | 0.0001283 | 3.2899e-06 | No
2019-12-02 | 16:52 | 35824 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 66 | 170 | 0.036912 | 0.00021713 | No
2019-12-02 | 17:01 | C826 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 514 | 45.2665 | 0.031047 | 0.00068588 | No
2019-12-02 | 17:09 | NA1218 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 629 | 127.372 | 0.10691 | 0.00083934 | No
2019-12-02 | 17:18 | S738 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 493 | 64 | 0.1038 | 0.0016219 | No
2019-12-02 | 18:27 | MG1219 | Short rural | Other | Probable Equipment Failure | 1 | 177 | 0.00058231 | 3.2899e-06 | No
2019-12-02 | 18:28 | L591 | Short rural | Weather |  | 22 | 130.7273 | 0.0094616 | 7.2377e-05 | No
2019-12-02 | 18:43 | L582 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 301 | 124.5349 | 0.12332 | 0.00099025 | No
2019-12-02 | 19:44 | GG1269 | Short rural | Weather |  | 1 | 111 | 0.00036517 | 3.2899e-06 | No
2019-12-02 | 20:14 | 35818 | Short rural | Third Party | Unauthorised access | 3 | 26 | 0.00025661 | 9.8696e-06 | No
2019-12-03 | 3:26 | HBB2 | Short rural | Animal | Animal Impact | 585 | 157.4615 | 0.30305 | 0.0019246 | No
2019-12-03 | 5:23 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 272 | 499.2941 | 0.44679 | 0.00089484 | No
2019-12-03 | 7:44 | A046 | Short rural | Unknown | Unknown | 1 | 56 | 0.00018423 | 3.2899e-06 | No
2019-12-03 | 8:40 | L942 | Short rural | Other | Isolation Request by EE | 10 | 26 | 0.00085536 | 3.2899e-05 | No
2019-12-03 | 10:20 | 4873 | Urban | Third Party | Vehicle impact | 45 | 439.4222 | 0.026386 | 6.0048e-05 | No
2019-12-03 | 12:50 | X482 | Short rural | Asset Failure | Distribution substation | 1 | 125 | 0.00041123 | 3.2899e-06 | No
2019-12-03 | 15:03 | TM1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 126 | 0.00041452 | 3.2899e-06 | No
2019-12-03 | 15:19 | BX1222 | Urban | Asset Failure | Distribution substation | 7 | 228 | 0.0021297 | 9.3408e-06 | No
2019-12-03 | 18:22 | 68204 | Urban | Asset Failure | Distribution substation | 8 | 432 | 0.0046117 | 1.0675e-05 | No
2019-12-03 | 21:12 | S764 | Short rural | Third Party | Vehicle impact | 6 | 77 | 0.0015199 | 1.9739e-05 | No
2019-12-04 | 0:03 | ULL2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1575 | 127.9365 | 0.66291 | 0.0051815 | No
2019-12-04 | 0:30 | T883 | Urban | Asset Failure | Distribution substation | 24 | 424.8333 | 0.013606 | 3.2026e-05 | No
2019-12-04 | 5:41 | WT1215 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 421 | 141.7055 | 0.19627 | 0.001385 | No
2019-12-04 | 8:44 | L579 | Urban | Asset Failure | Distribution substation | 1 | 167 | 0.00022284 | 1.3344e-06 | No
2019-12-04 | 9:25 | WT1215 | Short rural | Unknown | Unknown | 44 | 118 | 0.017081 | 0.00014475 | No
2019-12-04 | 12:17 | KME2 | Short rural | Asset Failure | Distribution substation | 22 | 70.5455 | 0.0051059 | 7.2377e-05 | No
2019-12-04 | 13:27 | 68197 | Urban | Asset Failure | Distribution substation | 1 | 426 | 0.00056845 | 1.3344e-06 | No
2019-12-04 | 15:18 | HS1142 | Short rural | Asset Failure | LV | 18 | 212 | 0.012554 | 5.9218e-05 | No
2019-12-04 | 15:40 | 9052 | Urban | Third Party | Other | 54 | 246 | 0.017726 | 7.2058e-05 | No
2019-12-04 | 15:54 | ULL2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 381 | 189.4856 | 0.23751 | 0.0012534 | No
2019-12-04 | 16:12 | MG1282 | Short rural | Asset Failure | Distribution substation | 1 | 247 | 0.0008126 | 3.2899e-06 | No
2019-12-04 | 17:04 | 35816 | Short rural | Asset Failure | Distribution substation | 34 | 220.5588 | 0.024671 | 0.00011186 | No
2019-12-04 | 17:14 | 35418 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 27 | 193.8889 | 0.017222 | 8.8826e-05 | No
2019-12-04 | 22:18 | TM1284 | Short rural | Asset Failure | Distribution substation | 108 | 46 | 0.016344 | 0.00035531 | No
2019-12-05 | 5:01 | RW1292 | Short rural | Vegetation | Grow-in - NSP responsibility | 24 | 222.8333 | 0.017594 | 7.8957e-05 | No
2019-12-05 | 5:01 | RW1292 | Short rural | Asset Failure | HV | 24 | 247.6667 | 0.019555 | 7.8957e-05 | No
2019-12-05 | 5:14 | RW1292 | Short rural | Unknown | Unknown | 1 | 676 | 0.0022239 | 3.2899e-06 | No
2019-12-05 | 8:21 | NA1218 | Urban | Asset Failure | Distribution substation | 1 | 619 | 0.00082599 | 1.3344e-06 | No
2019-12-05 | 9:56 | B710 | Urban | Asset Failure | Distribution substation | 1 | 370 | 0.00049373 | 1.3344e-06 | No
2019-12-05 | 9:59 | 27335 | Urban | Unknown | Unknown | 513 | 79.7739 | 0.054609 | 0.00068455 | No
2019-12-05 | 14:07 | CX1232 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 128 | 10089.7969 | 4.2488 | 0.0004211 | No
2019-12-05 | 16:42 | KC1288 | Short rural | Unknown | Unknown | 225 | 160.9022 | 0.1191 | 0.00074022 | No
2019-12-05 | 16:42 | SZ1242 | Short rural | Asset Failure | HV | 135 | 134.7407 | 0.059843 | 0.00044413 | No
2019-12-05 | 16:51 | ULC2 | Short rural | Asset Failure | HV | 1297 | 41.1943 | 0.17577 | 0.004267 | No
2019-12-05 | 17:56 | 9050 | Urban | Asset Failure | Distribution substation | 17 | 83.2353 | 0.0018882 | 2.2685e-05 | No
2019-12-05 | 18:09 | W163 | Short rural | Vegetation | Grow-in - NSP responsibility | 70 | 208.9 | 0.048108 | 0.00023029 | No
2019-12-05 | 18:31 | DP1243 | Urban | Asset Failure | Distribution substation | 1 | 50 | 6.672e-05 | 1.3344e-06 | No
2019-12-05 | 18:55 | D814 | Short rural | Other | Fire | 149.7608 | 76.9172 | 0.037897 | 0.00049269 | No
2019-12-05 | 18:55 | 35418 | Short rural | Other | Fire | 164.2392 | 76.9172 | 0.04156 | 0.00054032 | No
2019-12-05 | 20:17 | CR1210 | Urban | Asset Failure | Distribution substation | 7 | 135 | 0.001261 | 9.3408e-06 | No
2019-12-05 | 20:34 | ULE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 2638 | 0.017357 | 6.5797e-06 | No
2019-12-05 | 22:38 | RW1218 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 731 | 0.016834 | 2.3029e-05 | No
2019-12-05 | 23:05 | P608 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 156 | 883.5705 | 0.45346 | 0.00051322 | No
2019-12-05 | 23:16 | RW1218 | Short rural | Vegetation | Grow-in - NSP responsibility | 11 | 687 | 0.024861 | 3.6188e-05 | No
2019-12-06 | 1:00 | H745 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 7 | 202 | 0.0046519 | 2.3029e-05 | No
2019-12-06 | 4:10 | HKC2 | Short rural | Unknown | Unknown | 826 | 200.9177 | 0.54598 | 0.0027174 | No
2019-12-06 | 7:36 | RW1218 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 101 | 0.0013291 | 1.3159e-05 | No
2019-12-06 | 7:52 | BYB2 | Short rural | Animal | Animal Impact | 2 | 200 | 0.0013159 | 6.5797e-06 | No
2019-12-06 | 8:44 | ULL2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1214 | 2002.6376 | 7.9983 | 0.0039939 | No
2019-12-06 | 9:49 | ER1252 | Short rural | Third Party | Other | 6 | 90 | 0.0017765 | 1.9739e-05 | No
2019-12-06 | 10:43 | OA1233 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 144 | 2255.1875 | 1.0684 | 0.00047374 | No
2019-12-06 | 10:56 | ULE2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 422 | 477.9573 | 0.66356 | 0.0013883 | No
2019-12-06 | 11:50 | T828 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 24 | 0.00094748 | 3.9478e-05 | No
2019-12-06 | 13:13 | 8799 | Short rural | Vegetation | Grow-in - NSP responsibility | 1174 | 141.0358 | 0.54472 | 0.0038623 | No
2019-12-06 | 14:48 | ER1252 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 312 | 0.0071851 | 2.3029e-05 | No
2019-12-06 | 16:27 | LL1112 | Urban | Asset Failure | Distribution substation | 1 | 61 | 8.1398e-05 | 1.3344e-06 | No
2019-12-06 | 18:52 | P608 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 17 | 6934 | 0.3878 | 5.5928e-05 | No
2019-12-06 | 19:46 | H745 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 7 | 7095 | 0.16339 | 2.3029e-05 | No
2019-12-06 | 20:17 | P608 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 68 | 7101.0147 | 1.5886 | 0.00022371 | No
2019-12-06 | 20:27 | 35418 | Short rural | Vegetation | Grow-in - NSP responsibility | 24 | 96.5833 | 0.0076259 | 7.8957e-05 | No
2019-12-06 | 20:29 | P608 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 15 | 4152 | 0.20489 | 4.9348e-05 | No
2019-12-07 | 8:55 | 9027 | Urban | Asset Failure | HV | 880 | 67.55 | 0.079322 | 0.0011743 | No
2019-12-07 | 11:12 | OA1207 | Short rural | Animal | Animal Impact | 1 | 111 | 0.00036517 | 3.2899e-06 | No
2019-12-07 | 11:21 | CD1271 | Short rural | Asset Failure | Distribution substation | 4 | 183 | 0.0024082 | 1.3159e-05 | No
2019-12-07 | 11:34 | MVD2 | Short rural | Asset Failure | Distribution substation | 2 | 101 | 0.00066455 | 6.5797e-06 | No
2019-12-07 | 12:06 | C890 | Urban | Unknown | Unknown | 1 | 115 | 0.00015346 | 1.3344e-06 | No
2019-12-07 | 12:55 | 317 | Short rural | Other | Fire | 1 | 3145 | 0.010347 | 3.2899e-06 | No
2019-12-07 | 15:22 | BK1288 | Short rural | Asset Failure | HV | 1463 | 186.8551 | 0.89935 | 0.0048131 | No
2019-12-07 | 16:14 | CLA2 | Short rural | Other | Probable Overload | 1 | 80 | 0.00026319 | 3.2899e-06 | No
2019-12-07 | 18:36 | T874 | Short rural | Unknown | Unknown | 1 | 145 | 0.00047703 | 3.2899e-06 | No
2019-12-08 | 5:00 | 19856 | Urban | Asset Failure | Distribution substation | 28 | 271 | 0.010125 | 3.7363e-05 | No
2019-12-08 | 5:16 | 35418 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 24 | 303.375 | 0.023953 | 7.8957e-05 | No
2019-12-08 | 6:15 | ULJ2 | Urban | Animal | Animal Impact | 60 | 141 | 0.011289 | 8.0064e-05 | No
2019-12-08 | 8:50 | NG1210 | Short rural | Vegetation | Grow-in - NSP responsibility | 10 | 134 | 0.0044084 | 3.2899e-05 | No
2019-12-08 | 15:35 | R208 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 167.4286 | 0.0038557 | 2.3029e-05 | No
2019-12-08 | 16:18 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 102 | 0.00067113 | 6.5797e-06 | No
2019-12-08 | 18:39 | X877 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 41 | 104 | 0.014028 | 0.00013488 | No
2019-12-08 | 19:46 | AZ1272 | Short rural | Asset Failure | Distribution substation | 1 | 152 | 0.00050006 | 3.2899e-06 | No
2019-12-08 | 21:50 | NWA2 | Urban | Asset Failure | Distribution substation | 23 | 47.4348 | 0.0014558 | 3.0691e-05 | No
2019-12-09 | 6:18 | C848 | Urban | Unknown | Unknown | 1 | 107 | 0.00014278 | 1.3344e-06 | No
2019-12-09 | 7:29 | NL1132 | Urban | Asset Failure | Distribution substation | 2 | 127.5 | 0.00034027 | 2.6688e-06 | No
2019-12-09 | 7:40 | 87220 | Short rural | Other | Probable Animals | 1 | 203 | 0.00066784 | 3.2899e-06 | No
2019-12-09 | 9:57 | 8799 | Short rural | Vegetation | Grow-in - NSP responsibility | 90 | 336 | 0.099485 | 0.00029609 | No
2019-12-09 | 12:04 | 35304 | Urban | Other | Isolation Request by EE | 1 | 20 | 2.6688e-05 | 1.3344e-06 | No
2019-12-09 | 12:36 | L588 | Short rural | Asset Failure | LV | 10 | 427 | 0.014048 | 3.2899e-05 | No
2019-12-09 | 12:40 | MM1192 | Short rural | Asset Failure | Distribution substation | 1 | 254 | 0.00083563 | 3.2899e-06 | No
2019-12-09 | 15:22 | 9029 | Urban | Unknown | Unknown | 10 | 375 | 0.005004 | 1.3344e-05 | No
2019-12-09 | 17:51 | J480 | Urban | Asset Failure | Distribution substation | 1 | 93 | 0.0001241 | 1.3344e-06 | No
2019-12-09 | 18:13 | OA1207 | Short rural | Vegetation | Grow-in - NSP responsibility | 306 | 69.6928 | 0.07016 | 0.0010067 | No
2019-12-09 | 18:50 | HS1132 | Urban | Asset Failure | HV | 3.9387 | 76 | 0.00039945 | 5.2559e-06 | No
2019-12-09 | 18:50 | HS1142 | Short rural | Asset Failure | HV | 98.0613 | 76 | 0.024518 | 0.00032261 | No
2019-12-09 | 19:04 | OA1233 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 29 | 360.931 | 0.034435 | 9.5406e-05 | No
2019-12-09 | 19:29 | 48178 | Urban | Asset Failure | Distribution substation | 1 | 121 | 0.00016146 | 1.3344e-06 | No
2019-12-09 | 20:03 | H745 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 33 | 0.00043426 | 1.3159e-05 | No
2019-12-10 | 0:17 | CX1232 | Short rural | Other | Fire | 2 | 330 | 0.0021713 | 6.5797e-06 | No
2019-12-10 | 0:58 | FF1280 | Urban | Animal | Animal Impact | 66 | 69 | 0.0060769 | 8.807e-05 | No
2019-12-10 | 4:50 | OA1207 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 39.4 | 0.0006481 | 1.6449e-05 | No
2019-12-10 | 9:49 | L579 | Urban | Network business | Switching or protection error | 22 | 6.5909 | 0.00019349 | 2.9357e-05 | No
2019-12-10 | 10:21 | 1962 | Urban | Asset Failure | Distribution substation | 1 | 219 | 0.00029223 | 1.3344e-06 | No
2019-12-10 | 11:31 | 4866 | Urban | Asset Failure | LV | 13 | 147 | 0.00255 | 1.7347e-05 | No
2019-12-10 | 12:02 | MM1192 | Short rural | Asset Failure | Distribution substation | 3 | 244.6667 | 0.0024148 | 9.8696e-06 | No
2019-12-10 | 12:10 | RV1280 | Urban | Asset Failure | Distribution substation | 41 | 146 | 0.0079877 | 5.471e-05 | No
2019-12-10 | 12:47 | HR1280 | Short rural | Asset Failure | HV | 609 | 64.8013 | 0.12983 | 0.0020035 | No
2019-12-10 | 13:36 | B215 | Urban | Asset Failure | HV | 653 | 56.7366 | 0.049438 | 0.00087136 | No
2019-12-10 | 15:25 | L942 | Short rural | Asset Failure | Distribution substation | 1 | 292 | 0.00096064 | 3.2899e-06 | No
2019-12-10 | 17:22 | A048 | Urban | Other | FOREIGN MATTER ON SYSTEM | 11 | 118 | 0.001732 | 1.4678e-05 | No
2019-12-10 | 20:13 | RD1228 | Urban | Asset Failure | Distribution substation | 184 | 189.5489 | 0.04654 | 0.00024553 | No
2019-12-10 | 23:45 | RD1228 | Urban | Asset Failure | Distribution substation | 54 | 132.037 | 0.0095143 | 7.2058e-05 | No
2019-12-11 | 5:36 | 8611 | Urban | Unknown | Unknown | 11 | 99 | 0.0014532 | 1.4678e-05 | No
2019-12-11 | 6:29 | A048 | Urban | Other | FOREIGN MATTER ON SYSTEM | 12 | 147 | 0.0023539 | 1.6013e-05 | No
2019-12-11 | 7:47 | A048 | Urban | Other | FOREIGN MATTER ON SYSTEM | 12 | 61 | 0.00097678 | 1.6013e-05 | No
2019-12-11 | 8:28 | A046 | Short rural | Asset Failure | Distribution substation | 1 | 201 | 0.00066126 | 3.2899e-06 | No
2019-12-11 | 12:07 | 35763 | Urban | Third Party | Other | 15 | 299.4 | 0.0059928 | 2.0016e-05 | No
2019-12-11 | 12:36 | RV1280 | Urban | Asset Failure | Distribution substation | 51 | 449 | 0.030556 | 6.8054e-05 | No
2019-12-11 | 14:21 | ULE2 | Short rural | Other | Fire | 1 | 2581 | 0.0084911 | 3.2899e-06 | No
2019-12-11 | 14:26 | BWH2 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 84 | 0.0013817 | 1.6449e-05 | No
2019-12-11 | 18:18 | 49917 | Urban | Asset Failure | Distribution substation | 1 | 353 | 0.00047104 | 1.3344e-06 | No
2019-12-11 | 20:58 | L582 | Short rural | Unknown | Unknown | 3 | 127 | 0.0012534 | 9.8696e-06 | No
2019-12-11 | 21:14 | MG1282 | Short rural | Asset Failure | Distribution substation | 2 | 45.5 | 0.00029938 | 6.5797e-06 | No
2019-12-12 | 12:05 | RBD2 | Short rural | Unknown | Unknown | 1 | 276 | 0.000908 | 3.2899e-06 | No
2019-12-12 | 13:08 | BWH2 | Short rural | Asset Failure | Distribution substation | 1 | 278 | 0.00091458 | 3.2899e-06 | No
2019-12-12 | 22:00 | PH1219 | Urban | Asset Failure | Distribution substation | 1 | 44 | 5.8714e-05 | 1.3344e-06 | No
2019-12-13 | 6:34 | ULK2 | Short rural | Asset Failure | Distribution substation | 1 | 297 | 0.00097709 | 3.2899e-06 | No
2019-12-13 | 8:19 | A096 | Short rural | Unknown | Unknown | 3 | 134 | 0.0013225 | 9.8696e-06 | No
2019-12-13 | 8:50 | 8683 | Urban | Asset Failure | Distribution substation | 124 | 122.0484 | 0.020195 | 0.00016547 | No
2019-12-13 | 10:45 | BK1251 | Short rural | Other | Isolation Request by EE | 2 | 13 | 8.5536e-05 | 6.5797e-06 | No
2019-12-13 | 11:41 | 10248 | Urban | Asset Failure | HV | 88 | 7 | 0.00082199 | 0.00011743 | No
2019-12-13 | 12:21 | 35982 | Short rural | Asset Failure | Distribution substation | 3 | 175 | 0.0017272 | 9.8696e-06 | No
2019-12-13 | 13:45 | J499 | Urban | Asset Failure | Distribution substation | 13 | 57 | 0.00098879 | 1.7347e-05 | No
2019-12-13 | 20:47 | WP1275 | Urban | Third Party | Vehicle impact | 0.15226 | 1215 | 0.00024686 | 2.0318e-07 | No
2019-12-13 | 20:47 | RS1262 | Urban | Third Party | Vehicle impact | 36.8477 | 1215 | 0.059741 | 4.917e-05 | No
2019-12-14 | 0:28 | CLC2 | Short rural | Animal | Animal Impact | 1245 | 110.5494 | 0.4528 | 0.0040959 | No
2019-12-14 | 4:54 | 8677 | Urban | Asset Failure | LV | 90 | 106.4778 | 0.012788 | 0.0001201 | No
2019-12-14 | 5:45 | J497 | Short rural | Asset Failure | LV | 126 | 41.6905 | 0.017282 | 0.00041452 | No
2019-12-14 | 7:40 | L946 | Short rural | Asset Failure | Distribution substation | 1 | 116 | 0.00038162 | 3.2899e-06 | No
2019-12-14 | 9:06 | ULE2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 23 | 32.8261 | 0.0024838 | 7.5667e-05 | No
2019-12-14 | 10:37 | C852 | Urban | Asset Failure | Distribution substation | 3 | 277 | 0.0011089 | 4.0032e-06 | No
2019-12-14 | 12:43 | WH1287 | Urban | Asset Failure | Distribution substation | 1 | 165 | 0.00022018 | 1.3344e-06 | No
2019-12-14 | 15:12 | C899 | Urban | Asset Failure | Distribution substation | 25 | 203.52 | 0.0067894 | 3.336e-05 | No
2019-12-14 | 15:57 | R260 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 248 | 15885.2903 | 12.9606 | 0.00081589 | No
2019-12-14 | 15:57 | J503 | Urban | Asset Failure | Distribution substation | 60 | 51.2167 | 0.0041006 | 8.0064e-05 | No
2019-12-14 | 17:09 | CD1267 | Urban | Asset Failure | Distribution substation | 12 | 588.1667 | 0.0094182 | 1.6013e-05 | No
2019-12-14 | 17:41 | P608 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 79.8 | 0.0013127 | 1.6449e-05 | No
2019-12-15 | 7:06 | TM1284 | Short rural | Other | Probable Overload | 20 | 176 | 0.01158 | 6.5797e-05 | No
2019-12-15 | 7:30 | SN1252 | Short rural | Asset Failure | Distribution substation | 1 | 264 | 0.00086852 | 3.2899e-06 | No
2019-12-15 | 8:43 | NWF2 | Urban | Asset Failure | HV | 1467 | 55.4063 | 0.10846 | 0.0019576 | No
2019-12-15 | 9:09 | RS1262 | Urban | Unknown | Unknown | 61 | 81 | 0.0065933 | 8.1398e-05 | No
2019-12-15 | 10:20 | W112 | Short rural | Asset Failure | Distribution substation | 3 | 81 | 0.00079944 | 9.8696e-06 | No
2019-12-15 | 13:15 | W120 | Short rural | Vegetation | Grow-in - NSP responsibility | 1170 | 110.1188 | 0.42386 | 0.0038491 | No
2019-12-15 | 14:06 | KVA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 28 | 9.2116e-05 | 3.2899e-06 | No
2019-12-15 | 14:26 | J483 | Urban | Asset Failure | Distribution substation | 1 | 100 | 0.00013344 | 1.3344e-06 | No
2019-12-15 | 17:43 | 8801 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 27 | 4219.1481 | 0.37477 | 8.8826e-05 | No
2019-12-15 | 18:21 | 8801 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 328 | 698.9878 | 0.75426 | 0.0010791 | No
2019-12-15 | 19:52 | 8799 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 334.4499 | 703.7244 | 0.7743 | 0.0011003 | No
2019-12-15 | 19:52 | 8801 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 202.5501 | 703.7244 | 0.46894 | 0.00066636 | No
2019-12-16 | 6:04 | RW1218 | Short rural | Unknown | Unknown | 1 | 406 | 0.0013357 | 3.2899e-06 | No
2019-12-16 | 8:01 | RV1280 | Urban | Other | Probable Equipment Failure | 35 | 535.6 | 0.025015 | 4.6704e-05 | No
2019-12-16 | 8:44 | 55866 | Urban | Asset Failure | Distribution substation | 1 | 186 | 0.0002482 | 1.3344e-06 | No
2019-12-16 | 9:33 | 9062 | Urban | Third Party | Other | 5 | 65 | 0.00043368 | 6.672e-06 | No
2019-12-16 | 9:58 | J503 | Urban | Asset Failure | Distribution substation | 28 | 30.1786 | 0.0011276 | 3.7363e-05 | No
2019-12-16 | 10:10 | 8801 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 20 | 1767.8 | 0.11632 | 6.5797e-05 | No
2019-12-16 | 10:11 | 35701 | Short rural | Unknown | Unknown | 22 | 89 | 0.0064416 | 7.2377e-05 | No
2019-12-16 | 10:54 | 35001 | Urban | Unknown | Unknown | 6 | 92 | 0.00073659 | 8.0064e-06 | No
2019-12-16 | 12:35 | 35001 | Urban | Asset Failure | Distribution substation | 1 | 573 | 0.00076461 | 1.3344e-06 | No
2019-12-16 | 13:15 | M160 | Urban | Unknown | Unknown | 1 | 185 | 0.00024686 | 1.3344e-06 | No
2019-12-16 | 14:02 | 87218 | Short rural | Vegetation | Grow-in - NSP responsibility | 8 | 78.75 | 0.0020726 | 2.6319e-05 | No
2019-12-16 | 14:03 | HT1203 | Urban | Asset Failure | HV | 11 | 125.2727 | 0.0018388 | 1.4678e-05 | No
2019-12-16 | 15:49 | R260 | Short rural | Other | Fire | 115 | 77 | 0.029132 | 0.00037833 | No
2019-12-16 | 16:24 | M160 | Urban | Unknown | Unknown | 1 | 28 | 3.7363e-05 | 1.3344e-06 | No
2019-12-16 | 16:34 | T828 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 17 | 1240.1176 | 0.069357 | 5.5928e-05 | No
2019-12-16 | 17:27 | 8801 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 5 | 961.4 | 0.015814 | 1.6449e-05 | No
2019-12-17 | 0:24 | 49391 | Urban | Asset Failure | Distribution substation | 25 | 497.76 | 0.016605 | 3.336e-05 | No
2019-12-17 | 0:54 | T828 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 146 | 474.5959 | 0.22796 | 0.00048032 | No
2019-12-17 | 0:57 | ULB2 | Short rural | Animal | Animal Impact | 1544 | 122.5997 | 0.62275 | 0.0050795 | No
2019-12-17 | 2:33 | T828 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 5 | 714.2 | 0.011748 | 1.6449e-05 | No
2019-12-17 | 6:22 | 55169 | Urban | Asset Failure | Distribution substation | 24 | 102.6667 | 0.003288 | 3.2026e-05 | No
2019-12-17 | 11:42 | T828 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 14 | 274.6429 | 0.01265 | 4.6058e-05 | No
2019-12-17 | 12:43 | J509 | Urban | Asset Failure | Distribution substation | 4 | 70.25 | 0.00037497 | 5.3376e-06 | No
2019-12-17 | 13:48 | T831 | Short rural | Asset Failure | Distribution substation | 1 | 45 | 0.00014804 | 3.2899e-06 | No
2019-12-17 | 18:00 | 35418 | Short rural | Vegetation | Grow-in - NSP responsibility | 10 | 194.7 | 0.0064054 | 3.2899e-05 | No
2019-12-17 | 18:35 | RBE2 | Short rural | Unknown | Unknown | 1 | 76 | 0.00025003 | 3.2899e-06 | No
2019-12-18 | 1:55 | 840 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 2 | 3430 | 0.022568 | 6.5797e-06 | No
2019-12-18 | 6:40 | HKF2 | Short rural | Animal | Animal Impact | 92 | 149 | 0.045097 | 0.00030267 | No
2019-12-18 | 8:23 | RBA2 | Short rural | Animal | Animal Impact | 5 | 24 | 0.00039478 | 1.6449e-05 | No
2019-12-18 | 9:43 | KVA2 | Short rural | Animal | Animal Impact | 1 | 213 | 0.00070074 | 3.2899e-06 | No
2019-12-18 | 10:47 | BYG2 | Short rural | Asset Failure | LV | 94 | 53.5106 | 0.016548 | 0.00030925 | No
2019-12-18 | 13:17 | KVB2 | Short rural | Unknown | Unknown | 3 | 135 | 0.0013324 | 9.8696e-06 | No
2019-12-18 | 14:15 | OP1172 | Urban | Other | Isolation Request by EE | 7 | 30 | 0.00028022 | 9.3408e-06 | No
2019-12-18 | 14:54 | X217 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 2 | 81.5 | 0.00053625 | 6.5797e-06 | No
2019-12-18 | 17:13 | 17061 | Urban | Animal | Animal Impact | 445.2656 | 97.0153 | 0.057643 | 0.00059416 | No
2019-12-18 | 17:13 | 46774 | Urban | Animal | Animal Impact | 402.7344 | 97.0153 | 0.052137 | 0.00053741 | No
2019-12-18 | 19:02 | 49010 | Short rural | Asset Failure | Distribution substation | 31 | 198.2903 | 0.020223 | 0.00010199 | No
2019-12-19 | 4:56 | J514 | Urban | Asset Failure | Distribution substation | 61 | 208.3115 | 0.016956 | 8.1398e-05 | No
2019-12-19 | 5:32 | DP1284 | Short rural | Asset Failure | Distribution substation | 8 | 164.5 | 0.0043295 | 2.6319e-05 | No
2019-12-19 | 7:01 | AZ1205 | Urban | Vegetation | Grow-in - NSP responsibility | 16 | 176 | 0.0037577 | 2.135e-05 | No
2019-12-19 | 9:39 | J469 | Urban | Asset Failure | Distribution substation | 1 | 137 | 0.00018281 | 1.3344e-06 | No
2019-12-19 | 11:14 | NK1342 | Urban | Weather |  | 15 | 82 | 0.0016413 | 2.0016e-05 | No
2019-12-19 | 12:06 | MG1267 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 104.0859 | 2045.2063 | 0.70034 | 0.00034243 | No
2019-12-19 | 12:06 | 35816 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 84.9141 | 2045.2063 | 0.57134 | 0.00027936 | No
2019-12-19 | 12:27 | T828 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 124 | 1215.6774 | 0.49593 | 0.00040794 | No
2019-12-19 | 12:38 | PH1230 | Urban | Weather |  | 6 | 66 | 0.00052842 | 8.0064e-06 | No
2019-12-19 | 12:49 | 35767 | Urban | Asset Failure | HV | 534 | 28.1985 | 0.020093 | 0.00071257 | No
2019-12-19 | 13:31 | 35825 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 441 | 1129.1088 | 1.6381 | 0.0014508 | No
2019-12-19 | 13:31 | 35825 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 360 | 1338.35 | 1.5851 | 0.0011844 | No
2019-12-19 | 13:50 | B716 | Urban | Asset Failure | HV | 1391 | 51.8677 | 0.096274 | 0.0018561 | No
2019-12-19 | 14:42 | 19857 | Urban | Unknown | Unknown | 2411 | 112.8299 | 0.363 | 0.0032172 | No
2019-12-19 | 14:44 | 845 | Short rural | Other | Fire | 1 | 341 | 0.0011218 | 3.2899e-06 | No
2019-12-19 | 14:45 | 7962 | Urban | Unknown | Unknown | 43 | 43 | 0.0024673 | 5.7379e-05 | No
2019-12-19 | 15:02 | S772 | Urban | Weather |  | 11 | 234 | 0.0034347 | 1.4678e-05 | No
2019-12-19 | 15:51 | B743 | Urban | Vegetation | Grow-in - NSP responsibility | 18 | 203.2222 | 0.0048812 | 2.4019e-05 | No
2019-12-19 | 15:54 | T868 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 996 | 138.1225 | 0.45259 | 0.0032767 | No
2019-12-19 | 15:55 | J472 | Urban | Vegetation | Grow-in - NSP responsibility | 5 | 65 | 0.00043368 | 6.672e-06 | No
2019-12-19 | 15:58 | HS1142 | Short rural | Other | Probable Accidental Damage - Foreign Matter On System | 21 | 77 | 0.0053197 | 6.9087e-05 | No
2019-12-19 | 16:48 | 35816 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1125 | 1361.2587 | 5.0381 | 0.0037011 | No
2019-12-19 | 17:32 | 35815 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 286.4298 | 326.0132 | 0.30721 | 0.00094231 | No
2019-12-19 | 17:32 | T868 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 547.5702 | 326.0132 | 0.58729 | 0.0018014 | No
2019-12-19 | 19:03 | S772 | Urban | Asset Failure | Distribution substation | 50 | 175.74 | 0.011725 | 6.672e-05 | No
2019-12-19 | 20:04 | CX1210 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 21 | 176 | 0.012159 | 6.9087e-05 | No
2019-12-19 | 21:43 | X482 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 40 | 1102.15 | 0.14504 | 0.00013159 | No
2019-12-20 | 6:52 | SZ1342 | Urban | Asset Failure | Distribution substation | 16 | 68 | 0.0014518 | 2.135e-05 | No
2019-12-20 | 8:06 | RBC2 | Short rural | Asset Failure | Distribution substation | 13 | 93 | 0.0039774 | 4.2768e-05 | No
2019-12-20 | 8:37 | SN1271 | Short rural | Unknown | Unknown | 29 | 90 | 0.0085865 | 9.5406e-05 | No
2019-12-20 | 11:20 | 8801 | Short rural | Other | Fire | 1 | 518 | 0.0017041 | 3.2899e-06 | No
2019-12-20 | 11:37 | CS1276 | Urban | Unknown | Unknown | 6 | 125 | 0.0010008 | 8.0064e-06 | No
2019-12-20 | 14:15 | T834 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 89.1521 | 1722.36 | 0.50517 | 0.0002933 | No
2019-12-20 | 14:15 | T828 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 185.8479 | 1722.36 | 1.0531 | 0.00061141 | No
2019-12-20 | 14:26 | MG1267 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 24 | 161 | 0.012712 | 7.8957e-05 | No
2019-12-20 | 14:27 | M399 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 11 | 11283 | 0.40831 | 3.6188e-05 | No
2019-12-20 | 14:35 | M399 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 110 | 2421.9909 | 0.87648 | 0.00036188 | No
2019-12-20 | 15:12 | 35982 | Short rural | Other | Fire | 1 | 80 | 0.00026319 | 3.2899e-06 | No
2019-12-20 | 17:29 | M399 | Short rural | Unknown | Unknown | 56 | 6 | 0.0011054 | 0.00018423 | No
2019-12-20 | 17:53 | CX1210 | Short rural | Vegetation | Grow-in - NSP responsibility | 22 | 137 | 0.0099156 | 7.2377e-05 | No
2019-12-20 | 20:34 | SC1289 | Short rural | Third Party | Vehicle impact | 15 | 103 | 0.0050828 | 4.9348e-05 | No
2019-12-20 | 21:09 | 35815 | Short rural | Unknown | Unknown | 11 | 91 | 0.0032932 | 3.6188e-05 | No
2019-12-21 | 3:41 | DS1290 | Urban | Asset Failure | HV | 1372 | 54.7908 | 0.10031 | 0.0018308 | No
2019-12-21 | 5:26 | 8735 | Urban | Unknown | Unknown | 31 | 152 | 0.0062877 | 4.1366e-05 | No
2019-12-21 | 6:48 | RV1246 | Short rural | Asset Failure | Distribution substation | 40 | 81.85 | 0.010771 | 0.00013159 | No
2019-12-21 | 10:02 | M399 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 9 | 1608.7778 | 0.047634 | 2.9609e-05 | No
2019-12-21 | 10:43 | R260 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 223 | 18161.3543 | 13.3239 | 0.00073364 | No
2019-12-21 | 11:09 | 35815 | Short rural | Other | Fire | 2 | 62 | 0.00040794 | 6.5797e-06 | No
2019-12-21 | 11:29 | RBB2 | Short rural | Asset Failure | Distribution substation | 1 | 366 | 0.0012041 | 3.2899e-06 | No
2019-12-21 | 13:02 | 35815 | Short rural | Other | Fire | 2 | 2985 | 0.01964 | 6.5797e-06 | No
2019-12-21 | 13:57 | MG1267 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1341 | 642.4489 | 2.8343 | 0.0044117 | No
2019-12-21 | 14:43 | 19857 | Urban | Asset Failure | HV | 2003.843 | 101.8368 | 0.2723 | 0.0026739 | No
2019-12-21 | 14:43 | 19856 | Urban | Asset Failure | HV | 918.157 | 101.8368 | 0.12477 | 0.0012252 | No
2019-12-21 | 14:58 | 8801 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 16 | 5068 | 0.26677 | 5.2638e-05 | No
2019-12-21 | 15:12 | BYC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 78 | 238.8462 | 0.06129 | 0.00025661 | No
2019-12-21 | 15:37 | RBD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 155 | 0.0010199 | 6.5797e-06 | No
2019-12-21 | 15:39 | 9055 | Urban | Weather |  | 40 | 43 | 0.0022952 | 5.3376e-05 | No
2019-12-21 | 15:43 | JBA2 | Short rural | Unknown | Unknown | 6 | 78 | 0.0015397 | 1.9739e-05 | No
2019-12-21 | 15:48 | ULE2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 3 | 1530 | 0.0151 | 9.8696e-06 | No
2019-12-21 | 16:25 | APC2 | Short rural | Third Party | Vehicle impact | 44 | 107.75 | 0.015597 | 0.00014475 | No
2019-12-21 | 17:12 | L588 | Short rural | Other | Fire | 31.1416 | 230.2727 | 0.023592 | 0.00010245 | No
2019-12-21 | 17:12 | L579 | Urban | Other | Fire | 23.8584 | 230.2727 | 0.0073311 | 3.1837e-05 | No
2019-12-21 | 17:17 | KVB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 217 | 0.0021417 | 9.8696e-06 | No
2019-12-21 | 17:37 | BWF2 | Short rural | Vegetation | Grow-in - NSP responsibility | 11 | 985 | 0.035646 | 3.6188e-05 | No
2019-12-21 | 17:40 | 8801 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1 | 1592 | 0.0052375 | 3.2899e-06 | No
2019-12-21 | 17:40 | M399 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 7 | 20204.8571 | 0.4653 | 2.3029e-05 | No
2019-12-21 | 17:56 | A095 | Short rural | Vegetation | Grow-in - NSP responsibility | 343 | 226.2915 | 0.25535 | 0.0011284 | No
2019-12-21 | 18:50 | J512 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 57 | 84 | 0.0063891 | 7.6061e-05 | No
2019-12-21 | 19:02 | KVC2 | Short rural | Asset Failure | Distribution substation | 4 | 1391 | 0.018305 | 1.3159e-05 | No
2019-12-21 | 19:07 | ULE2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 424 | 897.8726 | 1.2524 | 0.0013949 | No
2019-12-21 | 20:14 | L588 | Short rural | Vegetation | Grow-in - NSP responsibility | 170 | 160.8471 | 0.089958 | 0.00055928 | No
2019-12-21 | 21:00 | 10241 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2019-12-21 | 22:28 | BK1236 | Short rural | Vegetation | Grow-in - NSP responsibility | 16 | 1750.3125 | 0.092133 | 5.2638e-05 | No
2019-12-22 | 3:13 | R260 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1.1159 | 3794.25 | 0.01393 | 3.6713e-06 | No
2019-12-22 | 3:13 | BK1299 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 2.8841 | 3794.25 | 0.036001 | 9.4882e-06 | No
2019-12-22 | 4:12 | RD1232 | Urban | Asset Failure | Distribution substation | 1 | 546 | 0.00072858 | 1.3344e-06 | No
2019-12-22 | 5:21 | NA1270 | Short rural | Unknown | Unknown | 1 | 340 | 0.0011186 | 3.2899e-06 | No
2019-12-22 | 6:00 | BK1236 | Short rural | Weather |  | 28 | 281 | 0.025885 | 9.2116e-05 | No
2019-12-22 | 7:18 | 87220 | Short rural | Unknown | Unknown | 51 | 1567 | 0.26292 | 0.00016778 | No
2019-12-22 | 7:27 | KVB2 | Short rural | Weather |  | 36 | 314.3611 | 0.037231 | 0.00011844 | No
2019-12-22 | 7:50 | L588 | Short rural | Other | Fire | 2 | 3194 | 0.021016 | 6.5797e-06 | No
2019-12-22 | 7:54 | L588 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 35 | 1078.3429 | 0.12417 | 0.00011515 | No
2019-12-22 | 8:36 | MR2224 | Short rural | Unknown | Unknown | 48 | 120 | 0.01895 | 0.00015791 | No
2019-12-22 | 9:34 | J500 | Urban | Asset Failure | Distribution substation | 16 | 29.625 | 0.00063251 | 2.135e-05 | No
2019-12-22 | 12:11 | X217 | Short rural | Other | Fire | 194 | 1515.9227 | 0.96751 | 0.00063823 | No
2019-12-22 | 13:09 | 35815 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 141 | 0.0013916 | 9.8696e-06 | No
2019-12-22 | 13:50 | CA1221 | Urban | Asset Failure | Distribution substation | 47 | 124.2979 | 0.0077956 | 6.2717e-05 | No
2019-12-22 | 14:02 | BWF2 | Short rural | Vegetation | Grow-in - NSP responsibility | 15 | 136 | 0.0067113 | 4.9348e-05 | No
2019-12-22 | 14:44 | KVC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 17.3333 | 0.00017107 | 9.8696e-06 | No
2019-12-22 | 18:13 | X217 | Short rural | Other | Fire | 1 | 6934 | 0.022812 | 3.2899e-06 | No
2019-12-22 | 18:40 | 840 | Short rural | Unknown | Unknown | 2 | 780 | 0.0051322 | 6.5797e-06 | No
2019-12-22 | 18:58 | 35988 | Short rural | Other | Within Customer Installation | 1 | 235 | 0.00077312 | 3.2899e-06 | No
2019-12-22 | 19:25 | X217 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 137 | 935.4672 | 0.42163 | 0.00045071 | No
2019-12-22 | 21:08 | MG1234 | Short rural | Asset Failure | Distribution substation | 1 | 112 | 0.00036846 | 3.2899e-06 | No
2019-12-22 | 22:18 | D814 | Short rural | Asset Failure | LV | 146.3671 | 554.0556 | 0.26679 | 0.00048153 | No
2019-12-22 | 22:18 | 35418 | Short rural | Asset Failure | LV | 159.6329 | 554.0556 | 0.29097 | 0.00052517 | No
2019-12-23 | 2:09 | CT1225 | Short rural | Other | Fire | 25 | 591.12 | 0.048618 | 8.2247e-05 | No
2019-12-23 | 6:46 | BK1288 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 9 | 1420.4444 | 0.042058 | 2.9609e-05 | No
2019-12-23 | 7:24 | 27187 | Urban | Asset Failure | Distribution substation | 33 | 28.5758 | 0.0012583 | 4.4035e-05 | No
2019-12-23 | 9:00 | GV1208 | Urban | Asset Failure | Distribution substation | 24 | 129.2083 | 0.004138 | 3.2026e-05 | No
2019-12-23 | 11:14 | MG1267 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 12 | 709.8333 | 0.028023 | 3.9478e-05 | No
2019-12-23 | 11:42 | SL1112 | Short rural | Asset Failure | Distribution substation | 1 | 224 | 0.00073693 | 3.2899e-06 | No
2019-12-23 | 11:59 | MG1267 | Short rural | Other | Fire | 13 | 583.6923 | 0.024963 | 4.2768e-05 | No
2019-12-23 | 16:07 | L591 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 6 | 7034.6667 | 0.13886 | 1.9739e-05 | No
2019-12-23 | 16:24 | W127 | Short rural | Asset Failure | Distribution substation | 1 | 212 | 0.00069745 | 3.2899e-06 | No
2019-12-23 | 18:08 | X217 | Short rural | Other | Fire | 8 | 56.25 | 0.0014804 | 2.6319e-05 | No
2019-12-23 | 19:16 | CT1225 | Short rural | Asset Failure | Distribution substation | 1 | 159 | 0.00052309 | 3.2899e-06 | No
2019-12-23 | 20:38 | 87220 | Short rural | Unknown | Unknown | 39 | 48 | 0.0061586 | 0.0001283 | No
2019-12-23 | 21:54 | ULL2 | Short rural | Weather |  | 4 | 29.25 | 0.00038491 | 1.3159e-05 | No
2019-12-23 | 23:53 | SC1204 | Short rural | Asset Failure | Distribution substation | 82 | 95.9756 | 0.025891 | 0.00026977 | No
2019-12-24 | 1:11 | DS1241 | Urban | Third Party | Vehicle impact | 103.6127 | 344.1442 | 0.047582 | 0.00013826 | No
2019-12-24 | 1:11 | DS1226 | Urban | Third Party | Vehicle impact | 104.3873 | 344.1442 | 0.047937 | 0.00013929 | No
2019-12-24 | 4:40 | JBB2 | Short rural | Unknown | Unknown | 17 | 181 | 0.010123 | 5.5928e-05 | No
2019-12-24 | 7:34 | A348 | Urban | Asset Failure | HV | 19 | 128 | 0.0032453 | 2.5354e-05 | No
2019-12-24 | 7:39 | ULE2 | Short rural | Asset Failure | Distribution substation | 1 | 356 | 0.0011712 | 3.2899e-06 | No
2019-12-24 | 11:16 | J469 | Urban | Weather |  | 93 | 65 | 0.0080664 | 0.0001241 | No
2019-12-24 | 11:23 | SG1220 | Urban | Unknown | Unknown | 13 | 57 | 0.00098879 | 1.7347e-05 | No
2019-12-24 | 12:04 | M399 | Short rural | Other | Fire | 6 | 3122.5 | 0.061636 | 1.9739e-05 | No
2019-12-24 | 13:12 | L588 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1 | 23325 | 0.076736 | 3.2899e-06 | No
2019-12-24 | 13:24 | 55354 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 131 | 0.0019229 | 1.4678e-05 | No
2019-12-24 | 16:34 | R208 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1100 | 3.7 | 0.01339 | 0.0036188 | No
2019-12-24 | 16:34 | R210 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1223 | 0.16599 | 0.00066784 | 0.0040235 | No
2019-12-24 | 16:34 | R211 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1375 | 3.8996 | 0.01764 | 0.0045236 | No
2019-12-24 | 20:03 | SXD2 | Short rural | Weather |  | 85 | 48 | 0.013423 | 0.00027964 | No
2019-12-24 | 20:15 | 35001 | Urban | Asset Failure | Distribution substation | 27 | 268 | 0.0096557 | 3.6029e-05 | No
2019-12-24 | 20:51 | APE2 | Short rural | Asset Failure | Distribution substation | 1 | 831 | 0.0027339 | 3.2899e-06 | No
2019-12-24 | 21:52 | RBA2 | Short rural | Animal | Animal Impact | 2 | 939 | 0.0061784 | 6.5797e-06 | No
2019-12-25 | 2:12 | HBA2 | Short rural | Weather |  | 1 | 381 | 0.0012534 | 3.2899e-06 | No
2019-12-25 | 7:28 | MG1286 | Short rural | Vegetation | Grow-in - NSP responsibility | 1338 | 169.2915 | 0.74519 | 0.0044018 | No
2019-12-25 | 7:35 | MG1286 | Short rural | Asset Failure | Distribution substation | 1 | 567 | 0.0018654 | 3.2899e-06 | No
2019-12-25 | 7:35 | RW1218 | Short rural | Weather |  | 2 | 145 | 0.00095406 | 6.5797e-06 | No
2019-12-25 | 7:54 | MG1286 | Short rural | Vegetation | Grow-in - NSP responsibility | 93 | 168 | 0.051401 | 0.00030596 | No
2019-12-25 | 8:37 | T893 | Urban | Asset Failure | LV | 899 | 27.6719 | 0.033196 | 0.0011996 | No
2019-12-25 | 8:56 | S735 | Short rural | Vegetation | Grow-in - NSP responsibility | 9 | 10 | 0.00029609 | 2.9609e-05 | No
2019-12-25 | 9:03 | MG1234 | Short rural | Asset Failure | Distribution substation | 1 | 414 | 0.001362 | 3.2899e-06 | No
2019-12-25 | 9:08 | MG1282 | Short rural | Asset Failure | Distribution substation | 1 | 408 | 0.0013423 | 3.2899e-06 | No
2019-12-25 | 9:09 | MVC2 | Short rural | Asset Failure | Distribution substation | 1 | 615 | 0.0020233 | 3.2899e-06 | No
2019-12-25 | 9:13 | 1957 | Urban | Asset Failure | Distribution substation | 64 | 4 | 0.00034161 | 8.5402e-05 | No
2019-12-25 | 9:26 | RW1218 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 100 | 0.00098696 | 9.8696e-06 | No
2019-12-25 | 11:34 | MG1286 | Short rural | Asset Failure | Distribution substation | 1 | 361 | 0.0011876 | 3.2899e-06 | No
2019-12-25 | 13:05 | MVF2 | Short rural | Unknown | Unknown | 28 | 38 | 0.0035004 | 9.2116e-05 | No
2019-12-25 | 22:38 | 55361 | Urban | Vegetation | Grow-in - NSP responsibility | 3 | 56 | 0.00022418 | 4.0032e-06 | No
2019-12-26 | 8:31 | 48189 | Urban | Asset Failure | Distribution substation | 1 | 305 | 0.00040699 | 1.3344e-06 | No
2019-12-26 | 16:52 | MG1267 | Short rural | Other | Fire | 5 | 77 | 0.0012666 | 1.6449e-05 | No
2019-12-26 | 17:09 | 9015 | Urban | Other | FOREIGN MATTER ON SYSTEM | 4.7715 | 66.4625 | 0.00042317 | 6.3671e-06 | No
2019-12-26 | 17:09 | 9016 | Urban | Other | FOREIGN MATTER ON SYSTEM | 625.0676 | 66.4625 | 0.055436 | 0.00083409 | No
2019-12-26 | 17:09 | 9017 | Urban | Other | FOREIGN MATTER ON SYSTEM | 388.4008 | 66.4625 | 0.034446 | 0.00051828 | No
2019-12-26 | 17:09 | 9019 | Urban | Other | FOREIGN MATTER ON SYSTEM | 1046.869 | 66.4625 | 0.092844 | 0.0013969 | No
2019-12-26 | 17:09 | 9020 | Urban | Other | FOREIGN MATTER ON SYSTEM | 602.1644 | 66.4625 | 0.053404 | 0.00080353 | No
2019-12-26 | 17:09 | 9022 | Urban | Other | FOREIGN MATTER ON SYSTEM | 917.084 | 66.4625 | 0.081334 | 0.0012238 | No
2019-12-26 | 17:09 | 9025 | Urban | Other | FOREIGN MATTER ON SYSTEM | 2119.5041 | 66.4625 | 0.18797 | 0.0028283 | No
2019-12-26 | 17:09 | 9026 | Urban | Other | FOREIGN MATTER ON SYSTEM | 875.0947 | 66.4625 | 0.07761 | 0.0011677 | No
2019-12-26 | 17:09 | 9027 | Urban | Other | FOREIGN MATTER ON SYSTEM | 839.7855 | 66.4625 | 0.074478 | 0.0011206 | No
2019-12-26 | 17:09 | 9029 | Urban | Other | FOREIGN MATTER ON SYSTEM | 926.627 | 66.4625 | 0.08218 | 0.0012365 | No
2019-12-26 | 17:09 | 9030 | Urban | Other | FOREIGN MATTER ON SYSTEM | 1001.0625 | 66.4625 | 0.088782 | 0.0013358 | No
2019-12-26 | 17:09 | 9032 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 678.5085 | 66.4625 | 0.14836 | 0.0022322 | No
2019-12-26 | 17:09 | 9033 | Urban | Other | FOREIGN MATTER ON SYSTEM | 1899.0604 | 66.4625 | 0.16842 | 0.0025341 | No
2019-12-26 | 21:47 | LL1112 | Urban | Asset Failure | Distribution substation | 1 | 556 | 0.00074193 | 1.3344e-06 | No
2019-12-26 | 23:29 | WH1235 | Urban | Animal | Animal Impact | 67 | 47 | 0.004202 | 8.9405e-05 | No
2019-12-27 | 0:04 | 41535 | Urban | Unknown | Unknown | 52 | 31 | 0.0021511 | 6.9389e-05 | No
2019-12-27 | 9:16 | SWC2 | Urban | Asset Failure | Distribution substation | 3 | 205 | 0.00082066 | 4.0032e-06 | No
2019-12-27 | 10:51 | CS1276 | Urban | Unknown | Unknown | 6 | 96 | 0.00076861 | 8.0064e-06 | No
2019-12-27 | 11:53 | MG1267 | Short rural | Other | Fire | 1 | 83 | 0.00027306 | 3.2899e-06 | No
2019-12-27 | 15:07 | 8801 | Short rural | Other | Fire | 1 | 335 | 0.0011021 | 3.2899e-06 | No
2019-12-27 | 15:17 | MG1267 | Short rural | Other | Fire | 1 | 97 | 0.00031912 | 3.2899e-06 | No
2019-12-27 | 16:26 | X867 | Urban | Asset Failure | Distribution substation | 1 | 251 | 0.00033493 | 1.3344e-06 | No
2019-12-27 | 16:41 | TM1284 | Short rural | Vegetation | Grow-in - NSP responsibility | 840 | 116 | 0.32056 | 0.0027635 | No
2019-12-27 | 17:23 | MG1267 | Short rural | Asset Failure | Distribution substation | 4 | 300.75 | 0.0039577 | 1.3159e-05 | No
2019-12-27 | 19:32 | X213 | Short rural | Vegetation | Grow-in - NSP responsibility | 39 | 197 | 0.025276 | 0.0001283 | No
2019-12-28 | 1:13 | T870 | Urban | Asset Failure | HV | 845 | 84.8876 | 0.095716 | 0.0011276 | No
2019-12-28 | 5:12 | CJ1241 | Urban | Asset Failure | Distribution substation | 1 | 195 | 0.00026021 | 1.3344e-06 | No
2019-12-28 | 7:34 | X217 | Short rural | Unknown | Unknown | 20 | 453 | 0.029806 | 6.5797e-05 | No
2019-12-28 | 7:49 | 25740 | Urban | Unknown | Unknown | 62 | 32 | 0.0026474 | 8.2733e-05 | No
2019-12-28 | 9:08 | M399 | Short rural | Other | Fire | 1 | 245 | 0.00080602 | 3.2899e-06 | No
2019-12-28 | 10:11 | C854 | Urban | Third Party | Vehicle impact | 1 | 2762 | 0.0036856 | 1.3344e-06 | No
2019-12-28 | 11:23 | B720 | Urban | Asset Failure | HV | 1081 | 36.963 | 0.053319 | 0.0014425 | No
2019-12-28 | 11:41 | R260 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 297 | 499.3131 | 0.48787 | 0.00097709 | No
2019-12-28 | 14:53 | 2807 | Urban | Asset Failure | Distribution substation | 41 | 127.6829 | 0.0069856 | 5.471e-05 | No
2019-12-28 | 15:56 | D814 | Short rural | Asset Failure | Distribution substation | 1 | 257 | 0.00084549 | 3.2899e-06 | No
2019-12-28 | 16:35 | CV1221 | Urban | Asset Failure | Distribution substation | 54 | 96.8519 | 0.0069789 | 7.2058e-05 | No
2019-12-28 | 16:41 | S769 | Urban | Weather |  | 30 | 54 | 0.0021617 | 4.0032e-05 | No
2019-12-28 | 17:20 | SZ1152 | Urban | Asset Failure | Distribution substation | 20 | 443.6 | 0.011839 | 2.6688e-05 | No
2019-12-28 | 19:26 | SN1282 | Short rural | Asset Failure | LV | 8 | 87.5 | 0.0023029 | 2.6319e-05 | No
2019-12-28 | 23:15 | 9029 | Urban | Unknown | Unknown | 61 | 478 | 0.038908 | 8.1398e-05 | No
2019-12-28 | 23:49 | 35388 | Urban | Animal | Animal Impact | 1817 | 147.5575 | 0.35777 | 0.0024246 | No
2019-12-29 | 7:01 | SHK2 | Urban | Unknown | Unknown | 21 | 93 | 0.0026061 | 2.8022e-05 | No
2019-12-29 | 7:53 | NWB2 | Urban | Asset Failure | Distribution substation | 4 | 176 | 0.00093942 | 5.3376e-06 | No
2019-12-29 | 8:26 | S772 | Urban | Asset Failure | Distribution substation | 8 | 149 | 0.0015906 | 1.0675e-05 | No
2019-12-29 | 13:25 | MVC2 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 7 | 119 | 0.0027405 | 2.3029e-05 | No
2019-12-29 | 13:59 | SN1219 | Short rural | Other | Probable Animals | 1 | 84 | 0.00027635 | 3.2899e-06 | No
2019-12-29 | 17:25 | 8801 | Short rural | Other | Probable Overload | 29 | 276 | 0.026332 | 9.5406e-05 | No
2019-12-29 | 17:25 | 8799 | Short rural | Other | Probable Overload | 35 | 298 | 0.034313 | 0.00011515 | No
2019-12-29 | 19:52 | L591 | Short rural | Unknown | Unknown | 20 | 183 | 0.012041 | 6.5797e-05 | No
2019-12-29 | 21:30 | PH1201 | Urban | Asset Failure | Distribution substation | 1 | 104 | 0.00013878 | 1.3344e-06 | No
2019-12-29 | 21:41 | MR2206 | Urban | Asset Failure | Distribution substation | 20 | 68.8 | 0.0018361 | 2.6688e-05 | No
2019-12-29 | 22:01 | L591 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 7 | 5296 | 0.12196 | 2.3029e-05 | No
2019-12-30 | 7:59 | MVF2 | Short rural | Asset Failure | Distribution substation | 1 | 145 | 0.00047703 | 3.2899e-06 | No
2019-12-30 | 8:54 | 7540 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 3 | 3632.3333 | 0.03585 | 9.8696e-06 | No
2019-12-30 | 11:36 | ULL2 | Short rural | Asset Failure | Distribution substation | 16 | 126.9375 | 0.0066817 | 5.2638e-05 | No
2019-12-30 | 16:08 | NA1218 | Urban | Asset Failure | Distribution substation | 1 | 88 | 0.00011743 | 1.3344e-06 | No
2019-12-30 | 16:22 | OA1244 | Short rural | Vegetation | Grow-in - NSP responsibility | 44 | 182 | 0.026345 | 0.00014475 | No
2019-12-30 | 17:15 | DFA2 | Short rural | Unknown | Unknown | 1 | 64 | 0.00021055 | 3.2899e-06 | No
2019-12-30 | 19:08 | DP1243 | Urban | Asset Failure | Distribution substation | 1 | 113 | 0.00015079 | 1.3344e-06 | No
2019-12-30 | 19:19 | WD1258 | Urban | Asset Failure | Distribution substation | 1 | 126 | 0.00016813 | 1.3344e-06 | No
2019-12-30 | 22:01 | R211 | Short rural | Asset Failure | Distribution substation | 1 | 122 | 0.00040136 | 3.2899e-06 | No
2019-12-30 | 23:18 | L946 | Short rural | Unknown | Unknown | 31 | 164.4516 | 0.016772 | 0.00010199 | No
2019-12-31 | 0:15 | RBA2 | Short rural | Animal | Animal Impact | 501 | 189.2954 | 0.312 | 0.0016482 | No
2019-12-31 | 2:35 | KC1221 | Short rural | Asset Failure | HV | 560 | 190.5518 | 0.35106 | 0.0018423 | No
2019-12-31 | 2:37 | CX1206 | Short rural | Asset Failure | HV | 112 | 95.6786 | 0.035254 | 0.00036846 | No
2019-12-31 | 4:59 | HBA2 | Short rural | Animal | Animal Impact | 11 | 171 | 0.0061882 | 3.6188e-05 | No
2019-12-31 | 7:01 | 8777 | Urban | Asset Failure | Distribution substation | 1 | 104 | 0.00013878 | 1.3344e-06 | No
2019-12-31 | 7:29 | GG1232 | Short rural | Animal | Animal Impact | 1 | 218 | 0.00071719 | 3.2899e-06 | No
2019-12-31 | 9:58 | WBC2 | Short rural | Asset Failure | HV | 151 | 60.4305 | 0.03002 | 0.00049677 | No
2019-12-31 | 11:08 | YYA2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 64 | 6521.9688 | 1.3732 | 0.00021055 | No
2019-12-31 | 11:13 | YYA2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 459.1886 | 10637.7825 | 16.0702 | 0.0015107 | No
2019-12-31 | 11:13 | YYB2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 556.8114 | 10637.7825 | 19.4866 | 0.0018318 | No
2019-12-31 | 12:22 | ULB2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1647.5474 | 1695.4827 | 9.1899 | 0.0054202 | No
2019-12-31 | 12:22 | ULC2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 2451.6441 | 1695.4827 | 13.675 | 0.0080656 | No
2019-12-31 | 12:22 | ULD2 | Urban | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 959.3852 | 1695.4827 | 2.1706 | 0.0012802 | No
2019-12-31 | 12:22 | ULE2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 450.9749 | 1695.4827 | 2.5155 | 0.0014836 | No
2019-12-31 | 12:22 | ULF2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1821.9811 | 1695.4827 | 10.1628 | 0.0059941 | No
2019-12-31 | 12:22 | ULH2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 858.3413 | 1695.4827 | 4.7877 | 0.0028238 | No
2019-12-31 | 12:22 | ULJ2 | Urban | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 2005.9873 | 1695.4827 | 4.5384 | 0.0026768 | No
2019-12-31 | 12:22 | ULK2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1614.5752 | 1695.4827 | 9.0059 | 0.0053117 | No
2019-12-31 | 12:22 | ULL2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1781.5635 | 1695.4827 | 9.9374 | 0.0058611 | No
2019-12-31 | 12:30 | T834 | Short rural | Vegetation | Grow-in - NSP responsibility | 130 | 200.5231 | 0.08576 | 0.00042768 | No
2019-12-31 | 12:33 | YYB2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1232 | 11207.2394 | 45.4242 | 0.0040531 | No
2019-12-31 | 13:47 | SXC2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 844 | 3447.9325 | 9.5737 | 0.0027766 | No
2019-12-31 | 13:50 | SXD2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 792 | 4474.1591 | 11.6577 | 0.0026056 | No
2019-12-31 | 13:51 | SXB2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 424.4274 | 4460.5707 | 6.2283 | 0.0013963 | No
2019-12-31 | 13:51 | SXA2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 572.5726 | 4460.5707 | 8.4023 | 0.0018837 | No
2019-12-31 | 13:51 | SXA2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1345 | 4442.3383 | 19.6568 | 0.0044249 | No
2019-12-31 | 13:55 | RV1206 | Short rural | Asset Failure | Distribution substation | 1 | 67 | 0.00022042 | 3.2899e-06 | No
2019-12-31 | 14:09 | APE2 | Short rural | Unknown | Unknown | 2 | 87 | 0.00057244 | 6.5797e-06 | No
2019-12-31 | 14:26 | B211 | Urban | Other | FOREIGN MATTER ON SYSTEM | 68 | 15 | 0.0013611 | 9.0739e-05 | No
2019-12-31 | 14:35 | OA1244 | Short rural | Unknown | Unknown | 44 | 260 | 0.037636 | 0.00014475 | No
2019-12-31 | 14:52 | MVD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 16 | 57 | 0.0030004 | 5.2638e-05 | No
2019-12-31 | 15:04 | ER1252 | Short rural | Asset Failure | HV | 493 | 55.3529 | 0.089777 | 0.0016219 | No
2019-12-31 | 15:20 | 9055 | Urban | Weather |  | 40 | 88 | 0.0046971 | 5.3376e-05 | No
2019-12-31 | 15:53 | BWH2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 50 | 12342.76 | 2.0303 | 0.00016449 | No
2019-12-31 | 16:01 | A045 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 223 | 0.0022009 | 9.8696e-06 | No
2019-12-31 | 16:10 | SC1204 | Short rural | Unknown | Unknown | 39 | 65 | 0.0083398 | 0.0001283 | No
2019-12-31 | 16:16 | 19856 | Urban | Vegetation | Grow-in - NSP responsibility | 778.0139 | 132.8813 | 0.13795 | 0.0010382 | No
2019-12-31 | 16:16 | 19857 | Urban | Vegetation | Grow-in - NSP responsibility | 1697.9861 | 132.8813 | 0.30108 | 0.0022658 | No
2019-12-31 | 16:44 | BYB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 76 | 227.4737 | 0.056875 | 0.00025003 | No
2019-12-31 | 16:57 | WT1215 | Short rural | Asset Failure | HV | 11 | 155.4545 | 0.0056257 | 3.6188e-05 | No
2019-12-31 | 17:04 | SN1230 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 23 | 12901.6087 | 0.97622 | 7.5667e-05 | No
2019-12-31 | 17:17 | KC1288 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 117 | 83 | 0.031948 | 0.00038491 | No
2019-12-31 | 17:21 | LL1222 | Urban | Weather |  | 29 | 102 | 0.0039472 | 3.8698e-05 | No
2019-12-31 | 17:29 | 35304 | Urban | Asset Failure | Distribution substation | 22 | 320 | 0.0093942 | 2.9357e-05 | No
2019-12-31 | 17:29 | L516 | Urban | Asset Failure | HV | 670 | 78.8209 | 0.07047 | 0.00089405 | No
2019-12-31 | 17:53 | T883 | Urban | Unknown | Unknown | 9 | 133 | 0.0015973 | 1.201e-05 | No
2019-12-31 | 17:58 | C899 | Urban | Asset Failure | Distribution substation | 29 | 269.7241 | 0.010438 | 3.8698e-05 | No
2019-12-31 | 18:03 | CV1247 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1329 | 99 | 0.17557 | 0.0017734 | No
2019-12-31 | 18:15 | RS1262 | Urban | Asset Failure | HV | 1211 | 98.6474 | 0.15941 | 0.001616 | No
2019-12-31 | 18:22 | B715 | Urban | Other | Fault within LV customers installation - Defective Equipment | 27 | 122 | 0.0043955 | 3.6029e-05 | No
2019-12-31 | 18:32 | S741 | Short rural | Unknown | Unknown | 5 | 231 | 0.0037998 | 1.6449e-05 | No
2019-12-31 | 18:48 | ER1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 72 | 442.0833 | 0.10472 | 0.00023687 | No
2019-12-31 | 18:56 | L940 | Short rural | Vegetation | Grow-in - NSP responsibility | 580 | 313.15 | 0.59753 | 0.0019081 | No
2019-12-31 | 19:04 | 55874 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1380 | 127.163 | 0.23417 | 0.0018415 | No
2019-12-31 | 19:29 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 28 | 719 | 0.066232 | 9.2116e-05 | No
2019-12-31 | 20:01 | HBA2 | Short rural | Asset Failure | Distribution substation | 1 | 94 | 0.00030925 | 3.2899e-06 | No
2019-12-31 | 22:04 | BWH2 | Short rural | Unknown | Unknown | 13 | 587 | 0.025105 | 4.2768e-05 | No
2020-01-01 | 1:26 | S765 | Urban | Asset Failure | Distribution substation | 29 | 851.1379 | 0.032937 | 3.8698e-05 | No
2020-01-01 | 5:07 | HBA2 | Short rural | Unknown | Unknown | 11 | 177 | 0.0064054 | 3.6188e-05 | No
2020-01-01 | 7:25 | 10244 | Short rural | Animal | Animal Impact | 12 | 400 | 0.015791 | 3.9478e-05 | No
2020-01-01 | 8:19 | KVA2 | Short rural | Animal | Animal Impact | 13 | 1777 | 0.075999 | 4.2768e-05 | No
2020-01-01 | 9:05 | GL1255 | Short rural | Asset Failure | Distribution substation | 13 | 128 | 0.0054743 | 4.2768e-05 | No
2020-01-01 | 10:28 | 35013 | Short rural | Asset Failure | Distribution substation | 4 | 499.5 | 0.0065731 | 1.3159e-05 | No
2020-01-01 | 11:49 | L941 | Short rural | Other | Isolation Request by EE | 11 | 15 | 0.00054283 | 3.6188e-05 | No
2020-01-01 | 11:52 | NA1270 | Short rural | Vegetation | Grow-in - NSP responsibility | 50 | 1410.12 | 0.23196 | 0.00016449 | No
2020-01-01 | 12:09 | 61617 | Short rural | Asset Failure | Distribution substation | 18 | 157 | 0.0092972 | 5.9218e-05 | No
2020-01-01 | 13:32 | RW1229 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 68 | 0.00044742 | 6.5797e-06 | No
2020-01-01 | 18:30 | MM1392 | Urban | Asset Failure | Distribution substation | 24 | 39.25 | 0.001257 | 3.2026e-05 | No
2020-01-01 | 19:35 | AZ1205 | Urban | Animal | Animal Impact | 1021 | 6.0774 | 0.0082799 | 0.0013624 | No
2020-01-01 | 19:50 | D814 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1 | 9398 | 0.030918 | 3.2899e-06 | No
2020-01-01 | 20:30 | A344 | Urban | Asset Failure | LV | 84 | 67 | 0.00751 | 0.00011209 | No
2020-01-01 | 21:29 | X482 | Short rural | Vegetation | Grow-in - NSP responsibility | 108 | 54.537 | 0.019377 | 0.00035531 | No
2020-01-02 | 2:20 | 35990 | Short rural | Unknown | Unknown | 69 | 332 | 0.075364 | 0.000227 | No
2020-01-02 | 2:46 | 35816 | Short rural | Animal | Animal Impact | 580 | 85 | 0.16219 | 0.0019081 | No
2020-01-02 | 11:26 | HS1142 | Short rural | Asset Failure | Distribution substation | 27 | 154.6296 | 0.013735 | 8.8826e-05 | No
2020-01-02 | 11:31 | YYB2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1181.8936 | 7385 | 28.7149 | 0.0038883 | No
2020-01-02 | 11:31 | SXD2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 756.1064 | 7385 | 18.3701 | 0.0024875 | No
2020-01-02 | 12:41 | ULL2 | Short rural | Unknown | Unknown | 1 | 5711 | 0.018788 | 3.2899e-06 | No
2020-01-02 | 14:13 | 49008 | Short rural | Third Party | Other | 82 | 77 | 0.020772 | 0.00026977 | No
2020-01-02 | 15:31 | 8798 | Short rural | Asset Failure | Distribution substation | 1 | 100 | 0.00032899 | 3.2899e-06 | No
2020-01-02 | 19:03 | W127 | Short rural | Asset Failure | Distribution substation | 31 | 83 | 0.0084648 | 0.00010199 | No
2020-01-02 | 22:46 | RBB2 | Short rural | Unknown | Unknown | 3 | 102 | 0.0010067 | 9.8696e-06 | No
2020-01-03 | 1:02 | 35816 | Short rural | Unknown | Unknown | 1 | 355 | 0.0011679 | 3.2899e-06 | No
2020-01-03 | 11:48 | NA1225 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 7 | 2196.8571 | 0.050592 | 2.3029e-05 | No
2020-01-03 | 12:41 | CV1251 | Urban | Asset Failure | Distribution substation | 36 | 82.4444 | 0.0039605 | 4.8038e-05 | No
2020-01-03 | 13:40 | 9057 | Urban | Unknown | Unknown | 33 | 168 | 0.0073979 | 4.4035e-05 | No
2020-01-03 | 13:49 | FF1265 | Urban | Unknown | Unknown | 1 | 289 | 0.00038564 | 1.3344e-06 | No
2020-01-03 | 14:49 | KVA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 129 | 0.00084878 | 6.5797e-06 | No
2020-01-03 | 17:16 | FF1265 | Urban | Unknown | Unknown | 8 | 88 | 0.00093942 | 1.0675e-05 | No
2020-01-03 | 17:41 | FT1206 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 198 | 0.0013028 | 6.5797e-06 | No
2020-01-03 | 19:18 | C899 | Urban | Asset Failure | Distribution substation | 52 | 251.8462 | 0.017475 | 6.9389e-05 | No
2020-01-03 | 20:46 | FT1210 | Urban | Asset Failure | Distribution substation | 1 | 955 | 0.0012744 | 1.3344e-06 | No
2020-01-03 | 21:46 | CS1247 | Urban | Unknown | Unknown | 5 | 108 | 0.00072058 | 6.672e-06 | No
2020-01-04 | 0:28 | 68181 | Urban | Asset Failure | Distribution substation | 1 | 416 | 0.00055511 | 1.3344e-06 | No
2020-01-04 | 4:47 | HKF2 | Short rural | Animal | Animal Impact | 2340 | 274.0944 | 2.1101 | 0.0076983 | No
2020-01-04 | 8:46 | MG1282 | Short rural | Vegetation | Grow-in - NSP responsibility | 1086 | 195.4024 | 0.69813 | 0.0035728 | No
2020-01-04 | 9:23 | CT1225 | Short rural | Third Party | Other | 25 | 46.24 | 0.0038031 | 8.2247e-05 | No
2020-01-04 | 9:52 | 35816 | Short rural | Asset Failure | Distribution substation | 1 | 406 | 0.0013357 | 3.2899e-06 | No
2020-01-04 | 11:21 | RD1269 | Urban | Vegetation | Grow-in - NSP responsibility | 74 | 88.2703 | 0.0087163 | 9.8746e-05 | No
2020-01-04 | 11:21 | 49362 | Urban | Asset Failure | Distribution substation | 21 | 126.5238 | 0.0035455 | 2.8022e-05 | No
2020-01-04 | 12:33 | D814 | Short rural | Unknown | Unknown | 168 | 246.0238 | 0.13598 | 0.0005527 | No
2020-01-04 | 12:33 | D814 | Short rural | Unknown | Unknown | 137 | 167.7737 | 0.075618 | 0.00045071 | No
2020-01-04 | 12:44 | BYC2 | Short rural | Asset Failure | HV | 85 | 130.9765 | 0.036626 | 0.00027964 | No
2020-01-04 | 13:01 | WD1251 | Short rural | Asset Failure | Distribution substation | 1 | 117 | 0.00038491 | 3.2899e-06 | No
2020-01-04 | 13:12 | 9055 | Urban | Asset Failure | Distribution substation | 120 | 194.0833 | 0.031078 | 0.00016013 | No
2020-01-04 | 13:18 | 9052 | Urban | Asset Failure | Distribution substation | 91 | 129.3626 | 0.015709 | 0.00012143 | No
2020-01-04 | 13:28 | OA1244 | Short rural | Weather |  | 3 | 77 | 0.00075996 | 9.8696e-06 | No
2020-01-04 | 13:58 | A347 | Urban | Weather |  | 33 | 318 | 0.014003 | 4.4035e-05 | No
2020-01-04 | 14:00 | ULB2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1550.7278 | 275.5653 | 1.4058 | 0.0051017 | No
2020-01-04 | 14:00 | ULC2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 2306.0822 | 275.5653 | 2.0906 | 0.0075867 | No
2020-01-04 | 14:00 | ULD2 | Urban | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 902.4235 | 275.5653 | 0.33183 | 0.0012042 | No
2020-01-04 | 14:00 | ULE2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 424.1991 | 275.5653 | 0.38457 | 0.0013956 | No
2020-01-04 | 14:00 | ULF2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1713.8043 | 275.5653 | 1.5537 | 0.0056382 | No
2020-01-04 | 14:00 | ULH2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 807.3789 | 275.5653 | 0.73195 | 0.0026562 | No
2020-01-04 | 14:00 | ULJ2 | Urban | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1884.8846 | 275.5653 | 0.6931 | 0.0025152 | No
2020-01-04 | 14:00 | ULK2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1518.7127 | 275.5653 | 1.3768 | 0.0049964 | No
2020-01-04 | 14:00 | ULL2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1676.7869 | 275.5653 | 1.5201 | 0.0055164 | No
2020-01-04 | 14:13 | OA1244 | Short rural | Asset Failure | HV | 196 | 374.3827 | 0.24141 | 0.00064481 | No
2020-01-04 | 14:23 | 7974 | Urban | Asset Failure | Distribution substation | 25 | 149.16 | 0.004976 | 3.336e-05 | No
2020-01-04 | 14:28 | KC1262 | Short rural | Asset Failure | LV | 118 | 138.3644 | 0.053714 | 0.0003882 | No
2020-01-04 | 14:38 | S772 | Urban | Weather |  | 7 | 50 | 0.00046704 | 9.3408e-06 | No
2020-01-04 | 14:50 | TM1284 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1106 | 1846.9123 | 6.7202 | 0.0036386 | No
2020-01-04 | 15:07 | CS1280 | Short rural | Weather |  | 31 | 233 | 0.023763 | 0.00010199 | No
2020-01-04 | 15:08 | ULE2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 343.0362 | 893.9029 | 1.0088 | 0.0011285 | No
2020-01-04 | 15:08 | ULL2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 1355.9638 | 893.9029 | 3.9876 | 0.0044609 | No
2020-01-04 | 15:20 | SG1220 | Urban | Weather |  | 17 | 94 | 0.0021324 | 2.2685e-05 | No
2020-01-04 | 15:22 | A096 | Short rural | Vegetation | Grow-in - NSP responsibility | 49 | 120 | 0.019344 | 0.0001612 | No
2020-01-04 | 15:37 | B710 | Urban | Asset Failure | HV | 1136 | 66.103 | 0.1002 | 0.0015159 | No
2020-01-04 | 16:21 | 9047 | Urban | Weather |  | 36 | 372 | 0.01787 | 4.8038e-05 | No
2020-01-04 | 16:23 | SC1204 | Short rural | Asset Failure | Distribution substation | 28 | 310.25 | 0.028579 | 9.2116e-05 | No
2020-01-04 | 16:24 | NA1270 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 146 | 3821.8562 | 1.8357 | 0.00048032 | No
2020-01-04 | 16:31 | RW1218 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 132 | 572.4848 | 0.24861 | 0.00043426 | No
2020-01-04 | 16:31 | RW1218 | Short rural | Vegetation | Grow-in - NSP responsibility | 73 | 254.6712 | 0.061162 | 0.00024016 | No
2020-01-04 | 16:39 | SG1254 | Urban | Weather |  | 24 | 47 | 0.0015052 | 3.2026e-05 | No
2020-01-04 | 16:39 | BX1222 | Urban | Vegetation | Grow-in - NSP responsibility | 45 | 26.9778 | 0.00162 | 6.0048e-05 | No
2020-01-04 | 16:54 | DP1236 | Short rural | Weather |  | 30 | 94 | 0.0092774 | 9.8696e-05 | No
2020-01-04 | 16:54 | B720 | Urban | Weather |  | 42 | 50 | 0.0028022 | 5.6045e-05 | No
2020-01-04 | 17:06 | T870 | Urban | Asset Failure | HV | 284 | 143.7183 | 0.054465 | 0.00037897 | No
2020-01-04 | 17:21 | 8737 | Urban | Weather |  | 13 | 130 | 0.0022551 | 1.7347e-05 | No
2020-01-04 | 17:24 | C889 | Urban | Weather |  | 16 | 81 | 0.0017294 | 2.135e-05 | No
2020-01-04 | 17:32 | 2815 | Urban | Weather |  | 16 | 224 | 0.0047825 | 2.135e-05 | No
2020-01-04 | 17:49 | ULD2 | Urban | Weather |  | 1 | 70 | 9.3408e-05 | 1.3344e-06 | No
2020-01-04 | 17:50 | X482 | Short rural | Unknown | Unknown | 40 | 512.3 | 0.067416 | 0.00013159 | No
2020-01-04 | 18:05 | KVC2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 53 | 17020.2642 | 2.9677 | 0.00017436 | No
2020-01-04 | 18:38 | ULE2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 90.4533 | 1949.1607 | 0.58003 | 0.00029758 | No
2020-01-04 | 18:38 | ULL2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 357.5467 | 1949.1607 | 2.2928 | 0.0011763 | No
2020-01-04 | 18:43 | S765 | Urban | Weather |  | 18 | 86 | 0.0020656 | 2.4019e-05 | No
2020-01-04 | 19:09 | RD1299 | Urban | Other | Probable Overload | 21 | 838 | 0.023483 | 2.8022e-05 | No
2020-01-04 | 19:14 | SN1230 | Short rural | Vegetation | Grow-in - NSP responsibility | 348 | 407.0259 | 0.46599 | 0.0011449 | No
2020-01-04 | 19:17 | 8651 | Urban | Weather |  | 32 | 609.6562 | 0.026033 | 4.2701e-05 | No
2020-01-04 | 19:25 | MM1142 | Urban | Weather |  | 33 | 102 | 0.0044916 | 4.4035e-05 | No
2020-01-04 | 19:29 | KVC2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 67 | 5407.8507 | 1.192 | 0.00022042 | No
2020-01-04 | 19:34 | 8776 | Urban | Weather |  | 50 | 117 | 0.0078062 | 6.672e-05 | No
2020-01-04 | 19:39 | MR2299 | Urban | Weather |  | 29 | 100 | 0.0038698 | 3.8698e-05 | No
2020-01-04 | 19:42 | TM1232 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 39 | 8381.4359 | 1.0754 | 0.0001283 | No
2020-01-04 | 19:45 | SG1254 | Urban | Weather |  | 24 | 86 | 0.0027542 | 3.2026e-05 | No
2020-01-04 | 19:45 | KVC2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 62 | 5390.8387 | 1.0996 | 0.00020397 | No
2020-01-04 | 19:51 | D814 | Short rural | Weather |  | 81 | 93.2716 | 0.024855 | 0.00026648 | No
2020-01-04 | 19:54 | 49916 | Urban | Weather |  | 11 | 82 | 0.0012036 | 1.4678e-05 | No
2020-01-04 | 19:55 | CS1239 | Short rural | Weather |  | 9 | 86 | 0.0025464 | 2.9609e-05 | No
2020-01-04 | 19:57 | KVD2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 63 | 9967.0952 | 2.0658 | 0.00020726 | No
2020-01-04 | 19:59 | D845 | Urban | Asset Failure | Distribution substation | 21 | 40.6667 | 0.0011396 | 2.8022e-05 | No
2020-01-04 | 20:07 | BDA2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 176 | 3562.1989 | 2.0626 | 0.00057902 | No
2020-01-04 | 20:16 | 61617 | Short rural | Weather |  | 14 | 108 | 0.0049743 | 4.6058e-05 | No
2020-01-04 | 20:24 | S772 | Urban | Weather |  | 22 | 77 | 0.0022605 | 2.9357e-05 | No
2020-01-04 | 20:26 | 1959 | Urban | Weather |  | 15 | 122 | 0.002442 | 2.0016e-05 | No
2020-01-04 | 20:26 | B716 | Urban | Unknown | Unknown | 96 | 90 | 0.011529 | 0.0001281 | No
2020-01-04 | 20:45 | B720 | Urban | Weather |  | 42 | 34 | 0.0019055 | 5.6045e-05 | No
2020-01-04 | 20:46 | C899 | Urban | Weather |  | 51 | 76.7255 | 0.0052215 | 6.8054e-05 | No
2020-01-04 | 21:00 | RD1269 | Urban | Weather |  | 33 | 75 | 0.0033026 | 4.4035e-05 | No
2020-01-04 | 21:00 | 49006 | Short rural | Weather |  | 6 | 34 | 0.00067113 | 1.9739e-05 | No
2020-01-04 | 21:08 | S776 | Urban | Asset Failure | Distribution substation | 24 | 817.5 | 0.026181 | 3.2026e-05 | No
2020-01-04 | 21:33 | LP1142 | Urban | Weather |  | 17 | 66 | 0.0014972 | 2.2685e-05 | No
2020-01-04 | 21:52 | 46752 | Urban | Weather |  | 84 | 97 | 0.010873 | 0.00011209 | No
2020-01-04 | 21:55 | B720 | Urban | Weather |  | 42 | 72 | 0.0040352 | 5.6045e-05 | No
2020-01-04 | 22:00 | BWE2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 139 | 0.00045729 | 3.2899e-06 | No
2020-01-04 | 22:02 | CV1221 | Urban | Asset Failure | Distribution substation | 72 | 87 | 0.0083587 | 9.6077e-05 | No
2020-01-04 | 22:29 | RBA2 | Short rural | Asset Failure | HV | 193 | 1307.4922 | 0.83018 | 0.00063494 | No
2020-01-04 | 22:36 | S735 | Short rural | Weather |  | 10 | 715 | 0.023523 | 3.2899e-05 | No
2020-01-04 | 22:46 | MYE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 417 | 38.6499 | 0.053023 | 0.0013719 | No
2020-01-04 | 22:51 | RW1218 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 73 | 2468.9315 | 0.59294 | 0.00024016 | No
2020-01-04 | 23:49 | HBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 23 | 857.8261 | 0.064909 | 7.5667e-05 | No
2020-01-04 | 23:51 | RW1218 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 183 | 1184.3333 | 0.71302 | 0.00060204 | No
2020-01-05 | 0:10 | HBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 810 | 179.1494 | 0.4774 | 0.0026648 | No
2020-01-05 | 3:13 | RW1229 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 168 | 657.9643 | 0.36365 | 0.0005527 | No
2020-01-05 | 6:02 | X482 | Short rural | Unknown | Unknown | 23 | 875 | 0.066208 | 7.5667e-05 | No
2020-01-05 | 7:26 | GV1204 | Urban | Unknown | Unknown | 31 | 122 | 0.0050467 | 4.1366e-05 | No
2020-01-05 | 8:33 | CX1284 | Short rural | Asset Failure | Distribution substation | 4 | 237 | 0.0031188 | 1.3159e-05 | No
2020-01-05 | 11:12 | S776 | Urban | Asset Failure | Distribution substation | 24 | 117.125 | 0.003751 | 3.2026e-05 | No
2020-01-05 | 12:07 | B211 | Urban | Asset Failure | Distribution substation | 186 | 141.3871 | 0.035092 | 0.0002482 | No
2020-01-05 | 12:11 | RW1292 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 26 | 811.6538 | 0.069426 | 8.5536e-05 | No
2020-01-05 | 14:23 | 35989 | Short rural | Asset Failure | Distribution substation | 1 | 217 | 0.0007139 | 3.2899e-06 | No
2020-01-05 | 15:38 | RW1292 | Short rural | Other | Fire | 19 | 1613.1053 | 0.10083 | 6.2507e-05 | No
2020-01-05 | 16:12 | SHD2 | Short rural | Asset Failure | HV | 1516 | 122.6768 | 0.61184 | 0.0049874 | No
2020-01-05 | 16:41 | ULL2 | Short rural | Other | Fire | 8 | 2014.625 | 0.053023 | 2.6319e-05 | No
2020-01-05 | 18:32 | X482 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 43 | 775.2093 | 0.10966 | 0.00014146 | No
2020-01-05 | 18:35 | T829 | Urban | Vegetation | Grow-in - NSP responsibility | 13 | 44 | 0.00076328 | 1.7347e-05 | No
2020-01-05 | 20:12 | A098 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 12 | 0.00011844 | 9.8696e-06 | No
2020-01-05 | 20:15 | BWF2 | Short rural | Asset Failure | HV | 21 | 1190.0952 | 0.08222 | 6.9087e-05 | No
2020-01-05 | 20:24 | AB1265 | Urban | Asset Failure | Distribution substation | 27 | 224 | 0.0080704 | 3.6029e-05 | No
2020-01-05 | 20:49 | MG1219 | Short rural | Unknown | Unknown | 3 | 312 | 0.0030793 | 9.8696e-06 | No
2020-01-05 | 21:29 | AZ1272 | Short rural | Asset Failure | Distribution substation | 11 | 363 | 0.013136 | 3.6188e-05 | No
2020-01-05 | 22:10 | RBA2 | Short rural | Unknown | Unknown | 193 | 64.285 | 0.040817 | 0.00063494 | No
2020-01-05 | 23:29 | 87220 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 51 | 2315.4706 | 0.3885 | 0.00016778 | No
2020-01-06 | 0:54 | 7974 | Urban | Asset Failure | Distribution substation | 1 | 776 | 0.0010355 | 1.3344e-06 | No
2020-01-06 | 1:30 | T828 | Short rural | Unknown | Unknown | 147 | 536 | 0.25921 | 0.00048361 | No
2020-01-06 | 5:04 | S738 | Short rural | Unknown | Unknown | 19 | 136 | 0.008501 | 6.2507e-05 | No
2020-01-06 | 6:23 | 1962 | Urban | Asset Failure | HV | 1781 | 73.4919 | 0.17466 | 0.0023766 | No
2020-01-06 | 6:46 | MG1286 | Short rural | Asset Failure | Distribution substation | 3 | 844 | 0.0083299 | 9.8696e-06 | No
2020-01-06 | 7:57 | HT1268 | Short rural | Third Party | Unauthorised access | 3 | 143 | 0.0014114 | 9.8696e-06 | No
2020-01-06 | 10:00 | RW1218 | Short rural | Unknown | Unknown | 20 | 21.7 | 0.0014278 | 6.5797e-05 | No
2020-01-06 | 11:45 | MVF2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 23 | 991.6957 | 0.075038 | 7.5667e-05 | No
2020-01-06 | 12:03 | A098 | Short rural | Other | Probable Accidental Damage - Vehicle Impact | 52 | 210.6923 | 0.036044 | 0.00017107 | No
2020-01-06 | 12:36 | RW1218 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 13 | 476.4615 | 0.020377 | 4.2768e-05 | No
2020-01-06 | 12:48 | 7973 | Urban | Asset Failure | Distribution substation | 15 | 62 | 0.001241 | 2.0016e-05 | No
2020-01-06 | 13:02 | X482 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 96 | 425.3229 | 0.13433 | 0.00031583 | No
2020-01-06 | 14:19 | CLA2 | Short rural | Unknown | Unknown | 5 | 1554 | 0.025562 | 1.6449e-05 | No
2020-01-06 | 15:23 | OA1233 | Short rural | Asset Failure | Distribution substation | 1 | 314 | 0.001033 | 3.2899e-06 | No
2020-01-06 | 15:50 | RW1281 | Short rural | Vegetation | Grow-in - NSP responsibility | 21 | 38.2381 | 0.0026418 | 6.9087e-05 | No
2020-01-06 | 16:30 | R260 | Short rural | Other | Isolation Request by EE | 1 | 101 | 0.00033228 | 3.2899e-06 | No
2020-01-06 | 17:08 | R260 | Short rural | Other | Isolation Request by EE | 1 | 106 | 0.00034873 | 3.2899e-06 | No
2020-01-06 | 17:58 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 120 | 66 | 0.026056 | 0.00039478 | No
2020-01-06 | 18:04 | CLD2 | Short rural | Unknown | Unknown | 981 | 13 | 0.041956 | 0.0032274 | No
2020-01-06 | 18:09 | RW1292 | Short rural | Asset Failure | Distribution substation | 9 | 210 | 0.0062178 | 2.9609e-05 | No
2020-01-06 | 20:42 | OP1172 | Urban | Asset Failure | Distribution substation | 7 | 1412 | 0.013189 | 9.3408e-06 | No
2020-01-06 | 20:47 | J478 | Short rural | Third Party | Vehicle impact | 12 | 196 | 0.0077378 | 3.9478e-05 | No
2020-01-06 | 20:48 | L534 | Short rural | Asset Failure | Distribution substation | 87 | 344 | 0.098459 | 0.00028622 | No
2020-01-06 | 20:56 | H745 | Short rural | Other | Fire | 70 | 783.7143 | 0.18048 | 0.00023029 | No
2020-01-06 | 21:09 | RW1218 | Short rural | Unknown | Unknown | 21 | 356 | 0.024595 | 6.9087e-05 | No
2020-01-06 | 21:17 | 46397 | Urban | Weather |  | 141 | 30.2482 | 0.0056912 | 0.00018815 | No
2020-01-06 | 21:18 | BDC2 | Short rural | Asset Failure | Distribution substation | 15 | 1185 | 0.058477 | 4.9348e-05 | No
2020-01-06 | 21:23 | FT1206 | Short rural | Vegetation | Grow-in - NSP responsibility | 394 | 34 | 0.044071 | 0.0012962 | No
2020-01-06 | 21:36 | WWF2 | Urban | Asset Failure | Distribution substation | 21 | 236 | 0.0066133 | 2.8022e-05 | No
2020-01-06 | 21:47 | OA1207 | Short rural | Third Party | Vehicle impact | 170 | 138.6588 | 0.077549 | 0.00055928 | No
2020-01-07 | 1:27 | 6419 | Urban | Asset Failure | HV | 469 | 108.7612 | 0.068066 | 0.00062583 | No
2020-01-07 | 2:09 | HR1269 | Urban | Unknown | Unknown | 2 | 100 | 0.00026688 | 2.6688e-06 | No
2020-01-07 | 2:31 | 8767 | Urban | Asset Failure | Distribution substation | 11 | 529 | 0.0077649 | 1.4678e-05 | No
2020-01-07 | 4:08 | MG1286 | Short rural | Unknown | Unknown | 10 | 382 | 0.012567 | 3.2899e-05 | No
2020-01-07 | 4:13 | 4870 | Urban | Asset Failure | Distribution substation | 1 | 1870 | 0.0024953 | 1.3344e-06 | No
2020-01-07 | 6:16 | 76225 | Short rural | Unknown | Unknown | 8 | 541.375 | 0.014248 | 2.6319e-05 | No
2020-01-07 | 6:25 | RW1218 | Short rural | Other | Fire | 16 | 467.0625 | 0.024585 | 5.2638e-05 | No
2020-01-07 | 7:18 | NK1332 | Urban | Asset Failure | Distribution substation | 30 | 37.5667 | 0.0015039 | 4.0032e-05 | No
2020-01-07 | 7:26 | SZ1242 | Short rural | Unknown | Unknown | 15 | 139 | 0.0068594 | 4.9348e-05 | No
2020-01-07 | 8:49 | A324 | Urban | Asset Failure | Distribution substation | 1 | 368 | 0.00049106 | 1.3344e-06 | No
2020-01-07 | 8:57 | JBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 59 | 13.8814 | 0.0026944 | 0.0001941 | No
2020-01-07 | 9:32 | ULH2 | Short rural | Asset Failure | Distribution substation | 8 | 151.125 | 0.0039774 | 2.6319e-05 | No
2020-01-07 | 9:39 | RBB2 | Short rural | Other | Fire | 7 | 2010.7143 | 0.046305 | 2.3029e-05 | No
2020-01-07 | 9:49 | RW1218 | Short rural | Other | Probable Rain incl. Mist and Fog | 1 | 1634 | 0.0053756 | 3.2899e-06 | No
2020-01-07 | 10:15 | L588 | Short rural | Asset Failure | Distribution substation | 1 | 189 | 0.00062178 | 3.2899e-06 | No
2020-01-07 | 10:28 | BWC2 | Short rural | Asset Failure | Distribution substation | 1 | 718 | 0.0023621 | 3.2899e-06 | No
2020-01-07 | 10:31 | W111 | Short rural | Asset Failure | Distribution substation | 1 | 2022 | 0.0066521 | 3.2899e-06 | No
2020-01-07 | 11:43 | KVA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 366 | 210.6393 | 0.25363 | 0.0012041 | No
2020-01-07 | 12:08 | ULE2 | Short rural | Other | Fire | 1 | 40 | 0.00013159 | 3.2899e-06 | No
2020-01-07 | 12:30 | 35816 | Short rural | Asset Failure | Distribution substation | 4 | 1192.25 | 0.015689 | 1.3159e-05 | No
2020-01-07 | 15:12 | HBB2 | Short rural | Asset Failure | Distribution substation | 3 | 74 | 0.00073035 | 9.8696e-06 | No
2020-01-07 | 15:19 | MG1286 | Short rural | Vegetation | Grow-in - NSP responsibility | 10 | 219 | 0.0072048 | 3.2899e-05 | No
2020-01-07 | 15:25 | SC1238 | Urban | Third Party | Vehicle impact | 49 | 58 | 0.0037924 | 6.5386e-05 | No
2020-01-07 | 16:41 | FF1217 | Urban | Asset Failure | Distribution substation | 113 | 130.3274 | 0.019652 | 0.00015079 | No
2020-01-07 | 20:51 | GV1249 | Urban | Asset Failure | Distribution substation | 1 | 993 | 0.0013251 | 1.3344e-06 | No
2020-01-07 | 21:06 | B720 | Urban | Weather |  | 42 | 68 | 0.003811 | 5.6045e-05 | No
2020-01-07 | 21:29 | RW1255 | Short rural | Weather |  | 20 | 393 | 0.025858 | 6.5797e-05 | No
2020-01-07 | 23:07 | H745 | Short rural | Weather |  | 68 | 94.8382 | 0.021216 | 0.00022371 | No
2020-01-07 | 23:39 | 10251 | Urban | Weather |  | 56 | 168 | 0.012554 | 7.4726e-05 | No
2020-01-07 | 23:44 | OA1233 | Short rural | Weather |  | 3 | 139 | 0.0013719 | 9.8696e-06 | No
2020-01-07 | 23:45 | NN1233 | Short rural | Weather |  | 696 | 205.227 | 0.46992 | 0.0022897 | No
2020-01-08 | 0:04 | J478 | Short rural | Weather |  | 968.0251 | 313.2145 | 0.99748 | 0.0031847 | No
2020-01-08 | 0:04 | J495 | Short rural | Weather |  | 952.9749 | 313.2145 | 0.98198 | 0.0031352 | No
2020-01-08 | 0:21 | J506 | Urban | Asset Failure | Distribution substation | 29.3753 | 261.2927 | 0.010242 | 3.9198e-05 | No
2020-01-08 | 0:21 | 27341 | Urban | Asset Failure | Distribution substation | 11.6247 | 261.2927 | 0.0040532 | 1.5512e-05 | No
2020-01-08 | 0:34 | J489 | Urban | Other | Probable Lightning/Electrical Storm | 1 | 748 | 0.00099813 | 1.3344e-06 | No
2020-01-08 | 0:55 | 27454 | Short rural | Weather |  | 426 | 221.5469 | 0.31049 | 0.0014015 | No
2020-01-08 | 1:50 | LP1312 | Urban | Asset Failure | Distribution substation | 30 | 703 | 0.028142 | 4.0032e-05 | No
2020-01-08 | 1:50 | 55885 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 72 | 49 | 0.0047078 | 9.6077e-05 | No
2020-01-08 | 2:22 | D813 | Short rural | Weather |  | 3 | 1088 | 0.010738 | 9.8696e-06 | No
2020-01-08 | 2:24 | RW1255 | Short rural | Weather |  | 224 | 7 | 0.0051585 | 0.00073693 | No
2020-01-08 | 4:00 | LP1322 | Urban | Unknown | Unknown | 30 | 230 | 0.0092074 | 4.0032e-05 | No
2020-01-08 | 6:30 | HT1268 | Short rural | Third Party | Unauthorised access | 3 | 130 | 0.001283 | 9.8696e-06 | No
2020-01-08 | 6:32 | OA1233 | Short rural | Unknown | Unknown | 8 | 692 | 0.018213 | 2.6319e-05 | No
2020-01-08 | 6:42 | RBA2 | Short rural | Other | Fire | 16 | 308 | 0.016212 | 5.2638e-05 | No
2020-01-08 | 7:07 | 6420 | Urban | Weather |  | 10 | 268 | 0.0035762 | 1.3344e-05 | No
2020-01-08 | 7:31 | X881 | Short rural | Other | Probable Lightning/Electrical Storm | 17 | 389 | 0.021756 | 5.5928e-05 | No
2020-01-08 | 7:35 | S741 | Short rural | Asset Failure | Distribution substation | 2 | 535 | 0.0035202 | 6.5797e-06 | No
2020-01-08 | 9:00 | A095 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 836 | 0.0027503 | 3.2899e-06 | No
2020-01-08 | 9:35 | S769 | Urban | Asset Failure | Distribution substation | 30 | 575 | 0.023018 | 4.0032e-05 | No
2020-01-08 | 10:04 | BDC2 | Short rural | Asset Failure | Distribution substation | 2 | 134 | 0.00088168 | 6.5797e-06 | No
2020-01-08 | 10:46 | RW1281 | Short rural | Asset Failure | Distribution substation | 1 | 294 | 0.00096722 | 3.2899e-06 | No
2020-01-08 | 10:55 | C824 | Urban | Asset Failure | Distribution substation | 1 | 223 | 0.00029757 | 1.3344e-06 | No
2020-01-08 | 11:05 | RBA2 | Short rural | Asset Failure | Distribution substation | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2020-01-08 | 12:45 | L504 | Urban | Asset Failure | Distribution substation | 14 | 95 | 0.0017748 | 1.8682e-05 | No
2020-01-08 | 13:20 | X866 | Urban | Asset Failure | Distribution substation | 11 | 155 | 0.0022752 | 1.4678e-05 | No
2020-01-08 | 15:12 | 35815 | Short rural | Vegetation | Grow-in - NSP responsibility | 33 | 137 | 0.014873 | 0.00010857 | No
2020-01-08 | 15:42 | OA1207 | Short rural | Unknown | Unknown | 1 | 198 | 0.00065139 | 3.2899e-06 | No
2020-01-08 | 15:43 | J495 | Short rural | Weather |  | 16 | 74.9375 | 0.0039445 | 5.2638e-05 | No
2020-01-08 | 15:55 | NA1270 | Short rural | Asset Failure | HV | 8 | 2827.5 | 0.074417 | 2.6319e-05 | No
2020-01-08 | 18:02 | T828 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 270 | 160.8185 | 0.14285 | 0.00088826 | No
2020-01-08 | 18:12 | DS1226 | Urban | Vegetation | Grow-in - NSP responsibility | 22 | 100 | 0.0029357 | 2.9357e-05 | No
2020-01-08 | 18:27 | 55870 | Urban | Asset Failure | Distribution substation | 59 | 110 | 0.0086602 | 7.873e-05 | No
2020-01-09 | 4:59 | D813 | Short rural | Asset Failure | Distribution substation | 2 | 835 | 0.0054941 | 6.5797e-06 | No
2020-01-09 | 7:04 | R293 | Short rural | Unknown | Unknown | 5 | 218 | 0.003586 | 1.6449e-05 | No
2020-01-09 | 7:26 | A095 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 148 | 0.0019476 | 1.3159e-05 | No
2020-01-09 | 8:33 | R293 | Short rural | Unknown | Unknown | 2 | 132 | 0.00086852 | 6.5797e-06 | No
2020-01-09 | 9:30 | L585 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 5 | 421 | 0.0069252 | 1.6449e-05 | No
2020-01-09 | 9:55 | 19857 | Urban | Unknown | Unknown | 35 | 143 | 0.0066787 | 4.6704e-05 | No
2020-01-09 | 10:11 | YYB2 | Short rural | Other | Fire | 1 | 4511 | 0.014841 | 3.2899e-06 | No
2020-01-09 | 11:49 | BWH2 | Short rural | Other | Fire | 1176 | 97.4133 | 0.37688 | 0.0038689 | No
2020-01-09 | 12:28 | YYB2 | Short rural | Other | Fire | 1 | 194 | 0.00063823 | 3.2899e-06 | No
2020-01-09 | 13:29 | BX1232 | Urban | Asset Failure | Distribution substation | 24 | 153 | 0.0048999 | 3.2026e-05 | No
2020-01-09 | 14:15 | CS1276 | Urban | Asset Failure | Distribution substation | 1 | 141 | 0.00018815 | 1.3344e-06 | No
2020-01-09 | 16:10 | RW1218 | Short rural | Other | Fire | 13 | 1483.5385 | 0.063448 | 4.2768e-05 | No
2020-01-09 | 16:24 | T838 | Short rural | Asset Failure | Distribution substation | 21 | 239 | 0.016512 | 6.9087e-05 | No
2020-01-09 | 16:51 | 35983 | Short rural | Third Party | Other | 1 | 365 | 0.0012008 | 3.2899e-06 | No
2020-01-09 | 19:58 | BWH2 | Short rural | Other | Fire | 7 | 1718.8571 | 0.039584 | 2.3029e-05 | No
2020-01-09 | 20:13 | CV1236 | Urban | Animal | Animal Impact | 1660 | 45 | 0.09968 | 0.0022151 | No
2020-01-09 | 21:46 | 7501 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 766 | 0.0075601 | 9.8696e-06 | No
2020-01-09 | 22:38 | BDG2 | Short rural | Animal | Animal Impact | 18 | 178 | 0.010541 | 5.9218e-05 | No
2020-01-10 | 2:32 | L947 | Short rural | Animal | Animal Impact | 23 | 287 | 0.021716 | 7.5667e-05 | No
2020-01-10 | 4:41 | X482 | Short rural | Unknown | Unknown | 11 | 335.4545 | 0.01214 | 3.6188e-05 | No
2020-01-10 | 7:12 | B217 | Urban | Animal | Animal Impact | 38 | 37.7105 | 0.0019122 | 5.0707e-05 | No
2020-01-10 | 7:21 | L588 | Short rural | Animal | Animal Impact | 170 | 336.0765 | 0.18796 | 0.00055928 | No
2020-01-10 | 7:21 | L588 | Short rural | Unknown | Unknown | 313 | 261.8275 | 0.26961 | 0.0010297 | No
2020-01-10 | 8:47 | YYB2 | Short rural | Other | Fire | 1 | 3396 | 0.011172 | 3.2899e-06 | No
2020-01-10 | 9:04 | TM1284 | Short rural | Other | Fire | 12 | 298.3333 | 0.011778 | 3.9478e-05 | No
2020-01-10 | 9:14 | RV1206 | Short rural | Animal | Animal Impact | 212 | 113.3726 | 0.079072 | 0.00069745 | No
2020-01-10 | 11:06 | R211 | Short rural | Asset Failure | Distribution substation | 1 | 230 | 0.00075667 | 3.2899e-06 | No
2020-01-10 | 11:37 | 17058 | Urban | Third Party | Other | 19 | 68.1053 | 0.0017267 | 2.5354e-05 | No
2020-01-10 | 13:05 | 87222 | Long rural | Unknown | Unknown | 22 | 238.5 | 16.7102 | 0.070064 | No
2020-01-10 | 13:38 | BWH2 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 331 | 8133.7976 | 8.8573 | 0.0010889 | No
2020-01-10 | 14:08 | B720 | Urban | Weather |  | 42 | 134 | 0.00751 | 5.6045e-05 | No
2020-01-10 | 14:38 | YYB2 | Short rural | Other | Fire | 1 | 56 | 0.00018423 | 3.2899e-06 | No
2020-01-10 | 14:45 | CV1280 | Urban | Asset Failure | Distribution substation | 10 | 618 | 0.0082466 | 1.3344e-05 | No
2020-01-10 | 15:35 | BWH2 | Short rural | Asset Failure | HV | 829 | 78.5006 | 0.21409 | 0.0027273 | No
2020-01-10 | 15:41 | RBE2 | Short rural | Asset Failure | Distribution substation | 1 | 1414 | 0.0046519 | 3.2899e-06 | No
2020-01-10 | 16:14 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 349 | 399.2607 | 0.45842 | 0.0011482 | No
2020-01-10 | 16:37 | CX1210 | Short rural | Vegetation | Grow-in - NSP responsibility | 813 | 187.663 | 0.50193 | 0.0026747 | No
2020-01-10 | 17:18 | GG1232 | Short rural | Asset Failure | LV | 15 | 282.1333 | 0.013923 | 4.9348e-05 | No
2020-01-10 | 17:39 | 8801 | Short rural | Other | Probable Lightning/Electrical Storm | 5 | 22.4 | 0.00036846 | 1.6449e-05 | No
2020-01-10 | 17:53 | 8685 | Urban | Asset Failure | Distribution substation | 27 | 123.3704 | 0.0044449 | 3.6029e-05 | No
2020-01-10 | 18:14 | R293 | Short rural | Animal | Animal Impact | 2 | 196 | 0.0012896 | 6.5797e-06 | No
2020-01-10 | 18:19 | FF1217 | Urban | Asset Failure | Distribution substation | 38 | 172 | 0.0087216 | 5.0707e-05 | No
2020-01-10 | 18:45 | B720 | Urban | Overload |  | 127 | 297 | 0.050332 | 0.00016947 | No
2020-01-10 | 18:48 | 49006 | Short rural | Overload |  | 16 | 291 | 0.015318 | 5.2638e-05 | No
2020-01-10 | 19:40 | 19856 | Urban | Animal | Animal Impact | 18 | 317 | 0.0076141 | 2.4019e-05 | No
2020-01-10 | 19:44 | SN1230 | Short rural | Unknown | Unknown | 3 | 51 | 0.00050335 | 9.8696e-06 | No
2020-01-10 | 20:52 | SN1230 | Short rural | Unknown | Unknown | 3 | 62 | 0.00061191 | 9.8696e-06 | No
2020-01-10 | 21:28 | T893 | Urban | Asset Failure | Distribution substation | 1 | 112 | 0.00014945 | 1.3344e-06 | No
2020-01-11 | 6:48 | 1953 | Urban | Asset Failure | HV | 23 | 165.2174 | 0.0050707 | 3.0691e-05 | No
2020-01-11 | 7:12 | A098 | Short rural | Asset Failure | Distribution substation | 19 | 22.4211 | 0.0014015 | 6.2507e-05 | No
2020-01-11 | 8:35 | TM1284 | Short rural | Vegetation | Grow-in - NSP responsibility | 839 | 17.5161 | 0.048348 | 0.0027602 | No
2020-01-11 | 9:09 | KMF2 | Urban | Asset Failure | LV | 130 | 241 | 0.041807 | 0.00017347 | No
2020-01-11 | 9:19 | ULH2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 21 | 370.0476 | 0.025566 | 6.9087e-05 | No
2020-01-11 | 9:27 | 1960 | Urban | Asset Failure | HV | 804 | 2.0323 | 0.0021804 | 0.0010729 | No
2020-01-11 | 9:41 | NM1213 | Urban | Asset Failure | Distribution substation | 8 | 590 | 0.0062984 | 1.0675e-05 | No
2020-01-11 | 9:51 | J495 | Short rural | Unknown | Unknown | 2 | 68 | 0.00044742 | 6.5797e-06 | No
2020-01-11 | 15:07 | RW1218 | Short rural | Asset Failure | Distribution substation | 1 | 189 | 0.00062178 | 3.2899e-06 | No
2020-01-11 | 16:45 | ULE2 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 18 | 108 | 0.0063955 | 5.9218e-05 | No
2020-01-11 | 17:29 | ULH2 | Short rural | Unknown | Unknown | 1 | 917 | 0.0030168 | 3.2899e-06 | No
2020-01-11 | 20:05 | J515 | Urban | Asset Failure | Distribution substation | 1 | 502 | 0.00066987 | 1.3344e-06 | No
2020-01-12 | 3:06 | HR1269 | Urban | Unknown | Unknown | 5 | 267 | 0.0017814 | 6.672e-06 | No
2020-01-12 | 3:24 | R211 | Short rural | Vegetation | Grow-in - NSP responsibility | 263 | 151 | 0.13065 | 0.00086523 | No
2020-01-12 | 7:35 | SHB2 | Urban | Asset Failure | Distribution substation | 30 | 87 | 0.0034828 | 4.0032e-05 | No
2020-01-12 | 8:36 | HR1269 | Urban | Asset Failure | Distribution substation | 1 | 197 | 0.00026288 | 1.3344e-06 | No
2020-01-12 | 9:46 | 8801 | Short rural | Asset Failure | Distribution substation | 1 | 490 | 0.001612 | 3.2899e-06 | No
2020-01-12 | 10:44 | A046 | Short rural | Asset Failure | Distribution substation | 12 | 148 | 0.0058428 | 3.9478e-05 | No
2020-01-12 | 11:01 | SHB2 | Urban | Asset Failure | Distribution substation | 30 | 135 | 0.0054043 | 4.0032e-05 | No
2020-01-12 | 14:27 | MVB2 | Short rural | Asset Failure | Distribution substation | 1 | 164 | 0.00053954 | 3.2899e-06 | No
2020-01-12 | 16:36 | CD1234 | Short rural | Unknown | Unknown | 4 | 239 | 0.0031451 | 1.3159e-05 | No
2020-01-12 | 21:41 | HBC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 283 | 74.742 | 0.069587 | 0.00093103 | No
2020-01-12 | 23:50 | HBB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 34 | 618 | 0.069127 | 0.00011186 | No
2020-01-13 | 0:42 | KC1262 | Short rural | Asset Failure | HV | 2 | 518 | 0.0034083 | 6.5797e-06 | No
2020-01-13 | 2:03 | LL1112 | Urban | Asset Failure | Distribution substation | 13 | 116 | 0.0020123 | 1.7347e-05 | No
2020-01-13 | 4:18 | WBB2 | Short rural | Asset Failure | LV | 1058 | 149.3941 | 0.51999 | 0.0034807 | No
2020-01-13 | 5:08 | R260 | Short rural | Asset Failure | Subtransmission | 299 | 202.8829 | 0.19957 | 0.00098367 | No
2020-01-13 | 6:30 | KC1262 | Short rural | Asset Failure | LV | 30 | 170 | 0.016778 | 9.8696e-05 | No
2020-01-13 | 7:11 | NG1210 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 158 | 0.0005198 | 3.2899e-06 | No
2020-01-13 | 7:33 | L584 | Short rural | Asset Failure | Distribution substation | 3 | 76 | 0.00075009 | 9.8696e-06 | No
2020-01-13 | 8:36 | SXC2 | Short rural | Other | Fire | 1 | 488 | 0.0016055 | 3.2899e-06 | No
2020-01-13 | 9:19 | WD1225 | Short rural | Unknown | Unknown | 2 | 852 | 0.0056059 | 6.5797e-06 | No
2020-01-13 | 9:39 | BX1222 | Urban | Asset Failure | Distribution substation | 1 | 402 | 0.00053643 | 1.3344e-06 | No
2020-01-13 | 10:00 | J504 | Urban | Asset Failure | Distribution substation | 1 | 647 | 0.00086336 | 1.3344e-06 | No
2020-01-13 | 11:04 | CLC2 | Short rural | Asset Failure | HV | 293 | 165.215 | 0.15926 | 0.00096393 | No
2020-01-13 | 13:39 | YYA2 | Short rural | Other | Fire | 1 | 81 | 0.00026648 | 3.2899e-06 | No
2020-01-13 | 13:45 | 35990 | Short rural | Asset Failure | Distribution substation | 1 | 321 | 0.001056 | 3.2899e-06 | No
2020-01-13 | 14:05 | MVC2 | Short rural | Other | Fault within HV customers installation - Defective Equipment | 9 | 191 | 0.0056553 | 2.9609e-05 | No
2020-01-13 | 16:22 | T828 | Short rural | Asset Failure | HV | 31 | 31.0645 | 0.0031681 | 0.00010199 | No
2020-01-13 | 23:26 | J503 | Urban | Asset Failure | Distribution substation | 1 | 598 | 0.00079797 | 1.3344e-06 | No
2020-01-14 | 1:01 | 27027 | Urban | Asset Failure | Distribution substation | 21 | 209 | 0.0058567 | 2.8022e-05 | No
2020-01-14 | 5:39 | L940 | Short rural | Asset Failure | Distribution substation | 10 | 468.1 | 0.0154 | 3.2899e-05 | No
2020-01-14 | 5:55 | T831 | Short rural | Weather |  | 11 | 478.2727 | 0.017308 | 3.6188e-05 | No
2020-01-14 | 7:20 | LP1422 | Urban | Asset Failure | HV | 382 | 82.8717 | 0.042243 | 0.00050974 | No
2020-01-14 | 9:01 | T831 | Short rural | Unknown | Unknown | 15 | 439 | 0.021664 | 4.9348e-05 | No
2020-01-14 | 10:01 | SXB2 | Short rural | Asset Failure | Distribution substation | 1 | 86 | 0.00028293 | 3.2899e-06 | No
2020-01-14 | 10:42 | ULE2 | Short rural | Other | Fire | 3 | 102 | 0.0010067 | 9.8696e-06 | No
2020-01-14 | 10:49 | YYB2 | Short rural | Other | Fire | 1 | 141 | 0.00046387 | 3.2899e-06 | No
2020-01-14 | 11:05 | NK1342 | Urban | Vegetation | Grow-in - NSP responsibility | 42 | 571 | 0.032002 | 5.6045e-05 | No
2020-01-14 | 11:10 | 1962 | Urban | Unknown | Unknown | 1 | 228 | 0.00030424 | 1.3344e-06 | No
2020-01-14 | 11:14 | 811 | Short rural | Other | Fault within HV customers installation - Defective Equipment | 2 | 110 | 0.00072377 | 6.5797e-06 | No
2020-01-14 | 11:33 | NK1342 | Urban | Vegetation | Grow-in - NSP responsibility | 8 | 122 | 0.0013024 | 1.0675e-05 | No
2020-01-14 | 11:49 | NA1270 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 47 | 208.9574 | 0.03231 | 0.00015462 | No
2020-01-14 | 12:09 | MM1142 | Urban | Asset Failure | Distribution substation | 33 | 271.5758 | 0.011959 | 4.4035e-05 | No
2020-01-14 | 12:34 | ULE2 | Short rural | Other | Fire | 1 | 127 | 0.00041781 | 3.2899e-06 | No
2020-01-14 | 15:22 | 8685 | Urban | Unknown | Unknown | 9 | 288 | 0.0034588 | 1.201e-05 | No
2020-01-14 | 16:59 | X870 | Urban | Third Party | Vehicle impact | 8 | 475.75 | 0.0050787 | 1.0675e-05 | No
2020-01-14 | 17:05 | C852 | Urban | Vegetation | Grow-in - NSP responsibility | 86 | 74 | 0.0084921 | 0.00011476 | No
2020-01-14 | 18:29 | 35816 | Short rural | Asset Failure | Distribution substation | 1 | 186 | 0.00061191 | 3.2899e-06 | No
2020-01-14 | 20:40 | 68179 | Urban | Asset Failure | Distribution substation | 23 | 40.4348 | 0.001241 | 3.0691e-05 | No
2020-01-15 | 8:25 | SN1230 | Short rural | Other | Fire | 23 | 319 | 0.024138 | 7.5667e-05 | No
2020-01-15 | 9:16 | YYA2 | Short rural | Other | Fire | 12 | 191 | 0.0075404 | 3.9478e-05 | No
2020-01-15 | 11:04 | 27454 | Short rural | Other | Isolation Request by EE | 6 | 18 | 0.00035531 | 1.9739e-05 | No
2020-01-15 | 11:17 | ULH2 | Short rural | Other | Fire | 11 | 1757.7273 | 0.06361 | 3.6188e-05 | No
2020-01-15 | 15:46 | 1962 | Urban | Asset Failure | Distribution substation | 1 | 241 | 0.00032159 | 1.3344e-06 | No
2020-01-15 | 17:32 | 87222 | Long rural | Weather |  | 209 | 299.7129 | 199.4904 | 0.66561 | No
2020-01-15 | 18:17 | X217 | Short rural | Asset Failure | HV | 22 | 77 | 0.005573 | 7.2377e-05 | No
2020-01-16 | 2:26 | LL1112 | Urban | Asset Failure | Distribution substation | 38 | 405.8947 | 0.020582 | 5.0707e-05 | No
2020-01-16 | 4:46 | RW1218 | Short rural | Unknown | Unknown | 79 | 351 | 0.091225 | 0.0002599 | No
2020-01-16 | 5:29 | C857 | Urban | Weather |  | 267.9851 | 95.8695 | 0.034283 | 0.0003576 | No
2020-01-16 | 5:29 | PH1264 | Urban | Weather |  | 207.0149 | 95.8695 | 0.026483 | 0.00027624 | No
2020-01-16 | 5:44 | 35702 | Urban | Weather |  | 64 | 216 | 0.018447 | 8.5402e-05 | No
2020-01-16 | 6:06 | T874 | Short rural | Other | Probable Lightning/Electrical Storm | 457 | 85.1094 | 0.12796 | 0.0015035 | No
2020-01-16 | 6:08 | CD1230 | Short rural | Weather |  | 11 | 597 | 0.021605 | 3.6188e-05 | No
2020-01-16 | 6:10 | RW1218 | Short rural | Other | Probable Lightning/Electrical Storm | 79 | 272.3924 | 0.070795 | 0.0002599 | No
2020-01-16 | 6:26 | T868 | Short rural | Weather |  | 61 | 176.3934 | 0.035399 | 0.00020068 | No
2020-01-16 | 6:36 | RW1281 | Short rural | Weather |  | 1 | 461 | 0.0015166 | 3.2899e-06 | No
2020-01-16 | 6:45 | 87222 | Long rural | Other | Probable Rain incl. Mist and Fog | 4 | 381 | 4.8535 | 0.012739 | No
2020-01-16 | 7:00 | 35312 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 40 | 70 | 0.0037363 | 5.3376e-05 | No
2020-01-16 | 7:03 | ULH2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 377 | 0.0012403 | 3.2899e-06 | No
2020-01-16 | 7:03 | CR1214 | Urban | Asset Failure | LV | 905.0458 | 87.2831 | 0.10541 | 0.0012077 | No
2020-01-16 | 7:03 | CR1262 | Urban | Asset Failure | LV | 1764.9542 | 87.2831 | 0.20557 | 0.0023552 | No
2020-01-16 | 7:11 | 8685 | Urban | Asset Failure | Distribution substation | 77 | 244 | 0.025071 | 0.00010275 | No
2020-01-16 | 7:17 | 27454 | Short rural | Other | Probable Lightning/Electrical Storm | 8 | 462 | 0.012159 | 2.6319e-05 | No
2020-01-16 | 7:18 | OA1233 | Short rural | Other | Probable Lightning/Electrical Storm | 14 | 282.7143 | 0.013021 | 4.6058e-05 | No
2020-01-16 | 7:19 | RW1281 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 412 | 0.0013554 | 3.2899e-06 | No
2020-01-16 | 7:22 | LL1112 | Urban | Weather |  | 1045 | 116.7091 | 0.16274 | 0.0013944 | No
2020-01-16 | 7:25 | X881 | Short rural | Asset Failure | Distribution substation | 8 | 476 | 0.012528 | 2.6319e-05 | No
2020-01-16 | 7:31 | PH1230 | Urban | Asset Failure | Distribution substation | 18 | 299 | 0.0071817 | 2.4019e-05 | No
2020-01-16 | 8:05 | R211 | Short rural | Weather |  | 7 | 324 | 0.0074614 | 2.3029e-05 | No
2020-01-16 | 8:36 | 41533 | Short rural | Weather |  | 15 | 407 | 0.020085 | 4.9348e-05 | No
2020-01-16 | 9:30 | KVD2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 228 | 0.00075009 | 3.2899e-06 | No
2020-01-16 | 9:31 | MM1112 | Urban | Other | Probable Lightning/Electrical Storm | 6 | 101 | 0.00080865 | 8.0064e-06 | No
2020-01-16 | 9:32 | W123 | Short rural | Weather |  | 2 | 413 | 0.0027174 | 6.5797e-06 | No
2020-01-16 | 9:34 | 35695 | Short rural | Weather |  | 40 | 259 | 0.034083 | 0.00013159 | No
2020-01-16 | 9:35 | SY1322 | Urban | Other | Probable Lightning/Electrical Storm | 48 | 165 | 0.010568 | 6.4051e-05 | No
2020-01-16 | 10:10 | BWH2 | Short rural | Weather |  | 6 | 498 | 0.0098301 | 1.9739e-05 | No
2020-01-16 | 10:28 | CS1276 | Urban | Unknown | Unknown | 6 | 369 | 0.0029544 | 8.0064e-06 | No
2020-01-16 | 10:42 | CA1210 | Urban | Asset Failure | Distribution substation | 1 | 216 | 0.00028823 | 1.3344e-06 | No
2020-01-16 | 10:50 | LP1312 | Urban | Asset Failure | Distribution substation | 1 | 143 | 0.00019082 | 1.3344e-06 | No
2020-01-16 | 11:24 | B211 | Urban | Asset Failure | Distribution substation | 27 | 312 | 0.011241 | 3.6029e-05 | No
2020-01-16 | 12:01 | X217 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 26 | 162 | 0.013857 | 8.5536e-05 | No
2020-01-16 | 12:09 | WH1224 | Urban | Asset Failure | Distribution substation | 48 | 241 | 0.015436 | 6.4051e-05 | No
2020-01-16 | 12:26 | 25784 | Urban | Unknown | Unknown | 7 | 310 | 0.0028956 | 9.3408e-06 | No
2020-01-16 | 13:24 | W123 | Short rural | Weather |  | 1 | 175 | 0.00057573 | 3.2899e-06 | No
2020-01-16 | 13:24 | 35767 | Urban | Asset Failure | Distribution substation | 2 | 156 | 0.00041633 | 2.6688e-06 | No
2020-01-16 | 13:40 | RW1281 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 20 | 6.5797e-05 | 3.2899e-06 | No
2020-01-16 | 13:44 | RW1281 | Short rural | Weather |  | 2 | 150 | 0.00098696 | 6.5797e-06 | No
2020-01-16 | 14:24 | RW1281 | Short rural | Weather |  | 1 | 170 | 0.00055928 | 3.2899e-06 | No
2020-01-16 | 14:48 | RW1218 | Short rural | Weather |  | 5 | 61 | 0.0010034 | 1.6449e-05 | No
2020-01-16 | 14:55 | BWH2 | Short rural | Asset Failure | Distribution substation | 2 | 278 | 0.0018292 | 6.5797e-06 | No
2020-01-16 | 15:10 | CLD2 | Short rural | Weather |  | 982 | 104 | 0.33599 | 0.0032306 | No
2020-01-16 | 16:07 | DP1284 | Short rural | Weather |  | 40 | 105 | 0.013817 | 0.00013159 | No
2020-01-16 | 16:13 | NA1270 | Short rural | Weather |  | 4 | 127 | 0.0016713 | 1.3159e-05 | No
2020-01-16 | 16:28 | DP1206 | Urban | Weather |  | 2789 | 46.2209 | 0.17202 | 0.0037216 | No
2020-01-16 | 16:29 | APE2 | Short rural | Weather |  | 50 | 278.5 | 0.045811 | 0.00016449 | No
2020-01-16 | 16:30 | JS1122 | Short rural | Asset Failure | Distribution substation | 1 | 179 | 0.00058889 | 3.2899e-06 | No
2020-01-16 | 16:30 | 27454 | Short rural | Weather |  | 1 | 210 | 0.00069087 | 3.2899e-06 | No
2020-01-16 | 16:31 | L941 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 249 | 0.0016384 | 6.5797e-06 | No
2020-01-16 | 16:47 | FT1204 | Short rural | Weather |  | 211 | 167.1374 | 0.11602 | 0.00069416 | No
2020-01-16 | 17:10 | MG1267 | Short rural | Weather |  | 10 | 207 | 0.00681 | 3.2899e-05 | No
2020-01-16 | 17:20 | BDA2 | Short rural | Weather |  | 3 | 72 | 0.00071061 | 9.8696e-06 | No
2020-01-16 | 17:29 | S786 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 78 | 0.00051322 | 6.5797e-06 | No
2020-01-16 | 18:36 | OA1207 | Short rural | Weather |  | 7 | 224 | 0.0051585 | 2.3029e-05 | No
2020-01-16 | 18:38 | OA1244 | Short rural | Other | Probable Lightning/Electrical Storm | 11 | 105 | 0.0037998 | 3.6188e-05 | No
2020-01-16 | 18:54 | DP1284 | Short rural | Weather |  | 8 | 224 | 0.0058954 | 2.6319e-05 | No
2020-01-16 | 19:39 | FT1204 | Short rural | Weather |  | 36 | 155 | 0.018357 | 0.00011844 | No
2020-01-16 | 19:40 | BK1251 | Short rural | Other | Probable Rain incl. Mist and Fog | 1 | 82 | 0.00026977 | 3.2899e-06 | No
2020-01-16 | 19:44 | ER1122 | Short rural | Weather |  | 64 | 150 | 0.031583 | 0.00021055 | No
2020-01-16 | 19:54 | 35816 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 461 | 0.0015166 | 3.2899e-06 | No
2020-01-16 | 20:48 | MG1267 | Short rural | Asset Failure | Distribution substation | 1 | 978 | 0.0032175 | 3.2899e-06 | No
2020-01-16 | 20:53 | WD1221 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 144 | 0.001895 | 1.3159e-05 | No
2020-01-16 | 23:35 | J506 | Urban | Asset Failure | Distribution substation | 40 | 77 | 0.0041099 | 5.3376e-05 | No
2020-01-17 | 2:42 | CV1236 | Urban | Unknown | Unknown | 12 | 306 | 0.0048999 | 1.6013e-05 | No
2020-01-17 | 2:46 | OP1262 | Short rural | Other | Probable Lightning/Electrical Storm | 19 | 1017 | 0.06357 | 6.2507e-05 | No
2020-01-17 | 3:58 | PK1288 | Short rural | Weather |  | 27 | 541.4444 | 0.048095 | 8.8826e-05 | No
2020-01-17 | 4:37 | A053 | Urban | Asset Failure | HV | 149 | 263.4362 | 0.052378 | 0.00019883 | No
2020-01-17 | 6:24 | J502 | Urban | Asset Failure | Distribution substation | 117 | 92.4957 | 0.014441 | 0.00015612 | No
2020-01-17 | 6:36 | MR2232 | Short rural | Unknown | Unknown | 133 | 138.0602 | 0.060408 | 0.00043755 | No
2020-01-17 | 6:44 | MR2232 | Short rural | Unknown | Unknown | 177 | 266 | 0.15489 | 0.00058231 | No
2020-01-17 | 7:07 | HKF2 | Short rural | Asset Failure | Distribution substation | 1 | 254 | 0.00083563 | 3.2899e-06 | No
2020-01-17 | 9:44 | A324 | Urban | Asset Failure | Distribution substation | 1 | 539 | 0.00071924 | 1.3344e-06 | No
2020-01-17 | 10:49 | NN1251 | Short rural | Unknown | Unknown | 1 | 262 | 0.00086194 | 3.2899e-06 | No
2020-01-17 | 11:58 | L511 | Urban | Asset Failure | Distribution substation | 77 | 274.2468 | 0.028179 | 0.00010275 | No
2020-01-17 | 12:48 | APC2 | Short rural | Weather |  | 2 | 94 | 0.00061849 | 6.5797e-06 | No
2020-01-17 | 13:29 | PK1288 | Short rural | Weather |  | 27 | 325.6296 | 0.028924 | 8.8826e-05 | No
2020-01-17 | 15:26 | GL1255 | Short rural | Vegetation | Grow-in - NSP responsibility | 109 | 99.8716 | 0.035813 | 0.0003586 | No
2020-01-17 | 18:51 | WRB2 | Urban | Asset Failure | Distribution substation | 69.1528 | 107.8182 | 0.0099492 | 9.2277e-05 | No
2020-01-17 | 18:51 | SHD2 | Short rural | Asset Failure | Distribution substation | 73.8472 | 107.8182 | 0.026194 | 0.00024295 | No
2020-01-17 | 18:58 | 5498 | Urban | Asset Failure | LV | 756 | 33.6468 | 0.033943 | 0.0010088 | No
2020-01-17 | 20:46 | TM1210 | Short rural | Weather |  | 239 | 69.2218 | 0.054427 | 0.00078628 | No
2020-01-17 | 20:49 | CLC2 | Short rural | Asset Failure | Distribution substation | 19 | 160 | 0.010001 | 6.2507e-05 | No
2020-01-17 | 21:34 | BDF2 | Short rural | Weather |  | 24 | 126.5 | 0.009988 | 7.8957e-05 | No
2020-01-17 | 22:37 | BWA2 | Short rural | Asset Failure | HV | 1518 | 171.9209 | 0.85858 | 0.004994 | No
2020-01-17 | 22:59 | L940 | Short rural | Asset Failure | Distribution substation | 3 | 351 | 0.0034642 | 9.8696e-06 | No
2020-01-18 | 0:29 | 35304 | Urban | Animal | Animal Impact | 38 | 86 | 0.0043608 | 5.0707e-05 | No
2020-01-18 | 7:04 | RW1281 | Short rural | Asset Failure | Distribution substation | 1 | 702 | 0.0023095 | 3.2899e-06 | No
2020-01-18 | 8:13 | J491 | Urban | Asset Failure | Distribution substation | 35 | 126.4571 | 0.0059061 | 4.6704e-05 | No
2020-01-18 | 8:32 | BWH2 | Short rural | Asset Failure | Distribution substation | 1 | 271 | 0.00089155 | 3.2899e-06 | No
2020-01-18 | 8:54 | JBA2 | Short rural | Unknown | Unknown | 35 | 211.8571 | 0.024394 | 0.00011515 | No
2020-01-18 | 8:55 | RBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 501 | 189.9681 | 0.31311 | 0.0016482 | No
2020-01-18 | 9:55 | 35983 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 2 | 332 | 0.0021845 | 6.5797e-06 | No
2020-01-18 | 10:06 | GL1255 | Short rural | Asset Failure | LV | 327 | 123 | 0.13232 | 0.0010758 | No
2020-01-18 | 10:46 | BL1210 | Short rural | Vegetation | Grow-in - NSP responsibility | 1422 | 46.2665 | 0.21644 | 0.0046782 | No
2020-01-18 | 10:46 | 8802 | Short rural | Asset Failure | Distribution substation | 1 | 505 | 0.0016614 | 3.2899e-06 | No
2020-01-18 | 11:11 | HKD2 | Short rural | Asset Failure | Distribution substation | 1 | 128 | 0.0004211 | 3.2899e-06 | No
2020-01-18 | 11:59 | CLA2 | Short rural | Asset Failure | HV | 28 | 232.6786 | 0.021433 | 9.2116e-05 | No
2020-01-18 | 12:26 | ULK2 | Short rural | Asset Failure | Distribution substation | 1 | 140 | 0.00046058 | 3.2899e-06 | No
2020-01-18 | 13:00 | 35980 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 242 | 0.0015923 | 6.5797e-06 | No
2020-01-18 | 14:35 | L942 | Short rural | Vegetation | Grow-in - NSP responsibility | 23 | 400.3478 | 0.030293 | 7.5667e-05 | No
2020-01-18 | 15:18 | SC1289 | Short rural | Asset Failure | Distribution substation | 3 | 319 | 0.0031484 | 9.8696e-06 | No
2020-01-18 | 16:19 | CV1284 | Urban | Asset Failure | Distribution substation | 20 | 98 | 0.0026154 | 2.6688e-05 | No
2020-01-18 | 16:39 | KMD2 | Short rural | Asset Failure | Distribution substation | 1 | 395 | 0.0012995 | 3.2899e-06 | No
2020-01-18 | 18:18 | GL1233 | Short rural | Asset Failure | LV | 574 | 170.0122 | 0.32105 | 0.0018884 | No
2020-01-18 | 20:50 | 8676 | Urban | Other | FOREIGN MATTER ON SYSTEM | 86 | 80 | 0.0091807 | 0.00011476 | No
2020-01-18 | 21:34 | L588 | Short rural | Asset Failure | HV | 170 | 148.5471 | 0.083079 | 0.00055928 | No
2020-01-18 | 23:21 | BGA2 | Short rural | Asset Failure | Distribution substation | 1 | 2155 | 0.0070897 | 3.2899e-06 | No
2020-01-19 | 2:16 | S737 | Short rural | Vegetation | Grow-in - NSP responsibility | 25 | 656.48 | 0.053993 | 8.2247e-05 | No
2020-01-19 | 8:14 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 7444 | 0.02449 | 3.2899e-06 | No
2020-01-19 | 9:33 | KVD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 63 | 317.3492 | 0.065774 | 0.00020726 | No
2020-01-19 | 11:13 | 27142 | Urban | Asset Failure | Distribution substation | 1 | 464 | 0.00061916 | 1.3344e-06 | No
2020-01-19 | 12:33 | R260 | Short rural | Asset Failure | HV | 8 | 143 | 0.0037636 | 2.6319e-05 | No
2020-01-19 | 13:36 | S737 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 109 | 0.00071719 | 6.5797e-06 | No
2020-01-19 | 14:01 | T869 | Urban | Asset Failure | Distribution substation | 19 | 138.3684 | 0.0035081 | 2.5354e-05 | No
2020-01-19 | 16:22 | B214 | Urban | Asset Failure | HV | 871 | 139.132 | 0.16171 | 0.0011623 | No
2020-01-19 | 17:50 | AB1265 | Urban | Asset Failure | Distribution substation | 11 | 407.4545 | 0.0059808 | 1.4678e-05 | No
2020-01-19 | 20:41 | SWH2 | Urban | Third Party | Vehicle impact | 912 | 18.0669 | 0.021987 | 0.001217 | No
2020-01-19 | 21:00 | B743 | Urban | Asset Failure | Distribution substation | 1 | 130 | 0.00017347 | 1.3344e-06 | No
2020-01-20 | 2:19 | SWH2 | Urban | Third Party | Vehicle impact | 36 | 639.4444 | 0.030718 | 4.8038e-05 | No
2020-01-20 | 6:15 | RV1298 | Urban | Asset Failure | Distribution substation | 53 | 447 | 0.031613 | 7.0723e-05 | No
2020-01-20 | 7:16 | WQ1264 | Urban | Asset Failure | Distribution substation | 13 | 403 | 0.0069909 | 1.7347e-05 | No
2020-01-20 | 7:35 | RW1292 | Short rural | Other | Fire | 73 | 105 | 0.025217 | 0.00024016 | No
2020-01-20 | 7:54 | L504 | Urban | Asset Failure | Distribution substation | 5 | 415.6 | 0.0027729 | 6.672e-06 | No
2020-01-20 | 8:51 | T890 | Urban | Asset Failure | Distribution substation | 1 | 374 | 0.00049907 | 1.3344e-06 | No
2020-01-20 | 9:16 | DP1243 | Urban | Other | Probable Overload | 122 | 32.3607 | 0.0052682 | 0.0001628 | No
2020-01-20 | 11:40 | CLA2 | Short rural | Other | Probable Lightning/Electrical Storm | 16 | 133 | 0.0070008 | 5.2638e-05 | No
2020-01-20 | 11:53 | BL1232 | Short rural | Third Party | Other | 24 | 104 | 0.0082115 | 7.8957e-05 | No
2020-01-20 | 12:30 | C900 | Urban | Asset Failure | HV | 2671 | 44.8974 | 0.16002 | 0.0035642 | No
2020-01-20 | 14:09 | 9055 | Urban | Asset Failure | HV | 1508 | 122.8846 | 0.24728 | 0.0020123 | No
2020-01-20 | 14:14 | RW1218 | Short rural | Other | Probable Lightning/Electrical Storm | 13 | 294 | 0.012574 | 4.2768e-05 | No
2020-01-20 | 14:18 | RW1281 | Short rural | Weather |  | 1 | 164 | 0.00053954 | 3.2899e-06 | No
2020-01-20 | 14:19 | 87218 | Short rural | Other | Probable Lightning/Electrical Storm | 3 | 78 | 0.00076983 | 9.8696e-06 | No
2020-01-20 | 14:20 | SN1230 | Short rural | Other | Probable Lightning/Electrical Storm | 34 | 142 | 0.015883 | 0.00011186 | No
2020-01-20 | 14:21 | H745 | Short rural | Other | Probable Lightning/Electrical Storm | 139 | 130.6619 | 0.05975 | 0.00045729 | No
2020-01-20 | 14:28 | 87218 | Short rural | Asset Failure | Distribution substation | 3 | 542 | 0.0053493 | 9.8696e-06 | No
2020-01-20 | 14:29 | 35990 | Short rural | Other | Probable Lightning/Electrical Storm | 7 | 64 | 0.0014739 | 2.3029e-05 | No
2020-01-20 | 14:29 | NG1299 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 69 | 137.5072 | 0.031214 | 0.000227 | No
2020-01-20 | 14:35 | RBE2 | Short rural | Asset Failure | HV | 14 | 167 | 0.0076917 | 4.6058e-05 | No
2020-01-20 | 14:36 | OA1233 | Short rural | Weather |  | 415 | 0.89157 | 0.0012172 | 0.0013653 | No
2020-01-20 | 14:38 | BYC2 | Short rural | Other | Probable Lightning/Electrical Storm | 83 | 119.8313 | 0.032721 | 0.00027306 | No
2020-01-20 | 14:43 | NN1240 | Urban | Weather |  | 829 | 35.0929 | 0.03882 | 0.0011062 | No
2020-01-20 | 14:44 | RBA2 | Short rural | Other | Probable Lightning/Electrical Storm | 23 | 302 | 0.022851 | 7.5667e-05 | No
2020-01-20 | 14:51 | J500 | Urban | Other | Probable Lightning/Electrical Storm | 213 | 29.831 | 0.0084788 | 0.00028423 | No
2020-01-20 | 14:55 | CS1239 | Short rural | Asset Failure | Distribution substation | 1 | 317 | 0.0010429 | 3.2899e-06 | No
2020-01-20 | 14:57 | OA1233 | Short rural | Weather |  | 11 | 746 | 0.026997 | 3.6188e-05 | No
2020-01-20 | 14:59 | SHG2 | Short rural | Other | Probable Lightning/Electrical Storm | 79 | 79.8354 | 0.020749 | 0.0002599 | No
2020-01-20 | 14:59 | J500 | Urban | Asset Failure | HV | 765 | 127.0314 | 0.12968 | 0.0010208 | No
2020-01-20 | 15:05 | 35988 | Short rural | Weather |  | 7 | 495 | 0.011399 | 2.3029e-05 | No
2020-01-20 | 15:06 | 35982 | Short rural | Weather |  | 38 | 180 | 0.022503 | 0.00012501 | No
2020-01-20 | 15:09 | 35988 | Short rural | Other | Probable Lightning/Electrical Storm | 3 | 518 | 0.0051124 | 9.8696e-06 | No
2020-01-20 | 15:17 | 35988 | Short rural | Other | Probable Lightning/Electrical Storm | 13 | 395 | 0.016893 | 4.2768e-05 | No
2020-01-20 | 15:20 | APC2 | Short rural | Other | Probable Lightning/Electrical Storm | 12 | 188.5833 | 0.007445 | 3.9478e-05 | No
2020-01-20 | 15:25 | KVD2 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 154 | 0.0010133 | 6.5797e-06 | No
2020-01-20 | 15:28 | X877 | Short rural | Weather |  | 3 | 356 | 0.0035136 | 9.8696e-06 | No
2020-01-20 | 15:29 | 35989 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 280.5 | 0.0018456 | 6.5797e-06 | No
2020-01-20 | 15:29 | BYB2 | Short rural | Weather |  | 1 | 301 | 0.00099025 | 3.2899e-06 | No
2020-01-20 | 15:31 | OA1207 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 358 | 0.0023555 | 6.5797e-06 | No
2020-01-20 | 15:38 | BYB2 | Short rural | Other | Probable Lightning/Electrical Storm | 28 | 250 | 0.023029 | 9.2116e-05 | No
2020-01-20 | 15:54 | BYB2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 279 | 0.00091787 | 3.2899e-06 | No
2020-01-20 | 16:00 | X877 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 181 | 161.1105 | 0.095936 | 0.00059547 | No
2020-01-20 | 16:08 | OA1207 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 318 | 0.0020924 | 6.5797e-06 | No
2020-01-20 | 16:16 | OA1207 | Short rural | Other | Probable Lightning/Electrical Storm | 8 | 311 | 0.0081852 | 2.6319e-05 | No
2020-01-20 | 16:32 | BWF2 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 192 | 0.0025266 | 1.3159e-05 | No
2020-01-20 | 16:36 | X879 | Short rural | Other | Probable Lightning/Electrical Storm | 509 | 71.9391 | 0.12046 | 0.0016745 | No
2020-01-20 | 16:38 | CLA2 | Short rural | Other | Probable Lightning/Electrical Storm | 6 | 110 | 0.0021713 | 1.9739e-05 | No
2020-01-20 | 16:45 | W185 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 465 | 99 | 0.15145 | 0.0015298 | No
2020-01-20 | 16:50 | LP1142 | Urban | Weather |  | 1137 | 222.8892 | 0.33817 | 0.0015172 | No
2020-01-20 | 17:04 | CD1234 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 134 | 0.0017634 | 1.3159e-05 | No
2020-01-20 | 17:37 | OP1122 | Short rural | Weather |  | 1 | 262 | 0.00086194 | 3.2899e-06 | No
2020-01-20 | 17:50 | AZ1272 | Short rural | Weather |  | 50 | 148 | 0.024345 | 0.00016449 | No
2020-01-20 | 17:55 | 35988 | Short rural | Other | Probable Equipment Failure | 3 | 492 | 0.0048558 | 9.8696e-06 | No
2020-01-20 | 17:59 | APC2 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 243 | 0.0031977 | 1.3159e-05 | No
2020-01-20 | 18:02 | JBA2 | Short rural | Weather |  | 32 | 145.0938 | 0.015275 | 0.00010528 | No
2020-01-20 | 18:04 | JBB2 | Short rural | Other | Probable Lightning/Electrical Storm | 323 | 51.2229 | 0.054431 | 0.0010626 | No
2020-01-20 | 18:17 | CS1276 | Urban | Asset Failure | Distribution substation | 6 | 77 | 0.00061649 | 8.0064e-06 | No
2020-01-20 | 18:29 | BYC2 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 216 | 0.0014212 | 6.5797e-06 | No
2020-01-20 | 18:42 | 35982 | Short rural | Weather |  | 3 | 363 | 0.0035827 | 9.8696e-06 | No
2020-01-20 | 18:44 | SHG2 | Short rural | Other | Probable Lightning/Electrical Storm | 8 | 230.125 | 0.0060566 | 2.6319e-05 | No
2020-01-20 | 19:12 | 9052 | Urban | Asset Failure | Distribution substation | 44 | 17 | 0.00099813 | 5.8714e-05 | No
2020-01-20 | 19:54 | JBB2 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 213 | 0.0014015 | 6.5797e-06 | No
2020-01-20 | 20:21 | CA1210 | Urban | Unknown | Unknown | 17 | 19 | 0.00043101 | 2.2685e-05 | No
2020-01-20 | 20:35 | BYB2 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 129 | 0.00084878 | 6.5797e-06 | No
2020-01-20 | 20:45 | NN1251 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 134 | 0.00044084 | 3.2899e-06 | No
2020-01-20 | 20:55 | SN1282 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 193 | 0.0012699 | 6.5797e-06 | No
2020-01-20 | 22:38 | BYC2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 172 | 0.00056586 | 3.2899e-06 | No
2020-01-21 | 0:28 | T828 | Short rural | Vegetation | Grow-in - NSP responsibility | 270 | 155.4148 | 0.13805 | 0.00088826 | No
2020-01-21 | 0:57 | UNB2 | Urban | Animal | Animal Impact | 183 | 53.847 | 0.013149 | 0.0002442 | No
2020-01-21 | 2:04 | BWF2 | Short rural | Asset Failure | HV | 139 | 248.3165 | 0.11355 | 0.00045729 | No
2020-01-21 | 7:17 | WQ1260 | Urban | Asset Failure | Distribution substation | 14 | 128.2143 | 0.0023952 | 1.8682e-05 | No
2020-01-21 | 9:08 | BYD2 | Short rural | Asset Failure | Distribution substation | 1 | 123 | 0.00040465 | 3.2899e-06 | No
2020-01-21 | 9:26 | MR2231 | Urban | Asset Failure | Distribution substation | 1 | 101 | 0.00013477 | 1.3344e-06 | No
2020-01-21 | 12:36 | YYB2 | Short rural | Other | Fire | 3 | 305 | 0.0030102 | 9.8696e-06 | No
2020-01-21 | 12:40 | SN1230 | Short rural | Vegetation | Grow-in - NSP responsibility | 23 | 171.5217 | 0.012979 | 7.5667e-05 | No
2020-01-21 | 15:25 | KC1288 | Short rural | Asset Failure | Distribution substation | 1 | 275 | 0.00090471 | 3.2899e-06 | No
2020-01-21 | 15:27 | CR1228 | Urban | Overload |  | 41 | 68 | 0.0037203 | 5.471e-05 | No
2020-01-21 | 17:10 | KMC2 | Short rural | Asset Failure | Distribution substation | 8 | 137 | 0.0036057 | 2.6319e-05 | No
2020-01-21 | 20:00 | C899 | Urban | Asset Failure | Distribution substation | 1 | 404 | 0.0005391 | 1.3344e-06 | No
2020-01-21 | 21:09 | CX1206 | Short rural | Asset Failure | Distribution substation | 1 | 162 | 0.00053296 | 3.2899e-06 | No
2020-01-22 | 1:20 | J516 | Urban | Vegetation | Grow-in - NSP responsibility | 1451 | 100.8732 | 0.19531 | 0.0019362 | No
2020-01-22 | 2:37 | BL1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 15 | 93.8667 | 0.0046321 | 4.9348e-05 | No
2020-01-22 | 6:23 | KVA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 19 | 236 | 0.014752 | 6.2507e-05 | No
2020-01-22 | 9:27 | M399 | Short rural | Asset Failure | Distribution substation | 1 | 92 | 0.00030267 | 3.2899e-06 | No
2020-01-22 | 9:59 | KC1288 | Short rural | Asset Failure | Distribution substation | 1 | 242 | 0.00079615 | 3.2899e-06 | No
2020-01-22 | 10:10 | PK1225 | Urban | Asset Failure | LV | 1607 | 1.4984 | 0.0032132 | 0.0021444 | No
2020-01-22 | 10:30 | CN1243 | Urban | Unknown | Unknown | 12 | 68 | 0.0010889 | 1.6013e-05 | No
2020-01-22 | 11:00 | OP1262 | Short rural | Asset Failure | Distribution substation | 2 | 394.5 | 0.0025957 | 6.5797e-06 | No
2020-01-22 | 11:21 | PK1225 | Urban | Asset Failure | Distribution substation | 144 | 145.3125 | 0.027922 | 0.00019215 | No
2020-01-22 | 13:39 | J516 | Urban | Asset Failure | HV | 1451 | 87.4997 | 0.16942 | 0.0019362 | No
2020-01-22 | 13:40 | NK1332 | Urban | Vegetation | Grow-in - NSP responsibility | 18 | 151.2222 | 0.0036322 | 2.4019e-05 | No
2020-01-22 | 16:10 | 35983 | Short rural | Vegetation | Grow-in - NSP responsibility | 29 | 314.5517 | 0.03001 | 9.5406e-05 | No
2020-01-22 | 16:45 | CLA2 | Short rural | Unknown | Unknown | 1 | 298 | 0.00098038 | 3.2899e-06 | No
2020-01-22 | 18:20 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 35 | 153.2286 | 0.017644 | 0.00011515 | No
2020-01-22 | 19:41 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 42 | 282.0476 | 0.038972 | 0.00013817 | No
2020-01-22 | 19:47 | 19816 | Urban | Vegetation | Grow-in - NSP responsibility | 9 | 32.7778 | 0.00039365 | 1.201e-05 | No
2020-01-22 | 20:48 | A314 | Urban | Asset Failure | Distribution substation | 25 | 210.2 | 0.0070123 | 3.336e-05 | No
2020-01-22 | 23:37 | SC1238 | Urban | Asset Failure | Distribution substation | 1 | 687 | 0.00091673 | 1.3344e-06 | No
2020-01-23 | 1:34 | NA1214 | Urban | Animal | Animal Impact | 70 | 81.4571 | 0.0076087 | 9.3408e-05 | No
2020-01-23 | 3:05 | BWE2 | Short rural | Asset Failure | LV | 724 | 168.0649 | 0.40031 | 0.0023819 | No
2020-01-23 | 5:06 | HBA2 | Short rural | Animal | Animal Impact | 815 | 97.6098 | 0.26172 | 0.0026812 | No
2020-01-23 | 6:27 | BYB2 | Short rural | Unknown | Unknown | 5 | 168 | 0.0027635 | 1.6449e-05 | No
2020-01-23 | 6:30 | BX1352 | Urban | Unknown | Unknown | 37 | 119 | 0.0058754 | 4.9373e-05 | No
2020-01-23 | 6:33 | HBA2 | Short rural | Unknown | Unknown | 260 | 71.1808 | 0.060885 | 0.00085536 | No
2020-01-23 | 8:03 | BDG2 | Short rural | Third Party | Dig-in | 1547 | 131.3659 | 0.66858 | 0.0050894 | No
2020-01-23 | 8:54 | NK1332 | Urban | Vegetation | Grow-in - NSP responsibility | 20 | 52.8 | 0.0014091 | 2.6688e-05 | No
2020-01-23 | 10:02 | BWF2 | Short rural | Asset Failure | Distribution substation | 2 | 70 | 0.00046058 | 6.5797e-06 | No
2020-01-23 | 10:14 | 25450 | Short rural | Asset Failure | Distribution substation | 6 | 273 | 0.0053888 | 1.9739e-05 | No
2020-01-23 | 10:18 | WBD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 725 | 54.7324 | 0.13055 | 0.0023852 | No
2020-01-23 | 10:21 | MR2299 | Urban | Asset Failure | Distribution substation | 26 | 323.1538 | 0.011212 | 3.4694e-05 | No
2020-01-23 | 10:33 | GG1232 | Short rural | Asset Failure | LV | 11 | 102.8182 | 0.0037208 | 3.6188e-05 | No
2020-01-23 | 11:00 | 35693 | Short rural | Asset Failure | HV | 10 | 223.3 | 0.0073463 | 3.2899e-05 | No
2020-01-23 | 11:03 | KC1221 | Short rural | Asset Failure | Distribution substation | 1 | 276 | 0.000908 | 3.2899e-06 | No
2020-01-23 | 11:16 | 35989 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 258 | 201.9961 | 0.17145 | 0.00084878 | No
2020-01-23 | 11:44 | MYG2 | Urban | Asset Failure | Distribution substation | 1 | 192 | 0.0002562 | 1.3344e-06 | No
2020-01-23 | 11:46 | SXD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 403 | 101.2531 | 0.13424 | 0.0013258 | No
2020-01-23 | 12:21 | APG2 | Urban | Asset Failure | HV | 1691 | 235.819 | 0.53212 | 0.0022565 | No
2020-01-23 | 12:42 | JBA2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 35 | 339 | 0.039034 | 0.00011515 | No
2020-01-23 | 12:42 | JBA2 | Short rural | Weather |  | 31 | 327.2258 | 0.033372 | 0.00010199 | No
2020-01-23 | 12:44 | RW1255 | Short rural | Unknown | Unknown | 56 | 150 | 0.027635 | 0.00018423 | No
2020-01-23 | 12:49 | T831 | Short rural | Unknown | Unknown | 158 | 262.6392 | 0.13652 | 0.0005198 | No
2020-01-23 | 13:07 | GL1233 | Short rural | Vegetation | Grow-in - NSP responsibility | 314 | 164.1401 | 0.16956 | 0.001033 | No
2020-01-23 | 13:43 | 35693 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 30 | 256.7333 | 0.025339 | 9.8696e-05 | No
2020-01-23 | 13:48 | KMD2 | Short rural | Weather |  | 1320 | 77.3409 | 0.33586 | 0.0043426 | No
2020-01-23 | 13:51 | 16666 | Urban | Overload |  | 28 | 50 | 0.0018682 | 3.7363e-05 | No
2020-01-23 | 13:55 | NA1207 | Short rural | Asset Failure | Distribution substation | 2 | 157 | 0.001033 | 6.5797e-06 | No
2020-01-23 | 14:09 | 8799 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 109 | 0.0003586 | 3.2899e-06 | No
2020-01-23 | 14:13 | OA1244 | Short rural | Vegetation | Grow-in - NSP responsibility | 373 | 118.7828 | 0.14576 | 0.0012271 | No
2020-01-23 | 14:18 | A046 | Short rural | Weather |  | 6 | 183.5 | 0.0036221 | 1.9739e-05 | No
2020-01-23 | 14:22 | MG1286 | Short rural | Network business | Switching or protection error | 1082.6989 | 194.3276 | 0.69218 | 0.0035619 | No
2020-01-23 | 14:22 | BWH2 | Short rural | Network business | Switching or protection error | 892.3011 | 194.3276 | 0.57046 | 0.0029355 | No
2020-01-23 | 14:22 | TM1284 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 916 | 132.8635 | 0.40039 | 0.0030135 | No
2020-01-23 | 14:28 | DP1210 | Short rural | Weather |  | 47 | 181 | 0.027987 | 0.00015462 | No
2020-01-23 | 14:32 | HBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 260 | 72.3308 | 0.061869 | 0.00085536 | No
2020-01-23 | 14:50 | 53805 | Short rural | Unknown | Unknown | 1 | 1116 | 0.0036715 | 3.2899e-06 | No
2020-01-23 | 15:02 | RW1255 | Short rural | Unknown | Unknown | 49 | 9.8571 | 0.001589 | 0.0001612 | No
2020-01-23 | 15:05 | NG1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 462 | 0.0060797 | 1.3159e-05 | No
2020-01-23 | 15:10 | APC2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 5 | 140 | 0.0023029 | 1.6449e-05 | No
2020-01-23 | 15:25 | RW1292 | Short rural | 7 - STPIS Exclusion (3.3)(a) | Bushfire | 11 | 2602.8182 | 0.094192 | 3.6188e-05 | No
2020-01-23 | 15:53 | D841 | Urban | Asset Failure | Distribution substation | 3 | 409 | 0.0016373 | 4.0032e-06 | No
2020-01-23 | 15:59 | BWE2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 279 | 0.0018357 | 6.5797e-06 | No
2020-01-23 | 16:27 | 35418 | Short rural | Other | Fire | 73 | 95.2466 | 0.022874 | 0.00024016 | No
2020-01-23 | 16:35 | 35818 | Short rural | Asset Failure | Distribution substation | 30 | 265 | 0.026154 | 9.8696e-05 | No
2020-01-23 | 16:39 | 19857 | Urban | Unknown | Unknown | 2446 | 140.316 | 0.45798 | 0.0032639 | No
2020-01-23 | 16:56 | S765 | Urban | Weather |  | 18 | 319 | 0.0076621 | 2.4019e-05 | No
2020-01-23 | 17:00 | S765 | Urban | Weather |  | 1 | 316 | 0.00042167 | 1.3344e-06 | No
2020-01-23 | 17:40 | 27200 | Urban | Weather |  | 9 | 113 | 0.0013571 | 1.201e-05 | No
2020-01-23 | 17:43 | 27187 | Urban | Unknown | Unknown | 32 | 159 | 0.0067894 | 4.2701e-05 | No
2020-01-23 | 17:50 | 9056 | Urban | Asset Failure | Distribution substation | 17 | 191.1765 | 0.0043368 | 2.2685e-05 | No
2020-01-23 | 17:54 | BDA2 | Short rural | Asset Failure | HV | 36 | 300 | 0.035531 | 0.00011844 | No
2020-01-23 | 18:04 | J499 | Urban | Third Party | Vehicle impact | 6 | 362 | 0.0028983 | 8.0064e-06 | No
2020-01-23 | 18:06 | CX1284 | Short rural | Asset Failure | Distribution substation | 1 | 211 | 0.00069416 | 3.2899e-06 | No
2020-01-23 | 18:17 | SG1209 | Urban | Overload |  | 23 | 259 | 0.007949 | 3.0691e-05 | No
2020-01-23 | 18:31 | C832 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 1418 | 0.0018922 | 1.3344e-06 | No
2020-01-23 | 19:05 | MR2232 | Short rural | Weather |  | 2 | 1153 | 0.0075864 | 6.5797e-06 | No
2020-01-23 | 19:15 | CJ1241 | Urban | Weather |  | 15.7485 | 513 | 0.010781 | 2.1015e-05 | No
2020-01-23 | 19:15 | CJ1249 | Urban | Weather |  | 14.2515 | 513 | 0.0097558 | 1.9017e-05 | No
2020-01-23 | 19:30 | CJ1249 | Urban | Weather |  | 21.3772 | 486 | 0.013864 | 2.8526e-05 | No
2020-01-23 | 19:30 | CJ1241 | Urban | Weather |  | 23.6228 | 486 | 0.01532 | 3.1522e-05 | No
2020-01-23 | 19:31 | 9050 | Urban | Asset Failure | Distribution substation | 87 | 24 | 0.0027862 | 0.00011609 | No
2020-01-23 | 19:42 | SG1247 | Urban | Unknown | Unknown | 44 | 92 | 0.0054016 | 5.8714e-05 | No
2020-01-23 | 19:49 | 27188 | Urban | Weather |  | 10 | 169 | 0.0022551 | 1.3344e-05 | No
2020-01-23 | 20:11 | RW1292 | Short rural | Vegetation | Grow-in - NSP responsibility | 10 | 168 | 0.005527 | 3.2899e-05 | No
2020-01-23 | 20:40 | L940 | Short rural | Weather |  | 3 | 190 | 0.0018752 | 9.8696e-06 | No
2020-01-23 | 20:53 | 1959 | Urban | Weather |  | 15 | 102 | 0.0020416 | 2.0016e-05 | No
2020-01-23 | 20:58 | 2812 | Urban | Asset Failure | Distribution substation | 126 | 12.8571 | 0.0021617 | 0.00016813 | No
2020-01-23 | 21:34 | SY1132 | Urban | Weather |  | 50 | 107 | 0.007139 | 6.672e-05 | No
2020-01-23 | 21:57 | 27187 | Urban | Weather |  | 32 | 199 | 0.0084975 | 4.2701e-05 | No
2020-01-23 | 22:07 | 27200 | Urban | Weather |  | 9 | 118 | 0.0014171 | 1.201e-05 | No
2020-01-23 | 22:28 | SG1247 | Urban | Weather |  | 44 | 112 | 0.0065759 | 5.8714e-05 | No
2020-01-23 | 23:34 | 41533 | Short rural | Unknown | Unknown | 3 | 786 | 0.0077575 | 9.8696e-06 | No
2020-01-23 | 23:52 | L942 | Short rural | Unknown | Unknown | 3 | 735 | 0.0072541 | 9.8696e-06 | No
2020-01-24 | 0:25 | R293 | Short rural | Unknown | Unknown | 20 | 235 | 0.015462 | 6.5797e-05 | No
2020-01-24 | 0:41 | 53803 | Urban | Asset Failure | Distribution substation | 8 | 315.75 | 0.0033707 | 1.0675e-05 | No
2020-01-24 | 3:46 | T869 | Urban | Asset Failure | Distribution substation | 1 | 254 | 0.00033894 | 1.3344e-06 | No
2020-01-24 | 5:29 | SN1282 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 45 | 224.0889 | 0.033175 | 0.00014804 | No
2020-01-24 | 6:40 | 1953 | Urban | Animal | Animal Impact | 7 | 34.5714 | 0.00032292 | 9.3408e-06 | No
2020-01-24 | 7:29 | R260 | Short rural | Other | Probable Lightning/Electrical Storm | 290 | 215.5793 | 0.20568 | 0.00095406 | No
2020-01-24 | 7:35 | R208 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1104 | 101 | 0.36683 | 0.003632 | No
2020-01-24 | 7:38 | SHH2 | Short rural | Asset Failure | Distribution substation | 1 | 211 | 0.00069416 | 3.2899e-06 | No
2020-01-24 | 7:58 | 19856 | Urban | Weather |  | 27 | 238.7407 | 0.0086015 | 3.6029e-05 | No
2020-01-24 | 8:01 | HR1243 | Urban | Asset Failure | Distribution substation | 33 | 277 | 0.012198 | 4.4035e-05 | No
2020-01-24 | 8:04 | S786 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 144 | 329.4306 | 0.15606 | 0.00047374 | No
2020-01-24 | 8:13 | 35988 | Short rural | Other | Probable Lightning/Electrical Storm | 5 | 298 | 0.0049019 | 1.6449e-05 | No
2020-01-24 | 8:18 | R293 | Short rural | Weather |  | 20 | 433.75 | 0.02854 | 6.5797e-05 | No
2020-01-24 | 8:58 | L582 | Short rural | Asset Failure | Distribution substation | 2 | 114 | 0.00075009 | 6.5797e-06 | No
2020-01-24 | 9:05 | GL1207 | Short rural | Unknown | Unknown | 6 | 198 | 0.0039084 | 1.9739e-05 | No
2020-01-24 | 9:31 | D814 | Short rural | Unknown | Unknown | 4 | 532 | 0.0070008 | 1.3159e-05 | No
2020-01-24 | 9:32 | 8801 | Short rural | Unknown | Unknown | 1 | 245 | 0.00080602 | 3.2899e-06 | No
2020-01-24 | 9:43 | 25780 | Urban | Asset Failure | Distribution substation | 1 | 407 | 0.0005431 | 1.3344e-06 | No
2020-01-24 | 10:10 | DS1205 | Urban | Asset Failure | Distribution substation | 58 | 84.0172 | 0.0065025 | 7.7395e-05 | No
2020-01-24 | 11:05 | JBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 215 | 0.012024 | 5.5928e-05 | No
2020-01-24 | 11:15 | CX1210 | Short rural | Unknown | Unknown | 4 | 295 | 0.003882 | 1.3159e-05 | No
2020-01-24 | 11:16 | S786 | Short rural | Weather |  | 14 | 7 | 0.00032241 | 4.6058e-05 | No
2020-01-24 | 14:13 | CN1243 | Urban | Asset Failure | Distribution substation | 16 | 200 | 0.0042701 | 2.135e-05 | No
2020-01-24 | 14:15 | BDA2 | Short rural | Asset Failure | LV | 90 | 71 | 0.021022 | 0.00029609 | No
2020-01-24 | 14:39 | 27334 | Urban | Unknown | Unknown | 22 | 197 | 0.0057833 | 2.9357e-05 | No
2020-01-24 | 17:22 | 19856 | Urban | Other | Probable Lightning/Electrical Storm | 33 | 213 | 0.0093795 | 4.4035e-05 | No
2020-01-24 | 19:13 | SN1230 | Short rural | Other | Fire | 23 | 52 | 0.0039347 | 7.5667e-05 | No
2020-01-24 | 22:48 | MM1142 | Urban | Unknown | Unknown | 5 | 57 | 0.0003803 | 6.672e-06 | No
2020-01-24 | 22:58 | JBB2 | Short rural | Asset Failure | LV | 77 | 64.039 | 0.016222 | 0.00025332 | No
2020-01-25 | 0:19 | KME2 | Short rural | Asset Failure | HV | 1267 | 205.6369 | 0.85715 | 0.0041683 | No
2020-01-25 | 0:45 | L942 | Short rural | Unknown | Unknown | 1 | 120 | 0.00039478 | 3.2899e-06 | No
2020-01-25 | 2:01 | MM1142 | Urban | Asset Failure | Distribution substation | 14 | 556.5714 | 0.010398 | 1.8682e-05 | No
2020-01-25 | 8:37 | T876 | Urban | Asset Failure | Distribution substation | 1 | 400 | 0.00053376 | 1.3344e-06 | No
2020-01-25 | 11:02 | BDC2 | Short rural | Unknown | Unknown | 1 | 509 | 0.0016745 | 3.2899e-06 | No
2020-01-25 | 11:09 | W111 | Short rural | Asset Failure | Distribution substation | 12 | 253 | 0.009988 | 3.9478e-05 | No
2020-01-25 | 13:35 | 27334 | Urban | Asset Failure | Distribution substation | 1 | 102 | 0.00013611 | 1.3344e-06 | No
2020-01-25 | 16:47 | A314 | Urban | Vegetation | Grow-in - NSP responsibility | 11 | 76 | 0.0011156 | 1.4678e-05 | No
2020-01-25 | 16:53 | 87220 | Short rural | Weather |  | 12 | 315.75 | 0.012465 | 3.9478e-05 | No
2020-01-25 | 17:12 | X482 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 1031 | 0.0033918 | 3.2899e-06 | No
2020-01-25 | 17:26 | R293 | Short rural | Weather |  | 95 | 250.4 | 0.078259 | 0.00031254 | No
2020-01-25 | 17:42 | 87220 | Short rural | Unknown | Unknown | 42 | 62 | 0.0085668 | 0.00013817 | No
2020-01-25 | 17:57 | 87220 | Short rural | Weather |  | 2 | 810 | 0.0053296 | 6.5797e-06 | No
2020-01-25 | 20:49 | X877 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 119 | 0.0011745 | 9.8696e-06 | No
2020-01-25 | 23:04 | X482 | Short rural | Other | Probable Lightning/Electrical Storm | 7 | 617 | 0.014209 | 2.3029e-05 | No
2020-01-26 | 2:51 | X482 | Short rural | Other | Probable Lightning/Electrical Storm | 8 | 396 | 0.010422 | 2.6319e-05 | No
2020-01-26 | 4:40 | S735 | Short rural | Vegetation | Grow-in - NSP responsibility | 37 | 118 | 0.014364 | 0.00012172 | No
2020-01-26 | 7:36 | W163 | Short rural | Vegetation | Grow-in - NSP responsibility | 40 | 300.675 | 0.039567 | 0.00013159 | No
2020-01-26 | 7:48 | S737 | Short rural | Third Party | Other | 1 | 200 | 0.00065797 | 3.2899e-06 | No
2020-01-26 | 11:37 | RD1236 | Urban | Asset Failure | Distribution substation | 47 | 89 | 0.0055818 | 6.2717e-05 | No
2020-01-26 | 11:46 | RBB2 | Short rural | Asset Failure | Distribution substation | 1 | 166 | 0.00054612 | 3.2899e-06 | No
2020-01-26 | 11:48 | D810 | Short rural | Asset Failure | Distribution substation | 1 | 593 | 0.0019509 | 3.2899e-06 | No
2020-01-26 | 12:09 | X877 | Short rural | Asset Failure | Distribution substation | 1 | 124 | 0.00040794 | 3.2899e-06 | No
2020-01-26 | 12:12 | 1959 | Urban | Unknown | Unknown | 900 | 32.8544 | 0.039457 | 0.001201 | No
2020-01-26 | 13:20 | HR1213 | Urban | Asset Failure | Distribution substation | 66 | 64 | 0.0056365 | 8.807e-05 | No
2020-01-26 | 14:20 | A048 | Urban | Other | Probable Lightning/Electrical Storm | 2 | 133 | 0.00035495 | 2.6688e-06 | No
2020-01-26 | 14:37 | CX1210 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 89 | 83 | 0.024302 | 0.0002928 | No
2020-01-26 | 14:39 | CX1210 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 725 | 110.1324 | 0.26268 | 0.0023852 | No
2020-01-26 | 14:58 | 35990 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 674.6653 | 66.4303 | 0.14745 | 0.0022196 | No
2020-01-26 | 14:58 | 35983 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 594.3347 | 66.4303 | 0.12989 | 0.0019553 | No
2020-01-26 | 14:59 | 8799 | Short rural | Other | Probable Lightning/Electrical Storm | 3 | 173 | 0.0017074 | 9.8696e-06 | No
2020-01-26 | 15:19 | D810 | Short rural | Weather |  | 227 | 451.7841 | 0.33739 | 0.0007468 | No
2020-01-26 | 15:31 | 49918 | Urban | Weather |  | 1314 | 155 | 0.27178 | 0.0017534 | No
2020-01-26 | 15:37 | CV1251 | Urban | Weather |  | 632 | 135 | 0.11385 | 0.00084334 | No
2020-01-26 | 15:37 | 8762 | Urban | Weather |  | 1657 | 135 | 0.2985 | 0.0022111 | No
2020-01-26 | 15:38 | 68197 | Urban | Weather |  | 1207 | 188.4308 | 0.30349 | 0.0016106 | No
2020-01-26 | 15:44 | WQ1264 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 267 | 147 | 0.052374 | 0.00035628 | No
2020-01-26 | 15:44 | M162 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 96 | 287.5521 | 0.036836 | 0.0001281 | No
2020-01-26 | 15:45 | HR1206 | Urban | Asset Failure | Distribution substation | 23 | 671.4783 | 0.020608 | 3.0691e-05 | No
2020-01-26 | 15:48 | 9052 | Urban | Weather |  | 1163 | 99.8194 | 0.15491 | 0.0015519 | No
2020-01-26 | 15:58 | GV1271 | Urban | Weather |  | 1424 | 256.2065 | 0.48684 | 0.0019002 | No
2020-01-26 | 15:58 | B776 | Urban | Weather |  | 931.3005 | 664.1128 | 0.82531 | 0.0012427 | No
2020-01-26 | 15:58 | 19868 | Urban | Weather |  | 824.6995 | 664.1128 | 0.73084 | 0.0011005 | No
2020-01-26 | 16:17 | 19868 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 102 | 524.8235 | 0.071433 | 0.00013611 | No
2020-01-26 | 16:32 | B773 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 246 | 0.010504 | 4.2701e-05 | No
2020-01-26 | 16:34 | D852 | Urban | Other | FOREIGN MATTER ON SYSTEM | 28 | 1282 | 0.0479 | 3.7363e-05 | No
2020-01-26 | 16:46 | 68179 | Urban | Weather |  | 24 | 1344.8333 | 0.043069 | 3.2026e-05 | No
2020-01-26 | 16:51 | 19868 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 61 | 1406.2295 | 0.11446 | 8.1398e-05 | No
2020-01-26 | 17:01 | 49916 | Urban | Other | Probable Lightning/Electrical Storm | 57 | 422 | 0.032098 | 7.6061e-05 | No
2020-01-26 | 17:07 | C900 | Urban | Asset Failure | Distribution substation | 216 | 334 | 0.096269 | 0.00028823 | No
2020-01-26 | 17:16 | 9052 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 44 | 1104 | 0.06482 | 5.8714e-05 | No
2020-01-26 | 17:25 | CX1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 85 | 286.0941 | 0.080003 | 0.00027964 | No
2020-01-26 | 17:28 | S765 | Urban | Unknown | Unknown | 18 | 310 | 0.0074459 | 2.4019e-05 | No
2020-01-26 | 17:37 | APH2 | Urban | Other | Probable Overload | 12 | 56 | 0.00089672 | 1.6013e-05 | No
2020-01-26 | 17:55 | TM1217 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 71 | 0.00023358 | 3.2899e-06 | No
2020-01-26 | 17:59 | 68195 | Urban | Weather |  | 19 | 102 | 0.0025861 | 2.5354e-05 | No
2020-01-26 | 18:22 | A341 | Urban | Weather |  | 49 | 794 | 0.051916 | 6.5386e-05 | No
2020-01-26 | 18:38 | S774 | Urban | Unknown | Unknown | 21 | 224 | 0.006277 | 2.8022e-05 | No
2020-01-26 | 18:53 | CJ1249 | Urban | Unknown | Unknown | 7 | 360 | 0.0033627 | 9.3408e-06 | No
2020-01-26 | 19:00 | B776 | Urban | Other | Probable Lightning/Electrical Storm | 47 | 772 | 0.048417 | 6.2717e-05 | No
2020-01-26 | 19:58 | 68197 | Urban | Asset Failure | Distribution substation | 12 | 82 | 0.001313 | 1.6013e-05 | No
2020-01-26 | 20:14 | GV1271 | Urban | Weather |  | 1226 | 260.522 | 0.42621 | 0.001636 | No
2020-01-26 | 20:15 | GV1271 | Urban | Weather |  | 107 | 281.9252 | 0.040253 | 0.00014278 | No
2020-01-26 | 20:20 | CV1221 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 23 | 372 | 0.011417 | 3.0691e-05 | No
2020-01-26 | 20:28 | J459 | Short rural | Asset Failure | Distribution substation | 1 | 166 | 0.00054612 | 3.2899e-06 | No
2020-01-26 | 20:28 | KVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 90 | 161 | 0.04767 | 0.00029609 | No
2020-01-26 | 21:05 | GV1271 | Urban | Weather |  | 62 | 211.1452 | 0.017469 | 8.2733e-05 | No
2020-01-26 | 22:18 | 68188 | Urban | Weather |  | 61 | 34 | 0.0027675 | 8.1398e-05 | No
2020-01-27 | 6:23 | AZ1257 | Urban | Third Party | Vehicle impact | 47 | 433.6383 | 0.027196 | 6.2717e-05 | No
2020-01-27 | 6:40 | D810 | Short rural | Other | Probable Lightning/Electrical Storm | 17 | 328 | 0.018344 | 5.5928e-05 | No
2020-01-27 | 7:29 | RW1281 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 18 | 189 | 0.011192 | 5.9218e-05 | No
2020-01-27 | 7:53 | D810 | Short rural | Weather |  | 1 | 102 | 0.00033557 | 3.2899e-06 | No
2020-01-27 | 10:39 | APH2 | Urban | Asset Failure | Distribution substation | 36 | 122.8889 | 0.0059034 | 4.8038e-05 | No
2020-01-27 | 11:04 | 9019 | Urban | Asset Failure | Distribution substation | 1 | 70 | 9.3408e-05 | 1.3344e-06 | No
2020-01-27 | 12:13 | BWH2 | Short rural | Vegetation | Grow-in - NSP responsibility | 51 | 163 | 0.027349 | 0.00016778 | No
2020-01-27 | 14:03 | D810 | Short rural | Weather |  | 4 | 141 | 0.0018555 | 1.3159e-05 | No
2020-01-27 | 14:07 | ULL2 | Short rural | Unknown | Unknown | 1102 | 98.5272 | 0.3572 | 0.0036254 | No
2020-01-27 | 14:24 | GV1271 | Urban | Other | Probable Lightning/Electrical Storm | 49 | 81 | 0.0052962 | 6.5386e-05 | No
2020-01-27 | 15:25 | GV1271 | Urban | Other | Probable Lightning/Electrical Storm | 30 | 289 | 0.011569 | 4.0032e-05 | No
2020-01-27 | 15:52 | GV1271 | Urban | Other | Probable Lightning/Electrical Storm | 30 | 244 | 0.0097678 | 4.0032e-05 | No
2020-01-27 | 16:42 | D810 | Short rural | Weather |  | 4 | 416 | 0.0054743 | 1.3159e-05 | No
2020-01-27 | 17:09 | T834 | Short rural | Vegetation | Grow-in - NSP responsibility | 130 | 68.2154 | 0.029175 | 0.00042768 | No
2020-01-27 | 18:01 | D810 | Short rural | Weather |  | 107 | 23.8692 | 0.0084023 | 0.00035202 | No
2020-01-27 | 18:23 | C889 | Urban | Asset Failure | Distribution substation | 47 | 219.7872 | 0.013784 | 6.2717e-05 | No
2020-01-27 | 18:37 | SY1352 | Urban | Asset Failure | Distribution substation | 13 | 74 | 0.0012837 | 1.7347e-05 | No
2020-01-27 | 18:49 | 87222 | Long rural | Other | Probable Lightning/Electrical Storm | 1 | 1091 | 3.4745 | 0.0031847 | No
2020-01-27 | 20:54 | 49319 | Urban | Asset Failure | Distribution substation | 14 | 406 | 0.0075847 | 1.8682e-05 | No
2020-01-27 | 21:45 | M162 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 644 | 0.00085935 | 1.3344e-06 | No
2020-01-27 | 21:45 | M162 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 643 | 0.00085802 | 1.3344e-06 | No
2020-01-27 | 21:46 | L519 | Urban | Asset Failure | Distribution substation | 1 | 125 | 0.0001668 | 1.3344e-06 | No
2020-01-28 | 0:09 | BL1210 | Short rural | Asset Failure | Distribution substation | 26 | 183 | 0.015653 | 8.5536e-05 | No
2020-01-28 | 0:34 | A348 | Urban | Animal | Animal Impact | 51 | 120 | 0.0081665 | 6.8054e-05 | No
2020-01-28 | 0:41 | 49319 | Urban | Asset Failure | Distribution substation | 14 | 183.6429 | 0.0034307 | 1.8682e-05 | No
2020-01-28 | 2:04 | BDA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 30 | 459.9333 | 0.045394 | 9.8696e-05 | No
2020-01-28 | 6:14 | SXC2 | Short rural | Asset Failure | Distribution substation | 3 | 23 | 0.000227 | 9.8696e-06 | No
2020-01-28 | 7:16 | SXA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 9 | 275.5556 | 0.0081589 | 2.9609e-05 | No
2020-01-28 | 10:12 | J497 | Short rural | Asset Failure | Distribution substation | 1 | 192 | 0.00063165 | 3.2899e-06 | No
2020-01-28 | 10:44 | RD1296 | Urban | Asset Failure | Distribution substation | 1 | 100 | 0.00013344 | 1.3344e-06 | No
2020-01-28 | 11:35 | J473 | Urban | Asset Failure | Distribution substation | 27 | 28.7407 | 0.0010355 | 3.6029e-05 | No
2020-01-28 | 11:42 | KVB2 | Short rural | Unknown | Unknown | 6 | 160 | 0.0031583 | 1.9739e-05 | No
2020-01-28 | 13:21 | BWE2 | Short rural | Asset Failure | LV | 30 | 75.3667 | 0.0074384 | 9.8696e-05 | No
2020-01-28 | 14:13 | WQ1271 | Urban | Unknown | Unknown | 1 | 78 | 0.00010408 | 1.3344e-06 | No
2020-01-28 | 15:24 | X877 | Short rural | Asset Failure | Distribution substation | 4 | 414 | 0.005448 | 1.3159e-05 | No
2020-01-28 | 15:31 | OA1233 | Short rural | Animal | Animal Impact | 1 | 208 | 0.00068429 | 3.2899e-06 | No
2020-01-28 | 17:22 | F602 | Urban | Asset Failure | Distribution substation | 9 | 328 | 0.0039391 | 1.201e-05 | No
2020-01-28 | 17:23 | LP1322 | Urban | Unknown | Unknown | 42 | 62 | 0.0034748 | 5.6045e-05 | No
2020-01-28 | 17:24 | 27187 | Urban | Overload |  | 32 | 114 | 0.0048679 | 4.2701e-05 | No
2020-01-28 | 17:25 | 27200 | Urban | Overload |  | 9 | 113 | 0.0013571 | 1.201e-05 | No
2020-01-28 | 17:42 | 27187 | Urban | Overload |  | 7 | 177 | 0.0016533 | 9.3408e-06 | No
2020-01-28 | 17:44 | 27187 | Urban | Overload |  | 8 | 177 | 0.0018895 | 1.0675e-05 | No
2020-01-28 | 17:52 | 41535 | Urban | Asset Failure | Distribution substation | 1 | 991 | 0.0013224 | 1.3344e-06 | No
2020-01-28 | 19:29 | 27200 | Urban | Overload |  | 9 | 69 | 0.00082866 | 1.201e-05 | No
2020-01-28 | 19:45 | X879 | Short rural | Unknown | Unknown | 7 | 9 | 0.00020726 | 2.3029e-05 | No
2020-01-28 | 21:21 | DS1226 | Urban | Asset Failure | Distribution substation | 14 | 133.9286 | 0.002502 | 1.8682e-05 | No
2020-01-28 | 21:41 | D810 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 133 | 0.0017502 | 1.3159e-05 | No
2020-01-29 | 0:44 | SG1247 | Urban | Other | Isolation Request by EE | 1 | 125 | 0.0001668 | 1.3344e-06 | No
2020-01-29 | 0:45 | SG1247 | Urban | Unknown | Unknown | 26 | 124 | 0.0043021 | 3.4694e-05 | No
2020-01-29 | 8:05 | 49321 | Urban | Network business | Network error | 1.0002 | 23.2119 | 3.0981e-05 | 1.3347e-06 | No
2020-01-29 | 8:05 | 49319 | Urban | Network business | Network error | 820.1983 | 23.2119 | 0.025405 | 0.0010945 | No
2020-01-29 | 8:05 | 49328 | Urban | Network business | Network error | 713.1724 | 23.2119 | 0.02209 | 0.00095166 | No
2020-01-29 | 8:05 | 49335 | Short rural | Network business | Network error | 391.0946 | 23.2119 | 0.029866 | 0.0012866 | No
2020-01-29 | 8:05 | 49337 | Urban | Network business | Network error | 813.1966 | 23.2119 | 0.025188 | 0.0010851 | No
2020-01-29 | 8:05 | 49339 | Urban | Network business | Network error | 12.0029 | 23.2119 | 0.00037178 | 1.6017e-05 | No
2020-01-29 | 8:05 | 49341 | Urban | Network business | Network error | 738.1785 | 23.2119 | 0.022864 | 0.00098502 | No
2020-01-29 | 8:05 | 49348 | Urban | Network business | Network error | 947.229 | 23.2119 | 0.029339 | 0.001264 | No
2020-01-29 | 8:05 | 49353 | Urban | Network business | Network error | 80.0193 | 23.2119 | 0.0024785 | 0.00010678 | No
2020-01-29 | 8:05 | 49355 | Urban | Network business | Network error | 4.001 | 23.2119 | 0.00012393 | 5.3389e-06 | No
2020-01-29 | 8:05 | 49357 | Urban | Network business | Network error | 985.2382 | 23.2119 | 0.030517 | 0.0013147 | No
2020-01-29 | 8:05 | 49362 | Urban | Network business | Network error | 1089.2634 | 23.2119 | 0.033739 | 0.0014535 | No
2020-01-29 | 8:05 | 49364 | Urban | Network business | Network error | 1.0002 | 23.2119 | 3.0981e-05 | 1.3347e-06 | No
2020-01-29 | 8:05 | 49366 | Urban | Network business | Network error | 358.0866 | 23.2119 | 0.011091 | 0.00047783 | No
2020-01-29 | 8:05 | 49373 | Urban | Network business | Network error | 111.0268 | 23.2119 | 0.0034389 | 0.00014815 | No
2020-01-29 | 8:05 | 49382 | Urban | Network business | Network error | 190.0459 | 23.2119 | 0.0058865 | 0.0002536 | No
2020-01-29 | 8:05 | 49391 | Urban | Network business | Network error | 883.2135 | 23.2119 | 0.027357 | 0.0011786 | No
2020-01-29 | 8:05 | 49395 | Urban | Network business | Network error | 87.021 | 23.2119 | 0.0026954 | 0.00011612 | No
2020-01-29 | 8:05 | 49397 | Urban | Network business | Network error | 47.0114 | 23.2119 | 0.0014561 | 6.2732e-05 | No
2020-01-29 | 8:18 | J503 | Urban | Asset Failure | Distribution substation | 1 | 81 | 0.00010809 | 1.3344e-06 | No
2020-01-29 | 8:30 | 35418 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 542 | 0.0035662 | 6.5797e-06 | No
2020-01-29 | 8:58 | CT1265 | Urban | Asset Failure | Distribution substation | 38 | 168 | 0.0085188 | 5.0707e-05 | No
2020-01-29 | 9:31 | LP1112 | Urban | Third Party | Vehicle impact | 10.5439 | 412.8667 | 0.005809 | 1.407e-05 | No
2020-01-29 | 9:31 | 6421 | Urban | Third Party | Vehicle impact | 49.4561 | 412.8667 | 0.027247 | 6.5994e-05 | No
2020-01-29 | 10:25 | WBB2 | Short rural | Asset Failure | Distribution substation | 1 | 232 | 0.00076325 | 3.2899e-06 | No
2020-01-29 | 12:09 | D814 | Short rural | Unknown | Unknown | 3 | 150 | 0.0014804 | 9.8696e-06 | No
2020-01-29 | 12:16 | CS1243 | Urban | Unknown | Unknown | 3 | 336 | 0.0013451 | 4.0032e-06 | No
2020-01-29 | 14:03 | NG1210 | Short rural | Third Party | Other | 32 | 82 | 0.0086326 | 0.00010528 | No
2020-01-29 | 14:07 | HKC2 | Short rural | Third Party | Unauthorised access | 1 | 130 | 0.00042768 | 3.2899e-06 | No
2020-01-29 | 14:56 | 10244 | Short rural | Asset Failure | Distribution substation | 1 | 128 | 0.0004211 | 3.2899e-06 | No
2020-01-29 | 16:17 | DS1256 | Urban | Other | FOREIGN MATTER ON SYSTEM | 1668 | 33 | 0.073451 | 0.0022258 | No
2020-01-29 | 16:30 | 35988 | Short rural | Asset Failure | HV | 418 | 100.4904 | 0.13819 | 0.0013752 | No
2020-01-29 | 17:03 | LP1112 | Urban | Asset Failure | HV | 6 | 45 | 0.00036029 | 8.0064e-06 | No
2020-01-29 | 18:29 | L591 | Short rural | Asset Failure | Distribution substation | 1 | 161 | 0.00052967 | 3.2899e-06 | No
2020-01-29 | 20:06 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 50 | 161 | 0.026483 | 0.00016449 | No
2020-01-29 | 22:42 | TM1258 | Short rural | Asset Failure | HV | 1634 | 183.235 | 0.985 | 0.0053756 | No
2020-01-29 | 22:43 | NA1207 | Short rural | Animal | Animal Impact | 2 | 609 | 0.0040071 | 6.5797e-06 | No
2020-01-30 | 4:19 | 35824 | Short rural | Asset Failure | Distribution substation | 1 | 392 | 0.0012896 | 3.2899e-06 | No
2020-01-30 | 9:40 | SZ1322 | Short rural | Asset Failure | Distribution substation | 23 | 94.2609 | 0.0071324 | 7.5667e-05 | No
2020-01-30 | 11:03 | KVB2 | Short rural | Animal | Animal Impact | 1 | 472 | 0.0015528 | 3.2899e-06 | No
2020-01-30 | 11:54 | BK1288 | Short rural | Vegetation | Grow-in - NSP responsibility | 9 | 247 | 0.0073134 | 2.9609e-05 | No
2020-01-30 | 12:55 | OA1207 | Short rural | Asset Failure | Distribution substation | 1 | 189 | 0.00062178 | 3.2899e-06 | No
2020-01-30 | 17:57 | 8780 | Urban | Unknown | Unknown | 12 | 292 | 0.0046757 | 1.6013e-05 | No
2020-01-30 | 18:02 | 9059 | Urban | Asset Failure | Distribution substation | 1 | 325 | 0.00043368 | 1.3344e-06 | No
2020-01-30 | 18:16 | 68197 | Urban | Asset Failure | Distribution substation | 39 | 139 | 0.0072338 | 5.2042e-05 | No
2020-01-31 | 0:56 | D852 | Urban | Unknown | Unknown | 13 | 77 | 0.0013357 | 1.7347e-05 | No
2020-01-31 | 6:17 | LP1142 | Urban | Unknown | Unknown | 17 | 115 | 0.0026088 | 2.2685e-05 | No
2020-01-31 | 8:16 | MR2292 | Urban | Third Party | Unauthorised access | 1 | 38 | 5.0707e-05 | 1.3344e-06 | No
2020-01-31 | 8:44 | AZ1290 | Urban | Asset Failure | Distribution substation | 22 | 587.0455 | 0.017234 | 2.9357e-05 | No
2020-01-31 | 9:51 | ULH2 | Short rural | Vegetation | Grow-in - NSP responsibility | 25 | 145.2 | 0.011942 | 8.2247e-05 | No
2020-01-31 | 14:01 | DFA2 | Short rural | Asset Failure | Distribution substation | 1 | 45 | 0.00014804 | 3.2899e-06 | No
2020-01-31 | 16:43 | C899 | Urban | Weather |  | 9 | 91 | 0.0010929 | 1.201e-05 | No
2020-01-31 | 16:48 | 8777 | Urban | Asset Failure | Distribution substation | 26 | 393.5769 | 0.013655 | 3.4694e-05 | No
2020-01-31 | 16:54 | SY1322 | Urban | Unknown | Unknown | 64 | 101 | 0.0086256 | 8.5402e-05 | No
2020-01-31 | 16:59 | CLA2 | Short rural | Other | Probable Overload | 4 | 141 | 0.0018555 | 1.3159e-05 | No
2020-01-31 | 17:12 | S774 | Urban | Weather |  | 21 | 125 | 0.0035028 | 2.8022e-05 | No
2020-01-31 | 17:55 | WH1209 | Urban | Asset Failure | Distribution substation | 12 | 96 | 0.0015372 | 1.6013e-05 | No
2020-01-31 | 18:01 | HT1294 | Urban | Weather |  | 14 | 60 | 0.0011209 | 1.8682e-05 | No
2020-01-31 | 18:17 | NL1172 | Urban | Asset Failure | Distribution substation | 5 | 141 | 0.00094075 | 6.672e-06 | No
2020-01-31 | 18:57 | OP1262 | Short rural | Asset Failure | Distribution substation | 11 | 381.4545 | 0.013804 | 3.6188e-05 | No
2020-01-31 | 18:59 | S765 | Urban | Weather |  | 18 | 35 | 0.00084067 | 2.4019e-05 | No
2020-01-31 | 19:08 | 49006 | Short rural | Weather |  | 77 | 1287.1169 | 0.32605 | 0.00025332 | No
2020-01-31 | 19:44 | DS1256 | Urban | Weather |  | 25 | 52 | 0.0017347 | 3.336e-05 | No
2020-01-31 | 20:12 | SY1132 | Urban | Weather |  | 50 | 78 | 0.0052042 | 6.672e-05 | No
2020-01-31 | 20:27 | SG1220 | Urban | Asset Failure | Distribution substation | 26 | 341 | 0.011831 | 3.4694e-05 | No
2020-01-31 | 20:59 | S774 | Urban | Weather |  | 21 | 113 | 0.0031665 | 2.8022e-05 | No
2020-01-31 | 21:03 | 9049 | Urban | Weather |  | 110 | 132 | 0.019375 | 0.00014678 | No
2020-01-31 | 21:05 | 16660 | Urban | Weather |  | 7 | 435 | 0.0040632 | 9.3408e-06 | No
2020-01-31 | 21:19 | MR2231 | Urban | Asset Failure | HV | 1216 | 107.5469 | 0.17451 | 0.0016226 | No
2020-01-31 | 23:01 | 1954 | Urban | Asset Failure | Distribution substation | 30 | 294.1667 | 0.011776 | 4.0032e-05 | No
2020-02-01 | 0:58 | KVB2 | Short rural | Asset Failure | LV | 21 | 137.5238 | 0.0095011 | 6.9087e-05 | No
2020-02-01 | 6:21 | 8777 | Urban | Asset Failure | Distribution substation | 51 | 2.1176 | 0.00014412 | 6.8054e-05 | No
2020-02-01 | 6:59 | MM1352 | Short rural | Third Party | Dig-in | 1 | 385 | 0.0012666 | 3.2899e-06 | No
2020-02-01 | 7:21 | 2809 | Urban | Third Party | Other | 18 | 180 | 0.0043235 | 2.4019e-05 | No
2020-02-01 | 11:17 | L509 | Urban | Asset Failure | Distribution substation | 1 | 150 | 0.00020016 | 1.3344e-06 | No
2020-02-01 | 12:53 | SG1247 | Urban | Weather |  | 44 | 72 | 0.0042274 | 5.8714e-05 | No
2020-02-01 | 13:15 | BDA2 | Short rural | Asset Failure | Distribution substation | 2 | 155 | 0.0010199 | 6.5797e-06 | No
2020-02-01 | 13:23 | RS1207 | Urban | Weather |  | 57 | 90 | 0.0068455 | 7.6061e-05 | No
2020-02-01 | 13:31 | SG1254 | Urban | Weather |  | 24 | 62 | 0.0019856 | 3.2026e-05 | No
2020-02-01 | 13:37 | L582 | Short rural | Weather |  | 1 | 146 | 0.00048032 | 3.2899e-06 | No
2020-02-01 | 13:42 | BK1236 | Short rural | Weather |  | 17 | 75 | 0.0041946 | 5.5928e-05 | No
2020-02-01 | 13:58 | SG1220 | Urban | Weather |  | 24 | 776 | 0.024852 | 3.2026e-05 | No
2020-02-01 | 14:15 | MVC2 | Short rural | Weather |  | 14 | 96 | 0.0044216 | 4.6058e-05 | No
2020-02-01 | 14:22 | 7976 | Urban | Weather |  | 34 | 97.9412 | 0.0044435 | 4.537e-05 | No
2020-02-01 | 14:32 | 2812 | Urban | Weather |  | 126 | 180.7778 | 0.030395 | 0.00016813 | No
2020-02-01 | 14:42 | L538 | Urban | Weather |  | 1 | 69 | 9.2074e-05 | 1.3344e-06 | No
2020-02-01 | 16:33 | SG1254 | Urban | Unknown | Unknown | 24 | 83 | 0.0026581 | 3.2026e-05 | No
2020-02-01 | 16:44 | FF1206 | Urban | Weather |  | 21 | 118 | 0.0033066 | 2.8022e-05 | No
2020-02-01 | 16:51 | SG1247 | Urban | Weather |  | 47 | 98 | 0.0061462 | 6.2717e-05 | No
2020-02-01 | 17:02 | S774 | Urban | Weather |  | 21 | 50 | 0.0014011 | 2.8022e-05 | No
2020-02-01 | 17:22 | RD1269 | Urban | Weather |  | 33 | 123 | 0.0054163 | 4.4035e-05 | No
2020-02-01 | 17:27 | 68195 | Urban | Weather |  | 51 | 103 | 0.0070096 | 6.8054e-05 | No
2020-02-01 | 17:46 | 27194 | Urban | Weather |  | 8 | 311 | 0.00332 | 1.0675e-05 | No
2020-02-01 | 18:08 | BX1342 | Urban | Weather |  | 8 | 168 | 0.0017934 | 1.0675e-05 | No
2020-02-01 | 18:13 | 8615 | Urban | Weather |  | 25 | 65 | 0.0021684 | 3.336e-05 | No
2020-02-01 | 18:14 | 35702 | Urban | Weather |  | 11 | 169 | 0.0024806 | 1.4678e-05 | No
2020-02-01 | 18:17 | C820 | Urban | Weather |  | 22 | 254 | 0.0074566 | 2.9357e-05 | No
2020-02-01 | 18:34 | WL1295 | Urban | Weather |  | 66 | 104 | 0.0091593 | 8.807e-05 | No
2020-02-01 | 18:38 | AB1271 | Urban | Weather |  | 15 | 175 | 0.0035028 | 2.0016e-05 | No
2020-02-01 | 18:44 | 48178 | Urban | Weather |  | 12 | 108 | 0.0017294 | 1.6013e-05 | No
2020-02-01 | 18:47 | 61617 | Short rural | Weather |  | 14 | 135 | 0.0062178 | 4.6058e-05 | No
2020-02-01 | 18:50 | SG1220 | Urban | Asset Failure | Distribution substation | 26 | 308.5769 | 0.010706 | 3.4694e-05 | No
2020-02-01 | 18:51 | DS1256 | Urban | Weather |  | 25 | 104 | 0.0034694 | 3.336e-05 | No
2020-02-01 | 18:51 | ULH2 | Short rural | Unknown | Unknown | 31 | 267.5161 | 0.027283 | 0.00010199 | No
2020-02-01 | 18:52 | NG1247 | Urban | Asset Failure | Distribution substation | 18 | 235 | 0.0056445 | 2.4019e-05 | No
2020-02-01 | 18:53 | SC1289 | Short rural | Vegetation | Grow-in - NSP responsibility | 750.6173 | 98.9624 | 0.24438 | 0.0024694 | No
2020-02-01 | 18:53 | A053 | Urban | Vegetation | Grow-in - NSP responsibility | 127.3827 | 98.9624 | 0.016822 | 0.00016998 | No
2020-02-01 | 18:57 | CV1221 | Urban | Weather |  | 31 | 44 | 0.0018201 | 4.1366e-05 | No
2020-02-01 | 19:00 | NA1214 | Urban | Weather |  | 28 | 276.75 | 0.01034 | 3.7363e-05 | No
2020-02-01 | 19:03 | AZ1272 | Short rural | Weather |  | 36 | 204.5 | 0.02422 | 0.00011844 | No
2020-02-01 | 19:14 | B713 | Urban | Weather |  | 69 | 160 | 0.014732 | 9.2074e-05 | No
2020-02-01 | 19:16 | BDC2 | Short rural | Unknown | Unknown | 338.5735 | 75 | 0.08354 | 0.0011139 | No
2020-02-01 | 19:16 | KVA2 | Short rural | Unknown | Unknown | 316.9256 | 75 | 0.078198 | 0.0010426 | No
2020-02-01 | 19:16 | KVB2 | Short rural | Unknown | Unknown | 345.5009 | 75 | 0.085249 | 0.0011367 | No
2020-02-01 | 19:18 | T876 | Urban | Weather |  | 11 | 45 | 0.00066053 | 1.4678e-05 | No
2020-02-01 | 19:20 | 55361 | Urban | Asset Failure | Distribution substation | 12 | 265.5 | 0.0042514 | 1.6013e-05 | No
2020-02-01 | 19:21 | 1959 | Urban | Weather |  | 15 | 106 | 0.0021217 | 2.0016e-05 | No
2020-02-01 | 19:24 | BDC2 | Short rural | Asset Failure | Distribution substation | 7 | 967.1429 | 0.022272 | 2.3029e-05 | No
2020-02-01 | 19:24 | 2815 | Urban | Weather |  | 15 | 345 | 0.0069055 | 2.0016e-05 | No
2020-02-01 | 19:32 | CS1239 | Short rural | Weather |  | 9 | 256 | 0.0075798 | 2.9609e-05 | No
2020-02-01 | 19:32 | SY1132 | Urban | Weather |  | 50 | 146 | 0.0097411 | 6.672e-05 | No
2020-02-01 | 19:48 | AB1241 | Urban | Weather |  | 11 | 117 | 0.0017174 | 1.4678e-05 | No
2020-02-01 | 19:55 | 25782 | Urban | Weather |  | 10 | 97 | 0.0012944 | 1.3344e-05 | No
2020-02-01 | 20:09 | 25746 | Urban | Weather |  | 12 | 205 | 0.0032826 | 1.6013e-05 | No
2020-02-01 | 20:11 | WH1294 | Urban | Weather |  | 17 | 185 | 0.0041967 | 2.2685e-05 | No
2020-02-01 | 20:15 | T883 | Urban | Weather |  | 27 | 68 | 0.00245 | 3.6029e-05 | No
2020-02-01 | 20:26 | BDC2 | Short rural | Overload |  | 63 | 2 | 0.00041452 | 0.00020726 | No
2020-02-01 | 20:32 | 8651 | Urban | Weather |  | 37 | 193 | 0.0095289 | 4.9373e-05 | No
2020-02-01 | 20:35 | C851 | Urban | Weather |  | 20 | 113 | 0.0030157 | 2.6688e-05 | No
2020-02-01 | 20:38 | CS1213 | Urban | Weather |  | 67 | 53 | 0.0047385 | 8.9405e-05 | No
2020-02-01 | 20:43 | SXC2 | Short rural | Animal | Animal Impact | 202 | 235.6139 | 0.15658 | 0.00066455 | No
2020-02-01 | 21:11 | SG1247 | Urban | Weather |  | 47 | 222 | 0.013923 | 6.2717e-05 | No
2020-02-01 | 21:17 | 55874 | Urban | Weather |  | 12 | 138 | 0.0022098 | 1.6013e-05 | No
2020-02-01 | 21:37 | FT1207 | Urban | Weather |  | 12 | 35 | 0.00056045 | 1.6013e-05 | No
2020-02-01 | 21:38 | B716 | Urban | Weather |  | 8 | 49 | 0.00052308 | 1.0675e-05 | No
2020-02-01 | 21:41 | SG1250 | Urban | Weather |  | 10 | 104 | 0.0013878 | 1.3344e-05 | No
2020-02-01 | 21:43 | 2812 | Urban | Weather |  | 42 | 142 | 0.0079584 | 5.6045e-05 | No
2020-02-01 | 22:02 | 1959 | Urban | Weather |  | 15 | 57 | 0.0011409 | 2.0016e-05 | No
2020-02-01 | 22:02 | A347 | Urban | Asset Failure | Distribution substation | 33 | 56.3939 | 0.0024833 | 4.4035e-05 | No
2020-02-01 | 22:26 | SY1132 | Urban | Weather |  | 50 | 77 | 0.0051374 | 6.672e-05 | No
2020-02-01 | 22:31 | RD1269 | Urban | Weather |  | 33 | 95 | 0.0041833 | 4.4035e-05 | No
2020-02-01 | 22:33 | RS1262 | Urban | Weather |  | 29 | 150 | 0.0058046 | 3.8698e-05 | No
2020-02-01 | 22:36 | CS1213 | Urban | Weather |  | 67 | 197 | 0.017613 | 8.9405e-05 | No
2020-02-01 | 22:41 | 25747 | Urban | Weather |  | 13 | 72 | 0.001249 | 1.7347e-05 | No
2020-02-01 | 23:01 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 261 | 292.5824 | 0.25123 | 0.00085865 | No
2020-02-01 | 23:10 | CJ1267 | Urban | Weather |  | 1 | 146 | 0.00019482 | 1.3344e-06 | No
2020-02-01 | 23:12 | B748 | Urban | Asset Failure | Distribution substation | 8.0897 | 268.95 | 0.0029033 | 1.0795e-05 | No
2020-02-01 | 23:12 | 1962 | Urban | Asset Failure | Distribution substation | 11.9103 | 268.95 | 0.0042745 | 1.5893e-05 | No
2020-02-01 | 23:39 | ULH2 | Short rural | Unknown | Unknown | 120 | 18.7 | 0.0073825 | 0.00039478 | No
2020-02-02 | 0:17 | 1959 | Urban | Weather |  | 15 | 114 | 0.0022818 | 2.0016e-05 | No
2020-02-02 | 0:53 | 8737 | Urban | Asset Failure | Distribution substation | 37 | 885.4865 | 0.043719 | 4.9373e-05 | No
2020-02-02 | 0:53 | OA1233 | Short rural | Vegetation | Grow-in - NSP responsibility | 39 | 244.641 | 0.031389 | 0.0001283 | No
2020-02-02 | 1:11 | DS1235 | Urban | Weather |  | 54 | 87 | 0.006269 | 7.2058e-05 | No
2020-02-02 | 1:37 | RS1262 | Urban | Weather |  | 29 | 139 | 0.005379 | 3.8698e-05 | No
2020-02-02 | 4:19 | RBA2 | Short rural | Asset Failure | Zone substation | 552.2935 | 114.2257 | 0.20754 | 0.001817 | No
2020-02-02 | 4:19 | RBB2 | Short rural | Asset Failure | Zone substation | 388.0385 | 114.2257 | 0.14582 | 0.0012766 | No
2020-02-02 | 4:19 | RBC2 | Short rural | Asset Failure | Zone substation | 555.6006 | 114.2257 | 0.20879 | 0.0018279 | No
2020-02-02 | 4:19 | RBD2 | Short rural | Asset Failure | Zone substation | 223.7836 | 114.2257 | 0.084095 | 0.00073622 | No
2020-02-02 | 4:19 | RBE2 | Short rural | Asset Failure | Zone substation | 455.2838 | 114.2257 | 0.17109 | 0.0014978 | No
2020-02-02 | 4:46 | HBA2 | Short rural | Other | Probable Animals | 11 | 211 | 0.0076358 | 3.6188e-05 | No
2020-02-02 | 6:37 | GV1204 | Urban | Unknown | Unknown | 29 | 95 | 0.0036763 | 3.8698e-05 | No
2020-02-02 | 7:35 | BYB2 | Short rural | Unknown | Unknown | 2 | 393 | 0.0025858 | 6.5797e-06 | No
2020-02-02 | 8:13 | SC1289 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 167 | 0.00054941 | 3.2899e-06 | No
2020-02-02 | 8:21 | RW1255 | Short rural | Asset Failure | Distribution substation | 10 | 269.5 | 0.0088662 | 3.2899e-05 | No
2020-02-02 | 8:24 | J510 | Urban | Asset Failure | Distribution substation | 10 | 48.5 | 0.00064718 | 1.3344e-05 | No
2020-02-02 | 10:31 | CLC2 | Short rural | Asset Failure | Distribution substation | 32 | 338.125 | 0.035596 | 0.00010528 | No
2020-02-02 | 11:52 | C832 | Urban | Asset Failure | Distribution substation | 27 | 271.1852 | 0.0097705 | 3.6029e-05 | No
2020-02-02 | 13:47 | AB1271 | Urban | Overload |  | 15 | 62 | 0.001241 | 2.0016e-05 | No
2020-02-02 | 14:33 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 118 | 94 | 0.036491 | 0.0003882 | No
2020-02-02 | 14:33 | 35990 | Short rural | Asset Failure | Distribution substation | 53 | 1033 | 0.18012 | 0.00017436 | No
2020-02-02 | 15:11 | NN1251 | Short rural | Asset Failure | Distribution substation | 18 | 243.8889 | 0.014442 | 5.9218e-05 | No
2020-02-02 | 16:04 | WT1215 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 421 | 59.3658 | 0.082224 | 0.001385 | No
2020-02-02 | 16:23 | 7979 | Urban | Asset Failure | Distribution substation | 16 | 57 | 0.001217 | 2.135e-05 | No
2020-02-02 | 16:35 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 413 | 39.4746 | 0.053635 | 0.0013587 | No
2020-02-02 | 16:45 | L947 | Short rural | Unknown | Unknown | 16 | 91 | 0.00479 | 5.2638e-05 | No
2020-02-02 | 17:49 | ULH2 | Short rural | Weather |  | 169 | 87.3136 | 0.048545 | 0.00055599 | No
2020-02-02 | 17:53 | W163 | Short rural | Asset Failure | HV | 41 | 188.878 | 0.025477 | 0.00013488 | No
2020-02-02 | 18:03 | A045 | Short rural | Weather |  | 578 | 125.1159 | 0.23791 | 0.0019015 | No
2020-02-02 | 18:09 | SZ1242 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 4 | 153 | 0.0020134 | 1.3159e-05 | No
2020-02-02 | 18:37 | 4873 | Urban | Asset Failure | Distribution substation | 28 | 283 | 0.010574 | 3.7363e-05 | No
2020-02-02 | 18:41 | HR1206 | Urban | Weather |  | 1706.5208 | 12 | 0.027326 | 0.0022772 | No
2020-02-02 | 18:41 | HR1210 | Urban | Weather |  | 713.7797 | 12 | 0.01143 | 0.00095247 | No
2020-02-02 | 18:41 | HR1213 | Urban | Weather |  | 1049.211 | 12 | 0.016801 | 0.0014001 | No
2020-02-02 | 18:41 | HR1217 | Urban | Weather |  | 363.6662 | 12 | 0.0058233 | 0.00048528 | No
2020-02-02 | 18:41 | HR1236 | Urban | Weather |  | 1831.884 | 12 | 0.029334 | 0.0024445 | No
2020-02-02 | 18:41 | HR1239 | Urban | Weather |  | 1177.9624 | 12 | 0.018862 | 0.0015719 | No
2020-02-02 | 18:41 | HR1243 | Urban | Weather |  | 1260.4085 | 12 | 0.020183 | 0.0016819 | No
2020-02-02 | 18:41 | HR1247 | Urban | Weather |  | 1307.8432 | 12 | 0.020942 | 0.0017452 | No
2020-02-02 | 18:41 | HR1250 | Urban | Weather |  | 1892.8715 | 12 | 0.03031 | 0.0025258 | No
2020-02-02 | 18:41 | HR1269 | Urban | Weather |  | 791.7082 | 12 | 0.012677 | 0.0010565 | No
2020-02-02 | 18:41 | HR1273 | Urban | Weather |  | 1804.7784 | 12 | 0.0289 | 0.0024083 | No
2020-02-02 | 18:41 | HR1276 | Urban | Weather |  | 2126.6569 | 12 | 0.034054 | 0.0028378 | No
2020-02-02 | 18:41 | HR1280 | Short rural | Weather |  | 695.7093 | 12 | 0.027465 | 0.0022888 | No
2020-02-02 | 19:21 | OP1172 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 987 | 32.5603 | 0.042884 | 0.0013171 | No
2020-02-02 | 19:27 | 35702 | Urban | Other | Probable Lightning/Electrical Storm | 29 | 264 | 0.010216 | 3.8698e-05 | No
2020-02-02 | 19:32 | 9049 | Urban | Weather |  | 1302 | 137.4846 | 0.23886 | 0.0017374 | No
2020-02-02 | 19:41 | OP1122 | Short rural | Weather |  | 1 | 1491 | 0.0049052 | 3.2899e-06 | No
2020-02-02 | 19:49 | CV1269 | Urban | Asset Failure | Distribution substation | 51 | 178 | 0.012114 | 6.8054e-05 | No
2020-02-02 | 20:01 | CV1269 | Urban | Weather |  | 774 | 147.3385 | 0.15217 | 0.0010328 | No
2020-02-02 | 20:01 | 10245 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 918 | 85 | 0.25671 | 0.0030201 | No
2020-02-02 | 20:15 | HR1213 | Urban | Asset Failure | Distribution substation | 21 | 243 | 0.0068094 | 2.8022e-05 | No
2020-02-02 | 20:17 | J507 | Short rural | Vegetation | Grow-in - NSP responsibility | 55 | 282 | 0.051026 | 0.00018094 | No
2020-02-02 | 20:20 | 49328 | Urban | Asset Failure | Distribution substation | 1 | 819 | 0.0010929 | 1.3344e-06 | No
2020-02-02 | 20:27 | HS1142 | Short rural | Unknown | Unknown | 8 | 86 | 0.0022634 | 2.6319e-05 | No
2020-02-02 | 20:32 | BX1242 | Urban | Vegetation | Grow-in - NSP responsibility | 42 | 93.3333 | 0.0052308 | 5.6045e-05 | No
2020-02-02 | 20:34 | WWB2 | Short rural | Asset Failure | Distribution substation | 32 | 37 | 0.0038952 | 0.00010528 | No
2020-02-02 | 21:06 | 8802 | Short rural | Network business | Switching or protection error | 734.2322 | 69 | 0.16667 | 0.0024155 | No
2020-02-02 | 21:06 | L946 | Short rural | Network business | Switching or protection error | 451.7678 | 69 | 0.10255 | 0.0014863 | No
2020-02-02 | 21:17 | 8798 | Short rural | Weather |  | 10 | 77 | 0.0025332 | 3.2899e-05 | No
2020-02-02 | 21:36 | A045 | Short rural | Weather |  | 31 | 6.2581 | 0.00063823 | 0.00010199 | No
2020-02-02 | 21:41 | B217 | Urban | Asset Failure | HV | 2376 | 43.2715 | 0.13719 | 0.0031705 | No
2020-02-03 | 0:44 | SXD2 | Short rural | Weather |  | 86 | 141 | 0.039893 | 0.00028293 | No
2020-02-03 | 6:57 | SXB2 | Short rural | Asset Failure | Distribution substation | 1 | 637 | 0.0020956 | 3.2899e-06 | No
2020-02-03 | 7:17 | SZ1332 | Short rural | Unknown | Unknown | 1 | 200 | 0.00065797 | 3.2899e-06 | No
2020-02-03 | 7:34 | 8798 | Short rural | Unknown | Unknown | 2 | 323 | 0.0021253 | 6.5797e-06 | No
2020-02-03 | 8:24 | B211 | Urban | Unknown | Unknown | 1 | 81 | 0.00010809 | 1.3344e-06 | No
2020-02-03 | 8:27 | APE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 50 | 175.8 | 0.028918 | 0.00016449 | No
2020-02-03 | 8:35 | NN1236 | Urban | Asset Failure | Distribution substation | 51 | 221.7059 | 0.015088 | 6.8054e-05 | No
2020-02-03 | 9:04 | RBB2 | Short rural | Other | Probable Overload | 1 | 661 | 0.0021746 | 3.2899e-06 | No
2020-02-03 | 10:40 | HR1269 | Urban | Asset Failure | Distribution substation | 43 | 75.1163 | 0.0043101 | 5.7379e-05 | No
2020-02-03 | 10:48 | C900 | Urban | Asset Failure | Distribution substation | 1 | 294 | 0.00039231 | 1.3344e-06 | No
2020-02-03 | 10:50 | T889 | Urban | Vegetation | Grow-in - NSP responsibility | 31 | 40.3548 | 0.0016693 | 4.1366e-05 | No
2020-02-03 | 11:45 | ULH2 | Short rural | Vegetation | Grow-in - NSP responsibility | 35 | 66 | 0.0075996 | 0.00011515 | No
2020-02-03 | 12:08 | RBE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 142 | 141.2113 | 0.065968 | 0.00046716 | No
2020-02-03 | 13:18 | RBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 501 | 183.0359 | 0.30168 | 0.0016482 | No
2020-02-03 | 15:25 | D814 | Short rural | Other | Probable Lightning/Electrical Storm | 7 | 277 | 0.006379 | 2.3029e-05 | No
2020-02-03 | 15:33 | 8798 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 107.5 | 0.00070732 | 6.5797e-06 | No
2020-02-03 | 16:53 | CV1284 | Urban | Asset Failure | Distribution substation | 2 | 515 | 0.0013744 | 2.6688e-06 | No
2020-02-03 | 16:53 | H745 | Short rural | Unknown | Unknown | 593 | 89.9275 | 0.17544 | 0.0019509 | No
2020-02-03 | 17:52 | S786 | Short rural | Asset Failure | HV | 524.1464 | 131.6781 | 0.22706 | 0.0017244 | No
2020-02-03 | 17:52 | S788 | Short rural | Asset Failure | HV | 643.8536 | 131.6781 | 0.27892 | 0.0021182 | No
2020-02-03 | 18:28 | B720 | Urban | Overload |  | 42 | 361 | 0.020232 | 5.6045e-05 | No
2020-02-03 | 18:42 | HBA2 | Short rural | Asset Failure | HV | 815 | 17.5436 | 0.047038 | 0.0026812 | No
2020-02-03 | 18:46 | B210 | Urban | Network business | Network error | 1 | 295 | 0.00039365 | 1.3344e-06 | No
2020-02-03 | 19:09 | 7979 | Urban | Unknown | Unknown | 6 | 187 | 0.0014972 | 8.0064e-06 | No
2020-02-03 | 20:23 | OP1122 | Short rural | Asset Failure | Distribution substation | 1 | 412 | 0.0013554 | 3.2899e-06 | No
2020-02-03 | 22:00 | KC1284 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 517 | 61 | 0.10375 | 0.0017009 | No
2020-02-03 | 22:57 | X877 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 3 | 32 | 0.00031583 | 9.8696e-06 | No
2020-02-04 | 0:34 | BWD2 | Urban | Animal | Animal Impact | 28 | 156 | 0.0058287 | 3.7363e-05 | No
2020-02-04 | 3:18 | ULD2 | Urban | Asset Failure | HV | 902 | 100.898 | 0.12144 | 0.0012036 | No
2020-02-04 | 7:07 | WH1261 | Urban | Third Party | Dig-in | 1 | 742 | 0.00099012 | 1.3344e-06 | No
2020-02-04 | 7:13 | 35307 | Urban | Asset Failure | Distribution substation | 3 | 114 | 0.00045636 | 4.0032e-06 | No
2020-02-04 | 7:26 | S740 | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 109 | 0.0002909 | 2.6688e-06 | No
2020-02-04 | 7:56 | ULF2 | Short rural | Unknown | Unknown | 4 | 360.25 | 0.0047407 | 1.3159e-05 | No
2020-02-04 | 9:37 | WH1298 | Urban | Asset Failure | Distribution substation | 34 | 42.0294 | 0.0019069 | 4.537e-05 | No
2020-02-04 | 11:50 | 49395 | Urban | Third Party | Dig-in | 87 | 46.5977 | 0.0054097 | 0.00011609 | No
2020-02-04 | 13:19 | MR2292 | Urban | Third Party | Unauthorised access | 1 | 508 | 0.00067787 | 1.3344e-06 | No
2020-02-04 | 13:42 | B747 | Urban | Unknown | Unknown | 100 | 102 | 0.013611 | 0.00013344 | No
2020-02-04 | 13:48 | S738 | Short rural | Other | Isolation Request by EE | 7 | 15 | 0.00034544 | 2.3029e-05 | No
2020-02-04 | 14:03 | CR1262 | Urban | Asset Failure | Distribution substation | 214 | 90 | 0.025701 | 0.00028556 | No
2020-02-04 | 16:02 | 87220 | Short rural | Unknown | Unknown | 1 | 1350 | 0.0044413 | 3.2899e-06 | No
2020-02-04 | 17:14 | 35990 | Short rural | Asset Failure | Distribution substation | 53 | 28.2453 | 0.0049249 | 0.00017436 | No
2020-02-04 | 19:32 | W124 | Short rural | Asset Failure | Distribution substation | 1 | 183 | 0.00060204 | 3.2899e-06 | No
2020-02-05 | 7:45 | C820 | Urban | Unknown | Unknown | 1 | 110 | 0.00014678 | 1.3344e-06 | No
2020-02-05 | 9:31 | D813 | Short rural | Other | Isolation Request by EE | 5 | 44.2 | 0.00072706 | 1.6449e-05 | No
2020-02-05 | 9:58 | LP1232 | Urban | Asset Failure | Distribution substation | 69 | 135.1884 | 0.012447 | 9.2074e-05 | No
2020-02-05 | 10:01 | 53805 | Short rural | Asset Failure | Distribution substation | 1 | 345 | 0.001135 | 3.2899e-06 | No
2020-02-05 | 13:41 | A046 | Short rural | Vegetation | Blow-in/Fall-in - Other responsible party | 1090 | 35.8422 | 0.12853 | 0.003586 | No
2020-02-05 | 18:44 | CD1260 | Urban | Asset Failure | Distribution substation | 15 | 275.6 | 0.0055164 | 2.0016e-05 | No
2020-02-05 | 18:54 | 4870 | Urban | Other | FOREIGN MATTER ON SYSTEM | 2 | 46 | 0.00012276 | 2.6688e-06 | No
2020-02-05 | 19:58 | WD1225 | Short rural | Asset Failure | Distribution substation | 4 | 254 | 0.0033425 | 1.3159e-05 | No
2020-02-05 | 20:28 | J460 | Urban | Other | Within Customer Installation | 9 | 2602 | 0.031249 | 1.201e-05 | No
2020-02-05 | 22:01 | CV1247 | Urban | Asset Failure | Distribution substation | 10 | 55.9 | 0.00074593 | 1.3344e-05 | No
2020-02-05 | 22:14 | KME2 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 148 | 0.0014607 | 9.8696e-06 | No
2020-02-06 | 3:02 | S738 | Short rural | Asset Failure | Distribution substation | 10 | 502 | 0.016515 | 3.2899e-05 | No
2020-02-06 | 3:03 | DS1257 | Urban | Unknown | Unknown | 10 | 435 | 0.0058046 | 1.3344e-05 | No
2020-02-06 | 6:09 | 35988 | Short rural | Weather |  | 135 | 41.8815 | 0.018601 | 0.00044413 | No
2020-02-06 | 7:08 | WD1258 | Urban | Asset Failure | Distribution substation | 3 | 158 | 0.00063251 | 4.0032e-06 | No
2020-02-06 | 7:49 | SZ1132 | Urban | Vegetation | Grow-in - NSP responsibility | 242 | 55 | 0.017761 | 0.00032292 | No
2020-02-06 | 7:57 | 8798 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 277 | 0.00091129 | 3.2899e-06 | No
2020-02-06 | 10:00 | CV1236 | Urban | Asset Failure | HV | 1660 | 145.6747 | 0.32268 | 0.0022151 | No
2020-02-06 | 11:56 | 9017 | Urban | Asset Failure | HV | 272 | 61.114 | 0.022182 | 0.00036296 | No
2020-02-06 | 11:58 | CD1234 | Short rural | Asset Failure | Distribution substation | 1 | 430 | 0.0014146 | 3.2899e-06 | No
2020-02-06 | 15:37 | 35762 | Urban | Asset Failure | Distribution substation | 24 | 59.8333 | 0.0019162 | 3.2026e-05 | No
2020-02-06 | 15:58 | R293 | Short rural | Weather |  | 95 | 293.8421 | 0.091837 | 0.00031254 | No
2020-02-06 | 20:31 | 8611 | Urban | Vegetation | Grow-in - NSP responsibility | 126.8872 | 24 | 0.0040636 | 0.00016932 | No
2020-02-06 | 20:31 | 8615 | Urban | Vegetation | Grow-in - NSP responsibility | 824.1128 | 24 | 0.026393 | 0.0010997 | No
2020-02-06 | 21:30 | X482 | Short rural | Unknown | Unknown | 108 | 29.4259 | 0.010455 | 0.00035531 | No
2020-02-06 | 23:30 | FT1206 | Short rural | Vegetation | Grow-in - NSP responsibility | 52 | 126 | 0.021555 | 0.00017107 | No
2020-02-07 | 0:18 | HBC2 | Short rural | Animal | Animal Impact | 912 | 145.5219 | 0.43662 | 0.0030004 | No
2020-02-07 | 4:57 | W188 | Short rural | Vegetation | Grow-in - NSP responsibility | 37 | 97.8919 | 0.011916 | 0.00012172 | No
2020-02-07 | 5:27 | BL1251 | Urban | Animal | Animal Impact | 1554 | 63.6828 | 0.13206 | 0.0020737 | No
2020-02-07 | 5:34 | SZ1332 | Short rural | Vegetation | Grow-in - NSP responsibility | 366 | 113.7186 | 0.13693 | 0.0012041 | No
2020-02-07 | 6:26 | 35327 | Urban | Vegetation | Grow-in - NSP responsibility | 10 | 103 | 0.0013744 | 1.3344e-05 | No
2020-02-07 | 7:10 | CJ1204 | Urban | Unknown | Unknown | 41 | 105 | 0.0057446 | 5.471e-05 | No
2020-02-07 | 7:25 | SQ1332 | Urban | Unknown | Unknown | 10 | 221 | 0.002949 | 1.3344e-05 | No
2020-02-07 | 7:38 | RBD2 | Short rural | Unknown | Unknown | 1 | 171 | 0.00056257 | 3.2899e-06 | No
2020-02-07 | 8:07 | C852 | Urban | Asset Failure | Distribution substation | 21 | 255 | 0.0071457 | 2.8022e-05 | No
2020-02-07 | 9:03 | 35327 | Urban | Asset Failure | Distribution substation | 16 | 166.3125 | 0.0035508 | 2.135e-05 | No
2020-02-07 | 9:10 | MVC2 | Short rural | Unknown | Unknown | 1 | 245 | 0.00080602 | 3.2899e-06 | No
2020-02-07 | 9:35 | J503 | Urban | Unknown | Unknown | 10 | 146 | 0.0019482 | 1.3344e-05 | No
2020-02-07 | 9:37 | ULF2 | Short rural | Asset Failure | Distribution substation | 1 | 108 | 0.00035531 | 3.2899e-06 | No
2020-02-07 | 10:30 | FT1207 | Urban | Asset Failure | HV | 623.6334 | 87.5254 | 0.072837 | 0.00083218 | No
2020-02-07 | 10:30 | FT1206 | Short rural | Asset Failure | HV | 301.3666 | 87.5254 | 0.086777 | 0.00099145 | No
2020-02-07 | 11:17 | 8798 | Short rural | Vegetation | Grow-in - NSP responsibility | 256 | 107.1602 | 0.090251 | 0.0008422 | No
2020-02-07 | 11:33 | NA1218 | Urban | Asset Failure | LV | 2 | 257.5 | 0.00068722 | 2.6688e-06 | No
2020-02-07 | 12:01 | 53805 | Short rural | Unknown | Unknown | 1 | 64 | 0.00021055 | 3.2899e-06 | No
2020-02-07 | 12:22 | J503 | Urban | Asset Failure | Distribution substation | 34 | 173.0882 | 0.0078529 | 4.537e-05 | No
2020-02-07 | 12:24 | NK1332 | Urban | Asset Failure | Distribution substation | 1 | 271 | 0.00036162 | 1.3344e-06 | No
2020-02-07 | 13:27 | 9057 | Urban | Unknown | Unknown | 33 | 67 | 0.0029504 | 4.4035e-05 | No
2020-02-07 | 13:49 | CLC2 | Short rural | Weather |  | 54 | 243 | 0.04317 | 0.00017765 | No
2020-02-07 | 15:05 | M399 | Short rural | Asset Failure | HV | 105 | 151.6667 | 0.052391 | 0.00034544 | No
2020-02-07 | 15:28 | MVC2 | Short rural | Weather |  | 134 | 192.6119 | 0.084911 | 0.00044084 | No
2020-02-07 | 15:30 | NG1210 | Short rural | Vegetation | Grow-in - NSP responsibility | 6 | 167 | 0.0032964 | 1.9739e-05 | No
2020-02-07 | 17:18 | 9027 | Urban | Asset Failure | Distribution substation | 1 | 279 | 0.0003723 | 1.3344e-06 | No
2020-02-07 | 17:18 | 9027 | Urban | Asset Failure | Distribution substation | 1 | 281 | 0.00037497 | 1.3344e-06 | No
2020-02-07 | 18:42 | SN1271 | Short rural | Asset Failure | Distribution substation | 1 | 4013 | 0.013202 | 3.2899e-06 | No
2020-02-07 | 19:00 | 10290 | Short rural | Unknown | Unknown | 1 | 132 | 0.00043426 | 3.2899e-06 | No
2020-02-07 | 19:02 | CS1247 | Urban | Asset Failure | Distribution substation | 33 | 295.2424 | 0.013001 | 4.4035e-05 | No
2020-02-07 | 19:13 | A096 | Short rural | Third Party | Vehicle impact | 5 | 412 | 0.0067771 | 1.6449e-05 | No
2020-02-07 | 21:11 | RW1281 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 1147 | 0.0037735 | 3.2899e-06 | No
2020-02-08 | 0:58 | RBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 23 | 102.8261 | 0.0077805 | 7.5667e-05 | No
2020-02-08 | 2:23 | NG1210 | Short rural | Asset Failure | Distribution substation | 4 | 380 | 0.0050006 | 1.3159e-05 | No
2020-02-08 | 5:56 | R260 | Short rural | Vegetation | Grow-in - NSP responsibility | 100 | 1226.8 | 0.4036 | 0.00032899 | No
2020-02-08 | 7:32 | A344 | Urban | Unknown | Unknown | 43 | 97 | 0.0055658 | 5.7379e-05 | No
2020-02-08 | 8:11 | BYB2 | Short rural | Asset Failure | Distribution substation | 1 | 194 | 0.00063823 | 3.2899e-06 | No
2020-02-08 | 8:43 | SG1250 | Urban | Other | FOREIGN MATTER ON SYSTEM | 97 | 96.1237 | 0.012442 | 0.00012944 | No
2020-02-08 | 9:50 | CR1210 | Urban | Weather |  | 55 | 122.2182 | 0.0089698 | 7.3392e-05 | No
2020-02-08 | 10:15 | 35693 | Short rural | Asset Failure | Distribution substation | 43 | 3670.1628 | 0.5192 | 0.00014146 | No
2020-02-08 | 11:03 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 306 | 130.5163 | 0.13139 | 0.0010067 | No
2020-02-08 | 11:08 | 27341 | Urban | Unknown | Unknown | 22 | 149 | 0.0043742 | 2.9357e-05 | No
2020-02-08 | 11:10 | SHK2 | Urban | Asset Failure | HV | 1351 | 105.379 | 0.18997 | 0.0018028 | No
2020-02-08 | 12:20 | LP1362 | Urban | Asset Failure | HV | 338 | 65.932 | 0.029737 | 0.00045103 | No
2020-02-08 | 12:35 | YYA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 164 | 122.5122 | 0.0661 | 0.00053954 | No
2020-02-08 | 12:52 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 150 | 0.00049348 | 3.2899e-06 | No
2020-02-08 | 13:29 | YYB2 | Short rural | Asset Failure | Distribution substation | 40 | 140.2 | 0.01845 | 0.00013159 | No
2020-02-08 | 13:44 | R293 | Short rural | Asset Failure | HV | 117 | 122.5385 | 0.047167 | 0.00038491 | No
2020-02-08 | 14:40 | T828 | Short rural | Unknown | Unknown | 1 | 86 | 0.00028293 | 3.2899e-06 | No
2020-02-08 | 14:51 | 16651 | Urban | Unknown | Unknown | 23 | 46 | 0.0014118 | 3.0691e-05 | No
2020-02-08 | 15:16 | 35988 | Short rural | Asset Failure | Distribution substation | 1 | 232 | 0.00076325 | 3.2899e-06 | No
2020-02-08 | 15:53 | A344 | Urban | Asset Failure | Distribution substation | 64 | 146.8125 | 0.012538 | 8.5402e-05 | No
2020-02-08 | 15:58 | NN1233 | Short rural | Asset Failure | Distribution substation | 1 | 90 | 0.00029609 | 3.2899e-06 | No
2020-02-08 | 16:00 | BX1342 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 199 | 0.00026555 | 1.3344e-06 | No
2020-02-08 | 16:04 | CX1210 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 25 | 92.28 | 0.0075897 | 8.2247e-05 | No
2020-02-08 | 16:25 | 27454 | Short rural | Vegetation | Grow-in - NSP responsibility | 427 | 113.7447 | 0.15979 | 0.0014048 | No
2020-02-08 | 16:27 | 8799 | Short rural | Vegetation | Grow-in - NSP responsibility | 630 | 28.4651 | 0.058997 | 0.0020726 | No
2020-02-08 | 16:27 | SG1247 | Urban | Vegetation | Grow-in - NSP responsibility | 120 | 166.5667 | 0.026672 | 0.00016013 | No
2020-02-08 | 16:36 | 35988 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 4 | 64 | 0.0008422 | 1.3159e-05 | No
2020-02-08 | 16:37 | 6430 | Urban | Vegetation | Grow-in - NSP responsibility | 759 | 43.8155 | 0.044377 | 0.0010128 | No
2020-02-08 | 16:48 | A344 | Urban | Asset Failure | LV | 584 | 30.2825 | 0.023599 | 0.00077929 | No
2020-02-08 | 17:33 | BK1251 | Short rural | Vegetation | Grow-in - NSP responsibility | 965 | 41.8166 | 0.13276 | 0.0031747 | No
2020-02-08 | 17:57 | KC1284 | Short rural | Weather |  | 16 | 293 | 0.015423 | 5.2638e-05 | No
2020-02-08 | 18:22 | BDC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 63 | 185.619 | 0.038472 | 0.00020726 | No
2020-02-08 | 18:24 | MR2232 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 66 | 0.00086852 | 1.3159e-05 | No
2020-02-08 | 18:36 | BX1212 | Urban | Vegetation | Grow-in - NSP responsibility | 1078 | 32.7996 | 0.047182 | 0.0014385 | No
2020-02-08 | 18:36 | BX1332 | Urban | Asset Failure | HV | 908 | 38.4901 | 0.046636 | 0.0012116 | No
2020-02-08 | 19:30 | RBA2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 3 | 336 | 0.0033162 | 9.8696e-06 | No
2020-02-08 | 20:27 | BK1288 | Short rural | Vegetation | Grow-in - NSP responsibility | 1462 | 271.8509 | 1.3075 | 0.0048098 | No
2020-02-08 | 20:34 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 37 | 237.5946 | 0.028921 | 0.00012172 | No
2020-02-08 | 20:36 | 10242 | Short rural | Vegetation | Grow-in - NSP responsibility | 1360 | 171.7162 | 0.76829 | 0.0044742 | No
2020-02-08 | 20:43 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 51 | 144.8824 | 0.024309 | 0.00016778 | No
2020-02-08 | 20:56 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 6 | 253 | 0.004994 | 1.9739e-05 | No
2020-02-08 | 23:02 | LP1422 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 29 | 98 | 0.0037924 | 3.8698e-05 | No
2020-02-08 | 23:15 | PK1221 | Urban | Asset Failure | HV | 202 | 81.0099 | 0.021836 | 0.00026955 | No
2020-02-08 | 23:38 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 366.3656 | 193 | 0.23262 | 0.0012053 | No
2020-02-08 | 23:38 | KVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 399.3986 | 193 | 0.2536 | 0.001314 | No
2020-02-08 | 23:38 | KVC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 136.1359 | 193 | 0.086439 | 0.00044787 | No
2020-02-08 | 23:38 | KVD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 100.0999 | 193 | 0.063558 | 0.00032931 | No
2020-02-09 | 1:00 | 10244 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 977 | 87.1453 | 0.2801 | 0.0032142 | Yes
2020-02-09 | 1:09 | A348 | Urban | Animal | Animal Impact | 34 | 269 | 0.012204 | 4.537e-05 | Yes
2020-02-09 | 1:37 | HBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 607 | 34.6211 | 0.069136 | 0.0019969 | Yes
2020-02-09 | 4:34 | BK1236 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 47 | 3460 | 0.535 | 0.00015462 | Yes
2020-02-09 | 4:54 | SXC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 506 | 14 | 0.023305 | 0.0016647 | Yes
2020-02-09 | 5:15 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 13 | 79 | 0.0033787 | 4.2768e-05 | Yes
2020-02-09 | 5:34 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 548 | 154.4179 | 0.27839 | 0.0018028 | Yes
2020-02-09 | 5:50 | BDC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 299.4171 | 219.1344 | 0.21586 | 0.00098504 | Yes
2020-02-09 | 5:50 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 279.5578 | 219.1344 | 0.20154 | 0.00091971 | Yes
2020-02-09 | 5:50 | KVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 304.7638 | 219.1344 | 0.21971 | 0.0010026 | Yes
2020-02-09 | 5:50 | KVC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 103.8794 | 219.1344 | 0.074889 | 0.00034175 | Yes
2020-02-09 | 5:50 | KVD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 76.3819 | 219.1344 | 0.055065 | 0.00025129 | Yes
2020-02-09 | 5:59 | KVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 273 | 0.0053888 | 1.9739e-05 | Yes
2020-02-09 | 6:09 | 10251 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 176 | 449.9091 | 0.10566 | 0.00023485 | Yes
2020-02-09 | 6:38 | CD1271 | Short rural | Weather |  | 16 | 387 | 0.020371 | 5.2638e-05 | Yes
2020-02-09 | 6:55 | C832 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2048 | 85.8286 | 0.23456 | 0.0027328 | Yes
2020-02-09 | 6:59 | X870 | Urban | Unknown | Unknown | 17 | 93 | 0.0021097 | 2.2685e-05 | Yes
2020-02-09 | 7:35 | X879 | Short rural | Weather |  | 32 | 153 | 0.016107 | 0.00010528 | Yes
2020-02-09 | 8:11 | KC1284 | Short rural | Weather |  | 842 | 683.9644 | 1.8946 | 0.0027701 | Yes
2020-02-09 | 8:19 | GL1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 489 | 918.9591 | 1.4784 | 0.0016087 | Yes
2020-02-09 | 8:34 | HBB2 | Short rural | Unknown | Unknown | 24 | 96 | 0.0075798 | 7.8957e-05 | Yes
2020-02-09 | 8:37 | S743 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 600 | 0.0019739 | 3.2899e-06 | Yes
2020-02-09 | 8:37 | BK1236 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 33 | 31 | 0.0033655 | 0.00010857 | Yes
2020-02-09 | 8:42 | FT1206 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 139.2692 | 0.023825 | 0.00017107 | Yes
2020-02-09 | 8:42 | S737 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 357 | 670.1793 | 0.78711 | 0.0011745 | Yes
2020-02-09 | 8:43 | W164 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 70 | 246 | 0.056651 | 0.00023029 | Yes
2020-02-09 | 8:43 | R260 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 125 | 2851.256 | 1.1725 | 0.00041123 | Yes
2020-02-09 | 8:45 | 55870 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 1643 | 0.015347 | 9.3408e-06 | Yes
2020-02-09 | 8:58 | S738 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 235 | 1413.8043 | 1.093 | 0.00077312 | Yes
2020-02-09 | 9:01 | 35702 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 64 | 4487 | 0.3832 | 8.5402e-05 | Yes
2020-02-09 | 9:04 | 9046 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1180.0974 | 223.2804 | 0.3516 | 0.0015747 | Yes
2020-02-09 | 9:04 | 9055 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1594.9026 | 223.2804 | 0.47519 | 0.0021282 | Yes
2020-02-09 | 9:07 | CX1284 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 66 | 1517 | 0.32939 | 0.00021713 | Yes
2020-02-09 | 9:19 | X883 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 1888 | 0.050387 | 2.6688e-05 | Yes
2020-02-09 | 9:21 | 35418 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 172 | 4087.4709 | 2.3129 | 0.00056586 | Yes
2020-02-09 | 9:25 | 10248 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 45 | 3294 | 0.1978 | 6.0048e-05 | Yes
2020-02-09 | 9:26 | SY1132 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 73.4583 | 3357.3858 | 0.3291 | 9.8023e-05 | Yes
2020-02-09 | 9:26 | SY1352 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 53.5417 | 3357.3858 | 0.23987 | 7.1446e-05 | Yes
2020-02-09 | 9:28 | GV1282 | Short rural | Unknown | Unknown | 30 | 3020 | 0.29806 | 9.8696e-05 | Yes
2020-02-09 | 9:30 | 27454 | Short rural | Weather |  | 427 | 2038.3232 | 2.8634 | 0.0014048 | Yes
2020-02-09 | 9:31 | 10250 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1051 | 195.0942 | 0.67457 | 0.0034576 | Yes
2020-02-09 | 9:32 | 35702 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 803.2531 | 334.0571 | 0.35806 | 0.0010719 | Yes
2020-02-09 | 9:32 | 35695 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 528.7469 | 334.0571 | 0.58109 | 0.0017395 | Yes
2020-02-09 | 9:32 | LL1232 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 91 | 1856.5275 | 0.22544 | 0.00012143 | Yes
2020-02-09 | 9:38 | 19856 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 205 | 216.7073 | 0.059281 | 0.00027355 | Yes
2020-02-09 | 9:40 | F601 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1991.2322 | 556.5565 | 1.4788 | 0.0026571 | Yes
2020-02-09 | 9:40 | 5494 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 441.7678 | 556.5565 | 0.32809 | 0.00058949 | Yes
2020-02-09 | 9:42 | BK1251 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 964 | 702.388 | 2.2276 | 0.0031714 | Yes
2020-02-09 | 9:45 | BX1352 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19 | 3177 | 0.080548 | 2.5354e-05 | Yes
2020-02-09 | 9:52 | A350 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 13 | 3436 | 0.059605 | 1.7347e-05 | Yes
2020-02-09 | 9:57 | 9046 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 244 | 69.8893 | 0.022756 | 0.00032559 | Yes
2020-02-09 | 10:02 | 2813 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 786 | 408.841 | 0.42881 | 0.0010488 | Yes
2020-02-09 | 10:04 | CJ1241 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 789 | 342.9556 | 0.36108 | 0.0010528 | Yes
2020-02-09 | 10:07 | L947 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 867 | 1075.4025 | 3.0674 | 0.0028523 | Yes
2020-02-09 | 10:09 | 1959 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 35 | 263 | 0.012283 | 4.6704e-05 | Yes
2020-02-09 | 10:10 | RBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 16 | 300 | 0.015791 | 5.2638e-05 | Yes
2020-02-09 | 10:11 | 2813 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 23.1176 | 3669.8125 | 0.11321 | 3.0848e-05 | Yes
2020-02-09 | 10:11 | 2816 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 8.8824 | 3669.8125 | 0.043497 | 1.1853e-05 | Yes
2020-02-09 | 10:16 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 2999 | 0.26639 | 8.8826e-05 | Yes
2020-02-09 | 10:19 | W188 | Short rural | Other | Probable Rain incl. Mist and Fog | 278 | 99.1547 | 0.090685 | 0.00091458 | Yes
2020-02-09 | 10:21 | 35306 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 69 | 2253.3913 | 0.20748 | 9.2074e-05 | Yes
2020-02-09 | 10:22 | MG1267 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 879 | 159.5518 | 0.46139 | 0.0028918 | Yes
2020-02-09 | 10:25 | T883 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1339 | 96.242 | 0.17196 | 0.0017868 | Yes
2020-02-09 | 10:26 | JBB2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 3 | 221 | 0.0021812 | 9.8696e-06 | Yes
2020-02-09 | 10:26 | 35990 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 325 | 656.2462 | 0.70166 | 0.0010692 | Yes
2020-02-09 | 10:29 | HBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 34 | 14 | 0.001566 | 0.00011186 | Yes
2020-02-09 | 10:30 | 85G | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 151 | 0.00049677 | 3.2899e-06 | Yes
2020-02-09 | 10:31 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 29 | 3102.9655 | 0.29604 | 9.5406e-05 | Yes
2020-02-09 | 10:35 | 35693 | Short rural | Weather |  | 324 | 209.5 | 0.22331 | 0.0010659 | Yes
2020-02-09 | 10:39 | MVF2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 298.0435 | 0.022552 | 7.5667e-05 | Yes
2020-02-09 | 10:39 | BK1299 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 772 | 1596.1684 | 4.0539 | 0.0025398 | Yes
2020-02-09 | 10:44 | L517 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 815 | 194 | 0.21098 | 0.0010875 | Yes
2020-02-09 | 10:54 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 61 | 5596.2459 | 1.1231 | 0.00020068 | Yes
2020-02-09 | 11:03 | S743 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 279 | 336.5699 | 0.30893 | 0.00091787 | Yes
2020-02-09 | 11:04 | S741 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 703 | 280.8947 | 0.64965 | 0.0023128 | Yes
2020-02-09 | 11:06 | NL1132 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 26 | 1369 | 0.047497 | 3.4694e-05 | Yes
2020-02-09 | 11:07 | S737 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 30 | 3166 | 0.31247 | 9.8696e-05 | Yes
2020-02-09 | 11:08 | S738 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 409 | 473.1174 | 0.6366 | 0.0013456 | Yes
2020-02-09 | 11:11 | J515 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 43 | 1109 | 0.063633 | 5.7379e-05 | Yes
2020-02-09 | 11:11 | NK1352 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 1700 | 0.034027 | 2.0016e-05 | Yes
2020-02-09 | 11:14 | J507 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 895 | 154 | 0.45344 | 0.0029444 | Yes
2020-02-09 | 11:16 | 49010 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 939 | 209.5399 | 0.64731 | 0.0030892 | Yes
2020-02-09 | 11:20 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 152 | 128 | 0.064008 | 0.00050006 | Yes
2020-02-09 | 11:23 | NK1342 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 24 | 3058 | 0.097934 | 3.2026e-05 | Yes
2020-02-09 | 11:23 | S737 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 92 | 3039 | 0.91981 | 0.00030267 | Yes
2020-02-09 | 11:24 | 8683 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 62 | 3690 | 0.30528 | 8.2733e-05 | Yes
2020-02-09 | 11:43 | 8799 | Short rural | Weather |  | 6 | 3211 | 0.063383 | 1.9739e-05 | Yes
2020-02-09 | 11:58 | A046 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 831 | 244.0361 | 0.66716 | 0.0027339 | Yes
2020-02-09 | 11:58 | D852 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1452 | 730.9477 | 1.4162 | 0.0019375 | Yes
2020-02-09 | 11:59 | HBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 17 | 0.00027964 | 1.6449e-05 | Yes
2020-02-09 | 11:59 | DP1221 | Short rural | Asset Failure | HV | 1032 | 86.2694 | 0.2929 | 0.0033951 | Yes
2020-02-09 | 11:59 | NL1132 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 599.5565 | 1508.6979 | 1.207 | 0.00080005 | Yes
2020-02-09 | 11:59 | NL1172 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 109.8347 | 1508.6979 | 0.22112 | 0.00014656 | Yes
2020-02-09 | 11:59 | NL1182 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 360.7415 | 1508.6979 | 0.72625 | 0.00048137 | Yes
2020-02-09 | 11:59 | NL1322 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 328.4965 | 1508.6979 | 0.66133 | 0.00043835 | Yes
2020-02-09 | 11:59 | NL1332 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 180.3708 | 1508.6979 | 0.36312 | 0.00024069 | Yes
2020-02-09 | 12:03 | SHG2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 53 | 113 | 0.019703 | 0.00017436 | Yes
2020-02-09 | 12:07 | S740 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 417.0616 | 250.3111 | 0.1393 | 0.00055653 | Yes
2020-02-09 | 12:07 | C832 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 482.9384 | 250.3111 | 0.16131 | 0.00064443 | Yes
2020-02-09 | 12:14 | LP1322 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 332 | 0.0039872 | 1.201e-05 | Yes
2020-02-09 | 12:15 | RW1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 3002 | 0.0098762 | 3.2899e-06 | Yes
2020-02-09 | 12:16 | SG1250 | Urban | Unknown | Unknown | 24 | 2388 | 0.076477 | 3.2026e-05 | Yes
2020-02-09 | 12:16 | 9052 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 72 | 49 | 0.0047078 | 9.6077e-05 | Yes
2020-02-09 | 12:16 | GL1233 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 238 | 1695.2899 | 1.3274 | 0.00078299 | Yes
2020-02-09 | 12:20 | SHD2 | Short rural | Asset Failure | HV | 88 | 208.5455 | 0.060376 | 0.00028951 | Yes
2020-02-09 | 12:21 | T868 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1617 | 289.6926 | 1.5411 | 0.0053197 | Yes
2020-02-09 | 12:21 | T868 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 133 | 258.0677 | 0.11292 | 0.00043755 | Yes
2020-02-09 | 12:24 | RW1292 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 24 | 313 | 0.024713 | 7.8957e-05 | Yes
2020-02-09 | 12:36 | BX1342 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 483 | 951.3126 | 0.61314 | 0.00064451 | Yes
2020-02-09 | 12:40 | DS1241 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1320 | 212.9152 | 0.37503 | 0.0017614 | Yes
2020-02-09 | 12:40 | PH1219 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 58 | 412.9828 | 0.031963 | 7.7395e-05 | Yes
2020-02-09 | 12:45 | 2807 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 1573 | 0.048277 | 3.0691e-05 | Yes
2020-02-09 | 12:47 | 5496 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 88 | 1968.8182 | 0.23119 | 0.00011743 | Yes
2020-02-09 | 12:48 | 54701 | Short rural | Weather |  | 4 | 1988 | 0.026161 | 1.3159e-05 | Yes
2020-02-09 | 12:50 | BX1352 | Urban | Weather |  | 1205 | 619.156 | 0.99557 | 0.001608 | Yes
2020-02-09 | 12:52 | 8648 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 115 | 0.0010742 | 9.3408e-06 | Yes
2020-02-09 | 12:53 | 9025 | Urban | Weather |  | 26 | 726 | 0.025188 | 3.4694e-05 | Yes
2020-02-09 | 13:05 | HS1142 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 14 | 4257.9286 | 0.19611 | 4.6058e-05 | Yes
2020-02-09 | 13:07 | 10241 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 683 | 1482.6237 | 3.3314 | 0.002247 | Yes
2020-02-09 | 13:08 | 9049 | Urban | Other | Probable Rain incl. Mist and Fog | 50 | 2047 | 0.13658 | 6.672e-05 | Yes
2020-02-09 | 13:10 | RW1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 2796.2857 | 0.064396 | 2.3029e-05 | Yes
2020-02-09 | 13:12 | 8764 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 21 | 1519 | 0.042566 | 2.8022e-05 | Yes
2020-02-09 | 13:15 | 8676 | Urban | Asset Failure | Distribution substation | 58 | 3111 | 0.24078 | 7.7395e-05 | Yes
2020-02-09 | 13:17 | S743 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 1114 | 0.043979 | 3.9478e-05 | Yes
2020-02-09 | 13:19 | NM1236 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 1763 | 0.0023525 | 1.3344e-06 | Yes
2020-02-09 | 13:35 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 4125 | 0.027141 | 6.5797e-06 | Yes
2020-02-09 | 13:36 | RD1292 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 4532 | 0.036285 | 8.0064e-06 | Yes
2020-02-09 | 13:36 | WBC2 | Short rural | Weather |  | 961 | 87.975 | 0.27814 | 0.0031616 | Yes
2020-02-09 | 13:37 | 2815 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1117 | 741.8845 | 1.1058 | 0.0014905 | Yes
2020-02-09 | 13:41 | CD1260 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1191.1112 | 225.2976 | 0.35809 | 0.0015894 | Yes
2020-02-09 | 13:41 | CD1241 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 461.8888 | 225.2976 | 0.13886 | 0.00061634 | Yes
2020-02-09 | 13:42 | 68197 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 24 | 197.3333 | 0.0063197 | 3.2026e-05 | Yes
2020-02-09 | 13:43 | C897 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 25 | 3181.08 | 0.10612 | 3.336e-05 | Yes
2020-02-09 | 13:44 | CV1239 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 43 | 3890 | 0.2232 | 5.7379e-05 | Yes
2020-02-09 | 13:46 | C833 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 196 | 274 | 0.071663 | 0.00026154 | Yes
2020-02-09 | 13:52 | BK1288 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 182 | 1208 | 0.7233 | 0.00059876 | Yes
2020-02-09 | 13:53 | AZ1205 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 53 | 58 | 0.0041019 | 7.0723e-05 | Yes
2020-02-09 | 13:58 | JS1122 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 955.0376 | 224.7771 | 0.70624 | 0.0031419 | Yes
2020-02-09 | 13:58 | JS1252 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 538.9624 | 224.7771 | 0.39856 | 0.0017731 | Yes
2020-02-09 | 13:58 | JS1252 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 557 | 249.0808 | 0.45643 | 0.0018325 | Yes
2020-02-09 | 14:01 | KMA2 | Short rural | Weather |  | 43 | 43.5116 | 0.0061553 | 0.00014146 | Yes
2020-02-09 | 14:02 | A095 | Short rural | Weather |  | 343 | 754.7055 | 0.85163 | 0.0011284 | Yes
2020-02-09 | 14:03 | CJ1241 | Urban | Weather |  | 69 | 1626 | 0.14971 | 9.2074e-05 | Yes
2020-02-09 | 14:09 | LP1162 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 59 | 2706 | 0.21304 | 7.873e-05 | Yes
2020-02-09 | 14:11 | OA1244 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 44 | 1530 | 0.22147 | 0.00014475 | Yes
2020-02-09 | 14:15 | BX1352 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 2078 | 0.088732 | 4.2701e-05 | Yes
2020-02-09 | 14:18 | NL1322 | Urban | Unknown | Unknown | 1 | 4019 | 0.0053629 | 1.3344e-06 | Yes
2020-02-09 | 14:23 | KC1221 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 1371.6667 | 0.027076 | 1.9739e-05 | Yes
2020-02-09 | 14:23 | PK1221 | Urban | Other | Probable Rain incl. Mist and Fog | 777 | 86.2381 | 0.089414 | 0.0010368 | Yes
2020-02-09 | 14:24 | OP1172 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 988 | 45.4028 | 0.059858 | 0.0013184 | Yes
2020-02-09 | 14:25 | 10244 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 74 | 52 | 0.012659 | 0.00024345 | Yes
2020-02-09 | 14:26 | T831 | Short rural | Weather |  | 7 | 106 | 0.0024411 | 2.3029e-05 | Yes
2020-02-09 | 14:34 | 55876 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 1847 | 0.019717 | 1.0675e-05 | Yes
2020-02-09 | 14:35 | 68181 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 241 | 0.0086829 | 3.6029e-05 | Yes
2020-02-09 | 14:41 | 49008 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 53 | 2673 | 0.46607 | 0.00017436 | Yes
2020-02-09 | 14:41 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 962 | 468.9958 | 1.4843 | 0.0031648 | Yes
2020-02-09 | 14:44 | 2807 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2951 | 229.0152 | 0.90182 | 0.0039378 | Yes
2020-02-09 | 14:54 | 5495 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 143.7778 | 0.0051801 | 3.6029e-05 | Yes
2020-02-09 | 15:00 | 9046 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 36 | 1539 | 0.073931 | 4.8038e-05 | Yes
2020-02-09 | 15:01 | 55888 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 23 | 1199 | 0.036799 | 3.0691e-05 | Yes
2020-02-09 | 15:08 | APD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 72 | 45 | 0.010659 | 0.00023687 | Yes
2020-02-09 | 15:18 | CLA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 63 | 242.2063 | 0.0502 | 0.00020726 | Yes
2020-02-09 | 15:34 | A046 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 45 | 1757.8 | 0.26023 | 0.00014804 | Yes
2020-02-09 | 15:35 | BX1352 | Urban | Weather |  | 555 | 1003 | 0.74281 | 0.00074059 | Yes
2020-02-09 | 15:43 | 9022 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 81 | 3263.3333 | 0.35272 | 0.00010809 | Yes
2020-02-09 | 15:44 | T872 | Urban | Asset Failure | Distribution substation | 1 | 2618 | 0.0034935 | 1.3344e-06 | Yes
2020-02-09 | 15:47 | RD1228 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1790 | 366.7715 | 0.87606 | 0.0023886 | Yes
2020-02-09 | 15:48 | HBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 74 | 95 | 0.023128 | 0.00024345 | Yes
2020-02-09 | 15:55 | HKD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1051 | 56 | 0.19363 | 0.0034576 | Yes
2020-02-09 | 15:56 | 55874 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 9 | 1844 | 0.022146 | 1.201e-05 | Yes
2020-02-09 | 15:59 | S741 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 300 | 195 | 0.19246 | 0.00098696 | Yes
2020-02-09 | 16:01 | X877 | Short rural | Other | Probable Rain incl. Mist and Fog | 389 | 2151.4422 | 2.7533 | 0.0012798 | Yes
2020-02-09 | 16:02 | 55885 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1628 | 533.0074 | 1.1579 | 0.0021724 | Yes
2020-02-09 | 16:02 | 55874 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2982 | 36.0604 | 0.14349 | 0.0039792 | Yes
2020-02-09 | 16:03 | 8685 | Urban | Asset Failure | Distribution substation | 27 | 2593 | 0.093423 | 3.6029e-05 | Yes
2020-02-09 | 16:04 | DFC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 46 | 0.00030267 | 6.5797e-06 | Yes
2020-02-09 | 16:04 | WBC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 961 | 46 | 0.14543 | 0.0031616 | Yes
2020-02-09 | 16:05 | D814 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 36 | 5370.5 | 0.63606 | 0.00011844 | Yes
2020-02-09 | 16:07 | S741 | Short rural | Other | Probable Rain incl. Mist and Fog | 14 | 186 | 0.0085668 | 4.6058e-05 | Yes
2020-02-09 | 16:08 | W111 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 589 | 327.7674 | 0.63512 | 0.0019377 | Yes
2020-02-09 | 16:09 | W188 | Short rural | Weather |  | 172 | 337.8023 | 0.19115 | 0.00056586 | Yes
2020-02-09 | 16:12 | J491 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1958 | 60 | 0.15677 | 0.0026128 | Yes
2020-02-09 | 16:19 | W111 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 57 | 1591 | 0.29835 | 0.00018752 | Yes
2020-02-09 | 16:26 | CA1213 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 1941.4 | 0.025906 | 1.3344e-05 | Yes
2020-02-09 | 16:27 | CX1232 | Short rural | Weather |  | 42 | 4562.0952 | 0.63036 | 0.00013817 | Yes
2020-02-09 | 16:30 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 778.6776 | 1361.7712 | 3.4885 | 0.0025617 | Yes
2020-02-09 | 16:30 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 471.3224 | 1361.7712 | 2.1115 | 0.0015506 | Yes
2020-02-09 | 16:31 | J499 | Urban | Weather |  | 26 | 1427 | 0.049509 | 3.4694e-05 | Yes
2020-02-09 | 16:39 | 35418 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 182 | 569.9341 | 0.34125 | 0.00059876 | Yes
2020-02-09 | 16:40 | 53809 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 978 | 154.6022 | 0.20176 | 0.001305 | Yes
2020-02-09 | 16:43 | 6423 | Urban | Asset Failure | Distribution substation | 39 | 2287.2308 | 0.11903 | 5.2042e-05 | Yes
2020-02-09 | 16:44 | D842 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 244 | 730 | 0.23768 | 0.00032559 | Yes
2020-02-09 | 16:44 | A324 | Urban | Weather |  | 96 | 1532 | 0.19625 | 0.0001281 | Yes
2020-02-09 | 16:47 | S740 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 5.2552 | 346.3636 | 0.0024289 | 7.0125e-06 | Yes
2020-02-09 | 16:47 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5.7448 | 346.3636 | 0.0065462 | 1.89e-05 | Yes
2020-02-09 | 16:49 | 7979 | Urban | Other | Probable Rain incl. Mist and Fog | 6 | 1569 | 0.012562 | 8.0064e-06 | Yes
2020-02-09 | 16:49 | MG1267 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 40 | 1040 | 0.13686 | 0.00013159 | Yes
2020-02-09 | 16:54 | CA1206 | Short rural | Other | Probable Rain incl. Mist and Fog | 19 | 1295.5789 | 0.080983 | 6.2507e-05 | Yes
2020-02-09 | 16:56 | L588 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 484 | 179.8306 | 0.28634 | 0.0015923 | Yes
2020-02-09 | 17:01 | J515 | Urban | Weather |  | 14 | 1082 | 0.020213 | 1.8682e-05 | Yes
2020-02-09 | 17:03 | 49328 | Urban | Weather |  | 7 | 490 | 0.004577 | 9.3408e-06 | Yes
2020-02-09 | 17:04 | BX1222 | Urban | Weather |  | 78 | 1478.3333 | 0.15387 | 0.00010408 | Yes
2020-02-09 | 17:09 | AZ1272 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1426 | 1095.5042 | 5.1394 | 0.0046913 | Yes
2020-02-09 | 17:11 | B210 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 74 | 1390.2703 | 0.13728 | 9.8746e-05 | Yes
2020-02-09 | 17:16 | 8685 | Urban | Weather |  | 1 | 1521 | 0.0020296 | 1.3344e-06 | Yes
2020-02-09 | 17:17 | RW1292 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 34 | 64 | 0.0071587 | 0.00011186 | Yes
2020-02-09 | 17:19 | WM1252 | Urban | Other | Probable Rain incl. Mist and Fog | 17 | 1686 | 0.038247 | 2.2685e-05 | Yes
2020-02-09 | 17:19 | D850 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1240 | 817.6444 | 1.3529 | 0.0016547 | Yes
2020-02-09 | 17:22 | 35989 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 258 | 1048.6512 | 0.89008 | 0.00084878 | Yes
2020-02-09 | 17:30 | BX1222 | Urban | Weather |  | 102 | 1179 | 0.16047 | 0.00013611 | Yes
2020-02-09 | 17:32 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 13 | 4036 | 0.17261 | 4.2768e-05 | Yes
2020-02-09 | 17:36 | RBD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 203 | 1750.2906 | 1.1689 | 0.00066784 | Yes
2020-02-09 | 17:39 | GL1207 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 14 | 65 | 0.0029938 | 4.6058e-05 | Yes
2020-02-09 | 17:40 | 48185 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 2326 | 0.13774 | 5.9218e-05 | Yes
2020-02-09 | 17:41 | 4860 | Urban | Other | Probable Rain incl. Mist and Fog | 1 | 3940 | 0.0052575 | 1.3344e-06 | Yes
2020-02-09 | 17:44 | A045 | Short rural | Unknown | Unknown | 12 | 4245 | 0.16759 | 3.9478e-05 | Yes
2020-02-09 | 17:46 | NN1262 | Urban | Asset Failure | HV | 1443 | 61.9958 | 0.11938 | 0.0019255 | Yes
2020-02-09 | 17:47 | CX1273 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 109 | 0.001793 | 1.6449e-05 | Yes
2020-02-09 | 17:49 | RW1218 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 13 | 2389 | 0.10217 | 4.2768e-05 | Yes
2020-02-09 | 17:50 | 19857 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 38 | 26 | 0.0013184 | 5.0707e-05 | Yes
2020-02-09 | 17:52 | JBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 18.0978 | 155 | 0.0092286 | 5.9539e-05 | Yes
2020-02-09 | 17:52 | JBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 40.9022 | 155 | 0.020857 | 0.00013456 | Yes
2020-02-09 | 17:52 | RD1292 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 190 | 617.6842 | 0.15661 | 0.00025354 | Yes
2020-02-09 | 18:03 | BX1352 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 2508.8125 | 0.10713 | 4.2701e-05 | Yes
2020-02-09 | 18:03 | W188 | Short rural | Asset Failure | HV | 4 | 156.5 | 0.0020595 | 1.3159e-05 | Yes
2020-02-09 | 18:12 | DS1241 | Urban | Other | Probable Rain incl. Mist and Fog | 63 | 1688 | 0.14191 | 8.4067e-05 | Yes
2020-02-09 | 18:12 | 2813 | Urban | Weather |  | 68 | 1206 | 0.10943 | 9.0739e-05 | Yes
2020-02-09 | 18:12 | LP1422 | Urban | Unknown | Unknown | 5 | 1882 | 0.012557 | 6.672e-06 | Yes
2020-02-09 | 18:17 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 230 | 3845.6783 | 2.9099 | 0.00075667 | Yes
2020-02-09 | 18:30 | 48185 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 907 | 345.9283 | 1.0322 | 0.0029839 | Yes
2020-02-09 | 18:30 | RBC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 504 | 1219.4405 | 2.0219 | 0.0016581 | Yes
2020-02-09 | 18:41 | L588 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 875 | 0.034544 | 3.9478e-05 | Yes
2020-02-09 | 18:54 | MVF2 | Short rural | Unknown | Unknown | 1 | 2672 | 0.0087905 | 3.2899e-06 | Yes
2020-02-09 | 19:05 | KVC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 1010 | 0.0066455 | 6.5797e-06 | Yes
2020-02-09 | 19:05 | J483 | Urban | Unknown | Unknown | 31 | 1188 | 0.049143 | 4.1366e-05 | Yes
2020-02-09 | 19:20 | RBE2 | Short rural | Unknown | Unknown | 1 | 978 | 0.0032175 | 3.2899e-06 | Yes
2020-02-09 | 19:27 | RBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 2448 | 0.032214 | 1.3159e-05 | Yes
2020-02-09 | 19:38 | J495 | Short rural | Weather |  | 26 | 1146 | 0.098025 | 8.5536e-05 | Yes
2020-02-09 | 19:40 | NG1299 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 698 | 311.4083 | 0.71509 | 0.0022963 | Yes
2020-02-09 | 19:45 | BK1251 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 107 | 1418.7383 | 0.49942 | 0.00035202 | Yes
2020-02-09 | 19:53 | RD1232 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 125 | 1269.616 | 0.21177 | 0.0001668 | Yes
2020-02-09 | 19:57 | C899 | Urban | Weather |  | 11 | 943.8182 | 0.013854 | 1.4678e-05 | Yes
2020-02-09 | 20:01 | FF1217 | Urban | Weather |  | 560 | 315.7661 | 0.23596 | 0.00074726 | Yes
2020-02-09 | 20:12 | SV1142 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 55 | 2500 | 0.18348 | 7.3392e-05 | Yes
2020-02-09 | 20:12 | KVC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 34 | 1206 | 0.1349 | 0.00011186 | Yes
2020-02-09 | 20:17 | 9050 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 79 | 914 | 0.096352 | 0.00010542 | Yes
2020-02-09 | 20:21 | W185 | Short rural | Other | Probable Lightning/Electrical Storm | 26 | 2498 | 0.21367 | 8.5536e-05 | Yes
2020-02-09 | 20:21 | BX1222 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 75 | 0.0018014 | 2.4019e-05 | Yes
2020-02-09 | 20:23 | SZ1332 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 366 | 851.2978 | 1.025 | 0.0012041 | Yes
2020-02-09 | 20:24 | HBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 85 | 341.0824 | 0.09538 | 0.00027964 | Yes
2020-02-09 | 20:26 | NL1322 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 17 | 0.00013611 | 8.0064e-06 | Yes
2020-02-09 | 20:31 | 35990 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 990 | 0.0065139 | 6.5797e-06 | Yes
2020-02-09 | 20:44 | SHK2 | Urban | Weather |  | 115 | 92.4348 | 0.014185 | 0.00015346 | Yes
2020-02-09 | 20:51 | RBB2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 351 | 915.8148 | 1.0575 | 0.0011547 | Yes
2020-02-09 | 20:53 | W188 | Short rural | Weather |  | 1 | 1690 | 0.0055599 | 3.2899e-06 | Yes
2020-02-09 | 21:23 | RBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 499 | 1268.6012 | 2.0826 | 0.0016416 | Yes
2020-02-09 | 21:50 | BWF2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 2497 | 0.0082148 | 3.2899e-06 | Yes
2020-02-09 | 21:58 | OA1233 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 416 | 956.0673 | 1.3085 | 0.0013686 | Yes
2020-02-09 | 22:27 | NM1221 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 983 | 0.013117 | 1.3344e-05 | Yes
2020-02-09 | 22:35 | MM1112 | Urban | Asset Failure | Distribution substation | 8 | 874 | 0.0093301 | 1.0675e-05 | Yes
2020-02-09 | 22:49 | MG1286 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1341 | 700.1588 | 3.0889 | 0.0044117 | Yes
2020-02-09 | 22:58 | RV1298 | Urban | Asset Failure | Distribution substation | 9 | 511 | 0.0061369 | 1.201e-05 | Yes
2020-02-09 | 22:59 | BWE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 24 | 88 | 0.0069482 | 7.8957e-05 | Yes
2020-02-09 | 22:59 | S740 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 19 | 751 | 0.019041 | 2.5354e-05 | Yes
2020-02-09 | 23:35 | 8682 | Urban | Weather |  | 11 | 93 | 0.0013651 | 1.4678e-05 | Yes
2020-02-09 | 23:58 | S737 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 1104 | 0.007264 | 6.5797e-06 | Yes
2020-02-10 | 0:28 | BWF2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 88 | 0.00057902 | 6.5797e-06 | No
2020-02-10 | 0:32 | NN1285 | Short rural | Weather |  | 2 | 3414 | 0.022463 | 6.5797e-06 | No
2020-02-10 | 1:06 | NN1233 | Short rural | Weather |  | 3 | 3440 | 0.033951 | 9.8696e-06 | No
2020-02-10 | 1:22 | NN1233 | Short rural | Weather |  | 3 | 3424 | 0.033793 | 9.8696e-06 | No
2020-02-10 | 1:28 | MG1282 | Short rural | Third Party | Other | 455 | 471 | 0.70503 | 0.0014969 | No
2020-02-10 | 2:24 | 8679 | Urban | Other | Probable Equipment Failure | 1 | 3740 | 0.0049907 | 1.3344e-06 | No
2020-02-10 | 2:33 | 16653 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 676 | 765.6524 | 0.69066 | 0.00090205 | No
2020-02-10 | 2:41 | BYB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 108 | 183.8148 | 0.06531 | 0.00035531 | No
2020-02-10 | 3:17 | NN1233 | Short rural | Weather |  | 2 | 1963.5 | 0.012919 | 6.5797e-06 | No
2020-02-10 | 3:50 | NN1233 | Short rural | Weather |  | 1 | 1929 | 0.0063461 | 3.2899e-06 | No
2020-02-10 | 3:53 | NN1233 | Short rural | Weather |  | 17 | 1994 | 0.11152 | 5.5928e-05 | No
2020-02-10 | 3:55 | X877 | Short rural | Weather |  | 3 | 2494 | 0.024615 | 9.8696e-06 | No
2020-02-10 | 4:01 | X881 | Short rural | Weather |  | 30 | 803.1333 | 0.079266 | 9.8696e-05 | No
2020-02-10 | 4:11 | JBB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 33 | 393 | 0.042666 | 0.00010857 | No
2020-02-10 | 5:05 | BDG2 | Short rural | Weather |  | 6 | 527 | 0.010403 | 1.9739e-05 | No
2020-02-10 | 5:17 | WRA2 | Urban | Unknown | Unknown | 16 | 243 | 0.0051881 | 2.135e-05 | No
2020-02-10 | 5:19 | P608 | Short rural | Weather |  | 2 | 895 | 0.0058889 | 6.5797e-06 | No
2020-02-10 | 5:44 | AB1265 | Urban | Other | Probable Rain incl. Mist and Fog | 1 | 3153 | 0.0042074 | 1.3344e-06 | No
2020-02-10 | 6:00 | D850 | Urban | Other | Probable Rain incl. Mist and Fog | 1 | 3123 | 0.0041673 | 1.3344e-06 | No
2020-02-10 | 6:35 | 49008 | Short rural | Asset Failure | Distribution substation | 9 | 1979 | 0.058596 | 2.9609e-05 | No
2020-02-10 | 7:10 | RBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 1168 | 0.01537 | 1.3159e-05 | No
2020-02-10 | 7:11 | WRA2 | Urban | Asset Failure | Distribution substation | 1 | 180 | 0.00024019 | 1.3344e-06 | No
2020-02-10 | 7:54 | S788 | Short rural | Weather |  | 2 | 1507 | 0.0099156 | 6.5797e-06 | No
2020-02-10 | 8:06 | CV1236 | Urban | Unknown | Unknown | 63 | 674 | 0.056661 | 8.4067e-05 | No
2020-02-10 | 8:15 | CX1284 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 134 | 0.00044084 | 3.2899e-06 | No
2020-02-10 | 8:18 | S735 | Short rural | Unknown | Unknown | 526 | 301.2643 | 0.52133 | 0.0017305 | No
2020-02-10 | 8:19 | RW1292 | Short rural | Vegetation | Grow-in - NSP responsibility | 11 | 1904.2727 | 0.068913 | 3.6188e-05 | No
2020-02-10 | 8:28 | J495 | Short rural | Unknown | Unknown | 8 | 1702 | 0.044795 | 2.6319e-05 | No
2020-02-10 | 8:28 | W188 | Short rural | Asset Failure | Distribution substation | 1 | 22 | 7.2377e-05 | 3.2899e-06 | No
2020-02-10 | 8:31 | C833 | Urban | Asset Failure | LV | 1030 | 330.2689 | 0.45393 | 0.0013744 | No
2020-02-10 | 8:40 | 2813 | Urban | Asset Failure | Distribution substation | 29 | 374 | 0.014473 | 3.8698e-05 | No
2020-02-10 | 8:58 | ULL2 | Short rural | Asset Failure | LV | 371 | 11.0135 | 0.013442 | 0.0012205 | No
2020-02-10 | 9:14 | YYB2 | Short rural | Weather |  | 81 | 365.5062 | 0.0974 | 0.00026648 | No
2020-02-10 | 9:15 | T868 | Short rural | Vegetation | Grow-in - NSP responsibility | 18 | 138.1111 | 0.0081786 | 5.9218e-05 | No
2020-02-10 | 9:49 | GL1255 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 282 | 0.00092774 | 3.2899e-06 | No
2020-02-10 | 10:01 | BX1222 | Urban | Vegetation | Grow-in - NSP responsibility | 24 | 265.0417 | 0.0084881 | 3.2026e-05 | No
2020-02-10 | 10:13 | HBB2 | Short rural | Unknown | Unknown | 16 | 300.25 | 0.015805 | 5.2638e-05 | No
2020-02-10 | 10:23 | CA1276 | Urban | Unknown | Unknown | 26 | 852 | 0.02956 | 3.4694e-05 | No
2020-02-10 | 10:46 | WP1212 | Urban | Animal | Animal Impact | 28 | 28 | 0.0010462 | 3.7363e-05 | No
2020-02-10 | 10:48 | CD1260 | Urban | Asset Failure | Distribution substation | 6 | 501 | 0.0040112 | 8.0064e-06 | No
2020-02-10 | 10:53 | 19857 | Urban | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 1 | 3362 | 0.0044862 | 1.3344e-06 | No
2020-02-10 | 11:18 | 8799 | Short rural | Vegetation | Grow-in - NSP responsibility | 27 | 219.2963 | 0.019479 | 8.8826e-05 | No
2020-02-10 | 11:32 | CT1236 | Short rural | Asset Failure | Distribution substation | 16 | 1142.9375 | 0.060162 | 5.2638e-05 | No
2020-02-10 | 11:32 | SZ1352 | Urban | Weather |  | 16 | 1482 | 0.031641 | 2.135e-05 | No
2020-02-10 | 12:00 | HBB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 20 | 371.9 | 0.02447 | 6.5797e-05 | No
2020-02-10 | 12:10 | CX1206 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 301 | 0.00099025 | 3.2899e-06 | No
2020-02-10 | 12:33 | NL1132 | Urban | Vegetation | Grow-in - NSP responsibility | 19 | 126.3684 | 0.0032039 | 2.5354e-05 | No
2020-02-10 | 12:46 | MYG2 | Urban | Asset Failure | HV | 1 | 259 | 0.00034561 | 1.3344e-06 | No
2020-02-10 | 12:52 | AB1289 | Urban | Weather |  | 23 | 1103 | 0.033852 | 3.0691e-05 | No
2020-02-10 | 13:09 | A322 | Urban | Vegetation | Grow-in - NSP responsibility | 123 | 71.0488 | 0.011661 | 0.00016413 | No
2020-02-10 | 13:24 | B715 | Urban | Unknown | Unknown | 1 | 3414 | 0.0045556 | 1.3344e-06 | No
2020-02-10 | 13:30 | AZ1253 | Urban | Vegetation | Grow-in - NSP responsibility | 31 | 66.3226 | 0.0027435 | 4.1366e-05 | No
2020-02-10 | 13:38 | SG1250 | Urban | Third Party | Vehicle impact | 24 | 410.5417 | 0.013148 | 3.2026e-05 | No
2020-02-10 | 13:41 | J515 | Urban | Vegetation | Grow-in - NSP responsibility | 44 | 219.9091 | 0.012912 | 5.8714e-05 | No
2020-02-10 | 13:48 | HBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 101 | 105.6238 | 0.035096 | 0.00033228 | No
2020-02-10 | 13:52 | W123 | Short rural | Vegetation | Grow-in - NSP responsibility | 591 | 88.8545 | 0.17276 | 0.0019443 | No
2020-02-10 | 14:18 | CX1210 | Short rural | Weather |  | 4 | 1228 | 0.01616 | 1.3159e-05 | No
2020-02-10 | 14:23 | AB1213 | Urban | Asset Failure | Distribution substation | 1 | 2577 | 0.0034387 | 1.3344e-06 | No
2020-02-10 | 14:29 | MM1112 | Urban | Asset Failure | Distribution substation | 1 | 2945 | 0.0039298 | 1.3344e-06 | No
2020-02-10 | 14:32 | J478 | Short rural | Weather |  | 31 | 1645.8065 | 0.16785 | 0.00010199 | No
2020-02-10 | 14:43 | 1953 | Urban | Weather |  | 15 | 8.3333 | 0.0001668 | 2.0016e-05 | No
2020-02-10 | 14:52 | 8682 | Urban | Other | Probable Willful damage - damage/destruction of EE equipment | 31 | 419.2581 | 0.017343 | 4.1366e-05 | No
2020-02-10 | 15:15 | CD1260 | Urban | Asset Failure | Distribution substation | 1 | 984 | 0.001313 | 1.3344e-06 | No
2020-02-10 | 15:32 | 10241 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 21 | 347 | 0.023973 | 6.9087e-05 | No
2020-02-10 | 16:07 | RD1292 | Urban | Asset Failure | Distribution substation | 93 | 313.5269 | 0.038908 | 0.0001241 | No
2020-02-10 | 16:47 | HR1276 | Urban | Asset Failure | HV | 201 | 78.1244 | 0.020954 | 0.00026821 | No
2020-02-10 | 16:53 | 35990 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 92 | 0.00030267 | 3.2899e-06 | No
2020-02-10 | 17:13 | BDC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 99 | 0.0022799 | 2.3029e-05 | No
2020-02-10 | 18:10 | AZ1253 | Urban | Asset Failure | Distribution substation | 27 | 966.8889 | 0.034836 | 3.6029e-05 | No
2020-02-10 | 18:32 | APC2 | Short rural | Unknown | Unknown | 2 | 104 | 0.00068429 | 6.5797e-06 | No
2020-02-10 | 18:37 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 261 | 60.1801 | 0.051674 | 0.00085865 | No
2020-02-10 | 18:51 | A046 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 77 | 0.00025332 | 3.2899e-06 | No
2020-02-10 | 19:33 | L947 | Short rural | Weather |  | 33 | 790 | 0.085767 | 0.00010857 | No
2020-02-10 | 19:53 | LL1232 | Urban | Vegetation | Grow-in - NSP responsibility | 49 | 958 | 0.062639 | 6.5386e-05 | No
2020-02-10 | 20:15 | 16653 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 21 | 771 | 0.021605 | 2.8022e-05 | No
2020-02-10 | 20:22 | 2815 | Urban | Weather |  | 86 | 24 | 0.0027542 | 0.00011476 | No
2020-02-10 | 20:24 | BDD2 | Urban | Asset Failure | Distribution substation | 11 | 769 | 0.011288 | 1.4678e-05 | No
2020-02-10 | 21:03 | J510 | Urban | Asset Failure | Distribution substation | 33 | 1191.0909 | 0.05245 | 4.4035e-05 | No
2020-02-10 | 23:16 | YYA2 | Short rural | Animal | Animal Impact | 1018 | 42.1798 | 0.14126 | 0.0033491 | No
2020-02-11 | 2:47 | L947 | Short rural | Weather |  | 33 | 361 | 0.039192 | 0.00010857 | No
2020-02-11 | 2:51 | L534 | Short rural | Weather |  | 15 | 541.1333 | 0.026704 | 4.9348e-05 | No
2020-02-11 | 5:59 | L519 | Urban | Weather |  | 11 | 414.3636 | 0.0060822 | 1.4678e-05 | No
2020-02-11 | 6:16 | CV1236 | Urban | Asset Failure | Distribution substation | 9 | 2007 | 0.024103 | 1.201e-05 | No
2020-02-11 | 7:04 | 1960 | Urban | Other | Probable Equipment Failure | 94 | 177.7128 | 0.022291 | 0.00012543 | No
2020-02-11 | 7:37 | 9049 | Urban | Unknown | Unknown | 17 | 467.4706 | 0.010604 | 2.2685e-05 | No
2020-02-11 | 7:38 | C852 | Urban | Asset Failure | Distribution substation | 13 | 681 | 0.011813 | 1.7347e-05 | No
2020-02-11 | 8:08 | LP1162 | Urban | Unknown | Unknown | 47 | 467.6809 | 0.029331 | 6.2717e-05 | No
2020-02-11 | 8:09 | WH1213 | Urban | Unknown | Unknown | 6 | 877 | 0.0070216 | 8.0064e-06 | No
2020-02-11 | 8:12 | NG1299 | Short rural | Asset Failure | Distribution substation | 1 | 1603 | 0.0052737 | 3.2899e-06 | No
2020-02-11 | 8:31 | 49328 | Urban | Asset Failure | Distribution substation | 7 | 525.4286 | 0.0049079 | 9.3408e-06 | No
2020-02-11 | 8:32 | W188 | Short rural | Unknown | Unknown | 7 | 123 | 0.0028326 | 2.3029e-05 | No
2020-02-11 | 8:47 | BWH2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 1697 | 0.0055829 | 3.2899e-06 | No
2020-02-11 | 9:21 | 53805 | Short rural | Asset Failure | Distribution substation | 1 | 448 | 0.0014739 | 3.2899e-06 | No
2020-02-11 | 9:35 | LP1142 | Urban | Animal | Animal Impact | 47 | 30.0638 | 0.0018855 | 6.2717e-05 | No
2020-02-11 | 11:26 | J495 | Short rural | Weather |  | 7 | 465 | 0.010709 | 2.3029e-05 | No
2020-02-11 | 12:06 | RBB2 | Short rural | Unknown | Unknown | 31 | 117 | 0.011932 | 0.00010199 | No
2020-02-11 | 12:40 | FF1276 | Urban | Unknown | Unknown | 34 | 235 | 0.010662 | 4.537e-05 | No
2020-02-11 | 12:50 | MVB2 | Short rural | Unknown | Unknown | 2 | 91 | 0.00059876 | 6.5797e-06 | No
2020-02-11 | 13:11 | J499 | Urban | Asset Failure | Distribution substation | 1 | 1027 | 0.0013704 | 1.3344e-06 | No
2020-02-11 | 13:19 | CT1203 | Urban | Asset Failure | Distribution substation | 1 | 1215 | 0.0016213 | 1.3344e-06 | No
2020-02-11 | 13:28 | HBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 148 | 156.3649 | 0.076134 | 0.0004869 | No
2020-02-11 | 13:47 | BWE2 | Short rural | Unknown | Unknown | 4 | 94.5 | 0.0012436 | 1.3159e-05 | No
2020-02-11 | 13:55 | J495 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 400 | 0.0013159 | 3.2899e-06 | No
2020-02-11 | 14:05 | W185 | Short rural | Vegetation | Grow-in - NSP responsibility | 18 | 58 | 0.0034346 | 5.9218e-05 | No
2020-02-11 | 14:05 | NK1352 | Urban | Vegetation | Grow-in - NSP responsibility | 16 | 100 | 0.002135 | 2.135e-05 | No
2020-02-11 | 15:03 | WP1245 | Urban | Asset Failure | Distribution substation | 4 | 400 | 0.002135 | 5.3376e-06 | No
2020-02-11 | 15:08 | MG1282 | Short rural | Asset Failure | Distribution substation | 1 | 426 | 0.0014015 | 3.2899e-06 | No
2020-02-11 | 15:10 | KVA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 133 | 131.6241 | 0.057592 | 0.00043755 | No
2020-02-11 | 15:20 | BL1210 | Short rural | Asset Failure | HV | 202 | 66.7673 | 0.04437 | 0.00066455 | No
2020-02-11 | 15:21 | 35702 | Urban | Weather |  | 1 | 1309 | 0.0017467 | 1.3344e-06 | No
2020-02-11 | 16:02 | 49008 | Short rural | Asset Failure | Distribution substation | 3 | 98 | 0.00096722 | 9.8696e-06 | No
2020-02-11 | 16:30 | 19857 | Urban | Asset Failure | Distribution substation | 22 | 1104 | 0.03241 | 2.9357e-05 | No
2020-02-11 | 16:41 | CT1236 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 1 | 1230 | 0.0040465 | 3.2899e-06 | No
2020-02-11 | 16:59 | X858 | Urban | Asset Failure | Distribution substation | 12 | 268 | 0.0042914 | 1.6013e-05 | No
2020-02-11 | 17:09 | R260 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 81 | 0.00026648 | 3.2899e-06 | No
2020-02-11 | 17:30 | RW1292 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 76 | 149.1579 | 0.037294 | 0.00025003 | No
2020-02-11 | 17:48 | WD1221 | Short rural | Weather |  | 1 | 43 | 0.00014146 | 3.2899e-06 | No
2020-02-11 | 18:09 | LP1142 | Urban | Asset Failure | LV | 1139 | 98.1457 | 0.14917 | 0.0015199 | No
2020-02-11 | 18:25 | S737 | Short rural | Weather |  | 1 | 1025 | 0.0033721 | 3.2899e-06 | No
2020-02-11 | 18:38 | WL1236 | Urban | Asset Failure | Distribution substation | 1 | 1307 | 0.0017441 | 1.3344e-06 | No
2020-02-11 | 20:03 | 19871 | Urban | Vegetation | Grow-in - NSP responsibility | 121 | 1055 | 0.17034 | 0.00016146 | No
2020-02-11 | 20:05 | W163 | Short rural | Vegetation | Grow-in - NSP responsibility | 253 | 153.7352 | 0.12796 | 0.00083234 | No
2020-02-11 | 20:30 | LP1432 | Urban | Other | Probable Lightning/Electrical Storm | 214 | 47.7243 | 0.013628 | 0.00028556 | No
2020-02-11 | 20:50 | MVF2 | Short rural | Unknown | Unknown | 2 | 794.5 | 0.0052276 | 6.5797e-06 | No
2020-02-11 | 21:26 | MVF2 | Short rural | Weather |  | 2 | 1055 | 0.0069416 | 6.5797e-06 | No
2020-02-11 | 23:13 | 87222 | Long rural | Weather |  | 2 | 157 | 1 | 0.0063694 | No
2020-02-12 | 2:51 | MYM2 | Urban | Vegetation | Grow-in - NSP responsibility | 24 | 144.4583 | 0.0046264 | 3.2026e-05 | No
2020-02-12 | 6:36 | RW1229 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 387.3333 | 0.0038228 | 9.8696e-06 | No
2020-02-12 | 7:00 | L591 | Short rural | Other | Probable Lightning/Electrical Storm | 20 | 206 | 0.013554 | 6.5797e-05 | No
2020-02-12 | 7:57 | 87222 | Long rural | Weather |  | 1 | 124 | 0.3949 | 0.0031847 | No
2020-02-12 | 8:26 | BX1342 | Urban | Weather |  | 1 | 360 | 0.00048038 | 1.3344e-06 | No
2020-02-12 | 8:40 | RD1233 | Urban | Unknown | Unknown | 1 | 353 | 0.00047104 | 1.3344e-06 | No
2020-02-12 | 8:51 | J507 | Short rural | Asset Failure | Distribution substation | 44 | 565.7727 | 0.081898 | 0.00014475 | No
2020-02-12 | 11:09 | CX1232 | Short rural | Weather |  | 3 | 2859.6667 | 0.028224 | 9.8696e-06 | No
2020-02-12 | 11:30 | W196 | Urban | Asset Failure | Distribution substation | 25 | 411 | 0.013711 | 3.336e-05 | No
2020-02-12 | 11:38 | 8766 | Urban | Asset Failure | Distribution substation | 1 | 193 | 0.00025754 | 1.3344e-06 | No
2020-02-12 | 12:11 | RW1292 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 11.6 | 0.00019081 | 1.6449e-05 | No
2020-02-12 | 12:44 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 208 | 31.7837 | 0.021749 | 0.00068429 | No
2020-02-12 | 13:43 | J473 | Urban | Asset Failure | Distribution substation | 1 | 233 | 0.00031091 | 1.3344e-06 | No
2020-02-12 | 14:10 | SZ1322 | Short rural | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 393 | 0.0038787 | 9.8696e-06 | No
2020-02-12 | 14:54 | 87222 | Long rural | Other | Probable Lightning/Electrical Storm | 1 | 97 | 0.30892 | 0.0031847 | No
2020-02-12 | 15:05 | BK1251 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 73 | 0.00024016 | 3.2899e-06 | No
2020-02-12 | 16:51 | RW1218 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 141 | 0.00046387 | 3.2899e-06 | No
2020-02-12 | 17:02 | M399 | Short rural | Asset Failure | Distribution substation | 1 | 331 | 0.0010889 | 3.2899e-06 | No
2020-02-12 | 17:18 | NA1270 | Short rural | Asset Failure | HV | 49 | 1128.6327 | 0.18194 | 0.0001612 | No
2020-02-12 | 17:39 | 49357 | Urban | Unknown | Unknown | 20 | 68.7 | 0.0018335 | 2.6688e-05 | No
2020-02-12 | 18:09 | 7976 | Urban | Asset Failure | Distribution substation | 1 | 68 | 9.0739e-05 | 1.3344e-06 | No
2020-02-12 | 18:30 | R260 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 148 | 0.0004869 | 3.2899e-06 | No
2020-02-12 | 18:46 | 25738 | Urban | Vegetation | Grow-in - NSP responsibility | 1010 | 72.1822 | 0.097283 | 0.0013477 | No
2020-02-12 | 19:22 | 49357 | Urban | Asset Failure | Distribution substation | 20 | 335.35 | 0.0089498 | 2.6688e-05 | No
2020-02-12 | 19:49 | 9025 | Urban | Asset Failure | Distribution substation | 1 | 6416 | 0.0085615 | 1.3344e-06 | No
2020-02-12 | 20:33 | 8799 | Short rural | Asset Failure | Distribution substation | 1 | 192 | 0.00063165 | 3.2899e-06 | No
2020-02-12 | 20:43 | W185 | Short rural | Asset Failure | Distribution substation | 1 | 662 | 0.0021779 | 3.2899e-06 | No
2020-02-12 | 23:13 | T894 | Urban | Asset Failure | Distribution substation | 34 | 459.1765 | 0.020833 | 4.537e-05 | No
2020-02-13 | 4:43 | RBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 61 | 414.2951 | 0.083141 | 0.00020068 | No
2020-02-13 | 4:47 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 33 | 279.9394 | 0.030392 | 0.00010857 | No
2020-02-13 | 5:30 | BYB2 | Short rural | Unknown | Unknown | 2 | 248 | 0.0016318 | 6.5797e-06 | No
2020-02-13 | 5:38 | L582 | Short rural | Vegetation | Grow-in - NSP responsibility | 30 | 328.1667 | 0.032389 | 9.8696e-05 | No
2020-02-13 | 6:36 | 8622 | Urban | Asset Failure | Distribution substation | 1 | 233 | 0.00031091 | 1.3344e-06 | No
2020-02-13 | 6:39 | SN1230 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 360 | 0.014212 | 3.9478e-05 | No
2020-02-13 | 7:04 | 35824 | Short rural | Asset Failure | LV | 207 | 98.1449 | 0.066837 | 0.000681 | No
2020-02-13 | 7:41 | MM1392 | Urban | Asset Failure | Distribution substation | 1 | 262 | 0.00034961 | 1.3344e-06 | No
2020-02-13 | 8:28 | 8683 | Urban | Asset Failure | Distribution substation | 1 | 277 | 0.00036963 | 1.3344e-06 | No
2020-02-13 | 8:59 | J478 | Short rural | Asset Failure | Distribution substation | 37 | 123.973 | 0.015091 | 0.00012172 | No
2020-02-13 | 9:05 | B211 | Urban | Asset Failure | HV | 37 | 87.8378 | 0.0043368 | 4.9373e-05 | No
2020-02-13 | 9:20 | SZ1332 | Short rural | Unknown | Unknown | 37 | 98 | 0.011929 | 0.00012172 | No
2020-02-13 | 9:44 | FF1239 | Urban | Asset Failure | Distribution substation | 1 | 311 | 0.000415 | 1.3344e-06 | No
2020-02-13 | 10:08 | CT1225 | Short rural | Asset Failure | Distribution substation | 19 | 427.6842 | 0.026733 | 6.2507e-05 | No
2020-02-13 | 10:09 | S735 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 387.0833 | 0.015281 | 3.9478e-05 | No
2020-02-13 | 11:48 | OA1233 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 579 | 0.0019048 | 3.2899e-06 | No
2020-02-13 | 12:27 | KC1236 | Short rural | Asset Failure | LV | 11 | 120.4545 | 0.0043591 | 3.6188e-05 | No
2020-02-13 | 12:46 | 35695 | Short rural | Third Party | Other | 47 | 174 | 0.026905 | 0.00015462 | No
2020-02-13 | 14:19 | SHD2 | Short rural | Asset Failure | Distribution substation | 1 | 59 | 0.0001941 | 3.2899e-06 | No
2020-02-13 | 16:02 | CV1284 | Urban | Third Party | Other | 51 | 236.6078 | 0.016102 | 6.8054e-05 | No
2020-02-13 | 16:23 | 8769 | Urban | Unknown | Unknown | 31 | 97 | 0.0040125 | 4.1366e-05 | No
2020-02-13 | 16:39 | X858 | Urban | Asset Failure | Distribution substation | 47 | 120.8936 | 0.0075821 | 6.2717e-05 | No
2020-02-13 | 17:25 | WRE2 | Urban | Asset Failure | Distribution substation | 5 | 426.6 | 0.0028463 | 6.672e-06 | No
2020-02-13 | 18:10 | T890 | Urban | Asset Failure | Distribution substation | 1 | 649 | 0.00086602 | 1.3344e-06 | No
2020-02-13 | 18:17 | 27341 | Urban | Unknown | Unknown | 31 | 98 | 0.0040539 | 4.1366e-05 | No
2020-02-13 | 19:20 | J514 | Urban | Asset Failure | Distribution substation | 1 | 339 | 0.00045236 | 1.3344e-06 | No
2020-02-13 | 19:21 | SG1209 | Urban | Asset Failure | Distribution substation | 10 | 146.6 | 0.0019562 | 1.3344e-05 | No
2020-02-13 | 20:42 | J480 | Urban | Asset Failure | Distribution substation | 1 | 309 | 0.00041233 | 1.3344e-06 | No
2020-02-14 | 6:30 | SN1271 | Short rural | Third Party | Dig-in | 1 | 745 | 0.0024509 | 3.2899e-06 | No
2020-02-14 | 8:42 | X881 | Short rural | Asset Failure | Distribution substation | 10 | 61.2 | 0.0020134 | 3.2899e-05 | No
2020-02-14 | 9:18 | 35990 | Short rural | Asset Failure | Distribution substation | 8 | 304.5 | 0.0080141 | 2.6319e-05 | No
2020-02-14 | 10:14 | WQ1290 | Urban | Unknown | Unknown | 1 | 96 | 0.0001281 | 1.3344e-06 | No
2020-02-14 | 11:04 | J514 | Urban | Asset Failure | Distribution substation | 23 | 36.3913 | 0.0011169 | 3.0691e-05 | No
2020-02-14 | 12:15 | C833 | Urban | Unknown | Unknown | 10 | 147 | 0.0019616 | 1.3344e-05 | No
2020-02-14 | 13:15 | WQ1290 | Urban | Asset Failure | Distribution substation | 1 | 204 | 0.00027222 | 1.3344e-06 | No
2020-02-14 | 13:51 | T841 | Short rural | Asset Failure | Distribution substation | 1 | 195 | 0.00064152 | 3.2899e-06 | No
2020-02-14 | 15:08 | HKF2 | Short rural | Unknown | Unknown | 2 | 417 | 0.0027437 | 6.5797e-06 | No
2020-02-14 | 15:47 | H745 | Short rural | Asset Failure | Distribution substation | 1 | 697 | 0.002293 | 3.2899e-06 | No
2020-02-14 | 16:05 | C851 | Urban | Vegetation | Grow-in - NSP responsibility | 836 | 48.2333 | 0.053807 | 0.0011156 | No
2020-02-14 | 16:43 | CD1260 | Urban | Asset Failure | Distribution substation | 1 | 642 | 0.00085668 | 1.3344e-06 | No
2020-02-14 | 16:58 | L511 | Urban | Unknown | Unknown | 1 | 211 | 0.00028156 | 1.3344e-06 | No
2020-02-14 | 17:45 | ULE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 113 | 280.2301 | 0.10418 | 0.00037175 | No
2020-02-14 | 21:06 | AB1213 | Urban | Asset Failure | Distribution substation | 1 | 769 | 0.0010262 | 1.3344e-06 | No
2020-02-14 | 22:00 | 17069 | Urban | Asset Failure | HV | 23 | 97.9565 | 0.0030064 | 3.0691e-05 | No
2020-02-14 | 22:07 | SWC2 | Urban | Asset Failure | Distribution substation | 14 | 63.0714 | 0.0011783 | 1.8682e-05 | No
2020-02-14 | 22:19 | 46746 | Urban | Asset Failure | HV | 152.7128 | 92.6207 | 0.018874 | 0.00020378 | No
2020-02-14 | 22:19 | 17069 | Urban | Asset Failure | HV | 21.2872 | 92.6207 | 0.002631 | 2.8406e-05 | No
2020-02-14 | 23:58 | 17067 | Urban | Unknown | Unknown | 6 | 99 | 0.00079263 | 8.0064e-06 | No
2020-02-15 | 1:40 | PK1262 | Short rural | Third Party | Vehicle impact | 1054 | 25.4573 | 0.088274 | 0.0034675 | No
2020-02-15 | 4:26 | 35696 | Short rural | Asset Failure | Distribution substation | 34 | 961.1765 | 0.10751 | 0.00011186 | No
2020-02-15 | 5:59 | ULF2 | Short rural | Asset Failure | Distribution substation | 1 | 355 | 0.0011679 | 3.2899e-06 | No
2020-02-15 | 6:53 | APC2 | Short rural | Asset Failure | Distribution substation | 8 | 144.75 | 0.0038097 | 2.6319e-05 | No
2020-02-15 | 7:27 | J469 | Urban | Vegetation | Grow-in - NSP responsibility | 85 | 9.9412 | 0.0011276 | 0.00011342 | No
2020-02-15 | 8:33 | 49006 | Short rural | Asset Failure | Distribution substation | 1 | 396 | 0.0013028 | 3.2899e-06 | No
2020-02-15 | 8:52 | SZ1132 | Urban | Unknown | Unknown | 9 | 217 | 0.0026061 | 1.201e-05 | No
2020-02-15 | 11:11 | RW1292 | Short rural | Animal | Animal Impact | 4 | 95 | 0.0012501 | 1.3159e-05 | No
2020-02-15 | 11:21 | WD1225 | Short rural | Weather |  | 1 | 267 | 0.00087839 | 3.2899e-06 | No
2020-02-15 | 13:06 | 9029 | Urban | Asset Failure | Distribution substation | 1 | 118 | 0.00015746 | 1.3344e-06 | No
2020-02-15 | 13:32 | MM1142 | Urban | Asset Failure | Distribution substation | 1 | 179 | 0.00023886 | 1.3344e-06 | No
2020-02-15 | 16:23 | DS1275 | Urban | Asset Failure | Distribution substation | 38 | 589.8421 | 0.029909 | 5.0707e-05 | No
2020-02-15 | 16:52 | 48161 | Urban | Asset Failure | Distribution substation | 122 | 213.3525 | 0.034733 | 0.0001628 | No
2020-02-15 | 16:58 | RW1281 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 285 | 865.0702 | 0.8111 | 0.00093761 | No
2020-02-15 | 17:03 | ULE2 | Short rural | Unknown | Unknown | 1 | 186 | 0.00061191 | 3.2899e-06 | No
2020-02-15 | 17:26 | SC1271 | Urban | Asset Failure | Distribution substation | 34 | 834.4118 | 0.037857 | 4.537e-05 | No
2020-02-15 | 17:35 | MVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 239 | 1010.5649 | 0.79458 | 0.00078628 | No
2020-02-15 | 18:25 | OA1244 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 196 | 116.6735 | 0.075233 | 0.00064481 | No
2020-02-15 | 18:32 | W124 | Short rural | Unknown | Unknown | 1 | 114 | 0.00037504 | 3.2899e-06 | No
2020-02-15 | 18:34 | MG1286 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 292 | 0.0038426 | 1.3159e-05 | No
2020-02-15 | 18:36 | 8799 | Short rural | Weather |  | 2 | 226 | 0.001487 | 6.5797e-06 | No
2020-02-15 | 18:48 | X877 | Short rural | Asset Failure | LV | 123 | 210.6911 | 0.085257 | 0.00040465 | No
2020-02-15 | 19:01 | MG1267 | Short rural | Weather |  | 4 | 262 | 0.0034478 | 1.3159e-05 | No
2020-02-15 | 19:05 | X879 | Short rural | Vegetation | Grow-in - NSP responsibility | 175 | 109.3943 | 0.062981 | 0.00057573 | No
2020-02-15 | 19:08 | OA1233 | Short rural | Unknown | Unknown | 39 | 168 | 0.021555 | 0.0001283 | No
2020-02-15 | 20:04 | F601 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 390 | 0.021857 | 5.6045e-05 | No
2020-02-15 | 20:09 | CD1234 | Short rural | Weather |  | 13 | 211.8462 | 0.0090603 | 4.2768e-05 | No
2020-02-15 | 20:15 | C812 | Short rural | Asset Failure | Distribution substation | 0.31326 | 1357 | 0.0013985 | 1.0306e-06 | No
2020-02-15 | 20:15 | A315 | Urban | Asset Failure | Distribution substation | 0.68674 | 1357 | 0.0012435 | 9.1638e-07 | No
2020-02-15 | 20:24 | 35988 | Short rural | Asset Failure | Distribution substation | 2 | 1048 | 0.0068956 | 6.5797e-06 | No
2020-02-15 | 20:26 | CD1234 | Short rural | Weather |  | 10 | 223 | 0.0073364 | 3.2899e-05 | No
2020-02-15 | 21:12 | MVC2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 805 | 0.0026483 | 3.2899e-06 | No
2020-02-15 | 21:14 | BWH2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 1047 | 0.0034445 | 3.2899e-06 | No
2020-02-15 | 21:18 | APH2 | Urban | Asset Failure | Distribution substation | 1 | 3956 | 0.0052789 | 1.3344e-06 | No
2020-02-15 | 23:42 | RW1218 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 809 | 0.0026615 | 3.2899e-06 | No
2020-02-16 | 0:14 | MG1286 | Short rural | Asset Failure | LV | 10 | 292.8 | 0.0096327 | 3.2899e-05 | No
2020-02-16 | 2:05 | 55875 | Urban | Asset Failure | Distribution substation | 11 | 333.3636 | 0.0048932 | 1.4678e-05 | No
2020-02-16 | 2:29 | CD1234 | Short rural | Animal | Animal Impact | 5 | 212.2 | 0.0034905 | 1.6449e-05 | No
2020-02-16 | 4:55 | X877 | Short rural | Unknown | Unknown | 7 | 499 | 0.011491 | 2.3029e-05 | No
2020-02-16 | 5:08 | C833 | Urban | Unknown | Unknown | 10 | 196 | 0.0026154 | 1.3344e-05 | No
2020-02-16 | 6:26 | X877 | Short rural | Weather |  | 1 | 3281 | 0.010794 | 3.2899e-06 | No
2020-02-16 | 7:31 | CD1260 | Urban | Weather |  | 6 | 112 | 0.00089672 | 8.0064e-06 | No
2020-02-16 | 9:26 | CD1260 | Urban | Asset Failure | Distribution substation | 16 | 643.625 | 0.013742 | 2.135e-05 | No
2020-02-16 | 9:33 | BDC2 | Short rural | Asset Failure | Distribution substation | 1 | 135 | 0.00044413 | 3.2899e-06 | No
2020-02-16 | 10:01 | WWF2 | Urban | Asset Failure | Distribution substation | 1 | 14 | 1.8682e-05 | 1.3344e-06 | No
2020-02-16 | 10:09 | 27039 | Urban | Other | Probable Equipment Failure | 17 | 1246 | 0.028265 | 2.2685e-05 | No
2020-02-16 | 10:43 | PCA2 | Short rural | Third Party | Vehicle impact | 82 | 21.7561 | 0.0058691 | 0.00026977 | No
2020-02-16 | 11:34 | AB1271 | Urban | Asset Failure | Distribution substation | 1 | 160 | 0.0002135 | 1.3344e-06 | No
2020-02-16 | 11:38 | J506 | Urban | Asset Failure | Distribution substation | 1 | 317 | 0.000423 | 1.3344e-06 | No
2020-02-16 | 11:41 | T868 | Short rural | Asset Failure | Distribution substation | 1 | 490 | 0.001612 | 3.2899e-06 | No
2020-02-16 | 12:46 | LL1212 | Urban | Asset Failure | Distribution substation | 1 | 194 | 0.00025887 | 1.3344e-06 | No
2020-02-16 | 13:04 | X877 | Short rural | Weather |  | 1 | 11 | 3.6188e-05 | 3.2899e-06 | No
2020-02-16 | 14:02 | 27200 | Urban | Asset Failure | Distribution substation | 25 | 30.12 | 0.0010048 | 3.336e-05 | No
2020-02-16 | 15:52 | X217 | Short rural | Unknown | Unknown | 20 | 155.2 | 0.010212 | 6.5797e-05 | No
2020-02-16 | 16:14 | SC1271 | Urban | Asset Failure | Distribution substation | 21 | 6.4762 | 0.00018148 | 2.8022e-05 | No
2020-02-16 | 16:18 | RW1281 | Short rural | Unknown | Unknown | 1 | 59 | 0.0001941 | 3.2899e-06 | No
2020-02-16 | 16:50 | RBB2 | Short rural | Unknown | Unknown | 1 | 222 | 0.00073035 | 3.2899e-06 | No
2020-02-16 | 17:20 | 87220 | Short rural | Other | Probable Lightning/Electrical Storm | 7 | 273 | 0.0062869 | 2.3029e-05 | No
2020-02-16 | 17:34 | X877 | Short rural | Unknown | Unknown | 1 | 376 | 0.001237 | 3.2899e-06 | No
2020-02-16 | 17:50 | W123 | Short rural | Asset Failure | Distribution substation | 9 | 62.4444 | 0.0018489 | 2.9609e-05 | No
2020-02-16 | 18:33 | R293 | Short rural | Unknown | Unknown | 1 | 200 | 0.00065797 | 3.2899e-06 | No
2020-02-16 | 20:42 | J459 | Short rural | Asset Failure | Distribution substation | 35 | 1412.2286 | 0.16261 | 0.00011515 | No
2020-02-17 | 1:29 | UNH2 | Urban | Vegetation | Grow-in - NSP responsibility | 71 | 352 | 0.033349 | 9.4742e-05 | No
2020-02-17 | 2:12 | 55885 | Urban | Animal | Animal Impact | 48 | 47 | 0.0030104 | 6.4051e-05 | No
2020-02-17 | 3:54 | RV1280 | Urban | Weather |  | 674 | 249.9777 | 0.22483 | 0.00089938 | No
2020-02-17 | 3:55 | RV1298 | Urban | Weather |  | 1723 | 108.184 | 0.24873 | 0.0022992 | No
2020-02-17 | 6:31 | CR1280 | Urban | Vegetation | Grow-in - NSP responsibility | 43 | 307.4651 | 0.017642 | 5.7379e-05 | No
2020-02-17 | 6:33 | 87222 | Long rural | Weather |  | 51 | 213.7647 | 34.7197 | 0.16242 | No
2020-02-17 | 6:43 | X213 | Short rural | Weather |  | 1 | 593 | 0.0019509 | 3.2899e-06 | No
2020-02-17 | 7:41 | 87220 | Short rural | Weather |  | 7 | 508 | 0.011699 | 2.3029e-05 | No
2020-02-17 | 8:18 | X217 | Short rural | Weather |  | 20 | 460 | 0.030267 | 6.5797e-05 | No
2020-02-17 | 8:24 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 47 | 0.00030925 | 6.5797e-06 | No
2020-02-17 | 8:32 | SZ1332 | Short rural | Unknown | Unknown | 1 | 114 | 0.00037504 | 3.2899e-06 | No
2020-02-17 | 8:33 | RD1233 | Urban | Unknown | Unknown | 1 | 106 | 0.00014145 | 1.3344e-06 | No
2020-02-17 | 8:33 | 10248 | Urban | Asset Failure | Distribution substation | 1 | 184 | 0.00024553 | 1.3344e-06 | No
2020-02-17 | 10:44 | UNH2 | Urban | Asset Failure | Distribution substation | 1 | 185 | 0.00024686 | 1.3344e-06 | No
2020-02-17 | 11:14 | HBB2 | Short rural | Asset Failure | Distribution substation | 1 | 239 | 0.00078628 | 3.2899e-06 | No
2020-02-17 | 11:19 | H745 | Short rural | Vegetation | Grow-in - NSP responsibility | 16 | 175.1875 | 0.0092215 | 5.2638e-05 | No
2020-02-17 | 11:29 | L591 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 115 | 0.00037833 | 3.2899e-06 | No
2020-02-17 | 11:40 | 76225 | Short rural | Other | Probable Lightning/Electrical Storm | 24.0178 | 68 | 0.005373 | 7.9015e-05 | No
2020-02-17 | 11:40 | 77674 | Short rural | Other | Probable Lightning/Electrical Storm | 20.0148 | 68 | 0.0044775 | 6.5846e-05 | No
2020-02-17 | 11:40 | 87218 | Short rural | Other | Probable Lightning/Electrical Storm | 254.1882 | 68 | 0.056865 | 0.00083624 | No
2020-02-17 | 11:40 | 87220 | Short rural | Other | Probable Lightning/Electrical Storm | 757.5609 | 68 | 0.16947 | 0.0024923 | No
2020-02-17 | 11:40 | 87221 | Short rural | Other | Probable Lightning/Electrical Storm | 297.2201 | 68 | 0.066491 | 0.00097781 | No
2020-02-17 | 11:40 | 87222 | Long rural | Other | Probable Lightning/Electrical Storm | 312.2312 | 68 | 67.6169 | 0.99437 | No
2020-02-17 | 11:40 | 87223 | Short rural | Other | Probable Lightning/Electrical Storm | 427.3164 | 68 | 0.095595 | 0.0014058 | No
2020-02-17 | 11:40 | R290 | Short rural | Other | Probable Lightning/Electrical Storm | 32.0237 | 68 | 0.007164 | 0.00010535 | No
2020-02-17 | 11:40 | R293 | Short rural | Other | Probable Lightning/Electrical Storm | 95.0704 | 68 | 0.021268 | 0.00031277 | No
2020-02-17 | 11:40 | X213 | Short rural | Other | Probable Lightning/Electrical Storm | 75.0556 | 68 | 0.016791 | 0.00024692 | No
2020-02-17 | 11:40 | X217 | Short rural | Other | Probable Lightning/Electrical Storm | 225.1667 | 68 | 0.050372 | 0.00074077 | No
2020-02-17 | 11:40 | X482 | Short rural | Other | Probable Lightning/Electrical Storm | 181.1341 | 68 | 0.040522 | 0.00059591 | No
2020-02-17 | 11:41 | AZ1227 | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 405 | 0.0010809 | 2.6688e-06 | No
2020-02-17 | 11:43 | KC1288 | Short rural | Asset Failure | Distribution substation | 1 | 1377 | 0.0045301 | 3.2899e-06 | No
2020-02-17 | 12:56 | B205 | Urban | Unknown | Unknown | 677 | 40 | 0.036136 | 0.00090339 | No
2020-02-17 | 12:58 | B211 | Urban | Weather |  | 1295 | 7.4595 | 0.01289 | 0.001728 | No
2020-02-17 | 13:19 | HR1269 | Urban | Weather |  | 2327 | 85.4852 | 0.26544 | 0.0031051 | No
2020-02-17 | 13:41 | 7962 | Urban | Weather |  | 28 | 136 | 0.0050814 | 3.7363e-05 | No
2020-02-17 | 13:57 | RBD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 23 | 319.4783 | 0.024174 | 7.5667e-05 | No
2020-02-17 | 15:21 | J506 | Urban | Asset Failure | Distribution substation | 76 | 43.5395 | 0.0044155 | 0.00010141 | No
2020-02-17 | 15:45 | RW1255 | Short rural | Vegetation | Grow-in - NSP responsibility | 19 | 23.3684 | 0.0014607 | 6.2507e-05 | No
2020-02-17 | 15:59 | RBC2 | Short rural | Unknown | Unknown | 2 | 255 | 0.0016778 | 6.5797e-06 | No
2020-02-17 | 16:07 | B211 | Urban | Other | Probable Lightning/Electrical Storm | 62 | 190.0161 | 0.015721 | 8.2733e-05 | No
2020-02-17 | 16:14 | AZ1205 | Urban | Animal | Animal Impact | 1140 | 73.3991 | 0.11166 | 0.0015212 | No
2020-02-17 | 16:36 | X213 | Short rural | Weather |  | 3 | 39 | 0.00038491 | 9.8696e-06 | No
2020-02-17 | 16:44 | 87222 | Long rural | Weather |  | 4 | 127 | 1.6178 | 0.012739 | No
2020-02-17 | 16:49 | HR1269 | Urban | Weather |  | 611 | 394.8969 | 0.32197 | 0.00081532 | No
2020-02-17 | 16:50 | M399 | Short rural | Weather |  | 1 | 117 | 0.00038491 | 3.2899e-06 | No
2020-02-17 | 17:08 | MM1392 | Urban | Asset Failure | Distribution substation | 1 | 1037 | 0.0013838 | 1.3344e-06 | No
2020-02-17 | 20:48 | J499 | Urban | Unknown | Unknown | 27 | 42 | 0.0015132 | 3.6029e-05 | No
2020-02-18 | 2:09 | BYD2 | Short rural | Animal | Animal Impact | 962 | 1.4168 | 0.0044841 | 0.0031648 | Yes
2020-02-18 | 3:30 | RD1251 | Urban | Animal | Animal Impact | 1091 | 123.011 | 0.17908 | 0.0014558 | Yes
2020-02-18 | 10:01 | MYK2 | Urban | Network business | Switching or protection error | 1 | 38 | 5.0707e-05 | 1.3344e-06 | Yes
2020-02-18 | 10:26 | T831 | Short rural | Unknown | Unknown | 1 | 108 | 0.00035531 | 3.2899e-06 | Yes
2020-02-18 | 10:39 | MYK2 | Urban | Network business | Switching or protection error | 1 | 40 | 5.3376e-05 | 1.3344e-06 | Yes
2020-02-18 | 10:46 | X217 | Short rural | Unknown | Unknown | 3 | 136 | 0.0013423 | 9.8696e-06 | Yes
2020-02-18 | 12:24 | X213 | Short rural | Unknown | Unknown | 1 | 86 | 0.00028293 | 3.2899e-06 | Yes
2020-02-18 | 13:10 | MM1372 | Urban | Asset Failure | Distribution substation | 1 | 798 | 0.0010649 | 1.3344e-06 | Yes
2020-02-18 | 13:19 | CS1276 | Urban | Unknown | Unknown | 6 | 221 | 0.0017694 | 8.0064e-06 | Yes
2020-02-18 | 13:34 | S738 | Short rural | Asset Failure | Distribution substation | 5 | 115 | 0.0018917 | 1.6449e-05 | Yes
2020-02-18 | 13:48 | 840 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 74 | 0.0004869 | 6.5797e-06 | Yes
2020-02-18 | 15:45 | S785 | Urban | Asset Failure | Distribution substation | 1 | 188 | 0.00025087 | 1.3344e-06 | Yes
2020-02-18 | 16:32 | J506 | Urban | Asset Failure | Distribution substation | 1 | 265 | 0.00035362 | 1.3344e-06 | Yes
2020-02-18 | 16:35 | CX1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 291 | 0.00095735 | 3.2899e-06 | Yes
2020-02-18 | 16:45 | SG1209 | Urban | Asset Failure | Distribution substation | 66 | 14.4545 | 0.001273 | 8.807e-05 | Yes
2020-02-18 | 17:08 | RD1292 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 37 | 276 | 0.013627 | 4.9373e-05 | Yes
2020-02-18 | 17:16 | RW1292 | Short rural | Weather |  | 24 | 123 | 0.0097117 | 7.8957e-05 | Yes
2020-02-18 | 17:52 | NN1233 | Short rural | Asset Failure | Distribution substation | 20 | 273 | 0.017963 | 6.5797e-05 | Yes
2020-02-18 | 17:56 | DP1243 | Urban | Asset Failure | Distribution substation | 35 | 42.5429 | 0.0019869 | 4.6704e-05 | Yes
2020-02-18 | 18:12 | 19857 | Urban | Asset Failure | Distribution substation | 48 | 259.0208 | 0.016591 | 6.4051e-05 | Yes
2020-02-18 | 19:11 | J473 | Urban | Asset Failure | HV | 15 | 33.1333 | 0.0006632 | 2.0016e-05 | Yes
2020-02-18 | 19:28 | 87220 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 107 | 0.0014081 | 1.3159e-05 | Yes
2020-02-18 | 19:50 | KMD2 | Short rural | Asset Failure | Distribution substation | 19 | 250 | 0.015627 | 6.2507e-05 | Yes
2020-02-18 | 20:26 | MG1282 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 60 | 232 | 0.045795 | 0.00019739 | Yes
2020-02-18 | 20:40 | MVC2 | Short rural | Weather |  | 17 | 217 | 0.012136 | 5.5928e-05 | Yes
2020-02-18 | 20:49 | SN1219 | Short rural | Weather |  | 60 | 55.7667 | 0.011008 | 0.00019739 | Yes
2020-02-18 | 20:49 | 57448 | Short rural | Weather |  | 1 | 301 | 0.00099025 | 3.2899e-06 | Yes
2020-02-18 | 20:50 | FT1208 | Urban | Weather |  | 86 | 94 | 0.010787 | 0.00011476 | Yes
2020-02-18 | 20:54 | NN1236 | Urban | Asset Failure | Distribution substation | 1 | 6748 | 0.0090045 | 1.3344e-06 | Yes
2020-02-18 | 20:59 | SN1282 | Short rural | Weather |  | 45 | 192.2889 | 0.028467 | 0.00014804 | Yes
2020-02-18 | 21:04 | RBE2 | Short rural | Other | Probable Lightning/Electrical Storm | 13 | 159 | 0.0068001 | 4.2768e-05 | Yes
2020-02-18 | 21:05 | DP1221 | Short rural | Weather |  | 179 | 232.1508 | 0.13671 | 0.00058889 | Yes
2020-02-18 | 21:06 | PCA2 | Short rural | Weather |  | 82 | 84.8049 | 0.022878 | 0.00026977 | Yes
2020-02-18 | 21:10 | 25449 | Short rural | Weather |  | 536.6746 | 57.8001 | 0.10205 | 0.0017656 | Yes
2020-02-18 | 21:10 | 25450 | Short rural | Weather |  | 1054.3254 | 57.8001 | 0.20048 | 0.0034686 | Yes
2020-02-18 | 21:27 | L584 | Short rural | Other | Probable Lightning/Electrical Storm | 23 | 261 | 0.019749 | 7.5667e-05 | Yes
2020-02-18 | 21:30 | SN1230 | Short rural | Unknown | Unknown | 2 | 807 | 0.0053098 | 6.5797e-06 | Yes
2020-02-18 | 21:38 | CR1262 | Urban | Weather |  | 53 | 449 | 0.031755 | 7.0723e-05 | Yes
2020-02-18 | 21:56 | L582 | Short rural | Weather |  | 1 | 726 | 0.0023884 | 3.2899e-06 | Yes
2020-02-18 | 22:05 | 6420 | Urban | Weather |  | 196 | 126.4184 | 0.033064 | 0.00026154 | Yes
2020-02-18 | 22:05 | AZ1231 | Urban | Weather |  | 37 | 120.4324 | 0.0059461 | 4.9373e-05 | Yes
2020-02-18 | 22:09 | R260 | Short rural | Weather |  | 1 | 102 | 0.00033557 | 3.2899e-06 | Yes
2020-02-18 | 22:09 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 90 | 773.6333 | 0.22906 | 0.00029609 | Yes
2020-02-18 | 22:10 | LP1142 | Urban | Weather |  | 1386 | 167.5332 | 0.30985 | 0.0018495 | Yes
2020-02-18 | 22:12 | 8801 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 226 | 771.8496 | 0.57388 | 0.00074351 | Yes
2020-02-18 | 22:13 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 387.8384 | 901.0052 | 1.1496 | 0.0012759 | Yes
2020-02-18 | 22:13 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 328.9908 | 901.0052 | 0.97519 | 0.0010823 | Yes
2020-02-18 | 22:13 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 238.1708 | 901.0052 | 0.70598 | 0.00078355 | Yes
2020-02-18 | 22:14 | ER1232 | Short rural | Weather |  | 596 | 1041.8456 | 2.0428 | 0.0019608 | Yes
2020-02-18 | 22:14 | MM1392 | Urban | Asset Failure | Distribution substation | 25 | 822.36 | 0.027434 | 3.336e-05 | Yes
2020-02-18 | 22:15 | L941 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 441 | 271.5918 | 0.39403 | 0.0014508 | Yes
2020-02-18 | 22:15 | 10287 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 961 | 953.9178 | 1.2233 | 0.0012824 | Yes
2020-02-18 | 22:15 | 27454 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 427 | 1202.37 | 1.6891 | 0.0014048 | Yes
2020-02-18 | 22:16 | L948 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 444 | 874.3153 | 1.2771 | 0.0014607 | Yes
2020-02-18 | 22:17 | ER1132 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 604.1818 | 0.0088684 | 1.4678e-05 | Yes
2020-02-18 | 22:17 | L947 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 212 | 1214.3491 | 0.84695 | 0.00069745 | Yes
2020-02-18 | 22:18 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 366 | 562.7951 | 0.67766 | 0.0012041 | Yes
2020-02-18 | 22:18 | SZ1122 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 605 | 875.9339 | 1.7434 | 0.0019904 | Yes
2020-02-18 | 22:19 | L948 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 301 | 811.3322 | 0.80342 | 0.00099025 | Yes
2020-02-18 | 22:20 | WD1221 | Short rural | Weather |  | 540 | 982.1167 | 1.7448 | 0.0017765 | Yes
2020-02-18 | 22:20 | WD1284 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 300 | 953.77 | 0.94133 | 0.00098696 | Yes
2020-02-18 | 22:22 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 38 | 1586.8947 | 0.19839 | 0.00012501 | Yes
2020-02-18 | 22:23 | WD1225 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 270 | 936.3037 | 0.83168 | 0.00088826 | Yes
2020-02-18 | 22:24 | CX1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 89 | 1154.1573 | 0.33793 | 0.0002928 | Yes
2020-02-18 | 22:25 | SZ1332 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 366 | 1540.2514 | 1.8546 | 0.0012041 | Yes
2020-02-18 | 22:25 | A048 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 308 | 541.211 | 0.22243 | 0.00041099 | Yes
2020-02-18 | 22:25 | CX1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 725 | 565.5848 | 1.349 | 0.0023852 | Yes
2020-02-18 | 22:25 | 41533 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 398 | 267.6382 | 0.35044 | 0.0013094 | Yes
2020-02-18 | 22:26 | CX1232 | Short rural | Weather |  | 275 | 1967.4873 | 1.78 | 0.00090471 | Yes
2020-02-18 | 22:26 | A051 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 399 | 378.4912 | 0.20152 | 0.00053243 | Yes
2020-02-18 | 22:27 | CX1210 | Short rural | Weather |  | 237 | 1013.9662 | 0.79059 | 0.0007797 | Yes
2020-02-18 | 22:27 | A046 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 831 | 580.4091 | 1.5868 | 0.0027339 | Yes
2020-02-18 | 22:27 | SZ1322 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1015 | 1043.5783 | 3.4847 | 0.0033392 | Yes
2020-02-18 | 22:28 | MR2218 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1805 | 489.2122 | 2.905 | 0.0059382 | Yes
2020-02-18 | 22:28 | CD1260 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 13 | 185 | 0.0032092 | 1.7347e-05 | Yes
2020-02-18 | 22:28 | CX1206 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 466 | 457.8348 | 0.7019 | 0.0015331 | Yes
2020-02-18 | 22:29 | MR2225 | Urban | Weather |  | 2880 | 30 | 0.11529 | 0.0038431 | Yes
2020-02-18 | 22:30 | MR2292 | Urban | Weather |  | 1187 | 27.4499 | 0.043479 | 0.0015839 | Yes
2020-02-18 | 22:30 | MR2299 | Urban | Weather |  | 1472 | 29.733 | 0.058403 | 0.0019642 | Yes
2020-02-18 | 22:30 | MR2244 | Urban | Weather |  | 135 | 26.4667 | 0.0047678 | 0.00018014 | Yes
2020-02-18 | 22:30 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 539 | 987.6234 | 1.7513 | 0.0017732 | Yes
2020-02-18 | 22:30 | CX1273 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 386 | 1185.9637 | 1.506 | 0.0012699 | Yes
2020-02-18 | 22:30 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 2308 | 0.045558 | 1.9739e-05 | Yes
2020-02-18 | 22:31 | S741 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 300 | 1138.2767 | 1.1234 | 0.00098696 | Yes
2020-02-18 | 22:31 | MR2205 | Short rural | Weather |  | 1076 | 644.75 | 2.2823 | 0.0035399 | Yes
2020-02-18 | 22:32 | 9032 | Short rural | Weather |  | 17 | 958 | 0.053579 | 5.5928e-05 | Yes
2020-02-18 | 22:34 | D814 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 36 | 2172.3056 | 0.25728 | 0.00011844 | Yes
2020-02-18 | 22:35 | L947 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 71 | 2179 | 0.50897 | 0.00023358 | Yes
2020-02-18 | 22:35 | S738 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 235 | 1534.5149 | 1.1864 | 0.00077312 | Yes
2020-02-18 | 22:35 | S743 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 280 | 1089.7536 | 1.0038 | 0.00092116 | Yes
2020-02-18 | 22:35 | S738 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 111 | 862.9369 | 0.31512 | 0.00036517 | Yes
2020-02-18 | 22:36 | GL1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 750 | 1578.4467 | 3.8947 | 0.0024674 | Yes
2020-02-18 | 22:38 | B201 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 960 | 467.274 | 0.59859 | 0.001281 | Yes
2020-02-18 | 22:38 | S740 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 878 | 600.3827 | 0.70341 | 0.0011716 | Yes
2020-02-18 | 22:40 | 46752 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 99 | 952.5758 | 0.12584 | 0.00013211 | Yes
2020-02-18 | 22:42 | AZ1272 | Short rural | Weather |  | 50 | 653 | 0.10741 | 0.00016449 | Yes
2020-02-18 | 22:42 | FT1206 | Short rural | Weather |  | 22 | 36 | 0.0026056 | 7.2377e-05 | Yes
2020-02-18 | 22:45 | DP1295 | Urban | Weather |  | 109 | 82.3761 | 0.011982 | 0.00014545 | Yes
2020-02-18 | 22:45 | 35327 | Urban | Weather |  | 1445 | 300.6699 | 0.57975 | 0.0019282 | Yes
2020-02-18 | 22:45 | BX1222 | Urban | Other | Probable Lightning/Electrical Storm | 194 | 321 | 0.083098 | 0.00025887 | Yes
2020-02-18 | 22:48 | LL1172 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 38 | 587.6316 | 0.029797 | 5.0707e-05 | Yes
2020-02-18 | 22:49 | F601 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 104 | 668 | 0.092703 | 0.00013878 | Yes
2020-02-18 | 22:52 | 7966 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 37 | 857.3784 | 0.042331 | 4.9373e-05 | Yes
2020-02-18 | 23:04 | LL1232 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 91 | 574.978 | 0.06982 | 0.00012143 | Yes
2020-02-18 | 23:04 | KME2 | Short rural | Weather |  | 1272 | 71.566 | 0.29948 | 0.0041847 | Yes
2020-02-18 | 23:09 | 8764 | Urban | Weather |  | 45 | 497 | 0.029844 | 6.0048e-05 | Yes
2020-02-18 | 23:14 | A046 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 46 | 1796.9565 | 0.27194 | 0.00015133 | Yes
2020-02-18 | 23:20 | KC1236 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 1010 | 0.013291 | 1.3159e-05 | Yes
2020-02-18 | 23:22 | BX1332 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 67 | 619.2388 | 0.055363 | 8.9405e-05 | Yes
2020-02-18 | 23:24 | HR1273 | Urban | Vegetation | Grow-in - NSP responsibility | 76 | 978 | 0.099183 | 0.00010141 | Yes
2020-02-18 | 23:25 | X217 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 65 | 883.6923 | 0.18897 | 0.00021384 | Yes
2020-02-18 | 23:27 | 49008 | Short rural | Weather |  | 81 | 405.8642 | 0.10815 | 0.00026648 | Yes
2020-02-18 | 23:30 | T868 | Short rural | Weather |  | 2 | 458 | 0.0030135 | 6.5797e-06 | Yes
2020-02-18 | 23:36 | 7981 | Urban | Weather |  | 39 | 654 | 0.034035 | 5.2042e-05 | Yes
2020-02-18 | 23:44 | L582 | Short rural | Weather |  | 4 | 618 | 0.0081325 | 1.3159e-05 | Yes
2020-02-19 | 0:26 | WWF2 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 555 | 97.0162 | 0.071849 | 0.00074059 | No
2020-02-19 | 0:27 | WWF2 | Urban | Weather |  | 1021 | 74.0833 | 0.10093 | 0.0013624 | No
2020-02-19 | 0:30 | SG1228 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 347.2143 | 0.01946 | 5.6045e-05 | No
2020-02-19 | 0:36 | 77674 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 486 | 0.0015989 | 3.2899e-06 | No
2020-02-19 | 0:38 | SN1219 | Short rural | Unknown | Unknown | 6 | 684 | 0.013502 | 1.9739e-05 | No
2020-02-19 | 1:30 | RBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 702.8 | 0.023121 | 3.2899e-05 | No
2020-02-19 | 1:31 | RW1255 | Short rural | Weather |  | 6 | 420.8333 | 0.0083069 | 1.9739e-05 | No
2020-02-19 | 2:12 | DP1206 | Urban | Weather |  | 1 | 69 | 9.2074e-05 | 1.3344e-06 | No
2020-02-19 | 2:20 | 9032 | Short rural | Other | Probable Lightning/Electrical Storm | 25 | 716.08 | 0.058895 | 8.2247e-05 | No
2020-02-19 | 3:31 | S735 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 748.2857 | 0.10339 | 0.00013817 | No
2020-02-19 | 3:42 | 8685 | Urban | Weather |  | 9 | 502.8889 | 0.0060395 | 1.201e-05 | No
2020-02-19 | 3:52 | 2812 | Urban | Weather |  | 1029 | 8.3664 | 0.011488 | 0.0013731 | No
2020-02-19 | 4:15 | L940 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 2075.25 | 0.027309 | 1.3159e-05 | No
2020-02-19 | 4:18 | MR2232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 177 | 465.678 | 0.27117 | 0.00058231 | No
2020-02-19 | 4:24 | A048 | Urban | Weather |  | 12 | 2011.4167 | 0.032208 | 1.6013e-05 | No
2020-02-19 | 5:07 | 8799 | Short rural | Weather |  | 5 | 2239.4 | 0.036837 | 1.6449e-05 | No
2020-02-19 | 5:16 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 14 | 2009.4286 | 0.09255 | 4.6058e-05 | No
2020-02-19 | 5:20 | CX1206 | Short rural | Other | Probable Lightning/Electrical Storm | 14 | 2456.7857 | 0.11315 | 4.6058e-05 | No
2020-02-19 | 5:29 | GL1255 | Short rural | Weather |  | 1 | 1901 | 0.006254 | 3.2899e-06 | No
2020-02-19 | 5:50 | CX1206 | Short rural | Weather |  | 10 | 2200.1 | 0.07238 | 3.2899e-05 | No
2020-02-19 | 6:03 | B201 | Urban | Weather |  | 89 | 510.2472 | 0.060598 | 0.00011876 | No
2020-02-19 | 6:13 | GG1295 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 255 | 0.00083892 | 3.2899e-06 | No
2020-02-19 | 6:16 | MVC2 | Short rural | Weather |  | 1 | 95 | 0.00031254 | 3.2899e-06 | No
2020-02-19 | 6:26 | CD1260 | Urban | Asset Failure | HV | 1654 | 43.6735 | 0.096392 | 0.0022071 | No
2020-02-19 | 6:27 | CX1210 | Short rural | Weather |  | 3 | 1828 | 0.018042 | 9.8696e-06 | No
2020-02-19 | 6:48 | 2807 | Urban | Vegetation | Grow-in - NSP responsibility | 49 | 28.4694 | 0.0018615 | 6.5386e-05 | No
2020-02-19 | 6:51 | D813 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 192 | 0.0094748 | 4.9348e-05 | No
2020-02-19 | 7:08 | R211 | Short rural | Weather |  | 97 | 439.1959 | 0.14015 | 0.00031912 | No
2020-02-19 | 7:29 | BK1251 | Short rural | Weather |  | 3 | 502.6667 | 0.0049611 | 9.8696e-06 | No
2020-02-19 | 7:33 | MR2205 | Short rural | Weather |  | 1076 | 101 | 0.35753 | 0.0035399 | No
2020-02-19 | 7:57 | JBB2 | Short rural | Asset Failure | Distribution substation | 18 | 258.3333 | 0.015298 | 5.9218e-05 | No
2020-02-19 | 8:18 | SZ1122 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 1867 | 0.0061422 | 3.2899e-06 | No
2020-02-19 | 8:28 | 7962 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 41 | 278 | 0.015209 | 5.471e-05 | No
2020-02-19 | 8:39 | CX1206 | Short rural | Weather |  | 2 | 2005 | 0.013192 | 6.5797e-06 | No
2020-02-19 | 8:40 | 4860 | Urban | Unknown | Unknown | 6 | 684 | 0.0054764 | 8.0064e-06 | No
2020-02-19 | 9:11 | L941 | Short rural | Weather |  | 6 | 1414 | 0.027911 | 1.9739e-05 | No
2020-02-19 | 9:18 | SC1238 | Urban | Vegetation | Grow-in - NSP responsibility | 7 | 1690.2857 | 0.015789 | 9.3408e-06 | No
2020-02-19 | 9:26 | BK1251 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 26 | 542.0769 | 0.046367 | 8.5536e-05 | No
2020-02-19 | 9:29 | MR2205 | Short rural | Weather |  | 1076 | 18 | 0.063718 | 0.0035399 | No
2020-02-19 | 9:39 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 1811.7407 | 0.16093 | 8.8826e-05 | No
2020-02-19 | 9:45 | NN1251 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 535 | 0.0035202 | 6.5797e-06 | No
2020-02-19 | 9:49 | WD1288 | Urban | Weather |  | 1 | 1704 | 0.0022738 | 1.3344e-06 | No
2020-02-19 | 9:51 | SN1230 | Short rural | Unknown | Unknown | 2 | 72 | 0.00047374 | 6.5797e-06 | No
2020-02-19 | 9:53 | OA1233 | Short rural | Unknown | Unknown | 1 | 368 | 0.0012107 | 3.2899e-06 | No
2020-02-19 | 10:03 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 68 | 330.3971 | 0.073913 | 0.00022371 | No
2020-02-19 | 10:04 | T868 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 661 | 0.0086984 | 1.3159e-05 | No
2020-02-19 | 10:35 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 268 | 117 | 0.10316 | 0.00088168 | No
2020-02-19 | 10:58 | 35388 | Urban | Weather |  | 46 | 52.5 | 0.0032226 | 6.1382e-05 | No
2020-02-19 | 11:23 | MR2232 | Short rural | Weather |  | 82 | 1590 | 0.42893 | 0.00026977 | No
2020-02-19 | 12:02 | SZ1342 | Urban | Weather |  | 31 | 397.7742 | 0.016454 | 4.1366e-05 | No
2020-02-19 | 12:12 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 1518 | 0.009988 | 6.5797e-06 | No
2020-02-19 | 12:36 | L948 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 1501.5 | 0.0098795 | 6.5797e-06 | No
2020-02-19 | 12:36 | L948 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 1284 | 0.012673 | 9.8696e-06 | No
2020-02-19 | 12:46 | R260 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 400 | 0.0013159 | 3.2899e-06 | No
2020-02-19 | 12:55 | CD1234 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 294 | 0.00096722 | 3.2899e-06 | No
2020-02-19 | 13:15 | L940 | Short rural | Vegetation | Grow-in - NSP responsibility | 10 | 1389.1 | 0.045699 | 3.2899e-05 | No
2020-02-19 | 13:19 | L946 | Short rural | Vegetation | Grow-in - NSP responsibility | 47 | 1385.5106 | 0.21423 | 0.00015462 | No
2020-02-19 | 13:41 | GL1255 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 38 | 1103.1842 | 0.13791 | 0.00012501 | No
2020-02-19 | 13:50 | CX1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 184 | 0.00060533 | 3.2899e-06 | No
2020-02-19 | 13:58 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 1547.0625 | 0.16287 | 0.00010528 | No
2020-02-19 | 14:01 | C890 | Urban | Asset Failure | Distribution substation | 1 | 267 | 0.00035628 | 1.3344e-06 | No
2020-02-19 | 14:02 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 50 | 1695.04 | 0.27882 | 0.00016449 | No
2020-02-19 | 14:03 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 1526.8889 | 0.045209 | 2.9609e-05 | No
2020-02-19 | 14:11 | 25740 | Urban | Asset Failure | Distribution substation | 1 | 697 | 0.00093008 | 1.3344e-06 | No
2020-02-19 | 14:22 | 35304 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19 | 55 | 0.0013944 | 2.5354e-05 | No
2020-02-19 | 14:34 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 92 | 789.0761 | 0.23883 | 0.00030267 | No
2020-02-19 | 14:35 | L946 | Short rural | Other | Probable Lightning/Electrical Storm | 10 | 1318.6 | 0.04338 | 3.2899e-05 | No
2020-02-19 | 14:55 | S737 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 51 | 300.1961 | 0.050368 | 0.00016778 | No
2020-02-19 | 15:12 | L948 | Short rural | Weather |  | 34 | 1769 | 0.19787 | 0.00011186 | No
2020-02-19 | 15:13 | GL1233 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 19 | 1266.6316 | 0.079174 | 6.2507e-05 | No
2020-02-19 | 15:23 | NM1258 | Urban | Asset Failure | Distribution substation | 5 | 173.4 | 0.0011569 | 6.672e-06 | No
2020-02-19 | 15:55 | 8769 | Urban | Asset Failure | Distribution substation | 1 | 1043 | 0.0013918 | 1.3344e-06 | No
2020-02-19 | 16:18 | L947 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 2453 | 0.00807 | 3.2899e-06 | No
2020-02-19 | 16:36 | R211 | Short rural | Weather |  | 30 | 31.5 | 0.0031089 | 9.8696e-05 | No
2020-02-19 | 16:38 | R211 | Short rural | Weather |  | 66 | 31.2879 | 0.0067936 | 0.00021713 | No
2020-02-19 | 17:26 | ER1142 | Urban | Asset Failure | Distribution substation | 53 | 97.1509 | 0.0068708 | 7.0723e-05 | No
2020-02-19 | 18:15 | RBE2 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 99 | 0.00065139 | 6.5797e-06 | No
2020-02-19 | 18:16 | CX1232 | Short rural | Asset Failure | Distribution substation | 5 | 1551 | 0.025513 | 1.6449e-05 | No
2020-02-19 | 18:25 | R293 | Short rural | Unknown | Unknown | 1 | 1007 | 0.0033129 | 3.2899e-06 | No
2020-02-19 | 18:33 | 87222 | Long rural | Weather |  | 1 | 1122 | 3.5732 | 0.0031847 | No
2020-02-19 | 18:35 | SZ1242 | Short rural | Weather |  | 9 | 1016.2222 | 0.030089 | 2.9609e-05 | No
2020-02-19 | 18:53 | CX1206 | Short rural | Weather |  | 4 | 1389 | 0.018278 | 1.3159e-05 | No
2020-02-19 | 19:02 | 1952 | Urban | Asset Failure | Distribution substation | 14 | 1174 | 0.021932 | 1.8682e-05 | No
2020-02-19 | 19:07 | JBA2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 90 | 0.00029609 | 3.2899e-06 | No
2020-02-19 | 20:05 | L940 | Short rural | Weather |  | 1 | 958 | 0.0031517 | 3.2899e-06 | No
2020-02-19 | 20:08 | SZ1242 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 925.6667 | 0.027408 | 2.9609e-05 | No
2020-02-19 | 20:17 | ER1252 | Short rural | Unknown | Unknown | 1 | 1200 | 0.0039478 | 3.2899e-06 | No
2020-02-19 | 21:03 | S743 | Short rural | Weather |  | 1 | 1194 | 0.0039281 | 3.2899e-06 | No
2020-02-19 | 22:39 | L946 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 916 | 0.0030135 | 3.2899e-06 | No
2020-02-20 | 1:07 | 8798 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 806.5 | 0.01592 | 1.9739e-05 | No
2020-02-20 | 2:03 | X877 | Short rural | Weather |  | 137 | 99.4088 | 0.044805 | 0.00045071 | No
2020-02-20 | 2:24 | CA1210 | Urban | Asset Failure | Distribution substation | 23 | 729.087 | 0.022377 | 3.0691e-05 | No
2020-02-20 | 4:58 | CLA2 | Short rural | Asset Failure | Distribution substation | 21 | 113 | 0.0078068 | 6.9087e-05 | No
2020-02-20 | 6:47 | D813 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 746 | 0.0073627 | 9.8696e-06 | No
2020-02-20 | 7:23 | CR1280 | Urban | Asset Failure | Distribution substation | 82 | 265.2561 | 0.029025 | 0.00010942 | No
2020-02-20 | 7:46 | SZ1322 | Short rural | Vegetation | Grow-in - NSP responsibility | 22 | 497 | 0.035971 | 7.2377e-05 | No
2020-02-20 | 7:59 | DS1223 | Urban | Weather |  | 17 | 327.8824 | 0.0074379 | 2.2685e-05 | No
2020-02-20 | 7:59 | 8799 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 16 | 633 | 0.03332 | 5.2638e-05 | No
2020-02-20 | 8:11 | GG1232 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 220 | 0.00072377 | 3.2899e-06 | No
2020-02-20 | 8:24 | R293 | Short rural | Asset Failure | Distribution substation | 1 | 298 | 0.00098038 | 3.2899e-06 | No
2020-02-20 | 8:46 | CX1206 | Short rural | Weather |  | 4 | 552.75 | 0.0072739 | 1.3159e-05 | No
2020-02-20 | 9:08 | CS1247 | Urban | Asset Failure | Distribution substation | 19 | 677 | 0.017164 | 2.5354e-05 | No
2020-02-20 | 10:03 | CT1203 | Urban | Unknown | Unknown | 25 | 166 | 0.0055378 | 3.336e-05 | No
2020-02-20 | 10:28 | CX1273 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 661 | 0.0021746 | 3.2899e-06 | No
2020-02-20 | 10:44 | S790 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 162 | 0.00053296 | 3.2899e-06 | No
2020-02-20 | 11:21 | RW1281 | Short rural | Unknown | Unknown | 3 | 238 | 0.002349 | 9.8696e-06 | No
2020-02-20 | 11:54 | X217 | Short rural | Unknown | Unknown | 3 | 227 | 0.0022404 | 9.8696e-06 | No
2020-02-20 | 11:58 | 68197 | Urban | Asset Failure | LV | 323 | 504 | 0.21723 | 0.00043101 | No
2020-02-20 | 12:09 | 46397 | Urban | Weather |  | 59 | 44.5424 | 0.0035068 | 7.873e-05 | No
2020-02-20 | 12:43 | X217 | Short rural | Unknown | Unknown | 1 | 177 | 0.00058231 | 3.2899e-06 | No
2020-02-20 | 13:41 | L537 | Urban | Asset Failure | HV | 985 | 57.4171 | 0.075468 | 0.0013144 | No
2020-02-20 | 13:41 | L544 | Urban | Asset Failure | HV | 1005 | 57.4171 | 0.077 | 0.0013411 | No
2020-02-20 | 14:31 | S741 | Short rural | Weather |  | 1 | 113 | 0.00037175 | 3.2899e-06 | No
2020-02-20 | 15:32 | 8798 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 102.6667 | 0.0040531 | 3.9478e-05 | No
2020-02-20 | 15:44 | 16649 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 84 | 0.00011209 | 1.3344e-06 | No
2020-02-20 | 16:00 | 17061 | Urban | Asset Failure | Distribution substation | 31 | 1273.2903 | 0.052671 | 4.1366e-05 | No
2020-02-20 | 17:09 | S737 | Short rural | Weather |  | 10 | 140.5 | 0.0046223 | 3.2899e-05 | No
2020-02-20 | 18:06 | NA1207 | Short rural | Unknown | Unknown | 3 | 94 | 0.00092774 | 9.8696e-06 | No
2020-02-20 | 21:18 | MM1162 | Urban | Asset Failure | Distribution substation | 17 | 744.8824 | 0.016897 | 2.2685e-05 | No
2020-02-21 | 0:48 | J474 | Short rural | Asset Failure | Distribution substation | 1 | 478 | 0.0015726 | 3.2899e-06 | No
2020-02-21 | 1:18 | 27200 | Urban | Asset Failure | Distribution substation | 1 | 403 | 0.00053776 | 1.3344e-06 | No
2020-02-21 | 6:25 | WD1221 | Short rural | Asset Failure | Distribution substation | 8 | 235 | 0.0061849 | 2.6319e-05 | No
2020-02-21 | 7:00 | 49391 | Urban | Unknown | Unknown | 10 | 143 | 0.0019082 | 1.3344e-05 | No
2020-02-21 | 7:18 | HR1269 | Urban | Unknown | Unknown | 1 | 84 | 0.00011209 | 1.3344e-06 | No
2020-02-21 | 7:31 | GL1255 | Short rural | Asset Failure | Distribution substation | 1 | 721 | 0.002372 | 3.2899e-06 | No
2020-02-21 | 7:45 | A095 | Short rural | Unknown | Unknown | 1 | 100 | 0.00032899 | 3.2899e-06 | No
2020-02-21 | 8:31 | R260 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 406 | 0.0026714 | 6.5797e-06 | No
2020-02-21 | 8:55 | DS1223 | Urban | Asset Failure | Distribution substation | 17 | 249 | 0.0056485 | 2.2685e-05 | No
2020-02-21 | 9:00 | GL1255 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 840 | 0.0027635 | 3.2899e-06 | No
2020-02-21 | 10:42 | HR1276 | Urban | Unknown | Unknown | 48 | 175 | 0.011209 | 6.4051e-05 | No
2020-02-21 | 10:55 | D813 | Short rural | Unknown | Unknown | 1 | 160 | 0.00052638 | 3.2899e-06 | No
2020-02-21 | 10:57 | BK1251 | Short rural | Asset Failure | Distribution substation | 3 | 616 | 0.0060797 | 9.8696e-06 | No
2020-02-21 | 12:18 | CD1271 | Short rural | Unknown | Unknown | 1 | 162 | 0.00053296 | 3.2899e-06 | No
2020-02-21 | 15:15 | FT1206 | Short rural | Third Party | Vehicle impact | 395.5608 | 92.7152 | 0.12065 | 0.0013013 | No
2020-02-21 | 15:15 | FT1207 | Urban | Third Party | Vehicle impact | 819.4392 | 92.7152 | 0.10138 | 0.0010935 | No
2020-02-21 | 18:36 | BDG2 | Short rural | Asset Failure | HV | 1667 | 131.1728 | 0.71938 | 0.0054842 | No
2020-02-21 | 19:06 | B201 | Urban | Unknown | Unknown | 60 | 86 | 0.0068855 | 8.0064e-05 | No
2020-02-21 | 21:51 | 49391 | Urban | Asset Failure | Distribution substation | 1 | 766 | 0.0010221 | 1.3344e-06 | No
2020-02-22 | 2:23 | JBB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 43 | 242.814 | 0.034349 | 0.00014146 | No
2020-02-22 | 7:22 | 16660 | Urban | Unknown | Unknown | 1379 | 69 | 0.12697 | 0.0018401 | No
2020-02-22 | 7:27 | DS1226 | Urban | Asset Failure | Distribution substation | 49 | 224 | 0.014646 | 6.5386e-05 | No
2020-02-22 | 7:52 | RW1218 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 19 | 128 | 0.0080009 | 6.2507e-05 | No
2020-02-22 | 10:00 | FF1243 | Urban | Unknown | Unknown | 1 | 149 | 0.00019883 | 1.3344e-06 | No
2020-02-22 | 10:28 | W123 | Short rural | Asset Failure | Distribution substation | 75 | 125 | 0.030842 | 0.00024674 | No
2020-02-22 | 13:00 | FF1276 | Urban | Unknown | Unknown | 7 | 110 | 0.0010275 | 9.3408e-06 | No
2020-02-22 | 13:02 | JBB2 | Short rural | Unknown | Unknown | 4 | 125 | 0.0016449 | 1.3159e-05 | No
2020-02-22 | 18:48 | J499 | Urban | Unknown | Unknown | 1462 | 46.0472 | 0.089833 | 0.0019509 | No
2020-02-23 | 1:56 | 8675 | Urban | Third Party | Vehicle impact | 822 | 61 | 0.066909 | 0.0010969 | No
2020-02-23 | 3:29 | HKG2 | Short rural | Asset Failure | HV | 1458.2911 | 167.623 | 0.80418 | 0.0047976 | No
2020-02-23 | 3:29 | TM1258 | Short rural | Asset Failure | HV | 1236.7089 | 167.623 | 0.68199 | 0.0040686 | No
2020-02-23 | 6:49 | 25781 | Urban | Unknown | Unknown | 16 | 105 | 0.0022418 | 2.135e-05 | No
2020-02-23 | 16:34 | MM1382 | Urban | Asset Failure | Distribution substation | 1 | 425 | 0.00056712 | 1.3344e-06 | No
2020-02-23 | 17:55 | L591 | Short rural | Unknown | Unknown | 1 | 960 | 0.0031583 | 3.2899e-06 | No
2020-02-23 | 19:36 | 17067 | Urban | Unknown | Unknown | 6 | 68 | 0.00054443 | 8.0064e-06 | No
2020-02-23 | 21:13 | RW1218 | Short rural | Unknown | Unknown | 14 | 109 | 0.0050203 | 4.6058e-05 | No
2020-02-23 | 23:12 | 25781 | Urban | Unknown | Unknown | 6 | 96 | 0.00076861 | 8.0064e-06 | No
2020-02-24 | 1:29 | BX1222 | Urban | Asset Failure | LV | 523 | 171.3843 | 0.11961 | 0.00069789 | No
2020-02-24 | 8:10 | 9056 | Urban | Asset Failure | Distribution substation | 7 | 175.2857 | 0.0016373 | 9.3408e-06 | No
2020-02-24 | 9:12 | 35304 | Urban | Vegetation | Grow-in - NSP responsibility | 7 | 274 | 0.0025594 | 9.3408e-06 | No
2020-02-24 | 9:15 | CX1206 | Short rural | Weather |  | 2 | 108 | 0.00071061 | 6.5797e-06 | No
2020-02-24 | 9:57 | J497 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 8.75 | 0.00011515 | 1.3159e-05 | No
2020-02-24 | 10:50 | CS1243 | Urban | Asset Failure | Distribution substation | 39 | 63.8205 | 0.0033213 | 5.2042e-05 | No
2020-02-24 | 13:03 | M400 | Urban | Asset Failure | Distribution substation | 1 | 95 | 0.00012677 | 1.3344e-06 | No
2020-02-24 | 13:54 | 35696 | Short rural | Asset Failure | Distribution substation | 33 | 477 | 0.051786 | 0.00010857 | No
2020-02-24 | 14:09 | B709 | Urban | Third Party | Other | 31 | 155 | 0.0064118 | 4.1366e-05 | No
2020-02-24 | 15:27 | W185 | Short rural | Unknown | Unknown | 11 | 650.3636 | 0.023536 | 3.6188e-05 | No
2020-02-24 | 17:01 | BL1243 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 132 | 0.00086852 | 6.5797e-06 | No
2020-02-24 | 18:30 | 9055 | Urban | Unknown | Unknown | 68 | 68 | 0.0061703 | 9.0739e-05 | No
2020-02-24 | 23:12 | CX1210 | Short rural | Unknown | Unknown | 814 | 149.344 | 0.39994 | 0.0026779 | No
2020-02-25 | 3:51 | J506 | Urban | Asset Failure | Distribution substation | 40 | 521.05 | 0.027812 | 5.3376e-05 | No
2020-02-25 | 4:58 | J506 | Urban | Asset Failure | Distribution substation | 41 | 113.1707 | 0.0061916 | 5.471e-05 | No
2020-02-25 | 7:11 | J506 | Urban | Asset Failure | Distribution substation | 21 | 437.5238 | 0.01226 | 2.8022e-05 | No
2020-02-25 | 9:34 | BYB2 | Short rural | Asset Failure | Distribution substation | 24 | 134.9167 | 0.010653 | 7.8957e-05 | No
2020-02-25 | 9:45 | CJ1275 | Urban | Unknown | Unknown | 44 | 118 | 0.0069282 | 5.8714e-05 | No
2020-02-25 | 9:55 | WWB2 | Short rural | Asset Failure | Distribution substation | 35 | 19 | 0.0021878 | 0.00011515 | No
2020-02-25 | 10:49 | NM1221 | Urban | Unknown | Unknown | 12 | 104 | 0.0016653 | 1.6013e-05 | No
2020-02-25 | 10:53 | BWA2 | Short rural | Asset Failure | Distribution substation | 1 | 281 | 0.00092445 | 3.2899e-06 | No
2020-02-25 | 10:59 | 25781 | Urban | Unknown | Unknown | 16 | 196 | 0.0041847 | 2.135e-05 | No
2020-02-25 | 12:27 | 87223 | Short rural | Asset Failure | Distribution substation | 1 | 106 | 0.00034873 | 3.2899e-06 | No
2020-02-25 | 12:48 | MM1112 | Urban | Unknown | Unknown | 40 | 217 | 0.011583 | 5.3376e-05 | No
2020-02-25 | 13:00 | CJ1204 | Urban | Asset Failure | Distribution substation | 1 | 388 | 0.00051775 | 1.3344e-06 | No
2020-02-25 | 13:25 | L582 | Short rural | Asset Failure | Distribution substation | 1 | 65 | 0.00021384 | 3.2899e-06 | No
2020-02-25 | 16:11 | 25781 | Urban | Asset Failure | Distribution substation | 6 | 135 | 0.0010809 | 8.0064e-06 | No
2020-02-25 | 16:19 | J473 | Urban | Asset Failure | Distribution substation | 1 | 130 | 0.00017347 | 1.3344e-06 | No
2020-02-25 | 17:29 | BYB2 | Short rural | Asset Failure | Distribution substation | 23 | 24.3043 | 0.001839 | 7.5667e-05 | No
2020-02-25 | 18:02 | APC2 | Short rural | Asset Failure | Distribution substation | 2 | 245 | 0.001612 | 6.5797e-06 | No
2020-02-25 | 19:15 | C896 | Urban | Asset Failure | Distribution substation | 23 | 143.6522 | 0.0044089 | 3.0691e-05 | No
2020-02-25 | 21:45 | 35004 | Urban | Asset Failure | Distribution substation | 709.0348 | 114.1695 | 0.10802 | 0.00094614 | No
2020-02-25 | 21:45 | IHK2 | Urban | Asset Failure | Distribution substation | 4.9652 | 114.1695 | 0.00075644 | 6.6256e-06 | No
2020-02-25 | 22:23 | SY1242 | Urban | Unknown | Unknown | 52 | 72 | 0.004996 | 6.9389e-05 | No
2020-02-25 | 22:49 | LP1422 | Urban | Asset Failure | Distribution substation | 66 | 67 | 0.0059007 | 8.807e-05 | No
2020-02-26 | 0:33 | JBB2 | Short rural | Unknown | Unknown | 9 | 222 | 0.0065731 | 2.9609e-05 | No
2020-02-26 | 7:39 | 25773 | Urban | Asset Failure | Distribution substation | 1 | 272 | 0.00036296 | 1.3344e-06 | No
2020-02-26 | 7:42 | KC1236 | Short rural | Unknown | Unknown | 8 | 106 | 0.0027898 | 2.6319e-05 | No
2020-02-26 | 8:11 | 8799 | Short rural | Other | Probable Equipment Failure | 1 | 404 | 0.0013291 | 3.2899e-06 | No
2020-02-26 | 8:28 | C891 | Urban | Unknown | Unknown | 14 | 94 | 0.0017561 | 1.8682e-05 | No
2020-02-26 | 9:09 | CX1273 | Short rural | Asset Failure | LV | 222.432 | 169.6224 | 0.12412 | 0.00073177 | No
2020-02-26 | 9:09 | CX1232 | Short rural | Asset Failure | LV | 439.568 | 169.6224 | 0.24529 | 0.0014461 | No
2020-02-26 | 10:28 | C891 | Urban | Asset Failure | Distribution substation | 40 | 96.225 | 0.0051361 | 5.3376e-05 | No
2020-02-26 | 11:45 | CD1297 | Urban | Unknown | Unknown | 6 | 81 | 0.00064852 | 8.0064e-06 | No
2020-02-26 | 12:09 | X213 | Short rural | Other | Probable Lightning/Electrical Storm | 108 | 171.3889 | 0.060895 | 0.00035531 | No
2020-02-26 | 13:28 | 8802 | Short rural | Weather |  | 686 | 76 | 0.17152 | 0.0022568 | No
2020-02-26 | 13:30 | 8802 | Short rural | Weather |  | 837 | 75.3883 | 0.20759 | 0.0027536 | No
2020-02-26 | 14:22 | CX1210 | Short rural | Weather |  | 4 | 105 | 0.0013817 | 1.3159e-05 | No
2020-02-26 | 14:30 | BYB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 76 | 54.25 | 0.013564 | 0.00025003 | No
2020-02-26 | 14:32 | MR2206 | Urban | Asset Failure | Distribution substation | 1 | 46 | 6.1382e-05 | 1.3344e-06 | No
2020-02-26 | 16:11 | KMB2 | Short rural | Weather |  | 147 | 120.7483 | 0.058395 | 0.00048361 | No
2020-02-26 | 16:19 | ULL2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1102 | 171.2804 | 0.62096 | 0.0036254 | No
2020-02-26 | 16:22 | SXA2 | Short rural | Unknown | Unknown | 134 | 117 | 0.051578 | 0.00044084 | No
2020-02-26 | 16:32 | ULH2 | Short rural | Weather |  | 809 | 172.5661 | 0.45928 | 0.0026615 | No
2020-02-26 | 17:21 | MVB2 | Short rural | Unknown | Unknown | 6 | 152 | 0.0030004 | 1.9739e-05 | No
2020-02-26 | 18:21 | KVA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 30 | 1026 | 0.10126 | 9.8696e-05 | No
2020-02-26 | 18:39 | SHD2 | Short rural | Asset Failure | HV | 324 | 108 | 0.11512 | 0.0010659 | No
2020-02-26 | 18:48 | BYB2 | Short rural | Unknown | Unknown | 28 | 242 | 0.022292 | 9.2116e-05 | No
2020-02-26 | 19:18 | X213 | Short rural | Animal | Animal Impact | 1 | 81 | 0.00026648 | 3.2899e-06 | No
2020-02-26 | 20:02 | CV1284 | Urban | Asset Failure | LV | 48 | 69 | 0.0044195 | 6.4051e-05 | No
2020-02-26 | 20:04 | RD1292 | Urban | Asset Failure | Distribution substation | 6 | 129.8333 | 0.0010395 | 8.0064e-06 | No
2020-02-26 | 21:13 | A046 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 328 | 106.564 | 0.11499 | 0.0010791 | No
2020-02-27 | 1:47 | BWH2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1182 | 80.2699 | 0.31214 | 0.0038886 | No
2020-02-27 | 4:34 | CX1210 | Short rural | Weather |  | 2 | 321 | 0.0021121 | 6.5797e-06 | No
2020-02-27 | 9:02 | A046 | Short rural | Unknown | Unknown | 2 | 94 | 0.00061849 | 6.5797e-06 | No
2020-02-27 | 11:49 | WL1236 | Urban | Other | Probable Accidental Damage - Vehicle High Load | 71 | 135 | 0.01279 | 9.4742e-05 | No
2020-02-27 | 12:06 | 5495 | Urban | Asset Failure | Distribution substation | 1 | 316 | 0.00042167 | 1.3344e-06 | No
2020-02-27 | 13:00 | 35765 | Urban | Third Party | Vehicle impact | 33 | 301.8182 | 0.013291 | 4.4035e-05 | No
2020-02-27 | 13:09 | NA1225 | Short rural | Animal | Animal Impact | 3 | 108 | 0.0010659 | 9.8696e-06 | No
2020-02-27 | 15:27 | 68181 | Urban | Asset Failure | Distribution substation | 1 | 263 | 0.00035095 | 1.3344e-06 | No
2020-02-27 | 17:36 | T838 | Short rural | Asset Failure | Distribution substation | 1 | 62 | 0.00020397 | 3.2899e-06 | No
2020-02-27 | 18:18 | CLA2 | Short rural | Other | Probable Birds | 1324 | 11.5461 | 0.050292 | 0.0043558 | No
2020-02-27 | 18:42 | KC1236 | Short rural | Unknown | Unknown | 8 | 840 | 0.022108 | 2.6319e-05 | No
2020-02-27 | 18:54 | RBC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 504 | 57 | 0.094511 | 0.0016581 | No
2020-02-27 | 20:48 | RBC2 | Short rural | Asset Failure | HV | 152 | 37.6447 | 0.018825 | 0.00050006 | No
2020-02-27 | 21:25 | T828 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 220 | 0.00072377 | 3.2899e-06 | No
2020-02-27 | 23:45 | S788 | Short rural | Asset Failure | Distribution substation | 45 | 226.8444 | 0.033583 | 0.00014804 | No
2020-02-28 | 1:37 | W127 | Short rural | Asset Failure | HV | 1145 | 108.3511 | 0.40815 | 0.0037669 | No
2020-02-28 | 7:22 | MR2206 | Urban | Asset Failure | Distribution substation | 1 | 554 | 0.00073926 | 1.3344e-06 | No
2020-02-28 | 7:38 | APB2 | Short rural | Asset Failure | Distribution substation | 13 | 197 | 0.0084253 | 4.2768e-05 | No
2020-02-28 | 8:37 | CV1284 | Urban | Animal | Animal Impact | 90 | 224 | 0.026901 | 0.0001201 | No
2020-02-28 | 10:34 | W163 | Short rural | Unknown | Unknown | 1 | 69 | 0.000227 | 3.2899e-06 | No
2020-02-28 | 11:14 | 8677 | Urban | Third Party | Vehicle impact | 427 | 60.2131 | 0.034309 | 0.00056979 | No
2020-02-28 | 13:36 | SXA2 | Short rural | Asset Failure | Distribution substation | 58 | 25 | 0.0047703 | 0.00019081 | No
2020-02-28 | 15:15 | TM1258 | Short rural | Other | Isolation Request by EE | 51 | 23 | 0.003859 | 0.00016778 | No
2020-02-28 | 17:40 | 10241 | Short rural | Asset Failure | Distribution substation | 2 | 88 | 0.00057902 | 6.5797e-06 | No
2020-02-28 | 20:36 | 9033 | Urban | Vegetation | Grow-in - NSP responsibility | 1995 | 27 | 0.071877 | 0.0026621 | No
2020-02-28 | 21:38 | L947 | Short rural | Vegetation | Grow-in - NSP responsibility | 217 | 99 | 0.070676 | 0.0007139 | No
2020-02-29 | 7:17 | J465 | Urban | Asset Failure | Distribution substation | 1 | 274 | 0.00036563 | 1.3344e-06 | No
2020-02-29 | 7:42 | JBB2 | Short rural | Asset Failure | Distribution substation | 1 | 84 | 0.00027635 | 3.2899e-06 | No
2020-02-29 | 8:09 | 41535 | Urban | Third Party | Vehicle impact | 793 | 107.0177 | 0.11324 | 0.0010582 | No
2020-02-29 | 9:08 | MM1142 | Urban | Other | Probable Accidental Damage Excavation | 25 | 172 | 0.0057379 | 3.336e-05 | No
2020-02-29 | 10:41 | J512 | Urban | Asset Failure | Distribution substation | 15 | 148 | 0.0029624 | 2.0016e-05 | No
2020-02-29 | 11:08 | MVB2 | Short rural | Unknown | Unknown | 1 | 219 | 0.00072048 | 3.2899e-06 | No
2020-02-29 | 11:25 | 35693 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 148 | 0.0004869 | 3.2899e-06 | No
2020-02-29 | 13:50 | J512 | Urban | Asset Failure | Distribution substation | 1 | 257 | 0.00034294 | 1.3344e-06 | No
2020-02-29 | 16:09 | JBB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 43 | 79.9767 | 0.011314 | 0.00014146 | No
2020-02-29 | 16:55 | S738 | Short rural | Vegetation | Grow-in - NSP responsibility | 17 | 126 | 0.0070469 | 5.5928e-05 | No
2020-02-29 | 17:21 | RBB2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 83 | 0.00027306 | 3.2899e-06 | No
2020-02-29 | 21:55 | NA1270 | Short rural | Unknown | Unknown | 2 | 758 | 0.0049874 | 6.5797e-06 | No
2020-02-29 | 22:42 | 9052 | Urban | Asset Failure | Distribution substation | 142 | 160 | 0.030318 | 0.00018948 | No
2020-03-01 | 1:39 | BX1232 | Urban | Animal | Animal Impact | 531 | 107.7797 | 0.076369 | 0.00070857 | No
2020-03-01 | 7:59 | BWA2 | Short rural | Asset Failure | Distribution substation | 57 | 73 | 0.013689 | 0.00018752 | No
2020-03-01 | 14:47 | WQ1219 | Urban | Asset Failure | Distribution substation | 12 | 115 | 0.0018415 | 1.6013e-05 | No
2020-03-01 | 16:45 | D810 | Short rural | Other | Isolation Request by EE | 17 | 15 | 0.00083892 | 5.5928e-05 | No
2020-03-01 | 17:54 | J497 | Short rural | Unknown | Unknown | 19 | 817 | 0.051069 | 6.2507e-05 | No
2020-03-01 | 18:05 | ULC2 | Short rural | Unknown | Unknown | 8 | 104 | 0.0027372 | 2.6319e-05 | No
2020-03-01 | 18:22 | C852 | Urban | Asset Failure | Distribution substation | 39 | 943.1795 | 0.049085 | 5.2042e-05 | No
2020-03-01 | 18:44 | HBB2 | Short rural | Asset Failure | Distribution substation | 4 | 173 | 0.0022766 | 1.3159e-05 | No
2020-03-01 | 19:36 | RD1292 | Urban | Vegetation | Grow-in - NSP responsibility | 93 | 58 | 0.0071977 | 0.0001241 | No
2020-03-01 | 19:59 | 8735 | Urban | Vegetation | Grow-in - NSP responsibility | 93 | 17.3118 | 0.0021484 | 0.0001241 | No
2020-03-01 | 20:06 | D810 | Short rural | Other | Isolation Request by EE | 17 | 15 | 0.00083892 | 5.5928e-05 | No
2020-03-01 | 20:29 | C852 | Urban | Asset Failure | Distribution substation | 7 | 8 | 7.4726e-05 | 9.3408e-06 | No
2020-03-01 | 22:26 | 46397 | Urban | Asset Failure | Distribution substation | 31 | 60 | 0.002482 | 4.1366e-05 | No
2020-03-02 | 8:07 | CD1234 | Short rural | Asset Failure | Distribution substation | 5 | 97 | 0.0015956 | 1.6449e-05 | No
2020-03-02 | 8:20 | J495 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 400.4 | 0.0065863 | 1.6449e-05 | No
2020-03-02 | 8:58 | J497 | Short rural | Asset Failure | Distribution substation | 1 | 335 | 0.0011021 | 3.2899e-06 | No
2020-03-02 | 9:32 | ULE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 22 | 212.5909 | 0.015387 | 7.2377e-05 | No
2020-03-02 | 12:27 | KC1236 | Short rural | Unknown | Unknown | 11 | 187 | 0.0067672 | 3.6188e-05 | No
2020-03-02 | 13:07 | YYB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 919 | 62.6333 | 0.18936 | 0.0030234 | No
2020-03-02 | 13:34 | ULC2 | Short rural | Unknown | Unknown | 8 | 201.75 | 0.0053098 | 2.6319e-05 | No
2020-03-02 | 13:55 | RW1281 | Short rural | Asset Failure | Distribution substation | 1 | 183 | 0.00060204 | 3.2899e-06 | No
2020-03-02 | 14:46 | MM1352 | Short rural | Unknown | Unknown | 33 | 44.9394 | 0.0048789 | 0.00010857 | No
2020-03-02 | 14:49 | 19870 | Urban | Asset Failure | Distribution substation | 51 | 151 | 0.010276 | 6.8054e-05 | No
2020-03-02 | 15:51 | SG1209 | Urban | Asset Failure | Distribution substation | 66 | 119.0303 | 0.010483 | 8.807e-05 | No
2020-03-02 | 15:55 | SG1209 | Urban | Asset Failure | Distribution substation | 29 | 118.1379 | 0.0045717 | 3.8698e-05 | No
2020-03-02 | 16:51 | MR2232 | Short rural | Vegetation | Grow-in - NSP responsibility | 177 | 192.4407 | 0.11206 | 0.00058231 | No
2020-03-02 | 17:35 | 8648 | Urban | Vegetation | Grow-in - NSP responsibility | 651 | 128.318 | 0.11147 | 0.00086869 | No
2020-03-02 | 17:37 | T868 | Short rural | Vegetation | Grow-in - NSP responsibility | 935 | 108.8963 | 0.33497 | 0.003076 | No
2020-03-02 | 18:06 | J481 | Urban | Asset Failure | Distribution substation | 1 | 307 | 0.00040966 | 1.3344e-06 | No
2020-03-02 | 18:38 | SZ1242 | Short rural | Asset Failure | LV | 53 | 277.8113 | 0.04844 | 0.00017436 | No
2020-03-02 | 19:42 | DS1257 | Urban | Asset Failure | Distribution substation | 28 | 524.6071 | 0.019601 | 3.7363e-05 | No
2020-03-03 | 7:34 | MVC2 | Short rural | Asset Failure | HV | 1 | 544 | 0.0017897 | 3.2899e-06 | No
2020-03-03 | 11:44 | HBB2 | Short rural | Asset Failure | Distribution substation | 1 | 147 | 0.00048361 | 3.2899e-06 | No
2020-03-03 | 12:20 | X213 | Short rural | Unknown | Unknown | 108 | 168.4815 | 0.059862 | 0.00035531 | No
2020-03-03 | 14:03 | S741 | Short rural | Third Party | Vehicle impact | 16 | 450 | 0.023687 | 5.2638e-05 | No
2020-03-03 | 15:09 | ULE2 | Short rural | Asset Failure | Distribution substation | 2 | 114 | 0.00075009 | 6.5797e-06 | No
2020-03-03 | 15:39 | NA1236 | Short rural | Asset Failure | Distribution substation | 5 | 198 | 0.003257 | 1.6449e-05 | No
2020-03-03 | 15:56 | WWB2 | Short rural | Other | Probable Accidental Damage - Vehicle Impact | 577 | 31 | 0.058846 | 0.0018983 | No
2020-03-03 | 15:58 | 55879 | Urban | Unknown | Unknown | 1 | 153 | 0.00020416 | 1.3344e-06 | No
2020-03-03 | 16:02 | WWB2 | Short rural | Third Party | Vehicle impact | 424 | 23 | 0.032083 | 0.0013949 | No
2020-03-03 | 17:00 | MVB2 | Short rural | Unknown | Unknown | 4 | 309 | 0.0040663 | 1.3159e-05 | No
2020-03-03 | 19:11 | NA1281 | Urban | Unknown | Unknown | 9 | 285 | 0.0034227 | 1.201e-05 | No
2020-03-03 | 19:58 | S738 | Short rural | Vegetation | Grow-in - NSP responsibility | 36 | 1456.5 | 0.1725 | 0.00011844 | No
2020-03-03 | 20:28 | J497 | Short rural | Asset Failure | Distribution substation | 57 | 332 | 0.062257 | 0.00018752 | No
2020-03-03 | 21:00 | WWF2 | Urban | Weather |  | 26 | 12 | 0.00041633 | 3.4694e-05 | No
2020-03-03 | 21:33 | WWE2 | Urban | Weather |  | 36 | 16 | 0.00076861 | 4.8038e-05 | No
2020-03-03 | 22:55 | J496 | Urban | Asset Failure | HV | 85 | 38 | 0.0043101 | 0.00011342 | No
2020-03-03 | 23:39 | PCD2 | Urban | Weather |  | 27 | 24 | 0.00086469 | 3.6029e-05 | No
2020-03-03 | 23:51 | WWF2 | Urban | Weather |  | 59 | 61.7288 | 0.0048599 | 7.873e-05 | No
2020-03-04 | 0:23 | PK1225 | Urban | Weather |  | 43 | 47.6744 | 0.0027355 | 5.7379e-05 | No
2020-03-04 | 1:29 | ULL2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1102 | 176.4011 | 0.63953 | 0.0036254 | No
2020-03-04 | 4:45 | BX1362 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 158 | 0.0005198 | 3.2899e-06 | No
2020-03-04 | 5:32 | BDH2 | Short rural | Asset Failure | Distribution substation | 1 | 309 | 0.0010166 | 3.2899e-06 | No
2020-03-04 | 5:52 | BX1362 | Short rural | Vegetation | Grow-in - NSP responsibility | 320 | 76.05 | 0.080062 | 0.0010528 | No
2020-03-04 | 6:22 | S737 | Short rural | Vegetation | Grow-in - NSP responsibility | 14 | 193 | 0.0088892 | 4.6058e-05 | No
2020-03-04 | 6:49 | SXD2 | Short rural | Asset Failure | Distribution substation | 43 | 250.2326 | 0.035399 | 0.00014146 | No
2020-03-04 | 7:29 | SWC2 | Urban | Asset Failure | Distribution substation | 27 | 107 | 0.0038551 | 3.6029e-05 | No
2020-03-04 | 7:55 | BYG2 | Short rural | Vegetation | Grow-in - NSP responsibility | 94 | 101.5638 | 0.031408 | 0.00030925 | No
2020-03-04 | 8:51 | 35304 | Urban | Asset Failure | HV | 214 | 45.6262 | 0.013029 | 0.00028556 | No
2020-03-04 | 9:09 | MG1282 | Short rural | Asset Failure | Distribution substation | 1 | 279 | 0.00091787 | 3.2899e-06 | No
2020-03-04 | 9:58 | J459 | Short rural | Asset Failure | Distribution substation | 1 | 171 | 0.00056257 | 3.2899e-06 | No
2020-03-04 | 10:05 | FT1205 | Short rural | Asset Failure | Distribution substation | 1 | 144 | 0.00047374 | 3.2899e-06 | No
2020-03-04 | 10:17 | X213 | Short rural | Asset Failure | HV | 6 | 51 | 0.0010067 | 1.9739e-05 | No
2020-03-04 | 11:45 | NM1221 | Urban | Asset Failure | Distribution substation | 11 | 160.5455 | 0.0023565 | 1.4678e-05 | No
2020-03-04 | 12:23 | 19816 | Urban | Vegetation | Grow-in - NSP responsibility | 4 | 423 | 0.0022578 | 5.3376e-06 | No
2020-03-04 | 13:21 | 35771 | Urban | Third Party | Dig-in | 156 | 55.6731 | 0.011589 | 0.00020817 | No
2020-03-04 | 14:04 | NWE2 | Urban | Other | Probable Rain incl. Mist and Fog | 1 | 80 | 0.00010675 | 1.3344e-06 | No
2020-03-04 | 14:33 | 8680 | Urban | Asset Failure | LV | 1438 | 54.8574 | 0.10526 | 0.0019189 | No
2020-03-04 | 20:45 | HBA2 | Short rural | Asset Failure | Distribution substation | 1 | 190 | 0.00062507 | 3.2899e-06 | No
2020-03-05 | 7:14 | DS1245 | Short rural | Asset Failure | HV | 644.0944 | 103.6653 | 0.21966 | 0.002119 | No
2020-03-05 | 7:14 | DS1290 | Urban | Asset Failure | HV | 1318.9056 | 103.6653 | 0.18245 | 0.0017599 | No
2020-03-05 | 7:46 | NN1285 | Short rural | Unknown | Unknown | 1 | 64 | 0.00021055 | 3.2899e-06 | No
2020-03-05 | 9:11 | L591 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 1869.2 | 0.030747 | 1.6449e-05 | No
2020-03-05 | 9:53 | SXA2 | Short rural | Weather |  | 33 | 212 | 0.023016 | 0.00010857 | No
2020-03-05 | 11:07 | 9027 | Urban | Asset Failure | Distribution substation | 2 | 602 | 0.0016066 | 2.6688e-06 | No
2020-03-05 | 11:18 | 27030 | Urban | Unknown | Unknown | 11 | 69 | 0.0010128 | 1.4678e-05 | No
2020-03-05 | 11:36 | TM1284 | Short rural | Third Party | Other | 29 | 37.3448 | 0.0035629 | 9.5406e-05 | No
2020-03-05 | 11:47 | RW1281 | Short rural | Other | Isolation Request by EE | 1 | 12 | 3.9478e-05 | 3.2899e-06 | No
2020-03-05 | 13:22 | BK1299 | Short rural | Unknown | Unknown | 428 | 60.2827 | 0.084882 | 0.0014081 | No
2020-03-05 | 14:16 | KC1221 | Short rural | Unknown | Unknown | 560 | 87.4786 | 0.16116 | 0.0018423 | No
2020-03-05 | 14:36 | RBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 23 | 123 | 0.009307 | 7.5667e-05 | No
2020-03-05 | 16:08 | 87222 | Long rural | Unknown | Unknown | 1 | 164 | 0.52229 | 0.0031847 | No
2020-03-05 | 16:26 | PCE2 | Urban | Asset Failure | HV | 994 | 83.1901 | 0.11034 | 0.0013264 | No
2020-03-05 | 18:02 | WP1205 | Urban | Other | Fault within LV customers installation - Defective Equipment | 1 | 117 | 0.00015612 | 1.3344e-06 | No
2020-03-05 | 19:03 | APH2 | Urban | Asset Failure | Distribution substation | 30 | 274.4667 | 0.010987 | 4.0032e-05 | No
2020-03-05 | 21:10 | 35418 | Short rural | Vegetation | Grow-in - NSP responsibility | 26 | 483.2308 | 0.041334 | 8.5536e-05 | No
2020-03-06 | 0:18 | B212 | Urban | Vegetation | Grow-in - NSP responsibility | 9.0096 | 93.4779 | 0.0011238 | 1.2022e-05 | No
2020-03-06 | 0:18 | B201 | Urban | Vegetation | Grow-in - NSP responsibility | 103.9904 | 93.4779 | 0.012971 | 0.00013876 | No
2020-03-06 | 1:18 | L513 | Urban | Asset Failure | Distribution substation | 16 | 1077 | 0.022994 | 2.135e-05 | No
2020-03-06 | 2:18 | JS1152 | Urban | Asset Failure | Distribution substation | 23 | 379 | 0.011632 | 3.0691e-05 | No
2020-03-06 | 3:22 | RS1207 | Urban | Vegetation | Grow-in - NSP responsibility | 1234 | 83.684 | 0.1378 | 0.0016466 | No
2020-03-06 | 4:59 | SY1232 | Urban | Asset Failure | Distribution substation | 17 | 570 | 0.01293 | 2.2685e-05 | No
2020-03-06 | 8:09 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 15 | 57 | 0.0028128 | 4.9348e-05 | No
2020-03-06 | 9:41 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 40 | 0.00052638 | 1.3159e-05 | No
2020-03-06 | 9:53 | C869 | Urban | Asset Failure | Distribution substation | 7 | 195.2857 | 0.0018241 | 9.3408e-06 | No
2020-03-06 | 10:06 | D814 | Short rural | Asset Failure | Distribution substation | 2 | 525 | 0.0034544 | 6.5797e-06 | No
2020-03-06 | 10:28 | A343 | Urban | Asset Failure | HV | 427 | 64.0258 | 0.036481 | 0.00056979 | No
2020-03-06 | 10:43 | L540 | Urban | Asset Failure | HV | 437 | 130.8032 | 0.076276 | 0.00058313 | No
2020-03-06 | 10:49 | T873 | Short rural | Asset Failure | Distribution substation | 20 | 86 | 0.0056586 | 6.5797e-05 | No
2020-03-06 | 12:20 | 55891 | Urban | Unknown | Unknown | 32 | 145 | 0.0061916 | 4.2701e-05 | No
2020-03-06 | 12:28 | SN1208 | Short rural | Vegetation | Grow-in - NSP responsibility | 9 | 78.1111 | 0.0023128 | 2.9609e-05 | No
2020-03-06 | 14:08 | L541 | Urban | Network business | Switching or protection error | 5 | 136 | 0.00090739 | 6.672e-06 | No
2020-03-06 | 14:24 | R260 | Short rural | Vegetation | Grow-in - NSP responsibility | 67 | 179 | 0.039455 | 0.00022042 | No
2020-03-06 | 15:49 | BDG2 | Short rural | Asset Failure | HV | 5 | 65 | 0.0010692 | 1.6449e-05 | No
2020-03-06 | 19:29 | DS1256 | Urban | Animal | Animal Impact | 93 | 34 | 0.0042194 | 0.0001241 | No
2020-03-06 | 20:50 | X867 | Urban | Asset Failure | HV | 1429 | 45.9048 | 0.087534 | 0.0019069 | No
2020-03-06 | 21:42 | NE1212 | Urban | Asset Failure | Distribution substation | 1 | 675 | 0.00090072 | 1.3344e-06 | No
2020-03-07 | 6:06 | DS1257 | Urban | Weather |  | 3 | 451.3333 | 0.0018068 | 4.0032e-06 | No
2020-03-07 | 7:43 | KVA2 | Short rural | Weather |  | 1 | 259 | 0.00085207 | 3.2899e-06 | No
2020-03-07 | 8:10 | CLC2 | Short rural | Weather |  | 1 | 122 | 0.00040136 | 3.2899e-06 | No
2020-03-07 | 9:01 | RV1298 | Urban | Unknown | Unknown | 134 | 41 | 0.0073312 | 0.00017881 | No
2020-03-07 | 9:38 | FT1202 | Urban | Asset Failure | Distribution substation | 1 | 51 | 6.8054e-05 | 1.3344e-06 | No
2020-03-07 | 10:17 | 25741 | Short rural | Third Party | Unauthorised access | 26 | 243 | 0.020785 | 8.5536e-05 | No
2020-03-07 | 12:27 | J504 | Urban | Asset Failure | Distribution substation | 1 | 283 | 0.00037763 | 1.3344e-06 | No
2020-03-07 | 14:27 | NA1218 | Urban | Asset Failure | Distribution substation | 14 | 158 | 0.0029517 | 1.8682e-05 | No
2020-03-07 | 18:39 | MG1286 | Short rural | Asset Failure | LV | 66 | 122 | 0.02649 | 0.00021713 | No
2020-03-07 | 21:15 | CN1239 | Urban | Asset Failure | HV | 359 | 74.7409 | 0.035805 | 0.00047905 | No
2020-03-08 | 3:16 | WX1210 | Urban | Asset Failure | LV | 40 | 56.875 | 0.0030358 | 5.3376e-05 | No
2020-03-08 | 7:41 | T873 | Short rural | Asset Failure | Distribution substation | 1 | 367 | 0.0012074 | 3.2899e-06 | No
2020-03-08 | 7:53 | CV1239 | Urban | Asset Failure | Distribution substation | 1 | 16 | 2.135e-05 | 1.3344e-06 | No
2020-03-08 | 7:54 | CV1239 | Urban | Asset Failure | Distribution substation | 1 | 28 | 3.7363e-05 | 1.3344e-06 | No
2020-03-08 | 8:30 | MVE2 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 16 | 209.75 | 0.011041 | 5.2638e-05 | No
2020-03-08 | 9:02 | CJ1275 | Urban | Vegetation | Grow-in - NSP responsibility | 48 | 189.9375 | 0.012166 | 6.4051e-05 | No
2020-03-08 | 11:05 | ULJ2 | Urban | Asset Failure | Distribution substation | 1 | 168 | 0.00022418 | 1.3344e-06 | No
2020-03-08 | 13:20 | 25780 | Urban | Asset Failure | Distribution substation | 28 | 123.4643 | 0.004613 | 3.7363e-05 | No
2020-03-08 | 18:47 | A095 | Short rural | Unknown | Unknown | 1 | 69 | 0.000227 | 3.2899e-06 | No
2020-03-08 | 19:11 | W111 | Short rural | Asset Failure | Distribution substation | 28 | 121.8571 | 0.011225 | 9.2116e-05 | No
2020-03-08 | 19:29 | CLA2 | Short rural | Unknown | Unknown | 1 | 107 | 0.00035202 | 3.2899e-06 | No
2020-03-09 | 10:31 | CX1232 | Short rural | Third Party | Other | 31 | 134.9677 | 0.013765 | 0.00010199 | No
2020-03-09 | 11:32 | A095 | Short rural | Unknown | Unknown | 1 | 168 | 0.0005527 | 3.2899e-06 | No
2020-03-09 | 12:30 | MVF2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 3000.5 | 0.019742 | 6.5797e-06 | No
2020-03-09 | 13:08 | 87220 | Short rural | Asset Failure | Distribution substation | 2 | 84.5 | 0.00055599 | 6.5797e-06 | No
2020-03-09 | 13:24 | SG1250 | Urban | Third Party | Vehicle impact | 80 | 734.1 | 0.078367 | 0.00010675 | No
2020-03-09 | 16:42 | CD1297 | Urban | Asset Failure | Distribution substation | 37 | 176.2973 | 0.0087043 | 4.9373e-05 | No
2020-03-09 | 22:02 | CD1297 | Urban | Asset Failure | Distribution substation | 1 | 62 | 8.2733e-05 | 1.3344e-06 | No
2020-03-09 | 23:58 | JS1122 | Short rural | Third Party | Vehicle impact | 244 | 101.3525 | 0.081358 | 0.00080273 | No
2020-03-10 | 6:22 | A095 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 2 | 238 | 0.001566 | 6.5797e-06 | No
2020-03-10 | 7:37 | SG1247 | Urban | Asset Failure | Distribution substation | 5 | 362.8 | 0.0024206 | 6.672e-06 | No
2020-03-10 | 9:16 | 8769 | Urban | Asset Failure | Distribution substation | 1 | 126 | 0.00016813 | 1.3344e-06 | No
2020-03-10 | 12:45 | W124 | Short rural | Asset Failure | Distribution substation | 1 | 561 | 0.0018456 | 3.2899e-06 | No
2020-03-10 | 15:48 | NL1182 | Urban | Unknown | Unknown | 18 | 48.3889 | 0.0011623 | 2.4019e-05 | No
2020-03-10 | 20:35 | B211 | Urban | Asset Failure | Distribution substation | 66 | 191 | 0.016821 | 8.807e-05 | No
2020-03-11 | 9:10 | MR2292 | Urban | Vegetation | Grow-in - NSP responsibility | 4 | 126 | 0.00067254 | 5.3376e-06 | No
2020-03-11 | 9:34 | T831 | Short rural | Asset Failure | Distribution substation | 37 | 127.3243 | 0.015499 | 0.00012172 | No
2020-03-11 | 10:49 | OA1207 | Short rural | Other | Probable Equipment Failure | 1 | 171 | 0.00056257 | 3.2899e-06 | No
2020-03-11 | 14:17 | PCB2 | Short rural | Asset Failure | Distribution substation | 31 | 264.2258 | 0.026947 | 0.00010199 | No
2020-03-11 | 17:12 | MVB2 | Short rural | Unknown | Unknown | 1 | 2643 | 0.0086951 | 3.2899e-06 | No
2020-03-11 | 18:50 | MG1208 | Short rural | Asset Failure | Distribution substation | 1 | 335 | 0.0011021 | 3.2899e-06 | No
2020-03-12 | 11:05 | J474 | Short rural | Third Party | Dig-in | 23 | 685 | 0.051832 | 7.5667e-05 | No
2020-03-12 | 15:38 | NA1207 | Short rural | Asset Failure | Distribution substation | 23 | 245.3043 | 0.018561 | 7.5667e-05 | No
2020-03-12 | 15:47 | 35827 | Short rural | Asset Failure | Distribution substation | 2 | 230 | 0.0015133 | 6.5797e-06 | No
2020-03-12 | 15:57 | 4860 | Urban | Other | Fire | 19 | 452.9474 | 0.011484 | 2.5354e-05 | No
2020-03-12 | 16:46 | BWH2 | Short rural | Unknown | Unknown | 2 | 99 | 0.00065139 | 6.5797e-06 | No
2020-03-12 | 16:51 | CV1284 | Urban | Unknown | Unknown | 60 | 159 | 0.01273 | 8.0064e-05 | No
2020-03-12 | 17:11 | ULE2 | Short rural | Unknown | Unknown | 6 | 100 | 0.0019739 | 1.9739e-05 | No
2020-03-12 | 18:57 | RV1298 | Urban | Unknown | Unknown | 134 | 114 | 0.020384 | 0.00017881 | No
2020-03-13 | 0:22 | SWC2 | Urban | Unknown | Unknown | 35 | 390 | 0.018215 | 4.6704e-05 | No
2020-03-13 | 0:40 | HR1276 | Urban | Unknown | Unknown | 14 | 74 | 0.0013824 | 1.8682e-05 | No
2020-03-13 | 2:15 | BL1232 | Short rural | Animal | Animal Impact | 1611 | 159.3904 | 0.84476 | 0.0053 | No
2020-03-13 | 10:12 | W127 | Short rural | Unknown | Unknown | 67 | 49.0448 | 0.01081 | 0.00022042 | No
2020-03-13 | 12:33 | A346 | Urban | Third Party | Other | 1 | 160 | 0.0002135 | 1.3344e-06 | No
2020-03-13 | 13:46 | KC1262 | Short rural | Asset Failure | Distribution substation | 5 | 265 | 0.0043591 | 1.6449e-05 | No
2020-03-13 | 16:12 | T872 | Urban | Asset Failure | Distribution substation | 1 | 257 | 0.00034294 | 1.3344e-06 | No
2020-03-13 | 16:51 | WD1210 | Short rural | Animal | Animal Impact | 3 | 77 | 0.00075996 | 9.8696e-06 | No
2020-03-13 | 18:24 | SXB2 | Short rural | Asset Failure | HV | 283 | 139.5477 | 0.12992 | 0.00093103 | No
2020-03-13 | 18:38 | CN1221 | Urban | Unknown | Unknown | 4 | 49 | 0.00026154 | 5.3376e-06 | No
2020-03-14 | 2:29 | SWC2 | Urban | Unknown | Unknown | 52 | 252 | 0.017486 | 6.9389e-05 | No
2020-03-14 | 6:51 | AZ1205 | Urban | Third Party | Vehicle impact | 88 | 764.5682 | 0.089781 | 0.00011743 | No
2020-03-14 | 9:16 | D810 | Short rural | Vegetation | Grow-in - NSP responsibility | 117 | 167.9829 | 0.064659 | 0.00038491 | No
2020-03-14 | 10:02 | J483 | Urban | Asset Failure | Distribution substation | 1 | 27 | 3.6029e-05 | 1.3344e-06 | No
2020-03-14 | 10:21 | 35702 | Urban | Asset Failure | Distribution substation | 41 | 1008 | 0.055148 | 5.471e-05 | No
2020-03-14 | 11:46 | PK1221 | Urban | Asset Failure | Distribution substation | 1 | 80 | 0.00010675 | 1.3344e-06 | No
2020-03-14 | 12:36 | HBB2 | Short rural | Asset Failure | Distribution substation | 87 | 94 | 0.026905 | 0.00028622 | No
2020-03-14 | 13:49 | PK1221 | Urban | Asset Failure | HV | 1520 | 93.8184 | 0.19029 | 0.0020283 | No
2020-03-14 | 14:31 | SV1142 | Urban | Asset Failure | Distribution substation | 1 | 186 | 0.0002482 | 1.3344e-06 | No
2020-03-14 | 19:03 | S737 | Short rural | Vegetation | Grow-in - NSP responsibility | 8 | 48 | 0.0012633 | 2.6319e-05 | No
2020-03-14 | 22:08 | BK1251 | Short rural | Vegetation | Grow-in - NSP responsibility | 108 | 429.3519 | 0.15255 | 0.00035531 | No
2020-03-15 | 3:48 | W111 | Short rural | Unknown | Unknown | 3 | 246 | 0.0024279 | 9.8696e-06 | No
2020-03-15 | 9:52 | T828 | Short rural | Asset Failure | Distribution substation | 3 | 155 | 0.0015298 | 9.8696e-06 | No
2020-03-15 | 11:52 | JBB2 | Short rural | Asset Failure | Distribution substation | 1 | 209 | 0.00068758 | 3.2899e-06 | No
2020-03-15 | 14:37 | X871 | Urban | Asset Failure | Distribution substation | 1 | 220 | 0.00029357 | 1.3344e-06 | No
2020-03-16 | 6:27 | HR1276 | Urban | Asset Failure | Distribution substation | 48 | 342.6667 | 0.021948 | 6.4051e-05 | No
2020-03-16 | 7:19 | 27029 | Short rural | Overload |  | 16 | 104 | 0.0054743 | 5.2638e-05 | No
2020-03-16 | 11:47 | SY1232 | Urban | Unknown | Unknown | 2 | 88 | 0.00023485 | 2.6688e-06 | No
2020-03-16 | 13:48 | R260 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 218 | 0.0014344 | 6.5797e-06 | No
2020-03-16 | 13:56 | 57444 | Short rural | Asset Failure | LV | 13 | 420.0769 | 0.017966 | 4.2768e-05 | No
2020-03-16 | 15:27 | R260 | Short rural | Network business | Switching or protection error | 65 | 6.1231 | 0.0013094 | 0.00021384 | No
2020-03-16 | 18:14 | X867 | Urban | Unknown | Unknown | 40 | 70 | 0.0037363 | 5.3376e-05 | No
2020-03-17 | 3:44 | 35418 | Short rural | Vegetation | Grow-in - NSP responsibility | 10 | 747.2 | 0.024582 | 3.2899e-05 | No
2020-03-17 | 7:37 | ULH2 | Short rural | Unknown | Unknown | 7 | 90 | 0.0020726 | 2.3029e-05 | No
2020-03-17 | 8:58 | NN1262 | Urban | Asset Failure | Distribution substation | 1 | 47 | 6.2717e-05 | 1.3344e-06 | No
2020-03-17 | 9:48 | MG1267 | Short rural | Other | Isolation Request by EE | 6 | 16.3333 | 0.00032241 | 1.9739e-05 | No
2020-03-17 | 10:12 | NA1207 | Short rural | Unknown | Unknown | 2 | 74.5 | 0.00049019 | 6.5797e-06 | No
2020-03-17 | 10:59 | J497 | Short rural | Asset Failure | Distribution substation | 28 | 21.25 | 0.0019575 | 9.2116e-05 | No
2020-03-17 | 11:34 | MVC2 | Short rural | Other | Isolation Request by EE | 17 | 15 | 0.00083892 | 5.5928e-05 | No
2020-03-17 | 14:03 | MVB2 | Short rural | Other | Isolation Request by EE | 24 | 10 | 0.00078957 | 7.8957e-05 | No
2020-03-17 | 14:53 | 35816 | Short rural | Asset Failure | Distribution substation | 6 | 117 | 0.0023095 | 1.9739e-05 | No
2020-03-17 | 15:23 | J460 | Urban | Asset Failure | LV | 54.7365 | 120.8747 | 0.0088287 | 7.304e-05 | No
2020-03-17 | 15:23 | J473 | Urban | Asset Failure | LV | 743.2635 | 120.8747 | 0.11988 | 0.00099181 | No
2020-03-17 | 15:52 | NM1258 | Urban | Asset Failure | Distribution substation | 102 | 49.6569 | 0.0067587 | 0.00013611 | No
2020-03-17 | 17:19 | H745 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 97 | 0.00063823 | 6.5797e-06 | No
2020-03-17 | 19:47 | RBA2 | Short rural | Asset Failure | Distribution substation | 1 | 81 | 0.00026648 | 3.2899e-06 | No
2020-03-17 | 21:45 | GG1232 | Short rural | Asset Failure | Distribution substation | 1 | 135 | 0.00044413 | 3.2899e-06 | No
2020-03-17 | 22:08 | HR1276 | Urban | Asset Failure | Distribution substation | 16 | 133 | 0.0028396 | 2.135e-05 | No
2020-03-18 | 3:51 | T888 | Urban | Asset Failure | HV | 601 | 105.5324 | 0.084634 | 0.00080197 | No
2020-03-18 | 6:50 | S735 | Short rural | Asset Failure | Distribution substation | 21 | 96.3333 | 0.0066554 | 6.9087e-05 | No
2020-03-18 | 9:00 | AB1287 | Urban | Asset Failure | Distribution substation | 2 | 79 | 0.00021084 | 2.6688e-06 | No
2020-03-18 | 15:25 | JBB2 | Short rural | Other | Isolation Request by EE | 8 | 40 | 0.0010528 | 2.6319e-05 | No
2020-03-18 | 19:09 | S735 | Short rural | Asset Failure | Distribution substation | 3 | 59 | 0.00058231 | 9.8696e-06 | No
2020-03-18 | 19:51 | T895 | Urban | Asset Failure | Distribution substation | 1 | 441 | 0.00058847 | 1.3344e-06 | No
2020-03-18 | 20:05 | HT1203 | Urban | Asset Failure | Distribution substation | 3 | 299.3333 | 0.0011983 | 4.0032e-06 | No
2020-03-18 | 20:45 | JBA2 | Short rural | Asset Failure | HV | 35 | 34.0571 | 0.0039215 | 0.00011515 | No
2020-03-18 | 23:24 | 9046 | Urban | Unknown | Unknown | 10 | 44 | 0.00058714 | 1.3344e-05 | No
2020-03-19 | 7:42 | SC1204 | Short rural | Asset Failure | Distribution substation | 1 | 282 | 0.00092774 | 3.2899e-06 | No
2020-03-19 | 8:22 | L946 | Short rural | Asset Failure | HV | 68 | 56.2941 | 0.012594 | 0.00022371 | No
2020-03-19 | 8:42 | MG1286 | Short rural | Asset Failure | LV | 28 | 36 | 0.0033162 | 9.2116e-05 | No
2020-03-19 | 8:55 | JS1222 | Short rural | Third Party | Other | 4 | 137.25 | 0.0018061 | 1.3159e-05 | No
2020-03-19 | 9:57 | 1952 | Urban | Asset Failure | Distribution substation | 9 | 313.6667 | 0.003767 | 1.201e-05 | No
2020-03-19 | 10:57 | CD1234 | Short rural | Asset Failure | Distribution substation | 1 | 442 | 0.0014541 | 3.2899e-06 | No
2020-03-19 | 11:27 | DP1206 | Urban | Network business | Switching or protection error | 3825 | 8.8 | 0.044916 | 0.0051041 | No
2020-03-19 | 12:30 | BX1222 | Urban | Asset Failure | HV | 643.7146 | 210.3012 | 0.18064 | 0.00085897 | No
2020-03-19 | 12:30 | BX1342 | Urban | Asset Failure | HV | 591.2854 | 210.3012 | 0.16593 | 0.00078901 | No
2020-03-19 | 17:44 | OA1233 | Short rural | Unknown | Unknown | 10 | 108 | 0.0035531 | 3.2899e-05 | No
2020-03-19 | 19:34 | NA1270 | Short rural | Unknown | Unknown | 2 | 108 | 0.00071061 | 6.5797e-06 | No
2020-03-19 | 19:56 | 9057 | Urban | Unknown | Unknown | 53 | 96 | 0.0067894 | 7.0723e-05 | No
2020-03-19 | 20:26 | MM1382 | Urban | Asset Failure | Distribution substation | 25 | 32.32 | 0.0010782 | 3.336e-05 | No
2020-03-20 | 0:21 | NK1342 | Urban | Unknown | Unknown | 68 | 560 | 0.050814 | 9.0739e-05 | No
2020-03-20 | 9:33 | APB2 | Short rural | Third Party | Vehicle impact | 22 | 24.9091 | 0.0018028 | 7.2377e-05 | No
2020-03-20 | 11:39 | ULC2 | Short rural | Asset Failure | HV | 1317 | 4.5998 | 0.01993 | 0.0043327 | No
2020-03-20 | 11:40 | L946 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 6 | 153 | 0.0030201 | 1.9739e-05 | No
2020-03-20 | 16:23 | J499 | Urban | Weather |  | 83 | 144 | 0.015949 | 0.00011076 | No
2020-03-20 | 16:41 | DP1269 | Urban | Asset Failure | HV | 1116 | 51.8244 | 0.077176 | 0.0014892 | No
2020-03-20 | 17:50 | 35988 | Short rural | Asset Failure | Distribution substation | 2 | 385 | 0.0025332 | 6.5797e-06 | No
2020-03-20 | 18:14 | MR2231 | Urban | Asset Failure | Distribution substation | 20 | 569.65 | 0.015203 | 2.6688e-05 | No
2020-03-20 | 18:18 | J483 | Urban | Asset Failure | Distribution substation | 1 | 101 | 0.00013477 | 1.3344e-06 | No
2020-03-20 | 19:26 | NK1342 | Urban | Asset Failure | HV | 1474 | 53.0332 | 0.10431 | 0.0019669 | No
2020-03-20 | 20:26 | JBB2 | Short rural | Unknown | Unknown | 39 | 120.6667 | 0.015482 | 0.0001283 | No
2020-03-20 | 22:10 | ULC2 | Short rural | Asset Failure | Distribution substation | 22 | 181.0909 | 0.013107 | 7.2377e-05 | No
2020-03-20 | 22:11 | 8770 | Urban | Asset Failure | Distribution substation | 1 | 333 | 0.00044435 | 1.3344e-06 | No
2020-03-21 | 8:48 | C855 | Short rural | Unknown | Unknown | 19 | 22 | 0.0013752 | 6.2507e-05 | No
2020-03-21 | 9:14 | BDA2 | Short rural | Unknown | Unknown | 1 | 126 | 0.00041452 | 3.2899e-06 | No
2020-03-21 | 14:24 | BX1242 | Urban | Asset Failure | Distribution substation | 9 | 60.2222 | 0.00072324 | 1.201e-05 | No
2020-03-21 | 16:59 | WL1292 | Urban | Vegetation | Grow-in - NSP responsibility | 11 | 144.2727 | 0.0021177 | 1.4678e-05 | No
2020-03-21 | 18:27 | X859 | Urban | Asset Failure | Distribution substation | 1 | 183 | 0.0002442 | 1.3344e-06 | No
2020-03-22 | 6:50 | L947 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 55.5 | 0.00036517 | 6.5797e-06 | No
2020-03-22 | 8:13 | CR1280 | Urban | Network business | Switching or protection error | 1023 | 8 | 0.010921 | 0.0013651 | No
2020-03-22 | 8:13 | CR1228 | Urban | Network business | Switching or protection error | 1323 | 8 | 0.014123 | 0.0017654 | No
2020-03-22 | 9:04 | CX1273 | Short rural | Unknown | Unknown | 5 | 272 | 0.0044742 | 1.6449e-05 | No
2020-03-22 | 11:37 | SY1132 | Urban | Asset Failure | Distribution substation | 1 | 140 | 0.00018682 | 1.3344e-06 | No
2020-03-22 | 14:18 | C889 | Urban | Asset Failure | Distribution substation | 1 | 137 | 0.00018281 | 1.3344e-06 | No
2020-03-22 | 19:33 | RBC2 | Short rural | Asset Failure | HV | 20 | 289 | 0.019015 | 6.5797e-05 | No
2020-03-22 | 20:13 | S744 | Urban | Vegetation | Grow-in - NSP responsibility | 516 | 85.0775 | 0.05858 | 0.00068855 | No
2020-03-23 | 6:58 | MVB2 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 40 | 264.95 | 0.034866 | 0.00013159 | No
2020-03-23 | 7:13 | DP1210 | Short rural | Unknown | Unknown | 69 | 1.1449 | 0.0002599 | 0.000227 | No
2020-03-23 | 10:27 | SHK2 | Urban | Third Party | Other | 1.4709 | 300 | 0.00058883 | 1.9628e-06 | No
2020-03-23 | 10:27 | SHH2 | Short rural | Third Party | Other | 0.52911 | 300 | 0.00052221 | 1.7407e-06 | No
2020-03-23 | 11:24 | NG1299 | Short rural | Unknown | Unknown | 1 | 105 | 0.00034544 | 3.2899e-06 | No
2020-03-23 | 12:24 | WBB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 22 | 0.00014475 | 6.5797e-06 | No
2020-03-23 | 14:39 | 8799 | Short rural | Asset Failure | Distribution substation | 2 | 163 | 0.0010725 | 6.5797e-06 | No
2020-03-23 | 18:19 | CLA2 | Short rural | Asset Failure | Distribution substation | 2 | 128 | 0.0008422 | 6.5797e-06 | No
2020-03-24 | 3:41 | X863 | Urban | Asset Failure | HV | 622 | 128 | 0.10624 | 0.00083 | No
2020-03-24 | 4:50 | 7093/1 | Short rural | Animal | Animal Impact | 5 | 254.6 | 0.004188 | 1.6449e-05 | No
2020-03-24 | 7:55 | CR1210 | Urban | Asset Failure | Distribution substation | 43 | 41.4884 | 0.0023806 | 5.7379e-05 | No
2020-03-24 | 8:04 | HR1273 | Urban | Animal | Animal Impact | 1696 | 64.2241 | 0.14535 | 0.0022631 | No
2020-03-24 | 12:38 | NM1210 | Urban | Unknown | Unknown | 1 | 513 | 0.00068455 | 1.3344e-06 | No
2020-03-24 | 13:34 | 27030 | Urban | Asset Failure | Distribution substation | 1 | 274 | 0.00036563 | 1.3344e-06 | No
2020-03-24 | 13:44 | RBA2 | Short rural | Asset Failure | Distribution substation | 2 | 31 | 0.00020397 | 6.5797e-06 | No
2020-03-25 | 0:56 | SWC2 | Urban | Asset Failure | Distribution substation | 16 | 149 | 0.0031812 | 2.135e-05 | No
2020-03-25 | 1:35 | 6419 | Urban | Other | Probable Lightning/Electrical Storm | 68 | 362 | 0.032848 | 9.0739e-05 | No
2020-03-25 | 9:12 | X871 | Urban | Asset Failure | Distribution substation | 1 | 106 | 0.00014145 | 1.3344e-06 | No
2020-03-25 | 9:14 | 8686 | Short rural | Other | Isolation Request by EE | 687 | 4.1499 | 0.0093794 | 0.0022601 | No
2020-03-25 | 11:34 | L582 | Short rural | Asset Failure | Distribution substation | 1 | 550 | 0.0018094 | 3.2899e-06 | No
2020-03-25 | 12:14 | RW1218 | Short rural | Weather |  | 1 | 80 | 0.00026319 | 3.2899e-06 | No
2020-03-25 | 13:49 | MVC2 | Short rural | Weather |  | 2 | 109 | 0.00071719 | 6.5797e-06 | No
2020-03-25 | 13:59 | MVC2 | Short rural | Weather |  | 6 | 104 | 0.0020529 | 1.9739e-05 | No
2020-03-25 | 14:37 | 87222 | Long rural | Other | Probable Lightning/Electrical Storm | 1 | 135 | 0.42994 | 0.0031847 | No
2020-03-25 | 14:46 | 35989 | Short rural | Weather |  | 13 | 59 | 0.0025233 | 4.2768e-05 | No
2020-03-25 | 14:50 | MVB2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 132 | 0.00043426 | 3.2899e-06 | No
2020-03-25 | 15:19 | M168 | Urban | Third Party | Other | 10 | 31.1 | 0.000415 | 1.3344e-05 | No
2020-03-25 | 15:25 | H745 | Short rural | Other | Probable Lightning/Electrical Storm | 5 | 282 | 0.0046387 | 1.6449e-05 | No
2020-03-25 | 15:39 | NN1251 | Short rural | Other | Probable Lightning/Electrical Storm | 4 | 201 | 0.0026451 | 1.3159e-05 | No
2020-03-25 | 15:50 | MVC2 | Short rural | Weather |  | 5 | 60 | 0.00098696 | 1.6449e-05 | No
2020-03-25 | 15:57 | 35988 | Short rural | Weather |  | 6 | 47 | 0.00092774 | 1.9739e-05 | No
2020-03-25 | 16:20 | OP1122 | Short rural | Weather |  | 1 | 171 | 0.00056257 | 3.2899e-06 | No
2020-03-25 | 16:46 | WH1294 | Urban | Asset Failure | Distribution substation | 54 | 105 | 0.007566 | 7.2058e-05 | No
2020-03-25 | 17:09 | MM1352 | Short rural | Third Party | Other | 14 | 286.9286 | 0.013215 | 4.6058e-05 | No
2020-03-25 | 17:10 | S744 | Urban | Vegetation | Grow-in - NSP responsibility | 516 | 63.6957 | 0.043858 | 0.00068855 | No
2020-03-25 | 17:14 | T842 | Short rural | Other | Probable Lightning/Electrical Storm | 10 | 153.3 | 0.0050434 | 3.2899e-05 | No
2020-03-25 | 17:23 | OP1122 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 152 | 0.0010001 | 6.5797e-06 | No
2020-03-25 | 17:26 | 49366 | Urban | Asset Failure | Distribution substation | 1 | 147 | 0.00019616 | 1.3344e-06 | No
2020-03-25 | 17:54 | 8799 | Short rural | Weather |  | 3 | 49 | 0.00048361 | 9.8696e-06 | No
2020-03-25 | 18:25 | T829 | Urban | Other | Probable Lightning/Electrical Storm | 4 | 115 | 0.00061382 | 5.3376e-06 | No
2020-03-25 | 18:37 | W188 | Short rural | Other | Probable Lightning/Electrical Storm | 5 | 184 | 0.0030267 | 1.6449e-05 | No
2020-03-25 | 18:38 | RW1255 | Short rural | Weather |  | 1 | 98 | 0.00032241 | 3.2899e-06 | No
2020-03-25 | 18:50 | ER1262 | Short rural | Asset Failure | Distribution substation | 29 | 141.8966 | 0.013538 | 9.5406e-05 | No
2020-03-25 | 19:18 | CT1225 | Short rural | Other | Probable Lightning/Electrical Storm | 5 | 219 | 0.0036024 | 1.6449e-05 | No
2020-03-25 | 19:23 | SZ1212 | Short rural | Asset Failure | Distribution substation | 1 | 145 | 0.00047703 | 3.2899e-06 | No
2020-03-25 | 20:06 | 10244 | Short rural | Other | Probable Equipment Failure | 553 | 178.3382 | 0.32445 | 0.0018193 | No
2020-03-25 | 22:48 | 1960 | Urban | Asset Failure | HV | 804 | 58.8396 | 0.063126 | 0.0010729 | No
2020-03-25 | 23:12 | 10287 | Urban | Asset Failure | Distribution substation | 28 | 99 | 0.003699 | 3.7363e-05 | No
2020-03-26 | 6:15 | 35988 | Short rural | Asset Failure | Distribution substation | 1 | 344 | 0.0011317 | 3.2899e-06 | No
2020-03-26 | 7:19 | BDE2 | Urban | Unknown | Unknown | 3 | 73 | 0.00029223 | 4.0032e-06 | No
2020-03-26 | 9:14 | L591 | Short rural | Asset Failure | Distribution substation | 1 | 166 | 0.00054612 | 3.2899e-06 | No
2020-03-26 | 10:00 | BYD2 | Short rural | Asset Failure | LV | 14 | 146.5 | 0.0067475 | 4.6058e-05 | No
2020-03-26 | 10:51 | MM1202 | Urban | Asset Failure | Distribution substation | 6 | 118 | 0.00094475 | 8.0064e-06 | No
2020-03-26 | 11:34 | MVB2 | Short rural | Unknown | Unknown | 1 | 164 | 0.00053954 | 3.2899e-06 | No
2020-03-26 | 12:23 | RBB2 | Short rural | Unknown | Unknown | 2 | 300 | 0.0019739 | 6.5797e-06 | No
2020-03-26 | 14:06 | SC1289 | Short rural | Third Party | Other | 1 | 158 | 0.0005198 | 3.2899e-06 | No
2020-03-26 | 14:13 | 35980 | Short rural | Asset Failure | Distribution substation | 3 | 87.3333 | 0.00086194 | 9.8696e-06 | No
2020-03-26 | 16:55 | J513 | Urban | Asset Failure | Distribution substation | 2 | 52 | 0.00013878 | 2.6688e-06 | No
2020-03-26 | 18:11 | S740 | Urban | Asset Failure | LV | 28 | 34 | 0.0012703 | 3.7363e-05 | No
2020-03-27 | 1:02 | NM1239 | Urban | Third Party | Other | 24 | 214 | 0.0068535 | 3.2026e-05 | No
2020-03-27 | 2:09 | SXC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 581 | 53.1153 | 0.10153 | 0.0019114 | No
2020-03-27 | 3:09 | 7093/1 | Short rural | Unknown | Unknown | 5 | 539 | 0.0088662 | 1.6449e-05 | No
2020-03-27 | 4:06 | 9056 | Urban | Asset Failure | Distribution substation | 59 | 459.7119 | 0.036193 | 7.873e-05 | No
2020-03-27 | 7:42 | 7981 | Urban | Third Party | Other | 13 | 172 | 0.0029837 | 1.7347e-05 | No
2020-03-27 | 8:28 | 27188 | Urban | Asset Failure | LV | 366 | 12.8169 | 0.0062597 | 0.00048839 | No
2020-03-27 | 8:52 | CS1243 | Urban | Unknown | Unknown | 13 | 73 | 0.0012663 | 1.7347e-05 | No
2020-03-27 | 9:20 | MR2232 | Short rural | Unknown | Unknown | 3 | 233 | 0.0022996 | 9.8696e-06 | No
2020-03-27 | 11:00 | NN1207 | Short rural | Unknown | Unknown | 8 | 141 | 0.003711 | 2.6319e-05 | No
2020-03-27 | 11:09 | L591 | Short rural | Unknown | Unknown | 16 | 107 | 0.0056322 | 5.2638e-05 | No
2020-03-27 | 15:59 | L591 | Short rural | Asset Failure | Distribution substation | 1 | 131 | 0.00043097 | 3.2899e-06 | No
2020-03-27 | 16:17 | X879 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 509 | 127.2633 | 0.21311 | 0.0016745 | No
2020-03-27 | 16:20 | 87222 | Long rural | Other | Probable Lightning/Electrical Storm | 1 | 123 | 0.39172 | 0.0031847 | No
2020-03-27 | 20:43 | 8779 | Urban | Asset Failure | Distribution substation | 1 | 34 | 4.537e-05 | 1.3344e-06 | No
2020-03-27 | 21:51 | T873 | Short rural | Third Party | Other | 32 | 685 | 0.072114 | 0.00010528 | No
2020-03-27 | 23:30 | J495 | Short rural | Unknown | Unknown | 7 | 472 | 0.01087 | 2.3029e-05 | No
2020-03-28 | 7:12 | MS1112 | Short rural | Third Party | Other | 59 | 275.7458 | 0.053523 | 0.0001941 | No
2020-03-28 | 8:15 | RW1255 | Short rural | Unknown | Unknown | 2 | 180 | 0.0011844 | 6.5797e-06 | No
2020-03-28 | 8:51 | 35693 | Short rural | Asset Failure | HV | 324 | 39.966 | 0.0426 | 0.0010659 | No
2020-03-28 | 10:07 | CLA2 | Short rural | Asset Failure | Distribution substation | 1 | 175 | 0.00057573 | 3.2899e-06 | No
2020-03-28 | 13:04 | JBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 66 | 15.6818 | 0.003405 | 0.00021713 | No
2020-03-28 | 14:14 | NM1239 | Urban | Third Party | Vehicle impact | 559 | 34.483 | 0.025722 | 0.00074593 | No
2020-03-28 | 14:33 | 35693 | Short rural | Asset Failure | LV | 324 | 15.9815 | 0.017035 | 0.0010659 | No
2020-03-28 | 14:51 | WX1244 | Urban | Asset Failure | HV | 157 | 90.1783 | 0.018892 | 0.0002095 | No
2020-03-28 | 15:51 | KMA2 | Short rural | Asset Failure | Distribution substation | 58 | 339.9483 | 0.064866 | 0.00019081 | No
2020-03-28 | 16:21 | 8686 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 29 | 9.5406e-05 | 3.2899e-06 | No
2020-03-28 | 16:39 | J495 | Short rural | Asset Failure | Distribution substation | 22 | 109.5455 | 0.0079286 | 7.2377e-05 | No
2020-03-28 | 18:33 | SXD2 | Short rural | Asset Failure | Distribution substation | 4 | 121 | 0.0015923 | 1.3159e-05 | No
2020-03-28 | 20:46 | 35418 | Short rural | Third Party | Vehicle impact | 361 | 118.7981 | 0.14109 | 0.0011876 | No
2020-03-28 | 20:46 | D810 | Short rural | Third Party | Vehicle impact | 228 | 118.7981 | 0.089109 | 0.00075009 | No
2020-03-28 | 20:46 | D813 | Short rural | Third Party | Vehicle impact | 314 | 118.7981 | 0.12272 | 0.001033 | No
2020-03-28 | 20:46 | D814 | Short rural | Third Party | Vehicle impact | 330 | 118.7981 | 0.12897 | 0.0010857 | No
2020-03-29 | 4:33 | 9056 | Urban | Asset Failure | Distribution substation | 62 | 694 | 0.057417 | 8.2733e-05 | No
2020-03-29 | 7:16 | BYC2 | Short rural | Asset Failure | HV | 78 | 177.8077 | 0.045627 | 0.00025661 | No
2020-03-29 | 8:50 | NA1214 | Urban | Asset Failure | Distribution substation | 30 | 489 | 0.019576 | 4.0032e-05 | No
2020-03-29 | 10:52 | HR1273 | Urban | Asset Failure | Distribution substation | 32 | 252.3438 | 0.010775 | 4.2701e-05 | No
2020-03-29 | 11:02 | SHH2 | Short rural | Network business | Switching or protection error | 460 | 46.9652 | 0.071074 | 0.0015133 | No
2020-03-29 | 11:21 | 4873 | Urban | Asset Failure | Distribution substation | 13 | 127 | 0.0022031 | 1.7347e-05 | No
2020-03-29 | 23:44 | 19856 | Urban | Asset Failure | Distribution substation | 33 | 250.0606 | 0.011011 | 4.4035e-05 | No
2020-03-30 | 5:42 | MVE2 | Short rural | Unknown | Unknown | 8 | 157.125 | 0.0041354 | 2.6319e-05 | No
2020-03-30 | 8:04 | RW1292 | Short rural | Vegetation | Grow-in - NSP responsibility | 9 | 157.2222 | 0.0046552 | 2.9609e-05 | No
2020-03-30 | 9:17 | RD1206 | Urban | Asset Failure | Distribution substation | 1 | 63 | 8.4067e-05 | 1.3344e-06 | No
2020-03-30 | 9:32 | 48178 | Urban | Asset Failure | HV | 580.1358 | 72.7041 | 0.056283 | 0.00077413 | No
2020-03-30 | 9:32 | 53803 | Urban | Asset Failure | HV | 558.8642 | 72.7041 | 0.054219 | 0.00074575 | No
2020-03-30 | 11:05 | 9030 | Urban | Asset Failure | HV | 34 | 44.6471 | 0.0020256 | 4.537e-05 | No
2020-03-30 | 17:36 | BWH2 | Short rural | Asset Failure | Distribution substation | 8 | 85.125 | 0.0022404 | 2.6319e-05 | No
2020-03-30 | 17:56 | MR2232 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 106.3333 | 0.0010495 | 9.8696e-06 | No
2020-03-30 | 18:04 | MG1286 | Short rural | Asset Failure | Distribution substation | 9 | 202 | 0.005981 | 2.9609e-05 | No
2020-03-30 | 20:57 | 55888 | Urban | Asset Failure | Distribution substation | 10 | 142 | 0.0018948 | 1.3344e-05 | No
2020-03-30 | 22:06 | CD1260 | Urban | Vegetation | Grow-in - NSP responsibility | 19 | 59 | 0.0014959 | 2.5354e-05 | No
2020-03-31 | 5:03 | 27040 | Urban | Asset Failure | HV | 1373 | 90.6854 | 0.16615 | 0.0018321 | No
2020-03-31 | 11:13 | SY1152 | Urban | Asset Failure | LV | 265 | 97 | 0.034301 | 0.00035362 | No
2020-03-31 | 12:31 | 49917 | Urban | Asset Failure | Distribution substation | 33 | 16.4848 | 0.00072591 | 4.4035e-05 | No
2020-03-31 | 14:30 | 8611 | Urban | Unknown | Unknown | 11 | 20 | 0.00029357 | 1.4678e-05 | No
2020-03-31 | 21:41 | ER1232 | Short rural | Unknown | Unknown | 1 | 71 | 0.00023358 | 3.2899e-06 | No
2020-03-31 | 23:52 | 7093/1 | Short rural | Animal | Animal Impact | 5 | 183.2 | 0.0030135 | 1.6449e-05 | No
2020-04-01 | 7:03 | NM1239 | Urban | Unknown | Unknown | 24 | 85 | 0.0027222 | 3.2026e-05 | No
2020-04-01 | 8:26 | X881 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 291 | 0.00095735 | 3.2899e-06 | No
2020-04-01 | 8:51 | X213 | Short rural | Asset Failure | Distribution substation | 1 | 259 | 0.00085207 | 3.2899e-06 | No
2020-04-01 | 10:01 | CV1221 | Urban | Asset Failure | Distribution substation | 39 | 34.5128 | 0.0017961 | 5.2042e-05 | No
2020-04-01 | 11:15 | BX1232 | Urban | Other | Isolation Request by EE | 62 | 33 | 0.0027302 | 8.2733e-05 | No
2020-04-01 | 11:25 | MG1208 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 806 | 41 | 0.10872 | 0.0026516 | No
2020-04-01 | 12:02 | NM1213 | Urban | Asset Failure | HV | 878 | 75.32 | 0.088245 | 0.0011716 | No
2020-04-01 | 12:08 | AB1223 | Urban | Asset Failure | Distribution substation | 1 | 548 | 0.00073125 | 1.3344e-06 | No
2020-04-01 | 12:22 | WD1247 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 49 | 0.00032241 | 6.5797e-06 | No
2020-04-01 | 12:39 | YYB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1230 | 22.5171 | 0.091116 | 0.0040465 | No
2020-04-01 | 13:37 | A348 | Urban | Asset Failure | Distribution substation | 8 | 49.125 | 0.00052442 | 1.0675e-05 | No
2020-04-01 | 14:06 | NM1239 | Urban | Unknown | Unknown | 24 | 76 | 0.0024339 | 3.2026e-05 | No
2020-04-01 | 15:08 | NWA2 | Urban | Asset Failure | Distribution substation | 257 | 174.6615 | 0.059899 | 0.00034294 | No
2020-04-01 | 17:20 | RV1280 | Urban | Asset Failure | LV | 104 | 55.1346 | 0.0076514 | 0.00013878 | No
2020-04-02 | 6:12 | RV1298 | Urban | Unknown | Unknown | 7 | 81 | 0.0007566 | 9.3408e-06 | No
2020-04-02 | 7:37 | PK1225 | Urban | Asset Failure | Distribution substation | 15 | 59.7333 | 0.0011956 | 2.0016e-05 | No
2020-04-02 | 8:15 | 835 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 57 | 0.00018752 | 3.2899e-06 | No
2020-04-02 | 10:43 | B747 | Urban | Asset Failure | Distribution substation | 1 | 46 | 6.1382e-05 | 1.3344e-06 | No
2020-04-02 | 11:14 | 4873 | Urban | Third Party | Other | 16 | 55 | 0.0011743 | 2.135e-05 | No
2020-04-02 | 15:08 | 49006 | Short rural | Asset Failure | HV | 1182 | 80.5745 | 0.31332 | 0.0038886 | No
2020-04-02 | 15:27 | YYB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1230 | 23.5878 | 0.095449 | 0.0040465 | No
2020-04-02 | 16:12 | 41537 | Urban | Asset Failure | Distribution substation | 37 | 64.973 | 0.0032079 | 4.9373e-05 | No
2020-04-02 | 17:21 | NN1233 | Short rural | Third Party | Other | 113 | 346.4956 | 0.12881 | 0.00037175 | No
2020-04-02 | 18:27 | WL1295 | Urban | Asset Failure | Distribution substation | 1 | 1188 | 0.0015853 | 1.3344e-06 | No
2020-04-02 | 19:23 | WBD2 | Short rural | Vegetation | Grow-in - NSP responsibility | 13 | 243.6154 | 0.010419 | 4.2768e-05 | No
2020-04-03 | 13:40 | L582 | Short rural | Asset Failure | Distribution substation | 4 | 142 | 0.0018686 | 1.3159e-05 | No
2020-04-03 | 15:40 | FT1209 | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 24 | 6.4051e-05 | 2.6688e-06 | No
2020-04-03 | 17:54 | RD1269 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 75 | 137 | 0.013711 | 0.00010008 | No
2020-04-03 | 18:15 | M160 | Urban | Third Party | Vehicle impact | 6 | 64.3333 | 0.00051508 | 8.0064e-06 | No
2020-04-03 | 19:09 | L517 | Urban | Asset Failure | Distribution substation | 34 | 371.1765 | 0.01684 | 4.537e-05 | No
2020-04-04 | 0:43 | ER1252 | Short rural | Asset Failure | Distribution substation | 85 | 512.4353 | 0.1433 | 0.00027964 | No
2020-04-04 | 4:25 | W196 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 141 | 64.6383 | 0.012162 | 0.00018815 | No
2020-04-04 | 7:29 | 9019 | Urban | Asset Failure | Distribution substation | 1 | 128 | 0.0001708 | 1.3344e-06 | No
2020-04-04 | 8:18 | C832 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 323 | 0.00043101 | 1.3344e-06 | No
2020-04-04 | 9:30 | A325 | Urban | Asset Failure | Distribution substation | 1 | 250 | 0.0003336 | 1.3344e-06 | No
2020-04-04 | 9:31 | W188 | Short rural | Other | Probable Rain incl. Mist and Fog | 8 | 158 | 0.0041584 | 2.6319e-05 | No
2020-04-04 | 10:34 | CJ1245 | Urban | Asset Failure | Distribution substation | 1 | 378 | 0.0005044 | 1.3344e-06 | No
2020-04-04 | 12:03 | BDA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 177 | 205.2316 | 0.11951 | 0.00058231 | No
2020-04-04 | 12:03 | KVD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 63 | 255 | 0.052852 | 0.00020726 | No
2020-04-04 | 12:25 | NA1207 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 114 | 31 | 0.011626 | 0.00037504 | No
2020-04-04 | 12:39 | FT1206 | Short rural | Unknown | Unknown | 448 | 96 | 0.14149 | 0.0014739 | No
2020-04-04 | 12:51 | 2810 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 957 | 61.5705 | 0.078627 | 0.001277 | No
2020-04-04 | 13:12 | JS1252 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 188 | 111.2872 | 0.068831 | 0.00061849 | No
2020-04-04 | 13:15 | YYB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1230 | 31.9106 | 0.12913 | 0.0040465 | No
2020-04-04 | 13:17 | CX1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 334 | 0.021976 | 6.5797e-05 | No
2020-04-04 | 13:25 | FF1276 | Urban | Third Party | Vehicle impact | 561 | 131.8592 | 0.09871 | 0.0007486 | No
2020-04-04 | 13:34 | S737 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 146 | 376.5205 | 0.18085 | 0.00048032 | No
2020-04-04 | 13:38 | 9055 | Urban | Unknown | Unknown | 109 | 145 | 0.02109 | 0.00014545 | No
2020-04-04 | 13:50 | L947 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 71 | 593.9577 | 0.13874 | 0.00023358 | No
2020-04-04 | 13:54 | J506 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1618 | 67.9666 | 0.14674 | 0.0021591 | No
2020-04-04 | 13:56 | L941 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 28 | 236 | 0.021739 | 9.2116e-05 | No
2020-04-04 | 14:18 | BWB2 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 804 | 160.0211 | 0.17168 | 0.0010729 | No
2020-04-04 | 14:26 | KVB2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 358 | 0.0011778 | 3.2899e-06 | No
2020-04-04 | 14:27 | R208 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 31 | 88 | 0.0089747 | 0.00010199 | No
2020-04-04 | 14:32 | KVA2 | Short rural | Unknown | Unknown | 1 | 304 | 0.0010001 | 3.2899e-06 | No
2020-04-04 | 14:47 | SXC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 236.6667 | 0.021022 | 8.8826e-05 | No
2020-04-04 | 14:49 | 8802 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 109 | 526.2294 | 0.1887 | 0.0003586 | No
2020-04-04 | 15:20 | SXC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 154 | 0.0040531 | 2.6319e-05 | No
2020-04-04 | 15:40 | ULB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1558 | 113 | 0.57919 | 0.0051256 | No
2020-04-04 | 16:16 | BYF2 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 470 | 40 | 0.025087 | 0.00062717 | No
2020-04-04 | 16:46 | GG1295 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 3 | 230 | 0.00227 | 9.8696e-06 | No
2020-04-04 | 16:55 | M399 | Short rural | Unknown | Unknown | 1 | 107 | 0.00035202 | 3.2899e-06 | No
2020-04-04 | 17:20 | HKB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1111 | 60.2511 | 0.22022 | 0.003655 | No
2020-04-04 | 19:44 | CLC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 61 | 0.0012041 | 1.9739e-05 | No
2020-04-04 | 21:12 | CX1273 | Short rural | Animal | Animal Impact | 3 | 111 | 0.0010955 | 9.8696e-06 | No
2020-04-04 | 21:12 | JBA2 | Short rural | Asset Failure | HV | 64 | 66 | 0.013896 | 0.00021055 | No
2020-04-04 | 21:37 | S785 | Urban | Asset Failure | Distribution substation | 1 | 262 | 0.00034961 | 1.3344e-06 | No
2020-04-04 | 22:45 | BK1251 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 108 | 170 | 0.060402 | 0.00035531 | No
2020-04-05 | 0:58 | L582 | Short rural | Vegetation | Grow-in - NSP responsibility | 70.4054 | 177.4597 | 0.041104 | 0.00023162 | No
2020-04-05 | 0:58 | BK1251 | Short rural | Vegetation | Grow-in - NSP responsibility | 53.5946 | 177.4597 | 0.03129 | 0.00017632 | No
2020-04-05 | 3:12 | 8679 | Urban | Asset Failure | Distribution substation | 23 | 408 | 0.012522 | 3.0691e-05 | No
2020-04-05 | 9:10 | CS1247 | Urban | Asset Failure | Distribution substation | 37 | 155 | 0.0076528 | 4.9373e-05 | No
2020-04-05 | 12:29 | 7093 | Short rural | Asset Failure | LV | 5 | 176.4 | 0.0029017 | 1.6449e-05 | No
2020-04-05 | 15:48 | BGA2 | Short rural | Unknown | Unknown | 6 | 84 | 0.0016581 | 1.9739e-05 | No
2020-04-05 | 16:12 | X877 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 136 | 0.00089484 | 6.5797e-06 | No
2020-04-05 | 16:18 | R208 | Short rural | Vegetation | Grow-in - NSP responsibility | 19 | 83 | 0.0051881 | 6.2507e-05 | No
2020-04-05 | 18:54 | BDE2 | Urban | Asset Failure | Distribution substation | 1 | 309 | 0.00041233 | 1.3344e-06 | No
2020-04-05 | 20:03 | NA1236 | Short rural | Third Party | Unauthorised access | 31 | 166.7419 | 0.017005 | 0.00010199 | No
2020-04-06 | 3:15 | WBB2 | Short rural | Asset Failure | Distribution substation | 1 | 457 | 0.0015035 | 3.2899e-06 | No
2020-04-06 | 7:17 | CLA2 | Short rural | Unknown | Unknown | 6 | 110 | 0.0021713 | 1.9739e-05 | No
2020-04-06 | 8:28 | CLA2 | Short rural | Unknown | Unknown | 1 | 40 | 0.00013159 | 3.2899e-06 | No
2020-04-06 | 9:27 | L584 | Short rural | Asset Failure | Distribution substation | 2 | 74.5 | 0.00049019 | 6.5797e-06 | No
2020-04-06 | 11:16 | SXD2 | Short rural | Asset Failure | Distribution substation | 1 | 208 | 0.00068429 | 3.2899e-06 | No
2020-04-06 | 11:35 | WH1294 | Urban | Unknown | Unknown | 68 | 195 | 0.017694 | 9.0739e-05 | No
2020-04-06 | 13:25 | MG1286 | Short rural | Asset Failure | Distribution substation | 1 | 23 | 7.5667e-05 | 3.2899e-06 | No
2020-04-06 | 13:45 | KC1236 | Short rural | Asset Failure | Distribution substation | 4 | 386.5 | 0.0050861 | 1.3159e-05 | No
2020-04-06 | 14:00 | WH1294 | Urban | Unknown | Unknown | 71 | 51 | 0.0048319 | 9.4742e-05 | No
2020-04-06 | 15:49 | 46774 | Urban | Vegetation | Grow-in - NSP responsibility | 12 | 146 | 0.0023379 | 1.6013e-05 | No
2020-04-06 | 17:47 | GG1295 | Short rural | Vegetation | Grow-in - NSP responsibility | 7 | 101 | 0.0023259 | 2.3029e-05 | No
2020-04-06 | 18:12 | DS1290 | Urban | Asset Failure | Distribution substation | 1 | 589 | 0.00078596 | 1.3344e-06 | No
2020-04-06 | 19:19 | BWC2 | Short rural | Animal | Animal Impact | 60 | 80 | 0.015791 | 0.00019739 | No
2020-04-06 | 20:53 | 7093 | Short rural | Other | Probable Animals | 4 | 144 | 0.001895 | 1.3159e-05 | No
2020-04-07 | 8:10 | RV1298 | Urban | Unknown | Unknown | 7 | 87.2857 | 0.00081532 | 9.3408e-06 | No
2020-04-07 | 11:54 | RD1251 | Urban | Third Party | Other | 97 | 102 | 0.013203 | 0.00012944 | No
2020-04-07 | 14:12 | NL1182 | Urban | Unknown | Unknown | 7 | 77 | 0.00071924 | 9.3408e-06 | No
2020-04-07 | 14:56 | J514 | Urban | Asset Failure | Distribution substation | 30 | 38.5667 | 0.0015439 | 4.0032e-05 | No
2020-04-07 | 20:04 | 87220 | Short rural | Unknown | Unknown | 2 | 127 | 0.00083563 | 6.5797e-06 | No
2020-04-07 | 21:29 | X881 | Short rural | Unknown | Unknown | 12 | 85 | 0.0033557 | 3.9478e-05 | No
2020-04-08 | 9:08 | LP1322 | Urban | Animal | Animal Impact | 951 | 5 | 0.0063451 | 0.001269 | No
2020-04-08 | 9:26 | 35696 | Short rural | Vegetation | Grow-in - NSP responsibility | 23 | 148 | 0.011199 | 7.5667e-05 | No
2020-04-08 | 11:06 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 382 | 0.0062836 | 1.6449e-05 | No
2020-04-08 | 16:49 | CV1247 | Urban | Asset Failure | Distribution substation | 47 | 73 | 0.0045783 | 6.2717e-05 | No
2020-04-08 | 18:52 | ER1252 | Short rural | Asset Failure | Distribution substation | 14.7346 | 167.32 | 0.0081108 | 4.8475e-05 | No
2020-04-08 | 18:52 | ER1152 | Urban | Asset Failure | Distribution substation | 4.1899 | 167.32 | 0.0009355 | 5.5911e-06 | No
2020-04-08 | 18:52 | ER1232 | Short rural | Asset Failure | Distribution substation | 31.0754 | 167.32 | 0.017106 | 0.00010223 | No
2020-04-09 | 8:33 | GL1207 | Short rural | Unknown | Unknown | 11 | 144 | 0.0052111 | 3.6188e-05 | No
2020-04-09 | 11:25 | D814 | Short rural | Asset Failure | HV | 4 | 61.75 | 0.0008126 | 1.3159e-05 | No
2020-04-09 | 12:34 | 35403 | Urban | Other | FOREIGN MATTER ON SYSTEM | 88 | 6.1477 | 0.00072191 | 0.00011743 | No
2020-04-09 | 14:26 | C855 | Short rural | Other | Isolation Request by EE | 11 | 23 | 0.00083234 | 3.6188e-05 | No
2020-04-09 | 15:54 | 35981 | Short rural | Asset Failure | LV | 3 | 36 | 0.00035531 | 9.8696e-06 | No
2020-04-09 | 18:01 | J459 | Short rural | Asset Failure | Distribution substation | 10 | 64 | 0.0021055 | 3.2899e-05 | No
2020-04-09 | 19:28 | J459 | Short rural | Asset Failure | Distribution substation | 7 | 196.7143 | 0.0045301 | 2.3029e-05 | No
2020-04-09 | 23:16 | J473 | Urban | Asset Failure | Distribution substation | 1 | 571 | 0.00076194 | 1.3344e-06 | No
2020-04-10 | 3:34 | BK1236 | Short rural | Vegetation | Grow-in - NSP responsibility | 462 | 99 | 0.15047 | 0.0015199 | No
2020-04-10 | 5:48 | 8801 | Short rural | Asset Failure | LV | 226 | 27.0708 | 0.020127 | 0.00074351 | No
2020-04-10 | 7:00 | KVD2 | Short rural | Unknown | Unknown | 4 | 349 | 0.0045926 | 1.3159e-05 | No
2020-04-10 | 7:21 | CV1221 | Urban | Asset Failure | Distribution substation | 24 | 202.7083 | 0.0064919 | 3.2026e-05 | No
2020-04-10 | 8:05 | L940 | Short rural | Asset Failure | Distribution substation | 1 | 118 | 0.0003882 | 3.2899e-06 | No
2020-04-10 | 8:10 | CV1221 | Urban | Unknown | Unknown | 1 | 131 | 0.00017481 | 1.3344e-06 | No
2020-04-10 | 15:49 | KVB2 | Short rural | Weather |  | 2 | 310 | 0.0020397 | 6.5797e-06 | No
2020-04-10 | 16:26 | WRB2 | Urban | Weather |  | 558 | 70.2796 | 0.05233 | 0.00074459 | No
2020-04-10 | 16:53 | 35825 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 48 | 0.00078957 | 1.6449e-05 | No
2020-04-10 | 17:03 | B214 | Urban | Asset Failure | Distribution substation | 58 | 133.7931 | 0.010355 | 7.7395e-05 | No
2020-04-10 | 17:39 | RW1229 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 89 | 0.0002928 | 3.2899e-06 | No
2020-04-10 | 17:59 | L585 | Short rural | Asset Failure | HV | 2 | 203 | 0.0013357 | 6.5797e-06 | No
2020-04-10 | 18:13 | X877 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 152 | 0.0010001 | 6.5797e-06 | No
2020-04-10 | 18:44 | RW1281 | Short rural | Other | Probable Lightning/Electrical Storm | 2 | 74 | 0.0004869 | 6.5797e-06 | No
2020-04-10 | 18:44 | 9027 | Urban | Other | Probable Equipment Failure | 10 | 245 | 0.0032693 | 1.3344e-05 | No
2020-04-10 | 19:14 | X877 | Short rural | Unknown | Unknown | 1 | 222 | 0.00073035 | 3.2899e-06 | No
2020-04-10 | 20:47 | FF1269 | Urban | Animal | Animal Impact | 22 | 254 | 0.0074566 | 2.9357e-05 | No
2020-04-10 | 22:20 | CN1221 | Urban | Asset Failure | Distribution substation | 23 | 1494 | 0.045853 | 3.0691e-05 | No
2020-04-11 | 4:06 | 8799 | Short rural | Vegetation | Grow-in - NSP responsibility | 162.6241 | 188.092 | 0.10063 | 0.00053501 | No
2020-04-11 | 4:06 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 98.3759 | 188.092 | 0.060875 | 0.00032364 | No
2020-04-11 | 6:33 | JBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 40.3333 | 0.00039807 | 9.8696e-06 | No
2020-04-11 | 8:15 | FT1207 | Urban | Asset Failure | Distribution substation | 1 | 56 | 7.4726e-05 | 1.3344e-06 | No
2020-04-11 | 9:23 | R260 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 67 | 646.209 | 0.14244 | 0.00022042 | No
2020-04-11 | 9:35 | X877 | Short rural | Unknown | Unknown | 1 | 169 | 0.00055599 | 3.2899e-06 | No
2020-04-11 | 11:34 | L588 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 164 | 530.6098 | 0.28628 | 0.00053954 | No
2020-04-11 | 11:47 | KVB2 | Short rural | Unknown | Unknown | 1 | 87 | 0.00028622 | 3.2899e-06 | No
2020-04-11 | 11:49 | ULC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1321 | 35 | 0.15211 | 0.0043459 | No
2020-04-11 | 11:54 | RW1218 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 79 | 344.4304 | 0.089517 | 0.0002599 | No
2020-04-11 | 12:30 | SXC2 | Short rural | Unknown | Unknown | 1 | 354 | 0.0011646 | 3.2899e-06 | No
2020-04-11 | 12:35 | 35983 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 174 | 101.069 | 0.057856 | 0.00057244 | No
2020-04-11 | 12:40 | BWH2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 79 | 363 | 0.094343 | 0.0002599 | No
2020-04-11 | 12:42 | BX1242 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 29 | 314 | 0.012151 | 3.8698e-05 | No
2020-04-11 | 13:01 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 336 | 166.5417 | 0.18409 | 0.0011054 | No
2020-04-11 | 13:05 | OA1233 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 415 | 91 | 0.12424 | 0.0013653 | No
2020-04-11 | 13:08 | L544 | Urban | Asset Failure | Distribution substation | 199 | 86.2161 | 0.022894 | 0.00026555 | No
2020-04-11 | 13:16 | BX1212 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1078 | 120.4861 | 0.17332 | 0.0014385 | No
2020-04-11 | 13:25 | 27454 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 427 | 152.1101 | 0.21368 | 0.0014048 | No
2020-04-11 | 13:26 | 8798 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 22 | 549 | 0.039735 | 7.2377e-05 | No
2020-04-11 | 13:30 | T828 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 413.8824 | 0.023147 | 5.5928e-05 | No
2020-04-11 | 13:35 | MG1286 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 391 | 94.7263 | 0.12185 | 0.0012863 | No
2020-04-11 | 13:54 | 35695 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 85 | 0.0016778 | 1.9739e-05 | No
2020-04-11 | 13:55 | PH1286 | Urban | Unknown | Unknown | 59 | 133 | 0.010471 | 7.873e-05 | No
2020-04-11 | 14:00 | L584 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 398 | 170.9397 | 0.22382 | 0.0013094 | No
2020-04-11 | 14:07 | L588 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 452 | 0.001487 | 3.2899e-06 | No
2020-04-11 | 14:09 | A045 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 101 | 356.6139 | 0.11849 | 0.00033228 | No
2020-04-11 | 14:32 | 35827 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 150 | 157.5733 | 0.077759 | 0.00049348 | No
2020-04-11 | 14:35 | 55875 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 117 | 0.0014051 | 1.201e-05 | No
2020-04-11 | 14:49 | 35990 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 211 | 0.0013883 | 6.5797e-06 | No
2020-04-11 | 14:57 | BK1299 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 66 | 123 | 0.026707 | 0.00021713 | No
2020-04-11 | 15:14 | RBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 299 | 0.0049183 | 1.6449e-05 | No
2020-04-11 | 15:15 | 35989 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 102.7942 | 107.593 | 0.036386 | 0.00033818 | No
2020-04-11 | 15:15 | 35980 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 155.2058 | 107.593 | 0.054938 | 0.00051061 | No
2020-04-11 | 15:20 | ULE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 111 | 0.0018259 | 1.6449e-05 | No
2020-04-11 | 15:26 | RBD2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 291 | 0.0019147 | 6.5797e-06 | No
2020-04-11 | 15:34 | ED1252 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 14 | 82 | 0.0037768 | 4.6058e-05 | No
2020-04-11 | 15:44 | KVA2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 30 | 155 | 0.015298 | 9.8696e-05 | No
2020-04-11 | 16:03 | ER1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 647 | 48 | 0.10217 | 0.0021285 | No
2020-04-11 | 16:05 | 8770 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 21 | 674 | 0.018887 | 2.8022e-05 | No
2020-04-11 | 16:10 | L582 | Short rural | Asset Failure | HV | 9 | 1082 | 0.032037 | 2.9609e-05 | No
2020-04-11 | 16:11 | RW1281 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 286 | 38 | 0.035754 | 0.0009409 | No
2020-04-11 | 16:27 | RV1280 | Urban | Asset Failure | Distribution substation | 9 | 255 | 0.0030624 | 1.201e-05 | No
2020-04-11 | 16:46 | PCB2 | Short rural | Weather |  | 72 | 71.9722 | 0.017048 | 0.00023687 | No
2020-04-11 | 16:47 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 446 | 0.01614 | 3.6188e-05 | No
2020-04-11 | 17:27 | 8798 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 197 | 127 | 0.082309 | 0.0006481 | No
2020-04-11 | 17:38 | T882 | Urban | Unknown | Unknown | 18 | 69 | 0.0016573 | 2.4019e-05 | No
2020-04-11 | 18:00 | 35990 | Short rural | Weather |  | 36 | 98.0278 | 0.01161 | 0.00011844 | No
2020-04-11 | 18:03 | R210 | Short rural | Asset Failure | Distribution substation | 1 | 266 | 0.0008751 | 3.2899e-06 | No
2020-04-11 | 18:41 | MVD2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 7 | 219 | 0.0050434 | 2.3029e-05 | No
2020-04-11 | 20:28 | 8798 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 4 | 116 | 0.0015265 | 1.3159e-05 | No
2020-04-11 | 20:39 | L582 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 485.6667 | 0.0047933 | 9.8696e-06 | No
2020-04-11 | 20:47 | MG1286 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1409 | 61.4911 | 0.28504 | 0.0046354 | No
2020-04-11 | 22:11 | BWH2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 8 | 928 | 0.024424 | 2.6319e-05 | No
2020-04-11 | 23:34 | T882 | Urban | Unknown | Unknown | 18 | 209 | 0.00502 | 2.4019e-05 | No
2020-04-12 | 0:34 | WH1209 | Urban | Asset Failure | Distribution substation | 79 | 86 | 0.0090659 | 0.00010542 | No
2020-04-12 | 0:37 | 27200 | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 90 | 0.00024019 | 2.6688e-06 | No
2020-04-12 | 4:21 | FT1206 | Short rural | Vegetation | Grow-in - NSP responsibility | 2 | 164 | 0.0010791 | 6.5797e-06 | No
2020-04-12 | 7:48 | R260 | Short rural | Unknown | Unknown | 1 | 200 | 0.00065797 | 3.2899e-06 | No
2020-04-12 | 8:47 | RBA2 | Short rural | Animal | Animal Impact | 2 | 183 | 0.0012041 | 6.5797e-06 | No
2020-04-12 | 9:30 | T842 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 63 | 0.00062178 | 9.8696e-06 | No
2020-04-12 | 9:35 | BL1213 | Short rural | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 4 | 57 | 0.00075009 | 1.3159e-05 | No
2020-04-12 | 9:39 | M399 | Short rural | Asset Failure | Distribution substation | 1 | 284 | 0.00093432 | 3.2899e-06 | No
2020-04-12 | 10:17 | CR1210 | Urban | Asset Failure | Distribution substation | 34 | 66.3529 | 0.0030104 | 4.537e-05 | No
2020-04-12 | 12:05 | WQ1271 | Urban | Other | Probable Equipment Failure | 1 | 138 | 0.00018415 | 1.3344e-06 | No
2020-04-12 | 13:17 | T828 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 128 | 314.7891 | 0.13256 | 0.0004211 | No
2020-04-12 | 15:54 | CV1251 | Urban | Asset Failure | Distribution substation | 28 | 57.8571 | 0.0021617 | 3.7363e-05 | No
2020-04-12 | 20:35 | TM1217 | Short rural | Asset Failure | Distribution substation | 29 | 38 | 0.0036254 | 9.5406e-05 | No
2020-04-12 | 23:12 | NWE2 | Urban | Third Party | Vehicle impact | 25 | 105 | 0.0035028 | 3.336e-05 | No
2020-04-13 | 6:05 | APG2 | Urban | Asset Failure | HV | 1586 | 67.7831 | 0.14345 | 0.0021164 | No
2020-04-13 | 7:04 | NWE2 | Urban | Third Party | Vehicle impact | 41 | 34.2927 | 0.0018762 | 5.471e-05 | No
2020-04-13 | 10:50 | NN1236 | Urban | Unknown | Unknown | 7 | 52 | 0.00048572 | 9.3408e-06 | No
2020-04-13 | 11:16 | M400 | Urban | Weather |  | 9 | 60 | 0.00072058 | 1.201e-05 | No
2020-04-13 | 12:52 | 9029 | Urban | Asset Failure | Distribution substation | 1 | 838 | 0.0011182 | 1.3344e-06 | No
2020-04-13 | 16:59 | RBB2 | Short rural | Unknown | Unknown | 12 | 200 | 0.0078957 | 3.9478e-05 | No
2020-04-13 | 17:39 | M400 | Urban | Asset Failure | Distribution substation | 1 | 42 | 5.6045e-05 | 1.3344e-06 | No
2020-04-13 | 18:56 | DP1206 | Urban | Asset Failure | Distribution substation | 17 | 117 | 0.0026541 | 2.2685e-05 | No
2020-04-13 | 19:14 | DS1226 | Urban | Asset Failure | Distribution substation | 1 | 127 | 0.00016947 | 1.3344e-06 | No
2020-04-13 | 21:19 | BWH2 | Short rural | Unknown | Unknown | 34 | 47 | 0.0052572 | 0.00011186 | No
2020-04-14 | 3:30 | NN1236 | Urban | Other | Probable Equipment Failure | 46 | 538.6087 | 0.033061 | 6.1382e-05 | No
2020-04-14 | 10:44 | FF1206 | Urban | Asset Failure | Distribution substation | 1 | 68 | 9.0739e-05 | 1.3344e-06 | No
2020-04-14 | 11:44 | 35990 | Short rural | Other | Probable Equipment Failure | 945 | 66 | 0.20519 | 0.0031089 | No
2020-04-14 | 15:23 | RBA2 | Short rural | Asset Failure | Distribution substation | 1 | 161 | 0.00052967 | 3.2899e-06 | No
2020-04-14 | 16:05 | RV1298 | Urban | Unknown | Unknown | 137 | 43 | 0.0078609 | 0.00018281 | No
2020-04-14 | 16:26 | NN1277 | Urban | Asset Failure | Distribution substation | 19 | 271 | 0.0068708 | 2.5354e-05 | No
2020-04-14 | 16:47 | 8802 | Short rural | Unknown | Unknown | 3 | 69 | 0.000681 | 9.8696e-06 | No
2020-04-15 | 7:30 | 35981 | Short rural | Asset Failure | HV | 58 | 4.9483 | 0.00094419 | 0.00019081 | No
2020-04-15 | 8:03 | MVB2 | Short rural | Animal | Animal Impact | 2 | 155.5 | 0.0010231 | 6.5797e-06 | No
2020-04-15 | 9:37 | BWF2 | Short rural | Unknown | Unknown | 2 | 233 | 0.0015331 | 6.5797e-06 | No
2020-04-15 | 10:04 | WRF2 | Short rural | Asset Failure | LV | 95 | 94.3684 | 0.029494 | 0.00031254 | No
2020-04-15 | 10:54 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 237.8359 | 156.8399 | 0.12272 | 0.00078245 | No
2020-04-15 | 10:54 | 8799 | Short rural | Vegetation | Grow-in - NSP responsibility | 393.1641 | 156.8399 | 0.20287 | 0.0012935 | No
2020-04-15 | 11:00 | OA1207 | Short rural | Unknown | Unknown | 3 | 240 | 0.0023687 | 9.8696e-06 | No
2020-04-15 | 11:37 | BYG2 | Short rural | Vegetation | Grow-in - NSP responsibility | 94 | 217.5532 | 0.067278 | 0.00030925 | No
2020-04-15 | 12:28 | APC2 | Short rural | Asset Failure | Distribution substation | 1 | 225 | 0.00074022 | 3.2899e-06 | No
2020-04-15 | 14:58 | X867 | Urban | Network business | Switching or protection error | 238 | 8 | 0.0025407 | 0.00031759 | No
2020-04-15 | 15:45 | 9019 | Urban | Asset Failure | Distribution substation | 1 | 175 | 0.00023352 | 1.3344e-06 | No
2020-04-15 | 20:54 | WH1287 | Urban | Asset Failure | Distribution substation | 10 | 132.7 | 0.0017707 | 1.3344e-05 | No
2020-04-16 | 0:22 | NA1207 | Short rural | Animal | Animal Impact | 111 | 74 | 0.027023 | 0.00036517 | No
2020-04-16 | 6:48 | J493 | Urban | Other | Probable Equipment Failure | 48 | 198.0625 | 0.012686 | 6.4051e-05 | No
2020-04-16 | 10:26 | L588 | Short rural | Asset Failure | Distribution substation | 8 | 171 | 0.0045005 | 2.6319e-05 | No
2020-04-16 | 10:30 | CD1267 | Urban | Other | Probable Equipment Failure | 15 | 65 | 0.001301 | 2.0016e-05 | No
2020-04-16 | 10:41 | BYC2 | Short rural | Unknown | Unknown | 8 | 220 | 0.0057902 | 2.6319e-05 | No
2020-04-16 | 12:43 | NG1247 | Urban | Asset Failure | LV | 9 | 147 | 0.0017654 | 1.201e-05 | No
2020-04-16 | 13:38 | J514 | Urban | Asset Failure | Distribution substation | 9 | 481 | 0.0057766 | 1.201e-05 | No
2020-04-16 | 13:59 | 6420 | Urban | Asset Failure | Distribution substation | 1 | 224 | 0.00029891 | 1.3344e-06 | No
2020-04-16 | 14:39 | YYA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1019 | 124.3248 | 0.41678 | 0.0033524 | No
2020-04-16 | 15:09 | SN1208 | Short rural | Asset Failure | Distribution substation | 11 | 154 | 0.005573 | 3.6188e-05 | No
2020-04-16 | 15:46 | MR2205 | Short rural | Asset Failure | Distribution substation | 1 | 1318 | 0.004336 | 3.2899e-06 | No
2020-04-16 | 18:00 | BGA2 | Short rural | Asset Failure | Distribution substation | 12 | 88 | 0.0034741 | 3.9478e-05 | No
2020-04-16 | 19:22 | NN1285 | Short rural | Third Party | Other | 14 | 62 | 0.0028556 | 4.6058e-05 | No
2020-04-16 | 21:57 | AB1271 | Urban | Asset Failure | Distribution substation | 1 | 140 | 0.00018682 | 1.3344e-06 | No
2020-04-16 | 23:20 | SN1282 | Short rural | Asset Failure | Distribution substation | 19 | 330.6316 | 0.020667 | 6.2507e-05 | No
2020-04-17 | 7:01 | RW1281 | Short rural | Unknown | Unknown | 2 | 160 | 0.0010528 | 6.5797e-06 | No
2020-04-17 | 9:36 | 7977 | Urban | Third Party | Dig-in | 1 | 1717 | 0.0022912 | 1.3344e-06 | No
2020-04-17 | 10:20 | 16666 | Urban | Unknown | Unknown | 12 | 60 | 0.00096077 | 1.6013e-05 | No
2020-04-17 | 11:00 | WRB2 | Urban | Asset Failure | LV | 143 | 140.5035 | 0.026811 | 0.00019082 | No
2020-04-17 | 14:09 | PCB2 | Short rural | Asset Failure | Distribution substation | 106 | 14.9151 | 0.0052013 | 0.00034873 | No
2020-04-17 | 14:42 | BYB2 | Short rural | Third Party | Vehicle impact | 7 | 776.5714 | 0.017884 | 2.3029e-05 | No
2020-04-17 | 15:22 | NG1299 | Short rural | Other | Fault within LV customers installation - Defective Equipment | 3 | 108 | 0.0010659 | 9.8696e-06 | No
2020-04-17 | 17:33 | J495 | Short rural | Vegetation | Grow-in - NSP responsibility | 10 | 42.2 | 0.0013883 | 3.2899e-05 | No
2020-04-17 | 17:49 | RW1281 | Short rural | Asset Failure | Distribution substation | 1 | 175 | 0.00057573 | 3.2899e-06 | No
2020-04-17 | 22:17 | MVB2 | Short rural | Asset Failure | Distribution substation | 1 | 873 | 0.0028721 | 3.2899e-06 | No
2020-04-17 | 22:40 | MYE2 | Short rural | Unknown | Unknown | 15 | 82 | 0.0040465 | 4.9348e-05 | No
2020-04-18 | 4:23 | RS1262 | Urban | Asset Failure | Distribution substation | 1 | 305 | 0.00040699 | 1.3344e-06 | No
2020-04-18 | 6:57 | RW1281 | Short rural | Asset Failure | Distribution substation | 1 | 332 | 0.0010922 | 3.2899e-06 | No
2020-04-18 | 12:59 | X863 | Urban | Animal | Animal Impact | 26 | 146 | 0.0050654 | 3.4694e-05 | No
2020-04-18 | 15:24 | PK1288 | Short rural | Asset Failure | Distribution substation | 1 | 108 | 0.00035531 | 3.2899e-06 | No
2020-04-18 | 16:29 | ULE2 | Short rural | Asset Failure | Distribution substation | 1 | 111 | 0.00036517 | 3.2899e-06 | No
2020-04-19 | 7:01 | CA1280 | Short rural | Asset Failure | Distribution substation | 17 | 95.2353 | 0.0053263 | 5.5928e-05 | No
2020-04-19 | 18:03 | 8776 | Urban | Asset Failure | Distribution substation | 1 | 89 | 0.00011876 | 1.3344e-06 | No
2020-04-20 | 6:34 | 35825 | Short rural | Third Party | Other | 32 | 76 | 0.0080009 | 0.00010528 | No
2020-04-20 | 9:54 | OA1207 | Short rural | Asset Failure | Distribution substation | 2 | 242 | 0.0015923 | 6.5797e-06 | No
2020-04-20 | 10:47 | J480 | Urban | Asset Failure | Distribution substation | 1 | 286 | 0.00038164 | 1.3344e-06 | No
2020-04-20 | 11:40 | MVF2 | Short rural | Vegetation | Grow-in - NSP responsibility | 153 | 177.6993 | 0.089445 | 0.00050335 | No
2020-04-20 | 12:07 | 35825 | Short rural | Third Party | Other | 1 | 139 | 0.00045729 | 3.2899e-06 | No
2020-04-20 | 15:01 | 8776 | Urban | Asset Failure | Distribution substation | 11 | 34.9091 | 0.00051241 | 1.4678e-05 | No
2020-04-20 | 18:00 | WL1251 | Urban | Overload |  | 53 | 80.283 | 0.0056779 | 7.0723e-05 | No
2020-04-20 | 18:48 | BWE2 | Short rural | Unknown | Unknown | 21 | 32 | 0.0022108 | 6.9087e-05 | No
2020-04-20 | 19:50 | W123 | Short rural | Network business | Network error | 8 | 10 | 0.00026319 | 2.6319e-05 | No
2020-04-20 | 21:43 | RW1292 | Short rural | Animal | Animal Impact | 3 | 86 | 0.00084878 | 9.8696e-06 | No
2020-04-21 | 1:20 | 68204 | Urban | Third Party | Other | 2 | 500 | 0.0013344 | 2.6688e-06 | No
2020-04-21 | 4:22 | ULF2 | Short rural | Animal | Animal Impact | 1760 | 56 | 0.32425 | 0.0057902 | No
2020-04-21 | 11:07 | RW1218 | Short rural | Asset Failure | Distribution substation | 3 | 199 | 0.001964 | 9.8696e-06 | No
2020-04-21 | 12:57 | CT1206 | Urban | Other | Probable Equipment Failure | 14 | 92.2143 | 0.0017227 | 1.8682e-05 | No
2020-04-21 | 13:16 | 8694 | Urban | Asset Failure | Distribution substation | 6 | 140.8333 | 0.0011276 | 8.0064e-06 | No
2020-04-21 | 18:13 | SN1208 | Short rural | Asset Failure | Distribution substation | 10 | 114 | 0.0037504 | 3.2899e-05 | No
2020-04-22 | 6:46 | 35304 | Urban | Asset Failure | HV | 1147 | 62.6478 | 0.095886 | 0.0015306 | No
2020-04-22 | 7:23 | NN1233 | Short rural | Other | Probable Equipment Failure | 4 | 136.75 | 0.0017996 | 1.3159e-05 | No
2020-04-22 | 10:40 | 840 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 134 | 0.0013225 | 9.8696e-06 | No
2020-04-22 | 14:10 | CV1247 | Urban | Third Party | Vehicle impact | 129 | 181.8992 | 0.031312 | 0.00017214 | No
2020-04-22 | 14:36 | X877 | Short rural | Unknown | Unknown | 15 | 249 | 0.012288 | 4.9348e-05 | No
2020-04-22 | 16:55 | HR1280 | Short rural | Third Party | Other | 30 | 75 | 0.0074022 | 9.8696e-05 | No
2020-04-23 | 8:14 | NA1266 | Urban | Asset Failure | Distribution substation | 120 | 291.1333 | 0.046619 | 0.00016013 | No
2020-04-23 | 12:00 | RV1298 | Urban | Unknown | Unknown | 7 | 64 | 0.00059781 | 9.3408e-06 | No
2020-04-23 | 12:30 | 2813 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 153 | 0.00020416 | 1.3344e-06 | No
2020-04-23 | 16:49 | NM1239 | Urban | Third Party | Other | 24 | 108 | 0.0034588 | 3.2026e-05 | No
2020-04-23 | 17:38 | 9017 | Urban | Asset Failure | Distribution substation | 1 | 129 | 0.00017214 | 1.3344e-06 | No
2020-04-23 | 20:59 | J491 | Urban | Asset Failure | Distribution substation | 21 | 65.7143 | 0.0018415 | 2.8022e-05 | No
2020-04-24 | 3:57 | KC1236 | Short rural | Third Party | Other | 259 | 62.471 | 0.05323 | 0.00085207 | No
2020-04-24 | 8:56 | OP1192 | Urban | Asset Failure | Distribution substation | 14 | 102 | 0.0019055 | 1.8682e-05 | No
2020-04-24 | 10:03 | KC1236 | Short rural | Unknown | Unknown | 5 | 117 | 0.0019246 | 1.6449e-05 | No
2020-04-24 | 10:04 | RV1298 | Urban | Asset Failure | Distribution substation | 15 | 221 | 0.0044235 | 2.0016e-05 | No
2020-04-24 | 10:52 | NE1279 | Urban | Network business | Network error | 12 | 99.4167 | 0.0015919 | 1.6013e-05 | No
2020-04-24 | 15:18 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 42 | 20 | 0.0027635 | 0.00013817 | No
2020-04-24 | 17:17 | PH1286 | Urban | Network business | Switching or protection error | 1467.6849 | 13 | 0.02546 | 0.0019585 | No
2020-04-24 | 17:17 | PH1219 | Urban | Network business | Switching or protection error | 1082.3151 | 13 | 0.018775 | 0.0014442 | No
2020-04-24 | 21:26 | J493 | Urban | Asset Failure | Distribution substation | 4 | 413 | 0.0022044 | 5.3376e-06 | No
2020-04-25 | 9:22 | KC1236 | Short rural | Unknown | Unknown | 11 | 100 | 0.0036188 | 3.6188e-05 | No
2020-04-25 | 14:40 | KYH2 | Urban | Third Party | Vehicle impact | 142 | 74.1268 | 0.014046 | 0.00018948 | No
2020-04-25 | 19:00 | 55885 | Urban | Animal | Animal Impact | 48 | 73 | 0.0046757 | 6.4051e-05 | No
2020-04-26 | 1:30 | DFC2 | Short rural | Other | Probable Birds | 2 | 485.5 | 0.0031945 | 6.5797e-06 | No
2020-04-26 | 2:25 | 2809 | Urban | Asset Failure | LV | 619 | 113.0339 | 0.093365 | 0.00082599 | No
2020-04-26 | 16:43 | YYB2 | Short rural | Unknown | Unknown | 13 | 58 | 0.0024806 | 4.2768e-05 | No
2020-04-26 | 19:35 | RW1218 | Short rural | Vegetation | Grow-in - NSP responsibility | 80 | 259 | 0.068166 | 0.00026319 | No
2020-04-26 | 20:34 | X482 | Short rural | Unknown | Unknown | 26 | 70 | 0.0059876 | 8.5536e-05 | No
2020-04-26 | 22:24 | AZ1272 | Short rural | Animal | Animal Impact | 1429 | 127.7033 | 0.60036 | 0.0047012 | No
2020-04-27 | 4:42 | NA1214 | Urban | Asset Failure | Distribution substation | 70 | 509 | 0.047545 | 9.3408e-05 | No
2020-04-27 | 7:05 | CD1271 | Short rural | Asset Failure | Distribution substation | 5 | 531 | 0.0087346 | 1.6449e-05 | No
2020-04-27 | 7:33 | RW1292 | Short rural | Vegetation | Grow-in - NSP responsibility | 11 | 218 | 0.0078891 | 3.6188e-05 | No
2020-04-27 | 8:59 | B748 | Urban | Third Party | Other | 196 | 62 | 0.016216 | 0.00026154 | No
2020-04-27 | 9:22 | CD1297 | Urban | Asset Failure | Distribution substation | 1 | 203 | 0.00027088 | 1.3344e-06 | No
2020-04-27 | 12:20 | J480 | Urban | Asset Failure | Distribution substation | 20 | 33 | 0.0008807 | 2.6688e-05 | No
2020-04-27 | 13:38 | SC1216 | Urban | Third Party | Vehicle impact | 1154 | 81 | 0.12473 | 0.0015399 | No
2020-04-27 | 16:31 | BYC2 | Short rural | Asset Failure | LV | 24 | 32 | 0.0025266 | 7.8957e-05 | No
2020-04-27 | 16:38 | W111 | Short rural | Other | Isolation Request by EE | 9 | 15 | 0.00044413 | 2.9609e-05 | No
2020-04-27 | 21:03 | 27187 | Urban | Asset Failure | Distribution substation | 15 | 45.0667 | 0.00090205 | 2.0016e-05 | No
2020-04-28 | 1:51 | W124 | Short rural | Unknown | Unknown | 52 | 277 | 0.047387 | 0.00017107 | No
2020-04-28 | 12:00 | 49916 | Urban | Asset Failure | HV | 988 | 17.4271 | 0.022976 | 0.0013184 | No
2020-04-28 | 12:36 | APF2 | Short rural | Asset Failure | Distribution substation | 1 | 204 | 0.00067113 | 3.2899e-06 | No
2020-04-28 | 14:22 | S786 | Short rural | Asset Failure | Distribution substation | 2 | 79 | 0.0005198 | 6.5797e-06 | No
2020-04-28 | 16:28 | CD1260 | Urban | Unknown | Unknown | 82 | 90 | 0.0098479 | 0.00010942 | No
2020-04-28 | 16:56 | W196 | Urban | Asset Failure | Distribution substation | 1 | 51 | 6.8054e-05 | 1.3344e-06 | No
2020-04-28 | 17:16 | 35816 | Short rural | Asset Failure | Distribution substation | 10 | 86 | 0.0028293 | 3.2899e-05 | No
2020-04-29 | 9:17 | J514 | Urban | Asset Failure | Distribution substation | 1 | 92 | 0.00012276 | 1.3344e-06 | No
2020-04-29 | 12:34 | S788 | Short rural | Asset Failure | Distribution substation | 5 | 322.2 | 0.0053 | 1.6449e-05 | No
2020-04-29 | 18:08 | 35693 | Short rural | Weather |  | 28 | 79 | 0.0072772 | 9.2116e-05 | No
2020-04-29 | 18:34 | W124 | Short rural | Weather |  | 1 | 118 | 0.0003882 | 3.2899e-06 | No
2020-04-29 | 19:44 | BL1210 | Short rural | Asset Failure | HV | 1426 | 46.4102 | 0.21773 | 0.0046913 | No
2020-04-29 | 19:48 | J493 | Urban | Unknown | Unknown | 4 | 73 | 0.00038964 | 5.3376e-06 | No
2020-04-29 | 20:17 | 41537 | Urban | Asset Failure | Distribution substation | 29 | 101.9655 | 0.0039458 | 3.8698e-05 | No
2020-04-29 | 20:59 | BK1251 | Short rural | Vegetation | Grow-in - NSP responsibility | 106 | 137.5849 | 0.047979 | 0.00034873 | No
2020-04-29 | 21:16 | B743 | Urban | Asset Failure | HV | 853.3342 | 61.3023 | 0.069804 | 0.0011387 | No
2020-04-29 | 21:16 | CN1206 | Urban | Asset Failure | HV | 337.6658 | 61.3023 | 0.027622 | 0.00045058 | No
2020-04-30 | 1:22 | J514 | Urban | Unknown | Unknown | 8 | 342 | 0.0036509 | 1.0675e-05 | No
2020-04-30 | 7:40 | M399 | Short rural | Vegetation | Grow-in - NSP responsibility | 109 | 148.4679 | 0.05324 | 0.0003586 | No
2020-04-30 | 11:00 | KVC2 | Short rural | Other | Fire | 1 | 92 | 0.00030267 | 3.2899e-06 | No
2020-04-30 | 11:07 | ULC2 | Short rural | Asset Failure | HV | 1321 | 4.1998 | 0.018252 | 0.0043459 | No
2020-04-30 | 11:34 | X867 | Urban | Vegetation | Grow-in - NSP responsibility | 928.1526 | 70 | 0.086697 | 0.0012385 | No
2020-04-30 | 11:34 | 8735 | Urban | Vegetation | Grow-in - NSP responsibility | 535.8474 | 70 | 0.050052 | 0.00071503 | No
2020-04-30 | 12:02 | 35327 | Urban | Asset Failure | Distribution substation | 1 | 199 | 0.00026555 | 1.3344e-06 | No
2020-04-30 | 12:31 | J493 | Urban | Weather |  | 4 | 90 | 0.00048038 | 5.3376e-06 | No
2020-04-30 | 13:45 | JS1232 | Urban | Asset Failure | Distribution substation | 1 | 78 | 0.00010408 | 1.3344e-06 | No
2020-04-30 | 13:54 | 8777 | Urban | Asset Failure | Distribution substation | 43 | 40.5349 | 0.0023259 | 5.7379e-05 | No
2020-04-30 | 14:52 | T834 | Short rural | Vegetation | Grow-in - NSP responsibility | 131 | 145.9313 | 0.062892 | 0.00043097 | No
2020-04-30 | 15:17 | B743 | Urban | Asset Failure | Distribution substation | 31 | 322.1613 | 0.013327 | 4.1366e-05 | No
2020-04-30 | 15:58 | MM1202 | Urban | Asset Failure | Distribution substation | 1 | 451 | 0.00060181 | 1.3344e-06 | No
2020-04-30 | 16:21 | BWD2 | Urban | Asset Failure | Distribution substation | 18 | 63 | 0.0015132 | 2.4019e-05 | No
2020-04-30 | 17:52 | 35696 | Short rural | Asset Failure | Distribution substation | 17 | 101.7647 | 0.0056915 | 5.5928e-05 | No
2020-04-30 | 21:21 | 4873 | Urban | Asset Failure | Distribution substation | 13 | 54 | 0.00093675 | 1.7347e-05 | No
2020-05-01 | 0:08 | CA1206 | Short rural | Asset Failure | Distribution substation | 92 | 142.4348 | 0.04311 | 0.00030267 | No
2020-05-01 | 6:44 | 87222 | Long rural | Asset Failure | HV | 306 | 148.5784 | 144.793 | 0.97452 | No
2020-05-01 | 7:12 | CLC2 | Short rural | Asset Failure | Distribution substation | 29 | 83 | 0.0079187 | 9.5406e-05 | No
2020-05-01 | 7:53 | MVH2 | Short rural | Unknown | Unknown | 1 | 205 | 0.00067442 | 3.2899e-06 | No
2020-05-01 | 8:00 | L513 | Urban | Asset Failure | Distribution substation | 41 | 494.561 | 0.027058 | 5.471e-05 | No
2020-05-01 | 9:25 | CD1234 | Short rural | Weather |  | 1 | 38 | 0.00012501 | 3.2899e-06 | No
2020-05-01 | 9:31 | PH1230 | Urban | Asset Failure | Distribution substation | 8 | 78 | 0.00083267 | 1.0675e-05 | No
2020-05-01 | 10:27 | X877 | Short rural | Unknown | Unknown | 4 | 60 | 0.00078957 | 1.3159e-05 | No
2020-05-01 | 12:00 | WL1280 | Urban | Asset Failure | Distribution substation | 194 | 16 | 0.004142 | 0.00025887 | No
2020-05-01 | 12:27 | ER1252 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 133 | 0.0013127 | 9.8696e-06 | No
2020-05-01 | 12:51 | NG1262 | Short rural | Asset Failure | Distribution substation | 20 | 171 | 0.011251 | 6.5797e-05 | No
2020-05-01 | 13:14 | NA1236 | Short rural | Asset Failure | HV | 1720 | 39.3448 | 0.22263 | 0.0056586 | No
2020-05-01 | 13:32 | 8764 | Urban | Unknown | Unknown | 30 | 112 | 0.0044836 | 4.0032e-05 | No
2020-05-01 | 14:49 | J481 | Urban | Asset Failure | Distribution substation | 7 | 95 | 0.00088738 | 9.3408e-06 | No
2020-05-01 | 15:10 | J504 | Urban | Asset Failure | Distribution substation | 1 | 158 | 0.00021084 | 1.3344e-06 | No
2020-05-01 | 15:11 | YYB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 74 | 0.004869 | 6.5797e-05 | No
2020-05-01 | 17:26 | 35304 | Urban | Asset Failure | Distribution substation | 21 | 109 | 0.0030544 | 2.8022e-05 | No
2020-05-01 | 17:39 | A096 | Short rural | Asset Failure | Distribution substation | 2 | 184 | 0.0012107 | 6.5797e-06 | No
2020-05-01 | 19:36 | BWE2 | Short rural | Unknown | Unknown | 18 | 73 | 0.0043229 | 5.9218e-05 | No
2020-05-01 | 20:40 | WX1280 | Urban | Asset Failure | HV | 102 | 113.0784 | 0.015391 | 0.00013611 | No
2020-05-01 | 22:32 | NG1210 | Short rural | Unknown | Unknown | 241 | 119.6722 | 0.094883 | 0.00079286 | No
2020-05-02 | 0:37 | BX1332 | Urban | Third Party | Other | 1 | 411 | 0.00054844 | 1.3344e-06 | No
2020-05-02 | 0:48 | NG1210 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 199 | 188.6683 | 0.12352 | 0.00065468 | No
2020-05-02 | 2:44 | W111 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 283 | 206.7456 | 0.19249 | 0.00093103 | No
2020-05-02 | 4:37 | KVC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 37 | 892.3243 | 0.10862 | 0.00012172 | No
2020-05-02 | 7:40 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 162.6241 | 323.5479 | 0.1731 | 0.00053501 | No
2020-05-02 | 7:40 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 98.3759 | 323.5479 | 0.10471 | 0.00032364 | No
2020-05-02 | 7:56 | BDB2 | Urban | Weather |  | 79 | 91.1646 | 0.0096103 | 0.00010542 | No
2020-05-02 | 8:04 | CX1232 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 87.1695 | 280.9459 | 0.080568 | 0.00028678 | No
2020-05-02 | 8:04 | D810 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 23.8305 | 280.9459 | 0.022026 | 7.8399e-05 | No
2020-05-02 | 8:05 | WX1280 | Urban | Asset Failure | LV | 3 | 81 | 0.00032426 | 4.0032e-06 | No
2020-05-02 | 8:10 | BX1222 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 132 | 249.6591 | 0.043975 | 0.00017614 | No
2020-05-02 | 8:24 | L591 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 71 | 198.4789 | 0.046361 | 0.00023358 | No
2020-05-02 | 8:31 | J505 | Urban | Asset Failure | Distribution substation | 1 | 312 | 0.00041633 | 1.3344e-06 | No
2020-05-02 | 8:34 | JBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 40 | 47 | 0.0061849 | 0.00013159 | No
2020-05-02 | 8:44 | 10242 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 79 | 142.3038 | 0.036985 | 0.0002599 | No
2020-05-02 | 8:50 | DP1284 | Short rural | Weather |  | 16 | 199.1875 | 0.010485 | 5.2638e-05 | No
2020-05-02 | 8:55 | TM1217 | Short rural | Weather |  | 1628 | 109.8372 | 0.58828 | 0.0053559 | No
2020-05-02 | 9:13 | RBE2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 414 | 80.6667 | 0.10987 | 0.001362 | No
2020-05-02 | 9:27 | RW1218 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 328 | 0.0032372 | 9.8696e-06 | No
2020-05-02 | 9:34 | BYC2 | Short rural | Weather |  | 208 | 219.3846 | 0.15012 | 0.00068429 | No
2020-05-02 | 9:45 | NA1270 | Short rural | Other | Probable Wind (Windborne material - iron, wire, timber, kite) | 33 | 336 | 0.036478 | 0.00010857 | No
2020-05-02 | 9:49 | MVC2 | Short rural | Animal | Animal Impact | 3 | 80 | 0.00078957 | 9.8696e-06 | No
2020-05-02 | 9:52 | BYC2 | Short rural | Weather |  | 168 | 158.3452 | 0.087517 | 0.0005527 | No
2020-05-02 | 9:58 | W118 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 734 | 334.2779 | 0.8072 | 0.0024148 | No
2020-05-02 | 10:40 | YYB2 | Short rural | Asset Failure | Distribution substation | 14 | 174 | 0.0080141 | 4.6058e-05 | No
2020-05-02 | 10:48 | BDG2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 1074 | 182.4981 | 0.64482 | 0.0035333 | No
2020-05-02 | 11:07 | 25781 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1905 | 57 | 0.1449 | 0.002542 | No
2020-05-02 | 11:12 | NA1207 | Short rural | Weather |  | 116 | 217.7155 | 0.083085 | 0.00038162 | No
2020-05-02 | 11:13 | 35702 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 80 | 302.8 | 0.032324 | 0.00010675 | No
2020-05-02 | 11:45 | X877 | Short rural | Asset Failure | Distribution substation | 4 | 320 | 0.004211 | 1.3159e-05 | No
2020-05-02 | 12:00 | 55880 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 261 | 39.8659 | 0.013884 | 0.00034828 | No
2020-05-02 | 13:07 | 35010 | Urban | Asset Failure | Distribution substation | 21 | 156 | 0.0043715 | 2.8022e-05 | No
2020-05-02 | 13:09 | L588 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 116 | 0.0045795 | 3.9478e-05 | No
2020-05-02 | 13:14 | 8798 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 58 | 0.0011449 | 1.9739e-05 | No
2020-05-02 | 13:37 | MG1208 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 165 | 0.012485 | 7.5667e-05 | No
2020-05-02 | 13:42 | RBB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 140 | 222.4786 | 0.10247 | 0.00046058 | No
2020-05-02 | 14:12 | 8801 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 430.4 | 0.01416 | 3.2899e-05 | No
2020-05-02 | 14:14 | BYC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 78 | 136.7051 | 0.03508 | 0.00025661 | No
2020-05-02 | 14:17 | 8799 | Short rural | Weather |  | 1476 | 10.3476 | 0.050246 | 0.0048558 | No
2020-05-02 | 14:25 | WX1280 | Urban | Asset Failure | HV | 25 | 1687.64 | 0.0563 | 3.336e-05 | No
2020-05-02 | 14:28 | MVF2 | Short rural | Asset Failure | HV | 11 | 230.8182 | 0.008353 | 3.6188e-05 | No
2020-05-02 | 14:29 | CX1284 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 212 | 114 | 0.079509 | 0.00069745 | No
2020-05-02 | 14:46 | 8802 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1 | 119 | 0.00039149 | 3.2899e-06 | No
2020-05-02 | 14:47 | 8798 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 22 | 71 | 0.0051388 | 7.2377e-05 | No
2020-05-02 | 14:51 | JBA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 29 | 40 | 0.0038162 | 9.5406e-05 | No
2020-05-02 | 15:14 | BWH2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 34 | 264 | 0.02953 | 0.00011186 | No
2020-05-02 | 15:15 | L941 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 87 | 0.0031484 | 3.6188e-05 | No
2020-05-02 | 15:43 | ER1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 317 | 0.017729 | 5.5928e-05 | No
2020-05-02 | 15:54 | W118 | Short rural | Weather |  | 734.4282 | 99 | 0.2392 | 0.0024162 | No
2020-05-02 | 15:54 | W120 | Short rural | Weather |  | 1170.6825 | 99 | 0.38129 | 0.0038514 | No
2020-05-02 | 15:54 | W123 | Short rural | Weather |  | 1027.5991 | 99 | 0.33469 | 0.0033807 | No
2020-05-02 | 15:54 | W124 | Short rural | Weather |  | 1136.6626 | 99 | 0.37021 | 0.0037395 | No
2020-05-02 | 15:54 | W126 | Short rural | Weather |  | 82.0478 | 99 | 0.026723 | 0.00026993 | No
2020-05-02 | 15:54 | W127 | Short rural | Weather |  | 994.5798 | 99 | 0.32393 | 0.003272 | No
2020-05-02 | 15:57 | 55361 | Urban | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 8 | 168 | 0.0017934 | 1.0675e-05 | No
2020-05-02 | 16:14 | S788 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 747 | 247.1406 | 0.60735 | 0.0024575 | No
2020-05-02 | 16:17 | JS1252 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 48 | 2933.1667 | 0.46319 | 0.00015791 | No
2020-05-02 | 16:23 | S744 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 516 | 103.6899 | 0.071396 | 0.00068855 | No
2020-05-02 | 16:24 | 8798 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 1056 | 0.052111 | 4.9348e-05 | No
2020-05-02 | 16:24 | 8799 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 498 | 0.027852 | 5.5928e-05 | No
2020-05-02 | 16:49 | S788 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 33 | 28 | 0.0030398 | 0.00010857 | No
2020-05-02 | 17:37 | MVB2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 22 | 1184.2727 | 0.085714 | 7.2377e-05 | No
2020-05-02 | 17:49 | L947 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 102 | 958.2843 | 0.32157 | 0.00033557 | No
2020-05-02 | 17:55 | RD1251 | Urban | Asset Failure | Distribution substation | 37 | 100 | 0.0049373 | 4.9373e-05 | No
2020-05-02 | 17:59 | BYC2 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 2 | 218 | 0.0014344 | 6.5797e-06 | No
2020-05-02 | 18:01 | S786 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 615 | 164 | 0.33182 | 0.0020233 | No
2020-05-02 | 18:19 | PH1219 | Urban | Weather |  | 1132 | 95 | 0.1435 | 0.0015105 | No
2020-05-02 | 18:20 | BX1352 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 318 | 107.7421 | 0.045719 | 0.00042434 | No
2020-05-02 | 18:32 | 8762 | Urban | Asset Failure | LV | 1343 | 79.6761 | 0.14279 | 0.0017921 | No
2020-05-02 | 18:33 | ER1232 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 285.7308 | 204.678 | 0.1924 | 0.00094002 | No
2020-05-02 | 18:33 | ER1122 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 224.6863 | 204.678 | 0.1513 | 0.00073919 | No
2020-05-02 | 18:33 | ER1252 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 135.5829 | 204.678 | 0.091296 | 0.00044605 | No
2020-05-02 | 19:10 | PH1271 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 143 | 93.6993 | 0.01788 | 0.00019082 | No
2020-05-02 | 19:24 | 8798 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 1373 | 132 | 0.59624 | 0.004517 | No
2020-05-02 | 20:01 | ER1142 | Urban | Asset Failure | Distribution substation | 5 | 366.4 | 0.0024446 | 6.672e-06 | No
2020-05-02 | 20:16 | BDG2 | Short rural | Asset Failure | LV | 36 | 121.0556 | 0.014337 | 0.00011844 | No
2020-05-02 | 20:26 | S327 | Urban | Unknown | Unknown | 14 | 213 | 0.0039792 | 1.8682e-05 | No
2020-05-02 | 20:31 | JBB2 | Short rural | Weather |  | 6 | 98 | 0.0019344 | 1.9739e-05 | No
2020-05-02 | 22:38 | MM1222 | Urban | Asset Failure | HV | 958 | 57.715 | 0.07378 | 0.0012784 | No
2020-05-02 | 23:28 | ER1252 | Short rural | Other | Probable Wind (Growing or falling tree or branches not felled or lopped - bark, grass) | 3 | 605 | 0.0059711 | 9.8696e-06 | No
2020-05-03 | 0:15 | S327 | Urban | Other | Probable Accidental Damage Excavation | 14 | 500 | 0.0093408 | 1.8682e-05 | No
2020-05-03 | 1:47 | W123 | Short rural | Third Party | Vehicle impact | 25 | 531 | 0.043673 | 8.2247e-05 | No
2020-05-03 | 2:55 | S744 | Urban | Unknown | Unknown | 5 | 277 | 0.0018481 | 6.672e-06 | No
2020-05-03 | 7:27 | 5495 | Urban | Unknown | Unknown | 87 | 82 | 0.0095196 | 0.00011609 | No
2020-05-03 | 7:38 | 27454 | Short rural | Vegetation | Grow-in - NSP responsibility | 8 | 260 | 0.0068429 | 2.6319e-05 | No
2020-05-03 | 8:56 | BYC2 | Short rural | Weather |  | 2 | 184 | 0.0012107 | 6.5797e-06 | No
2020-05-03 | 9:15 | WD1221 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 47.8 | 0.00078628 | 1.6449e-05 | No
2020-05-03 | 10:47 | ER1122 | Short rural | Vegetation | Grow-in - NSP responsibility | 5 | 281 | 0.0046223 | 1.6449e-05 | No
2020-05-03 | 13:17 | KME2 | Short rural | Asset Failure | Distribution substation | 1 | 135 | 0.00044413 | 3.2899e-06 | No
2020-05-03 | 16:01 | J516 | Urban | Unknown | Unknown | 49 | 87 | 0.0056885 | 6.5386e-05 | No
2020-05-03 | 16:36 | KME2 | Short rural | Unknown | Unknown | 2 | 64 | 0.0004211 | 6.5797e-06 | No
2020-05-03 | 17:37 | J506 | Urban | Asset Failure | Distribution substation | 1 | 28 | 3.7363e-05 | 1.3344e-06 | No
2020-05-03 | 19:48 | OA1207 | Short rural | Animal | Animal Impact | 44 | 28 | 0.0040531 | 0.00014475 | No
2020-05-04 | 2:07 | J516 | Urban | Asset Failure | Distribution substation | 49 | 480 | 0.031385 | 6.5386e-05 | No
2020-05-04 | 6:26 | WL1292 | Urban | Animal | Animal Impact | 1259 | 81.4273 | 0.1368 | 0.00168 | No
2020-05-04 | 9:52 | SY1132 | Urban | Third Party | Other | 22 | 190 | 0.0055778 | 2.9357e-05 | No
2020-05-04 | 13:16 | A346 | Urban | Third Party | Other | 14 | 151 | 0.0028209 | 1.8682e-05 | No
2020-05-04 | 13:32 | S764 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 370 | 0.0036517 | 9.8696e-06 | No
2020-05-05 | 8:18 | 35767 | Urban | Third Party | Vehicle impact | 21 | 197 | 0.0055204 | 2.8022e-05 | No
2020-05-05 | 8:51 | 8798 | Short rural | Unknown | Unknown | 1 | 294 | 0.00096722 | 3.2899e-06 | No
2020-05-05 | 9:37 | 10251 | Urban | Asset Failure | Distribution substation | 93 | 197 | 0.024448 | 0.0001241 | No
2020-05-05 | 11:23 | CX1232 | Short rural | Weather |  | 8 | 47 | 0.001237 | 2.6319e-05 | No
2020-05-05 | 14:28 | NA1207 | Short rural | Asset Failure | HV | 5 | 64 | 0.0010528 | 1.6449e-05 | No
2020-05-05 | 14:44 | X881 | Short rural | Asset Failure | Distribution substation | 14 | 206 | 0.009488 | 4.6058e-05 | No
2020-05-05 | 16:01 | BL1251 | Urban | Asset Failure | Distribution substation | 45 | 17 | 0.0010208 | 6.0048e-05 | No
2020-05-05 | 18:20 | A346 | Urban | Other | Probable Accidental Damage - Vehicle High Load | 56 | 87 | 0.0065012 | 7.4726e-05 | No
2020-05-05 | 22:29 | A346 | Urban | Asset Failure | Distribution substation | 42 | 212.9286 | 0.011934 | 5.6045e-05 | No
2020-05-06 | 0:21 | LP1142 | Urban | Asset Failure | Distribution substation | 9 | 492 | 0.0059087 | 1.201e-05 | No
2020-05-06 | 4:52 | X482 | Short rural | Unknown | Unknown | 67 | 121 | 0.026671 | 0.00022042 | No
2020-05-06 | 8:35 | 35815 | Short rural | Third Party | Other | 524 | 63 | 0.1086 | 0.0017239 | No
2020-05-06 | 9:17 | CR1214 | Urban | Asset Failure | Distribution substation | 1 | 143 | 0.00019082 | 1.3344e-06 | No
2020-05-06 | 9:57 | 4871 | Urban | Asset Failure | Distribution substation | 37 | 202 | 0.0099733 | 4.9373e-05 | No
2020-05-06 | 11:02 | X881 | Short rural | Asset Failure | Distribution substation | 12 | 231 | 0.0091195 | 3.9478e-05 | No
2020-05-06 | 11:58 | JS1252 | Short rural | Asset Failure | Distribution substation | 30 | 24.5 | 0.002418 | 9.8696e-05 | No
2020-05-06 | 12:15 | SV1122 | Urban | Other | Isolation Request by EE | 60 | 4 | 0.00032026 | 8.0064e-05 | No
2020-05-06 | 12:56 | 27142 | Urban | Third Party | Dig-in | 1 | 589 | 0.00078596 | 1.3344e-06 | No
2020-05-06 | 14:26 | CN1239 | Urban | Asset Failure | Distribution substation | 20 | 328 | 0.0087537 | 2.6688e-05 | No
2020-05-06 | 17:45 | LP1422 | Urban | Other | Probable Equipment Failure | 1 | 174 | 0.00023219 | 1.3344e-06 | No
2020-05-06 | 18:01 | PH1286 | Urban | Asset Failure | Distribution substation | 11 | 186 | 0.0027302 | 1.4678e-05 | No
2020-05-06 | 21:15 | BGA2 | Short rural | Asset Failure | HV | 13 | 244 | 0.010435 | 4.2768e-05 | No
2020-05-07 | 6:38 | CD1230 | Short rural | Unknown | Unknown | 2 | 91 | 0.00059876 | 6.5797e-06 | No
2020-05-07 | 8:14 | MVE2 | Short rural | Unknown | Unknown | 4 | 67 | 0.00088168 | 1.3159e-05 | No
2020-05-07 | 8:31 | FT1202 | Urban | Asset Failure | Distribution substation | 1 | 73 | 9.7411e-05 | 1.3344e-06 | No
2020-05-07 | 9:11 | CV1251 | Urban | Asset Failure | Distribution substation | 1 | 251 | 0.00033493 | 1.3344e-06 | No
2020-05-07 | 11:51 | SHE2 | Urban | Third Party | Other | 1794 | 57.0992 | 0.13669 | 0.0023939 | No
2020-05-07 | 11:55 | TM1210 | Short rural | Asset Failure | Distribution substation | 9 | 44.2222 | 0.0013094 | 2.9609e-05 | No
2020-05-07 | 13:02 | ULH2 | Short rural | Asset Failure | LV | 1 | 84 | 0.00027635 | 3.2899e-06 | No
2020-05-07 | 15:53 | PCB2 | Short rural | Asset Failure | HV | 992 | 132.75 | 0.43324 | 0.0032635 | No
2020-05-07 | 16:56 | 8779 | Urban | Asset Failure | Distribution substation | 1 | 68 | 9.0739e-05 | 1.3344e-06 | No
2020-05-07 | 19:19 | ER1252 | Short rural | Third Party | Vehicle impact | 5 | 273 | 0.0044907 | 1.6449e-05 | No
2020-05-07 | 21:23 | 9027 | Urban | Asset Failure | HV | 286 | 68.2937 | 0.026063 | 0.00038164 | No
2020-05-08 | 4:18 | 55876 | Urban | Third Party | Other | 7 | 237 | 0.0022138 | 9.3408e-06 | No
2020-05-08 | 6:04 | X881 | Short rural | Asset Failure | Distribution substation | 14 | 53 | 0.0024411 | 4.6058e-05 | No
2020-05-08 | 8:22 | 87222 | Long rural | Animal | Animal Impact | 1 | 527 | 1.6783 | 0.0031847 | No
2020-05-08 | 9:50 | RBA2 | Short rural | Third Party | Other | 207 | 102.4493 | 0.069768 | 0.000681 | No
2020-05-08 | 10:58 | 35010 | Urban | Asset Failure | Distribution substation | 15 | 236 | 0.0047238 | 2.0016e-05 | No
2020-05-08 | 13:58 | MVC2 | Short rural | Unknown | Unknown | 7 | 135 | 0.0031089 | 2.3029e-05 | No
2020-05-08 | 15:19 | 68204 | Urban | Asset Failure | Distribution substation | 7 | 159.2857 | 0.0014879 | 9.3408e-06 | No
2020-05-08 | 15:20 | WH1235 | Urban | Third Party | Other | 26 | 78 | 0.0027062 | 3.4694e-05 | No
2020-05-08 | 21:59 | LP1422 | Urban | Other | Fire | 47 | 104 | 0.0065225 | 6.2717e-05 | No
2020-05-09 | 8:50 | BYC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 3 | 41 | 0.00040465 | 9.8696e-06 | No
2020-05-09 | 9:06 | L948 | Short rural | Third Party | Other | 8 | 274 | 0.0072114 | 2.6319e-05 | No
2020-05-09 | 10:46 | MVG2 | Urban | Asset Failure | Distribution substation | 2 | 161 | 0.00042968 | 2.6688e-06 | No
2020-05-09 | 17:15 | J495 | Short rural | Asset Failure | Distribution substation | 1 | 188 | 0.00061849 | 3.2899e-06 | No
2020-05-10 | 7:28 | C852 | Urban | Unknown | Unknown | 36 | 81 | 0.0038911 | 4.8038e-05 | No
2020-05-10 | 8:19 | ER1252 | Short rural | Asset Failure | Distribution substation | 45 | 193 | 0.028572 | 0.00014804 | No
2020-05-10 | 10:53 | X877 | Short rural | Third Party | Other | 7 | 9 | 0.00020726 | 2.3029e-05 | No
2020-05-10 | 12:10 | CR1210 | Urban | Asset Failure | Distribution substation | 35 | 80 | 0.0037363 | 4.6704e-05 | No
2020-05-10 | 21:57 | 8610 | Urban | Unknown | Unknown | 33 | 119 | 0.0052402 | 4.4035e-05 | No
2020-05-11 | 5:28 | L946 | Short rural | Asset Failure | HV | 50 | 183 | 0.030102 | 0.00016449 | No
2020-05-11 | 7:46 | SC1289 | Short rural | Unknown | Unknown | 3 | 114 | 0.0011251 | 9.8696e-06 | No
2020-05-11 | 7:48 | MYQ2 | Short rural | Unknown | Unknown | 5 | 243.8 | 0.0040103 | 1.6449e-05 | No
2020-05-11 | 9:01 | 87220 | Short rural | Asset Failure | Distribution substation | 1 | 357 | 0.0011745 | 3.2899e-06 | No
2020-05-11 | 11:36 | D813 | Short rural | Asset Failure | LV | 39 | 336.3333 | 0.043153 | 0.0001283 | No
2020-05-11 | 17:07 | GV1204 | Urban | Asset Failure | Distribution substation | 85 | 217.2353 | 0.02464 | 0.00011342 | No
2020-05-11 | 17:41 | L588 | Short rural | Asset Failure | Distribution substation | 2 | 171 | 0.0011251 | 6.5797e-06 | No
2020-05-11 | 18:32 | TM1258 | Short rural | Asset Failure | Distribution substation | 98 | 71.3469 | 0.023003 | 0.00032241 | No
2020-05-11 | 23:39 | 35990 | Short rural | Asset Failure | Distribution substation | 3 | 61 | 0.00060204 | 9.8696e-06 | No
2020-05-12 | 0:26 | LP1422 | Urban | Unknown | Unknown | 64 | 100 | 0.0085402 | 8.5402e-05 | No
2020-05-12 | 3:38 | HBB2 | Short rural | Asset Failure | Distribution substation | 1 | 550 | 0.0018094 | 3.2899e-06 | No
2020-05-12 | 7:31 | 5495 | Urban | Network business | Network error | 85 | 56 | 0.0063517 | 0.00011342 | No
2020-05-12 | 8:03 | MVE2 | Short rural | Asset Failure | Distribution substation | 3 | 132 | 0.0013028 | 9.8696e-06 | No
2020-05-12 | 11:08 | CR1210 | Urban | Unknown | Unknown | 35 | 401.3143 | 0.018743 | 4.6704e-05 | No
2020-05-12 | 16:38 | 49319 | Urban | Asset Failure | Distribution substation | 1 | 327 | 0.00043635 | 1.3344e-06 | No
2020-05-12 | 18:10 | C897 | Urban | Unknown | Unknown | 44 | 67 | 0.0039338 | 5.8714e-05 | No
2020-05-13 | 11:47 | JS1142 | Urban | Asset Failure | Distribution substation | 1 | 268 | 0.00035762 | 1.3344e-06 | No
2020-05-13 | 13:35 | J495 | Short rural | Asset Failure | HV | 1379 | 79.8339 | 0.36218 | 0.0045367 | No
2020-05-13 | 14:17 | OA1244 | Short rural | Animal | Animal Impact | 1 | 79 | 0.0002599 | 3.2899e-06 | No
2020-05-13 | 15:31 | J478 | Short rural | Asset Failure | HV | 105 | 32 | 0.011054 | 0.00034544 | No
2020-05-13 | 17:59 | RBC2 | Short rural | Asset Failure | HV | 61 | 188.9836 | 0.037926 | 0.00020068 | No
2020-05-13 | 19:32 | MG1219 | Short rural | Unknown | Unknown | 21 | 212 | 0.014646 | 6.9087e-05 | No
2020-05-14 | 0:41 | ULC2 | Short rural | Asset Failure | HV | 67 | 180 | 0.039676 | 0.00022042 | No
2020-05-14 | 1:07 | J497 | Short rural | Asset Failure | Distribution substation | 12 | 301 | 0.011883 | 3.9478e-05 | No
2020-05-14 | 8:04 | SC1216 | Urban | Third Party | Dig-in | 1155 | 104 | 0.16029 | 0.0015412 | No
2020-05-14 | 9:42 | CT1233 | Urban | Asset Failure | Distribution substation | 14 | 258 | 0.0048198 | 1.8682e-05 | No
2020-05-14 | 11:04 | CV1236 | Urban | Asset Failure | Distribution substation | 149 | 246 | 0.048911 | 0.00019883 | No
2020-05-14 | 12:10 | NG1299 | Short rural | Asset Failure | Distribution substation | 35 | 430.0286 | 0.049516 | 0.00011515 | No
2020-05-14 | 12:38 | CX1273 | Short rural | Vegetation | Grow-in - NSP responsibility | 419 | 158 | 0.2178 | 0.0013785 | No
2020-05-14 | 12:38 | CX1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 832 | 157 | 0.42974 | 0.0027372 | No
2020-05-14 | 12:38 | 35418 | Short rural | Vegetation | Grow-in - NSP responsibility | 362 | 136.8541 | 0.16298 | 0.0011909 | No
2020-05-14 | 12:38 | D810 | Short rural | Vegetation | Grow-in - NSP responsibility | 228 | 136.8541 | 0.10265 | 0.00075009 | No
2020-05-14 | 12:38 | D813 | Short rural | Vegetation | Grow-in - NSP responsibility | 314 | 136.8541 | 0.14137 | 0.001033 | No
2020-05-14 | 12:38 | D814 | Short rural | Vegetation | Grow-in - NSP responsibility | 330 | 136.8541 | 0.14858 | 0.0010857 | No
2020-05-14 | 14:10 | BWB2 | Urban | Unknown | Unknown | 14 | 103 | 0.0019242 | 1.8682e-05 | No
2020-05-14 | 17:02 | 35767 | Urban | Asset Failure | Distribution substation | 50 | 378 | 0.02522 | 6.672e-05 | No
2020-05-14 | 19:28 | 35983 | Short rural | Third Party | Vehicle impact | 36 | 803 | 0.095103 | 0.00011844 | No
2020-05-14 | 22:10 | SG1257 | Urban | Third Party | Vehicle impact | 86 | 272 | 0.031214 | 0.00011476 | No
2020-05-15 | 9:25 | S765 | Urban | Third Party | Other | 2 | 149 | 0.00039765 | 2.6688e-06 | No
2020-05-15 | 13:21 | H745 | Short rural | Unknown | Unknown | 4 | 598 | 0.0078694 | 1.3159e-05 | No
2020-05-15 | 15:17 | 68195 | Urban | Unknown | Unknown | 9 | 60 | 0.00072058 | 1.201e-05 | No
2020-05-15 | 17:10 | APB2 | Short rural | Third Party | Vehicle impact | 3 | 111 | 0.0010955 | 9.8696e-06 | No
2020-05-15 | 18:19 | W127 | Short rural | Asset Failure | Distribution substation | 6 | 44.6667 | 0.00088168 | 1.9739e-05 | No
2020-05-15 | 23:38 | KVC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 35 | 331.7143 | 0.038195 | 0.00011515 | No
2020-05-16 | 9:12 | D814 | Short rural | Asset Failure | Distribution substation | 1 | 340 | 0.0011186 | 3.2899e-06 | No
2020-05-16 | 12:15 | BYE2 | Short rural | Asset Failure | Distribution substation | 2 | 112.5 | 0.00074022 | 6.5797e-06 | No
2020-05-16 | 12:31 | RV1280 | Urban | Unknown | Unknown | 47 | 62 | 0.0038884 | 6.2717e-05 | No
2020-05-17 | 4:41 | JBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 112 | 0.0014739 | 1.3159e-05 | No
2020-05-18 | 8:05 | MVB2 | Short rural | Animal | Animal Impact | 2 | 142 | 0.00093432 | 6.5797e-06 | No
2020-05-18 | 10:19 | CD1234 | Short rural | Third Party | Other | 4 | 42 | 0.0005527 | 1.3159e-05 | No
2020-05-18 | 14:06 | KVA2 | Short rural | Unknown | Unknown | 4 | 14 | 0.00018423 | 1.3159e-05 | No
2020-05-18 | 14:46 | C855 | Short rural | Other | Isolation Request by EE | 9 | 15 | 0.00044413 | 2.9609e-05 | No
2020-05-18 | 17:34 | BYC2 | Short rural | Unknown | Unknown | 8 | 117 | 0.0030793 | 2.6319e-05 | No
2020-05-18 | 18:13 | CR1262 | Urban | Asset Failure | Distribution substation | 18 | 68 | 0.0016333 | 2.4019e-05 | No
2020-05-18 | 18:23 | BK1236 | Short rural | Unknown | Unknown | 462 | 80.7273 | 0.1227 | 0.0015199 | No
2020-05-18 | 22:46 | B710 | Urban | Asset Failure | LV | 1136 | 89.5511 | 0.13575 | 0.0015159 | No
2020-05-19 | 1:00 | H745 | Short rural | Asset Failure | LV | 27 | 409 | 0.03633 | 8.8826e-05 | No
2020-05-19 | 1:01 | B710 | Urban | Asset Failure | Distribution substation | 62 | 69 | 0.0057086 | 8.2733e-05 | No
2020-05-19 | 1:50 | W124 | Short rural | Unknown | Unknown | 40 | 105 | 0.013817 | 0.00013159 | No
2020-05-19 | 2:51 | 2815 | Urban | Animal | Animal Impact | 131 | 163.4885 | 0.028579 | 0.00017481 | No
2020-05-19 | 4:28 | BK1288 | Short rural | Asset Failure | HV | 1798 | 139.5261 | 0.82532 | 0.0059152 | No
2020-05-19 | 5:32 | FF1243 | Urban | Asset Failure | Distribution substation | 1 | 114 | 0.00015212 | 1.3344e-06 | No
2020-05-19 | 6:39 | CLA2 | Short rural | Unknown | Unknown | 1 | 192 | 0.00063165 | 3.2899e-06 | No
2020-05-19 | 8:30 | C889 | Urban | Asset Failure | Distribution substation | 1 | 84 | 0.00011209 | 1.3344e-06 | No
2020-05-19 | 8:42 | ULL2 | Short rural | Asset Failure | Distribution substation | 20 | 41 | 0.0026977 | 6.5797e-05 | No
2020-05-19 | 9:26 | B710 | Urban | Asset Failure | Distribution substation | 608 | 136 | 0.11034 | 0.00081131 | No
2020-05-19 | 10:06 | NL1332 | Urban | Asset Failure | Distribution substation | 1 | 277 | 0.00036963 | 1.3344e-06 | No
2020-05-19 | 10:36 | RD1299 | Urban | Asset Failure | Distribution substation | 33 | 65 | 0.0028623 | 4.4035e-05 | No
2020-05-19 | 13:06 | BK1288 | Short rural | Asset Failure | Distribution substation | 1 | 130 | 0.00042768 | 3.2899e-06 | No
2020-05-19 | 15:43 | 35590 | Short rural | Other | FOREIGN MATTER ON SYSTEM | 6 | 273 | 0.0053888 | 1.9739e-05 | No
2020-05-20 | 8:54 | JBB2 | Short rural | Asset Failure | Distribution substation | 3 | 156 | 0.0015397 | 9.8696e-06 | No
2020-05-20 | 9:10 | 4869 | Urban | Asset Failure | Distribution substation | 58 | 99 | 0.0076621 | 7.7395e-05 | No
2020-05-20 | 11:45 | NK1332 | Urban | Third Party | Vehicle impact | 684 | 44 | 0.04016 | 0.00091273 | No
2020-05-20 | 12:31 | 68190 | Urban | Asset Failure | HV | 515 | 14.3398 | 0.0098545 | 0.00068722 | No
2020-05-20 | 13:51 | UNF2 | Urban | Asset Failure | Distribution substation | 30 | 127 | 0.0050841 | 4.0032e-05 | No
2020-05-20 | 16:50 | 27188 | Urban | Asset Failure | Distribution substation | 2 | 123.5 | 0.0003296 | 2.6688e-06 | No
2020-05-20 | 20:34 | 9025 | Urban | Other | FOREIGN MATTER ON SYSTEM | 2225 | 70.2746 | 0.20865 | 0.002969 | No
2020-05-21 | 9:06 | R260 | Short rural | Asset Failure | LV | 74 | 288.4595 | 0.070225 | 0.00024345 | No
2020-05-21 | 10:07 | 9029 | Urban | Unknown | Unknown | 43 | 138.5116 | 0.0079477 | 5.7379e-05 | No
2020-05-21 | 10:36 | CS1250 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1068 | 50 | 0.071257 | 0.0014251 | No
2020-05-21 | 10:59 | 8677 | Urban | Overload |  | 187.9378 | 47 | 0.011787 | 0.00025078 | No
2020-05-21 | 10:59 | 8679 | Urban | Overload |  | 498.3863 | 47 | 0.031257 | 0.00066505 | No
2020-05-21 | 10:59 | 8686 | Short rural | Overload |  | 611.6759 | 47 | 0.09458 | 0.0020123 | No
2020-05-21 | 11:07 | BX1232 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 531 | 68.8154 | 0.04876 | 0.00070857 | No
2020-05-21 | 11:11 | 8677 | Urban | Asset Failure | LV | 215.1583 | 8 | 0.0022969 | 0.00028711 | No
2020-05-21 | 11:11 | 8679 | Urban | Asset Failure | LV | 570.5717 | 8 | 0.006091 | 0.00076137 | No
2020-05-21 | 11:11 | 8686 | Short rural | Asset Failure | LV | 700.27 | 8 | 0.01843 | 0.0023038 | No
2020-05-21 | 11:18 | GL1233 | Short rural | Asset Failure | Distribution substation | 8 | 138 | 0.003632 | 2.6319e-05 | No
2020-05-21 | 11:36 | 8801 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 38 | 0.00050006 | 1.3159e-05 | No
2020-05-21 | 12:17 | 41535 | Urban | Unknown | Unknown | 12 | 89 | 0.0014251 | 1.6013e-05 | No
2020-05-21 | 12:59 | SN1230 | Short rural | Third Party | Vehicle impact | 3 | 105.6667 | 0.0010429 | 9.8696e-06 | No
2020-05-21 | 13:24 | 8764 | Urban | Third Party | Vehicle impact | 36 | 35.3611 | 0.0016987 | 4.8038e-05 | No
2020-05-21 | 13:50 | 8780 | Urban | Third Party | Vehicle impact | 74 | 185.1351 | 0.018281 | 9.8746e-05 | No
2020-05-21 | 15:03 | GL1233 | Short rural | Asset Failure | Distribution substation | 2 | 539.5 | 0.0035498 | 6.5797e-06 | No
2020-05-21 | 15:29 | SN1230 | Short rural | Asset Failure | Distribution substation | 3 | 228.6667 | 0.0022568 | 9.8696e-06 | No
2020-05-21 | 15:40 | A053 | Urban | Unknown | Unknown | 1 | 166 | 0.00022151 | 1.3344e-06 | No
2020-05-21 | 15:48 | SC1289 | Short rural | Unknown | Unknown | 1 | 80 | 0.00026319 | 3.2899e-06 | No
2020-05-21 | 17:09 | BWH2 | Short rural | Other | Probable Lightning/Electrical Storm | 1 | 125 | 0.00041123 | 3.2899e-06 | No
2020-05-21 | 17:56 | RW1292 | Short rural | Other | Probable Lightning/Electrical Storm | 11 | 1076 | 0.038939 | 3.6188e-05 | No
2020-05-21 | 18:15 | RW1218 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 1082 | 0.010679 | 9.8696e-06 | No
2020-05-21 | 19:03 | 48196 | Urban | Asset Failure | HV | 258 | 55.2248 | 0.019013 | 0.00034427 | No
2020-05-21 | 19:07 | RBD2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 65 | 504.3538 | 0.10785 | 0.00021384 | No
2020-05-21 | 20:23 | BWC2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 60 | 793 | 0.15653 | 0.00019739 | No
2020-05-21 | 20:25 | CS1250 | Urban | Asset Failure | Distribution substation | 20 | 244 | 0.0065119 | 2.6688e-05 | No
2020-05-21 | 21:05 | 9017 | Urban | Asset Failure | Distribution substation | 1 | 78 | 0.00010408 | 1.3344e-06 | No
2020-05-21 | 21:15 | MVF2 | Short rural | Weather |  | 1154 | 89.0009 | 0.33789 | 0.0037965 | No
2020-05-21 | 22:55 | CLA2 | Short rural | Other | Probable Lightning/Electrical Storm | 28 | 158.6786 | 0.014617 | 9.2116e-05 | No
2020-05-21 | 23:22 | 4873 | Urban | Unknown | Unknown | 13 | 118 | 0.002047 | 1.7347e-05 | No
2020-05-22 | 1:45 | W118 | Short rural | Asset Failure | Zone substation | 734 | 20.0342 | 0.048378 | 0.0024148 | No
2020-05-22 | 1:45 | W120 | Short rural | Asset Failure | Zone substation | 1171 | 20.0342 | 0.07718 | 0.0038524 | No
2020-05-22 | 1:45 | W123 | Short rural | Asset Failure | Zone substation | 1028 | 20.0342 | 0.067755 | 0.003382 | No
2020-05-22 | 1:45 | W126 | Short rural | Asset Failure | Zone substation | 82 | 20.0342 | 0.0054046 | 0.00026977 | No
2020-05-22 | 7:45 | CLA2 | Short rural | Asset Failure | Distribution substation | 5 | 370 | 0.0060862 | 1.6449e-05 | No
2020-05-22 | 8:35 | CA1210 | Urban | Asset Failure | Distribution substation | 4 | 730 | 0.0038964 | 5.3376e-06 | No
2020-05-22 | 9:19 | CLA2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 28 | 68 | 0.0062639 | 9.2116e-05 | No
2020-05-22 | 9:55 | BWH2 | Short rural | Unknown | Unknown | 831 | 79 | 0.21598 | 0.0027339 | No
2020-05-22 | 10:01 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - NSP responsibility | 118 | 258 | 0.10016 | 0.0003882 | No
2020-05-22 | 10:12 | MM1162 | Urban | Asset Failure | Distribution substation | 1 | 523 | 0.00069789 | 1.3344e-06 | No
2020-05-22 | 11:48 | KVA2 | Short rural | Other | Probable Lightning/Electrical Storm | 368 | 168.3832 | 0.20386 | 0.0012107 | No
2020-05-22 | 16:14 | 8686 | Short rural | Asset Failure | Distribution substation | 62 | 163 | 0.033247 | 0.00020397 | No
2020-05-22 | 18:35 | SG1220 | Urban | Asset Failure | Distribution substation | 25 | 315 | 0.010508 | 3.336e-05 | No
2020-05-22 | 19:15 | R293 | Short rural | Animal | Animal Impact | 2 | 150 | 0.00098696 | 6.5797e-06 | No
2020-05-22 | 21:31 | WBE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 32 | 318.0938 | 0.033488 | 0.00010528 | No
2020-05-22 | 22:35 | KMB2 | Short rural | Weather |  | 1050 | 72.1581 | 0.24926 | 0.0034544 | No
2020-05-22 | 23:03 | 25449 | Short rural | Vegetation | Grow-in - NSP responsibility | 593 | 108.4098 | 0.2115 | 0.0019509 | No
2020-05-23 | 0:28 | 4869 | Urban | Asset Failure | Distribution substation | 13 | 766 | 0.013288 | 1.7347e-05 | No
2020-05-23 | 0:58 | WWB2 | Short rural | Animal | Animal Impact | 33 | 156 | 0.016936 | 0.00010857 | No
2020-05-23 | 1:07 | KMB2 | Short rural | Unknown | Unknown | 14 | 408 | 0.018792 | 4.6058e-05 | No
2020-05-23 | 1:15 | J493 | Urban | Weather |  | 8 | 539 | 0.0057539 | 1.0675e-05 | No
2020-05-23 | 7:05 | L517 | Urban | Asset Failure | HV | 822 | 37.3005 | 0.040914 | 0.0010969 | No
2020-05-23 | 8:00 | HKG2 | Short rural | Asset Failure | Distribution substation | 1 | 199 | 0.00065468 | 3.2899e-06 | No
2020-05-23 | 9:48 | 55165 | Urban | Asset Failure | Distribution substation | 1 | 262 | 0.00034961 | 1.3344e-06 | No
2020-05-23 | 10:35 | J493 | Urban | Other | Probable Equipment Failure | 24 | 429 | 0.013739 | 3.2026e-05 | No
2020-05-23 | 14:54 | GG1232 | Short rural | Vegetation | Grow-in - NSP responsibility | 964 | 62 | 0.19663 | 0.0031714 | No
2020-05-23 | 15:22 | GG1295 | Short rural | Vegetation | Grow-in - NSP responsibility | 83 | 71.8554 | 0.019621 | 0.00027306 | No
2020-05-23 | 15:42 | 35695 | Short rural | Third Party | Vehicle impact | 574 | 15.5679 | 0.029398 | 0.0018884 | No
2020-05-23 | 20:05 | MVB2 | Short rural | Asset Failure | Distribution substation | 1 | 159 | 0.00052309 | 3.2899e-06 | No
2020-05-23 | 22:37 | 35702 | Urban | Third Party | Vehicle impact | 23 | 85.3043 | 0.0026181 | 3.0691e-05 | No
2020-05-24 | 12:18 | L946 | Short rural | Unknown | Unknown | 10 | 126 | 0.0041452 | 3.2899e-05 | No
2020-05-24 | 13:08 | CLB2 | Short rural | Asset Failure | LV | 140 | 118 | 0.054349 | 0.00046058 | No
2020-05-24 | 13:21 | J507 | Short rural | Vegetation | Grow-in - NSP responsibility | 897 | 46 | 0.13575 | 0.002951 | No
2020-05-24 | 13:21 | SWE2 | Urban | Animal | Animal Impact | 1359 | 71.6225 | 0.12988 | 0.0018134 | No
2020-05-24 | 14:08 | 55874 | Urban | Asset Failure | Distribution substation | 13 | 97 | 0.0016827 | 1.7347e-05 | No
2020-05-24 | 14:23 | HKF2 | Short rural | Unknown | Unknown | 2350 | 83.7387 | 0.6474 | 0.0077312 | No
2020-05-24 | 14:57 | GG1295 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 176 | 0.0023161 | 1.3159e-05 | No
2020-05-24 | 15:21 | JBB2 | Short rural | Asset Failure | LV | 5 | 32 | 0.00052638 | 1.6449e-05 | No
2020-05-24 | 16:29 | T882 | Urban | Vegetation | Grow-in - NSP responsibility | 17 | 400 | 0.0090739 | 2.2685e-05 | No
2020-05-25 | 7:41 | C900 | Urban | Unknown | Unknown | 8 | 94 | 0.0010035 | 1.0675e-05 | No
2020-05-25 | 12:04 | T828 | Short rural | Unknown | Unknown | 149 | 256 | 0.12549 | 0.00049019 | No
2020-05-25 | 12:05 | SC1271 | Urban | Third Party | Other | 6 | 159 | 0.001273 | 8.0064e-06 | No
2020-05-25 | 15:05 | BK1251 | Short rural | Unknown | Unknown | 5 | 220 | 0.0036188 | 1.6449e-05 | No
2020-05-25 | 16:47 | T828 | Short rural | Asset Failure | LV | 148 | 48.1892 | 0.023463 | 0.0004869 | No
2020-05-25 | 17:56 | GL1255 | Short rural | Vegetation | Grow-in - NSP responsibility | 53 | 80 | 0.013949 | 0.00017436 | No
2020-05-25 | 19:52 | HBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 160 | 70.85 | 0.037294 | 0.00052638 | No
2020-05-25 | 21:29 | SXD2 | Short rural | Asset Failure | HV | 401 | 329.4888 | 0.43467 | 0.0013192 | No
2020-05-26 | 7:01 | 8779 | Urban | Unknown | Unknown | 9 | 99 | 0.0011889 | 1.201e-05 | No
2020-05-26 | 7:08 | GG1295 | Short rural | Asset Failure | Distribution substation | 1 | 416 | 0.0013686 | 3.2899e-06 | No
2020-05-26 | 9:01 | RBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 295 | 0.011646 | 3.9478e-05 | No
2020-05-26 | 9:45 | R260 | Short rural | Third Party | Unauthorised access | 3 | 60 | 0.00059218 | 9.8696e-06 | No
2020-05-26 | 14:01 | RD1228 | Urban | Third Party | Other | 132 | 745 | 0.13122 | 0.00017614 | No
2020-05-26 | 15:25 | T873 | Short rural | Asset Failure | Distribution substation | 6 | 98 | 0.0019344 | 1.9739e-05 | No
2020-05-26 | 15:46 | RD1269 | Urban | Unknown | Unknown | 192 | 342 | 0.087622 | 0.0002562 | No
2020-05-26 | 15:54 | KMF2 | Urban | Asset Failure | Distribution substation | 130 | 146.5077 | 0.025415 | 0.00017347 | No
2020-05-26 | 16:17 | RD1269 | Urban | Third Party | Vehicle impact | 18 | 420.3889 | 0.010097 | 2.4019e-05 | No
2020-05-26 | 17:42 | J489 | Urban | Unknown | Unknown | 58 | 78 | 0.0060368 | 7.7395e-05 | No
2020-05-26 | 19:48 | 35989 | Short rural | Other | Probable Overload | 2 | 129 | 0.00084878 | 6.5797e-06 | No
2020-05-26 | 21:24 | J493 | Urban | Asset Failure | Distribution substation | 1 | 87 | 0.00011609 | 1.3344e-06 | No
2020-05-27 | 12:19 | W111 | Short rural | Other | Probable Willful damage - damage/destruction of EE equipment | 6 | 11 | 0.00021713 | 1.9739e-05 | No
2020-05-27 | 17:20 | 55177 | Urban | Asset Failure | Distribution substation | 5 | 349 | 0.0023285 | 6.672e-06 | No
2020-05-28 | 0:34 | LP1132 | Urban | Asset Failure | Distribution substation | 15 | 513 | 0.010268 | 2.0016e-05 | No
2020-05-28 | 6:09 | APB2 | Short rural | Other | Fire | 12 | 54 | 0.0021318 | 3.9478e-05 | No
2020-05-28 | 9:51 | 7037 | Urban | Asset Failure | Subtransmission | 1 | 379 | 0.00050574 | 1.3344e-06 | No
2020-05-28 | 14:48 | RBE2 | Short rural | Unknown | Unknown | 2 | 132 | 0.00086852 | 6.5797e-06 | No
2020-05-28 | 15:59 | RD1232 | Urban | Asset Failure | Distribution substation | 97 | 397.5876 | 0.051462 | 0.00012944 | No
2020-05-28 | 16:24 | CD1260 | Urban | Unknown | Unknown | 58 | 107 | 0.0082813 | 7.7395e-05 | No
2020-05-28 | 16:44 | 55874 | Urban | Asset Failure | Distribution substation | 22 | 178 | 0.0052255 | 2.9357e-05 | No
2020-05-28 | 23:09 | J459 | Short rural | Asset Failure | Distribution substation | 1 | 335 | 0.0011021 | 3.2899e-06 | No
2020-05-29 | 10:08 | SHE2 | Urban | Asset Failure | HV | 1625 | 26.2357 | 0.056889 | 0.0021684 | No
2020-05-29 | 10:22 | MR2218 | Short rural | Unknown | Unknown | 3 | 194 | 0.0019147 | 9.8696e-06 | No
2020-05-29 | 17:47 | WRB2 | Urban | Unknown | Unknown | 168 | 133.994 | 0.030039 | 0.00022418 | No
2020-05-29 | 19:52 | WD1284 | Short rural | Asset Failure | Distribution substation | 3 | 105 | 0.0010363 | 9.8696e-06 | No
2020-05-29 | 23:12 | 46774 | Urban | Asset Failure | Distribution substation | 213 | 27.6901 | 0.0078703 | 0.00028423 | No
2020-05-30 | 7:04 | HKG2 | Short rural | Asset Failure | Distribution substation | 1 | 105 | 0.00034544 | 3.2899e-06 | No
2020-05-30 | 8:21 | MM1202 | Urban | Asset Failure | Distribution substation | 1 | 176 | 0.00023485 | 1.3344e-06 | No
2020-05-30 | 12:44 | CLC2 | Short rural | Asset Failure | HV | 1338 | 74.9402 | 0.32987 | 0.0044018 | No
2020-05-30 | 15:04 | J503 | Urban | Asset Failure | Distribution substation | 29 | 22.3103 | 0.00086336 | 3.8698e-05 | No
2020-05-30 | 15:57 | X877 | Short rural | Unknown | Unknown | 1 | 95 | 0.00031254 | 3.2899e-06 | No
2020-05-30 | 17:42 | RW1281 | Short rural | Asset Failure | LV | 38 | 102 | 0.012752 | 0.00012501 | No
2020-05-31 | 5:45 | DS1241 | Urban | Asset Failure | LV | 182 | 45 | 0.010929 | 0.00024286 | No
2020-05-31 | 8:33 | C899 | Urban | Third Party | Vehicle impact | 14 | 146 | 0.0027275 | 1.8682e-05 | No
2020-05-31 | 9:29 | 5498 | Urban | Asset Failure | HV | 192 | 117 | 0.029976 | 0.0002562 | No
2020-05-31 | 10:06 | 49391 | Urban | Asset Failure | Distribution substation | 1 | 337 | 0.00044969 | 1.3344e-06 | No
2020-05-31 | 12:48 | RV1280 | Urban | Asset Failure | Distribution substation | 122 | 192 | 0.031257 | 0.0001628 | No
2020-05-31 | 18:06 | 1957 | Urban | Asset Failure | Distribution substation | 13 | 45 | 0.00078062 | 1.7347e-05 | No
2020-06-01 | 0:06 | 49366 | Urban | Asset Failure | Distribution substation | 33 | 1151 | 0.050684 | 4.4035e-05 | No
2020-06-01 | 5:21 | J493 | Urban | Asset Failure | Distribution substation | 23 | 242.4348 | 0.0074406 | 3.0691e-05 | No
2020-06-01 | 6:52 | WRF2 | Short rural | Asset Failure | Distribution substation | 23 | 48 | 0.003632 | 7.5667e-05 | No
2020-06-01 | 7:51 | WD1251 | Short rural | Asset Failure | LV | 9 | 180 | 0.0053296 | 2.9609e-05 | No
2020-06-01 | 14:57 | SC1289 | Short rural | Unknown | Unknown | 3 | 123 | 0.001214 | 9.8696e-06 | No
2020-06-01 | 15:00 | 41533 | Short rural | Vegetation | Grow-in - NSP responsibility | 13 | 65 | 0.0027799 | 4.2768e-05 | No
2020-06-02 | 10:42 | RBB2 | Short rural | Asset Failure | HV | 139 | 97.8273 | 0.044736 | 0.00045729 | No
2020-06-02 | 11:31 | WBC2 | Short rural | Vegetation | Grow-in - NSP responsibility | 127 | 246.8425 | 0.10313 | 0.00041781 | No
2020-06-02 | 14:18 | PK1262 | Short rural | Asset Failure | Distribution substation | 1 | 68 | 0.00022371 | 3.2899e-06 | No
2020-06-02 | 14:18 | 55890 | Urban | Asset Failure | Distribution substation | 1 | 61 | 8.1398e-05 | 1.3344e-06 | No
2020-06-02 | 14:58 | NK1342 | Urban | Animal | Animal Impact | 388 | 33 | 0.017086 | 0.00051775 | No
2020-06-02 | 17:09 | 55890 | Urban | Asset Failure | LV | 1451 | 113.9097 | 0.22055 | 0.0019362 | No
2020-06-02 | 18:24 | WM1112 | Urban | Asset Failure | HV | 2194 | 114.5351 | 0.33532 | 0.0029277 | No
2020-06-02 | 18:59 | 7972 | Urban | Overload |  | 4 | 92 | 0.00049106 | 5.3376e-06 | No
2020-06-02 | 20:02 | 35693 | Short rural | Unknown | Unknown | 8 | 85 | 0.0022371 | 2.6319e-05 | No
2020-06-03 | 4:46 | BWF2 | Short rural | Unknown | Unknown | 1 | 191 | 0.00062836 | 3.2899e-06 | No
2020-06-03 | 6:28 | TM1210 | Short rural | Unknown | Unknown | 4 | 305 | 0.0040136 | 1.3159e-05 | No
2020-06-03 | 6:54 | UNJ2 | Urban | Third Party | Vehicle impact | 99 | 69 | 0.0091153 | 0.00013211 | No
2020-06-03 | 8:45 | APC2 | Short rural | Unknown | Unknown | 4 | 132 | 0.001737 | 1.3159e-05 | No
2020-06-03 | 13:16 | JS1252 | Short rural | Asset Failure | HV | 37 | 126.1081 | 0.015351 | 0.00012172 | No
2020-06-03 | 13:18 | 55890 | Urban | Asset Failure | Distribution substation | 1 | 60 | 8.0064e-05 | 1.3344e-06 | No
2020-06-03 | 20:33 | J489 | Urban | Asset Failure | Distribution substation | 13 | 831 | 0.014416 | 1.7347e-05 | No
2020-06-03 | 22:21 | MM1382 | Urban | Asset Failure | Distribution substation | 36 | 40.0556 | 0.0019242 | 4.8038e-05 | No
2020-06-04 | 6:22 | WM1222 | Urban | Asset Failure | Distribution substation | 2 | 391 | 0.0010435 | 2.6688e-06 | No
2020-06-04 | 6:52 | J495 | Short rural | Asset Failure | Distribution substation | 1 | 45 | 0.00014804 | 3.2899e-06 | No
2020-06-04 | 7:59 | BWE2 | Short rural | Network business | Switching or protection error | 2087 | 7 | 0.048062 | 0.0068659 | No
2020-06-04 | 11:50 | JS1122 | Short rural | Asset Failure | Distribution substation | 2 | 482 | 0.0031714 | 6.5797e-06 | No
2020-06-04 | 17:29 | 8776 | Urban | Animal | Animal Impact | 8 | 63 | 0.00067254 | 1.0675e-05 | No
2020-06-04 | 21:22 | 49328 | Urban | Asset Failure | Distribution substation | 19 | 143 | 0.0036256 | 2.5354e-05 | No
2020-06-05 | 6:15 | NL1322 | Urban | Other | Probable Growing or falling tree or branches not felled or lopped (bark, grass) | 378 | 149.5026 | 0.07541 | 0.0005044 | No
2020-06-05 | 6:58 | J503 | Urban | Unknown | Unknown | 11 | 61 | 0.00089538 | 1.4678e-05 | No
2020-06-05 | 13:32 | TM1284 | Short rural | Unknown | Unknown | 31 | 120 | 0.012238 | 0.00010199 | No
2020-06-05 | 14:01 | TM1284 | Short rural | Unknown | Unknown | 9 | 91 | 0.0026944 | 2.9609e-05 | No
2020-06-05 | 15:32 | BK1251 | Short rural | Asset Failure | Distribution substation | 15 | 145 | 0.0071555 | 4.9348e-05 | No
2020-06-05 | 17:07 | BL1243 | Short rural | Vegetation | Grow-in - NSP responsibility | 20 | 33 | 0.0021713 | 6.5797e-05 | No
2020-06-05 | 21:37 | D845 | Urban | Asset Failure | Distribution substation | 43 | 67.5349 | 0.0038751 | 5.7379e-05 | No
2020-06-06 | 7:02 | SZ1132 | Urban | Unknown | Unknown | 1 | 54 | 7.2058e-05 | 1.3344e-06 | No
2020-06-06 | 8:38 | 87220 | Short rural | Asset Failure | HV | 31 | 195.8387 | 0.019973 | 0.00010199 | No
2020-06-06 | 18:15 | NA1288 | Urban | Unknown | Unknown | 73 | 48 | 0.0046757 | 9.7411e-05 | No
2020-06-06 | 21:20 | HKC2 | Short rural | Other | Probable Overload | 27 | 115 | 0.010215 | 8.8826e-05 | No
2020-06-07 | 6:34 | T876 | Urban | Asset Failure | HV | 916 | 104.5022 | 0.12773 | 0.0012223 | No
2020-06-07 | 9:51 | CLC2 | Short rural | Overload |  | 35 | 118 | 0.013587 | 0.00011515 | No
2020-06-07 | 10:49 | MVC2 | Short rural | Unknown | Unknown | 14 | 95 | 0.0043755 | 4.6058e-05 | No
2020-06-07 | 12:22 | WRF2 | Short rural | Asset Failure | HV | 1301 | 5 | 0.021401 | 0.0042801 | No
2020-06-07 | 15:59 | ULE2 | Short rural | Asset Failure | HV | 57 | 379.2632 | 0.07112 | 0.00018752 | No
2020-06-07 | 16:08 | W112 | Short rural | Asset Failure | HV | 17 | 74 | 0.0041386 | 5.5928e-05 | No
2020-06-07 | 16:40 | W124 | Short rural | Unknown | Unknown | 1 | 24 | 7.8957e-05 | 3.2899e-06 | No
2020-06-07 | 16:43 | BWH2 | Short rural | Unknown | Unknown | 1 | 87 | 0.00028622 | 3.2899e-06 | No
2020-06-07 | 17:33 | HKC2 | Short rural | Overload |  | 27 | 118 | 0.010482 | 8.8826e-05 | No
2020-06-07 | 17:38 | DS1204 | Urban | Asset Failure | Distribution substation | 32 | 202 | 0.0086256 | 4.2701e-05 | No
2020-06-07 | 18:30 | NM1258 | Urban | Asset Failure | Distribution substation | 56 | 123 | 0.0091913 | 7.4726e-05 | No
2020-06-07 | 20:39 | CLC2 | Short rural | Asset Failure | Distribution substation | 13 | 79 | 0.0033787 | 4.2768e-05 | No
2020-06-08 | 9:29 | J495 | Short rural | Asset Failure | Distribution substation | 28 | 80 | 0.0073693 | 9.2116e-05 | No
2020-06-08 | 11:43 | J465 | Urban | Other | Isolation Request by EE | 72 | 10 | 0.00096077 | 9.6077e-05 | No
2020-06-08 | 18:27 | 48198 | Urban | Asset Failure | Distribution substation | 1 | 158 | 0.00021084 | 1.3344e-06 | No
2020-06-09 | 2:35 | T882 | Urban | Unknown | Unknown | 18 | 266 | 0.0063891 | 2.4019e-05 | No
2020-06-09 | 7:05 | M166 | Urban | Other | Probable Overload | 5 | 103 | 0.00068722 | 6.672e-06 | No
2020-06-09 | 8:50 | 35981 | Short rural | Unknown | Unknown | 2 | 80 | 0.00052638 | 6.5797e-06 | No
2020-06-09 | 9:11 | MVB2 | Short rural | Unknown | Unknown | 1 | 225 | 0.00074022 | 3.2899e-06 | No
2020-06-09 | 9:55 | RW1281 | Short rural | Asset Failure | Distribution substation | 1 | 62 | 0.00020397 | 3.2899e-06 | No
2020-06-09 | 11:20 | MVH2 | Short rural | Unknown | Unknown | 2 | 168 | 0.0011054 | 6.5797e-06 | No
2020-06-09 | 12:32 | CLA2 | Short rural | Asset Failure | HV | 63 | 77.0635 | 0.015972 | 0.00020726 | No
2020-06-09 | 15:16 | SZ1322 | Short rural | Other | Isolation Request by EE | 22 | 10 | 0.00072377 | 7.2377e-05 | No
2020-06-09 | 17:17 | OP1122 | Short rural | Asset Failure | Distribution substation | 1 | 110 | 0.00036188 | 3.2899e-06 | No
2020-06-09 | 18:31 | ULF2 | Short rural | Asset Failure | LV | 2 | 48.5 | 0.00031912 | 6.5797e-06 | No
2020-06-09 | 19:21 | 35388 | Urban | Asset Failure | Distribution substation | 61 | 202 | 0.016442 | 8.1398e-05 | No
2020-06-09 | 19:47 | 6423 | Urban | Unknown | Unknown | 42 | 93 | 0.0052122 | 5.6045e-05 | No
2020-06-10 | 7:37 | FF1217 | Urban | Asset Failure | Distribution substation | 10 | 164.2 | 0.0021911 | 1.3344e-05 | No
2020-06-10 | 9:30 | 35815 | Short rural | Vegetation | Grow-in - NSP responsibility | 524 | 49.0248 | 0.084513 | 0.0017239 | No
2020-06-10 | 11:52 | 1953 | Urban | Other | Probable Accidental Damage - Vehicle Impact | 23 | 59.087 | 0.0018134 | 3.0691e-05 | No
2020-06-10 | 12:51 | UNB2 | Urban | Asset Failure | HV | 142.5157 | 75.0038 | 0.014264 | 0.00019017 | No
2020-06-10 | 12:51 | UNH2 | Urban | Asset Failure | HV | 378.4843 | 75.0038 | 0.037881 | 0.00050505 | No
2020-06-10 | 13:30 | 1953 | Urban | Unknown | Unknown | 6 | 205 | 0.0016413 | 8.0064e-06 | No
2020-06-10 | 14:01 | BYB2 | Short rural | Other | Probable Equipment Failure | 1 | 287 | 0.00094419 | 3.2899e-06 | No
2020-06-10 | 18:05 | T882 | Urban | Unknown | Unknown | 18 | 55 | 0.0013211 | 2.4019e-05 | No
2020-06-10 | 23:46 | TM1210 | Short rural | Unknown | Unknown | 6 | 87 | 0.0017173 | 1.9739e-05 | No
2020-06-11 | 5:11 | C855 | Short rural | Vegetation | Grow-in - NSP responsibility | 23 | 141 | 0.010669 | 7.5667e-05 | No
2020-06-11 | 9:05 | B201 | Urban | Third Party | Other | 27 | 380 | 0.013691 | 3.6029e-05 | No
2020-06-11 | 13:44 | NL1322 | Urban | Asset Failure | Distribution substation | 5 | 266 | 0.0017748 | 6.672e-06 | No
2020-06-11 | 15:08 | DS1204 | Urban | Asset Failure | Distribution substation | 9 | 162 | 0.0019456 | 1.201e-05 | No
2020-06-11 | 16:21 | SG1220 | Urban | Third Party | Vehicle impact | 129 | 314.0853 | 0.054066 | 0.00017214 | No
2020-06-11 | 19:27 | 35695 | Short rural | Asset Failure | Distribution substation | 2 | 1307 | 0.0085997 | 6.5797e-06 | No
2020-06-12 | 6:00 | FF1243 | Urban | Animal | Animal Impact | 3 | 70 | 0.00028022 | 4.0032e-06 | No
2020-06-12 | 12:19 | ULE2 | Short rural | Asset Failure | Distribution substation | 1 | 134 | 0.00044084 | 3.2899e-06 | No
2020-06-12 | 12:40 | MR2292 | Urban | Asset Failure | Distribution substation | 5 | 66 | 0.00044035 | 6.672e-06 | No
2020-06-12 | 16:47 | BWA2 | Short rural | Third Party | Vehicle impact | 1517 | 43.7587 | 0.21839 | 0.0049907 | No
2020-06-12 | 22:44 | 2810 | Urban | Asset Failure | Distribution substation | 84 | 135 | 0.015132 | 0.00011209 | No
2020-06-13 | 7:50 | MM1372 | Urban | Asset Failure | Distribution substation | 1 | 428 | 0.00057112 | 1.3344e-06 | No
2020-06-13 | 16:44 | MYC2 | Urban | Third Party | Vehicle impact | 213 | 37.4883 | 0.010655 | 0.00028423 | No
2020-06-14 | 10:16 | WRD2 | Urban | Asset Failure | Distribution substation | 43 | 153 | 0.008779 | 5.7379e-05 | No
2020-06-14 | 10:27 | TM1210 | Short rural | Third Party | Unauthorised access | 2 | 51 | 0.00033557 | 6.5797e-06 | No
2020-06-14 | 12:16 | 35825 | Short rural | Asset Failure | Distribution substation | 8 | 114 | 0.0030004 | 2.6319e-05 | No
2020-06-14 | 13:35 | J503 | Urban | Unknown | Unknown | 8 | 72 | 0.00076861 | 1.0675e-05 | No
2020-06-14 | 15:22 | 9033 | Urban | Third Party | Vehicle impact | 1812 | 52 | 0.12573 | 0.0024179 | No
2020-06-14 | 15:45 | W164 | Short rural | Unknown | Unknown | 15 | 290.3333 | 0.014327 | 4.9348e-05 | No
2020-06-14 | 20:48 | A343 | Urban | Asset Failure | LV | 107 | 68 | 0.0097091 | 0.00014278 | No
2020-06-14 | 21:42 | GG1269 | Short rural | Asset Failure | Distribution substation | 5 | 59 | 0.00097051 | 1.6449e-05 | No
2020-06-15 | 3:17 | BYC2 | Short rural | Weather |  | 78 | 119.6923 | 0.030714 | 0.00025661 | No
2020-06-15 | 7:04 | J492 | Urban | Asset Failure | Distribution substation | 1 | 473 | 0.00063117 | 1.3344e-06 | No
2020-06-15 | 7:53 | NG1247 | Urban | Asset Failure | HV | 6 | 277 | 0.0022178 | 8.0064e-06 | No
2020-06-15 | 9:08 | BYG2 | Short rural | Asset Failure | Distribution substation | 2 | 294 | 0.0019344 | 6.5797e-06 | No
2020-06-15 | 9:58 | 55879 | Urban | Unknown | Unknown | 1 | 63 | 8.4067e-05 | 1.3344e-06 | No
2020-06-15 | 13:08 | MR2232 | Short rural | Third Party | Vehicle impact | 7 | 148 | 0.0034083 | 2.3029e-05 | No
2020-06-15 | 16:14 | S738 | Short rural | Asset Failure | Distribution substation | 8 | 168.25 | 0.0044282 | 2.6319e-05 | No
2020-06-15 | 16:18 | AB1263 | Urban | Asset Failure | Distribution substation | 6 | 30 | 0.00024019 | 8.0064e-06 | No
2020-06-15 | 17:18 | RV1206 | Short rural | Asset Failure | HV | 1029 | 67.9174 | 0.22992 | 0.0033853 | No
2020-06-15 | 19:14 | SWC2 | Urban | Asset Failure | Distribution substation | 11 | 145 | 0.0021284 | 1.4678e-05 | No
2020-06-15 | 22:55 | J503 | Urban | Unknown | Unknown | 11 | 77 | 0.0011302 | 1.4678e-05 | No
2020-06-16 | 6:21 | PH1297 | Urban | Asset Failure | HV | 324 | 31 | 0.013403 | 0.00043235 | No
2020-06-16 | 8:47 | BYE2 | Short rural | Asset Failure | Distribution substation | 17 | 114 | 0.0063758 | 5.5928e-05 | No
2020-06-16 | 10:46 | L582 | Short rural | Asset Failure | LV | 1270 | 116.5795 | 0.48708 | 0.0041781 | No
2020-06-16 | 16:07 | WRA2 | Urban | Unknown | Unknown | 2 | 35 | 9.3408e-05 | 2.6688e-06 | No
2020-06-16 | 19:51 | BWE2 | Short rural | Vegetation | Grow-in - NSP responsibility | 1 | 90 | 0.00029609 | 3.2899e-06 | No
2020-06-16 | 21:53 | S744 | Urban | Asset Failure | Distribution substation | 18 | 389.5 | 0.0093555 | 2.4019e-05 | No
2020-06-17 | 13:56 | WRE2 | Urban | Unknown | Unknown | 16 | 142 | 0.0030318 | 2.135e-05 | No
2020-06-17 | 15:44 | WRC2 | Short rural | Animal | Animal Impact | 1626.6446 | 5.5253 | 0.029568 | 0.0053514 | No
2020-06-17 | 15:44 | WRD2 | Urban | Animal | Animal Impact | 1585.5778 | 5.5253 | 0.01169 | 0.0021158 | No
2020-06-17 | 15:44 | WRE2 | Urban | Animal | Animal Impact | 2046.3269 | 5.5253 | 0.015087 | 0.0027306 | No
2020-06-17 | 15:44 | WRF2 | Short rural | Animal | Animal Impact | 1507.4508 | 5.5253 | 0.027402 | 0.0049593 | No
2020-06-17 | 16:47 | WRE2 | Urban | Asset Failure | Distribution substation | 16 | 210 | 0.0044836 | 2.135e-05 | No
2020-06-17 | 18:10 | PK1288 | Short rural | Asset Failure | HV | 2018 | 52.111 | 0.34596 | 0.0066389 | No
2020-06-17 | 18:33 | J474 | Short rural | Asset Failure | Distribution substation | 1 | 88 | 0.00028951 | 3.2899e-06 | No
2020-06-17 | 19:09 | 9029 | Urban | Asset Failure | Distribution substation | 8 | 412 | 0.0043982 | 1.0675e-05 | No
2020-06-17 | 20:00 | C855 | Short rural | Asset Failure | Distribution substation | 8 | 114 | 0.0030004 | 2.6319e-05 | No
2020-06-17 | 20:20 | HS1222 | Short rural | Asset Failure | Distribution substation | 7 | 73 | 0.0016811 | 2.3029e-05 | No
2020-06-18 | 6:46 | 19868 | Urban | Animal | Animal Impact | 84 | 53.6667 | 0.0060155 | 0.00011209 | No
2020-06-18 | 7:28 | WRA2 | Urban | Unknown | Unknown | 2 | 71 | 0.00018948 | 2.6688e-06 | No
2020-06-18 | 8:16 | CV1269 | Urban | Asset Failure | Distribution substation | 12 | 149 | 0.0023859 | 1.6013e-05 | No
2020-06-18 | 9:00 | 35388 | Urban | Asset Failure | HV | 1525.5921 | 87.476 | 0.17808 | 0.0020357 | No
2020-06-18 | 9:00 | 2809 | Urban | Asset Failure | HV | 474.4079 | 87.476 | 0.055377 | 0.00063305 | No
2020-06-18 | 12:06 | 87222 | Long rural | Asset Failure | Distribution substation | 1 | 296 | 0.94268 | 0.0031847 | No
2020-06-18 | 13:31 | CLA2 | Short rural | Asset Failure | Distribution substation | 3 | 70 | 0.00069087 | 9.8696e-06 | No
2020-06-18 | 15:10 | NG1210 | Short rural | Asset Failure | LV | 14 | 125 | 0.0057573 | 4.6058e-05 | No
2020-06-18 | 15:31 | J514 | Urban | Asset Failure | Distribution substation | 30 | 372 | 0.014892 | 4.0032e-05 | No
2020-06-18 | 16:41 | MM1112 | Urban | Asset Failure | Distribution substation | 1 | 253 | 0.0003376 | 1.3344e-06 | No
2020-06-18 | 17:42 | J506 | Urban | Asset Failure | Distribution substation | 1 | 166 | 0.00022151 | 1.3344e-06 | No
2020-06-18 | 21:44 | LL1162 | Urban | Third Party | Vehicle impact | 64 | 443.625 | 0.037886 | 8.5402e-05 | No
2020-06-19 | 7:05 | LL1162 | Urban | Asset Failure | Distribution substation | 1 | 121 | 0.00016146 | 1.3344e-06 | No
2020-06-19 | 7:53 | HR1273 | Urban | Asset Failure | Distribution substation | 60 | 109 | 0.008727 | 8.0064e-05 | No
2020-06-19 | 8:14 | J495 | Short rural | Asset Failure | Distribution substation | 1 | 131 | 0.00043097 | 3.2899e-06 | No
2020-06-19 | 20:00 | J493 | Urban | Asset Failure | Distribution substation | 14 | 1057 | 0.019746 | 1.8682e-05 | No
2020-06-20 | 8:31 | CT1265 | Urban | Asset Failure | LV | 38 | 99 | 0.00502 | 5.0707e-05 | No
2020-06-20 | 11:12 | 57040 | Urban | Asset Failure | Distribution substation | 12 | 124 | 0.0019856 | 1.6013e-05 | No
2020-06-20 | 12:51 | J493 | Urban | Asset Failure | Distribution substation | 1 | 68 | 9.0739e-05 | 1.3344e-06 | No
2020-06-20 | 16:53 | NA1281 | Urban | Asset Failure | Distribution substation | 31 | 38 | 0.0015719 | 4.1366e-05 | No
2020-06-20 | 17:07 | L585 | Short rural | Vegetation | Grow-in - NSP responsibility | 26 | 39 | 0.0033359 | 8.5536e-05 | No
2020-06-21 | 1:35 | 2812 | Urban | Asset Failure | Distribution substation | 110 | 394.4818 | 0.057904 | 0.00014678 | No
2020-06-21 | 7:40 | BK1251 | Short rural | Asset Failure | Distribution substation | 1 | 134 | 0.00044084 | 3.2899e-06 | No
2020-06-21 | 8:27 | T882 | Urban | Unknown | Unknown | 18 | 39 | 0.00093675 | 2.4019e-05 | No
2020-06-21 | 10:13 | R290 | Short rural | Animal | Animal Impact | 17 | 273 | 0.015268 | 5.5928e-05 | No
2020-06-21 | 15:19 | 8679 | Urban | Asset Failure | Distribution substation | 10 | 163.3 | 0.0021791 | 1.3344e-05 | No
2020-06-21 | 16:17 | RBA2 | Short rural | Asset Failure | Distribution substation | 1 | 236 | 0.00077641 | 3.2899e-06 | No
2020-06-21 | 16:54 | J495 | Short rural | Asset Failure | Distribution substation | 89 | 19.3371 | 0.0056619 | 0.0002928 | No
2020-06-21 | 21:12 | CA1236 | Urban | Unknown | Unknown | 9 | 49 | 0.00058847 | 1.201e-05 | No
2020-06-22 | 7:51 | BYG2 | Short rural | Asset Failure | Distribution substation | 1 | 141 | 0.00046387 | 3.2899e-06 | No
2020-06-22 | 8:35 | CA1236 | Urban | Asset Failure | Distribution substation | 1 | 317 | 0.000423 | 1.3344e-06 | No
2020-06-22 | 9:31 | ER1132 | Urban | Other | Fault within HV customers installation - Defective Equipment | 10 | 75 | 0.0010008 | 1.3344e-05 | No
2020-06-22 | 12:17 | J495 | Short rural | Vegetation | Grow-in - NSP responsibility | 1459 | 42 | 0.2016 | 0.0047999 | No
2020-06-22 | 13:55 | L533 | Urban | Overload |  | 8 | 149 | 0.0015906 | 1.0675e-05 | No
2020-06-22 | 15:42 | S786 | Short rural | Unknown | Unknown | 10 | 131 | 0.0043097 | 3.2899e-05 | No
2020-06-22 | 18:24 | J477 | Urban | Asset Failure | Distribution substation | 1 | 55 | 7.3392e-05 | 1.3344e-06 | No
2020-06-22 | 18:32 | KMB2 | Short rural | Asset Failure | Distribution substation | 29 | 55 | 0.0052473 | 9.5406e-05 | No
2020-06-22 | 18:43 | CV1236 | Urban | Asset Failure | Distribution substation | 5 | 316 | 0.0021084 | 6.672e-06 | No
2020-06-22 | 19:44 | 4870 | Urban | Asset Failure | Distribution substation | 1 | 76 | 0.00010141 | 1.3344e-06 | No
2020-06-22 | 21:49 | J493 | Urban | Weather |  | 9 | 101 | 0.001213 | 1.201e-05 | No
2020-06-23 | 1:01 | LP1422 | Urban | Asset Failure | Distribution substation | 1 | 1266 | 0.0016893 | 1.3344e-06 | No
2020-06-23 | 3:26 | 35982 | Short rural | Unknown | Unknown | 4 | 108 | 0.0014212 | 1.3159e-05 | No
2020-06-23 | 8:07 | J503 | Urban | Asset Failure | Distribution substation | 1 | 534 | 0.00071257 | 1.3344e-06 | No
2020-06-23 | 9:56 | 55890 | Urban | Third Party | Dig-in | 1318 | 58.453 | 0.1028 | 0.0017587 | No
2020-06-23 | 9:58 | KVB2 | Short rural | Vegetation | Grow-in - NSP responsibility | 12 | 112 | 0.0044216 | 3.9478e-05 | No
2020-06-23 | 10:03 | WX1258 | Urban | Asset Failure | LV | 60 | 127.5167 | 0.010209 | 8.0064e-05 | No
2020-06-23 | 16:24 | CD1234 | Short rural | Vegetation | Grow-in - NSP responsibility | 38 | 232 | 0.029003 | 0.00012501 | No
2020-06-23 | 17:36 | SG1250 | Urban | Asset Failure | Distribution substation | 51 | 189 | 0.012862 | 6.8054e-05 | No
2020-06-23 | 18:06 | S776 | Urban | Asset Failure | Distribution substation | 1 | 107 | 0.00014278 | 1.3344e-06 | No
2020-06-23 | 18:11 | S776 | Urban | Asset Failure | Distribution substation | 1 | 163 | 0.00021751 | 1.3344e-06 | No
2020-06-23 | 18:17 | D852 | Urban | Weather |  | 13 | 43 | 0.00074593 | 1.7347e-05 | No
2020-06-24 | 7:44 | 55866 | Urban | Asset Failure | Distribution substation | 1 | 216 | 0.00028823 | 1.3344e-06 | No
2020-06-24 | 8:40 | RBD2 | Short rural | Network business | Switching or protection error | 78 | 14 | 0.0035925 | 0.00025661 | No
2020-06-24 | 8:40 | MVF2 | Short rural | Network business | Switching or protection error | 56 | 65 | 0.011975 | 0.00018423 | No
2020-06-24 | 15:27 | RBB2 | Short rural | Asset Failure | Distribution substation | 1 | 101 | 0.00033228 | 3.2899e-06 | No
2020-06-24 | 16:17 | SY1232 | Urban | Asset Failure | Distribution substation | 1 | 268 | 0.00035762 | 1.3344e-06 | No
2020-06-24 | 20:12 | 35418 | Short rural | Asset Failure | Distribution substation | 2 | 407 | 0.0026779 | 6.5797e-06 | No
2020-06-25 | 5:18 | 9033 | Urban | Third Party | Other | 41 | 279.6585 | 0.0153 | 5.471e-05 | No
2020-06-25 | 5:59 | M162 | Urban | Unknown | Unknown | 1 | 156 | 0.00020817 | 1.3344e-06 | No
2020-06-25 | 6:15 | CX1210 | Short rural | Asset Failure | HV | 184 | 184.7391 | 0.11183 | 0.00060533 | No
2020-06-25 | 10:16 | 8799 | Short rural | Other | Isolation Request by EE | 8 | 43 | 0.0011317 | 2.6319e-05 | No
2020-06-25 | 14:19 | J491 | Urban | Asset Failure | Distribution substation | 22 | 44.7727 | 0.0013144 | 2.9357e-05 | No
2020-06-25 | 17:20 | 35304 | Urban | Asset Failure | Distribution substation | 23 | 50 | 0.0015346 | 3.0691e-05 | No
2020-06-26 | 3:11 | BDA2 | Short rural | Unknown | Unknown | 2 | 271 | 0.0017831 | 6.5797e-06 | No
2020-06-26 | 11:07 | L942 | Short rural | Asset Failure | Distribution substation | 2 | 240 | 0.0015791 | 6.5797e-06 | No
2020-06-26 | 18:32 | L582 | Short rural | Network business | Switching or protection error | 83 | 35 | 0.0095571 | 0.00027306 | No
2020-06-26 | 19:20 | L588 | Short rural | Network business | Switching or protection error | 170 | 18 | 0.010067 | 0.00055928 | No
2020-06-26 | 22:57 | T895 | Urban | Asset Failure | Distribution substation | 1 | 1269 | 0.0016934 | 1.3344e-06 | No
2020-06-26 | 23:20 | 52237 | Urban | Asset Failure | Distribution substation | 8 | 295 | 0.0031492 | 1.0675e-05 | No
2020-06-26 | 23:48 | R211 | Short rural | Animal | Animal Impact | 1378 | 170.8099 | 0.77435 | 0.0045334 | No
2020-06-27 | 11:13 | BWF2 | Short rural | Unknown | Unknown | 6 | 185 | 0.0036517 | 1.9739e-05 | No
2020-06-27 | 13:29 | 19816 | Urban | Vegetation | Grow-in - NSP responsibility | 967 | 113 | 0.14581 | 0.0012904 | No
2020-06-28 | 8:39 | 35010 | Urban | Asset Failure | Distribution substation | 16 | 98 | 0.0020923 | 2.135e-05 | No
2020-06-28 | 16:49 | T865 | Urban | Unknown | Unknown | 5 | 34 | 0.00022685 | 6.672e-06 | No
2020-06-28 | 17:55 | HBB2 | Short rural | Asset Failure | Distribution substation | 94 | 10 | 0.0030925 | 0.00030925 | No
2020-06-28 | 18:10 | NA1214 | Urban | Other | Probable Overload | 28 | 127 | 0.0047451 | 3.7363e-05 | No
2020-06-28 | 21:04 | A322 | Urban | Unknown | Unknown | 38 | 123 | 0.006237 | 5.0707e-05 | No
2020-06-29 | 6:40 | BDA2 | Short rural | Unknown | Unknown | 16 | 241 | 0.012686 | 5.2638e-05 | No
2020-06-29 | 10:38 | SHG2 | Short rural | Asset Failure | Distribution substation | 6 | 73.6667 | 0.0014541 | 1.9739e-05 | No
2020-06-29 | 11:10 | BWH2 | Short rural | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 39 | 0.00038491 | 9.8696e-06 | No
2020-06-29 | 12:50 | AB1241 | Urban | Asset Failure | Distribution substation | 1 | 288 | 0.00038431 | 1.3344e-06 | No
2020-06-29 | 14:54 | CX1210 | Short rural | Unknown | Unknown | 22 | 112 | 0.0081062 | 7.2377e-05 | No
2020-06-29 | 15:13 | SWJ2 | Urban | Asset Failure | HV | 641.5594 | 18.0775 | 0.015476 | 0.0008561 | No
2020-06-29 | 15:13 | SWE2 | Urban | Asset Failure | HV | 1062.4406 | 18.0775 | 0.025629 | 0.0014177 | No
2020-06-29 | 17:42 | BL1243 | Short rural | Asset Failure | Distribution substation | 9 | 88 | 0.0026056 | 2.9609e-05 | No
2020-06-29 | 18:47 | FT1203 | Urban | Asset Failure | Distribution substation | 14 | 71.9286 | 0.0013437 | 1.8682e-05 | No
2020-06-29 | 21:24 | MG1286 | Short rural | Animal | Animal Impact | 20 | 84 | 0.005527 | 6.5797e-05 | No
2020-06-29 | 22:11 | CV1221 | Urban | Overload |  | 3 | 69 | 0.00027622 | 4.0032e-06 | No
2020-06-30 | 7:01 | NA1214 | Urban | Unknown | Unknown | 19 | 111 | 0.0028142 | 2.5354e-05 | No
2020-06-30 | 8:18 | SN1230 | Short rural | Asset Failure | Distribution substation | 12 | 28 | 0.0011054 | 3.9478e-05 | No
2020-06-30 | 10:12 | SG1257 | Urban | Asset Failure | Distribution substation | 1 | 234 | 0.00031225 | 1.3344e-06 | No
2020-06-30 | 13:58 | X217 | Short rural | Overload |  | 2 | 17 | 0.00011186 | 6.5797e-06 | No
2020-06-30 | 16:37 | JBA2 | Short rural | Vegetation | Grow-in - NSP responsibility | 4 | 38 | 0.00050006 | 1.3159e-05 | No
2020-06-30 | 18:38 | BYB2 | Short rural | Other | Probable Overload | 9 | 183 | 0.0054184 | 2.9609e-05 | No
2020-06-30 | 19:06 | TM1284 | Short rural | Asset Failure | Distribution substation | 20 | 58 | 0.0038162 | 6.5797e-05 | No
2020-06-30 | 19:10 | MG1267 | Short rural | Asset Failure | Distribution substation | 38 | 58 | 0.0072509 | 0.00012501 | No
2020-06-30 | 19:40 | GL1255 | Short rural | Unknown | Unknown | 16 | 70 | 0.0036846 | 5.2638e-05 | No
2020-06-30 | 22:05 | W124 | Short rural | Asset Failure | Distribution substation | 18 | 149 | 0.0088234 | 5.9218e-05 | No
2019-07-01 | 5:00 | SL1142 | Short rural | Planned |  | 2 | 0 | 0 | 6.5797e-06 | No
2019-07-01 | 8:00 | HR1236 | Urban | Planned |  | 3 | 420 | 0.0016813 | 4.0032e-06 | No
2019-07-01 | 9:00 | T893 | Urban | Planned |  | 76 | 450 | 0.045636 | 0.00010141 | No
2019-07-01 | 8:00 | HBA2 | Short rural | Planned |  | 65 | 260 | 0.055599 | 0.00021384 | No
2019-07-01 | 8:00 | CR1280 | Urban | Planned |  | 43 | 260 | 0.014919 | 5.7379e-05 | No
2019-07-01 | 8:30 | T828 | Short rural | Planned |  | 66 | 340 | 0.073825 | 0.00021713 | No
2019-07-02 | 8:00 | RV1280 | Urban | Planned |  | 87 | 400 | 0.046437 | 0.00011609 | No
2019-07-02 | 6:00 | WX1284 | Urban | Planned |  | 2 | 660 | 0.0017614 | 2.6688e-06 | No
2019-07-02 | 8:00 | SHC2 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2019-07-02 | 11:30 | APC2 | Short rural | Planned |  | 23 | 220 | 0.016647 | 7.5667e-05 | No
2019-07-02 | 8:30 | SN1230 | Short rural | Planned |  | 4 | 380 | 0.0050006 | 1.3159e-05 | No
2019-07-02 | 8:30 | JBB2 | Short rural | Planned |  | 11 | 150 | 0.0054283 | 3.6188e-05 | No
2019-07-02 | 8:30 | JBA2 | Short rural | Planned |  | 31 | 300 | 0.030596 | 0.00010199 | No
2019-07-02 | 8:00 | X863 | Urban | Planned |  | 86 | 450 | 0.051641 | 0.00011476 | No
2019-07-02 | 8:30 | ULH2 | Short rural | Planned |  | 29 | 345 | 0.032915 | 9.5406e-05 | No
2019-07-02 | 12:00 | JBB2 | Short rural | Planned |  | 2 | 96 | 0.00063165 | 6.5797e-06 | No
2019-07-02 | 9:00 | 5496 | Urban | Planned |  | 129 | 240 | 0.041313 | 0.00017214 | No
2019-07-02 | 8:00 | L946 | Short rural | Planned |  | 5 | 500 | 0.0082247 | 1.6449e-05 | No
2019-07-02 | 7:00 | W126 | Short rural | Planned |  | 82 | 510 | 0.13758 | 0.00026977 | No
2019-07-02 | 8:30 | WX1284 | Urban | Planned |  | 2 | 600 | 0.0016013 | 2.6688e-06 | No
2019-07-02 | 8:00 | 87218 | Short rural | Planned |  | 12 | 315 | 0.012436 | 3.9478e-05 | No
2019-07-02 | 7:00 | SJ1142 | Urban | Planned |  | 211 | 510 | 0.14359 | 0.00028156 | No
2019-07-02 | 9:00 | SXA2 | Short rural | Planned |  | 186 | 391 | 0.23926 | 0.00061191 | No
2019-07-02 | 8:00 | NN1240 | Urban | Planned |  | 1 | 420 | 0.00056045 | 1.3344e-06 | No
2019-07-03 | 8:00 | HR1206 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2019-07-03 | 8:30 | KMF2 | Urban | Planned |  | 169 | 420 | 0.094716 | 0.00022551 | No
2019-07-03 | 8:00 | A053 | Urban | Planned |  | 49 | 205 | 0.013404 | 6.5386e-05 | No
2019-07-03 | 8:00 | 2810 | Urban | Planned |  | 134 | 420 | 0.0751 | 0.00017881 | No
2019-07-03 | 8:00 | FT1208 | Urban | Planned |  | 4 | 340 | 0.0018148 | 5.3376e-06 | No
2019-07-03 | 8:00 | HBB2 | Short rural | Planned |  | 289 | 410 | 0.38982 | 0.00095077 | No
2019-07-03 | 8:00 | MG1204 | Short rural | Planned |  | 9 | 420 | 0.012436 | 2.9609e-05 | No
2019-07-03 | 7:30 | X883 | Urban | Planned |  | 79 | 913.4177 | 0.09629 | 0.00010542 | No
2019-07-03 | 8:30 | JBA2 | Short rural | Planned |  | 27 | 385 | 0.034198 | 8.8826e-05 | No
2019-07-03 | 8:30 | JBB2 | Short rural | Planned |  | 25 | 455 | 0.037422 | 8.2247e-05 | No
2019-07-02 | 7:30 | X883 | Urban | Planned |  | 3 | 24053.3333 | 0.09629 | 4.0032e-06 | No
2019-07-03 | 8:00 | 9030 | Urban | Planned |  | 61 | 435 | 0.035408 | 8.1398e-05 | No
2019-07-03 | 8:30 | SXC2 | Short rural | Planned |  | 64 | 360 | 0.075798 | 0.00021055 | No
2019-07-03 | 8:00 | 87218 | Short rural | Planned |  | 3 | 208 | 0.0020529 | 9.8696e-06 | No
2019-07-03 | 8:30 | TM1258 | Short rural | Planned |  | 8 | 320 | 0.008422 | 2.6319e-05 | No
2019-07-03 | 9:30 | NN1233 | Short rural | Planned |  | 87 | 330 | 0.094452 | 0.00028622 | No
2019-07-04 | 7:00 | B207 | Urban | Planned |  | 2 | 600 | 0.0016013 | 2.6688e-06 | No
2019-07-04 | 8:30 | APA2 | Urban | Planned |  | 3 | 370 | 0.0014812 | 4.0032e-06 | No
2019-07-04 | 8:30 | 7120 | Urban | Planned |  | 5 | 380 | 0.0025354 | 6.672e-06 | No
2019-07-04 | 8:30 | APC2 | Short rural | Planned |  | 27 | 380 | 0.033754 | 8.8826e-05 | No
2019-07-04 | 8:00 | L591 | Short rural | Planned |  | 39 | 510 | 0.065435 | 0.0001283 | No
2019-07-04 | 8:00 | 8650 | Short rural | Planned |  | 5 | 420 | 0.0069087 | 1.6449e-05 | No
2019-07-04 | 8:30 | GG1232 | Short rural | Planned |  | 16 | 204 | 0.010738 | 5.2638e-05 | No
2019-07-04 | 9:00 | S744 | Urban | Planned |  | 47 | 330 | 0.020697 | 6.2717e-05 | No
2019-07-04 | 8:00 | MYE2 | Short rural | Planned |  | 103 | 414 | 0.14029 | 0.00033886 | No
2019-07-05 | 6:00 | KC1284 | Short rural | Planned |  | 7 | 964.2857 | 0.022207 | 2.3029e-05 | No
2019-07-05 | 6:30 | KC1284 | Short rural | Planned |  | 2 | 3240 | 0.021318 | 6.5797e-06 | No
2019-07-05 | 8:00 | 25744 | Short rural | Planned |  | 19 | 120 | 0.0075009 | 6.2507e-05 | No
2019-07-05 | 5:30 | 25744 | Short rural | Planned |  | 19 | 60 | 0.0037504 | 6.2507e-05 | No
2019-07-05 | 8:00 | 1959 | Urban | Planned |  | 35 | 420 | 0.019616 | 4.6704e-05 | No
2019-07-05 | 8:00 | SL1132 | Short rural | Planned |  | 22 | 488 | 0.03532 | 7.2377e-05 | No
2019-07-05 | 11:30 | MVF2 | Short rural | Planned |  | 3 | 70 | 0.00069087 | 9.8696e-06 | No
2019-07-05 | 8:00 | PK1262 | Short rural | Planned |  | 92 | 430 | 0.13015 | 0.00030267 | No
2019-07-05 | 6:30 | KC1284 | Short rural | Planned |  | 42 | 840 | 0.11607 | 0.00013817 | No
2019-07-05 | 8:30 | KME2 | Short rural | Planned |  | 6 | 133 | 0.0026253 | 1.9739e-05 | No
2019-07-05 | 8:00 | L591 | Short rural | Planned |  | 67 | 480 | 0.1058 | 0.00022042 | No
2019-07-05 | 8:00 | L526 | Urban | Planned |  | 48 | 380 | 0.024339 | 6.4051e-05 | No
2019-07-06 | 7:00 | 6426 | Urban | Planned |  | 4 | 565 | 0.0030157 | 5.3376e-06 | No
2019-07-07 | 7:00 | 6426 | Urban | Planned |  | 4 | 310 | 0.0016547 | 5.3376e-06 | No
2019-07-08 | 8:00 | MG1286 | Short rural | Planned |  | 135 | 405 | 0.17987 | 0.00044413 | No
2019-07-08 | 8:30 | BDC2 | Short rural | Planned |  | 10 | 404 | 0.013291 | 3.2899e-05 | No
2019-07-08 | 8:00 | SG1220 | Urban | Planned |  | 34 | 480 | 0.021777 | 4.537e-05 | No
2019-07-08 | 8:00 | NM1213 | Urban | Planned |  | 23 | 450 | 0.013811 | 3.0691e-05 | No
2019-07-08 | 7:00 | DS1235 | Urban | Planned |  | 2 | 305 | 0.00081398 | 2.6688e-06 | No
2019-07-08 | 8:00 | 35981 | Short rural | Planned |  | 61 | 540 | 0.10837 | 0.00020068 | No
2019-07-09 | 8:00 | X213 | Short rural | Planned |  | 5 | 255 | 0.0041946 | 1.6449e-05 | No
2019-07-09 | 8:00 | RBC2 | Short rural | Planned |  | 18 | 370 | 0.02191 | 5.9218e-05 | No
2019-07-09 | 8:00 | 35773 | Urban | Planned |  | 20 | 475 | 0.012677 | 2.6688e-05 | No
2019-07-09 | 8:00 | 35818 | Short rural | Planned |  | 9 | 475 | 0.014064 | 2.9609e-05 | No
2019-07-09 | 9:00 | 8641 | Urban | Planned |  | 53 | 246 | 0.017398 | 7.0723e-05 | No
2019-07-09 | 8:00 | HR1276 | Urban | Planned |  | 98 | 495 | 0.064732 | 0.00013077 | No
2019-07-09 | 8:00 | NA1218 | Urban | Planned |  | 195 | 398 | 0.10356 | 0.00026021 | No
2019-07-09 | 8:30 | JBB2 | Short rural | Planned |  | 9 | 491 | 0.014538 | 2.9609e-05 | No
2019-07-09 | 8:30 | GG1295 | Short rural | Planned |  | 22 | 395 | 0.028589 | 7.2377e-05 | No
2019-07-09 | 8:00 | MYE2 | Short rural | Planned |  | 149 | 465 | 0.22794 | 0.00049019 | No
2019-07-09 | 8:30 | 35590 | Short rural | Planned |  | 6 | 420 | 0.0082905 | 1.9739e-05 | No
2019-07-09 | 8:30 | YYA2 | Short rural | Planned |  | 66 | 410 | 0.089024 | 0.00021713 | No
2019-07-09 | 9:00 | 10248 | Urban | Planned |  | 7 | 210 | 0.0019616 | 9.3408e-06 | No
2019-07-09 | 8:30 | 7123 | Urban | Planned |  | 3 | 420 | 0.0016813 | 4.0032e-06 | No
2019-07-09 | 1:00 | BYD2 | Short rural | Planned |  | 1 | 70 | 0.00023029 | 3.2899e-06 | No
2019-07-09 | 8:00 | CS1213 | Urban | Planned |  | 41 | 540 | 0.029544 | 5.471e-05 | No
2019-07-09 | 8:00 | RV1280 | Urban | Planned |  | 19 | 420 | 0.010649 | 2.5354e-05 | No
2019-07-10 | 8:30 | ULD2 | Urban | Planned |  | 76 | 420 | 0.042594 | 0.00010141 | No
2019-07-10 | 8:00 | BWH2 | Short rural | Planned |  | 81 | 480 | 0.12791 | 0.00026648 | No
2019-07-10 | 8:30 | GG1295 | Short rural | Planned |  | 24 | 420 | 0.033162 | 7.8957e-05 | No
2019-07-10 | 8:00 | 8799 | Short rural | Planned |  | 10 | 385 | 0.012666 | 3.2899e-05 | No
2019-07-10 | 8:00 | S741 | Short rural | Planned |  | 40 | 345 | 0.0454 | 0.00013159 | No
2019-07-10 | 8:00 | MG1219 | Short rural | Planned |  | 27 | 375 | 0.03331 | 8.8826e-05 | No
2019-07-10 | 8:30 | BDA2 | Short rural | Planned |  | 13 | 420 | 0.017963 | 4.2768e-05 | No
2019-07-10 | 8:00 | X217 | Short rural | Planned |  | 9 | 390 | 0.011547 | 2.9609e-05 | No
2019-07-10 | 8:30 | DP1210 | Short rural | Planned |  | 9 | 420 | 0.012436 | 2.9609e-05 | No
2019-07-10 | 8:00 | R210 | Short rural | Planned |  | 71 | 365 | 0.085257 | 0.00023358 | No
2019-07-10 | 8:30 | KVD2 | Short rural | Planned |  | 63 | 309 | 0.064044 | 0.00020726 | No
2019-07-10 | 8:00 | WWA2 | Short rural | Planned |  | 59 | 313 | 0.060754 | 0.0001941 | No
2019-07-10 | 8:00 | A327 | Urban | Planned |  | 144 | 540 | 0.10376 | 0.00019215 | No
2019-07-10 | 6:30 | 9030 | Urban | Planned |  | 1 | 510 | 0.00068054 | 1.3344e-06 | No
2019-07-10 | 8:00 | FT1206 | Short rural | Planned |  | 231 | 420 | 0.31918 | 0.00075996 | No
2019-07-10 | 8:30 | BDA2 | Short rural | Planned |  | 5 | 255 | 0.0041946 | 1.6449e-05 | No
2019-07-10 | 8:00 | A095 | Short rural | Planned |  | 7 | 237 | 0.0054579 | 2.3029e-05 | No
2019-07-10 | 8:00 | W124 | Short rural | Planned |  | 11 | 450 | 0.016285 | 3.6188e-05 | No
2019-07-10 | 8:00 | MR2224 | Short rural | Planned |  | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2019-07-11 | 8:00 | 8645 | Urban | Planned |  | 38 | 210 | 0.010649 | 5.0707e-05 | No
2019-07-11 | 8:00 | RV1246 | Short rural | Planned |  | 155 | 480 | 0.24477 | 0.00050993 | No
2019-07-11 | 8:00 | SY1132 | Urban | Planned |  | 245 | 335 | 0.10952 | 0.00032693 | No
2019-07-11 | 8:00 | S740 | Urban | Planned |  | 37 | 440 | 0.021724 | 4.9373e-05 | No
2019-07-11 | 8:30 | APH2 | Urban | Planned |  | 88 | 195 | 0.022898 | 0.00011743 | No
2019-07-11 | 8:00 | GL1233 | Short rural | Planned |  | 27 | 345 | 0.030645 | 8.8826e-05 | No
2019-07-11 | 8:00 | WWF2 | Urban | Planned |  | 118 | 365 | 0.057473 | 0.00015746 | No
2019-07-11 | 7:30 | 9052 | Urban | Planned |  | 42 | 570 | 0.031946 | 5.6045e-05 | No
2019-07-11 | 8:00 | X217 | Short rural | Planned |  | 23 | 345 | 0.026105 | 7.5667e-05 | No
2019-07-11 | 8:00 | 1962 | Urban | Planned |  | 95 | 360 | 0.045636 | 0.00012677 | No
2019-07-12 | 9:00 | 41361 | Urban | Planned |  | 52 | 165 | 0.011449 | 6.9389e-05 | No
2019-07-12 | 8:00 | 35981 | Short rural | Planned |  | 5 | 40 | 0.00065797 | 1.6449e-05 | No
2019-07-12 | 8:00 | RBD2 | Short rural | Planned |  | 2 | 80 | 0.00052638 | 6.5797e-06 | No
2019-07-12 | 8:30 | BDA2 | Short rural | Planned |  | 37 | 365 | 0.04443 | 0.00012172 | No
2019-07-12 | 12:00 | RBD2 | Short rural | Planned |  | 1 | 75 | 0.00024674 | 3.2899e-06 | No
2019-07-12 | 8:00 | 8798 | Short rural | Planned |  | 35 | 365 | 0.042028 | 0.00011515 | No
2019-07-12 | 10:00 | RBD2 | Short rural | Planned |  | 2 | 60 | 0.00039478 | 6.5797e-06 | No
2019-07-12 | 8:30 | BDF2 | Short rural | Planned |  | 82 | 262 | 0.070679 | 0.00026977 | No
2019-07-12 | 8:30 | 7529 | Short rural | Planned |  | 1 | 420 | 0.0013817 | 3.2899e-06 | No
2019-07-12 | 8:00 | 49001 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2019-07-12 | 8:00 | DS1226 | Urban | Planned |  | 65 | 480 | 0.041633 | 8.6736e-05 | No
2019-07-12 | 8:00 | A096 | Short rural | Planned |  | 49 | 520 | 0.083826 | 0.0001612 | No
2019-07-12 | 8:00 | A051 | Urban | Planned |  | 16 | 380 | 0.0081131 | 2.135e-05 | No
2019-07-13 | 8:00 | 2816 | Urban | Planned |  | 220 | 460 | 0.13504 | 0.00029357 | No
2019-07-15 | 9:00 | 41361 | Urban | Planned |  | 69 | 95 | 0.008747 | 9.2074e-05 | No
2019-07-15 | 8:00 | 1957 | Urban | Planned |  | 38 | 375 | 0.019015 | 5.0707e-05 | No
2019-07-15 | 8:00 | X213 | Short rural | Planned |  | 4 | 260 | 0.0034215 | 1.3159e-05 | No
2019-07-15 | 9:00 | 8679 | Urban | Planned |  | 46 | 360 | 0.022098 | 6.1382e-05 | No
2019-07-15 | 8:00 | MR2224 | Short rural | Planned |  | 8 | 540 | 0.014212 | 2.6319e-05 | No
2019-07-15 | 7:00 | 48161 | Urban | Planned |  | 1 | 510 | 0.00068054 | 1.3344e-06 | No
2019-07-16 | 9:00 | KVA2 | Short rural | Planned |  | 19 | 300 | 0.018752 | 6.2507e-05 | No
2019-07-16 | 8:00 | CX1232 | Short rural | Planned |  | 20 | 370 | 0.024345 | 6.5797e-05 | No
2019-07-16 | 8:00 | 8683 | Urban | Planned |  | 97 | 360 | 0.046597 | 0.00012944 | No
2019-07-16 | 8:00 | RD1232 | Urban | Planned |  | 97 | 480 | 0.06213 | 0.00012944 | No
2019-07-16 | 9:00 | ULL2 | Short rural | Planned |  | 4 | 190 | 0.0025003 | 1.3159e-05 | No
2019-07-16 | 8:00 | J514 | Urban | Planned |  | 86 | 460 | 0.052789 | 0.00011476 | No
2019-07-16 | 7:30 | 48205 | Urban | Planned |  | 77 | 490 | 0.050347 | 0.00010275 | No
2019-07-16 | 9:00 | ULL2 | Short rural | Planned |  | 1 | 200 | 0.00065797 | 3.2899e-06 | No
2019-07-16 | 8:00 | ULB2 | Short rural | Planned |  | 54 | 200 | 0.035531 | 0.00017765 | No
2019-07-16 | 8:00 | BWE2 | Short rural | Planned |  | 6 | 440 | 0.0086852 | 1.9739e-05 | No
2019-07-16 | 8:30 | APE2 | Short rural | Planned |  | 6 | 380 | 0.0075009 | 1.9739e-05 | No
2019-07-16 | 9:00 | 25777 | Urban | Planned |  | 69 | 165 | 0.015192 | 9.2074e-05 | No
2019-07-16 | 7:30 | 19871 | Urban | Planned |  | 6 | 390 | 0.0031225 | 8.0064e-06 | No
2019-07-16 | 8:00 | OA1233 | Short rural | Planned |  | 38 | 370 | 0.046255 | 0.00012501 | No
2019-07-16 | 8:00 | T841 | Short rural | Planned |  | 58 | 460 | 0.087774 | 0.00019081 | No
2019-07-16 | 10:00 | ULL2 | Short rural | Planned |  | 1 | 250 | 0.00082247 | 3.2899e-06 | No
2019-07-17 | 8:00 | 2809 | Urban | Planned |  | 85 | 385 | 0.043668 | 0.00011342 | No
2019-07-17 | 8:30 | KVA2 | Short rural | Planned |  | 6 | 205 | 0.0040465 | 1.9739e-05 | No
2019-07-17 | 8:00 | T831 | Short rural | Planned |  | 15 | 434 | 0.021417 | 4.9348e-05 | No
2019-07-17 | 8:00 | HR1269 | Urban | Planned |  | 58 | 495 | 0.038311 | 7.7395e-05 | No
2019-07-17 | 8:30 | APC2 | Short rural | Planned |  | 7 | 280 | 0.0064481 | 2.3029e-05 | No
2019-07-17 | 8:30 | KVA2 | Short rural | Planned |  | 3 | 338 | 0.0033359 | 9.8696e-06 | No
2019-07-17 | 8:00 | YYA2 | Short rural | Planned |  | 70 | 125 | 0.028786 | 0.00023029 | No
2019-07-17 | 9:00 | ULH2 | Short rural | Planned |  | 1 | 160 | 0.00052638 | 3.2899e-06 | No
2019-07-17 | 8:30 | WRA2 | Urban | Planned |  | 320 | 400 | 0.1708 | 0.00042701 | No
2019-07-17 | 8:30 | KVA2 | Short rural | Planned |  | 1 | 145 | 0.00047703 | 3.2899e-06 | No
2019-07-17 | 8:00 | SC1204 | Short rural | Planned |  | 163 | 440 | 0.23595 | 0.00053625 | No
2019-07-17 | 8:00 | WH1294 | Urban | Planned |  | 129 | 345 | 0.059387 | 0.00017214 | No
2019-07-17 | 8:00 | 8801 | Short rural | Planned |  | 17 | 470 | 0.026286 | 5.5928e-05 | No
2019-07-17 | 8:00 | MYM2 | Urban | Planned |  | 144 | 405 | 0.077822 | 0.00019215 | No
2019-07-17 | 8:30 | BDA2 | Short rural | Planned |  | 26 | 245 | 0.020956 | 8.5536e-05 | No
2019-07-17 | 6:30 | C811 | Urban | Planned |  | 2 | 350 | 0.00093408 | 2.6688e-06 | No
2019-07-17 | 8:00 | RBB2 | Short rural | Planned |  | 36 | 380 | 0.045005 | 0.00011844 | No
2019-07-17 | 8:00 | W127 | Short rural | Planned |  | 93 | 410 | 0.12544 | 0.00030596 | No
2019-07-18 | 8:00 | NM1258 | Urban | Planned |  | 103 | 435 | 0.059788 | 0.00013744 | No
2019-07-18 | 8:00 | ULH2 | Short rural | Planned |  | 2 | 242 | 0.0015923 | 6.5797e-06 | No
2019-07-18 | 8:00 | T828 | Short rural | Planned |  | 19 | 372 | 0.023253 | 6.2507e-05 | No
2019-07-18 | 8:30 | APE2 | Short rural | Planned |  | 5 | 195 | 0.0032076 | 1.6449e-05 | No
2019-07-18 | 9:00 | ULH2 | Short rural | Planned |  | 2 | 206 | 0.0013554 | 6.5797e-06 | No
2019-07-18 | 8:00 | DFA2 | Short rural | Planned |  | 51 | 430 | 0.072147 | 0.00016778 | No
2019-07-18 | 8:00 | 55870 | Urban | Planned |  | 147 | 300 | 0.058847 | 0.00019616 | No
2019-07-18 | 12:00 | NA1270 | Short rural | Planned |  | 3 | 162 | 0.0015989 | 9.8696e-06 | No
2019-07-18 | 8:00 | MVF2 | Short rural | Planned |  | 10 | 325 | 0.010692 | 3.2899e-05 | No
2019-07-18 | 7:30 | CV1284 | Urban | Planned |  | 87 | 615 | 0.071397 | 0.00011609 | No
2019-07-18 | 8:30 | JBA2 | Short rural | Planned |  | 31 | 300 | 0.030596 | 0.00010199 | No
2019-07-18 | 9:00 | ULH2 | Short rural | Planned |  | 3 | 58 | 0.00057244 | 9.8696e-06 | No
2019-07-18 | 8:30 | NA1270 | Short rural | Planned |  | 3 | 172 | 0.0016976 | 9.8696e-06 | No
2019-07-18 | 8:30 | BYB2 | Short rural | Planned |  | 31 | 300 | 0.030596 | 0.00010199 | No
2019-07-18 | 10:00 | ULH2 | Short rural | Planned |  | 2 | 58 | 0.00038162 | 6.5797e-06 | No
2019-07-18 | 8:00 | 8801 | Short rural | Planned |  | 22 | 340 | 0.024608 | 7.2377e-05 | No
2019-07-18 | 7:00 | HR1269 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2019-07-18 | 7:00 | DP1269 | Urban | Planned |  | 80 | 30 | 0.0032026 | 0.00010675 | No
2019-07-19 | 8:00 | HR1269 | Urban | Planned |  | 43 | 405 | 0.023239 | 5.7379e-05 | No
2019-07-19 | 8:00 | BX1242 | Urban | Planned |  | 52 | 360 | 0.02498 | 6.9389e-05 | No
2019-07-19 | 8:00 | 77674 | Short rural | Planned |  | 5 | 275 | 0.0045236 | 1.6449e-05 | No
2019-07-19 | 8:00 | L941 | Short rural | Planned |  | 31 | 390 | 0.039774 | 0.00010199 | No
2019-07-19 | 8:00 | 1953 | Urban | Planned |  | 2 | 480 | 0.001281 | 2.6688e-06 | No
2019-07-19 | 8:00 | 35305 | Urban | Planned |  | 60 | 370 | 0.029624 | 8.0064e-05 | No
2019-07-19 | 8:00 | S743 | Short rural | Planned |  | 43 | 310 | 0.043854 | 0.00014146 | No
2019-07-19 | 9:00 | ULE2 | Short rural | Planned |  | 5 | 240 | 0.0039478 | 1.6449e-05 | No
2019-07-19 | 8:30 | GG1232 | Short rural | Planned |  | 16 | 300 | 0.015791 | 5.2638e-05 | No
2019-07-19 | 8:00 | SL1132 | Short rural | Planned |  | 20 | 480 | 0.031583 | 6.5797e-05 | No
2019-07-19 | 8:00 | BL1210 | Short rural | Planned |  | 164 | 440 | 0.2374 | 0.00053954 | No
2019-07-19 | 8:30 | W163 | Short rural | Planned |  | 10 | 210 | 0.0069087 | 3.2899e-05 | No
2019-07-19 | 11:00 | NG1262 | Short rural | Planned |  | 6 | 115 | 0.00227 | 1.9739e-05 | No
2019-07-19 | 10:00 | ULE2 | Short rural | Planned |  | 1 | 235 | 0.00077312 | 3.2899e-06 | No
2019-07-19 | 8:00 | GL1207 | Short rural | Planned |  | 18 | 225 | 0.013324 | 5.9218e-05 | No
2019-07-19 | 8:00 | T831 | Short rural | Planned |  | 6 | 350 | 0.0069087 | 1.9739e-05 | No
2019-07-19 | 8:00 | RD1228 | Urban | Planned |  | 107 | 285 | 0.040692 | 0.00014278 | No
2019-07-20 | 8:00 | X877 | Short rural | Planned |  | 12 | 450 | 0.017765 | 3.9478e-05 | No
2019-07-20 | 7:00 | SQ1452 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2019-07-20 | 8:00 | 6430 | Urban | Planned |  | 4 | 600 | 0.0032026 | 5.3376e-06 | No
2019-07-21 | 8:00 | KYH2 | Urban | Planned |  | 23 | 510 | 0.015653 | 3.0691e-05 | No
2019-07-22 | 8:00 | MG1286 | Short rural | Planned |  | 188 | 500 | 0.30925 | 0.00061849 | No
2019-07-23 | 8:00 | RD1228 | Urban | Planned |  | 53 | 420 | 0.029704 | 7.0723e-05 | No
2019-07-22 | 9:00 | MR2224 | Short rural | Planned |  | 3 | 250 | 0.0024674 | 9.8696e-06 | No
2019-07-22 | 8:30 | NN1255 | Urban | Planned |  | 57 | 265 | 0.020156 | 7.6061e-05 | No
2019-07-23 | 8:30 | KVA2 | Short rural | Planned |  | 20 | 390 | 0.025661 | 6.5797e-05 | No
2019-07-23 | 9:00 | KVB2 | Short rural | Planned |  | 2 | 390 | 0.0025661 | 6.5797e-06 | No
2019-07-23 | 8:30 | APC2 | Short rural | Planned |  | 1 | 435 | 0.0014311 | 3.2899e-06 | No
2019-07-23 | 9:00 | CR1280 | Urban | Planned |  | 28 | 420 | 0.015693 | 3.7363e-05 | No
2019-07-23 | 9:00 | YYB2 | Short rural | Planned |  | 27 | 290 | 0.02576 | 8.8826e-05 | No
2019-07-23 | 8:00 | T894 | Urban | Planned |  | 4 | 420 | 0.0022418 | 5.3376e-06 | No
2019-07-23 | 8:00 | CS1213 | Urban | Planned |  | 127 | 455 | 0.077108 | 0.00016947 | No
2019-07-23 | 8:00 | A051 | Urban | Planned |  | 21 | 380 | 0.010649 | 2.8022e-05 | No
2019-07-23 | 10:30 | RW1229 | Short rural | Planned |  | 23 | 40 | 0.0030267 | 7.5667e-05 | No
2019-07-23 | 8:00 | 8798 | Short rural | Planned |  | 4 | 450 | 0.0059218 | 1.3159e-05 | No
2019-07-23 | 8:00 | RW1229 | Short rural | Planned |  | 1 | 48 | 0.00015791 | 3.2899e-06 | No
2019-07-23 | 8:30 | CLC2 | Short rural | Planned |  | 8 | 368 | 0.0096854 | 2.6319e-05 | No
2019-07-23 | 12:00 | CLA2 | Short rural | Planned |  | 12 | 240 | 0.0094748 | 3.9478e-05 | No
2019-07-23 | 8:00 | 35990 | Short rural | Planned |  | 89 | 425 | 0.12444 | 0.0002928 | No
2019-07-23 | 8:30 | JBA2 | Short rural | Planned |  | 15 | 235 | 0.011597 | 4.9348e-05 | No
2019-07-23 | 9:00 | BYD2 | Short rural | Planned |  | 110 | 360 | 0.13028 | 0.00036188 | No
2019-07-23 | 8:00 | 87218 | Short rural | Planned |  | 8 | 230 | 0.0060533 | 2.6319e-05 | No
2019-07-23 | 8:00 | R208 | Short rural | Planned |  | 251 | 380 | 0.31379 | 0.00082576 | No
2019-07-23 | 9:00 | MYM2 | Urban | Planned |  | 148 | 598.7838 | 0.11825 | 0.00019749 | No
2019-07-23 | 8:30 | MYM2 | Urban | Planned |  | 63 | 1507.1429 | 0.1267 | 8.4067e-05 | No
2019-07-23 | 8:00 | A098 | Short rural | Planned |  | 3 | 525 | 0.0051815 | 9.8696e-06 | No
2019-07-23 | 8:00 | PH1290 | Urban | Planned |  | 1 | 465 | 0.0006205 | 1.3344e-06 | No
2019-07-23 | 8:30 | CLC2 | Short rural | Planned |  | 3 | 240 | 0.0023687 | 9.8696e-06 | No
2019-07-23 | 8:00 | CX1210 | Short rural | Planned |  | 32 | 400 | 0.04211 | 0.00010528 | No
2019-07-24 | 9:00 | 8679 | Urban | Planned |  | 40 | 360 | 0.019215 | 5.3376e-05 | No
2019-07-24 | 8:30 | BDB2 | Urban | Planned |  | 4 | 190 | 0.0010141 | 5.3376e-06 | No
2019-07-24 | 9:00 | NA1270 | Short rural | Planned |  | 2 | 279 | 0.0018357 | 6.5797e-06 | No
2019-07-24 | 8:00 | ULJ2 | Urban | Planned |  | 92 | 70 | 0.0085935 | 0.00012276 | No
2019-07-24 | 8:30 | SXD2 | Short rural | Planned |  | 398 | 340 | 0.44518 | 0.0013094 | No
2019-07-24 | 9:00 | ULH2 | Short rural | Planned |  | 6 | 145 | 0.0028622 | 1.9739e-05 | No
2019-07-24 | 8:00 | T868 | Short rural | Planned |  | 6 | 540 | 0.010659 | 1.9739e-05 | No
2019-07-24 | 12:00 | WBE2 | Short rural | Planned |  | 8 | 90 | 0.0023687 | 2.6319e-05 | No
2019-07-24 | 8:00 | J459 | Short rural | Planned |  | 100 | 405 | 0.13324 | 0.00032899 | No
2019-07-24 | 8:00 | X217 | Short rural | Planned |  | 23 | 480 | 0.03632 | 7.5667e-05 | No
2019-07-24 | 8:00 | MYM2 | Urban | Planned |  | 180 | 356 | 0.085508 | 0.00024019 | No
2019-07-24 | 7:30 | HS1142 | Short rural | Planned |  | 31 | 450 | 0.045894 | 0.00010199 | No
2019-07-24 | 8:00 | MR2232 | Short rural | Planned |  | 2 | 380 | 0.0025003 | 6.5797e-06 | No
2019-07-24 | 8:30 | 35335 | Urban | Planned |  | 66 | 315 | 0.027742 | 8.807e-05 | No
2019-07-24 | 8:30 | L526 | Urban | Planned |  | 70 | 420 | 0.039231 | 9.3408e-05 | No
2019-07-24 | 10:00 | ULE2 | Short rural | Planned |  | 5 | 40 | 0.00065797 | 1.6449e-05 | No
2019-07-24 | 9:30 | HKF2 | Short rural | Planned |  | 69 | 210 | 0.04767 | 0.000227 | No
2019-07-24 | 8:30 | APA2 | Urban | Planned |  | 77 | 420 | 0.043154 | 0.00010275 | No
2019-07-24 | 8:00 | L941 | Short rural | Planned |  | 12 | 330 | 0.013028 | 3.9478e-05 | No
2019-07-24 | 8:30 | SHG2 | Short rural | Planned |  | 6 | 35 | 0.00069087 | 1.9739e-05 | No
2019-07-24 | 12:00 | TM1217 | Short rural | Planned |  | 5 | 190 | 0.0031254 | 1.6449e-05 | No
2019-07-24 | 8:30 | HKD2 | Short rural | Planned |  | 109 | 135 | 0.04841 | 0.0003586 | No
2019-07-24 | 8:00 | 8743 | Urban | Planned |  | 105 | 255 | 0.035729 | 0.00014011 | No
2019-07-24 | 8:00 | DFA2 | Short rural | Planned |  | 5 | 215 | 0.0035366 | 1.6449e-05 | No
2019-07-25 | 8:00 | L947 | Short rural | Planned |  | 5 | 345 | 0.005675 | 1.6449e-05 | No
2019-07-25 | 9:00 | A098 | Short rural | Planned |  | 3 | 4620 | 0.045598 | 9.8696e-06 | No
2019-07-25 | 8:30 | BYB2 | Short rural | Planned |  | 71 | 310 | 0.07241 | 0.00023358 | No
2019-07-25 | 7:00 | PH1264 | Urban | Planned |  | 36 | 690 | 0.033146 | 4.8038e-05 | No
2019-07-25 | 9:00 | A095 | Short rural | Planned |  | 7 | 540 | 0.012436 | 2.3029e-05 | No
2019-07-25 | 8:00 | RW1255 | Short rural | Planned |  | 16 | 275 | 0.014475 | 5.2638e-05 | No
2019-07-25 | 8:00 | R290 | Short rural | Planned |  | 35 | 510 | 0.058724 | 0.00011515 | No
2019-07-25 | 8:00 | CT1225 | Short rural | Planned |  | 68 | 250 | 0.055928 | 0.00022371 | No
2019-07-25 | 8:00 | SL1112 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2019-07-25 | 8:00 | RV1246 | Short rural | Planned |  | 168 | 460 | 0.25424 | 0.0005527 | No
2019-07-25 | 9:00 | A098 | Short rural | Planned |  | 8 | 742.5 | 0.019542 | 2.6319e-05 | No
2019-07-25 | 8:00 | R211 | Short rural | Planned |  | 116 | 390 | 0.14883 | 0.00038162 | No
2019-07-25 | 8:00 | CX1210 | Short rural | Planned |  | 52 | 360 | 0.061586 | 0.00017107 | No
2019-07-26 | 8:00 | BL1243 | Short rural | Planned |  | 70 | 210 | 0.048361 | 0.00023029 | No
2019-07-26 | 8:00 | SC1238 | Urban | Planned |  | 40 | 470 | 0.025087 | 5.3376e-05 | No
2019-07-26 | 8:00 | MVF2 | Short rural | Planned |  | 14 | 120 | 0.005527 | 4.6058e-05 | No
2019-07-26 | 9:00 | 7502 | Urban | Planned |  | 2 | 300 | 0.00080064 | 2.6688e-06 | No
2019-07-26 | 8:00 | 25784 | Urban | Planned |  | 131 | 455 | 0.079537 | 0.00017481 | No
2019-07-26 | 8:30 | YYA2 | Short rural | Planned |  | 120 | 450 | 0.17765 | 0.00039478 | No
2019-07-26 | 8:00 | OA1244 | Short rural | Planned |  | 23 | 218 | 0.016495 | 7.5667e-05 | No
2019-07-26 | 8:00 | S744 | Urban | Planned |  | 101 | 350 | 0.047171 | 0.00013477 | No
2019-07-26 | 7:30 | 49916 | Urban | Planned |  | 70 | 355 | 0.03316 | 9.3408e-05 | No
2019-07-26 | 8:00 | 8744 | Urban | Planned |  | 95 | 390 | 0.049439 | 0.00012677 | No
2019-07-26 | 8:30 | TM1210 | Short rural | Planned |  | 42 | 125 | 0.017272 | 0.00013817 | No
2019-07-26 | 8:30 | DP1210 | Short rural | Planned |  | 86 | 390 | 0.11034 | 0.00028293 | No
2019-07-26 | 9:00 | TM1210 | Short rural | Planned |  | 1 | 135 | 0.00044413 | 3.2899e-06 | No
2019-07-26 | 8:00 | L948 | Short rural | Planned |  | 19 | 385 | 0.024065 | 6.2507e-05 | No
2019-07-27 | 7:00 | WL1299 | Urban | Planned |  | 4 | 525 | 0.0028022 | 5.3376e-06 | No
2019-07-28 | 8:00 | 27335 | Urban | Planned |  | 32 | 315 | 0.013451 | 4.2701e-05 | No
2019-07-28 | 8:00 | SWJ2 | Urban | Planned |  | 197 | 570 | 0.14984 | 0.00026288 | No
2019-07-28 | 7:00 | CT1233 | Urban | Planned |  | 4 | 565 | 0.0030157 | 5.3376e-06 | No
2019-07-28 | 8:00 | 9026 | Urban | Planned |  | 66 | 515 | 0.045356 | 8.807e-05 | No
2019-07-29 | 8:30 | KVA2 | Short rural | Planned |  | 14 | 279 | 0.01285 | 4.6058e-05 | No
2019-07-29 | 8:00 | 53807 | Short rural | Planned |  | 13 | 585 | 0.025019 | 4.2768e-05 | No
2019-07-29 | 8:00 | MG1219 | Short rural | Planned |  | 9 | 390 | 0.011547 | 2.9609e-05 | No
2019-07-29 | 11:00 | NA1270 | Short rural | Planned |  | 1 | 40 | 0.00013159 | 3.2899e-06 | No
2019-07-29 | 8:00 | BL1232 | Short rural | Planned |  | 119 | 400 | 0.1566 | 0.00039149 | No
2019-07-29 | 10:00 | NA1270 | Short rural | Planned |  | 1 | 50 | 0.00016449 | 3.2899e-06 | No
2019-07-29 | 8:00 | L584 | Short rural | Planned |  | 23 | 360 | 0.02724 | 7.5667e-05 | No
2019-07-29 | 8:00 | 9032 | Short rural | Planned |  | 45 | 930 | 0.13768 | 0.00014804 | No
2019-07-29 | 9:00 | NA1270 | Short rural | Planned |  | 3 | 65 | 0.00064152 | 9.8696e-06 | No
2019-07-30 | 8:00 | 87220 | Short rural | Planned |  | 2 | 505 | 0.0033228 | 6.5797e-06 | No
2019-07-30 | 9:00 | CLB2 | Short rural | Planned |  | 59 | 312 | 0.06056 | 0.0001941 | No
2019-07-30 | 8:00 | WWC2 | Short rural | Planned |  | 129 | 345 | 0.14642 | 0.00042439 | No
2019-07-30 | 8:30 | KVA2 | Short rural | Planned |  | 2 | 386 | 0.0025398 | 6.5797e-06 | No
2019-07-30 | 12:30 | BDA2 | Short rural | Planned |  | 1 | 90 | 0.00029609 | 3.2899e-06 | No
2019-07-30 | 8:00 | 35980 | Short rural | Planned |  | 9 | 345 | 0.010215 | 2.9609e-05 | No
2019-07-30 | 8:30 | APA2 | Urban | Planned |  | 34 | 300 | 0.013611 | 4.537e-05 | No
2019-07-30 | 8:30 | BDA2 | Short rural | Planned |  | 8 | 109 | 0.0028688 | 2.6319e-05 | No
2019-07-30 | 8:00 | 87218 | Short rural | Planned |  | 7 | 410 | 0.0094419 | 2.3029e-05 | No
2019-07-30 | 9:00 | WRE2 | Urban | Planned |  | 115 | 300 | 0.046037 | 0.00015346 | No
2019-07-30 | 8:00 | WWC2 | Short rural | Planned |  | 28 | 480 | 0.044216 | 9.2116e-05 | No
2019-07-30 | 8:30 | JBB2 | Short rural | Planned |  | 17 | 530 | 0.029642 | 5.5928e-05 | No
2019-07-30 | 8:00 | 7962 | Urban | Planned |  | 96 | 525 | 0.067254 | 0.0001281 | No
2019-07-30 | 10:00 | 25747 | Urban | Planned |  | 2 | 10 | 2.6688e-05 | 2.6688e-06 | No
2019-07-30 | 8:30 | APC2 | Short rural | Planned |  | 8 | 155 | 0.0040794 | 2.6319e-05 | No
2019-07-30 | 8:00 | 27029 | Short rural | Planned |  | 20 | 420 | 0.027635 | 6.5797e-05 | No
2019-07-30 | 9:00 | B201 | Urban | Planned |  | 15 | 360 | 0.0072058 | 2.0016e-05 | No
2019-07-30 | 8:30 | KVD2 | Short rural | Planned |  | 11 | 215 | 0.0077805 | 3.6188e-05 | No
2019-07-30 | 9:00 | KVB2 | Short rural | Planned |  | 3 | 78 | 0.00076983 | 9.8696e-06 | No
2019-07-30 | 9:30 | KVB2 | Short rural | Planned |  | 1 | 278 | 0.00091458 | 3.2899e-06 | No
2019-07-30 | 8:00 | R260 | Short rural | Planned |  | 175 | 420 | 0.2418 | 0.00057573 | No
2019-07-30 | 10:00 | KVB2 | Short rural | Planned |  | 1 | 53 | 0.00017436 | 3.2899e-06 | No
2019-07-30 | 8:00 | SL1142 | Short rural | Planned |  | 25 | 530 | 0.043591 | 8.2247e-05 | No
2019-07-30 | 8:00 | CT1225 | Short rural | Planned |  | 33 | 360 | 0.039084 | 0.00010857 | No
2019-07-30 | 9:30 | KVB2 | Short rural | Planned |  | 5 | 257 | 0.0042275 | 1.6449e-05 | No
2019-07-31 | 8:00 | 1959 | Urban | Planned |  | 36 | 240 | 0.011529 | 4.8038e-05 | No
2019-07-31 | 8:00 | 17059 | Urban | Planned |  | 25 | 270 | 0.0090072 | 3.336e-05 | No
2019-07-31 | 8:00 | APE2 | Short rural | Planned |  | 12 | 385 | 0.015199 | 3.9478e-05 | No
2019-07-31 | 8:00 | RBC2 | Short rural | Planned |  | 16 | 405 | 0.021318 | 5.2638e-05 | No
2019-07-31 | 7:30 | L509 | Urban | Planned |  | 94 | 300 | 0.03763 | 0.00012543 | No
2019-07-31 | 10:00 | X883 | Urban | Planned |  | 20 | 215 | 0.0057379 | 2.6688e-05 | No
2019-07-31 | 8:00 | DP1210 | Short rural | Planned |  | 35 | 670 | 0.077147 | 0.00011515 | No
2019-07-31 | 8:00 | 9055 | Urban | Planned |  | 13 | 410 | 0.0071123 | 1.7347e-05 | No
2019-07-31 | 8:00 | PH1271 | Urban | Planned |  | 38 | 540 | 0.027382 | 5.0707e-05 | No
2019-07-31 | 7:30 | KC1262 | Short rural | Planned |  | 19 | 400 | 0.025003 | 6.2507e-05 | No
2019-07-31 | 8:00 | ULH2 | Short rural | Planned |  | 4 | 510 | 0.0067113 | 1.3159e-05 | No
2019-07-31 | 8:30 | BYB2 | Short rural | Planned |  | 13 | 388 | 0.016594 | 4.2768e-05 | No
2019-07-31 | 8:30 | JBA2 | Short rural | Planned |  | 62 | 410 | 0.083628 | 0.00020397 | No
2019-07-31 | 8:30 | APB2 | Short rural | Planned |  | 3 | 385 | 0.0037998 | 9.8696e-06 | No
2019-07-31 | 8:00 | BL1210 | Short rural | Planned |  | 162 | 430 | 0.22917 | 0.00053296 | No
2019-08-01 | 8:00 | WBC2 | Short rural | Planned |  | 104 | 450 | 0.15397 | 0.00034215 | No
2019-08-01 | 8:00 | AB1280 | Urban | Planned |  | 47 | 315 | 0.019756 | 6.2717e-05 | No
2019-08-01 | 8:00 | S740 | Urban | Planned |  | 29 | 480 | 0.018575 | 3.8698e-05 | No
2019-08-01 | 8:00 | HR1273 | Urban | Planned |  | 42 | 375 | 0.021017 | 5.6045e-05 | No
2019-08-01 | 8:00 | RBE2 | Short rural | Planned |  | 26 | 510 | 0.043624 | 8.5536e-05 | No
2019-08-01 | 8:00 | MR2218 | Short rural | Planned |  | 18 | 465 | 0.027536 | 5.9218e-05 | No
2019-08-01 | 8:00 | R208 | Short rural | Planned |  | 91 | 245 | 0.073348 | 0.00029938 | No
2019-08-01 | 8:00 | 35988 | Short rural | Planned |  | 171 | 540 | 0.30379 | 0.00056257 | No
2019-08-01 | 8:00 | 2815 | Urban | Planned |  | 299 | 480 | 0.19151 | 0.00039899 | No
2019-08-01 | 8:30 | YYA2 | Short rural | Planned |  | 14 | 372 | 0.017134 | 4.6058e-05 | No
2019-08-01 | 9:00 | 7532 | Short rural | Planned |  | 4 | 340 | 0.0044742 | 1.3159e-05 | No
2019-08-01 | 8:00 | J459 | Short rural | Planned |  | 92 | 235 | 0.071127 | 0.00030267 | No
2019-08-01 | 8:00 | CX1210 | Short rural | Planned |  | 2 | 390 | 0.0025661 | 6.5797e-06 | No
2019-08-01 | 8:00 | HBC2 | Short rural | Planned |  | 109 | 240 | 0.086063 | 0.0003586 | No
2019-08-01 | 8:00 | HR1273 | Urban | Planned |  | 38 | 450 | 0.022818 | 5.0707e-05 | No
2019-08-01 | 8:30 | GG1295 | Short rural | Planned |  | 9 | 142 | 0.0042044 | 2.9609e-05 | No
2019-08-02 | 8:00 | HR1269 | Urban | Planned |  | 160 | 280 | 0.059781 | 0.0002135 | No
2019-08-02 | 8:30 | KVB2 | Short rural | Planned |  | 16 | 390 | 0.020529 | 5.2638e-05 | No
2019-08-02 | 8:00 | 10290 | Short rural | Planned |  | 27 | 525 | 0.046634 | 8.8826e-05 | No
2019-08-02 | 8:30 | 7529 | Short rural | Planned |  | 9 | 280 | 0.0082905 | 2.9609e-05 | No
2019-08-02 | 8:30 | KVB2 | Short rural | Planned |  | 19 | 301 | 0.018815 | 6.2507e-05 | No
2019-08-02 | 8:00 | FT1208 | Urban | Planned |  | 45 | 200 | 0.01201 | 6.0048e-05 | No
2019-08-02 | 8:00 | RV1298 | Urban | Planned |  | 139 | 375 | 0.069556 | 0.00018548 | No
2019-08-02 | 8:00 | J459 | Short rural | Planned |  | 138 | 125 | 0.05675 | 0.000454 | No
2019-08-02 | 8:00 | WWF2 | Urban | Planned |  | 204 | 375 | 0.10208 | 0.00027222 | No
2019-08-02 | 8:30 | BYB2 | Short rural | Planned |  | 15 | 295 | 0.014558 | 4.9348e-05 | No
2019-08-02 | 8:00 | 10244 | Short rural | Planned |  | 139 | 390 | 0.17834 | 0.00045729 | No
2019-08-02 | 9:00 | BYC2 | Short rural | Planned |  | 3 | 314 | 0.0030991 | 9.8696e-06 | No
2019-08-02 | 9:00 | BYC2 | Short rural | Planned |  | 4 | 205 | 0.0026977 | 1.3159e-05 | No
2019-08-02 | 9:00 | APE2 | Short rural | Planned |  | 49 | 170 | 0.027405 | 0.0001612 | No
2019-08-02 | 8:00 | 27038 | Short rural | Planned |  | 4 | 440 | 0.0057902 | 1.3159e-05 | No
2019-08-02 | 6:00 | NK1352 | Urban | Planned |  | 2 | 450 | 0.001201 | 2.6688e-06 | No
2019-08-02 | 8:00 | 8735 | Urban | Planned |  | 37 | 480 | 0.023699 | 4.9373e-05 | No
2019-08-03 | 6:00 | NM1243 | Urban | Planned |  | 1 | 405 | 0.00054043 | 1.3344e-06 | No
2019-08-03 | 8:00 | WL1236 | Urban | Planned |  | 9 | 495 | 0.0059447 | 1.201e-05 | No
2019-08-03 | 7:00 | 54695 | Short rural | Planned |  | 1 | 600 | 0.0019739 | 3.2899e-06 | No
2019-08-04 | 8:00 | TM1258 | Short rural | Planned |  | 31 | 460 | 0.046913 | 0.00010199 | No
2019-08-04 | 7:00 | 8611 | Urban | Planned |  | 44 | 540 | 0.031705 | 5.8714e-05 | No
2019-08-04 | 8:30 | M399 | Short rural | Planned |  | 10 | 295 | 0.0097051 | 3.2899e-05 | No
2019-08-05 | 8:00 | A046 | Short rural | Planned |  | 25 | 210 | 0.017272 | 8.2247e-05 | No
2019-08-05 | 9:30 | 35983 | Short rural | Planned |  | 13 | 175 | 0.0074844 | 4.2768e-05 | No
2019-08-05 | 12:30 | MYE2 | Short rural | Planned |  | 1 | 210 | 0.00069087 | 3.2899e-06 | No
2019-08-05 | 8:30 | KVD2 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2019-08-05 | 8:00 | HBB2 | Short rural | Planned |  | 211 | 465 | 0.32278 | 0.00069416 | No
2019-08-05 | 8:00 | 35988 | Short rural | Planned |  | 27 | 461 | 0.040949 | 8.8826e-05 | No
2019-08-05 | 8:00 | CS1284 | Urban | Planned |  | 81 | 412 | 0.044532 | 0.00010809 | No
2019-08-05 | 7:30 | T876 | Urban | Planned |  | 76 | 365 | 0.037016 | 0.00010141 | No
2019-08-05 | 8:30 | MYM2 | Urban | Planned |  | 96 | 180 | 0.023058 | 0.0001281 | No
2019-08-05 | 12:30 | MYM2 | Urban | Planned |  | 52 | 210 | 0.014572 | 6.9389e-05 | No
2019-08-06 | 8:00 | WBC2 | Short rural | Planned |  | 1 | 200 | 0.00065797 | 3.2899e-06 | No
2019-08-06 | 8:00 | NN1233 | Short rural | Planned |  | 9 | 480 | 0.014212 | 2.9609e-05 | No
2019-08-06 | 8:30 | ULD2 | Urban | Planned |  | 99 | 450 | 0.059447 | 0.00013211 | No
2019-08-06 | 9:30 | BX1332 | Urban | Planned |  | 53 | 245 | 0.017327 | 7.0723e-05 | No
2019-08-06 | 8:00 | HBB2 | Short rural | Planned |  | 36 | 480 | 0.056849 | 0.00011844 | No
2019-08-06 | 8:00 | BWH2 | Short rural | Planned |  | 17 | 410 | 0.02293 | 5.5928e-05 | No
2019-08-06 | 8:00 | NN1207 | Short rural | Planned |  | 20 | 480 | 0.031583 | 6.5797e-05 | No
2019-08-06 | 8:30 | ULB2 | Short rural | Planned |  | 129 | 180 | 0.076391 | 0.00042439 | No
2019-08-06 | 8:00 | HBB2 | Short rural | Planned |  | 20 | 250 | 0.016449 | 6.5797e-05 | No
2019-08-06 | 8:30 | KVB2 | Short rural | Planned |  | 11 | 196 | 0.0070929 | 3.6188e-05 | No
2019-08-06 | 8:00 | BDA2 | Short rural | Planned |  | 88 | 395 | 0.11436 | 0.00028951 | No
2019-08-06 | 8:00 | 8799 | Short rural | Planned |  | 37 | 365 | 0.04443 | 0.00012172 | No
2019-08-07 | 8:00 | SWD2 | Urban | Planned |  | 1 | 282 | 0.0003763 | 1.3344e-06 | No
2019-08-07 | 8:00 | X217 | Short rural | Planned |  | 5 | 445 | 0.0073199 | 1.6449e-05 | No
2019-08-07 | 8:00 | MR2224 | Short rural | Planned |  | 3 | 420 | 0.0041452 | 9.8696e-06 | No
2019-08-07 | 9:30 | SL1112 | Short rural | Planned |  | 29 | 335 | 0.031961 | 9.5406e-05 | No
2019-08-07 | 8:00 | OA1207 | Short rural | Planned |  | 13 | 410 | 0.017535 | 4.2768e-05 | No
2019-08-07 | 8:00 | APE2 | Short rural | Planned |  | 2 | 330 | 0.0021713 | 6.5797e-06 | No
2019-08-07 | 8:00 | LL1222 | Urban | Planned |  | 72 | 390 | 0.03747 | 9.6077e-05 | No
2019-08-07 | 10:00 | T841 | Short rural | Planned |  | 1 | 170 | 0.00055928 | 3.2899e-06 | No
2019-08-07 | 8:00 | CX1284 | Short rural | Planned |  | 9 | 435 | 0.01288 | 2.9609e-05 | No
2019-08-07 | 8:00 | L941 | Short rural | Planned |  | 27 | 375 | 0.03331 | 8.8826e-05 | No
2019-08-07 | 8:30 | KVA2 | Short rural | Planned |  | 106 | 370 | 0.12903 | 0.00034873 | No
2019-08-07 | 8:30 | APC2 | Short rural | Planned |  | 69 | 375 | 0.085125 | 0.000227 | No
2019-08-07 | 8:00 | UNJ2 | Urban | Planned |  | 173 | 440 | 0.10157 | 0.00023085 | No
2019-08-07 | 8:00 | A098 | Short rural | Planned |  | 30 | 495 | 0.048854 | 9.8696e-05 | No
2019-08-08 | 8:00 | GL1255 | Short rural | Planned |  | 21 | 320 | 0.022108 | 6.9087e-05 | No
2019-08-08 | 8:00 | F601 | Urban | Planned |  | 200 | 480 | 0.1281 | 0.00026688 | No
2019-08-08 | 9:00 | ULL2 | Short rural | Planned |  | 2 | 300 | 0.0019739 | 6.5797e-06 | No
2019-08-08 | 8:30 | APF2 | Short rural | Planned |  | 107 | 180 | 0.063363 | 0.00035202 | No
2019-08-08 | 7:30 | GV1208 | Urban | Planned |  | 101 | 480 | 0.064692 | 0.00013477 | No
2019-08-08 | 8:00 | ULE2 | Short rural | Planned |  | 2 | 110 | 0.00072377 | 6.5797e-06 | No
2019-08-08 | 8:00 | X217 | Short rural | Planned |  | 6 | 295 | 0.0058231 | 1.9739e-05 | No
2019-08-08 | 8:00 | 5498 | Urban | Planned |  | 130 | 510 | 0.088471 | 0.00017347 | No
2019-08-08 | 8:00 | 8802 | Short rural | Planned |  | 27 | 330 | 0.029313 | 8.8826e-05 | No
2019-08-08 | 8:30 | HKC2 | Short rural | Planned |  | 556 | 370 | 0.67679 | 0.0018292 | No
2019-08-08 | 9:00 | SXC2 | Short rural | Planned |  | 73 | 353 | 0.084776 | 0.00024016 | No
2019-08-08 | 8:00 | RW1281 | Short rural | Planned |  | 25 | 370 | 0.030431 | 8.2247e-05 | No
2019-08-08 | 8:00 | BL1210 | Short rural | Planned |  | 306 | 405 | 0.40771 | 0.0010067 | No
2019-08-08 | 8:00 | 9025 | Urban | Planned |  | 103 | 90 | 0.01237 | 0.00013744 | No
2019-08-08 | 8:30 | JBB2 | Short rural | Planned |  | 11 | 295 | 0.010676 | 3.6188e-05 | No
2019-08-08 | 8:00 | A055 | Short rural | Planned |  | 149 | 350 | 0.17157 | 0.00049019 | No
2019-08-09 | 8:30 | KVB2 | Short rural | Planned |  | 1 | 450 | 0.0014804 | 3.2899e-06 | Yes
2019-08-09 | 8:00 | CR1280 | Urban | Planned |  | 37 | 480 | 0.023699 | 4.9373e-05 | Yes
2019-08-09 | 10:00 | NL1332 | Urban | Planned |  | 3 | 35 | 0.00014011 | 4.0032e-06 | Yes
2019-08-09 | 8:30 | JBA2 | Short rural | Planned |  | 90 | 450 | 0.13324 | 0.00029609 | Yes
2019-08-09 | 8:30 | KVB2 | Short rural | Planned |  | 21 | 450 | 0.031089 | 6.9087e-05 | Yes
2019-08-09 | 8:30 | SXC2 | Short rural | Planned |  | 33 | 450 | 0.048854 | 0.00010857 | Yes
2019-08-09 | 6:00 | L541 | Urban | Planned |  | 9 | 570 | 0.0068455 | 1.201e-05 | Yes
2019-08-09 | 9:00 | SXC2 | Short rural | Planned |  | 18 | 420 | 0.024871 | 5.9218e-05 | Yes
2019-08-09 | 8:00 | 35816 | Short rural | Planned |  | 16 | 440 | 0.023161 | 5.2638e-05 | Yes
2019-08-09 | 8:00 | SZ1242 | Short rural | Planned |  | 43 | 220 | 0.031122 | 0.00014146 | Yes
2019-08-09 | 8:30 | KVD2 | Short rural | Planned |  | 1 | 450 | 0.0014804 | 3.2899e-06 | Yes
2019-08-10 | 7:00 | X877 | Short rural | Planned |  | 55 | 600 | 0.10857 | 0.00018094 | No
2019-08-10 | 8:00 | A324 | Urban | Planned |  | 105 | 435 | 0.060949 | 0.00014011 | No
2019-08-11 | 8:00 | APD2 | Short rural | Planned |  | 4 | 880 | 0.01158 | 1.3159e-05 | No
2019-08-11 | 8:00 | MYE2 | Short rural | Planned |  | 118 | 490 | 0.19022 | 0.0003882 | No
2019-08-11 | 7:00 | 1958 | Urban | Planned |  | 19 | 520 | 0.013184 | 2.5354e-05 | No
2019-08-11 | 6:00 | 1953 | Urban | Planned |  | 5 | 380 | 0.0025354 | 6.672e-06 | No
2019-08-12 | 8:00 | HR1236 | Urban | Planned |  | 468 | 280 | 0.17486 | 0.0006245 | No
2019-08-12 | 9:00 | 7120 | Urban | Planned |  | 16 | 420 | 0.0089672 | 2.135e-05 | No
2019-08-12 | 8:00 | BWC2 | Short rural | Planned |  | 27 | 505 | 0.044857 | 8.8826e-05 | No
2019-08-12 | 8:00 | APD2 | Short rural | Planned |  | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2019-08-12 | 8:30 | BDF2 | Short rural | Planned |  | 8 | 305 | 0.0080273 | 2.6319e-05 | No
2019-08-13 | 8:00 | RBB2 | Short rural | Planned |  | 88 | 400 | 0.1158 | 0.00028951 | No
2019-08-13 | 8:30 | BDH2 | Short rural | Planned |  | 7 | 370 | 0.0085207 | 2.3029e-05 | No
2019-08-13 | 8:30 | SXC2 | Short rural | Planned |  | 6 | 450 | 0.0088826 | 1.9739e-05 | No
2019-08-13 | 8:00 | ULH2 | Short rural | Planned |  | 3 | 410 | 0.0040465 | 9.8696e-06 | No
2019-08-13 | 8:30 | ULE2 | Short rural | Planned |  | 1 | 220 | 0.00072377 | 3.2899e-06 | No
2019-08-13 | 8:00 | BL1232 | Short rural | Planned |  | 8 | 480 | 0.012633 | 2.6319e-05 | No
2019-08-13 | 8:00 | WWA2 | Short rural | Planned |  | 107 | 410 | 0.14433 | 0.00035202 | No
2019-08-13 | 8:00 | RV1298 | Urban | Planned |  | 109 | 480 | 0.069816 | 0.00014545 | No
2019-08-13 | 8:00 | S772 | Urban | Planned |  | 67 | 480 | 0.042914 | 8.9405e-05 | No
2019-08-13 | 7:30 | LP1132 | Urban | Planned |  | 98 | 495 | 0.064732 | 0.00013077 | No
2019-08-13 | 8:00 | 25777 | Urban | Planned |  | 5 | 400 | 0.0026688 | 6.672e-06 | No
2019-08-13 | 8:30 | BDB2 | Urban | Planned |  | 38 | 230 | 0.011663 | 5.0707e-05 | No
2019-08-13 | 7:30 | 35982 | Short rural | Planned |  | 1 | 540 | 0.0017765 | 3.2899e-06 | No
2019-08-14 | 8:00 | A098 | Short rural | Planned |  | 43 | 570 | 0.080635 | 0.00014146 | No
2019-08-14 | 9:00 | TM1284 | Short rural | Planned |  | 2 | 270 | 0.0017765 | 6.5797e-06 | No
2019-08-14 | 7:30 | AZ1205 | Urban | Planned |  | 15 | 510 | 0.010208 | 2.0016e-05 | No
2019-08-14 | 8:30 | APH2 | Urban | Planned |  | 65 | 420 | 0.036429 | 8.6736e-05 | No
2019-08-14 | 8:30 | CLD2 | Short rural | Planned |  | 100 | 390 | 0.1283 | 0.00032899 | No
2019-08-14 | 8:00 | CR1228 | Urban | Planned |  | 124 | 795 | 0.13155 | 0.00016547 | No
2019-08-14 | 8:00 | WD1225 | Short rural | Planned |  | 43 | 420 | 0.059415 | 0.00014146 | No
2019-08-14 | 8:00 | X482 | Short rural | Planned |  | 39 | 450 | 0.057737 | 0.0001283 | No
2019-08-14 | 8:00 | RW1218 | Short rural | Planned |  | 72 | 380 | 0.090011 | 0.00023687 | No
2019-08-14 | 8:00 | CX1210 | Short rural | Planned |  | 12 | 385 | 0.015199 | 3.9478e-05 | No
2019-08-14 | 8:30 | 2813 | Urban | Planned |  | 41 | 300 | 0.016413 | 5.471e-05 | No
2019-08-14 | 8:00 | CLB2 | Short rural | Planned |  | 128 | 425 | 0.17897 | 0.0004211 | No
2019-08-14 | 8:00 | A098 | Short rural | Planned |  | 7 | 540 | 0.012436 | 2.3029e-05 | No
2019-08-14 | 8:00 | 87221 | Short rural | Planned |  | 27 | 480 | 0.042637 | 8.8826e-05 | No
2019-08-15 | 8:00 | OP1262 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2019-08-15 | 8:00 | RV1246 | Short rural | Planned |  | 261 | 420 | 0.36063 | 0.00085865 | No
2019-08-15 | 8:30 | BDA2 | Short rural | Planned |  | 37 | 378 | 0.046012 | 0.00012172 | No
2019-08-15 | 8:00 | L582 | Short rural | Planned |  | 10 | 365 | 0.012008 | 3.2899e-05 | No
2019-08-15 | 8:30 | WRD2 | Urban | Planned |  | 118 | 410 | 0.064558 | 0.00015746 | No
2019-08-15 | 7:30 | R260 | Short rural | Planned |  | 4 | 420 | 0.005527 | 1.3159e-05 | No
2019-08-15 | 7:00 | W112 | Short rural | Planned |  | 4 | 460 | 0.0060533 | 1.3159e-05 | No
2019-08-15 | 7:30 | J493 | Urban | Planned |  | 80 | 540 | 0.057646 | 0.00010675 | No
2019-08-15 | 8:00 | SN1271 | Short rural | Planned |  | 21 | 510 | 0.035234 | 6.9087e-05 | No
2019-08-15 | 8:30 | SXC2 | Short rural | Planned |  | 4 | 308 | 0.0040531 | 1.3159e-05 | No
2019-08-15 | 8:00 | RV1220 | Urban | Planned |  | 11 | 320 | 0.0046971 | 1.4678e-05 | No
2019-08-15 | 6:30 | J499 | Urban | Planned |  | 1 | 365 | 0.00048706 | 1.3344e-06 | No
2019-08-15 | 8:30 | TM1258 | Short rural | Planned |  | 1 | 71 | 0.00023358 | 3.2899e-06 | No
2019-08-15 | 7:30 | J514 | Urban | Planned |  | 85 | 630 | 0.071457 | 0.00011342 | No
2019-08-15 | 8:00 | RBC2 | Short rural | Planned |  | 18 | 450 | 0.026648 | 5.9218e-05 | No
2019-08-15 | 8:00 | 8798 | Short rural | Planned |  | 52 | 390 | 0.066718 | 0.00017107 | No
2019-08-15 | 7:30 | D813 | Short rural | Planned |  | 1 | 470 | 0.0015462 | 3.2899e-06 | No
2019-08-16 | 9:00 | 41361 | Urban | Planned |  | 76 | 175 | 0.017748 | 0.00010141 | No
2019-08-16 | 8:00 | WWB2 | Short rural | Planned |  | 120 | 400 | 0.15791 | 0.00039478 | No
2019-08-16 | 8:00 | KVB2 | Short rural | Planned |  | 17 | 375 | 0.020973 | 5.5928e-05 | No
2019-08-16 | 8:00 | 87222 | Long rural | Planned |  | 2 | 255 | 1.6242 | 0.0063694 | No
2019-08-16 | 1:00 | BDA2 | Short rural | Planned |  | 1 | 65 | 0.00021384 | 3.2899e-06 | No
2019-08-16 | 8:00 | W163 | Short rural | Planned |  | 2 | 330 | 0.0021713 | 6.5797e-06 | No
2019-08-16 | 7:30 | J514 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2019-08-16 | 8:30 | APG2 | Urban | Planned |  | 10 | 405 | 0.0054043 | 1.3344e-05 | No
2019-08-16 | 8:00 | J495 | Short rural | Planned |  | 99 | 85 | 0.027684 | 0.0003257 | No
2019-08-16 | 8:00 | A046 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2019-08-16 | 8:00 | BDA2 | Short rural | Planned |  | 3 | 100 | 0.00098696 | 9.8696e-06 | No
2019-08-16 | 8:00 | J459 | Short rural | Planned |  | 74 | 250 | 0.060862 | 0.00024345 | No
2019-08-16 | 8:00 | CX1210 | Short rural | Planned |  | 39 | 600 | 0.076983 | 0.0001283 | No
2019-08-16 | 8:00 | R260 | Short rural | Planned |  | 2 | 175 | 0.0011515 | 6.5797e-06 | No
2019-08-16 | 8:00 | S786 | Short rural | Planned |  | 23 | 390 | 0.02951 | 7.5667e-05 | No
2019-08-16 | 8:00 | CX1206 | Short rural | Planned |  | 20 | 225 | 0.014804 | 6.5797e-05 | No
2019-08-16 | 8:00 | BL1232 | Short rural | Planned |  | 2 | 440 | 0.0028951 | 6.5797e-06 | No
2019-08-16 | 8:00 | B217 | Urban | Planned |  | 34 | 420 | 0.019055 | 4.537e-05 | No
2019-08-17 | 7:00 | FF1280 | Urban | Planned |  | 44 | 400 | 0.023485 | 5.8714e-05 | No
2019-08-17 | 7:00 | MG1286 | Short rural | Planned |  | 11 | 510 | 0.018456 | 3.6188e-05 | No
2019-08-17 | 7:00 | 6426 | Urban | Planned |  | 4 | 660 | 0.0035228 | 5.3376e-06 | No
2019-08-18 | 8:00 | NN1240 | Urban | Planned |  | 16 | 510 | 0.010889 | 2.135e-05 | No
2019-08-19 | 8:00 | NN1262 | Urban | Planned |  | 111 | 430 | 0.063691 | 0.00014812 | No
2019-08-19 | 8:00 | CX1232 | Short rural | Planned |  | 4 | 390 | 0.0051322 | 1.3159e-05 | No
2019-08-19 | 7:00 | MM1192 | Short rural | Planned |  | 1 | 60 | 0.00019739 | 3.2899e-06 | No
2019-08-19 | 8:00 | MR2205 | Short rural | Planned |  | 9 | 540 | 0.015989 | 2.9609e-05 | No
2019-08-19 | 8:00 | BWH2 | Short rural | Planned |  | 47 | 480 | 0.074219 | 0.00015462 | No
2019-08-19 | 8:00 | CA1280 | Short rural | Planned |  | 53 | 250 | 0.043591 | 0.00017436 | No
2019-08-19 | 8:00 | MR2292 | Urban | Planned |  | 44 | 600 | 0.035228 | 5.8714e-05 | No
2019-08-19 | 5:00 | B747 | Urban | Planned |  | 42 | 780 | 0.043715 | 5.6045e-05 | No
2019-08-19 | 7:30 | 8769 | Urban | Planned |  | 91 | 500 | 0.060715 | 0.00012143 | No
2019-08-19 | 8:00 | 41533 | Short rural | Planned |  | 29 | 145 | 0.013834 | 9.5406e-05 | No
2019-08-19 | 12:00 | RW1218 | Short rural | Planned |  | 1 | 42 | 0.00013817 | 3.2899e-06 | No
2019-08-19 | 8:00 | SHK2 | Urban | Planned |  | 60 | 560 | 0.044836 | 8.0064e-05 | No
2019-08-19 | 8:00 | L941 | Short rural | Planned |  | 10 | 100 | 0.0032899 | 3.2899e-05 | No
2019-08-19 | 8:30 | CLA2 | Short rural | Planned |  | 12 | 265 | 0.010462 | 3.9478e-05 | No
2019-08-19 | 9:30 | SHK2 | Urban | Planned |  | 13 | 330 | 0.0057246 | 1.7347e-05 | No
2019-08-20 | 1:00 | BWH2 | Short rural | Planned |  | 1 | 50 | 0.00016449 | 3.2899e-06 | No
2019-08-20 | 8:30 | SXD2 | Short rural | Planned |  | 84 | 385 | 0.10639 | 0.00027635 | No
2019-08-20 | 8:00 | APC2 | Short rural | Planned |  | 1 | 262 | 0.00086194 | 3.2899e-06 | No
2019-08-20 | 8:00 | SZ1242 | Short rural | Planned |  | 45 | 400 | 0.059218 | 0.00014804 | No
2019-08-20 | 8:00 | SZ1332 | Short rural | Planned |  | 64 | 385 | 0.081062 | 0.00021055 | No
2019-08-20 | 8:30 | DP1210 | Short rural | Planned |  | 76 | 350 | 0.08751 | 0.00025003 | No
2019-08-20 | 8:30 | BYC2 | Short rural | Planned |  | 82 | 381 | 0.10278 | 0.00026977 | No
2019-08-20 | 8:00 | BL1243 | Short rural | Planned |  | 188 | 420 | 0.25977 | 0.00061849 | No
2019-08-20 | 8:30 | BYB2 | Short rural | Planned |  | 15 | 404 | 0.019937 | 4.9348e-05 | No
2019-08-20 | 8:30 | SXB2 | Short rural | Planned |  | 265 | 375 | 0.32693 | 0.00087181 | No
2019-08-20 | 10:00 | BWH2 | Short rural | Planned |  | 1 | 55 | 0.00018094 | 3.2899e-06 | No
2019-08-20 | 8:00 | BWH2 | Short rural | Planned |  | 2 | 290 | 0.0019081 | 6.5797e-06 | No
2019-08-20 | 9:30 | APC2 | Short rural | Planned |  | 47 | 380 | 0.058757 | 0.00015462 | No
2019-08-20 | 8:00 | HBB2 | Short rural | Planned |  | 7 | 380 | 0.008751 | 2.3029e-05 | No
2019-08-20 | 8:00 | L584 | Short rural | Planned |  | 18 | 480 | 0.028424 | 5.9218e-05 | No
2019-08-20 | 8:00 | SG1220 | Urban | Planned |  | 74 | 450 | 0.044435 | 9.8746e-05 | No
2019-08-20 | 8:00 | 35980 | Short rural | Planned |  | 4 | 370 | 0.004869 | 1.3159e-05 | No
2019-08-20 | 8:00 | NN1207 | Short rural | Planned |  | 54 | 510 | 0.090603 | 0.00017765 | No
2019-08-20 | 8:00 | 49337 | Urban | Planned |  | 5 | 540 | 0.0036029 | 6.672e-06 | No
2019-08-21 | 8:30 | YYA2 | Short rural | Planned |  | 100 | 405 | 0.13324 | 0.00032899 | No
2019-08-21 | 8:00 | WWA2 | Short rural | Planned |  | 58 | 275 | 0.052473 | 0.00019081 | No
2019-08-21 | 8:00 | L543 | Urban | Planned |  | 73 | 250 | 0.024353 | 9.7411e-05 | No
2019-08-21 | 8:00 | RBD2 | Short rural | Planned |  | 22 | 320 | 0.023161 | 7.2377e-05 | No
2019-08-21 | 8:00 | WWC2 | Short rural | Planned |  | 155 | 480 | 0.24477 | 0.00050993 | No
2019-08-21 | 8:00 | CLC2 | Short rural | Planned |  | 79 | 240 | 0.062376 | 0.0002599 | No
2019-08-21 | 8:00 | T831 | Short rural | Planned |  | 15 | 500 | 0.024674 | 4.9348e-05 | No
2019-08-21 | 8:00 | X213 | Short rural | Planned |  | 12 | 390 | 0.015397 | 3.9478e-05 | No
2019-08-22 | 9:00 | ULJ2 | Urban | Planned |  | 138 | 235 | 0.043275 | 0.00018415 | No
2019-08-22 | 8:00 | 8801 | Short rural | Planned |  | 15 | 450 | 0.022207 | 4.9348e-05 | No
2019-08-22 | 8:00 | 9034 | Urban | Planned |  | 210 | 420 | 0.11769 | 0.00028022 | No
2019-08-22 | 7:30 | CV1251 | Urban | Planned |  | 114 | 430 | 0.065412 | 0.00015212 | No
2019-08-22 | 8:00 | RW1281 | Short rural | Planned |  | 1 | 60 | 0.00019739 | 3.2899e-06 | No
2019-08-22 | 8:00 | 87220 | Short rural | Planned |  | 23 | 380 | 0.028753 | 7.5667e-05 | No
2019-08-22 | 8:00 | RV1206 | Short rural | Planned |  | 20 | 410 | 0.026977 | 6.5797e-05 | No
2019-08-22 | 11:30 | RW1218 | Short rural | Planned |  | 1 | 0 | 0 | 3.2899e-06 | No
2019-08-22 | 8:00 | RW1281 | Short rural | Planned |  | 8 | 510 | 0.013423 | 2.6319e-05 | No
2019-08-22 | 8:00 | 8801 | Short rural | Planned |  | 64 | 390 | 0.082115 | 0.00021055 | No
2019-08-23 | 8:30 | KVB2 | Short rural | Planned |  | 3 | 135 | 0.0013324 | 9.8696e-06 | No
2019-08-23 | 8:00 | RW1218 | Short rural | Planned |  | 2 | 55 | 0.00036188 | 6.5797e-06 | No
2019-08-23 | 8:00 | BL1210 | Short rural | Planned |  | 162 | 300 | 0.15989 | 0.00053296 | No
2019-08-23 | 8:30 | YYA2 | Short rural | Planned |  | 161 | 450 | 0.23835 | 0.00052967 | No
2019-08-23 | 8:30 | JBA2 | Short rural | Planned |  | 90 | 381 | 0.11281 | 0.00029609 | No
2019-08-23 | 9:00 | B201 | Urban | Planned |  | 15 | 300 | 0.0060048 | 2.0016e-05 | No
2019-08-23 | 8:30 | SN1230 | Short rural | Planned |  | 35 | 385 | 0.044331 | 0.00011515 | No
2019-08-23 | 1:00 | MVF2 | Short rural | Planned |  | 1 | 55 | 0.00018094 | 3.2899e-06 | No
2019-08-23 | 8:00 | S737 | Short rural | Planned |  | 14 | 345 | 0.01589 | 4.6058e-05 | No
2019-08-23 | 9:00 | KVB2 | Short rural | Planned |  | 5 | 330 | 0.0054283 | 1.6449e-05 | No
2019-08-23 | 8:30 | KVA2 | Short rural | Planned |  | 1 | 320 | 0.0010528 | 3.2899e-06 | No
2019-08-23 | 8:30 | SN1219 | Short rural | Planned |  | 7 | 160 | 0.0036846 | 2.3029e-05 | No
2019-08-23 | 10:30 | KVB2 | Short rural | Planned |  | 4 | 330 | 0.0043426 | 1.3159e-05 | No
2019-08-23 | 1:00 | RW1292 | Short rural | Planned |  | 3 | 25 | 0.00024674 | 9.8696e-06 | No
2019-08-23 | 8:00 | RW1292 | Short rural | Planned |  | 1 | 135 | 0.00044413 | 3.2899e-06 | No
2019-08-23 | 8:00 | CX1210 | Short rural | Planned |  | 24 | 381 | 0.030083 | 7.8957e-05 | No
2019-08-23 | 8:00 | 87220 | Short rural | Planned |  | 31 | 107 | 0.010912 | 0.00010199 | No
2019-08-23 | 8:30 | YYA2 | Short rural | Planned |  | 160 | 450 | 0.23687 | 0.00052638 | No
2019-08-23 | 8:00 | SC1208 | Short rural | Planned |  | 24 | 470 | 0.03711 | 7.8957e-05 | No
2019-08-23 | 8:00 | OP1262 | Short rural | Planned |  | 3 | 480 | 0.0047374 | 9.8696e-06 | No
2019-08-24 | 9:00 | NN1277 | Urban | Planned |  | 88 | 50 | 0.0058714 | 0.00011743 | No
2019-08-24 | 6:00 | SJ1142 | Urban | Planned |  | 1 | 110 | 0.00014678 | 1.3344e-06 | No
2019-08-24 | 8:00 | SC1271 | Urban | Planned |  | 16 | 435 | 0.0092874 | 2.135e-05 | No
2019-08-24 | 8:00 | NN1233 | Short rural | Planned |  | 6 | 60 | 0.0011844 | 1.9739e-05 | No
2019-08-25 | 8:00 | NWF2 | Urban | Planned |  | 38 | 240 | 0.01217 | 5.0707e-05 | No
2019-08-25 | 6:30 | WX1206 | Urban | Planned |  | 34 | 475 | 0.021551 | 4.537e-05 | No
2019-08-25 | 9:00 | SWJ2 | Urban | Planned |  | 134 | 400 | 0.071524 | 0.00017881 | No
2019-08-25 | 10:00 | W127 | Short rural | Planned |  | 58 | 175 | 0.033392 | 0.00019081 | No
2019-08-25 | 7:00 | 35771 | Urban | Planned |  | 1 | 370 | 0.00049373 | 1.3344e-06 | No
2019-08-26 | 8:00 | 87220 | Short rural | Planned |  | 1 | 105 | 0.00034544 | 3.2899e-06 | No
2019-08-26 | 8:00 | WBB2 | Short rural | Planned |  | 28 | 235 | 0.021647 | 9.2116e-05 | No
2019-08-26 | 8:00 | 1950 | Urban | Planned |  | 52 | 495 | 0.034347 | 6.9389e-05 | No
2019-08-26 | 8:00 | L582 | Short rural | Planned |  | 22 | 318 | 0.023016 | 7.2377e-05 | No
2019-08-26 | 8:00 | J491 | Urban | Planned |  | 143 | 240 | 0.045797 | 0.00019082 | No
2019-08-27 | 8:00 | 25783 | Urban | Planned |  | 13 | 540 | 0.0093675 | 1.7347e-05 | No
2019-08-27 | 8:00 | J495 | Short rural | Planned |  | 80 | 395 | 0.10396 | 0.00026319 | No
2019-08-27 | 8:00 | WD1225 | Short rural | Planned |  | 17 | 420 | 0.02349 | 5.5928e-05 | No
2019-08-27 | 8:00 | YYB2 | Short rural | Planned |  | 118 | 220 | 0.085405 | 0.0003882 | No
2019-08-27 | 9:00 | SXC2 | Short rural | Planned |  | 18 | 210 | 0.012436 | 5.9218e-05 | No
2019-08-27 | 8:00 | JS1252 | Short rural | Planned |  | 10 | 360 | 0.011844 | 3.2899e-05 | No
2019-08-27 | 10:00 | NA1270 | Short rural | Planned |  | 1 | 280 | 0.00092116 | 3.2899e-06 | No
2019-08-27 | 9:00 | NA1270 | Short rural | Planned |  | 30 | 230 | 0.0227 | 9.8696e-05 | No
2019-08-27 | 9:00 | SHE2 | Urban | Planned |  | 163 | 120 | 0.026101 | 0.00021751 | No
2019-08-27 | 7:00 | 35590 | Short rural | Planned |  | 6 | 600 | 0.011844 | 1.9739e-05 | No
2019-08-27 | 8:00 | T899 | Urban | Planned |  | 2 | 540 | 0.0014412 | 2.6688e-06 | No
2019-08-27 | 8:00 | 48185 | Short rural | Planned |  | 76 | 660 | 0.16502 | 0.00025003 | No
2019-08-27 | 11:00 | HBA2 | Short rural | Planned |  | 59 | 200 | 0.03882 | 0.0001941 | No
2019-08-27 | 8:00 | 87222 | Long rural | Planned |  | 1 | 320 | 1.0191 | 0.0031847 | No
2019-08-27 | 7:00 | 35590 | Short rural | Planned |  | 6 | 600 | 0.011844 | 1.9739e-05 | No
2019-08-27 | 8:30 | GG1295 | Short rural | Planned |  | 88 | 395 | 0.11436 | 0.00028951 | No
2019-08-27 | 8:00 | FT1202 | Urban | Planned |  | 155 | 245 | 0.050674 | 0.00020683 | No
2019-08-27 | 8:00 | HBA2 | Short rural | Planned |  | 15 | 435 | 0.021466 | 4.9348e-05 | No
2019-08-27 | 8:00 | BL1232 | Short rural | Planned |  | 84 | 325 | 0.089813 | 0.00027635 | No
2019-08-27 | 8:00 | RW1292 | Short rural | Planned |  | 1 | 245 | 0.00080602 | 3.2899e-06 | No
2019-08-27 | 8:00 | 35990 | Short rural | Planned |  | 155 | 330 | 0.16828 | 0.00050993 | No
2019-08-27 | 8:00 | ER1262 | Short rural | Planned |  | 4 | 205 | 0.0026977 | 1.3159e-05 | No
2019-08-28 | 8:00 | R293 | Short rural | Planned |  | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2019-08-28 | 8:30 | APB2 | Short rural | Planned |  | 407 | 420 | 0.56237 | 0.001339 | No
2019-08-28 | 8:00 | 25744 | Short rural | Planned |  | 31 | 510 | 0.052013 | 0.00010199 | No
2019-08-28 | 8:00 | OA1233 | Short rural | Planned |  | 56 | 270 | 0.049743 | 0.00018423 | No
2019-08-28 | 8:00 | 55866 | Urban | Planned |  | 64 | 385 | 0.03288 | 8.5402e-05 | No
2019-08-28 | 10:00 | A341 | Urban | Planned |  | 1 | 51 | 6.8054e-05 | 1.3344e-06 | No
2019-08-28 | 8:00 | RBD2 | Short rural | Planned |  | 23 | 415 | 0.031402 | 7.5667e-05 | No
2019-08-28 | 8:00 | J495 | Short rural | Planned |  | 75 | 460 | 0.1135 | 0.00024674 | No
2019-08-28 | 8:30 | KVB2 | Short rural | Planned |  | 1 | 450 | 0.0014804 | 3.2899e-06 | No
2019-08-28 | 8:00 | L582 | Short rural | Planned |  | 8 | 368 | 0.0096854 | 2.6319e-05 | No
2019-08-28 | 8:30 | KVD2 | Short rural | Planned |  | 1 | 375 | 0.0012337 | 3.2899e-06 | No
2019-08-28 | 8:30 | SXC2 | Short rural | Planned |  | 33 | 450 | 0.048854 | 0.00010857 | No
2019-08-28 | 8:30 | ULE2 | Short rural | Planned |  | 35 | 270 | 0.031089 | 0.00011515 | No
2019-08-28 | 8:30 | BYG2 | Short rural | Planned |  | 11 | 240 | 0.0086852 | 3.6188e-05 | No
2019-08-28 | 8:30 | BYG2 | Short rural | Planned |  | 6 | 450 | 0.0088826 | 1.9739e-05 | No
2019-08-28 | 8:00 | C900 | Urban | Planned |  | 235 | 450 | 0.14111 | 0.00031358 | No
2019-08-29 | 8:00 | RV1220 | Urban | Planned |  | 226 | 380 | 0.1146 | 0.00030157 | No
2019-08-29 | 8:00 | BWH2 | Short rural | Planned |  | 2 | 105 | 0.00069087 | 6.5797e-06 | No
2019-08-29 | 8:00 | T874 | Short rural | Planned |  | 4 | 450 | 0.0059218 | 1.3159e-05 | No
2019-08-29 | 8:00 | 35824 | Short rural | Planned |  | 23 | 380 | 0.028753 | 7.5667e-05 | No
2019-08-29 | 9:00 | BYE2 | Short rural | Planned |  | 22 | 255 | 0.018456 | 7.2377e-05 | No
2019-08-29 | 7:00 | 8738 | Urban | Planned |  | 23 | 630 | 0.019335 | 3.0691e-05 | No
2019-08-29 | 8:30 | SHE2 | Urban | Planned |  | 162 | 330 | 0.071337 | 0.00021617 | No
2019-08-29 | 8:00 | SWC2 | Urban | Planned |  | 52 | 215 | 0.014919 | 6.9389e-05 | No
2019-08-29 | 10:00 | BWH2 | Short rural | Planned |  | 1 | 30 | 9.8696e-05 | 3.2899e-06 | No
2019-08-29 | 12:30 | RW1281 | Short rural | Planned |  | 1 | -30 | -9.8696e-05 | 3.2899e-06 | No
2019-08-29 | 8:00 | L584 | Short rural | Planned |  | 30 | 395 | 0.038985 | 9.8696e-05 | No
2019-08-29 | 8:00 | RW1281 | Short rural | Planned |  | 2 | 150 | 0.00098696 | 6.5797e-06 | No
2019-08-29 | 8:00 | KC1236 | Short rural | Planned |  | 2 | 490 | 0.0032241 | 6.5797e-06 | No
2019-08-29 | 8:00 | T893 | Urban | Planned |  | 10 | 285 | 0.003803 | 1.3344e-05 | No
2019-08-29 | 8:00 | CX1284 | Short rural | Planned |  | 30 | 480 | 0.047374 | 9.8696e-05 | No
2019-08-29 | 8:00 | 25783 | Urban | Planned |  | 2 | 300 | 0.00080064 | 2.6688e-06 | No
2019-08-29 | 8:30 | CLB2 | Short rural | Planned |  | 98 | 450 | 0.14508 | 0.00032241 | No
2019-08-29 | 8:00 | X877 | Short rural | Planned |  | 17 | 530 | 0.029642 | 5.5928e-05 | No
2019-08-29 | 8:30 | APG2 | Urban | Planned |  | 10 | 315 | 0.0042034 | 1.3344e-05 | No
2019-08-29 | 9:00 | MR2224 | Short rural | Planned |  | 37 | 180 | 0.02191 | 0.00012172 | No
2019-08-29 | 7:30 | AB1265 | Urban | Planned |  | 71 | 270 | 0.02558 | 9.4742e-05 | No
2019-08-30 | 8:30 | CLB2 | Short rural | Planned |  | 98 | 450 | 0.14508 | 0.00032241 | No
2019-08-30 | 7:00 | SC1241 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2019-08-30 | 8:30 | WRB2 | Urban | Planned |  | 256 | 390 | 0.13323 | 0.00034161 | No
2019-08-30 | 8:00 | SC1241 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2019-08-30 | 8:00 | 87220 | Short rural | Planned |  | 43 | 245 | 0.034659 | 0.00014146 | No
2019-08-30 | 8:00 | 35988 | Short rural | Planned |  | 175 | 360 | 0.20726 | 0.00057573 | No
2019-08-30 | 9:00 | 27029 | Short rural | Planned |  | 5 | 180 | 0.0029609 | 1.6449e-05 | No
2019-08-30 | 8:00 | FT1202 | Urban | Planned |  | 2 | 189 | 0.0005044 | 2.6688e-06 | No
2019-08-30 | 8:00 | 2816 | Urban | Planned |  | 42 | 240 | 0.013451 | 5.6045e-05 | No
2019-08-30 | 8:00 | JBA2 | Short rural | Planned |  | 28 | 265 | 0.024411 | 9.2116e-05 | No
2019-08-30 | 8:30 | SXC2 | Short rural | Planned |  | 35 | 175 | 0.02015 | 0.00011515 | No
2019-08-30 | 8:00 | 35982 | Short rural | Planned |  | 22 | 310 | 0.022437 | 7.2377e-05 | No
2019-08-30 | 8:00 | 35825 | Short rural | Planned |  | 58 | 270 | 0.051519 | 0.00019081 | No
2019-08-30 | 8:00 | S336 | Urban | Planned |  | 3 | 360 | 0.0014412 | 4.0032e-06 | No
2019-08-31 | 9:00 | B207 | Urban | Planned |  | 8 | 435 | 0.0046437 | 1.0675e-05 | No
2019-08-31 | 8:00 | KMD2 | Short rural | Planned |  | 19 | 160 | 0.010001 | 6.2507e-05 | No
2019-08-31 | 6:00 | 54701 | Short rural | Planned |  | 1 | 750 | 0.0024674 | 3.2899e-06 | No
2019-09-02 | 8:00 | 87220 | Short rural | Planned |  | 5 | 210 | 0.0034544 | 1.6449e-05 | No
2019-09-02 | 10:00 | 10251 | Urban | Planned |  | 20 | 120 | 0.0032026 | 2.6688e-05 | No
2019-09-02 | 8:00 | MVC2 | Short rural | Planned |  | 21 | 115 | 0.007945 | 6.9087e-05 | No
2019-09-02 | 9:00 | KC1236 | Short rural | Planned |  | 3 | 435 | 0.0042933 | 9.8696e-06 | No
2019-09-02 | 8:00 | MVB2 | Short rural | Planned |  | 76 | 330 | 0.08251 | 0.00025003 | No
2019-09-02 | 9:00 | SXD2 | Short rural | Planned |  | 158 | 310 | 0.16114 | 0.0005198 | No
2019-09-02 | 8:00 | 27029 | Short rural | Planned |  | 6 | 360 | 0.0071061 | 1.9739e-05 | No
2019-09-02 | 8:00 | SHK2 | Urban | Planned |  | 4 | 480 | 0.002562 | 5.3376e-06 | No
2019-09-03 | 12:30 | RBB2 | Short rural | Planned |  | 3 | 30 | 0.00029609 | 9.8696e-06 | No
2019-09-03 | 8:00 | L941 | Short rural | Planned |  | 9 | 235 | 0.0069581 | 2.9609e-05 | No
2019-09-03 | 8:30 | DP1210 | Short rural | Planned |  | 265 | 385 | 0.33565 | 0.00087181 | No
2019-09-03 | 8:30 | APH2 | Urban | Planned |  | 129 | 350 | 0.060248 | 0.00017214 | No
2019-09-03 | 8:00 | MVC2 | Short rural | Planned |  | 4 | 450 | 0.0059218 | 1.3159e-05 | No
2019-09-03 | 8:00 | L591 | Short rural | Planned |  | 31 | 395 | 0.040284 | 0.00010199 | No
2019-09-03 | 8:00 | T883 | Urban | Planned |  | 6 | 360 | 0.0028823 | 8.0064e-06 | No
2019-09-03 | 8:00 | 27038 | Short rural | Planned |  | 83 | 540 | 0.14745 | 0.00027306 | No
2019-09-03 | 12:30 | RW1292 | Short rural | Planned |  | 2 | 80 | 0.00052638 | 6.5797e-06 | No
2019-09-03 | 8:00 | CLB2 | Short rural | Planned |  | 182 | 502 | 0.30058 | 0.00059876 | No
2019-09-03 | 8:00 | WT1215 | Short rural | Planned |  | 17 | 290 | 0.016219 | 5.5928e-05 | No
2019-09-03 | 8:00 | 8735 | Urban | Planned |  | 37 | 480 | 0.023699 | 4.9373e-05 | No
2019-09-03 | 10:00 | L941 | Short rural | Planned |  | 8 | 290 | 0.0076325 | 2.6319e-05 | No
2019-09-03 | 7:30 | L519 | Urban | Planned |  | 74 | 295 | 0.02913 | 9.8746e-05 | No
2019-09-03 | 8:00 | BWF2 | Short rural | Planned |  | 20 | 270 | 0.017765 | 6.5797e-05 | No
2019-09-03 | 10:00 | RBB2 | Short rural | Planned |  | 2 | 90 | 0.00059218 | 6.5797e-06 | No
2019-09-03 | 8:30 | KVC2 | Short rural | Planned |  | 34 | 308 | 0.034451 | 0.00011186 | No
2019-09-03 | 8:00 | S788 | Short rural | Planned |  | 19 | 450 | 0.028128 | 6.2507e-05 | No
2019-09-03 | 8:00 | 9052 | Urban | Planned |  | 44 | 480 | 0.028183 | 5.8714e-05 | No
2019-09-03 | 8:00 | CJ1249 | Urban | Planned |  | 87 | 495 | 0.057466 | 0.00011609 | No
2019-09-03 | 8:30 | ULL2 | Short rural | Planned |  | 8 | 210 | 0.005527 | 2.6319e-05 | No
2019-09-03 | 8:00 | HR1236 | Urban | Planned |  | 69 | 420 | 0.038671 | 9.2074e-05 | No
2019-09-04 | 9:00 | SXC2 | Short rural | Planned |  | 7 | 130 | 0.0029938 | 2.3029e-05 | No
2019-09-04 | 8:00 | 61617 | Short rural | Planned |  | 2 | 345 | 0.00227 | 6.5797e-06 | No
2019-09-04 | 7:30 | A348 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2019-09-04 | 8:00 | CLB2 | Short rural | Planned |  | 74 | 420 | 0.10225 | 0.00024345 | No
2019-09-04 | 8:30 | TM1284 | Short rural | Planned |  | 2 | 247 | 0.0016252 | 6.5797e-06 | No
2019-09-04 | 10:00 | 35988 | Short rural | Planned |  | 2 | 280 | 0.0018423 | 6.5797e-06 | No
2019-09-04 | 7:30 | D840 | Urban | Planned |  | 67 | 470 | 0.04202 | 8.9405e-05 | No
2019-09-04 | 8:00 | 87218 | Short rural | Planned |  | 4 | 311 | 0.0040926 | 1.3159e-05 | No
2019-09-04 | 9:00 | 35980 | Short rural | Planned |  | 2 | 65 | 0.00042768 | 6.5797e-06 | No
2019-09-04 | 8:00 | L584 | Short rural | Planned |  | 16 | 350 | 0.018423 | 5.2638e-05 | No
2019-09-04 | 8:00 | 35980 | Short rural | Planned |  | 11 | 25 | 0.00090471 | 3.6188e-05 | No
2019-09-04 | 8:00 | W188 | Short rural | Planned |  | 22 | 455 | 0.032932 | 7.2377e-05 | No
2019-09-04 | 9:00 | 35988 | Short rural | Planned |  | 8 | 185 | 0.004869 | 2.6319e-05 | No
2019-09-04 | 8:30 | JBB2 | Short rural | Planned |  | 18 | 390 | 0.023095 | 5.9218e-05 | No
2019-09-04 | 8:00 | 35988 | Short rural | Planned |  | 3 | 180 | 0.0017765 | 9.8696e-06 | No
2019-09-04 | 11:00 | W163 | Short rural | Planned |  | 4 | 170 | 0.0022371 | 1.3159e-05 | No
2019-09-04 | 8:00 | BK1288 | Short rural | Planned |  | 66 | 395 | 0.085767 | 0.00021713 | No
2019-09-04 | 8:00 | RBC2 | Short rural | Planned |  | 16 | 465 | 0.024477 | 5.2638e-05 | No
2019-09-04 | 8:00 | L946 | Short rural | Planned |  | 21 | 405 | 0.02798 | 6.9087e-05 | No
2019-09-05 | 11:00 | 35990 | Short rural | Planned |  | 3 | 180 | 0.0017765 | 9.8696e-06 | No
2019-09-05 | 9:00 | OA1244 | Short rural | Planned |  | 1 | 121 | 0.00039807 | 3.2899e-06 | No
2019-09-05 | 10:00 | 35983 | Short rural | Planned |  | 1 | 125 | 0.00041123 | 3.2899e-06 | No
2019-09-05 | 7:30 | 8777 | Urban | Planned |  | 70 | 330 | 0.030825 | 9.3408e-05 | No
2019-09-05 | 8:30 | 25451 | Short rural | Planned |  | 28 | 240 | 0.022108 | 9.2116e-05 | No
2019-09-05 | 8:00 | HBC2 | Short rural | Planned |  | 28 | 360 | 0.033162 | 9.2116e-05 | No
2019-09-05 | 8:00 | J500 | Urban | Planned |  | 75 | 445 | 0.044536 | 0.00010008 | No
2019-09-05 | 8:00 | MVB2 | Short rural | Planned |  | 4 | 70 | 0.00092116 | 1.3159e-05 | No
2019-09-05 | 12:30 | MVB2 | Short rural | Planned |  | 1 | -65 | -0.00021384 | 3.2899e-06 | No
2019-09-05 | 5:00 | DP1221 | Short rural | Planned |  | 8 | 495 | 0.013028 | 2.6319e-05 | No
2019-09-05 | 8:00 | BDC2 | Short rural | Planned |  | 97 | 525 | 0.16754 | 0.00031912 | No
2019-09-05 | 8:00 | RW1281 | Short rural | Planned |  | 1 | 240 | 0.00078957 | 3.2899e-06 | No
2019-09-05 | 8:30 | WRE2 | Urban | Planned |  | 251 | 365 | 0.12225 | 0.00033493 | No
2019-09-05 | 10:00 | MVB2 | Short rural | Planned |  | 1 | 25 | 8.2247e-05 | 3.2899e-06 | No
2019-09-05 | 8:00 | CLB2 | Short rural | Planned |  | 188 | 420 | 0.25977 | 0.00061849 | No
2019-09-05 | 10:00 | MG1267 | Short rural | Planned |  | 5 | 15 | 0.00024674 | 1.6449e-05 | No
2019-09-05 | 8:00 | 87218 | Short rural | Planned |  | 25 | 430 | 0.035366 | 8.2247e-05 | No
2019-09-05 | 8:00 | 27194 | Urban | Planned |  | 17 | 420 | 0.0095276 | 2.2685e-05 | No
2019-09-05 | 9:30 | CD1234 | Short rural | Planned |  | 2 | 150 | 0.00098696 | 6.5797e-06 | No
2019-09-05 | 8:00 | L941 | Short rural | Planned |  | 21 | 385 | 0.026599 | 6.9087e-05 | No
2019-09-05 | 10:00 | 10251 | Urban | Planned |  | 20 | 30 | 0.00080064 | 2.6688e-05 | No
2019-09-06 | 8:00 | WX1206 | Urban | Planned |  | 1 | 230 | 0.00030691 | 1.3344e-06 | Yes
2019-09-06 | 10:00 | CX1206 | Short rural | Planned |  | 7 | 280 | 0.0064481 | 2.3029e-05 | Yes
2019-09-06 | 8:00 | AB1287 | Urban | Planned |  | 44 | 345 | 0.020256 | 5.8714e-05 | Yes
2019-09-06 | 8:00 | CX1210 | Short rural | Planned |  | 10 | 165 | 0.0054283 | 3.2899e-05 | Yes
2019-09-06 | 8:00 | MVH2 | Short rural | Planned |  | 44 | 480 | 0.069482 | 0.00014475 | Yes
2019-09-06 | 8:00 | 8798 | Short rural | Planned |  | 10 | 190 | 0.0062507 | 3.2899e-05 | Yes
2019-09-06 | 8:00 | MG1267 | Short rural | Planned |  | 9 | 120 | 0.0035531 | 2.9609e-05 | Yes
2019-09-06 | 11:00 | 10290 | Short rural | Planned |  | 12 | 95 | 0.0037504 | 3.9478e-05 | Yes
2019-09-06 | 8:00 | BWH2 | Short rural | Planned |  | 11 | 360 | 0.013028 | 3.6188e-05 | Yes
2019-09-06 | 8:00 | GL1233 | Short rural | Planned |  | 31 | 555 | 0.056602 | 0.00010199 | Yes
2019-09-06 | 8:30 | APB2 | Short rural | Planned |  | 205 | 385 | 0.25965 | 0.00067442 | Yes
2019-09-06 | 7:30 | KC1262 | Short rural | Planned |  | 6 | 242 | 0.0047769 | 1.9739e-05 | Yes
2019-09-06 | 8:00 | CR1280 | Urban | Planned |  | 68 | 515 | 0.046731 | 9.0739e-05 | Yes
2019-09-06 | 8:30 | CLD2 | Short rural | Planned |  | 48 | 355 | 0.056059 | 0.00015791 | Yes
2019-09-08 | 8:00 | WWA2 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2019-09-09 | 8:00 | 53807 | Short rural | Planned |  | 39 | 480 | 0.061586 | 0.0001283 | No
2019-09-10 | 11:00 | 7120 | Urban | Planned |  | 2 | 120 | 0.00032026 | 2.6688e-06 | No
2019-09-09 | 8:00 | R260 | Short rural | Planned |  | 1 | 370 | 0.0012172 | 3.2899e-06 | No
2019-09-09 | 8:00 | R290 | Short rural | Planned |  | 29 | 480 | 0.045795 | 9.5406e-05 | No
2019-09-09 | 8:00 | 9034 | Urban | Planned |  | 210 | 420 | 0.11769 | 0.00028022 | No
2019-09-10 | 8:30 | APE2 | Short rural | Planned |  | 12 | 450 | 0.017765 | 3.9478e-05 | No
2019-09-10 | 8:00 | W163 | Short rural | Planned |  | 5 | 480 | 0.0078957 | 1.6449e-05 | No
2019-09-10 | 11:00 | 8799 | Short rural | Planned |  | 15 | 195 | 0.0096229 | 4.9348e-05 | No
2019-09-10 | 8:30 | BYB2 | Short rural | Planned |  | 15 | 450 | 0.022207 | 4.9348e-05 | No
2019-09-10 | 8:00 | CLB2 | Short rural | Planned |  | 203 | 480 | 0.32056 | 0.00066784 | No
2019-09-10 | 8:00 | 8799 | Short rural | Planned |  | 28 | 195 | 0.017963 | 9.2116e-05 | No
2019-09-10 | 10:00 | 8799 | Short rural | Planned |  | 22 | 285 | 0.020627 | 7.2377e-05 | No
2019-09-10 | 8:00 | 87220 | Short rural | Planned |  | 1 | 193 | 0.00063494 | 3.2899e-06 | No
2019-09-10 | 8:00 | CX1232 | Short rural | Planned |  | 9 | 390 | 0.011547 | 2.9609e-05 | No
2019-09-10 | 8:30 | TM1258 | Short rural | Planned |  | 127 | 450 | 0.18802 | 0.00041781 | No
2019-09-10 | 8:00 | 8772 | Urban | Planned |  | 100 | 210 | 0.028022 | 0.00013344 | No
2019-09-10 | 8:30 | BYC2 | Short rural | Planned |  | 83 | 420 | 0.11468 | 0.00027306 | No
2019-09-10 | 8:00 | L519 | Urban | Planned |  | 66 | 450 | 0.039632 | 8.807e-05 | No
2019-09-11 | 8:00 | CLB2 | Short rural | Planned |  | 237 | 480 | 0.37425 | 0.0007797 | No
2019-09-11 | 8:00 | HBA2 | Short rural | Planned |  | 21 | 510 | 0.035234 | 6.9087e-05 | No
2019-09-11 | 8:00 | OP1112 | Short rural | Planned |  | 4 | 510 | 0.0067113 | 1.3159e-05 | No
2019-09-11 | 8:00 | NA1270 | Short rural | Planned |  | 134 | 480 | 0.2116 | 0.00044084 | No
2019-09-11 | 8:00 | L940 | Short rural | Planned |  | 17 | 160 | 0.0089484 | 5.5928e-05 | No
2019-09-11 | 9:30 | L940 | Short rural | Planned |  | 45 | 325 | 0.048114 | 0.00014804 | No
2019-09-11 | 8:00 | WD1225 | Short rural | Planned |  | 50 | 445 | 0.073199 | 0.00016449 | No
2019-09-11 | 12:00 | SZ1242 | Short rural | Planned |  | 6 | 140 | 0.0027635 | 1.9739e-05 | No
2019-09-11 | 8:00 | CLB2 | Short rural | Planned |  | 584 | 429 | 0.82423 | 0.0019213 | No
2019-09-11 | 7:30 | 8762 | Urban | Planned |  | 35 | 345 | 0.016113 | 4.6704e-05 | No
2019-09-11 | 8:00 | BWH2 | Short rural | Planned |  | 18 | 435 | 0.02576 | 5.9218e-05 | No
2019-09-11 | 12:00 | MVF2 | Short rural | Planned |  | 2 | 110 | 0.00072377 | 6.5797e-06 | No
2019-09-11 | 8:00 | 8741 | Urban | Planned |  | 42 | 330 | 0.018495 | 5.6045e-05 | No
2019-09-11 | 8:00 | BK1251 | Short rural | Planned |  | 18 | 387 | 0.022917 | 5.9218e-05 | No
2019-09-11 | 8:00 | BWE2 | Short rural | Planned |  | 22 | 410 | 0.029675 | 7.2377e-05 | No
2019-09-11 | 8:00 | 25780 | Urban | Planned |  | 1 | 420 | 0.00056045 | 1.3344e-06 | No
2019-09-11 | 7:00 | OP1112 | Short rural | Planned |  | 1 | 570 | 0.0018752 | 3.2899e-06 | No
2019-09-11 | 8:00 | 87222 | Long rural | Planned |  | 6 | 150 | 2.8662 | 0.019108 | No
2019-09-11 | 8:00 | SZ1242 | Short rural | Planned |  | 45 | 240 | 0.035531 | 0.00014804 | No
2019-09-12 | 8:00 | 35418 | Short rural | Planned |  | 5 | 295 | 0.0048525 | 1.6449e-05 | No
2019-09-12 | 8:00 | 9033 | Urban | Planned |  | 2 | 540 | 0.0014412 | 2.6688e-06 | No
2019-09-12 | 8:00 | 35418 | Short rural | Planned |  | 1 | 170 | 0.00055928 | 3.2899e-06 | No
2019-09-12 | 8:00 | BDC2 | Short rural | Planned |  | 38 | 450 | 0.056257 | 0.00012501 | No
2019-09-12 | 8:00 | CX1206 | Short rural | Planned |  | 19 | 420 | 0.026253 | 6.2507e-05 | No
2019-09-12 | 8:00 | A096 | Short rural | Planned |  | 8 | 600 | 0.015791 | 2.6319e-05 | No
2019-09-12 | 8:00 | MYQ2 | Short rural | Planned |  | 73 | 510 | 0.12248 | 0.00024016 | No
2019-09-12 | 8:00 | RW1292 | Short rural | Planned |  | 13 | 353 | 0.015097 | 4.2768e-05 | No
2019-09-12 | 8:30 | DP1258 | Short rural | Planned |  | 16 | 450 | 0.023687 | 5.2638e-05 | No
2019-09-12 | 1:00 | MVF2 | Short rural | Planned |  | 1 | 30 | 9.8696e-05 | 3.2899e-06 | No
2019-09-12 | 8:00 | 87222 | Long rural | Planned |  | 3 | 340 | 3.2484 | 0.0095541 | No
2019-09-12 | 9:00 | RBD2 | Short rural | Planned |  | 1 | 70 | 0.00023029 | 3.2899e-06 | No
2019-09-12 | 8:00 | CLB2 | Short rural | Planned |  | 237 | 220 | 0.17153 | 0.0007797 | No
2019-09-12 | 8:30 | WRB2 | Urban | Planned |  | 57 | 90 | 0.0068455 | 7.6061e-05 | No
2019-09-12 | 8:00 | HR1236 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2019-09-13 | 7:30 | J516 | Urban | Planned |  | 130 | 440 | 0.076328 | 0.00017347 | No
2019-09-13 | 8:00 | L582 | Short rural | Planned |  | 10 | 390 | 0.01283 | 3.2899e-05 | No
2019-09-13 | 9:00 | SXC2 | Short rural | Planned |  | 6 | 330 | 0.0065139 | 1.9739e-05 | No
2019-09-13 | 8:00 | R293 | Short rural | Planned |  | 27 | 280 | 0.024871 | 8.8826e-05 | No
2019-09-13 | 8:00 | BK1251 | Short rural | Planned |  | 21 | 200 | 0.013817 | 6.9087e-05 | No
2019-09-13 | 8:00 | M399 | Short rural | Planned |  | 54 | 480 | 0.085273 | 0.00017765 | No
2019-09-13 | 8:30 | DP1206 | Urban | Planned |  | 120 | 102 | 0.016333 | 0.00016013 | No
2019-09-13 | 7:30 | CN1239 | Urban | Planned |  | 24 | 480 | 0.015372 | 3.2026e-05 | No
2019-09-13 | 8:30 | BDG2 | Short rural | Planned |  | 12 | 450 | 0.017765 | 3.9478e-05 | No
2019-09-13 | 8:00 | L948 | Short rural | Planned |  | 24 | 165 | 0.013028 | 7.8957e-05 | No
2019-09-13 | 9:00 | SXC2 | Short rural | Planned |  | 1 | 360 | 0.0011844 | 3.2899e-06 | No
2019-09-13 | 10:00 | Unknown (South Wollongong) | Urban | Planned |  | 39 | 120 | 0.006245 | 5.2042e-05 | No
2019-09-13 | 8:00 | 49918 | Urban | Planned |  | 62 | 280 | 0.023165 | 8.2733e-05 | No
2019-09-13 | 8:00 | 49918 | Urban | Planned |  | 86 | 270 | 0.030985 | 0.00011476 | No
2019-09-13 | 8:00 | WD1221 | Short rural | Planned |  | 2 | 265 | 0.0017436 | 6.5797e-06 | No
2019-09-14 | 8:00 | CX1232 | Short rural | Planned |  | 265 | 405 | 0.35308 | 0.00087181 | No
2019-09-14 | 8:30 | KVB2 | Short rural | Planned |  | 6 | 215 | 0.0042439 | 1.9739e-05 | No
2019-09-14 | 7:00 | 2812 | Urban | Planned |  | 2 | 470 | 0.0012543 | 2.6688e-06 | No
2019-09-15 | 8:00 | C889 | Urban | Planned |  | 104 | 360 | 0.04996 | 0.00013878 | No
2019-09-15 | 7:00 | MYB2 | Urban | Planned |  | 3 | 220 | 0.0008807 | 4.0032e-06 | No
2019-09-15 | 7:00 | 35763 | Urban | Planned |  | 25 | 520 | 0.017347 | 3.336e-05 | No
2019-09-15 | 9:00 | RV1298 | Urban | Planned |  | 144 | 525 | 0.10088 | 0.00019215 | No
2019-09-15 | 8:00 | C889 | Urban | Planned |  | 30 | 360 | 0.014412 | 4.0032e-05 | No
2019-09-16 | 5:30 | PH1223 | Urban | Planned |  | 20 | 750 | 0.020016 | 2.6688e-05 | No
2019-09-16 | 8:00 | MVF2 | Short rural | Planned |  | 4 | 235 | 0.0030925 | 1.3159e-05 | No
2019-09-16 | 8:00 | WWC2 | Short rural | Planned |  | 20 | 430 | 0.028293 | 6.5797e-05 | No
2019-09-16 | 8:00 | FT1203 | Urban | Planned |  | 4 | 245 | 0.0013077 | 5.3376e-06 | No
2019-09-16 | 8:00 | AB1265 | Urban | Planned |  | 75 | 475 | 0.047538 | 0.00010008 | No
2019-09-16 | 8:00 | 87220 | Short rural | Planned |  | 2 | 85 | 0.00055928 | 6.5797e-06 | No
2019-09-16 | 8:00 | 55876 | Urban | Planned |  | 1 | 630 | 0.00084067 | 1.3344e-06 | No
2019-09-16 | 8:00 | BDG2 | Short rural | Planned |  | 44 | 480 | 0.069482 | 0.00014475 | No
2019-09-17 | 8:30 | ULL2 | Short rural | Planned |  | 90 | 155 | 0.045894 | 0.00029609 | No
2019-09-17 | 8:00 | L941 | Short rural | Planned |  | 39 | 210 | 0.026944 | 0.0001283 | No
2019-09-17 | 8:00 | PH1260 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2019-09-17 | 8:00 | L941 | Short rural | Planned |  | 41 | 205 | 0.027651 | 0.00013488 | No
2019-09-18 | 9:00 | PCB2 | Short rural | Planned |  | 28 | 420 | 0.038689 | 9.2116e-05 | No
2019-09-18 | 8:00 | T883 | Urban | Planned |  | 1 | 420 | 0.00056045 | 1.3344e-06 | No
2019-09-18 | 8:00 | D813 | Short rural | Planned |  | 6 | 162 | 0.0031977 | 1.9739e-05 | No
2019-09-18 | 8:00 | X217 | Short rural | Planned |  | 3 | 300 | 0.0029609 | 9.8696e-06 | No
2019-09-18 | 8:30 | DP1206 | Urban | Planned |  | 208 | 550 | 0.15266 | 0.00027756 | No
2019-09-18 | 8:00 | CA1276 | Urban | Planned |  | 80 | 85 | 0.0090739 | 0.00010675 | No
2019-09-18 | 8:00 | CLB2 | Short rural | Planned |  | 582 | 412 | 0.78886 | 0.0019147 | No
2019-09-18 | 8:00 | 87220 | Short rural | Planned |  | 8 | 310 | 0.0081589 | 2.6319e-05 | No
2019-09-18 | 8:30 | APE2 | Short rural | Planned |  | 8 | 420 | 0.011054 | 2.6319e-05 | No
2019-09-19 | 8:00 | 57448 | Short rural | Planned |  | 9 | 350 | 0.010363 | 2.9609e-05 | No
2019-09-19 | 9:00 | NA1270 | Short rural | Planned |  | 11 | 335 | 0.012123 | 3.6188e-05 | No
2019-09-19 | 8:00 | RW1281 | Short rural | Planned |  | 49 | 405 | 0.065287 | 0.0001612 | No
2019-09-19 | 8:00 | 76225 | Short rural | Planned |  | 4 | 260 | 0.0034215 | 1.3159e-05 | No
2019-09-19 | 8:00 | RV1246 | Short rural | Planned |  | 192 | 440 | 0.27793 | 0.00063165 | No
2019-09-19 | 8:00 | 27454 | Short rural | Planned |  | 15 | 216 | 0.010659 | 4.9348e-05 | No
2019-09-19 | 11:00 | S786 | Short rural | Planned |  | 13 | 200 | 0.0085536 | 4.2768e-05 | No
2019-09-19 | 8:00 | D810 | Short rural | Planned |  | 23 | 330 | 0.02497 | 7.5667e-05 | No
2019-09-19 | 10:00 | CX1206 | Short rural | Planned |  | 8 | 245 | 0.0064481 | 2.6319e-05 | No
2019-09-19 | 8:00 | 49382 | Urban | Planned |  | 65 | 555 | 0.048138 | 8.6736e-05 | No
2019-09-19 | 11:00 | 8798 | Short rural | Planned |  | 28 | 255 | 0.02349 | 9.2116e-05 | No
2019-09-19 | 8:00 | B217 | Urban | Planned |  | 82 | 540 | 0.059087 | 0.00010942 | No
2019-09-19 | 8:30 | CLA2 | Short rural | Planned |  | 254 | 435 | 0.3635 | 0.00083563 | No
2019-09-19 | 8:00 | ULC2 | Short rural | Planned |  | 29 | 465 | 0.044364 | 9.5406e-05 | No
2019-09-19 | 8:00 | 8798 | Short rural | Planned |  | 4 | 270 | 0.0035531 | 1.3159e-05 | No
2019-09-19 | 8:00 | ULF2 | Short rural | Planned |  | 2 | 465 | 0.0030596 | 6.5797e-06 | No
2019-09-19 | 8:00 | RBA2 | Short rural | Planned |  | 14 | 134 | 0.0061718 | 4.6058e-05 | No
2019-09-19 | 8:00 | RW1218 | Short rural | Planned |  | 7 | 368 | 0.0084747 | 2.3029e-05 | No
2019-09-20 | 8:00 | WWB2 | Short rural | Planned |  | 19 | 365 | 0.022815 | 6.2507e-05 | No
2019-09-20 | 8:00 | T831 | Short rural | Planned |  | 5 | 210 | 0.0034544 | 1.6449e-05 | No
2019-09-20 | 9:30 | CX1210 | Short rural | Planned |  | 25 | 280 | 0.023029 | 8.2247e-05 | No
2019-09-20 | 8:00 | X217 | Short rural | Planned |  | 1 | 164 | 0.00053954 | 3.2899e-06 | No
2019-09-20 | 8:00 | D814 | Short rural | Planned |  | 19 | 375 | 0.02344 | 6.2507e-05 | No
2019-09-20 | 10:00 | X217 | Short rural | Planned |  | 26 | 360 | 0.030793 | 8.5536e-05 | No
2019-09-20 | 8:00 | CX1210 | Short rural | Planned |  | 4 | 370 | 0.004869 | 1.3159e-05 | No
2019-09-20 | 8:30 | SHE2 | Urban | Planned |  | 163 | 456 | 0.099183 | 0.00021751 | No
2019-09-20 | 8:00 | L517 | Urban | Planned |  | 57 | 255 | 0.019395 | 7.6061e-05 | No
2019-09-20 | 8:30 | BDG2 | Short rural | Planned |  | 35 | 450 | 0.051815 | 0.00011515 | No
2019-09-20 | 8:30 | BYB2 | Short rural | Planned |  | 28 | 210 | 0.019344 | 9.2116e-05 | No
2019-09-20 | 8:00 | AB1245 | Urban | Planned |  | 129 | 470 | 0.080905 | 0.00017214 | No
2019-09-21 | 7:00 | 35015 | Urban | Planned |  | 1 | 525 | 0.00070056 | 1.3344e-06 | No
2019-09-21 | 8:30 | 4873 | Urban | Planned |  | 22 | 460 | 0.013504 | 2.9357e-05 | No
2019-09-22 | 8:00 | WD1284 | Short rural | Planned |  | 1 | 345 | 0.001135 | 3.2899e-06 | No
2019-09-22 | 8:00 | SZ1342 | Urban | Planned |  | 2 | 95 | 0.00025354 | 2.6688e-06 | No
2019-09-22 | 8:00 | 27335 | Urban | Planned |  | 93 | 375 | 0.046537 | 0.0001241 | No
2019-09-22 | 8:00 | D813 | Short rural | Planned |  | 23 | 183 | 0.013847 | 7.5667e-05 | No
2019-09-22 | 7:00 | AB1287 | Urban | Planned |  | 1 | 270 | 0.00036029 | 1.3344e-06 | No
2019-09-22 | 8:00 | CT1233 | Urban | Planned |  | 10 | 450 | 0.0060048 | 1.3344e-05 | No
2019-09-22 | 11:00 | SZ1322 | Short rural | Planned |  | 8 | 140 | 0.0036846 | 2.6319e-05 | No
2019-09-22 | 8:30 | CR1228 | Urban | Planned |  | 64 | 510 | 0.043555 | 8.5402e-05 | No
2019-09-22 | 8:00 | MG1286 | Short rural | Planned |  | 79 | 480 | 0.12475 | 0.0002599 | No
2019-09-23 | 8:00 | WT1252 | Short rural | Planned |  | 130 | 315 | 0.13472 | 0.00042768 | No
2019-09-23 | 8:00 | T828 | Short rural | Planned |  | 12 | 350 | 0.013817 | 3.9478e-05 | No
2019-09-23 | 8:30 | HBD2 | Urban | Planned |  | 3 | 390 | 0.0015612 | 4.0032e-06 | No
2019-09-23 | 8:30 | JS1222 | Short rural | Planned |  | 1 | 390 | 0.001283 | 3.2899e-06 | No
2019-09-23 | 8:00 | D841 | Urban | Planned |  | 50 | 390 | 0.026021 | 6.672e-05 | No
2019-09-23 | 8:00 | B719 | Short rural | Planned |  | 26 | 460 | 0.039347 | 8.5536e-05 | No
2019-09-23 | 8:00 | L584 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2019-09-23 | 8:00 | T836 | Short rural | Planned |  | 2 | 285 | 0.0018752 | 6.5797e-06 | No
2019-09-24 | 8:00 | 55875 | Urban | Planned |  | 157 | 420 | 0.08799 | 0.0002095 | No
2019-09-24 | 8:00 | WWB2 | Short rural | Planned |  | 233 | 450 | 0.34494 | 0.00076654 | No
2019-09-24 | 8:00 | L588 | Short rural | Planned |  | 43 | 360 | 0.050927 | 0.00014146 | No
2019-09-24 | 8:30 | KVA2 | Short rural | Planned |  | 72 | 202 | 0.047848 | 0.00023687 | No
2019-09-24 | 8:00 | W196 | Urban | Planned |  | 31 | 360 | 0.014892 | 4.1366e-05 | No
2019-09-24 | 12:30 | KC1288 | Short rural | Planned |  | 3 | 110 | 0.0010857 | 9.8696e-06 | No
2019-09-24 | 8:30 | MM1192 | Short rural | Planned |  | 10 | 305 | 0.010034 | 3.2899e-05 | No
2019-09-24 | 8:00 | 25783 | Urban | Planned |  | 9 | 540 | 0.0064852 | 1.201e-05 | No
2019-09-24 | 8:30 | A098 | Short rural | Planned |  | 20 | 120 | 0.0078957 | 6.5797e-05 | No
2019-09-24 | 8:00 | X881 | Short rural | Planned |  | 39 | 445 | 0.057096 | 0.0001283 | No
2019-09-24 | 9:00 | 49395 | Urban | Planned |  | 29 | 460 | 0.017801 | 3.8698e-05 | No
2019-09-24 | 8:00 | RV1280 | Urban | Planned |  | 136 | 470 | 0.085295 | 0.00018148 | No
2019-09-24 | 11:00 | 8801 | Short rural | Planned |  | 5 | 160 | 0.0026319 | 1.6449e-05 | No
2019-09-24 | 8:00 | 35827 | Short rural | Planned |  | 15 | 240 | 0.011844 | 4.9348e-05 | No
2019-09-24 | 8:30 | KC1288 | Short rural | Planned |  | 16 | 98 | 0.0051585 | 5.2638e-05 | No
2019-09-24 | 8:00 | BDE2 | Urban | Planned |  | 1 | 151 | 0.00020149 | 1.3344e-06 | No
2019-09-24 | 8:00 | 8802 | Short rural | Planned |  | 59 | 215 | 0.041732 | 0.0001941 | No
2019-09-24 | 8:00 | CLB2 | Short rural | Planned |  | 582 | 390 | 0.74673 | 0.0019147 | No
2019-09-24 | 8:00 | 27454 | Short rural | Planned |  | 35 | 285 | 0.032816 | 0.00011515 | No
2019-09-25 | 8:30 | BX1222 | Urban | Planned |  | 41 | 160 | 0.0087537 | 5.471e-05 | No
2019-09-25 | 7:30 | J514 | Urban | Planned |  | 67 | 480 | 0.042914 | 8.9405e-05 | No
2019-09-25 | 8:00 | 8801 | Short rural | Planned |  | 9 | 345 | 0.010215 | 2.9609e-05 | No
2019-09-25 | 8:00 | CX1273 | Short rural | Planned |  | 20 | 200 | 0.013159 | 6.5797e-05 | No
2019-09-25 | 11:00 | CX1273 | Short rural | Planned |  | 17 | 135 | 0.0075502 | 5.5928e-05 | No
2019-09-25 | 8:30 | NA1225 | Short rural | Planned |  | 4 | 270 | 0.0035531 | 1.3159e-05 | No
2019-09-25 | 8:00 | MYQ2 | Short rural | Planned |  | 22 | 410 | 0.029675 | 7.2377e-05 | No
2019-09-25 | 8:00 | L582 | Short rural | Planned |  | 19 | 361 | 0.022565 | 6.2507e-05 | No
2019-09-25 | 8:00 | UNJ2 | Urban | Planned |  | 182 | 475 | 0.11536 | 0.00024286 | No
2019-09-25 | 8:00 | RW1292 | Short rural | Planned |  | 1 | 234 | 0.00076983 | 3.2899e-06 | No
2019-09-25 | 9:00 | 27189 | Urban | Planned |  | 1 | 445 | 0.00059381 | 1.3344e-06 | No
2019-09-25 | 8:00 | HBA2 | Short rural | Planned |  | 44 | 220 | 0.031846 | 0.00014475 | No
2019-09-25 | 8:30 | A095 | Short rural | Planned |  | 6 | 120 | 0.0023687 | 1.9739e-05 | No
2019-09-25 | 8:00 | H745 | Short rural | Planned |  | 101 | 740 | 0.24588 | 0.00033228 | No
2019-09-25 | 8:00 | NL1172 | Urban | Planned |  | 15 | 530 | 0.010608 | 2.0016e-05 | No
2019-09-25 | 8:30 | CLA2 | Short rural | Planned |  | 9 | 410 | 0.01214 | 2.9609e-05 | No
2019-09-25 | 8:00 | CN1210 | Urban | Planned |  | 70 | 190 | 0.017748 | 9.3408e-05 | No
2019-09-25 | 10:00 | J462 | Urban | Planned |  | 2 | 230 | 0.00061382 | 2.6688e-06 | No
2019-09-25 | 8:00 | CX1210 | Short rural | Planned |  | 102 | 345 | 0.11577 | 0.00033557 | No
2019-09-25 | 8:00 | T868 | Short rural | Planned |  | 4 | 395 | 0.005198 | 1.3159e-05 | No
2019-09-25 | 8:00 | GL1255 | Short rural | Planned |  | 21 | 225 | 0.015545 | 6.9087e-05 | No
2019-09-25 | 8:00 | DP1295 | Urban | Planned |  | 1 | 420 | 0.00056045 | 1.3344e-06 | No
2019-09-26 | 8:00 | MG1267 | Short rural | Planned |  | 16 | 395 | 0.020792 | 5.2638e-05 | No
2019-09-26 | 8:00 | CX1284 | Short rural | Planned |  | 1 | 370 | 0.0012172 | 3.2899e-06 | No
2019-09-26 | 9:00 | 49395 | Urban | Planned |  | 7 | 380 | 0.0035495 | 9.3408e-06 | No
2019-09-26 | 8:30 | BDG2 | Short rural | Planned |  | 78 | 450 | 0.11547 | 0.00025661 | No
2019-09-26 | 8:30 | CR1254 | Urban | Planned |  | 240 | 105 | 0.033627 | 0.00032026 | No
2019-09-26 | 8:00 | RV1280 | Urban | Planned |  | 61 | 390 | 0.031745 | 8.1398e-05 | No
2019-09-26 | 7:30 | J482 | Urban | Planned |  | 60 | 465 | 0.03723 | 8.0064e-05 | No
2019-09-26 | 8:30 | BYC2 | Short rural | Planned |  | 35 | 421 | 0.048476 | 0.00011515 | No
2019-09-26 | 8:00 | A095 | Short rural | Planned |  | 25 | 505 | 0.041535 | 8.2247e-05 | No
2019-09-26 | 11:00 | D810 | Short rural | Planned |  | 22 | 195 | 0.014114 | 7.2377e-05 | No
2019-09-26 | 8:30 | NA1236 | Short rural | Planned |  | 86 | 358 | 0.10129 | 0.00028293 | No
2019-09-26 | 7:30 | 68181 | Urban | Planned |  | 88 | 285 | 0.033467 | 0.00011743 | No
2019-10-11 | 9:30 | DFC2 | Short rural | Planned |  | 1 | -1125 | -0.0037011 | 3.2899e-06 | No
2019-09-26 | 8:00 | RBA2 | Short rural | Planned |  | 13 | 380 | 0.016252 | 4.2768e-05 | No
2019-09-26 | 8:00 | MVF2 | Short rural | Planned |  | 3 | 160 | 0.0015791 | 9.8696e-06 | No
2019-09-26 | 8:00 | CX1210 | Short rural | Planned |  | 10 | 185 | 0.0060862 | 3.2899e-05 | No
2019-09-26 | 8:00 | KVA2 | Short rural | Planned |  | 7 | 415 | 0.0095571 | 2.3029e-05 | No
2019-09-26 | 9:00 | MG1219 | Short rural | Planned |  | 6 | 135 | 0.0026648 | 1.9739e-05 | No
2019-09-26 | 8:00 | CJ1204 | Urban | Planned |  | 101 | 435 | 0.058627 | 0.00013477 | No
2019-09-27 | 8:00 | MYE2 | Short rural | Planned |  | 64 | 435 | 0.09159 | 0.00021055 | No
2019-09-27 | 8:00 | A046 | Short rural | Planned |  | 18 | 210 | 0.012436 | 5.9218e-05 | No
2019-09-27 | 8:00 | L591 | Short rural | Planned |  | 5 | 225 | 0.0037011 | 1.6449e-05 | No
2019-09-27 | 7:30 | W196 | Urban | Planned |  | 45 | 475 | 0.028523 | 6.0048e-05 | No
2019-09-27 | 8:00 | 57444 | Short rural | Planned |  | 1 | 330 | 0.0010857 | 3.2899e-06 | No
2019-09-27 | 8:00 | BDC2 | Short rural | Planned |  | 83 | 397 | 0.1084 | 0.00027306 | No
2019-09-27 | 8:30 | BDG2 | Short rural | Planned |  | 110 | 420 | 0.15199 | 0.00036188 | No
2019-09-27 | 8:00 | 87220 | Short rural | Planned |  | 31 | 205 | 0.020907 | 0.00010199 | No
2019-09-27 | 8:00 | CJ1204 | Urban | Planned |  | 106 | 465 | 0.065773 | 0.00014145 | No
2019-09-27 | 8:30 | SN1271 | Short rural | Planned |  | 2 | 135 | 0.00088826 | 6.5797e-06 | No
2019-09-27 | 11:00 | L942 | Short rural | Planned |  | 1 | 95 | 0.00031254 | 3.2899e-06 | No
2019-09-27 | 8:00 | BX1212 | Urban | Planned |  | 316 | 430 | 0.18132 | 0.00042167 | No
2019-09-27 | 7:30 | NG1247 | Urban | Planned |  | 107 | 270 | 0.038551 | 0.00014278 | No
2019-09-27 | 8:00 | L942 | Short rural | Planned |  | 21 | 165 | 0.011399 | 6.9087e-05 | No
2019-09-27 | 8:00 | 8799 | Short rural | Planned |  | 114 | 185 | 0.069383 | 0.00037504 | No
2019-09-27 | 7:30 | 8777 | Urban | Planned |  | 73 | 240 | 0.023379 | 9.7411e-05 | No
2019-09-27 | 10:00 | 8799 | Short rural | Planned |  | 29 | 225 | 0.021466 | 9.5406e-05 | No
2019-09-28 | 8:00 | CA1236 | Urban | Planned |  | 22 | 189 | 0.0055484 | 2.9357e-05 | No
2019-09-28 | 8:00 | X881 | Short rural | Planned |  | 92 | 510 | 0.15436 | 0.00030267 | No
2019-09-28 | 6:30 | S735 | Short rural | Planned |  | 3 | 305 | 0.0030102 | 9.8696e-06 | No
2019-09-28 | 9:00 | FT1206 | Short rural | Planned |  | 51 | 301 | 0.050503 | 0.00016778 | No
2019-09-28 | 8:00 | MYQ2 | Short rural | Planned |  | 275 | 275 | 0.2488 | 0.00090471 | No
2019-09-28 | 8:00 | NG1210 | Short rural | Planned |  | 20 | 370 | 0.024345 | 6.5797e-05 | No
2019-09-28 | 7:00 | SC1253 | Short rural | Planned |  | 355 | 600 | 0.70074 | 0.0011679 | No
2019-09-28 | 8:00 | NG1210 | Short rural | Planned |  | 19 | 500 | 0.031254 | 6.2507e-05 | No
2019-09-28 | 8:00 | BX1242 | Urban | Planned |  | 34 | 360 | 0.016333 | 4.537e-05 | No
2019-09-28 | 8:00 | T829 | Urban | Planned |  | 1 | 430 | 0.00057379 | 1.3344e-06 | No
2019-09-29 | 7:00 | WQ1249 | Urban | Planned |  | 1 | 570 | 0.00076061 | 1.3344e-06 | No
2019-09-29 | 7:00 | SY1252 | Urban | Planned |  | 5 | 510 | 0.0034027 | 6.672e-06 | No
2019-09-29 | 7:00 | WX1270 | Urban | Planned |  | 15 | 510 | 0.010208 | 2.0016e-05 | No
2019-09-30 | 8:00 | RW1292 | Short rural | Planned |  | 12 | 350 | 0.013817 | 3.9478e-05 | No
2019-09-30 | 9:00 | 49382 | Urban | Planned |  | 4 | 319 | 0.0017027 | 5.3376e-06 | No
2019-09-30 | 8:00 | KME2 | Short rural | Planned |  | 23 | 470 | 0.035563 | 7.5667e-05 | No
2019-09-30 | 8:00 | KMA2 | Short rural | Planned |  | 78 | 495 | 0.12702 | 0.00025661 | No
2019-09-30 | 8:00 | M158 | Urban | Planned |  | 1 | 240 | 0.00032026 | 1.3344e-06 | No
2019-09-30 | 8:00 | T842 | Short rural | Planned |  | 11 | 365 | 0.013209 | 3.6188e-05 | No
2019-09-30 | 8:00 | X217 | Short rural | Planned |  | 13 | 360 | 0.015397 | 4.2768e-05 | No
2019-09-30 | 8:00 | BWH2 | Short rural | Planned |  | 4 | 540 | 0.0071061 | 1.3159e-05 | No
2019-09-30 | 8:00 | NN1277 | Urban | Planned |  | 5 | 235 | 0.0015679 | 6.672e-06 | No
2019-09-30 | 8:00 | CR1262 | Urban | Planned |  | 87 | 350 | 0.040632 | 0.00011609 | No
2019-09-30 | 9:00 | 5496 | Urban | Planned |  | 1 | 360 | 0.00048038 | 1.3344e-06 | No
2019-10-01 | 8:00 | T868 | Short rural | Planned |  | 7 | 375 | 0.0086359 | 2.3029e-05 | No
2019-10-01 | 8:30 | WRB2 | Urban | Planned |  | 147 | 240 | 0.047078 | 0.00019616 | No
2019-10-01 | 8:00 | MYE2 | Short rural | Planned |  | 39 | 420 | 0.053888 | 0.0001283 | No
2019-10-01 | 8:30 | KMD2 | Short rural | Planned |  | 20 | 330 | 0.021713 | 6.5797e-05 | No
2019-10-01 | 8:00 | SC1204 | Short rural | Planned |  | 7 | 435 | 0.010018 | 2.3029e-05 | No
2019-10-01 | 8:00 | CR1254 | Urban | Planned |  | 108 | 445 | 0.064131 | 0.00014412 | No
2019-10-01 | 8:30 | NA1225 | Short rural | Planned |  | 30 | 380 | 0.037504 | 9.8696e-05 | No
2019-10-01 | 8:30 | ULB2 | Short rural | Planned |  | 75 | 450 | 0.11103 | 0.00024674 | No
2019-10-01 | 8:00 | L591 | Short rural | Planned |  | 7 | 300 | 0.0069087 | 2.3029e-05 | No
2019-10-01 | 8:00 | BWH2 | Short rural | Planned |  | 19 | 500 | 0.031254 | 6.2507e-05 | No
2019-10-01 | 7:30 | 7977 | Urban | Planned |  | 20 | 510 | 0.013611 | 2.6688e-05 | No
2019-10-01 | 9:00 | 49382 | Urban | Planned |  | 55 | 450 | 0.033026 | 7.3392e-05 | No
2019-10-01 | 8:00 | MG1267 | Short rural | Planned |  | 114 | 540 | 0.20252 | 0.00037504 | No
2019-10-01 | 8:00 | BK1251 | Short rural | Planned |  | 59 | 405 | 0.078611 | 0.0001941 | No
2019-10-02 | 8:00 | 19857 | Urban | Planned |  | 1 | 425 | 0.00056712 | 1.3344e-06 | No
2019-10-02 | 8:00 | T841 | Short rural | Planned |  | 124 | 44 | 0.017949 | 0.00040794 | No
2019-10-02 | 7:30 | A352 | Urban | Planned |  | 19 | 445 | 0.011282 | 2.5354e-05 | No
2019-10-02 | 8:00 | WWB2 | Short rural | Planned |  | 213 | 255 | 0.17869 | 0.00070074 | No
2019-10-02 | 8:00 | GG1232 | Short rural | Planned |  | 42 | 580 | 0.080141 | 0.00013817 | No
2019-10-02 | 8:00 | MVB2 | Short rural | Planned |  | 7 | 285 | 0.0065633 | 2.3029e-05 | No
2019-10-02 | 8:00 | BDG2 | Short rural | Planned |  | 26 | 440 | 0.037636 | 8.5536e-05 | No
2019-10-02 | 7:00 | S765 | Urban | Planned |  | 1 | 285 | 0.0003803 | 1.3344e-06 | No
2019-10-02 | 8:00 | CX1206 | Short rural | Planned |  | 24 | 252 | 0.019897 | 7.8957e-05 | No
2019-10-02 | 8:30 | APC2 | Short rural | Planned |  | 135 | 205 | 0.091047 | 0.00044413 | No
2019-10-02 | 8:00 | WL1258 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2019-10-02 | 8:30 | BDG2 | Short rural | Planned |  | 28 | 450 | 0.041452 | 9.2116e-05 | No
2019-10-02 | 9:00 | T899 | Urban | Planned |  | 68 | 380 | 0.034481 | 9.0739e-05 | No
2019-10-02 | 9:00 | 76225 | Short rural | Planned |  | 7 | 110 | 0.0025332 | 2.3029e-05 | No
2019-10-03 | 8:00 | NWD2 | Urban | Planned |  | 55 | 435 | 0.031925 | 7.3392e-05 | No
2019-10-03 | 8:00 | MM1202 | Urban | Planned |  | 127 | 230 | 0.038978 | 0.00016947 | No
2019-10-03 | 8:00 | H745 | Short rural | Planned |  | 33 | 400 | 0.043426 | 0.00010857 | No
2019-10-03 | 9:00 | PH1223 | Urban | Planned |  | 4 | 495 | 0.0026421 | 5.3376e-06 | No
2019-10-03 | 8:30 | ULC2 | Short rural | Planned |  | 254 | 440 | 0.36768 | 0.00083563 | No
2019-10-03 | 8:00 | 49918 | Urban | Planned |  | 87 | 335 | 0.038891 | 0.00011609 | No
2019-10-03 | 8:30 | CLA2 | Short rural | Planned |  | 205 | 445 | 0.30012 | 0.00067442 | No
2019-10-03 | 9:00 | 55876 | Urban | Planned |  | 47 | 266 | 0.016683 | 6.2717e-05 | No
2019-10-03 | 7:30 | 7970 | Urban | Planned |  | 77 | 405 | 0.041613 | 0.00010275 | No
2019-10-03 | 8:00 | CR1210 | Urban | Planned |  | 220 | 480 | 0.14091 | 0.00029357 | No
2019-10-03 | 8:00 | 48198 | Urban | Planned |  | 13 | 410 | 0.0071123 | 1.7347e-05 | No
2019-10-03 | 8:30 | WWF2 | Urban | Planned |  | 103 | 450 | 0.061849 | 0.00013744 | No
2019-10-03 | 8:00 | RW1292 | Short rural | Planned |  | 33 | 320 | 0.034741 | 0.00010857 | No
2019-10-03 | 8:00 | BX1222 | Urban | Planned |  | 262 | 450 | 0.15733 | 0.00034961 | No
2019-10-04 | 8:30 | BDG2 | Short rural | Planned |  | 50 | 450 | 0.074022 | 0.00016449 | No
2019-10-04 | 8:00 | 7979 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2019-10-04 | 8:30 | TM1258 | Short rural | Planned |  | 126 | 201 | 0.083319 | 0.00041452 | No
2019-10-04 | 8:00 | S740 | Urban | Planned |  | 14 | 480 | 0.0089672 | 1.8682e-05 | No
2019-10-04 | 8:00 | BK1251 | Short rural | Planned |  | 36 | 204 | 0.024161 | 0.00011844 | No
2019-10-04 | 8:00 | CR1214 | Urban | Planned |  | 74 | 385 | 0.038017 | 9.8746e-05 | No
2019-10-07 | 8:00 | T831 | Short rural | Planned |  | 30 | 315 | 0.031089 | 9.8696e-05 | No
2019-10-08 | 8:00 | MM1112 | Urban | Planned |  | 20 | 330 | 0.008807 | 2.6688e-05 | No
2019-10-08 | 8:30 | MVB2 | Short rural | Planned |  | 18 | 255 | 0.0151 | 5.9218e-05 | No
2019-10-08 | 7:30 | A325 | Urban | Planned |  | 258 | 400 | 0.13771 | 0.00034427 | No
2019-10-08 | 8:00 | L591 | Short rural | Planned |  | 16 | 385 | 0.020266 | 5.2638e-05 | No
2019-10-08 | 8:00 | 49918 | Urban | Planned |  | 1 | 420 | 0.00056045 | 1.3344e-06 | No
2019-10-08 | 7:30 | CT1206 | Urban | Planned |  | 64 | 430 | 0.036723 | 8.5402e-05 | No
2019-10-08 | 8:00 | J503 | Urban | Planned |  | 63 | 540 | 0.045396 | 8.4067e-05 | No
2019-10-08 | 9:00 | SHE2 | Urban | Planned |  | 95 | 45 | 0.0057046 | 0.00012677 | No
2019-10-08 | 5:00 | NWF2 | Urban | Planned |  | 37 | 885 | 0.043695 | 4.9373e-05 | No
2019-10-09 | 8:00 | CR1210 | Urban | Planned |  | 102 | 440 | 0.059888 | 0.00013611 | No
2019-10-09 | 8:00 | KVB2 | Short rural | Planned |  | 14 | 290 | 0.013357 | 4.6058e-05 | No
2019-10-09 | 7:30 | A095 | Short rural | Planned |  | 25 | 825 | 0.067853 | 8.2247e-05 | No
2019-10-09 | 8:00 | MR2224 | Short rural | Planned |  | 30 | 465 | 0.045894 | 9.8696e-05 | No
2019-10-09 | 8:00 | L942 | Short rural | Planned |  | 1 | 500 | 0.0016449 | 3.2899e-06 | No
2019-10-09 | 7:30 | L579 | Urban | Planned |  | 22 | 430 | 0.012623 | 2.9357e-05 | No
2019-10-09 | 8:00 | MR2224 | Short rural | Planned |  | 53 | 540 | 0.094156 | 0.00017436 | No
2019-10-09 | 8:00 | 2809 | Urban | Planned |  | 36 | 540 | 0.025941 | 4.8038e-05 | No
2019-10-09 | 8:30 | CLA2 | Short rural | Planned |  | 9 | 450 | 0.013324 | 2.9609e-05 | No
2019-10-10 | 8:30 | BDG2 | Short rural | Planned |  | 131 | 440 | 0.18963 | 0.00043097 | No
2019-10-10 | 12:30 | KMD2 | Short rural | Planned |  | 92 | 200 | 0.060533 | 0.00030267 | No
2019-10-10 | 8:00 | MVC2 | Short rural | Planned |  | 64 | 480 | 0.10106 | 0.00021055 | No
2019-10-10 | 8:00 | JS1252 | Short rural | Planned |  | 19 | 405 | 0.025315 | 6.2507e-05 | No
2019-10-10 | 8:30 | KME2 | Short rural | Planned |  | 109 | 210 | 0.075305 | 0.0003586 | No
2019-10-10 | 8:00 | L579 | Urban | Planned |  | 72 | 402 | 0.038623 | 9.6077e-05 | No
2019-10-10 | 8:00 | CX1210 | Short rural | Planned |  | 17 | 405 | 0.022651 | 5.5928e-05 | No
2019-10-10 | 8:00 | CR1210 | Urban | Planned |  | 185 | 480 | 0.11849 | 0.00024686 | No
2019-10-10 | 8:00 | CA1210 | Urban | Planned |  | 42 | 300 | 0.016813 | 5.6045e-05 | No
2019-10-10 | 8:00 | BDG2 | Short rural | Planned |  | 136 | 420 | 0.18792 | 0.00044742 | No
2019-10-10 | 8:30 | SHA2 | Urban | Planned |  | 216 | 330 | 0.095116 | 0.00028823 | No
2019-10-10 | 8:00 | WWA2 | Short rural | Planned |  | 8 | 545 | 0.014344 | 2.6319e-05 | No
2019-10-10 | 5:00 | WL1296 | Urban | Planned |  | 61 | 705 | 0.057386 | 8.1398e-05 | No
2019-10-10 | 9:30 | S764 | Short rural | Planned |  | 1 | 510 | 0.0016778 | 3.2899e-06 | No
2019-10-11 | 8:00 | 35818 | Short rural | Planned |  | 4 | 555 | 0.0073035 | 1.3159e-05 | No
2019-10-11 | 7:30 | CV1221 | Urban | Planned |  | 54 | 410 | 0.029544 | 7.2058e-05 | No
2019-10-11 | 8:00 | 9032 | Short rural | Planned |  | 17 | 480 | 0.026845 | 5.5928e-05 | No
2019-10-11 | 8:00 | 9032 | Short rural | Planned |  | 17 | 540 | 0.030201 | 5.5928e-05 | No
2019-10-11 | 8:30 | SN1208 | Short rural | Planned |  | 1 | 370 | 0.0012172 | 3.2899e-06 | No
2019-10-11 | 8:00 | 8610 | Urban | Planned |  | 85 | 380 | 0.043101 | 0.00011342 | No
2019-10-11 | 8:00 | CX1210 | Short rural | Planned |  | 8 | 390 | 0.010264 | 2.6319e-05 | No
2019-10-11 | 7:30 | 68202 | Urban | Planned |  | 61 | 350 | 0.028489 | 8.1398e-05 | No
2019-10-11 | 8:00 | W123 | Short rural | Planned |  | 38 | 198 | 0.024753 | 0.00012501 | No
2019-10-11 | 8:00 | BYB2 | Short rural | Planned |  | 21 | 275 | 0.018999 | 6.9087e-05 | No
2019-10-11 | 8:00 | L948 | Short rural | Planned |  | 4 | 225 | 0.0029609 | 1.3159e-05 | No
2019-10-11 | 8:00 | NA1236 | Short rural | Planned |  | 23 | 510 | 0.03859 | 7.5667e-05 | No
2019-10-11 | 7:30 | CV1221 | Urban | Planned |  | 76 | 410 | 0.04158 | 0.00010141 | No
2019-10-11 | 8:00 | 27194 | Urban | Planned |  | 43 | 405 | 0.023239 | 5.7379e-05 | No
2019-10-12 | 7:30 | MYB2 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2019-10-12 | 11:00 | NM1243 | Urban | Planned |  | 2 | 240 | 0.00064051 | 2.6688e-06 | No
2019-10-12 | 8:00 | MR2272 | Short rural | Planned |  | 44 | 450 | 0.065139 | 0.00014475 | No
2019-10-12 | 7:00 | 9017 | Urban | Planned |  | 75 | 610 | 0.061049 | 0.00010008 | No
2019-10-13 | 8:00 | 25741 | Short rural | Planned |  | 11 | 480 | 0.01737 | 3.6188e-05 | No
2019-10-13 | 7:00 | FF1243 | Urban | Planned |  | 26 | 750 | 0.026021 | 3.4694e-05 | No
2019-10-13 | 7:30 | SN1208 | Short rural | Planned |  | 27 | 520 | 0.04619 | 8.8826e-05 | No
2019-10-13 | 4:00 | J500 | Urban | Planned |  | 3 | 60 | 0.00024019 | 4.0032e-06 | No
2019-10-14 | 7:30 | J495 | Short rural | Planned |  | 51 | 585 | 0.098153 | 0.00016778 | No
2019-10-14 | 4:00 | L516 | Urban | Planned |  | 4 | 480 | 0.002562 | 5.3376e-06 | No
2019-10-14 | 8:00 | 9032 | Short rural | Planned |  | 21 | 455 | 0.031435 | 6.9087e-05 | No
2019-10-14 | 10:00 | A095 | Short rural | Planned |  | 2 | 200 | 0.0013159 | 6.5797e-06 | No
2019-10-14 | 8:30 | Unknown (Mount Ousley) | Urban | Planned |  | 32 | 420 | 0.017934 | 4.2701e-05 | No
2019-10-14 | 8:00 | 8648 | Urban | Planned |  | 13 | 385 | 0.0066787 | 1.7347e-05 | No
2019-10-14 | 8:30 | BDG2 | Short rural | Planned |  | 41 | 450 | 0.060698 | 0.00013488 | No
2019-10-14 | 8:00 | MVE2 | Short rural | Planned |  | 239 | 480 | 0.37741 | 0.00078628 | No
2019-10-14 | 8:30 | BYC2 | Short rural | Planned |  | 2 | 360 | 0.0023687 | 6.5797e-06 | No
2019-10-14 | 6:00 | 4873 | Urban | Planned |  | 26 | 721 | 0.025015 | 3.4694e-05 | No
2019-10-15 | 8:00 | KVB2 | Short rural | Planned |  | 4 | 380 | 0.0050006 | 1.3159e-05 | No
2019-10-15 | 8:00 | MYQ2 | Short rural | Planned |  | 4 | 440 | 0.0057902 | 1.3159e-05 | No
2019-10-15 | 8:00 | 19816 | Urban | Planned |  | 7 | 120 | 0.0011209 | 9.3408e-06 | No
2019-10-15 | 9:00 | MM1202 | Urban | Planned |  | 150 | 280 | 0.056045 | 0.00020016 | No
2019-10-15 | 8:00 | BWH2 | Short rural | Planned |  | 19 | 440 | 0.027503 | 6.2507e-05 | No
2019-10-15 | 8:30 | CLA2 | Short rural | Planned |  | 245 | 420 | 0.33853 | 0.00080602 | No
2019-10-15 | 8:30 | ULE2 | Short rural | Planned |  | 6 | 235 | 0.0046387 | 1.9739e-05 | No
2019-10-15 | 7:30 | 4867 | Urban | Planned |  | 18 | 480 | 0.011529 | 2.4019e-05 | No
2019-10-15 | 8:00 | NK1332 | Urban | Planned |  | 16 | 475 | 0.010141 | 2.135e-05 | No
2019-10-15 | 8:00 | L948 | Short rural | Planned |  | 33 | 370 | 0.040169 | 0.00010857 | No
2019-10-15 | 8:00 | APH2 | Urban | Planned |  | 13 | 540 | 0.0093675 | 1.7347e-05 | No
2019-10-15 | 8:30 | BDC2 | Short rural | Planned |  | 72 | 450 | 0.10659 | 0.00023687 | No
2019-10-16 | 8:00 | KC1288 | Short rural | Planned |  | 16 | 200 | 0.010528 | 5.2638e-05 | No
2019-10-16 | 8:00 | 8801 | Short rural | Planned |  | 7 | 350 | 0.0080602 | 2.3029e-05 | No
2019-10-16 | 7:30 | 35990 | Short rural | Planned |  | 1 | 415 | 0.0013653 | 3.2899e-06 | No
2019-10-16 | 8:30 | 87220 | Short rural | Planned |  | 4 | 250 | 0.0032899 | 1.3159e-05 | No
2019-10-16 | 8:00 | 35981 | Short rural | Planned |  | 5 | 340 | 0.0055928 | 1.6449e-05 | No
2019-10-16 | 9:00 | L588 | Short rural | Planned |  | 2 | 70 | 0.00046058 | 6.5797e-06 | No
2019-10-16 | 8:00 | NK1332 | Urban | Planned |  | 69 | 435 | 0.040052 | 9.2074e-05 | No
2019-10-16 | 7:30 | L588 | Short rural | Planned |  | 5 | 57 | 0.00093761 | 1.6449e-05 | No
2019-10-16 | 8:00 | S744 | Urban | Planned |  | 118 | 470 | 0.074006 | 0.00015746 | No
2019-10-16 | 6:00 | KC1214 | Short rural | Planned |  | 1 | 255 | 0.00083892 | 3.2899e-06 | No
2019-10-16 | 8:30 | BYB2 | Short rural | Planned |  | 71 | 375 | 0.087593 | 0.00023358 | No
2019-10-16 | 8:30 | YYA2 | Short rural | Planned |  | 5 | 420 | 0.0069087 | 1.6449e-05 | No
2019-10-16 | 8:30 | C855 | Short rural | Planned |  | 33 | 410 | 0.044512 | 0.00010857 | No
2019-10-16 | 8:00 | RBD2 | Short rural | Planned |  | 7 | 555 | 0.012781 | 2.3029e-05 | No
2019-10-16 | 8:00 | MYC2 | Urban | Planned |  | 208 | 380 | 0.10547 | 0.00027756 | No
2019-10-16 | 8:30 | SHD2 | Short rural | Planned |  | 176 | 200 | 0.1158 | 0.00057902 | No
2019-10-17 | 8:00 | B217 | Urban | Planned |  | 82 | 540 | 0.059087 | 0.00010942 | No
2019-10-17 | 8:00 | 55885 | Urban | Planned |  | 122 | 540 | 0.08791 | 0.0001628 | No
2019-10-17 | 8:00 | RW1292 | Short rural | Planned |  | 29 | 440 | 0.041979 | 9.5406e-05 | No
2019-10-17 | 8:00 | X482 | Short rural | Planned |  | 2 | 260 | 0.0017107 | 6.5797e-06 | No
2019-10-17 | 8:00 | WD1284 | Short rural | Planned |  | 3 | 220 | 0.0021713 | 9.8696e-06 | No
2019-10-17 | 8:30 | CLA2 | Short rural | Planned |  | 254 | 430 | 0.35932 | 0.00083563 | No
2019-10-17 | 8:30 | ULL2 | Short rural | Planned |  | 33 | 410 | 0.044512 | 0.00010857 | No
2019-10-17 | 8:00 | BDG2 | Short rural | Planned |  | 36 | 480 | 0.056849 | 0.00011844 | No
2019-10-17 | 8:00 | WWB2 | Short rural | Planned |  | 46 | 205 | 0.031023 | 0.00015133 | No
2019-10-17 | 5:00 | A095 | Short rural | Planned |  | 12 | 2551.25 | 0.10072 | 3.9478e-05 | No
2019-10-17 | 8:00 | L591 | Short rural | Planned |  | 4 | 450 | 0.0059218 | 1.3159e-05 | No
2019-10-17 | 8:00 | CJ1253 | Urban | Planned |  | 58 | 370 | 0.028636 | 7.7395e-05 | No
2019-10-17 | 8:00 | NA1270 | Short rural | Planned |  | 134 | 365 | 0.16091 | 0.00044084 | No
2019-10-17 | 8:00 | SXC2 | Short rural | Planned |  | 74 | 330 | 0.080338 | 0.00024345 | No
2019-10-17 | 7:30 | A095 | Short rural | Planned |  | 27 | 917.2222 | 0.081473 | 8.8826e-05 | No
2019-10-18 | 8:00 | T869 | Urban | Planned |  | 94 | 215 | 0.026968 | 0.00012543 | No
2019-10-18 | 7:00 | LL1122 | Urban | Planned |  | 73 | 475 | 0.04627 | 9.7411e-05 | No
2019-10-18 | 8:30 | WRB2 | Urban | Planned |  | 207 | 175 | 0.048339 | 0.00027622 | No
2019-10-18 | 8:00 | ULL2 | Short rural | Planned |  | 1 | 375 | 0.0012337 | 3.2899e-06 | No
2019-10-18 | 12:00 | WRB2 | Urban | Planned |  | 40 | 160 | 0.0085402 | 5.3376e-05 | No
2019-10-18 | 8:00 | L588 | Short rural | Planned |  | 20 | 480 | 0.031583 | 6.5797e-05 | No
2019-10-18 | 8:00 | NK1342 | Urban | Planned |  | 56 | 360 | 0.026901 | 7.4726e-05 | No
2019-10-18 | 8:00 | MR2205 | Short rural | Planned |  | 27 | 420 | 0.037307 | 8.8826e-05 | No
2019-10-18 | 8:00 | MG1286 | Short rural | Planned |  | 40 | 400 | 0.052638 | 0.00013159 | No
2019-10-18 | 8:30 | BDE2 | Urban | Planned |  | 182 | 250 | 0.060715 | 0.00024286 | No
2019-10-18 | 8:30 | JBB2 | Short rural | Planned |  | 23 | 400 | 0.030267 | 7.5667e-05 | No
2019-10-18 | 8:30 | BYG2 | Short rural | Planned |  | 70 | 340 | 0.078299 | 0.00023029 | No
2019-10-19 | 8:30 | 4873 | Urban | Planned |  | 65 | 480 | 0.041633 | 8.6736e-05 | No
2019-10-19 | 6:30 | 49395 | Urban | Planned |  | 1 | 720 | 0.00096077 | 1.3344e-06 | No
2019-10-20 | 7:00 | T887 | Urban | Planned |  | 12 | 570 | 0.0091273 | 1.6013e-05 | No
2019-10-20 | 6:30 | M162 | Urban | Planned |  | 61 | 640 | 0.052095 | 8.1398e-05 | No
2019-10-20 | 9:00 | APB2 | Short rural | Planned |  | 139 | 420 | 0.19206 | 0.00045729 | No
2019-10-20 | 8:00 | CN1261 | Urban | Planned |  | 63 | 380 | 0.031946 | 8.4067e-05 | No
2019-10-20 | 8:00 | J482 | Urban | Planned |  | 62 | 480 | 0.039712 | 8.2733e-05 | No
2019-10-20 | 7:00 | T887 | Urban | Planned |  | 3 | 600 | 0.0024019 | 4.0032e-06 | No
2019-10-21 | 7:00 | 35312 | Urban | Planned |  | 4 | 505 | 0.0026955 | 5.3376e-06 | No
2019-10-21 | 5:00 | PH1212 | Urban | Planned |  | 13 | 140 | 0.0024286 | 1.7347e-05 | No
2019-10-21 | 7:30 | J495 | Short rural | Planned |  | 73 | 465 | 0.11167 | 0.00024016 | No
2019-10-21 | 8:00 | HBB2 | Short rural | Planned |  | 150 | 395 | 0.19492 | 0.00049348 | No
2019-10-21 | 8:00 | 17069 | Urban | Planned |  | 1 | -1175 | -0.0015679 | 1.3344e-06 | No
2019-10-21 | 8:00 | L517 | Urban | Planned |  | 57 | 480 | 0.036509 | 7.6061e-05 | No
2019-10-21 | 11:30 | ULH2 | Short rural | Planned |  | 2 | 215 | 0.0014146 | 6.5797e-06 | No
2019-10-21 | 8:00 | BWE2 | Short rural | Planned |  | 41 | 560 | 0.075535 | 0.00013488 | No
2019-10-21 | 9:00 | 7021 | Urban | Planned |  | 4 | 420 | 0.0022418 | 5.3376e-06 | No
2019-10-21 | 8:00 | T841 | Short rural | Planned |  | 124 | 240 | 0.097906 | 0.00040794 | No
2019-10-21 | 8:30 | ULH2 | Short rural | Planned |  | 34 | 345 | 0.03859 | 0.00011186 | No
2019-10-21 | 8:00 | GL1233 | Short rural | Planned |  | 6 | 99 | 0.0019542 | 1.9739e-05 | No
2019-10-22 | 8:00 | KVA2 | Short rural | Planned |  | 72 | 445 | 0.10541 | 0.00023687 | No
2019-10-22 | 8:30 | CLA2 | Short rural | Planned |  | 24 | 390 | 0.030793 | 7.8957e-05 | No
2019-10-22 | 8:00 | L582 | Short rural | Planned |  | 9 | 370 | 0.010955 | 2.9609e-05 | No
2019-10-22 | 8:00 | KVA2 | Short rural | Planned |  | 7 | 420 | 0.0096722 | 2.3029e-05 | No
2019-10-22 | 8:00 | 7970 | Urban | Planned |  | 55 | 420 | 0.030825 | 7.3392e-05 | No
2019-10-22 | 9:30 | MG1286 | Short rural | Planned |  | 4 | 75 | 0.00098696 | 1.3159e-05 | No
2019-10-22 | 8:30 | BDA2 | Short rural | Planned |  | 3 | 425 | 0.0041946 | 9.8696e-06 | No
2019-10-22 | 8:00 | R293 | Short rural | Planned |  | 19 | 491 | 0.030691 | 6.2507e-05 | No
2019-10-22 | 8:30 | APG2 | Urban | Planned |  | 54 | 180 | 0.01297 | 7.2058e-05 | No
2019-10-22 | 8:30 | MVB2 | Short rural | Planned |  | 18 | 410 | 0.024279 | 5.9218e-05 | No
2019-10-22 | 8:00 | 8798 | Short rural | Planned |  | 5 | 450 | 0.0074022 | 1.6449e-05 | No
2019-10-22 | 8:00 | SZ1242 | Short rural | Planned |  | 23 | 435 | 0.032915 | 7.5667e-05 | No
2019-10-22 | 8:00 | WBD2 | Short rural | Planned |  | 25 | 462 | 0.037998 | 8.2247e-05 | No
2019-10-22 | 8:30 | ULL2 | Short rural | Planned |  | 8 | 129 | 0.0033951 | 2.6319e-05 | No
2019-10-22 | 8:30 | CLC2 | Short rural | Planned |  | 141 | 127 | 0.058912 | 0.00046387 | No
2019-10-22 | 7:30 | WL1280 | Urban | Planned |  | 9 | 355 | 0.0042634 | 1.201e-05 | No
2019-10-21 | 11:00 | 17069 | Urban | Planned |  | 1 | 270 | 0.00036029 | 1.3344e-06 | No
2019-10-22 | 8:00 | X866 | Urban | Planned |  | 57 | 480 | 0.036509 | 7.6061e-05 | No
2019-10-23 | 8:00 | L591 | Short rural | Planned |  | 3 | 420 | 0.0041452 | 9.8696e-06 | No
2019-10-23 | 8:00 | 8801 | Short rural | Planned |  | 15 | 390 | 0.019246 | 4.9348e-05 | No
2019-10-23 | 8:30 | KMC2 | Short rural | Planned |  | 75 | 205 | 0.050582 | 0.00024674 | No
2019-10-23 | 8:30 | SHG2 | Short rural | Planned |  | 6 | 290 | 0.0057244 | 1.9739e-05 | No
2019-10-23 | 8:00 | 35304 | Urban | Planned |  | 26 | 465 | 0.016133 | 3.4694e-05 | No
2019-10-23 | 8:00 | SXC2 | Short rural | Planned |  | 6 | 380 | 0.0075009 | 1.9739e-05 | No
2019-10-23 | 8:00 | S771 | Urban | Planned |  | 102 | 450 | 0.061249 | 0.00013611 | No
2019-10-23 | 8:00 | SL1112 | Short rural | Planned |  | 7 | 495 | 0.011399 | 2.3029e-05 | No
2019-10-23 | 8:00 | RV1280 | Urban | Planned |  | 66 | 470 | 0.041393 | 8.807e-05 | No
2019-10-23 | 7:30 | MR2218 | Short rural | Planned |  | 23 | 315 | 0.023835 | 7.5667e-05 | No
2019-10-23 | 8:00 | A045 | Short rural | Planned |  | 10 | 225 | 0.0074022 | 3.2899e-05 | No
2019-10-23 | 8:00 | 4867 | Urban | Planned |  | 59 | 600 | 0.047238 | 7.873e-05 | No
2019-10-23 | 8:00 | RBB2 | Short rural | Planned |  | 98 | 250 | 0.080602 | 0.00032241 | No
2019-10-23 | 8:00 | W124 | Short rural | Planned |  | 13 | 375 | 0.016038 | 4.2768e-05 | No
2019-10-24 | 8:30 | CLA2 | Short rural | Planned |  | 15 | 365 | 0.018012 | 4.9348e-05 | No
2019-10-24 | 8:00 | RW1218 | Short rural | Planned |  | 17 | 330 | 0.018456 | 5.5928e-05 | No
2019-10-24 | 7:00 | L508 | Urban | Planned |  | 398 | 220 | 0.11684 | 0.00053109 | No
2019-10-24 | 8:00 | WX1258 | Urban | Planned |  | 12 | 470 | 0.007526 | 1.6013e-05 | No
2019-10-24 | 8:30 | BYB2 | Short rural | Planned |  | 98 | 405 | 0.13057 | 0.00032241 | No
2019-10-24 | 10:00 | A095 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2019-10-24 | 7:00 | CR1288 | Urban | Planned |  | 3 | 760 | 0.0030424 | 4.0032e-06 | No
2019-10-24 | 8:00 | R293 | Short rural | Planned |  | 19 | 480 | 0.030004 | 6.2507e-05 | No
2019-10-24 | 8:00 | 55875 | Urban | Planned |  | 39 | 350 | 0.018215 | 5.2042e-05 | No
2019-10-24 | 10:00 | OP1132 | Short rural | Planned |  | 48 | 55 | 0.0086852 | 0.00015791 | No
2019-10-25 | 8:00 | W188 | Short rural | Planned |  | 7 | 470 | 0.010824 | 2.3029e-05 | No
2019-10-25 | 8:00 | BDG2 | Short rural | Planned |  | 124 | 330 | 0.13462 | 0.00040794 | No
2019-10-25 | 8:00 | TM1284 | Short rural | Planned |  | 31 | 372 | 0.037939 | 0.00010199 | No
2019-10-25 | 8:30 | DP1206 | Urban | Planned |  | 159 | 420 | 0.089111 | 0.00021217 | No
2019-10-25 | 8:00 | 2806 | Urban | Planned |  | 130 | 290 | 0.050307 | 0.00017347 | No
2019-10-25 | 8:00 | CX1232 | Short rural | Planned |  | 5 | 330 | 0.0054283 | 1.6449e-05 | No
2019-10-25 | 8:00 | 9046 | Urban | Planned |  | 69 | 350 | 0.032226 | 9.2074e-05 | No
2019-10-25 | 8:30 | GG1232 | Short rural | Planned |  | 13 | 200 | 0.0085536 | 4.2768e-05 | No
2019-10-26 | 10:00 | HR1206 | Urban | Planned |  | 1 | 360 | 0.00048038 | 1.3344e-06 | No
2019-10-27 | 8:00 | KYF2 | Urban | Planned |  | 24 | 465 | 0.014892 | 3.2026e-05 | No
2019-10-27 | 8:00 | 4874 | Urban | Planned |  | 10 | 495 | 0.0066053 | 1.3344e-05 | No
2019-10-27 | 7:00 | 35761 | Urban | Planned |  | 21 | 600 | 0.016813 | 2.8022e-05 | No
2019-10-27 | 8:00 | L584 | Short rural | Planned |  | 4 | 350 | 0.0046058 | 1.3159e-05 | No
2019-10-27 | 8:00 | KYE2 | Urban | Planned |  | 36 | 480 | 0.023058 | 4.8038e-05 | No
2019-10-27 | 8:00 | JS1122 | Short rural | Planned |  | 7 | 460 | 0.010593 | 2.3029e-05 | No
2019-10-28 | 8:00 | 9032 | Short rural | Planned |  | 3 | 210 | 0.0020726 | 9.8696e-06 | No
2019-10-28 | 12:30 | CLB2 | Short rural | Planned |  | 211 | 496.4929 | 0.34465 | 0.00069416 | No
2019-10-28 | 8:00 | APC2 | Short rural | Planned |  | 54 | 570 | 0.10126 | 0.00017765 | No
2019-10-28 | 8:00 | JBA2 | Short rural | Planned |  | 27 | 380 | 0.033754 | 8.8826e-05 | No
2019-10-28 | 8:00 | 10248 | Urban | Planned |  | 20 | 540 | 0.014412 | 2.6688e-05 | No
2019-10-28 | 6:00 | DS1204 | Urban | Planned |  | 2 | 450 | 0.001201 | 2.6688e-06 | No
2019-10-28 | 8:00 | 35693 | Short rural | Planned |  | 65 | 400 | 0.085536 | 0.00021384 | No
2019-10-31 | 4:30 | CLB2 | Short rural | Planned |  | 582 | 180 | 0.34465 | 0.0019147 | No
2019-10-28 | 2:30 | CLB2 | Short rural | Planned |  | 371 | 94.124 | 0.11488 | 0.0012205 | No
2019-10-28 | 12:00 | J477 | Urban | Planned |  | 90 | 120 | 0.014412 | 0.0001201 | No
2019-10-28 | 7:30 | J499 | Urban | Planned |  | 94 | 480 | 0.060208 | 0.00012543 | No
2019-10-29 | 8:00 | 9059 | Urban | Planned |  | 31 | 360 | 0.014892 | 4.1366e-05 | No
2019-10-29 | 8:00 | 87220 | Short rural | Planned |  | 81 | 390 | 0.10393 | 0.00026648 | No
2019-10-29 | 8:00 | NN1233 | Short rural | Planned |  | 4 | 405 | 0.0053296 | 1.3159e-05 | No
2019-10-29 | 5:00 | SHB2 | Urban | Planned |  | 27 | 170 | 0.0061249 | 3.6029e-05 | No
2019-10-29 | 9:00 | BGA2 | Short rural | Planned |  | 28 | 162 | 0.014923 | 9.2116e-05 | No
2019-10-29 | 8:00 | J474 | Short rural | Planned |  | 3 | 490 | 0.0048361 | 9.8696e-06 | No
2019-10-29 | 12:01 | CJ1286 | Urban | Planned |  | 63 | 119 | 0.010004 | 8.4067e-05 | No
2019-10-29 | 8:00 | BWH2 | Short rural | Planned |  | 19 | 385 | 0.024065 | 6.2507e-05 | No
2019-10-29 | 7:30 | OP1262 | Short rural | Planned |  | 6 | 450 | 0.0088826 | 1.9739e-05 | No
2019-10-30 | 5:30 | UNJ2 | Urban | Planned |  | 4 | 125 | 0.0006672 | 5.3376e-06 | No
2019-10-30 | 10:00 | DP1210 | Short rural | Planned |  | 129 | 170 | 0.072147 | 0.00042439 | No
2019-10-30 | 7:30 | MG1267 | Short rural | Planned |  | 49 | 525 | 0.084632 | 0.0001612 | No
2019-10-30 | 8:00 | SHD2 | Short rural | Planned |  | 1 | 240 | 0.00078957 | 3.2899e-06 | No
2019-10-30 | 8:00 | CR1210 | Urban | Planned |  | 147 | 455 | 0.089251 | 0.00019616 | No
2019-10-30 | 8:00 | 19857 | Urban | Planned |  | 9 | 460 | 0.0055244 | 1.201e-05 | No
2019-10-30 | 10:00 | SN1271 | Short rural | Planned |  | 82 | 360 | 0.097117 | 0.00026977 | No
2019-10-30 | 8:00 | M163 | Urban | Planned |  | 4 | 440 | 0.0023485 | 5.3376e-06 | No
2019-10-30 | 7:30 | BWK2 | Short rural | Planned |  | 109 | 620 | 0.22233 | 0.0003586 | No
2019-10-30 | 8:00 | 55865 | Urban | Planned |  | 25 | 465 | 0.015512 | 3.336e-05 | No
2019-10-30 | 8:00 | NG1210 | Short rural | Planned |  | 50 | 500 | 0.082247 | 0.00016449 | No
2019-10-31 | 8:00 | GL1255 | Short rural | Planned |  | 34 | 230 | 0.025727 | 0.00011186 | No
2019-10-31 | 8:00 | C855 | Short rural | Planned |  | 29 | 415 | 0.039594 | 9.5406e-05 | No
2019-10-31 | 8:00 | R260 | Short rural | Planned |  | 11 | 390 | 0.014114 | 3.6188e-05 | No
2019-10-31 | 10:30 | A046 | Short rural | Planned |  | 18 | 30 | 0.0017765 | 5.9218e-05 | No
2019-10-31 | 8:00 | CR1262 | Urban | Planned |  | 68 | 400 | 0.036296 | 9.0739e-05 | No
2019-10-31 | 8:00 | T842 | Short rural | Planned |  | 6 | 375 | 0.0074022 | 1.9739e-05 | No
2019-10-31 | 7:30 | J491 | Urban | Planned |  | 75 | 450 | 0.045036 | 0.00010008 | No
2019-10-31 | 9:30 | T869 | Urban | Planned |  | 160 | 180 | 0.038431 | 0.0002135 | No
2019-10-31 | 8:00 | MVC2 | Short rural | Planned |  | 64 | 435 | 0.09159 | 0.00021055 | No
2019-10-31 | 8:00 | 7970 | Urban | Planned |  | 54 | 480 | 0.034588 | 7.2058e-05 | No
2019-10-31 | 8:00 | JBB2 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2019-10-31 | 8:00 | OP1132 | Short rural | Planned |  | 39 | 480 | 0.061586 | 0.0001283 | No
2019-10-31 | 8:00 | 8798 | Short rural | Planned |  | 3 | 425 | 0.0041946 | 9.8696e-06 | No
2019-10-31 | 7:30 | WT1215 | Short rural | Planned |  | 5 | 480 | 0.0078957 | 1.6449e-05 | No
2019-10-31 | 8:30 | APE2 | Short rural | Planned |  | 75 | 170 | 0.041946 | 0.00024674 | No
2019-11-01 | 8:00 | A095 | Short rural | Planned |  | 123 | 420 | 0.16995 | 0.00040465 | No
2019-11-01 | 8:00 | NK1342 | Urban | Planned |  | 110 | 300 | 0.044035 | 0.00014678 | No
2019-11-01 | 8:00 | SHL2 | Urban | Planned |  | 86 | 510 | 0.058527 | 0.00011476 | No
2019-11-01 | 7:00 | SHL2 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2019-11-01 | 8:00 | CR1228 | Urban | Planned |  | 176 | 385 | 0.090419 | 0.00023485 | No
2019-11-01 | 8:00 | A045 | Short rural | Planned |  | 26 | 465 | 0.039774 | 8.5536e-05 | No
2019-11-01 | 8:00 | MVB2 | Short rural | Planned |  | 7 | 385 | 0.0088662 | 2.3029e-05 | No
2019-11-02 | 8:00 | D852 | Urban | Planned |  | 58 | 530 | 0.041019 | 7.7395e-05 | No
2019-11-02 | 8:00 | CS1276 | Urban | Planned |  | 4 | 285 | 0.0015212 | 5.3376e-06 | No
2019-11-02 | 6:00 | 17059 | Urban | Planned |  | 3 | 420 | 0.0016813 | 4.0032e-06 | No
2019-11-02 | 7:00 | SHL2 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2019-11-02 | 8:00 | MS1202 | Short rural | Planned |  | 6 | 410 | 0.0080931 | 1.9739e-05 | No
2019-11-03 | 7:30 | SC1253 | Short rural | Planned |  | 4 | 570 | 0.0075009 | 1.3159e-05 | No
2019-11-03 | 8:00 | PH1260 | Urban | Planned |  | 27 | 540 | 0.019456 | 3.6029e-05 | No
2019-11-03 | 8:00 | APD2 | Short rural | Planned |  | 4 | 468 | 0.0061586 | 1.3159e-05 | No
2019-11-04 | 4:00 | D845 | Urban | Planned |  | 11 | 240 | 0.0035228 | 1.4678e-05 | No
2019-11-04 | 9:30 | F603 | Urban | Planned |  | 136 | 240 | 0.043555 | 0.00018148 | No
2019-11-04 | 9:00 | WQ1219 | Urban | Planned |  | 1 | 315 | 0.00042034 | 1.3344e-06 | No
2019-11-04 | 11:00 | 68181 | Urban | Planned |  | 50 | 240 | 0.016013 | 6.672e-05 | No
2019-11-04 | 8:00 | CR1254 | Urban | Planned |  | 120 | 380 | 0.060849 | 0.00016013 | No
2019-11-04 | 8:30 | GG1295 | Short rural | Planned |  | 35 | 265 | 0.030513 | 0.00011515 | No
2019-11-04 | 8:00 | J502 | Urban | Planned |  | 161 | 480 | 0.10312 | 0.00021484 | No
2019-11-04 | 7:30 | D814 | Short rural | Planned |  | 10 | 1155 | 0.037998 | 3.2899e-05 | No
2019-11-04 | 8:00 | D814 | Short rural | Planned |  | 12 | 907.5 | 0.035827 | 3.9478e-05 | No
2019-11-05 | 8:00 | T841 | Short rural | Planned |  | 86 | 210 | 0.059415 | 0.00028293 | No
2019-11-05 | 8:00 | NG1299 | Short rural | Planned |  | 38 | 270 | 0.033754 | 0.00012501 | No
2019-11-05 | 8:00 | R293 | Short rural | Planned |  | 19 | 480 | 0.030004 | 6.2507e-05 | No
2019-11-05 | 8:00 | RV1298 | Urban | Planned |  | 63 | 190 | 0.015973 | 8.4067e-05 | No
2019-11-05 | 7:30 | CN1213 | Urban | Planned |  | 21 | 440 | 0.01233 | 2.8022e-05 | No
2019-11-05 | 7:30 | J495 | Short rural | Planned |  | 106 | 470 | 0.1639 | 0.00034873 | No
2019-11-05 | 7:30 | CLB2 | Short rural | Planned |  | 582 | 39 | 0.074673 | 0.0019147 | No
2019-11-05 | 8:00 | MVB2 | Short rural | Planned |  | 18 | 350 | 0.020726 | 5.9218e-05 | No
2019-11-05 | 8:00 | 25450 | Short rural | Planned |  | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2019-11-05 | 10:00 | 48180 | Urban | Planned |  | 55 | 480 | 0.035228 | 7.3392e-05 | No
2019-11-06 | 8:00 | 10290 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2019-11-06 | 8:00 | 1959 | Urban | Planned |  | 43 | 422 | 0.024214 | 5.7379e-05 | No
2019-11-06 | 8:00 | MR2218 | Short rural | Planned |  | 21 | 390 | 0.026944 | 6.9087e-05 | No
2019-11-06 | 8:00 | T889 | Urban | Planned |  | 71 | 460 | 0.043581 | 9.4742e-05 | No
2019-11-06 | 8:00 | S740 | Urban | Planned |  | 35 | 205 | 0.0095743 | 4.6704e-05 | No
2019-11-06 | 8:00 | 6430 | Urban | Planned |  | 37 | 210 | 0.010368 | 4.9373e-05 | No
2019-11-06 | 8:30 | JBB2 | Short rural | Planned |  | 29 | 289 | 0.027572 | 9.5406e-05 | No
2019-11-06 | 9:00 | PCB2 | Short rural | Planned |  | 28 | 420 | 0.038689 | 9.2116e-05 | No
2019-11-06 | 9:00 | BGB2 | Urban | Planned |  | 15 | 165 | 0.0033026 | 2.0016e-05 | No
2019-11-06 | 9:00 | LP1222 | Urban | Planned |  | 10 | 285 | 0.003803 | 1.3344e-05 | No
2019-11-06 | 8:30 | W127 | Short rural | Planned |  | 3 | 335 | 0.0033063 | 9.8696e-06 | No
2019-11-06 | 8:00 | RW1292 | Short rural | Planned |  | 25 | 405 | 0.03331 | 8.2247e-05 | No
2019-11-06 | 8:00 | W163 | Short rural | Planned |  | 3 | 180 | 0.0017765 | 9.8696e-06 | No
2019-11-07 | 8:00 | A046 | Short rural | Planned |  | 39 | 630 | 0.080832 | 0.0001283 | No
2019-11-07 | 7:00 | ULB2 | Short rural | Planned |  | 2 | 420 | 0.0027635 | 6.5797e-06 | No
2019-11-07 | 8:00 | 48198 | Urban | Planned |  | 20 | 480 | 0.01281 | 2.6688e-05 | No
2019-11-07 | 8:00 | 9027 | Urban | Planned |  | 101 | 150 | 0.020216 | 0.00013477 | No
2019-11-07 | 8:00 | R293 | Short rural | Planned |  | 19 | 480 | 0.030004 | 6.2507e-05 | No
2019-11-07 | 10:00 | CN1258 | Urban | Planned |  | 94 | 300 | 0.03763 | 0.00012543 | No
2019-11-06 | 11:00 | 35443 | Urban | Planned |  | 39 | 280 | 0.014572 | 5.2042e-05 | No
2019-11-07 | 5:30 | CLB2 | Short rural | Planned |  | 582 | 180 | 0.34465 | 0.0019147 | No
2019-11-07 | 8:00 | CJ1267 | Urban | Planned |  | 35 | 540 | 0.02522 | 4.6704e-05 | No
2019-11-07 | 8:00 | BWF2 | Short rural | Planned |  | 12 | 405 | 0.015989 | 3.9478e-05 | No
2019-11-07 | 7:30 | LP1162 | Urban | Planned |  | 67 | 495 | 0.044255 | 8.9405e-05 | No
2019-11-07 | 8:00 | W196 | Urban | Planned |  | 66 | 462 | 0.040688 | 8.807e-05 | No
2019-11-07 | 7:30 | 4866 | Urban | Planned |  | 28 | 410 | 0.015319 | 3.7363e-05 | No
2019-11-08 | 8:00 | 8741 | Urban | Planned |  | 42 | 480 | 0.026901 | 5.6045e-05 | No
2019-11-08 | 11:00 | L582 | Short rural | Planned |  | 4 | 175 | 0.0023029 | 1.3159e-05 | No
2019-11-08 | 8:00 | 35767 | Urban | Planned |  | 8 | 450 | 0.0048038 | 1.0675e-05 | No
2019-11-08 | 8:00 | WBC2 | Short rural | Planned |  | 104 | 365 | 0.12488 | 0.00034215 | No
2019-11-08 | 8:30 | APB2 | Short rural | Planned |  | 200 | 450 | 0.29609 | 0.00065797 | No
2019-11-08 | 8:00 | L582 | Short rural | Planned |  | 1 | 80 | 0.00026319 | 3.2899e-06 | No
2019-11-08 | 8:00 | 48185 | Short rural | Planned |  | 27 | 470 | 0.041748 | 8.8826e-05 | No
2019-11-08 | 9:00 | 7142 | Urban | Planned |  | 19 | 300 | 0.0076061 | 2.5354e-05 | No
2019-11-08 | 8:00 | FF1284 | Urban | Planned |  | 38 | 360 | 0.018255 | 5.0707e-05 | No
2019-11-08 | 8:00 | D813 | Short rural | Planned |  | 58 | 480 | 0.09159 | 0.00019081 | No
2019-11-09 | 8:00 | 35766 | Urban | Planned |  | 24 | 445 | 0.014251 | 3.2026e-05 | No
2019-11-09 | 12:30 | WWE2 | Urban | Planned |  | 20 | 30 | 0.00080064 | 2.6688e-05 | No
2019-11-09 | 8:00 | T893 | Urban | Planned |  | 20 | 525 | 0.014011 | 2.6688e-05 | No
2019-11-09 | 7:00 | WL1259 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2019-11-09 | 12:01 | 8617 | Urban | Planned |  | 23 | 309 | 0.0094836 | 3.0691e-05 | No
2019-11-09 | 8:00 | R260 | Short rural | Planned |  | 2 | 545 | 0.003586 | 6.5797e-06 | No
2019-11-09 | 3:30 | MM1292 | Urban | Planned |  | 2 | 0 | 0 | 2.6688e-06 | No
2019-11-09 | 12:30 | WWE2 | Urban | Planned |  | 1 | 30 | 4.0032e-05 | 1.3344e-06 | No
2019-11-09 | 6:00 | MM1122 | Urban | Planned |  | 1 | 13 | 1.7347e-05 | 1.3344e-06 | No
2019-11-10 | 8:00 | 35701 | Short rural | Planned |  | 9 | 420 | 0.012436 | 2.9609e-05 | No
2019-11-10 | 8:30 | MYE2 | Short rural | Planned |  | 7 | 570 | 0.013127 | 2.3029e-05 | No
2019-11-10 | 9:00 | SWJ2 | Urban | Planned |  | 2 | 195 | 0.00052042 | 2.6688e-06 | No
2019-11-10 | 7:30 | 4866 | Urban | Planned |  | 17 | 430 | 0.0097545 | 2.2685e-05 | No
2019-11-10 | 8:00 | W124 | Short rural | Planned |  | 130 | 540 | 0.23095 | 0.00042768 | No
2019-11-10 | 8:00 | FT1206 | Short rural | Planned |  | 51 | 368 | 0.061744 | 0.00016778 | No
2019-11-11 | 8:00 | WBD2 | Short rural | Planned |  | 16 | 480 | 0.025266 | 5.2638e-05 | No
2019-11-11 | 8:00 | OP1202 | Urban | Planned |  | 21 | 480 | 0.013451 | 2.8022e-05 | No
2019-11-11 | 9:00 | SN1271 | Short rural | Planned |  | 3 | 355 | 0.0035037 | 9.8696e-06 | No
2019-11-11 | 8:30 | HKF2 | Short rural | Planned |  | 126 | 282 | 0.1169 | 0.00041452 | No
2019-11-11 | 8:00 | 35315 | Urban | Planned |  | 82 | 270 | 0.029544 | 0.00010942 | No
2019-11-11 | 8:00 | RW1255 | Short rural | Planned |  | 17 | 375 | 0.020973 | 5.5928e-05 | No
2019-11-11 | 8:00 | CR1280 | Urban | Planned |  | 205 | 245 | 0.06702 | 0.00027355 | No
2019-11-11 | 7:00 | DP1295 | Urban | Planned |  | 79 | 60 | 0.0063251 | 0.00010542 | No
2019-11-11 | 8:00 | APH2 | Urban | Planned |  | 13 | 570 | 0.0098879 | 1.7347e-05 | No
2019-11-11 | 8:00 | 10244 | Short rural | Planned |  | 49 | 370 | 0.059645 | 0.0001612 | No
2019-11-11 | 9:00 | 27336 | Urban | Planned |  | 2 | 195 | 0.00052042 | 2.6688e-06 | No
2019-11-11 | 8:00 | MM1162 | Urban | Planned |  | 64 | 390 | 0.033307 | 8.5402e-05 | No
2019-11-11 | 7:30 | J493 | Urban | Planned |  | 98 | 480 | 0.06277 | 0.00013077 | No
2019-11-12 | 8:00 | OP1262 | Short rural | Planned |  | 12 | 510 | 0.020134 | 3.9478e-05 | No
2019-11-12 | 8:30 | NA1270 | Short rural | Planned |  | 6 | 450 | 0.0088826 | 1.9739e-05 | No
2019-11-13 | 8:30 | APC2 | Short rural | Planned |  | 23 | 420 | 0.03178 | 7.5667e-05 | No
2019-11-13 | 8:30 | KMF2 | Urban | Planned |  | 127 | 240 | 0.040672 | 0.00016947 | No
2019-11-13 | 8:00 | FT1203 | Urban | Planned |  | 11 | 425 | 0.0062383 | 1.4678e-05 | No
2019-11-13 | 7:30 | 4866 | Urban | Planned |  | 35 | 390 | 0.018215 | 4.6704e-05 | No
2019-11-13 | 8:00 | NA1270 | Short rural | Planned |  | 3 | 390 | 0.0038491 | 9.8696e-06 | No
2019-11-13 | 8:30 | BDG2 | Short rural | Planned |  | 51 | 450 | 0.075502 | 0.00016778 | No
2019-11-13 | 8:00 | R208 | Short rural | Planned |  | 89 | 408 | 0.11946 | 0.0002928 | No
2019-11-13 | 8:00 | NG1299 | Short rural | Planned |  | 30 | 515 | 0.050828 | 9.8696e-05 | No
2019-11-13 | 10:00 | BK1299 | Short rural | Planned |  | 2 | 160 | 0.0010528 | 6.5797e-06 | No
2019-11-13 | 8:00 | HR1239 | Urban | Planned |  | 120 | 480 | 0.076861 | 0.00016013 | No
2019-11-13 | 8:00 | ULF2 | Short rural | Planned |  | 1 | 270 | 0.00088826 | 3.2899e-06 | No
2019-11-13 | 8:00 | RW1229 | Short rural | Planned |  | 11 | 315 | 0.011399 | 3.6188e-05 | No
2019-11-13 | 8:00 | FT1209 | Urban | Planned |  | 82 | 480 | 0.052522 | 0.00010942 | No
2019-11-14 | 8:00 | 35816 | Short rural | Planned |  | 27 | 425 | 0.037751 | 8.8826e-05 | No
2019-11-14 | 6:00 | AB1213 | Urban | Planned |  | 4 | 660 | 0.0035228 | 5.3376e-06 | No
2019-11-14 | 8:00 | MYM2 | Urban | Planned |  | 236 | 385 | 0.12124 | 0.00031492 | No
2019-11-14 | 8:00 | HKD2 | Short rural | Planned |  | 188 | 420 | 0.25977 | 0.00061849 | No
2019-11-14 | 8:30 | CLA2 | Short rural | Planned |  | 15 | 370 | 0.018259 | 4.9348e-05 | No
2019-11-14 | 10:00 | DP1273 | Urban | Planned |  | 1 | 210 | 0.00028022 | 1.3344e-06 | No
2019-11-14 | 8:30 | ULL2 | Short rural | Planned |  | 77 | 30 | 0.0075996 | 0.00025332 | No
2019-11-14 | 8:00 | 8798 | Short rural | Planned |  | 17 | 390 | 0.021812 | 5.5928e-05 | No
2019-11-14 | 8:00 | 19857 | Urban | Planned |  | 52 | 473 | 0.032821 | 6.9389e-05 | No
2019-11-14 | 8:00 | SHL2 | Urban | Planned |  | 86 | 510 | 0.058527 | 0.00011476 | No
2019-11-14 | 8:00 | BDA2 | Short rural | Planned |  | 14 | 231 | 0.010639 | 4.6058e-05 | No
2019-11-14 | 8:00 | NK1352 | Urban | Planned |  | 2 | 200 | 0.00053376 | 2.6688e-06 | No
2019-11-14 | 8:00 | MVC2 | Short rural | Planned |  | 64 | 410 | 0.086326 | 0.00021055 | No
2019-11-14 | 9:30 | BK1299 | Short rural | Planned |  | 2 | 165 | 0.0010857 | 6.5797e-06 | No
2019-11-14 | 8:00 | 87222 | Long rural | Planned |  | 13 | 300 | 12.4204 | 0.041401 | No
2019-11-14 | 8:00 | 9063 | Urban | Planned |  | 60 | 390 | 0.031225 | 8.0064e-05 | No
2019-11-15 | 7:30 | LP1162 | Urban | Planned |  | 66 | -1140 | -0.1004 | 8.807e-05 | No
2019-11-15 | 8:00 | MG1219 | Short rural | Planned |  | 1 | 320 | 0.0010528 | 3.2899e-06 | No
2019-11-15 | 8:00 | NN1285 | Short rural | Planned |  | 7 | 500 | 0.011515 | 2.3029e-05 | No
2019-11-15 | 8:30 | KMA2 | Short rural | Planned |  | 291 | 360 | 0.34465 | 0.00095735 | No
2019-11-15 | 8:00 | W127 | Short rural | Planned |  | 23 | 345 | 0.026105 | 7.5667e-05 | No
2019-11-15 | 6:30 | WRA2 | Urban | Planned |  | 53 | 60 | 0.0042434 | 7.0723e-05 | No
2019-11-15 | 8:00 | S737 | Short rural | Planned |  | 25 | 350 | 0.028786 | 8.2247e-05 | No
2019-11-15 | 8:00 | WWB2 | Short rural | Planned |  | 214 | 435 | 0.30625 | 0.00070403 | No
2019-11-15 | 8:00 | BL1232 | Short rural | Planned |  | 93 | 440 | 0.13462 | 0.00030596 | No
2019-11-15 | 8:00 | KVB2 | Short rural | Planned |  | 25 | 420 | 0.034544 | 8.2247e-05 | No
2019-11-15 | 8:00 | FT1210 | Urban | Planned |  | 66 | 345 | 0.030384 | 8.807e-05 | No
2019-11-15 | 8:00 | L582 | Short rural | Planned |  | 9 | 420 | 0.012436 | 2.9609e-05 | No
2019-11-15 | 8:00 | LP1422 | Urban | Planned |  | 41 | 525 | 0.028723 | 5.471e-05 | No
2019-11-15 | 8:00 | MG1267 | Short rural | Planned |  | 24 | 455 | 0.035925 | 7.8957e-05 | No
2019-11-15 | 8:00 | 19857 | Urban | Planned |  | 53 | 480 | 0.033947 | 7.0723e-05 | No
2019-11-16 | 8:00 | PH1260 | Urban | Planned |  | 19 | 530 | 0.013437 | 2.5354e-05 | No
2019-11-16 | 7:00 | A095 | Short rural | Planned |  | 19 | 660 | 0.041255 | 6.2507e-05 | No
2019-11-17 | 8:00 | 9034 | Urban | Planned |  | 189 | 455 | 0.11475 | 0.0002522 | No
2019-11-17 | 8:00 | APH2 | Urban | Planned |  | 2 | 3510 | 0.0093675 | 2.6688e-06 | No
2019-11-17 | 7:00 | T874 | Short rural | Planned |  | 1 | 600 | 0.0019739 | 3.2899e-06 | No
2019-11-17 | 10:00 | MM1382 | Urban | Planned |  | 3 | 345 | 0.0013811 | 4.0032e-06 | No
2019-11-17 | 9:00 | 35983 | Short rural | Planned |  | 101 | 480 | 0.15949 | 0.00033228 | No
2019-11-17 | 8:00 | MYK2 | Urban | Planned |  | 149 | 540 | 0.10737 | 0.00019883 | No
2019-11-17 | 7:00 | APH2 | Urban | Planned |  | 11 | 709.0909 | 0.010408 | 1.4678e-05 | No
2019-11-17 | 7:00 | AB1287 | Urban | Planned |  | 1 | 415 | 0.00055378 | 1.3344e-06 | No
2019-11-17 | 6:00 | WQ1290 | Urban | Planned |  | 12 | 600 | 0.0096077 | 1.6013e-05 | No
2019-11-18 | 6:00 | CN1247 | Urban | Planned |  | 1 | 575 | 0.00076728 | 1.3344e-06 | No
2019-11-18 | 8:00 | MYQ2 | Short rural | Planned |  | 274 | 450 | 0.40564 | 0.00090142 | No
2019-11-18 | 8:00 | C808 | Urban | Planned |  | 51 | 270 | 0.018375 | 6.8054e-05 | No
2019-11-18 | 8:00 | SXB2 | Short rural | Planned |  | 8 | 425 | 0.011186 | 2.6319e-05 | No
2019-11-18 | 11:00 | L588 | Short rural | Planned |  | 9 | 42 | 0.0012436 | 2.9609e-05 | No
2019-11-18 | 8:00 | W164 | Short rural | Planned |  | 2 | 390 | 0.0025661 | 6.5797e-06 | No
2019-11-18 | 6:00 | HR1269 | Urban | Planned |  | 5 | 380 | 0.0025354 | 6.672e-06 | No
2019-11-18 | 10:00 | SWJ2 | Urban | Planned |  | 7 | 130 | 0.0012143 | 9.3408e-06 | No
2019-11-18 | 8:00 | OP1112 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2019-11-18 | 8:00 | L588 | Short rural | Planned |  | 9 | 82 | 0.0024279 | 2.9609e-05 | No
2019-11-19 | 8:00 | CX1232 | Short rural | Planned |  | 8 | 150 | 0.0039478 | 2.6319e-05 | No
2019-11-19 | 8:00 | MM1392 | Urban | Planned |  | 94 | 330 | 0.041393 | 0.00012543 | No
2019-11-19 | 8:00 | MVB2 | Short rural | Planned |  | 23 | 435 | 0.032915 | 7.5667e-05 | No
2019-11-19 | 8:00 | BL1243 | Short rural | Planned |  | 110 | 500 | 0.18094 | 0.00036188 | No
2019-11-19 | 8:30 | 25449 | Short rural | Planned |  | 50 | 380 | 0.062507 | 0.00016449 | No
2019-11-19 | 8:00 | R293 | Short rural | Planned |  | 19 | 555 | 0.034692 | 6.2507e-05 | No
2019-11-19 | 8:00 | F601 | Urban | Planned |  | 199 | 465 | 0.12348 | 0.00026555 | No
2019-11-19 | 8:00 | CLB2 | Short rural | Planned |  | 482 | 413 | 0.6549 | 0.0015857 | No
2019-11-19 | 8:00 | WWC2 | Short rural | Planned |  | 135 | 375 | 0.16655 | 0.00044413 | No
2019-11-19 | 7:30 | 68202 | Urban | Planned |  | 49 | 490 | 0.032039 | 6.5386e-05 | No
2019-11-19 | 8:00 | JBB2 | Short rural | Planned |  | 18 | 487 | 0.028839 | 5.9218e-05 | No
2019-11-20 | 8:00 | BYE2 | Short rural | Planned |  | 22 | 458 | 0.033149 | 7.2377e-05 | No
2019-11-20 | 7:30 | MG1267 | Short rural | Planned |  | 50 | 510 | 0.083892 | 0.00016449 | No
2019-11-20 | 8:00 | RW1292 | Short rural | Planned |  | 25 | 380 | 0.031254 | 8.2247e-05 | No
2019-11-20 | 8:00 | M399 | Short rural | Planned |  | 1 | 405 | 0.0013324 | 3.2899e-06 | No
2019-11-20 | 8:30 | DP1206 | Urban | Planned |  | 168 | 120 | 0.026901 | 0.00022418 | No
2019-11-20 | 8:00 | 76225 | Short rural | Planned |  | 7 | 410 | 0.0094419 | 2.3029e-05 | No
2019-11-20 | 8:30 | APE2 | Short rural | Planned |  | 3 | 330 | 0.003257 | 9.8696e-06 | No
2019-11-20 | 7:30 | CN1213 | Urban | Planned |  | 20 | 540 | 0.014412 | 2.6688e-05 | No
2019-11-20 | 7:30 | 8776 | Urban | Planned |  | 65 | 290 | 0.025153 | 8.6736e-05 | No
2019-11-20 | 7:30 | MR2232 | Short rural | Planned |  | 40 | 245 | 0.032241 | 0.00013159 | No
2019-11-20 | 8:00 | BDG2 | Short rural | Planned |  | 123 | 465 | 0.18816 | 0.00040465 | No
2019-11-20 | 8:00 | S741 | Short rural | Planned |  | 54 | 225 | 0.039972 | 0.00017765 | No
2019-11-20 | 8:00 | 48185 | Short rural | Planned |  | 21 | 540 | 0.037307 | 6.9087e-05 | No
2019-11-20 | 8:00 | 35767 | Urban | Planned |  | 170 | 460 | 0.10435 | 0.00022685 | No
2019-11-21 | 8:00 | 8801 | Short rural | Planned |  | 20 | 325 | 0.021384 | 6.5797e-05 | No
2019-11-21 | 8:00 | A046 | Short rural | Planned |  | 39 | 455 | 0.058379 | 0.0001283 | No
2019-11-21 | 9:00 | J460 | Urban | Planned |  | 1 | 450 | 0.00060048 | 1.3344e-06 | No
2019-11-21 | 7:30 | B747 | Urban | Planned |  | 8 | 480 | 0.0051241 | 1.0675e-05 | No
2019-11-21 | 8:30 | 25449 | Short rural | Planned |  | 33 | 431 | 0.046792 | 0.00010857 | No
2019-11-21 | 8:00 | OA1233 | Short rural | Planned |  | 23 | 525 | 0.039725 | 7.5667e-05 | No
2019-11-21 | 8:00 | R293 | Short rural | Planned |  | 19 | 492 | 0.030754 | 6.2507e-05 | No
2019-11-21 | 6:00 | 1960 | Urban | Planned |  | 1 | 105 | 0.00014011 | 1.3344e-06 | No
2019-11-21 | 8:00 | MVD2 | Short rural | Planned |  | 16 | 165 | 0.0086852 | 5.2638e-05 | No
2019-11-21 | 8:45 | BWF2 | Short rural | Planned |  | 10 | 350 | 0.011515 | 3.2899e-05 | No
2019-11-21 | 8:30 | CLD2 | Short rural | Planned |  | 153 | 397 | 0.19983 | 0.00050335 | No
2019-11-21 | 8:00 | 19857 | Urban | Planned |  | 52 | 400 | 0.027756 | 6.9389e-05 | No
2019-11-21 | 8:30 | NA1270 | Short rural | Planned |  | 6 | 450 | 0.0088826 | 1.9739e-05 | No
2019-11-21 | 9:00 | J459 | Short rural | Planned |  | 13 | 345 | 0.014755 | 4.2768e-05 | No
2019-11-22 | 8:00 | HT1293 | Short rural | Planned |  | 1 | 270 | 0.00088826 | 3.2899e-06 | No
2019-11-22 | 8:30 | BYC2 | Short rural | Planned |  | 28 | 365 | 0.033622 | 9.2116e-05 | No
2019-11-22 | 8:00 | 1960 | Urban | Planned |  | 1 | -5 | -6.672e-06 | 1.3344e-06 | No
2019-11-22 | 8:00 | 68188 | Urban | Planned |  | 112 | 480 | 0.071737 | 0.00014945 | No
2019-11-22 | 8:00 | KC1236 | Short rural | Planned |  | 11 | 410 | 0.014837 | 3.6188e-05 | No
2019-11-22 | 8:30 | ULJ2 | Urban | Planned |  | 197 | 390 | 0.10252 | 0.00026288 | No
2019-11-22 | 8:00 | WWD2 | Urban | Planned |  | 223 | 430 | 0.12796 | 0.00029757 | No
2019-11-22 | 8:00 | BYG2 | Short rural | Planned |  | 1 | 335 | 0.0011021 | 3.2899e-06 | No
2019-11-22 | 8:00 | 8798 | Short rural | Planned |  | 17 | 344 | 0.019239 | 5.5928e-05 | No
2019-11-22 | 8:00 | UNJ2 | Urban | Planned |  | 3 | 395 | 0.0015813 | 4.0032e-06 | No
2019-11-22 | 8:00 | NA1270 | Short rural | Planned |  | 14 | 407 | 0.018746 | 4.6058e-05 | No
2019-11-22 | 9:00 | J462 | Urban | Planned |  | 1 | 395 | 0.00052709 | 1.3344e-06 | No
2019-11-23 | 11:30 | CT1202 | Urban | Planned |  | 12 | 225 | 0.0036029 | 1.6013e-05 | No
2019-11-23 | 6:30 | MYB2 | Urban | Planned |  | 1 | 60 | 8.0064e-05 | 1.3344e-06 | No
2019-11-23 | 8:00 | MG1234 | Short rural | Planned |  | 21 | 405 | 0.02798 | 6.9087e-05 | No
2019-11-22 | 9:00 | J459 | Short rural | Planned |  | 1 | 460 | 0.0015133 | 3.2899e-06 | No
2019-11-23 | 8:00 | 35762 | Urban | Planned |  | 116 | 595 | 0.0921 | 0.00015479 | No
2019-11-23 | 9:00 | 27339 | Urban | Planned |  | 2 | 165 | 0.00044035 | 2.6688e-06 | No
2019-11-24 | 8:00 | WD1225 | Short rural | Planned |  | 5 | 315 | 0.0051815 | 1.6449e-05 | No
2019-11-24 | 7:30 | 4873 | Urban | Planned |  | 43 | 315 | 0.018074 | 5.7379e-05 | No
2019-11-24 | 6:00 | WL1259 | Urban | Planned |  | 5 | 245 | 0.0016346 | 6.672e-06 | No
2019-11-24 | 8:00 | X877 | Short rural | Planned |  | 4 | 460 | 0.0060533 | 1.3159e-05 | No
2019-11-24 | 7:00 | MM1342 | Urban | Planned |  | 4 | 600 | 0.0032026 | 5.3376e-06 | No
2019-11-24 | 10:00 | 35989 | Short rural | Planned |  | 1 | 150 | 0.00049348 | 3.2899e-06 | No
2019-11-25 | 8:00 | NA1270 | Short rural | Planned |  | 8 | 388 | 0.010212 | 2.6319e-05 | No
2019-11-25 | 8:00 | T831 | Short rural | Planned |  | 6 | 490 | 0.0096722 | 1.9739e-05 | No
2019-11-25 | 8:30 | 35590 | Short rural | Planned |  | 6 | 420 | 0.0082905 | 1.9739e-05 | No
2019-11-25 | 8:00 | BWE2 | Short rural | Planned |  | 22 | 405 | 0.029313 | 7.2377e-05 | No
2019-11-25 | 8:30 | J510 | Urban | Planned |  | 128 | 426 | 0.072762 | 0.0001708 | No
2019-11-25 | 7:00 | 27187 | Urban | Planned |  | 6 | 180 | 0.0014412 | 8.0064e-06 | No
2019-11-25 | 8:00 | SC1253 | Short rural | Planned |  | 45 | 450 | 0.06662 | 0.00014804 | No
2019-11-26 | 5:00 | MG1286 | Short rural | Planned |  | 5 | 840 | 0.013817 | 1.6449e-05 | Yes
2019-11-26 | 10:00 | 8798 | Short rural | Planned |  | 8 | 180 | 0.0047374 | 2.6319e-05 | Yes
2019-11-26 | 7:00 | 1950 | Urban | Planned |  | 2 | 742.5 | 0.0019816 | 2.6688e-06 | Yes
2019-11-26 | 8:30 | WRF2 | Short rural | Planned |  | 151 | 130 | 0.06458 | 0.00049677 | Yes
2019-11-26 | 8:00 | JS1122 | Short rural | Planned |  | 46 | 405 | 0.06129 | 0.00015133 | Yes
2019-11-26 | 8:00 | C896 | Urban | Planned |  | 155 | 300 | 0.06205 | 0.00020683 | Yes
2019-11-26 | 8:00 | MVF2 | Short rural | Planned |  | 16 | 390 | 0.020529 | 5.2638e-05 | Yes
2019-11-26 | 8:00 | DFA2 | Short rural | Planned |  | 2 | 231 | 0.0015199 | 6.5797e-06 | Yes
2019-11-26 | 8:00 | CX1273 | Short rural | Planned |  | 21 | 190 | 0.013127 | 6.9087e-05 | Yes
2019-11-26 | 10:00 | D813 | Short rural | Planned |  | 10 | 210 | 0.0069087 | 3.2899e-05 | Yes
2019-11-26 | 8:30 | ULC2 | Short rural | Planned |  | 50 | 450 | 0.074022 | 0.00016449 | Yes
2019-11-26 | 8:00 | 1950 | Urban | Planned |  | 1 | 1305 | 0.0017414 | 1.3344e-06 | Yes
2019-11-26 | 8:00 | 35701 | Short rural | Planned |  | 93 | 240 | 0.07343 | 0.00030596 | Yes
2019-11-26 | 8:00 | CV1213 | Urban | Planned |  | 141 | 525 | 0.098779 | 0.00018815 | Yes
2019-11-26 | 8:00 | JBB2 | Short rural | Planned |  | 10 | 447 | 0.014706 | 3.2899e-05 | Yes
2019-11-26 | 8:30 | 25449 | Short rural | Planned |  | 33 | 450 | 0.048854 | 0.00010857 | Yes
2019-11-26 | 9:00 | CX1284 | Short rural | Planned |  | 45 | 400 | 0.059218 | 0.00014804 | Yes
2019-11-26 | 8:00 | T831 | Short rural | Planned |  | 12 | 425 | 0.016778 | 3.9478e-05 | Yes
2019-11-27 | 8:00 | OP1262 | Short rural | Planned |  | 12 | 510 | 0.020134 | 3.9478e-05 | No
2019-11-27 | 8:00 | 76225 | Short rural | Planned |  | 12 | 460 | 0.01816 | 3.9478e-05 | No
2019-11-27 | 7:30 | 4870 | Urban | Planned |  | 23 | 480 | 0.014732 | 3.0691e-05 | No
2019-11-27 | 8:00 | BDF2 | Short rural | Planned |  | 6 | 360 | 0.0071061 | 1.9739e-05 | No
2019-11-27 | 8:00 | CR1262 | Urban | Planned |  | 96 | 430 | 0.055084 | 0.0001281 | No
2019-11-27 | 8:00 | 49362 | Urban | Planned |  | 305 | 470 | 0.19129 | 0.00040699 | No
2019-11-27 | 8:00 | R211 | Short rural | Planned |  | 11 | 495 | 0.017913 | 3.6188e-05 | No
2019-11-27 | 8:00 | X879 | Short rural | Planned |  | 38 | 660 | 0.08251 | 0.00012501 | No
2019-11-27 | 11:00 | CD1297 | Urban | Planned |  | 77 | 40 | 0.0041099 | 0.00010275 | No
2019-11-27 | 8:00 | SC1204 | Short rural | Planned |  | 85 | 580 | 0.16219 | 0.00027964 | No
2019-11-27 | 8:00 | SC1253 | Short rural | Planned |  | 16 | 450 | 0.023687 | 5.2638e-05 | No
2019-11-27 | 8:30 | TM1284 | Short rural | Planned |  | 60 | 358 | 0.070666 | 0.00019739 | No
2019-11-27 | 8:00 | NG1299 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2019-11-27 | 8:00 | FT1205 | Short rural | Planned |  | 194 | 649 | 0.41421 | 0.00063823 | No
2019-11-27 | 8:00 | L584 | Short rural | Planned |  | 3 | 400 | 0.0039478 | 9.8696e-06 | No
2019-11-27 | 8:00 | CV1221 | Urban | Planned |  | 148 | 480 | 0.094796 | 0.00019749 | No
2019-11-27 | 2:00 | WRF2 | Short rural | Planned |  | 151 | 180 | 0.089418 | 0.00049677 | No
2019-11-27 | 8:00 | CJ1275 | Urban | Planned |  | 42 | 540 | 0.030264 | 5.6045e-05 | No
2019-11-27 | 8:30 | APB2 | Short rural | Planned |  | 22 | 360 | 0.026056 | 7.2377e-05 | No
2019-11-28 | 8:00 | 9030 | Urban | Planned |  | 181 | 465 | 0.11231 | 0.00024153 | No
2019-11-28 | 8:00 | B210 | Urban | Planned |  | 61 | 375 | 0.030524 | 8.1398e-05 | No
2019-11-28 | 8:30 | CLA2 | Short rural | Planned |  | 205 | 345 | 0.23268 | 0.00067442 | No
2019-11-28 | 8:00 | 68188 | Urban | Planned |  | 78 | 375 | 0.039031 | 0.00010408 | No
2019-11-28 | 8:00 | MR2292 | Urban | Planned |  | 34 | 495 | 0.022458 | 4.537e-05 | No
2019-11-28 | 8:00 | RW1218 | Short rural | Planned |  | 6 | 265 | 0.0052309 | 1.9739e-05 | No
2019-11-28 | 5:00 | UNB2 | Urban | Planned |  | 13 | 60 | 0.0010408 | 1.7347e-05 | No
2019-11-28 | 8:00 | T841 | Short rural | Planned |  | 83 | 375 | 0.1024 | 0.00027306 | No
2019-11-28 | 8:00 | CLB2 | Short rural | Planned |  | 582 | 494 | 0.94586 | 0.0019147 | No
2019-11-28 | 8:00 | 10290 | Short rural | Planned |  | 47 | 405 | 0.062623 | 0.00015462 | No
2019-11-28 | 8:00 | J502 | Urban | Planned |  | 63 | 430 | 0.036149 | 8.4067e-05 | No
2019-11-28 | 8:00 | NN1233 | Short rural | Planned |  | 1 | 510 | 0.0016778 | 3.2899e-06 | No
2019-11-29 | 8:30 | ULJ2 | Urban | Planned |  | 148 | 404 | 0.079786 | 0.00019749 | No
2019-11-29 | 8:00 | NG1210 | Short rural | Planned |  | 35 | 510 | 0.058724 | 0.00011515 | No
2019-11-29 | 8:00 | A096 | Short rural | Planned |  | 27 | 465 | 0.041304 | 8.8826e-05 | No
2019-11-29 | 8:30 | CLA2 | Short rural | Planned |  | 24 | 305 | 0.024082 | 7.8957e-05 | No
2019-11-29 | 8:00 | SZ1332 | Short rural | Planned |  | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2019-11-29 | 8:00 | BWE2 | Short rural | Planned |  | 8 | 390 | 0.010264 | 2.6319e-05 | No
2019-11-29 | 8:00 | SV1142 | Urban | Planned |  | 20 | 455 | 0.012143 | 2.6688e-05 | No
2019-11-29 | 6:00 | 49006 | Short rural | Planned |  | 14 | 215 | 0.0099025 | 4.6058e-05 | No
2019-11-30 | 8:00 | X881 | Short rural | Planned |  | 51 | 540 | 0.090603 | 0.00016778 | No
2019-12-01 | 7:00 | 6426 | Urban | Planned |  | 6 | 525 | 0.0042034 | 8.0064e-06 | No
2019-12-01 | 6:00 | ED1122 | Urban | Planned |  | 1 | 720 | 0.00096077 | 1.3344e-06 | No
2019-12-01 | 7:00 | T874 | Short rural | Planned |  | 10 | 375 | 0.012337 | 3.2899e-05 | No
2019-12-01 | 7:00 | B743 | Urban | Planned |  | 31 | 565 | 0.023372 | 4.1366e-05 | No
2019-12-01 | 8:00 | PH1264 | Urban | Planned |  | 35 | 520 | 0.024286 | 4.6704e-05 | No
2019-12-02 | 8:00 | DS1241 | Urban | Planned |  | 77 | 420 | 0.043154 | 0.00010275 | No
2019-12-02 | 8:00 | BWB2 | Urban | Planned |  | 25 | 300 | 0.010008 | 3.336e-05 | No
2019-12-02 | 8:30 | GG1232 | Short rural | Planned |  | 17 | 450 | 0.025167 | 5.5928e-05 | No
2019-12-02 | 8:00 | X217 | Short rural | Planned |  | 8 | 155 | 0.0040794 | 2.6319e-05 | No
2019-12-02 | 8:00 | 48198 | Urban | Planned |  | 10 | 390 | 0.0052042 | 1.3344e-05 | No
2019-12-03 | 8:00 | 46395 | Urban | Planned |  | 13 | 280 | 0.0048572 | 1.7347e-05 | No
2019-12-03 | 7:30 | L509 | Urban | Planned |  | 21 | 240 | 0.0067254 | 2.8022e-05 | No
2019-12-03 | 10:30 | 49918 | Urban | Planned |  | 15 | 240 | 0.0048038 | 2.0016e-05 | No
2019-12-03 | 12:30 | L519 | Urban | Planned |  | 14 | 240 | 0.0044836 | 1.8682e-05 | No
2019-12-03 | 8:00 | BL1243 | Short rural | Planned |  | 110 | 525 | 0.18999 | 0.00036188 | No
2019-12-03 | 8:00 | A048 | Urban | Planned |  | 17 | 430 | 0.0097545 | 2.2685e-05 | No
2019-12-03 | 9:00 | C899 | Urban | Planned |  | 25 | 420 | 0.014011 | 3.336e-05 | No
2019-12-03 | 8:00 | 55870 | Urban | Planned |  | 55 | 415 | 0.030458 | 7.3392e-05 | No
2019-12-03 | 8:00 | T883 | Urban | Planned |  | 1 | 255 | 0.00034027 | 1.3344e-06 | No
2019-12-03 | 8:30 | CLA2 | Short rural | Planned |  | 2 | 350 | 0.0023029 | 6.5797e-06 | No
2019-12-03 | 8:00 | C889 | Urban | Planned |  | 29 | 360 | 0.013931 | 3.8698e-05 | No
2019-12-03 | 8:00 | C889 | Urban | Planned |  | 92 | 520 | 0.063838 | 0.00012276 | No
2019-12-03 | 8:00 | W124 | Short rural | Planned |  | 21 | 140 | 0.0096722 | 6.9087e-05 | No
2019-12-03 | 8:00 | CD1234 | Short rural | Planned |  | 4 | 325 | 0.0042768 | 1.3159e-05 | No
2019-12-03 | 8:00 | S738 | Short rural | Planned |  | 16 | 450 | 0.023687 | 5.2638e-05 | No
2019-12-03 | 9:00 | NN1255 | Urban | Planned |  | 99 | 350 | 0.046237 | 0.00013211 | No
2019-12-03 | 8:00 | T831 | Short rural | Planned |  | 12 | 97 | 0.0038294 | 3.9478e-05 | No
2019-12-03 | 8:00 | JBB2 | Short rural | Planned |  | 8 | 445 | 0.011712 | 2.6319e-05 | No
2019-12-03 | 8:00 | MG1282 | Short rural | Planned |  | 16 | 395 | 0.020792 | 5.2638e-05 | No
2019-12-03 | 8:30 | ULD2 | Urban | Planned |  | 134 | 375 | 0.067054 | 0.00017881 | No
2019-12-03 | 7:30 | J499 | Urban | Planned |  | 99 | 370 | 0.048879 | 0.00013211 | No
2019-12-03 | 8:00 | MG1267 | Short rural | Planned |  | 6 | 420 | 0.0082905 | 1.9739e-05 | No
2019-12-03 | 8:00 | 87220 | Short rural | Planned |  | 38 | 257 | 0.032129 | 0.00012501 | No
2019-12-03 | 7:30 | 6430 | Urban | Planned |  | 51 | 330 | 0.022458 | 6.8054e-05 | No
2019-12-03 | 8:00 | UNF2 | Urban | Planned |  | 258 | 275 | 0.094676 | 0.00034427 | No
2019-12-04 | 8:00 | H745 | Short rural | Planned |  | 8 | 540 | 0.014212 | 2.6319e-05 | No
2019-12-04 | 8:00 | 55879 | Urban | Planned |  | 154 | 360 | 0.073979 | 0.0002055 | No
2019-12-04 | 8:30 | ULC2 | Short rural | Planned |  | 214 | 430 | 0.30273 | 0.00070403 | No
2019-12-04 | 8:00 | OP1112 | Short rural | Planned |  | 1 | 460 | 0.0015133 | 3.2899e-06 | No
2019-12-04 | 8:00 | PK1236 | Short rural | Planned |  | 3 | 460 | 0.00454 | 9.8696e-06 | No
2019-12-04 | 9:00 | NM1213 | Urban | Planned |  | 5 | 320 | 0.002135 | 6.672e-06 | No
2019-12-04 | 11:00 | 87222 | Long rural | Planned |  | 7 | 157 | 3.5 | 0.022293 | No
2019-12-04 | 8:00 | 87222 | Long rural | Planned |  | 13 | 194 | 8.0318 | 0.041401 | No
2019-12-04 | 9:00 | 49001 | Short rural | Planned |  | 12 | 360 | 0.014212 | 3.9478e-05 | No
2019-12-04 | 8:30 | APH2 | Urban | Planned |  | 1 | 150 | 0.00020016 | 1.3344e-06 | No
2019-12-04 | 8:00 | L948 | Short rural | Planned |  | 19 | 520 | 0.032504 | 6.2507e-05 | No
2019-12-04 | 8:00 | RBD2 | Short rural | Planned |  | 23 | 440 | 0.033293 | 7.5667e-05 | No
2019-12-04 | 8:00 | 61617 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2019-12-05 | 8:00 | RW1281 | Short rural | Planned |  | 38 | 480 | 0.060007 | 0.00012501 | No
2019-12-05 | 9:00 | 2816 | Urban | Planned |  | 22 | 330 | 0.0096877 | 2.9357e-05 | No
2019-12-05 | 8:00 | OA1233 | Short rural | Planned |  | 14 | 300 | 0.013817 | 4.6058e-05 | No
2019-12-05 | 8:00 | 87220 | Short rural | Planned |  | 31 | 345 | 0.035185 | 0.00010199 | No
2019-12-05 | 9:00 | 49001 | Short rural | Planned |  | 83 | 210 | 0.057342 | 0.00027306 | No
2019-12-05 | 8:00 | MVB2 | Short rural | Planned |  | 122 | 330 | 0.13245 | 0.00040136 | No
2019-12-05 | 8:00 | BWF2 | Short rural | Planned |  | 12 | 370 | 0.014607 | 3.9478e-05 | No
2019-12-05 | 8:00 | APB2 | Short rural | Planned |  | 348 | 405 | 0.46367 | 0.0011449 | No
2019-12-05 | 8:30 | CLA2 | Short rural | Planned |  | 6 | 350 | 0.0069087 | 1.9739e-05 | No
2019-12-05 | 8:00 | MR2205 | Short rural | Planned |  | 36 | 480 | 0.056849 | 0.00011844 | No
2019-12-05 | 8:00 | M399 | Short rural | Planned |  | 116 | 380 | 0.14502 | 0.00038162 | No
2019-12-05 | 8:00 | AZ1227 | Urban | Planned |  | 84 | 30 | 0.0033627 | 0.00011209 | No
2019-12-05 | 8:30 | ULC2 | Short rural | Planned |  | 74 | 590 | 0.14364 | 0.00024345 | No
2019-12-06 | 8:30 | APC2 | Short rural | Planned |  | 51 | 260 | 0.043624 | 0.00016778 | No
2019-12-06 | 7:30 | WL1217 | Urban | Planned |  | 35 | 510 | 0.023819 | 4.6704e-05 | No
2019-12-06 | 8:00 | A046 | Short rural | Planned |  | 39 | 375 | 0.048114 | 0.0001283 | No
2019-12-06 | 8:00 | CR1228 | Urban | Planned |  | 67 | 420 | 0.03755 | 8.9405e-05 | No
2019-12-06 | 8:00 | X482 | Short rural | Planned |  | 14 | -415 | -0.019114 | 4.6058e-05 | No
2019-12-06 | 8:30 | JBA2 | Short rural | Planned |  | 88 | 182 | 0.05269 | 0.00028951 | No
2019-12-06 | 8:00 | FT1207 | Urban | Planned |  | 147 | 330 | 0.064732 | 0.00019616 | No
2019-12-06 | 8:00 | CR1228 | Urban | Planned |  | 64 | 400 | 0.034161 | 8.5402e-05 | No
2019-12-06 | 7:00 | WX1244 | Urban | Planned |  | 1 | 260 | 0.00034694 | 1.3344e-06 | No
2019-12-06 | 8:00 | WL1217 | Urban | Planned |  | 35 | 360 | 0.016813 | 4.6704e-05 | No
2019-12-06 | 8:00 | KC1262 | Short rural | Planned |  | 1 | 336 | 0.0011054 | 3.2899e-06 | No
2019-12-06 | 8:00 | 35335 | Urban | Planned |  | 47 | 255 | 0.015993 | 6.2717e-05 | No
2019-12-07 | 8:00 | B217 | Urban | Planned |  | 116 | 420 | 0.065012 | 0.00015479 | No
2019-12-07 | 8:00 | X881 | Short rural | Planned |  | 27 | 435 | 0.038639 | 8.8826e-05 | No
2019-12-07 | 10:30 | 19868 | Urban | Planned |  | 28 | 300 | 0.011209 | 3.7363e-05 | No
2019-12-08 | 8:00 | LP1232 | Urban | Planned |  | 86 | 240 | 0.027542 | 0.00011476 | No
2019-12-08 | 8:00 | CT1206 | Urban | Planned |  | 64 | 540 | 0.046117 | 8.5402e-05 | No
2019-12-08 | 8:00 | J510 | Urban | Planned |  | 79 | 420 | 0.044275 | 0.00010542 | No
2019-12-08 | 8:00 | 68188 | Urban | Planned |  | 41 | 460 | 0.025167 | 5.471e-05 | No
2019-12-08 | 7:00 | SY1152 | Urban | Planned |  | 38 | 480 | 0.024339 | 5.0707e-05 | No
2019-12-08 | 5:00 | WM1222 | Urban | Planned |  | 155 | 283 | 0.058533 | 0.00020683 | No
2019-12-09 | 7:30 | 55874 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2019-12-09 | 8:00 | B719 | Short rural | Planned |  | 28 | 420 | 0.038689 | 9.2116e-05 | No
2019-12-09 | 8:00 | MVD2 | Short rural | Planned |  | 35 | 510 | 0.058724 | 0.00011515 | No
2019-12-09 | 6:00 | J459 | Short rural | Planned |  | 2 | 300 | 0.0019739 | 6.5797e-06 | No
2019-12-09 | 8:30 | JBB2 | Short rural | Planned |  | 10 | 438 | 0.01441 | 3.2899e-05 | No
2019-12-09 | 8:00 | J497 | Short rural | Planned |  | 164 | 435 | 0.2347 | 0.00053954 | No
2019-12-09 | 8:00 | RW1281 | Short rural | Planned |  | 9 | 240 | 0.0071061 | 2.9609e-05 | No
2019-12-09 | 9:30 | GG1232 | Short rural | Planned |  | 11 | 188 | 0.0068034 | 3.6188e-05 | No
2019-12-09 | 9:00 | DP1295 | Urban | Planned |  | 55 | 556 | 0.040806 | 7.3392e-05 | No
2019-12-10 | 8:00 | 35824 | Short rural | Planned |  | 16 | 480 | 0.025266 | 5.2638e-05 | No
2019-12-10 | 8:30 | CLA2 | Short rural | Planned |  | 3 | 217 | 0.0021417 | 9.8696e-06 | No
2019-12-10 | 8:00 | CR1254 | Urban | Planned |  | 310 | 480 | 0.19856 | 0.00041366 | No
2019-12-10 | 8:30 | BDG2 | Short rural | Planned |  | 241 | 460 | 0.36471 | 0.00079286 | No
2019-12-10 | 8:00 | AZ1272 | Short rural | Planned |  | 21 | 240 | 0.016581 | 6.9087e-05 | No
2019-12-10 | 8:00 | 10245 | Short rural | Planned |  | 3 | 274 | 0.0027043 | 9.8696e-06 | No
2019-12-10 | 8:00 | 48185 | Short rural | Planned |  | 12 | 555 | 0.02191 | 3.9478e-05 | No
2019-12-10 | 8:00 | M159 | Urban | Planned |  | 20 | 480 | 0.01281 | 2.6688e-05 | No
2019-12-10 | 8:00 | GG1258 | Urban | Planned |  | 47 | 440 | 0.027595 | 6.2717e-05 | No
2019-12-11 | 8:00 | S741 | Short rural | Planned |  | 39 | 350 | 0.044907 | 0.0001283 | No
2019-12-11 | 12:00 | L588 | Short rural | Planned |  | 3 | 145 | 0.0014311 | 9.8696e-06 | No
2019-12-11 | 7:00 | A095 | Short rural | Planned |  | 25 | 645 | 0.053049 | 8.2247e-05 | No
2019-12-11 | 8:00 | BWF2 | Short rural | Planned |  | 20 | 230 | 0.015133 | 6.5797e-05 | No
2019-12-11 | 7:30 | A344 | Urban | Planned |  | 39 | 480 | 0.02498 | 5.2042e-05 | No
2019-12-11 | 6:00 | WD1284 | Short rural | Planned |  | 1 | 60 | 0.00019739 | 3.2899e-06 | No
2019-12-11 | 7:00 | A095 | Short rural | Planned |  | 7 | 630 | 0.014508 | 2.3029e-05 | No
2019-12-11 | 8:00 | WH1224 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2019-12-11 | 8:30 | APH2 | Urban | Planned |  | 237 | 445 | 0.14073 | 0.00031625 | No
2019-12-11 | 8:30 | BDA2 | Short rural | Planned |  | 5 | 360 | 0.0059218 | 1.6449e-05 | No
2019-12-11 | 5:00 | GV1208 | Urban | Planned |  | 3 | 1110 | 0.0044435 | 4.0032e-06 | No
2019-12-11 | 8:00 | BL1232 | Short rural | Planned |  | 5 | 455 | 0.0074844 | 1.6449e-05 | No
2019-12-12 | 8:00 | 49008 | Short rural | Planned |  | 82 | 420 | 0.1133 | 0.00026977 | No
2019-12-12 | 8:00 | APB2 | Short rural | Planned |  | 222 | 410 | 0.29944 | 0.00073035 | No
2019-12-12 | 8:00 | A098 | Short rural | Planned |  | 12 | 625 | 0.024674 | 3.9478e-05 | No
2019-12-12 | 8:00 | WBC2 | Short rural | Planned |  | 38 | 580 | 0.072509 | 0.00012501 | No
2019-12-12 | 8:30 | GG1269 | Short rural | Planned |  | 151 | 325 | 0.16145 | 0.00049677 | No
2019-12-12 | 8:00 | W163 | Short rural | Planned |  | 6 | 400 | 0.0078957 | 1.9739e-05 | No
2019-12-12 | 8:30 | WRA2 | Urban | Planned |  | 163 | 365 | 0.07939 | 0.00021751 | No
2019-12-12 | 8:00 | MVF2 | Short rural | Planned |  | 10 | 390 | 0.01283 | 3.2899e-05 | No
2019-12-13 | 12:00 | APB2 | Short rural | Planned |  | 3 | 500 | 0.0049348 | 9.8696e-06 | No
2019-12-12 | 8:00 | 25783 | Urban | Planned |  | 14 | 420 | 0.0078463 | 1.8682e-05 | No
2019-12-12 | 8:00 | ULE2 | Short rural | Planned |  | 2 | 465 | 0.0030596 | 6.5797e-06 | No
2019-12-12 | 8:30 | BDC2 | Short rural | Planned |  | 10 | 215 | 0.0070732 | 3.2899e-05 | No
2019-12-12 | 10:00 | APB2 | Short rural | Planned |  | 1 | 1800 | 0.0059218 | 3.2899e-06 | No
2019-12-12 | 8:00 | APB2 | Short rural | Planned |  | 1 | 1500 | 0.0049348 | 3.2899e-06 | No
2019-12-12 | 8:00 | NA1236 | Short rural | Planned |  | 129 | 340 | 0.14429 | 0.00042439 | No
2019-12-13 | 8:00 | OP1202 | Urban | Planned |  | 2 | 480 | 0.001281 | 2.6688e-06 | No
2019-12-13 | 8:00 | 35816 | Short rural | Planned |  | 27 | 420 | 0.037307 | 8.8826e-05 | No
2019-12-13 | 8:00 | J514 | Urban | Planned |  | 65 | 300 | 0.026021 | 8.6736e-05 | No
2019-12-13 | 8:30 | HBA2 | Short rural | Planned |  | 139 | 240 | 0.10975 | 0.00045729 | No
2019-12-13 | 8:00 | PH1219 | Urban | Planned |  | 49 | 480 | 0.031385 | 6.5386e-05 | No
2019-12-13 | 8:00 | BYB2 | Short rural | Planned |  | 1 | 395 | 0.0012995 | 3.2899e-06 | No
2019-12-13 | 8:00 | 10290 | Short rural | Planned |  | 17 | 255 | 0.014262 | 5.5928e-05 | No
2019-12-13 | 8:00 | 19856 | Urban | Planned |  | 227 | 480 | 0.1454 | 0.00030291 | No
2019-12-13 | 8:30 | APH2 | Urban | Planned |  | 130 | 230 | 0.039899 | 0.00017347 | No
2019-12-13 | 8:00 | X879 | Short rural | Planned |  | 16 | 330 | 0.01737 | 5.2638e-05 | No
2019-12-13 | 7:30 | 4857 | Urban | Planned |  | 28 | 470 | 0.017561 | 3.7363e-05 | No
2019-12-14 | 9:00 | 68179 | Urban | Planned |  | 12 | 240 | 0.0038431 | 1.6013e-05 | No
2019-12-14 | 8:00 | WD1288 | Urban | Planned |  | 1 | 720 | 0.00096077 | 1.3344e-06 | No
2019-12-14 | 10:00 | 35982 | Short rural | Planned |  | 2 | 10 | 6.5797e-05 | 6.5797e-06 | No
2019-12-14 | 12:30 | OA1233 | Short rural | Planned |  | 6 | 10 | 0.00019739 | 1.9739e-05 | No
2019-12-15 | 8:00 | CN1206 | Urban | Planned |  | 33 | 495 | 0.021797 | 4.4035e-05 | No
2019-12-15 | 6:00 | MR2217 | Urban | Planned |  | 40 | 720 | 0.038431 | 5.3376e-05 | No
2019-12-15 | 8:00 | 25450 | Short rural | Planned |  | 8 | 560 | 0.014739 | 2.6319e-05 | No
2019-12-15 | 8:00 | CN1221 | Urban | Planned |  | 76 | 290 | 0.02941 | 0.00010141 | No
2019-12-15 | 8:00 | W164 | Short rural | Planned |  | 6 | 1272 | 0.025108 | 1.9739e-05 | No
2019-12-16 | 8:00 | BWH2 | Short rural | Planned |  | 37 | 480 | 0.058428 | 0.00012172 | No
2019-12-16 | 11:00 | CR1228 | Urban | Planned |  | 148 | 224 | 0.044238 | 0.00019749 | No
2019-12-16 | 10:00 | 6427 | Urban | Planned |  | 1 | 210 | 0.00028022 | 1.3344e-06 | No
2019-12-16 | 8:00 | DFA2 | Short rural | Planned |  | 39 | 415 | 0.053246 | 0.0001283 | No
2019-12-16 | 8:30 | YYA2 | Short rural | Planned |  | 1 | 320 | 0.0010528 | 3.2899e-06 | No
2019-12-16 | 9:00 | J493 | Urban | Planned |  | 82 | 385 | 0.042127 | 0.00010942 | No
2019-12-16 | 8:00 | T868 | Short rural | Planned |  | 4 | 260 | 0.0034215 | 1.3159e-05 | No
2019-12-16 | 10:00 | RD1233 | Urban | Planned |  | 1 | 330 | 0.00044035 | 1.3344e-06 | No
2019-12-16 | 8:00 | M169 | Urban | Planned |  | 5 | 360 | 0.0024019 | 6.672e-06 | No
2019-12-17 | 8:00 | L509 | Urban | Planned |  | 5 | 360 | 0.0024019 | 6.672e-06 | No
2019-12-17 | 8:00 | KVA2 | Short rural | Planned |  | 19 | 365 | 0.022815 | 6.2507e-05 | No
2019-12-17 | 8:00 | MR2224 | Short rural | Planned |  | 7 | 480 | 0.011054 | 2.3029e-05 | No
2019-12-17 | 8:00 | J492 | Urban | Planned |  | 135 | 360 | 0.064852 | 0.00018014 | No
2019-12-17 | 8:00 | CV1247 | Urban | Planned |  | 101 | 495 | 0.066713 | 0.00013477 | No
2019-12-17 | 8:00 | RBE2 | Short rural | Planned |  | 24 | 445 | 0.035136 | 7.8957e-05 | No
2019-12-17 | 11:00 | 87220 | Short rural | Planned |  | 10 | 70 | 0.0023029 | 3.2899e-05 | No
2019-12-17 | 8:00 | RBA2 | Short rural | Planned |  | 13 | 455 | 0.01946 | 4.2768e-05 | No
2019-12-17 | 8:00 | OP1262 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2019-12-17 | 8:00 | BYB2 | Short rural | Planned |  | 64 | 410 | 0.086326 | 0.00021055 | No
2019-12-17 | 8:00 | 19857 | Urban | Planned |  | 276 | 460 | 0.16942 | 0.00036829 | No
2019-12-17 | 8:30 | BDF2 | Short rural | Planned |  | 36 | 405 | 0.047966 | 0.00011844 | No
2019-12-17 | 8:30 | KMF2 | Urban | Planned |  | 1 | 420 | 0.00056045 | 1.3344e-06 | No
2019-12-17 | 8:00 | 87220 | Short rural | Planned |  | 3 | 175 | 0.0017272 | 9.8696e-06 | No
2019-12-17 | 8:00 | MYM2 | Urban | Planned |  | 245 | 570 | 0.18635 | 0.00032693 | No
2019-12-18 | 8:00 | BWA2 | Short rural | Planned |  | 127 | 475 | 0.19846 | 0.00041781 | No
2019-12-18 | 8:30 | JBB2 | Short rural | Planned |  | 5 | 315 | 0.0051815 | 1.6449e-05 | No
2019-12-18 | 8:00 | GL1233 | Short rural | Planned |  | 23 | 405 | 0.030645 | 7.5667e-05 | No
2019-12-18 | 8:00 | NG1299 | Short rural | Planned |  | 1 | 660 | 0.0021713 | 3.2899e-06 | No
2019-12-18 | 8:00 | 25784 | Urban | Planned |  | 34 | 420 | 0.019055 | 4.537e-05 | No
2019-12-18 | 8:00 | C896 | Urban | Planned |  | 1 | 435 | 0.00058046 | 1.3344e-06 | No
2019-12-17 | 2:00 | WM1142 | Urban | Planned |  | 88 | 60 | 0.0070456 | 0.00011743 | No
2019-12-18 | 8:00 | KMD2 | Short rural | Planned |  | 7 | 450 | 0.010363 | 2.3029e-05 | No
2019-12-18 | 8:00 | 87218 | Short rural | Planned |  | 6 | 375 | 0.0074022 | 1.9739e-05 | No
2019-12-18 | 8:30 | BDF2 | Short rural | Planned |  | 36 | 340 | 0.040268 | 0.00011844 | No
2019-12-18 | 8:00 | S735 | Short rural | Planned |  | 15 | 370 | 0.018259 | 4.9348e-05 | No
2019-12-18 | 8:30 | BYC2 | Short rural | Planned |  | 32 | 303 | 0.031899 | 0.00010528 | No
2019-12-18 | 7:30 | KMC2 | Short rural | Planned |  | 19 | 510 | 0.031879 | 6.2507e-05 | No
2019-12-18 | 8:00 | NM1236 | Urban | Planned |  | 43 | 270 | 0.015492 | 5.7379e-05 | No
2019-12-18 | 8:00 | MVC2 | Short rural | Planned |  | 11 | 175 | 0.006333 | 3.6188e-05 | No
2019-12-18 | 8:30 | WRF2 | Short rural | Planned |  | 69 | 10 | 0.00227 | 0.000227 | No
2019-12-18 | 8:30 | A046 | Short rural | Planned |  | 6 | 90 | 0.0017765 | 1.9739e-05 | No
2019-12-18 | 8:00 | UNF2 | Urban | Planned |  | 79 | 90 | 0.0094876 | 0.00010542 | No
2019-12-18 | 8:30 | ULE2 | Short rural | Planned |  | 7 | 527 | 0.012136 | 2.3029e-05 | No
2019-12-19 | 8:30 | 27031 | Urban | Planned |  | 13 | 420 | 0.0072858 | 1.7347e-05 | No
2019-12-19 | 8:00 | MR2205 | Short rural | Planned |  | 1 | 540 | 0.0017765 | 3.2899e-06 | No
2019-12-19 | 8:30 | DP1206 | Urban | Planned |  | 43 | 135 | 0.0077462 | 5.7379e-05 | No
2019-12-19 | 9:30 | ULC2 | Short rural | Planned |  | 164 | 240 | 0.12949 | 0.00053954 | No
2019-12-19 | 7:30 | WL1236 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2019-12-19 | 8:30 | APB2 | Short rural | Planned |  | 176 | 420 | 0.24319 | 0.00057902 | No
2019-12-19 | 8:00 | SWC2 | Urban | Planned |  | 77 | 415 | 0.042641 | 0.00010275 | No
2019-12-19 | 8:00 | 27029 | Short rural | Planned |  | 18 | 480 | 0.028424 | 5.9218e-05 | No
2019-12-20 | 8:00 | 35696 | Short rural | Planned |  | 79 | 480 | 0.12475 | 0.0002599 | No
2019-12-20 | 10:00 | J496 | Urban | Planned |  | 3 | 350 | 0.0014011 | 4.0032e-06 | No
2019-12-20 | 7:30 | J504 | Urban | Planned |  | 110 | 460 | 0.067521 | 0.00014678 | No
2019-12-20 | 8:00 | SZ1112 | Urban | Planned |  | 19 | 235 | 0.0059581 | 2.5354e-05 | No
2019-12-20 | 8:00 | NK1332 | Urban | Planned |  | 63 | 435 | 0.036569 | 8.4067e-05 | No
2019-12-20 | 6:45 | NWG2 | Urban | Planned |  | 5 | 10 | 6.672e-05 | 6.672e-06 | No
2019-12-20 | 8:30 | DP1221 | Short rural | Planned |  | 161 | 140 | 0.074154 | 0.00052967 | No
2019-12-20 | 8:30 | ULJ2 | Urban | Planned |  | 146 | 379 | 0.073838 | 0.00019482 | No
2019-12-20 | 8:00 | MR2205 | Short rural | Planned |  | 6 | 540 | 0.010659 | 1.9739e-05 | No
2019-12-20 | 8:00 | 35388 | Urban | Planned |  | 95 | 300 | 0.03803 | 0.00012677 | No
2019-12-20 | 7:00 | NWG2 | Urban | Planned |  | 8 | 5 | 5.3376e-05 | 1.0675e-05 | No
2019-12-21 | 8:00 | MVF2 | Short rural | Planned |  | 6 | 180 | 0.0035531 | 1.9739e-05 | No
2019-12-21 | 8:00 | MYB2 | Urban | Planned |  | 1 | 465 | 0.0006205 | 1.3344e-06 | No
2019-12-22 | 8:00 | MYK2 | Urban | Planned |  | 6 | 250 | 0.0020016 | 8.0064e-06 | No
2019-12-22 | 8:00 | CA1213 | Urban | Planned |  | 4 | 480 | 0.002562 | 5.3376e-06 | No
2019-12-23 | 6:00 | 7972 | Urban | Planned |  | 2 | 325 | 0.00086736 | 2.6688e-06 | No
2019-12-23 | 8:00 | WBD2 | Short rural | Planned |  | 16 | 480 | 0.025266 | 5.2638e-05 | No
2019-12-23 | 8:00 | B745 | Urban | Planned |  | 21 | 380 | 0.010649 | 2.8022e-05 | No
2019-12-29 | 6:00 | B745 | Urban | Planned |  | 54 | 50 | 0.0036029 | 7.2058e-05 | No
2019-12-29 | 11:00 | 9017 | Urban | Planned |  | 19 | 285 | 0.0072258 | 2.5354e-05 | No
2019-12-31 | 6:00 | PH1230 | Urban | Planned |  | 1 | 75 | 0.00010008 | 1.3344e-06 | No
2020-01-03 | 8:00 | B776 | Urban | Planned |  | 16 | 480 | 0.010248 | 2.135e-05 | No
2020-01-09 | 8:00 | 9034 | Urban | Planned |  | 86 | 530 | 0.060822 | 0.00011476 | No
2020-01-09 | 8:00 | 49337 | Urban | Planned |  | 62 | 540 | 0.044676 | 8.2733e-05 | No
2020-01-09 | 8:00 | 49337 | Urban | Planned |  | 2 | 540 | 0.0014412 | 2.6688e-06 | No
2020-01-10 | 10:30 | B215 | Urban | Planned |  | 2 | 90 | 0.00024019 | 2.6688e-06 | No
2020-01-12 | 6:30 | NWE2 | Urban | Planned |  | 17 | 555 | 0.01259 | 2.2685e-05 | No
2020-01-13 | 8:00 | WWB2 | Short rural | Planned |  | 227 | 480 | 0.35846 | 0.0007468 | No
2020-01-13 | 8:00 | 87222 | Long rural | Planned |  | 59 | 480 | 90.1911 | 0.1879 | No
2020-01-13 | 7:30 | J489 | Urban | Planned |  | 57 | 155 | 0.011789 | 7.6061e-05 | No
2020-01-14 | 8:00 | MM1162 | Urban | Planned |  | 64 | 450 | 0.038431 | 8.5402e-05 | No
2020-01-14 | 8:00 | X881 | Short rural | Planned |  | 66 | 470 | 0.10205 | 0.00021713 | No
2020-01-14 | 8:30 | CR1280 | Urban | Planned |  | 2 | 480 | 0.001281 | 2.6688e-06 | No
2020-01-14 | 8:00 | 19857 | Urban | Planned |  | 276 | 480 | 0.17678 | 0.00036829 | No
2020-01-15 | 8:00 | 25744 | Short rural | Planned |  | 2 | 105 | 0.00069087 | 6.5797e-06 | No
2020-01-15 | 8:00 | B776 | Urban | Planned |  | 20 | 480 | 0.01281 | 2.6688e-05 | No
2020-01-15 | 9:30 | J497 | Short rural | Planned |  | 63 | 340 | 0.070469 | 0.00020726 | No
2020-01-15 | 7:30 | J500 | Urban | Planned |  | 27 | 470 | 0.016934 | 3.6029e-05 | No
2020-01-15 | 8:00 | WD1258 | Urban | Planned |  | 96 | 410 | 0.052522 | 0.0001281 | No
2020-01-15 | 8:00 | MVB2 | Short rural | Planned |  | 61 | 415 | 0.083283 | 0.00020068 | No
2020-01-15 | 7:30 | X866 | Urban | Planned |  | 106 | 240 | 0.033947 | 0.00014145 | No
2020-01-16 | 8:00 | 7981 | Urban | Planned |  | 27 | 480 | 0.017294 | 3.6029e-05 | No
2020-01-16 | 7:30 | X870 | Urban | Planned |  | 29 | 240 | 0.0092874 | 3.8698e-05 | No
2020-01-16 | 8:00 | CT1206 | Urban | Planned |  | 16 | 270 | 0.0057646 | 2.135e-05 | No
2020-01-16 | 8:30 | WRC2 | Short rural | Planned |  | 51 | 210 | 0.035234 | 0.00016778 | No
2020-01-16 | 8:00 | CA1210 | Urban | Planned |  | 53 | 600 | 0.042434 | 7.0723e-05 | No
2020-01-17 | 8:00 | HR1247 | Urban | Planned |  | 102 | 480 | 0.065332 | 0.00013611 | No
2020-01-17 | 7:30 | HR1269 | Urban | Planned |  | 45 | 480 | 0.028823 | 6.0048e-05 | No
2020-01-17 | 8:00 | S740 | Urban | Planned |  | 90 | 240 | 0.028823 | 0.0001201 | No
2020-01-17 | 8:00 | 46397 | Urban | Planned |  | 40 | 400 | 0.02135 | 5.3376e-05 | No
2020-01-17 | 8:00 | 19856 | Urban | Planned |  | 227 | 460 | 0.13934 | 0.00030291 | No
2020-01-17 | 7:00 | MM1202 | Urban | Planned |  | 1 | 465 | 0.0006205 | 1.3344e-06 | No
2020-01-18 | 8:00 | OP1112 | Short rural | Planned |  | 8 | 215 | 0.0056586 | 2.6319e-05 | No
2020-01-18 | 7:00 | SZ1132 | Urban | Planned |  | 32 | 535 | 0.022845 | 4.2701e-05 | No
2020-01-19 | 9:00 | 35773 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-01-19 | 7:00 | 35769 | Urban | Planned |  | 18 | 508 | 0.012202 | 2.4019e-05 | No
2020-01-19 | 7:00 | A048 | Urban | Planned |  | 12 | 445 | 0.0071257 | 1.6013e-05 | No
2020-01-20 | 8:00 | A045 | Short rural | Planned |  | 56 | 440 | 0.081062 | 0.00018423 | No
2020-01-20 | 8:00 | SY1352 | Urban | Planned |  | 73 | 210 | 0.020456 | 9.7411e-05 | No
2020-01-20 | 8:00 | BL1243 | Short rural | Planned |  | 141 | 340 | 0.15772 | 0.00046387 | No
2020-01-20 | 6:00 | 10248 | Urban | Planned |  | 7 | 150 | 0.0014011 | 9.3408e-06 | No
2020-01-20 | 8:00 | 87220 | Short rural | Planned |  | 1 | 45 | 0.00014804 | 3.2899e-06 | No
2020-01-20 | 8:00 | 87220 | Short rural | Planned |  | 1 | 115 | 0.00037833 | 3.2899e-06 | No
2020-01-20 | 8:00 | 87220 | Short rural | Planned |  | 1 | 65 | 0.00021384 | 3.2899e-06 | No
2020-01-23 | 2:00 | J465 | Urban | Planned |  | 67 | 360 | 0.032186 | 8.9405e-05 | No
2020-01-20 | 8:00 | 87220 | Short rural | Planned |  | 1 | 85 | 0.00027964 | 3.2899e-06 | No
2020-01-21 | 7:30 | 16653 | Urban | Planned |  | 5 | 150 | 0.0010008 | 6.672e-06 | No
2020-01-21 | 8:00 | HS1242 | Urban | Planned |  | 22 | 509 | 0.014943 | 2.9357e-05 | No
2020-01-21 | 8:00 | CR1228 | Urban | Planned |  | 220 | 490 | 0.14385 | 0.00029357 | No
2020-01-21 | 8:00 | 1952 | Urban | Planned |  | 52 | 435 | 0.030184 | 6.9389e-05 | No
2020-01-21 | 8:00 | BWA2 | Short rural | Planned |  | 106 | 450 | 0.15693 | 0.00034873 | No
2020-01-21 | 8:00 | 19857 | Urban | Planned |  | 428 | 422 | 0.24101 | 0.00057112 | No
2020-01-21 | 8:30 | DP1269 | Urban | Planned |  | 59 | 360 | 0.028343 | 7.873e-05 | No
2020-01-21 | 8:00 | B217 | Urban | Planned |  | 13 | 480 | 0.0083267 | 1.7347e-05 | No
2020-01-21 | 8:30 | WRB2 | Urban | Planned |  | 104 | 135 | 0.018735 | 0.00013878 | No
2020-01-21 | 8:30 | ULL2 | Short rural | Planned |  | 403 | 420 | 0.55684 | 0.0013258 | No
2020-01-22 | 8:00 | MR2205 | Short rural | Planned |  | 1 | 540 | 0.0017765 | 3.2899e-06 | No
2020-01-22 | 8:00 | SC1253 | Short rural | Planned |  | 12 | 300 | 0.011844 | 3.9478e-05 | No
2020-01-22 | 8:00 | 8648 | Urban | Planned |  | 16 | 395 | 0.0084334 | 2.135e-05 | No
2020-01-22 | 8:00 | MR2205 | Short rural | Planned |  | 1 | 510 | 0.0016778 | 3.2899e-06 | No
2020-01-22 | 8:30 | YYA2 | Short rural | Planned |  | 45 | 360 | 0.053296 | 0.00014804 | No
2020-01-22 | 8:00 | X217 | Short rural | Planned |  | 8 | 360 | 0.0094748 | 2.6319e-05 | No
2020-01-22 | 8:00 | PH1286 | Urban | Planned |  | 63 | 465 | 0.039091 | 8.4067e-05 | No
2020-01-22 | 8:30 | APD2 | Short rural | Planned |  | 151 | 370 | 0.1838 | 0.00049677 | No
2020-01-22 | 8:00 | 35418 | Short rural | Planned |  | 10 | 348 | 0.011449 | 3.2899e-05 | No
2020-01-22 | 8:00 | MR2206 | Urban | Planned |  | 76 | 450 | 0.045636 | 0.00010141 | No
2020-01-22 | 8:00 | WL1292 | Urban | Planned |  | 84 | 350 | 0.039231 | 0.00011209 | No
2020-01-22 | 8:00 | S735 | Short rural | Planned |  | 21 | 260 | 0.017963 | 6.9087e-05 | No
2020-01-22 | 8:00 | 61617 | Short rural | Planned |  | 31 | 255 | 0.026006 | 0.00010199 | No
2020-01-22 | 7:30 | WT1252 | Short rural | Planned |  | 136 | 570 | 0.25503 | 0.00044742 | No
2020-01-23 | 7:00 | GV1286 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2020-01-23 | 8:00 | SZ1122 | Short rural | Planned |  | 2 | 518 | 0.0034083 | 6.5797e-06 | No
2020-01-23 | 8:00 | OA1233 | Short rural | Planned |  | 14 | 274 | 0.01262 | 4.6058e-05 | No
2020-01-23 | 8:00 | CR1262 | Urban | Planned |  | 75 | 195 | 0.019516 | 0.00010008 | No
2020-01-23 | 8:30 | DP1269 | Urban | Planned |  | 122 | 255 | 0.041513 | 0.0001628 | No
2020-01-23 | 6:00 | M169 | Urban | Planned |  | 51 | 930 | 0.063291 | 6.8054e-05 | No
2020-01-23 | 9:00 | APB2 | Short rural | Planned |  | 66 | 435 | 0.094452 | 0.00021713 | No
2020-01-23 | 8:00 | S786 | Short rural | Planned |  | 23 | 195 | 0.014755 | 7.5667e-05 | No
2020-01-24 | 8:00 | X867 | Urban | Planned |  | 42 | 240 | 0.013451 | 5.6045e-05 | No
2020-01-24 | 8:00 | 4866 | Urban | Planned |  | 18 | 270 | 0.0064852 | 2.4019e-05 | No
2020-01-24 | 8:00 | 48198 | Urban | Planned |  | 4 | 490 | 0.0026154 | 5.3376e-06 | No
2020-01-28 | 8:30 | DP1258 | Short rural | Planned |  | 157 | 205 | 0.10588 | 0.00051651 | No
2020-01-28 | 8:00 | DP1221 | Short rural | Planned |  | 3 | 400 | 0.0039478 | 9.8696e-06 | No
2020-01-28 | 8:00 | T889 | Urban | Planned |  | 65 | 255 | 0.022118 | 8.6736e-05 | No
2020-01-28 | 8:00 | CS1247 | Urban | Planned |  | 37 | 540 | 0.026661 | 4.9373e-05 | No
2020-01-28 | 8:00 | S737 | Short rural | Planned |  | 14 | 570 | 0.026253 | 4.6058e-05 | No
2020-01-28 | 8:00 | NM1258 | Urban | Planned |  | 27 | 360 | 0.01297 | 3.6029e-05 | No
2020-01-28 | 7:30 | J502 | Urban | Planned |  | 132 | 330 | 0.058126 | 0.00017614 | No
2020-01-28 | 8:00 | WBD2 | Short rural | Planned |  | 16 | 205 | 0.010791 | 5.2638e-05 | No
2020-01-28 | 8:00 | NL1182 | Urban | Planned |  | 24 | 255 | 0.0081665 | 3.2026e-05 | No
2020-01-28 | 8:00 | 1957 | Urban | Planned |  | 88 | 270 | 0.031705 | 0.00011743 | No
2020-01-29 | 6:00 | APB2 | Short rural | Planned |  | 2 | 780 | 0.0051322 | 6.5797e-06 | No
2020-01-29 | 8:00 | 46395 | Urban | Planned |  | 65 | 480 | 0.041633 | 8.6736e-05 | No
2020-01-29 | 7:30 | 17061 | Urban | Planned |  | 6 | 540 | 0.0043235 | 8.0064e-06 | No
2020-01-29 | 8:00 | PK1236 | Short rural | Planned |  | 3 | 480 | 0.0047374 | 9.8696e-06 | No
2020-01-29 | 8:00 | J481 | Urban | Planned |  | 87 | 570 | 0.066173 | 0.00011609 | No
2020-01-29 | 8:00 | B776 | Urban | Planned |  | 26 | 480 | 0.016653 | 3.4694e-05 | No
2020-01-29 | 8:00 | X217 | Short rural | Planned |  | 8 | 280 | 0.0073693 | 2.6319e-05 | No
2020-01-29 | 8:00 | S735 | Short rural | Planned |  | 32 | 375 | 0.039478 | 0.00010528 | No
2020-01-29 | 7:30 | B743 | Urban | Planned |  | 17 | 475 | 0.010775 | 2.2685e-05 | No
2020-01-29 | 8:00 | SY1132 | Urban | Planned |  | 388 | 470 | 0.24334 | 0.00051775 | No
2020-01-29 | 8:00 | 8690 | Urban | Planned |  | 141 | 350 | 0.065853 | 0.00018815 | No
2020-01-30 | 8:00 | OP1262 | Short rural | Planned |  | 35 | 490 | 0.056421 | 0.00011515 | No
2020-01-30 | 8:00 | WD1225 | Short rural | Planned |  | 59 | 480 | 0.093169 | 0.0001941 | No
2020-01-30 | 8:00 | MVF2 | Short rural | Planned |  | 16 | 375 | 0.019739 | 5.2638e-05 | No
2020-01-30 | 8:00 | 41537 | Urban | Planned |  | 118 | 415 | 0.065346 | 0.00015746 | No
2020-01-30 | 7:00 | CR1280 | Urban | Planned |  | 84 | 630 | 0.070616 | 0.00011209 | No
2020-01-30 | 8:00 | CT1265 | Urban | Planned |  | 203 | 630 | 0.17066 | 0.00027088 | No
2020-01-30 | 9:00 | T894 | Urban | Planned |  | 35 | 155 | 0.0072391 | 4.6704e-05 | No
2020-01-30 | 8:00 | T842 | Short rural | Planned |  | 5 | 240 | 0.0039478 | 1.6449e-05 | No
2020-01-30 | 9:00 | J474 | Short rural | Planned |  | 71 | 450 | 0.10511 | 0.00023358 | No
2020-01-30 | 8:00 | MVB2 | Short rural | Planned |  | 136 | 435 | 0.19463 | 0.00044742 | No
2020-01-30 | 8:00 | 8767 | Urban | Planned |  | 42 | 420 | 0.023539 | 5.6045e-05 | No
2020-01-30 | 8:00 | APC2 | Short rural | Planned |  | 21 | 540 | 0.037307 | 6.9087e-05 | No
2020-01-30 | 8:00 | SHJ2 | Urban | Planned |  | 57 | 456 | 0.034684 | 7.6061e-05 | No
2020-01-30 | 8:00 | CV1239 | Urban | Planned |  | 21 | 635 | 0.017794 | 2.8022e-05 | No
2020-01-30 | 9:00 | APC2 | Short rural | Planned |  | 8 | 420 | 0.011054 | 2.6319e-05 | No
2020-01-30 | 8:30 | DP1295 | Urban | Planned |  | 163 | 360 | 0.078303 | 0.00021751 | No
2020-01-31 | 8:00 | 4866 | Urban | Planned |  | 26 | 480 | 0.016653 | 3.4694e-05 | No
2020-01-31 | 8:00 | CX1210 | Short rural | Planned |  | 4 | 205 | 0.0026977 | 1.3159e-05 | No
2020-01-31 | 8:00 | 8651 | Urban | Planned |  | 280 | 431 | 0.16104 | 0.00037363 | No
2020-01-31 | 8:00 | PH1201 | Urban | Planned |  | 44 | 247 | 0.014502 | 5.8714e-05 | No
2020-01-31 | 8:00 | B715 | Urban | Planned |  | 144 | 240 | 0.046117 | 0.00019215 | No
2020-01-31 | 8:00 | APB2 | Short rural | Planned |  | 222 | 360 | 0.26293 | 0.00073035 | No
2020-01-31 | 8:00 | 35816 | Short rural | Planned |  | 91 | 380 | 0.11376 | 0.00029938 | No
2020-01-31 | 8:00 | W163 | Short rural | Planned |  | 5 | 300 | 0.0049348 | 1.6449e-05 | No
2020-01-31 | 8:00 | L582 | Short rural | Planned |  | 4 | 215 | 0.0028293 | 1.3159e-05 | No
2020-02-01 | 8:00 | 19857 | Urban | Planned |  | 3 | 240 | 0.00096077 | 4.0032e-06 | No
2020-02-01 | 8:00 | MVF2 | Short rural | Planned |  | 7 | 180 | 0.0041452 | 2.3029e-05 | No
2020-02-01 | 6:00 | 10248 | Urban | Planned |  | 7 | 105 | 0.00098078 | 9.3408e-06 | No
2020-02-01 | 8:00 | MYP2 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2020-02-01 | 8:00 | 49916 | Urban | Planned |  | 59 | 480 | 0.03779 | 7.873e-05 | No
2020-02-01 | 8:00 | C833 | Urban | Planned |  | 196 | 135 | 0.035308 | 0.00026154 | No
2020-02-01 | 8:30 | WL1251 | Urban | Planned |  | 21 | 435 | 0.01219 | 2.8022e-05 | No
2020-02-02 | 8:00 | C812 | Short rural | Planned |  | 22 | 290 | 0.020989 | 7.2377e-05 | No
2020-02-02 | 8:00 | RS1203 | Urban | Planned |  | 35 | 465 | 0.021717 | 4.6704e-05 | No
2020-02-02 | 8:00 | CR1254 | Urban | Planned |  | 62 | 367 | 0.030363 | 8.2733e-05 | No
2020-02-03 | 8:00 | L941 | Short rural | Planned |  | 19 | 450 | 0.028128 | 6.2507e-05 | No
2020-02-03 | 8:00 | CR1262 | Urban | Planned |  | 261 | 185 | 0.064431 | 0.00034828 | No
2020-02-03 | 8:00 | 87220 | Short rural | Planned |  | 1 | 400 | 0.0013159 | 3.2899e-06 | No
2020-02-03 | 8:30 | BDG2 | Short rural | Planned |  | 4 | 417 | 0.0054875 | 1.3159e-05 | No
2020-02-03 | 8:00 | 87220 | Short rural | Planned |  | 1 | 110 | 0.00036188 | 3.2899e-06 | No
2020-02-03 | 8:00 | 87220 | Short rural | Planned |  | 1 | 160 | 0.00052638 | 3.2899e-06 | No
2020-02-03 | 8:30 | SXC2 | Short rural | Planned |  | 40 | 165 | 0.021713 | 0.00013159 | No
2020-02-03 | 8:00 | 87220 | Short rural | Planned |  | 1 | 100 | 0.00032899 | 3.2899e-06 | No
2020-02-04 | 8:30 | ULE2 | Short rural | Planned |  | 10 | 390 | 0.01283 | 3.2899e-05 | No
2020-02-04 | 11:00 | S766 | Urban | Planned |  | 117 | 170 | 0.026541 | 0.00015612 | No
2020-02-04 | 7:00 | S765 | Urban | Planned |  | 12 | 170 | 0.0027222 | 1.6013e-05 | No
2020-02-04 | 9:00 | BYB2 | Short rural | Planned |  | 1 | 180 | 0.00059218 | 3.2899e-06 | No
2020-02-04 | 8:30 | DP1258 | Short rural | Planned |  | 136 | 425 | 0.19015 | 0.00044742 | No
2020-02-04 | 8:00 | CR1210 | Urban | Planned |  | 55 | 440 | 0.032292 | 7.3392e-05 | No
2020-02-04 | 8:00 | S764 | Short rural | Planned |  | 6 | 540 | 0.010659 | 1.9739e-05 | No
2020-02-04 | 8:00 | FT1207 | Urban | Planned |  | 148 | 135 | 0.026661 | 0.00019749 | No
2020-02-04 | 8:00 | 10250 | Short rural | Planned |  | 51 | 460 | 0.07718 | 0.00016778 | No
2020-02-04 | 8:00 | NM1221 | Urban | Planned |  | 140 | 420 | 0.078463 | 0.00018682 | No
2020-02-04 | 7:30 | WL1217 | Urban | Planned |  | 147 | 385 | 0.07552 | 0.00019616 | No
2020-02-04 | 8:30 | BDE2 | Urban | Planned |  | 191 | 380 | 0.096851 | 0.00025487 | No
2020-02-04 | 8:00 | M399 | Short rural | Planned |  | 116 | 400 | 0.15265 | 0.00038162 | No
2020-02-05 | 8:30 | ULL2 | Short rural | Planned |  | 324 | 392 | 0.41784 | 0.0010659 | No
2020-02-05 | 8:00 | CV1247 | Urban | Planned |  | 36 | 480 | 0.023058 | 4.8038e-05 | No
2020-02-05 | 10:00 | A317 | Urban | Planned |  | 17 | 45 | 0.0010208 | 2.2685e-05 | No
2020-02-05 | 8:00 | MVB2 | Short rural | Planned |  | 18 | 465 | 0.027536 | 5.9218e-05 | No
2020-02-05 | 8:00 | 9034 | Urban | Planned |  | 74 | 560 | 0.055297 | 9.8746e-05 | No
2020-02-05 | 8:00 | SHD2 | Short rural | Planned |  | 51 | 420 | 0.070469 | 0.00016778 | No
2020-02-05 | 8:00 | BWB2 | Urban | Planned |  | 74 | 540 | 0.053323 | 9.8746e-05 | No
2020-02-05 | 7:30 | 9059 | Urban | Planned |  | 73 | 530 | 0.051628 | 9.7411e-05 | No
2020-02-05 | 8:00 | JS1252 | Short rural | Planned |  | 31 | 420 | 0.042834 | 0.00010199 | No
2020-02-05 | 11:00 | CR1228 | Urban | Planned |  | 22 | 90 | 0.0026421 | 2.9357e-05 | No
2020-02-05 | 8:00 | 10251 | Urban | Planned |  | 56 | 315 | 0.023539 | 7.4726e-05 | No
2020-02-05 | 8:00 | 8690 | Urban | Planned |  | 149 | 390 | 0.077542 | 0.00019883 | No
2020-02-05 | 8:00 | BWB2 | Urban | Planned |  | 6 | 570 | 0.0045636 | 8.0064e-06 | No
2020-02-05 | 8:00 | B217 | Urban | Planned |  | 220 | 210 | 0.061649 | 0.00029357 | No
2020-02-05 | 8:00 | 10251 | Urban | Planned |  | 66 | 450 | 0.039632 | 8.807e-05 | No
2020-02-05 | 8:30 | WRB2 | Urban | Planned |  | 285 | 145 | 0.055144 | 0.0003803 | No
2020-02-05 | 7:00 | 9025 | Urban | Planned |  | 20 | 150 | 0.0040032 | 2.6688e-05 | No
2020-02-05 | 8:00 | 19857 | Urban | Planned |  | 64 | 330 | 0.028183 | 8.5402e-05 | No
2020-02-05 | 8:00 | 35418 | Short rural | Planned |  | 10 | 338 | 0.01112 | 3.2899e-05 | No
2020-02-05 | 6:00 | 68190 | Urban | Planned |  | 1 | 660 | 0.0008807 | 1.3344e-06 | No
2020-02-05 | 8:00 | APE2 | Short rural | Planned |  | 12 | 385 | 0.015199 | 3.9478e-05 | No
2020-02-06 | 7:00 | PH1264 | Urban | Planned |  | 7 | 455 | 0.0042501 | 9.3408e-06 | No
2020-02-06 | 8:00 | CX1210 | Short rural | Planned |  | 47 | 265 | 0.040975 | 0.00015462 | No
2020-02-06 | 7:30 | J496 | Urban | Planned |  | 108 | 465 | 0.067014 | 0.00014412 | No
2020-02-06 | 8:00 | NWB2 | Urban | Planned |  | 21 | 570 | 0.015973 | 2.8022e-05 | No
2020-02-06 | 8:00 | S735 | Short rural | Planned |  | 10 | 301 | 0.0099025 | 3.2899e-05 | No
2020-02-06 | 8:30 | BDE2 | Urban | Planned |  | 191 | 405 | 0.10322 | 0.00025487 | No
2020-02-06 | 8:00 | T834 | Short rural | Planned |  | 1 | 262 | 0.00086194 | 3.2899e-06 | No
2020-02-06 | 7:00 | S788 | Short rural | Planned |  | 1 | 155 | 0.00050993 | 3.2899e-06 | No
2020-02-06 | 8:00 | CR1214 | Urban | Planned |  | 118 | 435 | 0.068495 | 0.00015746 | No
2020-02-06 | 8:00 | S735 | Short rural | Planned |  | 30 | 555 | 0.054776 | 9.8696e-05 | No
2020-02-06 | 8:00 | CX1284 | Short rural | Planned |  | 30 | 315 | 0.031089 | 9.8696e-05 | No
2020-02-06 | 7:30 | 9056 | Urban | Planned |  | 57 | 480 | 0.036509 | 7.6061e-05 | No
2020-02-07 | 11:00 | 25777 | Urban | Planned |  | 7 | 120 | 0.0011209 | 9.3408e-06 | No
2020-02-07 | 8:00 | NWA2 | Urban | Planned |  | 67 | 480 | 0.042914 | 8.9405e-05 | No
2020-02-07 | 8:30 | APC2 | Short rural | Planned |  | 173 | 420 | 0.23904 | 0.00056915 | No
2020-02-07 | 8:00 | 27194 | Urban | Planned |  | 10 | 420 | 0.0056045 | 1.3344e-05 | No
2020-02-07 | 8:30 | DP1258 | Short rural | Planned |  | 37 | 330 | 0.040169 | 0.00012172 | No
2020-02-07 | 7:30 | 8610 | Urban | Planned |  | 6 | 245 | 0.0019616 | 8.0064e-06 | No
2020-02-08 | 8:00 | W112 | Short rural | Planned |  | 4 | 15 | 0.00019739 | 1.3159e-05 | No
2020-02-09 | 8:00 | MM1112 | Urban | Planned |  | 6 | 480 | 0.0038431 | 8.0064e-06 | Yes
2020-02-09 | 7:00 | GV1245 | Urban | Planned |  | 52 | 660 | 0.045797 | 6.9389e-05 | Yes
2020-02-11 | 8:30 | NA1207 | Short rural | Planned |  | 6 | 290 | 0.0057244 | 1.9739e-05 | No
2020-02-11 | 8:30 | BYG2 | Short rural | Planned |  | 26 | 145 | 0.012403 | 8.5536e-05 | No
2020-02-11 | 8:00 | APG2 | Urban | Planned |  | 165 | 420 | 0.092474 | 0.00022018 | No
2020-02-11 | 8:00 | 9032 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-02-12 | 8:00 | C889 | Urban | Planned |  | 12 | 360 | 0.0057646 | 1.6013e-05 | No
2020-02-12 | 8:00 | W188 | Short rural | Planned |  | 3 | 420 | 0.0041452 | 9.8696e-06 | No
2020-02-12 | 7:30 | J472 | Urban | Planned |  | 119 | 280 | 0.044462 | 0.00015879 | No
2020-02-12 | 7:30 | J472 | Urban | Planned |  | 242 | 210 | 0.067814 | 0.00032292 | No
2020-02-12 | 8:00 | 19816 | Urban | Planned |  | 61 | 620 | 0.050467 | 8.1398e-05 | No
2020-02-12 | 8:30 | KMA2 | Short rural | Planned |  | 281 | 305 | 0.28196 | 0.00092445 | No
2020-02-12 | 8:00 | 19816 | Urban | Planned |  | 63 | 540 | 0.045396 | 8.4067e-05 | No
2020-02-12 | 8:00 | OP1262 | Short rural | Planned |  | 26 | 480 | 0.041057 | 8.5536e-05 | No
2020-02-12 | 8:00 | MG1267 | Short rural | Planned |  | 31 | 520 | 0.053033 | 0.00010199 | No
2020-02-13 | 7:30 | AB1246 | Urban | Planned |  | 102 | 210 | 0.028583 | 0.00013611 | No
2020-02-13 | 8:00 | RW1218 | Short rural | Planned |  | 49 | 495 | 0.079796 | 0.0001612 | No
2020-02-13 | 11:00 | 87220 | Short rural | Planned |  | 1 | 210 | 0.00069087 | 3.2899e-06 | No
2020-02-13 | 8:00 | OP1282 | Urban | Planned |  | 21 | 480 | 0.013451 | 2.8022e-05 | No
2020-02-13 | 8:00 | 76225 | Short rural | Planned |  | 12 | 510 | 0.020134 | 3.9478e-05 | No
2020-02-13 | 11:00 | 87220 | Short rural | Planned |  | 2 | 175 | 0.0011515 | 6.5797e-06 | No
2020-02-13 | 8:30 | APB2 | Short rural | Planned |  | 297 | 570 | 0.55694 | 0.00097709 | No
2020-02-13 | 6:00 | 8611 | Urban | Planned |  | 46 | 150 | 0.0092074 | 6.1382e-05 | No
2020-02-14 | 9:00 | 25782 | Urban | Planned |  | 102 | 95 | 0.01293 | 0.00013611 | No
2020-02-14 | 8:00 | CR1262 | Urban | Planned |  | 165 | 480 | 0.10568 | 0.00022018 | No
2020-02-14 | 9:00 | RS1262 | Urban | Planned |  | 1 | 120 | 0.00016013 | 1.3344e-06 | No
2020-02-14 | 8:30 | KMB2 | Short rural | Planned |  | 104 | 420 | 0.1437 | 0.00034215 | No
2020-02-14 | 8:30 | ULL2 | Short rural | Planned |  | 69 | 170 | 0.03859 | 0.000227 | No
2020-02-14 | 8:00 | 8680 | Urban | Planned |  | 146 | 360 | 0.070136 | 0.00019482 | No
2020-02-14 | 8:00 | 87220 | Short rural | Planned |  | 1 | 180 | 0.00059218 | 3.2899e-06 | No
2020-02-14 | 8:30 | ULL2 | Short rural | Planned |  | 1 | 46 | 0.00015133 | 3.2899e-06 | No
2020-02-14 | 8:30 | NA1285 | Urban | Planned |  | 65 | 335 | 0.029057 | 8.6736e-05 | No
2020-02-14 | 8:00 | 8798 | Short rural | Planned |  | 50 | 275 | 0.045236 | 0.00016449 | No
2020-02-14 | 8:00 | 87220 | Short rural | Planned |  | 2 | 180 | 0.0011844 | 6.5797e-06 | No
2020-02-14 | 8:00 | 87220 | Short rural | Planned |  | 2 | 300 | 0.0019739 | 6.5797e-06 | No
2020-02-14 | 8:00 | X482 | Short rural | Planned |  | 1 | 50 | 0.00016449 | 3.2899e-06 | No
2020-02-14 | 8:30 | BDG2 | Short rural | Planned |  | 325 | 356 | 0.38064 | 0.0010692 | No
2020-02-14 | 9:00 | YYB2 | Short rural | Planned |  | 2 | 360 | 0.0023687 | 6.5797e-06 | No
2020-02-15 | 10:30 | C854 | Urban | Planned |  | 2 | 8 | 2.135e-05 | 2.6688e-06 | No
2020-02-15 | 6:30 | L508 | Urban | Planned |  | 3 | 525 | 0.0021017 | 4.0032e-06 | No
2020-02-15 | 8:00 | S764 | Short rural | Planned |  | 1 | 540 | 0.0017765 | 3.2899e-06 | No
2020-02-16 | 8:00 | SWE2 | Urban | Planned |  | 188 | 540 | 0.13547 | 0.00025087 | No
2020-02-16 | 7:00 | GV1245 | Urban | Planned |  | 54 | 660 | 0.047558 | 7.2058e-05 | No
2020-02-16 | 6:00 | A315 | Urban | Planned |  | 57 | 2703.1579 | 0.2056 | 7.6061e-05 | No
2020-02-16 | 8:00 | 8617 | Urban | Planned |  | 67 | 480 | 0.042914 | 8.9405e-05 | No
2020-02-16 | 8:00 | A315 | Urban | Planned |  | 157 | 817.8344 | 0.17134 | 0.0002095 | No
2020-02-17 | 8:30 | APH2 | Urban | Planned |  | 13 | 420 | 0.0072858 | 1.7347e-05 | No
2020-02-17 | 8:00 | DP1269 | Urban | Planned |  | 14 | 480 | 0.0089672 | 1.8682e-05 | No
2020-02-17 | 8:00 | 5495 | Urban | Planned |  | 55 | 450 | 0.033026 | 7.3392e-05 | No
2020-02-17 | 8:00 | 8617 | Urban | Planned |  | 52 | 290 | 0.020123 | 6.9389e-05 | No
2020-02-17 | 9:00 | CJ1249 | Urban | Planned |  | 23 | 390 | 0.01197 | 3.0691e-05 | No
2020-02-17 | 8:00 | BWA2 | Short rural | Planned |  | 85 | 490 | 0.13702 | 0.00027964 | No
2020-02-18 | 8:00 | WD1221 | Short rural | Planned |  | 87 | 285 | 0.081572 | 0.00028622 | Yes
2020-02-18 | 8:00 | BGA2 | Short rural | Planned |  | 79 | 390 | 0.10136 | 0.0002599 | Yes
2020-02-18 | 8:00 | 10250 | Short rural | Planned |  | 51 | 400 | 0.067113 | 0.00016778 | Yes
2020-02-18 | 6:00 | 4870 | Urban | Planned |  | 2 | 840 | 0.0022418 | 2.6688e-06 | Yes
2020-02-18 | 8:00 | 9032 | Short rural | Planned |  | 10 | 570 | 0.018752 | 3.2899e-05 | Yes
2020-02-18 | 8:00 | RV1246 | Short rural | Planned |  | 86 | 420 | 0.11883 | 0.00028293 | Yes
2020-02-18 | 8:30 | WRE2 | Urban | Planned |  | 333 | 365 | 0.16219 | 0.00044435 | Yes
2020-02-18 | 8:00 | RBE2 | Short rural | Planned |  | 24 | 270 | 0.021318 | 7.8957e-05 | Yes
2020-02-18 | 8:30 | KMF2 | Urban | Planned |  | 130 | 433 | 0.075113 | 0.00017347 | Yes
2020-02-18 | 8:00 | S764 | Short rural | Planned |  | 6 | 525 | 0.010363 | 1.9739e-05 | Yes
2020-02-18 | 8:30 | 25783 | Urban | Planned |  | 1 | 175 | 0.00023352 | 1.3344e-06 | Yes
2020-02-18 | 8:00 | 19857 | Urban | Planned |  | 67 | 450 | 0.040232 | 8.9405e-05 | Yes
2020-02-18 | 8:00 | MYG2 | Urban | Planned |  | 76 | 420 | 0.042594 | 0.00010141 | Yes
2020-02-18 | 7:30 | NL1132 | Urban | Planned |  | 35 | 480 | 0.022418 | 4.6704e-05 | Yes
2020-02-18 | 8:00 | HBA2 | Short rural | Planned |  | 21 | 574 | 0.039656 | 6.9087e-05 | Yes
2020-02-19 | 8:00 | 27194 | Urban | Planned |  | 10 | 420 | 0.0056045 | 1.3344e-05 | No
2020-02-19 | 8:00 | MG1267 | Short rural | Planned |  | 31 | 530 | 0.054052 | 0.00010199 | No
2020-02-19 | 8:30 | BDG2 | Short rural | Planned |  | 74 | 210 | 0.051124 | 0.00024345 | No
2020-02-19 | 8:00 | FT1207 | Urban | Planned |  | 148 | 250 | 0.049373 | 0.00019749 | No
2020-02-19 | 8:00 | BDC2 | Short rural | Planned |  | 20 | 400 | 0.026319 | 6.5797e-05 | No
2020-02-20 | 8:00 | RW1218 | Short rural | Planned |  | 24 | 500 | 0.039478 | 7.8957e-05 | No
2020-02-20 | 8:00 | CV1284 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2020-02-20 | 8:00 | 9046 | Urban | Planned |  | 14 | 480 | 0.0089672 | 1.8682e-05 | No
2020-02-20 | 8:00 | APD2 | Short rural | Planned |  | 2 | 700 | 0.0046058 | 6.5797e-06 | No
2020-02-21 | 8:00 | X877 | Short rural | Planned |  | 12 | 540 | 0.021318 | 3.9478e-05 | No
2020-02-21 | 8:30 | NA1270 | Short rural | Planned |  | 101 | 350 | 0.1163 | 0.00033228 | No
2020-02-21 | 8:30 | KME2 | Short rural | Planned |  | 14 | 300 | 0.013817 | 4.6058e-05 | No
2020-02-21 | 8:00 | X217 | Short rural | Planned |  | 2 | 320 | 0.0021055 | 6.5797e-06 | No
2020-02-21 | 9:00 | 35403 | Urban | Planned |  | 1 | 165 | 0.00022018 | 1.3344e-06 | No
2020-02-21 | 8:00 | 8798 | Short rural | Planned |  | 100 | 480 | 0.15791 | 0.00032899 | No
2020-02-22 | 6:00 | M160 | Urban | Planned |  | 2 | 550 | 0.0014678 | 2.6688e-06 | No
2020-02-22 | 10:00 | OA1233 | Short rural | Planned |  | 7 | 80 | 0.0018423 | 2.3029e-05 | No
2020-02-22 | 8:00 | CJ1249 | Urban | Planned |  | 48 | 180 | 0.011529 | 6.4051e-05 | No
2020-02-22 | 8:00 | 16653 | Urban | Planned |  | 125 | 430 | 0.071724 | 0.0001668 | No
2020-02-23 | 8:00 | PH1230 | Urban | Planned |  | 44 | 480 | 0.028183 | 5.8714e-05 | No
2020-02-23 | 7:00 | WX1218 | Urban | Planned |  | 23 | 780 | 0.023939 | 3.0691e-05 | No
2020-02-23 | 8:00 | PH1230 | Urban | Planned |  | 55 | 540 | 0.039632 | 7.3392e-05 | No
2020-02-24 | 8:00 | DP1295 | Urban | Planned |  | 1 | 410 | 0.0005471 | 1.3344e-06 | No
2020-02-24 | 9:00 | 7120 | Urban | Planned |  | 2 | 390 | 0.0010408 | 2.6688e-06 | No
2020-02-24 | 8:00 | 53807 | Short rural | Planned |  | 57 | 540 | 0.10126 | 0.00018752 | No
2020-02-24 | 8:00 | X217 | Short rural | Planned |  | 8 | 510 | 0.013423 | 2.6319e-05 | No
2020-02-24 | 8:00 | WL1299 | Urban | Planned |  | 1 | 510 | 0.00068054 | 1.3344e-06 | No
2020-02-24 | 8:30 | KYH2 | Urban | Planned |  | 25 | 450 | 0.015012 | 3.336e-05 | No
2020-02-25 | 7:30 | AB1223 | Urban | Planned |  | 22 | 480 | 0.014091 | 2.9357e-05 | No
2020-02-25 | 8:00 | 55879 | Urban | Planned |  | 76 | 350 | 0.035495 | 0.00010141 | No
2020-02-25 | 7:30 | LP1422 | Urban | Planned |  | 112 | 570 | 0.085188 | 0.00014945 | No
2020-02-25 | 8:00 | BYE2 | Short rural | Planned |  | 8 | 485 | 0.012765 | 2.6319e-05 | No
2020-02-25 | 8:00 | ULH2 | Short rural | Planned |  | 25 | 405 | 0.03331 | 8.2247e-05 | No
2020-02-25 | 8:00 | NM1221 | Urban | Planned |  | 71 | 375 | 0.035528 | 9.4742e-05 | No
2020-02-25 | 7:30 | 68204 | Urban | Planned |  | 81 | 280 | 0.030264 | 0.00010809 | No
2020-02-25 | 8:00 | RW1292 | Short rural | Planned |  | 19 | 450 | 0.028128 | 6.2507e-05 | No
2020-02-25 | 8:30 | BDF2 | Short rural | Planned |  | 34 | 450 | 0.050335 | 0.00011186 | No
2020-02-25 | 10:00 | B716 | Urban | Planned |  | 131 | 125 | 0.021851 | 0.00017481 | No
2020-02-25 | 8:00 | 19857 | Urban | Planned |  | 138 | 515 | 0.094836 | 0.00018415 | No
2020-02-25 | 8:00 | FF1284 | Urban | Planned |  | 47 | 450 | 0.028223 | 6.2717e-05 | No
2020-02-25 | 8:00 | SV1142 | Urban | Planned |  | 9 | 430 | 0.0051641 | 1.201e-05 | No
2020-02-25 | 8:00 | W163 | Short rural | Planned |  | 4 | 180 | 0.0023687 | 1.3159e-05 | No
2020-02-25 | 8:00 | M399 | Short rural | Planned |  | 11 | 145 | 0.0052473 | 3.6188e-05 | No
2020-02-25 | 8:00 | FT1210 | Urban | Planned |  | 81 | 425 | 0.045937 | 0.00010809 | No
2020-02-25 | 8:00 | BWH2 | Short rural | Planned |  | 19 | 400 | 0.025003 | 6.2507e-05 | No
2020-02-26 | 8:00 | OA1207 | Short rural | Planned |  | 3 | -1305 | -0.01288 | 9.8696e-06 | No
2020-02-26 | 8:30 | APE2 | Short rural | Planned |  | 18 | 450 | 0.026648 | 5.9218e-05 | No
2020-02-26 | 8:00 | L584 | Short rural | Planned |  | 8 | 205 | 0.0053954 | 2.6319e-05 | No
2020-02-26 | 8:00 | JS1122 | Short rural | Planned |  | 41 | 470 | 0.063396 | 0.00013488 | No
2020-02-26 | 8:00 | 35418 | Short rural | Planned |  | 4 | 240 | 0.0031583 | 1.3159e-05 | No
2020-02-26 | 8:00 | 8680 | Urban | Planned |  | 88 | 460 | 0.054016 | 0.00011743 | No
2020-02-26 | 8:00 | J502 | Urban | Planned |  | 90 | 480 | 0.057646 | 0.0001201 | No
2020-02-26 | 8:00 | R293 | Short rural | Planned |  | 19 | 480 | 0.030004 | 6.2507e-05 | No
2020-02-26 | 8:00 | BWA2 | Short rural | Planned |  | 61 | -1050 | -0.21072 | 0.00020068 | No
2020-02-26 | 8:00 | X883 | Urban | Planned |  | 17 | -975 | -0.022118 | 2.2685e-05 | No
2020-02-26 | 8:00 | 9056 | Urban | Planned |  | 23 | 480 | 0.014732 | 3.0691e-05 | No
2020-02-26 | 8:00 | ULK2 | Short rural | Planned |  | 181 | 429 | 0.25545 | 0.00059547 | No
2020-02-26 | 10:00 | B712 | Urban | Planned |  | 29 | 115 | 0.0044502 | 3.8698e-05 | No
2020-02-26 | 8:00 | RW1281 | Short rural | Planned |  | 9 | -990 | -0.029313 | 2.9609e-05 | No
2020-02-26 | 8:00 | BL1243 | Short rural | Planned |  | 99 | 550 | 0.17913 | 0.0003257 | No
2020-02-27 | 12:30 | DP1258 | Short rural | Planned |  | 2 | 180 | 0.0011844 | 6.5797e-06 | No
2020-02-27 | 9:00 | A095 | Short rural | Planned |  | 16 | 180 | 0.0094748 | 5.2638e-05 | No
2020-02-27 | 8:00 | CX1210 | Short rural | Planned |  | 16 | 405 | 0.021318 | 5.2638e-05 | No
2020-02-27 | 8:00 | WWC2 | Short rural | Planned |  | 88 | 435 | 0.12594 | 0.00028951 | No
2020-02-27 | 7:30 | X877 | Short rural | Planned |  | 4 | 460 | 0.0060533 | 1.3159e-05 | No
2020-02-27 | 8:00 | 2807 | Urban | Planned |  | 46 | 290 | 0.017801 | 6.1382e-05 | No
2020-02-27 | 8:00 | 9032 | Short rural | Planned |  | 11 | 480 | 0.01737 | 3.6188e-05 | No
2020-02-27 | 7:00 | M169 | Urban | Planned |  | 1 | 660 | 0.0008807 | 1.3344e-06 | No
2020-02-27 | 12:00 | UNJ2 | Urban | Planned |  | 64 | 145 | 0.012383 | 8.5402e-05 | No
2020-02-27 | 8:00 | SY1322 | Urban | Planned |  | 190 | 390 | 0.098879 | 0.00025354 | No
2020-02-27 | 9:30 | T884 | Urban | Planned |  | 6 | 105 | 0.00084067 | 8.0064e-06 | No
2020-02-27 | 8:00 | NWF2 | Urban | Planned |  | 45 | 420 | 0.02522 | 6.0048e-05 | No
2020-02-27 | 11:00 | JS1122 | Short rural | Planned |  | 75 | 305 | 0.075256 | 0.00024674 | No
2020-02-27 | 7:30 | J495 | Short rural | Planned |  | 85 | 70 | 0.019575 | 0.00027964 | No
2020-02-27 | 8:00 | X482 | Short rural | Planned |  | 31 | 395 | 0.040284 | 0.00010199 | No
2020-02-27 | 8:00 | MVF2 | Short rural | Planned |  | 16 | 410 | 0.021582 | 5.2638e-05 | No
2020-02-27 | 8:00 | S764 | Short rural | Planned |  | 67 | 420 | 0.092577 | 0.00022042 | No
2020-02-27 | 8:00 | 10250 | Short rural | Planned |  | 110 | 410 | 0.14837 | 0.00036188 | No
2020-02-27 | 8:00 | 48185 | Short rural | Planned |  | 18 | 330 | 0.019542 | 5.9218e-05 | No
2020-02-27 | 9:00 | ULK2 | Short rural | Planned |  | 179 | 300 | 0.17667 | 0.00058889 | No
2020-02-28 | 8:30 | ULE2 | Short rural | Planned |  | 9 | 337 | 0.0099782 | 2.9609e-05 | No
2020-02-28 | 8:00 | CR1254 | Urban | Planned |  | 399 | 405 | 0.21563 | 0.00053243 | No
2020-02-28 | 8:00 | BYG2 | Short rural | Planned |  | 11 | 368 | 0.013317 | 3.6188e-05 | No
2020-02-28 | 8:00 | M399 | Short rural | Planned |  | 7 | 480 | 0.011054 | 2.3029e-05 | No
2020-02-28 | 8:00 | DP1258 | Short rural | Planned |  | 1 | 570 | 0.0018752 | 3.2899e-06 | No
2020-02-28 | 7:30 | J493 | Urban | Planned |  | 80 | 60 | 0.0064051 | 0.00010675 | No
2020-02-28 | 10:00 | WH1261 | Urban | Planned |  | 82 | 140 | 0.015319 | 0.00010942 | No
2020-02-28 | 8:00 | 9032 | Short rural | Planned |  | 35 | 440 | 0.050664 | 0.00011515 | No
2020-02-28 | 8:00 | 8676 | Urban | Planned |  | 207 | 310 | 0.085628 | 0.00027622 | No
2020-02-28 | 8:00 | L947 | Short rural | Planned |  | 143 | 390 | 0.18348 | 0.00047045 | No
2020-02-28 | 8:00 | OP1262 | Short rural | Planned |  | 3 | 540 | 0.0053296 | 9.8696e-06 | No
2020-02-28 | 8:00 | 10244 | Short rural | Planned |  | 45 | 370 | 0.054776 | 0.00014804 | No
2020-02-28 | 9:30 | B778 | Urban | Planned |  | 233 | 180 | 0.055965 | 0.00031091 | No
2020-02-28 | 7:00 | W196 | Urban | Planned |  | 27 | 720 | 0.025941 | 3.6029e-05 | No
2020-02-28 | 8:30 | ULL2 | Short rural | Planned |  | 2 | 211 | 0.0013883 | 6.5797e-06 | No
2020-02-28 | 8:00 | ULH2 | Short rural | Planned |  | 15 | 400 | 0.019739 | 4.9348e-05 | No
2020-02-29 | 7:00 | R231 | Short rural | Planned |  | 1 | 520 | 0.0017107 | 3.2899e-06 | No
2020-02-29 | 8:00 | X867 | Urban | Planned |  | 24 | 420 | 0.013451 | 3.2026e-05 | No
2020-02-29 | 6:00 | FF1243 | Urban | Planned |  | 53 | 900 | 0.063651 | 7.0723e-05 | No
2020-02-29 | 6:30 | MR2292 | Urban | Planned |  | 10 | 690 | 0.0092074 | 1.3344e-05 | No
2020-03-01 | 8:00 | 46397 | Urban | Planned |  | 46 | 600 | 0.036829 | 6.1382e-05 | No
2020-03-01 | 8:00 | W124 | Short rural | Planned |  | 263 | 238 | 0.20593 | 0.00086523 | No
2020-03-01 | 8:00 | SZ1212 | Short rural | Planned |  | 3 | 285 | 0.0028128 | 9.8696e-06 | No
2020-03-01 | 5:00 | LP1222 | Urban | Planned |  | 103 | 780 | 0.10721 | 0.00013744 | No
2020-03-01 | 8:00 | J504 | Urban | Planned |  | 88 | 470 | 0.055191 | 0.00011743 | No
2020-03-01 | 8:00 | CR1214 | Urban | Planned |  | 105 | 410 | 0.057446 | 0.00014011 | No
2020-03-01 | 7:00 | NK1332 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2020-03-02 | 8:00 | RBC2 | Short rural | Planned |  | 30 | 480 | 0.047374 | 9.8696e-05 | No
2020-03-02 | 8:00 | 27038 | Short rural | Planned |  | 14 | 480 | 0.022108 | 4.6058e-05 | No
2020-03-02 | 8:00 | RW1292 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2020-03-02 | 8:00 | NK1342 | Urban | Planned |  | 64 | 405 | 0.034588 | 8.5402e-05 | No
2020-03-02 | 7:00 | MR2218 | Short rural | Planned |  | 10 | 540 | 0.017765 | 3.2899e-05 | No
2020-03-02 | 8:30 | ULE2 | Short rural | Planned |  | 7 | 369 | 0.0084977 | 2.3029e-05 | No
2020-03-02 | 8:30 | ULL2 | Short rural | Planned |  | 22 | 420 | 0.030398 | 7.2377e-05 | No
2020-03-02 | 8:00 | 8802 | Short rural | Planned |  | 52 | 308 | 0.05269 | 0.00017107 | No
2020-03-02 | 10:00 | C824 | Urban | Planned |  | 7 | 315 | 0.0029423 | 9.3408e-06 | No
2020-03-02 | 8:00 | 27194 | Urban | Planned |  | 51 | 285 | 0.019395 | 6.8054e-05 | No
2020-03-03 | 8:00 | FT1210 | Urban | Planned |  | 106 | 420 | 0.059407 | 0.00014145 | No
2020-03-03 | 9:00 | 8802 | Short rural | Planned |  | 58 | 220 | 0.041979 | 0.00019081 | No
2020-03-03 | 7:30 | WL1236 | Urban | Planned |  | 186 | 300 | 0.074459 | 0.0002482 | No
2020-03-03 | 8:30 | APC2 | Short rural | Planned |  | 173 | 380 | 0.21628 | 0.00056915 | No
2020-03-03 | 8:00 | 19857 | Urban | Planned |  | 108 | 435 | 0.06269 | 0.00014412 | No
2020-03-03 | 9:30 | X863 | Urban | Planned |  | 87 | 150 | 0.017414 | 0.00011609 | No
2020-03-03 | 8:00 | DP1269 | Urban | Planned |  | 7 | 480 | 0.0044836 | 9.3408e-06 | No
2020-03-03 | 8:30 | SN1230 | Short rural | Planned |  | 35 | 251 | 0.028901 | 0.00011515 | No
2020-03-03 | 8:00 | MG1267 | Short rural | Planned |  | 85 | 390 | 0.10906 | 0.00027964 | No
2020-03-03 | 7:30 | X877 | Short rural | Planned |  | 1 | 465 | 0.0015298 | 3.2899e-06 | No
2020-03-03 | 8:30 | SXC2 | Short rural | Planned |  | 12 | 450 | 0.017765 | 3.9478e-05 | No
2020-03-03 | 8:00 | CX1210 | Short rural | Planned |  | 4 | 340 | 0.0044742 | 1.3159e-05 | No
2020-03-03 | 8:00 | W163 | Short rural | Planned |  | 5 | 366 | 0.0060204 | 1.6449e-05 | No
2020-03-04 | 8:00 | 8802 | Short rural | Planned |  | 73 | 450 | 0.10807 | 0.00024016 | No
2020-03-05 | 6:30 | DP1258 | Short rural | Planned |  | 18 | 1190 | 0.070469 | 5.9218e-05 | No
2020-03-05 | 10:00 | NM1243 | Urban | Planned |  | 24 | 115 | 0.0036829 | 3.2026e-05 | No
2020-03-05 | 8:00 | CA1254 | Urban | Planned |  | 202 | 400 | 0.10782 | 0.00026955 | No
2020-03-05 | 8:00 | 2810 | Urban | Planned |  | 120 | 390 | 0.06245 | 0.00016013 | No
2020-03-05 | 8:00 | CV1251 | Urban | Planned |  | 104 | 385 | 0.053429 | 0.00013878 | No
2020-03-05 | 8:00 | A314 | Urban | Planned |  | 90 | 510 | 0.061249 | 0.0001201 | No
2020-03-06 | 8:30 | ULL2 | Short rural | Planned |  | 1 | 360 | 0.0011844 | 3.2899e-06 | No
2020-03-06 | 8:30 | ULE2 | Short rural | Planned |  | 24 | 420 | 0.033162 | 7.8957e-05 | No
2020-03-06 | 8:00 | BDF2 | Short rural | Planned |  | 24 | 371 | 0.029293 | 7.8957e-05 | No
2020-03-06 | 8:00 | C812 | Short rural | Planned |  | 58 | 255 | 0.048657 | 0.00019081 | No
2020-03-06 | 10:00 | 19857 | Urban | Planned |  | 39 | 360 | 0.018735 | 5.2042e-05 | No
2020-03-06 | 8:00 | 87220 | Short rural | Planned |  | 1 | 100 | 0.00032899 | 3.2899e-06 | No
2020-03-06 | 8:00 | 87220 | Short rural | Planned |  | 1 | 165 | 0.00054283 | 3.2899e-06 | No
2020-03-06 | 8:00 | 87220 | Short rural | Planned |  | 1 | 130 | 0.00042768 | 3.2899e-06 | No
2020-03-06 | 8:00 | FT1210 | Urban | Planned |  | 106 | 495 | 0.070016 | 0.00014145 | No
2020-03-06 | 9:30 | 8737 | Urban | Planned |  | 67 | 141 | 0.012606 | 8.9405e-05 | No
2020-03-06 | 8:00 | 55870 | Urban | Planned |  | 75 | 405 | 0.040532 | 0.00010008 | No
2020-03-06 | 7:00 | HKB2 | Short rural | Planned |  | 60 | 60 | 0.011844 | 0.00019739 | No
2020-03-06 | 8:00 | 27038 | Short rural | Planned |  | 4 | 505 | 0.0066455 | 1.3159e-05 | No
2020-03-06 | 8:00 | BWA2 | Short rural | Planned |  | 110 | 355 | 0.12847 | 0.00036188 | No
2020-03-06 | 8:00 | NK1332 | Urban | Planned |  | 68 | 405 | 0.036749 | 9.0739e-05 | No
2020-03-06 | 10:30 | SY1152 | Urban | Planned |  | 1 | 250 | 0.0003336 | 1.3344e-06 | No
2020-03-06 | 7:30 | 9052 | Urban | Planned |  | 73 | 560 | 0.05455 | 9.7411e-05 | No
2020-03-06 | 8:00 | 87220 | Short rural | Planned |  | 1 | 75 | 0.00024674 | 3.2899e-06 | No
2020-03-06 | 8:00 | R260 | Short rural | Planned |  | 10 | 340 | 0.011186 | 3.2899e-05 | No
2020-03-06 | 8:00 | 41533 | Short rural | Planned |  | 73 | 410 | 0.098466 | 0.00024016 | No
2020-03-07 | 7:00 | SG1247 | Urban | Planned |  | 32 | 600 | 0.02562 | 4.2701e-05 | No
2020-03-07 | 6:30 | WX1284 | Urban | Planned |  | 15 | 570 | 0.011409 | 2.0016e-05 | No
2020-03-07 | 10:00 | 49395 | Urban | Planned |  | 2 | 390 | 0.0010408 | 2.6688e-06 | No
2020-03-07 | 8:00 | 49917 | Urban | Planned |  | 1 | 200 | 0.00026688 | 1.3344e-06 | No
2020-03-07 | 8:00 | 41533 | Short rural | Planned |  | 28 | 320 | 0.029477 | 9.2116e-05 | No
2020-03-08 | 8:00 | 19856 | Urban | Planned |  | 167 | 345 | 0.076881 | 0.00022284 | No
2020-03-08 | 7:00 | MM1192 | Short rural | Planned |  | 1 | 540 | 0.0017765 | 3.2899e-06 | No
2020-03-08 | 7:00 | L517 | Urban | Planned |  | 44 | 310 | 0.018201 | 5.8714e-05 | No
2020-03-08 | 8:00 | MYK2 | Urban | Planned |  | 109 | 340 | 0.049453 | 0.00014545 | No
2020-03-09 | 8:00 | T889 | Urban | Planned |  | 62 | 460 | 0.038057 | 8.2733e-05 | No
2020-03-09 | 11:30 | 8798 | Short rural | Planned |  | 7 | 15 | 0.00034544 | 2.3029e-05 | No
2020-03-09 | 8:00 | S764 | Short rural | Planned |  | 1 | 630 | 0.0020726 | 3.2899e-06 | No
2020-03-09 | 8:00 | T831 | Short rural | Planned |  | 12 | 490 | 0.019344 | 3.9478e-05 | No
2020-03-09 | 8:00 | ULC2 | Short rural | Planned |  | 252 | 370 | 0.30675 | 0.00082905 | No
2020-03-09 | 8:00 | 7970 | Urban | Planned |  | 56 | 415 | 0.031011 | 7.4726e-05 | No
2020-03-09 | 8:00 | A350 | Urban | Planned |  | 127 | 480 | 0.081345 | 0.00016947 | No
2020-03-10 | 8:30 | GG1295 | Short rural | Planned |  | 9 | 380 | 0.011251 | 2.9609e-05 | No
2020-03-10 | 8:30 | GG1232 | Short rural | Planned |  | 11 | 278 | 0.01006 | 3.6188e-05 | No
2020-03-10 | 8:00 | 19857 | Urban | Planned |  | 429 | 480 | 0.27478 | 0.00057246 | No
2020-03-10 | 8:00 | OP1122 | Short rural | Planned |  | 9 | 520 | 0.015397 | 2.9609e-05 | No
2020-03-10 | 8:00 | CV1276 | Urban | Planned |  | 48 | 260 | 0.016653 | 6.4051e-05 | No
2020-03-10 | 8:00 | W113 | Short rural | Planned |  | 1 | 360 | 0.0011844 | 3.2899e-06 | No
2020-03-10 | 8:30 | DP1258 | Short rural | Planned |  | 176 | 310 | 0.17949 | 0.00057902 | No
2020-03-10 | 8:00 | CLB2 | Short rural | Planned |  | 482 | 340 | 0.53914 | 0.0015857 | No
2020-03-10 | 8:00 | RV1220 | Urban | Planned |  | 340 | 360 | 0.16333 | 0.0004537 | No
2020-03-10 | 8:00 | CS1276 | Urban | Planned |  | 49 | 480 | 0.031385 | 6.5386e-05 | No
2020-03-10 | 8:00 | X482 | Short rural | Planned |  | 21 | 480 | 0.033162 | 6.9087e-05 | No
2020-03-10 | 8:00 | NL1182 | Urban | Planned |  | 21 | 380 | 0.010649 | 2.8022e-05 | No
2020-03-10 | 9:00 | WM1142 | Urban | Planned |  | 5 | 300 | 0.0020016 | 6.672e-06 | No
2020-03-10 | 10:00 | 10248 | Urban | Planned |  | 20 | 120 | 0.0032026 | 2.6688e-05 | No
2020-03-10 | 8:00 | T831 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2020-03-10 | 8:00 | 8650 | Short rural | Planned |  | 9 | 240 | 0.0071061 | 2.9609e-05 | No
2020-03-10 | 8:00 | 8798 | Short rural | Planned |  | 22 | 405 | 0.029313 | 7.2377e-05 | No
2020-03-11 | 8:00 | MYG2 | Urban | Planned |  | 234 | 420 | 0.13114 | 0.00031225 | No
2020-03-11 | 8:00 | 35590 | Short rural | Planned |  | 5 | 480 | 0.0078957 | 1.6449e-05 | No
2020-03-11 | 8:00 | S740 | Urban | Planned |  | 90 | 365 | 0.043835 | 0.0001201 | No
2020-03-11 | 8:00 | TM1284 | Short rural | Planned |  | 7 | 385 | 0.0088662 | 2.3029e-05 | No
2020-03-11 | 8:00 | CV1247 | Urban | Planned |  | 100 | 480 | 0.064051 | 0.00013344 | No
2020-03-11 | 8:00 | 8798 | Short rural | Planned |  | 14 | 390 | 0.017963 | 4.6058e-05 | No
2020-03-11 | 8:00 | 35418 | Short rural | Planned |  | 10 | 369 | 0.01214 | 3.2899e-05 | No
2020-03-11 | 8:00 | 25783 | Urban | Planned |  | 23 | 540 | 0.016573 | 3.0691e-05 | No
2020-03-11 | 8:00 | RW1229 | Short rural | Planned |  | 2 | 510 | 0.0033557 | 6.5797e-06 | No
2020-03-11 | 8:30 | APH2 | Urban | Planned |  | 13 | 420 | 0.0072858 | 1.7347e-05 | No
2020-03-11 | 8:00 | 68181 | Urban | Planned |  | 105 | 510 | 0.071457 | 0.00014011 | No
2020-03-11 | 8:00 | RD1292 | Urban | Planned |  | 189 | 630 | 0.15889 | 0.0002522 | No
2020-03-11 | 8:00 | NK1342 | Urban | Planned |  | 38 | 380 | 0.019269 | 5.0707e-05 | No
2020-03-12 | 8:00 | FT1207 | Urban | Planned |  | 148 | 235 | 0.04641 | 0.00019749 | No
2020-03-12 | 8:15 | APC2 | Short rural | Planned |  | 20 | 465 | 0.030596 | 6.5797e-05 | No
2020-03-12 | 8:00 | APB2 | Short rural | Planned |  | 301 | 480 | 0.47532 | 0.00099025 | No
2020-03-12 | 8:00 | WRB2 | Urban | Planned |  | 221 | 410 | 0.12091 | 0.0002949 | No
2020-03-12 | 8:00 | X482 | Short rural | Planned |  | 31 | 470 | 0.047933 | 0.00010199 | No
2020-03-12 | 8:00 | SWC2 | Urban | Planned |  | 145 | 415 | 0.080297 | 0.00019349 | No
2020-03-12 | 8:30 | ULL2 | Short rural | Planned |  | 186 | 390 | 0.23865 | 0.00061191 | No
2020-03-12 | 8:00 | WD1284 | Short rural | Planned |  | 8 | 335 | 0.0088168 | 2.6319e-05 | No
2020-03-12 | 8:00 | T831 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2020-03-12 | 8:30 | WRF2 | Short rural | Planned |  | 158 | 180 | 0.093564 | 0.0005198 | No
2020-03-12 | 8:30 | SXC2 | Short rural | Planned |  | 42 | 377 | 0.052092 | 0.00013817 | No
2020-03-12 | 8:00 | MG1267 | Short rural | Planned |  | 24 | 480 | 0.037899 | 7.8957e-05 | No
2020-03-12 | 8:00 | R211 | Short rural | Planned |  | 96 | 475 | 0.15002 | 0.00031583 | No
2020-03-12 | 8:00 | ER1122 | Short rural | Planned |  | 124 | 330 | 0.13462 | 0.00040794 | No
2020-03-13 | 8:00 | X217 | Short rural | Planned |  | 8 | 255 | 0.0067113 | 2.6319e-05 | No
2020-03-13 | 8:00 | GL1233 | Short rural | Planned |  | 41 | 480 | 0.064745 | 0.00013488 | No
2020-03-13 | 8:30 | SHE2 | Urban | Planned |  | 60 | 65 | 0.0052042 | 8.0064e-05 | No
2020-03-13 | 8:00 | MG1267 | Short rural | Planned |  | 6 | 405 | 0.0079944 | 1.9739e-05 | No
2020-03-13 | 8:30 | GG1269 | Short rural | Planned |  | 235 | 350 | 0.27059 | 0.00077312 | No
2020-03-13 | 8:00 | CR1210 | Urban | Planned |  | 353 | 420 | 0.19784 | 0.00047104 | No
2020-03-13 | 8:00 | 10290 | Short rural | Planned |  | 1 | 375 | 0.0012337 | 3.2899e-06 | No
2020-03-13 | 10:00 | W163 | Short rural | Planned |  | 3 | 60 | 0.00059218 | 9.8696e-06 | No
2020-03-13 | 7:30 | 49914 | Urban | Planned |  | 16 | 480 | 0.010248 | 2.135e-05 | No
2020-03-13 | 8:00 | CX1232 | Short rural | Planned |  | 71 | 340 | 0.079417 | 0.00023358 | No
2020-03-13 | 10:00 | 10248 | Urban | Planned |  | 20 | 30 | 0.00080064 | 2.6688e-05 | No
2020-03-13 | 8:00 | NM1239 | Urban | Planned |  | 53 | 520 | 0.036776 | 7.0723e-05 | No
2020-03-13 | 8:00 | BDG2 | Short rural | Planned |  | 49 | 438 | 0.070607 | 0.0001612 | No
2020-03-13 | 8:00 | 35765 | Urban | Planned |  | 68 | 480 | 0.043555 | 9.0739e-05 | No
2020-03-13 | 8:30 | BYB2 | Short rural | Planned |  | 69 | 350 | 0.07945 | 0.000227 | No
2020-03-13 | 8:00 | T831 | Short rural | Planned |  | 12 | 492 | 0.019423 | 3.9478e-05 | No
2020-03-13 | 6:30 | J512 | Urban | Planned |  | 234 | 720 | 0.22482 | 0.00031225 | No
2020-03-13 | 8:00 | S738 | Short rural | Planned |  | 34 | 340 | 0.038031 | 0.00011186 | No
2020-03-14 | 6:00 | L503 | Urban | Planned |  | 1 | 297 | 0.00039632 | 1.3344e-06 | No
2020-03-14 | 8:00 | H745 | Short rural | Planned |  | 15 | 540 | 0.026648 | 4.9348e-05 | No
2020-03-14 | 8:00 | A098 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2020-03-15 | 10:00 | 6420 | Urban | Planned |  | 14 | 180 | 0.0033627 | 1.8682e-05 | No
2020-03-15 | 8:00 | 35771 | Urban | Planned |  | 4 | 510 | 0.0027222 | 5.3376e-06 | No
2020-03-15 | 7:00 | FF1243 | Urban | Planned |  | 4 | 450 | 0.0024019 | 5.3376e-06 | No
2020-03-16 | 8:30 | KMB2 | Short rural | Planned |  | 74 | 57 | 0.013877 | 0.00024345 | No
2020-03-16 | 8:00 | CJ1204 | Urban | Planned |  | 64 | 385 | 0.03288 | 8.5402e-05 | No
2020-03-16 | 6:00 | W196 | Urban | Planned |  | 1 | 405 | 0.00054043 | 1.3344e-06 | No
2020-03-16 | 8:00 | WBE2 | Short rural | Planned |  | 32 | 480 | 0.050532 | 0.00010528 | No
2020-03-16 | 8:00 | 8798 | Short rural | Planned |  | 3 | 205 | 0.0020233 | 9.8696e-06 | No
2020-03-17 | 8:00 | BYG2 | Short rural | Planned |  | 11 | 441 | 0.015959 | 3.6188e-05 | No
2020-03-17 | 8:00 | C812 | Short rural | Planned |  | 58 | 440 | 0.083957 | 0.00019081 | No
2020-03-17 | 8:30 | SHC2 | Short rural | Planned |  | 7 | 205 | 0.004721 | 2.3029e-05 | No
2020-03-17 | 8:30 | BDF2 | Short rural | Planned |  | 35 | 420 | 0.048361 | 0.00011515 | No
2020-03-17 | 6:00 | 9029 | Urban | Planned |  | 6 | 60 | 0.00048038 | 8.0064e-06 | No
2020-03-17 | 8:00 | WWB2 | Short rural | Planned |  | 229 | 415 | 0.31265 | 0.00075338 | No
2020-03-17 | 9:30 | 16666 | Urban | Planned |  | 26 | 270 | 0.0093675 | 3.4694e-05 | No
2020-03-17 | 8:00 | WD1284 | Short rural | Planned |  | 3 | 375 | 0.0037011 | 9.8696e-06 | No
2020-03-17 | 7:00 | WRE2 | Urban | Planned |  | 113 | 685 | 0.10329 | 0.00015079 | No
2020-03-17 | 8:00 | 19857 | Urban | Planned |  | 83 | 480 | 0.053162 | 0.00011076 | No
2020-03-17 | 8:00 | S735 | Short rural | Planned |  | 30 | 365 | 0.036024 | 9.8696e-05 | No
2020-03-17 | 8:00 | 25738 | Urban | Planned |  | 1 | 240 | 0.00032026 | 1.3344e-06 | No
2020-03-17 | 8:30 | ULE2 | Short rural | Planned |  | 33 | 480 | 0.052111 | 0.00010857 | No
2020-03-18 | 10:00 | L947 | Short rural | Planned |  | 8 | 30 | 0.00078957 | 2.6319e-05 | No
2020-03-18 | 8:00 | CLB2 | Short rural | Planned |  | 582 | 415 | 0.7946 | 0.0019147 | No
2020-03-18 | 9:30 | ULC2 | Short rural | Planned |  | 90 | 250 | 0.074022 | 0.00029609 | No
2020-03-18 | 8:00 | 8650 | Short rural | Planned |  | 4 | 240 | 0.0031583 | 1.3159e-05 | No
2020-03-18 | 8:00 | 87222 | Long rural | Planned |  | 1 | 416 | 1.3248 | 0.0031847 | No
2020-03-18 | 12:30 | JBB2 | Short rural | Planned |  | 21 | 105 | 0.0072541 | 6.9087e-05 | No
2020-03-18 | 8:00 | A098 | Short rural | Planned |  | 11 | 485 | 0.017551 | 3.6188e-05 | No
2020-03-18 | 8:00 | MG1282 | Short rural | Planned |  | 18 | 370 | 0.02191 | 5.9218e-05 | No
2020-03-18 | 8:30 | ULE2 | Short rural | Planned |  | 35 | 238 | 0.027405 | 0.00011515 | No
2020-03-18 | 8:00 | 87220 | Short rural | Planned |  | 1 | 258 | 0.00084878 | 3.2899e-06 | No
2020-03-18 | 8:00 | 87220 | Short rural | Planned |  | 1 | 296 | 0.0009738 | 3.2899e-06 | No
2020-03-18 | 8:00 | 8798 | Short rural | Planned |  | 256 | 435 | 0.36636 | 0.0008422 | No
2020-03-18 | 8:00 | 9027 | Urban | Planned |  | 108 | 320 | 0.046117 | 0.00014412 | No
2020-03-18 | 8:00 | 87220 | Short rural | Planned |  | 2 | 187 | 0.0012304 | 6.5797e-06 | No
2020-03-18 | 8:00 | 87220 | Short rural | Planned |  | 1 | 340 | 0.0011186 | 3.2899e-06 | No
2020-03-18 | 8:00 | W163 | Short rural | Planned |  | 6 | 365 | 0.0072048 | 1.9739e-05 | No
2020-03-18 | 8:30 | ULL2 | Short rural | Planned |  | 22 | 180 | 0.013028 | 7.2377e-05 | No
2020-03-18 | 8:00 | DS1226 | Urban | Planned |  | 254 | 380 | 0.1288 | 0.00033894 | No
2020-03-18 | 8:00 | NWA2 | Urban | Planned |  | 67 | 440 | 0.039338 | 8.9405e-05 | No
2020-03-18 | 7:30 | WL1236 | Urban | Planned |  | 109 | 460 | 0.066907 | 0.00014545 | No
2020-03-18 | 10:00 | 8650 | Short rural | Planned |  | 1 | 240 | 0.00078957 | 3.2899e-06 | No
2020-03-18 | 8:30 | DP1258 | Short rural | Planned |  | 52 | 450 | 0.076983 | 0.00017107 | No
2020-03-19 | 8:30 | TM1258 | Short rural | Planned |  | 218 | 457 | 0.32776 | 0.00071719 | No
2020-03-19 | 8:00 | SY1112 | Urban | Planned |  | 95 | 430 | 0.05451 | 0.00012677 | No
2020-03-19 | 8:00 | WWB2 | Short rural | Planned |  | 136 | 400 | 0.17897 | 0.00044742 | No
2020-03-19 | 8:00 | MVF2 | Short rural | Planned |  | 16 | 480 | 0.025266 | 5.2638e-05 | No
2020-03-19 | 8:00 | BX1342 | Urban | Planned |  | 124 | 480 | 0.079423 | 0.00016547 | No
2020-03-19 | 8:00 | R211 | Short rural | Planned |  | 85 | 420 | 0.11745 | 0.00027964 | No
2020-03-19 | 7:30 | NL1132 | Urban | Planned |  | 35 | 480 | 0.022418 | 4.6704e-05 | No
2020-03-19 | 8:00 | DP1221 | Short rural | Planned |  | 247 | 480 | 0.39005 | 0.0008126 | No
2020-03-19 | 8:00 | F601 | Urban | Planned |  | 55 | 480 | 0.035228 | 7.3392e-05 | No
2020-03-19 | 8:00 | S764 | Short rural | Planned |  | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2020-03-19 | 8:00 | X881 | Short rural | Planned |  | 85 | 600 | 0.16778 | 0.00027964 | No
2020-03-19 | 8:00 | 19856 | Urban | Planned |  | 176 | 395 | 0.092767 | 0.00023485 | No
2020-03-20 | 8:30 | ULC2 | Short rural | Planned |  | 74 | 260 | 0.063297 | 0.00024345 | No
2020-03-20 | 8:30 | APC2 | Short rural | Planned |  | 51 | 420 | 0.070469 | 0.00016778 | No
2020-03-20 | 8:00 | CX1210 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2020-03-20 | 8:00 | M399 | Short rural | Planned |  | 8 | 497 | 0.01308 | 2.6319e-05 | No
2020-03-20 | 8:00 | SY1112 | Urban | Planned |  | 165 | 460 | 0.10128 | 0.00022018 | No
2020-03-20 | 8:00 | D813 | Short rural | Planned |  | 39 | 245 | 0.031435 | 0.0001283 | No
2020-03-20 | 1:00 | MG1267 | Short rural | Planned |  | 6 | 180 | 0.0035531 | 1.9739e-05 | No
2020-03-20 | 8:00 | 87220 | Short rural | Planned |  | 1 | 155 | 0.00050993 | 3.2899e-06 | No
2020-03-20 | 8:00 | 87220 | Short rural | Planned |  | 2 | 190 | 0.0012501 | 6.5797e-06 | No
2020-03-20 | 8:00 | 87220 | Short rural | Planned |  | 1 | 125 | 0.00041123 | 3.2899e-06 | No
2020-03-20 | 8:00 | MVB2 | Short rural | Planned |  | 3 | 240 | 0.0023687 | 9.8696e-06 | No
2020-03-20 | 8:00 | DP1210 | Short rural | Planned |  | 134 | 480 | 0.2116 | 0.00044084 | No
2020-03-20 | 8:00 | WWB2 | Short rural | Planned |  | 163 | 420 | 0.22522 | 0.00053625 | No
2020-03-21 | 8:00 | X217 | Short rural | Planned |  | 5 | 218 | 0.003586 | 1.6449e-05 | No
2020-03-21 | 12:00 | 7962 | Urban | Planned |  | 9 | 5 | 6.0048e-05 | 1.201e-05 | No
2020-03-21 | 9:30 | ULC2 | Short rural | Planned |  | 90 | 390 | 0.11547 | 0.00029609 | No
2020-03-21 | 8:00 | HR1247 | Urban | Planned |  | 12 | 480 | 0.0076861 | 1.6013e-05 | No
2020-03-21 | 5:00 | BWB2 | Urban | Planned |  | 5 | 419 | 0.0027956 | 6.672e-06 | No
2020-03-21 | 8:00 | CX1206 | Short rural | Planned |  | 3 | 410 | 0.0040465 | 9.8696e-06 | No
2020-03-21 | 8:00 | 8798 | Short rural | Planned |  | 54 | 455 | 0.080832 | 0.00017765 | No
2020-03-21 | 8:30 | CA1276 | Urban | Planned |  | 21 | 480 | 0.013451 | 2.8022e-05 | No
2020-03-22 | 8:00 | WD1221 | Short rural | Planned |  | 15 | 499 | 0.024625 | 4.9348e-05 | No
2020-03-22 | 8:00 | 1962 | Urban | Planned |  | 38 | 450 | 0.022818 | 5.0707e-05 | No
2020-03-23 | 8:00 | PCD2 | Urban | Planned |  | 150 | 415 | 0.083066 | 0.00020016 | No
2020-03-23 | 8:00 | 49337 | Urban | Planned |  | 2 | 540 | 0.0014412 | 2.6688e-06 | No
2020-03-23 | 8:00 | A098 | Short rural | Planned |  | 31 | 540 | 0.055072 | 0.00010199 | No
2020-03-23 | 8:00 | MVD2 | Short rural | Planned |  | 84 | 480 | 0.13265 | 0.00027635 | No
2020-03-23 | 8:00 | 49337 | Urban | Planned |  | 2 | 540 | 0.0014412 | 2.6688e-06 | No
2020-03-23 | 8:00 | A352 | Urban | Planned |  | 12 | 480 | 0.0076861 | 1.6013e-05 | No
2020-03-23 | 8:30 | 35590 | Short rural | Planned |  | 5 | 420 | 0.0069087 | 1.6449e-05 | No
2020-03-23 | 8:00 | T828 | Short rural | Planned |  | 13 | 370 | 0.015824 | 4.2768e-05 | No
2020-03-24 | 8:00 | MVE2 | Short rural | Planned |  | 2 | 510 | 0.0033557 | 6.5797e-06 | No
2020-03-24 | 8:00 | 19857 | Urban | Planned |  | 429 | 450 | 0.25761 | 0.00057246 | No
2020-03-24 | 8:30 | KMD2 | Short rural | Planned |  | 138 | 380 | 0.17252 | 0.000454 | No
2020-03-24 | 8:00 | BWA2 | Short rural | Planned |  | 37 | 480 | 0.058428 | 0.00012172 | No
2020-03-24 | 8:00 | MG1286 | Short rural | Planned |  | 204 | 480 | 0.32214 | 0.00067113 | No
2020-03-24 | 8:00 | B205 | Urban | Planned |  | 75 | 240 | 0.024019 | 0.00010008 | No
2020-03-24 | 8:00 | GL1207 | Short rural | Planned |  | 12 | 380 | 0.015002 | 3.9478e-05 | No
2020-03-24 | 8:00 | WD1221 | Short rural | Planned |  | 11 | 345 | 0.012485 | 3.6188e-05 | No
2020-03-25 | 8:00 | MVH2 | Short rural | Planned |  | 81 | 480 | 0.12791 | 0.00026648 | No
2020-03-25 | 8:00 | 27038 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2020-03-25 | 8:00 | 48185 | Short rural | Planned |  | 14 | 480 | 0.022108 | 4.6058e-05 | No
2020-03-25 | 7:30 | LP1162 | Urban | Planned |  | 66 | 480 | 0.042274 | 8.807e-05 | No
2020-03-25 | 8:00 | 8686 | Short rural | Planned |  | 139 | 450 | 0.20578 | 0.00045729 | No
2020-03-25 | 8:00 | UNH2 | Urban | Planned |  | 133 | 480 | 0.085188 | 0.00017748 | No
2020-03-25 | 8:00 | BL1232 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2020-03-25 | 8:00 | 35418 | Short rural | Planned |  | 10 | 390 | 0.01283 | 3.2899e-05 | No
2020-03-25 | 8:00 | S741 | Short rural | Planned |  | 52 | 480 | 0.082115 | 0.00017107 | No
2020-03-25 | 8:30 | JBA2 | Short rural | Planned |  | 33 | 435 | 0.047226 | 0.00010857 | No
2020-03-25 | 8:00 | 87220 | Short rural | Planned |  | 39 | 390 | 0.050039 | 0.0001283 | No
2020-03-25 | 8:00 | T890 | Urban | Planned |  | 65 | 245 | 0.02125 | 8.6736e-05 | No
2020-03-25 | 8:00 | 8676 | Urban | Planned |  | 201 | 365 | 0.097898 | 0.00026821 | No
2020-03-26 | 8:00 | SZ1122 | Short rural | Planned |  | 73 | 370 | 0.088859 | 0.00024016 | No
2020-03-26 | 8:00 | WD1221 | Short rural | Planned |  | 38 | 430 | 0.053756 | 0.00012501 | No
2020-03-26 | 8:00 | 49914 | Urban | Planned |  | 109 | 480 | 0.069816 | 0.00014545 | No
2020-03-26 | 8:00 | ULK2 | Short rural | Planned |  | 2 | 510 | 0.0033557 | 6.5797e-06 | No
2020-03-26 | 8:00 | JBB2 | Short rural | Planned |  | 8 | 490 | 0.012896 | 2.6319e-05 | No
2020-03-26 | 7:30 | J499 | Urban | Planned |  | 140 | 540 | 0.10088 | 0.00018682 | No
2020-03-26 | 8:00 | 19856 | Urban | Planned |  | 228 | 415 | 0.12626 | 0.00030424 | No
2020-03-26 | 8:00 | MVH2 | Short rural | Planned |  | 39 | 480 | 0.061586 | 0.0001283 | No
2020-03-26 | 8:00 | BYC2 | Short rural | Planned |  | 45 | 390 | 0.057737 | 0.00014804 | No
2020-03-26 | 8:00 | S740 | Urban | Planned |  | 28 | 540 | 0.020176 | 3.7363e-05 | No
2020-03-26 | 8:30 | KMD2 | Short rural | Planned |  | 177 | 405 | 0.23583 | 0.00058231 | No
2020-03-26 | 8:00 | CR1214 | Urban | Planned |  | 150 | 480 | 0.096077 | 0.00020016 | No
2020-03-27 | 8:00 | 8686 | Short rural | Planned |  | 145 | 320 | 0.15265 | 0.00047703 | No
2020-03-27 | 8:00 | 41367 | Urban | Planned |  | 20 | 420 | 0.011209 | 2.6688e-05 | No
2020-03-27 | 8:00 | S738 | Short rural | Planned |  | 18 | 540 | 0.031977 | 5.9218e-05 | No
2020-03-27 | 11:00 | 1953 | Urban | Planned |  | 8 | 230 | 0.0024553 | 1.0675e-05 | No
2020-03-28 | 7:00 | M162 | Urban | Planned |  | 3 | 540 | 0.0021617 | 4.0032e-06 | No
2020-03-28 | 8:00 | A098 | Short rural | Planned |  | 13 | 510 | 0.021812 | 4.2768e-05 | No
2020-03-28 | 8:00 | HR1236 | Urban | Planned |  | 35 | 480 | 0.022418 | 4.6704e-05 | No
2020-03-29 | 8:00 | 19856 | Urban | Planned |  | 167 | 430 | 0.095823 | 0.00022284 | No
2020-03-29 | 7:30 | FF1276 | Urban | Planned |  | 7 | 540 | 0.005044 | 9.3408e-06 | No
2020-03-29 | 10:00 | RD1299 | Urban | Planned |  | 62 | 180 | 0.014892 | 8.2733e-05 | No
2020-03-29 | 8:00 | KYF2 | Urban | Planned |  | 7 | 580 | 0.0054177 | 9.3408e-06 | No
2020-03-29 | 8:00 | SZ1322 | Short rural | Planned |  | 16 | 480 | 0.025266 | 5.2638e-05 | No
2020-03-29 | 8:00 | 35767 | Urban | Planned |  | 132 | 435 | 0.076621 | 0.00017614 | No
2020-03-30 | 8:00 | ER1122 | Short rural | Planned |  | 28 | 180 | 0.016581 | 9.2116e-05 | No
2020-03-30 | 8:00 | 41533 | Short rural | Planned |  | 18 | 340 | 0.020134 | 5.9218e-05 | No
2020-03-30 | 8:30 | ULE2 | Short rural | Planned |  | 1 | 290 | 0.00095406 | 3.2899e-06 | No
2020-03-30 | 8:30 | ULE2 | Short rural | Planned |  | 1 | 210 | 0.00069087 | 3.2899e-06 | No
2020-03-30 | 8:00 | OP1202 | Urban | Planned |  | 12 | 480 | 0.0076861 | 1.6013e-05 | No
2020-03-30 | 6:00 | J513 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-03-31 | 8:00 | 8798 | Short rural | Planned |  | 85 | 270 | 0.075502 | 0.00027964 | No
2020-03-31 | 9:30 | CA1284 | Urban | Planned |  | 120 | 120 | 0.019215 | 0.00016013 | No
2020-03-31 | 8:30 | KMD2 | Short rural | Planned |  | 346 | 365 | 0.41548 | 0.0011383 | No
2020-03-31 | 8:00 | BWF2 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-03-31 | 7:30 | L588 | Short rural | Planned |  | 35 | 510 | 0.058724 | 0.00011515 | No
2020-03-31 | 8:00 | HR1206 | Urban | Planned |  | 91 | 360 | 0.043715 | 0.00012143 | No
2020-03-31 | 8:00 | J497 | Short rural | Planned |  | 79 | 420 | 0.10916 | 0.0002599 | No
2020-03-31 | 8:00 | MR2218 | Short rural | Planned |  | 11 | 510 | 0.018456 | 3.6188e-05 | No
2020-03-31 | 8:00 | T834 | Short rural | Planned |  | 1 | 390 | 0.001283 | 3.2899e-06 | No
2020-03-31 | 8:00 | 35305 | Urban | Planned |  | 81 | 420 | 0.045396 | 0.00010809 | No
2020-03-31 | 8:00 | 19857 | Urban | Planned |  | 282 | 530 | 0.19944 | 0.0003763 | No
2020-03-31 | 8:30 | CR1280 | Urban | Planned |  | 64 | 450 | 0.038431 | 8.5402e-05 | No
2020-03-31 | 8:00 | 8610 | Urban | Planned |  | 86 | 480 | 0.055084 | 0.00011476 | No
2020-04-01 | 9:00 | BK1299 | Short rural | Planned |  | 467 | 325 | 0.49932 | 0.0015364 | No
2020-04-01 | 8:00 | CR1254 | Urban | Planned |  | 326 | 410 | 0.17836 | 0.00043501 | No
2020-04-01 | 8:00 | H745 | Short rural | Planned |  | 27 | 480 | 0.042637 | 8.8826e-05 | No
2020-04-01 | 8:00 | ULB2 | Short rural | Planned |  | 183 | 341 | 0.2053 | 0.00060204 | No
2020-04-01 | 8:00 | 2813 | Urban | Planned |  | 38 | 480 | 0.024339 | 5.0707e-05 | No
2020-04-01 | 8:00 | MVF2 | Short rural | Planned |  | 12 | 480 | 0.01895 | 3.9478e-05 | No
2020-04-01 | 7:30 | WL1236 | Urban | Planned |  | 169 | 480 | 0.10825 | 0.00022551 | No
2020-04-01 | 8:00 | S735 | Short rural | Planned |  | 153 | 480 | 0.24161 | 0.00050335 | No
2020-04-01 | 8:00 | CLB2 | Short rural | Planned |  | 419 | 398 | 0.54862 | 0.0013785 | No
2020-04-01 | 8:00 | SY1252 | Urban | Planned |  | 1 | 425 | 0.00056712 | 1.3344e-06 | No
2020-04-01 | 8:30 | APC2 | Short rural | Planned |  | 7 | 245 | 0.0056421 | 2.3029e-05 | No
2020-04-01 | 8:00 | MR2205 | Short rural | Planned |  | 2 | 420 | 0.0027635 | 6.5797e-06 | No
2020-04-01 | 8:00 | 35418 | Short rural | Planned |  | 10 | 395 | 0.012995 | 3.2899e-05 | No
2020-04-01 | 8:00 | J505 | Urban | Planned |  | 74 | 420 | 0.041473 | 9.8746e-05 | No
2020-04-01 | 8:30 | APC2 | Short rural | Planned |  | 11 | 415 | 0.015018 | 3.6188e-05 | No
2020-04-01 | 8:00 | A315 | Urban | Planned |  | 75 | 360 | 0.036029 | 0.00010008 | No
2020-04-01 | 9:00 | T884 | Urban | Planned |  | 210 | 180 | 0.05044 | 0.00028022 | No
2020-04-01 | 9:00 | B713 | Urban | Planned |  | 4 | 90 | 0.00048038 | 5.3376e-06 | No
2020-04-01 | 8:00 | W163 | Short rural | Planned |  | 6 | 330 | 0.0065139 | 1.9739e-05 | No
2020-04-02 | 8:00 | OP1262 | Short rural | Planned |  | 35 | 510 | 0.058724 | 0.00011515 | No
2020-04-02 | 10:00 | 35983 | Short rural | Planned |  | 46 | 420 | 0.06356 | 0.00015133 | No
2020-04-02 | 8:30 | APB2 | Short rural | Planned |  | 17 | 510 | 0.028523 | 5.5928e-05 | No
2020-04-02 | 8:00 | 8798 | Short rural | Planned |  | 54 | 437 | 0.077634 | 0.00017765 | No
2020-04-02 | 8:30 | TM1284 | Short rural | Planned |  | 10 | 247 | 0.008126 | 3.2899e-05 | No
2020-04-02 | 8:00 | LL1172 | Urban | Planned |  | 35 | 300 | 0.014011 | 4.6704e-05 | No
2020-04-02 | 8:00 | WWB2 | Short rural | Planned |  | 62 | 370 | 0.075469 | 0.00020397 | No
2020-04-02 | 8:00 | APF2 | Short rural | Planned |  | 95 | 570 | 0.17815 | 0.00031254 | No
2020-04-02 | 8:00 | L942 | Short rural | Planned |  | 47 | 450 | 0.069581 | 0.00015462 | No
2020-04-02 | 8:00 | SZ1332 | Short rural | Planned |  | 60 | 265 | 0.052309 | 0.00019739 | No
2020-04-02 | 8:00 | OP1262 | Short rural | Planned |  | 15 | 480 | 0.023687 | 4.9348e-05 | No
2020-04-02 | 8:30 | KMB2 | Short rural | Planned |  | 104 | 420 | 0.1437 | 0.00034215 | No
2020-04-02 | 8:00 | T890 | Urban | Planned |  | 65 | 285 | 0.02472 | 8.6736e-05 | No
2020-04-02 | 7:30 | R260 | Short rural | Planned |  | 175 | 540 | 0.31089 | 0.00057573 | No
2020-04-02 | 8:30 | DP1206 | Urban | Planned |  | 30 | 450 | 0.018014 | 4.0032e-05 | No
2020-04-02 | 8:00 | JS1122 | Short rural | Planned |  | 110 | 495 | 0.17913 | 0.00036188 | No
2020-04-02 | 8:00 | APH2 | Urban | Planned |  | 13 | 460 | 0.0079797 | 1.7347e-05 | No
2020-04-03 | 8:00 | BX1222 | Urban | Planned |  | 21 | 280 | 0.0078463 | 2.8022e-05 | No
2020-04-03 | 8:30 | KME2 | Short rural | Planned |  | 10 | 370 | 0.012172 | 3.2899e-05 | No
2020-04-03 | 8:30 | BDG2 | Short rural | Planned |  | 36 | 340 | 0.040268 | 0.00011844 | No
2020-04-03 | 12:00 | APF2 | Short rural | Planned |  | 14 | 240 | 0.011054 | 4.6058e-05 | No
2020-04-03 | 8:30 | APH2 | Urban | Planned |  | 13 | 380 | 0.0065919 | 1.7347e-05 | No
2020-04-03 | 8:00 | CX1210 | Short rural | Planned |  | 20 | 300 | 0.019739 | 6.5797e-05 | No
2020-04-03 | 8:00 | S740 | Urban | Planned |  | 70 | 540 | 0.05044 | 9.3408e-05 | No
2020-04-03 | 8:00 | FT1210 | Urban | Planned |  | 191 | 410 | 0.1045 | 0.00025487 | No
2020-04-03 | 8:00 | APF2 | Short rural | Planned |  | 18 | 240 | 0.014212 | 5.9218e-05 | No
2020-04-03 | 8:00 | 87220 | Short rural | Planned |  | 1 | 165 | 0.00054283 | 3.2899e-06 | No
2020-04-03 | 8:00 | 87220 | Short rural | Planned |  | 1 | 127 | 0.00041781 | 3.2899e-06 | No
2020-04-03 | 8:00 | 19856 | Urban | Planned |  | 63 | 280 | 0.023539 | 8.4067e-05 | No
2020-04-03 | 8:00 | 87220 | Short rural | Planned |  | 1 | 97 | 0.00031912 | 3.2899e-06 | No
2020-04-03 | 8:00 | 87220 | Short rural | Planned |  | 1 | 70 | 0.00023029 | 3.2899e-06 | No
2020-04-04 | 8:00 | J512 | Urban | Planned |  | 113 | 480 | 0.072378 | 0.00015079 | No
2020-04-04 | 10:00 | 9022 | Urban | Planned |  | 1 | 285 | 0.0003803 | 1.3344e-06 | No
2020-04-04 | 6:00 | SZ1112 | Urban | Planned |  | 64 | 30.9375 | 0.0026421 | 8.5402e-05 | No
2020-04-04 | 8:00 | X881 | Short rural | Planned |  | 61 | 540 | 0.10837 | 0.00020068 | No
2020-04-04 | 8:00 | 55354 | Urban | Planned |  | 40 | 370 | 0.019749 | 5.3376e-05 | No
2020-04-04 | 7:00 | 54688 | Short rural | Planned |  | 2 | 555 | 0.0036517 | 6.5797e-06 | No
2020-04-04 | 8:30 | 7976 | Urban | Planned |  | 78 | 380 | 0.039552 | 0.00010408 | No
2020-04-04 | 7:00 | SZ1112 | Urban | Planned |  | 2 | 19800 | 0.052842 | 2.6688e-06 | No
2020-04-04 | 8:00 | 55163 | Short rural | Planned |  | 17 | 510 | 0.028523 | 5.5928e-05 | No
2020-04-05 | 7:00 | L502 | Short rural | Planned |  | 1 | 420 | 0.0013817 | 3.2899e-06 | No
2020-04-05 | 8:00 | WD1284 | Short rural | Planned |  | 1 | 590 | 0.001941 | 3.2899e-06 | No
2020-04-05 | 8:00 | APD2 | Short rural | Planned |  | 56 | 370 | 0.068166 | 0.00018423 | No
2020-04-05 | 8:00 | NN1214 | Short rural | Planned |  | 11 | 540 | 0.019542 | 3.6188e-05 | No
2020-04-05 | 8:00 | 8799 | Short rural | Planned |  | 42 | 478 | 0.066047 | 0.00013817 | No
2020-04-06 | 8:00 | RBC2 | Short rural | Planned |  | 3 | 480 | 0.0047374 | 9.8696e-06 | No
2020-04-06 | 8:00 | RBE2 | Short rural | Planned |  | 9 | 360 | 0.010659 | 2.9609e-05 | No
2020-04-06 | 8:00 | NL1332 | Urban | Planned |  | 25 | 510 | 0.017014 | 3.336e-05 | No
2020-04-06 | 7:00 | 35325 | Urban | Planned |  | 1 | 300 | 0.00040032 | 1.3344e-06 | No
2020-04-06 | 8:30 | ULH2 | Short rural | Planned |  | 9 | 345 | 0.010215 | 2.9609e-05 | No
2020-04-06 | 8:00 | R293 | Short rural | Planned |  | 2 | 375 | 0.0024674 | 6.5797e-06 | No
2020-04-06 | 8:00 | 9050 | Urban | Planned |  | 99 | 480 | 0.063411 | 0.00013211 | No
2020-04-07 | 8:00 | D813 | Short rural | Planned |  | 76 | 420 | 0.10501 | 0.00025003 | No
2020-04-07 | 8:00 | SN1271 | Short rural | Planned |  | 83 | 450 | 0.12288 | 0.00027306 | No
2020-04-07 | 8:00 | 61617 | Short rural | Planned |  | 29 | 540 | 0.051519 | 9.5406e-05 | No
2020-04-07 | 8:00 | 8682 | Urban | Planned |  | 78 | 240 | 0.02498 | 0.00010408 | No
2020-04-07 | 8:00 | SN1219 | Short rural | Planned |  | 8 | 295 | 0.0077641 | 2.6319e-05 | No
2020-04-07 | 8:30 | SN1271 | Short rural | Planned |  | 85 | 450 | 0.12584 | 0.00027964 | No
2020-04-07 | 8:00 | 55361 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2020-04-07 | 8:00 | 1962 | Urban | Planned |  | 43 | 390 | 0.022378 | 5.7379e-05 | No
2020-04-07 | 8:00 | 5496 | Urban | Planned |  | 138 | 480 | 0.088391 | 0.00018415 | No
2020-04-07 | 8:00 | A098 | Short rural | Planned |  | 19 | 675 | 0.042192 | 6.2507e-05 | No
2020-04-07 | 8:30 | BDH2 | Short rural | Planned |  | 137 | 450 | 0.20282 | 0.00045071 | No
2020-04-07 | 8:00 | A098 | Short rural | Planned |  | 7 | 540 | 0.012436 | 2.3029e-05 | No
2020-04-07 | 8:30 | KMD2 | Short rural | Planned |  | 330 | 485 | 0.52654 | 0.0010857 | No
2020-04-07 | 8:00 | BL1232 | Short rural | Planned |  | 229 | 405 | 0.30512 | 0.00075338 | No
2020-04-07 | 8:00 | 8675 | Urban | Planned |  | 95 | 220 | 0.027889 | 0.00012677 | No
2020-04-07 | 7:30 | L588 | Short rural | Planned |  | 41 | 465 | 0.062721 | 0.00013488 | No
2020-04-08 | 8:00 | 68188 | Urban | Planned |  | 48 | 360 | 0.023058 | 6.4051e-05 | No
2020-04-08 | 8:30 | GG1232 | Short rural | Planned |  | 41 | 420 | 0.056651 | 0.00013488 | No
2020-04-08 | 10:00 | C832 | Urban | Planned |  | 60 | 450 | 0.036029 | 8.0064e-05 | No
2020-04-08 | 8:00 | 27029 | Short rural | Planned |  | 5 | 120 | 0.0019739 | 1.6449e-05 | No
2020-04-08 | 8:00 | B748 | Urban | Planned |  | 213 | 480 | 0.13643 | 0.00028423 | No
2020-04-08 | 9:00 | 25783 | Urban | Planned |  | 15 | 300 | 0.0060048 | 2.0016e-05 | No
2020-04-08 | 8:00 | 25784 | Urban | Planned |  | 17 | 300 | 0.0068054 | 2.2685e-05 | No
2020-04-08 | 8:00 | WM1232 | Urban | Planned |  | 6 | 510 | 0.0040833 | 8.0064e-06 | No
2020-04-08 | 8:00 | RBC2 | Short rural | Planned |  | 33 | 480 | 0.052111 | 0.00010857 | No
2020-04-08 | 7:30 | B776 | Urban | Planned |  | 30 | 480 | 0.019215 | 4.0032e-05 | No
2020-04-08 | 8:00 | 35701 | Short rural | Planned |  | 28 | 335 | 0.030859 | 9.2116e-05 | No
2020-04-08 | 8:00 | 8683 | Urban | Planned |  | 139 | 435 | 0.080684 | 0.00018548 | No
2020-04-08 | 8:30 | DP1210 | Short rural | Planned |  | 129 | 345 | 0.14642 | 0.00042439 | No
2020-04-08 | 8:00 | R211 | Short rural | Planned |  | 12 | 395 | 0.015594 | 3.9478e-05 | No
2020-04-08 | 8:00 | 25449 | Short rural | Planned |  | 31 | 525 | 0.053543 | 0.00010199 | No
2020-04-08 | 8:00 | 35418 | Short rural | Planned |  | 6 | 360 | 0.0071061 | 1.9739e-05 | No
2020-04-09 | 11:00 | M165 | Urban | Planned |  | 13 | 360 | 0.006245 | 1.7347e-05 | No
2020-04-09 | 8:00 | R260 | Short rural | Planned |  | 193 | 497 | 0.31557 | 0.00063494 | No
2020-04-09 | 8:30 | KMD2 | Short rural | Planned |  | 330 | 316 | 0.34307 | 0.0010857 | No
2020-04-09 | 8:00 | X217 | Short rural | Planned |  | 8 | 335 | 0.0088168 | 2.6319e-05 | No
2020-04-09 | 8:00 | CR1262 | Urban | Planned |  | 103 | 119 | 0.016356 | 0.00013744 | No
2020-04-09 | 7:30 | WQ1212 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-04-09 | 1:00 | HKB2 | Short rural | Planned |  | 17 | 40 | 0.0022371 | 5.5928e-05 | No
2020-04-09 | 8:00 | RV1246 | Short rural | Planned |  | 85 | 201 | 0.056207 | 0.00027964 | No
2020-04-09 | 8:00 | WWA2 | Short rural | Planned |  | 137 | 410 | 0.18479 | 0.00045071 | No
2020-04-09 | 8:00 | HKB2 | Short rural | Planned |  | 2 | 340 | 0.0022371 | 6.5797e-06 | No
2020-04-09 | 8:00 | BWC2 | Short rural | Planned |  | 88 | 360 | 0.10422 | 0.00028951 | No
2020-04-09 | 8:30 | DP1236 | Short rural | Planned |  | 3 | 360 | 0.0035531 | 9.8696e-06 | No
2020-04-09 | 8:00 | 68188 | Urban | Planned |  | 46 | 360 | 0.022098 | 6.1382e-05 | No
2020-04-12 | 6:00 | J459 | Short rural | Planned |  | 1 | 720 | 0.0023687 | 3.2899e-06 | No
2020-04-13 | 6:00 | RD1228 | Urban | Planned |  | 187 | 120 | 0.029944 | 0.00024953 | No
2020-04-15 | 8:00 | W163 | Short rural | Planned |  | 1 | 385 | 0.0012666 | 3.2899e-06 | No
2020-04-15 | 8:00 | X867 | Urban | Planned |  | 59 | 480 | 0.03779 | 7.873e-05 | No
2020-04-15 | 8:00 | JBB2 | Short rural | Planned |  | 8 | 375 | 0.0098696 | 2.6319e-05 | No
2020-04-15 | 8:00 | YYA2 | Short rural | Planned |  | 1 | 430 | 0.0014146 | 3.2899e-06 | No
2020-04-15 | 8:00 | SZ1242 | Short rural | Planned |  | 26 | 390 | 0.033359 | 8.5536e-05 | No
2020-04-15 | 6:00 | CA1210 | Urban | Planned |  | 18 | 720 | 0.017294 | 2.4019e-05 | No
2020-04-15 | 8:00 | BWE2 | Short rural | Planned |  | 48 | 360 | 0.056849 | 0.00015791 | No
2020-04-16 | 8:30 | DP1206 | Urban | Planned |  | 16 | 288 | 0.0061489 | 2.135e-05 | No
2020-04-16 | 9:30 | CT1225 | Short rural | Planned |  | 16 | 420 | 0.022108 | 5.2638e-05 | No
2020-04-16 | 8:00 | NN1285 | Short rural | Planned |  | 11 | 540 | 0.019542 | 3.6188e-05 | No
2020-04-16 | 8:00 | J512 | Urban | Planned |  | 44 | 360 | 0.021137 | 5.8714e-05 | No
2020-04-16 | 9:30 | 7979 | Urban | Planned |  | 8 | 270 | 0.0028823 | 1.0675e-05 | No
2020-04-16 | 12:00 | KMB2 | Short rural | Planned |  | 231 | 70 | 0.053197 | 0.00075996 | No
2020-04-16 | 8:00 | CR1228 | Urban | Planned |  | 35 | 295 | 0.013778 | 4.6704e-05 | No
2020-04-16 | 8:00 | MG1286 | Short rural | Planned |  | 21 | 360 | 0.024871 | 6.9087e-05 | No
2020-04-16 | 8:00 | MYQ2 | Short rural | Planned |  | 172 | 411 | 0.23257 | 0.00056586 | No
2020-04-16 | 8:30 | NA1270 | Short rural | Planned |  | 3 | 340 | 0.0033557 | 9.8696e-06 | No
2020-04-16 | 7:30 | A347 | Urban | Planned |  | 345 | 480 | 0.22098 | 0.00046037 | No
2020-04-16 | 8:30 | ULF2 | Short rural | Planned |  | 9 | 390 | 0.011547 | 2.9609e-05 | No
2020-04-16 | 8:00 | NM1258 | Urban | Planned |  | 19 | 360 | 0.0091273 | 2.5354e-05 | No
2020-04-16 | 8:00 | S740 | Urban | Planned |  | 38 | 540 | 0.027382 | 5.0707e-05 | No
2020-04-16 | 8:00 | SXD2 | Short rural | Planned |  | 2 | 423 | 0.0027832 | 6.5797e-06 | No
2020-04-17 | 8:00 | J495 | Short rural | Planned |  | 17 | 360 | 0.020134 | 5.5928e-05 | No
2020-04-17 | 8:00 | T838 | Short rural | Planned |  | 6 | 85 | 0.0016778 | 1.9739e-05 | No
2020-04-17 | 8:00 | 87220 | Short rural | Planned |  | 1 | 177 | 0.00058231 | 3.2899e-06 | No
2020-04-17 | 8:00 | TM1258 | Short rural | Planned |  | 380 | 400 | 0.50006 | 0.0012501 | No
2020-04-17 | 7:30 | HR1269 | Urban | Planned |  | 45 | 260 | 0.015612 | 6.0048e-05 | No
2020-04-17 | 8:00 | CR1214 | Urban | Planned |  | 49 | 195 | 0.01275 | 6.5386e-05 | No
2020-04-17 | 8:00 | X482 | Short rural | Planned |  | 1 | 75 | 0.00024674 | 3.2899e-06 | No
2020-04-17 | 8:00 | 16649 | Urban | Planned |  | 117 | 480 | 0.07494 | 0.00015612 | No
2020-04-17 | 8:00 | X482 | Short rural | Planned |  | 2 | 145 | 0.00095406 | 6.5797e-06 | No
2020-04-17 | 8:00 | X482 | Short rural | Planned |  | 2 | 48 | 0.00031583 | 6.5797e-06 | No
2020-04-17 | 8:00 | X482 | Short rural | Planned |  | 1 | 105 | 0.00034544 | 3.2899e-06 | No
2020-04-18 | 8:00 | SZ1242 | Short rural | Planned |  | 23 | 390 | 0.02951 | 7.5667e-05 | No
2020-04-18 | 8:30 | HR1250 | Urban | Planned |  | 5 | 450 | 0.0030024 | 6.672e-06 | No
2020-04-18 | 8:30 | HR1269 | Urban | Planned |  | 57 | 250 | 0.019015 | 7.6061e-05 | No
2020-04-18 | 7:00 | RD1236 | Urban | Planned |  | 4 | 660 | 0.0035228 | 5.3376e-06 | No
2020-04-18 | 8:00 | CT1236 | Short rural | Planned |  | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2020-04-18 | 8:00 | A098 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2020-04-19 | 7:00 | RD1288 | Urban | Planned |  | 20 | 570 | 0.015212 | 2.6688e-05 | No
2020-04-19 | 8:00 | PK1236 | Short rural | Planned |  | 3 | 520 | 0.0051322 | 9.8696e-06 | No
2020-04-20 | 8:00 | GV1208 | Urban | Planned |  | 85 | 420 | 0.047638 | 0.00011342 | No
2020-04-20 | 7:00 | J510 | Urban | Planned |  | 1 | 420 | 0.00056045 | 1.3344e-06 | No
2020-04-20 | 8:00 | H745 | Short rural | Planned |  | 13 | 600 | 0.025661 | 4.2768e-05 | No
2020-04-20 | 8:00 | H745 | Short rural | Planned |  | 15 | 600 | 0.029609 | 4.9348e-05 | No
2020-04-20 | 8:00 | NL1332 | Urban | Planned |  | 11 | 510 | 0.007486 | 1.4678e-05 | No
2020-04-20 | 8:00 | CR1262 | Urban | Planned |  | 82 | 450 | 0.049239 | 0.00010942 | No
2020-04-20 | 8:00 | 7981 | Urban | Planned |  | 31 | 480 | 0.019856 | 4.1366e-05 | No
2020-04-21 | 7:00 | T887 | Urban | Planned |  | 1 | 595 | 0.00079397 | 1.3344e-06 | No
2020-04-21 | 9:00 | KVD2 | Short rural | Planned |  | 11 | 225 | 0.0081424 | 3.6188e-05 | No
2020-04-21 | 8:30 | JBB2 | Short rural | Planned |  | 33 | 331 | 0.035935 | 0.00010857 | No
2020-04-21 | 8:30 | BDE2 | Urban | Planned |  | 191 | 385 | 0.098125 | 0.00025487 | No
2020-04-21 | 8:00 | M162 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-04-21 | 8:00 | MYG2 | Urban | Planned |  | 86 | 420 | 0.048198 | 0.00011476 | No
2020-04-21 | 8:00 | WWC2 | Short rural | Planned |  | 144 | 440 | 0.20845 | 0.00047374 | No
2020-04-21 | 8:30 | ULC2 | Short rural | Planned |  | 45 | 345 | 0.051075 | 0.00014804 | No
2020-04-21 | 8:30 | C833 | Urban | Planned |  | 64 | 480 | 0.040993 | 8.5402e-05 | No
2020-04-21 | 8:00 | MG1286 | Short rural | Planned |  | 12 | 360 | 0.014212 | 3.9478e-05 | No
2020-04-21 | 8:00 | 8615 | Urban | Planned |  | 134 | 480 | 0.085829 | 0.00017881 | No
2020-04-21 | 8:00 | MR2218 | Short rural | Planned |  | 6 | 540 | 0.010659 | 1.9739e-05 | No
2020-04-21 | 8:00 | R210 | Short rural | Planned |  | 60 | 365 | 0.072048 | 0.00019739 | No
2020-04-21 | 9:00 | A046 | Short rural | Planned |  | 14 | 480 | 0.022108 | 4.6058e-05 | No
2020-04-21 | 8:00 | 8675 | Urban | Planned |  | 84 | 480 | 0.053803 | 0.00011209 | No
2020-04-21 | 8:00 | X482 | Short rural | Planned |  | 31 | 478 | 0.048749 | 0.00010199 | No
2020-04-21 | 8:00 | CX1210 | Short rural | Planned |  | 51 | 270 | 0.045301 | 0.00016778 | No
2020-04-21 | 8:00 | BX1342 | Urban | Planned |  | 234 | 520 | 0.16237 | 0.00031225 | No
2020-04-22 | 8:00 | 25783 | Urban | Planned |  | 42 | 405 | 0.022698 | 5.6045e-05 | No
2020-04-22 | 8:00 | M399 | Short rural | Planned |  | 27 | 595 | 0.052852 | 8.8826e-05 | No
2020-04-22 | 8:00 | 9026 | Urban | Planned |  | 13 | 360 | 0.006245 | 1.7347e-05 | No
2020-04-22 | 8:00 | UNJ2 | Urban | Planned |  | 165 | 480 | 0.10568 | 0.00022018 | No
2020-04-22 | 8:30 | KVA2 | Short rural | Planned |  | 32 | 365 | 0.038426 | 0.00010528 | No
2020-04-22 | 8:00 | 10251 | Urban | Planned |  | 21 | 220 | 0.0061649 | 2.8022e-05 | No
2020-04-22 | 11:00 | R210 | Short rural | Planned |  | 2 | 230 | 0.0015133 | 6.5797e-06 | No
2020-04-22 | 6:00 | MM1242 | Urban | Planned |  | 4 | 660 | 0.0035228 | 5.3376e-06 | No
2020-04-22 | 8:00 | SZ1242 | Short rural | Planned |  | 26 | 320 | 0.027372 | 8.5536e-05 | No
2020-04-22 | 8:00 | 49357 | Urban | Planned |  | 1 | 340 | 0.0004537 | 1.3344e-06 | No
2020-04-22 | 8:00 | CR1210 | Urban | Planned |  | 79 | 445 | 0.046911 | 0.00010542 | No
2020-04-22 | 8:30 | BYB2 | Short rural | Planned |  | 55 | 250 | 0.045236 | 0.00018094 | No
2020-04-22 | 8:00 | MVH2 | Short rural | Planned |  | 81 | 360 | 0.095932 | 0.00026648 | No
2020-04-22 | 8:00 | B217 | Urban | Planned |  | 158 | 420 | 0.088551 | 0.00021084 | No
2020-04-22 | 8:00 | CV1284 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2020-04-22 | 8:00 | 35335 | Urban | Planned |  | 33 | 540 | 0.023779 | 4.4035e-05 | No
2020-04-22 | 8:15 | NWB2 | Urban | Planned |  | 29 | 435 | 0.016833 | 3.8698e-05 | No
2020-04-22 | 7:30 | HR1276 | Urban | Planned |  | 74 | 380 | 0.037523 | 9.8746e-05 | No
2020-04-23 | 8:00 | CR1214 | Urban | Planned |  | 145 | 390 | 0.07546 | 0.00019349 | No
2020-04-23 | 8:30 | SHC2 | Short rural | Planned |  | 71 | 450 | 0.10511 | 0.00023358 | No
2020-04-23 | 7:00 | WRF2 | Short rural | Planned |  | 1 | 710 | 0.0023358 | 3.2899e-06 | No
2020-04-23 | 8:00 | 19856 | Urban | Planned |  | 169 | 480 | 0.10825 | 0.00022551 | No
2020-04-23 | 8:00 | X482 | Short rural | Planned |  | 21 | 480 | 0.033162 | 6.9087e-05 | No
2020-04-23 | 8:00 | KVD2 | Short rural | Planned |  | 4 | 345 | 0.00454 | 1.3159e-05 | No
2020-04-23 | 7:30 | R260 | Short rural | Planned |  | 175 | 540 | 0.31089 | 0.00057573 | No
2020-04-23 | 8:00 | MVD2 | Short rural | Planned |  | 86 | 360 | 0.10185 | 0.00028293 | No
2020-04-23 | 8:30 | JBA2 | Short rural | Planned |  | 29 | 470 | 0.044841 | 9.5406e-05 | No
2020-04-23 | 8:00 | 9032 | Short rural | Planned |  | 24 | 540 | 0.042637 | 7.8957e-05 | No
2020-04-23 | 8:00 | BYC2 | Short rural | Planned |  | 20 | 410 | 0.026977 | 6.5797e-05 | No
2020-04-23 | 8:00 | 8685 | Urban | Planned |  | 113 | 480 | 0.072378 | 0.00015079 | No
2020-04-24 | 7:30 | 7979 | Urban | Planned |  | 50 | 465 | 0.031025 | 6.672e-05 | No
2020-04-24 | 8:00 | 8690 | Urban | Planned |  | 44 | 480 | 0.028183 | 5.8714e-05 | No
2020-04-24 | 8:30 | ULL2 | Short rural | Planned |  | 2 | 215 | 0.0014146 | 6.5797e-06 | No
2020-04-24 | 6:30 | SC1289 | Short rural | Planned |  | 1 | 630 | 0.0020726 | 3.2899e-06 | No
2020-04-24 | 8:00 | 9032 | Short rural | Planned |  | 5 | 300 | 0.0049348 | 1.6449e-05 | No
2020-04-24 | 8:00 | 35990 | Short rural | Planned |  | 9 | 480 | 0.014212 | 2.9609e-05 | No
2020-04-24 | 8:00 | X217 | Short rural | Planned |  | 13 | 480 | 0.020529 | 4.2768e-05 | No
2020-04-24 | 8:00 | L946 | Short rural | Planned |  | 23 | 450 | 0.03405 | 7.5667e-05 | No
2020-04-24 | 8:00 | MG1204 | Short rural | Planned |  | 15 | 480 | 0.023687 | 4.9348e-05 | No
2020-04-24 | 8:30 | TM1210 | Short rural | Planned |  | 25 | 450 | 0.037011 | 8.2247e-05 | No
2020-04-24 | 8:00 | KC1284 | Short rural | Planned |  | 71 | 420 | 0.098104 | 0.00023358 | No
2020-04-24 | 8:30 | BYB2 | Short rural | Planned |  | 71 | 380 | 0.088761 | 0.00023358 | No
2020-04-24 | 8:00 | BX1332 | Urban | Planned |  | 76 | 480 | 0.048679 | 0.00010141 | No
2020-04-24 | 9:00 | PCE2 | Urban | Planned |  | 6 | 360 | 0.0028823 | 8.0064e-06 | No
2020-04-24 | 8:30 | DP1210 | Short rural | Planned |  | 134 | 153 | 0.067449 | 0.00044084 | No
2020-04-26 | 6:00 | 35981 | Short rural | Planned |  | 19 | 810 | 0.050631 | 6.2507e-05 | No
2020-04-26 | 9:00 | 4870 | Urban | Planned |  | 31 | 480 | 0.019856 | 4.1366e-05 | No
2020-04-26 | 7:00 | SC1216 | Urban | Planned |  | 2 | 600 | 0.0016013 | 2.6688e-06 | No
2020-04-26 | 8:00 | WQ1271 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-04-27 | 8:00 | T836 | Short rural | Planned |  | 10 | 420 | 0.013817 | 3.2899e-05 | No
2020-04-27 | 8:00 | 27188 | Urban | Planned |  | 1 | 315 | 0.00042034 | 1.3344e-06 | No
2020-04-27 | 8:00 | RS1207 | Urban | Planned |  | 65 | 480 | 0.041633 | 8.6736e-05 | No
2020-04-27 | 8:00 | M400 | Urban | Planned |  | 22 | 360 | 0.010568 | 2.9357e-05 | No
2020-04-27 | 8:00 | CD1297 | Urban | Planned |  | 138 | 510 | 0.093915 | 0.00018415 | No
2020-04-27 | 8:30 | JBA2 | Short rural | Planned |  | 2 | 75 | 0.00049348 | 6.5797e-06 | No
2020-04-28 | 8:00 | 19856 | Urban | Planned |  | 228 | 480 | 0.14604 | 0.00030424 | No
2020-04-28 | 8:00 | 87222 | Long rural | Planned |  | 20 | 480 | 30.5732 | 0.063694 | No
2020-04-28 | 8:00 | CS1247 | Urban | Planned |  | 50 | 540 | 0.036029 | 6.672e-05 | No
2020-04-28 | 8:00 | 8798 | Short rural | Planned |  | 35 | 350 | 0.040301 | 0.00011515 | No
2020-04-28 | 7:30 | LP1422 | Urban | Planned |  | 93 | 480 | 0.059568 | 0.0001241 | No
2020-04-28 | 8:00 | BYG2 | Short rural | Planned |  | 99 | 390 | 0.12702 | 0.0003257 | No
2020-04-28 | 8:00 | 27454 | Short rural | Planned |  | 19 | 360 | 0.022503 | 6.2507e-05 | No
2020-04-28 | 8:00 | NM1236 | Urban | Planned |  | 130 | 480 | 0.083267 | 0.00017347 | No
2020-04-28 | 7:30 | D845 | Urban | Planned |  | 61 | 480 | 0.039071 | 8.1398e-05 | No
2020-04-28 | 8:00 | CLA2 | Short rural | Planned |  | 2 | 230 | 0.0015133 | 6.5797e-06 | No
2020-04-28 | 8:00 | MG1286 | Short rural | Planned |  | 12 | 360 | 0.014212 | 3.9478e-05 | No
2020-04-28 | 7:30 | J492 | Urban | Planned |  | 191 | 540 | 0.13763 | 0.00025487 | No
2020-04-28 | 7:30 | L588 | Short rural | Planned |  | 44 | 540 | 0.078167 | 0.00014475 | No
2020-04-28 | 8:30 | YYB2 | Short rural | Planned |  | 55 | 216 | 0.039084 | 0.00018094 | No
2020-04-28 | 8:00 | SY1132 | Urban | Planned |  | 258 | 480 | 0.16525 | 0.00034427 | No
2020-04-28 | 8:00 | BK1251 | Short rural | Planned |  | 12 | 540 | 0.021318 | 3.9478e-05 | No
2020-04-29 | 8:00 | 35418 | Short rural | Planned |  | 10 | 350 | 0.011515 | 3.2899e-05 | No
2020-04-29 | 8:00 | W114 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2020-04-29 | 9:00 | 9060 | Urban | Planned |  | 55 | 420 | 0.030825 | 7.3392e-05 | No
2020-04-29 | 8:00 | CR1254 | Urban | Planned |  | 13 | 480 | 0.0083267 | 1.7347e-05 | No
2020-04-29 | 8:00 | T868 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2020-04-29 | 8:30 | TM1258 | Short rural | Planned |  | 89 | 355 | 0.10394 | 0.0002928 | No
2020-04-29 | 8:00 | DS1256 | Urban | Planned |  | 93 | 390 | 0.048399 | 0.0001241 | No
2020-04-29 | 8:00 | RW1218 | Short rural | Planned |  | 73 | 360 | 0.086458 | 0.00024016 | No
2020-04-29 | 9:00 | L582 | Short rural | Planned |  | 2 | 300 | 0.0019739 | 6.5797e-06 | No
2020-04-29 | 8:00 | M399 | Short rural | Planned |  | 104 | 480 | 0.16423 | 0.00034215 | No
2020-04-29 | 8:00 | SC1241 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2020-04-29 | 11:00 | 35815 | Short rural | Planned |  | 19 | 120 | 0.0075009 | 6.2507e-05 | No
2020-04-29 | 8:00 | 55867 | Urban | Planned |  | 127 | 480 | 0.081345 | 0.00016947 | No
2020-04-30 | 8:00 | 35818 | Short rural | Planned |  | 74 | 420 | 0.10225 | 0.00024345 | No
2020-04-30 | 7:30 | CV1213 | Urban | Planned |  | 95 | 480 | 0.060849 | 0.00012677 | No
2020-04-30 | 8:00 | NG1299 | Short rural | Planned |  | 9 | 540 | 0.015989 | 2.9609e-05 | No
2020-04-30 | 8:30 | ULC2 | Short rural | Planned |  | 74 | 205 | 0.049907 | 0.00024345 | No
2020-04-30 | 8:00 | L940 | Short rural | Planned |  | 62 | 345 | 0.07037 | 0.00020397 | No
2020-04-30 | 8:00 | 19856 | Urban | Planned |  | 70 | 480 | 0.044836 | 9.3408e-05 | No
2020-04-30 | 8:30 | KMD2 | Short rural | Planned |  | 329 | 315 | 0.34094 | 0.0010824 | No
2020-04-30 | 8:30 | APE2 | Short rural | Planned |  | 2 | 95 | 0.00062507 | 6.5797e-06 | No
2020-04-30 | 8:00 | ULB2 | Short rural | Planned |  | 53 | 325 | 0.056668 | 0.00017436 | No
2020-04-30 | 8:00 | X863 | Urban | Planned |  | 82 | 480 | 0.052522 | 0.00010942 | No
2020-04-30 | 8:00 | 8735 | Urban | Planned |  | 28 | 480 | 0.017934 | 3.7363e-05 | No
2020-04-30 | 8:30 | APC2 | Short rural | Planned |  | 4 | 115 | 0.0015133 | 1.3159e-05 | No
2020-05-01 | 8:30 | DP1206 | Urban | Planned |  | 109 | 210 | 0.030544 | 0.00014545 | No
2020-05-01 | 8:00 | X482 | Short rural | Planned |  | 1 | 420 | 0.0013817 | 3.2899e-06 | No
2020-05-01 | 8:00 | X482 | Short rural | Planned |  | 1 | 420 | 0.0013817 | 3.2899e-06 | No
2020-05-01 | 8:00 | X482 | Short rural | Planned |  | 1 | 420 | 0.0013817 | 3.2899e-06 | No
2020-05-01 | 8:00 | X482 | Short rural | Planned |  | 2 | 420 | 0.0027635 | 6.5797e-06 | No
2020-05-01 | 8:00 | X482 | Short rural | Planned |  | 2 | 420 | 0.0027635 | 6.5797e-06 | No
2020-05-01 | 8:00 | SZ1322 | Short rural | Planned |  | 87 | 275 | 0.07871 | 0.00028622 | No
2020-05-01 | 12:00 | DP1236 | Short rural | Planned |  | 140 | 175 | 0.080602 | 0.00046058 | No
2020-05-01 | 7:30 | J506 | Urban | Planned |  | 16 | 510 | 0.010889 | 2.135e-05 | No
2020-05-01 | 8:00 | CX1232 | Short rural | Planned |  | 12 | 420 | 0.016581 | 3.9478e-05 | No
2020-05-01 | 8:00 | CLA2 | Short rural | Planned |  | 106 | 215 | 0.074976 | 0.00034873 | No
2020-05-01 | 8:00 | 2812 | Urban | Planned |  | 70 | 480 | 0.044836 | 9.3408e-05 | No
2020-05-01 | 8:00 | BYE2 | Short rural | Planned |  | 33 | 210 | 0.022799 | 0.00010857 | No
2020-05-02 | 6:30 | 54647 | Short rural | Planned |  | 5 | 810 | 0.013324 | 1.6449e-05 | No
2020-05-02 | 8:00 | X877 | Short rural | Planned |  | 6 | 540 | 0.010659 | 1.9739e-05 | No
2020-05-02 | 6:00 | M170 | Urban | Planned |  | 5 | 600 | 0.0040032 | 6.672e-06 | No
2020-05-02 | 9:00 | 8802 | Short rural | Planned |  | 93 | 420 | 0.1285 | 0.00030596 | No
2020-05-02 | 8:00 | 68188 | Urban | Planned |  | 23 | 480 | 0.014732 | 3.0691e-05 | No
2020-05-02 | 8:00 | HS1152 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2020-05-02 | 8:00 | L544 | Urban | Planned |  | 117 | 55 | 0.0085869 | 0.00015612 | No
2020-05-02 | 7:00 | W112 | Short rural | Planned |  | 5 | 660 | 0.010857 | 1.6449e-05 | No
2020-05-02 | 8:30 | FF1206 | Urban | Planned |  | 44 | 480 | 0.028183 | 5.8714e-05 | No
2020-05-03 | 8:00 | BWD2 | Urban | Planned |  | 7 | 360 | 0.0033627 | 9.3408e-06 | No
2020-05-03 | 6:00 | WQ1271 | Urban | Planned |  | 2 | 360 | 0.00096077 | 2.6688e-06 | No
2020-05-03 | 8:00 | CR1214 | Urban | Planned |  | 62 | 430 | 0.035575 | 8.2733e-05 | No
2020-05-03 | 8:00 | UNB2 | Urban | Planned |  | 19 | 430 | 0.010902 | 2.5354e-05 | No
2020-05-03 | 8:00 | PH1201 | Urban | Planned |  | 2 | 540 | 0.0014412 | 2.6688e-06 | No
2020-05-03 | 8:00 | 35701 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-05-02 | 6:30 | 54647 | Short rural | Planned |  | 2 | 630 | 0.0041452 | 6.5797e-06 | No
2020-05-03 | 8:00 | 8617 | Urban | Planned |  | 67 | 480 | 0.042914 | 8.9405e-05 | No
2020-05-04 | 7:00 | GV1208 | Urban | Planned |  | 5 | 600 | 0.0040032 | 6.672e-06 | No
2020-05-04 | 8:00 | CR1280 | Urban | Planned |  | 53 | 445 | 0.031472 | 7.0723e-05 | No
2020-05-04 | 8:00 | T828 | Short rural | Planned |  | 12 | 480 | 0.01895 | 3.9478e-05 | No
2020-05-04 | 7:00 | 25783 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2020-05-05 | 8:30 | NM1258 | Urban | Planned |  | 117 | 480 | 0.07494 | 0.00015612 | No
2020-05-05 | 8:00 | L947 | Short rural | Planned |  | 148 | 350 | 0.17041 | 0.0004869 | No
2020-05-05 | 8:00 | RBE2 | Short rural | Planned |  | 24 | 480 | 0.037899 | 7.8957e-05 | No
2020-05-05 | 8:30 | BYC2 | Short rural | Planned |  | 35 | 247 | 0.028441 | 0.00011515 | No
2020-05-05 | 8:00 | APE2 | Short rural | Planned |  | 8 | 432 | 0.01137 | 2.6319e-05 | No
2020-05-05 | 5:00 | WT1245 | Short rural | Planned |  | 11 | 960 | 0.034741 | 3.6188e-05 | No
2020-05-05 | 8:00 | 87222 | Long rural | Planned |  | 5 | 480 | 7.6433 | 0.015924 | No
2020-05-05 | 8:30 | DP1221 | Short rural | Planned |  | 8 | 595 | 0.01566 | 2.6319e-05 | No
2020-05-05 | 8:00 | 35696 | Short rural | Planned |  | 240 | 480 | 0.37899 | 0.00078957 | No
2020-05-05 | 8:00 | BYB2 | Short rural | Planned |  | 22 | 450 | 0.03257 | 7.2377e-05 | No
2020-05-05 | 7:30 | 9046 | Urban | Planned |  | 15 | 480 | 0.0096077 | 2.0016e-05 | No
2020-05-05 | 8:00 | J516 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2020-05-05 | 8:00 | WWC2 | Short rural | Planned |  | 115 | 390 | 0.14755 | 0.00037833 | No
2020-05-05 | 9:00 | NM1228 | Urban | Planned |  | 16 | 300 | 0.0064051 | 2.135e-05 | No
2020-05-05 | 8:00 | WH1294 | Urban | Planned |  | 82 | 480 | 0.052522 | 0.00010942 | No
2020-05-06 | 8:00 | X482 | Short rural | Planned |  | 31 | 480 | 0.048953 | 0.00010199 | No
2020-05-06 | 6:00 | MM1342 | Urban | Planned |  | 4 | 720 | 0.0038431 | 5.3376e-06 | No
2020-05-06 | 8:30 | SHK2 | Urban | Planned |  | 80 | 205 | 0.021884 | 0.00010675 | No
2020-05-06 | 7:30 | R260 | Short rural | Planned |  | 175 | 540 | 0.31089 | 0.00057573 | No
2020-05-06 | 8:00 | OA1233 | Short rural | Planned |  | 27 | 480 | 0.042637 | 8.8826e-05 | No
2020-05-06 | 8:00 | NWF2 | Urban | Planned |  | 102 | 225 | 0.030624 | 0.00013611 | No
2020-05-06 | 8:00 | BYB2 | Short rural | Planned |  | 29 | 410 | 0.039116 | 9.5406e-05 | No
2020-05-06 | 8:30 | KMD2 | Short rural | Planned |  | 31 | 235 | 0.023967 | 0.00010199 | No
2020-05-06 | 8:00 | OA1244 | Short rural | Planned |  | 29 | 360 | 0.034346 | 9.5406e-05 | No
2020-05-06 | 8:00 | CR1214 | Urban | Planned |  | 45 | 440 | 0.026421 | 6.0048e-05 | No
2020-05-06 | 8:00 | 9032 | Short rural | Planned |  | 9 | 540 | 0.015989 | 2.9609e-05 | No
2020-05-06 | 8:30 | JBB2 | Short rural | Planned |  | 47 | 50 | 0.0077312 | 0.00015462 | No
2020-05-06 | 8:00 | 35418 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2020-05-06 | 8:00 | 8680 | Urban | Planned |  | 34 | 480 | 0.021777 | 4.537e-05 | No
2020-05-06 | 8:00 | WL1292 | Urban | Planned |  | 68 | 480 | 0.043555 | 9.0739e-05 | No
2020-05-06 | 8:30 | 8620 | Urban | Planned |  | 136 | 480 | 0.08711 | 0.00018148 | No
2020-05-06 | 7:00 | 35764 | Urban | Planned |  | 2 | 600 | 0.0016013 | 2.6688e-06 | No
2020-05-06 | 8:00 | 35765 | Urban | Planned |  | 100 | 480 | 0.064051 | 0.00013344 | No
2020-05-06 | 7:30 | LP1132 | Urban | Planned |  | 93 | 510 | 0.063291 | 0.0001241 | No
2020-05-07 | 8:00 | 25741 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2020-05-07 | 8:30 | NM1258 | Urban | Planned |  | 77 | 480 | 0.049319 | 0.00010275 | No
2020-05-07 | 8:00 | BYB2 | Short rural | Planned |  | 22 | 395 | 0.028589 | 7.2377e-05 | No
2020-05-07 | 8:30 | DP1221 | Short rural | Planned |  | 8 | 275 | 0.0072377 | 2.6319e-05 | No
2020-05-07 | 8:30 | KVA2 | Short rural | Planned |  | 76 | 275 | 0.068758 | 0.00025003 | No
2020-05-07 | 7:30 | BK1299 | Short rural | Planned |  | 39 | 480 | 0.061586 | 0.0001283 | No
2020-05-07 | 7:30 | A344 | Urban | Planned |  | 221 | 460 | 0.13566 | 0.0002949 | No
2020-05-07 | 8:00 | A098 | Short rural | Planned |  | 12 | 545 | 0.021516 | 3.9478e-05 | No
2020-05-07 | 7:00 | MM1282 | Urban | Planned |  | 1 | 310 | 0.00041366 | 1.3344e-06 | No
2020-05-07 | 7:00 | M169 | Urban | Planned |  | 5 | 600 | 0.0040032 | 6.672e-06 | No
2020-05-07 | 7:30 | C833 | Urban | Planned |  | 51 | 540 | 0.036749 | 6.8054e-05 | No
2020-05-07 | 8:00 | BWH2 | Short rural | Planned |  | 167 | 480 | 0.26372 | 0.00054941 | No
2020-05-07 | 8:00 | 19857 | Urban | Planned |  | 303 | 480 | 0.19408 | 0.00040432 | No
2020-05-08 | 8:00 | 10250 | Short rural | Planned |  | 110 | 480 | 0.1737 | 0.00036188 | No
2020-05-08 | 8:00 | NN1251 | Short rural | Planned |  | 9 | 420 | 0.012436 | 2.9609e-05 | No
2020-05-08 | 8:00 | CX1273 | Short rural | Planned |  | 2 | 413 | 0.0027174 | 6.5797e-06 | No
2020-05-08 | 8:00 | CX1232 | Short rural | Planned |  | 16 | 480 | 0.025266 | 5.2638e-05 | No
2020-05-08 | 8:00 | WH1235 | Urban | Planned |  | 37 | 480 | 0.023699 | 4.9373e-05 | No
2020-05-08 | 8:30 | BYC2 | Short rural | Planned |  | 2 | 320 | 0.0021055 | 6.5797e-06 | No
2020-05-08 | 8:00 | 1959 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2020-05-08 | 8:30 | BYC2 | Short rural | Planned |  | 10 | 280 | 0.0092116 | 3.2899e-05 | No
2020-05-08 | 8:00 | 4870 | Urban | Planned |  | 79 | 480 | 0.0506 | 0.00010542 | No
2020-05-08 | 8:30 | KMF2 | Urban | Planned |  | 74 | 225 | 0.022218 | 9.8746e-05 | No
2020-05-08 | 8:00 | SN1230 | Short rural | Planned |  | 25 | 200 | 0.016449 | 8.2247e-05 | No
2020-05-08 | 8:00 | 87218 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2020-05-08 | 7:00 | 8762 | Urban | Planned |  | 1 | 300 | 0.00040032 | 1.3344e-06 | No
2020-05-08 | 8:00 | R260 | Short rural | Planned |  | 2 | 510 | 0.0033557 | 6.5797e-06 | No
2020-05-08 | 7:30 | J516 | Urban | Planned |  | 33 | 510 | 0.022458 | 4.4035e-05 | No
2020-05-08 | 9:30 | 49335 | Short rural | Planned |  | 67 | 136 | 0.029977 | 0.00022042 | No
2020-05-08 | 8:30 | APC2 | Short rural | Planned |  | 1 | 210 | 0.00069087 | 3.2899e-06 | No
2020-05-08 | 8:00 | SY1322 | Urban | Planned |  | 70 | 480 | 0.044836 | 9.3408e-05 | No
2020-05-08 | 8:00 | BWE2 | Short rural | Planned |  | 16 | 510 | 0.026845 | 5.2638e-05 | No
2020-05-08 | 8:00 | SWG2 | Urban | Planned |  | 28 | 375 | 0.014011 | 3.7363e-05 | No
2020-05-08 | 8:00 | 9032 | Short rural | Planned |  | 42 | 540 | 0.074614 | 0.00013817 | No
2020-05-09 | 8:00 | RV1280 | Urban | Planned |  | 36 | 417 | 0.020032 | 4.8038e-05 | No
2020-05-09 | 6:30 | 54684 | Urban | Planned |  | 1 | 870 | 0.0011609 | 1.3344e-06 | No
2020-05-09 | 7:00 | RD1236 | Urban | Planned |  | 3 | 600 | 0.0024019 | 4.0032e-06 | No
2020-05-09 | 12:00 | WL1280 | Urban | Planned |  | 112 | 480 | 0.071737 | 0.00014945 | No
2020-05-09 | 7:00 | 16662 | Urban | Planned |  | 96 | 600 | 0.076861 | 0.0001281 | No
2020-05-10 | 8:00 | RD1251 | Urban | Planned |  | 87 | 480 | 0.055725 | 0.00011609 | No
2020-05-10 | 8:00 | 35695 | Short rural | Planned |  | 154 | 480 | 0.24319 | 0.00050664 | No
2020-05-10 | 8:00 | CX1210 | Short rural | Planned |  | 38 | 275 | 0.034379 | 0.00012501 | No
2020-05-10 | 8:00 | SWD2 | Urban | Planned |  | 8 | 530 | 0.0056579 | 1.0675e-05 | No
2020-05-10 | 8:30 | 8770 | Urban | Planned |  | 26 | 480 | 0.016653 | 3.4694e-05 | No
2020-05-11 | 8:00 | MVC2 | Short rural | Planned |  | 3 | 510 | 0.0050335 | 9.8696e-06 | No
2020-05-11 | 8:00 | CR1262 | Urban | Planned |  | 188 | 400 | 0.10035 | 0.00025087 | No
2020-05-11 | 7:30 | CD1230 | Short rural | Planned |  | 30 | 540 | 0.053296 | 9.8696e-05 | No
2020-05-11 | 8:00 | 35304 | Urban | Planned |  | 51 | 480 | 0.032666 | 6.8054e-05 | No
2020-05-11 | 8:00 | BWF2 | Short rural | Planned |  | 28 | 480 | 0.044216 | 9.2116e-05 | No
2020-05-11 | 8:00 | S786 | Short rural | Planned |  | 20 | 540 | 0.035531 | 6.5797e-05 | No
2020-05-11 | 8:00 | MR2292 | Urban | Planned |  | 222 | 360 | 0.10665 | 0.00029624 | No
2020-05-11 | 10:00 | BDE2 | Urban | Planned |  | 139 | 345 | 0.063991 | 0.00018548 | No
2020-05-11 | 9:00 | 7021 | Urban | Planned |  | 3 | 360 | 0.0014412 | 4.0032e-06 | No
2020-05-12 | 8:00 | 5495 | Urban | Planned |  | 49 | 480 | 0.031385 | 6.5386e-05 | No
2020-05-12 | 8:30 | BYC2 | Short rural | Planned |  | 34 | 210 | 0.02349 | 0.00011186 | No
2020-05-12 | 8:00 | RV1228 | Urban | Planned |  | 75 | 124 | 0.01241 | 0.00010008 | No
2020-05-12 | 8:00 | 8689 | Urban | Planned |  | 62 | 480 | 0.039712 | 8.2733e-05 | No
2020-05-12 | 8:00 | GL1207 | Short rural | Planned |  | 14 | 280 | 0.012896 | 4.6058e-05 | No
2020-05-12 | 8:00 | BYB2 | Short rural | Planned |  | 98 | 450 | 0.14508 | 0.00032241 | No
2020-05-12 | 8:00 | 4857 | Urban | Planned |  | 33 | 420 | 0.018495 | 4.4035e-05 | No
2020-05-12 | 7:00 | 2810 | Urban | Planned |  | 216 | 360 | 0.10376 | 0.00028823 | No
2020-05-12 | 8:00 | SZ1242 | Short rural | Planned |  | 5 | 480 | 0.0078957 | 1.6449e-05 | No
2020-05-12 | 8:30 | KVC2 | Short rural | Planned |  | 37 | 462.1622 | 0.056257 | 0.00012172 | No
2020-05-12 | 8:00 | KVC2 | Short rural | Planned |  | 1 | 18240 | 0.060007 | 3.2899e-06 | No
2020-05-12 | 8:00 | MYC2 | Urban | Planned |  | 20 | 410 | 0.010942 | 2.6688e-05 | No
2020-05-12 | 7:30 | LP1142 | Urban | Planned |  | 70 | 480 | 0.044836 | 9.3408e-05 | No
2020-05-13 | 7:30 | HR1247 | Urban | Planned |  | 109 | 480 | 0.069816 | 0.00014545 | No
2020-05-12 | 8:00 | 9030 | Urban | Planned |  | 184 | 480 | 0.11785 | 0.00024553 | No
2020-05-12 | 8:30 | KVB2 | Short rural | Planned |  | 22 | 240 | 0.01737 | 7.2377e-05 | No
2020-05-12 | 8:00 | L588 | Short rural | Planned |  | 35 | 480 | 0.05527 | 0.00011515 | No
2020-05-12 | 8:00 | C832 | Urban | Planned |  | 18 | 480 | 0.011529 | 2.4019e-05 | No
2020-05-12 | 8:00 | UNJ2 | Urban | Planned |  | 6 | 480 | 0.0038431 | 8.0064e-06 | No
2020-05-12 | 8:00 | 2810 | Urban | Planned |  | 60 | 480 | 0.038431 | 8.0064e-05 | No
2020-05-13 | 8:00 | W164 | Short rural | Planned |  | 8 | 480 | 0.012633 | 2.6319e-05 | No
2020-05-13 | 8:00 | MG1282 | Short rural | Planned |  | 26 | 480 | 0.041057 | 8.5536e-05 | No
2020-05-13 | 8:30 | ULE2 | Short rural | Planned |  | 10 | 178 | 0.005856 | 3.2899e-05 | No
2020-05-13 | 8:00 | MM1112 | Urban | Planned |  | 7 | 480 | 0.0044836 | 9.3408e-06 | No
2020-05-13 | 8:00 | 2813 | Urban | Planned |  | 61 | 480 | 0.039071 | 8.1398e-05 | No
2020-05-13 | 8:00 | 35590 | Short rural | Planned |  | 40 | 510 | 0.067113 | 0.00013159 | No
2020-05-13 | 8:00 | 35304 | Urban | Planned |  | 164 | 480 | 0.10504 | 0.00021884 | No
2020-05-13 | 8:30 | WRF2 | Short rural | Planned |  | 121 | 320 | 0.12738 | 0.00039807 | No
2020-05-13 | 8:00 | APG2 | Urban | Planned |  | 74 | 460 | 0.045423 | 9.8746e-05 | No
2020-05-13 | 8:00 | L582 | Short rural | Planned |  | 2 | 270 | 0.0017765 | 6.5797e-06 | No
2020-05-13 | 8:00 | 35418 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2020-05-13 | 8:00 | RW1218 | Short rural | Planned |  | 32 | 385 | 0.040531 | 0.00010528 | No
2020-05-13 | 8:00 | BX1242 | Urban | Planned |  | 43 | 480 | 0.027542 | 5.7379e-05 | No
2020-05-13 | 8:00 | 35824 | Short rural | Planned |  | 39 | 590 | 0.0757 | 0.0001283 | No
2020-05-13 | 8:30 | 25449 | Short rural | Planned |  | 10 | 310 | 0.010199 | 3.2899e-05 | No
2020-05-13 | 8:00 | A347 | Urban | Planned |  | 103 | 360 | 0.04948 | 0.00013744 | No
2020-05-13 | 8:00 | RBA2 | Short rural | Planned |  | 25 | 420 | 0.034544 | 8.2247e-05 | No
2020-05-14 | 8:00 | MVC2 | Short rural | Planned |  | 59 | 480 | 0.093169 | 0.0001941 | No
2020-05-14 | 8:30 | KVC2 | Short rural | Planned |  | 10 | 330 | 0.010857 | 3.2899e-05 | No
2020-05-14 | 7:30 | 9059 | Urban | Planned |  | 187 | 480 | 0.11978 | 0.00024953 | No
2020-05-14 | 7:30 | R260 | Short rural | Planned |  | 175 | 540 | 0.31089 | 0.00057573 | No
2020-05-14 | 8:00 | APE2 | Short rural | Planned |  | 59 | 480 | 0.093169 | 0.0001941 | No
2020-05-14 | 8:00 | HT1203 | Urban | Planned |  | 12 | 480 | 0.0076861 | 1.6013e-05 | No
2020-05-14 | 8:00 | 77674 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2020-05-14 | 8:00 | CR1210 | Urban | Planned |  | 104 | 270 | 0.03747 | 0.00013878 | No
2020-05-14 | 9:00 | SHH2 | Short rural | Planned |  | 3 | 420 | 0.0041452 | 9.8696e-06 | No
2020-05-14 | 8:30 | BL1232 | Short rural | Planned |  | 38 | 510 | 0.063758 | 0.00012501 | No
2020-05-21 | 8:00 | APA2 | Urban | Planned |  | 4 | 360 | 0.0019215 | 5.3376e-06 | No
2020-05-14 | 6:00 | J472 | Urban | Planned |  | 2 | 480 | 0.001281 | 2.6688e-06 | No
2020-05-14 | 8:00 | MR2232 | Short rural | Planned |  | 19 | 540 | 0.033754 | 6.2507e-05 | No
2020-05-14 | 8:30 | DP1206 | Urban | Planned |  | 43 | 467 | 0.026796 | 5.7379e-05 | No
2020-05-14 | 8:30 | JBB2 | Short rural | Planned |  | 21 | 295 | 0.020381 | 6.9087e-05 | No
2020-05-14 | 8:30 | ULK2 | Short rural | Planned |  | 505 | 380 | 0.63132 | 0.0016614 | No
2020-05-14 | 8:00 | L591 | Short rural | Planned |  | 27 | 540 | 0.047966 | 8.8826e-05 | No
2020-05-15 | 1:00 | APG2 | Urban | Planned |  | 74 | 225 | 0.022218 | 9.8746e-05 | No
2020-05-15 | 8:00 | CX1232 | Short rural | Planned |  | 229 | 480 | 0.36162 | 0.00075338 | No
2020-05-15 | 8:00 | 10244 | Short rural | Planned |  | 56 | 420 | 0.077378 | 0.00018423 | No
2020-05-15 | 7:30 | 9046 | Urban | Planned |  | 58 | 480 | 0.03715 | 7.7395e-05 | No
2020-05-15 | 8:00 | BWC2 | Short rural | Planned |  | 10 | 475 | 0.015627 | 3.2899e-05 | No
2020-05-15 | 8:00 | 8694 | Urban | Planned |  | 135 | 480 | 0.086469 | 0.00018014 | No
2020-05-15 | 8:00 | 9032 | Short rural | Planned |  | 37 | 540 | 0.065731 | 0.00012172 | No
2020-05-15 | 8:00 | OP1172 | Urban | Planned |  | 2 | 465 | 0.001241 | 2.6688e-06 | No
2020-05-15 | 9:00 | KVA2 | Short rural | Planned |  | 61 | 255 | 0.051174 | 0.00020068 | No
2020-05-15 | 8:00 | 35769 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-05-15 | 8:00 | 68195 | Urban | Planned |  | 140 | 420 | 0.078463 | 0.00018682 | No
2020-05-15 | 8:00 | MYG2 | Urban | Planned |  | 75 | 380 | 0.03803 | 0.00010008 | No
2020-05-16 | 8:00 | BK1299 | Short rural | Planned |  | 50 | 450 | 0.074022 | 0.00016449 | No
2020-05-16 | 8:30 | R260 | Short rural | Planned |  | 12 | 390 | 0.015397 | 3.9478e-05 | No
2020-05-16 | 7:30 | HR1206 | Urban | Planned |  | 129 | 480 | 0.082626 | 0.00017214 | No
2020-05-16 | 8:00 | X881 | Short rural | Planned |  | 66 | 510 | 0.11074 | 0.00021713 | No
2020-05-17 | 9:00 | C852 | Urban | Planned |  | 78 | 300 | 0.031225 | 0.00010408 | No
2020-05-17 | 10:00 | 35695 | Short rural | Planned |  | 23 | 360 | 0.02724 | 7.5667e-05 | No
2020-05-17 | 8:00 | 8685 | Urban | Planned |  | 53 | 480 | 0.033947 | 7.0723e-05 | No
2020-05-17 | 8:00 | 8610 | Urban | Planned |  | 13 | 400 | 0.0069389 | 1.7347e-05 | No
2020-05-17 | 8:00 | MVH2 | Short rural | Planned |  | 3 | 479 | 0.0047275 | 9.8696e-06 | No
2020-05-17 | 7:00 | RD1233 | Urban | Planned |  | 34 | 420 | 0.019055 | 4.537e-05 | No
2020-05-17 | 8:00 | DFA2 | Short rural | Planned |  | 7 | 485 | 0.011169 | 2.3029e-05 | No
2020-05-17 | 6:00 | SQ1352 | Urban | Planned |  | 215 | 630 | 0.18074 | 0.0002869 | No
2020-05-18 | 8:00 | MG1267 | Short rural | Planned |  | 110 | 440 | 0.15923 | 0.00036188 | No
2020-05-18 | 7:00 | HT1203 | Urban | Planned |  | 10 | 600 | 0.0080064 | 1.3344e-05 | No
2020-05-18 | 8:00 | DP1284 | Short rural | Planned |  | 11 | 460 | 0.016647 | 3.6188e-05 | No
2020-05-18 | 8:00 | LL1162 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2020-05-18 | 8:00 | WL1292 | Urban | Planned |  | 121 | 420 | 0.067814 | 0.00016146 | No
2020-05-18 | 8:00 | 8611 | Urban | Planned |  | 11 | 360 | 0.0052842 | 1.4678e-05 | No
2020-05-18 | 7:30 | CV1251 | Urban | Planned |  | 61 | 445 | 0.036222 | 8.1398e-05 | No
2020-05-19 | 8:00 | CS1247 | Urban | Planned |  | 58 | 540 | 0.041793 | 7.7395e-05 | No
2020-05-19 | 8:00 | LP1142 | Urban | Planned |  | 47 | 480 | 0.030104 | 6.2717e-05 | No
2020-05-19 | 8:00 | L588 | Short rural | Planned |  | 5 | 450 | 0.0074022 | 1.6449e-05 | No
2020-05-19 | 8:30 | NA1270 | Short rural | Planned |  | 3 | 458 | 0.0045203 | 9.8696e-06 | No
2020-05-19 | 8:30 | JBB2 | Short rural | Planned |  | 5 | 340 | 0.0055928 | 1.6449e-05 | No
2020-05-19 | 8:00 | MYG2 | Urban | Planned |  | 117 | 425 | 0.066353 | 0.00015612 | No
2020-05-19 | 8:00 | SN1230 | Short rural | Planned |  | 23 | 320 | 0.024213 | 7.5667e-05 | No
2020-05-19 | 8:00 | 8650 | Short rural | Planned |  | 2 | 120 | 0.00078957 | 6.5797e-06 | No
2020-05-19 | 8:00 | BWF2 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-05-19 | 8:00 | SY1222 | Urban | Planned |  | 83 | 480 | 0.053162 | 0.00011076 | No
2020-05-19 | 8:00 | CX1210 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-05-19 | 8:00 | MR2205 | Short rural | Planned |  | 2 | 540 | 0.0035531 | 6.5797e-06 | No
2020-05-19 | 8:00 | X482 | Short rural | Planned |  | 31 | 480 | 0.048953 | 0.00010199 | No
2020-05-19 | 8:30 | ULL2 | Short rural | Planned |  | 4 | 393 | 0.0051717 | 1.3159e-05 | No
2020-05-19 | 8:00 | BL1210 | Short rural | Planned |  | 66 | 220 | 0.047769 | 0.00021713 | No
2020-05-19 | 8:00 | A098 | Short rural | Planned |  | 11 | 540 | 0.019542 | 3.6188e-05 | No
2020-05-20 | 8:00 | RD1251 | Urban | Planned |  | 152 | 480 | 0.097358 | 0.00020283 | No
2020-05-20 | 8:00 | KVC2 | Short rural | Planned |  | 14 | 397 | 0.018285 | 4.6058e-05 | No
2020-05-20 | 8:00 | PH1219 | Urban | Planned |  | 2 | 540 | 0.0014412 | 2.6688e-06 | No
2020-05-20 | 8:00 | 35418 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-05-20 | 8:00 | R260 | Short rural | Planned |  | 1 | 50 | 0.00016449 | 3.2899e-06 | No
2020-05-20 | 8:00 | X217 | Short rural | Planned |  | 13 | 480 | 0.020529 | 4.2768e-05 | No
2020-05-20 | 8:00 | NWE2 | Urban | Planned |  | 69 | 385 | 0.035448 | 9.2074e-05 | No
2020-05-20 | 8:30 | JBB2 | Short rural | Planned |  | 5 | 430 | 0.0070732 | 1.6449e-05 | No
2020-05-20 | 8:00 | RBE2 | Short rural | Planned |  | 24 | 386 | 0.030477 | 7.8957e-05 | No
2020-05-20 | 8:00 | 10251 | Urban | Planned |  | 74 | 334 | 0.032981 | 9.8746e-05 | No
2020-05-20 | 7:30 | HR1236 | Urban | Planned |  | 258 | 480 | 0.16525 | 0.00034427 | No
2020-05-20 | 8:30 | SHB2 | Urban | Planned |  | 19 | 410 | 0.010395 | 2.5354e-05 | No
2020-05-20 | 8:00 | T889 | Urban | Planned |  | 78 | 480 | 0.04996 | 0.00010408 | No
2020-05-20 | 8:00 | 25450 | Short rural | Planned |  | 13 | 428 | 0.018305 | 4.2768e-05 | No
2020-05-20 | 8:30 | ULE2 | Short rural | Planned |  | 12 | 403 | 0.01591 | 3.9478e-05 | No
2020-05-20 | 8:00 | W164 | Short rural | Planned |  | 8 | 480 | 0.012633 | 2.6319e-05 | No
2020-05-21 | 8:00 | YYB2 | Short rural | Planned |  | 54 | 586 | 0.1041 | 0.00017765 | No
2020-05-21 | 8:00 | T836 | Short rural | Planned |  | 1 | 380 | 0.0012501 | 3.2899e-06 | No
2020-05-21 | 8:30 | BDA2 | Short rural | Planned |  | 13 | 385 | 0.016466 | 4.2768e-05 | No
2020-05-21 | 8:00 | 8615 | Urban | Planned |  | 37 | 480 | 0.023699 | 4.9373e-05 | No
2020-05-21 | 8:30 | CR1280 | Urban | Planned |  | 68 | 450 | 0.040833 | 9.0739e-05 | No
2020-05-21 | 8:00 | 9033 | Urban | Planned |  | 83 | 540 | 0.059808 | 0.00011076 | No
2020-05-21 | 7:00 | 25783 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2020-05-21 | 8:00 | TM1232 | Short rural | Planned |  | 32 | 315 | 0.033162 | 0.00010528 | No
2020-05-21 | 8:30 | JBB2 | Short rural | Planned |  | 5 | 235 | 0.0038656 | 1.6449e-05 | No
2020-05-21 | 8:00 | 9033 | Urban | Planned |  | 246 | 540 | 0.17726 | 0.00032826 | No
2020-05-21 | 8:00 | CX1232 | Short rural | Planned |  | 5 | 480 | 0.0078957 | 1.6449e-05 | No
2020-05-21 | 8:00 | SG1247 | Urban | Planned |  | 63 | 480 | 0.040352 | 8.4067e-05 | No
2020-05-21 | 8:00 | BWH2 | Short rural | Planned |  | 49 | 409 | 0.065932 | 0.0001612 | No
2020-05-21 | 8:00 | BYB2 | Short rural | Planned |  | 29 | 380 | 0.036254 | 9.5406e-05 | No
2020-05-21 | 8:00 | CX1232 | Short rural | Planned |  | 16 | 480 | 0.025266 | 5.2638e-05 | No
2020-05-21 | 8:00 | 7981 | Urban | Planned |  | 32 | 480 | 0.020496 | 4.2701e-05 | No
2020-05-22 | 8:00 | X217 | Short rural | Planned |  | 9 | 480 | 0.014212 | 2.9609e-05 | No
2020-05-22 | 8:00 | T828 | Short rural | Planned |  | 1 | 240 | 0.00078957 | 3.2899e-06 | No
2020-05-22 | 8:00 | OP1262 | Short rural | Planned |  | 60 | 510 | 0.10067 | 0.00019739 | No
2020-05-22 | 8:00 | 8683 | Urban | Planned |  | 240 | 480 | 0.15372 | 0.00032026 | No
2020-05-22 | 8:00 | BL1232 | Short rural | Planned |  | 96 | 425 | 0.13423 | 0.00031583 | No
2020-05-22 | 8:00 | NA1225 | Short rural | Planned |  | 13 | 198 | 0.0084681 | 4.2768e-05 | No
2020-05-22 | 8:00 | 8686 | Short rural | Planned |  | 145 | 480 | 0.22897 | 0.00047703 | No
2020-05-22 | 7:30 | HR1247 | Urban | Planned |  | 186 | 480 | 0.11914 | 0.0002482 | No
2020-05-22 | 7:00 | HT1203 | Urban | Planned |  | 6 | 240 | 0.0019215 | 8.0064e-06 | No
2020-05-22 | 8:30 | KMC2 | Short rural | Planned |  | 68 | 280 | 0.062639 | 0.00022371 | No
2020-05-23 | 5:30 | 54684 | Urban | Planned |  | 1 | 1230 | 0.0016413 | 1.3344e-06 | No
2020-05-23 | 9:00 | L509 | Urban | Planned |  | 22 | 480 | 0.014091 | 2.9357e-05 | No
2020-05-23 | 8:00 | OP1122 | Short rural | Planned |  | 9 | 540 | 0.015989 | 2.9609e-05 | No
2020-05-23 | 8:00 | X877 | Short rural | Planned |  | 23 | 540 | 0.04086 | 7.5667e-05 | No
2020-05-23 | 8:00 | S738 | Short rural | Planned |  | 8 | 480 | 0.012633 | 2.6319e-05 | No
2020-05-24 | 9:00 | WP1290 | Urban | Planned |  | 4 | 300 | 0.0016013 | 5.3376e-06 | No
2020-05-24 | 8:00 | NWE2 | Urban | Planned |  | 22 | 240 | 0.0070456 | 2.9357e-05 | No
2020-05-24 | 7:30 | A051 | Urban | Planned |  | 49 | 570 | 0.03727 | 6.5386e-05 | No
2020-05-24 | 8:00 | GL1207 | Short rural | Planned |  | 23 | 540 | 0.04086 | 7.5667e-05 | No
2020-05-24 | 10:00 | CA1269 | Urban | Planned |  | 64 | 495 | 0.042274 | 8.5402e-05 | No
2020-05-24 | 7:00 | T900 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2020-05-25 | 8:00 | 9032 | Short rural | Planned |  | 24 | 600 | 0.047374 | 7.8957e-05 | No
2020-05-25 | 10:00 | RBB2 | Short rural | Planned |  | 2 | 240 | 0.0015791 | 6.5797e-06 | No
2020-05-25 | 10:00 | C823 | Urban | Planned |  | 60 | 121 | 0.0096877 | 8.0064e-05 | No
2020-05-25 | 9:00 | BYD2 | Short rural | Planned |  | 8 | 90 | 0.0023687 | 2.6319e-05 | No
2020-05-25 | 3:00 | B204 | Urban | Planned |  | 39 | 420 | 0.021857 | 5.2042e-05 | No
2020-05-25 | 8:00 | MR2205 | Short rural | Planned |  | 82 | 540 | 0.14568 | 0.00026977 | No
2020-05-25 | 8:00 | 8648 | Urban | Planned |  | 6 | 480 | 0.0038431 | 8.0064e-06 | No
2020-05-23 | 5:30 | 54684 | Urban | Planned |  | 1 | 1230 | 0.0016413 | 1.3344e-06 | No
2020-05-25 | 8:00 | MG1219 | Short rural | Planned |  | 13 | 480 | 0.020529 | 4.2768e-05 | No
2020-05-25 | 8:00 | SV1142 | Urban | Planned |  | 6 | 540 | 0.0043235 | 8.0064e-06 | No
2020-05-25 | 8:00 | MR2205 | Short rural | Planned |  | 11 | 540 | 0.019542 | 3.6188e-05 | No
2020-05-26 | 7:30 | A347 | Urban | Planned |  | 34 | 278 | 0.012613 | 4.537e-05 | No
2020-05-26 | 8:00 | S764 | Short rural | Planned |  | 6 | 540 | 0.010659 | 1.9739e-05 | No
2020-05-26 | 8:00 | 10250 | Short rural | Planned |  | 51 | 450 | 0.075502 | 0.00016778 | No
2020-05-26 | 8:00 | X867 | Urban | Planned |  | 195 | 249 | 0.064792 | 0.00026021 | No
2020-05-26 | 8:00 | T834 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2020-05-26 | 8:00 | S764 | Short rural | Planned |  | 6 | 540 | 0.010659 | 1.9739e-05 | No
2020-05-26 | 8:00 | C855 | Short rural | Planned |  | 40 | 360 | 0.047374 | 0.00013159 | No
2020-05-26 | 8:30 | NL1322 | Urban | Planned |  | 147 | 210 | 0.041193 | 0.00019616 | No
2020-05-26 | 8:00 | D810 | Short rural | Planned |  | 40 | 480 | 0.063165 | 0.00013159 | No
2020-05-26 | 8:00 | 9022 | Urban | Planned |  | 62 | 480 | 0.039712 | 8.2733e-05 | No
2020-05-26 | 8:00 | MS1202 | Short rural | Planned |  | 1 | 540 | 0.0017765 | 3.2899e-06 | No
2020-05-26 | 8:00 | RV1246 | Short rural | Planned |  | 77 | 190 | 0.048131 | 0.00025332 | No
2020-05-26 | 8:00 | S737 | Short rural | Planned |  | 27 | 754 | 0.066975 | 8.8826e-05 | No
2020-05-26 | 8:00 | NK1352 | Urban | Planned |  | 4 | 239 | 0.0012757 | 5.3376e-06 | No
2020-05-26 | 8:00 | DS1204 | Urban | Planned |  | 83 | 480 | 0.053162 | 0.00011076 | No
2020-05-26 | 8:30 | SHH2 | Short rural | Planned |  | 67 | 420 | 0.092577 | 0.00022042 | No
2020-05-26 | 8:00 | MYQ2 | Short rural | Planned |  | 72 | 480 | 0.1137 | 0.00023687 | No
2020-05-26 | 8:00 | 6431 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-05-26 | 8:00 | BDD2 | Urban | Planned |  | 4 | 460 | 0.0024553 | 5.3376e-06 | No
2020-05-27 | 8:30 | GG1232 | Short rural | Planned |  | 41 | 85 | 0.011465 | 0.00013488 | No
2020-05-27 | 8:00 | RW1281 | Short rural | Planned |  | 28 | 360 | 0.033162 | 9.2116e-05 | No
2020-05-27 | 8:30 | 25449 | Short rural | Planned |  | 5 | 390 | 0.0064152 | 1.6449e-05 | No
2020-05-27 | 8:00 | CT1296 | Urban | Planned |  | 11 | 420 | 0.0061649 | 1.4678e-05 | No
2020-05-27 | 8:00 | WP1241 | Urban | Planned |  | 12 | 480 | 0.0076861 | 1.6013e-05 | No
2020-05-27 | 7:30 | CV1213 | Urban | Planned |  | 67 | 480 | 0.042914 | 8.9405e-05 | No
2020-05-27 | 9:00 | ULD2 | Urban | Planned |  | 298 | 450 | 0.17894 | 0.00039765 | No
2020-05-27 | 8:00 | CLB2 | Short rural | Planned |  | 419 | 385 | 0.5307 | 0.0013785 | No
2020-05-27 | 8:00 | RW1292 | Short rural | Planned |  | 21 | 480 | 0.033162 | 6.9087e-05 | No
2020-05-27 | 8:00 | X482 | Short rural | Planned |  | 25 | 480 | 0.039478 | 8.2247e-05 | No
2020-05-27 | 8:00 | MYQ2 | Short rural | Planned |  | 210 | 421 | 0.29086 | 0.00069087 | No
2020-05-27 | 8:00 | L582 | Short rural | Planned |  | 10 | 510 | 0.016778 | 3.2899e-05 | No
2020-05-27 | 8:00 | CX1273 | Short rural | Planned |  | 20 | 480 | 0.031583 | 6.5797e-05 | No
2020-05-27 | 8:30 | APB2 | Short rural | Planned |  | 45 | 320 | 0.047374 | 0.00014804 | No
2020-05-27 | 8:00 | R210 | Short rural | Planned |  | 49 | 450 | 0.072541 | 0.0001612 | No
2020-05-27 | 8:00 | T889 | Urban | Planned |  | 58 | 265 | 0.02051 | 7.7395e-05 | No
2020-05-28 | 7:30 | WL1236 | Urban | Planned |  | 134 | 397 | 0.070987 | 0.00017881 | No
2020-05-28 | 7:30 | R260 | Short rural | Planned |  | 10 | 420 | 0.013817 | 3.2899e-05 | No
2020-05-28 | 8:00 | APB2 | Short rural | Planned |  | 7 | 510 | 0.011745 | 2.3029e-05 | No
2020-05-28 | 8:00 | 35418 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-05-28 | 8:00 | MVF2 | Short rural | Planned |  | 16 | 378 | 0.019897 | 5.2638e-05 | No
2020-05-28 | 8:00 | CX1232 | Short rural | Planned |  | 12 | 480 | 0.01895 | 3.9478e-05 | No
2020-05-28 | 8:00 | 1962 | Urban | Planned |  | 87 | 480 | 0.055725 | 0.00011609 | No
2020-05-28 | 8:00 | 87222 | Long rural | Planned |  | 6 | 480 | 9.172 | 0.019108 | No
2020-05-28 | 8:30 | CX1210 | Short rural | Planned |  | 8 | 420 | 0.011054 | 2.6319e-05 | No
2020-05-28 | 8:00 | L591 | Short rural | Planned |  | 49 | 540 | 0.08705 | 0.0001612 | No
2020-05-28 | 7:30 | 35983 | Short rural | Planned |  | 121 | 540 | 0.21496 | 0.00039807 | No
2020-05-28 | 8:00 | 1957 | Urban | Planned |  | 171 | 480 | 0.10953 | 0.00022818 | No
2020-05-29 | 8:00 | 9022 | Urban | Planned |  | 97 | 120 | 0.015532 | 0.00012944 | No
2020-05-29 | 8:00 | S741 | Short rural | Planned |  | 52 | 480 | 0.082115 | 0.00017107 | No
2020-05-29 | 8:00 | A048 | Urban | Planned |  | 8 | 315 | 0.0033627 | 1.0675e-05 | No
2020-05-29 | 8:00 | CLA2 | Short rural | Planned |  | 18 | 390 | 0.023095 | 5.9218e-05 | No
2020-05-29 | 8:00 | 8690 | Urban | Planned |  | 189 | 480 | 0.12106 | 0.0002522 | No
2020-05-29 | 8:30 | SXC2 | Short rural | Planned |  | 10 | 320 | 0.010528 | 3.2899e-05 | No
2020-05-29 | 8:00 | APE2 | Short rural | Planned |  | 67 | 415 | 0.091475 | 0.00022042 | No
2020-05-29 | 8:30 | SHD2 | Short rural | Planned |  | 104 | 435 | 0.14883 | 0.00034215 | No
2020-05-29 | 8:00 | W124 | Short rural | Planned |  | 209 | 300 | 0.20627 | 0.00068758 | No
2020-05-29 | 1:00 | 35388 | Urban | Planned |  | 33 | 240 | 0.010568 | 4.4035e-05 | No
2020-05-30 | 8:00 | 35004 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-05-30 | 8:00 | AZ1264 | Urban | Planned |  | 7 | 480 | 0.0044836 | 9.3408e-06 | No
2020-05-30 | 7:00 | RS1262 | Urban | Planned |  | 11 | 660 | 0.0096877 | 1.4678e-05 | No
2020-05-30 | 9:00 | 25450 | Short rural | Planned |  | 5 | 660 | 0.010857 | 1.6449e-05 | No
2020-05-31 | 8:00 | KYE2 | Urban | Planned |  | 22 | 480 | 0.014091 | 2.9357e-05 | No
2020-05-31 | 6:00 | 27189 | Urban | Planned |  | 3 | 600 | 0.0024019 | 4.0032e-06 | No
2020-05-31 | 8:00 | 27335 | Urban | Planned |  | 33 | 480 | 0.021137 | 4.4035e-05 | No
2020-05-31 | 7:30 | FF1243 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-05-31 | 8:00 | 9022 | Urban | Planned |  | 122 | 480 | 0.078142 | 0.0001628 | No
2020-05-31 | 7:00 | 17069 | Urban | Planned |  | 4 | 480 | 0.002562 | 5.3376e-06 | No
2020-05-31 | 8:00 | 27191 | Urban | Planned |  | 21 | 540 | 0.015132 | 2.8022e-05 | No
2020-05-31 | 8:00 | SN1208 | Short rural | Planned |  | 93 | 300 | 0.091787 | 0.00030596 | No
2020-05-31 | 8:00 | W190 | Urban | Planned |  | 23 | 480 | 0.014732 | 3.0691e-05 | No
2020-05-31 | 8:00 | S738 | Short rural | Planned |  | 10 | 540 | 0.017765 | 3.2899e-05 | No
2020-05-31 | 8:00 | 25783 | Urban | Planned |  | 21 | 540 | 0.015132 | 2.8022e-05 | No
2020-06-01 | 10:00 | SWE2 | Urban | Planned |  | 14 | 200 | 0.0037363 | 1.8682e-05 | No
2020-06-01 | 8:00 | B775 | Urban | Planned |  | 1 | 195 | 0.00026021 | 1.3344e-06 | No
2020-06-01 | 11:30 | WP1245 | Urban | Planned |  | 32 | 240 | 0.010248 | 4.2701e-05 | No
2020-06-01 | 8:00 | CR1228 | Urban | Planned |  | 115 | 600 | 0.092074 | 0.00015346 | No
2020-06-01 | 8:00 | M399 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-06-02 | 8:00 | 35982 | Short rural | Planned |  | 22 | 215 | 0.015561 | 7.2377e-05 | No
2020-06-02 | 8:00 | S790 | Short rural | Planned |  | 4 | 420 | 0.005527 | 1.3159e-05 | No
2020-06-02 | 6:00 | J499 | Urban | Planned |  | 199 | 680 | 0.18057 | 0.00026555 | No
2020-06-02 | 8:30 | ULH2 | Short rural | Planned |  | 6 | 355 | 0.0070074 | 1.9739e-05 | No
2020-06-02 | 8:00 | NM1213 | Urban | Planned |  | 57 | 600 | 0.045636 | 7.6061e-05 | No
2020-06-02 | 8:00 | RW1218 | Short rural | Planned |  | 32 | 465 | 0.048953 | 0.00010528 | No
2020-06-02 | 8:00 | ER1232 | Short rural | Planned |  | 105 | 480 | 0.16581 | 0.00034544 | No
2020-06-02 | 8:00 | CD1260 | Urban | Planned |  | 236 | 450 | 0.14171 | 0.00031492 | No
2020-06-02 | 8:00 | X213 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2020-06-02 | 2:00 | RW1255 | Short rural | Planned |  | 1 | 38 | 0.00012501 | 3.2899e-06 | No
2020-06-02 | 8:30 | KMF2 | Urban | Planned |  | 127 | 420 | 0.071177 | 0.00016947 | No
2020-06-02 | 8:30 | APA2 | Urban | Planned |  | 3 | 390 | 0.0015612 | 4.0032e-06 | No
2020-06-02 | 8:00 | WP1245 | Urban | Planned |  | 67 | 239 | 0.021368 | 8.9405e-05 | No
2020-06-02 | 8:00 | A095 | Short rural | Planned |  | 25 | 540 | 0.044413 | 8.2247e-05 | No
2020-06-02 | 2:00 | HS1242 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-06-02 | 8:00 | BK1288 | Short rural | Planned |  | 9 | 340 | 0.010067 | 2.9609e-05 | No
2020-06-02 | 12:30 | RW1255 | Short rural | Planned |  | 2 | 46 | 0.00030267 | 6.5797e-06 | No
2020-06-02 | 1:30 | NM1243 | Urban | Planned |  | 21 | 210 | 0.0058847 | 2.8022e-05 | No
2020-06-02 | 7:30 | D845 | Urban | Planned |  | 64 | 480 | 0.040993 | 8.5402e-05 | No
2020-06-02 | 8:00 | CR1228 | Urban | Planned |  | 82 | 600 | 0.065652 | 0.00010942 | No
2020-06-02 | 8:00 | RS1262 | Urban | Planned |  | 15 | 600 | 0.01201 | 2.0016e-05 | No
2020-06-02 | 8:00 | 5496 | Urban | Planned |  | 138 | 480 | 0.088391 | 0.00018415 | No
2020-06-02 | 10:30 | RW1292 | Short rural | Planned |  | 1 | 40 | 0.00013159 | 3.2899e-06 | No
2020-06-03 | 7:30 | HS1222 | Short rural | Planned |  | 22 | 352 | 0.025477 | 7.2377e-05 | No
2020-06-03 | 8:30 | KVB2 | Short rural | Planned |  | 29 | 425 | 0.040548 | 9.5406e-05 | No
2020-06-03 | 1:00 | WP1264 | Urban | Planned |  | 25 | 240 | 0.0080064 | 3.336e-05 | No
2020-06-03 | 8:30 | WWE2 | Urban | Planned |  | 89 | 510 | 0.060568 | 0.00011876 | No
2020-06-03 | 8:00 | MG1267 | Short rural | Planned |  | 2 | 120 | 0.00078957 | 6.5797e-06 | No
2020-06-03 | 8:00 | X217 | Short rural | Planned |  | 13 | 221 | 0.0094518 | 4.2768e-05 | No
2020-06-03 | 8:00 | W111 | Short rural | Planned |  | 41 | 240 | 0.032372 | 0.00013488 | No
2020-06-03 | 8:00 | FT1205 | Short rural | Planned |  | 65 | 460 | 0.098367 | 0.00021384 | No
2020-06-03 | 12:00 | 35990 | Short rural | Planned |  | 1 | 300 | 0.00098696 | 3.2899e-06 | No
2020-06-03 | 2:00 | MG1282 | Short rural | Planned |  | 6 | 45 | 0.00088826 | 1.9739e-05 | No
2020-06-03 | 8:00 | BWC2 | Short rural | Planned |  | 38 | 400 | 0.050006 | 0.00012501 | No
2020-06-03 | 8:00 | CX1273 | Short rural | Planned |  | 20 | 480 | 0.031583 | 6.5797e-05 | No
2020-06-03 | 8:00 | OA1233 | Short rural | Planned |  | 19 | 328 | 0.020502 | 6.2507e-05 | No
2020-06-03 | 12:00 | MG1282 | Short rural | Planned |  | 2 | 55 | 0.00036188 | 6.5797e-06 | No
2020-06-03 | 8:00 | 9032 | Short rural | Planned |  | 111 | 540 | 0.19719 | 0.00036517 | No
2020-06-03 | 7:30 | BK1299 | Short rural | Planned |  | 40 | 480 | 0.063165 | 0.00013159 | No
2020-06-03 | 8:00 | M400 | Urban | Planned |  | 59 | 510 | 0.040152 | 7.873e-05 | No
2020-06-03 | 8:00 | RS1262 | Urban | Planned |  | 1 | 239 | 0.00031892 | 1.3344e-06 | No
2020-06-03 | 8:00 | 9027 | Urban | Planned |  | 109 | 540 | 0.078543 | 0.00014545 | No
2020-06-03 | 10:00 | MG1219 | Short rural | Planned |  | 1 | 76 | 0.00025003 | 3.2899e-06 | No
2020-06-04 | 7:30 | A347 | Urban | Planned |  | 32 | 2400.625 | 0.10251 | 4.2701e-05 | No
2020-06-04 | 8:00 | RBE2 | Short rural | Planned |  | 24 | 405 | 0.031977 | 7.8957e-05 | No
2020-06-04 | 8:00 | R210 | Short rural | Planned |  | 60 | 450 | 0.088826 | 0.00019739 | No
2020-06-04 | 8:00 | 35405 | Urban | Planned |  | 21 | 239 | 0.0066973 | 2.8022e-05 | No
2020-06-04 | 8:00 | T838 | Short rural | Planned |  | 5 | 480 | 0.0078957 | 1.6449e-05 | No
2020-06-04 | 8:00 | APC2 | Short rural | Planned |  | 4 | 735 | 0.0096722 | 1.3159e-05 | No
2020-06-04 | 8:00 | CLB2 | Short rural | Planned |  | 419 | 425 | 0.58584 | 0.0013785 | No
2020-06-04 | 8:00 | CX1206 | Short rural | Planned |  | 16 | 410 | 0.021582 | 5.2638e-05 | No
2020-06-04 | 8:00 | SY1112 | Urban | Planned |  | 100 | 480 | 0.064051 | 0.00013344 | No
2020-06-04 | 8:00 | J505 | Urban | Planned |  | 91 | 340 | 0.041286 | 0.00012143 | No
2020-06-04 | 8:00 | B202 | Urban | Planned |  | 1 | 416 | 0.00055511 | 1.3344e-06 | No
2020-06-04 | 8:00 | APE2 | Short rural | Planned |  | 7 | 510 | 0.011745 | 2.3029e-05 | No
2020-06-04 | 8:00 | NWF2 | Urban | Planned |  | 55 | 415 | 0.030458 | 7.3392e-05 | No
2020-06-04 | 8:00 | PH1264 | Urban | Planned |  | 3 | 540 | 0.0021617 | 4.0032e-06 | No
2020-06-04 | 8:00 | A347 | Urban | Planned |  | 135 | 531.9259 | 0.095823 | 0.00018014 | No
2020-06-04 | 7:00 | 35764 | Urban | Planned |  | 2 | 3900 | 0.010408 | 2.6688e-06 | No
2020-06-04 | 8:00 | WWB2 | Short rural | Planned |  | 95 | 395 | 0.12345 | 0.00031254 | No
2020-06-04 | 8:00 | 35764 | Urban | Planned |  | 11 | 638.1818 | 0.0093675 | 1.4678e-05 | No
2020-06-04 | 8:00 | 8735 | Urban | Planned |  | 27 | 480 | 0.017294 | 3.6029e-05 | No
2020-06-04 | 8:30 | KMF2 | Urban | Planned |  | 127 | 350 | 0.059314 | 0.00016947 | No
2020-06-04 | 8:00 | X482 | Short rural | Planned |  | 22 | 480 | 0.034741 | 7.2377e-05 | No
2020-06-04 | 8:00 | MVB2 | Short rural | Planned |  | 116 | 540 | 0.20608 | 0.00038162 | No
2020-06-04 | 8:00 | WWD2 | Urban | Planned |  | 1 | 120 | 0.00016013 | 1.3344e-06 | No
2020-06-04 | 8:00 | CX1210 | Short rural | Planned |  | 4 | 480 | 0.0063165 | 1.3159e-05 | No
2020-06-05 | 10:00 | DP1258 | Short rural | Planned |  | 17 | 13 | 0.00072706 | 5.5928e-05 | No
2020-06-05 | 8:30 | JBA2 | Short rural | Planned |  | 70 | 482 | 0.111 | 0.00023029 | No
2020-06-05 | 1:00 | 35405 | Urban | Planned |  | 11 | 240 | 0.0035228 | 1.4678e-05 | No
2020-06-05 | 8:00 | L588 | Short rural | Planned |  | 12 | 240 | 0.0094748 | 3.9478e-05 | No
2020-06-05 | 8:00 | 1957 | Urban | Planned |  | 65 | 480 | 0.041633 | 8.6736e-05 | No
2020-06-05 | 8:00 | CX1232 | Short rural | Planned |  | 12 | 480 | 0.01895 | 3.9478e-05 | No
2020-06-05 | 8:30 | 25449 | Short rural | Planned |  | 23 | 30 | 0.00227 | 7.5667e-05 | No
2020-06-05 | 8:00 | NA1225 | Short rural | Planned |  | 50 | 358 | 0.058889 | 0.00016449 | No
2020-06-05 | 8:00 | CX1232 | Short rural | Planned |  | 229 | 480 | 0.36162 | 0.00075338 | No
2020-06-05 | 7:30 | WQ1275 | Urban | Planned |  | 14 | 400 | 0.0074726 | 1.8682e-05 | No
2020-06-05 | 9:00 | MG1267 | Short rural | Planned |  | 2 | 180 | 0.0011844 | 6.5797e-06 | No
2020-06-05 | 8:00 | MG1267 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2020-06-05 | 8:00 | NG1247 | Urban | Planned |  | 71 | 480 | 0.045476 | 9.4742e-05 | No
2020-06-05 | 8:00 | X217 | Short rural | Planned |  | 51 | 420 | 0.070469 | 0.00016778 | No
2020-06-05 | 11:00 | L591 | Short rural | Planned |  | 2 | 240 | 0.0015791 | 6.5797e-06 | No
2020-06-06 | 8:00 | A045 | Short rural | Planned |  | 144 | 480 | 0.2274 | 0.00047374 | No
2020-06-06 | 9:30 | BDH2 | Short rural | Planned |  | 117 | 510 | 0.19631 | 0.00038491 | No
2020-06-06 | 8:00 | HT1291 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-06-07 | 6:00 | NN1285 | Short rural | Planned |  | 14 | 600 | 0.027635 | 4.6058e-05 | No
2020-06-07 | 8:00 | NM1243 | Urban | Planned |  | 34 | 480 | 0.021777 | 4.537e-05 | No
2020-06-07 | 6:00 | 55354 | Urban | Planned |  | 205 | 480 | 0.1313 | 0.00027355 | No
2020-06-07 | 2:00 | SY1152 | Urban | Planned |  | 30 | 74 | 0.0029624 | 4.0032e-05 | No
2020-06-07 | 7:00 | SY1152 | Urban | Planned |  | 44 | 1009.0909 | 0.059247 | 5.8714e-05 | No
2020-06-07 | 8:00 | SN1208 | Short rural | Planned |  | 10 | 426 | 0.014015 | 3.2899e-05 | No
2020-06-08 | 9:00 | W127 | Short rural | Planned |  | 3 | 360 | 0.0035531 | 9.8696e-06 | No
2020-06-09 | 8:00 | GL1233 | Short rural | Planned |  | 33 | 540 | 0.058625 | 0.00010857 | No
2020-06-09 | 8:00 | MVC2 | Short rural | Planned |  | 3 | 462 | 0.0045598 | 9.8696e-06 | No
2020-06-09 | 8:00 | MVH2 | Short rural | Planned |  | 20 | 358 | 0.023555 | 6.5797e-05 | No
2020-06-09 | 8:00 | SZ1122 | Short rural | Planned |  | 20 | 540 | 0.035531 | 6.5797e-05 | No
2020-06-09 | 21:00 | S744 | Urban | Planned |  | 48 | 417 | 0.026709 | 6.4051e-05 | No
2020-06-09 | 8:30 | ULL2 | Short rural | Planned |  | 1 | 485 | 0.0015956 | 3.2899e-06 | No
2020-06-09 | 8:00 | HS1112 | Urban | Planned |  | 5 | 540 | 0.0036029 | 6.672e-06 | No
2020-06-09 | 8:00 | T834 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2020-06-09 | 7:30 | 7972 | Urban | Planned |  | 20 | 480 | 0.01281 | 2.6688e-05 | No
2020-06-09 | 8:00 | B748 | Urban | Planned |  | 91 | 540 | 0.065572 | 0.00012143 | No
2020-06-09 | 10:00 | BWA2 | Short rural | Planned |  | 93 | 105 | 0.032126 | 0.00030596 | No
2020-06-09 | 8:00 | 8689 | Urban | Planned |  | 75 | 480 | 0.048038 | 0.00010008 | No
2020-06-10 | 9:00 | ULK2 | Short rural | Planned |  | 6 | 360 | 0.0071061 | 1.9739e-05 | No
2020-06-10 | 10:00 | R290 | Short rural | Planned |  | 1 | 240 | 0.00078957 | 3.2899e-06 | No
2020-06-10 | 8:30 | SXC2 | Short rural | Planned |  | 12 | 420 | 0.016581 | 3.9478e-05 | No
2020-06-10 | 8:00 | W112 | Short rural | Planned |  | 3 | 350 | 0.0034544 | 9.8696e-06 | No
2020-06-10 | 8:00 | 35818 | Short rural | Planned |  | 68 | 440 | 0.098433 | 0.00022371 | No
2020-06-10 | 6:30 | 27188 | Urban | Planned |  | 56 | 570 | 0.042594 | 7.4726e-05 | No
2020-06-10 | 8:00 | 35333 | Urban | Planned |  | 37 | 480 | 0.023699 | 4.9373e-05 | No
2020-06-10 | 7:30 | A352 | Urban | Planned |  | 43 | 480 | 0.027542 | 5.7379e-05 | No
2020-06-10 | 8:00 | MYQ2 | Short rural | Planned |  | 86 | 370 | 0.10468 | 0.00028293 | No
2020-06-10 | 8:00 | BWF2 | Short rural | Planned |  | 10 | 365 | 0.012008 | 3.2899e-05 | No
2020-06-10 | 8:00 | 87220 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2020-06-10 | 8:30 | ULD2 | Urban | Planned |  | 15 | 450 | 0.0090072 | 2.0016e-05 | No
2020-06-10 | 8:30 | KMF2 | Urban | Planned |  | 127 | 270 | 0.045757 | 0.00016947 | No
2020-06-10 | 8:00 | W164 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2020-06-10 | 8:00 | BWF2 | Short rural | Planned |  | 1 | 410 | 0.0013488 | 3.2899e-06 | No
2020-06-11 | 8:00 | D814 | Short rural | Planned |  | 6 | 480 | 0.0094748 | 1.9739e-05 | No
2020-06-11 | 8:00 | 8615 | Urban | Planned |  | 66 | 480 | 0.042274 | 8.807e-05 | No
2020-06-11 | 8:00 | 25783 | Urban | Planned |  | 2 | 420 | 0.0011209 | 2.6688e-06 | No
2020-06-11 | 8:00 | 87222 | Long rural | Planned |  | 1 | 240 | 0.76433 | 0.0031847 | No
2020-06-11 | 8:00 | NN1251 | Short rural | Planned |  | 11 | 480 | 0.01737 | 3.6188e-05 | No
2020-06-11 | 8:00 | SN1230 | Short rural | Planned |  | 4 | 270 | 0.0035531 | 1.3159e-05 | No
2020-06-11 | 8:00 | CJ1204 | Urban | Planned |  | 65 | 480 | 0.041633 | 8.6736e-05 | No
2020-06-11 | 8:00 | BK1251 | Short rural | Planned |  | 17 | 540 | 0.030201 | 5.5928e-05 | No
2020-06-11 | 8:00 | CX1232 | Short rural | Planned |  | 12 | 480 | 0.01895 | 3.9478e-05 | No
2020-06-11 | 8:00 | RBE2 | Short rural | Planned |  | 36 | 480 | 0.056849 | 0.00011844 | No
2020-06-11 | 8:00 | SN1219 | Short rural | Planned |  | 16 | 395 | 0.020792 | 5.2638e-05 | No
2020-06-11 | 8:30 | KMD2 | Short rural | Planned |  | 303 | 380 | 0.37879 | 0.00099683 | No
2020-06-11 | 7:30 | B214 | Urban | Planned |  | 74 | 480 | 0.047398 | 9.8746e-05 | No
2020-06-11 | 8:00 | 87222 | Long rural | Planned |  | 20 | 480 | 30.5732 | 0.063694 | No
2020-06-11 | 8:00 | FT1205 | Short rural | Planned |  | 15 | 400 | 0.019739 | 4.9348e-05 | No
2020-06-11 | 9:00 | 55876 | Urban | Planned |  | 41 | 540 | 0.029544 | 5.471e-05 | No
2020-06-11 | 8:00 | 55177 | Urban | Planned |  | 7 | 480 | 0.0044836 | 9.3408e-06 | No
2020-06-11 | 8:00 | CD1260 | Urban | Planned |  | 156 | 540 | 0.11241 | 0.00020817 | No
2020-06-11 | 9:30 | NL1332 | Urban | Planned |  | 3 | 390 | 0.0015612 | 4.0032e-06 | No
2020-06-11 | 8:00 | T838 | Short rural | Planned |  | 5 | 480 | 0.0078957 | 1.6449e-05 | No
2020-06-12 | 8:30 | GG1258 | Urban | Planned |  | 102 | 360 | 0.048999 | 0.00013611 | No
2020-06-12 | 8:00 | J497 | Short rural | Planned |  | 19 | 300 | 0.018752 | 6.2507e-05 | No
2020-06-12 | 8:00 | ULL2 | Short rural | Planned |  | 29 | 257 | 0.024519 | 9.5406e-05 | No
2020-06-12 | 8:00 | 35388 | Urban | Planned |  | 127 | 480 | 0.081345 | 0.00016947 | No
2020-06-12 | 8:00 | 9032 | Short rural | Planned |  | 11 | 420 | 0.015199 | 3.6188e-05 | No
2020-06-12 | 8:00 | MYM2 | Urban | Planned |  | 40 | 440 | 0.023485 | 5.3376e-05 | No
2020-06-12 | 8:00 | 55870 | Urban | Planned |  | 110 | 330 | 0.048439 | 0.00014678 | No
2020-06-12 | 8:00 | 35418 | Short rural | Planned |  | 24 | 480 | 0.037899 | 7.8957e-05 | No
2020-06-12 | 5:30 | R210 | Short rural | Planned |  | 1 | 60 | 0.00019739 | 3.2899e-06 | No
2020-06-12 | 10:00 | 61617 | Short rural | Planned |  | 75 | 336 | 0.082905 | 0.00024674 | No
2020-06-12 | 12:00 | SWJ2 | Urban | Planned |  | 31 | 170 | 0.0070323 | 4.1366e-05 | No
2020-06-12 | 8:00 | BWE2 | Short rural | Planned |  | 5 | 510 | 0.0083892 | 1.6449e-05 | No
2020-06-12 | 8:00 | L591 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2020-06-12 | 8:00 | J495 | Short rural | Planned |  | 11 | 430 | 0.015561 | 3.6188e-05 | No
2020-06-12 | 8:00 | MVH2 | Short rural | Planned |  | 85 | 340 | 0.095077 | 0.00027964 | No
2020-06-12 | 8:00 | 87222 | Long rural | Planned |  | 1 | 420 | 1.3376 | 0.0031847 | No
2020-06-12 | 6:00 | MR2244 | Urban | Planned |  | 106 | 66 | 0.0093355 | 0.00014145 | No
2020-06-12 | 8:00 | TM1210 | Short rural | Planned |  | 28 | 480 | 0.044216 | 9.2116e-05 | No
2020-06-12 | 7:30 | 68179 | Urban | Planned |  | 173 | 480 | 0.11081 | 0.00023085 | No
2020-06-12 | 8:30 | RW1281 | Short rural | Planned |  | 10 | 461 | 0.015166 | 3.2899e-05 | No
2020-06-13 | 8:00 | J474 | Short rural | Planned |  | 12 | 540 | 0.021318 | 3.9478e-05 | No
2020-06-13 | 9:00 | WX1244 | Urban | Planned |  | 1 | 360 | 0.00048038 | 1.3344e-06 | No
2020-06-13 | 8:00 | PCB2 | Short rural | Planned |  | 33 | 490 | 0.053197 | 0.00010857 | No
2020-06-13 | 8:00 | X881 | Short rural | Planned |  | 47 | 540 | 0.083497 | 0.00015462 | No
2020-06-13 | 7:00 | 35767 | Urban | Planned |  | 1 | 720 | 0.00096077 | 1.3344e-06 | No
2020-06-13 | 8:00 | L544 | Urban | Planned |  | 65 | 480 | 0.041633 | 8.6736e-05 | No
2020-06-14 | 6:00 | 27341 | Urban | Planned |  | 5 | 720 | 0.0048038 | 6.672e-06 | No
2020-06-14 | 5:00 | 49010 | Short rural | Planned |  | 2 | 300 | 0.0019739 | 6.5797e-06 | No
2020-06-14 | 9:00 | 35769 | Urban | Planned |  | 14 | 600 | 0.011209 | 1.8682e-05 | No
2020-06-14 | 7:30 | 49917 | Urban | Planned |  | 62 | 510 | 0.042194 | 8.2733e-05 | No
2020-06-14 | 8:00 | 19856 | Urban | Planned |  | 170 | 480 | 0.10889 | 0.00022685 | No
2020-06-15 | 8:00 | 87222 | Long rural | Planned |  | 6 | 480 | 9.172 | 0.019108 | No
2020-06-15 | 8:30 | KVC2 | Short rural | Planned |  | 2 | 384 | 0.0025266 | 6.5797e-06 | No
2020-06-15 | 8:00 | S738 | Short rural | Planned |  | 52 | 405 | 0.069285 | 0.00017107 | No
2020-06-15 | 8:00 | HBA2 | Short rural | Planned |  | 87 | 340 | 0.097314 | 0.00028622 | No
2020-06-15 | 10:00 | RBB2 | Short rural | Planned |  | 2 | 240 | 0.0015791 | 6.5797e-06 | No
2020-06-16 | 8:00 | 35590 | Short rural | Planned |  | 5 | 455 | 0.0074844 | 1.6449e-05 | No
2020-06-16 | 8:00 | 35816 | Short rural | Planned |  | 26 | 480 | 0.041057 | 8.5536e-05 | No
2020-06-16 | 7:30 | J495 | Short rural | Planned |  | 126 | 810 | 0.33576 | 0.00041452 | No
2020-06-16 | 8:00 | 9032 | Short rural | Planned |  | 4 | 540 | 0.0071061 | 1.3159e-05 | No
2020-06-16 | 7:30 | L588 | Short rural | Planned |  | 35 | 510 | 0.058724 | 0.00011515 | No
2020-06-16 | 8:00 | NA1236 | Short rural | Planned |  | 141 | 155 | 0.0719 | 0.00046387 | No
2020-06-16 | 8:00 | S740 | Urban | Planned |  | 22 | 420 | 0.01233 | 2.9357e-05 | No
2020-06-16 | 8:00 | 35418 | Short rural | Planned |  | 90 | 480 | 0.14212 | 0.00029609 | No
2020-06-16 | 8:00 | 35305 | Urban | Planned |  | 11 | 480 | 0.0070456 | 1.4678e-05 | No
2020-06-16 | 8:00 | MYQ2 | Short rural | Planned |  | 80 | 440 | 0.1158 | 0.00026319 | No
2020-06-16 | 9:00 | PH1223 | Urban | Planned |  | 4 | 300 | 0.0016013 | 5.3376e-06 | No
2020-06-16 | 8:00 | RW1218 | Short rural | Planned |  | 5 | 510 | 0.0083892 | 1.6449e-05 | No
2020-06-16 | 7:30 | 49917 | Urban | Planned |  | 54 | 480 | 0.034588 | 7.2058e-05 | No
2020-06-16 | 8:00 | L537 | Urban | Planned |  | 76 | 360 | 0.036509 | 0.00010141 | No
2020-06-16 | 8:00 | MVC2 | Short rural | Planned |  | 59 | 480 | 0.093169 | 0.0001941 | No
2020-06-16 | 8:00 | DP1284 | Short rural | Planned |  | 3 | 427 | 0.0042143 | 9.8696e-06 | No
2020-06-17 | 8:00 | MG1267 | Short rural | Planned |  | 10 | 480 | 0.015791 | 3.2899e-05 | No
2020-06-17 | 8:30 | YYA2 | Short rural | Planned |  | 8 | 480 | 0.012633 | 2.6319e-05 | No
2020-06-17 | 8:00 | X482 | Short rural | Planned |  | 31 | 480 | 0.048953 | 0.00010199 | No
2020-06-17 | 8:30 | MVF2 | Short rural | Planned |  | 32 | 450 | 0.047374 | 0.00010528 | No
2020-06-17 | 8:00 | J497 | Short rural | Planned |  | 95 | 480 | 0.15002 | 0.00031254 | No
2020-06-17 | 22:00 | WH1257 | Urban | Planned |  | 2 | 300 | 0.00080064 | 2.6688e-06 | No
2020-06-17 | 8:00 | LP1112 | Urban | Planned |  | 5 | 415 | 0.0027689 | 6.672e-06 | No
2020-06-17 | 8:00 | CLB2 | Short rural | Planned |  | 419 | 382 | 0.52657 | 0.0013785 | No
2020-06-17 | 12:00 | RBC2 | Short rural | Planned |  | 2 | 120 | 0.00078957 | 6.5797e-06 | No
2020-06-17 | 8:00 | APB2 | Short rural | Planned |  | 23 | 640 | 0.048427 | 7.5667e-05 | No
2020-06-17 | 9:00 | 7021 | Urban | Planned |  | 3 | 360 | 0.0014412 | 4.0032e-06 | No
2020-06-18 | 8:00 | GL1255 | Short rural | Planned |  | 23 | 480 | 0.03632 | 7.5667e-05 | No
2020-06-18 | 8:00 | TM1258 | Short rural | Planned |  | 306 | 385 | 0.38758 | 0.0010067 | No
2020-06-18 | 8:30 | YYB2 | Short rural | Planned |  | 16 | 330 | 0.01737 | 5.2638e-05 | No
2020-06-18 | 8:00 | ER1252 | Short rural | Planned |  | 156 | 540 | 0.27714 | 0.00051322 | No
2020-06-18 | 8:30 | KMD2 | Short rural | Planned |  | 279 | 355 | 0.32584 | 0.00091787 | No
2020-06-18 | 8:00 | RW1218 | Short rural | Planned |  | 32 | 445 | 0.046848 | 0.00010528 | No
2020-06-18 | 8:00 | KC1236 | Short rural | Planned |  | 13 | 410 | 0.017535 | 4.2768e-05 | No
2020-06-18 | 7:30 | A344 | Urban | Planned |  | 77 | 510 | 0.052402 | 0.00010275 | No
2020-06-18 | 8:00 | 8801 | Short rural | Planned |  | 313 | 480 | 0.49427 | 0.0010297 | No
2020-06-18 | 8:00 | WWA2 | Short rural | Planned |  | 62 | 540 | 0.11014 | 0.00020397 | No
2020-06-18 | 7:30 | R260 | Short rural | Planned |  | 10 | 540 | 0.017765 | 3.2899e-05 | No
2020-06-18 | 8:00 | BDG2 | Short rural | Planned |  | 14 | 500 | 0.023029 | 4.6058e-05 | No
2020-06-18 | 8:00 | X482 | Short rural | Planned |  | 11 | 480 | 0.01737 | 3.6188e-05 | No
2020-06-18 | 8:00 | ULL2 | Short rural | Planned |  | 240 | 405 | 0.31977 | 0.00078957 | No
2020-06-18 | 8:30 | MG1219 | Short rural | Planned |  | 3 | 540 | 0.0053296 | 9.8696e-06 | No
2020-06-18 | 8:00 | 19856 | Urban | Planned |  | 129 | 480 | 0.082626 | 0.00017214 | No
2020-06-19 | 8:00 | D813 | Short rural | Planned |  | 75 | 480 | 0.11844 | 0.00024674 | No
2020-06-19 | 8:00 | CT1225 | Short rural | Planned |  | 69 | 540 | 0.12258 | 0.000227 | No
2020-06-19 | 7:30 | B776 | Urban | Planned |  | 168 | 480 | 0.10761 | 0.00022418 | No
2020-06-19 | 8:00 | KVA2 | Short rural | Planned |  | 19 | 140 | 0.008751 | 6.2507e-05 | No
2020-06-19 | 8:00 | 8798 | Short rural | Planned |  | 20 | 540 | 0.035531 | 6.5797e-05 | No
2020-06-19 | 8:00 | CJ1204 | Urban | Planned |  | 80 | 480 | 0.051241 | 0.00010675 | No
2020-06-19 | 8:00 | KVA2 | Short rural | Planned |  | 7 | 445 | 0.010248 | 2.3029e-05 | No
2020-06-19 | 8:00 | P608 | Short rural | Planned |  | 5 | 480 | 0.0078957 | 1.6449e-05 | No
2020-06-19 | 8:30 | MVF2 | Short rural | Planned |  | 37 | 450 | 0.054776 | 0.00012172 | No
2020-06-19 | 8:30 | ULE2 | Short rural | Planned |  | 3 | 366 | 0.0036123 | 9.8696e-06 | No
2020-06-19 | 8:00 | KC1236 | Short rural | Planned |  | 11 | 349 | 0.01263 | 3.6188e-05 | No
2020-06-19 | 8:00 | BK1236 | Short rural | Planned |  | 82 | 450 | 0.1214 | 0.00026977 | No
2020-06-20 | 9:00 | PH1260 | Urban | Planned |  | 170 | 480 | 0.10889 | 0.00022685 | No
2020-06-20 | 10:00 | 9022 | Urban | Planned |  | 1 | 270 | 0.00036029 | 1.3344e-06 | No
2020-06-21 | 8:00 | C855 | Short rural | Planned |  | 6 | 540 | 0.010659 | 1.9739e-05 | No
2020-06-22 | 7:30 | 9055 | Urban | Planned |  | 53 | 450 | 0.031825 | 7.0723e-05 | No
2020-06-22 | 8:30 | BYB2 | Short rural | Planned |  | 98 | 394 | 0.12703 | 0.00032241 | No
2020-06-22 | 8:00 | RBE2 | Short rural | Planned |  | 4 | 470 | 0.0061849 | 1.3159e-05 | No
2020-06-22 | 8:00 | S786 | Short rural | Planned |  | 25 | 480 | 0.039478 | 8.2247e-05 | No
2020-06-22 | 8:00 | R210 | Short rural | Planned |  | 174 | 450 | 0.2576 | 0.00057244 | No
2020-06-22 | 7:00 | LP1142 | Urban | Planned |  | 78 | 540 | 0.056205 | 0.00010408 | No
2020-06-22 | 8:00 | PH1201 | Urban | Planned |  | 3 | 360 | 0.0014412 | 4.0032e-06 | No
2020-06-22 | 8:00 | S738 | Short rural | Planned |  | 57 | 435 | 0.081572 | 0.00018752 | No
2020-06-22 | 8:00 | S735 | Short rural | Planned |  | 36 | 350 | 0.041452 | 0.00011844 | No
2020-06-22 | 8:30 | ULL2 | Short rural | Planned |  | 5 | 481 | 0.0079121 | 1.6449e-05 | No
2020-06-23 | 8:00 | NG1262 | Short rural | Planned |  | 85 | 480 | 0.13423 | 0.00027964 | No
2020-06-23 | 7:00 | 35695 | Short rural | Planned |  | 18 | 420 | 0.024871 | 5.9218e-05 | No
2020-06-23 | 8:00 | SHK2 | Urban | Planned |  | 79 | 436 | 0.045962 | 0.00010542 | No
2020-06-23 | 2:00 | WH1220 | Urban | Planned |  | 1 | 480 | 0.00064051 | 1.3344e-06 | No
2020-06-23 | 7:00 | CA1210 | Urban | Planned |  | 56 | 600 | 0.044836 | 7.4726e-05 | No
2020-06-23 | 8:00 | ULC2 | Short rural | Planned |  | 143 | 430 | 0.20229 | 0.00047045 | No
2020-06-23 | 8:00 | A051 | Urban | Planned |  | 16 | 480 | 0.010248 | 2.135e-05 | No
2020-06-23 | 7:00 | HT1203 | Urban | Planned |  | 1 | 600 | 0.00080064 | 1.3344e-06 | No
2020-06-23 | 8:00 | MVF2 | Short rural | Planned |  | 17 | 440 | 0.024608 | 5.5928e-05 | No
2020-06-23 | 8:00 | 2806 | Urban | Planned |  | 122 | 420 | 0.068375 | 0.0001628 | No
2020-06-23 | 8:00 | L582 | Short rural | Planned |  | 8 | 420 | 0.011054 | 2.6319e-05 | No
2020-06-23 | 8:00 | S737 | Short rural | Planned |  | 58 | 365 | 0.069646 | 0.00019081 | No
2020-06-23 | 8:00 | X482 | Short rural | Planned |  | 17 | 480 | 0.026845 | 5.5928e-05 | No
2020-06-23 | 8:00 | KMD2 | Short rural | Planned |  | 177 | 480 | 0.27951 | 0.00058231 | No
2020-06-23 | 7:30 | 49917 | Urban | Planned |  | 2 | 465 | 0.001241 | 2.6688e-06 | No
2020-06-23 | 8:30 | APA2 | Urban | Planned |  | 3 | 390 | 0.0015612 | 4.0032e-06 | No
2020-06-23 | 7:30 | L588 | Short rural | Planned |  | 35 | 510 | 0.058724 | 0.00011515 | No
2020-06-23 | 8:00 | L588 | Short rural | Planned |  | 27 | 510 | 0.045301 | 8.8826e-05 | No
2020-06-23 | 8:00 | 48198 | Urban | Planned |  | 3 | 480 | 0.0019215 | 4.0032e-06 | No
2020-06-23 | 8:00 | WD1247 | Short rural | Planned |  | 36 | 480 | 0.056849 | 0.00011844 | No
2020-06-24 | 8:00 | 5495 | Urban | Planned |  | 2 | 480 | 0.001281 | 2.6688e-06 | No
2020-06-24 | 8:00 | BWH2 | Short rural | Planned |  | 45 | 480 | 0.071061 | 0.00014804 | No
2020-06-24 | 8:00 | L591 | Short rural | Planned |  | 7 | 480 | 0.011054 | 2.3029e-05 | No
2020-06-24 | 6:00 | WD1284 | Short rural | Planned |  | 1 | 60 | 0.00019739 | 3.2899e-06 | No
2020-06-24 | 8:00 | CR1254 | Urban | Planned |  | 92 | 424 | 0.052052 | 0.00012276 | No
2020-06-24 | 8:00 | 55890 | Urban | Planned |  | 76 | 480 | 0.048679 | 0.00010141 | No
2020-06-24 | 8:00 | R260 | Short rural | Planned |  | 13 | 470 | 0.020101 | 4.2768e-05 | No
2020-06-24 | 11:00 | L582 | Short rural | Planned |  | 4 | 240 | 0.0031583 | 1.3159e-05 | No
2020-06-24 | 7:30 | 7964 | Urban | Planned |  | 177 | 480 | 0.11337 | 0.00023619 | No
2020-06-24 | 8:00 | OA1233 | Short rural | Planned |  | 6 | 420 | 0.0082905 | 1.9739e-05 | No
2020-06-24 | 8:00 | L588 | Short rural | Planned |  | 9 | 240 | 0.0071061 | 2.9609e-05 | No
2020-06-24 | 10:00 | 35989 | Short rural | Planned |  | 7 | 120 | 0.0027635 | 2.3029e-05 | No
2020-06-24 | 8:30 | GG1232 | Short rural | Planned |  | 41 | 420 | 0.056651 | 0.00013488 | No
2020-06-24 | 8:00 | CLB2 | Short rural | Planned |  | 274 | 400 | 0.36057 | 0.00090142 | No
2020-06-24 | 8:00 | ER1262 | Short rural | Planned |  | 52 | 480 | 0.082115 | 0.00017107 | No
2020-06-24 | 8:30 | W112 | Short rural | Planned |  | 1 | 510 | 0.0016778 | 3.2899e-06 | No
2020-06-24 | 8:00 | CT1296 | Urban | Planned |  | 8 | 540 | 0.0057646 | 1.0675e-05 | No
2020-06-24 | 8:00 | 8799 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2020-06-24 | 7:30 | W112 | Short rural | Planned |  | 1 | 570 | 0.0018752 | 3.2899e-06 | No
2020-06-24 | 8:00 | RBA2 | Short rural | Planned |  | 25 | 420 | 0.034544 | 8.2247e-05 | No
2020-06-24 | 8:00 | 8675 | Urban | Planned |  | 134 | 480 | 0.085829 | 0.00017881 | No
2020-06-24 | 8:00 | D845 | Urban | Planned |  | 285 | 540 | 0.20536 | 0.0003803 | No
2020-06-25 | 8:00 | KVA2 | Short rural | Planned |  | 4 | 365 | 0.0048032 | 1.3159e-05 | No
2020-06-25 | 8:30 | RW1218 | Short rural | Planned |  | 16 | 450 | 0.023687 | 5.2638e-05 | No
2020-06-25 | 8:30 | YYB2 | Short rural | Planned |  | 4 | 375 | 0.0049348 | 1.3159e-05 | No
2020-06-25 | 7:30 | 68181 | Urban | Planned |  | 57 | 480 | 0.036509 | 7.6061e-05 | No
2020-06-25 | 8:00 | MVF2 | Short rural | Planned |  | 16 | 480 | 0.025266 | 5.2638e-05 | No
2020-06-25 | 8:00 | C826 | Urban | Planned |  | 179 | 480 | 0.11465 | 0.00023886 | No
2020-06-25 | 7:30 | HR1206 | Urban | Planned |  | 27 | 480 | 0.017294 | 3.6029e-05 | No
2020-06-25 | 8:00 | 1962 | Urban | Planned |  | 71 | 480 | 0.045476 | 9.4742e-05 | No
2020-06-25 | 8:00 | 8798 | Short rural | Planned |  | 30 | 480 | 0.047374 | 9.8696e-05 | No
2020-06-25 | 8:00 | X863 | Urban | Planned |  | 82 | 480 | 0.052522 | 0.00010942 | No
2020-06-25 | 7:00 | WD1225 | Short rural | Planned |  | 1 | 480 | 0.0015791 | 3.2899e-06 | No
2020-06-25 | 8:00 | JS1252 | Short rural | Planned |  | 33 | 480 | 0.052111 | 0.00010857 | No
2020-06-25 | 8:00 | SXC2 | Short rural | Planned |  | 63 | 410 | 0.084977 | 0.00020726 | No
2020-06-25 | 8:00 | D845 | Urban | Planned |  | 271 | 540 | 0.19528 | 0.00036162 | No
2020-06-25 | 8:00 | X482 | Short rural | Planned |  | 31 | 480 | 0.048953 | 0.00010199 | No
2020-06-25 | 8:00 | 19856 | Urban | Planned |  | 35 | 480 | 0.022418 | 4.6704e-05 | No
2020-06-26 | 8:30 | SHE2 | Urban | Planned |  | 32 | 360 | 0.015372 | 4.2701e-05 | No
2020-06-26 | 8:00 | NG1247 | Urban | Planned |  | 21 | 480 | 0.013451 | 2.8022e-05 | No
2020-06-26 | 7:30 | HR1236 | Urban | Planned |  | 12 | 480 | 0.0076861 | 1.6013e-05 | No
2020-06-26 | 8:00 | 41533 | Short rural | Planned |  | 50 | 480 | 0.078957 | 0.00016449 | No
2020-06-26 | 8:00 | BWB2 | Urban | Planned |  | 15 | 480 | 0.0096077 | 2.0016e-05 | No
2020-06-26 | 8:30 | SXC2 | Short rural | Planned |  | 5 | 220 | 0.0036188 | 1.6449e-05 | No
2020-06-26 | 7:30 | A315 | Urban | Planned |  | 67 | 480 | 0.042914 | 8.9405e-05 | No
2020-06-26 | 8:00 | L588 | Short rural | Planned |  | 17 | 480 | 0.026845 | 5.5928e-05 | No
2020-06-26 | 8:00 | WWC2 | Short rural | Planned |  | 97 | 191 | 0.060951 | 0.00031912 | No
2020-06-26 | 8:30 | BGA2 | Short rural | Planned |  | 16 | 370 | 0.019476 | 5.2638e-05 | No
2020-06-26 | 8:30 | DP1206 | Urban | Planned |  | 19 | 165 | 0.0041833 | 2.5354e-05 | No
2020-06-26 | 8:30 | RW1281 | Short rural | Planned |  | 16 | 450 | 0.023687 | 5.2638e-05 | No
2020-06-26 | 8:00 | 87222 | Long rural | Planned |  | 12 | 420 | 16.051 | 0.038217 | No
2020-06-26 | 8:30 | 10244 | Short rural | Planned |  | 1 | 360 | 0.0011844 | 3.2899e-06 | No
2020-06-26 | 8:00 | CX1210 | Short rural | Planned |  | 6 | 450 | 0.0088826 | 1.9739e-05 | No
2020-06-26 | 8:00 | ULC2 | Short rural | Planned |  | 79 | 400 | 0.10396 | 0.0002599 | No
2020-06-27 | 8:00 | A098 | Short rural | Planned |  | 12 | 540 | 0.021318 | 3.9478e-05 | No
2020-06-27 | 7:00 | S790 | Short rural | Planned |  | 1 | 600 | 0.0019739 | 3.2899e-06 | No
2020-06-27 | 6:00 | MR2217 | Urban | Planned |  | 31 | 120 | 0.004964 | 4.1366e-05 | No
2020-06-28 | 7:00 | NE1216 | Short rural | Planned |  | 3 | 300 | 0.0029609 | 9.8696e-06 | No
2020-06-28 | 9:30 | BDH2 | Short rural | Planned |  | 117 | 510 | 0.19631 | 0.00038491 | No
2020-06-28 | 7:00 | WH1235 | Urban | Planned |  | 1 | 540 | 0.00072058 | 1.3344e-06 | No
2020-06-28 | 8:00 | PC1132 | Urban | Planned |  | 14 | 480 | 0.0089672 | 1.8682e-05 | No
2020-06-28 | 9:00 | DP1221 | Short rural | Planned |  | 8 | 480 | 0.012633 | 2.6319e-05 | No
2020-06-29 | 8:00 | NA1236 | Short rural | Planned |  | 161 | 395 | 0.20922 | 0.00052967 | No
2020-06-29 | 8:00 | 35816 | Short rural | Planned |  | 3 | 420 | 0.0041452 | 9.8696e-06 | No
2020-06-29 | 8:00 | RBE2 | Short rural | Planned |  | 24 | 400 | 0.031583 | 7.8957e-05 | No
2020-06-29 | 8:00 | 1962 | Urban | Planned |  | 135 | 480 | 0.086469 | 0.00018014 | No
2020-06-29 | 8:30 | CX1210 | Short rural | Planned |  | 5 | 420 | 0.0069087 | 1.6449e-05 | No
2020-06-29 | 8:00 | X217 | Short rural | Planned |  | 13 | 480 | 0.020529 | 4.2768e-05 | No
2020-06-29 | 7:30 | 7966 | Urban | Planned |  | 16 | 480 | 0.010248 | 2.135e-05 | No
2020-06-30 | 7:30 | 4860 | Urban | Planned |  | 12 | 435 | 0.0069656 | 1.6013e-05 | No
2020-06-30 | 8:00 | 9059 | Urban | Planned |  | 58 | 425 | 0.032893 | 7.7395e-05 | No
2020-06-30 | 8:00 | CR1262 | Urban | Planned |  | 47 | 525 | 0.032926 | 6.2717e-05 | No
2020-06-30 | 8:00 | ULF2 | Short rural | Planned |  | 134 | 480 | 0.2116 | 0.00044084 | No
2020-06-30 | 8:00 | M399 | Short rural | Planned |  | 2 | 480 | 0.0031583 | 6.5797e-06 | No
2020-06-30 | 8:00 | NG1247 | Urban | Planned |  | 67 | 480 | 0.042914 | 8.9405e-05 | No
2020-06-30 | 8:30 | KMD2 | Short rural | Planned |  | 166 | 370 | 0.20206 | 0.00054612 | No
2020-06-30 | 8:00 | 8689 | Urban | Planned |  | 217 | 480 | 0.13899 | 0.00028956 | No
2020-06-30 | 8:00 | 87220 | Short rural | Planned |  | 29 | 480 | 0.045795 | 9.5406e-05 | No
2020-06-30 | 8:00 | ER1252 | Short rural | Planned |  | 50 | 390 | 0.064152 | 0.00016449 | No
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## Amendments
This sheet may be used to identify amendments made to data resubmitted to the AER.
NSP data amendments
Worksheet | Table | Comments
Contents
Instructions