## Cover
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | Energex
DNSP - Australian business number: |  | 40 078 849 055
Reporting year: |  | 2012-13
Business address | Address |  | 26 Reddacliff Street
| Suburb |  | Newstead
|  | State | QLD |  | 4006
Postal address | Address |  | 26 Reddacliff Street
| Suburb |  | Newstead
|  | State | QLD | Postcode | 4006
Contact name/s | Michael Ryan / Guy Mutasa
Contact phone/s | 07 3664 4125 / 07 3664 4459
Contact email address/s | mickryan@energex.com.au / guymutasa@energex.com.au

## Contents
Electricity DNSP Annual Reporting Template
Table of contents
Cover sheet | 3. Quality of service and customer service
1. Service Target Performance Incentive Scheme | 4. General Information
1a. STPIS - Reliability | 5. Outages
1b. STPIS - Customer service | 5a. Network data - outages
1c. STPIS - Daily performance | 5b. Network data - feeder reliability
1d. STPIS - MED threshold | 5c. Network data - outages
1e. STPIS - Exclusions | 5d. Network data - planned outages
1f. STPIS - GSL | 6. Weighted average cost of debt
2. Demand | 7. Asset installation

## 1a. STPIS Reliability
Energex
STPIS Data Reporting
2012-13
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI
Unplanned SAIDI | CBD | Urban | Rural short | Rural long | Whole network
Total | 3.8623 | 383.6717 | 975.6003 | NA | 535.7435
Total - after removing excluded events | 0.73105 | 54.4463 | 104.5964 | NA | 67.323
Table 2: SAIFI
Unplanned SAIFI | CBD | Urban | Rural short | Rural long | Whole network
Total | 0.0069145 | 1.1151 | 2.1102 | NA | 1.3686
Total - after removing excluded events | 0.0065 | 0.7232 | 1.3442 | NA | 0.88205
Table 3: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers at the start of period | 3776.87 | 1000064 | 335172 | 0 | 1339012.87
Customer numbers at the end of period | 3754 | 996606 | 345816 | 0 | 1346176
Average distribution customer numbers | 3765.435 | 998335 | 340494 | 0 | 1342594.435
Contents

## 1b. STPIS Customer Service
Energex
STPIS Data Reporting
2012-13
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering
Telephone answering | Total - after removing excluded events | Total
Total number of calls | 108737 | 156423
Number of calls answered within 30 seconds | 92025
Percentage of calls answered within 30 seconds | 84.63%
Table 2: New connections
Note: this is for newly energised properties only
New connections
Number of new connections
Number of new connections not provided on or before the agreed date
Percentage of new connections not provided on or before the agreed date
Table 3: Streetlight repair
Streetlight repair
Total number of streetlights
Total number of streetlight faults
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neigbouring business
Faulty streetlights not repaired within 5 days of fault report or agreed date
Percentage of faulty streetlights not repaired within 5 days of fault report or agreed date
Table 4 Response to written enquiries
Note: this does not include Saturdays, Sundays and Public holidays
Response to written enquiries
Number of written enquiries
Number of written enquiries not responded to in 5 days
Percentage of written enquiries not responded to in 5 days
Contents

## 1c. STPIS Daily Performance
Energex
STPIS Data Reporting |  |  |  | 2012-07-01
2012-13 |  |  |  | 2013-07-01
Daily Performance |  |  |  | 2014-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Daily performance data (Unplanned SAIDI, Unplanned SAIFI)
Note: the excluded events to be removed from the data refer only to events listed in clause 3.3(a) of the STPIS, with respect to reliability data, and in clause 5.4(a) of the STPIS with respect to customer service parameters.
Customer service
Date | Network SAIDI all events total | Network SAIDI all events after removing excluded events | CBD SAIDI all events total | CBD SAIDI all events after removing excluded events | Urban SAIDI all events total | Urban SAIDI all events after removing excluded events | Long rural SAIDI all events total | Long rural all events after removing excluded events | Short rural SAIDI all events total | Short rural SAIDI all events after removing excluded events | Network SAIFI all events total | Network SAIFI all events after removing excluded events | CBD SAIFI all events total | CBD SAIFI all events after removing excluded events | Urban SAIFI all events total | Urban SAIFI all events after removing excluded events | Long rural SAIFI all events total | Long rural SAIFI all events after removing excluded events | Short rural SAIFI all events total | Short Rural SAIFI all events after removing excluded events | Total number of calls (after removing excluded events) | Total number of calls answered in 30 seconds (after removing excluded events) | MED
2012-07-01 | 0.011006 | 0.011006 | 0 | 0 | 0.0021267 | 0.0021267 |  |  | 0.037622 | 0.037622 | 0.00011222 | 0.00011222 | 0 | 0 | 2.7758e-05 | 2.7758e-05 |  |  | 0.00036548 | 0.00036548 | 106 | 103 | NO
2012-07-02 | 0.12043 | 0.12043 | 0 | 0 | 0.15417 | 0.15417 |  |  | 0.021006 | 0.021006 | 0.0022344 | 0.0022344 | 0 | 0 | 0.0028911 | 0.0028911 |  |  | 0.00029855 | 0.00029855 | 296 | 243.2 | NO
2012-07-03 | 0.15906 | 0.15906 | 0 | 0 | 0.023197 | 0.023197 |  |  | 0.56702 | 0.56702 | 0.0023855 | 0.0023855 | 0 | 0 | 0.00023428 | 0.00023428 |  |  | 0.0088432 | 0.0088432 | 279 | 246.4 | NO
2012-07-04 | 0.029897 | 0.029897 | 0 | 0 | 0.027723 | 0.027723 |  |  | 0.03674 | 0.03674 | 0.00047257 | 0.00047257 | 0 | 0 | 0.00050315 | 0.00050315 |  |  | 0.00038638 | 0.00038638 | 274 | 240.6 | NO
2012-07-05 | 0.14499 | 0.14499 | 0 | 0 | 0.02264 | 0.02264 |  |  | 0.5126 | 0.5126 | 0.0099091 | 0.0099091 | 0 | 0 | 0.0013204 | 0.0013204 |  |  | 0.035712 | 0.035712 | 396 | 312.4 | NO
2012-07-06 | 0.20694 | 0.20694 | 0 | 0 | 0.276 | 0.276 |  |  | 0.0027923 | 0.0027923 | 0.0024288 | 0.0024288 | 0 | 0 | 0.0032421 | 0.0032421 |  |  | 2.3901e-05 | 2.3901e-05 | 382 | 285.6 | NO
2012-07-07 | 0.0062019 | 0.0062019 | 0 | 0 | 0.0026985 | 0.0026985 |  |  | 0.016744 | 0.016744 | 0.00012744 | 0.00012744 | 0 | 0 | 0.00010291 | 0.00010291 |  |  | 0.00020217 | 0.00020217 | 205 | 172.8 | NO
2012-07-08 | 0.085257 | 0.085257 | 0 | 0 | 0.080528 | 0.080528 |  |  | 0.10034 | 0.10034 | 0.00097467 | 0.00097467 | 0 | 0 | 0.00089532 | 0.00089532 |  |  | 0.0012227 | 0.0012227 | 157 | 145.4 | NO
2012-07-09 | 0.0081026 | 0.0081026 | 0 | 0 | 0.0090145 | 0.0090145 |  |  | 0.0054715 | 0.0054715 | 0.00010972 | 0.00010972 | 0 | 0 | 0.00012092 | 0.00012092 |  |  | 7.7536e-05 | 7.7536e-05 | 379 | 350.6 | NO
2012-07-10 | 0.020532 | 0.020532 | 0 | 0 | 0.012575 | 0.012575 |  |  | 0.044495 | 0.044495 | 0.00043392 | 0.00043392 | 0 | 0 | 0.00048083 | 0.00048083 |  |  | 0.00029887 | 0.00029887 | 276 | 256.4 | NO
2012-07-11 | 0.11786 | 0.11786 | 0 | 0 | 0.036151 | 0.036151 |  |  | 0.36278 | 0.36278 | 0.0019881 | 0.0019881 | 0 | 0 | 0.00080115 | 0.00080115 |  |  | 0.0055489 | 0.0055489 | 282 | 260 | NO
2012-07-12 | 0.20179 | 0.20179 | 0 | 0 | 0.15218 | 0.15218 |  |  | 0.35184 | 0.35184 | 0.0023006 | 0.0023006 | 0 | 0 | 0.0016313 | 0.0016313 |  |  | 0.0043206 | 0.0043206 | 318 | 277.6 | NO
2012-07-13 | 0.053906 | 0.053906 | 0 | 0 | 0.041927 | 0.041927 |  |  | 0.09018 | 0.09018 | 0.0007176 | 0.0007176 | 0 | 0 | 0.00062289 | 0.00062289 |  |  | 0.0010077 | 0.0010077 | 284 | 250.2 | NO
2012-07-14 | 0.20266 | 0.20266 | 0 | 0 | 0.17857 | 0.17857 |  |  | 0.27662 | 0.27662 | 0.0019674 | 0.0019674 | 0 | 0 | 0.0019669 | 0.0019669 |  |  | 0.0019911 | 0.0019911 | 248 | 182.4 | NO
2012-07-15 | 0.067762 | 0.067762 | 0 | 0 | 0.081794 | 0.081794 |  |  | 0.026784 | 0.026784 | 0.0010459 | 0.0010459 | 0 | 0 | 0.0013395 | 0.0013395 |  |  | 0.00018442 | 0.00018442 | 160 | 142.6 | NO
2012-07-16 | 0.069062 | 0.069062 | 0 | 0 | 0.034254 | 0.034254 |  |  | 0.1733 | 0.1733 | 0.00085364 | 0.00085364 | 0 | 0 | 0.00045383 | 0.00045383 |  |  | 0.0020517 | 0.0020517 | 292 | 256.6 | NO
2012-07-17 | 0.065611 | 0.065611 | 0 | 0 | 0.049981 | 0.049981 |  |  | 0.11277 | 0.11277 | 0.0018507 | 0.0018507 | 0 | 0 | 0.0010401 | 0.0010401 |  |  | 0.0042794 | 0.0042794 | 278 | 244 | NO
2012-07-18 | 0.017586 | 0.017586 | 0 | 0 | 0.0071202 | 0.0071202 |  |  | 0.04885 | 0.04885 | 0.00019362 | 0.00019362 | 0 | 0 | 9.6217e-05 | 9.6217e-05 |  |  | 0.00048492 | 0.00048492 | 236 | 215.2 | NO
2012-07-19 | 0.026824 | 0.026824 | 0 | 0 | 0.030518 | 0.030518 |  |  | 0.016166 | 0.016166 | 0.00038667 | 0.00038667 | 0 | 0 | 0.00048913 | 0.00048913 |  |  | 8.7044e-05 | 8.7044e-05 | 214 | 180.4 | NO
2012-07-20 | 0.13945 | 0.13945 | 0 | 0 | 0.043298 | 0.043298 |  |  | 0.42592 | 0.42592 | 0.0026364 | 0.0026364 | 0 | 0 | 0.00039952 | 0.00039952 |  |  | 0.0092942 | 0.0092942 | 247 | 221.2 | NO
2012-07-21 | 0.077782 | 0.077782 | 0 | 0 | 0.10163 | 0.10163 |  |  | 0.0080575 | 0.0080575 | 0.0014165 | 0.0014165 | 0 | 0 | 0.0016652 | 0.0016652 |  |  | 0.00069626 | 0.00069626 | 145 | 130.2 | NO
2012-07-22 | 0.14085 | 0.14085 | 0 | 0 | 0.10372 | 0.10372 |  |  | 0.25222 | 0.25222 | 0.0025099 | 0.0025099 | 0 | 0 | 0.0023172 | 0.0023172 |  |  | 0.0031079 | 0.0031079 | 161 | 132 | NO
2012-07-23 | 0.082039 | 0.082039 | 0 | 0 | 0.073907 | 0.073907 |  |  | 0.10698 | 0.10698 | 0.00050876 | 0.00050876 | 0 | 0 | 0.00052215 | 0.00052215 |  |  | 0.00047483 | 0.00047483 | 221 | 184.2 | NO
2012-07-24 | 0.034524 | 0.034524 | 0 | 0 | 0.043553 | 0.043553 |  |  | 0.008263 | 0.008263 | 0.00056405 | 0.00056405 | 0 | 0 | 0.0006071 | 0.0006071 |  |  | 0.00044329 | 0.00044329 | 233 | 220.2 | NO
2012-07-25 | 0.081811 | 0.081811 | 0 | 0 | 0.034834 | 0.034834 |  |  | 0.22117 | 0.22117 | 0.00091972 | 0.00091972 | 0 | 0 | 0.00071597 | 0.00071597 |  |  | 0.0015304 | 0.0015304 | 236 | 193.8 | NO
2012-07-26 | 0.038311 | 0.038311 | 0 | 0 | 0.050766 | 0.050766 |  |  | 0.0018751 | 0.0018751 | 0.0010205 | 0.0010205 | 0 | 0 | 0.0013655 | 0.0013655 |  |  | 1.1798e-05 | 1.1798e-05 | 188 | 182 | NO
2012-07-27 | 0.18619 | 0.18619 | 0 | 0 | 0.2461 | 0.2461 |  |  | 0.012134 | 0.012134 | 0.003465 | 0.003465 | 0 | 0 | 0.0046026 | 0.0046026 |  |  | 0.00015941 | 0.00015941 | 198 | 181.4 | NO
2012-07-28 | 0.27437 | 0.27437 | 0 | 0 | 0.0064366 | 0.0064366 |  |  | 1.0642 | 1.0642 | 0.0065355 | 0.0065355 | 0 | 0 | 8.522e-05 | 8.522e-05 |  |  | 0.02555 | 0.02555 | 252 | 214 | NO
2012-07-29 | 0.059248 | 0.059248 | 0 | 0 | 0.054866 | 0.054866 |  |  | 0.072756 | 0.072756 | 0.0016137 | 0.0016137 | 0 | 0 | 0.0017258 | 0.0017258 |  |  | 0.0013031 | 0.0013031 | 160 | 117.4 | NO
2012-07-30 | 0.030037 | 0.030037 | 0 | 0 | 0.0047003 | 0.0047003 |  |  | 0.10457 | 0.10457 | 0.0020372 | 0.0020372 | 0 | 0 | 0.00013156 | 0.00013156 |  |  | 0.0076408 | 0.0076408 | 231 | 213.6 | NO
2012-07-31 | 0.06766 | 0.06766 | 0 | 0 | 0.089932 | 0.089932 |  |  | 0.0032624 | 0.0032624 | 0.0010583 | 0.0010583 | 0 | 0 | 0.0014082 | 0.0014082 |  |  | 4.6461e-05 | 4.6461e-05 | 273 | 259 | NO
2012-08-01 | 0.11051 | 0.11051 | 0 | 0 | 0.14786 | 0.14786 |  |  | 0.0026209 | 0.0026209 | 0.0011122 | 0.0011122 | 0 | 0 | 0.0014905 | 0.0014905 |  |  | 1.9351e-05 | 1.9351e-05 | 193 | 185 | NO
2012-08-02 | 0.050663 | 0.050663 | 0 | 0 | 0.017409 | 0.017409 |  |  | 0.1508 | 0.1508 | 0.00062536 | 0.00062536 | 0 | 0 | 0.00069439 | 0.00069439 |  |  | 0.00058278 | 0.00058278 | 219 | 210 | NO
2012-08-03 | 0.36375 | 0.36375 | 0 | 0 | 0.22908 | 0.22908 |  |  | 0.76003 | 0.76003 | 0.0035013 | 0.0035013 | 0 | 0 | 0.001527 | 0.001527 |  |  | 0.0092903 | 0.0092903 | 351 | 296.4 | NO
2012-08-04 | 0.016409 | 0.016409 | 0 | 0 | 0.0073302 | 0.0073302 |  |  | 0.043032 | 0.043032 | 0.0017369 | 0.0017369 | 0 | 0 | 0.0015626 | 0.0015626 |  |  | 0.0022639 | 0.0022639 | 183 | 169.4 | NO
2012-08-05 | 0.32158 | 0.32158 | 0 | 0 | 0.40385 | 0.40385 |  |  | 0.085542 | 0.085542 | 0.004327 | 0.004327 | 0 | 0 | 0.0053991 | 0.0053991 |  |  | 0.0012527 | 0.0012527 | 209 | 183.2 | NO
2012-08-06 | 0.64872 | 0.64872 | 0 | 0 | 0.75144 | 0.75144 |  |  | 0.35678 | 0.35678 | 0.009995 | 0.009995 | 0 | 0 | 0.011608 | 0.011608 |  |  | 0.0054085 | 0.0054085 | 379 | 321.4 | NO
2012-08-07 | 0.040951 | 0.040951 | 0 | 0 | 0.025494 | 0.025494 |  |  | 0.086411 | 0.086411 | 0.00094729 | 0.00094729 | 0 | 0 | 0.00022885 | 0.00022885 |  |  | 0.0030497 | 0.0030497 | 272 | 256.6 | NO
2012-08-08 | 0.1538 | 0.1538 | 0 | 0 | 0.026664 | 0.026664 |  |  | 0.52572 | 0.52572 | 0.0032863 | 0.0032863 | 0 | 0 | 0.0013937 | 0.0013937 |  |  | 0.0088338 | 0.0088338 | 249 | 232.6 | NO
2012-08-09 | 0.41912 | 0.41912 | 0 | 0 | 0.44496 | 0.44496 |  |  | 0.34847 | 0.34847 | 0.0031356 | 0.0031356 | 0 | 0 | 0.0022677 | 0.0022677 |  |  | 0.0056976 | 0.0056976 | 274 | 232.4 | NO
2012-08-10 | 0.32074 | 0.32074 | 0 | 0 | 0.1857 | 0.1857 |  |  | 0.71748 | 0.71748 | 0.008009 | 0.008009 | 0 | 0 | 0.0047561 | 0.0047561 |  |  | 0.017569 | 0.017569 | 348 | 311.6 | NO
2012-08-11 | 0.10928 | 0.10928 | 0 | 0 | 0.13084 | 0.13084 |  |  | 0.047714 | 0.047714 | 0.00124 | 0.00124 | 0 | 0 | 0.0016315 | 0.0016315 |  |  | 0.000114 | 0.000114 | 185 | 157.8 | NO
2012-08-12 | 0.029878 | 0.029878 | 0 | 0 | 0.0014085 | 0.0014085 |  |  | 0.11307 | 0.11307 | 0.00045419 | 0.00045419 | 0 | 0 | 1.4057e-05 | 1.4057e-05 |  |  | 0.0017403 | 0.0017403 | 159 | 148.4 | NO
2012-08-13 | 0.046793 | 0.046793 | 0 | 0 | 0.051376 | 0.051376 |  |  | 0.03397 | 0.03397 | 0.00094797 | 0.00094797 | 0 | 0 | 0.00084255 | 0.00084255 |  |  | 0.0012652 | 0.0012652 | 249 | 237 | NO
2012-08-14 | 0.024411 | 0.024411 | 0 | 0 | 0.0012885 | 0.0012885 |  |  | 0.09196 | 0.09196 | 0.00035041 | 0.00035041 | 0 | 0 | 1.7068e-05 | 1.7068e-05 |  |  | 0.0013242 | 0.0013242 | 207 | 204.2 | NO
2012-08-15 | 0.007306 | 0.007306 | 0 | 0 | 0.0053351 | 0.0053351 |  |  | 0.01312 | 0.01312 | 6.9735e-05 | 6.9735e-05 | 0 | 0 | 6.2844e-05 | 6.2844e-05 |  |  | 9.0549e-05 | 9.0549e-05 | 155 | 150.2 | NO
2012-08-16 | 0.083366 | 0.083366 | 0 | 0 | 0.068286 | 0.068286 |  |  | 0.12815 | 0.12815 | 0.0028721 | 0.0028721 | 0 | 0 | 0.0022759 | 0.0022759 |  |  | 0.0046381 | 0.0046381 | 210 | 186.6 | NO
2012-08-17 | 0.021384 | 0.021384 | 0 | 0 | 0.022613 | 0.022613 |  |  | 0.018044 | 0.018044 | 0.00089151 | 0.00089151 | 0 | 0 | 0.0011445 | 0.0011445 |  |  | 0.00016552 | 0.00016552 | 193 | 178.6 | NO
2012-08-18 | 0.0051455 | 0.0051455 | 0 | 0 | 0.00096383 | 0.00096383 |  |  | 0.017363 | 0.017363 | 0.00028102 | 0.00028102 | 0 | 0 | 9.0357e-06 | 9.0357e-06 |  |  | 0.0010751 | 0.0010751 | 158 | 136.4 | NO
2012-08-19 | 0.050513 | 0.050513 | 0 | 0 | 0.067326 | 0.067326 |  |  | 0.0021836 | 0.0021836 | 0.00055321 | 0.00055321 | 0 | 0 | 0.00073954 | 0.00073954 |  |  | 1.7515e-05 | 1.7515e-05 | 114 | 105.4 | NO
2012-08-20 | 0.2906 | 0.2906 | 0 | 0 | 0.2016 | 0.2016 |  |  | 0.55254 | 0.55254 | 0.003416 | 0.003416 | 0 | 0 | 0.0020254 | 0.0020254 |  |  | 0.0074964 | 0.0074964 | 299 | 228.6 | NO
2012-08-21 | 0.037684 | 0.037684 | 0 | 0 | 0.049955 | 0.049955 |  |  | 0.0024309 | 0.0024309 | 0.00079678 | 0.00079678 | 0 | 0 | 0.0010599 | 0.0010599 |  |  | 4.0855e-05 | 4.0855e-05 | 236 | 228.4 | NO
2012-08-22 | 0.015278 | 0.015278 | 0.0083774 | 0.0083774 | 0.017343 | 0.017343 |  |  | 0.0093503 | 0.0093503 | 0.0022949 | 0.0022949 | 0.00026525 | 0.00026525 | 0.0030186 | 0.0030186 |  |  | 0.00021404 | 0.00021404 | 195 | 175.2 | NO
2012-08-23 | 0.15578 | 0.15578 | 0 | 0 | 0.051904 | 0.051904 |  |  | 0.4593 | 0.4593 | 0.0039025 | 0.0039025 | 0 | 0 | 0.0018507 | 0.0018507 |  |  | 0.0099072 | 0.0099072 | 265 | 239.6 | NO
2012-08-24 | 0.096181 | 0.096181 | 0 | 0 | 0.014301 | 0.014301 |  |  | 0.33509 | 0.33509 | 0.0007521 | 0.0007521 | 0 | 0 | 0.00011646 | 0.00011646 |  |  | 0.0026068 | 0.0026068 | 257 | 235.6 | NO
2012-08-25 | 0.023951 | 0.023951 | 0 | 0 | 0.024914 | 0.024914 |  |  | 0.021417 | 0.021417 | 0.00083977 | 0.00083977 | 0 | 0 | 0.0010337 | 0.0010337 |  |  | 0.00028573 | 0.00028573 | 146 | 134.4 | NO
2012-08-26 | 0.071707 | 0.071707 | 0 | 0 | 0.087526 | 0.087526 |  |  | 0.026576 | 0.026576 | 0.0012301 | 0.0012301 | 0 | 0 | 0.001603 | 0.001603 |  |  | 0.00016104 | 0.00016104 | 103 | 103 | NO
2012-08-27 | 0.032281 | 0.032281 | 0 | 0 | 0.018213 | 0.018213 |  |  | 0.073456 | 0.073456 | 0.00042189 | 0.00042189 | 0 | 0 | 0.00018933 | 0.00018933 |  |  | 0.0011013 | 0.0011013 | 212 | 197 | NO
2012-08-28 | 0.028563 | 0.028563 | 0 | 0 | 0.037934 | 0.037934 |  |  | 0.0017003 | 0.0017003 | 0.00061632 | 0.00061632 | 0 | 0 | 0.00082414 | 0.00082414 |  |  | 2.0387e-05 | 2.0387e-05 | 220 | 199.6 | NO
2012-08-29 | 0.087599 | 0.087599 | 0 | 0 | 0.1041 | 0.1041 |  |  | 0.040719 | 0.040719 | 0.002221 | 0.002221 | 0 | 0 | 0.0029279 | 0.0029279 |  |  | 0.00019637 | 0.00019637 | 202 | 186.4 | NO
2012-08-30 | 0.51874 | 0.51874 | 0 | 0 | 0.45861 | 0.45861 |  |  | 0.69867 | 0.69867 | 0.0045318 | 0.0045318 | 0 | 0 | 0.00353 | 0.00353 |  |  | 0.0074844 | 0.0074844 | 216 | 200.6 | NO
2012-08-31 | 0.053628 | 0.053628 | 0 | 0 | 0.040155 | 0.040155 |  |  | 0.093235 | 0.093235 | 0.0010893 | 0.0010893 | 0 | 0 | 0.00027702 | 0.00027702 |  |  | 0.0034535 | 0.0034535 | 230 | 196 | NO
2012-09-01 | 0.071791 | 0.071791 | 0 | 0 | 0.029277 | 0.029277 |  |  | 0.19563 | 0.19563 | 0.0024618 | 0.0024618 | 0 | 0 | 0.0018012 | 0.0018012 |  |  | 0.0044009 | 0.0044009 | 153 | 146.2 | NO
2012-09-02 | 0.01663 | 0.01663 | 0 | 0 | 0.0099866 | 0.0099866 |  |  | 0.036033 | 0.036033 | 0.00018867 | 0.00018867 | 0 | 0 | 0.0001224 | 0.0001224 |  |  | 0.00038244 | 0.00038244 | 116 | 104.8 | NO
2012-09-03 | 0.084938 | 0.084938 | 0 | 0 | 0.10043 | 0.10043 |  |  | 0.041083 | 0.041083 | 0.0011493 | 0.0011493 | 0 | 0 | 0.001361 | 0.001361 |  |  | 0.0005498 | 0.0005498 | 266 | 196 | NO
2012-09-04 | 0.036423 | 0.036423 | 0 | 0 | 0.0065991 | 0.0065991 |  |  | 0.12301 | 0.12301 | 0.00023045 | 0.00023045 | 0 | 0 | 0.00011382 | 0.00011382 |  |  | 0.00057005 | 0.00057005 | 204 | 178.4 | NO
2012-09-05 | 0.042128 | 0.042128 | 0 | 0 | 0.010022 | 0.010022 |  |  | 0.13533 | 0.13533 | 0.0012599 | 0.0012599 | 0 | 0 | 0.00017478 | 0.00017478 |  |  | 0.0044083 | 0.0044083 | 197 | 189.2 | NO
2012-09-06 | 0.023029 | 0.023029 | 0 | 0 | 0.030253 | 0.030253 |  |  | 0.0024229 | 0.0024229 | 0.0013911 | 0.0013911 | 0 | 0 | 0.0018732 | 0.0018732 |  |  | 1.4508e-05 | 1.4508e-05 | 196 | 191 | NO
2012-09-07 | 0.062391 | 0.062391 | 0 | 0 | 0.048002 | 0.048002 |  |  | 0.1046 | 0.1046 | 0.00078406 | 0.00078406 | 0 | 0 | 0.00084327 | 0.00084327 |  |  | 0.00062178 | 0.00062178 | 208 | 183.4 | NO
2012-09-08 | 0.019878 | 0.019878 | 0 | 0 | 0.026494 | 0.026494 |  |  | 0.0010122 | 0.0010122 | 0.00015883 | 0.00015883 | 0 | 0 | 0.00021148 | 0.00021148 |  |  | 8.6982e-06 | 8.6982e-06 | 133 | 126.2 | NO
2012-09-09 | 0.020847 | 0.020847 | 0 | 0 | 0.014212 | 0.014212 |  |  | 0.040202 | 0.040202 | 0.00027759 | 0.00027759 | 0 | 0 | 0.00014472 | 0.00014472 |  |  | 0.00066371 | 0.00066371 | 95 | 87.2 | NO
2012-09-10 | 0.24664 | 0.24664 | 0 | 0 | 0.31618 | 0.31618 |  |  | 0.047299 | 0.047299 | 0.0039431 | 0.0039431 | 0 | 0 | 0.0051414 | 0.0051414 |  |  | 0.00042913 | 0.00042913 | 213 | 202 | NO
2012-09-11 | 0.13897 | 0.13897 | 0 | 0 | 0.0037352 | 0.0037352 |  |  | 0.53001 | 0.53001 | 0.0022988 | 0.0022988 | 0 | 0 | 3.5192e-05 | 3.5192e-05 |  |  | 0.0088439 | 0.0088439 | 220 | 213.6 | NO
2012-09-12 | 0.05729 | 0.05729 | 0 | 0 | 0.071684 | 0.071684 |  |  | 0.016474 | 0.016474 | 0.001135 | 0.001135 | 0 | 0 | 0.0014673 | 0.0014673 |  |  | 0.00019049 | 0.00019049 | 175 | 173.2 | NO
2012-09-13 | 0.024482 | 0.024482 | 0 | 0 | 0.012673 | 0.012673 |  |  | 0.058733 | 0.058733 | 0.00028341 | 0.00028341 | 0 | 0 | 0.00022822 | 0.00022822 |  |  | 0.00044534 | 0.00044534 | 207 | 189.8 | NO
2012-09-14 | 0.2027 | 0.2027 | 0 | 0 | 0.24485 | 0.24485 |  |  | 0.083646 | 0.083646 | 0.0032599 | 0.0032599 | 0 | 0 | 0.0029268 | 0.0029268 |  |  | 0.0042535 | 0.0042535 | 539 | 419.6 | NO
2012-09-15 | 0.21412 | 0.21412 | 0 | 0 | 0.014499 | 0.014499 |  |  | 0.79032 | 0.79032 | 0.0013873 | 0.0013873 | 0 | 0 | 0.00012205 | 0.00012205 |  |  | 0.00504 | 0.00504 | 142 | 132.4 | NO
2012-09-16 | 0.15911 | 0.15911 | 0 | 0 | 0.17207 | 0.17207 |  |  | 0.12361 | 0.12361 | 0.0024929 | 0.0024929 | 0 | 0 | 0.002076 | 0.002076 |  |  | 0.0037178 | 0.0037178 | 145 | 136.2 | NO
2012-09-17 | 0.055545 | 0.055545 | 0 | 0 | 0.02661 | 0.02661 |  |  | 0.13925 | 0.13925 | 0.00073305 | 0.00073305 | 0 | 0 | 0.00011484 | 0.00011484 |  |  | 0.0025166 | 0.0025166 | 266 | 237.4 | NO
2012-09-18 | 0.057444 | 0.057444 | 0 | 0 | 0.075615 | 0.075615 |  |  | 0.0059049 | 0.0059049 | 0.00090407 | 0.00090407 | 0 | 0 | 0.0012144 | 0.0012144 |  |  | 2.3106e-05 | 2.3106e-05 | 260 | 239.4 | NO
2012-09-19 | 0.13422 | 0.13422 | 0 | 0 | 0.083738 | 0.083738 |  |  | 0.28053 | 0.28053 | 0.0011076 | 0.0011076 | 0 | 0 | 0.00049388 | 0.00049388 |  |  | 0.0028807 | 0.0028807 | 237 | 228.4 | NO
2012-09-20 | 0.060467 | 0.060467 | 0 | 0 | 0.025537 | 0.025537 |  |  | 0.16129 | 0.16129 | 0.00086141 | 0.00086141 | 0 | 0 | 0.00038285 | 0.00038285 |  |  | 0.0022431 | 0.0022431 | 206 | 184.4 | NO
2012-09-21 | 0.31328 | 0.31328 | 0 | 0 | 0.14552 | 0.14552 |  |  | 0.79746 | 0.79746 | 0.0029738 | 0.0029738 | 0 | 0 | 0.0016486 | 0.0016486 |  |  | 0.0068043 | 0.0068043 | 315 | 274 | NO
2012-09-22 | 0.32379 | 0.32379 | 0 | 0 | 0.058077 | 0.058077 |  |  | 1.0884 | 1.0884 | 0.0035232 | 0.0035232 | 0 | 0 | 0.00094641 | 0.00094641 |  |  | 0.010943 | 0.010943 | 220 | 197 | NO
2012-09-23 | 0.065733 | 0.065733 | 0 | 0 | 0.00024278 | 0.00024278 |  |  | 0.25394 | 0.25394 | 0.00057905 | 0.00057905 | 0 | 0 | 3.0174e-06 | 3.0174e-06 |  |  | 0.0022345 | 0.0022345 | 88 | 85.2 | NO
2012-09-24 | 1.0441 | 1.0441 | 0 | 0 | 0.70847 | 0.70847 |  |  | 2.0156 | 2.0156 | 0.0096794 | 0.0096794 | 0 | 0 | 0.0071606 | 0.0071606 |  |  | 0.016988 | 0.016988 | 567 | 469.2 | NO
2012-09-25 | 0.013393 | 0.013393 | 0 | 0 | 0.0070503 | 0.0070503 |  |  | 0.031683 | 0.031683 | 0.0001532 | 0.0001532 | 0 | 0 | 9.446e-05 | 9.446e-05 |  |  | 0.00032291 | 0.00032291 | 282 | 262.6 | NO
2012-09-26 | 0.14923 | 0.14923 | 0 | 0 | 0.19813 | 0.19813 |  |  | 0.010984 | 0.010984 | 0.00082356 | 0.00082356 | 0 | 0 | 0.0010609 | 0.0010609 |  |  | 0.00015385 | 0.00015385 | 264 | 234.8 | NO
2012-09-27 | 0.081516 | 0.081516 | 0 | 0 | 0.10845 | 0.10845 |  |  | 0.0053765 | 0.0053765 | 0.0011492 | 0.0011492 | 0 | 0 | 0.0015183 | 0.0015183 |  |  | 0.00010636 | 0.00010636 | 178 | 158.8 | NO
2012-09-28 | 0.026405 | 0.026405 | 0 | 0 | 0.031933 | 0.031933 |  |  | 0.010889 | 0.010889 | 0.00072349 | 0.00072349 | 0 | 0 | 0.0008782 | 0.0008782 |  |  | 0.00028912 | 0.00028912 | 227 | 209.4 | NO
2012-09-29 | 0.24855 | 0.24855 | 0 | 0 | 0.008212 | 0.008212 |  |  | 0.93813 | 0.93813 | 0.0040783 | 0.0040783 | 0 | 0 | 0.0001126 | 0.0001126 |  |  | 0.015456 | 0.015456 | 192 | 165.8 | NO
2012-09-30 | 0.020944 | 0.020944 | 0 | 0 | 0.013727 | 0.013727 |  |  | 0.041794 | 0.041794 | 0.00020703 | 0.00020703 | 0 | 0 | 0.00015871 | 0.00015871 |  |  | 0.00034736 | 0.00034736 | 89 | 87 | NO
2012-10-01 | 0.0011358 | 0.0011358 | 0 | 0 | 0.00087516 | 0.00087516 |  |  | 0.0018929 | 0.0018929 | 1.2134e-05 | 1.2134e-05 | 0 | 0 | 9.0426e-06 | 9.0426e-06 |  |  | 2.1097e-05 | 2.1097e-05 | 115 | 111.4 | NO
2012-10-02 | 0.2083 | 0.2083 | 0 | 0 | 0.18675 | 0.18675 |  |  | 0.27213 | 0.27213 | 0.0023403 | 0.0023403 | 0 | 0 | 0.0022396 | 0.0022396 |  |  | 0.0026534 | 0.0026534 | 260 | 212.8 | NO
2012-10-03 | 0.11969 | 0.11969 | 0 | 0 | 0.15881 | 0.15881 |  |  | 0.0090107 | 0.0090107 | 0.0021528 | 0.0021528 | 0 | 0 | 0.0028876 | 0.0028876 |  |  | 7.1719e-05 | 7.1719e-05 | 282 | 233.2 | NO
2012-10-04 | 0.12208 | 0.12208 | 0 | 0 | 0.10336 | 0.10336 |  |  | 0.17688 | 0.17688 | 0.0027855 | 0.0027855 | 0 | 0 | 0.003548 | 0.003548 |  |  | 0.00063819 | 0.00063819 | 228 | 195.8 | NO
2012-10-05 | 0.079588 | 0.079588 | 0 | 0 | 0.057207 | 0.057207 |  |  | 0.1444 | 0.1444 | 0.0026633 | 0.0026633 | 0 | 0 | 0.0012644 | 0.0012644 |  |  | 0.0066893 | 0.0066893 | 238 | 217.6 | NO
2012-10-06 | 0.055371 | 0.055371 | 0 | 0 | 0.02221 | 0.02221 |  |  | 0.15075 | 0.15075 | 0.00092488 | 0.00092488 | 0 | 0 | 0.00085113 | 0.00085113 |  |  | 0.0011457 | 0.0011457 | 163 | 141.2 | NO
2012-10-07 | 0.018189 | 0.018189 | 0 | 0 | 0.0040036 | 0.0040036 |  |  | 0.05894 | 0.05894 | 0.00018441 | 0.00018441 | 0 | 0 | 4.8423e-05 | 4.8423e-05 |  |  | 0.00057518 | 0.00057518 | 138 | 132.2 | NO
2012-10-08 | 0.070534 | 0.070534 | 0 | 0 | 0.083441 | 0.083441 |  |  | 0.034305 | 0.034305 | 0.0042022 | 0.0042022 | 0 | 0 | 0.0014731 | 0.0014731 |  |  | 0.012046 | 0.012046 | 225 | 211.2 | NO
2012-10-09 | 0.19493 | 0.19493 | 0 | 0 | 0.25367 | 0.25367 |  |  | 0.029035 | 0.029035 | 0.0034675 | 0.0034675 | 0 | 0 | 0.0046021 | 0.0046021 |  |  | 0.00025981 | 0.00025981 | 233 | 207.8 | NO
2012-10-10 | 0.067437 | 0.067437 | 0 | 0 | 0.058506 | 0.058506 |  |  | 0.09373 | 0.09373 | 0.0018774 | 0.0018774 | 0 | 0 | 0.0021748 | 0.0021748 |  |  | 0.001047 | 0.001047 | 249 | 223 | NO
2012-10-11 | 0.60481 | 0.60481 | 0 | 0 | 0.41452 | 0.41452 |  |  | 1.156 | 1.156 | 0.0078866 | 0.0078866 | 0 | 0 | 0.0051156 | 0.0051156 |  |  | 0.015903 | 0.015903 | 448 | 370 | NO
2012-10-12 | 0.21356 | 0.21356 | 0 | 0 | 0.2116 | 0.2116 |  |  | 0.2214 | 0.2214 | 0.0020728 | 0.0020728 | 0 | 0 | 0.0021648 | 0.0021648 |  |  | 0.0018193 | 0.0018193 | 460 | 342.8 | NO
2012-10-13 | 0.22674 | 0.22674 | 0 | 0 | 0.11842 | 0.11842 |  |  | 0.53937 | 0.53937 | 0.002736 | 0.002736 | 0 | 0 | 0.0021131 | 0.0021131 |  |  | 0.0045497 | 0.0045497 | 192 | 165.6 | NO
2012-10-14 | 0.44799 | 0.44799 | 0 | 0 | 0.48353 | 0.48353 |  |  | 0.35111 | 0.35111 | 0.0038737 | 0.0038737 | 0 | 0 | 0.0044964 | 0.0044964 |  |  | 0.0021326 | 0.0021326 | 141 | 134.6 | NO
2012-10-15 | 0.042527 | 0.042527 | 0 | 0 | 0.014117 | 0.014117 |  |  | 0.12438 | 0.12438 | 0.00026208 | 0.00026208 | 0 | 0 | 0.00010871 | 0.00010871 |  |  | 0.00070432 | 0.00070432 | 231 | 203.2 | NO
2012-10-16 | 0.1305 | 0.1305 | 0 | 0 | 0.15366 | 0.15366 |  |  | 0.065583 | 0.065583 | 0.001552 | 0.001552 | 0 | 0 | 0.0012702 | 0.0012702 |  |  | 0.0023768 | 0.0023768 | 214 | 195.4 | NO
2012-10-17 | 0.012388 | 0.012388 | 0 | 0 | 0.011036 | 0.011036 |  |  | 0.016397 | 0.016397 | 0.00020975 | 0.00020975 | 0 | 0 | 0.00022159 | 0.00022159 |  |  | 0.00017812 | 0.00017812 | 183 | 174.4 | NO
2012-10-18 | 0.14868 | 0.14868 | 0 | 0 | 0.12029 | 0.12029 |  |  | 0.23171 | 0.23171 | 0.0025754 | 0.0025754 | 0 | 0 | 0.0019391 | 0.0019391 |  |  | 0.004428 | 0.004428 | 267 | 250.6 | NO
2012-10-19 | 0.04721 | 0.04721 | 0 | 0 | 0.059535 | 0.059535 |  |  | 0.012231 | 0.012231 | 0.00077099 | 0.00077099 | 0 | 0 | 0.00097346 | 0.00097346 |  |  | 0.00019445 | 0.00019445 | 268 | 251 | NO
2012-10-20 | 0.095089 | 0.095089 | 0 | 0 | 0.11211 | 0.11211 |  |  | 0.047297 | 0.047297 | 0.0011483 | 0.0011483 | 0 | 0 | 0.0013944 | 0.0013944 |  |  | 0.00045482 | 0.00045482 | 194 | 174.4 | NO
2012-10-21 | 0.29145 | 0.29145 | 0 | 0 | 0.27058 | 0.27058 |  |  | 0.35442 | 0.35442 | 0.0048989 | 0.0048989 | 0 | 0 | 0.0043056 | 0.0043056 |  |  | 0.006652 | 0.006652 | 170 | 157.2 | NO
2012-10-22 | 0.39259 | 0.39259 | 0 | 0 | 0.31589 | 0.31589 |  |  | 0.61708 | 0.61708 | 0.003329 | 0.003329 | 0 | 0 | 0.0031748 | 0.0031748 |  |  | 0.003808 | 0.003808 | 393 | 304.2 | NO
2012-10-23 | 0.32885 | 0.32885 | 0 | 0 | 0.43283 | 0.43283 |  |  | 0.033814 | 0.033814 | 0.0027682 | 0.0027682 | 0 | 0 | 0.0036012 | 0.0036012 |  |  | 0.00040632 | 0.00040632 | 415 | 358.6 | NO
2012-10-24 | 0.082862 | 0.082862 | 0 | 0 | 0.036474 | 0.036474 |  |  | 0.21704 | 0.21704 | 0.0012082 | 0.0012082 | 0 | 0 | 0.00025534 | 0.00025534 |  |  | 0.0039589 | 0.0039589 | 208 | 192 | NO
2012-10-25 | 0.010633 | 0.010633 | 0 | 0 | 0.0018694 | 0.0018694 |  |  | 0.035935 | 0.035935 | 0.00012897 | 0.00012897 | 0 | 0 | 3.0388e-05 | 3.0388e-05 |  |  | 0.00041369 | 0.00041369 | 191 | 186.4 | NO
2012-10-26 | 0.25724 | 0.25724 | 0 | 0 | 0.1355 | 0.1355 |  |  | 0.61006 | 0.61006 | 0.0042147 | 0.0042147 | 0 | 0 | 0.00187 | 0.00187 |  |  | 0.011002 | 0.011002 | 241 | 221 | NO
2012-10-27 | 0.18136 | 0.18136 | 0 | 0 | 0.1172 | 0.1172 |  |  | 0.36733 | 0.36733 | 0.0026937 | 0.0026937 | 0 | 0 | 0.0015355 | 0.0015355 |  |  | 0.0060487 | 0.0060487 | 232 | 199.4 | NO
2012-10-28 | 0.47184 | 0.47184 | 0 | 0 | 0.46158 | 0.46158 |  |  | 0.50656 | 0.50656 | 0.005623 | 0.005623 | 0 | 0 | 0.0045368 | 0.0045368 |  |  | 0.0088097 | 0.0088097 | 167 | 158.4 | NO
2012-10-29 | 0.04655 | 0.04655 | 0 | 0 | 0.01163 | 0.01163 |  |  | 0.14757 | 0.14757 | 0.0019519 | 0.0019519 | 0 | 0 | 0.00012268 | 0.00012268 |  |  | 0.0072383 | 0.0072383 | 272 | 260 | NO
2012-10-30 | 0.079377 | 0.079377 | 0 | 0 | 0.007036 | 0.007036 |  |  | 0.28853 | 0.28853 | 0.0014386 | 0.0014386 | 0 | 0 | 0.00011488 | 0.00011488 |  |  | 0.0052655 | 0.0052655 | 235 | 226.4 | NO
2012-10-31 | 0.089409 | 0.089409 | 0 | 0 | 0.11648 | 0.11648 |  |  | 0.012461 | 0.012461 | 0.0014727 | 0.0014727 | 0 | 0 | 0.0019413 | 0.0019413 |  |  | 0.00013943 | 0.00013943 | 228 | 215.6 | NO
2012-11-01 | 0.18744 | 0.18744 | 0 | 0 | 0.23767 | 0.23767 |  |  | 0.044889 | 0.044889 | 0.0039658 | 0.0039658 | 0 | 0 | 0.0052175 | 0.0052175 |  |  | 0.00040551 | 0.00040551 | 266 | 243.8 | NO
2012-11-02 | 0.62912 | 0.62912 | 0 | 0 | 0.28632 | 0.28632 |  |  | 1.6233 | 1.6233 | 0.016296 | 0.016296 | 0 | 0 | 0.01183 | 0.01183 |  |  | 0.029338 | 0.029338 | 367 | 297.6 | NO
2012-11-03 | 0.06632 | 0.06632 | 0 | 0 | 0.086451 | 0.086451 |  |  | 0.0090991 | 0.0090991 | 0.00084555 | 0.00084555 | 0 | 0 | 0.0011121 | 0.0011121 |  |  | 8.7639e-05 | 8.7639e-05 | 196 | 171.6 | NO
2012-11-04 | 0.0062412 | 0.0062412 | 0 | 0 | 0.00069486 | 0.00069486 |  |  | 0.022273 | 0.022273 | 5.871e-05 | 5.871e-05 | 0 | 0 | 8.99e-06 | 8.99e-06 |  |  | 0.00020246 | 0.00020246 | 86 | 84 | NO
2012-11-05 | 0.0023718 | 0.0023718 | 0 | 0 | 0.0016713 | 0.0016713 |  |  | 0.0044126 | 0.0044126 | 2.8991e-05 | 2.8991e-05 | 0 | 0 | 1.9201e-05 | 1.9201e-05 |  |  | 5.7464e-05 | 5.7464e-05 | 209 | 203.2 | NO
2012-11-06 | 0.1264 | 0.1264 | 0 | 0 | 0.012459 | 0.012459 |  |  | 0.45535 | 0.45535 | 0.0019888 | 0.0019888 | 0 | 0 | 4.459e-05 | 4.459e-05 |  |  | 0.0075997 | 0.0075997 | 233 | 214 | NO
2012-11-07 | 0.015788 | 0.015788 | 0 | 0 | 0.019502 | 0.019502 |  |  | 0.0052911 | 0.0052911 | 0.00017933 | 0.00017933 | 0 | 0 | 0.00022581 | 0.00022581 |  |  | 4.7718e-05 | 4.7718e-05 | 193 | 178.6 | NO
2012-11-08 | 0.23637 | 0.23637 | 0 | 0 | 0.1884 | 0.1884 |  |  | 0.37674 | 0.37674 | 0.0034684 | 0.0034684 | 0 | 0 | 0.0029702 | 0.0029702 |  |  | 0.0049373 | 0.0049373 | 310 | 264.2 | NO
2012-11-09 | 0.28751 | 0.28751 | 0 | 0 | 0.013919 | 0.013919 |  |  | 1.0762 | 1.0762 | 0.0026437 | 0.0026437 | 0 | 0 | 0.00020784 | 0.00020784 |  |  | 0.0096666 | 0.0096666 | 289 | 229.6 | NO
2012-11-10 | 0.89352 | 0.89352 | 0 | 0 | 0.60834 | 0.60834 |  |  | 1.7218 | 1.7218 | 0.0067495 | 0.0067495 | 0 | 0 | 0.0050432 | 0.0050432 |  |  | 0.01172 | 0.01172 | 322 | 239.6 | NO
2012-11-11 | 0.6754 | 0.6754 | 0 | 0 | 0.27861 | 0.27861 |  |  | 1.8214 | 1.8214 | 0.005136 | 0.005136 | 0 | 0 | 0.0028571 | 0.0028571 |  |  | 0.011732 | 0.011732 | 294 | 208.4 | NO
2012-11-12 | 0.080187 | 0.080187 | 0 | 0 | 0.046853 | 0.046853 |  |  | 0.17666 | 0.17666 | 0.00092628 | 0.00092628 | 0 | 0 | 0.00065125 | 0.00065125 |  |  | 0.0017251 | 0.0017251 | 259 | 238.4 | NO
2012-11-13 | 0.027587 | 0.027587 | 0 | 0 | 0.0075907 | 0.0075907 |  |  | 0.085211 | 0.085211 | 0.00088784 | 0.00088784 | 0 | 0 | 0.00011495 | 0.00011495 |  |  | 0.0031132 | 0.0031132 | 211 | 192.2 | NO
2012-11-14 | 0.039788 | 0.039788 | 0 | 0 | 0.052549 | 0.052549 |  |  | 0.0036546 | 0.0036546 | 0.0011503 | 0.0011503 | 0 | 0 | 0.0015492 | 0.0015492 |  |  | 2.0051e-05 | 2.0051e-05 | 172 | 171 | NO
2012-11-15 | 0.092439 | 0.092439 | 0 | 0 | 0.017051 | 0.017051 |  |  | 0.30942 | 0.30942 | 0.0011224 | 0.0011224 | 0 | 0 | 0.00016072 | 0.00016072 |  |  | 0.0038898 | 0.0038898 | 228 | 213.6 | NO
2012-11-16 | 0.010944 | 0.010944 | 0 | 0 | 0.014246 | 0.014246 |  |  | 0.0016076 | 0.0016076 | 0.00011438 | 0.00011438 | 0 | 0 | 0.00015074 | 0.00015074 |  |  | 1.1461e-05 | 1.1461e-05 | 258 | 248.6 | NO
2012-11-17 | 6.2383 | 6.2383 | 0 | 0 | 5.6459 | 5.6459 |  |  | 7.9884 | 7.9884 | 0.050737 | 0.050737 | 0 | 0 | 0.049083 | 0.049083 |  |  | 0.056123 | 0.056123 | 0 | 0 | Yes
2012-11-18 | 2.1418 | 2.1418 | 0 | 0 | 1.901 | 1.901 |  |  | 2.8545 | 2.8545 | 0.018704 | 0.018704 | 0 | 0 | 0.015464 | 0.015464 |  |  | 0.028183 | 0.028183 | 1096 | 601.8 | NO
2012-11-19 | 0.44702 | 0.44702 | 0 | 0 | 0.44834 | 0.44834 |  |  | 0.44811 | 0.44811 | 0.0062759 | 0.0062759 | 0 | 0 | 0.0061852 | 0.0061852 |  |  | 0.0066038 | 0.0066038 | 678 | 581.4 | NO
2012-11-20 | 0.14043 | 0.14043 | 0 | 0 | 0.17769 | 0.17769 |  |  | 0.035331 | 0.035331 | 0.0016946 | 0.0016946 | 0 | 0 | 0.0022813 | 0.0022813 |  |  | 0.00029637 | 0.00029637 | 377 | 337 | NO
2012-11-21 | 0.17904 | 0.17904 | 0 | 0 | 0.22777 | 0.22777 |  |  | 0.041575 | 0.041575 | 0.0063971 | 0.0063971 | 0 | 0 | 0.0068789 | 0.0068789 |  |  | 0.0050884 | 0.0050884 | 311 | 291.4 | NO
2012-11-22 | 0.097879 | 0.097879 | 0 | 0 | 0.035822 | 0.035822 |  |  | 0.27644 | 0.27644 | 0.0013602 | 0.0013602 | 0 | 0 | 0.0005637 | 0.0005637 |  |  | 0.0036532 | 0.0036532 | 379 | 308.4 | NO
2012-11-23 | 0.11956 | 0.11956 | 0 | 0 | 0.13215 | 0.13215 |  |  | 0.084655 | 0.084655 | 0.0023896 | 0.0023896 | 0 | 0 | 0.0026749 | 0.0026749 |  |  | 0.0015984 | 0.0015984 | 347 | 302 | NO
2012-11-24 | 0.38686 | 0.38686 | 0 | 0 | 0.52196 | 0.52196 |  |  | 0.0048618 | 0.0048618 | 0.0044866 | 0.0044866 | 0 | 0 | 0.0061974 | 0.0061974 |  |  | 5.0741e-05 | 5.0741e-05 | 249 | 213.4 | NO
2012-11-25 | 0.51576 | 0.51576 | 0 | 0 | 0.057875 | 0.057875 |  |  | 1.8299 | 1.8299 | 0.0042695 | 0.0042695 | 0 | 0 | 0.00018856 | 0.00018856 |  |  | 0.015979 | 0.015979 | 192 | 169.8 | NO
2012-11-26 | 0.02833 | 0.02833 | 0 | 0 | 0.011813 | 0.011813 |  |  | 0.075829 | 0.075829 | 0.00029963 | 0.00029963 | 0 | 0 | 0.00026291 | 0.00026291 |  |  | 0.00040779 | 0.00040779 | 251 | 228.4 | NO
2012-11-27 | 0.14122 | 0.14122 | 0 | 0 | 0.044314 | 0.044314 |  |  | 0.41957 | 0.41957 | 0.0022786 | 0.0022786 | 0 | 0 | 0.0015112 | 0.0015112 |  |  | 0.0044951 | 0.0044951 | 271 | 246.4 | NO
2012-11-28 | 0.22322 | 0.22322 | 0 | 0 | 0.058165 | 0.058165 |  |  | 0.69697 | 0.69697 | 0.0036303 | 0.0036303 | 0 | 0 | 0.00090975 | 0.00090975 |  |  | 0.011438 | 0.011438 | 266 | 237.6 | NO
2012-11-29 | 0.31443 | 0.31443 | 0 | 0 | 0.31052 | 0.31052 |  |  | 0.329 | 0.329 | 0.0035247 | 0.0035247 | 0 | 0 | 0.0032713 | 0.0032713 |  |  | 0.0042864 | 0.0042864 | 336 | 270.8 | NO
2012-11-30 | 0.37619 | 0.37619 | 0 | 0 | 0.39568 | 0.39568 |  |  | 0.32451 | 0.32451 | 0.007636 | 0.007636 | 0 | 0 | 0.0085492 | 0.0085492 |  |  | 0.0051089 | 0.0051089 | 328 | 271 | NO
2012-12-01 | 0.16656 | 0.16656 | 0 | 0 | 0.22251 | 0.22251 |  |  | 0.0085882 | 0.0085882 | 0.0010195 | 0.0010195 | 0 | 0 | 0.0013569 | 0.0013569 |  |  | 6.7086e-05 | 6.7086e-05 | 211 | 173.6 | NO
2012-12-02 | 0.13579 | 0.13579 | 0 | 0 | 0.15516 | 0.15516 |  |  | 0.081929 | 0.081929 | 0.0025119 | 0.0025119 | 0 | 0 | 0.0018184 | 0.0018184 |  |  | 0.0045194 | 0.0045194 | 152 | 139.8 | NO
2012-12-03 | 0.54476 | 0.54476 | 0 | 0 | 0.53469 | 0.53469 |  |  | 0.57942 | 0.57942 | 0.011465 | 0.011465 | 0 | 0 | 0.013526 | 0.013526 |  |  | 0.0057026 | 0.0057026 | 432 | 323.6 | NO
2012-12-04 | 0.46318 | 0.46318 | 0 | 0 | 0.50366 | 0.50366 |  |  | 0.35256 | 0.35256 | 0.0042079 | 0.0042079 | 0 | 0 | 0.004915 | 0.004915 |  |  | 0.0022336 | 0.0022336 | 527 | 409.2 | NO
2012-12-05 | 0.64821 | 0.64821 | 0 | 0 | 0.3377 | 0.3377 |  |  | 1.5423 | 1.5423 | 0.015772 | 0.015772 | 0 | 0 | 0.0088385 | 0.0088385 |  |  | 0.035752 | 0.035752 | 674 | 548 | NO
2012-12-06 | 0.13907 | 0.13907 | 0 | 0 | 0.16471 | 0.16471 |  |  | 0.067291 | 0.067291 | 0.0027162 | 0.0027162 | 0 | 0 | 0.0029256 | 0.0029256 |  |  | 0.0021457 | 0.0021457 | 343 | 317 | NO
2012-12-07 | 0.31127 | 0.31127 | 0 | 0 | 0.32677 | 0.32677 |  |  | 0.27034 | 0.27034 | 0.0036403 | 0.0036403 | 0 | 0 | 0.0038208 | 0.0038208 |  |  | 0.0031637 | 0.0031637 | 365 | 336.2 | NO
2012-12-08 | 0.08539 | 0.08539 | 0 | 0 | 0.085889 | 0.085889 |  |  | 0.084888 | 0.084888 | 0.001739 | 0.001739 | 0 | 0 | 0.0011391 | 0.0011391 |  |  | 0.0034721 | 0.0034721 | 248 | 213.6 | NO
2012-12-09 | 0.24954 | 0.24954 | 0 | 0 | 0.19624 | 0.19624 |  |  | 0.40458 | 0.40458 | 0.0020835 | 0.0020835 | 0 | 0 | 0.0023605 | 0.0023605 |  |  | 0.0013143 | 0.0013143 | 156 | 148.6 | NO
2012-12-10 | 0.34165 | 0.34165 | 0 | 0 | 0.209 | 0.209 |  |  | 0.72452 | 0.72452 | 0.0051978 | 0.0051978 | 0 | 0 | 0.0026787 | 0.0026787 |  |  | 0.012455 | 0.012455 | 296 | 250.8 | NO
2012-12-11 | 0.22814 | 0.22814 | 0.016455 | 0.016455 | 0.29773 | 0.29773 |  |  | 0.031216 | 0.031216 | 0.0027938 | 0.0027938 | 0.00026676 | 0.00026676 | 0.003712 | 0.003712 |  |  | 0.00031717 | 0.00031717 | 333 | 293.4 | NO
2012-12-12 | 0.077645 | 0.077645 | 0 | 0 | 0.091039 | 0.091039 |  |  | 0.04019 | 0.04019 | 0.0010968 | 0.0010968 | 0 | 0 | 0.0012812 | 0.0012812 |  |  | 0.00058123 | 0.00058123 | 250 | 232.6 | NO
2012-12-13 | 0.025299 | 0.025299 | 0 | 0 | 0.012127 | 0.012127 |  |  | 0.063237 | 0.063237 | 0.00070178 | 0.00070178 | 0 | 0 | 0.00030312 | 0.00030312 |  |  | 0.0018494 | 0.0018494 | 214 | 193.2 | NO
2012-12-14 | 0.31048 | 0.31048 | 0 | 0 | 0.20812 | 0.20812 |  |  | 0.60657 | 0.60657 | 0.0051864 | 0.0051864 | 0 | 0 | 0.0049733 | 0.0049733 |  |  | 0.005851 | 0.005851 | 306 | 240.2 | NO
2012-12-15 | 0.11956 | 0.11956 | 0 | 0 | 0.018875 | 0.018875 |  |  | 0.40879 | 0.40879 | 0.0015514 | 0.0015514 | 0 | 0 | 0.00024811 | 0.00024811 |  |  | 0.0052951 | 0.0052951 | 229 | 185.8 | NO
2012-12-16 | 0.085979 | 0.085979 | 0 | 0 | 0.047548 | 0.047548 |  |  | 0.19681 | 0.19681 | 0.0023735 | 0.0023735 | 0 | 0 | 0.0015432 | 0.0015432 |  |  | 0.0047733 | 0.0047733 | 148 | 131.2 | NO
2012-12-17 | 0.33549 | 0.33549 | 0 | 0 | 0.19597 | 0.19597 |  |  | 0.73806 | 0.73806 | 0.0055854 | 0.0055854 | 0 | 0 | 0.0028114 | 0.0028114 |  |  | 0.013818 | 0.013818 | 371 | 290.4 | NO
2012-12-18 | 0.4062 | 0.4062 | 0 | 0 | 0.34909 | 0.34909 |  |  | 0.57387 | 0.57387 | 0.0038015 | 0.0038015 | 0 | 0 | 0.0019014 | 0.0019014 |  |  | 0.0092757 | 0.0092757 | 559 | 465 | NO
2012-12-19 | 0.28736 | 0.28736 | 0 | 0 | 0.35868 | 0.35868 |  |  | 0.086528 | 0.086528 | 0.0052494 | 0.0052494 | 0 | 0 | 0.0066969 | 0.0066969 |  |  | 0.0011672 | 0.0011672 | 457 | 315.4 | NO
2012-12-20 | 0.058639 | 0.058639 | 0 | 0 | 0.076809 | 0.076809 |  |  | 0.0073177 | 0.0073177 | 0.001921 | 0.001921 | 0 | 0 | 0.0025535 | 0.0025535 |  |  | 0.00013308 | 0.00013308 | 303 | 252 | NO
2012-12-21 | 0.10638 | 0.10638 | 0 | 0 | 0.12034 | 0.12034 |  |  | 0.067601 | 0.067601 | 0.0019388 | 0.0019388 | 0 | 0 | 0.0018296 | 0.0018296 |  |  | 0.0022722 | 0.0022722 | 288 | 262 | NO
2012-12-22 | 0.26529 | 0.26529 | 0 | 0 | 0.062207 | 0.062207 |  |  | 0.84891 | 0.84891 | 0.0028812 | 0.0028812 | 0 | 0 | 0.00052311 | 0.00052311 |  |  | 0.0096554 | 0.0096554 | 241 | 206.4 | NO
2012-12-23 | 0.14298 | 0.14298 | 0 | 0 | 0.18994 | 0.18994 |  |  | 0.0018966 | 0.0018966 | 0.0017574 | 0.0017574 | 0 | 0 | 0.0023587 | 0.0023587 |  |  | 2.0151e-05 | 2.0151e-05 | 152 | 138 | NO
2012-12-24 | 0.091848 | 0.091848 | 0 | 0 | 0.050616 | 0.050616 |  |  | 0.21075 | 0.21075 | 0.001412 | 0.001412 | 0 | 0 | 0.0014607 | 0.0014607 |  |  | 0.0012881 | 0.0012881 | 177 | 167.4 | NO
2012-12-25 | 0.011869 | 0.011869 | 0 | 0 | 0.0128 | 0.0128 |  |  | 0.0093359 | 0.0093359 | 0.00015459 | 0.00015459 | 0 | 0 | 0.00017642 | 0.00017642 |  |  | 9.3827e-05 | 9.3827e-05 | 105 | 97.2 | NO
2012-12-26 | 0.30561 | 0.30561 | 0 | 0 | 0.17558 | 0.17558 |  |  | 0.68077 | 0.68077 | 0.0044378 | 0.0044378 | 0 | 0 | 0.0021098 | 0.0021098 |  |  | 0.011143 | 0.011143 | 204 | 193.4 | NO
2012-12-27 | 0.054456 | 0.054456 | 0 | 0 | 0.065889 | 0.065889 |  |  | 0.022345 | 0.022345 | 0.0021767 | 0.0021767 | 0 | 0 | 0.0028952 | 0.0028952 |  |  | 0.00014552 | 0.00014552 | 214 | 204.2 | NO
2012-12-28 | 0.25573 | 0.25573 | 0 | 0 | 0.12724 | 0.12724 |  |  | 0.62599 | 0.62599 | 0.0031239 | 0.0031239 | 0 | 0 | 0.0015046 | 0.0015046 |  |  | 0.0077889 | 0.0077889 | 262 | 243.8 | NO
2012-12-29 | 0.15025 | 0.15025 | 0 | 0 | 0.19448 | 0.19448 |  |  | 0.025385 | 0.025385 | 0.0014505 | 0.0014505 | 0 | 0 | 0.0018971 | 0.0018971 |  |  | 0.0001891 | 0.0001891 | 168 | 151.4 | NO
2012-12-30 | 0.096379 | 0.096379 | 0 | 0 | 0.011489 | 0.011489 |  |  | 0.34023 | 0.34023 | 0.0013249 | 0.0013249 | 0 | 0 | 0.00019803 | 0.00019803 |  |  | 0.0045623 | 0.0045623 | 184 | 147.4 | NO
2012-12-31 | 0.26927 | 0.26927 | 0 | 0 | 0.34383 | 0.34383 |  |  | 0.058932 | 0.058932 | 0.0032008 | 0.0032008 | 0 | 0 | 0.0036811 | 0.0036811 |  |  | 0.0018614 | 0.0018614 | 192 | 181.4 | NO
2013-01-01 | 0.0093194 | 0.0093194 | 0 | 0 | 0.010955 | 0.010955 |  |  | 0.0047401 | 0.0047401 | 0.00011863 | 0.00011863 | 0 | 0 | 0.00014562 | 0.00014562 |  |  | 4.2714e-05 | 4.2714e-05 | 122 | 308.6 | NO
2013-01-02 | 0.13707 | 0.13707 | 0 | 0 | 0.18063 | 0.18063 |  |  | 0.013945 | 0.013945 | 0.0012911 | 0.0012911 | 0 | 0 | 0.0016504 | 0.0016504 |  |  | 0.00027716 | 0.00027716 | 232 | 210 | NO
2013-01-03 | 0.17745 | 0.17745 | 0 | 0 | 0.2093 | 0.2093 |  |  | 0.088226 | 0.088226 | 0.0011642 | 0.0011642 | 0 | 0 | 0.0014666 | 0.0014666 |  |  | 0.00031172 | 0.00031172 | 198 | 179.4 | NO
2013-01-04 | 0.19141 | 0.19141 | 0 | 0 | 0.17321 | 0.17321 |  |  | 0.24553 | 0.24553 | 0.0027499 | 0.0027499 | 0 | 0 | 0.0021128 | 0.0021128 |  |  | 0.0046021 | 0.0046021 | 240 | 214 | NO
2013-01-05 | 0.066925 | 0.066925 | 0 | 0 | 0.087372 | 0.087372 |  |  | 0.0091491 | 0.0091491 | 0.0016292 | 0.0016292 | 0 | 0 | 0.0021576 | 0.0021576 |  |  | 0.00013506 | 0.00013506 | 154 | 139.4 | NO
2013-01-06 | 0.34425 | 0.34425 | 0 | 0 | 0.40021 | 0.40021 |  |  | 0.18788 | 0.18788 | 0.0043282 | 0.0043282 | 0 | 0 | 0.0051302 | 0.0051302 |  |  | 0.0020803 | 0.0020803 | 152 | 144.8 | NO
2013-01-07 | 0.15748 | 0.15748 | 0 | 0 | 0.019093 | 0.019093 |  |  | 0.55516 | 0.55516 | 0.0020522 | 0.0020522 | 0 | 0 | 0.00017196 | 0.00017196 |  |  | 0.0074544 | 0.0074544 | 250 | 231.4 | NO
2013-01-08 | 0.16198 | 0.16198 | 0 | 0 | 0.029857 | 0.029857 |  |  | 0.54178 | 0.54178 | 0.0020168 | 0.0020168 | 0 | 0 | 0.00071355 | 0.00071355 |  |  | 0.0057677 | 0.0057677 | 252 | 245.4 | NO
2013-01-09 | 0.39608 | 0.39608 | 0 | 0 | 0.22759 | 0.22759 |  |  | 0.88252 | 0.88252 | 0.0045293 | 0.0045293 | 0 | 0 | 0.0028548 | 0.0028548 |  |  | 0.0093701 | 0.0093701 | 379 | 341.6 | NO
2013-01-10 | 0.11413 | 0.11413 | 0 | 0 | 0.023973 | 0.023973 |  |  | 0.37336 | 0.37336 | 0.0010043 | 0.0010043 | 0 | 0 | 0.00025784 | 0.00025784 |  |  | 0.0031512 | 0.0031512 | 341 | 314 | NO
2013-01-11 | 0.094838 | 0.094838 | 0 | 0 | 0.066461 | 0.066461 |  |  | 0.17703 | 0.17703 | 0.010316 | 0.010316 | 0 | 0 | 0.012783 | 0.012783 |  |  | 0.0033551 | 0.0033551 | 351 | 337 | NO
2013-01-12 | 0.65964 | 0.65964 | 0 | 0 | 0.45344 | 0.45344 |  |  | 1.257 | 1.257 | 0.0094797 | 0.0094797 | 0 | 0 | 0.0055721 | 0.0055721 |  |  | 0.020766 | 0.020766 | 578 | 350.6 | NO
2013-01-13 | 0.18548 | 0.18548 | 0 | 0 | 0.203 | 0.203 |  |  | 0.13736 | 0.13736 | 0.0025475 | 0.0025475 | 0 | 0 | 0.0028459 | 0.0028459 |  |  | 0.0017213 | 0.0017213 | 273 | 246 | NO
2013-01-14 | 0.87039 | 0.87039 | 0 | 0 | 0.74449 | 0.74449 |  |  | 1.2402 | 1.2402 | 0.0056168 | 0.0056168 | 0 | 0 | 0.0044744 | 0.0044744 |  |  | 0.0089478 | 0.0089478 | 374 | 335 | NO
2013-01-15 | 0.35575 | 0.35575 | 0 | 0 | 0.4595 | 0.4595 |  |  | 0.062712 | 0.062712 | 0.0020316 | 0.0020316 | 0 | 0 | 0.002585 | 0.002585 |  |  | 0.00046997 | 0.00046997 | 282 | 268 | NO
2013-01-16 | 0.097892 | 0.097892 | 0 | 0 | 0.11989 | 0.11989 |  |  | 0.036003 | 0.036003 | 0.00084643 | 0.00084643 | 0 | 0 | 0.00090137 | 0.00090137 |  |  | 0.00069846 | 0.00069846 | 267 | 218.8 | NO
2013-01-17 | 0.077135 | 0.077135 | 0 | 0 | 0.054755 | 0.054755 |  |  | 0.14203 | 0.14203 | 0.0016821 | 0.0016821 | 0 | 0 | 0.0014851 | 0.0014851 |  |  | 0.0022644 | 0.0022644 | 231 | 21.6 | NO
2013-01-18 | 0.17698 | 0.17698 | 0 | 0 | 0.034468 | 0.034468 |  |  | 0.58674 | 0.58674 | 0.0021444 | 0.0021444 | 0 | 0 | 0.00043776 | 0.00043776 |  |  | 0.0070518 | 0.0070518 | 284 | 264.6 | NO
2013-01-19 | 0.55284 | 0.55284 | 0 | 0 | 0.45481 | 0.45481 |  |  | 0.83928 | 0.83928 | 0.0063433 | 0.0063433 | 0 | 0 | 0.0061485 | 0.0061485 |  |  | 0.0069703 | 0.0069703 | 395 | 282.6 | NO
2013-01-20 | 0.2227 | 0.2227 | 0 | 0 | 0.198 | 0.198 |  |  | 0.2958 | 0.2958 | 0.0041655 | 0.0041655 | 0 | 0 | 0.0041121 | 0.0041121 |  |  | 0.0043639 | 0.0043639 | 203 | 186.8 | NO
2013-01-21 | 0.502 | 0.502 | 0 | 0 | 0.39137 | 0.39137 |  |  | 0.82372 | 0.82372 | 0.010123 | 0.010123 | 0 | 0 | 0.0090609 | 0.0090609 |  |  | 0.013271 | 0.013271 | 532 | 444.6 | NO
2013-01-22 | 0.22935 | 0.22935 | 0 | 0 | 0.22461 | 0.22461 |  |  | 0.24544 | 0.24544 | 0.0032402 | 0.0032402 | 0 | 0 | 0.0036392 | 0.0036392 |  |  | 0.0021359 | 0.0021359 | 351 | 336.2 | NO
2013-01-23 | 0.27636 | 0.27636 | 0 | 0 | 0.075962 | 0.075962 |  |  | 0.85194 | 0.85194 | 0.0037072 | 0.0037072 | 0 | 0 | 0.0018074 | 0.0018074 |  |  | 0.0091759 | 0.0091759 | 280 | 251.4 | NO
2013-01-24 | 0.13636 | 0.13636 | 0 | 0 | 0.054332 | 0.054332 |  |  | 0.3721 | 0.3721 | 0.0022398 | 0.0022398 | 0 | 0 | 0.0016673 | 0.0016673 |  |  | 0.0038994 | 0.0038994 | 316 | 278.2 | NO
2013-01-25 | 0.31723 | 0.31723 | 0 | 0 | 0.14519 | 0.14519 |  |  | 0.81181 | 0.81181 | 0.0025503 | 0.0025503 | 0 | 0 | 0.00086811 | 0.00086811 |  |  | 0.0073803 | 0.0073803 | 490 | 409.2 | NO
2013-01-26 | 8.3576 | 8.3576 | 0 | 0 | 0.84861 | 0.84861 |  |  | 29.8776 | 29.8776 | 0.018828 | 0.018828 | 0 | 0 | 0.0061704 | 0.0061704 |  |  | 0.055156 | 0.055156 | 0 | 0 | Yes
2013-01-27 | 281.2041 | 281.2041 | 0 | 0 | 167.4015 | 167.4015 |  |  | 609.0153 | 609.0153 | 0.20803 | 0.20803 | 0 | 0 | 0.15079 | 0.15079 |  |  | 0.37364 | 0.37364 | 0 | 0 | Yes
2013-01-28 | 139.6935 | 139.6935 | 0 | 0 | 131.149 | 131.149 |  |  | 165.6135 | 165.6135 | 0.13557 | 0.13557 | 0 | 0 | 0.13934 | 0.13934 |  |  | 0.12634 | 0.12634 | 0 | 0 | Yes
2013-01-29 | 14.2725 | 14.2725 | 3.1312 | 3.1312 | 13.136 | 13.136 |  |  | 17.6362 | 17.6362 | 0.022767 | 0.022767 | 0.00044046 | 0.00044046 | 0.017208 | 0.017208 |  |  | 0.038863 | 0.038863 | 0 | 0 | Yes
2013-01-30 | 3.2322 | 3.2322 | 0 | 0 | 2.6179 | 2.6179 |  |  | 5.0187 | 5.0187 | 0.0089118 | 0.0089118 | 0 | 0 | 0.00702 | 0.00702 |  |  | 0.014402 | 0.014402 | 5318 | 3560 | NO
2013-01-31 | 1.1063 | 1.1063 | 0 | 0 | 1.0976 | 1.0976 |  |  | 1.1413 | 1.1413 | 0.0041588 | 0.0041588 | 0 | 0 | 0.0038797 | 0.0038797 |  |  | 0.004992 | 0.004992 | 2711 | 1444.6 | NO
2013-02-01 | 0.9833 | 0.9833 | 0 | 0 | 0.62765 | 0.62765 |  |  | 2.0067 | 2.0067 | 0.0080628 | 0.0080628 | 0 | 0 | 0.005566 | 0.005566 |  |  | 0.015257 | 0.015257 | 1812 | 1146.4 | NO
2013-02-02 | 0.32374 | 0.32374 | 0.0076511 | 0.0076511 | 0.28565 | 0.28565 |  |  | 0.43578 | 0.43578 | 0.0031462 | 0.0031462 | 0.00025776 | 0.00025776 | 0.0031794 | 0.0031794 |  |  | 0.0030854 | 0.0030854 | 923 | 663.8 | NO
2013-02-03 | 0.076128 | 0.076128 | 0 | 0 | 0.099965 | 0.099965 |  |  | 0.0091307 | 0.0091307 | 0.0012249 | 0.0012249 | 0 | 0 | 0.0014771 | 0.0014771 |  |  | 0.00052045 | 0.00052045 | 298 | 267.8 | NO
2013-02-04 | 0.42473 | 0.42473 | 0 | 0 | 0.3224 | 0.3224 |  |  | 0.7206 | 0.7206 | 0.0054474 | 0.0054474 | 0 | 0 | 0.0046092 | 0.0046092 |  |  | 0.0078928 | 0.0078928 | 736 | 656.6 | NO
2013-02-05 | 0.36634 | 0.36634 | 0 | 0 | 0.32146 | 0.32146 |  |  | 0.49808 | 0.49808 | 0.0050543 | 0.0050543 | 0 | 0 | 0.0040021 | 0.0040021 |  |  | 0.0081031 | 0.0081031 | 520 | 491.4 | NO
2013-02-06 | 0.4287 | 0.4287 | 0 | 0 | 0.38089 | 0.38089 |  |  | 0.56942 | 0.56942 | 0.0055944 | 0.0055944 | 0 | 0 | 0.0062399 | 0.0062399 |  |  | 0.0038217 | 0.0038217 | 514 | 426.6 | NO
2013-02-07 | 0.11721 | 0.11721 | 0 | 0 | 0.13581 | 0.13581 |  |  | 0.065645 | 0.065645 | 0.00094449 | 0.00094449 | 0 | 0 | 0.0010182 | 0.0010182 |  |  | 0.0007455 | 0.0007455 | 352 | 311 | NO
2013-02-08 | 0.13703 | 0.13703 | 0 | 0 | 0.17187 | 0.17187 |  |  | 0.039584 | 0.039584 | 0.0014377 | 0.0014377 | 0 | 0 | 0.001788 | 0.001788 |  |  | 0.00045838 | 0.00045838 | 362 | 315.8 | NO
2013-02-09 | 0.18025 | 0.18025 | 0 | 0 | 0.13905 | 0.13905 |  |  | 0.29927 | 0.29927 | 0.015911 | 0.015911 | 0 | 0 | 0.016518 | 0.016518 |  |  | 0.014363 | 0.014363 | 310 | 263 | NO
2013-02-10 | 0.062783 | 0.062783 | 0 | 0 | 0.02849 | 0.02849 |  |  | 0.16552 | 0.16552 | 0.0010178 | 0.0010178 | 0 | 0 | 0.00052937 | 0.00052937 |  |  | 0.0024216 | 0.0024216 | 182 | 166.6 | NO
2013-02-11 | 0.090203 | 0.090203 | 0 | 0 | 0.11362 | 0.11362 |  |  | 0.02476 | 0.02476 | 0.0013289 | 0.0013289 | 0 | 0 | 0.0017472 | 0.0017472 |  |  | 0.00015677 | 0.00015677 | 421 | 377.4 | NO
2013-02-12 | 0.27412 | 0.27412 | 0 | 0 | 0.045246 | 0.045246 |  |  | 0.92646 | 0.92646 | 0.0034029 | 0.0034029 | 0 | 0 | 0.00033853 | 0.00033853 |  |  | 0.012134 | 0.012134 | 321 | 297.6 | NO
2013-02-13 | 0.5219 | 0.5219 | 0 | 0 | 0.38849 | 0.38849 |  |  | 0.90603 | 0.90603 | 0.0050598 | 0.0050598 | 0 | 0 | 0.0024768 | 0.0024768 |  |  | 0.012441 | 0.012441 | 420 | 335 | NO
2013-02-14 | 0.29969 | 0.29969 | 0 | 0 | 0.30517 | 0.30517 |  |  | 0.28748 | 0.28748 | 0.0049846 | 0.0049846 | 0 | 0 | 0.0046711 | 0.0046711 |  |  | 0.0059287 | 0.0059287 | 416 | 357.6 | NO
2013-02-15 | 0.076718 | 0.076718 | 0 | 0 | 0.10116 | 0.10116 |  |  | 0.0082956 | 0.0082956 | 0.0021812 | 0.0021812 | 0 | 0 | 0.0029018 | 0.0029018 |  |  | 0.0001633 | 0.0001633 | 288 | 270.2 | NO
2013-02-16 | 0.097893 | 0.097893 | 0 | 0 | 0.026845 | 0.026845 |  |  | 0.30033 | 0.30033 | 0.0017056 | 0.0017056 | 0 | 0 | 0.00033837 | 0.00033837 |  |  | 0.0055991 | 0.0055991 | 294 | 241 | NO
2013-02-17 | 0.14434 | 0.14434 | 0 | 0 | 0.10642 | 0.10642 |  |  | 0.25339 | 0.25339 | 0.0023585 | 0.0023585 | 0 | 0 | 0.0024055 | 0.0024055 |  |  | 0.0022515 | 0.0022515 | 212 | 189.4 | NO
2013-02-18 | 0.58917 | 0.58917 | 0.14226 | 0.14226 | 0.39945 | 0.39945 |  |  | 1.1315 | 1.1315 | 0.004895 | 0.004895 | 0.00077315 | 0.00077315 | 0.0037806 | 0.0037806 |  |  | 0.0080958 | 0.0080958 | 532 | 465.2 | NO
2013-02-19 | 0.22568 | 0.22568 | 0 | 0 | 0.16086 | 0.16086 |  |  | 0.41187 | 0.41187 | 0.0035746 | 0.0035746 | 0 | 0 | 0.0031133 | 0.0031133 |  |  | 0.0049211 | 0.0049211 | 615 | 478.6 | NO
2013-02-20 | 0.21028 | 0.21028 | 0 | 0 | 0.024624 | 0.024624 |  |  | 0.73866 | 0.73866 | 0.0030723 | 0.0030723 | 0 | 0 | 0.00012607 | 0.00012607 |  |  | 0.011454 | 0.011454 | 422 | 371.8 | NO
2013-02-21 | 0.23639 | 0.23639 | 0 | 0 | 0.24422 | 0.24422 |  |  | 0.21685 | 0.21685 | 0.0039989 | 0.0039989 | 0 | 0 | 0.0041783 | 0.0041783 |  |  | 0.0035348 | 0.0035348 | 349 | 317.4 | NO
2013-02-22 | 0.93196 | 0.93196 | 0 | 0 | 0.80227 | 0.80227 |  |  | 1.3097 | 1.3097 | 0.010786 | 0.010786 | 0 | 0 | 0.010377 | 0.010377 |  |  | 0.012065 | 0.012065 | 713 | 643.8 | NO
2013-02-23 | 0.14714 | 0.14714 | 0 | 0 | 0.19007 | 0.19007 |  |  | 0.027173 | 0.027173 | 0.0025163 | 0.0025163 | 0 | 0 | 0.0033134 | 0.0033134 |  |  | 0.00028645 | 0.00028645 | 325 | 281.4 | NO
2013-02-24 | 0.16378 | 0.16378 | 0 | 0 | 0.19123 | 0.19123 |  |  | 0.087842 | 0.087842 | 0.0017761 | 0.0017761 | 0 | 0 | 0.0018937 | 0.0018937 |  |  | 0.0014626 | 0.0014626 | 270 | 243.6 | NO
2013-02-25 | 0.58004 | 0.58004 | 0 | 0 | 0.3184 | 0.3184 |  |  | 1.3275 | 1.3275 | 0.0040919 | 0.0040919 | 0 | 0 | 0.002098 | 0.002098 |  |  | 0.0097844 | 0.0097844 | 616 | 530.8 | NO
2013-02-26 | 0.29083 | 0.29083 | 0 | 0 | 0.35819 | 0.35819 |  |  | 0.10329 | 0.10329 | 0.0031701 | 0.0031701 | 0 | 0 | 0.0041674 | 0.0041674 |  |  | 0.00038072 | 0.00038072 | 456 | 407.8 | NO
2013-02-27 | 0.11445 | 0.11445 | 0 | 0 | 0.042871 | 0.042871 |  |  | 0.31843 | 0.31843 | 0.0021313 | 0.0021313 | 0 | 0 | 0.00090652 | 0.00090652 |  |  | 0.0056237 | 0.0056237 | 345 | 306.4 | NO
2013-02-28 | 0.034921 | 0.034921 | 0 | 0 | 0.025031 | 0.025031 |  |  | 0.063316 | 0.063316 | 0.00063407 | 0.00063407 | 0 | 0 | 0.00021719 | 0.00021719 |  |  | 0.0018217 | 0.0018217 | 350 | 315.6 | NO
2013-03-01 | 0.1374 | 0.1374 | 0 | 0 | 0.0077226 | 0.0077226 |  |  | 0.50617 | 0.50617 | 0.00086445 | 0.00086445 | 0 | 0 | 7.373e-05 | 7.373e-05 |  |  | 0.0031133 | 0.0031133 | 298 | 253.6 | NO
2013-03-02 | 0.082823 | 0.082823 | 0 | 0 | 0.10876 | 0.10876 |  |  | 0.0103 | 0.0103 | 0.00099927 | 0.00099927 | 0 | 0 | 0.0013239 | 0.0013239 |  |  | 9.1064e-05 | 9.1064e-05 | 321 | 267.6 | NO
2013-03-03 | 0.2011 | 0.2011 | 0.013305 | 0.013305 | 0.1818 | 0.1818 |  |  | 0.25784 | 0.25784 | 0.0032861 | 0.0032861 | 0.00025819 | 0.00025819 | 0.0026247 | 0.0026247 |  |  | 0.0051927 | 0.0051927 | 341 | 289 | NO
2013-03-04 | 0.10712 | 0.10712 | 0.02164 | 0.02164 | 0.04463 | 0.04463 |  |  | 0.2851 | 0.2851 | 0.0010007 | 0.0010007 | 0.00025823 | 0.00025823 | 0.00034462 | 0.00034462 |  |  | 0.0028673 | 0.0028673 | 425 | 363 | NO
2013-03-05 | 0.085884 | 0.085884 | 0 | 0 | 0.076686 | 0.076686 |  |  | 0.1129 | 0.1129 | 0.0026614 | 0.0026614 | 0 | 0 | 0.00038644 | 0.00038644 |  |  | 0.0091367 | 0.0091367 | 444 | 394.2 | NO
2013-03-06 | 0.055078 | 0.055078 | 0.070247 | 0.070247 | 0.049919 | 0.049919 |  |  | 0.069529 | 0.069529 | 0.0013966 | 0.0013966 | 0.00025831 | 0.00025831 | 0.00089147 | 0.00089147 |  |  | 0.0028407 | 0.0028407 | 314 | 280.8 | NO
2013-03-07 | 0.093144 | 0.093144 | 0 | 0 | 0.031729 | 0.031729 |  |  | 0.26823 | 0.26823 | 0.0014946 | 0.0014946 | 0 | 0 | 0.00091313 | 0.00091313 |  |  | 0.003159 | 0.003159 | 309 | 276.8 | NO
2013-03-08 | 0.066845 | 0.066845 | 0 | 0 | 0.082022 | 0.082022 |  |  | 0.024568 | 0.024568 | 0.0012214 | 0.0012214 | 0 | 0 | 0.0016 | 0.0016 |  |  | 0.00016181 | 0.00016181 | 322 | 293.2 | NO
2013-03-09 | 0.062914 | 0.062914 | 0 | 0 | 0.070072 | 0.070072 |  |  | 0.04332 | 0.04332 | 0.00064526 | 0.00064526 | 0 | 0 | 0.00057639 | 0.00057639 |  |  | 0.00084763 | 0.00084763 | 209 | 194.6 | NO
2013-03-10 | 0.031493 | 0.031493 | 0 | 0 | 0.0049868 | 0.0049868 |  |  | 0.10698 | 0.10698 | 0.00015719 | 0.00015719 | 0 | 0 | 4.8487e-05 | 4.8487e-05 |  |  | 0.00046707 | 0.00046707 | 156 | 151.2 | NO
2013-03-11 | 0.23614 | 0.23614 | 0 | 0 | 0.17877 | 0.17877 |  |  | 0.40145 | 0.40145 | 0.0029653 | 0.0029653 | 0 | 0 | 0.0026601 | 0.0026601 |  |  | 0.0038636 | 0.0038636 | 343 | 292.6 | NO
2013-03-12 | 0.1067 | 0.1067 | 0 | 0 | 0.078859 | 0.078859 |  |  | 0.18683 | 0.18683 | 0.0020675 | 0.0020675 | 0 | 0 | 0.001403 | 0.001403 |  |  | 0.0039747 | 0.0039747 | 308 | 259.2 | NO
2013-03-13 | 0.073349 | 0.073349 | 0 | 0 | 0.077654 | 0.077654 |  |  | 0.061954 | 0.061954 | 0.00082796 | 0.00082796 | 0 | 0 | 0.0010689 | 0.0010689 |  |  | 0.00015371 | 0.00015371 | 246 | 219.2 | NO
2013-03-14 | 0.47438 | 0.47438 | 0 | 0 | 0.089649 | 0.089649 |  |  | 1.5711 | 1.5711 | 0.0028813 | 0.0028813 | 0 | 0 | 0.00098878 | 0.00098878 |  |  | 0.0082823 | 0.0082823 | 348 | 278.2 | NO
2013-03-15 | 0.056621 | 0.056621 | 0 | 0 | 0.067737 | 0.067737 |  |  | 0.025707 | 0.025707 | 0.0010557 | 0.0010557 | 0 | 0 | 0.0012783 | 0.0012783 |  |  | 0.00043577 | 0.00043577 | 294 | 247 | NO
2013-03-16 | 0.046889 | 0.046889 | 0 | 0 | 0.022268 | 0.022268 |  |  | 0.11728 | 0.11728 | 0.0014066 | 0.0014066 | 0 | 0 | 0.0014255 | 0.0014255 |  |  | 0.0013683 | 0.0013683 | 218 | 200.6 | NO
2013-03-17 | 0.43081 | 0.43081 | 0 | 0 | 0.5351 | 0.5351 |  |  | 0.13959 | 0.13959 | 0.0057209 | 0.0057209 | 0 | 0 | 0.0068112 | 0.0068112 |  |  | 0.0026899 | 0.0026899 | 261 | 234.2 | NO
2013-03-18 | 0.074554 | 0.074554 | 0 | 0 | 0.03454 | 0.03454 |  |  | 0.18898 | 0.18898 | 0.0019912 | 0.0019912 | 0 | 0 | 0.0015712 | 0.0015712 |  |  | 0.0032058 | 0.0032058 | 270 | 231.8 | NO
2013-03-19 | 0.063629 | 0.063629 | 0 | 0 | 0.016811 | 0.016811 |  |  | 0.19727 | 0.19727 | 0.0015676 | 0.0015676 | 0 | 0 | 0.00021711 | 0.00021711 |  |  | 0.0054195 | 0.0054195 | 306 | 282.8 | NO
2013-03-20 | 0.14125 | 0.14125 | 0 | 0 | 0.059937 | 0.059937 |  |  | 0.37377 | 0.37377 | 0.0018295 | 0.0018295 | 0 | 0 | 0.0005464 | 0.0005464 |  |  | 0.005494 | 0.005494 | 279 | 256.4 | NO
2013-03-21 | 0.0987 | 0.0987 | 0 | 0 | 0.12581 | 0.12581 |  |  | 0.022774 | 0.022774 | 0.0010228 | 0.0010228 | 0 | 0 | 0.001317 | 0.001317 |  |  | 0.0001984 | 0.0001984 | 264 | 249.2 | NO
2013-03-22 | 0.013118 | 0.013118 | 0 | 0 | 0.014658 | 0.014658 |  |  | 0.0088851 | 0.0088851 | 0.00022563 | 0.00022563 | 0 | 0 | 0.00020608 | 0.00020608 |  |  | 0.00028366 | 0.00028366 | 234 | 220 | NO
2013-03-23 | 0.12202 | 0.12202 | 0 | 0 | 0.024159 | 0.024159 |  |  | 0.39685 | 0.39685 | 0.0011387 | 0.0011387 | 0 | 0 | 0.00013359 | 0.00013359 |  |  | 0.0039649 | 0.0039649 | 229 | 203 | NO
2013-03-24 | 18.7464 | 18.7464 | 0 | 0 | 11.0361 | 11.0361 |  |  | 40.8729 | 40.8729 | 0.051733 | 0.051733 | 0 | 0 | 0.029379 | 0.029379 |  |  | 0.11585 | 0.11585 | 0 | 0 | Yes
2013-03-25 | 0.72845 | 0.72845 | 0 | 0 | 0.30094 | 0.30094 |  |  | 1.9523 | 1.9523 | 0.0049255 | 0.0049255 | 0 | 0 | 0.0034002 | 0.0034002 |  |  | 0.0093179 | 0.0093179 | 1661 | 1185 | NO
2013-03-26 | 0.40946 | 0.40946 | 0 | 0 | 0.2498 | 0.2498 |  |  | 0.86788 | 0.86788 | 0.0039687 | 0.0039687 | 0 | 0 | 0.0019332 | 0.0019332 |  |  | 0.0098005 | 0.0098005 | 522 | 431.8 | NO
2013-03-27 | 0.31392 | 0.31392 | 0 | 0 | 0.36155 | 0.36155 |  |  | 0.18187 | 0.18187 | 0.0022149 | 0.0022149 | 0 | 0 | 0.0026067 | 0.0026067 |  |  | 0.0011246 | 0.0011246 | 413 | 317.8 | NO
2013-03-28 | 0.015548 | 0.015548 | 0 | 0 | 0.016513 | 0.016513 |  |  | 0.012974 | 0.012974 | 0.00037208 | 0.00037208 | 0 | 0 | 0.00048052 | 0.00048052 |  |  | 6.7484e-05 | 6.7484e-05 | 292 | 242.2 | NO
2013-03-29 | 0.50887 | 0.50887 | 0 | 0 | 0.68704 | 0.68704 |  |  | 0.0071592 | 0.0071592 | 0.0031839 | 0.0031839 | 0 | 0 | 0.0042808 | 0.0042808 |  |  | 9.5874e-05 | 9.5874e-05 | 283 | 266.6 | NO
2013-03-30 | 0.046321 | 0.046321 | 0 | 0 | 0.013014 | 0.013014 |  |  | 0.1417 | 0.1417 | 0.0003835 | 0.0003835 | 0 | 0 | 0.00015002 | 0.00015002 |  |  | 0.0010528 | 0.0010528 | 139 | 127.4 | NO
2013-03-31 | 0.45075 | 0.45075 | 0 | 0 | 0.58152 | 0.58152 |  |  | 0.082763 | 0.082763 | 0.003509 | 0.003509 | 0 | 0 | 0.0040047 | 0.0040047 |  |  | 0.0021332 | 0.0021332 | 335 | 266.2 | NO
2013-04-01 | 0.032647 | 0.032647 | 0 | 0 | 0.022674 | 0.022674 |  |  | 0.061425 | 0.061425 | 0.00024024 | 0.00024024 | 0 | 0 | 0.00024337 | 0.00024337 |  |  | 0.00023398 | 0.00023398 | 168 | 150 | NO
2013-04-02 | 0.17826 | 0.17826 | 0 | 0 | 0.2377 | 0.2377 |  |  | 0.010306 | 0.010306 | 0.0023109 | 0.0023109 | 0 | 0 | 0.0030976 | 0.0030976 |  |  | 8.6213e-05 | 8.6213e-05 | 409 | 372.2 | NO
2013-04-03 | 0.35421 | 0.35421 | 0 | 0 | 0.178 | 0.178 |  |  | 0.86042 | 0.86042 | 0.0056856 | 0.0056856 | 0 | 0 | 0.0051774 | 0.0051774 |  |  | 0.0071974 | 0.0071974 | 418 | 327 | NO
2013-04-04 | 0.13791 | 0.13791 | 0 | 0 | 0.070587 | 0.070587 |  |  | 0.33138 | 0.33138 | 0.0028307 | 0.0028307 | 0 | 0 | 0.0017927 | 0.0017927 |  |  | 0.0058211 | 0.0058211 | 357 | 269.6 | NO
2013-04-05 | 0.32831 | 0.32831 | 0 | 0 | 0.43892 | 0.43892 |  |  | 0.016232 | 0.016232 | 0.0037075 | 0.0037075 | 0 | 0 | 0.0048816 | 0.0048816 |  |  | 0.0003954 | 0.0003954 | 357 | 332.8 | NO
2013-04-06 | 0.0038181 | 0.0038181 | 0 | 0 | 0.00071412 | 0.00071412 |  |  | 0.012713 | 0.012713 | 4.4685e-05 | 4.4685e-05 | 0 | 0 | 9.1739e-06 | 9.1739e-06 |  |  | 0.00014645 | 0.00014645 | 143 | 131.6 | NO
2013-04-07 | 0.073874 | 0.073874 | 0 | 0 | 0.081573 | 0.081573 |  |  | 0.052739 | 0.052739 | 0.00086261 | 0.00086261 | 0 | 0 | 0.00093114 | 0.00093114 |  |  | 0.00067675 | 0.00067675 | 123 | 113.6 | NO
2013-04-08 | 0.17963 | 0.17963 | 0.031174 | 0.031174 | 0.037751 | 0.037751 |  |  | 0.58613 | 0.58613 | 0.0042493 | 0.0042493 | 0.00025863 | 0.00025863 | 0.00070737 | 0.00070737 |  |  | 0.014401 | 0.014401 | 325 | 266.4 | NO
2013-04-09 | 0.11663 | 0.11663 | 0 | 0 | 0.073649 | 0.073649 |  |  | 0.2406 | 0.2406 | 0.0010016 | 0.0010016 | 0 | 0 | 0.00045672 | 0.00045672 |  |  | 0.0025679 | 0.0025679 | 229 | 205.8 | NO
2013-04-10 | 0.16846 | 0.16846 | 0 | 0 | 0.18194 | 0.18194 |  |  | 0.13184 | 0.13184 | 0.0027607 | 0.0027607 | 0 | 0 | 0.0032935 | 0.0032935 |  |  | 0.0012702 | 0.0012702 | 333 | 274.6 | NO
2013-04-11 | 0.17508 | 0.17508 | 0 | 0 | 0.20673 | 0.20673 |  |  | 0.086662 | 0.086662 | 0.0036364 | 0.0036364 | 0 | 0 | 0.003814 | 0.003814 |  |  | 0.00317 | 0.00317 | 335 | 251.2 | NO
2013-04-12 | 0.17908 | 0.17908 | 0 | 0 | 0.16069 | 0.16069 |  |  | 0.2336 | 0.2336 | 0.0020087 | 0.0020087 | 0 | 0 | 0.0019878 | 0.0019878 |  |  | 0.0020908 | 0.0020908 | 231 | 198.2 | NO
2013-04-13 | 0.14751 | 0.14751 | 0 | 0 | 0.044954 | 0.044954 |  |  | 0.44209 | 0.44209 | 0.00095741 | 0.00095741 | 0 | 0 | 0.00016917 | 0.00016917 |  |  | 0.0032196 | 0.0032196 | 241 | 209 | NO
2013-04-14 | 0.028328 | 0.028328 | 0 | 0 | 0.025888 | 0.025888 |  |  | 0.037333 | 0.037333 | 0.0001707 | 0.0001707 | 0 | 0 | 0.00012718 | 0.00012718 |  |  | 0.00031707 | 0.00031707 | 164 | 140.4 | NO
2013-04-15 | 0.013683 | 0.013683 | 0 | 0 | 0.018806 | 0.018806 |  |  | 0.0012996 | 0.0012996 | 0.00017005 | 0.00017005 | 0 | 0 | 0.00022465 | 0.00022465 |  |  | 3.6099e-05 | 3.6099e-05 | 266 | 238.6 | NO
2013-04-16 | 0.2708 | 0.2708 | 0 | 0 | 0.019443 | 0.019443 |  |  | 0.99415 | 0.99415 | 0.0037351 | 0.0037351 | 0 | 0 | 0.00036237 | 0.00036237 |  |  | 0.013441 | 0.013441 | 403 | 332.4 | NO
2013-04-17 | 0.48683 | 0.48683 | 0 | 0 | 0.33512 | 0.33512 |  |  | 0.92969 | 0.92969 | 0.0098277 | 0.0098277 | 0 | 0 | 0.0090857 | 0.0090857 |  |  | 0.012087 | 0.012087 | 365 | 312.4 | NO
2013-04-18 | 0.13854 | 0.13854 | 0 | 0 | 0.14031 | 0.14031 |  |  | 0.13885 | 0.13885 | 0.0012462 | 0.0012462 | 0 | 0 | 0.00083 | 0.00083 |  |  | 0.0025017 | 0.0025017 | 340 | 268.2 | NO
2013-04-19 | 0.043132 | 0.043132 | 0 | 0 | 0.043536 | 0.043536 |  |  | 0.047439 | 0.047439 | 0.0010487 | 0.0010487 | 0 | 0 | 0.00024224 | 0.00024224 |  |  | 0.0033893 | 0.0033893 | 239 | 214.6 | NO
2013-04-20 | 0.071214 | 0.071214 | 0 | 0 | 0.097396 | 0.097396 |  |  | 0 | 0 | 0.0012779 | 0.0012779 | 0 | 0 | 0.0017399 | 0.0017399 |  |  | 0 | 0 | 203 | 169.8 | NO
2013-04-21 | 0.078153 | 0.078153 | 0 | 0 | 0.00057452 | 0.00057452 |  |  | 0.30254 | 0.30254 | 0.0011831 | 0.0011831 | 0 | 0 | 6.0429e-06 | 6.0429e-06 |  |  | 0.0045799 | 0.0045799 | 113 | 109 | NO
2013-04-22 | 0.015485 | 0.015485 | 0 | 0 | 0.021529 | 0.021529 |  |  | 0.0046377 | 0.0046377 | 0.00026541 | 0.00026541 | 0 | 0 | 0.0003673 | 0.0003673 |  |  | 3.4567e-05 | 3.4567e-05 | 245 | 199.2 | NO
2013-04-23 | 0.16217 | 0.16217 | 0 | 0 | 0.067325 | 0.067325 |  |  | 0.43829 | 0.43829 | 0.0031029 | 0.0031029 | 0 | 0 | 0.0018437 | 0.0018437 |  |  | 0.0067685 | 0.0067685 | 273 | 224.8 | NO
2013-04-24 | 0.022726 | 0.022726 | 0 | 0 | 0.021482 | 0.021482 |  |  | 0.030888 | 0.030888 | 0.00021372 | 0.00021372 | 0 | 0 | 0.00019157 | 0.00019157 |  |  | 0.00032269 | 0.00032269 | 229 | 193.4 | NO
2013-04-25 | 0.31658 | 0.31658 | 0 | 0 | 0.42836 | 0.42836 |  |  | 0.0028669 | 0.0028669 | 0.0021057 | 0.0021057 | 0 | 0 | 0.0028568 | 0.0028568 |  |  | 1.4406e-05 | 1.4406e-05 | 189 | 151 | NO
2013-04-26 | 0.079282 | 0.079282 | 0 | 0 | 0.078482 | 0.078482 |  |  | 0.086443 | 0.086443 | 0.0015173 | 0.0015173 | 0 | 0 | 0.00070613 | 0.00070613 |  |  | 0.0038899 | 0.0038899 | 248 | 227.6 | NO
2013-04-27 | 0.053384 | 0.053384 | 0 | 0 | 0.067144 | 0.067144 |  |  | 0.018188 | 0.018188 | 0.0020699 | 0.0020699 | 0 | 0 | 0.002754 | 0.002754 |  |  | 0.0001583 | 0.0001583 | 171 | 153.6 | NO
2013-04-28 | 0.078725 | 0.078725 | 0 | 0 | 0.050609 | 0.050609 |  |  | 0.16254 | 0.16254 | 0.0013066 | 0.0013066 | 0 | 0 | 0.00088658 | 0.00088658 |  |  | 0.0025549 | 0.0025549 | 112 | 106.2 | NO
2013-04-29 | 0.038902 | 0.038902 | 0 | 0 | 0.026123 | 0.026123 |  |  | 0.079855 | 0.079855 | 0.00074635 | 0.00074635 | 0 | 0 | 0.00019013 | 0.00019013 |  |  | 0.002384 | 0.002384 | 251 | 226.4 | NO
2013-04-30 | 0.14027 | 0.14027 | 0 | 0 | 0.15479 | 0.15479 |  |  | 0.10178 | 0.10178 | 0.0017799 | 0.0017799 | 0 | 0 | 0.0022128 | 0.0022128 |  |  | 0.00057466 | 0.00057466 | 283 | 265.6 | NO
2013-05-01 | 0.13385 | 0.13385 | 0 | 0 | 0.003287 | 0.003287 |  |  | 0.51149 | 0.51149 | 0.00058182 | 0.00058182 | 0 | 0 | 2.67e-05 | 2.67e-05 |  |  | 0.0022005 | 0.0022005 | 225 | 217.8 | NO
2013-05-02 | 0.093417 | 0.093417 | 0 | 0 | 0.1258 | 0.1258 |  |  | 0.0012784 | 0.0012784 | 0.0015007 | 0.0015007 | 0 | 0 | 0.0020246 | 0.0020246 |  |  | 1.4412e-05 | 1.4412e-05 | 258 | 236.8 | NO
2013-05-03 | 0.0050133 | 0.0050133 | 0 | 0 | 0.0015962 | 0.0015962 |  |  | 0.014853 | 0.014853 | 5.0894e-05 | 5.0894e-05 | 0 | 0 | 1.7517e-05 | 1.7517e-05 |  |  | 0.00014703 | 0.00014703 | 236 | 203.4 | NO
2013-05-04 | 0.032424 | 0.032424 | 0 | 0 | 0.036744 | 0.036744 |  |  | 0.020415 | 0.020415 | 0.00037637 | 0.00037637 | 0 | 0 | 0.00043749 | 0.00043749 |  |  | 0.00020554 | 0.00020554 | 209 | 187 | NO
2013-05-05 | 0.17949 | 0.17949 | 0 | 0 | 0.16332 | 0.16332 |  |  | 0.22778 | 0.22778 | 0.0016633 | 0.0016633 | 0 | 0 | 0.002165 | 0.002165 |  |  | 0.00024504 | 0.00024504 | 144 | 138.2 | NO
2013-05-06 | 0.039403 | 0.039403 | 0 | 0 | 0.047077 | 0.047077 |  |  | 0.017862 | 0.017862 | 0.0010927 | 0.0010927 | 0 | 0 | 0.0014106 | 0.0014106 |  |  | 0.0001946 | 0.0001946 | 310 | 238.6 | NO
2013-05-07 | 0.11293 | 0.11293 | 0 | 0 | 0.13975 | 0.13975 |  |  | 0.037398 | 0.037398 | 0.0033683 | 0.0033683 | 0 | 0 | 0.004396 | 0.004396 |  |  | 0.0004622 | 0.0004622 | 261 | 239.8 | NO
2013-05-08 | 0.34688 | 0.34688 | 0 | 0 | 0.44662 | 0.44662 |  |  | 0.065046 | 0.065046 | 0.0021242 | 0.0021242 | 0 | 0 | 0.0026585 | 0.0026585 |  |  | 0.00061737 | 0.00061737 | 293 | 265.2 | NO
2013-05-09 | 0.017673 | 0.017673 | 0 | 0 | 0.0098244 | 0.0098244 |  |  | 0.040348 | 0.040348 | 0.00018581 | 0.00018581 | 0 | 0 | 8.6164e-05 | 8.6164e-05 |  |  | 0.00047324 | 0.00047324 | 247 | 230 | NO
2013-05-10 | 0.048431 | 0.048431 | 0 | 0 | 0.062672 | 0.062672 |  |  | 0.0081784 | 0.0081784 | 0.00039447 | 0.00039447 | 0 | 0 | 0.00048664 | 0.00048664 |  |  | 0.00013482 | 0.00013482 | 239 | 219.6 | NO
2013-05-11 | 0.095347 | 0.095347 | 0.41995 | 0.41995 | 0.12866 | 0.12866 |  |  | 0.00097966 | 0.00097966 | 0.0008802 | 0.0008802 | 0.0038778 | 0.0038778 | 0.0011889 | 0.0011889 |  |  | 5.7661e-06 | 5.7661e-06 | 185 | 174.6 | NO
2013-05-12 | 0.017932 | 0.017932 | 0 | 0 | 0.023819 | 0.023819 |  |  | 0.0012663 | 0.0012663 | 0.00015233 | 0.00015233 | 0 | 0 | 0.00020207 | 0.00020207 |  |  | 1.1533e-05 | 1.1533e-05 | 90 | 81.2 | NO
2013-05-13 | 0.22857 | 0.22857 | 0 | 0 | 0.029653 | 0.029653 |  |  | 0.80144 | 0.80144 | 0.0028257 | 0.0028257 | 0 | 0 | 0.0014409 | 0.0014409 |  |  | 0.0068272 | 0.0068272 | 262 | 253.8 | NO
2013-05-14 | 0.06516 | 0.06516 | 0 | 0 | 0.0764 | 0.0764 |  |  | 0.033652 | 0.033652 | 0.00073934 | 0.00073934 | 0 | 0 | 0.00090898 | 0.00090898 |  |  | 0.0002611 | 0.0002611 | 276 | 263.2 | NO
2013-05-15 | 0.015683 | 0.015683 | 0 | 0 | 0.0019825 | 0.0019825 |  |  | 0.055148 | 0.055148 | 0.0001625 | 0.0001625 | 0 | 0 | 1.3532e-05 | 1.3532e-05 |  |  | 0.00059149 | 0.00059149 | 223 | 204.8 | NO
2013-05-16 | 0.023389 | 0.023389 | 0 | 0 | 0.026002 | 0.026002 |  |  | 0.016156 | 0.016156 | 0.00023058 | 0.00023058 | 0 | 0 | 0.00027162 | 0.00027162 |  |  | 0.00011542 | 0.00011542 | 232 | 216.6 | NO
2013-05-17 | 0.39836 | 0.39836 | 0 | 0 | 0.46173 | 0.46173 |  |  | 0.22099 | 0.22099 | 0.0051683 | 0.0051683 | 0 | 0 | 0.0061791 | 0.0061791 |  |  | 0.002326 | 0.002326 | 313 | 273.6 | NO
2013-05-18 | 0.015819 | 0.015819 | 0 | 0 | 0.0013844 | 0.0013844 |  |  | 0.057402 | 0.057402 | 0.00025277 | 0.00025277 | 0 | 0 | 1.3078e-05 | 1.3078e-05 |  |  | 0.0009432 | 0.0009432 | 188 | 148 | NO
2013-05-19 | 0.030419 | 0.030419 | 0 | 0 | 0.020237 | 0.020237 |  |  | 0.059967 | 0.059967 | 0.0011876 | 0.0011876 | 0 | 0 | 0.00057918 | 0.00057918 |  |  | 0.0029464 | 0.0029464 | 136 | 127.2 | NO
2013-05-20 | 0.028625 | 0.028625 | 0 | 0 | 0.037856 | 0.037856 |  |  | 0.0053057 | 0.0053057 | 0.00029561 | 0.00029561 | 0 | 0 | 0.00038166 | 0.00038166 |  |  | 5.4842e-05 | 5.4842e-05 | 297 | 275.6 | NO
2013-05-21 | 0.12663 | 0.12663 | 0 | 0 | 0.15916 | 0.15916 |  |  | 0.034645 | 0.034645 | 0.0033394 | 0.0033394 | 0 | 0 | 0.0037618 | 0.0037618 |  |  | 0.002164 | 0.002164 | 282 | 258.4 | NO
2013-05-22 | 0.094772 | 0.094772 | 0 | 0 | 0.05375 | 0.05375 |  |  | 0.2136 | 0.2136 | 0.0024741 | 0.0024741 | 0 | 0 | 0.0025789 | 0.0025789 |  |  | 0.0022008 | 0.0022008 | 319 | 285.4 | NO
2013-05-23 | 0.08361 | 0.08361 | 0 | 0 | 0.027765 | 0.027765 |  |  | 0.2449 | 0.2449 | 0.00057207 | 0.00057207 | 0 | 0 | 0.0002194 | 0.0002194 |  |  | 0.0015911 | 0.0015911 | 271 | 249.2 | NO
2013-05-24 | 0.033062 | 0.033062 | 0 | 0 | 0.009809 | 0.009809 |  |  | 0.10023 | 0.10023 | 0.00074811 | 0.00074811 | 0 | 0 | 0.00010978 | 0.00010978 |  |  | 0.0025901 | 0.0025901 | 273 | 228.6 | NO
2013-05-25 | 0.13522 | 0.13522 | 0 | 0 | 0.03399 | 0.03399 |  |  | 0.42758 | 0.42758 | 0.0016479 | 0.0016479 | 0 | 0 | 0.0001297 | 0.0001297 |  |  | 0.0060284 | 0.0060284 | 208 | 198.2 | NO
2013-05-26 | 0.014283 | 0.014283 | 0 | 0 | 0.017859 | 0.017859 |  |  | 0.0041648 | 0.0041648 | 8.2104e-05 | 8.2104e-05 | 0 | 0 | 9.7921e-05 | 9.7921e-05 |  |  | 3.7558e-05 | 3.7558e-05 | 117 | 117 | NO
2013-05-27 | 0.080198 | 0.080198 | 0 | 0 | 0.027874 | 0.027874 |  |  | 0.23151 | 0.23151 | 0.0018988 | 0.0018988 | 0 | 0 | 0.001381 | 0.001381 |  |  | 0.0034085 | 0.0034085 | 305 | 289.4 | NO
2013-05-28 | 0.18818 | 0.18818 | 0 | 0 | 0.14099 | 0.14099 |  |  | 0.32595 | 0.32595 | 0.00128 | 0.00128 | 0 | 0 | 0.0011659 | 0.0011659 |  |  | 0.0016223 | 0.0016223 | 376 | 358.8 | NO
2013-05-29 | 0.0097488 | 0.0097488 | 0 | 0 | 0.012136 | 0.012136 |  |  | 0.0029907 | 0.0029907 | 0.00010559 | 0.00010559 | 0 | 0 | 0.00013266 | 0.00013266 |  |  | 2.8908e-05 | 2.8908e-05 | 232 | 224.4 | NO
2013-05-30 | 0.070296 | 0.070296 | 0 | 0 | 0.087773 | 0.087773 |  |  | 0.020581 | 0.020581 | 0.0013413 | 0.0013413 | 0 | 0 | 0.0016954 | 0.0016954 |  |  | 0.0003344 | 0.0003344 | 244 | 224.6 | NO
2013-05-31 | 0.021212 | 0.021212 | 0 | 0 | 0.026406 | 0.026406 |  |  | 0.0064995 | 0.0064995 | 0.00024005 | 0.00024005 | 0 | 0 | 0.00029122 | 0.00029122 |  |  | 9.5425e-05 | 9.5425e-05 | 210 | 188.4 | NO
2013-06-01 | 0.043383 | 0.043383 | 0 | 0 | 0.029991 | 0.029991 |  |  | 0.082411 | 0.082411 | 0.0018286 | 0.0018286 | 0 | 0 | 0.0009854 | 0.0009854 |  |  | 0.004276 | 0.004276 | 196 | 179.6 | NO
2013-06-02 | 0.15159 | 0.15159 | 0 | 0 | 0.0034083 | 0.0034083 |  |  | 0.57988 | 0.57988 | 0.0022678 | 0.0022678 | 0 | 0 | 3.7192e-05 | 3.7192e-05 |  |  | 0.0087146 | 0.0087146 | 197 | 179 | NO
2013-06-03 | 0.14164 | 0.14164 | 0 | 0 | 0.1836 | 0.1836 |  |  | 0.022396 | 0.022396 | 0.003497 | 0.003497 | 0 | 0 | 0.0040392 | 0.0040392 |  |  | 0.0019742 | 0.0019742 | 409 | 348.6 | NO
2013-06-04 | 0.024377 | 0.024377 | 0 | 0 | 0.031389 | 0.031389 |  |  | 0.0044478 | 0.0044478 | 0.00023347 | 0.00023347 | 0 | 0 | 0.00030105 | 0.00030105 |  |  | 4.1373e-05 | 4.1373e-05 | 264 | 230.8 | NO
2013-06-05 | 0.072684 | 0.072684 | 0 | 0 | 0.093842 | 0.093842 |  |  | 0.012523 | 0.012523 | 0.00096313 | 0.00096313 | 0 | 0 | 0.0012388 | 0.0012388 |  |  | 0.0001794 | 0.0001794 | 261 | 210.2 | NO
2013-06-06 | 0.01638 | 0.01638 | 0 | 0 | 0.019968 | 0.019968 |  |  | 0.0062222 | 0.0062222 | 0.00015823 | 0.00015823 | 0 | 0 | 0.00019968 | 0.00019968 |  |  | 4.0515e-05 | 4.0515e-05 | 187 | 160.2 | NO
2013-06-07 | 0.15755 | 0.15755 | 0 | 0 | 0.20137 | 0.20137 |  |  | 0.03297 | 0.03297 | 0.0016043 | 0.0016043 | 0 | 0 | 0.0020965 | 0.0020965 |  |  | 0.00020277 | 0.00020277 | 271 | 245.4 | NO
2013-06-08 | 0.011071 | 0.011071 | 0 | 0 | 0.013764 | 0.013764 |  |  | 0.0034275 | 0.0034275 | 0.00014324 | 0.00014324 | 0 | 0 | 0.00018643 | 0.00018643 |  |  | 2.0265e-05 | 2.0265e-05 | 236 | 218.6 | NO
2013-06-09 | 0.095138 | 0.095138 | 0 | 0 | 0.0021708 | 0.0021708 |  |  | 0.36428 | 0.36428 | 0.00094598 | 0.00094598 | 0 | 0 | 1.506e-05 | 1.506e-05 |  |  | 0.0036409 | 0.0036409 | 153 | 137.2 | NO
2013-06-10 | 0.46395 | 0.46395 | 0 | 0 | 0.44434 | 0.44434 |  |  | 0.52558 | 0.52558 | 0.0061829 | 0.0061829 | 0 | 0 | 0.0049143 | 0.0049143 |  |  | 0.0099089 | 0.0099089 | 428 | 344 | NO
2013-06-11 | 0.13027 | 0.13027 | 0 | 0 | 0.15219 | 0.15219 |  |  | 0.068456 | 0.068456 | 0.0018818 | 0.0018818 | 0 | 0 | 0.0019696 | 0.0019696 |  |  | 0.0016491 | 0.0016491 | 360 | 306.2 | NO
2013-06-12 | 0.27923 | 0.27923 | 0 | 0 | 0.33904 | 0.33904 |  |  | 0.10979 | 0.10979 | 0.0035382 | 0.0035382 | 0 | 0 | 0.004379 | 0.004379 |  |  | 0.0011521 | 0.0011521 | 347 | 288.6 | NO
2013-06-13 | 0.11489 | 0.11489 | 0 | 0 | 0.10185 | 0.10185 |  |  | 0.15377 | 0.15377 | 0.0014939 | 0.0014939 | 0 | 0 | 0.0015717 | 0.0015717 |  |  | 0.0012855 | 0.0012855 | 339 | 301 | NO
2013-06-14 | 0.22528 | 0.22528 | 0 | 0 | 0.2997 | 0.2997 |  |  | 0.013051 | 0.013051 | 0.0026175 | 0.0026175 | 0 | 0 | 0.0034378 | 0.0034378 |  |  | 0.00027943 | 0.00027943 | 295 | 272 | NO
2013-06-15 | 0.11467 | 0.11467 | 0 | 0 | 0.037342 | 0.037342 |  |  | 0.33904 | 0.33904 | 0.0038328 | 0.0038328 | 0 | 0 | 0.00075989 | 0.00075989 |  |  | 0.012741 | 0.012741 | 236 | 163.2 | NO
2013-06-16 | 0.11809 | 0.11809 | 0 | 0 | 0.15861 | 0.15861 |  |  | 0.0024426 | 0.0024426 | 0.0013857 | 0.0013857 | 0 | 0 | 0.0018631 | 0.0018631 |  |  | 2.3169e-05 | 2.3169e-05 | 147 | 118.2 | NO
2013-06-17 | 0.14089 | 0.14089 | 0 | 0 | 0.14291 | 0.14291 |  |  | 0.13659 | 0.13659 | 0.0026761 | 0.0026761 | 0 | 0 | 0.0015672 | 0.0015672 |  |  | 0.005906 | 0.005906 | 341 | 279.6 | NO
2013-06-18 | 0.4291 | 0.4291 | 0 | 0 | 0.26797 | 0.26797 |  |  | 0.89896 | 0.89896 | 0.0036595 | 0.0036595 | 0 | 0 | 0.0021011 | 0.0021011 |  |  | 0.0081981 | 0.0081981 | 351 | 313.4 | NO
2013-06-19 | 0.036313 | 0.036313 | 0 | 0 | 0.018039 | 0.018039 |  |  | 0.089469 | 0.089469 | 0.00041572 | 0.00041572 | 0 | 0 | 6.7707e-05 | 6.7707e-05 |  |  | 0.0014251 | 0.0014251 | 266 | 231.8 | NO
2013-06-20 | 0.13285 | 0.13285 | 0 | 0 | 0.16509 | 0.16509 |  |  | 0.04057 | 0.04057 | 0.0016914 | 0.0016914 | 0 | 0 | 0.0021976 | 0.0021976 |  |  | 0.00024581 | 0.00024581 | 246 | 224.8 | NO
2013-06-21 | 0.42697 | 0.42697 | 0 | 0 | 0.45569 | 0.45569 |  |  | 0.34868 | 0.34868 | 0.0017962 | 0.0017962 | 0 | 0 | 0.0013404 | 0.0013404 |  |  | 0.0031318 | 0.0031318 | 256 | 218.8 | NO
2013-06-22 | 0.0054145 | 0.0054145 | 0 | 0 | 0.0041875 | 0.0041875 |  |  | 0.0092191 | 0.0092191 | 6.7617e-05 | 6.7617e-05 | 0 | 0 | 5.8182e-05 | 5.8182e-05 |  |  | 9.8494e-05 | 9.8494e-05 | 206 | 196.4 | NO
2013-06-23 | 0.15443 | 0.15443 | 0 | 0 | 0.20799 | 0.20799 |  |  | 0.0014372 | 0.0014372 | 0.0025907 | 0.0025907 | 0 | 0 | 0.0034868 | 0.0034868 |  |  | 3.1327e-05 | 3.1327e-05 | 172 | 143.2 | NO
2013-06-24 | 0.018538 | 0.018538 | 0 | 0 | 0.016629 | 0.016629 |  |  | 0.024342 | 0.024342 | 0.00023319 | 0.00023319 | 0 | 0 | 0.0001919 | 0.0001919 |  |  | 0.00035788 | 0.00035788 | 252 | 230.4 | NO
2013-06-25 | 0.0063634 | 0.0063634 | 0 | 0 | 0.0070498 | 0.0070498 |  |  | 0.0044503 | 0.0044503 | 6.4563e-05 | 6.4563e-05 | 0 | 0 | 6.5597e-05 | 6.5597e-05 |  |  | 6.2279e-05 | 6.2279e-05 | 243 | 212.8 | NO
2013-06-26 | 0.59846 | 0.59846 | 0 | 0 | 0.75941 | 0.75941 |  |  | 0.14011 | 0.14011 | 0.0004717 | 0.0004717 | 0 | 0 | 0.00037954 | 0.00037954 |  |  | 0.00074301 | 0.00074301 | 250 | 214 | NO
2013-06-27 | 0.30902 | 0.30902 | 0 | 0 | 0.24535 | 0.24535 |  |  | 0.49627 | 0.49627 | 0.0087374 | 0.0087374 | 0 | 0 | 0.009929 | 0.009929 |  |  | 0.0053906 | 0.0053906 | 369 | 301.2 | NO
2013-06-28 | 0.048314 | 0.048314 | 0 | 0 | 0.0317 | 0.0317 |  |  | 0.096829 | 0.096829 | 0.0004123 | 0.0004123 | 0 | 0 | 0.00016222 | 0.00016222 |  |  | 0.0011391 | 0.0011391 | 273 | 245.4 | NO
2013-06-29 | 0.071555 | 0.071555 | 0 | 0 | 0.091011 | 0.091011 |  |  | 0.016259 | 0.016259 | 0.0011466 | 0.0011466 | 0 | 0 | 0.0014279 | 0.0014279 |  |  | 0.00034818 | 0.00034818 | 233 | 197.2 | NO
2013-06-30 | 0.0014087 | 0.0014087 | 0 | 0 | 0.0013516 | 0.0013516 |  |  | 0.0015885 | 0.0015885 | 1.3371e-05 | 1.3371e-05 | 0 | 0 | 1.3044e-05 | 1.3044e-05 |  |  | 1.4459e-05 | 1.4459e-05 | 104 | 100.2 | NO
Contents

## 1d. STPIS MED Threshold
Energex
STPIS Data Reporting
2012-13 |  |  |  | 2007-07-01
MED Threshold |  |  |  | 2008-07-01
2009-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: MED threshold
MED threshold (timed) year ending 30 June | 3.3183
Alpha - average of Ln(Saidi) | -2.0752
Beta-standard deviation of Ln(SAIDI) | 1.3098
X Beta from the mean | 2.5
Table 2: MED calculation
Date | Unplanned SAIDI - total (after removing exluded events allowed under clause 3.3(a) of the STPIS) | Total unplanned customer minutes off supply (after removing exluded events allowed under clause 3.3(a) of the STPIS) | Ln (SAIDI)
2007-07-01 | 0.027021 | 32373.1338 | -3.6111
2007-07-02 | 0.22801 | 273176.2667 | -1.4784
2007-07-03 | 0.15477 | 185423.5615 | -1.8658
2007-07-04 | 0.035707 | 42779.9117 | -3.3324
2007-07-05 | 0.95812 | 1147893.5254 | -0.042785
2007-07-06 | 0.10426 | 124914.6562 | -2.2608
2007-07-07 | 0.33922 | 406405.8233 | -1.0811
2007-07-08 | 0.11359 | 136091.214 | -2.1751
2007-07-09 | 0.1791 | 214579.6685 | -1.7198
2007-07-10 | 0.38963 | 466801.586 | -0.94256
2007-07-11 | 0.06636 | 79503.7035 | -2.7127
2007-07-12 | 0.012333 | 14775.4642 | -4.3955
2007-07-13 | 0.1822 | 218292.3436 | -1.7026
2007-07-14 | 0.029856 | 35769.6983 | -3.5114
2007-07-15 | 0.39353 | 471481.265 | -0.93259
2007-07-16 | 0.33028 | 395696.1686 | -1.1078
2007-07-17 | 0.099556 | 119274.97 | -2.307
2007-07-18 | 0.17544 | 210186.2607 | -1.7405
2007-07-19 | 0.18878 | 226167.5684 | -1.6672
2007-07-20 | 0.22446 | 268919.1161 | -1.4941
2007-07-21 | 0.028277 | 33878.2795 | -3.5657
2007-07-22 | 0.63939 | 766034.9102 | -0.44724
2007-07-23 | 0.33934 | 406550.2573 | -1.0808
2007-07-24 | 0.11947 | 143133.1807 | -2.1247
2007-07-25 | 0.076327 | 91445.3919 | -2.5727
2007-07-26 | 0.040188 | 48148.112 | -3.2142
2007-07-27 | 0.15796 | 189249.8017 | -1.8454
2007-07-28 | 0.22997 | 275519.9191 | -1.4698
2007-07-29 | 0.062517 | 74899.3533 | -2.7723
2007-07-30 | 0.030967 | 37100.7866 | -3.4748
2007-07-31 | 0.09251 | 110834.0539 | -2.3804
2007-08-01 | 0.031728 | 37945.1738 | -3.4505
2007-08-02 | 0.1058 | 126532.5542 | -2.2462
2007-08-03 | 0.023538 | 28149.5967 | -3.7492
2007-08-04 | 0.18395 | 219994.6727 | -1.6931
2007-08-05 | 0.13267 | 158663.0145 | -2.0199
2007-08-06 | 0.031605 | 37797.3533 | -3.4545
2007-08-07 | 0.20372 | 243638.9883 | -1.591
2007-08-08 | 0.046226 | 55283.24 | -3.0742
2007-08-09 | 0.027057 | 32358.8633 | -3.6098
2007-08-10 | 0.27186 | 325131.2961 | -1.3025
2007-08-11 | 0.1039 | 124256.8701 | -2.2643
2007-08-12 | 0.037686 | 45070.6714 | -3.2785
2007-08-13 | 0.11983 | 143310.0021 | -2.1217
2007-08-14 | 0.037205 | 44494.61 | -3.2913
2007-08-15 | 0.026085 | 31195.8098 | -3.6464
2007-08-16 | 0.2008 | 240147.0683 | -1.6054
2007-08-17 | 0.026407 | 31581.6767 | -3.6341
2007-08-18 | 0.065568 | 78415.7926 | -2.7247
2007-08-19 | 0.4193 | 501458.54 | -0.86917
2007-08-20 | 0.47328 | 566013.9332 | -0.74807
2007-08-21 | 3.9505 | 4724576.6492 | 1.3738
2007-08-22 | 2.9814 | 3565547.5325 | 1.0924
2007-08-23 | 2.3511 | 2811731.7744 | 0.85486
2007-08-24 | 1.4359 | 1717255.0679 | 0.36179
2007-08-25 | 0.31329 | 374679.8375 | -1.1606
2007-08-26 | 0.10706 | 128042.79 | -2.2343
2007-08-27 | 0.28942 | 346128.15 | -1.2399
2007-08-28 | 0.027476 | 32859.46 | -3.5945
2007-08-29 | 0.21018 | 251361.0774 | -1.5598
2007-08-30 | 0.072152 | 86289.9867 | -2.629
2007-08-31 | 0.010027 | 11991.2983 | -4.6025
2007-09-01 | 0.0048906 | 5872.1147 | -5.3204
2007-09-02 | 0.19931 | 239315.7817 | -1.6129
2007-09-03 | 0.0079486 | 9543.8971 | -4.8348
2007-09-04 | 0.60181 | 722585.8667 | -0.50782
2007-09-05 | 0.35163 | 422204.1487 | -1.0452
2007-09-06 | 0.36583 | 439254.363 | -1.0056
2007-09-07 | 0.076732 | 92131.4854 | -2.5674
2007-09-08 | 0.1133 | 136041.6437 | -2.1777
2007-09-09 | 0.17082 | 205099.1215 | -1.7672
2007-09-10 | 0.0090649 | 10884.2233 | -4.7033
2007-09-11 | 0.18685 | 224350.0253 | -1.6775
2007-09-12 | 0.0052504 | 6304.1433 | -5.2495
2007-09-13 | 0.029006 | 34827.255 | -3.5403
2007-09-14 | 0.16678 | 200255.9036 | -1.7911
2007-09-15 | 0.36036 | 432681.4567 | -1.0207
2007-09-16 | 0.069508 | 83457.6 | -2.6663
2007-09-17 | 0.28125 | 337693.9628 | -1.2685
2007-09-18 | 0.050928 | 61149.6643 | -2.9773
2007-09-19 | 0.07805 | 93714.9192 | -2.5504
2007-09-20 | 0.37913 | 455221.1767 | -0.96987
2007-09-21 | 0.060181 | 72259.5156 | -2.8104
2007-09-22 | 0.31665 | 380203.4997 | -1.15
2007-09-23 | 0.30417 | 365212.7567 | -1.1902
2007-09-24 | 0.070501 | 84649.8551 | -2.6521
2007-09-25 | 0.032851 | 39444.2526 | -3.4158
2007-09-26 | 0.071009 | 85260.605 | -2.6449
2007-09-27 | 0.16584 | 199119.4667 | -1.7968
2007-09-28 | 0.17803 | 213758.485 | -1.7258
2007-09-29 | 0.025695 | 30851.3534 | -3.6615
2007-09-30 | 0.034014 | 40840.7423 | -3.381
2007-10-01 | 0.30559 | 368262.5443 | -1.1855
2007-10-02 | 0.26196 | 315679.8963 | -1.3396
2007-10-03 | 0.24238 | 292082.95 | -1.4173
2007-10-04 | 0.045732 | 55110.4512 | -3.085
2007-10-05 | 0.24937 | 300505.1683 | -1.3888
2007-10-06 | 0.099737 | 120189.5133 | -2.3052
2007-10-07 | 1.65 | 1988416.8576 | 0.5008
2007-10-08 | 1.863 | 2245041.5197 | 0.62219
2007-10-09 | 1.7105 | 2061308.73 | 0.5368
2007-10-10 | 3.7507 | 4519856.8409 | 1.3219
2007-10-11 | 0.31669 | 381631.225 | -1.1498
2007-10-12 | 1.2656 | 1525120.8583 | 0.23554
2007-10-13 | 0.18342 | 221030.55 | -1.696
2007-10-14 | 0.48824 | 588358.4549 | -0.71696
2007-10-15 | 0.39503 | 476042.8971 | -0.92878
2007-10-16 | 0.27626 | 332914.3967 | -1.2864
2007-10-17 | 0.21195 | 255409.4808 | -1.5514
2007-10-18 | 0.04903 | 59084.1033 | -3.0153
2007-10-19 | 0.26453 | 318781.6633 | -1.3298
2007-10-20 | 0.16803 | 202486.6209 | -1.7836
2007-10-21 | 0.020621 | 24849.3933 | -3.8815
2007-10-22 | 0.079498 | 95800.7236 | -2.532
2007-10-23 | 0.14133 | 170316.1617 | -1.9566
2007-10-24 | 0.024454 | 29469.2815 | -3.7109
2007-10-25 | 0.47339 | 570468.7112 | -0.74783
2007-10-26 | 0.46285 | 557768.3436 | -0.77035
2007-10-27 | 0.21209 | 255581.2609 | -1.5508
2007-10-28 | 3.3302 | 4013134.4116 | 1.203
2007-10-29 | 0.6041 | 727982.387 | -0.50402
2007-10-30 | 0.011712 | 14113.895 | -4.4471
2007-10-31 | 0.17982 | 216700.885 | -1.7158
2007-11-01 | 0.023926 | 28856.276 | -3.7328
2007-11-02 | 0.040057 | 48312.148 | -3.2174
2007-11-03 | 0.13493 | 162731.0376 | -2.003
2007-11-04 | 0.24423 | 294557.6536 | -1.4097
2007-11-05 | 0.13581 | 163795.9247 | -1.9965
2007-11-06 | 0.28192 | 340023.79 | -1.2661
2007-11-07 | 0.38964 | 469934.9718 | -0.94254
2007-11-08 | 0.09976 | 120318.7747 | -2.305
2007-11-09 | 0.26128 | 315125.2718 | -1.3422
2007-11-10 | 0.3433 | 414042.3633 | -1.0692
2007-11-11 | 0.0046932 | 5660.395 | -5.3616
2007-11-12 | 0.15494 | 186873.59 | -1.8647
2007-11-13 | 0.0991 | 119522.1485 | -2.3116
2007-11-14 | 0.037485 | 45210.4667 | -3.2838
2007-11-15 | 0.086436 | 104249.0348 | -2.4483
2007-11-16 | 0.042886 | 51724.48 | -3.1492
2007-11-17 | 0.30872 | 372344.0772 | -1.1753
2007-11-18 | 0.11285 | 136108.0807 | -2.1817
2007-11-19 | 0.083846 | 101124.42 | -2.4788
2007-11-20 | 0.0041438 | 4997.7527 | -5.4861
2007-11-21 | 0.094286 | 113715.9831 | -2.3614
2007-11-22 | 0.55559 | 670090.665 | -0.58772
2007-11-23 | 0.29057 | 350454.9058 | -1.2359
2007-11-24 | 0.18563 | 223882.784 | -1.684
2007-11-25 | 0.15021 | 181160.86 | -1.8957
2007-11-26 | 0.30966 | 373479.7754 | -1.1723
2007-11-27 | 0.14408 | 173777.8098 | -1.9374
2007-11-28 | 0.51667 | 623145.96 | -0.66035
2007-11-29 | 0.10156 | 122485.34 | -2.2871
2007-11-30 | 0.14521 | 175139.243 | -1.9295
2007-12-01 | 0.038346 | 46319.4592 | -3.2611
2007-12-02 | 0.029907 | 36126.1566 | -3.5097
2007-12-03 | 0.107 | 129251.7135 | -2.2349
2007-12-04 | 0.41642 | 503016.6472 | -0.87605
2007-12-05 | 1.1485 | 1387376.015 | 0.1385
2007-12-06 | 0.030452 | 36784.2783 | -3.4916
2007-12-07 | 0.20427 | 246744.656 | -1.5883
2007-12-08 | 0.46711 | 564237.0571 | -0.7612
2007-12-09 | 0.33334 | 402660.5167 | -1.0986
2007-12-10 | 0.18014 | 217604.8912 | -1.714
2007-12-11 | 0.092628 | 111889.4225 | -2.3792
2007-12-12 | 0.41603 | 502536.7896 | -0.87701
2007-12-13 | 0.076691 | 92638.67 | -2.568
2007-12-14 | 0.20399 | 246405.4363 | -1.5897
2007-12-15 | 0.088913 | 107401.5313 | -2.4201
2007-12-16 | 0.015021 | 18144.6199 | -4.1983
2007-12-17 | 0.24066 | 290708.6353 | -1.4244
2007-12-18 | 0.023094 | 27896.6533 | -3.7682
2007-12-19 | 0.065736 | 79405.5098 | -2.7221
2007-12-20 | 0.1245 | 150385.93 | -2.0835
2007-12-21 | 0.025905 | 31291.8933 | -3.6533
2007-12-22 | 0.41069 | 496092.9333 | -0.88991
2007-12-23 | 0.60989 | 736707.67 | -0.49448
2007-12-24 | 0.029869 | 36080.0867 | -3.5109
2007-12-25 | 1.0382 | 1254033.3233 | 0.037446
2007-12-26 | 0.20512 | 247775.661 | -1.5842
2007-12-27 | 0.27236 | 329000.5583 | -1.3006
2007-12-28 | 0.14652 | 176992.0417 | -1.9206
2007-12-29 | 0.53408 | 645141.8133 | -0.6272
2007-12-30 | 0.53167 | 642230.09 | -0.63173
2007-12-31 | 2.3851 | 2881070.4267 | 0.86924
2008-01-01 | 0.28436 | 343183.0483 | -1.2575
2008-01-02 | 0.52617 | 635015.7467 | -0.64212
2008-01-03 | 0.79786 | 962901.3433 | -0.22582
2008-01-04 | 0.42677 | 515055.6767 | -0.8515
2008-01-05 | 1.4043 | 1694771.9783 | 0.33953
2008-01-06 | 1.4882 | 1796043.5527 | 0.39757
2008-01-07 | 0.35175 | 424514.302 | -1.0448
2008-01-08 | 1.0603 | 1279660.5219 | 0.058576
2008-01-09 | 0.17052 | 205791.6767 | -1.7689
2008-01-10 | 0.11424 | 137873.0233 | -2.1694
2008-01-11 | 0.21181 | 255623.3967 | -1.5521
2008-01-12 | 0.51443 | 620840.2417 | -0.6647
2008-01-13 | 0.11726 | 141521.3433 | -2.1433
2008-01-14 | 0.14339 | 173056.6984 | -1.9422
2008-01-15 | 0.11896 | 143571.3065 | -2.1289
2008-01-16 | 0.071317 | 86069.7668 | -2.6406
2008-01-17 | 0.10816 | 130530.4171 | -2.2242
2008-01-18 | 0.10941 | 132041.7383 | -2.2127
2008-01-19 | 0.032421 | 39127.1133 | -3.429
2008-01-20 | 0.27644 | 333618.7367 | -1.2858
2008-01-21 | 0.81363 | 981928.0183 | -0.20626
2008-01-22 | 0.30633 | 369698.11 | -1.1831
2008-01-23 | 0.10459 | 126223.4592 | -2.2577
2008-01-24 | 0.16331 | 197097.1251 | -1.8121
2008-01-25 | 0.011606 | 14006.6333 | -4.4562
2008-01-26 | 0.50057 | 604114.0133 | -0.69201
2008-01-27 | 0.091034 | 109864.4567 | -2.3965
2008-01-28 | 0.04956 | 59811.8888 | -3.0046
2008-01-29 | 0.17256 | 208249.3933 | -1.757
2008-01-30 | 0.29965 | 361638.8867 | -1.2051
2008-01-31 | 0.30607 | 369387.8295 | -1.1839
2008-02-01 | 0.088046 | 106319.1983 | -2.4299
2008-02-02 | 0.20852 | 251800.4667 | -1.5677
2008-02-03 | 0.21184 | 255806.8147 | -1.5519
2008-02-04 | 0.11373 | 137328.5767 | -2.174
2008-02-05 | 0.36484 | 440561.5889 | -1.0083
2008-02-06 | 0.6188 | 747225.3092 | -0.47997
2008-02-07 | 0.43552 | 525909.1994 | -0.83121
2008-02-08 | 0.27052 | 326667.5335 | -1.3074
2008-02-09 | 0.17069 | 206109.6382 | -1.7679
2008-02-10 | 0.11012 | 132978.5867 | -2.2061
2008-02-11 | 0.2229 | 269164.468 | -1.501
2008-02-12 | 0.21316 | 257399.2883 | -1.5457
2008-02-13 | 0.22374 | 270171.77 | -1.4973
2008-02-14 | 0.022576 | 27260.97 | -3.7909
2008-02-15 | 0.31324 | 378243.5668 | -1.1608
2008-02-16 | 0.74282 | 896983.4633 | -0.2973
2008-02-17 | 0.3865 | 466711.0133 | -0.95063
2008-02-18 | 0.072083 | 87042.6831 | -2.6299
2008-02-19 | 0.0037055 | 4474.5118 | -5.5979
2008-02-20 | 0.082759 | 99934.982 | -2.4918
2008-02-21 | 0.21977 | 265382.2549 | -1.5152
2008-02-22 | 0.10192 | 123070.9774 | -2.2836
2008-02-23 | 2.0421 | 2465923.5023 | 0.71398
2008-02-24 | 0.040911 | 49401.4048 | -3.1964
2008-02-25 | 0.3274 | 395352.8697 | -1.1166
2008-02-26 | 0.82031 | 990556.7233 | -0.19807
2008-02-27 | 0.27955 | 337565.5041 | -1.2746
2008-02-28 | 0.51183 | 618053.7883 | -0.66976
2008-02-29 | 0.031493 | 38029.2402 | -3.458
2008-03-01 | 0.028254 | 34182.439 | -3.5665
2008-03-02 | 0.017103 | 20691.1567 | -4.0685
2008-03-03 | 0.37094 | 448779.8039 | -0.9917
2008-03-04 | 0.022124 | 26766.04 | -3.8111
2008-03-05 | 0.17492 | 211619.6717 | -1.7434
2008-03-06 | 0.09871 | 119422.1534 | -2.3156
2008-03-07 | 0.1446 | 174939.0337 | -1.9338
2008-03-08 | 0.2227 | 269429.3511 | -1.5019
2008-03-09 | 0.18402 | 222635.6617 | -1.6927
2008-03-10 | 0.40288 | 487421.755 | -0.90911
2008-03-11 | 0.036455 | 44104.19 | -3.3117
2008-03-12 | 0.53704 | 649726.768 | -0.62168
2008-03-13 | 0.050211 | 60746.5653 | -2.9915
2008-03-14 | 0.52719 | 637814.99 | -0.64019
2008-03-15 | 0.25468 | 308123.5567 | -1.3677
2008-03-16 | 0.053314 | 64500.908 | -2.9316
2008-03-17 | 0.26389 | 319268.24 | -1.3322
2008-03-18 | 0.065948 | 79785.7185 | -2.7189
2008-03-19 | 0.4534 | 548538.7428 | -0.79098
2008-03-20 | 0.11957 | 144662.1034 | -2.1238
2008-03-21 | 0.23195 | 280620.4767 | -1.4612
2008-03-22 | 0.052027 | 62944.321 | -2.956
2008-03-23 | 0.027753 | 33575.9667 | -3.5844
2008-03-24 | 0.0096233 | 11642.6167 | -4.6436
2008-03-25 | 0.084593 | 102343.2183 | -2.4699
2008-03-26 | 0.51885 | 627722.8833 | -0.65614
2008-03-27 | 0.12142 | 146902.702 | -2.1085
2008-03-28 | 0.6039 | 730622.4224 | -0.50434
2008-03-29 | 0.81262 | 983136.405 | -0.20749
2008-03-30 | 0.31625 | 382612.6675 | -1.1512
2008-03-31 | 0.39148 | 473620.4633 | -0.93783
2008-04-01 | 0.14903 | 180702.4767 | -1.9036
2008-04-02 | 0.2126 | 257774.5567 | -1.5483
2008-04-03 | 0.14479 | 175556.367 | -1.9325
2008-04-04 | 0.30651 | 371640.3583 | -1.1825
2008-04-05 | 0.089466 | 108476.0833 | -2.4139
2008-04-06 | 0.086769 | 105206.3304 | -2.4445
2008-04-07 | 0.056504 | 68510.76 | -2.8734
2008-04-08 | 0.046656 | 56570.1431 | -3.0649
2008-04-09 | 0.22362 | 271138.1667 | -1.4978
2008-04-10 | 0.36222 | 439187.6849 | -1.0155
2008-04-11 | 0.2517 | 305178.9005 | -1.3795
2008-04-12 | 0.22904 | 277713.0367 | -1.4738
2008-04-13 | 0.052078 | 63144.3861 | -2.955
2008-04-14 | 0.83338 | 1010458.6218 | -0.18227
2008-04-15 | 0.032887 | 39874.6078 | -3.4147
2008-04-16 | 0.44068 | 534321.5733 | -0.81943
2008-04-17 | 0.22098 | 267929.64 | -1.5097
2008-04-18 | 0.18728 | 227073.5584 | -1.6752
2008-04-19 | 0.28425 | 344651.7017 | -1.2579
2008-04-20 | 0.04183 | 50718.3167 | -3.1741
2008-04-21 | 0.086232 | 104555.18 | -2.4507
2008-04-22 | 0.090754 | 110037.6333 | -2.3996
2008-04-23 | 0.095878 | 116250.4472 | -2.3447
2008-04-24 | 0.083461 | 101195.1931 | -2.4834
2008-04-25 | 0.13624 | 165183.6067 | -1.9934
2008-04-26 | 0.060823 | 73747.5592 | -2.7998
2008-04-27 | 0.0051243 | 6213.1685 | -5.2738
2008-04-28 | 0.60538 | 734017.0778 | -0.5019
2008-04-29 | 0.2764 | 335130.4049 | -1.2859
2008-04-30 | 0.48014 | 582168.9419 | -0.73367
2008-05-01 | 0.022026 | 26749.9733 | -3.8155
2008-05-02 | 0.25624 | 311186.3537 | -1.3617
2008-05-03 | 0.018424 | 22375.5183 | -3.9941
2008-05-04 | 0.033062 | 40152.4302 | -3.4094
2008-05-05 | 0.14513 | 176257.2727 | -1.9301
2008-05-06 | 0.53638 | 651401.05 | -0.62292
2008-05-07 | 0.060044 | 72920.97 | -2.8127
2008-05-08 | 0.072095 | 87555.678 | -2.6298
2008-05-09 | 0.22659 | 275178.2733 | -1.4846
2008-05-10 | 0.047847 | 58107.2333 | -3.0398
2008-05-11 | 0.045618 | 55401.2967 | -3.0874
2008-05-12 | 0.015596 | 18940.0131 | -4.1608
2008-05-13 | 0.92871 | 1127866.1733 | -0.073963
2008-05-14 | 0.81715 | 992384.1083 | -0.20194
2008-05-15 | 0.020579 | 24991.6924 | -3.8835
2008-05-16 | 0.014553 | 17673.5433 | -4.23
2008-05-17 | 1.1681 | 1418623.2392 | 0.1554
2008-05-18 | 1.9707 | 2393347.5024 | 0.6784
2008-05-19 | 0.075695 | 91927.5667 | -2.581
2008-05-20 | 0.031729 | 38533.0467 | -3.4505
2008-05-21 | 0.015432 | 18741.6933 | -4.1713
2008-05-22 | 0.60721 | 737429.0287 | -0.49888
2008-05-23 | 0.09046 | 109859.27 | -2.4028
2008-05-24 | 0.19522 | 237080.9133 | -1.6336
2008-05-25 | 0.10064 | 122221.49 | -2.2962
2008-05-26 | 0.21114 | 256421.0412 | -1.5552
2008-05-27 | 0.25635 | 311326.5133 | -1.3612
2008-05-28 | 0.045036 | 54694.4355 | -3.1003
2008-05-29 | 0.58909 | 715421.846 | -0.52917
2008-05-30 | 1.1431 | 1388213.9068 | 0.13373
2008-05-31 | 0.39637 | 481365.8258 | -0.92542
2008-06-01 | 0.19658 | 239548.5592 | -1.6267
2008-06-02 | 0.41818 | 509586.1567 | -0.87184
2008-06-03 | 0.61494 | 749352.2717 | -0.48623
2008-06-04 | 0.4635 | 564810.0767 | -0.76895
2008-06-05 | 0.057826 | 70465.11 | -2.8503
2008-06-06 | 0.041706 | 50821.9967 | -3.1771
2008-06-07 | 0.06627 | 80755.3717 | -2.714
2008-06-08 | 0.065308 | 79582.76 | -2.7286
2008-06-09 | 0.10162 | 123832.9038 | -2.2865
2008-06-10 | 0.013723 | 16722.085 | -4.2887
2008-06-11 | 0.069906 | 85186.1967 | -2.6606
2008-06-12 | 0.2253 | 274541.5 | -1.4903
2008-06-13 | 0.13864 | 168949.175 | -1.9758
2008-06-14 | 0.22091 | 269198.9783 | -1.51
2008-06-15 | 0.077867 | 94887.6433 | -2.5527
2008-06-16 | 0.042491 | 51778.5098 | -3.1585
2008-06-17 | 0.03852 | 46939.9691 | -3.2566
2008-06-18 | 0.12642 | 154049.6283 | -2.0682
2008-06-19 | 0.14038 | 171060.6233 | -1.9634
2008-06-20 | 0.22069 | 268929.4833 | -1.511
2008-06-21 | 0.061789 | 75295.364 | -2.784
2008-06-22 | 0.067844 | 82673.5649 | -2.6905
2008-06-23 | 0.12234 | 149075.4567 | -2.101
2008-06-24 | 0.0076282 | 9295.5244 | -4.8759
2008-06-25 | 0.042083 | 51281.094 | -3.1681
2008-06-26 | 0.034028 | 41466.0391 | -3.3806
2008-06-27 | 0.16349 | 199226.3436 | -1.811
2008-06-28 | 0.11871 | 144652.0733 | -2.1311
2008-06-29 | 0.011774 | 14347.0833 | -4.4419
2008-06-30 | 0.12479 | 152071.8595 | -2.0811
2008-07-01 | 0.18795 | 229707.8467 | -1.6716
2008-07-02 | 0.16709 | 204213.8363 | -1.7892
2008-07-03 | 0.17515 | 214065.9404 | -1.7421
2008-07-04 | 0.064286 | 78570.6567 | -2.7444
2008-07-05 | 0.31313 | 382709.8733 | -1.1611
2008-07-06 | 0.22547 | 275574.3095 | -1.4896
2008-07-07 | 0.02845 | 34771.597 | -3.5596
2008-07-08 | 0.09072 | 110878.83 | -2.4
2008-07-09 | 0.64862 | 792747.2938 | -0.43291
2008-07-10 | 0.3626 | 443170.7925 | -1.0145
2008-07-11 | 0.20583 | 251565.076 | -1.5807
2008-07-12 | 0.16222 | 198261.337 | -1.8188
2008-07-13 | 0.0748 | 91421.0773 | -2.5929
2008-07-14 | 0.26976 | 329704.1653 | -1.3102
2008-07-15 | 0.060413 | 73836.9988 | -2.8066
2008-07-16 | 0.11514 | 140729.2883 | -2.1616
2008-07-17 | 0.2992 | 365678.57 | -1.2067
2008-07-18 | 0.11486 | 140382.68 | -2.164
2008-07-19 | 0.18104 | 221262.2833 | -1.7091
2008-07-20 | 0.1492 | 182352.7267 | -1.9025
2008-07-21 | 0.2226 | 272057.3367 | -1.5024
2008-07-22 | 0.11213 | 137042.3399 | -2.1881
2008-07-23 | 0.16004 | 195599.22 | -1.8323
2008-07-24 | 0.057727 | 70554.4685 | -2.852
2008-07-25 | 0.10078 | 123171.3438 | -2.2948
2008-07-26 | 0.37089 | 453309.5977 | -0.99184
2008-07-27 | 0.48035 | 587091.7363 | -0.73323
2008-07-28 | 0.12771 | 156088.8889 | -2.058
2008-07-29 | 0.031718 | 38765.6758 | -3.4509
2008-07-30 | 0.041822 | 51115.5767 | -3.1743
2008-07-31 | 0.090632 | 110770.7283 | -2.4009
2008-08-01 | 0.11174 | 137313.9536 | -2.1915
2008-08-02 | 0.44312 | 544519.562 | -0.81391
2008-08-03 | 0.16648 | 204578.6633 | -1.7929
2008-08-04 | 0.29244 | 359356.7567 | -1.2295
2008-08-05 | 0.036367 | 44688.8333 | -3.3141
2008-08-06 | 0.091934 | 112970.5653 | -2.3867
2008-08-07 | 0.066206 | 81355.2933 | -2.715
2008-08-08 | 0.055994 | 68807.085 | -2.8825
2008-08-09 | 0.094065 | 115589.2033 | -2.3638
2008-08-10 | 0.85495 | 1050580.45 | -0.15671
2008-08-11 | 0.20253 | 248878.0809 | -1.5968
2008-08-12 | 0.18292 | 224771.1072 | -1.6987
2008-08-13 | 1.4911 | 1832266.6599 | 0.3995
2008-08-14 | 0.32029 | 393573.7067 | -1.1385
2008-08-15 | 0.059511 | 73128.2829 | -2.8216
2008-08-16 | 0.46001 | 565275.3658 | -0.7765
2008-08-17 | 0.028734 | 35309.1646 | -3.5497
2008-08-18 | 0.13774 | 169262.7258 | -1.9824
2008-08-19 | 0.047526 | 58400.8467 | -3.0465
2008-08-20 | 0.073623 | 90469.75 | -2.6088
2008-08-21 | 0.19343 | 237692.5861 | -1.6428
2008-08-22 | 0.062366 | 76637.0341 | -2.7747
2008-08-23 | 0.26677 | 327808.675 | -1.3214
2008-08-24 | 0.10295 | 126511.2283 | -2.2735
2008-08-25 | 0.1074 | 131971.3116 | -2.2312
2008-08-26 | 0.090349 | 111022.3575 | -2.4041
2008-08-27 | 0.087851 | 107953.39 | -2.4321
2008-08-28 | 0.031333 | 38502.5833 | -3.4631
2008-08-29 | 0.32301 | 396926.3583 | -1.1301
2008-08-30 | 0.059094 | 72616.06 | -2.8286
2008-08-31 | 0.79054 | 971430.0757 | -0.23504
2008-09-01 | 0.014436 | 17789.0267 | -4.238
2008-09-02 | 0.024302 | 29947.0161 | -3.7172
2008-09-03 | 0.22713 | 279893.23 | -1.4822
2008-09-04 | 0.19746 | 243322.5928 | -1.6222
2008-09-05 | 0.068104 | 83924.0431 | -2.6867
2008-09-06 | 0.36743 | 452777.1183 | -1.0012
2008-09-07 | 0.087057 | 107279.4067 | -2.4412
2008-09-08 | 0.23512 | 289732.5617 | -1.4477
2008-09-09 | 0.0079384 | 9782.3836 | -4.836
2008-09-10 | 0.054588 | 67268.6167 | -2.9079
2008-09-11 | 0.15623 | 192518.3689 | -1.8564
2008-09-12 | 0.025445 | 31355.46 | -3.6712
2008-09-13 | 0.20875 | 257238.8328 | -1.5666
2008-09-14 | 0.14832 | 182774.92 | -1.9084
2008-09-15 | 0.099493 | 122603.8817 | -2.3077
2008-09-16 | 0.086681 | 106815.735 | -2.4455
2008-09-17 | 0.077504 | 95507.73 | -2.5574
2008-09-18 | 0.006813 | 8395.5253 | -4.9889
2008-09-19 | 0.047428 | 58445.5636 | -3.0485
2008-09-20 | 1.0993 | 1354708.8628 | 0.094714
2008-09-21 | 0.76486 | 942522.6305 | -0.26807
2008-09-22 | 0.13397 | 165090.7383 | -2.0101
2008-09-23 | 0.080224 | 98859.49 | -2.5229
2008-09-24 | 0.184 | 226743.7377 | -1.6928
2008-09-25 | 0.21577 | 265896.7534 | -1.5335
2008-09-26 | 0.65738 | 810076.5833 | -0.4195
2008-09-27 | 0.033334 | 41077.6467 | -3.4012
2008-09-28 | 0.052225 | 64356.2067 | -2.9522
2008-09-29 | 0.19717 | 242966.6933 | -1.6237
2008-09-30 | 0.010595 | 13056.1383 | -4.5474
2008-10-01 | 0.0059781 | 7405.6233 | -5.1196
2008-10-02 | 0.29926 | 370715.8067 | -1.2065
2008-10-03 | 0.034672 | 42951.5821 | -3.3618
2008-10-04 | 0.11693 | 144848.8133 | -2.1462
2008-10-05 | 0.34009 | 421299.0702 | -1.0785
2008-10-06 | 0.090346 | 111919.585 | -2.4041
2008-10-07 | 0.10013 | 124038.895 | -2.3013
2008-10-08 | 0.24194 | 299709.405 | -1.4191
2008-10-09 | 0.068274 | 84576.4067 | -2.6842
2008-10-10 | 0.065228 | 80803.3332 | -2.7299
2008-10-11 | 0.1269 | 157196.0833 | -2.0644
2008-10-12 | 0.15358 | 190257.4867 | -1.8735
2008-10-13 | 0.11101 | 137514.555 | -2.1982
2008-10-14 | 0.041914 | 51922.2048 | -3.1721
2008-10-15 | 2.2041 | 2730460.9543 | 0.79034
2008-10-16 | 0.19038 | 235834.4158 | -1.6588
2008-10-17 | 0.22007 | 272613.825 | -1.5138
2008-10-18 | 0.0092038 | 11401.5033 | -4.6881
2008-10-19 | 0.29587 | 366523.94 | -1.2178
2008-10-20 | 0.0095368 | 11814.0983 | -4.6526
2008-10-21 | 1.0401 | 1288420.5495 | 0.039286
2008-10-22 | 0.029411 | 36433.8325 | -3.5264
2008-10-23 | 0.15244 | 188842.5633 | -1.881
2008-10-24 | 0.1578 | 195480.5167 | -1.8464
2008-10-25 | 0.087002 | 107776.5508 | -2.4418
2008-10-26 | 0.30335 | 375785.1585 | -1.1929
2008-10-27 | 0.059769 | 74040.4617 | -2.8173
2008-10-28 | 0.27533 | 341068.5978 | -1.2898
2008-10-29 | 0.094667 | 117272.0455 | -2.3574
2008-10-30 | 0.17441 | 216057 | -1.7463
2008-10-31 | 0.015662 | 19402.4717 | -4.1565
2008-11-01 | 0.092614 | 115112.128 | -2.3793
2008-11-02 | 0.0091009 | 11311.7433 | -4.6994
2008-11-03 | 0.15359 | 190904.3367 | -1.8734
2008-11-04 | 0.62689 | 779171.8033 | -0.46699
2008-11-05 | 0.39514 | 491134.1454 | -0.9285
2008-11-06 | 0.1607 | 199738.2833 | -1.8282
2008-11-07 | 0.12121 | 150655.8886 | -2.1102
2008-11-08 | 0.61912 | 769519.4461 | -0.47945
2008-11-09 | 0.013699 | 17026.9883 | -4.2904
2008-11-10 | 0.26256 | 326337.8025 | -1.3373
2008-11-11 | 0.22693 | 282052.9204 | -1.4831
2008-11-12 | 0.24746 | 307575.48 | -1.3965
2008-11-13 | 0.014981 | 18619.9125 | -4.201
2008-11-14 | 0.058801 | 73085.3003 | -2.8336
2008-11-15 | 0.035968 | 44704.8496 | -3.3251
2008-11-16 | 85.182 | 105874618.9873 | 4.4448
2008-11-17 | 1.7483 | 2172956.0674 | 0.55862
2008-11-18 | 0.26439 | 328612.6795 | -1.3303
2008-11-19 | 0.70722 | 879014.24 | -0.34642
2008-11-20 | 11.153 | 13862290.6362 | 2.4117
2008-11-21 | 0.48952 | 608432.4356 | -0.71433
2008-11-22 | 0.42404 | 527047.002 | -0.85793
2008-11-23 | 1.1153 | 1386265.45 | 0.10915
2008-11-24 | 0.14612 | 181621.3904 | -1.9233
2008-11-25 | 0.29808 | 370490.9868 | -1.2104
2008-11-26 | 0.11706 | 145501.0817 | -2.145
2008-11-27 | 0.16534 | 205502.7338 | -1.7998
2008-11-28 | 0.56032 | 696431.8388 | -0.57925
2008-11-29 | 1.7888 | 2223378.7036 | 0.58156
2008-11-30 | 0.30508 | 379184.746 | -1.1872
2008-12-01 | 0.35008 | 435932.0567 | -1.0496
2008-12-02 | 0.23116 | 287847.9383 | -1.4646
2008-12-03 | 4.4234 | 5508236.7677 | 1.4869
2008-12-04 | 1.0745 | 1338001.4279 | 0.07185
2008-12-05 | 0.11912 | 148336.7995 | -2.1276
2008-12-06 | 1.0034 | 1249529.8364 | 0.0034404
2008-12-07 | 0.96085 | 1196485.64 | -0.039938
2008-12-08 | 0.085531 | 106505.9223 | -2.4589
2008-12-09 | 0.068066 | 84757.9167 | -2.6873
2008-12-10 | 0.61556 | 766522.3866 | -0.48522
2008-12-11 | 1.301 | 1620110.2897 | 0.26317
2008-12-12 | 0.11888 | 148038.9568 | -2.1296
2008-12-13 | 0.13278 | 165345.2856 | -2.019
2008-12-14 | 0.89035 | 1108702.4824 | -0.11614
2008-12-15 | 0.336 | 418403.4697 | -1.0906
2008-12-16 | 0.19956 | 248504.1027 | -1.6116
2008-12-17 | 0.35461 | 441570.7034 | -1.0367
2008-12-18 | 0.24369 | 303446.1382 | -1.4119
2008-12-19 | 0.66973 | 833967.7023 | -0.40089
2008-12-20 | 0.26007 | 323845.185 | -1.3468
2008-12-21 | 0.061794 | 76948.085 | -2.784
2008-12-22 | 0.11199 | 139458.5586 | -2.1893
2008-12-23 | 0.39421 | 490889.51 | -0.93086
2008-12-24 | 0.33639 | 418888.8592 | -1.0895
2008-12-25 | 0.17988 | 223993.0315 | -1.7155
2008-12-26 | 0.022732 | 28306.46 | -3.784
2008-12-27 | 0.055493 | 69102.3617 | -2.8915
2008-12-28 | 0.47146 | 587081.3628 | -0.75192
2008-12-29 | 4.4286 | 5514634.5896 | 1.4881
2008-12-30 | 0.54277 | 675872.8719 | -0.61108
2008-12-31 | 0.23079 | 287383.9899 | -1.4663
2009-01-01 | 1.334 | 1664056.9915 | 0.28815
2009-01-02 | 0.25305 | 315670.4553 | -1.3742
2009-01-03 | 0.33304 | 415451.4544 | -1.0995
2009-01-04 | 0.056194 | 70099.4717 | -2.8789
2009-01-05 | 0.16764 | 209126.83 | -1.7859
2009-01-06 | 0.17286 | 215637.236 | -1.7553
2009-01-07 | 0.14548 | 181474.7103 | -1.9277
2009-01-08 | 0.089066 | 111106.0841 | -2.4184
2009-01-09 | 0.35816 | 446787.1881 | -1.0268
2009-01-10 | 0.14786 | 184449.9851 | -1.9115
2009-01-11 | 0.022011 | 27457.71 | -3.8162
2009-01-12 | 0.023361 | 29142.0717 | -3.7567
2009-01-13 | 0.45003 | 561393.3253 | -0.79844
2009-01-14 | 0.39614 | 494165.5418 | -0.92599
2009-01-15 | 0.18744 | 233817.875 | -1.6743
2009-01-16 | 0.1991 | 248374.1543 | -1.6139
2009-01-17 | 0.448 | 558859.165 | -0.80297
2009-01-18 | 0.070716 | 88215.8333 | -2.6491
2009-01-19 | 0.42499 | 530160.3083 | -0.85568
2009-01-20 | 0.15773 | 196758.4033 | -1.8469
2009-01-21 | 0.57681 | 719545.2682 | -0.55024
2009-01-22 | 1.1783 | 1469920.7687 | 0.1641
2009-01-23 | 2.4366 | 3039615.3563 | 0.89062
2009-01-24 | 0.12689 | 158284.8564 | -2.0645
2009-01-25 | 0.84514 | 1054272.407 | -0.16826
2009-01-26 | 0.25382 | 316634.24 | -1.3711
2009-01-27 | 0.069663 | 86902.0234 | -2.6641
2009-01-28 | 0.32164 | 401226.6032 | -1.1343
2009-01-29 | 0.018458 | 23025.2772 | -3.9923
2009-01-30 | 0.015636 | 19504.7658 | -4.1582
2009-01-31 | 0.064163 | 80040.324 | -2.7463
2009-02-01 | 0.083382 | 104221.47 | -2.4843
2009-02-02 | 0.12319 | 153982.0625 | -2.094
2009-02-03 | 0.1481 | 185110.885 | -1.9099
2009-02-04 | 0.090408 | 113003.3066 | -2.4034
2009-02-05 | 0.02536 | 31698.1867 | -3.6746
2009-02-06 | 0.029208 | 36507.7117 | -3.5333
2009-02-07 | 0.070583 | 88223.2267 | -2.651
2009-02-08 | 0.34331 | 429110.945 | -1.0691
2009-02-09 | 0.62905 | 786266.2095 | -0.46355
2009-02-10 | 4.7996 | 5999213.0826 | 1.5685
2009-02-11 | 0.048808 | 61007.1 | -3.0199
2009-02-12 | 0.36281 | 453492.3817 | -1.0139
2009-02-13 | 0.15367 | 192081.22 | -1.8729
2009-02-14 | 0.27147 | 339312.7017 | -1.3039
2009-02-15 | 0.30081 | 375992.345 | -1.2013
2009-02-16 | 0.23505 | 293797.617 | -1.448
2009-02-17 | 0.38342 | 479244.336 | -0.95863
2009-02-18 | 0.30225 | 377787.3722 | -1.1965
2009-02-19 | 0.18195 | 227419.3017 | -1.704
2009-02-20 | 0.73366 | 917020.8433 | -0.30971
2009-02-21 | 0.18788 | 234840.24 | -1.6719
2009-02-22 | 0.21549 | 269349.7217 | -1.5348
2009-02-23 | 0.38184 | 477270.4415 | -0.96276
2009-02-24 | 0.41598 | 519944.9733 | -0.87712
2009-02-25 | 0.21758 | 271960.6032 | -1.5252
2009-02-26 | 0.24922 | 311510.3101 | -1.3894
2009-02-27 | 0.039398 | 49244.6091 | -3.234
2009-02-28 | 0.10477 | 130959.3039 | -2.256
2009-03-01 | 0.78812 | 986597.0804 | -0.23811
2009-03-02 | 0.24966 | 312537.585 | -1.3876
2009-03-03 | 0.023277 | 29138.6932 | -3.7603
2009-03-04 | 0.32387 | 405432.6033 | -1.1274
2009-03-05 | 0.2947 | 368914.8683 | -1.2218
2009-03-06 | 0.13577 | 169964.7067 | -1.9968
2009-03-07 | 0.26822 | 335767.8371 | -1.316
2009-03-08 | 0.044019 | 55104.6719 | -3.1231
2009-03-09 | 0.12148 | 152078.87 | -2.108
2009-03-10 | 0.7639 | 956280.4165 | -0.26932
2009-03-11 | 0.52729 | 660079.5167 | -0.64001
2009-03-12 | 0.21111 | 264276.2167 | -1.5554
2009-03-13 | 0.28293 | 354187.7093 | -1.2625
2009-03-14 | 0.039073 | 48913.2968 | -3.2423
2009-03-15 | 0.13555 | 169682.0635 | -1.9984
2009-03-16 | 1.0183 | 1274730.0539 | 0.01812
2009-03-17 | 0.32105 | 401904.7649 | -1.1362
2009-03-18 | 0.018316 | 22928.215 | -4
2009-03-19 | 0.041972 | 52542.05 | -3.1708
2009-03-20 | 0.37626 | 471019.2383 | -0.97747
2009-03-21 | 0.014731 | 18441.2732 | -4.2178
2009-03-22 | 0.11872 | 148615.4734 | -2.131
2009-03-23 | 0.19663 | 246149.9041 | -1.6264
2009-03-24 | 0.083994 | 105147.3483 | -2.477
2009-03-25 | 0.12766 | 159813.3237 | -2.0584
2009-03-26 | 0.079621 | 99673.1381 | -2.5305
2009-03-27 | 0.025595 | 32041.3685 | -3.6653
2009-03-28 | 0.19858 | 248593.41 | -1.6166
2009-03-29 | 0.28308 | 354369.4295 | -1.262
2009-03-30 | 0.87742 | 1098389.2567 | -0.13077
2009-03-31 | 0.23701 | 296696.49 | -1.4397
2009-04-01 | 0.10703 | 134166.2765 | -2.2347
2009-04-02 | 3.2411 | 4063024.4507 | 1.1759
2009-04-03 | 0.46933 | 588355.1483 | -0.75644
2009-04-04 | 0.33075 | 414629.913 | -1.1064
2009-04-05 | 0.013778 | 17272.425 | -4.2847
2009-04-06 | 0.15007 | 188124.4483 | -1.8967
2009-04-07 | 0.2235 | 280184.7633 | -1.4983
2009-04-08 | 0.16631 | 208481.5935 | -1.7939
2009-04-09 | 0.01995 | 25009.1859 | -3.9145
2009-04-10 | 0.051187 | 64167.7017 | -2.9723
2009-04-11 | 0.0032297 | 4048.78 | -5.7354
2009-04-12 | 0.081259 | 101866.15 | -2.5101
2009-04-13 | 0.71695 | 898763.2246 | -0.33275
2009-04-14 | 0.35381 | 443538.8168 | -1.039
2009-04-15 | 0.37287 | 467430.5726 | -0.98652
2009-04-16 | 0.17224 | 215915.1477 | -1.7589
2009-04-17 | 0.32428 | 406512.4133 | -1.1262
2009-04-18 | 0.054335 | 68113.935 | -2.9126
2009-04-19 | 0.13768 | 172596.1586 | -1.9828
2009-04-20 | 0.20365 | 255296.0062 | -1.5913
2009-04-21 | 0.036748 | 46067.525 | -3.3037
2009-04-22 | 0.074778 | 93741.3429 | -2.5932
2009-04-23 | 0.11455 | 143604.1567 | -2.1667
2009-04-24 | 0.26062 | 326716.8716 | -1.3447
2009-04-25 | 0.087074 | 109155.7527 | -2.441
2009-04-26 | 0.090449 | 113386.5783 | -2.403
2009-04-27 | 0.013171 | 16510.8433 | -4.3298
2009-04-28 | 0.020426 | 25605.4358 | -3.891
2009-04-29 | 0.023402 | 29336.8467 | -3.7549
2009-04-30 | 0.071841 | 90059.355 | -2.6333
2009-05-01 | 0.22283 | 279757.1727 | -1.5013
2009-05-02 | 0.051674 | 64875.23 | -2.9628
2009-05-03 | 0.012608 | 15828.516 | -4.3735
2009-05-04 | 0.0067856 | 8519.1952 | -4.9929
2009-05-05 | 0.42584 | 534630.16 | -0.8537
2009-05-06 | 0.12554 | 157617.34 | -2.0751
2009-05-07 | 0.24382 | 306112.9067 | -1.4113
2009-05-08 | 0.074326 | 93314.6662 | -2.5993
2009-05-09 | 0.008173 | 10261.0767 | -4.8069
2009-05-10 | 0.0158 | 19835.977 | -4.1478
2009-05-11 | 0.0171 | 21469.1144 | -4.0687
2009-05-12 | 0.023471 | 29467.7983 | -3.752
2009-05-13 | 0.033668 | 42269.3733 | -3.3912
2009-05-14 | 0.026171 | 32857.6767 | -3.6431
2009-05-15 | 0.026711 | 33535.4233 | -3.6227
2009-05-16 | 0.089234 | 112030.9804 | -2.4165
2009-05-17 | 0.02155 | 27055.4367 | -3.8374
2009-05-18 | 0.25984 | 326219.0476 | -1.3477
2009-05-19 | 0.95687 | 1201333.7774 | -0.044084
2009-05-20 | 14.3492 | 18015133.0339 | 2.6637
2009-05-21 | 0.4041 | 507335.7824 | -0.9061
2009-05-22 | 0.14553 | 182711.8177 | -1.9274
2009-05-23 | 0.55141 | 692288.6033 | -0.59527
2009-05-24 | 0.35365 | 443994.8985 | -1.0395
2009-05-25 | 0.083664 | 105038.1433 | -2.4809
2009-05-26 | 0.062269 | 78177.7933 | -2.7763
2009-05-27 | 0.092095 | 115622.9925 | -2.3849
2009-05-28 | 0.2125 | 266792.3667 | -1.5488
2009-05-29 | 0.12551 | 157569.7233 | -2.0754
2009-05-30 | 0.004498 | 5647.1967 | -5.4041
2009-05-31 | 0.11655 | 146330.0413 | -2.1494
2009-06-01 | 0.066733 | 83855.5103 | -2.707
2009-06-02 | 0.28344 | 356160.4867 | -1.2608
2009-06-03 | 0.1315 | 165242.9767 | -2.0287
2009-06-04 | 0.10115 | 127097.6017 | -2.2912
2009-06-05 | 0.071374 | 89687.2467 | -2.6398
2009-06-06 | 0.069093 | 86820.7458 | -2.6723
2009-06-07 | 0.13818 | 173634.4302 | -1.9792
2009-06-08 | 0.024704 | 31041.84 | -3.7008
2009-06-09 | 0.0528 | 66347.01 | -2.9412
2009-06-10 | 0.25777 | 323904.94 | -1.3557
2009-06-11 | 0.20365 | 255898.82 | -1.5914
2009-06-12 | 0.42888 | 538917.8333 | -0.84658
2009-06-13 | 0.049475 | 62168.4458 | -3.0063
2009-06-14 | 0.11631 | 146147.353 | -2.1515
2009-06-15 | 0.21113 | 265300.6577 | -1.5553
2009-06-16 | 0.03394 | 42648.42 | -3.3832
2009-06-17 | 0.053801 | 67604.5433 | -2.9225
2009-06-18 | 0.036695 | 46110.1196 | -3.3051
2009-06-19 | 0.10342 | 129951.0196 | -2.269
2009-06-20 | 0.076686 | 96361.5873 | -2.568
2009-06-21 | 0.33615 | 422394.4433 | -1.0902
2009-06-22 | 0.40466 | 508488.645 | -0.9047
2009-06-23 | 0.031315 | 39350.1933 | -3.4636
2009-06-24 | 0.061716 | 77550.7067 | -2.7852
2009-06-25 | 0.087321 | 109725.5583 | -2.4382
2009-06-26 | 0.056693 | 71238.7483 | -2.8701
2009-06-27 | 0.011504 | 14455.8223 | -4.465
2009-06-28 | 0.14828 | 186324.9595 | -1.9087
2009-06-29 | 0.020467 | 25718.1797 | -3.8889
2009-06-30 | 0.15957 | 200509.7733 | -1.8353
2009-07-01 | 0.119 | 149747.7033 | -2.1286
2009-07-02 | 0.072358 | 91052.798 | -2.6261
2009-07-03 | 0.47373 | 596121.1867 | -0.74713
2009-07-04 | 0.12319 | 155014.469 | -2.0941
2009-07-05 | 0.056839 | 71524.3017 | -2.8675
2009-07-06 | 0.13472 | 169532.4035 | -2.0045
2009-07-07 | 0.19906 | 250487.29 | -1.6142
2009-07-08 | 0.13493 | 169791.1233 | -2.003
2009-07-09 | 0.15096 | 189961.4867 | -1.8907
2009-07-10 | 0.061066 | 76842.955 | -2.7958
2009-07-11 | 0.014742 | 18550.6911 | -4.2171
2009-07-12 | 0.030317 | 38150.3469 | -3.496
2009-07-13 | 0.069864 | 87914.618 | -2.6612
2009-07-14 | 0.030634 | 38548.8183 | -3.4856
2009-07-15 | 0.048138 | 60575.7733 | -3.0337
2009-07-16 | 0.79771 | 1003809.0227 | -0.22601
2009-07-17 | 0.20064 | 252482.3117 | -1.6062
2009-07-18 | 0.033942 | 42710.9933 | -3.3831
2009-07-19 | 0.016969 | 21353.6931 | -4.0763
2009-07-20 | 0.089936 | 113172.5652 | -2.4087
2009-07-21 | 0.038059 | 47892.3 | -3.2686
2009-07-22 | 0.015638 | 19678.0516 | -4.1581
2009-07-23 | 1.3946 | 1754920.2283 | 0.33261
2009-07-24 | 0.038645 | 48629.5942 | -3.2533
2009-07-25 | 0.060611 | 76270.3333 | -2.8033
2009-07-26 | 0.14548 | 183062.5967 | -1.9277
2009-07-27 | 0.025984 | 32697.2916 | -3.6503
2009-07-28 | 0.054773 | 68924.8717 | -2.9046
2009-07-29 | 0.03853 | 48485.0133 | -3.2563
2009-07-30 | 0.032685 | 41129.49 | -3.4208
2009-07-31 | 0.11296 | 142145.64 | -2.1807
2009-08-01 | 0.047869 | 60344.82 | -3.0393
2009-08-02 | 0.097569 | 122998.3233 | -2.3272
2009-08-03 | 0.072591 | 91510.3933 | -2.6229
2009-08-04 | 0.3496 | 440716.76 | -1.051
2009-08-05 | 0.0036418 | 4590.93 | -5.6153
2009-08-06 | 0.0099651 | 12562.2467 | -4.6087
2009-08-07 | 0.08044 | 101404.7 | -2.5202
2009-08-08 | 0.021072 | 26564.3633 | -3.8598
2009-08-09 | 0.0088826 | 11197.6667 | -4.7237
2009-08-10 | 0.011735 | 14793.92 | -4.4451
2009-08-11 | 0.020826 | 26253.2333 | -3.8716
2009-08-12 | 0.29948 | 377531.5817 | -1.2057
2009-08-13 | 0.36055 | 454519.9899 | -1.0201
2009-08-14 | 0.37528 | 473088.122 | -0.98008
2009-08-15 | 0.078137 | 98501.4883 | -2.5493
2009-08-16 | 0.31672 | 399265.9433 | -1.1497
2009-08-17 | 0.069724 | 87896.3233 | -2.6632
2009-08-18 | 0.071319 | 89907.19 | -2.6406
2009-08-19 | 0.029137 | 36731.205 | -3.5357
2009-08-20 | 0.26218 | 330511.5 | -1.3387
2009-08-21 | 0.12814 | 161541.6965 | -2.0546
2009-08-22 | 0.086327 | 108826.3517 | -2.4496
2009-08-23 | 0.04169 | 52555.39 | -3.1775
2009-08-24 | 0.059153 | 74569.58 | -2.8276
2009-08-25 | 0.17261 | 217594.54 | -1.7567
2009-08-26 | 0.358 | 451306.585 | -1.0272
2009-08-27 | 0.1938 | 244311.0808 | -1.6409
2009-08-28 | 0.12451 | 156957.7559 | -2.0834
2009-08-29 | 0.012219 | 15404.0493 | -4.4047
2009-08-30 | 0.20623 | 259974.8367 | -1.5788
2009-08-31 | 0.63678 | 802738.6419 | -0.45134
2009-09-01 | 0.16281 | 205551.4096 | -1.8152
2009-09-02 | 0.068234 | 86149.3017 | -2.6848
2009-09-03 | 0.12428 | 156913.3618 | -2.0852
2009-09-04 | 0.0092139 | 11633.0667 | -4.687
2009-09-05 | 1.2545 | 1583903.1883 | 0.22675
2009-09-06 | 0.43747 | 552336.3572 | -0.82674
2009-09-07 | 0.78428 | 990194.72 | -0.24299
2009-09-08 | 0.80008 | 1010151.4023 | -0.22304
2009-09-09 | 0.080508 | 101646.47 | -2.5194
2009-09-10 | 0.03903 | 49277.5333 | -3.2434
2009-09-11 | 0.014483 | 18285.9333 | -4.2348
2009-09-12 | 0.14219 | 179524.9933 | -1.9506
2009-09-13 | 0.25217 | 318378.0467 | -1.3777
2009-09-14 | 0.034117 | 43074.6908 | -3.378
2009-09-15 | 0.21185 | 267472.5633 | -1.5519
2009-09-16 | 0.28364 | 358110.7967 | -1.2601
2009-09-17 | 0.22568 | 284933.4633 | -1.4886
2009-09-18 | 0.12456 | 157268.8493 | -2.0829
2009-09-19 | 0.088829 | 112151.57 | -2.421
2009-09-20 | 0.036121 | 45604.8317 | -3.3209
2009-09-21 | 0.069492 | 87737.1869 | -2.6666
2009-09-22 | 0.18484 | 233365.3316 | -1.6883
2009-09-23 | 0.59593 | 752393.2605 | -0.51764
2009-09-24 | 0.0063832 | 8059.2067 | -5.0541
2009-09-25 | 0.19435 | 245374.26 | -1.6381
2009-09-26 | 0.22799 | 287855.5133 | -1.4784
2009-09-27 | 0.12269 | 154906.5644 | -2.0981
2009-09-28 | 0.20925 | 264191.1487 | -1.5642
2009-09-29 | 0.2339 | 295311.62 | -1.4529
2009-09-30 | 0.020474 | 25849.9137 | -3.8886
2009-10-01 | 0.029838 | 37724.93 | -3.512
2009-10-02 | 0.025121 | 31760.48 | -3.6841
2009-10-03 | 0.50296 | 635899.9966 | -0.68724
2009-10-04 | 0.099632 | 125966.1333 | -2.3063
2009-10-05 | 0.16657 | 210595.5395 | -1.7923
2009-10-06 | 0.35645 | 450665.9367 | -1.0316
2009-10-07 | 0.16742 | 211665.46 | -1.7873
2009-10-08 | 0.072171 | 91246.3367 | -2.6287
2009-10-09 | 0.010742 | 13581.2267 | -4.5336
2009-10-10 | 0.092248 | 116630.3033 | -2.3833
2009-10-11 | 0.1413 | 178652.5359 | -1.9568
2009-10-12 | 0.041671 | 52684.7533 | -3.178
2009-10-13 | 9.4412 | 11936625.1067 | 2.2451
2009-10-14 | 0.62709 | 792835.5367 | -0.46667
2009-10-15 | 0.032622 | 41243.9567 | -3.4228
2009-10-16 | 0.29255 | 369871.3396 | -1.2291
2009-10-17 | 0.056636 | 71605.9683 | -2.8711
2009-10-18 | 0.28119 | 355509.5229 | -1.2687
2009-10-19 | 0.050129 | 63379.423 | -2.9931
2009-10-20 | 0.047761 | 60384.9135 | -3.0415
2009-10-21 | 0.090684 | 114653.5967 | -2.4004
2009-10-22 | 0.079644 | 100695.42 | -2.5302
2009-10-23 | 0.14912 | 188533.4433 | -1.903
2009-10-24 | 0.055725 | 70453.5483 | -2.8873
2009-10-25 | 0.057288 | 72430.085 | -2.8597
2009-10-26 | 1.8066 | 2284060.4082 | 0.59142
2009-10-27 | 0.56076 | 708974.9733 | -0.57847
2009-10-28 | 0.70756 | 894585.1217 | -0.34593
2009-10-29 | 0.069158 | 87437.9768 | -2.6714
2009-10-30 | 0.017459 | 22073.4433 | -4.0479
2009-10-31 | 0.089672 | 113373.2733 | -2.4116
2009-11-01 | 0.084662 | 107198.892 | -2.4691
2009-11-02 | 0.043745 | 55390.12 | -3.1294
2009-11-03 | 0.15733 | 199215.5317 | -1.8494
2009-11-04 | 0.086253 | 109214.0726 | -2.4505
2009-11-05 | 2.1307 | 2697830.4391 | 0.75643
2009-11-06 | 0.55886 | 707634.4285 | -0.58185
2009-11-07 | 0.4895 | 619804.5 | -0.71437
2009-11-08 | 0.11136 | 141007.63 | -2.195
2009-11-09 | 0.35705 | 452093.0595 | -1.0299
2009-11-10 | 0.29904 | 378647.8707 | -1.2072
2009-11-11 | 0.23478 | 297272.2638 | -1.4491
2009-11-12 | 0.25626 | 324475.264 | -1.3616
2009-11-13 | 0.2261 | 286281.485 | -1.4868
2009-11-14 | 0.25689 | 325275.5483 | -1.3591
2009-11-15 | 0.23187 | 293594.242 | -1.4616
2009-11-16 | 1.0848 | 1373615.8388 | 0.081426
2009-11-17 | 2.8697 | 3633668.3535 | 1.0542
2009-11-18 | 0.37225 | 471340.5222 | -0.98819
2009-11-19 | 0.057369 | 72640.4993 | -2.8583
2009-11-20 | 0.10127 | 128230.876 | -2.2899
2009-11-21 | 0.15205 | 192519.5433 | -1.8836
2009-11-22 | 0.13837 | 175199.915 | -1.9778
2009-11-23 | 0.50476 | 639123.7217 | -0.68368
2009-11-24 | 0.18263 | 231244.0736 | -1.7003
2009-11-25 | 0.29905 | 378652.4871 | -1.2072
2009-11-26 | 0.43589 | 551920.2474 | -0.83037
2009-11-27 | 0.16526 | 209250.1163 | -1.8002
2009-11-28 | 0.63284 | 801299.552 | -0.45754
2009-11-29 | 3.7112 | 4699096.6796 | 1.3114
2009-11-30 | 0.30245 | 382967.02 | -1.1958
2009-12-01 | 0.20827 | 264680.3033 | -1.5689
2009-12-02 | 0.43014 | 546638.62 | -0.84364
2009-12-03 | 0.24859 | 315916.57 | -1.3919
2009-12-04 | 0.074472 | 94641.3907 | -2.5973
2009-12-05 | 0.068223 | 86699.996 | -2.685
2009-12-06 | 0.091007 | 115654.6285 | -2.3968
2009-12-07 | 0.43775 | 556303.41 | -0.82611
2009-12-08 | 0.22177 | 281831.8497 | -1.5061
2009-12-09 | 0.28145 | 357678.5433 | -1.2678
2009-12-10 | 1.4577 | 1852526.81 | 0.37688
2009-12-11 | 0.35395 | 449813.6058 | -1.0386
2009-12-12 | 0.31782 | 403893.8394 | -1.1463
2009-12-13 | 0.33018 | 419600.001 | -1.1081
2009-12-14 | 0.12216 | 155246.156 | -2.1024
2009-12-15 | 0.045283 | 57546.3593 | -3.0948
2009-12-16 | 0.44653 | 567462.8967 | -0.80625
2009-12-17 | 0.27355 | 347628.6242 | -1.2963
2009-12-18 | 0.33369 | 424056.11 | -1.0976
2009-12-19 | 0.26917 | 342073.6718 | -1.3124
2009-12-20 | 0.58553 | 744105.1939 | -0.53524
2009-12-21 | 0.080214 | 101938.44 | -2.5231
2009-12-22 | 6.7535 | 8582567.0931 | 1.9101
2009-12-23 | 0.43244 | 549556.0453 | -0.83831
2009-12-24 | 0.63057 | 801348.3033 | -0.46113
2009-12-25 | 0.38143 | 484726.9767 | -0.96384
2009-12-26 | 0.19558 | 248544.6533 | -1.6318
2009-12-27 | 0.19582 | 248849.59 | -1.6306
2009-12-28 | 0.1124 | 142843.8267 | -2.1857
2009-12-29 | 0.35887 | 456066.1559 | -1.0248
2009-12-30 | 0.21996 | 279525.1063 | -1.5143
2009-12-31 | 0.22026 | 279915.5533 | -1.5129
2010-01-01 | 0.15929 | 203342.61 | -1.837
2010-01-02 | 0.11178 | 142693.7643 | -2.1912
2010-01-03 | 0.90288 | 1152578.8067 | -0.10216
2010-01-04 | 0.16472 | 210279.905 | -1.8035
2010-01-05 | 0.37284 | 475949.5037 | -0.98661
2010-01-06 | 0.33631 | 429312.8228 | -1.0897
2010-01-07 | 0.33198 | 423793.83 | -1.1027
2010-01-08 | 0.19478 | 248644.5333 | -1.6359
2010-01-09 | 0.1934 | 246886.7833 | -1.643
2010-01-10 | 0.18256 | 233052.5 | -1.7007
2010-01-11 | 0.035266 | 45019.073 | -3.3448
2010-01-12 | 0.26609 | 339672.7633 | -1.3239
2010-01-13 | 0.28022 | 357720.0238 | -1.2722
2010-01-14 | 0.18833 | 240407.6911 | -1.6696
2010-01-15 | 0.14086 | 179820.1979 | -1.96
2010-01-16 | 0.29861 | 381188.6088 | -1.2086
2010-01-17 | 0.30648 | 391233.7545 | -1.1826
2010-01-18 | 0.75449 | 963149.628 | -0.28171
2010-01-19 | 0.22334 | 285099.2233 | -1.4991
2010-01-20 | 0.08088 | 103248.1623 | -2.5148
2010-01-21 | 0.10022 | 127937.7877 | -2.3004
2010-01-22 | 0.05553 | 70886.7767 | -2.8908
2010-01-23 | 0.13826 | 176498.0695 | -1.9786
2010-01-24 | 0.63512 | 810759.11 | -0.45395
2010-01-25 | 0.12928 | 165034.24 | -2.0458
2010-01-26 | 0.10931 | 139541.4257 | -2.2136
2010-01-27 | 0.38414 | 490374.1454 | -0.95675
2010-01-28 | 0.48652 | 621063.9567 | -0.72049
2010-01-29 | 1.6312 | 2082306.4782 | 0.48931
2010-01-30 | 0.1617 | 206413.1867 | -1.822
2010-01-31 | 0.33057 | 421994.128 | -1.1069
2010-02-01 | 1.1685 | 1493864.8133 | 0.15574
2010-02-02 | 0.22167 | 283386.0072 | -1.5066
2010-02-03 | 0.077752 | 99400.505 | -2.5542
2010-02-04 | 0.079745 | 101948.5367 | -2.5289
2010-02-05 | 0.019342 | 24726.7929 | -3.9455
2010-02-06 | 0.40406 | 516565.5041 | -0.90618
2010-02-07 | 0.54362 | 694977.3356 | -0.60951
2010-02-08 | 0.15201 | 194337.1467 | -1.8838
2010-02-09 | 0.59733 | 763636.8717 | -0.51529
2010-02-10 | 0.46715 | 597219.7233 | -0.7611
2010-02-11 | 0.25882 | 330885.6533 | -1.3516
2010-02-12 | 0.021796 | 27865.0194 | -3.826
2010-02-13 | 0.37128 | 474653.02 | -0.9908
2010-02-14 | 0.29138 | 372512.5294 | -1.2331
2010-02-15 | 1.7002 | 2173604.9586 | 0.53076
2010-02-16 | 2.3815 | 3044533.5622 | 0.86772
2010-02-17 | 0.97583 | 1247521.7033 | -0.02447
2010-02-18 | 0.62467 | 798594.5967 | -0.47053
2010-02-19 | 0.13863 | 177223.2369 | -1.976
2010-02-20 | 0.21924 | 280282.7083 | -1.5176
2010-02-21 | 0.22244 | 284367.1784 | -1.5031
2010-02-22 | 0.033182 | 42420.57 | -3.4058
2010-02-23 | 0.3254 | 416000.8193 | -1.1227
2010-02-24 | 0.23711 | 303131.53 | -1.4392
2010-02-25 | 0.12364 | 158058.9734 | -2.0904
2010-02-26 | 0.19822 | 253411.6533 | -1.6184
2010-02-27 | 0.16769 | 214373.8329 | -1.7857
2010-02-28 | 0.35114 | 448911.5433 | -1.0466
2010-03-01 | 0.11433 | 146355.7723 | -2.1686
2010-03-02 | 1.2723 | 1628711.9874 | 0.24086
2010-03-03 | 0.59867 | 766350.6633 | -0.51304
2010-03-04 | 0.025741 | 32951.0433 | -3.6597
2010-03-05 | 0.039854 | 51016.495 | -3.2225
2010-03-06 | 0.43048 | 551051.8269 | -0.84285
2010-03-07 | 0.2151 | 275350.5083 | -1.5366
2010-03-08 | 0.2409 | 308377.5218 | -1.4234
2010-03-09 | 0.68723 | 879714.0534 | -0.37508
2010-03-10 | 0.39679 | 507929.5079 | -0.92434
2010-03-11 | 0.31584 | 404296.6477 | -1.1525
2010-03-12 | 0.51142 | 654666.7021 | -0.67056
2010-03-13 | 0.14786 | 189276.67 | -1.9115
2010-03-14 | 0.47039 | 602135.3619 | -0.7542
2010-03-15 | 0.32795 | 419805.7232 | -1.1149
2010-03-16 | 0.10648 | 136307.9404 | -2.2398
2010-03-17 | 0.061416 | 78617.211 | -2.7901
2010-03-18 | 0.022171 | 28380.8206 | -3.809
2010-03-19 | 0.060311 | 77203.4193 | -2.8082
2010-03-20 | 0.10556 | 135123.508 | -2.2485
2010-03-21 | 0.11181 | 143130.85 | -2.1909
2010-03-22 | 0.09147 | 117088.8557 | -2.3917
2010-03-23 | 0.027632 | 35370.905 | -3.5888
2010-03-24 | 0.12905 | 165189.3033 | -2.0476
2010-03-25 | 0.4189 | 536227.5245 | -0.87012
2010-03-26 | 0.061463 | 78678.0927 | -2.7893
2010-03-27 | 0.02921 | 37390.755 | -3.5333
2010-03-28 | 0.012656 | 16200.2607 | -4.3697
2010-03-29 | 0.19556 | 250328.185 | -1.6319
2010-03-30 | 0.031408 | 40204.8433 | -3.4607
2010-03-31 | 0.24845 | 318041.1564 | -1.3925
2010-04-01 | 0.13969 | 179195.6153 | -1.9684
2010-04-02 | 0.063258 | 81149.9904 | -2.7605
2010-04-03 | 0.089834 | 115243.2367 | -2.4098
2010-04-04 | 0.1122 | 143930.98 | -2.1875
2010-04-05 | 0.096485 | 123775.5867 | -2.3384
2010-04-06 | 0.022619 | 29017.2316 | -3.7889
2010-04-07 | 0.12029 | 154309.0201 | -2.1179
2010-04-08 | 0.12461 | 159859.314 | -2.0825
2010-04-09 | 0.01522 | 19524.9299 | -4.1851
2010-04-10 | 0.062064 | 79618.9833 | -2.7796
2010-04-11 | 0.049742 | 63810.84 | -3.0009
2010-04-12 | 0.012181 | 15626.6116 | -4.4079
2010-04-13 | 0.075687 | 97095.02 | -2.5811
2010-04-14 | 0.2372 | 304296.59 | -1.4388
2010-04-15 | 0.18961 | 243245.9367 | -1.6628
2010-04-16 | 0.11918 | 152890.6517 | -2.1271
2010-04-17 | 0.081429 | 104461.6967 | -2.508
2010-04-18 | 0.19598 | 251406.5633 | -1.6298
2010-04-19 | 0.050025 | 64174.84 | -2.9952
2010-04-20 | 0.17255 | 221356.15 | -1.7571
2010-04-21 | 0.29244 | 375157.2077 | -1.2295
2010-04-22 | 0.12317 | 158002.5869 | -2.0942
2010-04-23 | 0.086102 | 110456.3433 | -2.4522
2010-04-24 | 0.10176 | 130546.9967 | -2.2851
2010-04-25 | 0.12613 | 161808.2467 | -2.0704
2010-04-26 | 0.4546 | 583176.7475 | -0.78835
2010-04-27 | 0.14308 | 183548.9333 | -1.9444
2010-04-28 | 0.12348 | 158409.5063 | -2.0917
2010-04-29 | 0.080926 | 103815.88 | -2.5142
2010-04-30 | 0.17431 | 223616.9833 | -1.7469
2010-05-01 | 0.19987 | 256784.3267 | -1.6101
2010-05-02 | 0.027615 | 35479.74 | -3.5894
2010-05-03 | 0.14571 | 187201.6212 | -1.9262
2010-05-04 | 0.52274 | 671616.4644 | -0.64866
2010-05-05 | 0.32104 | 412473.6933 | -1.1362
2010-05-06 | 0.10257 | 131778.8783 | -2.2772
2010-05-07 | 0.2161 | 277643.57 | -1.532
2010-05-08 | 0.21042 | 270351.4567 | -1.5586
2010-05-09 | 0.029962 | 38495.0134 | -3.5078
2010-05-10 | 0.095662 | 122905.92 | -2.3469
2010-05-11 | 0.093618 | 120279.4333 | -2.3685
2010-05-12 | 0.34777 | 446812.4083 | -1.0562
2010-05-13 | 0.079917 | 102676.5083 | -2.5268
2010-05-14 | 0.059826 | 76863.5828 | -2.8163
2010-05-15 | 0.014895 | 19136.96 | -4.2067
2010-05-16 | 0.059424 | 76347.6333 | -2.8231
2010-05-17 | 0.25876 | 332451.9133 | -1.3519
2010-05-18 | 0.089518 | 115012.15 | -2.4133
2010-05-19 | 0.1264 | 162395.56 | -2.0683
2010-05-20 | 0.48006 | 616774.7117 | -0.73385
2010-05-21 | 0.3288 | 422441.2703 | -1.1123
2010-05-22 | 0.0062421 | 8019.7797 | -5.0764
2010-05-23 | 0.0090765 | 11661.425 | -4.7021
2010-05-24 | 0.04306 | 55322.8993 | -3.1452
2010-05-25 | 0.1086 | 139528.7 | -2.2201
2010-05-26 | 0.22899 | 294209.37 | -1.4741
2010-05-27 | 0.11181 | 143657.4367 | -2.1909
2010-05-28 | 0.092131 | 118368.5567 | -2.3845
2010-05-29 | 0.047873 | 61506.38 | -3.0392
2010-05-30 | 0.38913 | 499948.3854 | -0.94384
2010-05-31 | 0.090837 | 116706.85 | -2.3987
2010-06-01 | 0.05191 | 66801.0383 | -2.9583
2010-06-02 | 0.22995 | 295919.26 | -1.4699
2010-06-03 | 0.047914 | 61659.2067 | -3.0383
2010-06-04 | 0.15019 | 193278.647 | -1.8958
2010-06-05 | 0.16455 | 211756.1682 | -1.8045
2010-06-06 | 0.13833 | 178018.3667 | -1.9781
2010-06-07 | 0.091344 | 117547.72 | -2.3931
2010-06-08 | 0.32019 | 412040.0304 | -1.1388
2010-06-09 | 0.080052 | 103016.5233 | -2.5251
2010-06-10 | 0.08595 | 110606.7117 | -2.454
2010-06-11 | 0.083648 | 107643.8033 | -2.4811
2010-06-12 | 0.29253 | 376448.905 | -1.2292
2010-06-13 | 0.093422 | 120221.4867 | -2.3706
2010-06-14 | 0.0031129 | 4005.9333 | -5.7722
2010-06-15 | 0.19886 | 255910.3647 | -1.6151
2010-06-16 | 0.0027695 | 3569.35 | -5.8891
2010-06-17 | 0.011712 | 15072.0167 | -4.4471
2010-06-18 | 0.23368 | 300711.6867 | -1.4538
2010-06-19 | 0.014554 | 18728.89 | -4.2299
2010-06-20 | 0.01888 | 24296.2133 | -3.9696
2010-06-21 | 0.018511 | 23820.65 | -3.9894
2010-06-22 | 0.38131 | 490696.2901 | -0.96414
2010-06-23 | 0.17016 | 218976.6767 | -1.771
2010-06-24 | 0.25215 | 324483.5296 | -1.3777
2010-06-25 | 0.24552 | 315957.9672 | -1.4044
2010-06-26 | 0.0046579 | 5994.0525 | -5.3692
2010-06-27 | 0.2179 | 280414.2668 | -1.5237
2010-06-28 | 0.051043 | 65685.413 | -2.9751
2010-06-29 | 0.10885 | 140081.8067 | -2.2177
2010-06-30 | 0.088532 | 113929.2991 | -2.4244
2010-07-01 | 0.019444 | 25059.4167 | -3.9402
2010-07-02 | 0.26449 | 340879.8466 | -1.33
2010-07-03 | 0.48646 | 626967.16 | -0.72059
2010-07-04 | 0.023448 | 30220.8847 | -3.753
2010-07-05 | 0.019391 | 24991.178 | -3.943
2010-07-06 | 0.0097562 | 12574.0813 | -4.6299
2010-07-07 | 0.0038027 | 4900.99 | -5.5721
2010-07-08 | 0.02448 | 31550.4967 | -3.7099
2010-07-09 | 0.2774 | 357522.2337 | -1.2823
2010-07-10 | 0.35762 | 460914.84 | -1.0283
2010-07-11 | 0.01497 | 19293.8516 | -4.2017
2010-07-12 | 0.18195 | 234502.8467 | -1.704
2010-07-13 | 0.07437 | 95850.2458 | -2.5987
2010-07-14 | 0.11848 | 152700.0083 | -2.133
2010-07-15 | 0.043392 | 55924.6155 | -3.1375
2010-07-16 | 0.095823 | 123499.5867 | -2.3453
2010-07-17 | 0.0089971 | 11595.67 | -4.7109
2010-07-18 | 0.079947 | 103038.3067 | -2.5264
2010-07-19 | 0.15815 | 203830.4509 | -1.8442
2010-07-20 | 0.35251 | 454321.4017 | -1.0427
2010-07-21 | 0.42452 | 547131.106 | -0.8568
2010-07-22 | 0.027792 | 35819.3627 | -3.583
2010-07-23 | 0.10145 | 130747.41 | -2.2882
2010-07-24 | 0.007961 | 10260.4 | -4.8332
2010-07-25 | 0.036721 | 47326.5467 | -3.3044
2010-07-26 | 0.11015 | 141958.1351 | -2.206
2010-07-27 | 0.093574 | 120600.2767 | -2.369
2010-07-28 | 0.30656 | 395105.2867 | -1.1823
2010-07-29 | 0.098332 | 126733.134 | -2.3194
2010-07-30 | 0.1147 | 147824.1573 | -2.1655
2010-07-31 | 0.18428 | 237500.972 | -1.6913
2010-08-01 | 0.17585 | 228662.535 | -1.7381
2010-08-02 | 0.066966 | 87075.0767 | -2.7036
2010-08-03 | 0.45066 | 585989.3346 | -0.79704
2010-08-04 | 1.0364 | 1347615.2716 | 0.035746
2010-08-05 | 0.15548 | 202170.7766 | -1.8612
2010-08-06 | 0.14075 | 183014.2273 | -1.9608
2010-08-07 | 0.04501 | 58526.6067 | -3.1009
2010-08-08 | 0.014567 | 18941.78 | -4.229
2010-08-09 | 0.10714 | 139315.5567 | -2.2336
2010-08-10 | 0.97055 | 1262007.124 | -0.029888
2010-08-11 | 0.097165 | 126342.8822 | -2.3313
2010-08-12 | 0.56543 | 735223.0027 | -0.57017
2010-08-13 | 0.018379 | 23898.6345 | -3.9965
2010-08-14 | 0.0098523 | 12810.8633 | -4.6201
2010-08-15 | 0.18923 | 246060.6633 | -1.6648
2010-08-16 | 0.011324 | 14724.7883 | -4.4808
2010-08-17 | 0.075063 | 97604.5357 | -2.5894
2010-08-18 | 0.32591 | 423781.72 | -1.1211
2010-08-19 | 0.2491 | 323904.5229 | -1.3899
2010-08-20 | 0.20599 | 267853.6333 | -1.5799
2010-08-21 | 0.0162 | 21064.1944 | -4.1228
2010-08-22 | 0.050572 | 65759.05 | -2.9843
2010-08-23 | 0.20503 | 266595.401 | -1.5846
2010-08-24 | 0.34567 | 449469.4647 | -1.0623
2010-08-25 | 0.03733 | 48539.6271 | -3.288
2010-08-26 | 0.0089366 | 11620.26 | -4.7176
2010-08-27 | 0.4342 | 564588.55 | -0.83425
2010-08-28 | 0.17077 | 222051.8193 | -1.7674
2010-08-29 | 0.21287 | 276793.5759 | -1.5471
2010-08-30 | 0.078013 | 101439.29 | -2.5509
2010-08-31 | 0.29137 | 378864.3424 | -1.2332
2010-09-01 | 0.15815 | 205990.9476 | -1.8442
2010-09-02 | 0.26435 | 344330.1515 | -1.3305
2010-09-03 | 0.27814 | 362293.2417 | -1.2796
2010-09-04 | 0.21858 | 284715.3559 | -1.5206
2010-09-05 | 0.168 | 218821.0014 | -1.7838
2010-09-06 | 0.030088 | 39191.4133 | -3.5036
2010-09-07 | 0.17419 | 226884.0048 | -1.7476
2010-09-08 | 0.027208 | 35440.1233 | -3.6042
2010-09-09 | 0.24184 | 315009.1233 | -1.4195
2010-09-10 | 0.039533 | 51493.5077 | -3.2306
2010-09-11 | 0.20564 | 267857.5267 | -1.5816
2010-09-12 | 0.0083376 | 10860.06 | -4.787
2010-09-13 | 0.049855 | 64938.6782 | -2.9986
2010-09-14 | 0.034514 | 44956.1667 | -3.3664
2010-09-15 | 0.38338 | 499362.591 | -0.95874
2010-09-16 | 0.11446 | 149093.91 | -2.1675
2010-09-17 | 0.042685 | 55598.3967 | -3.1539
2010-09-18 | 0.088373 | 115109.5368 | -2.4262
2010-09-19 | 0.20036 | 260977.5904 | -1.6076
2010-09-20 | 0.19104 | 248831.21 | -1.6553
2010-09-21 | 0.36075 | 469889.6268 | -1.0196
2010-09-22 | 0.24684 | 321520.8367 | -1.399
2010-09-23 | 0.0051884 | 6758.0833 | -5.2613
2010-09-24 | 0.092931 | 121046.4867 | -2.3759
2010-09-25 | 0.11834 | 154146.855 | -2.1342
2010-09-26 | 0.032866 | 42809.0697 | -3.4153
2010-09-27 | 0.25265 | 329090.0698 | -1.3757
2010-09-28 | 0.11696 | 152338.5917 | -2.146
2010-09-29 | 0.21339 | 277949.8605 | -1.5446
2010-09-30 | 0.057524 | 74927.9 | -2.8555
2010-10-01 | 0.13832 | 180511.6977 | -1.9782
2010-10-02 | 0.012614 | 16461.99 | -4.3729
2010-10-03 | 0.034116 | 44522.3867 | -3.378
2010-10-04 | 0.22492 | 293528.21 | -1.492
2010-10-05 | 0.19946 | 260304.0493 | -1.6121
2010-10-06 | 0.081439 | 106279.7703 | -2.5079
2010-10-07 | 0.20753 | 270826.8892 | -1.5725
2010-10-08 | 0.15432 | 201393.5094 | -1.8687
2010-10-09 | 0.11848 | 154620.4306 | -2.133
2010-10-10 | 0.99043 | 1292531.407 | -0.0096164
2010-10-11 | 1.0804 | 1409946.0833 | 0.077332
2010-10-12 | 0.042957 | 56059.2033 | -3.1476
2010-10-13 | 0.04032 | 52618.4127 | -3.2109
2010-10-14 | 0.01294 | 16886.6107 | -4.3475
2010-10-15 | 0.82734 | 1079697.2973 | -0.18954
2010-10-16 | 2.4472 | 3193586.4917 | 0.89493
2010-10-17 | 0.0039968 | 5215.9067 | -5.5223
2010-10-18 | 0.15114 | 197247.0247 | -1.8895
2010-10-19 | 0.17677 | 230690.5119 | -1.7329
2010-10-20 | 0.049063 | 64028.8387 | -3.0146
2010-10-21 | 0.025386 | 33128.69 | -3.6736
2010-10-22 | 0.58438 | 762625.0733 | -0.53721
2010-10-23 | 0.10802 | 140969.9233 | -2.2254
2010-10-24 | 0.88472 | 1154582.6193 | -0.12248
2010-10-25 | 0.13027 | 170000.249 | -2.0382
2010-10-26 | 0.10372 | 135359.6633 | -2.266
2010-10-27 | 0.12531 | 163536.0275 | -2.0769
2010-10-28 | 0.22068 | 287990.769 | -1.511
2010-10-29 | 0.041458 | 54103.5235 | -3.1831
2010-10-30 | 0.039819 | 51963.9938 | -3.2234
2010-10-31 | 0.30533 | 398465.6833 | -1.1864
2010-11-01 | 0.049824 | 65092.0602 | -2.9992
2010-11-02 | 0.03939 | 51460.5167 | -3.2342
2010-11-03 | 0.23865 | 311779.3317 | -1.4328
2010-11-04 | 0.12128 | 158447.9133 | -2.1096
2010-11-05 | 0.020715 | 27062.58 | -3.8769
2010-11-06 | 0.10769 | 140684.0267 | -2.2285
2010-11-07 | 0.040799 | 53301.21 | -3.1991
2010-11-08 | 0.31292 | 408813.6 | -1.1618
2010-11-09 | 0.096816 | 126482.9267 | -2.3349
2010-11-10 | 0.042588 | 55637.7467 | -3.1562
2010-11-11 | 0.2383 | 311321.32 | -1.4342
2010-11-12 | 0.081065 | 105905.397 | -2.5125
2010-11-13 | 0.0062096 | 8112.4 | -5.0817
2010-11-14 | 0.028937 | 37804.7067 | -3.5426
2010-11-15 | 0.040442 | 52834.7 | -3.2079
2010-11-16 | 0.12731 | 166316.06 | -2.0612
2010-11-17 | 0.085991 | 112341.3123 | -2.4535
2010-11-18 | 0.2411 | 314973.8623 | -1.4226
2010-11-19 | 0.23046 | 301078.7047 | -1.4677
2010-11-20 | 0.030491 | 39834.7292 | -3.4903
2010-11-21 | 0.031895 | 41668.64 | -3.4453
2010-11-22 | 0.12093 | 157992.2002 | -2.1125
2010-11-23 | 0.25402 | 331863.7523 | -1.3703
2010-11-24 | 0.12816 | 167429.6184 | -2.0545
2010-11-25 | 0.076172 | 99513.4461 | -2.5748
2010-11-26 | 0.040894 | 53424.7142 | -3.1968
2010-11-27 | 0.058079 | 75875.84 | -2.846
2010-11-28 | 0.021743 | 28406.12 | -3.8284
2010-11-29 | 0.033948 | 44350.3585 | -3.3829
2010-11-30 | 0.061787 | 80720.4633 | -2.7841
2010-12-01 | 0.43027 | 563044.9723 | -0.84335
2010-12-02 | 0.42506 | 556231.8833 | -0.85552
2010-12-03 | 0.15212 | 199068.3817 | -1.8831
2010-12-04 | 0.070404 | 92129.52 | -2.6535
2010-12-05 | 0.65103 | 851928.4066 | -0.4292
2010-12-06 | 0.19053 | 249326.08 | -1.6579
2010-12-07 | 0.2507 | 328070.5777 | -1.3835
2010-12-08 | 0.080851 | 105801.1267 | -2.5151
2010-12-09 | 0.14782 | 193430.19 | -1.9118
2010-12-10 | 0.086216 | 112821.2554 | -2.4509
2010-12-11 | 0.22742 | 297601.755 | -1.481
2010-12-12 | 0.10606 | 138791.81 | -2.2437
2010-12-13 | 0.12374 | 161926.2333 | -2.0896
2010-12-14 | 0.38537 | 504293.957 | -0.95355
2010-12-15 | 6.4335 | 8418811.1648 | 1.8615
2010-12-16 | 25.2212 | 33004256.0181 | 3.2277
2010-12-17 | 2.1573 | 2823037.0098 | 0.76886
2010-12-18 | 0.70078 | 917040.6816 | -0.35556
2010-12-19 | 0.33807 | 442401.2433 | -1.0845
2010-12-20 | 0.34997 | 457969.7067 | -1.0499
2010-12-21 | 0.043051 | 56336.2333 | -3.1454
2010-12-22 | 0.54679 | 715530.0272 | -0.60368
2010-12-23 | 0.1725 | 225728.0117 | -1.7574
2010-12-24 | 0.35876 | 469468.719 | -1.0251
2010-12-25 | 0.39136 | 512126.7817 | -0.93814
2010-12-26 | 0.47204 | 617713.3545 | -0.75068
2010-12-27 | 1.9116 | 2501467.373 | 0.64793
2010-12-28 | 0.60613 | 793171.7506 | -0.50067
2010-12-29 | 0.23782 | 311213.3475 | -1.4362
2010-12-30 | 0.12491 | 163455.0163 | -2.0802
2010-12-31 | 0.18927 | 247680.13 | -1.6646
2011-01-01 | 0.20002 | 262066.525 | -1.6094
2011-01-02 | 0.048241 | 63206.2983 | -3.0316
2011-01-03 | 0.26992 | 353658.9787 | -1.3096
2011-01-04 | 0.13414 | 175752.26 | -2.0089
2011-01-05 | 0.77234 | 1011934.1328 | -0.25834
2011-01-06 | 0.23227 | 304332.8695 | -1.4598
2011-01-07 | 0.69743 | 913788.1665 | -0.36036
2011-01-08 | 0.2889 | 378519.2128 | -1.2417
2011-01-09 | 8.7012 | 11400585.8584 | 2.1635
2011-01-10 | 15.7354 | 20616919.4133 | 2.7559
2011-01-11 | 83.2972 | 109138253.3043 | 4.4224
2011-01-12 | 292.2949 | 382972653.7053 | 5.6778
2011-01-13 | 1.5882 | 2080893.44 | 0.4626
2011-01-14 | 0.82649 | 1082884.8055 | -0.19057
2011-01-15 | 0.7484 | 980569.6628 | -0.28982
2011-01-16 | 0.099143 | 129899.28 | -2.3112
2011-01-17 | 0.50311 | 659194.0633 | -0.68694
2011-01-18 | 7.1078 | 9312810.6801 | 1.9612
2011-01-19 | 1.6375 | 2145552.8422 | 0.4932
2011-01-20 | 0.71815 | 940942.588 | -0.33107
2011-01-21 | 0.39822 | 521762.79 | -0.92074
2011-01-22 | 0.48455 | 634865.9683 | -0.72454
2011-01-23 | 0.12007 | 157313.6467 | -2.1197
2011-01-24 | 0.050989 | 66807.7 | -2.9761
2011-01-25 | 0.079324 | 103933.0521 | -2.5342
2011-01-26 | 0.0072836 | 9543.1629 | -4.9221
2011-01-27 | 0.033944 | 44474.4233 | -3.383
2011-01-28 | 0.18374 | 240734.5583 | -1.6943
2011-01-29 | 0.074591 | 97730.5383 | -2.5957
2011-01-30 | 0.10336 | 135430.4833 | -2.2695
2011-01-31 | 0.13938 | 182623.8681 | -1.9705
2011-02-01 | 0.48096 | 630665.2128 | -0.73197
2011-02-02 | 0.13052 | 171144.9025 | -2.0362
2011-02-03 | 0.37551 | 492396.5017 | -0.97946
2011-02-04 | 0.32377 | 424545.6602 | -1.1277
2011-02-05 | 0.10302 | 135091.1633 | -2.2728
2011-02-06 | 0.46452 | 609108.3174 | -0.76675
2011-02-07 | 0.75168 | 985639.2378 | -0.28545
2011-02-08 | 0.24314 | 318814.072 | -1.4141
2011-02-09 | 0.16404 | 215104.2 | -1.8076
2011-02-10 | 0.13065 | 171321.1083 | -2.0352
2011-02-11 | 0.05836 | 76525.3687 | -2.8411
2011-02-12 | 0.25807 | 338398.0467 | -1.3545
2011-02-13 | 0.25264 | 331272.8767 | -1.3758
2011-02-14 | 0.11402 | 149509.4653 | -2.1714
2011-02-15 | 0.1148 | 150532.4573 | -2.1646
2011-02-16 | 0.15842 | 207729.7758 | -1.8425
2011-02-17 | 0.38657 | 506886.3133 | -0.95045
2011-02-18 | 0.20831 | 273146.0091 | -1.5687
2011-02-19 | 0.13208 | 173192.9448 | -2.0243
2011-02-20 | 0.1865 | 244550.3279 | -1.6793
2011-02-21 | 8.0625 | 10571960.1877 | 2.0872
2011-02-22 | 1.4803 | 1941089.5509 | 0.39226
2011-02-23 | 0.37994 | 498194.9367 | -0.96775
2011-02-24 | 0.35134 | 460700.6788 | -1.046
2011-02-25 | 0.2236 | 293192.3882 | -1.4979
2011-02-26 | 0.19094 | 250371.5367 | -1.6558
2011-02-27 | 0.071758 | 94093.41 | -2.6345
2011-02-28 | 0.32236 | 422690.9183 | -1.1321
2011-03-01 | 0.31484 | 413296.0127 | -1.1557
2011-03-02 | 0.70155 | 920936.2766 | -0.35446
2011-03-03 | 0.93846 | 1231928.5047 | -0.063514
2011-03-04 | 0.11251 | 147694.4332 | -2.1847
2011-03-05 | 0.26573 | 348826.2296 | -1.3253
2011-03-06 | 0.32239 | 423206.0255 | -1.132
2011-03-07 | 0.14224 | 186718.7199 | -1.9502
2011-03-08 | 0.049356 | 64790.01 | -3.0087
2011-03-09 | 0.086504 | 113554.2167 | -2.4476
2011-03-10 | 0.064813 | 85081.1295 | -2.7362
2011-03-11 | 0.38626 | 507047.9633 | -0.95124
2011-03-12 | 0.063152 | 82899.75 | -2.7622
2011-03-13 | 0.15296 | 200798.1833 | -1.8775
2011-03-14 | 0.21233 | 278724.6875 | -1.5496
2011-03-15 | 0.043915 | 57647.3518 | -3.1255
2011-03-16 | 0.239 | 313743.4167 | -1.4313
2011-03-17 | 0.16268 | 213553.5393 | -1.816
2011-03-18 | 0.062081 | 81494.3433 | -2.7793
2011-03-19 | 0.28852 | 378746.6601 | -1.243
2011-03-20 | 0.17169 | 225384.2917 | -1.762
2011-03-21 | 0.4156 | 545561.64 | -0.87803
2011-03-22 | 0.55796 | 732437.084 | -0.58347
2011-03-23 | 0.18421 | 241814.0427 | -1.6917
2011-03-24 | 0.17636 | 231509.3907 | -1.7352
2011-03-25 | 0.1467 | 192574.071 | -1.9194
2011-03-26 | 0.26159 | 343394.9497 | -1.341
2011-03-27 | 0.18079 | 237324.6452 | -1.7104
2011-03-28 | 0.20703 | 271767.9071 | -1.5749
2011-03-29 | 0.11256 | 147762.7935 | -2.1842
2011-03-30 | 0.23031 | 302324.05 | -1.4684
2011-03-31 | 0.23321 | 306139.1261 | -1.4558
2011-04-01 | 0.34204 | 449041.3541 | -1.0728
2011-04-02 | 0.12717 | 166952.0733 | -2.0622
2011-04-03 | 0.24372 | 319964.3983 | -1.4117
2011-04-04 | 0.10902 | 143126.73 | -2.2162
2011-04-05 | 0.26998 | 354432.5323 | -1.3094
2011-04-06 | 0.23249 | 305221.9382 | -1.4589
2011-04-07 | 0.16762 | 220052.7993 | -1.7861
2011-04-08 | 0.20044 | 263140.672 | -1.6073
2011-04-09 | 0.26817 | 352058.4467 | -1.3161
2011-04-10 | 0.019298 | 25335.4867 | -3.9477
2011-04-11 | 0.095888 | 125884.1828 | -2.3446
2011-04-12 | 0.31971 | 419721.8777 | -1.1403
2011-04-13 | 0.046728 | 61345.2933 | -3.0634
2011-04-14 | 0.024719 | 32451.5367 | -3.7002
2011-04-15 | 0.15296 | 200814.6567 | -1.8776
2011-04-16 | 0.042689 | 56043.41 | -3.1538
2011-04-17 | 0.019387 | 25451.4847 | -3.9432
2011-04-18 | 0.156 | 204800.7333 | -1.8579
2011-04-19 | 0.11001 | 144420.7816 | -2.2072
2011-04-20 | 0.17299 | 227111.6983 | -1.7545
2011-04-21 | 0.037747 | 49554.9617 | -3.2769
2011-04-22 | 0.20243 | 265752.3467 | -1.5974
2011-04-23 | 0.19445 | 255282.3467 | -1.6376
2011-04-24 | 0.21574 | 283224.5253 | -1.5337
2011-04-25 | 0.0084506 | 11094.2167 | -4.7735
2011-04-26 | 0.0055103 | 7234.0228 | -5.2011
2011-04-27 | 0.34924 | 458488.0624 | -1.052
2011-04-28 | 0.0043593 | 5722.9971 | -5.4354
2011-04-29 | 0.014627 | 19202.2 | -4.2249
2011-04-30 | 0.10007 | 131376.7078 | -2.3019
2011-05-01 | 0.005647 | 7421.7133 | -5.1766
2011-05-02 | 0.0061947 | 8141.62 | -5.0841
2011-05-03 | 1.4676 | 1928791.1884 | 0.3836
2011-05-04 | 0.17125 | 225072.8875 | -1.7646
2011-05-05 | 0.035698 | 46917.09 | -3.3327
2011-05-06 | 0.022551 | 29637.9433 | -3.792
2011-05-07 | 0.13088 | 172015.2093 | -2.0335
2011-05-08 | 0.11681 | 153522.72 | -2.1472
2011-05-09 | 0.21167 | 278197.6391 | -1.5527
2011-05-10 | 0.012826 | 16857.1467 | -4.3563
2011-05-11 | 0.057698 | 75831.2226 | -2.8525
2011-05-12 | 0.18917 | 248622.64 | -1.6651
2011-05-13 | 0.069391 | 91199.402 | -2.668
2011-05-14 | 0.029529 | 38809.3119 | -3.5224
2011-05-15 | 0.10422 | 136968.1547 | -2.2613
2011-05-16 | 0.011055 | 14529.2167 | -4.5049
2011-05-17 | 0.046832 | 61551.1658 | -3.0612
2011-05-18 | 0.15167 | 199342.6335 | -1.886
2011-05-19 | 0.10752 | 141314.1875 | -2.2301
2011-05-20 | 0.079762 | 104829.8933 | -2.5287
2011-05-21 | 0.32953 | 433093.57 | -1.1101
2011-05-22 | 0.19631 | 258010.887 | -1.628
2011-05-23 | 0.040551 | 53296.0982 | -3.2052
2011-05-24 | 0.012873 | 16918.7767 | -4.3526
2011-05-25 | 0.099282 | 130485.33 | -2.3098
2011-05-26 | 0.020669 | 27165.5063 | -3.8791
2011-05-27 | 0.1139 | 149697.5832 | -2.1724
2011-05-28 | 0.41869 | 550278.7381 | -0.87062
2011-05-29 | 0.044529 | 58523.1823 | -3.1116
2011-05-30 | 0.24167 | 317627.8905 | -1.4202
2011-05-31 | 0.028681 | 37695.5892 | -3.5515
2011-06-01 | 0.13473 | 177274.7171 | -2.0045
2011-06-02 | 0.10645 | 140068.0283 | -2.2401
2011-06-03 | 0.070702 | 93031.7633 | -2.6493
2011-06-04 | 0.15985 | 210337.5517 | -1.8335
2011-06-05 | 0.067205 | 88430.2267 | -2.7
2011-06-06 | 0.021961 | 28896.52 | -3.8185
2011-06-07 | 0.055318 | 72788.7767 | -2.8947
2011-06-08 | 0.15405 | 202696.9877 | -1.8705
2011-06-09 | 0.031468 | 41406.6378 | -3.4588
2011-06-10 | 0.031254 | 41124.2767 | -3.4656
2011-06-11 | 0.20668 | 271950.3767 | -1.5766
2011-06-12 | 0.28295 | 372307.3187 | -1.2625
2011-06-13 | 0.016737 | 22022.2567 | -4.0902
2011-06-14 | 0.10624 | 139791.4899 | -2.2421
2011-06-15 | 0.026126 | 34377.1212 | -3.6448
2011-06-16 | 0.62796 | 826279.8831 | -0.46528
2011-06-17 | 0.015567 | 20483.1515 | -4.1626
2011-06-18 | 0.043841 | 57687.13 | -3.1272
2011-06-19 | 0.11367 | 149565.2866 | -2.1745
2011-06-20 | 0.27811 | 365947.8943 | -1.2797
2011-06-21 | 0.26138 | 343922.7656 | -1.3418
2011-06-22 | 0.14959 | 196828.085 | -1.8999
2011-06-23 | 0.079851 | 105069.7569 | -2.5276
2011-06-24 | 0.20548 | 270380.628 | -1.5824
2011-06-25 | 0.096095 | 126443.9784 | -2.3424
2011-06-26 | 0.022946 | 30192.5033 | -3.7746
2011-06-27 | 0.12364 | 162692.6267 | -2.0904
2011-06-28 | 0.049481 | 65108.6204 | -3.0062
2011-06-29 | 0.15169 | 199592.2967 | -1.8859
2011-06-30 | 0.016348 | 21510.75 | -4.1137
2011-07-01 | 0.14462 | 190495.8625 | -1.9336
2011-07-02 | 0.0060514 | 7970.8833 | -5.1075
2011-07-03 | 0.019697 | 25944.4367 | -3.9273
2011-07-04 | 0.063893 | 84158.6733 | -2.7506
2011-07-05 | 0.014203 | 18707.97 | -4.2543
2011-07-06 | 0.29974 | 394812.0908 | -1.2048
2011-07-07 | 0.12623 | 166272.2567 | -2.0696
2011-07-08 | 0.12126 | 159727.313 | -2.1098
2011-07-09 | 0.11402 | 150187.18 | -2.1714
2011-07-10 | 0.033341 | 43915.7667 | -3.401
2011-07-11 | 0.13985 | 184213.5277 | -1.9672
2011-07-12 | 0.086683 | 114177.9667 | -2.4455
2011-07-13 | 0.022516 | 29657.41 | -3.7935
2011-07-14 | 0.32024 | 421812.8067 | -1.1387
2011-07-15 | 0.14355 | 189085.43 | -1.9411
2011-07-16 | 0.048364 | 63704.9615 | -3.029
2011-07-17 | 0.04804 | 63278.225 | -3.0357
2011-07-18 | 0.05636 | 74237.0967 | -2.876
2011-07-19 | 0.05624 | 74079.11 | -2.8781
2011-07-20 | 0.05267 | 69375.8067 | -2.9437
2011-07-21 | 0.24816 | 326872.6833 | -1.3937
2011-07-22 | 0.10653 | 140325.4827 | -2.2393
2011-07-23 | 0.33913 | 446704.5167 | -1.0814
2011-07-24 | 0.098958 | 130345.8167 | -2.3131
2011-07-25 | 0.0052438 | 6907.0633 | -5.2507
2011-07-26 | 0.12973 | 170885.1847 | -2.0423
2011-07-27 | 0.092557 | 121915.2515 | -2.3799
2011-07-28 | 0.049105 | 64680.5922 | -3.0138
2011-07-29 | 0.075438 | 99366.485 | -2.5844
2011-07-30 | 0.043082 | 56747.285 | -3.1446
2011-07-31 | 0.039526 | 52063.79 | -3.2308
2011-08-01 | 0.029621 | 39102.2467 | -3.5193
2011-08-02 | 0.0028258 | 3730.2955 | -5.869
2011-08-03 | 0.044086 | 58197.2767 | -3.1216
2011-08-04 | 0.057542 | 75960.5067 | -2.8552
2011-08-05 | 0.0027368 | 3612.8833 | -5.901
2011-08-06 | 0.058684 | 77467.9425 | -2.8356
2011-08-07 | 0.011385 | 15029.619 | -4.4754
2011-08-08 | 0.028446 | 37551.4653 | -3.5597
2011-08-09 | 0.093145 | 122960.615 | -2.3736
2011-08-10 | 0.018371 | 24252.0781 | -3.997
2011-08-11 | 0.022939 | 30281.24 | -3.7749
2011-08-12 | 0.11637 | 153617.874 | -2.151
2011-08-13 | 0.05864 | 77410.2033 | -2.8363
2011-08-14 | 0.0071911 | 9492.9666 | -4.9349
2011-08-15 | 0.062364 | 82326.2867 | -2.7748
2011-08-16 | 0.0057393 | 7576.46 | -5.1604
2011-08-17 | 0.034749 | 45872.5833 | -3.3596
2011-08-18 | 0.053036 | 70013.02 | -2.9368
2011-08-19 | 0.049213 | 64965.82 | -3.0116
2011-08-20 | 0.28007 | 369712.4 | -1.2727
2011-08-21 | 0.41677 | 550175.5565 | -0.87522
2011-08-22 | 0.79645 | 1051385.0689 | -0.22759
2011-08-23 | 0.53025 | 699981.5958 | -0.6344
2011-08-24 | 0.16382 | 216261.3657 | -1.809
2011-08-25 | 0.11009 | 145328.0467 | -2.2065
2011-08-26 | 0.037607 | 49644.3766 | -3.2806
2011-08-27 | 0.20948 | 276528.0203 | -1.5631
2011-08-28 | 0.1231 | 162510.0507 | -2.0947
2011-08-29 | 0.13878 | 183202.7057 | -1.9749
2011-08-30 | 0.47507 | 627132.3 | -0.7443
2011-08-31 | 0.038811 | 51234.4933 | -3.249
2011-09-01 | 0.061464 | 81134.44 | -2.7893
2011-09-02 | 0.023156 | 30566.6366 | -3.7655
2011-09-03 | 0.13894 | 183407.45 | -1.9737
2011-09-04 | 0.059086 | 77994.8503 | -2.8288
2011-09-05 | 0.25523 | 336911.7273 | -1.3656
2011-09-06 | 0.18473 | 243855.04 | -1.6888
2011-09-07 | 0.010032 | 13242.9045 | -4.6019
2011-09-08 | 0.2071 | 273381.9533 | -1.5745
2011-09-09 | 0.32347 | 426990.485 | -1.1286
2011-09-10 | 0.34314 | 452960.4725 | -1.0696
2011-09-11 | 0.32682 | 431411.4033 | -1.1183
2011-09-12 | 0.082793 | 109288.76 | -2.4914
2011-09-13 | 0.12908 | 170392.44 | -2.0473
2011-09-14 | 0.049348 | 65140.6873 | -3.0089
2011-09-15 | 0.15683 | 207020.8967 | -1.8526
2011-09-16 | 0.18087 | 238755.8372 | -1.71
2011-09-17 | 0.0095671 | 12628.7717 | -4.6494
2011-09-18 | 0.28218 | 372486.4355 | -1.2652
2011-09-19 | 0.24131 | 318531.211 | -1.4217
2011-09-20 | 0.086219 | 113811.5268 | -2.4509
2011-09-21 | 0.14027 | 185166.0861 | -1.9642
2011-09-22 | 0.033441 | 44143.1558 | -3.398
2011-09-23 | 0.078852 | 104087.3257 | -2.5402
2011-09-24 | 0.042391 | 55957.2433 | -3.1608
2011-09-25 | 0.046801 | 61779.0433 | -3.0618
2011-09-26 | 0.11164 | 147367.0023 | -2.1925
2011-09-27 | 0.0013589 | 1793.8333 | -6.6011
2011-09-28 | 0.032753 | 43235.1033 | -3.4188
2011-09-29 | 0.2053 | 271007.8733 | -1.5833
2011-09-30 | 0.034995 | 46194.17 | -3.3526
2011-10-01 | 0.803 | 1061122.0867 | -0.2194
2011-10-02 | 0.07948 | 105028.67 | -2.5322
2011-10-03 | 0.12651 | 167175.5188 | -2.0674
2011-10-04 | 0.31292 | 413509.6733 | -1.1618
2011-10-05 | 0.0080784 | 10675.1233 | -4.8186
2011-10-06 | 0.1943 | 256759.1056 | -1.6383
2011-10-07 | 0.16342 | 215943.64 | -1.8115
2011-10-08 | 1.5921 | 2103805.2967 | 0.46502
2011-10-09 | 0.036635 | 48410.4164 | -3.3068
2011-10-10 | 0.179 | 236533.7741 | -1.7204
2011-10-11 | 0.26246 | 346826.3225 | -1.3377
2011-10-12 | 0.03511 | 46395.8867 | -3.3493
2011-10-13 | 0.39604 | 523346.032 | -0.92624
2011-10-14 | 0.1479 | 195440.7729 | -1.9112
2011-10-15 | 2.252 | 2975908.2134 | 0.81182
2011-10-16 | 0.16994 | 224571.03 | -1.7723
2011-10-17 | 0.054992 | 72668.4768 | -2.9006
2011-10-18 | 0.40073 | 529538.5267 | -0.91447
2011-10-19 | 0.053056 | 70109.9466 | -2.9364
2011-10-20 | 0.060784 | 80321.99 | -2.8004
2011-10-21 | 0.17629 | 232961.0797 | -1.7356
2011-10-22 | 0.021939 | 28991.0765 | -3.8195
2011-10-23 | 0.012051 | 15924.1083 | -4.4186
2011-10-24 | 0.11444 | 151222.4 | -2.1677
2011-10-25 | 0.30377 | 401414.2125 | -1.1915
2011-10-26 | 0.089017 | 117631.25 | -2.4189
2011-10-27 | 0.11285 | 149122.4145 | -2.1817
2011-10-28 | 0.086487 | 114287.2083 | -2.4478
2011-10-29 | 0.019483 | 25745.2993 | -3.9382
2011-10-30 | 2.2498 | 2973018.2367 | 0.81085
2011-10-31 | 0.1829 | 241687.8977 | -1.6988
2011-11-01 | 0.17956 | 237490.99 | -1.7172
2011-11-02 | 0.079278 | 104852.3117 | -2.5348
2011-11-03 | 0.028386 | 37543.8488 | -3.5618
2011-11-04 | 0.073272 | 96909.4351 | -2.6136
2011-11-05 | 0.024546 | 32465.078 | -3.7072
2011-11-06 | 0.09145 | 120951.53 | -2.392
2011-11-07 | 0.0224 | 29626.3429 | -3.7987
2011-11-08 | 0.0090549 | 11976.0333 | -4.7044
2011-11-09 | 0.40077 | 530051.0833 | -0.91438
2011-11-10 | 0.06208 | 82106.9012 | -2.7793
2011-11-11 | 0.049464 | 65420.6974 | -3.0065
2011-11-12 | 0.372 | 492000.6267 | -0.98887
2011-11-13 | 0.043378 | 57372.0433 | -3.1378
2011-11-14 | 0.07396 | 97819.1367 | -2.6042
2011-11-15 | 0.055756 | 73742.2593 | -2.8868
2011-11-16 | 0.16724 | 221197.5658 | -1.7883
2011-11-17 | 0.020541 | 27167.4983 | -3.8853
2011-11-18 | 0.026135 | 34566.3717 | -3.6445
2011-11-19 | 0.0067079 | 8871.8867 | -5.0045
2011-11-20 | 0.17513 | 231626.9867 | -1.7422
2011-11-21 | 0.037073 | 49033.17 | -3.2949
2011-11-22 | 0.065774 | 86991.9133 | -2.7215
2011-11-23 | 0.27883 | 368780.3067 | -1.2772
2011-11-24 | 0.41489 | 548727.5813 | -0.87975
2011-11-25 | 0.30811 | 407500.0429 | -1.1773
2011-11-26 | 0.25513 | 337432.3033 | -1.366
2011-11-27 | 0.10813 | 143015.8233 | -2.2244
2011-11-28 | 0.017532 | 23187.1224 | -4.0438
2011-11-29 | 0.11354 | 150173.9393 | -2.1756
2011-11-30 | 0.039335 | 52023.666 | -3.2357
2011-12-01 | 0.54982 | 728088.4283 | -0.59816
2011-12-02 | 0.13509 | 178887.9978 | -2.0018
2011-12-03 | 0.091672 | 121395.0504 | -2.3895
2011-12-04 | 0.14918 | 197547.2392 | -1.9026
2011-12-05 | 0.23189 | 307071.8108 | -1.4615
2011-12-06 | 0.079768 | 105631.1462 | -2.5286
2011-12-07 | 0.25026 | 331397.2601 | -1.3853
2011-12-08 | 0.036249 | 48001.614 | -3.3173
2011-12-09 | 0.48452 | 641616.7157 | -0.72459
2011-12-10 | 0.54963 | 727832.7798 | -0.59851
2011-12-11 | 0.98736 | 1307489.416 | -0.012719
2011-12-12 | 0.10954 | 145050.1198 | -2.2115
2011-12-13 | 0.28737 | 380541.3667 | -1.247
2011-12-14 | 0.032296 | 42767.7633 | -3.4328
2011-12-15 | 0.049789 | 65932.0042 | -3
2011-12-16 | 0.28963 | 383535.6333 | -1.2392
2011-12-17 | 0.030981 | 41025.65 | -3.4744
2011-12-18 | 0.34107 | 451652.7017 | -1.0757
2011-12-19 | 0.32805 | 434418.3917 | -1.1146
2011-12-20 | 0.11374 | 150620.8367 | -2.1738
2011-12-21 | 0.010622 | 14065.5933 | -4.5449
2011-12-22 | 0.17798 | 235691.692 | -1.7261
2011-12-23 | 0.30049 | 397923.1396 | -1.2023
2011-12-24 | 0.23004 | 304629.6716 | -1.4695
2011-12-25 | 0.086871 | 115036.5583 | -2.4433
2011-12-26 | 0.0089211 | 11813.6159 | -4.7193
2011-12-27 | 0.31704 | 419829.7933 | -1.1487
2011-12-28 | 0.030871 | 40879.625 | -3.478
2011-12-29 | 0.080073 | 106034.46 | -2.5248
2011-12-30 | 0.082169 | 108810.6542 | -2.499
2011-12-31 | 0.054373 | 72001.9733 | -2.9119
2012-01-01 | 0.20095 | 266347.14 | -1.6047
2012-01-02 | 0.018502 | 24522.7655 | -3.9899
2012-01-03 | 0.031785 | 42128.6941 | -3.4488
2012-01-04 | 0.089931 | 119195.9867 | -2.4087
2012-01-05 | 0.09088 | 120453.9633 | -2.3982
2012-01-06 | 0.60204 | 797953.1387 | -0.50743
2012-01-07 | 0.62642 | 830266.8771 | -0.46773
2012-01-08 | 0.030835 | 40868.8233 | -3.4791
2012-01-09 | 0.11625 | 154083.7133 | -2.152
2012-01-10 | 0.13916 | 184440.1405 | -1.9722
2012-01-11 | 0.14897 | 197448.954 | -1.904
2012-01-12 | 0.019918 | 26400.0265 | -3.9161
2012-01-13 | 0.065818 | 87236.5502 | -2.7209
2012-01-14 | 0.029386 | 38949.1965 | -3.5272
2012-01-15 | 0.36013 | 477322.0533 | -1.0213
2012-01-16 | 0.3909 | 518104.93 | -0.9393
2012-01-17 | 0.14553 | 192885.21 | -1.9274
2012-01-18 | 0.096078 | 127343.53 | -2.3426
2012-01-19 | 0.58096 | 770011.404 | -0.54307
2012-01-20 | 0.087196 | 115571.0938 | -2.4396
2012-01-21 | 0.004156 | 5508.4633 | -5.4832
2012-01-22 | 0.14645 | 194112.8482 | -1.921
2012-01-23 | 0.38016 | 503864.05 | -0.96717
2012-01-24 | 0.6375 | 844954.7404 | -0.4502
2012-01-25 | 0.41309 | 547515.609 | -0.88409
2012-01-26 | 0.16215 | 214919.49 | -1.8192
2012-01-27 | 0.22805 | 302264.583 | -1.4782
2012-01-28 | 0.1844 | 244401.6167 | -1.6907
2012-01-29 | 0.4087 | 541692.1067 | -0.89478
2012-01-30 | 0.071917 | 95320.1779 | -2.6322
2012-01-31 | 0.065151 | 86352.1173 | -2.731
2012-02-01 | 0.12412 | 164740.8925 | -2.0865
2012-02-02 | 0.26155 | 347138.2505 | -1.3411
2012-02-03 | 0.14361 | 190601.4167 | -1.9407
2012-02-04 | 0.036072 | 47877.14 | -3.3222
2012-02-05 | 0.22143 | 293886.6218 | -1.5077
2012-02-06 | 0.20841 | 276617.4251 | -1.5682
2012-02-07 | 0.054664 | 72552.1931 | -2.9066
2012-02-08 | 0.077823 | 103290.3233 | -2.5533
2012-02-09 | 0.21714 | 288204.2437 | -1.5272
2012-02-10 | 0.052324 | 69447.188 | -2.9503
2012-02-11 | 0.040576 | 53854.5293 | -3.2046
2012-02-12 | 0.32249 | 428022.42 | -1.1317
2012-02-13 | 1.5445 | 2049977.7651 | 0.43472
2012-02-14 | 0.095598 | 126882.8324 | -2.3476
2012-02-15 | 0.014882 | 19752.0017 | -4.2076
2012-02-16 | 0.16572 | 219945.7767 | -1.7975
2012-02-17 | 0.036789 | 48828.5133 | -3.3025
2012-02-18 | 0.12969 | 172124.4297 | -2.0426
2012-02-19 | 0.115 | 152634.1628 | -2.1628
2012-02-20 | 0.15762 | 209202.2166 | -1.8476
2012-02-21 | 3.5413 | 4700167.3883 | 1.2645
2012-02-22 | 0.51618 | 685093.3483 | -0.66131
2012-02-23 | 0.058607 | 77786.3675 | -2.8369
2012-02-24 | 0.88913 | 1180095.266 | -0.11751
2012-02-25 | 0.66749 | 885927.1597 | -0.40423
2012-02-26 | 0.18703 | 248238.491 | -1.6765
2012-02-27 | 0.07068 | 93809.7644 | -2.6496
2012-02-28 | 0.099402 | 131931.5657 | -2.3086
2012-02-29 | 0.38476 | 510678.2678 | -0.95512
2012-03-01 | 0.1065 | 141754.9251 | -2.2396
2012-03-02 | 0.10231 | 136182.3244 | -2.2797
2012-03-03 | 0.70165 | 933953.3341 | -0.35432
2012-03-04 | 0.19517 | 259785.1067 | -1.6339
2012-03-05 | 0.7822 | 1041163.6897 | -0.24565
2012-03-06 | 0.025248 | 33606.5467 | -3.679
2012-03-07 | 0.31898 | 424583.1015 | -1.1426
2012-03-08 | 0.060741 | 80851.21 | -2.8011
2012-03-09 | 0.068208 | 90789.6567 | -2.6852
2012-03-10 | 0.040071 | 53337.26 | -3.2171
2012-03-11 | 0.087855 | 116942.39 | -2.4321
2012-03-12 | 0.059061 | 78615.2452 | -2.8292
2012-03-13 | 0.56472 | 751688.3688 | -0.57142
2012-03-14 | 0.10487 | 139589.5828 | -2.255
2012-03-15 | 0.032245 | 42920.6379 | -3.4344
2012-03-16 | 0.025344 | 33734.566 | -3.6752
2012-03-17 | 0.10964 | 145933.2788 | -2.2106
2012-03-18 | 0.048596 | 64685.4 | -3.0242
2012-03-19 | 0.12957 | 172466.8383 | -2.0435
2012-03-20 | 0.20685 | 275331.9959 | -1.5758
2012-03-21 | 0.065087 | 86635.9967 | -2.732
2012-03-22 | 0.54271 | 722388.56 | -0.61118
2012-03-23 | 0.37437 | 498310.9503 | -0.98252
2012-03-24 | 0.1041 | 138558.9008 | -2.2624
2012-03-25 | 0.021002 | 27955.2833 | -3.8631
2012-03-26 | 0.13181 | 175452.5224 | -2.0264
2012-03-27 | 0.041591 | 55360.4977 | -3.1799
2012-03-28 | 0.074152 | 98701.6833 | -2.6016
2012-03-29 | 0.33394 | 444496.1222 | -1.0968
2012-03-30 | 0.094683 | 126030.94 | -2.3572
2012-03-31 | 0.078449 | 104421.4633 | -2.5453
2012-04-01 | 0.020007 | 26693.48 | -3.9117
2012-04-02 | 0.0083832 | 11184.7675 | -4.7815
2012-04-03 | 0.1156 | 154231.0789 | -2.1576
2012-04-04 | 0.065395 | 87248.699 | -2.7273
2012-04-05 | 0.058657 | 78258.7695 | -2.8361
2012-04-06 | 0.15658 | 208909.4533 | -1.8542
2012-04-07 | 0.023202 | 30956.2592 | -3.7635
2012-04-08 | 0.1181 | 157573.54 | -2.1362
2012-04-09 | 0.10425 | 139093.752 | -2.2609
2012-04-10 | 0.20736 | 276657.5541 | -1.5733
2012-04-11 | 0.066039 | 88107.9017 | -2.7175
2012-04-12 | 0.093141 | 124266.4533 | -2.3736
2012-04-13 | 0.17861 | 238296.3967 | -1.7226
2012-04-14 | 0.19886 | 265318.3817 | -1.6151
2012-04-15 | 0.13478 | 179822.4433 | -2.0041
2012-04-16 | 0.0046201 | 6164.05 | -5.3773
2012-04-17 | 0.1528 | 203857.07 | -1.8787
2012-04-18 | 0.24975 | 333217.8147 | -1.3873
2012-04-19 | 0.10846 | 144709.0906 | -2.2213
2012-04-20 | 0.048916 | 65263.3033 | -3.0176
2012-04-21 | 0.063687 | 84970.1869 | -2.7538
2012-04-22 | 0.14182 | 189214.2333 | -1.9532
2012-04-23 | 0.038175 | 50932.8367 | -3.2656
2012-04-24 | 0.035365 | 47183.6168 | -3.342
2012-04-25 | 0.032745 | 43687.7 | -3.419
2012-04-26 | 0.12795 | 170704.72 | -2.0561
2012-04-27 | 0.091567 | 122166.5533 | -2.3907
2012-04-28 | 0.50994 | 680354.194 | -0.67346
2012-04-29 | 0.37949 | 506313.866 | -0.96892
2012-04-30 | 0.099852 | 133221.245 | -2.3041
2012-05-01 | 0.020602 | 27541.3916 | -3.8823
2012-05-02 | 0.028817 | 38522.98 | -3.5468
2012-05-03 | 0.0042286 | 5652.8667 | -5.4659
2012-05-04 | 0.12213 | 163259.5307 | -2.1027
2012-05-05 | 0.030033 | 40148.83 | -3.5054
2012-05-06 | 0.16606 | 221988.43 | -1.7954
2012-05-07 | 0.009731 | 13008.392 | -4.6324
2012-05-08 | 0.061191 | 81800.4216 | -2.7938
2012-05-09 | 0.0668 | 89298.5517 | -2.7061
2012-05-10 | 0.50164 | 670598.637 | -0.68986
2012-05-11 | 1.2401 | 1657740.1344 | 0.21518
2012-05-12 | 0.0076504 | 10227.0667 | -4.873
2012-05-13 | 0.25784 | 344686.84 | -1.3554
2012-05-14 | 0.017925 | 23962.2818 | -4.0216
2012-05-15 | 0.319 | 426436.605 | -1.1426
2012-05-16 | 0.16854 | 225309.56 | -1.7806
2012-05-17 | 0.018489 | 24716.5067 | -3.9906
2012-05-18 | 0.041163 | 55026.8389 | -3.1902
2012-05-19 | 0.047933 | 64077.58 | -3.0379
2012-05-20 | 0.14015 | 187358.7387 | -1.965
2012-05-21 | 0.010479 | 14008.4 | -4.5584
2012-05-22 | 0.095953 | 128270.7099 | -2.3439
2012-05-23 | 0.11724 | 156723.19 | -2.1436
2012-05-24 | 0.07047 | 94204.09 | -2.6526
2012-05-25 | 0.044596 | 59615.5042 | -3.1101
2012-05-26 | 0.026622 | 35588.4697 | -3.626
2012-05-27 | 0.017639 | 23579.7811 | -4.0376
2012-05-28 | 0.26291 | 351461.7433 | -1.3359
2012-05-29 | 0.099057 | 132419.8733 | -2.3121
2012-05-30 | 0.05932 | 79299.4767 | -2.8248
2012-05-31 | 0.06048 | 80849.75 | -2.8054
2012-06-01 | 0.26869 | 359791.1233 | -1.3142
2012-06-02 | 0.091208 | 122130.8058 | -2.3946
2012-06-03 | 0.25965 | 347684.4567 | -1.3484
2012-06-04 | 1.4507 | 1942599.2999 | 0.37208
2012-06-05 | 0.45665 | 611476.0059 | -0.78383
2012-06-06 | 0.068819 | 92151.7017 | -2.6763
2012-06-07 | 0.06566 | 87921.5 | -2.7233
2012-06-08 | 0.052215 | 69918.4867 | -2.9524
2012-06-09 | 0.012222 | 16366 | -4.4045
2012-06-10 | 0.09784 | 131010.9367 | -2.3244
2012-06-11 | 0.85492 | 1144770.7533 | -0.15675
2012-06-12 | 0.1573 | 210635.8004 | -1.8496
2012-06-13 | 0.050309 | 67365.18 | -2.9896
2012-06-14 | 0.17292 | 231548.778 | -1.7549
2012-06-15 | 0.28691 | 384190.0667 | -1.2486
2012-06-16 | 0.24232 | 324474.2733 | -1.4175
2012-06-17 | 0.16481 | 220683.5633 | -1.803
2012-06-18 | 0.025394 | 34003.68 | -3.6732
2012-06-19 | 0.0071941 | 9633.2333 | -4.9345
2012-06-20 | 0.06424 | 86020.3602 | -2.7451
2012-06-21 | 0.012706 | 17013.9367 | -4.3657
2012-06-22 | 0.045221 | 60552.7 | -3.0962
2012-06-23 | 0.055973 | 74950.2033 | -2.8829
2012-06-24 | 0.037941 | 50803.871 | -3.2717
2012-06-25 | 0.042424 | 56807.0967 | -3.16
2012-06-26 | 0.17445 | 233597.6067 | -1.7461
2012-06-27 | 0.11261 | 150795.66 | -2.1838
2012-06-28 | 0.034518 | 46220.3233 | -3.3663
2012-06-29 | 0.064158 | 85909.5133 | -2.7464
2012-06-30 | 0.038581 | 51661.42 | -3.255
Contents

## 1e. STPIS Exclusions
Energex | [11 empty] | Weather
STPIS Data Reporting | [11 empty] | Equipment failure
2012-13 | [11 empty] | Operational error
Exclusions | [11 empty] | Vegetation
Animals
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Exclusions | [11 empty] | Third party impacts
Transmission failure
Date of event (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of event | Number of customers interrupted | Duration of interruption (mins) | Total unplanned customer minutes off supply | Excluded Event category (Use Exclusion categories listed in section 3.3 (a) of the AER's STPIS) | Unplanned SAIDI Impact | Unplanned SAIFI impact | Further information (Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning) |  | Load shedding
Other
Contents

## 1f. STPIS GSL
Energex
STPIS Data Reporting - AER Definitions
2012-13
Guaranteed Service Level
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Did the AER's GSL Scheme apply at any time during the regulatory year? | No
If the AER's GSL scheme applied at any time during the regulatory year, table 1 must be completed. Do not complete table 1 if the AER's GSL scheme did not apply during the regulatory year.
Table 1: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
Total GSL payments payable under the AER's GSL scheme ($) | 0
Contents

## 2. Demand
Energex
Demand
2012-13
The information is required to assess forecasts against outturn demand, and will inform the AER’s review of demand forecasts in future regulatory proposals. The information may be used in performance reports.
Note: a) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
b) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
c) The PoE level only applies to the forecasts
Table 1: Maximum coincident demand at the network level
Network coincident maximum demand | Forecast | Actual - raw | Actual - weather normalised | Variation % | t+1 forecast
90% PoE level
Network coincident maximum demand (MW)
Network coincident maximum demand (MVA)
50% PoE level
Network coincident maximum demand (MW) | 5328 | 4475 | 4590 | -16.01% | 4710
Network coincident maximum demand (MVA)
10% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA)
Table 2: Summer and winter non-coincident maximum demand by zone substation
Summer and winter maximum demand - ZS | [12 empty] | t+1 forecast |  |  |  | Nameplate rating (MVA)
POE level = 50% | Forecast |  |  |  | Actual - raw |  |  |  | Actual - weather normalised
Location | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF
Acacia Ridge SD maximum demand | 21.81 | 22.38 | 5.02 | 0.975 | 15.87 | 16.36 | 4 | 0.97 | 17.72 | 18.28 | 4.47 | 0.97 | 16.17 | 16.18 | 0.54 | 0.999 | 40
Acacia Ridge SN maximum demand | 18.45 | 18.58 | 2.21 | 0.993 | 15.12 | 15.46 | 3.23 | 0.978 | 16.88 | 17.26 | 3.6 | 0.978 | 15.41 | 15.41 | 0.09 | 1 | 40
Acacia Ridge WD maximum demand | 18.84 | 18.9 | 1.54 | 0.997 | 15.4 | 15.69 | 3 | 0.981 | 17.31 | 17.64 | 3.38 | 0.981 | 16.37 | 16.98 | 4.52 | 0.964 | 40
Acacia Ridge WN maximum demand | 16.76 | 16.77 | 0.52 | 1 | 15.14 | 15.23 | 1.66 | 0.994 | 17.02 | 17.13 | 1.87 | 0.994 | 17.17 | 17.87 | 4.97 | 0.96 | 40
Albany Creek SD maximum demand | 28.64 | 30.7 | 11.07 | 0.933 | 22.73 | 23.65 | 6.53 | 0.961 | 26.25 | 27.31 | 7.54 | 0.961 | 23.91 | 25.36 | 8.45 | 0.943 | 50
Albany Creek SN maximum demand | 29.13 | 31.17 | 11.1 | 0.934 | 23.77 | 24.71 | 6.75 | 0.962 | 27.44 | 28.52 | 7.79 | 0.962 | 25 | 26.39 | 8.47 | 0.947 | 50
Albany Creek WD maximum demand | 21.62 | 22.25 | 5.25 | 0.972 | 16.91 | 17.03 | 2.06 | 0.993 | 19.45 | 19.6 | 2.37 | 0.993 | 19.5 | 19.97 | 4.29 | 0.977 | 50
Albany Creek WN maximum demand | 24.84 | 25.63 | 6.32 | 0.969 | 18.81 | 19.05 | 2.98 | 0.988 | 21.65 | 21.92 | 3.43 | 0.988 | 21.7 | 22.22 | 4.78 | 0.977 | 50
Alexandra Headland SD maximum demand | 90.49 | 97.16 | 35.37 | 0.931 | 59.59 | 61.64 | 15.78 | 0.967 | 68.41 | 70.77 | 18.12 | 0.967 | 62 | 64.89 | 19.16 | 0.955 | 120
Alexandra Headland SN maximum demand | 86.71 | 90.9 | 27.3 | 0.954 | 57.23 | 58.84 | 13.68 | 0.973 | 65.7 | 67.55 | 15.7 | 0.973 | 59.54 | 61.51 | 15.46 | 0.968 | 120
Alexandra Headland WD maximum demand | 64.29 | 65 | 9.55 | 0.989 | 49.71 | 49.83 | 3.46 | 0.998 | 51.94 | 52.06 | 3.62 | 0.998 | 53.64 | 53.93 | 5.51 | 0.995 | 120
Alexandra Headland WN maximum demand | 73.9 | 75.01 | 12.8 | 0.985 | 51.97 | 52.06 | 3.05 | 0.998 | 54.3 | 54.4 | 3.19 | 0.998 | 56.21 | 56.48 | 5.51 | 0.995 | 120
Algester SD maximum demand | 22.43 | 22.68 | 3.39 | 0.989 | 18.9 | 19.24 | 3.59 | 0.982 | 20.2 | 20.56 | 3.83 | 0.982 | 19.87 | 20.25 | 3.9 | 0.981 | 50
Algester SN maximum demand | 19.57 | 19.58 | 0.53 | 1 | 17.01 | 17.05 | 1.09 | 0.998 | 18.18 | 18.22 | 1.16 | 0.998 | 17.88 | 17.96 | 1.64 | 0.996 | 50
Algester WD maximum demand | 18.98 | 18.98 | -0.01 | 1 | 15.88 | 16.78 | 5.41 | 0.947 | 17.57 | 18.56 | 5.98 | 0.947 | 17.97 | 17.99 | 0.77 | 0.999 | 50
Algester WN maximum demand | 18.25 | 18.29 | -1.22 | 0.998 | 15.43 | 16.26 | 5.13 | 0.949 | 17.06 | 17.98 | 5.67 | 0.949 | 17.46 | 18.4 | 5.82 | 0.949 | 50
Amamoor SD maximum demand | 4.16 | 4.73 | 2.24 | 0.881 | 3.91 | 4.45 | 2.11 | 0.881 | 3.91 | 4.45 | 2.11 | 0.881 | 3.58 | 4.07 | 1.93 | 0.88 | 6
Amamoor SN maximum demand | 4.69 | 5.22 | 2.31 | 0.897 | 3.37 | 3.79 | 1.73 | 0.889 | 3.37 | 3.79 | 1.73 | 0.889 | 3.08 | 3.46 | 1.57 | 0.891 | 6
Amamoor WD maximum demand | 4.54 | 5.16 | 2.45 | 0.88 | 3.2 | 3.67 | 1.79 | 0.873 | 3.2 | 3.67 | 1.79 | 0.873 | 3.23 | 3.67 | 1.75 | 0.879 | 6
Amamoor WN maximum demand | 5.32 | 5.91 | 2.57 | 0.9 | 3.35 | 3.73 | 1.63 | 0.899 | 3.35 | 3.73 | 1.63 | 0.899 | 3.38 | 3.75 | 1.62 | 0.901 | 6
Amberley SD maximum demand | 6.04 | 7.34 | 4.17 | 0.823 | 2.96 | 3.3 | 1.48 | 0.894 | 3.14 | 3.51 | 1.57 | 0.894 | 2.83 | 3.13 | 1.35 | 0.902 | 25
Amberley SN maximum demand | 4.95 | 5.95 | 3.3 | 0.832 | 3.02 | 3.31 | 1.35 | 0.913 | 3.21 | 3.51 | 1.43 | 0.913 | 2.89 | 3.17 | 1.31 | 0.91 | 25
Amberley WD maximum demand | 3.9 | 4.63 | 2.5 | 0.842 | 2.83 | 3.08 | 1.22 | 0.918 | 3.27 | 3.56 | 1.41 | 0.918 | 3.22 | 3.54 | 1.46 | 0.91 | 25
Amberley WN maximum demand | 3 | 3.49 | 1.78 | 0.859 | 3.11 | 3.39 | 1.35 | 0.917 | 3.6 | 3.92 | 1.56 | 0.917 | 3.54 | 3.87 | 1.56 | 0.915 | 25
Ann St SD maximum demand | 102.82 | 108.03 | 33.14 | 0.952 | 46.83 | 47.81 | 9.65 | 0.979 | 50.79 | 51.86 | 10.46 | 0.979 | 45.68 | 45.69 | 0.77 | 1 | 120
Ann St SN maximum demand | 86.94 | 90.13 | 23.76 | 0.965 | 40.89 | 41.48 | 6.96 | 0.986 | 44.35 | 44.99 | 7.55 | 0.986 | 39.89 | 39.93 | 1.81 | 0.999 | 120
Ann St WD maximum demand | 79.99 | 81.29 | 14.49 | 0.984 | 37.18 | 37.41 | 4.17 | 0.994 | 37.67 | 37.9 | 4.23 | 0.994 | 37.07 | 37.21 | 3.14 | 0.996 | 120
Ann St WN maximum demand | 69.52 | 71.3 | 15.8 | 0.975 | 34.12 | 34.28 | 3.36 | 0.995 | 34.57 | 34.73 | 3.4 | 0.995 | 34.02 | 34.14 | 2.86 | 0.996 | 120
Annerley SD maximum demand | 13.78 | 15.68 | 7.47 | 0.879 | 17.73 | 18.71 | 5.98 | 0.948 | 18.13 | 19.13 | 6.11 | 0.948 | 14.84 | 16.29 | 6.73 | 0.911 | 50
Annerley SN maximum demand | 13.75 | 15.57 | 7.31 | 0.883 | 17.69 | 18.59 | 5.74 | 0.951 | 18.09 | 19.01 | 5.87 | 0.951 | 14.79 | 16.18 | 6.56 | 0.914 | 50
Annerley WD maximum demand | 10.06 | 10.75 | 3.8 | 0.935 | 12.3 | 12.57 | 2.61 | 0.978 | 14.34 | 14.66 | 3.04 | 0.978 | 17.54 | 18.34 | 5.35 | 0.957 | 50
Annerley WN maximum demand | 11.26 | 12.17 | 4.61 | 0.925 | 13.99 | 14.34 | 3.15 | 0.976 | 16.32 | 16.72 | 3.67 | 0.976 | 20.24 | 21.32 | 6.7 | 0.949 | 50
Arana Hills SD maximum demand | 31.43 | 32.22 | 7.12 | 0.975 | 28.23 | 28.89 | 6.17 | 0.977 | 31.21 | 31.95 | 6.82 | 0.977 | 27.27 | 27.48 | 3.42 | 0.992 | 50
Arana Hills SN maximum demand | 33.64 | 34.48 | 7.57 | 0.976 | 30.03 | 30.68 | 6.3 | 0.979 | 33.2 | 33.93 | 6.97 | 0.979 | 28.99 | 29.2 | 3.46 | 0.993 | 50
Arana Hills WD maximum demand | 25.73 | 25.76 | 1.26 | 0.999 | 24.44 | 24.66 | 3.28 | 0.991 | 27.85 | 28.1 | 3.74 | 0.991 | 26.66 | 27.13 | 5.01 | 0.983 | 50
Arana Hills WN maximum demand | 31.6 | 31.73 | 2.92 | 0.996 | 29.14 | 29.31 | 3.22 | 0.994 | 33.19 | 33.4 | 3.66 | 0.994 | 31.7 | 31.7 | 0.27 | 1 | 50
Archerfield SD maximum demand | 24.37 | 24.96 | 5.4 | 0.976 | 20.44 | 21.01 | 4.85 | 0.973 | 21.15 | 21.74 | 5.02 | 0.973 | 18.96 | 18.97 | 0.48 | 1 | 50
Archerfield SN maximum demand | 18.61 | 18.69 | 1.67 | 0.996 | 17.36 | 17.54 | 2.52 | 0.99 | 17.96 | 18.15 | 2.61 | 0.99 | 16.1 | 16.56 | 3.88 | 0.972 | 50
Archerfield WD maximum demand | 19.79 | 19.94 | 2.5 | 0.992 | 19.16 | 19.2 | -1.26 | 0.998 | 19.15 | 19.19 | -1.26 | 0.998 | 17.98 | 18.58 | 4.7 | 0.968 | 50
Archerfield WN maximum demand | 15.98 | 15.99 | -0.28 | 1 | 18.1 | 18.22 | -2.01 | 0.994 | 18.09 | 18.2 | -2.01 | 0.994 | 17.03 | 17.47 | 3.94 | 0.974 | 50
Arundel SD maximum demand | 26.14 | 26.17 | 1.26 | 0.999 | 22.47 | 22.74 | 3.5 | 0.988 | 22.69 | 22.96 | 3.53 | 0.988 | 15.81 | 15.87 | 1.35 | 0.996 | 50
Arundel SN maximum demand | 24.33 | 24.33 | 0.11 | 1 | 21.63 | 21.74 | 2.28 | 0.995 | 21.84 | 21.96 | 2.3 | 0.995 | 15.29 | 15.3 | 0.73 | 0.999 | 50
Arundel WD maximum demand | 22.02 | 22.18 | -2.65 | 0.993 | 19.72 | 20.51 | 5.62 | 0.962 | 22.25 | 23.13 | 6.35 | 0.962 | 16.22 | 17 | 5.07 | 0.954 | 50
Arundel WN maximum demand | 21.39 | 21.62 | -3.12 | 0.99 | 19.48 | 20.13 | 5.08 | 0.968 | 21.97 | 22.71 | 5.73 | 0.968 | 16.17 | 16.85 | 4.72 | 0.96 | 50
Ashgrove SD maximum demand | 30.02 | 30.51 | 5.46 | 0.984 | 23.75 | 24.11 | 4.14 | 0.985 | 27.25 | 27.66 | 4.75 | 0.985 | 24.83 | 24.85 | 0.92 | 0.999 | 50
Ashgrove SN maximum demand | 31.02 | 31.48 | 5.39 | 0.985 | 24.14 | 24.48 | 4.08 | 0.986 | 27.7 | 28.09 | 4.69 | 0.986 | 25.24 | 25.25 | 0.8 | 0.999 | 50
Ashgrove WD maximum demand | 24.29 | 24.29 | -0.54 | 1 | 20.98 | 21.78 | 5.82 | 0.964 | 24.84 | 25.78 | 6.89 | 0.964 | 23.78 | 23.93 | 2.66 | 0.994 | 50
Ashgrove WN maximum demand | 28.79 | 28.85 | 1.87 | 0.998 | 22.59 | 22.63 | 1.3 | 0.998 | 26.75 | 26.79 | 1.54 | 0.998 | 25.48 | 25.79 | 3.98 | 0.988 | 50
Aspley SD maximum demand | 18.6935 | 19.226 | 4.4933 | 0.97231 | 0 | 0 | 0 |  | 0 | 0 | 0
Aspley SN maximum demand | 17.6267 | 18.0379 | 3.8296 | 0.9772 | 0 | 0 | 0 |  | 0 | 0 | 0
Aspley WD maximum demand | 13.6131 | 13.6159 | 0.27523 | 0.9998 | 0 | 0 | 0 |  | 0 | 0 | 0
Aspley WN maximum demand | 15.1264 | 15.1584 | 0.98531 | 0.99789 | 0 | 0 | 0 |  | 0 | 0 | 0
Astor Terrace SD maximum demand | 45.39 | 45.4 | -0.79 | 1 | 24.76 | 24.92 | 2.9 | 0.993 | 28.49 | 28.69 | 3.33 | 0.993 | 26.19 | 26.19 | 0.22 | 1 | 60
Astor Terrace SN maximum demand | 38 | 38.34 | -5.04 | 0.991 | 21.9 | 21.97 | 1.76 | 0.997 | 25.21 | 25.29 | 2.02 | 0.997 | 23.17 | 23.48 | 3.81 | 0.987 | 60
Astor Terrace WD maximum demand | 30.18 | 31.57 | -9.26 | 0.956 | 18.45 | 19.24 | 5.48 | 0.959 | 18.47 | 19.26 | 5.49 | 0.959 | 18.03 | 18.03 | 0.25 | 1 | 60
Astor Terrace WN maximum demand | 26.87 | 29.01 | -10.92 | 0.926 | 15.92 | 16.41 | 3.97 | 0.97 | 15.93 | 16.42 | 3.98 | 0.97 | 15.54 | 16.15 | 4.36 | 0.963 | 60
Bald Hills Bus 1 SD maximum demand | 13.16 | 13.96 | 4.67 | 0.942 | 8.38 | 8.64 | 2.11 | 0.97 | 10.34 | 10.66 | 2.6 | 0.97 | 10.76 | 11.17 | 2.98 | 0.964 | 20
Bald Hills Bus 1 SN maximum demand | 12.9 | 13.73 | 4.68 | 0.94 | 8.77 | 9.03 | 2.14 | 0.971 | 10.82 | 11.14 | 2.64 | 0.971 | 11.23 | 11.66 | 3.13 | 0.963 | 20
Bald Hills Bus 1 WD maximum demand | 11.92 | 12.1 | 2.07 | 0.985 | 7.05 | 7.12 | 1 | 0.99 | 8.02 | 8.1 | 1.14 | 0.99 | 9.13 | 9.2 | 1.14 | 0.992 | 20
Bald Hills Bus 1 WN maximum demand | 13.91 | 14.35 | 3.51 | 0.97 | 7.82 | 7.92 | 1.28 | 0.987 | 8.9 | 9.01 | 1.45 | 0.987 | 10.22 | 10.37 | 1.78 | 0.985 | 20
Bald Hills Bus 2 SD maximum demand | 11.92 | 12.8 | 4.65 | 0.932 | 11.17 | 11.77 | 3.7 | 0.949 | 12.66 | 13.33 | 4.19 | 0.949 | 10.22 | 10.93 | 3.87 | 0.935 | 25
Bald Hills Bus 2 SN maximum demand | 12.24 | 13.09 | 4.65 | 0.935 | 11.38 | 12.02 | 3.86 | 0.947 | 12.9 | 13.62 | 4.37 | 0.947 | 10.41 | 11.09 | 3.81 | 0.939 | 25
Bald Hills Bus 2 WD maximum demand | 8.59 | 8.83 | 2.03 | 0.973 | 8.21 | 8.39 | 1.7 | 0.979 | 9.46 | 9.66 | 1.96 | 0.979 | 8.44 | 8.66 | 1.96 | 0.974 | 25
Bald Hills Bus 2 WN maximum demand | 9.89 | 10.24 | 2.66 | 0.966 | 9.47 | 9.65 | 1.87 | 0.981 | 10.92 | 11.13 | 2.15 | 0.981 | 9.69 | 9.96 | 2.31 | 0.973 | 25
Beaudesert SD maximum demand | 16 | 16.07 | 1.57 | 0.995 | 14.38 | 16.06 | 7.14 | 0.896 | 15.72 | 17.54 | 7.8 | 0.896 | 14.22 | 14.47 | 2.68 | 0.983 | 18
Beaudesert SN maximum demand | 15.15 | 15.15 | 0.16 | 1 | 13.59 | 14.96 | 6.24 | 0.909 | 14.85 | 16.34 | 6.82 | 0.909 | 13.44 | 13.56 | 1.8 | 0.991 | 18
Beaudesert WD maximum demand | 13.8 | 13.97 | -2.15 | 0.988 | 10.54 | 10.99 | 3.13 | 0.959 | 12.86 | 13.41 | 3.81 | 0.959 | 12.34 | 12.36 | 0.57 | 0.999 | 18
Beaudesert WN maximum demand | 14.3 | 14.66 | -3.24 | 0.975 | 10.89 | 11.29 | 2.97 | 0.965 | 13.29 | 13.78 | 3.62 | 0.965 | 13.26 | 14.09 | 4.77 | 0.941 | 18
Beenleigh SD maximum demand | 38.92 | 40.4 | 10.83 | 0.963 | 34.69 | 35.21 | 6.02 | 0.985 | 37.9 | 38.47 | 6.58 | 0.985 | 31.92 | 32.49 | 6.04 | 0.983 | 50
Beenleigh SN maximum demand | 37.41 | 38.37 | 8.56 | 0.975 | 33.22 | 33.47 | 4.06 | 0.993 | 36.3 | 36.57 | 4.44 | 0.993 | 31.34 | 31.66 | 4.5 | 0.99 | 50
Beenleigh WD maximum demand | 28.01 | 28.01 | -0.09 | 1 | 26.07 | 26.36 | 3.89 | 0.989 | 28.74 | 29.05 | 4.29 | 0.989 | 29.46 | 29.46 | 0.08 | 1 | 50
Beenleigh WN maximum demand | 29.7 | 29.7 | 0.01 | 1 | 25.6 | 25.68 | 2.03 | 0.997 | 28.21 | 28.3 | 2.24 | 0.997 | 30.44 | 30.71 | 4.01 | 0.991 | 50
Beenleigh North SD maximum demand | 11.3 | 11.36 | 1.2 | 0.994 | 8.87 | 9.78 | 4.13 | 0.907 | 9.57 | 10.56 | 4.46 | 0.907 | 8.61 | 9.55 | 4.12 | 0.902 | 25
Beenleigh North SN maximum demand | 11.41 | 11.42 | 0.41 | 0.999 | 8.24 | 8.99 | 3.61 | 0.916 | 8.89 | 9.71 | 3.89 | 0.916 | 8 | 8.75 | 3.55 | 0.914 | 25
Beenleigh North WD maximum demand | 9.09 | 9.22 | -1.57 | 0.985 | 8.19 | 8.75 | 3.06 | 0.937 | 8.44 | 9.01 | 3.16 | 0.937 | 8.31 | 9.01 | 3.5 | 0.921 | 25
Beenleigh North WN maximum demand | 10.08 | 10.21 | -1.66 | 0.987 | 7.89 | 8.35 | 2.74 | 0.945 | 8.12 | 8.6 | 2.82 | 0.945 | 8 | 8.54 | 3.01 | 0.936 | 25
Beerwah SD maximum demand | 15.7 | 16.38 | 4.66 | 0.959 | 11.84 | 12.31 | 3.35 | 0.962 | 13.06 | 13.57 | 3.69 | 0.962 | 11.38 | 12.59 | 5.38 | 0.904 | 50
Beerwah SN maximum demand | 14.42 | 14.81 | 3.39 | 0.973 | 11.89 | 12.37 | 3.41 | 0.961 | 13.11 | 13.64 | 3.76 | 0.961 | 11.46 | 12.45 | 4.87 | 0.92 | 50
Beerwah WD maximum demand | 11.33 | 11.44 | 1.59 | 0.99 | 8.86 | 9.08 | 1.96 | 0.977 | 9.86 | 10.1 | 2.18 | 0.977 | 11.51 | 12.39 | 4.58 | 0.929 | 50
Beerwah WN maximum demand | 11.8 | 11.85 | 1.02 | 0.996 | 9.71 | 9.81 | 1.39 | 0.99 | 10.8 | 10.91 | 1.55 | 0.99 | 12.59 | 13.24 | 4.12 | 0.95 | 50
Bells Creek North SD maximum demand | 16.54 | 16.89 | 3.42 | 0.979 | 0 | 0 | 0 |  | 0 | 0 | 0
Bells Creek North SN maximum demand | 16.05 | 16.29 | 2.75 | 0.986 | 0 | 0 | 0 |  | 0 | 0 | 0
Bells Creek North WD maximum demand | 12.02 | 12.03 | -0.57 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0
Bells Creek North WN maximum demand | 12.8 | 12.81 | -0.47 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0
Belmont SD maximum demand | 14.9 | 15.1 | 2.47 | 0.987 | 8.07 | 9.72 | 5.43 | 0.83 | 9.92 | 11.96 | 6.68 | 0.83 | 14.13 | 14.25 | 1.8 | 0.992 | 42
Belmont SN maximum demand | 15.02 | 15.13 | 1.84 | 0.993 | 8.3 | 9.75 | 5.11 | 0.852 | 10.21 | 11.98 | 6.28 | 0.852 | 10.44 | 11.54 | 4.9 | 0.905 | 42
Belmont WD maximum demand | 12.29 | 12.3 | -0.63 | 0.999 | 10.04 | 10.55 | 3.26 | 0.951 | 11.66 | 12.26 | 3.79 | 0.951 | 12.91 | 13.69 | 4.54 | 0.943 | 42
Belmont WN maximum demand | 13.06 | 13.06 | -0.27 | 1 | 10.36 | 10.77 | 2.95 | 0.962 | 12.03 | 12.51 | 3.42 | 0.962 | 13.46 | 14.15 | 4.38 | 0.951 | 42
Bethania SD maximum demand | 15.64 | 16 | -3.35 | 0.978 | 14.49 | 14.81 | 3.07 | 0.978 | 16.26 | 16.62 | 3.44 | 0.978 | 15.36 | 16.26 | 5.32 | 0.945 | 45
Bethania SN maximum demand | 16.07 | 16.44 | -3.43 | 0.978 | 15.57 | 15.91 | 3.25 | 0.979 | 17.48 | 17.85 | 3.65 | 0.979 | 16.5 | 17.36 | 5.39 | 0.95 | 45
Bethania WD maximum demand | 12.51 | 13.13 | 3.98 | 0.953 | 12.21 | 12.24 | 0.9 | 0.997 | 13.79 | 13.83 | 1.02 | 0.997 | 13.68 | 14.02 | 3.07 | 0.976 | 45
Bethania WN maximum demand | 13.81 | 14.35 | 3.9 | 0.962 | 13.37 | 13.41 | 1.01 | 0.997 | 15.1 | 15.15 | 1.14 | 0.997 | 14.96 | 15.27 | 3.03 | 0.98 | 45
Birkdale SD maximum demand | 27.05 | 30.5 | 14.09 | 0.887 | 22.25 | 22.93 | 5.54 | 0.97 | 26.31 | 27.12 | 6.55 | 0.97 | 24.62 | 24.7 | 2 | 0.997 | 50
Birkdale SN maximum demand | 30.27 | 33.43 | 14.17 | 0.906 | 24.08 | 24.08 | 0.37 | 1 | 28.47 | 28.48 | 0.44 | 1 | 26.63 | 26.72 | 2.12 | 0.997 | 50
Birkdale WD maximum demand | 25 | 26.56 | 8.96 | 0.941 | 22.53 | 22.63 | 2.17 | 0.995 | 24.99 | 25.1 | 2.41 | 0.995 | 24.57 | 24.83 | 3.6 | 0.989 | 50
Birkdale WN maximum demand | 29.16 | 30.84 | 10.06 | 0.945 | 24.85 | 25.07 | 3.28 | 0.991 | 27.57 | 27.81 | 3.64 | 0.991 | 27.07 | 27.34 | 3.81 | 0.99 | 50
Black Mountain SD maximum demand | 9.36 | 9.41 | 1.01 | 0.994 | 8.55 | 8.73 | 1.78 | 0.979 | 8.91 | 9.1 | 1.85 | 0.979 | 3.32 | 3.35 | 0.41 | 0.992 | 15
Black Mountain SN maximum demand | 9.87 | 9.89 | 0.67 | 0.998 | 8.5 | 8.67 | 1.67 | 0.981 | 8.86 | 9.03 | 1.74 | 0.981 | 3.14 | 3.15 | 0.16 | 0.999 | 15
Black Mountain WD maximum demand | 10.64 | 10.64 | -0.29 | 1 | 9.41 | 9.66 | -2.22 | 0.973 | 11.21 | 11.52 | -2.64 | 0.973 | 5.5 | 5.55 | 0.72 | 0.992 | 15
Black Mountain WN maximum demand | 11.7 | 11.71 | -0.34 | 1 | 10.97 | 11.19 | -2.21 | 0.98 | 13.07 | 13.34 | -2.63 | 0.98 | 6.53 | 6.6 | 0.9 | 0.991 | 15
Boonah SD maximum demand | 8.17 | 9.09 | 3.97 | 0.899 | 6.31 | 6.35 | 0.69 | 0.994 | 7.2 | 7.25 | 0.78 | 0.994 | 6.59 | 6.69 | 1.13 | 0.986 | 15
Boonah SN maximum demand | 7.58 | 8.29 | 3.36 | 0.914 | 5.99 | 6.01 | 0.52 | 0.996 | 6.83 | 6.86 | 0.6 | 0.996 | 6.25 | 6.31 | 0.86 | 0.991 | 15
Boonah WD maximum demand | 7.73 | 8.05 | 2.25 | 0.96 | 5.45 | 5.45 | -0.25 | 0.999 | 6.03 | 6.04 | -0.27 | 0.999 | 6.03 | 6.28 | 1.75 | 0.96 | 15
Boonah WN maximum demand | 7.53 | 7.9 | 2.37 | 0.954 | 5.18 | 5.2 | -0.44 | 0.996 | 5.74 | 5.76 | -0.49 | 0.996 | 5.74 | 5.96 | 1.58 | 0.964 | 15
Booval SD maximum demand | 28.92 | 29 | 2.22 | 0.997 | 21.99 | 22.06 | 1.74 | 0.997 | 24.37 | 24.45 | 1.93 | 0.997 | 22.25 | 22.42 | 2.79 | 0.992 | 45
Booval SN maximum demand | 28.92 | 29.01 | 2.24 | 0.997 | 21.12 | 21.14 | 0.89 | 0.999 | 23.41 | 23.43 | 0.99 | 0.999 | 21.37 | 21.49 | 2.29 | 0.994 | 45
Booval WD maximum demand | 24.23 | 24.36 | -2.54 | 0.995 | 17.91 | 18.39 | 4.17 | 0.974 | 21.18 | 21.75 | 4.93 | 0.974 | 20.21 | 20.87 | 5.22 | 0.968 | 45
Booval WN maximum demand | 27.8 | 27.86 | -1.83 | 0.998 | 19.61 | 19.69 | -1.76 | 0.996 | 23.2 | 23.29 | -2.08 | 0.996 | 22.09 | 22.69 | 5.19 | 0.974 | 45
Bowen Hills SD maximum demand | 7.2 | 8.27 | 4.06 | 0.871
Bowen Hills SN maximum demand | 7.35 | 8.25 | 3.76 | 0.89
Bowen Hills WD maximum demand | 3.24 | 3.46 | 1.22 | 0.935
Bowen Hills WN maximum demand | 3.6 | 3.83 | 1.32 | 0.939
Brendale SD maximum demand | 28.17 | 28.17 | -0.69 | 1 | 28.09 | 28.12 | 1.2 | 0.999 | 32.89 | 32.92 | 1.4 | 0.999 | 30.35 | 30.63 | 4.11 | 0.991 | 50
Brendale SN maximum demand | 29.22 | 29.22 | -0.06 | 1 | 31.33 | 31.37 | 1.56 | 0.999 | 36.68 | 36.72 | 1.83 | 0.999 | 30.78 | 31.05 | 4.08 | 0.991 | 50
Brendale WD maximum demand | 26.81 | 26.88 | -1.84 | 0.998 | 22.32 | 22.46 | 2.59 | 0.993 | 24.38 | 24.54 | 2.82 | 0.993 | 24.66 | 24.68 | 0.89 | 0.999 | 50
Brendale WN maximum demand | 31.84 | 31.85 | -1.1 | 0.999 | 26.73 | 26.92 | 3.24 | 0.993 | 29.19 | 29.41 | 3.54 | 0.993 | 29.54 | 29.58 | 1.66 | 0.998 | 50
Bribie Island SD maximum demand | 24.53 | 24.53 | -0.14 | 1 | 16.49 | 17.28 | 5.17 | 0.954 | 19.57 | 20.51 | 6.13 | 0.954 | 17.65 | 17.66 | 0.61 | 0.999 | 36
Bribie Island SN maximum demand | 24.3 | 24.31 | -0.75 | 1 | 17.76 | 18.34 | 4.56 | 0.969 | 21.08 | 21.77 | 5.42 | 0.969 | 19.02 | 19.02 | 0.57 | 1 | 36
Bribie Island WD maximum demand | 21.22 | 21.69 | -4.45 | 0.979 | 16.39 | 16.63 | 2.81 | 0.986 | 17.73 | 17.99 | 3.04 | 0.986 | 17.46 | 17.84 | 3.66 | 0.979 | 36
Bribie Island WN maximum demand | 24.65 | 24.91 | -3.64 | 0.989 | 18.35 | 18.63 | 3.19 | 0.985 | 19.86 | 20.15 | 3.45 | 0.985 | 19.55 | 20 | 4.19 | 0.978 | 36
Brighton SD maximum demand | 10.92 | 12.37 | 5.81 | 0.883 | 7.51 | 7.78 | 2.06 | 0.964 | 8.68 | 9.01 | 2.38 | 0.964 | 7.8 | 8.54 | 3.46 | 0.914 | 30
Brighton SN maximum demand | 11.65 | 13.33 | 6.48 | 0.874 | 8.32 | 8.68 | 2.47 | 0.959 | 9.63 | 10.04 | 2.85 | 0.959 | 8.65 | 9.53 | 4.01 | 0.907 | 30
Brighton WD maximum demand | 10.09 | 10.72 | 3.61 | 0.942 | 7.75 | 7.91 | 1.57 | 0.98 | 8.87 | 9.05 | 1.8 | 0.98 | 8.71 | 9.09 | 2.59 | 0.959 | 30
Brighton WN maximum demand | 12.14 | 13.06 | 4.8 | 0.93 | 8.62 | 8.83 | 1.92 | 0.976 | 9.86 | 10.1 | 2.2 | 0.976 | 9.68 | 10.23 | 3.3 | 0.947 | 30
Broadbeach SD maximum demand | 57.44 | 58.36 | 10.3 | 0.984 | 48.45 | 50.7 | 14.93 | 0.956 | 53.28 | 55.75 | 16.42 | 0.956 | 49.29 | 49.35 | 2.43 | 0.999 | 120
Broadbeach SN maximum demand | 56.89 | 57.6 | 8.99 | 0.988 | 48.39 | 50.57 | 14.69 | 0.957 | 53.21 | 55.61 | 16.15 | 0.957 | 49.2 | 49.24 | 2.02 | 0.999 | 120
Broadbeach WD maximum demand | 41.42 | 41.59 | -3.75 | 0.996 | 36.91 | 38.54 | 11.09 | 0.958 | 39.79 | 41.55 | 11.96 | 0.958 | 39.54 | 39.77 | 4.32 | 0.994 | 120
Broadbeach WN maximum demand | 48 | 48.03 | -1.72 | 0.999 | 40.16 | 41.81 | 11.66 | 0.96 | 43.29 | 45.08 | 12.57 | 0.96 | 43.03 | 43.29 | 4.77 | 0.994 | 120
Bromelton SD maximum demand | 14.65 | 15.05 | 3.45 | 0.973 | 7.61 | 7.63 | 0.62 | 0.997 | 8.21 | 8.24 | 0.67 | 0.997 | 7.42 | 7.52 | 1.18 | 0.988 | 30
Bromelton SN maximum demand | 14.22 | 14.5 | 2.82 | 0.981 | 7.35 | 7.37 | 0.54 | 0.997 | 7.93 | 7.95 | 0.58 | 0.997 | 7.17 | 7.19 | 0.48 | 0.998 | 30
Bromelton WD maximum demand | 9.29 | 9.38 | 1.34 | 0.99 | 6.75 | 6.92 | 1.54 | 0.975 | 6.95 | 7.13 | 1.58 | 0.975 | 7.92 | 8.02 | 1.31 | 0.987 | 30
Bromelton WN maximum demand | 9.5 | 9.56 | 1.09 | 0.993 | 6.67 | 6.85 | 1.54 | 0.975 | 6.88 | 7.06 | 1.58 | 0.975 | 7.83 | 7.93 | 1.25 | 0.988 | 30
Browns Plains SD maximum demand | 65.4 | 66.93 | 14.24 | 0.977 | 42.96 | 43.74 | 8.24 | 0.982 | 50.63 | 51.55 | 9.71 | 0.982 | 45.63 | 45.66 | 1.75 | 0.999 | 75
Browns Plains SN maximum demand | 64.8 | 65.97 | 12.4 | 0.982 | 42.46 | 43.16 | 7.74 | 0.984 | 50.04 | 50.87 | 9.12 | 0.984 | 45.1 | 45.11 | 0.88 | 1 | 75
Browns Plains WD maximum demand | 49.51 | 49.54 | -1.66 | 0.999 | 32.44 | 32.94 | 5.74 | 0.985 | 36.2 | 36.76 | 6.4 | 0.985 | 35.7 | 35.83 | 3.07 | 0.996 | 75
Browns Plains WN maximum demand | 58.65 | 58.65 | 0.29 | 1 | 34.35 | 34.93 | 6.3 | 0.984 | 38.33 | 38.97 | 7.03 | 0.984 | 37.81 | 37.92 | 2.95 | 0.997 | 75
Bulimba SD maximum demand | 26.65 | 26.8 | 2.8 | 0.995 | 21.41 | 21.53 | 2.26 | 0.994 | 24.65 | 24.78 | 2.6 | 0.994 | 22.25 | 22.68 | 4.39 | 0.981 | 34
Bulimba SN maximum demand | 27.27 | 27.33 | 1.84 | 0.998 | 22.85 | 22.97 | 2.34 | 0.995 | 26.3 | 26.44 | 2.69 | 0.995 | 23.74 | 24.07 | 3.94 | 0.987 | 34
Bulimba WD maximum demand | 22.49 | 22.8 | 3.79 | 0.986 | 17.4 | 18.06 | 4.81 | 0.964 | 19.98 | 20.73 | 5.52 | 0.964 | 19.81 | 19.83 | 1 | 0.999 | 34
Bulimba WN maximum demand | 25.24 | 25.58 | 4.16 | 0.987 | 19.3 | 19.9 | 4.86 | 0.97 | 22.16 | 22.85 | 5.58 | 0.97 | 21.97 | 22.01 | 1.3 | 0.998 | 34
Bundall SD maximum demand | 28.19 | 28.75 | 5.62 | 0.981 | 20.2 | 20.21 | 0.51 | 1 | 25.32 | 25.32 | 0.64 | 1 | 22.84 | 22.94 | 2.19 | 0.995 | 42
Bundall SN maximum demand | 25.17 | 25.35 | 3.01 | 0.993 | 18.8 | 18.84 | -1.24 | 0.998 | 23.55 | 23.61 | -1.56 | 0.998 | 21.25 | 21.26 | 0.53 | 1 | 42
Bundall WD maximum demand | 18.87 | 19.06 | -2.72 | 0.99 | 16.14 | 17.21 | 5.97 | 0.938 | 17.21 | 18.35 | 6.36 | 0.938 | 16.29 | 16.3 | 0.68 | 0.999 | 42
Bundall WN maximum demand | 19.15 | 19.29 | -2.31 | 0.993 | 15.72 | 16.56 | 5.21 | 0.949 | 16.76 | 17.65 | 5.55 | 0.949 | 15.86 | 15.87 | 0.42 | 1 | 42
Bundamba SD maximum demand | 35.99 | 36.28 | 4.61 | 0.992 | 33.98 | 35.31 | 9.59 | 0.962 | 37.47 | 38.94 | 10.58 | 0.962 | 33.9 | 34 | 2.68 | 0.997 | 120
Bundamba SN maximum demand | 35.29 | 35.74 | 5.67 | 0.987 | 33.17 | 34.28 | 8.64 | 0.968 | 36.58 | 37.8 | 9.53 | 0.968 | 33.09 | 33.15 | 2.02 | 0.998 | 120
Bundamba WD maximum demand | 30.73 | 30.9 | 3.2 | 0.995 | 30.08 | 30.89 | 7.02 | 0.974 | 31.28 | 32.12 | 7.3 | 0.974 | 30.94 | 30.94 | 0.26 | 1 | 120
Bundamba WN maximum demand | 30.48 | 30.55 | 2.05 | 0.998 | 32.63 | 33.45 | 7.37 | 0.975 | 33.93 | 34.78 | 7.66 | 0.975 | 33.56 | 33.57 | 0.86 | 1 | 120
Bunyaville SD maximum demand | 22.2049 | 22.2442 | -1.3219 | 0.99823 | 0 | 0 | 0 |  | 0 | 0 | 0
Bunyaville SN maximum demand | 23.0695 | 23.0981 | -1.1477 | 0.99876 | 0 | 0 | 0 |  | 0 | 0 | 0
Bunyaville WD maximum demand | 17.454 | 18.168 | -5.0433 | 0.9607 | 0 | 0 | 0 |  | 0 | 0 | 0
Bunyaville WN maximum demand | 21.1432 | 21.505 | -3.928 | 0.98318 | 0 | 0 | 0 |  | 0 | 0 | 0
Buranda SD maximum demand | 31.9 | 34.45 | 13 | 0.926 | 17.06 | 17.7 | 4.74 | 0.964 | 17.89 | 18.57 | 4.97 | 0.964 | 17.03 | 17.67 | 4.73 | 0.964 | 50
Buranda SN maximum demand | 30.7 | 32.8 | 11.55 | 0.936 | 14.1 | 14.54 | 3.54 | 0.97 | 14.79 | 15.25 | 3.72 | 0.97 | 14.57 | 15.02 | 3.66 | 0.97 | 50
Buranda WD maximum demand | 23.09 | 23.65 | 5.13 | 0.976 | 11.08 | 11.1 | 0.59 | 0.999 | 12.62 | 12.64 | 0.67 | 0.999 | 15.7 | 15.72 | 0.84 | 0.999 | 50
Buranda WN maximum demand | 24.75 | 25.44 | 5.87 | 0.973 | 10.52 | 10.52 | 0 | 1 | 11.98 | 11.98 | 0 | 1 | 15.19 | 15.19 | 0 | 1 | 50
Burleigh Heads SD maximum demand | 58.73 | 59.98 | 12.18 | 0.979 | 46.02 | 46.33 | 5.39 | 0.993 | 50.75 | 51.1 | 5.95 | 0.993 | 44.77 | 44.78 | 0.81 | 1 | 120
Burleigh Heads SN maximum demand | 56.56 | 57.04 | 7.42 | 0.991 | 45.64 | 45.72 | 2.71 | 0.998 | 50.33 | 50.42 | 2.99 | 0.998 | 44.45 | 44.57 | 3.18 | 0.997 | 120
Burleigh Heads WD maximum demand | 59.69 | 59.7 | 1.04 | 1 | 44.33 | 44.85 | 6.8 | 0.988 | 47.57 | 48.13 | 7.3 | 0.988 | 45.42 | 45.59 | 3.85 | 0.996 | 120
Burleigh Heads WN maximum demand | 62.9 | 62.9 | 0.19 | 1 | 48.67 | 49.08 | 6.31 | 0.992 | 52.23 | 52.66 | 6.78 | 0.992 | 49.91 | 50 | 2.85 | 0.998 | 120
Burpengary SD maximum demand | 30.97 | 31.11 | 2.96 | 0.995 | 20.36 | 21.09 | 5.52 | 0.965 | 24.4 | 25.28 | 6.62 | 0.965 | 22.55 | 22.58 | 1 | 0.999 | 50
Burpengary SN maximum demand | 31.83 | 31.9 | 2.01 | 0.998 | 20.86 | 21.54 | 5.39 | 0.968 | 25 | 25.82 | 6.46 | 0.968 | 23.11 | 23.11 | 0.34 | 1 | 50
Burpengary WD maximum demand | 23.51 | 23.63 | -2.45 | 0.995 | 14.04 | 14.11 | 1.46 | 0.995 | 15.21 | 15.29 | 1.58 | 0.995 | 15.57 | 15.68 | 1.87 | 0.993 | 50
Burpengary WN maximum demand | 26.29 | 26.42 | -2.59 | 0.995 | 15.9 | 16.06 | 2.24 | 0.99 | 17.23 | 17.4 | 2.42 | 0.99 | 17.64 | 17.82 | 2.55 | 0.99 | 50
Caboolture SD maximum demand | 16.24 | 17.22 | 5.72 | 0.943 | 16.19 | 17.17 | 5.74 | 0.943 | 18.02 | 19.12 | 6.39 | 0.943 | 19.28 | 19.45 | 2.56 | 0.991 | 25
Caboolture SN maximum demand | 16.23 | 16.89 | 4.65 | 0.961 | 15.88 | 16.54 | 4.63 | 0.96 | 17.68 | 18.42 | 5.15 | 0.96 | 18.86 | 18.87 | 0.69 | 0.999 | 25
Caboolture WD maximum demand | 13.21 | 13.26 | 1.19 | 0.996 | 11.63 | 11.82 | 2.13 | 0.984 | 12.58 | 12.79 | 2.3 | 0.984 | 14.71 | 15.1 | 3.44 | 0.974 | 25
Caboolture WN maximum demand | 14.54 | 14.6 | 1.36 | 0.996 | 12.56 | 12.77 | 2.3 | 0.984 | 13.59 | 13.82 | 2.49 | 0.984 | 16.05 | 16.34 | 3.1 | 0.982 | 25
Caboolture West SD maximum demand | 31.1 | 31.99 | 7.49 | 0.972 | 23.95 | 23.97 | 0.87 | 0.999 | 27.96 | 27.98 | 1.02 | 0.999 | 22.58 | 22.64 | 1.66 | 0.997 | 37
Caboolture West SN maximum demand | 29.9 | 30.59 | 6.48 | 0.977 | 24.04 | 24.04 | 0.2 | 1 | 28.06 | 28.06 | 0.24 | 1 | 22.84 | 22.86 | 0.91 | 0.999 | 37
Caboolture West WD maximum demand | 24.17 | 24.18 | 0.72 | 1 | 19.83 | 20.06 | -3.05 | 0.988 | 21.48 | 21.73 | -3.3 | 0.988 | 18.35 | 18.48 | 2.15 | 0.993 | 37
Caboolture West WN maximum demand | 26.36 | 26.39 | 1.16 | 0.999 | 21.04 | 21.13 | 2.05 | 0.995 | 22.79 | 22.9 | 2.22 | 0.995 | 18.6 | 18.68 | 1.75 | 0.996 | 37
Cades County SD maximum demand | 72 | 73.42 | 14.4 | 0.981 | 55.28 | 55.82 | 7.75 | 0.99 | 62.98 | 63.59 | 8.83 | 0.99 | 57.73 | 57.82 | 3.31 | 0.998 | 120
Cades County SN maximum demand | 68.76 | 69.54 | 10.35 | 0.989 | 52.46 | 52.81 | 5.99 | 0.994 | 59.77 | 60.15 | 6.82 | 0.994 | 54.83 | 54.84 | 0.94 | 1 | 120
Cades County WD maximum demand | 54.99 | 54.99 | -0.92 | 1 | 37.21 | 37.7 | 6.07 | 0.987 | 40.05 | 40.58 | 6.53 | 0.987 | 40.85 | 40.88 | 1.7 | 0.999 | 120
Cades County WN maximum demand | 61.06 | 61.08 | -1.53 | 1 | 41.79 | 42.39 | 7.13 | 0.986 | 44.98 | 45.63 | 7.67 | 0.986 | 45.92 | 45.94 | 1.06 | 1 | 120
Calamvale SD maximum demand | 27.06 | 27.06 | 0.45 | 1 | 33.4 | 33.53 | 2.93 | 0.996 | 36.62 | 36.76 | 3.22 | 0.996 | 34.05 | 34.06 | 0.5 | 1 | 50
Calamvale SN maximum demand | 26.84 | 26.84 | 0.16 | 1 | 32.79 | 32.93 | 3.02 | 0.996 | 35.95 | 36.1 | 3.31 | 0.996 | 33.43 | 33.43 | 0.05 | 1 | 50
Calamvale WD maximum demand | 21.56 | 21.98 | -4.3 | 0.981 | 25.27 | 25.47 | 3.17 | 0.992 | 27.26 | 27.47 | 3.42 | 0.992 | 27.82 | 28.31 | 5.24 | 0.983 | 50
Calamvale WN maximum demand | 23.75 | 23.98 | -3.28 | 0.991 | 29.83 | 30.06 | 3.67 | 0.993 | 32.18 | 32.42 | 3.96 | 0.993 | 32.84 | 32.86 | 1.11 | 0.999 | 50
Caloundra SD maximum demand | 58.91 | 61.55 | 17.84 | 0.957 | 38.67 | 40.75 | 12.85 | 0.949 | 42.01 | 44.27 | 13.95 | 0.949 | 38.61 | 38.97 | 5.31 | 0.991 | 120
Caloundra SN maximum demand | 58.12 | 60.21 | 15.75 | 0.965 | 40.41 | 41.76 | 10.54 | 0.968 | 43.9 | 45.36 | 11.45 | 0.968 | 40.37 | 40.59 | 4.23 | 0.995 | 120
Caloundra WD maximum demand | 49.52 | 49.72 | 4.47 | 0.996 | 37.99 | 38.72 | 7.45 | 0.981 | 40.47 | 41.25 | 7.94 | 0.981 | 40.41 | 40.66 | 4.5 | 0.994 | 120
Caloundra WN maximum demand | 54.48 | 54.77 | 5.56 | 0.995 | 44.28 | 44.94 | 7.64 | 0.985 | 47.17 | 47.87 | 8.14 | 0.985 | 47.1 | 47.1 | 0.37 | 1 | 120
Camp Hill SD maximum demand | 40.64 | 41.85 | 10 | 0.971 | 24.97 | 26.37 | 8.49 | 0.947 | 30.71 | 32.44 | 10.45 | 0.947 | 28.14 | 28.18 | 1.38 | 0.999 | 50
Camp Hill SN maximum demand | 42.71 | 44.16 | 11.22 | 0.967 | 27.14 | 28.7 | 9.33 | 0.946 | 33.38 | 35.3 | 11.48 | 0.946 | 30.59 | 30.71 | 2.67 | 0.996 | 50
Camp Hill WD maximum demand | 35.08 | 35.25 | 3.49 | 0.995 | 23.58 | 24.25 | 5.65 | 0.972 | 26.94 | 27.7 | 6.46 | 0.972 | 27.03 | 27.21 | 3.19 | 0.993 | 50
Camp Hill WN maximum demand | 43.62 | 44.28 | 7.62 | 0.985 | 28.06 | 29.08 | 7.63 | 0.965 | 32.06 | 33.23 | 8.72 | 0.965 | 32.17 | 32.17 | 0.05 | 1 | 50
Canungra SD maximum demand | 4.61 | 4.67 | -0.69 | 0.989 | 0 | 0 | 0 |  | 0 | 0 | 0
Canungra SN maximum demand | 5.24 | 5.32 | -0.89 | 0.986 | 0 | 0 | 0 |  | 0 | 0 | 0
Canungra WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Canungra WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Capalaba SD maximum demand | 36.29 | 36.7 | 5.52 | 0.989 | 28.5 | 28.67 | 3.13 | 0.994 | 31.62 | 31.81 | 3.47 | 0.994 | 13.05 | 13.14 | 1.54 | 0.993 | 37
Capalaba SN maximum demand | 34.83 | 35.04 | 3.8 | 0.994 | 27.25 | 27.29 | 1.46 | 0.999 | 30.24 | 30.28 | 1.62 | 0.999 | 12.81 | 12.86 | 1.11 | 0.996 | 37
Capalaba WD maximum demand | 27.98 | 28.1 | -2.52 | 0.996 | 21.34 | 21.37 | -1.11 | 0.999 | 22.81 | 22.85 | -1.19 | 0.999 | 22.63 | 23.09 | 4.61 | 0.98 | 37
Capalaba WN maximum demand | 31.35 | 31.42 | -2.12 | 0.998 | 21.66 | 21.75 | 1.92 | 0.996 | 23.16 | 23.25 | 2.05 | 0.996 | 22.97 | 23.17 | 3.09 | 0.991 | 37
Capalaba South SD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 19.47 | 20.13 | 5.13 | 0.967 | 50
Capalaba South SN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 18.72 | 19.19 | 4.21 | 0.976 | 50
Capalaba South WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | [5 empty] | 50
Capalaba South WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | [5 empty] | 50
Carole Park SD maximum demand | 21.57 | 21.78 | -3.04 | 0.99 | 20.34 | 21.23 | 6.09 | 0.958 | 24.26 | 25.33 | 7.26 | 0.958 | 19.44 | 19.44 | 0.25 | 1 | 50
Carole Park SN maximum demand | 21.24 | 21.57 | -3.77 | 0.985 | 19.55 | 20.11 | 4.73 | 0.972 | 23.31 | 23.99 | 5.65 | 0.972 | 18.62 | 19.17 | 4.53 | 0.972 | 50
Carole Park WD maximum demand | 21.39 | 22.08 | -5.44 | 0.969 | 18.33 | 18.53 | -2.73 | 0.989 | 19.76 | 19.98 | -2.95 | 0.989 | 19.54 | 19.86 | 3.55 | 0.984 | 50
Carole Park WN maximum demand | 22.42 | 23.17 | -5.86 | 0.968 | 18.83 | 19.01 | -2.62 | 0.99 | 20.3 | 20.5 | -2.83 | 0.99 | 20.07 | 20.37 | 3.46 | 0.985 | 50
Carole Park Central SD maximum demand | 29.25 | 33.45 | 16.22 | 0.875 | 20.54 | 21.73 | 7.1 | 0.945 | 21.98 | 23.26 | 7.6 | 0.945 | 19.75 | 21.58 | 8.69 | 0.915 | 50
Carole Park Central SN maximum demand | 27.04 | 30.53 | 14.18 | 0.886 | 19.92 | 20.41 | 4.44 | 0.976 | 21.32 | 21.84 | 4.76 | 0.976 | 19.15 | 20.42 | 7.09 | 0.938 | 50
Carole Park Central WD maximum demand | 26.9 | 29.67 | 12.53 | 0.907 | 20.22 | 22.91 | 10.79 | 0.882 | 19.95 | 22.61 | 10.64 | 0.882 | 19.62 | 20.85 | 7.07 | 0.941 | 50
Carole Park Central WN maximum demand | 25.54 | 27.85 | 11.11 | 0.917 | 20.57 | 22.94 | 10.16 | 0.897 | 20.3 | 22.64 | 10.03 | 0.897 | 19.96 | 21.15 | 6.99 | 0.944 | 50
Carpendale SD maximum demand | 0.94 | 0.97 | -0.28 | 0.959 | 1.41 | 1.45 | 0.34 | 0.972 | 1.52 | 1.57 | 0.37 | 0.972 | 1.38 | 1.45 | 0.44 | 0.952 | 8
Carpendale SN maximum demand | 0.96 | 1.01 | -0.3 | 0.955 | 1.49 | 1.52 | 0.32 | 0.977 | 1.61 | 1.64 | 0.35 | 0.977 | 1.45 | 1.51 | 0.43 | 0.959 | 8
Carpendale WD maximum demand | 0.8 | 0.93 | -0.47 | 0.862 | 0.94 | 0.95 | 0 | 1 | 1.11 | 1.11 | -0.01 | 1 | 1.09 | 1.13 | 0.28 | 0.97 | 8
Carpendale WN maximum demand | 0.96 | 1.04 | -0.4 | 0.922 | 1.13 | 1.13 | 0.04 | 0.999 | 1.32 | 1.32 | 0.04 | 0.999 | 1.31 | 1.33 | 0.26 | 0.98 | 8
Carseldine SD maximum demand | 18.16 | 18.64 | 4.21 | 0.974 | 0 | 0 | 0 |  | 0 | 0 | 0
Carseldine SN maximum demand | 17.12 | 17.49 | 3.57 | 0.979 | 0 | 0 | 0 |  | 0 | 0 | 0
Carseldine WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Carseldine WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Cedar Creek SD maximum demand | 2.67 | 3.09 | 1.56 | 0.864 | 0 | 0 | 0 |  | 0 | 0 | 0
Cedar Creek SN maximum demand | 2.63 | 2.97 | 1.39 | 0.885 | 0 | 0 | 0 |  | 0 | 0 | 0
Cedar Creek WD maximum demand | 2.3 | 2.52 | 1.04 | 0.912 | 0 | 0 | 0 |  | 0 | 0 | 0
Cedar Creek WN maximum demand | 2.43 | 2.64 | 1.02 | 0.922 | 0 | 0 | 0 |  | 0 | 0 | 0
Charlotte St SD maximum demand | 142.41 | 143.12 | 14.29 | 0.995 | 90.12 | 91.28 | 14.52 | 0.987 | 102.75 | 104.07 | 16.55 | 0.987 | 92.93 | 92.93 | 0.98 | 1 | 180
Charlotte St SN maximum demand | 119.42 | 119.49 | 3.97 | 0.999 | 81 | 81.65 | 10.32 | 0.992 | 92.35 | 93.09 | 11.77 | 0.992 | 83.53 | 83.57 | 2.72 | 0.999 | 180
Charlotte St WD maximum demand | 98.94 | 99.41 | -9.66 | 0.995 | 67.66 | 68.56 | 11.1 | 0.987 | 69.5 | 70.43 | 11.4 | 0.987 | 68.36 | 68.39 | 2.03 | 1 | 180
Charlotte St WN maximum demand | 90.57 | 91.71 | -14.38 | 0.988 | 63.09 | 63.86 | 9.88 | 0.988 | 64.81 | 65.6 | 10.15 | 0.988 | 63.75 | 63.95 | 5.01 | 0.997 | 180
Chermside SD maximum demand | 47.33 | 48.26 | 9.43 | 0.981 | 36.86 | 37.3 | 5.75 | 0.988 | 42.78 | 43.29 | 6.67 | 0.988 | 38.53 | 38.57 | 1.71 | 0.999 | 65
Chermside SN maximum demand | 44.51 | 45.14 | 7.51 | 0.986 | 35.18 | 35.48 | 4.66 | 0.991 | 40.83 | 41.18 | 5.41 | 0.991 | 36.77 | 36.78 | 0.53 | 1 | 65
Chermside WD maximum demand | 32.36 | 32.47 | -2.61 | 0.997 | 28.48 | 29.19 | 6.4 | 0.976 | 31.49 | 32.27 | 7.07 | 0.976 | 31.02 | 31.08 | 1.99 | 0.998 | 65
Chermside WN maximum demand | 35.32 | 35.39 | -2.23 | 0.998 | 29.16 | 29.86 | 6.45 | 0.976 | 32.24 | 33.02 | 7.13 | 0.976 | 31.75 | 31.76 | 0.83 | 1 | 65
Clayfield SD maximum demand | 20.81 | 21.72 | 6.24 | 0.958 | 16.83 | 16.89 | 1.44 | 0.996 | 20.09 | 20.16 | 1.72 | 0.996 | 18.26 | 18.67 | 3.88 | 0.978 | 34
Clayfield SN maximum demand | 18.71 | 19.27 | 4.61 | 0.971 | 15.32 | 15.32 | 0.32 | 1 | 18.28 | 18.28 | 0.38 | 1 | 16.62 | 16.82 | 2.61 | 0.988 | 34
Clayfield WD maximum demand | 14.7 | 14.72 | 0.76 | 0.999 | 13.89 | 14.4 | 3.81 | 0.964 | 15.44 | 16.01 | 4.24 | 0.964 | 14.77 | 15.58 | 4.94 | 0.948 | 34
Clayfield WN maximum demand | 15.65 | 15.71 | 1.35 | 0.996 | 14.61 | 15.19 | 4.18 | 0.961 | 16.24 | 16.89 | 4.65 | 0.961 | 15.53 | 15.53 | 0.28 | 1 | 34
Cleveland SD maximum demand | 31.65 | 32.08 | 5.23 | 0.987 | 25.01 | 26.69 | 9.32 | 0.937 | 27.52 | 29.37 | 10.25 | 0.937 | 17.74 | 17.91 | 2.46 | 0.991 | 55
Cleveland SN maximum demand | 34.53 | 34.93 | 5.3 | 0.988 | 26.24 | 27.74 | 9.01 | 0.946 | 28.88 | 30.53 | 9.92 | 0.946 | 18.47 | 18.59 | 2.05 | 0.994 | 55
Cleveland WD maximum demand | 30.1 | 30.1 | 0.62 | 1 | 22.53 | 23.08 | 4.99 | 0.976 | 25.17 | 25.78 | 5.58 | 0.976 | 22.08 | 22.11 | 1.11 | 0.999 | 55
Cleveland WN maximum demand | 33.21 | 33.22 | 0.8 | 1 | 24.88 | 25.43 | 5.28 | 0.978 | 27.78 | 28.4 | 5.89 | 0.978 | 24.26 | 24.29 | 1.27 | 0.999 | 55
Coolum SD maximum demand | 33.37 | 33.63 | 4.19 | 0.992 | 17.28 | 17.89 | 4.63 | 0.966 | 19.31 | 19.99 | 5.17 | 0.966 | 17.55 | 17.58 | 0.92 | 0.999 | 50
Coolum SN maximum demand | 36.79 | 36.94 | 3.33 | 0.996 | 17.95 | 18.41 | 4.06 | 0.975 | 20.06 | 20.56 | 4.53 | 0.975 | 18.24 | 18.24 | 0.12 | 1 | 50
Coolum WD maximum demand | 31.32 | 31.37 | -1.79 | 0.998 | 18.11 | 18.31 | 2.73 | 0.989 | 20.39 | 20.62 | 3.08 | 0.989 | 20.27 | 20.65 | 3.94 | 0.982 | 50
Coolum WN maximum demand | 36.61 | 36.62 | -1.19 | 0.999 | 20.42 | 20.6 | 2.73 | 0.991 | 22.99 | 23.2 | 3.08 | 0.991 | 22.86 | 23.21 | 4.05 | 0.985 | 50
Coomera SD maximum demand | 33.31 | 33.51 | 3.63 | 0.994 | 23.08 | 23.08 | 0.22 | 1 | 28.04 | 28.04 | 0.26 | 1 | 27.33 | 27.55 | 3.5 | 0.992 | 50
Coomera SN maximum demand | 30.07 | 30.12 | 1.61 | 0.999 | 22.36 | 22.36 | -0.04 | 1 | 27.17 | 27.17 | -0.05 | 1 | 26.63 | 26.74 | 2.41 | 0.996 | 50
Coomera WD maximum demand | 21.34 | 21.75 | -4.21 | 0.981 | 17.19 | 17.3 | 2 | 0.993 | 19.17 | 19.3 | 2.23 | 0.993 | 18.93 | 19.6 | 5.05 | 0.966 | 50
Coomera WN maximum demand | 21.75 | 22.25 | -4.7 | 0.977 | 18.47 | 18.57 | 1.98 | 0.994 | 20.6 | 20.71 | 2.2 | 0.994 | 20.85 | 21.47 | 5.11 | 0.971 | 50
Coominya SD maximum demand | 5.63 | 5.7 | 0.89 | 0.988 | 6.05 | 6.13 | -0.94 | 0.988 | 6.05 | 6.13 | -0.94 | 0.988 | 5.45 | 5.49 | 0.59 | 0.994 | 10
Coominya SN maximum demand | 4.7 | 4.8 | 1.02 | 0.977 | 6.02 | 6.09 | -0.94 | 0.988 | 6.02 | 6.09 | -0.94 | 0.988 | 5.42 | 5.49 | 0.86 | 0.988 | 10
Coominya WD maximum demand | 4.59 | 4.6 | 0.29 | 0.998 | 3.96 | 3.98 | 0.4 | 0.995 | 3.93 | 3.95 | 0.4 | 0.995 | 3.87 | 3.88 | 0.27 | 0.998 | 10
Coominya WN maximum demand | 3.94 | 3.95 | 0.33 | 0.997 | 3.69 | 3.7 | 0.27 | 0.997 | 3.66 | 3.67 | 0.27 | 0.997 | 3.61 | 3.61 | 0.24 | 0.998 | 10
Cooneana SD maximum demand | 10.23 | 12 | 6.27 | 0.853 | 2.34 | 2.4 | 0.56 | 0.973 | 2.78 | 2.86 | 0.66 | 0.973 | 3.85 | 4.39 | 2.12 | 0.876 | 30
Cooneana SN maximum demand | 6.69 | 7.64 | 3.7 | 0.875 | 2.31 | 2.38 | 0.57 | 0.971 | 2.74 | 2.82 | 0.68 | 0.971 | 3.64 | 4.14 | 1.99 | 0.878 | 30
Cooneana WD maximum demand | 7.94 | 9.14 | 4.53 | 0.869 | 1.95 | 2.09 | 0.75 | 0.933 | 1.93 | 2.07 | 0.75 | 0.933 | 3.73 | 4.24 | 2.02 | 0.88 | 30
Cooneana WN maximum demand | 5.68 | 6.25 | 2.61 | 0.909 | 2 | 2.09 | 0.61 | 0.957 | 1.98 | 2.07 | 0.6 | 0.957 | 3.56 | 3.98 | 1.78 | 0.894 | 30
Coopers Plains SD maximum demand | 21.23 | 21.54 | 3.65 | 0.986 | 21.26 | 22.56 | 7.56 | 0.942 | 22.55 | 23.93 | 8.02 | 0.942 | 24.91 | 25.41 | 5.01 | 0.98 | 40
Coopers Plains SN maximum demand | 15.49 | 15.49 | -0.39 | 1 | 15.55 | 16.11 | 4.18 | 0.966 | 16.5 | 17.09 | 4.43 | 0.966 | 16.13 | 16.8 | 4.67 | 0.961 | 40
Coopers Plains WD maximum demand | 15.04 | 15.15 | -1.77 | 0.993 | 17.35 | 17.97 | 4.69 | 0.965 | 18.19 | 18.84 | 4.91 | 0.965 | 17.94 | 18.46 | 4.33 | 0.972 | 40
Coopers Plains WN maximum demand | 13.35 | 13.64 | -2.79 | 0.979 | 15.34 | 15.76 | 3.65 | 0.973 | 16.07 | 16.52 | 3.83 | 0.973 | 15.86 | 16.18 | 3.22 | 0.98 | 40
Cooran SD maximum demand | 8.65 | 8.65 | 0.17 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5.38 | 5.97 | 2.58 | 0.902 | 30
Cooran SN maximum demand | 8.89 | 8.89 | -0.21 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5.52 | 6.02 | 2.4 | 0.917 | 30
Cooran WD maximum demand | 6.97 | 7.24 | -1.94 | 0.964 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 6.41 | 6.73 | 2.05 | 0.952 | 30
Cooran WN maximum demand | 7.59 | 7.84 | -1.98 | 0.968 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 7.29 | 7.6 | 2.14 | 0.96 | 30
Cooroy SD maximum demand | 7.01 | 7.29 | 2.02 | 0.961 | 4.76 | 4.83 | -0.85 | 0.985 | 5.17 | 5.25 | -0.92 | 0.985 | 4.73 | 4.87 | 1.15 | 0.972 | 25
Cooroy SN maximum demand | 7.19 | 7.45 | 1.94 | 0.966 | 4.8 | 4.9 | -0.98 | 0.98 | 5.22 | 5.33 | -1.06 | 0.98 | 4.77 | 4.91 | 1.13 | 0.973 | 25
Cooroy WD maximum demand | 6.09 | 6.2 | 1.18 | 0.982 | 4.43 | 4.46 | 0.52 | 0.993 | 4.93 | 4.96 | 0.58 | 0.993 | 4.98 | 5.02 | 0.67 | 0.991 | 25
Cooroy WN maximum demand | 6.91 | 7.06 | 1.44 | 0.979 | 5.45 | 5.49 | 0.61 | 0.994 | 6.06 | 6.1 | 0.68 | 0.994 | 6.12 | 6.19 | 0.91 | 0.989 | 25
Coorparoo SD maximum demand | 18.49 | 18.53 | 1.35 | 0.997 | 18.78 | 19.1 | 3.49 | 0.983 | 20.92 | 21.28 | 3.89 | 0.983 | 20.03 | 20.03 | 0.52 | 1 | 26
Coorparoo SN maximum demand | 16.66 | 16.66 | -0.52 | 1 | 17.84 | 18.05 | 2.75 | 0.988 | 19.86 | 20.1 | 3.06 | 0.988 | 19.11 | 19.64 | 4.51 | 0.973 | 26
Coorparoo WD maximum demand | 13.21 | 13.86 | -4.2 | 0.953 | 12.54 | 13.1 | 3.79 | 0.957 | 13.78 | 14.39 | 4.16 | 0.957 | 17.84 | 17.9 | 1.41 | 0.997 | 26
Coorparoo WN maximum demand | 14.75 | 15.17 | -3.53 | 0.973 | 13.55 | 14.19 | 4.21 | 0.955 | 14.89 | 15.59 | 4.62 | 0.955 | 19.36 | 19.44 | 1.69 | 0.996 | 26
Cornubia SD maximum demand | 15.23 | 15.57 | 3.25 | 0.978 | 9.63 | 9.93 | 2.43 | 0.969 | 11.87 | 12.24 | 3 | 0.969 | 10.7 | 11.03 | 2.66 | 0.97 | 25
Cornubia SN maximum demand | 15.95 | 16.17 | 2.67 | 0.986 | 9.95 | 10.17 | 2.09 | 0.979 | 12.27 | 12.53 | 2.57 | 0.979 | 11.07 | 11.29 | 2.24 | 0.98 | 25
Cornubia WD maximum demand | 12.4 | 12.43 | -0.82 | 0.998 | 8.84 | 8.91 | 1.11 | 0.992 | 10.14 | 10.22 | 1.27 | 0.992 | 10.01 | 10.13 | 1.56 | 0.988 | 25
Cornubia WN maximum demand | 14.37 | 14.37 | -0.36 | 1 | 9.69 | 9.72 | 0.76 | 0.997 | 11.11 | 11.14 | 0.87 | 0.997 | 10.97 | 11.04 | 1.29 | 0.993 | 25
Crestmead SD maximum demand | 34.62 | 34.67 | 1.95 | 0.998 | 24.17 | 24.17 | 0.16 | 1 | 27.01 | 27.01 | 0.18 | 1 | 26.38 | 26.82 | 4.87 | 0.983 | 50
Crestmead SN maximum demand | 32.26 | 32.32 | -1.89 | 0.998 | 23.85 | 23.85 | -0.43 | 1 | 26.65 | 26.65 | -0.48 | 1 | 26.05 | 26.21 | 2.88 | 0.994 | 50
Crestmead WD maximum demand | 32.78 | 32.89 | -2.65 | 0.997 | 22.04 | 22.21 | 2.72 | 0.992 | 23.14 | 23.32 | 2.85 | 0.992 | 22.94 | 22.94 | 0.64 | 1 | 50
Crestmead WN maximum demand | 31.08 | 31.6 | -5.73 | 0.983 | 22.41 | 22.45 | 1.31 | 0.998 | 23.53 | 23.57 | 1.37 | 0.998 | 23.33 | 23.86 | 4.99 | 0.978 | 50
Currimundi SD maximum demand | 16.32 | 16.74 | 3.69 | 0.975 | 15.53 | 15.67 | 2.11 | 0.991 | 17.25 | 17.41 | 2.35 | 0.991 | 18.46 | 18.76 | 3.38 | 0.984 | 60
Currimundi SN maximum demand | 16.82 | 17.09 | 3 | 0.984 | 18.83 | 19.02 | 2.63 | 0.99 | 20.93 | 21.13 | 2.92 | 0.99 | 22.16 | 22.48 | 3.8 | 0.986 | 60
Currimundi WD maximum demand | 16.26 | 16.26 | 0.3 | 1 | 16.12 | 16.15 | 0.98 | 0.998 | 17.38 | 17.42 | 1.05 | 0.998 | 17.66 | 17.72 | 1.39 | 0.997 | 60
Currimundi WN maximum demand | 18 | 18.02 | 0.93 | 0.999 | 19.08 | 19.14 | 1.49 | 0.997 | 20.57 | 20.63 | 1.61 | 0.997 | 20.9 | 21 | 2.06 | 0.995 | 60
Currumbin SD maximum demand |  |  |  |  | 17.84 | 18.71 | 5.63 | 0.954 | 20.88 | 21.89 | 6.59 | 0.954 | 18.98 | 19.07 | 1.92 | 0.995 | 40
Currumbin SN maximum demand |  |  |  |  | 17.27 | 17.28 | -0.26 | 1 | 20.21 | 20.22 | -0.31 | 1 | 18.38 | 19.11 | 5.24 | 0.962 | 40
Currumbin WD maximum demand |  |  |  |  | 19.88 | 20.28 | 3.98 | 0.981 | 21.58 | 22.01 | 4.32 | 0.981 | 20.47 | 20.47 | 0.31 | 1 | 40
Currumbin WN maximum demand |  |  |  |  | 22.62 | 23.06 | 4.5 | 0.981 | 24.55 | 25.03 | 4.88 | 0.981 | 23.34 | 23.84 | 4.89 | 0.979 | 40
Currumbin Package SD maximum demand | 20.25 | 20.25 | 0.57 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0
Currumbin Package SN maximum demand | 20.55 | 20.61 | -1.54 | 0.997 | 0 | 0 | 0 |  | 0 | 0 | 0
Currumbin Package WD maximum demand | 20.65 | 20.8 | -2.45 | 0.993 | 0 | 0 | 0 |  | 0 | 0 | 0
Currumbin Package WN maximum demand | 21.9 | 22.12 | -3.09 | 0.99 | 0 | 0 | 0 |  | 0 | 0 | 0
Darra SD maximum demand | 27.19 | 27.39 | 3.31 | 0.993 | 18.46 | 21.48 | 10.97 | 0.86 | 20.24 | 23.55 | 12.03 | 0.86 | 20.47 | 21.99 | 8.01 | 0.931 | 50
Darra SN maximum demand | 20.49 | 20.61 | -2.17 | 0.994 | 14.56 | 16.79 | 8.36 | 0.867 | 15.97 | 18.41 | 9.17 | 0.867 | 16.69 | 17.53 | 5.37 | 0.952 | 50
Darra WD maximum demand | 22.19 | 22.21 | -0.77 | 0.999 | 18.03 | 18.64 | 4.71 | 0.968 | 19.01 | 19.65 | 4.97 | 0.968 | 18 | 18.94 | 5.9 | 0.95 | 50
Darra WN maximum demand | 19.35 | 19.72 | -3.82 | 0.981 | 16.72 | 17.14 | 3.78 | 0.975 | 17.63 | 18.07 | 3.98 | 0.975 | 16.89 | 17.46 | 4.43 | 0.967 | 50
Deception Bay SD maximum demand | 24.12 | 24.16 | 1.36 | 0.998 | 19.96 | 20.06 | 2.03 | 0.995 | 23.33 | 23.45 | 2.38 | 0.995 | 22.36 | 22.82 | 4.55 | 0.98 | 36
Deception Bay SN maximum demand | 23.61 | 23.62 | 0.86 | 0.999 | 20.26 | 20.3 | 1.28 | 0.998 | 23.68 | 23.73 | 1.49 | 0.998 | 22.59 | 22.87 | 3.59 | 0.988 | 36
Deception Bay WD maximum demand | 21.78 | 21.84 | -1.65 | 0.997 | 17.27 | 17.3 | -1.01 | 0.998 | 19.45 | 19.48 | -1.14 | 0.998 | 19.32 | 19.33 | 0.7 | 0.999 | 36
Deception Bay WN maximum demand | 25.23 | 25.26 | -1.41 | 0.998 | 18.05 | 18.45 | 3.84 | 0.978 | 20.32 | 20.78 | 4.33 | 0.978 | 20.19 | 20.19 | 0.33 | 1 | 36
Doboy SD maximum demand | 21.78 | 22.85 | 6.91 | 0.953 | 14.71 | 14.87 | 2.15 | 0.989 | 17.69 | 17.87 | 2.59 | 0.989 | 15.99 | 15.99 | 0.24 | 1 | 50
Doboy SN maximum demand | 19.43 | 20.04 | 4.93 | 0.969 | 11.91 | 13.06 | 5.37 | 0.912 | 14.32 | 15.7 | 6.45 | 0.912 | 12.94 | 12.96 | 0.72 | 0.998 | 50
Doboy WD maximum demand | 16.47 | 16.86 | 3.59 | 0.977 | 10.28 | 11.38 | 4.89 | 0.903 | 11.65 | 12.9 | 5.54 | 0.903 | 11.29 | 12.5 | 5.37 | 0.903 | 50
Doboy WN maximum demand | 15.38 | 15.56 | 2.38 | 0.988 | 9.04 | 9.96 | 4.17 | 0.908 | 10.24 | 11.28 | 4.73 | 0.908 | 9.93 | 10.94 | 4.58 | 0.908 | 50
Duffield Road SD maximum demand | 21.93 | 23.1 | 7.25 | 0.95 | 18.03 | 18.06 | 0.89 | 0.999 | 22 | 22.02 | 1.09 | 0.999 | 22.49 | 22.98 | 4.69 | 0.979 | 50
Duffield Road SN maximum demand | 21.8 | 22.76 | 6.56 | 0.958 | 18.25 | 18.28 | -1 | 0.999 | 22.26 | 22.29 | -1.22 | 0.999 | 22.54 | 22.83 | 3.59 | 0.988 | 50
Duffield Road WD maximum demand | 20.09 | 20.32 | 3.04 | 0.989 | 17.58 | 17.78 | 2.67 | 0.989 | 18.84 | 19.06 | 2.86 | 0.989 | 19.82 | 19.82 | 0.3 | 1 | 50
Duffield Road WN maximum demand | 21.68 | 22.03 | 3.9 | 0.984 | 18.99 | 19.18 | 2.65 | 0.99 | 20.35 | 20.55 | 2.84 | 0.99 | 21.46 | 21.47 | 0.43 | 1 | 50
Ebbw Vale T1-T2 SD maximum demand | 1.41 | 2.04 | 1.47 | 0.694 | [12 empty] | 6
Ebbw Vale T1-T2 SN maximum demand | 1.29 | 1.84 | 1.31 | 0.702 | [12 empty] | 6
Ebbw Vale T1-T2 WD maximum demand | 1.33 | 1.9 | 1.35 | 0.699 | [12 empty] | 6
Ebbw Vale T1-T2 WN maximum demand | 1.25 | 1.72 | 1.18 | 0.728 | [12 empty] | 6
Eight Mile Plains Bus 1 SD maximum demand | 15.41 | 15.99 | 4.27 | 0.964 | 14.94 | 15.88 | 5.37 | 0.941 | 17.65 | 18.75 | 6.34 | 0.941 | 15.97 | 16.23 | 2.89 | 0.984 | 24
Eight Mile Plains Bus 1 SN maximum demand | 14.53 | 14.9 | 3.31 | 0.975 | 14.62 | 15.01 | 3.39 | 0.974 | 17.27 | 17.72 | 4.01 | 0.974 | 15.62 | 15.77 | 2.18 | 0.99 | 24
Eight Mile Plains Bus 1 WD maximum demand | 11.17 | 11.19 | -0.71 | 0.998 | 11.81 | 11.98 | 2.04 | 0.985 | 13.11 | 13.31 | 2.27 | 0.985 | 13.05 | 13.74 | 4.28 | 0.95 | 24
Eight Mile Plains Bus 1 WN maximum demand | 11.69 | 11.69 | 0 | 1 | 11.98 | 12.22 | 2.43 | 0.98 | 13.3 | 13.57 | 2.7 | 0.98 | 13.24 | 14.01 | 4.56 | 0.946 | 24
Eight Mile Plains Bus 2 SD maximum demand | 9.91 | 9.91 | 0.05 | 1 | 11.97 | 12.59 | 3.89 | 0.951 | 14.1 | 14.82 | 4.58 | 0.951 | 12.97 | 12.97 | 0.21 | 1 | 25
Eight Mile Plains Bus 2 SN maximum demand | 10.03 | 10.03 | -0.11 | 1 | 11.71 | 12.24 | 3.54 | 0.957 | 13.79 | 14.41 | 4.17 | 0.957 | 12.68 | 13.77 | 5.35 | 0.921 | 25
Eight Mile Plains Bus 2 WD maximum demand | 8.18 | 8.46 | -2.18 | 0.966 | 9.99 | 10.12 | 1.59 | 0.988 | 11.12 | 11.26 | 1.76 | 0.988 | 11.27 | 11.71 | 3.19 | 0.962 | 25
Eight Mile Plains Bus 2 WN maximum demand | 9.5 | 9.62 | -1.5 | 0.988 | 10.34 | 10.49 | 1.76 | 0.986 | 11.51 | 11.67 | 1.96 | 0.986 | 11.66 | 12.12 | 3.32 | 0.962 | 25
Enoggera SD maximum demand | 29.82 | 32.73 | 13.5 | 0.911 | 23.74 | 24.41 | 5.68 | 0.973 | 25.94 | 26.67 | 6.21 | 0.973 | 18.08 | 18.81 | 5.2 | 0.961 | 50
Enoggera SN maximum demand | 27.55 | 29.83 | 11.44 | 0.923 | 21.37 | 21.74 | 3.99 | 0.983 | 23.34 | 23.75 | 4.36 | 0.983 | 16.33 | 16.74 | 3.69 | 0.975 | 50
Enoggera WD maximum demand | 24.85 | 25.61 | 6.21 | 0.97 | 18.22 | 19.05 | 5.57 | 0.956 | 20.93 | 21.89 | 6.39 | 0.956 | 21.61 | 21.88 | 3.4 | 0.988 | 50
Enoggera WN maximum demand | 26.18 | 27.31 | 7.78 | 0.959 | 18.18 | 19 | 5.51 | 0.957 | 20.89 | 21.83 | 6.33 | 0.957 | 21.69 | 22.01 | 3.76 | 0.985 | 50
Ergon Supply SD maximum demand | 13.12 | 14.36 | 5.84 | 0.914 | 7.27 | 7.99 | 3.31 | 0.91 | 9.66 | 10.62 | 4.4 | 0.91 | 8.64 | 9.51 | 3.96 | 0.909
Ergon Supply SN maximum demand | 13.98 | 15.3 | 6.22 | 0.914 | 9.41 | 10.49 | 4.64 | 0.897 | 12.49 | 13.93 | 6.16 | 0.897 | 11.18 | 12.17 | 4.82 | 0.918
Ergon Supply WD maximum demand | 13.71 | 14.59 | 4.99 | 0.94 | 12.37 | 13.37 | 5.06 | 0.926 | 13.56 | 14.64 | 5.54 | 0.926 | 13.28 | 14.35 | 5.45 | 0.925
Ergon Supply WN maximum demand | 14.34 | 15.37 | 5.54 | 0.933 | 9.21 | 9.43 | 2.04 | 0.976 | 10.09 | 10.33 | 2.23 | 0.976 | 9.88 | 10.59 | 3.81 | 0.933
Esk SD maximum demand | 3.28 | 3.51 | 1.26 | 0.934 | 2.51 | 2.72 | 1.04 | 0.924 | 3.17 | 3.43 | 1.31 | 0.924 | 2.87 | 2.99 | 0.84 | 0.96 | 8
Esk SN maximum demand | 3.35 | 3.54 | 1.15 | 0.946 | 2.52 | 2.64 | 0.76 | 0.957 | 3.18 | 3.32 | 0.96 | 0.957 | 2.88 | 2.97 | 0.71 | 0.971 | 8
Esk WD maximum demand | 2.62 | 2.68 | 0.57 | 0.977 | 1.96 | 1.96 | 0.02 | 1 | 2.24 | 2.24 | 0.02 | 1 | 2.23 | 2.25 | 0.3 | 0.991 | 8
Esk WN maximum demand | 2.87 | 2.9 | 0.46 | 0.987 | 2.05 | 2.05 | -0.06 | 1 | 2.35 | 2.35 | -0.07 | 1 | 2.34 | 2.34 | 0.13 | 0.998 | 8
Ethanol Plant SD maximum demand | 5.38 | 6.2 | 3.08 | 0.868 | 0 | 0 | 0 |  | 0 | 0 | 0
Ethanol Plant SN maximum demand | 5.26 | 6.04 | 2.98 | 0.87 | 0 | 0 | 0 |  | 0 | 0 | 0
Ethanol Plant WD maximum demand | 2.44 | 2.79 | 1.35 | 0.874 | 0 | 0 | 0 |  | 0 | 0 | 0
Ethanol Plant WN maximum demand | 2.47 | 2.81 | 1.34 | 0.878 | 0 | 0 | 0 |  | 0 | 0 | 0
Eumundi SD maximum demand | 5.21 | 5.61 | 2.08 | 0.929 | 2.29 | 2.91 | -1.78 | 0.789 | 2.64 | 3.35 | -2.05 | 0.789 | 2.41 | 3.06 | 1.88 | 0.789 | 8
Eumundi SN maximum demand | 5.11 | 5.45 | 1.9 | 0.937 | 2.29 | 3.42 | -2.54 | 0.67 | 2.64 | 3.94 | -2.93 | 0.67 | 2.41 | 3.6 | 2.67 | 0.67 | 8
Eumundi WD maximum demand | 4.66 | 4.79 | 1.1 | 0.973 | 2.01 | 2.39 | 1.28 | 0.843 | 2.3 | 2.72 | 1.46 | 0.843 | 2.29 | 2.72 | 1.46 | 0.843 | 8
Eumundi WN maximum demand | 5.04 | 5.19 | 1.25 | 0.97 | 2.34 | 2.86 | 1.66 | 0.816 | 2.66 | 3.26 | 1.89 | 0.816 | 2.66 | 3.26 | 1.89 | 0.816 | 8
Fisherman Is A SD maximum demand | 18.29 | 19.17 | 5.74 | 0.954 | 10.53 | 12.09 | 5.94 | 0.871 | 10.53 | 12.09 | 5.94 | 0.871 | 17.93 | 19 | 6.3 | 0.943 | 36
Fisherman Is A SN maximum demand | 17.3 | 17.91 | 4.61 | 0.966 | 11.11 | 11.81 | 4.02 | 0.94 | 11.11 | 11.81 | 4.02 | 0.94 | 17.78 | 18.47 | 4.98 | 0.963 | 36
Fisherman Is A WD maximum demand | 20.68 | 23.82 | 11.82 | 0.868 | 10.08 | 12.02 | 6.56 | 0.838 | 9.88 | 11.78 | 6.43 | 0.838 | 13.07 | 13.79 | 4.4 | 0.948 | 36
Fisherman Is A WN maximum demand | 19.39 | 21.51 | 9.29 | 0.902 | 9.49 | 11.44 | 6.4 | 0.829 | 9.3 | 11.22 | 6.27 | 0.829 | 12.3 | 12.82 | 3.61 | 0.96 | 36
Fisherman Is North SD maximum demand | 12.87 | 13.2 | 2.97 | 0.974 | 0 | 0 | 0 |  | 0 | 0 | 0
Fisherman Is North SN maximum demand | 12.36 | 12.5 | 1.88 | 0.989 | 0 | 0 | 0 |  | 0 | 0 | 0
Fisherman Is North WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Fisherman Is North WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Flagstone SD maximum demand | 7.45 | 7.7 | -1.95 | 0.968 | 0 | 0 | 0 |  | 0 | 0 | 0
Flagstone SN maximum demand | 7.52 | 7.81 | -2.12 | 0.963 | 0 | 0 | 0 |  | 0 | 0 | 0
Flagstone WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Flagstone WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Flinders SD maximum demand | 5.03 | 5.13 | 1.03 | 0.98 | 4.52 | 4.61 | 0.9 | 0.981 | 5.49 | 5.59 | 1.1 | 0.981 | 4.75 | 4.83 | 0.87 | 0.984 | 10
Flinders SN maximum demand | 5.03 | 5.12 | 0.98 | 0.982 | 4.32 | 4.38 | 0.71 | 0.987 | 5.24 | 5.31 | 0.86 | 0.987 | 4.54 | 4.58 | 0.62 | 0.991 | 10
Flinders WD maximum demand | 4.87 | 5.14 | 1.64 | 0.948 | 3.38 | 3.38 | -0.16 | 0.999 | 3.91 | 3.91 | -0.18 | 0.999 | 4.33 | 4.41 | 0.83 | 0.982 | 10
Flinders WN maximum demand | 5.07 | 5.27 | 1.42 | 0.963 | 3.45 | 3.46 | -0.14 | 0.999 | 3.99 | 4 | -0.16 | 0.999 | 4.42 | 4.47 | 0.67 | 0.989 | 10
Gatton A SD maximum demand | 21.32 | 21.61 | 3.52 | 0.987 | 17.47 | 17.6 | 2.11 | 0.993 | 20.95 | 21.1 | 2.53 | 0.993 | 19.06 | 19.28 | 2.91 | 0.989 | 50
Gatton A SN maximum demand | 20.11 | 20.29 | 2.65 | 0.991 | 15.95 | 16 | 1.33 | 0.997 | 19.13 | 19.19 | 1.59 | 0.997 | 17.4 | 17.52 | 2.03 | 0.993 | 50
Gatton A WD maximum demand | 18.27 | 18.27 | -0.5 | 1 | 13.86 | 14.55 | 4.43 | 0.952 | 15.12 | 15.87 | 4.83 | 0.952 | 15.08 | 15.81 | 4.72 | 0.954 | 50
Gatton A WN maximum demand | 19.34 | 19.35 | -0.36 | 1 | 12.91 | 13.51 | 3.98 | 0.956 | 14.08 | 14.73 | 4.34 | 0.956 | 14.04 | 14.65 | 4.16 | 0.959 | 50
Gatton B SD maximum demand | 30.31 | 31.83 | 9.72 | 0.952 | 0 | 0 | 0 |  | 0 | 0 | 0
Gatton B SN maximum demand | 28.24 | 29.25 | 7.61 | 0.966 | 0 | 0 | 0 |  | 0 | 0 | 0
Gatton B WD maximum demand | 26.05 | 26.07 | 1.03 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0
Gatton B WN maximum demand | 27.43 | 27.45 | 1.04 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0
Gaven SD maximum demand | 26.79 | 26.83 | 1.35 | 0.999 | 19.9 | 19.91 | 0.41 | 1 | 23.07 | 23.07 | 0.48 | 1 | 20.76 | 20.92 | 2.57 | 0.992 | 50
Gaven SN maximum demand | 26.48 | 26.48 | -0.36 | 1 | 19.79 | 19.8 | -0.17 | 1 | 22.94 | 22.94 | -0.2 | 1 | 20.65 | 20.74 | 1.93 | 0.996 | 50
Gaven WD maximum demand | 23.27 | 23.54 | -3.55 | 0.989 | 16.93 | 17.14 | 2.69 | 0.988 | 18.74 | 18.98 | 2.98 | 0.988 | 18.71 | 19.21 | 4.35 | 0.974 | 50
Gaven WN maximum demand | 23.7 | 24.05 | -4.05 | 0.986 | 18.17 | 18.33 | 2.43 | 0.991 | 20.11 | 20.29 | 2.69 | 0.991 | 20.08 | 20.48 | 4.03 | 0.98 | 50
Geebung SD maximum demand | 37.56 | 38.03 | 6 | 0.987 | 32.18 | 32.29 | 2.69 | 0.997 | 37.35 | 37.48 | 3.13 | 0.997 | 38.85 | 39.05 | 3.98 | 0.995 | 50
Geebung SN maximum demand | 28.73 | 28.73 | 0.16 | 1 | 25.73 | 25.73 | 0.65 | 1 | 29.86 | 29.87 | 0.76 | 1 | 31.83 | 31.83 | 0.43 | 1 | 50
Geebung WD maximum demand | 26.48 | 26.49 | -0.59 | 1 | 25.73 | 27.58 | 9.93 | 0.933 | 25.47 | 27.3 | 9.83 | 0.933 | 23.98 | 23.98 | 0.07 | 1 | 50
Geebung WN maximum demand | 22.26 | 22.92 | -5.5 | 0.971 | 23.66 | 23.67 | -0.78 | 0.999 | 23.42 | 23.44 | -0.77 | 0.999 | 22.06 | 22.24 | 2.85 | 0.992 | 50
Gibson Island SD maximum demand | 21.54 | 21.55 | -0.86 | 0.999 | 19.01 | 19.04 | 0.98 | 0.999 | 20.17 | 20.2 | 1.04 | 0.999 | 20.17 | 20.32 | 2.41 | 0.993 | 40
Gibson Island SN maximum demand | 20.79 | 20.84 | -1.39 | 0.998 | 18.95 | 18.98 | 1.15 | 0.998 | 20.11 | 20.14 | 1.22 | 0.998 | 20.11 | 20.22 | 2.15 | 0.994 | 40
Gibson Island WD maximum demand | 20.84 | 20.88 | -1.27 | 0.998 | 22.14 | 22.38 | 3.24 | 0.989 | 23.77 | 24.02 | 3.48 | 0.989 | 19.13 | 19.23 | 2 | 0.995 | 40
Gibson Island WN maximum demand | 20.52 | 20.59 | -1.7 | 0.997 | 21.79 | 21.96 | 2.69 | 0.992 | 23.39 | 23.57 | 2.89 | 0.992 | 18.95 | 19.04 | 1.77 | 0.996 | 40
Glass House SD maximum demand | 7.03 | 8.09 | 4 | 0.87
Glass House SN maximum demand | 6.57 | 7.34 | 3.27 | 0.895
Glass House WD maximum demand | 6.08 | 6.84 | 3.13 | 0.889
Glass House WN maximum demand | 6.47 | 7.03 | 2.77 | 0.919
Glenore Grove SD maximum demand | 8.68 | 8.68 | -0.1 | 1 | 7.14 | 7.19 | 0.77 | 0.994 | 8.32 | 8.37 | 0.9 | 0.994 | 7.33 | 7.4 | 1.02 | 0.991 | 14
Glenore Grove SN maximum demand | 9.04 | 9.05 | -0.16 | 1 | 7.37 | 7.44 | 1.02 | 0.991 | 8.58 | 8.66 | 1.18 | 0.991 | 7.54 | 7.6 | 0.96 | 0.992 | 14
Glenore Grove WD maximum demand | 6.16 | 6.36 | -1.59 | 0.968 | 5.65 | 5.66 | -0.38 | 0.998 | 6.46 | 6.48 | -0.44 | 0.998 | 6.54 | 6.54 | 0.03 | 1 | 14
Glenore Grove WN maximum demand | 7.36 | 7.48 | -1.37 | 0.983 | 5.45 | 5.5 | -0.74 | 0.991 | 6.23 | 6.29 | -0.85 | 0.991 | 6.31 | 6.51 | 1.58 | 0.97 | 14
Goodna SD maximum demand | 11.03 | 11.04 | -0.58 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 9.28 | 10.08 | 3.93 | 0.921 | 25
Goodna SN maximum demand | 11.12 | 11.13 | -0.45 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 9.54 | 10.31 | 3.92 | 0.925 | 25
Goodna WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | [5 empty] | 25
Goodna WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | [5 empty] | 25
Goomboorian SD maximum demand | 2.06 | 2.42 | 1.28 | 0.85 | 2.04 | 2.11 | 0.55 | 0.965 | 1.98 | 2.05 | 0.54 | 0.965 | 1.81 | 1.87 | 0.49 | 0.965 | 8
Goomboorian SN maximum demand | 1.97 | 2.27 | 1.13 | 0.868 | 2.48 | 2.56 | 0.66 | 0.966 | 2.4 | 2.48 | 0.64 | 0.966 | 2.19 | 2.27 | 0.58 | 0.966 | 8
Goomboorian WD maximum demand | 1.71 | 1.86 | 0.75 | 0.916 | 1.72 | 1.73 | 0.19 | 0.994 | 1.92 | 1.93 | 0.21 | 0.994 | 2.21 | 2.22 | 0.25 | 0.994 | 8
Goomboorian WN maximum demand | 1.7 | 1.85 | 0.73 | 0.918 | 2.11 | 2.12 | 0.26 | 0.993 | 2.34 | 2.36 | 0.29 | 0.993 | 2.37 | 2.39 | 0.29 | 0.993 | 8
Grovely SD maximum demand | 25.33 | 26.38 | 7.36 | 0.96 | 18.08 | 19.57 | 7.48 | 0.924 | 20.82 | 22.53 | 8.62 | 0.924 | 18.83 | 19.07 | 3.02 | 0.987 | 50
Grovely SN maximum demand | 24.25 | 25.18 | 6.8 | 0.963 | 17.5 | 18.83 | 6.95 | 0.929 | 20.15 | 21.68 | 8.01 | 0.929 | 18.23 | 18.43 | 2.71 | 0.989 | 50
Grovely WD maximum demand | 18.96 | 19.08 | 2.12 | 0.994 | 13.34 | 13.7 | 3.14 | 0.973 | 15.27 | 15.68 | 3.59 | 0.973 | 15.11 | 15.92 | 5.02 | 0.949 | 50
Grovely WN maximum demand | 21.91 | 22.23 | 3.77 | 0.986 | 14.76 | 15.38 | 4.34 | 0.959 | 16.89 | 17.61 | 4.97 | 0.959 | 16.72 | 16.72 | 0.17 | 1 | 50
Gympie SD maximum demand | 23.37 | 23.76 | 4.31 | 0.983 | 23.16 | 25.48 | 10.63 | 0.909 | 26.95 | 29.66 | 12.37 | 0.909 | 21.75 | 21.85 | 2.1 | 0.995 | 50
Gympie SN maximum demand | 22.39 | 22.54 | 2.62 | 0.993 | 22.11 | 24.21 | 9.87 | 0.913 | 25.73 | 28.18 | 11.49 | 0.913 | 20.89 | 20.92 | 1 | 0.999 | 50
Gympie WD maximum demand | 17.53 | 17.66 | -2.11 | 0.993 | 17.42 | 18.16 | 5.11 | 0.96 | 19.3 | 20.12 | 5.66 | 0.96 | 17.72 | 17.81 | 1.73 | 0.995 | 50
Gympie WN maximum demand | 17.43 | 17.58 | -2.24 | 0.992 | 17.06 | 17.88 | 5.33 | 0.955 | 18.91 | 19.81 | 5.9 | 0.955 | 17.55 | 17.6 | 1.35 | 0.997 | 50
Gympie North SD maximum demand | 15.99 | 16.7 | 4.82 | 0.957 | 13.19 | 14.41 | 5.8 | 0.915 | 13.88 | 15.16 | 6.1 | 0.915 | 14.8 | 14.84 | 1.11 | 0.997 | 25
Gympie North SN maximum demand | 15.32 | 15.75 | 3.66 | 0.973 | 13.02 | 14.11 | 5.45 | 0.922 | 13.7 | 14.85 | 5.74 | 0.922 | 14.42 | 14.44 | 0.64 | 0.999 | 25
Gympie North WD maximum demand | 13.24 | 13.27 | 0.89 | 0.998 | 10.93 | 11.36 | 3.11 | 0.962 | 12.72 | 13.22 | 3.62 | 0.962 | 14.4 | 14.97 | 4.09 | 0.962 | 25
Gympie North WN maximum demand | 13.17 | 13.19 | 0.79 | 0.998 | 10.93 | 11.41 | 3.28 | 0.958 | 12.72 | 13.28 | 3.82 | 0.958 | 14.18 | 14.8 | 4.26 | 0.958 | 25
Gympie South SD maximum demand | 9.16 | 11.4 | 6.79 | 0.804 | 6.99 | 7.43 | 2.51 | 0.941 | 6.83 | 7.26 | 2.45 | 0.941 | 7.48 | 9.06 | 5.12 | 0.825 | 15
Gympie South SN maximum demand | 9 | 10.83 | 6.02 | 0.831 | 6.31 | 7.55 | 4.16 | 0.835 | 6.16 | 7.37 | 4.06 | 0.835 | 6 | 7.18 | 3.95 | 0.835 | 15
Gympie South WD maximum demand | 9.68 | 11.09 | 5.41 | 0.873 | 6.93 | 8.03 | 4.05 | 0.863 | 6.89 | 7.98 | 4.03 | 0.863 | 7.34 | 8.67 | 4.61 | 0.847 | 15
Gympie South WN maximum demand | 9.67 | 10.93 | 5.1 | 0.885 | 7.23 | 8.25 | 3.97 | 0.876 | 7.19 | 8.2 | 3.95 | 0.876 | 7.64 | 8.86 | 4.49 | 0.862 | 15
Hamilton SD maximum demand | 22.25 | 23.39 | 7.23 | 0.951 | 19.16 | 19.35 | 2.74 | 0.99 | 23.69 | 23.93 | 3.38 | 0.99 | 20.69 | 20.7 | 0.61 | 1 | 50
Hamilton SN maximum demand | 20.81 | 21.66 | 6 | 0.961 | 18.43 | 18.52 | 1.82 | 0.995 | 22.79 | 22.9 | 2.25 | 0.995 | 19.93 | 20.45 | 4.57 | 0.975 | 50
Hamilton WD maximum demand | 14.92 | 14.99 | 1.42 | 0.996 | 14.32 | 14.49 | 2.23 | 0.988 | 16.14 | 16.34 | 2.52 | 0.988 | 13.62 | 13.63 | 0.46 | 0.999 | 50
Hamilton WN maximum demand | 16.08 | 16.21 | 2.09 | 0.992 | 15.25 | 15.25 | -0.3 | 1 | 17.18 | 17.19 | -0.34 | 1 | 14.4 | 14.4 | 0.24 | 1 | 50
Hamilton Lands SD maximum demand | 27.26 | 30.6 | 13.91 | 0.891 | 20.19 | 20.21 | 0.96 | 0.999 | 22.81 | 22.83 | 1.08 | 0.999 | 29.75 | 30.57 | 7.04 | 0.973 | 50
Hamilton Lands SN maximum demand | 19.21 | 20.98 | 8.43 | 0.916 | 15.82 | 16.19 | 3.45 | 0.977 | 17.87 | 18.29 | 3.9 | 0.977 | 23.32 | 23.63 | 3.81 | 0.987 | 50
Hamilton Lands WD maximum demand | 21.79 | 23.96 | 9.97 | 0.909 | 15.99 | 16.31 | 3.19 | 0.981 | 16.25 | 16.57 | 3.25 | 0.981 | 15.97 | 16.6 | 4.5 | 0.962 | 50
Hamilton Lands WN maximum demand | 16.7 | 17.63 | 5.67 | 0.947 | 14.52 | 14.71 | 2.39 | 0.987 | 14.75 | 14.95 | 2.43 | 0.987 | 14.5 | 14.86 | 3.27 | 0.975 | 50
Heathwood SD maximum demand | 29.01 | 29.01 | -0.11 | 1 | 23.99 | 24.01 | 1.02 | 0.999 | 28.38 | 28.4 | 1.21 | 0.999 | 25.88 | 26.04 | 2.87 | 0.994 | 50
Heathwood SN maximum demand | 28.24 | 28.25 | -0.71 | 1 | 24.27 | 24.3 | 1.15 | 0.999 | 28.71 | 28.74 | 1.36 | 0.999 | 26.18 | 26.31 | 2.62 | 0.995 | 50
Heathwood WD maximum demand | 20.93 | 21.54 | -5.07 | 0.972 | 18.01 | 18.23 | 2.83 | 0.988 | 20.19 | 20.44 | 3.17 | 0.988 | 20.18 | 20.62 | 4.24 | 0.979 | 50
Heathwood WN maximum demand | 22.1 | 22.56 | -4.54 | 0.98 | 19.38 | 19.64 | 3.15 | 0.987 | 21.72 | 22.01 | 3.53 | 0.987 | 21.71 | 22.19 | 4.56 | 0.979 | 50
Helidon SD maximum demand | 2.47 | 2.7 | -1.1 | 0.914 | 2.98 | 3.24 | 1.28 | 0.919 | 3.2 | 3.48 | 1.37 | 0.919 | 2.97 | 2.99 | 0.35 | 0.993 | 8
Helidon SN maximum demand | 2.32 | 2.74 | -1.45 | 0.849 | 3.04 | 3.28 | 1.24 | 0.926 | 3.27 | 3.53 | 1.33 | 0.926 | 3.04 | 3.04 | 0.06 | 1 | 8
Helidon WD maximum demand | 3.67 | 3.68 | -0.15 | 0.999 | 2.14 | 2.26 | 0.75 | 0.944 | 2.37 | 2.51 | 0.83 | 0.944 | 2.44 | 2.68 | 1.12 | 0.909 | 8
Helidon WN maximum demand | 3.34 | 3.37 | -0.46 | 0.991 | 2.31 | 2.43 | 0.76 | 0.95 | 2.56 | 2.69 | 0.84 | 0.95 | 2.63 | 2.82 | 1.01 | 0.934 | 8
Hemmant SD maximum demand | 13.9 | 16.11 | 8.15 | 0.863 | 10.96 | 12.11 | 5.14 | 0.905 | 12.57 | 13.89 | 5.9 | 0.905 | 11.45 | 12.97 | 6.1 | 0.882 | 26
Hemmant SN maximum demand | 11.64 | 13.21 | 6.25 | 0.881 | 10.04 | 11.06 | 4.64 | 0.908 | 11.51 | 12.68 | 5.32 | 0.908 | 10.48 | 11.73 | 5.27 | 0.894 | 26
Hemmant WD maximum demand | 12.32 | 14.4 | 7.47 | 0.855 | 8.85 | 9.63 | 3.78 | 0.92 | 8.82 | 9.59 | 3.77 | 0.92 | 8.78 | 9.8 | 4.36 | 0.896 | 26
Hemmant WN maximum demand | 10.23 | 11.64 | 5.56 | 0.879 | 8.64 | 9.37 | 3.65 | 0.921 | 8.6 | 9.34 | 3.63 | 0.921 | 8.22 | 9.13 | 3.98 | 0.9 | 26
Hendra SD maximum demand | 24.32 | 27.93 | 13.74 | 0.871 | 16.54 | 17.84 | 6.69 | 0.927 | 19.61 | 21.15 | 7.94 | 0.927 | 18.99 | 19.3 | 3.43 | 0.984 | 25
Hendra SN maximum demand | 22.59 | 25.73 | 12.32 | 0.878 | 16.3 | 17.46 | 6.26 | 0.934 | 19.32 | 20.7 | 7.42 | 0.934 | 18.66 | 18.89 | 2.92 | 0.988 | 25
Hendra WD maximum demand | 16.99 | 18.59 | 7.54 | 0.914 | 13.43 | 14.04 | 4.09 | 0.957 | 15.37 | 16.06 | 4.67 | 0.957 | 7.86 | 8.35 | 2.8 | 0.942 | 25
Hendra WN maximum demand | 19.11 | 20.91 | 8.48 | 0.914 | 14.28 | 14.95 | 4.43 | 0.955 | 16.34 | 17.11 | 5.07 | 0.955 | 8.06 | 8.56 | 2.86 | 0.942 | 25
Holland Park SD maximum demand | 26.29 | 30.05 | 14.54 | 0.875 | 15.63 | 16.84 | 6.28 | 0.928 | 19.54 | 21.06 | 7.85 | 0.928 | 15.55 | 17.38 | 7.76 | 0.895 | 40
Holland Park SN maximum demand | 26.47 | 30.09 | 14.3 | 0.88 | 15.36 | 16.42 | 5.82 | 0.935 | 19.21 | 20.54 | 7.27 | 0.935 | 15.21 | 16.89 | 7.35 | 0.9 | 40
Holland Park WD maximum demand | 22.09 | 23.58 | 8.24 | 0.937 | 19 | 19.7 | 5.19 | 0.965 | 21.37 | 22.15 | 5.84 | 0.965 | 10.73 | 11.33 | 3.64 | 0.947 | 40
Holland Park WN maximum demand | 26.18 | 28.23 | 10.56 | 0.927 | 20.38 | 21.3 | 6.2 | 0.957 | 22.91 | 23.95 | 6.97 | 0.957 | 10.95 | 11.67 | 4.04 | 0.938 | 40
Holland Park East SD maximum demand | 19.81 | 20.8 | 6.34 | 0.952 | 17.36 | 17.39 | 0.91 | 0.999 | 20.73 | 20.75 | 1.09 | 0.999 | 18.18 | 18.31 | 2.18 | 0.993 | 50
Holland Park East SN maximum demand | 20.79 | 21.7 | 6.21 | 0.958 | 17.67 | 17.7 | 1.11 | 0.998 | 21.09 | 21.13 | 1.32 | 0.998 | 18.47 | 18.6 | 2.11 | 0.994 | 50
Holland Park East WD maximum demand | 17.41 | 17.51 | 1.88 | 0.994 | 15.25 | 15.71 | 3.78 | 0.971 | 17.54 | 18.07 | 4.35 | 0.971 | 16.87 | 17.51 | 4.69 | 0.963 | 50
Holland Park East WN maximum demand | 20.07 | 20.33 | 3.27 | 0.987 | 17.38 | 17.96 | 4.5 | 0.968 | 19.99 | 20.65 | 5.17 | 0.968 | 19.18 | 19.19 | 0.61 | 0.999 | 50
Hollywell SD maximum demand | 35.17 | 35.48 | 4.66 | 0.991 | 29.94 | 30.13 | 3.35 | 0.994 | 36.79 | 37.02 | 4.11 | 0.994 | 33.13 | 33.17 | 1.7 | 0.999 | 50
Hollywell SN maximum demand | 33.74 | 33.95 | 3.75 | 0.994 | 29.72 | 29.91 | 3.35 | 0.994 | 36.53 | 36.76 | 4.11 | 0.994 | 32.89 | 32.91 | 1.11 | 0.999 | 50
Hollywell WD maximum demand | 25.64 | 25.8 | -2.92 | 0.994 | 25.79 | 26.09 | 3.91 | 0.989 | 26.94 | 27.25 | 4.09 | 0.989 | 26.59 | 26.6 | 0.81 | 1 | 50
Hollywell WN maximum demand | 30.2 | 30.29 | -2.26 | 0.997 | 28.62 | 29.09 | 5.22 | 0.984 | 29.89 | 30.38 | 5.45 | 0.984 | 29.5 | 29.53 | 1.34 | 0.999 | 50
Hope Island SD maximum demand | 45.76 | 46.31 | 7.06 | 0.988 | 26.79 | 27.05 | 3.76 | 0.99 | 32.75 | 33.07 | 4.59 | 0.99 | 29.05 | 29.44 | 4.81 | 0.987 | 50
Hope Island SN maximum demand | 46.42 | 46.9 | 6.69 | 0.99 | 26.47 | 26.68 | 3.37 | 0.992 | 32.35 | 32.61 | 4.12 | 0.992 | 28.67 | 29.01 | 4.43 | 0.988 | 50
Hope Island WD maximum demand | 29.57 | 29.66 | -2.34 | 0.997 | 18.4 | 18.63 | 2.87 | 0.988 | 20.72 | 20.97 | 3.23 | 0.988 | 19.95 | 20.42 | 4.34 | 0.977 | 50
Hope Island WN maximum demand | 34.42 | 34.42 | -0.45 | 1 | 21.32 | 21.73 | 4.24 | 0.981 | 24 | 24.46 | 4.77 | 0.981 | 23.09 | 23.09 | 0.09 | 1 | 50
Ibis SD maximum demand | 0.4 | 0.46 | 0.24 | 0.857 | 0.02 | 0.21 | 0.21 | 0.117 | 0.04 | 0.3 | 0.3 | 0.117 | 0.1 | 0.14 | 0.1 | 0.724 | 5
Ibis SN maximum demand | 0.39 | 0.48 | 0.27 | 0.824 | 0.06 | 0.25 | 0.24 | 0.25 | 0.09 | 0.35 | 0.34 | 0.25 | 0.09 | 0.13 | 0.09 | 0.731 | 5
Ibis WD maximum demand | 0.36 | 0.49 | 0.34 | 0.735 | 0.08 | 0.34 | 0.33 | 0.243 | 0.11 | 0.44 | 0.42 | 0.243 | 0.2 | 0.29 | 0.22 | 0.674 | 5
Ibis WN maximum demand | 0.48 | 0.64 | 0.42 | 0.759 | 0.09 | 0.35 | 0.33 | 0.275 | 0.12 | 0.44 | 0.42 | 0.275 | 0.22 | 0.33 | 0.25 | 0.671 | 5
Imbil SD maximum demand | 3.01 | 3.09 | 0.69 | 0.975 | 2.26 | 3.06 | 2.07 | 0.738 | 2.36 | 3.2 | 2.16 | 0.738 | 2.38 | 2.51 | 0.8 | 0.948 | 8
Imbil SN maximum demand | 2.94 | 2.95 | -0.23 | 0.997 | 2.21 | 3.02 | 2.07 | 0.73 | 2.31 | 3.16 | 2.16 | 0.73 | 2.32 | 2.41 | 0.63 | 0.965 | 8
Imbil WD maximum demand | 2.46 | 2.47 | 0.08 | 0.999 | 2.3 | 3 | 1.93 | 0.765 | 2.63 | 3.44 | 2.21 | 0.765 | 2.66 | 2.77 | 0.76 | 0.962 | 8
Imbil WN maximum demand | 2.71 | 2.74 | -0.37 | 0.991 | 2.33 | 3.1 | 2.05 | 0.752 | 2.67 | 3.55 | 2.34 | 0.752 | 2.7 | 2.78 | 0.69 | 0.969 | 8
Inala SD maximum demand | 31.82 | 33.22 | 9.53 | 0.958 | 24.81 | 24.99 | 2.98 | 0.993 | 31.43 | 31.66 | 3.77 | 0.993 | 24.89 | 25.38 | 4.95 | 0.981 | 50
Inala SN maximum demand | 30.7 | 31.97 | 8.91 | 0.96 | 24.53 | 24.67 | 2.56 | 0.995 | 31.08 | 31.24 | 3.25 | 0.995 | 24.65 | 25.07 | 4.56 | 0.983 | 50
Inala WD maximum demand | 24.49 | 24.63 | 2.6 | 0.994 | 19.27 | 19.71 | 4.13 | 0.978 | 21.12 | 21.6 | 4.52 | 0.978 | 20.34 | 21.16 | 5.82 | 0.961 | 50
Inala WN maximum demand | 27.83 | 28.12 | 3.99 | 0.99 | 21.66 | 22.08 | 4.28 | 0.981 | 23.74 | 24.2 | 4.69 | 0.981 | 22.85 | 22.86 | 0.77 | 0.999 | 50
Indooroopilly SD maximum demand | 27.89 | 28.68 | 6.68 | 0.972 | 22.88 | 23.5 | 5.35 | 0.974 | 26.3 | 27.01 | 6.15 | 0.974 | 27.55 | 27.9 | 4.42 | 0.987 | 50
Indooroopilly SN maximum demand | 26.33 | 26.93 | 5.67 | 0.978 | 20.77 | 21.14 | 3.93 | 0.983 | 23.88 | 24.31 | 4.52 | 0.983 | 25.04 | 25.2 | 2.84 | 0.994 | 50
Indooroopilly WD maximum demand | 18.51 | 18.51 | -0.05 | 1 | 15.21 | 16.07 | 5.19 | 0.946 | 16.3 | 17.22 | 5.57 | 0.946 | 16.32 | 16.51 | 2.49 | 0.989 | 50
Indooroopilly WN maximum demand | 20.47 | 20.47 | 0.03 | 1 | 16.3 | 17.25 | 5.65 | 0.945 | 17.46 | 18.48 | 6.05 | 0.945 | 17.48 | 17.62 | 2.19 | 0.992 | 50
Innisplain SD maximum demand | 3.41 | 3.43 | -0.34 | 0.995 | 3.64 | 3.72 | 0.81 | 0.976 | 4.42 | 4.53 | 0.98 | 0.976 | 3.99 | 4.12 | 1.03 | 0.968 | 8
Innisplain SN maximum demand | 3.6 | 3.63 | -0.42 | 0.993 | 4.14 | 4.28 | 1.11 | 0.966 | 5.03 | 5.2 | 1.35 | 0.966 | 4.54 | 4.65 | 0.98 | 0.978 | 8
Innisplain WD maximum demand | 3.37 | 3.48 | -0.86 | 0.969 | 2.95 | 2.98 | 0.41 | 0.99 | 3.06 | 3.09 | 0.43 | 0.99 | 3.02 | 3.03 | 0.1 | 0.999 | 8
Innisplain WN maximum demand | 4.11 | 4.2 | -0.87 | 0.978 | 3.65 | 3.65 | 0.13 | 0.999 | 3.78 | 3.79 | 0.14 | 0.999 | 3.74 | 3.74 | 0.13 | 0.999 | 8
Ipswich South SD maximum demand | 31.03 | 31.24 | 3.63 | 0.993 | 27.36 | 28.42 | 7.71 | 0.962 | 29.53 | 30.69 | 8.33 | 0.962 | 15.69 | 15.7 | 0.39 | 1 | 50
Ipswich South SN maximum demand | 29.44 | 29.54 | 2.41 | 0.997 | 27.51 | 28.41 | 7.11 | 0.968 | 29.7 | 30.67 | 7.67 | 0.968 | 15.77 | 15.77 | 0.18 | 1 | 50
Ipswich South WD maximum demand | 30.5 | 30.5 | -0.08 | 1 | 18.93 | 19.24 | 3.48 | 0.984 | 20.64 | 20.99 | 3.79 | 0.984 | 19.59 | 20.29 | 5.3 | 0.965 | 50
Ipswich South WN maximum demand | 31.57 | 31.59 | -1.25 | 0.999 | 21.73 | 22.04 | 3.67 | 0.986 | 23.7 | 24.04 | 4.01 | 0.986 | 22.51 | 23.11 | 5.22 | 0.974 | 50
Jimboomba SD maximum demand | 15.96 | 15.97 | 0.63 | 0.999 | 19.25 | 19.78 | 4.56 | 0.973 | 20.95 | 21.53 | 4.97 | 0.973 | 19.01 | 19.06 | 1.41 | 0.997 | 40
Jimboomba SN maximum demand | 15.64 | 15.64 | 0.26 | 1 | 19.29 | 19.31 | 0.78 | 0.999 | 21 | 21.02 | 0.85 | 0.999 | 19.05 | 19.07 | 0.78 | 0.999 | 40
Jimboomba WD maximum demand | 13.98 | 14.04 | -1.32 | 0.996 | 13.45 | 13.63 | 2.19 | 0.987 | 15.23 | 15.43 | 2.49 | 0.987 | 15.13 | 15.56 | 3.64 | 0.972 | 40
Jimboomba WN maximum demand | 16.46 | 16.5 | -1.21 | 0.997 | 15.62 | 15.86 | 2.76 | 0.985 | 17.69 | 17.97 | 3.13 | 0.985 | 17.57 | 18.01 | 3.95 | 0.976 | 40
Jindalee SD maximum demand | 21.25 | 21.25 | -0.13 | 1 | 13.84 | 14.75 | 5.1 | 0.938 | 16.63 | 17.72 | 6.13 | 0.938 | 15.03 | 15.09 | 1.28 | 0.996 | 30
Jindalee SN maximum demand | 20.65 | 20.67 | -0.82 | 0.999 | 13.38 | 14.18 | 4.72 | 0.943 | 16.07 | 17.05 | 5.67 | 0.943 | 14.53 | 14.56 | 0.87 | 0.998 | 30
Jindalee WD maximum demand | 15.92 | 16.75 | -5.2 | 0.951 | 9.65 | 9.89 | 2.18 | 0.975 | 10.89 | 11.17 | 2.46 | 0.975 | 10.81 | 11.23 | 3.06 | 0.962 | 30
Jindalee WN maximum demand | 17.4 | 18.04 | -4.73 | 0.965 | 9.78 | 10.03 | 2.23 | 0.975 | 11.04 | 11.33 | 2.52 | 0.975 | 11.26 | 11.69 | 3.15 | 0.963 | 30
Kalbar SD maximum demand | 5.27 | 5.3 | 0.6 | 0.993 | 5.56 | 5.56 | -0.11 | 1 | 6.81 | 6.81 | -0.13 | 1 | 6.18 | 6.26 | 1.02 | 0.987 | 15
Kalbar SN maximum demand | 5.45 | 5.49 | 0.64 | 0.993 | 5.82 | 5.82 | -0.11 | 1 | 7.13 | 7.13 | -0.13 | 1 | 6.46 | 6.54 | 0.96 | 0.989 | 15
Kalbar WD maximum demand | 5.07 | 5.08 | 0.36 | 0.998 | 4.17 | 4.17 | 0.02 | 1 | 4.64 | 4.64 | 0.02 | 1 | 4.6 | 4.78 | 1.32 | 0.961 | 15
Kalbar WN maximum demand | 5.37 | 5.38 | 0.42 | 0.997 | 5.37 | 5.4 | 0.56 | 0.995 | 5.97 | 6 | 0.63 | 0.995 | 5.91 | 5.93 | 0.44 | 0.997 | 15
Kallangur SD maximum demand | 35.33 | 35.46 | 3.07 | 0.996 | 30.75 | 30.79 | 1.74 | 0.998 | 36.09 | 36.15 | 2.04 | 0.998 | 29.64 | 29.9 | 3.93 | 0.991 | 49
Kallangur SN maximum demand | 36.48 | 36.65 | 3.51 | 0.995 | 32.27 | 32.31 | 1.65 | 0.999 | 37.88 | 37.93 | 1.94 | 0.999 | 31.09 | 31.34 | 3.98 | 0.992 | 49
Kallangur WD maximum demand | 27.8 | 28.03 | -3.59 | 0.992 | 24.05 | 24.2 | 2.65 | 0.994 | 25.08 | 25.23 | 2.76 | 0.994 | 24.89 | 25.26 | 4.27 | 0.986 | 49
Kallangur WN maximum demand | 34.25 | 34.3 | -1.88 | 0.998 | 26.6 | 26.82 | 3.45 | 0.992 | 27.73 | 27.96 | 3.6 | 0.992 | 27.53 | 28.04 | 5.36 | 0.982 | 49
Karrabin SD maximum demand | 18.21 | 18.78 | 4.58 | 0.97 | 14.04 | 14.68 | 4.3 | 0.956 | 17.43 | 18.23 | 5.34 | 0.956 | 15.47 | 15.52 | 1.27 | 0.997 | 40
Karrabin SN maximum demand | 17.13 | 17.44 | 3.27 | 0.982 | 14.21 | 14.87 | 4.37 | 0.956 | 17.64 | 18.46 | 5.42 | 0.956 | 15.66 | 15.68 | 0.72 | 0.999 | 40
Karrabin WD maximum demand | 15.7 | 15.76 | 1.35 | 0.996 | 14.23 | 14.9 | 4.41 | 0.955 | 15.66 | 16.39 | 4.85 | 0.955 | 15.23 | 16.1 | 5.21 | 0.946 | 40
Karrabin WN maximum demand | 15.16 | 15.18 | 0.76 | 0.999 | 14.17 | 14.75 | 4.11 | 0.96 | 15.59 | 16.23 | 4.52 | 0.96 | 15.16 | 15.94 | 4.93 | 0.951 | 40
Kawana SD maximum demand | 43.2 | 47.29 | 19.22 | 0.914 | 24.04 | 25.49 | 8.48 | 0.943 | 27.72 | 29.4 | 9.78 | 0.943 | 25.23 | 27.4 | 10.68 | 0.921 | 60
Kawana SN maximum demand | 39.68 | 42.63 | 15.58 | 0.931 | 22.09 | 23.08 | 6.69 | 0.957 | 25.47 | 26.62 | 7.72 | 0.957 | 23.19 | 24.73 | 8.62 | 0.937 | 60
Kawana WD maximum demand | 30.79 | 32.06 | 8.92 | 0.961 | 20.76 | 21.2 | 4.28 | 0.979 | 21.3 | 21.75 | 4.39 | 0.979 | 21.32 | 22.03 | 5.55 | 0.968 | 60
Kawana WN maximum demand | 34.18 | 35.38 | 9.11 | 0.966 | 21.08 | 21.47 | 4.07 | 0.982 | 21.63 | 22.03 | 4.17 | 0.982 | 21.66 | 22.26 | 5.14 | 0.973 | 60
Kedron SD maximum demand | 30.21 | 30.31 | 2.49 | 0.997 | 24.97 | 25.51 | 5.22 | 0.979 | 28.29 | 28.9 | 5.92 | 0.979 | 25.69 | 25.86 | 2.99 | 0.993 | 50
Kedron SN maximum demand | 28.82 | 28.84 | 1.09 | 0.999 | 24.52 | 24.96 | 4.71 | 0.982 | 27.78 | 28.28 | 5.33 | 0.982 | 25.22 | 25.31 | 2.06 | 0.997 | 50
Kedron WD maximum demand | 22.96 | 23.55 | -5.27 | 0.975 | 20.86 | 20.88 | 0.87 | 0.999 | 23.32 | 23.34 | 0.97 | 0.999 | 21.56 | 21.75 | 2.89 | 0.991 | 50
Kedron WN maximum demand | 26.03 | 26.29 | -3.69 | 0.99 | 23.63 | 23.74 | 2.38 | 0.995 | 26.41 | 26.54 | 2.66 | 0.995 | 24.38 | 24.73 | 4.13 | 0.986 | 50
Kelvin Grove SD maximum demand | 36.1 | 39.09 | 14.99 | 0.924 | 0 | 0 | 0 |  | 0 | 0 | 0
Kelvin Grove SN maximum demand | 30.93 | 32.99 | 11.47 | 0.938 | 0 | 0 | 0 |  | 0 | 0 | 0
Kelvin Grove WD maximum demand | 25.38 | 26.62 | 8.03 | 0.953 | 0 | 0 | 0 |  | 0 | 0 | 0
Kelvin Grove WN maximum demand | 24.93 | 25.75 | 6.47 | 0.968 | 0 | 0 | 0 |  | 0 | 0 | 0
Kenilworth SD maximum demand | 5.71 | 6.27 | 2.59 | 0.911 | 4.14 | 4.4 | 1.49 | 0.941 | 4.82 | 5.13 | 1.74 | 0.941 | 4.34 | 4.62 | 1.59 | 0.939 | 5
Kenilworth SN maximum demand | 5.8 | 6.22 | 2.25 | 0.932 | 3.93 | 4.2 | 1.48 | 0.936 | 4.58 | 4.9 | 1.72 | 0.936 | 4.12 | 4.37 | 1.44 | 0.944 | 5
Kenilworth WD maximum demand | 5.8 | 6.21 | 2.21 | 0.934 | 4.12 | 4.2 | 0.81 | 0.981 | 4.62 | 4.71 | 0.9 | 0.981 | 4.56 | 4.7 | 1.17 | 0.969 | 5
Kenilworth WN maximum demand | 5.83 | 6.21 | 2.13 | 0.939 | 4.14 | 4.22 | 0.83 | 0.981 | 4.65 | 4.74 | 0.93 | 0.981 | 4.58 | 4.73 | 1.17 | 0.969 | 5
Kenmore SD maximum demand | 29.21 | 29.83 | 6.01 | 0.979 | 29.16 | 29.29 | 2.8 | 0.995 | 33.54 | 33.69 | 3.22 | 0.995 | 30.25 | 30.71 | 5.26 | 0.985 | 50
Kenmore SN maximum demand | 30.3 | 31.01 | 6.62 | 0.977 | 29.12 | 29.25 | 2.8 | 0.995 | 33.49 | 33.64 | 3.22 | 0.995 | 30.21 | 30.62 | 5.01 | 0.987 | 50
Kenmore WD maximum demand | 24.63 | 24.7 | 1.82 | 0.997 | 26.33 | 26.72 | 4.54 | 0.985 | 31.14 | 31.6 | 5.37 | 0.985 | 30.74 | 30.76 | 1.21 | 0.999 | 50
Kenmore WN maximum demand | 27.61 | 27.85 | 3.66 | 0.991 | 29.01 | 29.01 | 0.28 | 1 | 34.3 | 34.3 | 0.33 | 1 | 33.86 | 33.98 | 2.83 | 0.997 | 50
Kenmore Bus 2 SD maximum demand | 12.62 | 13.84 | 5.69 | 0.912 | 0 | 0 | 0 |  | 0 | 0 | 0
Kenmore Bus 2 SN maximum demand | 14.13 | 15.41 | 6.15 | 0.917 | 0 | 0 | 0 |  | 0 | 0 | 0
Kenmore Bus 2 WD maximum demand | 12.46 | 12.91 | 3.39 | 0.965 | 0 | 0 | 0 |  | 0 | 0 | 0
Kenmore Bus 2 WN maximum demand | 13.97 | 14.62 | 4.32 | 0.955 | 0 | 0 | 0 |  | 0 | 0 | 0
Kilcoy SD maximum demand | 8.36 | 8.64 | 2.18 | 0.968 | 8.71 | 9.21 | 3 | 0.946 | 9.56 | 10.11 | 3.29 | 0.946 | 8.68 | 8.93 | 2.08 | 0.972 | 10
Kilcoy SN maximum demand | 8.35 | 8.58 | 2.01 | 0.972 | 8.68 | 9.13 | 2.84 | 0.95 | 9.53 | 10.03 | 3.12 | 0.95 | 8.65 | 8.84 | 1.81 | 0.979 | 10
Kilcoy WD maximum demand | 7.21 | 7.25 | 0.71 | 0.995 | 7.16 | 7.18 | 0.52 | 0.997 | 7.41 | 7.43 | 0.54 | 0.997 | 7.38 | 7.41 | 0.64 | 0.996 | 10
Kilcoy WN maximum demand | 7.8 | 7.84 | 0.87 | 0.994 | 7.77 | 7.8 | 0.71 | 0.996 | 8.04 | 8.07 | 0.73 | 0.996 | 8 | 8.03 | 0.66 | 0.997 | 10
Kingston SD maximum demand | 29.88 | 29.92 | 1.52 | 0.999 | 26.73 | 26.93 | 3.28 | 0.993 | 29.82 | 30.05 | 3.66 | 0.993 | 27.41 | 27.41 | 0.13 | 1 | 50
Kingston SN maximum demand | 30.33 | 30.37 | 1.48 | 0.999 | 27.31 | 27.48 | 3.06 | 0.994 | 30.48 | 30.67 | 3.42 | 0.994 | 28.01 | 28.45 | 4.98 | 0.985 | 50
Kingston WD maximum demand | 25.32 | 25.66 | -4.16 | 0.987 | 22.94 | 23.43 | 4.74 | 0.979 | 25.25 | 25.78 | 5.21 | 0.979 | 25.12 | 25.13 | 0.83 | 0.999 | 50
Kingston WN maximum demand | 29.24 | 29.46 | -3.65 | 0.992 | 25.64 | 26.08 | 4.76 | 0.983 | 28.21 | 28.69 | 5.24 | 0.983 | 28.07 | 28.08 | 0.73 | 1 | 50
Kirra SD maximum demand | 22.95 | 23.55 | 5.3 | 0.974 | 15.65 | 17.17 | 7.06 | 0.911 | 16.41 | 18.01 | 7.41 | 0.911 | 14.77 | 14.9 | 1.97 | 0.991 | 23
Kirra SN maximum demand | 22.71 | 23.18 | 4.69 | 0.979 | 15.72 | 17.13 | 6.81 | 0.918 | 16.49 | 17.97 | 7.14 | 0.918 | 14.84 | 14.91 | 1.49 | 0.995 | 23
Kirra WD maximum demand | 17.75 | 17.85 | 1.86 | 0.995 | 13.13 | 13.19 | -1.23 | 0.996 | 13.74 | 13.8 | -1.29 | 0.996 | 13.58 | 14.26 | 4.37 | 0.952 | 23
Kirra WN maximum demand | 19.87 | 20.06 | 2.76 | 0.99 | 13.86 | 13.88 | -0.79 | 0.998 | 14.5 | 14.52 | -0.82 | 0.998 | 14.33 | 15.13 | 4.86 | 0.947 | 23
Labrador SD maximum demand | 26.89 | 27.11 | 3.39 | 0.992 | 20.68 | 20.98 | 3.54 | 0.986 | 24.25 | 24.6 | 4.16 | 0.986 | 21.86 | 22.38 | 4.78 | 0.977 | 37
Labrador SN maximum demand | 26.52 | 26.65 | 2.65 | 0.995 | 20.41 | 20.69 | 3.4 | 0.986 | 23.94 | 24.27 | 3.98 | 0.986 | 21.58 | 22.04 | 4.47 | 0.979 | 37
Labrador WD maximum demand | 23.47 | 23.5 | -1.15 | 0.999 | 17.97 | 18.74 | -5.32 | 0.959 | 19.32 | 20.15 | -5.72 | 0.959 | 19.09 | 19.11 | 0.99 | 0.999 | 37
Labrador WN maximum demand | 26.24 | 26.27 | -1.29 | 0.999 | 20.07 | 20.68 | -4.97 | 0.971 | 21.58 | 22.23 | -5.34 | 0.971 | 21.32 | 21.36 | 1.34 | 0.998 | 37
Lagoon Pocket SD maximum demand | 1.52 | 1.8 | 0.97 | 0.842 | 0 | 0 | 0 |  | 0 | 0 | 0
Lagoon Pocket SN maximum demand | 1.47 | 1.71 | 0.86 | 0.863 | 0 | 0 | 0 |  | 0 | 0 | 0
Lagoon Pocket WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Lagoon Pocket WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Laidley SD maximum demand | 9.92 | 10.4 | 3.13 | 0.954 | 9.36 | 9.51 | 1.72 | 0.984 | 9.63 | 9.8 | 1.77 | 0.984 | 8.86 | 8.87 | 0.07 | 1 | 12
Laidley SN maximum demand | 10.39 | 10.87 | 3.19 | 0.956 | 9.81 | 9.95 | 1.61 | 0.987 | 10.11 | 10.24 | 1.66 | 0.987 | 9.3 | 9.3 | 0.1 | 1 | 12
Laidley WD maximum demand | 7.82 | 7.9 | 1.14 | 0.99 | 6.53 | 6.79 | 1.87 | 0.961 | 7.52 | 7.83 | 2.16 | 0.961 | 7.59 | 7.62 | 0.64 | 0.996 | 12
Laidley WN maximum demand | 8.8 | 8.92 | 1.47 | 0.986 | 7.36 | 7.56 | 1.71 | 0.974 | 8.48 | 8.71 | 1.97 | 0.974 | 8.56 | 8.58 | 0.62 | 0.997 | 12
Landsborough SD maximum demand | 7.74 | 8.25 | 2.86 | 0.938 | 9.59 | 9.84 | 2.2 | 0.975 | 10.78 | 11.06 | 2.47 | 0.975 | 10.5 | 11.05 | 3.47 | 0.949 | 25
Landsborough SN maximum demand | 6.57 | 7.1 | 2.71 | 0.924 | 9.78 | 9.97 | 1.9 | 0.982 | 10.99 | 11.19 | 2.13 | 0.982 | 10.65 | 11.07 | 3.01 | 0.962 | 25
Landsborough WD maximum demand | 6.32 | 6.58 | 1.84 | 0.96 | 10.84 | 10.98 | 1.73 | 0.987 | 12.12 | 12.27 | 1.94 | 0.987 | 9.82 | 10.13 | 2.47 | 0.97 | 25
Landsborough WN maximum demand | 6.32 | 6.56 | 1.75 | 0.964 | 11.87 | 11.96 | 1.44 | 0.993 | 13.27 | 13.37 | 1.61 | 0.993 | 10.8 | 11 | 2.05 | 0.983 | 25
Lawnton SD maximum demand | 40.45 | 40.99 | 6.63 | 0.987 | 27.91 | 28.29 | 4.57 | 0.987 | 30.86 | 31.27 | 5.06 | 0.987 | 27.91 | 27.91 | 0.07 | 1 | 40
Lawnton SN maximum demand | 40.69 | 41.28 | 6.98 | 0.986 | 28.44 | 28.69 | 3.77 | 0.991 | 31.43 | 31.71 | 4.17 | 0.991 | 27.94 | 28.44 | 5.33 | 0.982 | 40
Lawnton WD maximum demand | 32.08 | 32.09 | -0.66 | 1 | 21.03 | 21.53 | 4.59 | 0.977 | 22.25 | 22.78 | 4.85 | 0.977 | 20.24 | 20.24 | 0.08 | 1 | 40
Lawnton WN maximum demand | 37.05 | 37.05 | 0.73 | 1 | 24.05 | 24.73 | 5.79 | 0.972 | 25.44 | 26.17 | 6.13 | 0.972 | 22.99 | 23.01 | 0.97 | 0.999 | 40
Lockrose SD maximum demand | 5.33 | 6.11 | 2.99 | 0.872 | 6.12 | 6.39 | 1.83 | 0.958 | 7.58 | 7.92 | 2.27 | 0.958 | 7.18 | 7.56 | 2.37 | 0.95 | 15
Lockrose SN maximum demand | 6.21 | 6.98 | 3.2 | 0.889 | 6.67 | 6.95 | 1.95 | 0.96 | 8.27 | 8.62 | 2.41 | 0.96 | 7.83 | 8.23 | 2.52 | 0.952 | 15
Lockrose WD maximum demand | 4.27 | 4.67 | 1.88 | 0.915 | 3.66 | 3.7 | 0.54 | 0.989 | 4.17 | 4.22 | 0.62 | 0.989 | 4.14 | 4.2 | 0.74 | 0.984 | 15
Lockrose WN maximum demand | 5.02 | 5.41 | 2 | 0.929 | 4.45 | 4.51 | 0.72 | 0.987 | 5.07 | 5.13 | 0.82 | 0.987 | 5.02 | 5.11 | 0.92 | 0.984 | 15
Logan Village SD maximum demand | 3.11 | 4.38 | -3.09 | 0.709 | 6.34 | 6.5 | 1.43 | 0.975 | 7.67 | 7.86 | 1.73 | 0.975 | 7.57 | 7.82 | 1.95 | 0.968 | 25
Logan Village SN maximum demand | 2.55 | 4.41 | -3.6 | 0.579 | 6.48 | 6.66 | 1.56 | 0.972 | 7.83 | 8.05 | 1.89 | 0.972 | 7.73 | 8 | 2.09 | 0.965 | 25
Logan Village WD maximum demand | 2.52 | 4.23 | -3.39 | 0.596 | 4.54 | 4.56 | 0.43 | 0.995 | 5.07 | 5.09 | 0.49 | 0.995 | 5.17 | 5.24 | 0.81 | 0.988 | 25
Logan Village WN maximum demand | 2.27 | 4.31 | -3.67 | 0.527 | 5.67 | 5.71 | 0.63 | 0.994 | 6.33 | 6.37 | 0.7 | 0.994 | 6.46 | 6.53 | 0.92 | 0.99 | 25
Loganholme SD maximum demand | 26.66 | 26.79 | 2.68 | 0.995 | 25.13 | 25.2 | 1.8 | 0.997 | 28.19 | 28.26 | 2.02 | 0.997 | 25.47 | 25.57 | 2.3 | 0.996 | 50
Loganholme SN maximum demand | 25.1 | 25.16 | 1.7 | 0.998 | 24.38 | 24.39 | 0.73 | 1 | 27.35 | 27.36 | 0.82 | 1 | 24.71 | 24.75 | 1.36 | 0.998 | 50
Loganholme WD maximum demand | 17.86 | 18.42 | -4.5 | 0.97 | 17.84 | 18.54 | -5.03 | 0.962 | 20.14 | 20.92 | -5.68 | 0.962 | 19.96 | 20.04 | 1.79 | 0.996 | 50
Loganholme WN maximum demand | 19.82 | 20.24 | -4.09 | 0.979 | 18.31 | 18.97 | -4.94 | 0.966 | 20.67 | 21.41 | -5.57 | 0.966 | 20.49 | 20.53 | 1.29 | 0.998 | 50
Loganlea SD maximum demand | 21.17 | 21.22 | 1.42 | 0.998 | 16.47 | 16.57 | 1.85 | 0.994 | 17.98 | 18.1 | 2.02 | 0.994 | 17.42 | 17.58 | 2.39 | 0.991 | 50
Loganlea SN maximum demand | 20.93 | 20.93 | 0 | 1 | 14.84 | 14.84 | 0 | 1 | 16.2 | 16.2 | 0 | 1 | 15.7 | 15.72 | 0.59 | 0.999 | 50
Loganlea WD maximum demand | 17.75 | 18.14 | -3.77 | 0.978 | 14.25 | 14.88 | 4.28 | 0.958 | 16.04 | 16.74 | 4.82 | 0.958 | 16.15 | 16.8 | 4.63 | 0.961 | 50
Loganlea WN maximum demand | 19.81 | 20.19 | -3.88 | 0.981 | 14.1 | 14.51 | 3.43 | 0.972 | 15.86 | 16.33 | 3.86 | 0.972 | 15.97 | 16.42 | 3.82 | 0.973 | 50
Lomandra Drive SD maximum demand | 24.33 | 28.83 | 15.46 | 0.844 | 0 | 0 | 0 |  | 0 | 0 | 0
Lomandra Drive SN maximum demand | 19.29 | 22.57 | 11.72 | 0.855 | 0 | 0 | 0 |  | 0 | 0 | 0
Lomandra Drive WD maximum demand | 19.68 | 22.66 | 11.24 | 0.868 | 0 | 0 | 0 |  | 0 | 0 | 0
Lomandra Drive WN maximum demand | 17.04 | 19.44 | 9.35 | 0.877 | 0 | 0 | 0 |  | 0 | 0 | 0
Lota SD maximum demand | 24.39 | 25.25 | 6.56 | 0.966 | 17.1 | 17.12 | 0.79 | 0.999 | 18.35 | 18.37 | 0.85 | 0.999 | 15.28 | 15.33 | 1.24 | 0.997 | 42
Lota SN maximum demand | 26.91 | 28.05 | 7.9 | 0.96 | 20.37 | 20.45 | 1.78 | 0.996 | 21.87 | 21.95 | 1.91 | 0.996 | 18.29 | 18.45 | 2.43 | 0.991 | 42
Lota WD maximum demand | 22.62 | 22.73 | 2.2 | 0.995 | 16.89 | 17.31 | 3.82 | 0.975 | 19.12 | 19.6 | 4.33 | 0.975 | 17.95 | 18.65 | 5.07 | 0.962 | 42
Lota WN maximum demand | 27.38 | 27.81 | 4.89 | 0.984 | 18.91 | 19.56 | 5.02 | 0.966 | 21.41 | 22.15 | 5.69 | 0.966 | 20 | 20.02 | 0.88 | 0.999 | 42
Lowood SD maximum demand | 3.41 | 4.07 | 2.23 | 0.837 | 2.24 | 2.44 | 0.96 | 0.92 | 2.56 | 2.78 | 1.09 | 0.92 | 2.31 | 2.48 | 0.92 | 0.929 | 8
Lowood SN maximum demand | 3.67 | 4.29 | 2.21 | 0.857 | 2.09 | 2.23 | 0.78 | 0.936 | 2.39 | 2.55 | 0.9 | 0.936 | 2.15 | 2.31 | 0.84 | 0.932 | 8
Lowood WD maximum demand | 2.89 | 3.32 | 1.63 | 0.871 | 1.51 | 1.53 | 0.2 | 0.991 | 1.72 | 1.73 | 0.23 | 0.991 | 1.7 | 1.78 | 0.51 | 0.958 | 8
Lowood WN maximum demand | 3.26 | 3.69 | 1.73 | 0.883 | 1.57 | 1.61 | 0.32 | 0.98 | 1.79 | 1.82 | 0.36 | 0.98 | 1.77 | 1.83 | 0.49 | 0.964 | 8
Lytton A SD maximum demand | 28.45 | 28.79 | 4.37 | 0.988 | 25.64 | 26.38 | 6.19 | 0.972 | 26.64 | 27.41 | 6.43 | 0.972 | 26.4 | 26.46 | 1.81 | 0.998 | 65
Lytton A SN maximum demand | 27.09 | 27.32 | 3.53 | 0.992 | 25.44 | 26.31 | 6.69 | 0.967 | 26.44 | 27.34 | 6.95 | 0.967 | 26.2 | 26.27 | 1.91 | 0.997 | 65
Lytton A WD maximum demand | 24.45 | 24.56 | 2.33 | 0.995 | 23.97 | 24.57 | 5.39 | 0.976 | 24.42 | 25.03 | 5.49 | 0.976 | 25 | 25.01 | 0.87 | 0.999 | 65
Lytton A WN maximum demand | 23.89 | 23.94 | 1.62 | 0.998 | 23.81 | 24.45 | 5.52 | 0.974 | 24.26 | 24.91 | 5.63 | 0.974 | 24.83 | 24.84 | 0.46 | 1 | 65
Lytton B SD maximum demand | 21.46 | 24.96 | 12.74 | 0.86 | 16.9 | 17.59 | 4.9 | 0.96 | 19.35 | 20.15 | 5.62 | 0.96 | 20.5 | 21.78 | 7.36 | 0.941 | 40
Lytton B SN maximum demand | 19.7 | 22.78 | 11.43 | 0.865 | 15.36 | 15.99 | 4.42 | 0.961 | 17.6 | 18.31 | 5.06 | 0.961 | 18.84 | 19.78 | 6.03 | 0.952 | 40
Lytton B WD maximum demand | 17.85 | 20.85 | 10.77 | 0.856 | 10.69 | 12.12 | 5.72 | 0.881 | 10.82 | 12.28 | 5.8 | 0.881 | 15.34 | 15.95 | 4.36 | 0.962 | 40
Lytton B WN maximum demand | 16.36 | 18.69 | 9.05 | 0.875 | 10.4 | 11.92 | 5.82 | 0.873 | 10.54 | 12.08 | 5.9 | 0.873 | 14.71 | 15.02 | 3.04 | 0.979 | 40
Makerston St SD maximum demand | 105.27 | 108.03 | 24.24 | 0.974 | 63.39 | 63.46 | 3.03 | 0.999 | 68.54 | 68.62 | 3.28 | 0.999 | 64.71 | 64.71 | 0.16 | 1 | 150
Makerston St SN maximum demand | 85.51 | 86.23 | 11.12 | 0.992 | 56.73 | 56.73 | -0.14 | 1 | 61.34 | 61.34 | -0.15 | 1 | 57.87 | 57.96 | 3.34 | 0.998 | 150
Makerston St WD maximum demand | 77.03 | 77.61 | 9.47 | 0.993 | 48.13 | 48.25 | -3.49 | 0.997 | 48.42 | 48.55 | -3.51 | 0.997 | 47.93 | 47.95 | 1.19 | 1 | 150
Makerston St WN maximum demand | 68.94 | 68.99 | 2.72 | 0.999 | 44.39 | 44.66 | -4.9 | 0.994 | 44.66 | 44.93 | -4.93 | 0.994 | 44.21 | 44.23 | 1.14 | 1 | 150
Maleny SD maximum demand | 7.64 | 7.8 | 1.56 | 0.98 | 5.46 | 5.47 | -0.15 | 1 | 5.64 | 5.65 | -0.16 | 1 | 5.17 | 5.3 | 1.16 | 0.976 | 10
Maleny SN maximum demand | 8.23 | 8.34 | 1.31 | 0.988 | 5.59 | 5.72 | 1.21 | 0.978 | 5.78 | 5.91 | 1.25 | 0.978 | 5.29 | 5.37 | 0.93 | 0.985 | 10
Maleny WD maximum demand | 8.57 | 8.59 | 0.56 | 0.998 | 7.22 | 7.25 | 0.57 | 0.997 | 7.84 | 7.87 | 0.62 | 0.997 | 7.85 | 7.88 | 0.78 | 0.995 | 10
Maleny WN maximum demand | 9.87 | 9.89 | 0.7 | 0.997 | 7.76 | 7.77 | 0.39 | 0.999 | 8.42 | 8.43 | 0.42 | 0.999 | 8.43 | 8.47 | 0.88 | 0.995 | 10
Mango Hill Bus 1 SD maximum demand | 29.11 | 30.39 | 8.73 | 0.958 | 19.66 | 20.05 | 3.93 | 0.981 | 25.29 | 25.79 | 5.06 | 0.981 | 33.61 | 33.78 | 3.32 | 0.995 | 50
Mango Hill Bus 1 SN maximum demand | 27.98 | 29.24 | 8.5 | 0.957 | 18.97 | 19.26 | 3.35 | 0.985 | 24.4 | 24.77 | 4.3 | 0.985 | 32.39 | 32.51 | 2.76 | 0.996 | 50
Mango Hill Bus 1 WD maximum demand | 24.33 | 24.67 | 4.06 | 0.986 | 11.45 | 11.48 | 0.85 | 0.997 | 12.46 | 12.5 | 0.92 | 0.997 | 13.38 | 13.5 | 1.77 | 0.991 | 50
Mango Hill Bus 1 WN maximum demand | 28.94 | 29.33 | 4.78 | 0.987 | 12.71 | 12.72 | 0.39 | 1 | 13.83 | 13.84 | 0.43 | 1 | 14.92 | 15.06 | 2.06 | 0.991 | 50
Mango Hill Bus 2 SD maximum demand |  |  |  |  | 12.73 | 13.01 | 2.67 | 0.979 | 14.5 | 14.81 | 3.04 | 0.979 | 12.39 | 12.66 | 2.6 | 0.979 | 25
Mango Hill Bus 2 SN maximum demand |  |  |  |  | 13.49 | 13.72 | 2.48 | 0.984 | 15.36 | 15.62 | 2.82 | 0.984 | 13.56 | 13.79 | 2.49 | 0.984 | 25
Mango Hill Bus 2 WD maximum demand |  |  |  |  | 8.43 | 8.44 | 0.46 | 0.999 | 9.18 | 9.19 | 0.5 | 0.999 | 9.35 | 9.36 | 0.51 | 0.999 | 25
Mango Hill Bus 2 WN maximum demand |  |  |  |  | 9.97 | 10.01 | 0.8 | 0.997 | 10.85 | 10.89 | 0.87 | 0.997 | 11.06 | 11.09 | 0.89 | 0.997 | 25
Mango Hill North SD maximum demand | 16.3749 | 16.3757 | 0.155 | 0.99996 | 0 | 0 | 0 |  | 0 | 0 | 0
Mango Hill North SN maximum demand | 15.8183 | 15.8203 | -0.24737 | 0.99988 | 0 | 0 | 0 |  | 0 | 0 | 0
Mango Hill North WD maximum demand | 10.2006 | 10.5173 | -2.5613 | 0.96989 | 0 | 0 | 0 |  | 0 | 0 | 0
Mango Hill North WN maximum demand | 11.5561 | 11.8523 | -2.6335 | 0.975 | 0 | 0 | 0 |  | 0 | 0 | 0
Marburg SD maximum demand | 4.36 | 4.63 | 1.56 | 0.941 | 3.38 | 3.73 | 1.57 | 0.907 | 4.23 | 4.66 | 1.96 | 0.907 | 3.84 | 4.09 | 1.4 | 0.939 | 5
Marburg SN maximum demand | 4.16 | 4.24 | 0.84 | 0.98 | 3.22 | 3.36 | 0.95 | 0.959 | 4.03 | 4.2 | 1.18 | 0.959 | 3.65 | 3.74 | 0.82 | 0.976 | 5
Marburg WD maximum demand | 3.47 | 3.53 | 0.66 | 0.982 | 2.78 | 2.97 | 1.05 | 0.935 | 3.08 | 3.3 | 1.17 | 0.935 | 3.08 | 3.17 | 0.78 | 0.969 | 5
Marburg WN maximum demand | 3.33 | 3.34 | 0.08 | 1 | 2.83 | 3.03 | 1.09 | 0.933 | 3.14 | 3.36 | 1.21 | 0.933 | 3.13 | 3.2 | 0.66 | 0.979 | 5
McLachlan St SD maximum demand | 70.95 | 73.29 | 18.35 | 0.968 | 45.36 | 45.49 | 3.36 | 0.997 | 51.74 | 51.89 | 3.83 | 0.997 | 46.77 | 46.79 | 1.2 | 1 | 120
McLachlan St SN maximum demand | 61.85 | 63.27 | 13.35 | 0.978 | 39.94 | 40.36 | 5.75 | 0.99 | 45.56 | 46.03 | 6.55 | 0.99 | 41.8 | 42.01 | 4.17 | 0.995 | 120
McLachlan St WD maximum demand | 45.49 | 45.7 | 4.3 | 0.996 | 29.76 | 31.65 | 10.79 | 0.94 | 31.68 | 33.69 | 11.48 | 0.94 | 30.64 | 30.78 | 3.02 | 0.995 | 120
McLachlan St WN maximum demand | 43.42 | 43.43 | 0.65 | 1 | 29.27 | 30.24 | 7.59 | 0.968 | 31.16 | 32.19 | 8.08 | 0.968 | 31.28 | 31.29 | 0.96 | 1 | 120
Meeandah SD maximum demand | 39 | 43.78 | 19.89 | 0.891 | 24.84 | 29.44 | 15.8 | 0.844 | 24.56 | 29.11 | 15.62 | 0.844 | 23.45 | 24.13 | 5.66 | 0.972 | 50
Meeandah SN maximum demand | 33.84 | 37.15 | 15.32 | 0.911 | 22.69 | 26.34 | 13.39 | 0.861 | 22.43 | 26.05 | 13.24 | 0.861 | 21.38 | 21.81 | 4.34 | 0.98 | 50
Meeandah WD maximum demand | 34.4 | 37.4 | 14.67 | 0.92 | 21.47 | 25.12 | 13.04 | 0.855 | 20.97 | 24.54 | 12.74 | 0.855 | 20.44 | 20.72 | 3.42 | 0.986 | 50
Meeandah WN maximum demand | 32.29 | 34.61 | 12.47 | 0.933 | 20.48 | 23.62 | 11.77 | 0.867 | 20.01 | 23.08 | 11.49 | 0.867 | 19.5 | 19.62 | 2.24 | 0.993 | 50
Merrimac SD maximum demand | 29.34 | 29.83 | 5.37 | 0.984 | 25.23 | 26.34 | 7.56 | 0.958 | 29.61 | 30.91 | 8.87 | 0.958 | 26.69 | 26.83 | 2.76 | 0.995 | 60
Merrimac SN maximum demand | 29.01 | 29.33 | 4.32 | 0.989 | 25.31 | 26.19 | 6.74 | 0.966 | 29.71 | 30.74 | 7.91 | 0.966 | 26.78 | 26.85 | 2.02 | 0.997 | 60
Merrimac WD maximum demand | 22.37 | 22.42 | -1.48 | 0.998 | 21.51 | 21.78 | 3.43 | 0.988 | 23.23 | 23.52 | 3.71 | 0.988 | 22.98 | 23.32 | 4 | 0.985 | 60
Merrimac WN maximum demand | 24.59 | 24.6 | -0.68 | 1 | 23.6 | 23.95 | 4.11 | 0.985 | 25.48 | 25.87 | 4.44 | 0.985 | 25.21 | 25.6 | 4.5 | 0.984 | 60
Miami SD maximum demand | 28.07 | 28.14 | -2.07 | 0.997 | 19.52 | 19.56 | 1.31 | 0.998 | 21.42 | 21.47 | 1.44 | 0.998 | 19.48 | 19.64 | 2.5 | 0.992 | 40
Miami SN maximum demand | 30.39 | 30.49 | -2.38 | 0.997 | 21.93 | 21.97 | 1.34 | 0.998 | 24.07 | 24.11 | 1.47 | 0.998 | 21.89 | 22.02 | 2.43 | 0.994 | 40
Miami WD maximum demand | 24.8 | 25.91 | -7.52 | 0.957 | 20.67 | 21.05 | 3.98 | 0.982 | 22.44 | 22.86 | 4.32 | 0.982 | 22.43 | 22.43 | 0.22 | 1 | 40
Miami WN maximum demand | 29.41 | 29.97 | -5.74 | 0.982 | 23.98 | 24.48 | 4.92 | 0.98 | 26.04 | 26.58 | 5.34 | 0.98 | 26.02 | 26.03 | 0.83 | 0.999 | 40
Milton SD maximum demand | 61.82 | 61.82 | 0.68 | 1 | 54.9 | 55.11 | 4.74 | 0.996 | 58.97 | 59.19 | 5.09 | 0.996 | 54.09 | 54.09 | 0.62 | 1 | 120
Milton SN maximum demand | 50.56 | 51.14 | -7.65 | 0.989 | 48.02 | 48.05 | 1.82 | 0.999 | 51.57 | 51.61 | 1.95 | 0.999 | 47.31 | 47.34 | 1.84 | 0.999 | 120
Milton WD maximum demand | 41.46 | 42.91 | -11.06 | 0.966 | 35.8 | 35.97 | 3.55 | 0.995 | 35.8 | 35.97 | 3.55 | 0.995 | 35.94 | 35.96 | 1.3 | 0.999 | 120
Milton WN maximum demand | 39.11 | 42.16 | -15.75 | 0.928 | 34.2 | 35.49 | 9.48 | 0.964 | 34.2 | 35.49 | 9.48 | 0.964 | 34.33 | 34.4 | 2.19 | 0.998 | 120
Moggill SD maximum demand | 17.47 | 17.75 | -3.13 | 0.984 | 14.37 | 14.97 | 4.22 | 0.959 | 16.03 | 16.7 | 4.71 | 0.959 | 14.42 | 14.42 | 0.07 | 1 | 40
Moggill SN maximum demand | 18.4 | 18.67 | -3.17 | 0.985 | 14.18 | 14.8 | 4.23 | 0.958 | 15.82 | 16.51 | 4.72 | 0.958 | 14.24 | 15.12 | 5.08 | 0.942 | 40
Moggill WD maximum demand | 15.33 | 16.48 | -6.06 | 0.93 | 10.42 | 10.55 | 1.64 | 0.988 | 12.51 | 12.67 | 1.97 | 0.988 | 12.09 | 12.4 | 2.76 | 0.975 | 40
Moggill WN maximum demand | 17.19 | 17.88 | -4.92 | 0.961 | 11.09 | 11.25 | 1.88 | 0.986 | 13.32 | 13.51 | 2.26 | 0.986 | 12.84 | 13.26 | 3.34 | 0.968 | 40
Molendinar SD maximum demand | 43.06 | 43.45 | 5.81 | 0.991 | 36.67 | 36.89 | 4.09 | 0.994 | 40.93 | 41.19 | 4.57 | 0.994 | 37.83 | 37.86 | 1.39 | 0.999 | 60
Molendinar SN maximum demand | 37.76 | 37.78 | 1.24 | 0.999 | 33.09 | 33.32 | 3.93 | 0.993 | 36.94 | 37.2 | 4.39 | 0.993 | 34.42 | 34.63 | 3.78 | 0.994 | 60
Molendinar WD maximum demand | 35.52 | 35.55 | 1.33 | 0.999 | 29.32 | 29.57 | 3.77 | 0.992 | 32.02 | 32.29 | 4.12 | 0.992 | 31.74 | 31.8 | 2.03 | 0.998 | 60
Molendinar WN maximum demand | 32.62 | 32.66 | -1.67 | 0.999 | 28.73 | 28.85 | 2.63 | 0.996 | 31.37 | 31.5 | 2.87 | 0.996 | 31.09 | 31.09 | 0.14 | 1 | 60
Montville SD maximum demand | 3.91 | 4.32 | 1.85 | 0.903 | 0 | 0 | 0 |  | 0 | 0 | 0
Montville SN maximum demand | 4.08 | 4.47 | 1.81 | 0.914 | 0 | 0 | 0 |  | 0 | 0 | 0
Montville WD maximum demand | 3.3 | 3.48 | 1.1 | 0.948 | 0 | 0 | 0 |  | 0 | 0 | 0
Montville WN maximum demand | 3.92 | 4.1 | 1.22 | 0.955 | 0 | 0 | 0 |  | 0 | 0 | 0
Mooloolaba SD maximum demand | 60.39 | 60.85 | 7.43 | 0.993 | 27.8 | 28.74 | 7.26 | 0.968 | 31.89 | 32.96 | 8.33 | 0.968 | 29.3 | 29.43 | 2.78 | 0.996 | 60
Mooloolaba SN maximum demand | 61.71 | 61.8 | 3.23 | 0.999 | 28.02 | 28.83 | 6.77 | 0.972 | 32.14 | 33.06 | 7.77 | 0.972 | 29.53 | 29.57 | 1.51 | 0.999 | 60
Mooloolaba WD maximum demand | 41.82 | 42.02 | -4.1 | 0.995 | 24.09 | 24.24 | 2.66 | 0.994 | 26.5 | 26.66 | 2.92 | 0.994 | 26.68 | 26.87 | 3.2 | 0.993 | 60
Mooloolaba WN maximum demand | 45.41 | 45.54 | -3.42 | 0.997 | 26.83 | 27 | 3.01 | 0.994 | 29.51 | 29.69 | 3.31 | 0.994 | 29.71 | 29.91 | 3.44 | 0.993 | 60
Moorooka SD maximum demand | 13.62 | 16.49 | 9.3 | 0.826 | 15.41 | 17.24 | 7.74 | 0.894 | 17.69 | 19.79 | 8.88 | 0.894 | 17.16 | 17.92 | 5.16 | 0.958 | 50
Moorooka SN maximum demand | 11.91 | 14.16 | 7.65 | 0.841 | 14.49 | 15.96 | 6.69 | 0.908 | 16.64 | 18.33 | 7.68 | 0.908 | 16.22 | 16.69 | 3.94 | 0.972 | 50
Moorooka WD maximum demand | 11.43 | 12.92 | 6.01 | 0.885 | 13.12 | 14.08 | 5.11 | 0.932 | 14.55 | 15.61 | 5.66 | 0.932 | 15.75 | 15.91 | 2.23 | 0.99 | 50
Moorooka WN maximum demand | 11.13 | 12.42 | 5.52 | 0.896 | 12.95 | 13.94 | 5.17 | 0.929 | 14.35 | 15.46 | 5.73 | 0.929 | 15.76 | 15.87 | 1.85 | 0.993 | 50
Morayfield SD maximum demand | 21.04 | 21.2 | 2.55 | 0.993 | 21.95 | 22.6 | 5.39 | 0.971 | 24.55 | 25.28 | 6.03 | 0.971 | 22.28 | 22.37 | 1.98 | 0.996 | 45
Morayfield SN maximum demand | 19.45 | 19.58 | 2.2 | 0.994 | 22.4 | 23.02 | 5.3 | 0.973 | 25.06 | 25.75 | 5.93 | 0.973 | 22.74 | 22.81 | 1.79 | 0.997 | 45
Morayfield WD maximum demand | 18.31 | 18.31 | 0.06 | 1 | 15.23 | 15.34 | 1.8 | 0.993 | 16.25 | 16.37 | 1.92 | 0.993 | 16.14 | 16.51 | 3.47 | 0.978 | 45
Morayfield WN maximum demand | 20.83 | 20.83 | 0.22 | 1 | 17.49 | 17.57 | 1.63 | 0.996 | 18.66 | 18.74 | 1.74 | 0.996 | 18.53 | 18.89 | 3.63 | 0.981 | 45
Morayfield East SD maximum demand | 12.92 | 14.23 | 5.97 | 0.908 | 0 | 0 | 0 |  | 0 | 0 | 0
Morayfield East SN maximum demand | 12.73 | 13.83 | 5.41 | 0.92 | 0 | 0 | 0 |  | 0 | 0 | 0
Morayfield East WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Morayfield East WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Morayfield North SD maximum demand | 27.34 | 30.47 | 13.44 | 0.897 | 23.64 | 25.8 | 10.32 | 0.916 | 27.46 | 29.96 | 11.99 | 0.916 | 25.24 | 27.83 | 11.72 | 0.907 | 50
Morayfield North SN maximum demand | 25.02 | 27.62 | 11.7 | 0.906 | 23.81 | 25.37 | 8.76 | 0.939 | 27.66 | 29.47 | 10.17 | 0.939 | 25.12 | 27.36 | 10.84 | 0.918 | 50
Morayfield North WD maximum demand | 19.57 | 20.94 | 7.44 | 0.935 | 18.06 | 18.65 | 4.67 | 0.968 | 20.58 | 21.25 | 5.32 | 0.968 | 20.45 | 21.58 | 6.89 | 0.948 | 50
Morayfield North WN maximum demand | 22.22 | 23.42 | 7.41 | 0.949 | 18.82 | 19.3 | 4.28 | 0.975 | 21.44 | 21.99 | 4.88 | 0.975 | 21.32 | 22.17 | 6.1 | 0.961 | 50
Moy Pocket SD maximum demand | 3.98 | 4.42 | 1.91 | 0.901 | 0 | 0 | 0 |  | 0 | 0 | 0
Moy Pocket SN maximum demand | 4.04 | 4.36 | 1.65 | 0.926 | 0 | 0 | 0 |  | 0 | 0 | 0
Moy Pocket WD maximum demand | 3.96 | 4.26 | 1.57 | 0.93 | 0 | 0 | 0 |  | 0 | 0 | 0
Moy Pocket WN maximum demand | 4.02 | 4.29 | 1.49 | 0.938 | 0 | 0 | 0 |  | 0 | 0 | 0
Mt Cotton SD maximum demand | 7.49 | 9 | 5 | 0.832 | 6.76 | 7.46 | 3.14 | 0.907 | 7.81 | 8.61 | 3.63 | 0.907 | 7.26 | 8.23 | 3.87 | 0.882 | 14
Mt Cotton SN maximum demand | 6.41 | 7.68 | 4.23 | 0.835 | 6.84 | 7.26 | 2.44 | 0.942 | 7.89 | 8.38 | 2.82 | 0.942 | 7.34 | 8.29 | 3.85 | 0.885 | 14
Mt Cotton WD maximum demand | 6.5 | 7.84 | 4.38 | 0.829 | 6.73 | 7.28 | 2.78 | 0.924 | 7.36 | 7.97 | 3.04 | 0.924 | 7.56 | 8.58 | 4.04 | 0.882 | 14
Mt Cotton WN maximum demand | 5.82 | 6.97 | 3.83 | 0.835 | 6.17 | 6.54 | 2.18 | 0.943 | 6.75 | 7.16 | 2.39 | 0.943 | 6.93 | 7.8 | 3.59 | 0.888 | 14
Mt Crosby West SD maximum demand | 12.58 | 12.58 | 0.27 | 1 | 11.15 | 12.1 | 4.71 | 0.921 | 12.66 | 13.75 | 5.35 | 0.921 | 11.36 | 12.26 | 4.6 | 0.927 | 20
Mt Crosby West SN maximum demand | 12.51 | 12.51 | 0.41 | 0.999 | 9.83 | 10.73 | 4.3 | 0.916 | 11.16 | 12.19 | 4.89 | 0.916 | 10.01 | 10.89 | 4.29 | 0.919 | 20
Mt Crosby West WD maximum demand | 9.9 | 9.94 | -0.88 | 0.996 | 7.13 | 7.67 | 2.84 | 0.929 | 6.97 | 7.51 | 2.78 | 0.929 | 6.85 | 7.4 | 2.81 | 0.925 | 20
Mt Crosby West WN maximum demand | 12.12 | 12.12 | -0.11 | 1 | 8.25 | 8.99 | 3.57 | 0.918 | 8.08 | 8.8 | 3.5 | 0.918 | 7.93 | 8.51 | 3.09 | 0.932 | 20
Mt Gravatt SD maximum demand | 27.68 | 31.22 | 14.43 | 0.887 | 24.31 | 24.67 | 4.19 | 0.985 | 26.45 | 26.84 | 4.56 | 0.985 | 23.02 | 23.02 | 0.3 | 1 | 50
Mt Gravatt SN maximum demand | 27.84 | 31.27 | 14.24 | 0.89 | 24.18 | 24.48 | 3.8 | 0.988 | 26.3 | 26.63 | 4.14 | 0.988 | 22.9 | 22.9 | 0.34 | 1 | 50
Mt Gravatt WD maximum demand | 24.38 | 25.92 | 8.79 | 0.941 | 20.9 | 21.45 | 4.82 | 0.974 | 23.74 | 24.37 | 5.48 | 0.974 | 22.78 | 22.91 | 2.44 | 0.994 | 50
Mt Gravatt WN maximum demand | 28.02 | 29.94 | 10.57 | 0.936 | 23.1 | 23.12 | 0.91 | 0.999 | 26.24 | 26.26 | 1.04 | 0.999 | 25.1 | 25.3 | 3.23 | 0.992 | 50
Mt Sylvia SD maximum demand | 0.74 | 0.88 | 0.48 | 0.84 | 1.04 | 1.24 | 0.67 | 0.843 | 1.04 | 1.24 | 0.67 | 0.843 | 0.94 | 1.12 | 0.61 | 0.841 | 3
Mt Sylvia SN maximum demand | 0.7 | 0.8 | 0.38 | 0.88 | 1.07 | 1.22 | 0.59 | 0.875 | 1.07 | 1.22 | 0.59 | 0.875 | 0.96 | 1.09 | 0.52 | 0.88 | 3
Mt Sylvia WD maximum demand | 0.84 | 1 | 0.54 | 0.841 | 0.64 | 0.75 | 0.4 | 0.848 | 0.64 | 0.75 | 0.4 | 0.848 | 0.63 | 0.75 | 0.4 | 0.842 | 3
Mt Sylvia WN maximum demand | 0.91 | 1.04 | 0.51 | 0.872 | 0.8 | 0.94 | 0.5 | 0.848 | 0.8 | 0.94 | 0.5 | 0.848 | 0.79 | 0.92 | 0.47 | 0.86 | 3
Mt Tamborine Bus 1 SD maximum demand | 9.27 | 9.41 | -1.61 | 0.985 | 6.41 | 6.77 | 2.18 | 0.947 | 6.18 | 6.53 | 2.1 | 0.947 | 5.81 | 6.13 | 1.98 | 0.946 | 18
Mt Tamborine Bus 1 SN maximum demand | 9.79 | 9.95 | -1.79 | 0.984 | 7.21 | 7.39 | 1.59 | 0.977 | 6.95 | 7.12 | 1.53 | 0.977 | 7.2 | 7.49 | 2.07 | 0.961 | 18
Mt Tamborine Bus 1 WD maximum demand | 13.19 | 13.43 | -2.52 | 0.982 | 5.81 | 5.89 | 0.96 | 0.986 | 6.48 | 6.57 | 1.08 | 0.986 | 7.25 | 7.39 | 1.42 | 0.981 | 18
Mt Tamborine Bus 1 WN maximum demand | 15.26 | 15.38 | -1.96 | 0.992 | 6.41 | 6.5 | 1.1 | 0.986 | 7.15 | 7.26 | 1.22 | 0.986 | 8.07 | 8.23 | 1.59 | 0.981 | 18
Mt Tamborine Bus 2 SD maximum demand |  |  |  |  | 6.94 | 7.12 | 1.6 | 0.974 | 7.58 | 7.78 | 1.75 | 0.974 | 7.89 | 8.23 | 2.33 | 0.959 | 15
Mt Tamborine Bus 2 SN maximum demand |  |  |  |  | 7.13 | 7.29 | 1.52 | 0.978 | 7.8 | 7.97 | 1.66 | 0.978 | 8.09 | 8.36 | 2.1 | 0.968 | 15
Mt Tamborine Bus 2 WD maximum demand |  |  |  |  | 10.01 | 10.13 | 1.57 | 0.988 | 9.81 | 9.93 | 1.54 | 0.988 | 5.29 | 5.38 | 1.01 | 0.982 | 15
Mt Tamborine Bus 2 WN maximum demand |  |  |  |  | 11.78 | 11.96 | 2.11 | 0.984 | 11.54 | 11.72 | 2.07 | 0.984 | 6.41 | 6.53 | 1.25 | 0.982 | 15
Mudgeeraba West Pkg SD maximum demand | 23.26 | 24.78 | 8.54 | 0.939 | 16.5 | 17.13 | 4.59 | 0.963 | 16.06 | 16.67 | 4.47 | 0.963 | 13.83 | 14.56 | 4.55 | 0.95 | 37
Mudgeeraba West Pkg SN maximum demand | 23.86 | 25.22 | 8.18 | 0.946 | 17.43 | 17.92 | 4.16 | 0.973 | 16.96 | 17.44 | 4.05 | 0.973 | 14.42 | 15.07 | 4.37 | 0.957 | 37
Mudgeeraba West Pkg WD maximum demand | 19.33 | 19.87 | 4.6 | 0.973 | 11.9 | 12 | 1.55 | 0.992 | 13.78 | 13.89 | 1.79 | 0.992 | 14.01 | 14.29 | 2.81 | 0.981 | 37
Mudgeeraba West Pkg WN maximum demand | 22.48 | 23.12 | 5.39 | 0.972 | 13.64 | 13.8 | 2.11 | 0.988 | 15.79 | 15.98 | 2.44 | 0.988 | 15.91 | 16.22 | 3.18 | 0.981 | 37
Murarrie SD maximum demand | 25.25 | 25.81 | 5.33 | 0.978 | 20.61 | 20.69 | 1.81 | 0.996 | 21.65 | 21.74 | 1.9 | 0.996 | 21.19 | 21.3 | 2.18 | 0.995 | 50
Murarrie SN maximum demand | 21.39 | 21.52 | 2.31 | 0.994 | 17.61 | 17.63 | -0.76 | 0.999 | 18.5 | 18.52 | -0.8 | 0.999 | 20.17 | 20.19 | 0.99 | 0.999 | 50
Murarrie WD maximum demand | 18.51 | 18.56 | 1.35 | 0.997 | 15.25 | 15.58 | 3.19 | 0.979 | 16.12 | 16.47 | 3.37 | 0.979 | 17.63 | 17.94 | 3.32 | 0.983 | 50
Murarrie WN maximum demand | 16.74 | 16.75 | -0.46 | 1 | 14.77 | 15.08 | 3.08 | 0.979 | 15.6 | 15.94 | 3.26 | 0.979 | 17.22 | 17.47 | 2.94 | 0.986 | 50
Murrumba SD maximum demand | 2.3 | 2.39 | 0.66 | 0.961 | 2.32 | 2.37 | 0.48 | 0.979 | 2.32 | 2.37 | 0.48 | 0.979 | 2.08 | 2.25 | 0.85 | 0.926 | 8
Murrumba SN maximum demand | 2.2 | 2.29 | 0.63 | 0.961 | 2.38 | 2.44 | 0.51 | 0.978 | 2.38 | 2.44 | 0.51 | 0.978 | 2.14 | 2.32 | 0.89 | 0.923 | 8
Murrumba WD maximum demand | 1.8 | 1.81 | 0.2 | 0.994 | 0.23 | 0.24 | 0.05 | 0.977 | 0.23 | 0.24 | 0.05 | 0.977 | 0.23 | 0.24 | 0.07 | 0.961 | 8
Murrumba WN maximum demand | 1.98 | 2.01 | 0.31 | 0.988 | 0.18 | 0.19 | 0.06 | 0.949 | 0.18 | 0.19 | 0.06 | 0.949 | 0.18 | 0.19 | 0.05 | 0.959 | 8
Myrtletown SD maximum demand | 20.85 | 21.29 | 4.33 | 0.979 | 22.33 | 22.79 | 4.56 | 0.98 | 25.74 | 26.27 | 5.26 | 0.98 | 23.27 | 23.83 | 5.14 | 0.976 | 50
Myrtletown SN maximum demand | 19.17 | 19.41 | 3.05 | 0.988 | 21.19 | 21.55 | 3.95 | 0.983 | 24.43 | 24.84 | 4.55 | 0.983 | 22.08 | 22.51 | 4.37 | 0.981 | 50
Myrtletown WD maximum demand | 12.79 | 12.8 | -0.25 | 1 | 20.34 | 20.56 | 2.94 | 0.99 | 21.94 | 22.17 | 3.18 | 0.99 | 21.7 | 21.89 | 2.87 | 0.991 | 50
Myrtletown WN maximum demand | 12.52 | 12.52 | -0.3 | 1 | 19.84 | 19.98 | 2.37 | 0.993 | 21.4 | 21.55 | 2.55 | 0.993 | 21.17 | 21.33 | 2.62 | 0.992 | 50
Nambour SD maximum demand | 33.52 | 37.53 | 16.89 | 0.893 | 30.05 | 30.41 | 4.71 | 0.988 | 34.63 | 35.05 | 5.42 | 0.988 | 31.37 | 31.66 | 4.26 | 0.991 | 50
Nambour SN maximum demand | 31.24 | 33.87 | 13.11 | 0.922 | 27.88 | 28.11 | 3.62 | 0.992 | 32.12 | 32.39 | 4.18 | 0.992 | 29.1 | 29.13 | 1.32 | 0.999 | 50
Nambour WD maximum demand | 25.6 | 27.05 | 8.74 | 0.946 | 25.41 | 26.1 | 5.98 | 0.973 | 27.05 | 27.79 | 6.37 | 0.973 | 26.9 | 28.08 | 8.03 | 0.958 | 50
Nambour WN maximum demand | 26.73 | 27.86 | 7.85 | 0.959 | 27.39 | 28.05 | 6.06 | 0.976 | 29.17 | 29.87 | 6.45 | 0.976 | 29 | 29.95 | 7.47 | 0.968 | 50
Narangba SD maximum demand | 22.18 | 22.51 | 3.81 | 0.986 | 14.82 | 15.21 | 3.41 | 0.975 | 15.65 | 16.06 | 3.6 | 0.975 |  |  |  |  | 45
Narangba SN maximum demand | 22.27 | 22.37 | 2.1 | 0.996 | 15.14 | 15.51 | 3.37 | 0.976 | 15.99 | 16.38 | 3.56 | 0.976 |  |  |  |  | 45
Narangba WD maximum demand | 22.95 | 23.16 | 3.09 | 0.991 | 12.69 | 13.02 | 2.93 | 0.974 | 14.29 | 14.67 | 3.3 | 0.974 | 14.27 | 14.93 | 4.38 | 0.956 | 45
Narangba WN maximum demand | 23.22 | 23.25 | 1.05 | 0.999 | 13.1 | 13.36 | 2.63 | 0.98 | 14.75 | 15.05 | 2.96 | 0.98 | 14.74 | 15.12 | 3.36 | 0.975 | 45
Narangba Bus 1 SD maximum demand | [12 empty] | 8.02 | 8.23 | 1.87 | 0.974 | 25
Narangba Bus 1 SN maximum demand | [12 empty] | 8.16 | 8.35 | 1.78 | 0.977 | 25
Narangba Bus 1 WD maximum demand | [16 empty] | 25
Narangba Bus 1 WN maximum demand | [16 empty] | 25
Narangba Bus 2 SD maximum demand | [12 empty] | 7.14 | 7.33 | 1.64 | 0.975 | 20
Narangba Bus 2 SN maximum demand | [12 empty] | 7.27 | 7.44 | 1.6 | 0.977 | 20
Narangba Bus 2 WD maximum demand | [16 empty] | 20
Narangba Bus 2 WN maximum demand | [16 empty] | 20
Nerang SD maximum demand | 59.14 | 59.51 | 6.64 | 0.994 | 47.23 | 49.91 | 16.12 | 0.946 | 55.27 | 58.4 | 18.87 | 0.946 | 49.9 | 50.08 | 4.23 | 0.996 | 120
Nerang SN maximum demand | 57.98 | 58.16 | 4.57 | 0.997 | 46.83 | 49.17 | 14.99 | 0.952 | 54.79 | 57.53 | 17.53 | 0.952 | 49.47 | 49.56 | 2.82 | 0.998 | 120
Nerang WD maximum demand | 44.17 | 44.73 | -7.03 | 0.988 | 38.13 | 38.91 | 7.78 | 0.98 | 40.48 | 41.31 | 8.26 | 0.98 | 40.16 | 40.43 | 4.62 | 0.993 | 120
Nerang WN maximum demand | 49.24 | 49.58 | -5.84 | 0.993 | 42.41 | 43.08 | 7.59 | 0.984 | 45.02 | 45.74 | 8.06 | 0.984 | 44.67 | 44.97 | 5.14 | 0.993 | 120
Newmarket SD maximum demand | 22.21 | 22.38 | 2.82 | 0.992 | 21.92 | 22.35 | 4.35 | 0.981 | 24.47 | 24.95 | 4.85 | 0.981 | 22.23 | 22.25 | 0.85 | 0.999 | 30
Newmarket SN maximum demand | 21.3 | 21.4 | 2 | 0.996 | 21.49 | 21.82 | 3.75 | 0.985 | 23.99 | 24.35 | 4.19 | 0.985 | 21.8 | 21.8 | 0.33 | 1 | 30
Newmarket WD maximum demand | 17.72 | 17.89 | -2.52 | 0.99 | 17.11 | 17.83 | 5.01 | 0.96 | 19.24 | 20.05 | 5.63 | 0.96 | 19.16 | 19.22 | 1.56 | 0.997 | 30
Newmarket WN maximum demand | 19.74 | 19.76 | -0.82 | 0.999 | 18.76 | 19.61 | 5.72 | 0.957 | 21.1 | 22.06 | 6.43 | 0.957 | 21 | 21.17 | 2.67 | 0.992 | 30
Newstead SD maximum demand | 52.96 | 53.22 | 5.31 | 0.995 | 30.43 | 31.39 | 7.7 | 0.969 | 38.03 | 39.23 | 9.62 | 0.969 | 39.28 | 39.32 | 1.87 | 0.999 | 120
Newstead SN maximum demand | 43.79 | 43.79 | 0.76 | 1 | 27.02 | 27.66 | 5.91 | 0.977 | 33.77 | 34.56 | 7.38 | 0.977 | 34.84 | 35.19 | 4.93 | 0.99 | 120
Newstead WD maximum demand | 33.54 | 33.86 | -4.69 | 0.99 | 19.62 | 20.59 | 6.26 | 0.953 | 19.62 | 20.59 | 6.26 | 0.953 | 22.08 | 22.21 | 2.33 | 0.994 | 120
Newstead WN maximum demand | 31.88 | 33.36 | -9.83 | 0.956 | 18.51 | 18.99 | 4.25 | 0.975 | 18.51 | 18.99 | 4.25 | 0.975 | 21.02 | 21.02 | 0.36 | 1 | 120
Ningi SD maximum demand | 6.77 | 6.88 | -1.2 | 0.985 | 7.34 | 7.86 | 2.83 | 0.933 | 7.5 | 8.04 | 2.89 | 0.933 | 6.83 | 7.3 | 2.56 | 0.936 | 15
Ningi SN maximum demand | 6.62 | 6.75 | -1.33 | 0.98 | 7.54 | 8.03 | 2.76 | 0.939 | 7.71 | 8.21 | 2.82 | 0.939 | 7.02 | 7.43 | 2.42 | 0.945 | 15
Ningi WD maximum demand | 6.24 | 6.39 | -1.4 | 0.976 | 5.99 | 6.15 | 1.38 | 0.975 | 6.44 | 6.61 | 1.48 | 0.975 | 6.46 | 6.58 | 1.25 | 0.982 | 15
Ningi WN maximum demand | 6.32 | 6.48 | -1.43 | 0.975 | 6.67 | 6.81 | 1.39 | 0.979 | 7.17 | 7.33 | 1.49 | 0.979 | 7.19 | 7.33 | 1.44 | 0.981 | 15
Noosaville SD maximum demand | 46.26 | 46.29 | -1.55 | 0.999 | 33.28 | 34.04 | 7.15 | 0.978 | 35.03 | 35.83 | 7.53 | 0.978 | 33.55 | 33.64 | 2.36 | 0.998 | 120
Noosaville SN maximum demand | 46.78 | 46.88 | -3.12 | 0.998 | 32.95 | 33.63 | 6.69 | 0.98 | 34.69 | 35.4 | 7.05 | 0.98 | 33.24 | 33.25 | 0.78 | 1 | 120
Noosaville WD maximum demand | 42.65 | 42.67 | 1.12 | 1 | 29.57 | 30.14 | 5.82 | 0.981 | 32.93 | 33.56 | 6.48 | 0.981 | 34.33 | 34.33 | 0.15 | 1 | 120
Noosaville WN maximum demand | 48.71 | 48.83 | 3.48 | 0.997 | 33.65 | 34.25 | 6.39 | 0.982 | 37.47 | 38.14 | 7.12 | 0.982 | 39.1 | 39.13 | 1.51 | 0.999 | 120
North Lakes SD maximum demand | 15.48 | 15.48 | -0.14 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0
North Lakes SN maximum demand | 14.95 | 14.96 | -0.52 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0
North Lakes WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
North Lakes WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
North Maclean SD maximum demand | 31.17 | 31.25 | 2.13 | 0.998 | 22.08 | 22.08 | 0.22 | 1 | 23.48 | 23.48 | 0.23 | 1 | 21.86 | 21.91 | 1.47 | 0.998 | 50
North Maclean SN maximum demand | 32.6 | 32.66 | 1.93 | 0.998 | 22.75 | 22.76 | 0.52 | 1 | 24.2 | 24.2 | 0.55 | 1 | 22.52 | 22.57 | 1.48 | 0.998 | 50
North Maclean WD maximum demand | 24.88 | 25.17 | -3.81 | 0.988 | 14.8 | 14.87 | 1.46 | 0.995 | 16.62 | 16.7 | 1.64 | 0.995 | 16.81 | 17.16 | 3.45 | 0.98 | 50
North Maclean WN maximum demand | 30.24 | 30.36 | -2.74 | 0.996 | 17.9 | 18.01 | 1.93 | 0.994 | 20.11 | 20.22 | 2.17 | 0.994 | 20.34 | 20.75 | 4.13 | 0.98 | 50
North Springwood SD maximum demand | 61.95 | 63.2 | 12.46 | 0.98 | 43.71 | 45.62 | 13.06 | 0.958 | 49.82 | 52 | 14.89 | 0.958 | 44.92 | 46.15 | 10.58 | 0.973 | 120
North Springwood SN maximum demand | 58.39 | 58.92 | 7.89 | 0.991 | 41.76 | 43.49 | 12.14 | 0.96 | 47.6 | 49.57 | 13.84 | 0.96 | 42.4 | 43.04 | 7.42 | 0.985 | 120
North Springwood WD maximum demand | 44.43 | 44.61 | -3.97 | 0.996 | 33.49 | 34 | 5.85 | 0.985 | 37.26 | 37.83 | 6.51 | 0.985 | 36.45 | 36.46 | 0.98 | 1 | 120
North Springwood WN maximum demand | 48.15 | 48.28 | -3.54 | 0.997 | 34.53 | 34.75 | 3.98 | 0.993 | 38.41 | 38.66 | 4.43 | 0.993 | 37.55 | 37.63 | 2.42 | 0.998 | 120
Nth Ipswich SD maximum demand | 25.06 | 25.19 | 2.57 | 0.995 | 20.88 | 20.96 | 1.84 | 0.996 | 27.17 | 27.28 | 2.39 | 0.996 | 23.93 | 23.94 | 0.58 | 1 | 50
Nth Ipswich SN maximum demand | 24.69 | 24.79 | 2.19 | 0.996 | 20.08 | 20.16 | 1.81 | 0.996 | 26.13 | 26.24 | 2.36 | 0.996 | 23.01 | 23.01 | 0.11 | 1 | 50
Nth Ipswich WD maximum demand | 23.04 | 23.07 | -1.1 | 0.999 | 14.8 | 15.2 | 3.46 | 0.974 | 17.4 | 17.87 | 4.07 | 0.974 | 16.76 | 16.76 | 0.19 | 1 | 50
Nth Ipswich WN maximum demand | 25.41 | 25.42 | -0.32 | 1 | 15.94 | 16.3 | 3.43 | 0.978 | 18.74 | 19.17 | 4.04 | 0.978 | 18.01 | 18.02 | 0.34 | 1 | 50
Nth Pine Dam SD maximum demand | 1.27 | 1.57 | 0.93 | 0.809 | 0.66 | 0.74 | 0.33 | 0.892 | 0.65 | 0.73 | 0.33 | 0.892 | 0.58 | 0.73 | 0.44 | 0.799 | 6
Nth Pine Dam SN maximum demand | 0.89 | 1.06 | 0.58 | 0.839 | 0.66 | 0.74 | 0.33 | 0.892 | 0.65 | 0.73 | 0.33 | 0.892 | 0.58 | 0.71 | 0.41 | 0.817 | 6
Nth Pine Dam WD maximum demand | 1.02 | 1.26 | 0.74 | 0.812 | 3.71 | 5.16 | 3.58 | 0.719 | 3.84 | 5.34 | 3.71 | 0.719 | 0.429 | 0.536 | 0.3218 | 0.8 | 6
Nth Pine Dam WN maximum demand | 0.77 | 0.92 | 0.5 | 0.837 | 3.44 | 4.82 | 3.37 | 0.714 | 3.56 | 4.99 | 3.5 | 0.714 | 0.3214 | 0.4038 | 0.2443 | 0.7959 | 6
Nudgee SD maximum demand | 18.94 | 19.06 | 2.09 | 0.994 | 27.23 | 28.36 | 7.92 | 0.96 | 30.96 | 32.24 | 9 | 0.96 | 29.57 | 30.2 | 6.16 | 0.979 | 45
Nudgee SN maximum demand | 15.25 | 15.26 | -0.49 | 0.999 | 21.57 | 23.96 | 10.43 | 0.9 | 24.52 | 27.24 | 11.86 | 0.9 | 23.66 | 23.79 | 2.47 | 0.995 | 45
Nudgee WD maximum demand | 14.47 | 14.56 | -1.59 | 0.994 | 23.1 | 24.66 | 8.63 | 0.937 | 23.19 | 24.75 | 8.66 | 0.937 | 22.87 | 22.89 | 1.02 | 0.999 | 45
Nudgee WN maximum demand | 13.09 | 13.39 | -2.82 | 0.978 | 22.51 | 24.45 | 9.55 | 0.921 | 22.59 | 24.54 | 9.59 | 0.921 | 22.28 | 22.92 | 5.37 | 0.972 | 45
Nundah SD maximum demand | 22.12 | 23.55 | 8.06 | 0.94 | 17.5 | 17.71 | 2.71 | 0.988 | 20.35 | 20.59 | 3.15 | 0.988 | 18.63 | 19.2 | 4.63 | 0.97 | 45
Nundah SN maximum demand | 20.14 | 21.06 | 6.16 | 0.956 | 18.34 | 18.46 | 2.03 | 0.994 | 21.33 | 21.46 | 2.36 | 0.994 | 19.53 | 20 | 4.3 | 0.977 | 45
Nundah WD maximum demand | 16.08 | 16.19 | 1.81 | 0.994 | 13.77 | 13.82 | -1.22 | 0.996 | 15.92 | 15.98 | -1.41 | 0.996 | 18.26 | 18.31 | 1.33 | 0.997 | 45
Nundah WN maximum demand | 17.53 | 17.79 | 3.02 | 0.985 | 14.75 | 14.78 | -0.97 | 0.998 | 17.06 | 17.1 | -1.13 | 0.998 | 21.08 | 21.24 | 2.57 | 0.993 | 45
Oxley SD maximum demand | 21.97 | 23.39 | 8.04 | 0.939 | 18 | 18.51 | 4.35 | 0.972 | 19.91 | 20.49 | 4.81 | 0.972 | 18.73 | 19.53 | 5.54 | 0.959 | 40
Oxley SN maximum demand | 19.42 | 20.43 | 6.36 | 0.95 | 15.8 | 15.91 | 1.93 | 0.993 | 17.48 | 17.61 | 2.13 | 0.993 | 16.58 | 16.99 | 3.74 | 0.975 | 40
Oxley WD maximum demand | 18.45 | 18.79 | 3.55 | 0.982 | 14.21 | 15.34 | 5.77 | 0.926 | 16.06 | 17.33 | 6.52 | 0.926 | 16.54 | 16.65 | 1.93 | 0.993 | 40
Oxley WN maximum demand | 18.55 | 18.96 | 3.91 | 0.978 | 13.82 | 14.64 | 4.85 | 0.944 | 15.61 | 16.54 | 5.48 | 0.944 | 16.32 | 16.42 | 1.75 | 0.994 | 40
Pacific Paradise SD maximum demand | 27.97 | 28.9 | 7.28 | 0.968 | 0 | 0 | 0 |  | 0 | 0 | 0
Pacific Paradise SN maximum demand | 27.44 | 27.96 | 5.37 | 0.981 | 0 | 0 | 0 |  | 0 | 0 | 0
Pacific Paradise WD maximum demand | 22.99 | 23.05 | 1.64 | 0.997 | 0 | 0 | 0 |  | 0 | 0 | 0
Pacific Paradise WN maximum demand | 24.79 | 24.85 | 1.7 | 0.998 | 0 | 0 | 0 |  | 0 | 0 | 0
Palm Beach SD maximum demand | 23.59 | 23.64 | -1.55 | 0.998 | 15.63 | 16.49 | 5.26 | 0.948 | 17.04 | 17.98 | 5.74 | 0.948 | 15.4 | 15.43 | 0.93 | 0.998 | 37
Palm Beach SN maximum demand | 24.22 | 24.31 | -2.05 | 0.996 | 17.05 | 17.71 | 4.76 | 0.963 | 18.6 | 19.31 | 5.19 | 0.963 | 16.81 | 16.81 | 0.37 | 1 | 37
Palm Beach WD maximum demand | 20.93 | 21.69 | -5.72 | 0.965 | 16.52 | 16.83 | 3.19 | 0.982 | 17.78 | 18.11 | 3.44 | 0.982 | 17.59 | 18.04 | 4.01 | 0.975 | 37
Palm Beach WN maximum demand | 24.15 | 24.6 | -4.7 | 0.982 | 19.63 | 20.05 | 4.09 | 0.979 | 21.13 | 21.58 | 4.4 | 0.979 | 20.9 | 21.43 | 4.72 | 0.975 | 37
Palmwoods Central SD maximum demand | 24.42 | 27.02 | 11.57 | 0.904 | 15.87 | 16.73 | 5.29 | 0.949 | 17.04 | 17.96 | 5.68 | 0.949 | 15.46 | 16.71 | 6.35 | 0.925 | 30
Palmwoods Central SN maximum demand | 25.51 | 27.9 | 11.31 | 0.914 | 16.65 | 17.42 | 5.14 | 0.955 | 17.88 | 18.71 | 5.52 | 0.955 | 16.22 | 17.37 | 6.22 | 0.934 | 30
Palmwoods Central WD maximum demand | 19.95 | 21.04 | 6.67 | 0.948 | 12.56 | 12.89 | 2.92 | 0.974 | 13.97 | 14.35 | 3.25 | 0.974 | 15.35 | 15.98 | 4.46 | 0.96 | 30
Palmwoods Central WN maximum demand | 23.72 | 24.85 | 7.39 | 0.955 | 14.68 | 15.05 | 3.33 | 0.975 | 16.33 | 16.75 | 3.7 | 0.975 | 17.96 | 18.62 | 4.91 | 0.965 | 30
Pandanus Avenue SD maximum demand | 21.05 | 22.77 | 8.69 | 0.924 | 0 | 0 | 0 |  | 0 | 0 | 0
Pandanus Avenue SN maximum demand | 20.2 | 21.81 | 8.23 | 0.926 | 0 | 0 | 0 |  | 0 | 0 | 0
Pandanus Avenue WD maximum demand | 16.89 | 17.72 | 5.37 | 0.953 | 0 | 0 | 0 |  | 0 | 0 | 0
Pandanus Avenue WN maximum demand | 16.89 | 17.9 | 5.94 | 0.943 | 0 | 0 | 0 |  | 0 | 0 | 0
Parkinson SD maximum demand | 16.51 | 16.6 | 1.66 | 0.995 | 0 | 0 | 0 |  | 0 | 0 | 0
Parkinson SN maximum demand | 16.3 | 16.35 | 1.37 | 0.996 | 0 | 0 | 0 |  | 0 | 0 | 0
Parkinson WD maximum demand | 13.29 | 13.36 | -1.36 | 0.995 | 0 | 0 | 0 |  | 0 | 0 | 0
Parkinson WN maximum demand | 14.69 | 14.72 | -0.83 | 0.998 | 0 | 0 | 0 |  | 0 | 0 | 0
Parkwood SD maximum demand | 20.79 | 21.65 | 6.03 | 0.96 | 2.95 | 2.97 | 0.29 | 0.995 | 3.22 | 3.23 | 0.32 | 0.995 | 12.22 | 12.27 | 1.2 | 0.995 | 50
Parkwood SN maximum demand | 18.56 | 19.1 | 4.51 | 0.972 | 3.19 | 3.23 | 0.47 | 0.989 | 3.47 | 3.51 | 0.51 | 0.989 | 12.03 | 12.16 | 1.78 | 0.989 | 50
Parkwood WD maximum demand | 15.2 | 15.22 | 0.78 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 9.87 | 10.88 | 4.58 | 0.907 | 50
Parkwood WN maximum demand | 15.18 | 15.2 | 0.71 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 9.92 | 10.9 | 4.5 | 0.911 | 50
Peregian SD maximum demand | 9.26 | 9.26 | -0.24 | 1 | 7.53 | 7.62 | 1.11 | 0.989 | 8.3 | 8.39 | 1.22 | 0.989 | 7.58 | 7.68 | 1.24 | 0.987 | 25
Peregian SN maximum demand | 10.35 | 10.35 | -0.25 | 1 | 7.53 | 7.59 | 0.92 | 0.993 | 8.3 | 8.36 | 1.02 | 0.993 | 7.58 | 7.66 | 1.13 | 0.989 | 25
Peregian WD maximum demand | 8.8 | 8.96 | -1.68 | 0.982 | 6.18 | 6.18 | 0.14 | 1 | 7.06 | 7.06 | 0.15 | 1 | 7.05 | 7.06 | 0.36 | 0.999 | 25
Peregian WN maximum demand | 10.21 | 10.3 | -1.34 | 0.992 | 7.24 | 7.24 | 0.19 | 1 | 8.26 | 8.27 | 0.22 | 1 | 8.26 | 8.27 | 0.53 | 0.998 | 25
Pimpama East SD maximum demand | 23.63 | 23.65 | 0.88 | 0.999 | 12.12 | 12.41 | 2.63 | 0.977 | 14.91 | 15.26 | 3.23 | 0.977 | 12.37 | 12.64 | 2.61 | 0.978 | 50
Pimpama East SN maximum demand | 20.74 | 20.78 | -1.23 | 0.998 | 12.12 | 12.35 | 2.37 | 0.981 | 14.91 | 15.19 | 2.91 | 0.981 | 12.16 | 12.44 | 2.59 | 0.978 | 50
Pimpama East WD maximum demand | 18.05 | 18.36 | -3.35 | 0.983 | 9.1 | 9.12 | 0.61 | 0.998 | 10.04 | 10.07 | 0.67 | 0.998 | 10.1 | 10.2 | 1.41 | 0.99 | 50
Pimpama East WN maximum demand | 17.55 | 18.1 | -4.46 | 0.969 | 10.89 | 10.99 | 1.52 | 0.99 | 12.01 | 12.13 | 1.68 | 0.99 | 12.08 | 12.24 | 1.95 | 0.987 | 50
Postmans Ridge SD maximum demand | 1.6 | 1.73 | 0.65 | 0.926 | 3.83 | 3.94 | 0.93 | 0.972 | 4.22 | 4.34 | 1.02 | 0.972 | 3.79 | 4.04 | 1.39 | 0.939 | 6
Postmans Ridge SN maximum demand | 1.71 | 1.83 | 0.65 | 0.935 | 4.03 | 4.14 | 0.93 | 0.975 | 4.45 | 4.56 | 1.02 | 0.975 | 4 | 4.21 | 1.31 | 0.95 | 6
Postmans Ridge WD maximum demand | 1.36 | 1.4 | 0.33 | 0.972 | 3.05 | 3.14 | 0.73 | 0.973 | 3.58 | 3.68 | 0.85 | 0.973 | 3.52 | 3.64 | 0.92 | 0.967 | 6
Postmans Ridge WN maximum demand | 1.43 | 1.46 | 0.31 | 0.977 | 3.32 | 3.39 | 0.69 | 0.979 | 3.89 | 3.98 | 0.81 | 0.979 | 3.83 | 3.89 | 0.7 | 0.984 | 6
Queensport SD maximum demand | 35.19 | 37.08 | 11.69 | 0.949 | 26.3 | 26.58 | 3.87 | 0.989 | 28.47 | 28.78 | 4.19 | 0.989 | 23.08 | 23.25 | 2.79 | 0.993 | 50
Queensport SN maximum demand | 30.58 | 31.56 | 7.77 | 0.969 | 24.56 | 24.7 | 2.57 | 0.995 | 26.59 | 26.74 | 2.78 | 0.995 | 21.7 | 21.76 | 1.58 | 0.997 | 50
Queensport WD maximum demand | 23.7 | 24.12 | 4.5 | 0.982 | 20.95 | 21.63 | 5.36 | 0.969 | 22.61 | 23.34 | 5.78 | 0.969 | 17.79 | 18.19 | 3.8 | 0.978 | 50
Queensport WN maximum demand | 22.31 | 22.4 | 1.98 | 0.996 | 20.77 | 21.33 | 4.87 | 0.974 | 22.41 | 23.02 | 5.25 | 0.974 | 17.73 | 17.91 | 2.6 | 0.989 | 50
Raby Bay SD maximum demand | 28.79 | 28.97 | 3.26 | 0.994 | 22.46 | 22.56 | 2.05 | 0.996 | 25.89 | 26 | 2.37 | 0.996 | 26.24 | 26.24 | 0.05 | 1 | 42
Raby Bay SN maximum demand | 29.81 | 29.94 | 2.77 | 0.996 | 23.72 | 23.77 | 1.53 | 0.998 | 27.34 | 27.4 | 1.77 | 0.998 | 27.75 | 28.27 | 5.43 | 0.981 | 42
Raby Bay WD maximum demand | 25.29 | 25.42 | -2.54 | 0.995 | 18.47 | 18.48 | -0.7 | 0.999 | 19.66 | 19.68 | -0.75 | 0.999 | 22.45 | 22.46 | 0.47 | 1 | 42
Raby Bay WN maximum demand | 29.68 | 29.72 | -1.5 | 0.999 | 22.77 | 22.77 | -0.05 | 1 | 24.24 | 24.24 | -0.06 | 1 | 27.43 | 27.47 | 1.48 | 0.999 | 42
Redbank SD maximum demand | 19.66 | 19.97 | 3.48 | 0.985 | 12.17 | 12.52 | -2.95 | 0.972 | 14.56 | 14.98 | -3.53 | 0.972 | 11.14 | 11.3 | 1.86 | 0.986 | 25
Redbank SN maximum demand | 17.97 | 18.08 | 2.01 | 0.994 | 11.85 | 11.94 | 1.42 | 0.993 | 14.17 | 14.27 | 1.7 | 0.993 | 10.81 | 10.9 | 1.42 | 0.992 | 25
Redbank WD maximum demand | 12.63 | 12.92 | -2.72 | 0.978 | 9.41 | 9.41 | 0.09 | 1 | 10.46 | 10.46 | 0.11 | 1 | 10.44 | 10.45 | 0.48 | 0.999 | 25
Redbank WN maximum demand | 13.1 | 13.39 | -2.8 | 0.978 | 9.18 | 9.19 | -0.42 | 0.999 | 10.2 | 10.21 | -0.47 | 0.999 | 10.18 | 10.18 | 0.05 | 1 | 25
Redbank Plains SD maximum demand | 25.68 | 27.71 | 10.42 | 0.927 | 21.99 | 22.88 | 6.31 | 0.961 | 27.22 | 28.31 | 7.81 | 0.961 | 21.23 | 22.41 | 7.19 | 0.947 | 50
Redbank Plains SN maximum demand | 26.14 | 28.28 | 10.79 | 0.924 | 22.38 | 23.25 | 6.29 | 0.963 | 27.7 | 28.77 | 7.78 | 0.963 | 21.46 | 22.71 | 7.43 | 0.945 | 50
Redbank Plains WD maximum demand | 24.47 | 25.3 | 6.4 | 0.967 | 17.38 | 17.62 | 2.87 | 0.987 | 19.71 | 19.98 | 3.26 | 0.987 | 20.15 | 20.59 | 4.24 | 0.979 | 50
Redbank Plains WN maximum demand | 30.19 | 31.31 | 8.3 | 0.964 | 21.09 | 21.46 | 3.94 | 0.983 | 23.92 | 24.34 | 4.47 | 0.983 | 24.45 | 25.05 | 5.46 | 0.976 | 50
Redcliffe SD maximum demand | 21.97 | 22.72 | 5.82 | 0.967 | 19.48 | 19.7 | 2.94 | 0.989 | 22.82 | 23.08 | 3.45 | 0.989 | 18.1 | 18.39 | 3.29 | 0.984 | 29
Redcliffe SN maximum demand | 20.06 | 20.55 | 4.49 | 0.976 | 19.07 | 19.14 | 1.65 | 0.996 | 22.34 | 22.43 | 1.94 | 0.996 | 17.86 | 18.03 | 2.52 | 0.99 | 29
Redcliffe WD maximum demand | 16.85 | 16.85 | -0.03 | 1 | 17.6 | 18.02 | 3.86 | 0.977 | 18.49 | 18.93 | 4.06 | 0.977 | 17.22 | 17.85 | 4.71 | 0.965 | 29
Redcliffe WN maximum demand | 19.32 | 19.33 | 0.65 | 0.999 | 18.22 | 18.66 | 4.01 | 0.977 | 19.14 | 19.6 | 4.21 | 0.977 | 17.72 | 18.28 | 4.49 | 0.969 | 29
Redland Bay SD maximum demand | 14.06 | 14.66 | -4.15 | 0.959 | 11.15 | 11.61 | 3.23 | 0.961 | 12.99 | 13.52 | 3.76 | 0.961 | 11.87 | 12.78 | 4.74 | 0.929 | 25
Redland Bay SN maximum demand | 15.11 | 15.59 | -3.84 | 0.969 | 13.26 | 13.68 | 3.37 | 0.969 | 15.44 | 15.93 | 3.93 | 0.969 | 14.11 | 14.11 | 0.09 | 1 | 25
Redland Bay WD maximum demand | 12.71 | 14.05 | -6 | 0.904 | 11.09 | 11.2 | 1.51 | 0.991 | 12.58 | 12.69 | 1.72 | 0.991 | 12.67 | 13.05 | 3.13 | 0.971 | 25
Redland Bay WN maximum demand | 14.73 | 15.72 | -5.49 | 0.937 | 12.24 | 12.34 | 1.6 | 0.992 | 13.87 | 13.99 | 1.81 | 0.992 | 13.97 | 14.44 | 3.66 | 0.967 | 25
Redland Bay South SD maximum demand | 8.14 | 8.25 | -1.34 | 0.987 | 0 | 0 | 0 |  | 0 | 0 | 0
Redland Bay South SN maximum demand | 8.63 | 8.73 | -1.31 | 0.989 | 0 | 0 | 0 |  | 0 | 0 | 0
Redland Bay South WD maximum demand | 7.67 | 8.04 | -2.43 | 0.953 | 0 | 0 | 0 |  | 0 | 0 | 0
Redland Bay South WN maximum demand | 8.73 | 9 | -2.2 | 0.97 | 0 | 0 | 0 |  | 0 | 0 | 0
Robina SD maximum demand | 56.51 | 56.72 | 4.87 | 0.996 | 43.63 | 43.79 | 3.74 | 0.996 | 48.04 | 48.22 | 4.12 | 0.996 | 45.47 | 45.52 | 2.2 | 0.999 | 120
Robina SN maximum demand | 55.11 | 55.24 | 3.81 | 0.998 | 41.38 | 41.44 | 2.28 | 0.998 | 45.56 | 45.63 | 2.51 | 0.998 | 43.4 | 43.41 | 1.21 | 1 | 120
Robina WD maximum demand | 40.75 | 41.56 | -8.16 | 0.981 | 34.15 | 34.62 | 5.72 | 0.986 | 36.65 | 37.16 | 6.14 | 0.986 | 36.38 | 36.57 | 3.71 | 0.995 | 120
Robina WN maximum demand | 46.11 | 46.51 | -6.11 | 0.991 | 36.21 | 36.68 | 5.91 | 0.987 | 38.86 | 39.38 | 6.34 | 0.987 | 38.69 | 38.95 | 4.51 | 0.993 | 120
Rocklea SD maximum demand | 20.73 | 20.74 | 0.76 | 0.999 | 18.24 | 18.58 | 3.54 | 0.982 | 20.06 | 20.44 | 3.9 | 0.982 | 15.45 | 15.67 | 2.65 | 0.986 | 30
Rocklea SN maximum demand | 15.22 | 15.46 | -2.71 | 0.985 | 13.96 | 15.07 | 5.66 | 0.927 | 15.36 | 16.58 | 6.23 | 0.927 | 12.02 | 12.03 | 0.49 | 0.999 | 30
Rocklea WD maximum demand | 14.72 | 15.09 | -3.33 | 0.975 | 13.1 | 13.1 | 0.14 | 1 | 13.7 | 13.7 | 0.15 | 1 | 18.14 | 18.25 | 2.01 | 0.994 | 30
Rocklea WN maximum demand | 12.46 | 13.55 | -5.33 | 0.919 | 12.16 | 12.17 | -0.38 | 1 | 12.72 | 12.73 | -0.39 | 1 | 16.62 | 16.64 | 0.84 | 0.999 | 30
Roderick St SD maximum demand | 27.93 | 28.91 | 7.49 | 0.966 | 22.23 | 22.97 | 5.79 | 0.968 | 27.25 | 28.15 | 7.1 | 0.968 | 28.67 | 29.35 | 6.3 | 0.977 | 45
Roderick St SN maximum demand | 23.95 | 24.35 | 4.41 | 0.983 | 17.88 | 18.23 | 3.57 | 0.981 | 21.91 | 22.34 | 4.37 | 0.981 | 23.54 | 23.73 | 2.98 | 0.992 | 45
Roderick St WD maximum demand | 18.3 | 18.33 | -1.1 | 0.998 | 16.1 | 16.1 | 0 | 1 | 17.78 | 17.78 | 0 | 1 | 20.97 | 21.3 | 3.69 | 0.985 | 45
Roderick St WN maximum demand | 17.06 | 17.23 | -2.39 | 0.99 | 13.49 | 13.64 | -1.98 | 0.989 | 14.91 | 15.07 | -2.19 | 0.989 | 18.12 | 18.19 | 1.62 | 0.996 | 45
Rosewood SD maximum demand | 5.89 | 6.11 | 1.62 | 0.964 | 4.85 | 4.89 | 0.61 | 0.992 | 6.45 | 6.5 | 0.81 | 0.992 | 5.85 | 6 | 1.3 | 0.976 | 10
Rosewood SN maximum demand | 6.14 | 6.37 | 1.68 | 0.965 | 5.5 | 5.609 | 1.1 | 0.9803 | 7.31 | 7.45 | 1.4623 | 0.981 | 5.18 | 5.26 | 0.9 | 0.985 | 10
Rosewood WD maximum demand | 5.09 | 5.14 | 0.73 | 0.99 | 3.7 | 3.99 | 1.48 | 0.928 | 4.31 | 4.64 | 1.72 | 0.928 | 4.3 | 4.32 | 0.37 | 0.996 | 10
Rosewood WN maximum demand | 5.77 | 5.79 | 0.45 | 0.997 | 4.16 | 4.38 | 1.38 | 0.949 | 4.84 | 5.1 | 1.6 | 0.949 | 4.83 | 5.18 | 1.87 | 0.933 | 10
Runcorn SD maximum demand | 28.15 | 28.73 | 5.75 | 0.98 | 19.55 | 19.59 | 1.2 | 0.998 | 21.67 | 21.71 | 1.33 | 0.998 | 19.98 | 20.06 | 1.81 | 0.996 | 30
Runcorn SN maximum demand | 30.12 | 30.8 | 6.46 | 0.978 | 20.36 | 20.37 | 0.76 | 0.999 | 22.57 | 22.58 | 0.85 | 0.999 | 20.8 | 20.89 | 1.93 | 0.996 | 30
Runcorn WD maximum demand | 24.86 | 24.88 | 1.01 | 0.999 | 17.46 | 17.8 | 3.5 | 0.98 | 19.43 | 19.81 | 3.9 | 0.98 | 19.59 | 20.09 | 4.49 | 0.975 | 30
Runcorn WN maximum demand | 29.94 | 30.03 | 2.27 | 0.997 | 21.48 | 21.88 | 4.14 | 0.982 | 23.91 | 24.35 | 4.6 | 0.982 | 24.1 | 24.68 | 5.31 | 0.977 | 30
Russell Island SD maximum demand | 5.79 | 6.98 | 3.9 | 0.83 | 3.56 | 3.68 | 0.91 | 0.969 | 3.5 | 3.62 | 0.9 | 0.969 | 3.18 | 3.29 | 0.82 | 0.969 | 25
Russell Island SN maximum demand | 6.14 | 7.47 | 4.26 | 0.821 | 3.85 | 3.96 | 0.96 | 0.97 | 3.78 | 3.9 | 0.94 | 0.97 | 3.44 | 3.54 | 0.85 | 0.97 | 25
Russell Island WD maximum demand | 4.65 | 6.1 | 3.96 | 0.761 | 4.15 | 4.19 | 0.56 | 0.991 | 4.68 | 4.72 | 0.64 | 0.991 | 4.65 | 4.69 | 0.63 | 0.991 | 25
Russell Island WN maximum demand | 5.74 | 7.52 | 4.86 | 0.763 | 4.61 | 4.65 | 0.65 | 0.99 | 5.19 | 5.24 | 0.74 | 0.99 | 5.16 | 5.21 | 0.73 | 0.99 | 25
Salisbury SD maximum demand | 21 | 21.39 | 4.09 | 0.982 | 7.83 | 8.59 | 3.52 | 0.912 | 9.13 | 10.01 | 4.11 | 0.912 | 13.32 | 13.66 | 3.01 | 0.975 | 27
Salisbury SN maximum demand | 16.35 | 16.35 | 0.5 | 1 | 6.59 | 7.02 | 2.44 | 0.938 | 7.67 | 8.18 | 2.84 | 0.938 | 11.04 | 11.11 | 1.28 | 0.993 | 27
Salisbury WD maximum demand | 17.97 | 17.97 | 0.06 | 1 | 14.95 | 15.05 | 1.68 | 0.994 | 17.18 | 17.29 | 1.93 | 0.994 | 8.55 | 9.61 | 4.39 | 0.89 | 27
Salisbury WN maximum demand | 15.32 | 15.41 | -1.64 | 0.994 | 13.92 | 13.96 | 1.03 | 0.997 | 16 | 16.04 | 1.18 | 0.997 | 8.06 | 8.94 | 3.86 | 0.902 | 27
Samford SD maximum demand | 18.37 | 19.59 | 6.81 | 0.938 | 12.12 | 12.49 | 3 | 0.971 | 14.37 | 14.81 | 3.55 | 0.971 | 13 | 13.66 | 4.2 | 0.952 | 25
Samford SN maximum demand | 19.6 | 20.78 | 6.88 | 0.944 | 12.12 | 12.46 | 2.87 | 0.973 | 14.37 | 14.77 | 3.4 | 0.973 | 13 | 13.6 | 3.99 | 0.956 | 25
Samford WD maximum demand | 14.31 | 14.71 | 3.39 | 0.973 | 10.67 | 10.75 | 1.35 | 0.992 | 12.76 | 12.86 | 1.61 | 0.992 | 11.35 | 11.57 | 2.27 | 0.981 | 25
Samford WN maximum demand | 17.45 | 17.91 | 4.06 | 0.974 | 12.89 | 13.02 | 1.87 | 0.99 | 15.41 | 15.57 | 2.24 | 0.99 | 13.62 | 13.89 | 2.76 | 0.98 | 25
Sandgate SD maximum demand | 44.02 | 46.74 | 15.69 | 0.942 | 25.47 | 26.71 | 8.04 | 0.954 | 30.1 | 31.56 | 9.5 | 0.954 | 27.32 | 28.08 | 6.5 | 0.973 | 65
Sandgate SN maximum demand | 45.43 | 48.44 | 16.8 | 0.938 | 26.58 | 27.84 | 8.27 | 0.955 | 31.41 | 32.89 | 9.77 | 0.955 | 28.51 | 29.32 | 6.87 | 0.972 | 65
Sandgate WD maximum demand | 34.48 | 34.95 | 5.72 | 0.987 | 22.57 | 23.09 | 4.89 | 0.977 | 25.42 | 26.01 | 5.5 | 0.977 | 26.01 | 26.06 | 1.63 | 0.998 | 65
Sandgate WN maximum demand | 41.31 | 42.39 | 9.52 | 0.974 | 25.08 | 25.7 | 5.61 | 0.976 | 28.25 | 28.94 | 6.31 | 0.976 | 28.97 | 29.23 | 3.9 | 0.991 | 65
Scarborough SD maximum demand | 21.9 | 24.38 | 10.72 | 0.898 | 13.26 | 13.73 | 3.57 | 0.966 | 14.92 | 15.45 | 4.01 | 0.966 | 16.31 | 17.59 | 6.61 | 0.927 | 45
Scarborough SN maximum demand | 23.32 | 25.68 | 10.77 | 0.908 | 15.02 | 15.42 | 3.51 | 0.974 | 16.9 | 17.36 | 3.95 | 0.974 | 18.32 | 19.61 | 6.98 | 0.934 | 45
Scarborough WD maximum demand | 18.3 | 18.78 | 4.21 | 0.975 | 13.18 | 13.31 | 1.84 | 0.99 | 14.47 | 14.61 | 2.02 | 0.99 | 14.3 | 14.6 | 2.97 | 0.979 | 45
Scarborough WN maximum demand | 22.25 | 23.06 | 6.07 | 0.965 | 15.27 | 15.42 | 2.07 | 0.991 | 16.77 | 16.93 | 2.28 | 0.991 | 16.57 | 16.97 | 3.68 | 0.976 | 45
Scrub Road SD maximum demand | 37.17 | 37.83 | 6.99 | 0.983 | 29.62 | 29.99 | 4.66 | 0.988 | 34.24 | 34.67 | 5.39 | 0.988 | 31.18 | 31.24 | 2.05 | 0.998 | 45
Scrub Road SN maximum demand | 36.21 | 36.82 | 6.7 | 0.983 | 29.13 | 29.36 | 3.65 | 0.992 | 33.68 | 33.94 | 4.22 | 0.992 | 30.66 | 30.71 | 1.83 | 0.998 | 45
Scrub Road WD maximum demand | 25.7 | 25.71 | -0.71 | 1 | 21.53 | 22.17 | 5.3 | 0.971 | 24.9 | 25.64 | 6.13 | 0.971 | 25.67 | 25.82 | 2.8 | 0.994 | 45
Scrub Road WN maximum demand | 30.1 | 30.13 | 1.26 | 0.999 | 23.88 | 24.44 | 5.2 | 0.977 | 27.63 | 28.27 | 6.02 | 0.977 | 28.51 | 28.66 | 2.96 | 0.995 | 45
Sherwood SD maximum demand | 28.66 | 29.02 | 4.54 | 0.988 | 22.42 | 22.63 | 3.05 | 0.991 | 27.43 | 27.68 | 3.73 | 0.991 | 25.76 | 26.32 | 5.42 | 0.979 | 50
Sherwood SN maximum demand | 29.27 | 29.58 | 4.25 | 0.99 | 22.29 | 22.41 | 2.37 | 0.994 | 27.26 | 27.42 | 2.9 | 0.994 | 25.52 | 25.98 | 4.85 | 0.982 | 50
Sherwood WD maximum demand | 21.77 | 21.8 | -1.18 | 0.999 | 18.89 | 19.54 | 5.01 | 0.967 | 22.4 | 23.18 | 5.94 | 0.967 | 23.07 | 23.2 | 2.49 | 0.994 | 50
Sherwood WN maximum demand | 23.33 | 23.34 | -0.76 | 0.999 | 19.94 | 20.54 | 4.94 | 0.971 | 23.65 | 24.37 | 5.86 | 0.971 | 24.34 | 24.51 | 2.87 | 0.993 | 50
Somerset Dam SD maximum demand | 0.33 | 0.37 | 0.16 | 0.902 | 0.46 | 0.53 | 0.26 | 0.869 | 0.46 | 0.53 | 0.26 | 0.869 | 0.46 | 0.51 | 0.22 | 0.901 | 8
Somerset Dam SN maximum demand | 0.4 | 0.44 | 0.2 | 0.897 | 0.5 | 0.58 | 0.28 | 0.875 | 0.5 | 0.58 | 0.28 | 0.875 | 0.5 | 0.56 | 0.25 | 0.899 | 8
Somerset Dam WD maximum demand | 0.25 | 0.28 | 0.12 | 0.899 | 0.23 | 0.25 | 0.11 | 0.902 | 0.23 | 0.25 | 0.11 | 0.902 | 0.23 | 0.26 | 0.11 | 0.895 | 8
Somerset Dam WN maximum demand | 0.28 | 0.32 | 0.15 | 0.887 | 0.25 | 0.28 | 0.12 | 0.902 | 0.25 | 0.28 | 0.12 | 0.902 | 0.25 | 0.28 | 0.13 | 0.889 | 8
Southport SD maximum demand | 93.41 | 96.07 | 22.46 | 0.972 | 74.9 | 75.49 | 9.4 | 0.992 | 90.97 | 91.68 | 11.42 | 0.992 | 79.96 | 80.63 | 10.36 | 0.992 | 180
Southport SN maximum demand | 81 | 82.14 | 13.67 | 0.986 | 68.59 | 69.3 | 9.89 | 0.99 | 83.3 | 84.16 | 12.01 | 0.99 | 73.24 | 73.44 | 5.42 | 0.997 | 180
Southport WD maximum demand | 61.01 | 61.2 | 4.85 | 0.997 | 56.91 | 57.38 | 7.34 | 0.992 | 57.43 | 57.91 | 7.41 | 0.992 | 57.75 | 57.75 | 0.17 | 1 | 180
Southport WN maximum demand | 61.71 | 61.92 | 5.05 | 0.997 | 57.75 | 58.16 | 6.88 | 0.993 | 58.28 | 58.69 | 6.95 | 0.993 | 58.61 | 58.85 | 5.34 | 0.996 | 180
Spring Creek SD maximum demand | 5.94 | 6.48 | 2.58 | 0.917 | 3.4 | 3.78 | 1.64 | 0.901 | 6.66 | 7.39 | 3.2 | 0.901 | 6 | 6.68 | 2.95 | 0.898 | 15
Spring Creek SN maximum demand | 5.47 | 5.96 | 2.37 | 0.918 | 2.72 | 2.89 | 1 | 0.939 | 5.31 | 5.66 | 1.95 | 0.939 | 4.78 | 5.15 | 1.9 | 0.929 | 15
Spring Creek WD maximum demand | 4.85 | 5.03 | 1.31 | 0.965 | 2.39 | 2.68 | 1.23 | 0.89 | 2.4 | 2.7 | 1.23 | 0.89 | 2.37 | 2.67 | 1.22 | 0.889 | 15
Spring Creek WN maximum demand | 4.85 | 5.03 | 1.33 | 0.964 | 2.08 | 2.24 | 0.85 | 0.925 | 2.09 | 2.26 | 0.86 | 0.925 | 2.06 | 2.23 | 0.85 | 0.925 | 15
Springfield SD maximum demand | 31.45 | 32.06 | 6.24 | 0.981 | 27.25 | 27.3 | 1.65 | 0.998 | 33.85 | 33.91 | 2.05 | 0.998 | 35.64 | 36.15 | 6.1 | 0.986 | 50
Springfield SN maximum demand | 30.77 | 31.29 | 5.7 | 0.983 | 26.79 | 26.83 | 1.39 | 0.999 | 33.28 | 33.33 | 1.73 | 0.999 | 35.06 | 35.45 | 5.22 | 0.989 | 50
Springfield WD maximum demand | 15.62 | 15.68 | -1.42 | 0.996 | 18.21 | 18.34 | 2.17 | 0.993 | 20.56 | 20.71 | 2.45 | 0.993 | 20.72 | 20.99 | 3.33 | 0.987 | 50
Springfield WN maximum demand | 17.43 | 17.44 | -0.37 | 1 | 21.34 | 21.54 | 2.95 | 0.991 | 24.1 | 24.33 | 3.34 | 0.991 | 24.28 | 24.8 | 5.07 | 0.979 | 50
Springfield Central Bus 1 SD maximum demand | 35.42 | 35.44 | -1.19 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0
Springfield Central Bus 1 SN maximum demand | 33.79 | 33.86 | -2.1 | 0.998 | 0 | 0 | 0 |  | 0 | 0 | 0
Springfield Central Bus 1 WD maximum demand | 20.06 | 22.27 | -9.67 | 0.901 | 0 | 0 | 0 |  | 0 | 0 | 0
Springfield Central Bus 1 WN maximum demand | 23.07 | 24.58 | -8.47 | 0.939 | 0 | 0 | 0 |  | 0 | 0 | 0
St Lucia SD maximum demand | 31.05 | 32.86 | 10.76 | 0.945 | 26.15 | 26.6 | 4.87 | 0.983 | 28.67 | 29.17 | 5.34 | 0.983 | 25.59 | 26.37 | 6.37 | 0.97 | 55
St Lucia SN maximum demand | 26.98 | 28.13 | 7.95 | 0.959 | 23.83 | 24.08 | 3.45 | 0.99 | 26.12 | 26.4 | 3.78 | 0.99 | 23.32 | 23.79 | 4.68 | 0.98 | 55
St Lucia WD maximum demand | 25.35 | 25.66 | 3.98 | 0.988 | 24.1 | 24.11 | 0.57 | 1 | 26.44 | 26.45 | 0.63 | 1 | 27.17 | 27.3 | 2.72 | 0.995 | 55
St Lucia WN maximum demand | 22.88 | 23.2 | 3.85 | 0.986 | 22.4 | 22.4 | -0.24 | 1 | 24.58 | 24.58 | -0.26 | 1 | 25.24 | 25.36 | 2.48 | 0.995 | 55
Stafford SD maximum demand | 28.25 | 29.1 | 6.99 | 0.971 | 25.62 | 26.58 | 7.05 | 0.964 | 29.66 | 30.76 | 8.17 | 0.964 | 27.37 | 27.71 | 4.34 | 0.988 | 50
Stafford SN maximum demand | 28.62 | 29.47 | 7.02 | 0.971 | 25.67 | 26.59 | 6.93 | 0.965 | 29.71 | 30.78 | 8.03 | 0.965 | 27.46 | 27.78 | 4.2 | 0.989 | 50
Stafford WD maximum demand | 20.89 | 20.98 | 1.96 | 0.996 | 20.33 | 20.65 | 3.64 | 0.984 | 23.15 | 23.52 | 4.15 | 0.984 | 23.36 | 23.37 | 0.58 | 1 | 50
Stafford WN maximum demand | 25.63 | 25.87 | 3.51 | 0.991 | 23.78 | 24.06 | 3.65 | 0.988 | 27.08 | 27.4 | 4.16 | 0.988 | 27.38 | 27.42 | 1.41 | 0.999 | 50
Stapylton SD maximum demand | 23.7 | 25.63 | 9.74 | 0.925 | 11.08 | 11.08 | 0.15 | 1 | 12.67 | 12.67 | 0.17 | 1 | 10.85 | 10.87 | 0.63 | 0.998 | 25
Stapylton SN maximum demand | 20.99 | 21.76 | 5.74 | 0.965 | 9.13 | 9.16 | -0.8 | 0.996 | 10.43 | 10.47 | -0.92 | 0.996 | 9.24 | 9.24 | 0.06 | 1 | 25
Stapylton WD maximum demand | 21.13 | 21.92 | 5.83 | 0.964 | 8.06 | 8.78 | 3.48 | 0.918 | 8.84 | 9.63 | 3.81 | 0.918 | 6.91 | 7.72 | 3.45 | 0.895 | 25
Stapylton WN maximum demand | 19.9 | 20.2 | 3.43 | 0.985 | 6.87 | 7.46 | 2.91 | 0.921 | 7.53 | 8.18 | 3.19 | 0.921 | 5.94 | 6.62 | 2.92 | 0.898 | 25
Stradbroke Is SD maximum demand | 5.08 | 5.61 | 2.4 | 0.904 | 4.07 | 4.35 | 1.54 | 0.936 | 4.65 | 4.97 | 1.76 | 0.936 | 4.19 | 4.55 | 1.8 | 0.919 | 6
Stradbroke Is SN maximum demand | 6.29 | 6.88 | 2.78 | 0.915 | 4.56 | 4.74 | 1.27 | 0.963 | 5.21 | 5.41 | 1.46 | 0.963 | 4.69 | 5.05 | 1.87 | 0.929 | 6
Stradbroke Is WD maximum demand | 3.8 | 4.07 | 1.46 | 0.934 | 3.52 | 3.68 | 1.05 | 0.958 | 3.82 | 3.99 | 1.14 | 0.958 | 3.77 | 3.93 | 1.12 | 0.958 | 6
Stradbroke Is WN maximum demand | 4.74 | 5.08 | 1.82 | 0.933 | 4.72 | 4.89 | 1.29 | 0.964 | 5.11 | 5.3 | 1.4 | 0.964 | 5.04 | 5.28 | 1.57 | 0.955 | 6
Strathpine SD maximum demand | 28.99 | 31.01 | 11.01 | 0.935 | 28.05 | 28.56 | 5.38 | 0.982 | 29.26 | 29.8 | 5.61 | 0.982 | 23.68 | 24.33 | 5.57 | 0.973 | 50
Strathpine SN maximum demand | 21.24 | 21.87 | 5.19 | 0.971 | 21.95 | 21.96 | 0.47 | 1 | 22.91 | 22.91 | 0.49 | 1 | 18.66 | 18.72 | 1.53 | 0.997 | 50
Strathpine WD maximum demand | 27.22 | 29.54 | 11.48 | 0.921 | 22.79 | 25.64 | 11.74 | 0.889 | 22.67 | 25.51 | 11.68 | 0.889 | 22.51 | 23.05 | 4.98 | 0.976 | 50
Strathpine WN maximum demand | 22.07 | 22.81 | 5.77 | 0.968 | 18.73 | 21.02 | 9.54 | 0.891 | 18.63 | 20.91 | 9.49 | 0.891 | 18.49 | 18.52 | 0.96 | 0.999 | 50
Strathpine West SD maximum demand | 17.1 | 17.77 | 4.81 | 0.963 | 0 | 0 | 0 |  | 0 | 0 | 0
Strathpine West SN maximum demand | 14.39 | 14.66 | 2.82 | 0.981 | 0 | 0 | 0 |  | 0 | 0 | 0
Strathpine West WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Strathpine West WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Sumner SD maximum demand | 40.5 | 40.61 | 2.99 | 0.997 | 33.58 | 34.98 | 9.81 | 0.96 | 37.88 | 39.47 | 11.07 | 0.96 | 34.2 | 34.2 | 0.32 | 1 | 120
Sumner SN maximum demand | 37.48 | 37.53 | 1.96 | 0.999 | 32.22 | 33.31 | 8.43 | 0.967 | 36.35 | 37.58 | 9.51 | 0.967 | 32.82 | 33.07 | 4.05 | 0.992 | 120
Sumner WD maximum demand | 32.36 | 32.44 | -2.29 | 0.997 | 27.05 | 27.58 | 5.39 | 0.981 | 30.18 | 30.77 | 6.02 | 0.981 | 29.89 | 29.92 | 1.13 | 0.999 | 120
Sumner WN maximum demand | 32.78 | 32.91 | -2.96 | 0.996 | 27.02 | 27.47 | 4.96 | 0.984 | 30.15 | 30.65 | 5.53 | 0.984 | 29.86 | 29.86 | 0 | 1 | 120
Sunnybank SD maximum demand | 28.34 | 29.23 | 7.14 | 0.97 | 25.5 | 25.63 | 2.53 | 0.995 | 29.48 | 29.62 | 2.92 | 0.995 | 24.29 | 24.43 | 2.63 | 0.994 | 36
Sunnybank SN maximum demand | 26.43 | 27.01 | 5.56 | 0.979 | 24.26 | 24.29 | 1.33 | 0.999 | 28.04 | 28.08 | 1.53 | 0.999 | 23.12 | 23.17 | 1.52 | 0.998 | 36
Sunnybank WD maximum demand | 20.13 | 20.17 | -1.23 | 0.998 | 19.41 | 19.6 | 2.71 | 0.99 | 19.92 | 20.11 | 2.78 | 0.99 | 22.23 | 22.57 | 3.91 | 0.985 | 36
Sunnybank WN maximum demand | 21.41 | 21.42 | 0.63 | 1 | 18.84 | 18.98 | 2.3 | 0.993 | 19.33 | 19.47 | 2.36 | 0.993 | 21.77 | 22.05 | 3.51 | 0.987 | 36
Surfers Paradise SD maximum demand | 74.13 | 77.28 | 21.86 | 0.959 | 57.92 | 59 | 11.25 | 0.982 | 60.25 | 61.38 | 11.71 | 0.982 | 54.27 | 54.75 | 7.2 | 0.991 | 160
Surfers Paradise SN maximum demand | 76.02 | 78.72 | 20.45 | 0.966 | 59.09 | 60.07 | 10.79 | 0.984 | 61.47 | 62.49 | 11.23 | 0.984 | 55.37 | 55.76 | 6.58 | 0.993 | 160
Surfers Paradise WD maximum demand | 51.4 | 51.44 | 2.02 | 0.999 | 45.78 | 48.4 | 15.72 | 0.946 | 48.76 | 51.55 | 16.74 | 0.946 | 45.84 | 45.88 | 1.86 | 0.999 | 160
Surfers Paradise WN maximum demand | 57.64 | 57.74 | 3.54 | 0.998 | 50.94 | 53.22 | 15.42 | 0.957 | 54.25 | 56.68 | 16.42 | 0.957 | 50.98 | 51.02 | 2.24 | 0.999 | 160
Tallebudgera SD maximum demand | 8.07 | 8.12 | -0.89 | 0.994 | 0 | 0 | 0 |  | 0 | 0 | 0
Tallebudgera SN maximum demand | 7.9 | 8.03 | -1.46 | 0.983 | 0 | 0 | 0 |  | 0 | 0 | 0
Tallebudgera WD maximum demand | 8.18 | 8.49 | -2.26 | 0.964 | 0 | 0 | 0 |  | 0 | 0 | 0
Tallebudgera WN maximum demand | 8.78 | 9.07 | -2.28 | 0.968 | 0 | 0 | 0 |  | 0 | 0 | 0
Tamborine Village SD maximum demand | 4.7 | 5.08 | 1.93 | 0.925 | 3.38 | 3.48 | 0.83 | 0.971 | 3.91 | 4.02 | 0.96 | 0.971 | 3.53 | 3.64 | 0.87 | 0.971 | 8
Tamborine Village SN maximum demand | 4.88 | 5.2 | 1.78 | 0.939 | 3.44 | 3.53 | 0.82 | 0.973 | 3.97 | 4.08 | 0.95 | 0.973 | 3.59 | 3.69 | 0.86 | 0.973 | 8
Tamborine Village WD maximum demand | 4.08 | 4.19 | 0.94 | 0.974 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 2.26 | 2.62 | 1.33 | 0.862 | 8
Tamborine Village WN maximum demand | 4.71 | 4.82 | 1.03 | 0.977 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 2.26 | 2.62 | 1.33 | 0.862 | 8
Tanah Merah SD maximum demand | 15.27 | 15.41 | 2.1 | 0.991 | 14.72 | 14.73 | -0.62 | 0.999 | 16.53 | 16.55 | -0.7 | 0.999 | 14.88 | 14.88 | 0.18 | 1 | 30
Tanah Merah SN maximum demand | 14.71 | 14.79 | 1.55 | 0.994 | 15.11 | 15.12 | -0.43 | 1 | 16.97 | 16.98 | -0.48 | 1 | 15.28 | 16.16 | 5.26 | 0.946 | 30
Tanah Merah WD maximum demand | 12.1 | 12.17 | -1.28 | 0.994 | 12.07 | 12.22 | 1.88 | 0.988 | 14.43 | 14.6 | 2.25 | 0.988 | 14.22 | 14.55 | 3.08 | 0.977 | 30
Tanah Merah WN maximum demand | 14 | 14.04 | -1.11 | 0.997 | 13.76 | 13.85 | 1.6 | 0.993 | 16.44 | 16.55 | 1.92 | 0.993 | 16.2 | 16.5 | 3.09 | 0.982 | 30
Tarampa SD maximum demand | 2.95 | 3.54 | 1.95 | 0.834 | 5.69 | 6.06 | 2.07 | 0.94 | 5.98 | 6.36 | 2.17 | 0.94 | 5.47 | 6.21 | 2.95 | 0.88 | 11
Tarampa SN maximum demand | 3.06 | 3.6 | 1.89 | 0.851 | 5.87 | 6.17 | 1.91 | 0.951 | 6.16 | 6.48 | 2.01 | 0.951 | 5.63 | 6.29 | 2.81 | 0.895 | 11
Tarampa WD maximum demand | 2.21 | 2.8 | 1.71 | 0.791 | 3.7 | 3.94 | 1.35 | 0.939 | 3.7 | 3.94 | 1.35 | 0.939 | 3.7 | 4.15 | 1.88 | 0.892 | 11
Tarampa WN maximum demand | 2.78 | 3.35 | 1.87 | 0.829 | 4.45 | 4.74 | 1.63 | 0.939 | 4.45 | 4.74 | 1.63 | 0.939 | 4.45 | 4.89 | 2.02 | 0.911 | 11
Taringa SD maximum demand | 16.94 | 17.28 | 3.41 | 0.98 | 9.4 | 9.93 | 3.19 | 0.947 | 11.51 | 12.16 | 3.91 | 0.947 | 10.46 | 11.43 | 4.6 | 0.915 | 15
Taringa SN maximum demand | 17.92 | 18.23 | 3.34 | 0.983 | 9.73 | 10.22 | 3.15 | 0.951 | 11.92 | 12.53 | 3.86 | 0.951 | 10.83 | 11.69 | 4.4 | 0.926 | 15
Taringa WD maximum demand | 14.26 | 14.26 | -0.47 | 0.999 | 9.72 | 9.91 | 1.95 | 0.98 | 11.28 | 11.5 | 2.26 | 0.98 | 10.58 | 10.97 | 2.9 | 0.964 | 15
Taringa WN maximum demand | 16.71 | 16.71 | 0.43 | 1 | 11.04 | 11.23 | 2.06 | 0.983 | 12.81 | 13.03 | 2.39 | 0.983 | 11.97 | 12.4 | 3.24 | 0.965 | 15
Tennyson SD maximum demand | 12.43 | 14.73 | 7.9 | 0.844 | 10.73 | 12.52 | 6.45 | 0.857 | 11.37 | 13.27 | 6.84 | 0.857 | 10.41 | 12.22 | 6.4 | 0.852 | 25
Tennyson SN maximum demand | 11.77 | 13.59 | 6.79 | 0.866 | 9.39 | 11.08 | 5.89 | 0.847 | 9.95 | 11.74 | 6.24 | 0.847 | 9.11 | 10.78 | 5.76 | 0.845 | 25
Tennyson WD maximum demand | 10.27 | 11.4 | 4.96 | 0.9 | 8.32 | 9.81 | 5.19 | 0.848 | 8.32 | 9.81 | 5.19 | 0.848 | 8.31 | 9.63 | 4.87 | 0.863 | 25
Tennyson WN maximum demand | 10.46 | 11.54 | 4.86 | 0.907 | 8 | 9.36 | 4.87 | 0.854 | 8 | 9.36 | 4.87 | 0.854 | 7.98 | 9.16 | 4.49 | 0.872 | 25
Tenthill SD maximum demand | 2.09 | 2.15 | -0.48 | 0.974 | 2.35 | 2.59 | 1.08 | 0.909 | 2.35 | 2.58 | 1.08 | 0.909 | 2.12 | 2.16 | 0.39 | 0.983 | 8
Tenthill SN maximum demand | 2.32 | 2.37 | -0.5 | 0.978 | 2.77 | 3.07 | 1.32 | 0.903 | 2.77 | 3.06 | 1.31 | 0.903 | 2.5 | 2.55 | 0.5 | 0.98 | 8
Tenthill WD maximum demand | 2.09 | 2.12 | -0.32 | 0.988 | 2 | 2.2 | 0.93 | 0.907 | 2.45 | 2.7 | 1.14 | 0.907 | 2.42 | 2.49 | 0.59 | 0.972 | 8
Tenthill WN maximum demand | 2.33 | 2.37 | -0.45 | 0.982 | 2.35 | 2.56 | 1.02 | 0.917 | 2.88 | 3.14 | 1.25 | 0.917 | 2.85 | 2.92 | 0.63 | 0.977 | 8
Tewantin SD maximum demand | 35.73 | 36.87 | 9.09 | 0.969 | 25.5 | 25.67 | 2.98 | 0.993 | 27.67 | 27.86 | 3.23 | 0.993 | 23.48 | 23.94 | 4.68 | 0.981 | 50
Tewantin SN maximum demand | 33.61 | 34.45 | 7.57 | 0.976 | 25.01 | 25.16 | 2.74 | 0.994 | 27.14 | 27.3 | 2.97 | 0.994 | 23 | 23.4 | 4.3 | 0.983 | 50
Tewantin WD maximum demand | 33.12 | 33.19 | 2.08 | 0.998 | 19.78 | 20.11 | 3.6 | 0.984 | 22.99 | 23.37 | 4.19 | 0.984 | 21.42 | 21.55 | 2.38 | 0.994 | 50
Tewantin WN maximum demand | 34.53 | 34.66 | 3.02 | 0.996 | 21.3 | 21.67 | 3.98 | 0.983 | 24.75 | 25.18 | 4.63 | 0.983 | 22.94 | 23.14 | 3.03 | 0.991 | 50
The Gap SD maximum demand | 23.56 | 25.04 | 8.49 | 0.941 | 15.92 | 16.38 | 3.89 | 0.971 | 18.16 | 18.69 | 4.44 | 0.971 | 16.36 | 17.2 | 5.28 | 0.952 | 30
The Gap SN maximum demand | 25.09 | 26.63 | 8.93 | 0.942 | 15.88 | 16.35 | 3.88 | 0.971 | 18.12 | 18.65 | 4.42 | 0.971 | 16.33 | 17.14 | 5.2 | 0.953 | 30
The Gap WD maximum demand | 19.89 | 20.33 | 4.21 | 0.978 | 14.25 | 14.37 | 1.87 | 0.992 | 16.45 | 16.59 | 2.15 | 0.992 | 16.18 | 16.48 | 3.14 | 0.982 | 30
The Gap WN maximum demand | 22.88 | 23.58 | 5.71 | 0.97 | 15.9 | 16.09 | 2.45 | 0.988 | 18.35 | 18.57 | 2.83 | 0.988 | 18.05 | 18.51 | 4.07 | 0.976 | 30
Tin Can Bay SD maximum demand | 9.9 | 9.93 | -0.72 | 0.997 | 6.47 | 6.48 | 0.17 | 1 | 6.58 | 6.58 | 0.17 | 1 | 5.98 | 6.06 | 1 | 0.986 | 10
Tin Can Bay SN maximum demand | 10.72 | 10.73 | -0.5 | 0.999 | 7.33 | 7.34 | 0.43 | 0.998 | 7.45 | 7.46 | 0.43 | 0.998 | 6.77 | 6.87 | 1.19 | 0.985 | 10
Tin Can Bay WD maximum demand | 7.61 | 8.13 | -2.86 | 0.936 | 6.63 | 6.64 | -0.37 | 0.998 | 7.62 | 7.63 | -0.43 | 0.998 | 7.57 | 7.58 | 0.41 | 0.999 | 10
Tin Can Bay WN maximum demand | 9.62 | 9.86 | -2.14 | 0.976 | 7 | 7.02 | -0.53 | 0.997 | 8.04 | 8.06 | -0.61 | 0.997 | 7.99 | 8.01 | 0.55 | 0.998 | 10
Tingalpa SD maximum demand | 26.33 | 28.52 | 10.96 | 0.923 | 22.75 | 23.62 | 6.37 | 0.963 | 25.73 | 26.72 | 7.2 | 0.963 | 21.88 | 23.24 | 7.82 | 0.942 | 50
Tingalpa SN maximum demand | 26.39 | 28.41 | 10.52 | 0.929 | 23.45 | 24.26 | 6.24 | 0.966 | 26.52 | 27.44 | 7.05 | 0.966 | 22.57 | 23.78 | 7.47 | 0.949 | 50
Tingalpa WD maximum demand | 21.55 | 22.43 | 6.24 | 0.961 | 18.71 | 18.94 | 2.93 | 0.988 | 20.81 | 21.06 | 3.26 | 0.988 | 19.38 | 19.95 | 4.71 | 0.972 | 50
Tingalpa WN maximum demand | 23.71 | 24.69 | 6.87 | 0.96 | 19.49 | 19.68 | 2.74 | 0.99 | 21.68 | 21.89 | 3.05 | 0.99 | 20.08 | 20.59 | 4.57 | 0.975 | 50
Toogoolawah SD maximum demand | 3.43 | 3.55 | -0.91 | 0.966 | 3.79 | 4.13 | 1.64 | 0.918 | 4.51 | 4.91 | 1.95 | 0.918 | 4.05 | 4.05 | 0.04 | 1 | 8
Toogoolawah SN maximum demand | 3.9 | 3.98 | -0.79 | 0.98 | 4.4 | 4.52 | 1.03 | 0.974 | 5.24 | 5.38 | 1.22 | 0.974 | 4.71 | 4.71 | 0.23 | 0.999 | 8
Toogoolawah WD maximum demand | 3.29 | 3.52 | -1.25 | 0.935 | 2.66 | 2.73 | 0.62 | 0.974 | 3.35 | 3.44 | 0.78 | 0.974 | 3.3 | 3.3 | 0.11 | 0.999 | 8
Toogoolawah WN maximum demand | 3.78 | 3.91 | -1.02 | 0.965 | 2.88 | 2.96 | 0.68 | 0.974 | 3.63 | 3.73 | 0.85 | 0.974 | 3.57 | 3.58 | 0.22 | 0.998 | 8
Toorbul Point SD maximum demand | 7.23 | 7.41 | -1.61 | 0.976 | 4.75 | 4.88 | 1.15 | 0.972 | 5.47 | 5.63 | 1.33 | 0.972 | 4.98 | 5.3 | 1.81 | 0.94 | 15
Toorbul Point SN maximum demand | 7.69 | 7.79 | -1.27 | 0.987 | 5.52 | 5.78 | 1.71 | 0.955 | 6.36 | 6.66 | 1.97 | 0.955 | 5.79 | 6.16 | 2.11 | 0.94 | 15
Toorbul Point WD maximum demand | 7.17 | 7.36 | -1.66 | 0.974 | 4.94 | 5.01 | 0.83 | 0.986 | 5.18 | 5.25 | 0.87 | 0.986 | 5.17 | 5.32 | 1.27 | 0.971 | 15
Toorbul Point WN maximum demand | 8.6 | 8.66 | -1.04 | 0.993 | 5.46 | 5.6 | 1.23 | 0.975 | 5.72 | 5.87 | 1.29 | 0.975 | 5.71 | 5.91 | 1.52 | 0.966 | 15
Toowong SD maximum demand | 39.25 | 39.26 | 1.16 | 1 | 28.35 | 28.53 | 3.25 | 0.994 | 32.12 | 32.33 | 3.68 | 0.994 | 29.22 | 29.7 | 5.31 | 0.984 | 40
Toowong SN maximum demand | 36.71 | 36.75 | -1.66 | 0.999 | 27.09 | 27.15 | 1.73 | 0.998 | 30.69 | 30.76 | 1.95 | 0.998 | 27.93 | 28.19 | 3.83 | 0.991 | 40
Toowong WD maximum demand | 30.2 | 31.26 | -8.07 | 0.966 | 23.45 | 23.53 | 1.95 | 0.997 | 27.04 | 27.14 | 2.25 | 0.997 | 26.86 | 27.33 | 5.06 | 0.983 | 40
Toowong WN maximum demand | 31.62 | 32.58 | -7.86 | 0.97 | 23.02 | 23.13 | 2.29 | 0.995 | 26.54 | 26.68 | 2.65 | 0.995 | 26.36 | 26.73 | 4.38 | 0.986 | 40
Traveston Pumps SD maximum demand | 7.86 | 8.93 | 4.25 | 0.88 | 0 | 0 | 0 |  | 0 | 0 | 0
Traveston Pumps SN maximum demand | 8.94 | 9.96 | 4.39 | 0.898 | 0 | 0 | 0 |  | 0 | 0 | 0
Traveston Pumps WD maximum demand | 3.64 | 4.14 | 1.97 | 0.88 | 0 | 0 | 0 |  | 0 | 0 | 0
Traveston Pumps WN maximum demand | 4.39 | 4.87 | 2.12 | 0.9 | 0 | 0 | 0 |  | 0 | 0 | 0
Upper Mt Gravatt SD maximum demand | 43.28 | 44.02 | 8.05 | 0.983 | 27.79 | 27.87 | 2.11 | 0.997 | 30.59 | 30.67 | 2.32 | 0.997 | 34.97 | 35 | 1.48 | 0.999 | 75
Upper Mt Gravatt SN maximum demand | 40.02 | 40.43 | 5.76 | 0.99 | 26.73 | 26.76 | 1.35 | 0.999 | 29.41 | 29.45 | 1.48 | 0.999 | 33.54 | 33.54 | 0.51 | 1 | 75
Upper Mt Gravatt WD maximum demand | 27.52 | 27.68 | 2.99 | 0.994 | 20.6 | 21.52 | 6.21 | 0.957 | 21.43 | 22.39 | 6.47 | 0.957 | 22.93 | 23.24 | 3.8 | 0.987 | 75
Upper Mt Gravatt WN maximum demand | 29.11 | 29.22 | 2.48 | 0.996 | 21.03 | 22.05 | 6.63 | 0.954 | 21.89 | 22.95 | 6.9 | 0.954 | 23.65 | 23.89 | 3.39 | 0.99 | 75
Varsity Lakes SD maximum demand | 44.68 | 44.83 | 3.64 | 0.997 | 29.38 | 29.5 | 2.69 | 0.996 | 33.25 | 33.39 | 3.05 | 0.996 | 30.13 | 30.43 | 4.28 | 0.99 | 60
Varsity Lakes SN maximum demand | 42.11 | 42.18 | 2.34 | 0.998 | 30.77 | 30.85 | 2.28 | 0.997 | 34.82 | 34.92 | 2.58 | 0.997 | 31.55 | 31.83 | 4.17 | 0.991 | 60
Varsity Lakes WD maximum demand | 30.78 | 31.3 | -5.71 | 0.983 | 25.53 | 25.6 | 1.91 | 0.997 | 28.34 | 28.42 | 2.12 | 0.997 | 28.11 | 28.35 | 3.73 | 0.991 | 60
Varsity Lakes WN maximum demand | 33.79 | 34.06 | -4.25 | 0.992 | 27.44 | 27.62 | 3.13 | 0.994 | 30.47 | 30.66 | 3.47 | 0.994 | 30.21 | 30.62 | 4.98 | 0.987 | 60
Victoria Park SD maximum demand | 62.99 | 64.54 | 14.07 | 0.976 | 42.1 | 42.14 | 1.79 | 0.999 | 47.69 | 47.73 | 2.02 | 0.999 | 47.29 | 47.33 | 1.87 | 0.999 | 60
Victoria Park SN maximum demand | 49.66 | 50.06 | 6.34 | 0.992 | 36.27 | 36.29 | -1.23 | 0.999 | 41.08 | 41.11 | -1.39 | 0.999 | 40.9 | 41.12 | 4.27 | 0.995 | 60
Victoria Park WD maximum demand | 38.82 | 38.83 | -1.03 | 1 | 32.76 | 32.9 | 3.03 | 0.996 | 32.75 | 32.89 | 3.03 | 0.996 | 32.87 | 33.05 | 3.45 | 0.995 | 60
Victoria Park WN maximum demand | 34.19 | 34.41 | -3.93 | 0.993 | 30.91 | 30.95 | 1.65 | 0.999 | 30.9 | 30.94 | 1.65 | 0.999 | 31 | 31.05 | 1.67 | 0.999 | 60
Victoria Point SD maximum demand | 31.64 | 32.51 | 7.5 | 0.973 | 19.07 | 19.08 | 0.65 | 0.999 | 23.06 | 23.08 | 0.79 | 0.999 | 20.85 | 20.92 | 1.78 | 0.996 | 50
Victoria Point SN maximum demand | 31.45 | 32.2 | 6.89 | 0.977 | 20.45 | 20.88 | 4.24 | 0.979 | 24.73 | 25.25 | 5.12 | 0.979 | 22.35 | 22.44 | 1.97 | 0.996 | 50
Victoria Point WD maximum demand | 25.83 | 25.84 | 0.83 | 0.999 | 17.38 | 17.5 | 2.02 | 0.993 | 18.99 | 19.11 | 2.21 | 0.993 | 18.87 | 19.26 | 3.84 | 0.98 | 50
Victoria Point WN maximum demand | 30.83 | 30.89 | 1.96 | 0.998 | 19.12 | 19.38 | 3.13 | 0.987 | 20.88 | 21.16 | 3.42 | 0.987 | 20.76 | 21.16 | 4.11 | 0.981 | 50
Wacol SD maximum demand | 27.74 | 29.79 | 10.84 | 0.931 | 25.38 | 27.94 | 11.68 | 0.908 | 26.77 | 29.47 | 12.32 | 0.908 | 25.1 | 26.02 | 6.86 | 0.965 | 57
Wacol SN maximum demand | 22.66 | 23.41 | 5.88 | 0.968 | 20.15 | 21.19 | 6.58 | 0.951 | 21.25 | 22.35 | 6.94 | 0.951 | 20.1 | 20.31 | 2.87 | 0.99 | 57
Wacol WD maximum demand | 21.75 | 22 | 3.35 | 0.988 | 21.56 | 23.09 | 8.25 | 0.934 | 23.43 | 25.09 | 8.97 | 0.934 | 22.81 | 23.06 | 3.41 | 0.989 | 57
Wacol WN maximum demand | 19.66 | 19.7 | 1.32 | 0.998 | 20.8 | 23.97 | 11.92 | 0.868 | 22.6 | 26.05 | 12.95 | 0.868 | 22.22 | 22.36 | 2.51 | 0.994 | 57
Wacol South SD maximum demand | 23.42 | 24.05 | 5.47 | 0.974 | 22.1 | 22.63 | 4.87 | 0.977 | 26.84 | 27.48 | 5.91 | 0.977 | 24.2 | 24.39 | 3.01 | 0.992 | 50
Wacol South SN maximum demand | 21.54 | 21.71 | 2.76 | 0.992 | 19.9 | 20.58 | 5.24 | 0.967 | 24.17 | 25 | 6.36 | 0.967 | 21.8 | 21.85 | 1.53 | 0.998 | 50
Wacol South WD maximum demand | 19.44 | 19.46 | 0.86 | 0.999 | 13.62 | 13.7 | 1.48 | 0.994 | 15.22 | 15.3 | 1.65 | 0.994 | 20.52 | 21.2 | 5.3 | 0.968 | 50
Wacol South WN maximum demand | 18.51 | 18.51 | -0.46 | 1 | 13.36 | 13.79 | 3.41 | 0.969 | 14.92 | 15.4 | 3.81 | 0.969 | 20.03 | 20.64 | 4.99 | 0.97 | 50
Wamuran SD maximum demand | 4.84 | 5.86 | 3.31 | 0.825 | 3.12 | 3.19 | 0.66 | 0.978 | 3.33 | 3.41 | 0.71 | 0.978 | 3.8 | 3.89 | 0.81 | 0.978 | 8
Wamuran SN maximum demand | 4.72 | 5.54 | 2.91 | 0.851 | 3.17 | 3.26 | 0.76 | 0.972 | 3.39 | 3.48 | 0.81 | 0.972 | 3.85 | 3.96 | 0.92 | 0.972 | 8
Wamuran WD maximum demand | 3.88 | 4.28 | 1.81 | 0.907 | 3.79 | 4.03 | 1.35 | 0.942 | 4.48 | 4.75 | 1.6 | 0.942 | 2.21 | 2.34 | 0.79 | 0.942 | 8
Wamuran WN maximum demand | 4.03 | 4.4 | 1.76 | 0.916 | 3.66 | 3.72 | 0.68 | 0.983 | 4.32 | 4.4 | 0.8 | 0.983 | 2.23 | 2.27 | 0.41 | 0.983 | 8
Wellington Rd SD maximum demand | 73.83 | 76.32 | 19.32 | 0.967 | 45.69 | 46.47 | 8.48 | 0.983 | 53.49 | 54.41 | 9.93 | 0.983 | 49.17 | 49.24 | 2.63 | 0.999 | 120
Wellington Rd SN maximum demand | 63.46 | 64.77 | 12.95 | 0.98 | 41.87 | 42.23 | 5.53 | 0.991 | 49.02 | 49.45 | 6.47 | 0.991 | 45.12 | 45.42 | 5.29 | 0.993 | 120
Wellington Rd WD maximum demand | 43.48 | 43.48 | -0.56 | 1 | 33.6 | 34.81 | 9.08 | 0.965 | 35.71 | 36.99 | 9.65 | 0.965 | 35.35 | 35.46 | 2.68 | 0.997 | 120
Wellington Rd WN maximum demand | 41.05 | 41.12 | -2.46 | 0.998 | 33.01 | 34.38 | 9.62 | 0.96 | 35.08 | 36.53 | 10.22 | 0.96 | 34.73 | 34.81 | 2.44 | 0.998 | 120
West Darra SD maximum demand | 23.76 | 24.03 | 3.54 | 0.989 | 0 | 0 | 0 |  | 0 | 0 | 0
West Darra SN maximum demand | 21.64 | 21.84 | 2.9 | 0.991 | 0 | 0 | 0 |  | 0 | 0 | 0
West Darra WD maximum demand | 19.89 | 19.9 | 0.7 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0
West Darra WN maximum demand | 19.91 | 19.91 | 0.19 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0
West End SD maximum demand | 76.19 | 80.24 | 25.17 | 0.95 | 58.72 | 59.84 | 11.54 | 0.981 | 72.92 | 74.32 | 14.33 | 0.981 | 66.57 | 68.07 | 14.22 | 0.978 | 120
West End SN maximum demand | 62.37 | 64.64 | 17.01 | 0.965 | 53.51 | 54.28 | 9.15 | 0.986 | 66.45 | 67.41 | 11.36 | 0.986 | 60.65 | 61.68 | 11.22 | 0.983 | 120
West End WD maximum demand | 46.59 | 47.42 | 8.85 | 0.982 | 40.78 | 44.23 | 17.12 | 0.922 | 42.71 | 46.32 | 17.93 | 0.922 | 42.67 | 42.91 | 4.49 | 0.994 | 120
West End WN maximum demand | 43.41 | 43.74 | 5.39 | 0.992 | 38.4 | 40.62 | 13.26 | 0.945 | 40.22 | 42.55 | 13.89 | 0.945 | 40.18 | 40.24 | 2.22 | 0.998 | 120
West Maroochydore SD maximum demand | 23.76 | 23.76 | -0.37 | 1 | 29.02 | 29.32 | 4.15 | 0.99 | 32.63 | 32.96 | 4.66 | 0.99 | 31.2 | 31.25 | 1.75 | 0.998 | 90
West Maroochydore SN maximum demand | 22.53 | 22.63 | -2.16 | 0.995 | 27.61 | 27.73 | 2.55 | 0.996 | 31.04 | 31.17 | 2.86 | 0.996 | 29.69 | 29.99 | 4.27 | 0.99 | 90
West Maroochydore WD maximum demand | 19.95 | 20.44 | -4.41 | 0.976 | 26.26 | 27.11 | 6.75 | 0.969 | 29.56 | 30.52 | 7.6 | 0.969 | 29.44 | 29.81 | 4.65 | 0.988 | 90
West Maroochydore WN maximum demand | 20.65 | 21.15 | -4.56 | 0.976 | 27.51 | 27.95 | 4.96 | 0.984 | 30.96 | 31.46 | 5.58 | 0.984 | 30.84 | 31.08 | 3.89 | 0.992 | 90
Whiteside SD maximum demand | 11.59 | 13.31 | 6.54 | 0.871 | 6.85 | 7.96 | 4.06 | 0.861 | 6.97 | 8.1 | 4.13 | 0.861 | 6.38 | 7.42 | 3.78 | 0.861 | 15
Whiteside SN maximum demand | 10.59 | 11.88 | 5.38 | 0.891 | 5.45 | 6.03 | 2.58 | 0.903 | 5.54 | 6.14 | 2.63 | 0.903 | 5.07 | 5.62 | 2.41 | 0.903 | 15
Whiteside WD maximum demand | 9.63 | 10.65 | 4.55 | 0.904 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 8.67 | 10.05 | 5.1 | 0.862 | 15
Whiteside WN maximum demand | 9.65 | 10.46 | 4.02 | 0.923 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 8.67 | 10.05 | 5.1 | 0.862 | 15
Windaroo SD maximum demand | 11.68 | 11.81 | 1.74 | 0.989 | 0 | 0 | 0 |  | 0 | 0 | 0
Windaroo SN maximum demand | 10.76 | 10.78 | 0.55 | 0.999 | 0 | 0 | 0 |  | 0 | 0 | 0
Windaroo WD maximum demand | 8.71 | 8.75 | -0.77 | 0.996 | 0 | 0 | 0 |  | 0 | 0 | 0
Windaroo WN maximum demand | 8.47 | 8.59 | -1.44 | 0.986 | 0 | 0 | 0 |  | 0 | 0 | 0
Withcott SD maximum demand | 2.44 | 2.63 | 0.98 | 0.928 | 0 | 0 | 0 |  | 0 | 0 | 0
Withcott SN maximum demand | 2.6 | 2.77 | 0.97 | 0.937 | 0 | 0 | 0 |  | 0 | 0 | 0
Withcott WD maximum demand | 2.2 | 2.26 | 0.51 | 0.975 | 0 | 0 | 0 |  | 0 | 0 | 0
Withcott WN maximum demand | 2.34 | 2.39 | 0.5 | 0.978 | 0 | 0 | 0 |  | 0 | 0 | 0
Wivenhoe SD maximum demand | 5.03 | 5.9 | 3.09 | 0.852 | 3.96 | 4.23 | 1.5 | 0.935 | 3.96 | 4.23 | 1.5 | 0.935 | 3.59 | 4.02 | 1.81 | 0.892 | 10
Wivenhoe SN maximum demand | 4.25 | 4.86 | 2.34 | 0.876 | 3.45 | 3.57 | 0.91 | 0.967 | 3.45 | 3.57 | 0.91 | 0.967 | 3.13 | 3.42 | 1.37 | 0.916 | 10
Wivenhoe WD maximum demand | 4.29 | 4.89 | 2.35 | 0.877 | 3.34 | 3.51 | 1.1 | 0.95 | 3.34 | 3.51 | 1.1 | 0.95 | 3.32 | 3.62 | 1.46 | 0.916 | 10
Wivenhoe WN maximum demand | 4.23 | 4.69 | 2.03 | 0.902 | 3.44 | 3.52 | 0.76 | 0.976 | 3.44 | 3.52 | 0.76 | 0.976 | 3.42 | 3.7 | 1.4 | 0.925 | 10
Woodford SD maximum demand | 8.27 | 8.37 | 1.28 | 0.988 | 8.28 | 8.78 | 2.92 | 0.943 | 9.28 | 9.84 | 3.27 | 0.943 | 8.33 | 9.33 | 4.21 | 0.893 | 15
Woodford SN maximum demand | 7.96 | 7.98 | 0.66 | 0.997 | 8.22 | 8.68 | 2.81 | 0.946 | 9.21 | 9.73 | 3.15 | 0.946 | 8.27 | 9.08 | 3.74 | 0.911 | 15
Woodford WD maximum demand | 6.86 | 6.91 | -0.83 | 0.993 | 5.73 | 5.74 | 0.36 | 0.998 | 6.35 | 6.36 | 0.4 | 0.998 | 7.42 | 7.95 | 2.88 | 0.932 | 15
Woodford WN maximum demand | 6.71 | 6.82 | -1.25 | 0.983 | 6.21 | 6.22 | 0.35 | 0.998 | 6.88 | 6.89 | 0.39 | 0.998 | 7.95 | 8.4 | 2.7 | 0.947 | 15
Woodridge SD maximum demand | 38.82 | 39.29 | 6.04 | 0.988 | 29.33 | 30.38 | 7.91 | 0.966 | 33.03 | 34.21 | 8.91 | 0.966 | 31.07 | 31.07 | 0.53 | 1 | 75
Woodridge SN maximum demand | 36.5 | 36.67 | 3.52 | 0.995 | 26.62 | 27.1 | 5.08 | 0.982 | 29.98 | 30.52 | 5.73 | 0.982 | 28.8 | 29.05 | 3.84 | 0.991 | 75
Woodridge WD maximum demand | 29.36 | 29.76 | -4.86 | 0.987 | 23 | 23 | 0.52 | 1 | 24.39 | 24.4 | 0.55 | 1 | 23.96 | 24.14 | 2.98 | 0.992 | 75
Woodridge WN maximum demand | 31.81 | 32.25 | -5.31 | 0.986 | 23.72 | 24.41 | 5.76 | 0.972 | 25.16 | 25.89 | 6.11 | 0.972 | 24.68 | 24.79 | 2.35 | 0.995 | 75
Wulkuraka SD maximum demand | 8.58 | 9.52 | 4.12 | 0.901 | 0 | 0 | 0 |  | 0 | 0 | 0
Wulkuraka SN maximum demand | 8.31 | 9.1 | 3.72 | 0.913 | 0 | 0 | 0 |  | 0 | 0 | 0
Wulkuraka WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Wulkuraka WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
Wynnum SD maximum demand | 27.63 | 28.18 | 5.56 | 0.98 | 19.57 | 21.1 | 7.88 | 0.928 | 21.92 | 23.63 | 8.83 | 0.928 | 19.07 | 19.6 | 4.51 | 0.973 | 50
Wynnum SN maximum demand | 27.77 | 28.2 | 4.91 | 0.985 | 20.23 | 21.72 | 7.88 | 0.932 | 22.66 | 24.32 | 8.83 | 0.932 | 19.81 | 20.31 | 4.44 | 0.976 | 50
Wynnum WD maximum demand | 23.04 | 23.04 | -0.46 | 1 | 18.26 | 19.03 | 5.35 | 0.96 | 20.99 | 21.87 | 6.14 | 0.96 | 22.41 | 23.83 | 8.11 | 0.94 | 50
Wynnum WN maximum demand | 25.33 | 25.34 | 0.51 | 1 | 19.88 | 20.75 | 5.92 | 0.958 | 22.85 | 23.84 | 6.81 | 0.958 | 24.44 | 25.94 | 8.71 | 0.942 | 50
Yamanto SD maximum demand | 8.08 | 8.23 | -1.54 | 0.982 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 10.38 | 11.07 | 3.83 | 0.938 | 25
Yamanto SN maximum demand | 7.85 | 8.04 | -1.77 | 0.976 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 10.43 | 11.06 | 3.66 | 0.944 | 25
Yamanto WD maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | [5 empty] | 25
Yamanto WN maximum demand |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | [5 empty] | 25
Yandina SD maximum demand | 9.45 | 10.43 | 4.43 | 0.905 | 5.76 | 5.87 | 1.15 | 0.981 | 5.84 | 5.95 | 1.16 | 0.981 | 5.77 | 5.93 | 1.35 | 0.974 | 15
Yandina SN maximum demand | 9.11 | 9.84 | 3.72 | 0.926 | 5.17 | 5.21 | 0.62 | 0.993 | 5.24 | 5.28 | 0.63 | 0.993 | 5.19 | 5.23 | 0.63 | 0.993 | 15
Yandina WD maximum demand | 7.94 | 8.42 | 2.81 | 0.943 | 5.2 | 5.26 | 0.77 | 0.989 | 5.87 | 5.93 | 0.87 | 0.989 | 5.51 | 5.56 | 0.77 | 0.99 | 15
Yandina WN maximum demand | 8.22 | 8.58 | 2.47 | 0.958 | 5.22 | 5.22 | 0.08 | 1 | 5.89 | 5.89 | 0.09 | 1 | 5.51 | 5.51 | 0.21 | 0.999 | 15
Yatala SD maximum demand | 25.12 | 25.48 | 4.31 | 0.986 | 33.68 | 35.35 | 10.76 | 0.953 | 36.89 | 38.73 | 11.78 | 0.953 | 40.58 | 42.05 | 11.04 | 0.965 | 60
Yatala SN maximum demand | 24.05 | 24.23 | 2.94 | 0.993 | 33.72 | 33.82 | 2.52 | 0.997 | 36.94 | 37.04 | 2.76 | 0.997 | 38.34 | 39.08 | 7.54 | 0.981 | 60
Yatala WD maximum demand | 19.31 | 19.31 | 0.37 | 1 | 29.68 | 30 | 4.35 | 0.989 | 33.87 | 34.23 | 4.96 | 0.989 | 35.56 | 36.14 | 6.46 | 0.984 | 60
Yatala WN maximum demand | 18.82 | 18.83 | -0.75 | 0.999 | 29.01 | 29.45 | 5.11 | 0.985 | 33.1 | 33.61 | 5.83 | 0.985 | 34.56 | 35.05 | 5.81 | 0.986 | 60
Zillmere SD maximum demand | 26.45 | 27.07 | -5.78 | 0.977 | 32.44 | 32.67 | 3.9 | 0.993 | 37.83 | 38.1 | 4.54 | 0.993 | 28.99 | 29.27 | 4.05 | 0.99 | 50
Zillmere SN maximum demand | 24.96 | 25.86 | -6.79 | 0.965 | 31.09 | 31.2 | 2.6 | 0.997 | 36.27 | 36.39 | 3.03 | 0.997 | 27.84 | 27.98 | 2.79 | 0.995 | 50
Zillmere WD maximum demand | 29.98 | 30.78 | -7 | 0.974 | 24.53 | 24.77 | 3.41 | 0.99 | 27.27 | 27.53 | 3.79 | 0.99 | 28.02 | 28.02 | 0.37 | 1 | 50
Zillmere WN maximum demand | 33.14 | 33.62 | -5.67 | 0.986 | 25.89 | 26.13 | 3.52 | 0.991 | 28.78 | 29.05 | 3.91 | 0.991 | 29.64 | 29.65 | 0.77 | 1 | 50
Contents

## 3. Outcomes customer service
Energex
Customer Service
2012-13
This information is used to monitor the service performance of the DNSP, and assist the AER understand service outcomes for customers. The information will inform the AER’s assessment of future service improvement expenditure proposals by the DNSP. The information may be used in performance reports.
Table 1: Quality of supply
2012-13
Over voltage events - due to high voltage injection
Customers receiving over-voltage - due to high voltage injection
Over voltage events - due to lightning
Customers receiving over-voltage - due to lightning
Over voltage events - due to voltage regulation or other cause
Customers receiving over-voltage - due to voltage regulation or other cause
Voltage variations - steady state (zone sub)
Voltage variations - one minute (zone sub)
Voltage variations - 10 seconds (zone sub) Min<0.7
Voltage variations - 10 seconds (zone sub) Min<0.8
Voltage variations - 10 seconds (zone sub) Min<0.9
Voltage variations - steady state (feeder)
Voltage variations - % zone subs monitored
Voltage variations - % feeders monitored
Customers - quality of supply improvement
Table 2: Complaints - technical quality of supply
2012-13
Complaints - technical quality of supply - number | 1185
Complaints by category (%)
Low voltage supply | 11
Voltage dips | 25.6
Voltage swell | 19
Voltage spike (impulsive transient) | 1.9
Waveform distortion | 4
TV or radio interference | 3.1
Noise from appliances | 3.4
Solar related | 32
Other | 0
Complaints by Likely Cause (%)
Network equipment faulty | 4.3
Network interference by NSP equipment | 11.9
Network interference by another customer | 1.2
Network limitation | 24.8
Customer internal problem | 13.3
No problem identified | 37.7
Environmental | 0.1
Other | 6.7
Table 3: Customer service
2012-13
Timely provision of services
Connections made | 20243
Connections not made on agreed date | 34
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 790
Streetlights - not repaired by "fix by" date | 14
Streetlights - average number of days to repair | 4
Total streetlights | 300841
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 758682
Calls to fault line not answered within 30 seconds | 51949
Calls to fault line - average waiting time before call answered | 43
Calls abandoned - percentage | 10
Call centre - number of overload events | 0
Customer complaints (number)
Complaint - reliability of supply | 61
Complaint - technical quality of supply | 1185
Complaint - administrative process or customer service | 1072
Complaint - connection or augmentation | 1166
Complaint - other | 197
Total complaints | 3681
Contents

## 4. General information
Energex
General information
2012-13
The information will enable the AER to better understand the network and service performance outcomes reported by the DNSP. Network characteristics will be used to normalise other information, to assist in any benchmarking or other comparisons between DNSP financial and service performance outcomes.
Table 1: Metered supply points
Where feeders cannot be classified to the feeder categories, please provide an explanation why not, and use an allocation method to classify the feeders. Describe the allocation method.
| Total no. | By type of customer |  | By supply voltage
Number of metered supply points |  | Domestic | Non-domestic | Subtransmission | HV | LV
CBD | 3452.2654 | 2042.8619 | 1409.4035 | 0 | 33.1765 | 3325.5061
Urban | 984130.2474 | 899217.0921 | 84913.1552 | 9.2857 | 137.81 | 983826.5789
Rural Short | 359612.4872 | 334480.0459 | 25132.4413 | 0.71429 | 17.0136 | 359844.915
Total | 1347195 | 1235740 | 111455 | 10 | 188 | 1346997
Table 2: Energy delivered
Where feeders cannot be classified to the feeder categories, please provide an explanation why not, and use an allocation method to classify the feeders. Describe the allocation method.
| Total GWh | By type of customer |  | By supply voltage
Energy delivered (GWh) |  | Domestic | Non-domestic | Subtransmission | HV | LV - residential | LV - non residential
CBD | 898.7886 | 9.0322 | 889.7564 | 0 | 432.6243 | 9.0322 | 481.5823
Urban | 16396.2891 | 5374.2381 | 11022.051 | 198.3871 | 2540.1724 | 5374.2381 | 8071.4655
Rural Short | 3724.9222 | 2226.7296 | 1498.1926 | 11.6129 | 172.2033 | 2226.7296 | 1501.9521
Total | 21020 | 7610 | 13410 | 210 | 3145 | 7610 | 10055
Table 3: Line length
Note: where a line supplies more than one feeder type, the line length should be proportionately allocated according to the number of feeders in each category. For example if a line supplied one each of a CBD and Urban feeder, 50% of the line length would be allocated to CBD and 50% to urban.
| Total km | Underground lines |  |  | Overhead lines
Line Length (km) |  | Subtransmission | HV | LV | Subtransmission | HV | LV
CBD | 208 | 47 | 102 | 40 | 19 | 0 | 0
Urban | 25269 | 974 | 3755 | 7040 | 3097 | 3652 | 6751
Rural Short | 26402.459 | 17.459 | 1433 | 3377 | 187 | 13877 | 7511
Rural Long | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 51879.459 | 1038.459 | 5290 | 10457 | 3303 | 17529 | 14262
Table 4: Customer numbers
| Total no. | By supply voltage
Customer numbers |  | Subtransmission | HV | LV - residential | LV - non residential
Total customer numbers beginning of period | 1333620 | 10 | 192 | 1220365 | 113053
Total customer numbers end of period | 1347195 | 10 | 188 | 1235740 | 111257
Controlled load customers | 727775 | 0 | 0 | 727775 | 0
Total new customer connections | 20243 | 0 | 0 | 15375 | 4868
Customer disconnections | 102433 | 0 | 0 | 100637 | 1796
Table 5: Number and capacity of transformers
Number & total capacity of transformers | Total no. | Capacity (MVA)
Distribution | 47436 | 13644
Zone substation | 424 | 10824
Table 6: Unmetered supply points
Number of unmetered supply points
CBD | 0
Urban | 14286
Rural Short | 2322
Rural Long | 0
Total | 16608
Table 7: Poles and substations
Number of poles and substations
Subtransmission poles | 28657
Distribution poles | 385142
Subtransmission and zone substations | 279
Distribution substations | 45880
Table 8: Other information
Other information
Distribution losses (% of purchases) | 4.9%
Network Service area (sq.km) | 25064
Network Maximum Coincident Demand (MW) | 4475
FTE employees | 3433
Contents

## 5a. Network data outage
Energex
Nework data - outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Unplanned Outages
Date (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of outage | Number of customers interrupted | Duration of interruption (Mins) | Total unplanned customer minutes off supply (Mins) | Unplanned SAIDI impact | Unplanned SAIFI impact
2012-07-01 | 275490 | ACR4 | URBAN | Equipment failure | 13.76 | 65 | 894.4 | 0.00089434 | 1.3759e-05
2012-07-01 | 275494 | TCB2 | RURAL | Third party impacts | 101 | 106 | 10706 | 0.031942 | 0.00030134
2012-07-01 | 275500 | KBN5A | RURAL | Other | 5 | 87 | 435 | 0.0012978 | 1.4918e-05
2012-07-01 | 275562 | JBB1B | RURAL | Other | 10.5 | 72 | 756 | 0.0022556 | 3.1327e-05
2012-07-02 | 275502 | ACR2A | URBAN | Other | 1240.5 | 46 | 57063 | 0.057043 | 0.0012401
2012-07-02 | 275502 | ACR2B | URBAN | Other | 1455.5 | 46.931 | 68060 | 0.068036 | 0.001455
2012-07-02 | 275720 | TWT11A | RURAL | Operational error | 30 | 66 | 1980 | 0.0059113 | 8.9565e-05
2012-07-02 | 275721 | TWT11A | RURAL | Operational error | 30 | 89 | 2670 | 0.0079713 | 8.9565e-05
2012-07-02 | 276079 | CBW7 | RURAL | Animals | 34 | 51 | 1734 | 0.0051769 | 0.00010151
2012-07-02 | 276470 | ARG9A | URBAN | Equipment failure | 103.83 | 122 | 12667.26 | 0.012663 | 0.00010379
2012-07-02 | 277858 | HPE13A | URBAN | Other | 70.264 | 203 | 14263.592 | 0.014259 | 7.0239e-05
2012-07-03 | 275640 | MCW11 | RURAL | Other | 822 | 20.878 | 14380.5 | 0.042961 | 0.0024557
2012-07-03 | 275680 | BRD5A | RURAL | Vegetation | 1681.51 | 69.98 | 111332.81 | 0.3326 | 0.0050234
2012-07-03 | 275695 | KBR5A | RURAL | Equipment failure | 96 | 49.027 | 5412 | 0.016168 | 0.0002868
2012-07-03 | 275696 | INA5A | URBAN | Equipment failure | 22.11 | 88 | 1945.68 | 0.0019444 | 2.2096e-05
2012-07-03 | 275698 | GYM9B | RURAL | Other | 161.5 | 324.0513 | 46483 | 0.13887 | 0.00048248
2012-07-03 | 275700 | SPO69A | URBAN | Operational error | 86.79 | 100 | 8679 | 0.0086734 | 8.6734e-05
2012-07-03 | 275722 | IBL2 | RURAL | Vegetation | 14 | 124 | 1736 | 0.0051862 | 4.1824e-05
2012-07-03 | 275723 | AHD12A | URBAN | Equipment failure | 31.33 | 76 | 2381.08 | 0.0023795 | 3.131e-05
2012-07-03 | 275724 | BMT2 | RURAL | Equipment failure | 9 | 77.3167 | 695.85 | 0.0020788 | 2.6887e-05
2012-07-03 | 275725 | NBR1 | RURAL | Other | 142.5 | 37 | 5272.5 | 0.015751 | 0.00042571
2012-07-03 | 276078 | WFD5A | RURAL | Operational error | 5.61 | 105 | 589.05 | 0.0017598 | 1.676e-05
2012-07-03 | 277323 | AHD12A | URBAN | Other | 77.2 | 109 | 8414.8 | 0.0084094 | 7.715e-05
2012-07-03 | 277810 | LGV6A | RURAL | Other | 20 | 129.8333 | 2596.6667 | 0.0077574 | 5.9749e-05
2012-07-04 | 275742 | CMY1 | RURAL | Other | 5.5 | 44 | 242 | 0.00072344 | 1.6442e-05
2012-07-04 | 275780 | TGW1 | RURAL | Equipment failure | 72 | 95 | 6840 | 0.020448 | 0.00021524
2012-07-04 | 275833 | BWH8A | RURAL | Equipment failure | 2.92 | 355 | 1036.6 | 0.0030988 | 8.7291e-06
2012-07-04 | 275898 | AHD5 | URBAN | Other | 143.25 | 27 | 3867.75 | 0.0038641 | 0.00014312
2012-07-04 | 275899 | AHD19 | URBAN | Animals | 83 | 88.2667 | 7326.1333 | 0.0073193 | 8.2923e-05
2012-07-04 | 275900 | CMD11A | RURAL | Equipment failure | 12.83 | 62.7833 | 805.5102 | 0.002408 | 3.8354e-05
2012-07-04 | 275904 | KRN12 | URBAN | Other | 95.04 | 47 | 4466.88 | 0.0044627 | 9.4951e-05
2012-07-04 | 276073 | ACR5 | RURAL | Other | 4 | 105 | 420 | 0.0012556 | 1.1958e-05
2012-07-04 | 276074 | RCF9A | URBAN | Other | 142.83 | 65 | 9283.95 | 0.0092753 | 0.0001427
2012-07-04 | 276075 | CBW11 | RURAL | Other | 20.5 | 47 | 963.5 | 0.0028803 | 6.1283e-05
2012-07-04 | 276076 | CLRSRD17 | URBAN | Other | 18.5 | 43 | 795.5 | 0.00079476 | 1.8483e-05
2012-07-04 | 276077 | WMR1 | RURAL | Other | 4.5 | 284 | 1278 | 0.0038205 | 1.3452e-05
2012-07-05 | 275841 | BMT1 | RURAL | Other | 1488.64 | 3 | 4465.92 | 0.013347 | 0.0044488
2012-07-05 | 275841 | BMT2 | RURAL | Other | 1304.94 | 3 | 3914.82 | 0.0117 | 0.0038999
2012-07-05 | 275841 | BMT3 | RURAL | Other | 1631.48 | 3 | 4894.44 | 0.014627 | 0.0048757
2012-07-05 | 275841 | BMT4 | RURAL | Other | 708.9 | 3 | 2126.7 | 0.0063557 | 0.0021186
2012-07-05 | 275841 | BMT5 | RURAL | Other | 329.16 | 3 | 987.48 | 0.0029511 | 0.0009837
2012-07-05 | 275841 | CRY2A | RURAL | Other | 732.98 | 15 | 10994.7 | 0.032858 | 0.0021905
2012-07-05 | 275841 | CRY3A | RURAL | Other | 967.93 | 15 | 14518.95 | 0.04339 | 0.0028927
2012-07-05 | 275841 | CRY5A | RURAL | Other | 95.99 | 15 | 1439.85 | 0.004303 | 0.00028687
2012-07-05 | 275841 | CRY6A | RURAL | Other | 707.48 | 15 | 10612.2 | 0.031715 | 0.0021143
2012-07-05 | 275841 | EMD1 | RURAL | Other | 353.49 | 3 | 1060.47 | 0.0031692 | 0.0010564
2012-07-05 | 275841 | EMD2 | RURAL | Other | 498.5 | 3 | 1495.5 | 0.0044693 | 0.0014898
2012-07-05 | 275841 | EMD3 | RURAL | Other | 644 | 3 | 1932 | 0.0057738 | 0.0019246
2012-07-05 | 275841 | YDA1B | RURAL | Other | 403 | 29 | 11687 | 0.034927 | 0.0012044
2012-07-05 | 275841 | YDA2B | RURAL | Other | 166.5 | 29 | 4828.5 | 0.01443 | 0.00049759
2012-07-05 | 275841 | YDA3A | RURAL | Other | 383.5 | 29 | 11121.5 | 0.033237 | 0.0011461
2012-07-05 | 275841 | YDA5A | RURAL | Other | 872.73 | 29 | 25309.17 | 0.075637 | 0.0026082
2012-07-05 | 275841 | YDA6A | URBAN | Other | 5 | 29 | 145 | 0.00014487 | 4.9955e-06
2012-07-05 | 275842 | NBR8 | RURAL | Equipment failure | 569.75 | 98 | 55835.5 | 0.16687 | 0.0017027
2012-07-05 | 275861 | SMF5A | RURAL | Other | 8 | 10 | 80 | 0.00023908 | 2.3908e-05
2012-07-05 | 275862 | AHL11A | URBAN | Equipment failure | 2.06 | 50 | 103 | 0.00010291 | 2.0581e-06
2012-07-05 | 275893 | ENG9 | URBAN | Equipment failure | 1171.5 | 3 | 3514.5 | 0.0035113 | 0.0011704
2012-07-05 | 275897 | HWL11A | URBAN | Equipment failure | 76.4478 | 190 | 14525.082 | 0.014512 | 7.6379e-05
2012-07-05 | 275901 | NBR8 | RURAL | Other | 6 | 145 | 870 | 0.0026 | 1.7931e-05
2012-07-05 | 275902 | NBR8 | RURAL | Equipment failure | 54 | 18 | 972 | 0.0029049 | 0.00016138
2012-07-05 | 275903 | NBR8 | RURAL | Equipment failure | 3 | 110 | 330 | 0.00098621 | 8.9656e-06
2012-07-05 | 276471 | JBB16A | RURAL | Animals | 5.61 | 16 | 89.76 | 0.00026825 | 1.6766e-05
2012-07-05 | 281137 | TRG5 | URBAN | Operational error | 49.6089 | 55 | 2728.4895 | 0.002726 | 4.9564e-05
2012-07-06 | 275924 | ARL13A | URBAN | Other | 956.33 | 88.9333 | 97805.85 | 0.09772 | 0.00095549
2012-07-06 | 275956 | TWG16 | URBAN | Equipment failure | 2 | 163 | 326 | 0.00032571 | 1.9982e-06
2012-07-06 | 275959 | CFD9A | URBAN | Equipment failure | 5.83 | 71 | 413.93 | 0.00041357 | 5.8249e-06
2012-07-06 | 275959 | KRN11 | URBAN | Equipment failure | 1299.49 | 77.1176 | 99763.07 | 0.099676 | 0.0012984
2012-07-06 | 275959 | NDH9 | URBAN | Equipment failure | 965.32 | 79 | 76260.28 | 0.076193 | 0.00096447
2012-07-07 | 275984 | KRN11 | URBAN | Equipment failure | 82 | 8 | 656 | 0.00065544 | 8.1931e-05
2012-07-07 | 276020 | MLY3 | RURAL | Equipment failure | 34.32 | 101 | 3466.32 | 0.010353 | 0.0001025
2012-07-07 | 276072 | LTN2 | RURAL | Other | 29.37 | 51 | 1497.87 | 0.0044737 | 8.772e-05
2012-07-08 | 275998 | WMR3 | RURAL | Third party impacts | 353.82 | 71.8932 | 27413.02 | 0.081834 | 0.0010562
2012-07-08 | 276000 | F1173 | URBAN | Third party impacts | 16.335 | 616 | 10123.7 | 0.010116 | 1.6323e-05
2012-07-08 | 276001 | CBW5 | URBAN | Other | 771.85 | 41.8333 | 58155.45 | 0.058112 | 0.00077127
2012-07-08 | 276045 | SPD4A | URBAN | Equipment failure | 71.8278 | 109 | 7829.2302 | 0.0078234 | 7.1774e-05
2012-07-08 | 276468 | 1129 | URBAN | Equipment failure | 21 | 150.3833 | 3158.05 | 0.0031557 | 2.0984e-05
2012-07-08 | 276469 | LHM5 | RURAL | Animals | 52.75 | 112 | 5908 | 0.017637 | 0.00015747
2012-07-08 | 277381 | JBB4A | URBAN | Other | 1.98 | 134 | 265.32 | 0.00026512 | 1.9785e-06
2012-07-09 | 276042 | KBR6A | RURAL | Other | 5 | 25 | 125 | 0.00037291 | 1.4917e-05
2012-07-09 | 276044 | GBN4 | RURAL | Equipment failure | 4 | 112 | 448 | 0.0013365 | 1.1933e-05
2012-07-09 | 276069 | BMG2A | URBAN | Equipment failure | 0.99 | 325 | 321.75 | 0.00032156 | 9.8941e-07
2012-07-09 | 276071 | WNM5 | URBAN | Equipment failure | 107 | 71 | 7597 | 0.0075925 | 0.00010694
2012-07-09 | 276120 | TGW3 | RURAL | Other | 0.99 | 97 | 96.03 | 0.00028649 | 2.9535e-06
2012-07-09 | 276466 | RLB13B | RURAL | Equipment failure | 9 | 67 | 603 | 0.0017989 | 2.685e-05
2012-07-10 | 276084 | CRBTHP14 | URBAN | Vegetation | 415 | 17 | 7055 | 0.0070519 | 0.00041482
2012-07-10 | 276088 | SRD4A | URBAN | Third party impacts | 7.7 | 205 | 1578.5 | 0.0015778 | 7.6967e-06
2012-07-10 | 276093 | QEN10 | URBAN | Third party impacts | 34.4 | 38 | 1307.2 | 0.0013066 | 3.4385e-05
2012-07-10 | 276094 | LDR11 | URBAN | Third party impacts | 3.28 | 164 | 537.92 | 0.00053769 | 3.2786e-06
2012-07-10 | 276121 | KBN2A | RURAL | Other | 28.8 | 153 | 4406.4 | 0.013137 | 8.5864e-05
2012-07-10 | 276164 | WFD3A | RURAL | Equipment failure | 0.99 | 135 | 133.65 | 0.00039846 | 2.9516e-06
2012-07-10 | 276166 | LTN8 | RURAL | Other | 2.805 | 173 | 485.265 | 0.0014468 | 8.3628e-06
2012-07-10 | 276167 | AHD8 | URBAN | Animals | 0.66 | 99 | 65.34 | 6.5312e-05 | 6.5971e-07
2012-07-10 | 277375 | INA7A | RURAL | Other | 64 | 148 | 9472 | 0.02824 | 0.00019081
2012-07-10 | 282961 | CBW11 | RURAL | Other | 1.65 | 107 | 176.55 | 0.00052637 | 4.9193e-06
2012-07-11 | 276117 | MCW11 | RURAL | Other | 822 | 56.1463 | 51803 | 0.15438 | 0.0024496
2012-07-11 | 276119 | WMR1 | RURAL | Weather | 635.5 | 18 | 11439 | 0.034089 | 0.0018938
2012-07-11 | 276119 | WMR2 | RURAL | Weather | 275.02 | 51.2481 | 29553.37 | 0.088071 | 0.00081957
2012-07-11 | 276126 | CLM4A | URBAN | Equipment failure | 681 | 38 | 25878 | 0.025869 | 0.00068077
2012-07-11 | 276140 | TBV3 | RURAL | Equipment failure | 115.5 | 231.9231 | 26334.5 | 0.078478 | 0.0003442
2012-07-11 | 276143 | MBG2 | RURAL | Equipment failure | 4 | 129 | 516 | 0.0015377 | 1.192e-05
2012-07-11 | 276168 | KWA10A | URBAN | Other | 35 | 116 | 4060 | 0.0040586 | 3.4988e-05
2012-07-11 | 276465 | ARG5A | URBAN | Animals | 68.42 | 67 | 4584.14 | 0.0045826 | 6.8397e-05
2012-07-11 | 277324 | IBL2 | RURAL | Other | 2 | 139 | 278 | 0.00082845 | 5.9601e-06
2012-07-12 | 276161 | HIS5A | URBAN | Other | 741 | 93 | 68913 | 0.068896 | 0.00074082
2012-07-12 | 276161 | HIS5B | URBAN | Other | 857 | 93 | 79701 | 0.079681 | 0.00085679
2012-07-12 | 276182 | MFN15A | RURAL | Third party impacts | 789.5 | 31 | 24474.5 | 0.072902 | 0.0023517
2012-07-12 | 276218 | MGP13A | RURAL | Weather | 97 | 117.2632 | 24695 | 0.073558 | 0.00028893
2012-07-12 | 276221 | YTA22A | RURAL | Equipment failure | 43 | 65 | 2795 | 0.0083254 | 0.00012808
2012-07-12 | 276222 | BWH13A | RURAL | Equipment failure | 18 | 110 | 1980 | 0.0058978 | 5.3616e-05
2012-07-12 | 276223 | TCB2 | RURAL | Animals | 409 | 120 | 49080 | 0.14619 | 0.0012183
2012-07-12 | 276240 | KBN5A | RURAL | Equipment failure | 2.5 | 146 | 365 | 0.0010872 | 7.4467e-06
2012-07-12 | 276241 | MDH4A | URBAN | Equipment failure | 13.695 | 103 | 1410.585 | 0.0014102 | 1.3692e-05
2012-07-12 | 276242 | WFD2B | RURAL | Other | 18.5 | 78 | 1443 | 0.0042982 | 5.5105e-05
2012-07-12 | 276262 | PWC6 | RURAL | Other | 17 | 63.6833 | 1082.6167 | 0.0032248 | 5.0637e-05
2012-07-12 | 276263 | LBH1B | RURAL | Third party impacts | 48 | 236 | 11328 | 0.033742 | 0.00014298
2012-07-13 | 276224 | AHD20 | URBAN | Equipment failure | 75.5 | 83 | 6266.5 | 0.0062655 | 7.5488e-05
2012-07-13 | 276260 | GLY6 | URBAN | Other | 465.985 | 65 | 30289.025 | 0.030284 | 0.00046591
2012-07-13 | 276261 | MLY1 | RURAL | Weather | 10.4 | 318 | 3307.2 | 0.0098465 | 3.0964e-05
2012-07-13 | 276280 | PWC5 | RURAL | Equipment failure | 289 | 72 | 20808 | 0.061951 | 0.00086044
2012-07-13 | 276288 | RLB15A | URBAN | Equipment failure | 16 | 36 | 576 | 0.00057591 | 1.5998e-05
2012-07-13 | 276309 | GYN5B | URBAN | Third party impacts | 42.5 | 57 | 2422.5 | 0.0024221 | 4.2494e-05
2012-07-13 | 276342 | CPK9 | RURAL | Other | 0.33 | 134 | 44.22 | 0.00013166 | 9.8251e-07
2012-07-13 | 276343 | PRG2A | RURAL | Other | 3.2 | 125 | 400 | 0.0011909 | 9.5273e-06
2012-07-13 | 276362 | PWC5 | RURAL | Other | 14.52 | 240.7833 | 3496.174 | 0.010409 | 4.323e-05
2012-07-13 | 276464 | CNB26A | RURAL | Other | 12 | 93 | 1116 | 0.0033227 | 3.5727e-05
2012-07-14 | 276311 | MLY4 | RURAL | Equipment failure | 623.49 | 124.5849 | 81384.63 | 0.24219 | 0.0018554
2012-07-14 | 276313 | BVL5A | URBAN | Equipment failure | 1949.99 | 90.9063 | 176352.59 | 0.17634 | 0.0019499
2012-07-14 | 276344 | IPL1 | RURAL | Other | 3.6 | 132 | 475.2 | 0.0014141 | 1.0713e-05
2012-07-14 | 276363 | MLY4 | RURAL | Equipment failure | 26.5 | 322 | 8533 | 0.025393 | 7.886e-05
2012-07-14 | 276364 | GBN4 | RURAL | Other | 12.5 | 83 | 1037.5 | 0.0030875 | 3.7198e-05
2012-07-15 | 276316 | WMR3 | RURAL | Third party impacts | 60 | 144 | 8640 | 0.025699 | 0.00017847
2012-07-15 | 276318 | ARG10 | URBAN | Other | 134.99 | 16 | 2159.84 | 0.0021599 | 0.00013499
2012-07-15 | 276338 | LGL15A | URBAN | Other | 955.99 | 63 | 60227.37 | 0.06023 | 0.00095602
2012-07-15 | 276402 | MLS15A | URBAN | Other | 147 | 8 | 1176 | 0.001176 | 0.00014701
2012-07-15 | 276460 | KLG4A | URBAN | Equipment failure | 91.5 | 186 | 17019 | 0.01702 | 9.1503e-05
2012-07-16 | 276381 | AMR2 | RURAL | Equipment failure | 33.34 | 20 | 666.8 | 0.0019824 | 9.912e-05
2012-07-16 | 276384 | WHO1 | RURAL | Equipment failure | 41.5 | 80 | 3320 | 0.0098704 | 0.00012338
2012-07-16 | 276385 | KBR2A | RURAL | Vegetation | 428.66 | 33 | 14145.78 | 0.042056 | 0.0012744
2012-07-16 | 276387 | JBB3A | RURAL | Equipment failure | 76 | 174.4516 | 24396 | 0.07253 | 0.00022595
2012-07-16 | 276397 | EMP21A | RURAL | Third party impacts | 41.6 | 153 | 6364.8 | 0.018923 | 0.00012368
2012-07-16 | 276462 | WED6A | URBAN | Other | 158.08 | 81 | 12804.48 | 0.012806 | 0.0001581
2012-07-16 | 276463 | CPR5 | URBAN | Equipment failure | 69 | 35 | 2415 | 0.0024153 | 6.9009e-05
2012-07-16 | 276499 | BWH8A | RURAL | Equipment failure | 64 | 138 | 8832 | 0.026258 | 0.00019027
2012-07-16 | 276500 | CLD30A | URBAN | Operational error | 121.5 | 57 | 6925.5 | 0.0069264 | 0.00012152
2012-07-16 | 276501 | CLD30A | URBAN | Equipment failure | 80.19 | 120 | 9622.8 | 0.009624 | 8.02e-05
2012-07-17 | 276420 | CBT8A | RURAL | Other | 1400.53 | 23 | 32212.19 | 0.095711 | 0.0041613
2012-07-17 | 276467 | MGP13A | RURAL | Other | 6 | 265 | 1590 | 0.0047243 | 1.7828e-05
2012-07-17 | 276494 | BBSRDL8 | RURAL | Equipment failure | 4.95 | 60 | 297 | 0.00088247 | 1.4708e-05
2012-07-17 | 276495 | RWD1 | RURAL | Other | 10 | 65 | 650 | 0.0019313 | 2.9713e-05
2012-07-17 | 276497 | MGP2A | URBAN | Animals | 982.5 | 48 | 47160 | 0.047172 | 0.00098276
2012-07-17 | 277295 | AHL11A | URBAN | Animals | 36.3 | 38 | 1379.4 | 0.0013798 | 3.6309e-05
2012-07-17 | 277380 | MGP4 | RURAL | Other | 10.7778 | 211 | 2274.1158 | 0.006757 | 3.2024e-05
2012-07-18 | 276541 | CCY21A | URBAN | Other | 1 | 26 | 26 | 2.601e-05 | 1.0004e-06
2012-07-18 | 276552 | MTB15A | RURAL | Weather | 13.5 | 7 | 94.5 | 0.00028062 | 4.0088e-05
2012-07-18 | 276580 | IBL2 | RURAL | Equipment failure | 102 | 123 | 12546 | 0.037255 | 0.00030289
2012-07-18 | 276582 | WFD2B | RURAL | Operational error | 18.5 | 42 | 777 | 0.0023073 | 5.4936e-05
2012-07-18 | 276600 | GGR3 | RURAL | Other | 2.8 | 85 | 238 | 0.00070674 | 8.3146e-06
2012-07-18 | 276840 | AHD4A | URBAN | Other | 81.18 | 68 | 5520.24 | 0.0055224 | 8.1211e-05
2012-07-18 | 276970 | WFD2B | RURAL | Other | 18.5 | 115 | 2127.5 | 0.0063176 | 5.4936e-05
2012-07-19 | 276583 | MDH1A | URBAN | Animals | 13 | 64 | 832 | 0.00083243 | 1.3007e-05
2012-07-19 | 276620 | TGW1 | RURAL | Equipment failure | 6.83 | 122 | 833.26 | 0.0024729 | 2.027e-05
2012-07-19 | 276643 | SMF2A | RURAL | Equipment failure | 13.5 | 225 | 3278.5 | 0.0097297 | 4.0064e-05
2012-07-19 | 276644 | MGL5 | URBAN | Other | 26.5 | 34 | 901 | 0.00090146 | 2.6514e-05
2012-07-19 | 276645 | MGL5 | URBAN | Other | 25 | 41 | 1025 | 0.0010255 | 2.5013e-05
2012-07-19 | 276677 | MGL5 | URBAN | Other | 26.5 | 55 | 1457.5 | 0.0014583 | 2.6514e-05
2012-07-19 | 276678 | MGL5 | URBAN | Other | 25 | 50 | 1250 | 0.0012506 | 2.5013e-05
2012-07-19 | 276679 | WED6A | URBAN | Other | 158.08 | 23 | 7271.68 | 0.0072754 | 0.00015816
2012-07-19 | 276680 | CHL8 | URBAN | Other | 17.3 | 28 | 484.4 | 0.00048465 | 1.7309e-05
2012-07-19 | 276700 | WHO1 | RURAL | Other | 4 | 178 | 712 | 0.002113 | 1.1871e-05
2012-07-19 | 276829 | BDA12B | URBAN | Equipment failure | 181.5 | 87 | 15790.5 | 0.015799 | 0.00018159
2012-07-20 | 276720 | BLH16A | RURAL | Third party impacts | 1914.67 | 34 | 65098.78 | 0.19304 | 0.0056778
2012-07-20 | 276720 | BLHSTN16 | RURAL | Third party impacts | 340.86 | 34 | 11589.24 | 0.034367 | 0.0010108
2012-07-20 | 276721 | EMD3 | RURAL | Other | 40.51 | 84 | 3402.84 | 0.010091 | 0.00012013
2012-07-20 | 276722 | NGI2B | RURAL | Other | 9 | 7 | 63 | 0.00018682 | 2.6689e-05
2012-07-20 | 276741 | BDT4 | RURAL | Equipment failure | 262.5 | 73 | 19162.5 | 0.056824 | 0.00077842
2012-07-20 | 276742 | TWT11A | RURAL | Other | 27 | 5 | 135 | 0.00040033 | 8.0066e-05
2012-07-20 | 276743 | TRG5 | URBAN | Equipment failure | 116 | 145 | 16820 | 0.016832 | 0.00011608
2012-07-20 | 276749 | RIS2 | URBAN | Third party impacts | 60.3 | 150.5 | 4428.7 | 0.0044319 | 6.0343e-05
2012-07-20 | 276786 | KCY5 | RURAL | Other | 522.5 | 70 | 36575 | 0.10846 | 0.0015494
2012-07-20 | 276830 | CPB3 | URBAN | Animals | 29 | 46 | 1334 | 0.0013349 | 2.9021e-05
2012-07-20 | 276831 | BTA15A | URBAN | Animals | 59.5 | 83.3167 | 4957.3417 | 0.0049609 | 5.9542e-05
2012-07-20 | 276841 | MLY4 | RURAL | Equipment failure | 15.18 | 486 | 7377.48 | 0.021877 | 4.5015e-05
2012-07-20 | 277298 | AGE8 | URBAN | Other | 69 | 88 | 6072 | 0.0060763 | 6.9049e-05
2012-07-20 | 277767 | SBH6 | URBAN | Other | 50.4339 | 137 | 6909.4443 | 0.0069144 | 5.047e-05
2012-07-21 | 276793 | PWC4 | RURAL | Vegetation | 227 | 10 | 2270 | 0.0067261 | 0.00067261
2012-07-21 | 276795 | BPN34A | URBAN | Equipment failure | 1616.49 | 57 | 92139.93 | 0.092223 | 0.001618
2012-07-21 | 276795 | BPN34B | URBAN | Equipment failure | 1 | 57 | 57 | 5.7052e-05 | 1.0009e-06
2012-07-21 | 276842 | CLD2 | URBAN | Other | 21.33 | 331 | 7060.23 | 0.0070666 | 2.1349e-05
2012-07-21 | 276845 | FDS1 | RURAL | Other | 1.98 | 19 | 37.62 | 0.00011147 | 5.8668e-06
2012-07-21 | 276860 | RBA37A | URBAN | Vegetation | 14.85 | 92 | 1366.2 | 0.0013674 | 1.4863e-05
2012-07-22 | 276796 | MTB13A | RURAL | Vegetation | 343.33 | 60 | 20599.8 | 0.060988 | 0.0010165
2012-07-22 | 276798 | CLD17A | URBAN | Other | 35.07 | 74 | 2595.18 | 0.0025981 | 3.5109e-05
2012-07-22 | 276799 | NBR4 | RURAL | Other | 460 | 88 | 40480 | 0.11985 | 0.0013619
2012-07-22 | 276800 | GYN7A | RURAL | Vegetation | 6.93 | 168 | 1164.24 | 0.0034468 | 2.0517e-05
2012-07-22 | 276805 | DBY9 | URBAN | Equipment failure | 1925.51 | 41.4884 | 80098.88 | 0.080188 | 0.0019277
2012-07-22 | 276810 | BBH16A | URBAN | Equipment failure | 162.33 | 11 | 1785.63 | 0.0017876 | 0.00016251
2012-07-22 | 276832 | CNB26A | RURAL | Other | 45 | 85 | 3825 | 0.011324 | 0.00013323
2012-07-22 | 276833 | CMA8A | RURAL | Equipment failure | 12.33 | 53.75 | 662.7375 | 0.0019621 | 3.6504e-05
2012-07-22 | 276834 | CHL11A | RURAL | Equipment failure | 133.5 | 80 | 10680 | 0.031619 | 0.00039524
2012-07-22 | 276843 | MLY1 | RURAL | Animals | 19 | 73 | 1387 | 0.0041064 | 5.6251e-05
2012-07-22 | 276844 | GYN7A | RURAL | Vegetation | 21 | 264 | 5544 | 0.016414 | 6.2173e-05
2012-07-22 | 276846 | THL3 | RURAL | Equipment failure | 0.67 | 113 | 75.71 | 0.00022415 | 1.9836e-06
2012-07-22 | 276967 | WNM2A | URBAN | Other | 133.5 | 111 | 14818.5 | 0.014835 | 0.00013365
2012-07-22 | 276968 | DBY9 | URBAN | Animals | 45.21 | 63 | 2848.23 | 0.0028514 | 4.526e-05
2012-07-23 | 276861 | MGP13A | RURAL | Equipment failure | 147 | 235 | 34545 | 0.1022 | 0.00043489
2012-07-23 | 276869 | BDA3A | URBAN | Third party impacts | 207.5 | 224 | 46480 | 0.04654 | 0.00020777
2012-07-23 | 276870 | WRG2A | URBAN | Other | 116.5 | 65 | 7572.5 | 0.0075823 | 0.00011665
2012-07-23 | 276901 | SBY3 | URBAN | Equipment failure | 10.5 | 56 | 588 | 0.00058876 | 1.0514e-05
2012-07-23 | 276966 | CBW12 | URBAN | Equipment failure | 144.9822 | 45 | 6524.199 | 0.0065326 | 0.00014517
2012-07-23 | 276969 | NBR8 | RURAL | Equipment failure | 8.5 | 123 | 1045.5 | 0.003093 | 2.5147e-05
2012-07-23 | 277856 | SBY2A | URBAN | Other | 28 | 397 | 11116 | 0.01113 | 2.8036e-05
2012-07-24 | 276902 | TMH5A | URBAN | Animals | 66 | 51 | 3366 | 0.0033713 | 6.6103e-05
2012-07-24 | 276903 | RBA43A | RURAL | Other | 21 | 2 | 42 | 0.00012413 | 6.2064e-05
2012-07-24 | 276905 | CPD2A | RURAL | Equipment failure | 121.99 | 16.5962 | 1882.95 | 0.0055649 | 0.00036053
2012-07-24 | 276907 | HMTPTR5 | URBAN | Third party impacts | 278 | 74 | 20572 | 0.020604 | 0.00027843
2012-07-24 | 276907 | PTR1 | URBAN | Third party impacts | 0.5 | 74 | 37 | 3.7058e-05 | 5.0078e-07
2012-07-24 | 276907 | PTR2 | URBAN | Third party impacts | 2.42 | 74 | 179.08 | 0.00017936 | 2.4238e-06
2012-07-24 | 276907 | PTR3 | URBAN | Third party impacts | 2 | 74 | 148 | 0.00014823 | 2.0031e-06
2012-07-24 | 276965 | DBY6 | URBAN | Animals | 98.5578 | 75 | 7391.835 | 0.0074034 | 9.8712e-05
2012-07-24 | 277063 | WED6A | URBAN | Animals | 144.67 | 73 | 10560.91 | 0.010577 | 0.0001449
2012-07-25 | 277002 | NMC5A | RURAL | Other | 42.5 | 27 | 1147.5 | 0.003388 | 0.00012548
2012-07-25 | 277039 | WSE6A | RURAL | Other | 395.75 | 129.0357 | 65330.75 | 0.19289 | 0.0011685
2012-07-25 | 277047 | MDR24A | URBAN | Other | 699.66 | 47 | 32884.02 | 0.032944 | 0.00070094
2012-07-25 | 277062 | TBV3 | RURAL | Other | 15 | 115 | 1725 | 0.0050931 | 4.4288e-05
2012-07-25 | 277067 | GYN6A | RURAL | Other | 19.5 | 63 | 1228.5 | 0.0036272 | 5.7574e-05
2012-07-25 | 277068 | BMT1 | RURAL | Equipment failure | 11 | 118 | 1298 | 0.0038324 | 3.2478e-05
2012-07-25 | 277069 | GYM7A | RURAL | Other | 12 | 90 | 1080 | 0.0031887 | 3.543e-05
2012-07-25 | 277803 | NMC3A | RURAL | Other | 19.6 | 146.4833 | 2871.0733 | 0.0084769 | 5.7869e-05
2012-07-26 | 277060 | MDR8A | URBAN | Other | 3 | 46 | 138 | 0.00013829 | 3.0063e-06
2012-07-26 | 277061 | LTA4B | URBAN | Animals | 36.96 | 65 | 2402.4 | 0.0024075 | 3.7038e-05
2012-07-26 | 277082 | SPE9 | URBAN | Third party impacts | 1059.68 | 41.0889 | 38567.76 | 0.038649 | 0.0010619
2012-07-26 | 277118 | BPN34A | URBAN | Third party impacts | 16 | 53 | 848 | 0.00084979 | 1.6034e-05
2012-07-26 | 277119 | BLB8B | URBAN | Animals | 99 | 18 | 1782 | 0.0017858 | 9.9208e-05
2012-07-26 | 277297 | MLS15A | URBAN | Other | 48.51 | 27 | 1309.77 | 0.0013125 | 4.8612e-05
2012-07-26 | 277300 | ZMR3 | URBAN | Other | 87 | 52 | 4524 | 0.0045335 | 8.7183e-05
2012-07-27 | 277117 | GBG26 | URBAN | Third party impacts | 921.99 | 83 | 76525.17 | 0.076708 | 0.00092419
2012-07-27 | 277117 | NDH10 | URBAN | Third party impacts | 173.49 | 132 | 22900.68 | 0.022955 | 0.0001739
2012-07-27 | 277122 | MLT24A | URBAN | Third party impacts | 31.2 | 158 | 4929.6 | 0.0049413 | 3.1274e-05
2012-07-27 | 277142 | RIS2 | URBAN | Other | 39.5 | 9 | 355.5 | 0.00035635 | 3.9594e-05
2012-07-27 | 277164 | RCF2A | URBAN | Weather | 1992.07 | 39.6786 | 77060.29 | 0.077244 | 0.0019968
2012-07-27 | 277200 | INA9A | URBAN | Third party impacts | 1253.58 | 29 | 36353.82 | 0.03644 | 0.0012566
2012-07-27 | 277201 | NBR5 | RURAL | Equipment failure | 5.6 | 220 | 1232 | 0.0036302 | 1.6501e-05
2012-07-27 | 277204 | INA9A | URBAN | Third party impacts | 62.83 | 256 | 16084.48 | 0.016123 | 6.298e-05
2012-07-27 | 277242 | GYM2A | RURAL | Equipment failure | 1 | 40 | 40 | 0.00011786 | 2.9466e-06
2012-07-27 | 277460 | CVL3A | URBAN | Other | 102 | 96 | 9792 | 0.0098153 | 0.00010224
2012-07-27 | 277461 | CLR3 | RURAL | Animals | 24.5 | 40 | 980 | 0.0028876 | 7.2191e-05
2012-07-27 | 277811 | LGV6A | RURAL | Other | 20 | 75 | 1500 | 0.0044198 | 5.8931e-05
2012-07-28 | 277203 | BMT2 | RURAL | Third party impacts | 227.5 | 190 | 43225 | 0.12726 | 0.0006698
2012-07-28 | 277207 | WFD1B | RURAL | Weather | 81.99 | 131.9643 | 15248.86 | 0.044896 | 0.00024139
2012-07-28 | 277208 | 403 | URBAN | Other | 1 | 31 | 31 | 3.108e-05 | 1.0026e-06
2012-07-28 | 277208 | MTB12A | URBAN | Other | 1 | 31 | 31 | 3.108e-05 | 1.0026e-06
2012-07-28 | 277208 | MTB13A | RURAL | Other | 1926.49 | 31 | 59721.19 | 0.17583 | 0.005672
2012-07-28 | 277208 | MTB15A | RURAL | Other | 777 | 31 | 24087 | 0.070917 | 0.0022876
2012-07-28 | 277208 | MTB16A | RURAL | Other | 377.33 | 31 | 11697.23 | 0.034439 | 0.0011109
2012-07-28 | 277208 | MTB17A | RURAL | Other | 689.34 | 31 | 21369.54 | 0.062916 | 0.0020296
2012-07-28 | 277208 | MTB1B | RURAL | Other | 968.83 | 26 | 25189.58 | 0.074163 | 0.0028524
2012-07-28 | 277208 | MTB2A | RURAL | Other | 598.99 | 26 | 15573.74 | 0.045852 | 0.0017635
2012-07-28 | 277208 | MTB3A | RURAL | Other | 989.33 | 26 | 25722.58 | 0.075732 | 0.0029128
2012-07-28 | 277208 | TBV1 | RURAL | Other | 41.17 | 26 | 1070.42 | 0.0031515 | 0.00012121
2012-07-28 | 277208 | TBV2 | RURAL | Other | 294.5 | 26 | 7657 | 0.022544 | 0.00086707
2012-07-28 | 277208 | TBV3 | RURAL | Other | 115.5 | 26 | 3003 | 0.0088414 | 0.00034005
2012-07-28 | 277208 | TBV4 | RURAL | Other | 776.17 | 26 | 20180.42 | 0.059415 | 0.0022852
2012-07-28 | 277209 | BLH12A | RURAL | Other | 658.49 | 63.3048 | 84522.44 | 0.24885 | 0.0019387
2012-07-28 | 277209 | UPC1 | RURAL | Other | 138 | 2 | 828 | 0.0024378 | 0.0004063
2012-07-28 | 277241 | TGW4 | RURAL | Animals | 15.41 | 147 | 2265.27 | 0.0066694 | 4.537e-05
2012-07-28 | 277462 | ARG5A | URBAN | Animals | 69 | 70 | 4830 | 0.0048425 | 6.9178e-05
2012-07-29 | 277211 | WFD1B | RURAL | Equipment failure | 277.97 | 45.3115 | 15546.8 | 0.045725 | 0.00081754
2012-07-29 | 277213 | RWD1 | RURAL | Equipment failure | 54.5 | 73 | 3978.5 | 0.011701 | 0.00016029
2012-07-29 | 277214 | BBH16A | URBAN | Equipment failure | 1567.33 | 29.375 | 44389.1 | 0.044516 | 0.0015718
2012-07-29 | 277296 | SHW10A | URBAN | Other | 144.5 | 66 | 9537 | 0.0095643 | 0.00014491
2012-07-29 | 277463 | UMG2B | RURAL | Animals | 60.33 | 21 | 1266.93 | 0.0037262 | 0.00017744
2012-07-29 | 277855 | UMG2B | RURAL | Other | 48.264 | 74.5833 | 3599.69 | 0.010587 | 0.00014195
2012-07-30 | 277229 | MTB1B | RURAL | Other | 968.83 | 12 | 11625.96 | 0.034157 | 0.0028464
2012-07-30 | 277229 | MTB2A | RURAL | Other | 598.99 | 12 | 7187.88 | 0.021118 | 0.0017598
2012-07-30 | 277229 | MTB3A | RURAL | Other | 989.33 | 12 | 11871.96 | 0.03488 | 0.0029067
2012-07-30 | 277240 | ALY8 | URBAN | Other | 76.5 | 20 | 1530 | 0.0015348 | 7.6741e-05
2012-07-30 | 277280 | TBV2 | RURAL | Third party impacts | 33.5 | 110 | 3685 | 0.010827 | 9.8424e-05
2012-07-30 | 277290 | BHD41A | URBAN | Equipment failure | 39 | 46 | 1794 | 0.0017997 | 3.9123e-05
2012-07-30 | 277291 | BPN2A | URBAN | Third party impacts | 1.65 | 95 | 156.75 | 0.00015724 | 1.6552e-06
2012-07-31 | 277320 | SPC2B | RURAL | Other | 2.83 | 11 | 31.13 | 9.1365e-05 | 8.306e-06
2012-07-31 | 277342 | MGP2A | URBAN | Equipment failure | 982.5 | 50 | 49125 | 0.049294 | 0.00098588
2012-07-31 | 277343 | NMK23A | URBAN | Vegetation | 10.783 | 110 | 1186.13 | 0.0011902 | 1.082e-05
2012-07-31 | 277366 | WSO3A | URBAN | Third party impacts | 34.5 | 55 | 1897.5 | 0.001904 | 3.4619e-05
2012-07-31 | 277373 | SMR7A | URBAN | Equipment failure | 90.22 | 203 | 18314.66 | 0.018378 | 9.053e-05
2012-07-31 | 277374 | TWG14A | URBAN | Other | 96.57 | 18 | 1738.26 | 0.0017442 | 9.6902e-05
2012-07-31 | 277376 | NRG6 | URBAN | Third party impacts | 2.805 | 168 | 471.24 | 0.00047286 | 2.8146e-06
2012-07-31 | 277423 | PRG2A | RURAL | Other | 1 | 84 | 84 | 0.00024654 | 2.935e-06
2012-07-31 | 277570 | BMT3 | RURAL | Equipment failure | 5 | 85 | 425 | 0.0012474 | 1.4675e-05
2012-07-31 | 277571 | CLD17A | URBAN | Other | 167 | 90.4 | 15096.8 | 0.015149 | 0.00016757
2012-08-01 | 277371 | WED16A | URBAN | Other | 1010.71 | 109.3571 | 111087.39 | 0.1115 | 0.0010145
2012-08-01 | 277421 | MHL12A | RURAL | Third party impacts | 4.6 | 127 | 584.2 | 0.0017128 | 1.3487e-05
2012-08-01 | 277453 | BBH12B | URBAN | Equipment failure | 188 | 35 | 6580 | 0.0066045 | 0.0001887
2012-08-01 | 277455 | WCL13A | URBAN | Third party impacts | 5 | 380 | 1900 | 0.0019071 | 5.0186e-06
2012-08-01 | 277455 | WCL3 | URBAN | Third party impacts | 128.66 | 123 | 16178.76 | 0.016239 | 0.00012914
2012-08-01 | 277765 | WNM2A | URBAN | Equipment failure | 115.5 | 72 | 8316 | 0.008347 | 0.00011593
2012-08-01 | 278383 | KMR17A | URBAN | Animals | 21.12 | 66 | 1393.92 | 0.0013991 | 2.1199e-05
2012-08-02 | 277456 | TGW2 | RURAL | Animals | 146.99 | 312 | 45860.88 | 0.13431 | 0.00043049
2012-08-02 | 277480 | NSD2B | URBAN | Other | 598.99 | 17 | 10182.83 | 0.010224 | 0.0006014
2012-08-02 | 277566 | GLY4 | URBAN | Equipment failure | 1.75 | 3 | 5.25 | 5.2711e-06 | 1.757e-06
2012-08-02 | 277569 | BTA1A | URBAN | Equipment failure | 18 | 232 | 4176 | 0.0041928 | 1.8072e-05
2012-08-02 | 277572 | MLB12A | RURAL | Equipment failure | 28 | 87.1 | 2438.8 | 0.0071425 | 8.2003e-05
2012-08-02 | 277573 | CLM3 | RURAL | Other | 15 | 141.5667 | 2123.5 | 0.0062191 | 4.393e-05
2012-08-03 | 277580 | PPE16A | RURAL | Equipment failure | 270.5 | 145.5455 | 36497.5 | 0.10677 | 0.00079134
2012-08-03 | 277581 | CMY1 | RURAL | Other | 1 | 21 | 21 | 6.1435e-05 | 2.9255e-06
2012-08-03 | 277584 | EMD1 | RURAL | Other | 358.49 | 98 | 35132.02 | 0.10278 | 0.0010487
2012-08-03 | 277620 | CMD11A | RURAL | Equipment failure | 2246.99 | 107.4091 | 151153.31 | 0.44219 | 0.0065735
2012-08-03 | 277634 | GYM7A | RURAL | Other | 86 | 119 | 10234 | 0.029939 | 0.00025159
2012-08-03 | 277650 | TRP3 | RURAL | Equipment failure | 72.51 | 171 | 12399.21 | 0.036273 | 0.00021213
2012-08-03 | 277652 | AHD21 | URBAN | Equipment failure | 1292.41 | 152.2381 | 201078.64 | 0.20195 | 0.001298
2012-08-03 | 277721 | PWC3 | RURAL | Other | 12.5 | 81 | 1012.5 | 0.002962 | 3.6568e-05
2012-08-03 | 277722 | CMD11A | RURAL | Operational error | 12.83 | 45 | 577.35 | 0.001689 | 3.7534e-05
2012-08-03 | 277724 | CPK13 | RURAL | Other | 95.3611 | 112 | 10680.4432 | 0.031245 | 0.00027898
2012-08-03 | 277763 | ZMR10 | URBAN | Other | 29.37 | 84 | 2467.08 | 0.0024778 | 2.9497e-05
2012-08-03 | 277764 | BHL5A | URBAN | Other | 81.18 | 131 | 10634.58 | 0.010681 | 8.1532e-05
2012-08-03 | 277814 | NSW33A | URBAN | Animals | 44.5 | 88 | 3916 | 0.003933 | 4.4693e-05
2012-08-03 | 277815 | JBB2A | RURAL | Operational error | 11.5 | 88 | 1012 | 0.0029606 | 3.3643e-05
2012-08-03 | 278384 | MGL5 | URBAN | Equipment failure | 53 | 149 | 7897 | 0.0079312 | 5.323e-05
2012-08-04 | 277657 | EMD3 | RURAL | Other | 645 | 17 | 10965 | 0.032073 | 0.0018866
2012-08-04 | 277658 | SHW5A | URBAN | Equipment failure | 30.5 | 5 | 152.5 | 0.00015316 | 3.0632e-05
2012-08-04 | 277662 | PBH8 | URBAN | Equipment failure | 1467.82 | 2 | 2935.64 | 0.0029483 | 0.0014742
2012-08-04 | 277682 | GYM7A | RURAL | Other | 86 | 18 | 1548 | 0.0045279 | 0.00025155
2012-08-04 | 277684 | BRD5A | RURAL | Equipment failure | 37 | 43 | 1591 | 0.0046537 | 0.00010822
2012-08-04 | 277725 | MBG1 | RURAL | Equipment failure | 1 | 70 | 70 | 0.00020475 | 2.925e-06
2012-08-04 | 278385 | AHL6A | URBAN | Animals | 37.95 | 64 | 2428.8 | 0.0024393 | 3.8114e-05
2012-08-04 | 281142 | SHW5A | URBAN | Equipment failure | 4.575 | 97 | 443.775 | 0.00044569 | 4.5948e-06
2012-08-05 | 277692 | KRA1 | URBAN | Equipment failure | 611.17 | 44 | 26891.48 | 0.027007 | 0.0006138
2012-08-05 | 277694 | FDS4 | RURAL | Third party impacts | 419.34 | 67.4973 | 28186.42 | 0.082431 | 0.0012264
2012-08-05 | 277701 | CRM13A | URBAN | Equipment failure | 1812.33 | 36 | 65243.88 | 0.065525 | 0.0018201
2012-08-05 | 277701 | CRM13B | URBAN | Equipment failure | 23.84 | 36 | 858.24 | 0.00086194 | 2.3943e-05
2012-08-05 | 277701 | CRM5A | URBAN | Equipment failure | 1088.8 | 36 | 39196.8 | 0.039366 | 0.0010935
2012-08-05 | 277701 | CRM5B | URBAN | Equipment failure | 31.16 | 36 | 1121.76 | 0.0011266 | 3.1294e-05
2012-08-05 | 277715 | KRN12 | URBAN | Equipment failure | 1713.83 | 159.7778 | 261898.59 | 0.26303 | 0.0017212
2012-08-05 | 277723 | GYM8B | URBAN | Other | 65.08 | 71 | 4620.68 | 0.0046406 | 6.536e-05
2012-08-05 | 282885 | SHW10A | URBAN | Other | 20.79 | 62 | 1288.98 | 0.0012945 | 2.088e-05
2012-08-06 | 277726 | SPE12 | URBAN | Third party impacts | 702.49 | 42.28 | 32050.09 | 0.032188 | 0.00070551
2012-08-06 | 277785 | KSN2A | RURAL | Other | 23.5 | 126 | 2961 | 0.0086579 | 6.8714e-05
2012-08-06 | 277793 | EMP23A | URBAN | Third party impacts | 9.4 | 86 | 808.4 | 0.00081187 | 9.4404e-06
2012-08-06 | 277794 | CPB3 | URBAN | Animals | 1195.83 | 80.5 | 97074.4 | 0.097491 | 0.001201
2012-08-06 | 277795 | 484 | URBAN | Animals | 1 | 98 | 98 | 9.8421e-05 | 1.0043e-06
2012-08-06 | 277795 | BKD12A | URBAN | Animals | 1727 | 64 | 110528 | 0.111 | 0.0017344
2012-08-06 | 277795 | BKD13A | URBAN | Animals | 2051.5 | 64 | 131296 | 0.13186 | 0.0020603
2012-08-06 | 277795 | BKD15A | URBAN | Animals | 1177.17 | 64 | 75338.88 | 0.075662 | 0.0011822
2012-08-06 | 277795 | BKD16A | URBAN | Animals | 1599.83 | 64 | 102389.12 | 0.10283 | 0.0016067
2012-08-06 | 277795 | BKD2A | URBAN | Animals | 1 | 64 | 64 | 6.4275e-05 | 1.0043e-06
2012-08-06 | 277795 | BKD2B | URBAN | Animals | 1287.16 | 64 | 82378.24 | 0.082732 | 0.0012927
2012-08-06 | 277795 | BKD3A | URBAN | Animals | 1791 | 64 | 114624 | 0.11512 | 0.0017987
2012-08-06 | 277795 | BKD5B | RURAL | Animals | 1778.67 | 64 | 113834.88 | 0.33285 | 0.0052008
2012-08-06 | 277797 | RWD1 | RURAL | Other | 2.01 | 68 | 136.68 | 0.00039965 | 5.8772e-06
2012-08-06 | 277798 | PRG1 | RURAL | Other | 4.8 | 167 | 801.6 | 0.0023439 | 1.4035e-05
2012-08-06 | 277799 | CCY8A | RURAL | Equipment failure | 3.4 | 130 | 442 | 0.0012924 | 9.9416e-06
2012-08-06 | 277816 | NMC5A | RURAL | Other | 14.5 | 64 | 928 | 0.0027135 | 4.2398e-05
2012-08-06 | 277962 | CMD11A | RURAL | Operational error | 12.83 | 141 | 1809.03 | 0.0052896 | 3.7515e-05
2012-08-07 | 277801 | MTB15A | RURAL | Other | 7 | 2 | 14 | 4.0937e-05 | 2.0469e-05
2012-08-07 | 277812 | NRA15A | RURAL | Other | 10 | 65 | 650 | 0.0019007 | 2.9241e-05
2012-08-07 | 277813 | MRE1 | URBAN | Other | 35.64 | 50 | 1782 | 0.0017895 | 3.579e-05
2012-08-07 | 277817 | CPB3 | URBAN | Animals | 29.04 | 101 | 2933.04 | 0.0029454 | 2.9162e-05
2012-08-07 | 277818 | RCN3A | URBAN | Third party impacts | 5.76 | 40 | 230.4 | 0.00023137 | 5.7843e-06
2012-08-07 | 277825 | CCY3B | URBAN | Equipment failure | 40.0155 | 54 | 2160.837 | 0.0021699 | 4.0184e-05
2012-08-07 | 277827 | TMH16A | URBAN | Equipment failure | 14.43 | 84 | 1212.12 | 0.0012172 | 1.4491e-05
2012-08-07 | 277852 | CRY3A | RURAL | Other | 967.93 | 23.963 | 23959.25 | 0.070059 | 0.0028303
2012-08-07 | 277853 | RIS4 | RURAL | Equipment failure | 11 | 140 | 1540 | 0.0045031 | 3.2165e-05
2012-08-07 | 277854 | MGP13A | RURAL | Animals | 13.86 | 75 | 1039.5 | 0.0030396 | 4.0528e-05
2012-08-07 | 277963 | LBH3A | RURAL | Other | 7 | 102 | 714 | 0.0020878 | 2.0469e-05
2012-08-07 | 278439 | CBW7 | RURAL | Animals | 17.16 | 51 | 875.16 | 0.002559 | 5.0177e-05
2012-08-07 | 278440 | ZMR7A | URBAN | Other | 82 | 190 | 15580 | 0.015646 | 8.2346e-05
2012-08-08 | 277857 | MFD8A | RURAL | Animals | 2126.16 | 67.24 | 141954.06 | 0.4151 | 0.0062172
2012-08-08 | 277864 | MGP1 | RURAL | Other | 579 | 5 | 2895 | 0.0084654 | 0.0016931
2012-08-08 | 277881 | GTN5B | RURAL | Third party impacts | 156.65 | 137.6512 | 21730.8 | 0.063544 | 0.00045807
2012-08-08 | 277908 | CMV12A | URBAN | Other | 18.4 | 63 | 1159.2 | 0.001164 | 1.8476e-05
2012-08-08 | 277921 | CCY25A | URBAN | Other | 10.09 | 42.5 | 857.65 | 0.0008612 | 1.0132e-05
2012-08-08 | 277946 | GYM7A | RURAL | Other | 86 | 24 | 2064 | 0.0060355 | 0.00025148
2012-08-08 | 277964 | MLY1 | RURAL | Animals | 6 | 142 | 852 | 0.0024914 | 1.7545e-05
2012-08-08 | 278018 | SGT7 | URBAN | Other | 1101.32 | 5.3333 | 5760.96 | 0.0057848 | 0.0011059
2012-08-08 | 278192 | CVL7A | RURAL | Other | 64.17 | 154 | 9882.18 | 0.028897 | 0.00018764
2012-08-08 | 278193 | LHM3 | URBAN | Animals | 30.36 | 85 | 2580.6 | 0.0025913 | 3.0486e-05
2012-08-08 | 278194 | BTA1A | URBAN | Other | 50 | 112.2667 | 5613.3333 | 0.0056366 | 5.0207e-05
2012-08-08 | 278382 | GAP9A | URBAN | Equipment failure | 36 | 53 | 1908 | 0.0019159 | 3.6149e-05
2012-08-08 | 278438 | SGT7 | URBAN | Animals | 123.83 | 53 | 6562.99 | 0.0065902 | 0.00012434
2012-08-09 | 277960 | MTB17A | RURAL | Third party impacts | 1 | 197 | 197 | 0.00057606 | 2.9241e-06
2012-08-09 | 278015 | ARL12A | URBAN | Equipment failure | 1349.49 | 95.5 | 257752.59 | 0.2588 | 0.001355
2012-08-09 | 278015 | ARL12B | URBAN | Equipment failure | 540 | 95.5 | 103140 | 0.10356 | 0.0005422
2012-08-09 | 278015 | ARL3A | URBAN | Equipment failure | 336 | 117.75 | 79104 | 0.079426 | 0.00033737
2012-08-09 | 278015 | ARLSNT3 | URBAN | Equipment failure | 5 | 96 | 480 | 0.00048195 | 5.0203e-06
2012-08-09 | 278017 | RLB13B | RURAL | Equipment failure | 1896.47 | 43.2949 | 102025.39 | 0.29834 | 0.0055455
2012-08-09 | 278136 | TWT3A | RURAL | Equipment failure | 11 | 120 | 1320 | 0.0038599 | 3.2166e-05
2012-08-09 | 278381 | INA5A | URBAN | Other | 11 | 116 | 1276 | 0.0012812 | 1.1045e-05
2012-08-09 | 278773 | NRA5A | RURAL | Animals | 29 | 93 | 2697 | 0.0078864 | 8.48e-05
2012-08-10 | 278022 | SBH6 | URBAN | Equipment failure | 2076.45 | 19 | 39452.55 | 0.039613 | 0.0020849
2012-08-10 | 278024 | MRK3 | URBAN | Equipment failure | 93.6 | 70 | 6552 | 0.0065786 | 9.398e-05
2012-08-10 | 278040 | NRG14A | RURAL | Other | 339 | 59 | 20001 | 0.058475 | 0.00099109
2012-08-10 | 278043 | JBB1B | RURAL | Equipment failure | 0.5 | 183 | 91.5 | 0.00026751 | 1.4618e-06
2012-08-10 | 278048 | GYM2A | RURAL | Other | 471.5 | 129.7753 | 55318 | 0.16173 | 0.0013785
2012-08-10 | 278061 | WMD13A | RURAL | Weather | 988.34 | 63.6111 | 33831.74 | 0.09891 | 0.0028895
2012-08-10 | 278082 | 404 | URBAN | Animals | 1 | 51 | 51 | 5.1207e-05 | 1.0041e-06
2012-08-10 | 278082 | IPL1 | RURAL | Animals | 731.97 | 36.214 | 28300.47 | 0.082739 | 0.00214
2012-08-10 | 278082 | IPL2 | RURAL | Animals | 331.48 | 51 | 16905.48 | 0.049425 | 0.00096911
2012-08-10 | 278082 | IPL3 | RURAL | Animals | 496.98 | 51 | 25345.98 | 0.074101 | 0.001453
2012-08-10 | 278083 | TWT11A | RURAL | Operational error | 1426.99 | 20 | 28539.8 | 0.083438 | 0.0041719
2012-08-10 | 278083 | TWT5B | RURAL | Operational error | 1143.25 | 19 | 21721.75 | 0.063505 | 0.0033424
2012-08-10 | 278084 | DBY6 | URBAN | Animals | 2285.32 | 33.4483 | 120899.94 | 0.12139 | 0.0022946
2012-08-10 | 278137 | GYM7A | RURAL | Other | 7.92 | 132 | 1045.44 | 0.0030564 | 2.3155e-05
2012-08-10 | 278138 | MLY3 | RURAL | Equipment failure | 6 | 109 | 654 | 0.001912 | 1.7541e-05
2012-08-10 | 278139 | WMD13A | RURAL | Equipment failure | 21 | 467 | 9807 | 0.028672 | 6.1395e-05
2012-08-10 | 278140 | PWC6 | RURAL | Equipment failure | 14.5 | 67 | 971.5 | 0.0028403 | 4.2392e-05
2012-08-10 | 278141 | CLD17A | URBAN | Animals | 151.67 | 61 | 9251.87 | 0.0092894 | 0.00015229
2012-08-10 | 278201 | NRG14A | RURAL | Animals | 15.84 | 80 | 1267.2 | 0.0037048 | 4.6309e-05
2012-08-10 | 278203 | PBH2B | URBAN | Equipment failure | 23.4 | 134 | 3135.6 | 0.0031483 | 2.3495e-05
2012-08-10 | 278437 | KLG17A | URBAN | Animals | 88.44 | 44 | 3891.36 | 0.0039072 | 8.8799e-05
2012-08-11 | 278087 | WMR3 | RURAL | Vegetation | 13 | 10 | 130 | 0.00037999 | 3.7999e-05
2012-08-11 | 278089 | CPR7 | URBAN | Equipment failure | 1613.91 | 97.9333 | 128986.61 | 0.12951 | 0.0016204
2012-08-11 | 278142 | CLD11 | RURAL | Equipment failure | 9 | 55 | 495 | 0.0014469 | 2.6307e-05
2012-08-11 | 278195 | HWD2B | RURAL | Other | 10 | 1523 | 15230 | 0.044518 | 2.923e-05
2012-08-12 | 278111 | MGP4 | RURAL | Vegetation | 591.49 | 68.9429 | 38470.45 | 0.11243 | 0.0017286
2012-08-13 | 278135 | LTN3 | URBAN | Other | 336.84 | 90 | 30315.6 | 0.030438 | 0.0003382
2012-08-13 | 278143 | MGP13A | RURAL | Other | 387.99 | 17 | 6595.83 | 0.019273 | 0.0011337
2012-08-13 | 278160 | DRD2A | RURAL | Third party impacts | 2 | 135 | 270 | 0.00078893 | 5.8439e-06
2012-08-13 | 278190 | SHW4 | URBAN | Animals | 486.33 | 40 | 19453.2 | 0.019532 | 0.00048829
2012-08-13 | 278196 | BLH12A | RURAL | Other | 13 | 104 | 1352 | 0.0039505 | 3.7985e-05
2012-08-13 | 278197 | JBB2A | RURAL | Other | 10 | 109 | 1090 | 0.0031849 | 2.9219e-05
2012-08-13 | 278436 | KCY2 | RURAL | Vegetation | 16 | 114 | 1824 | 0.0053296 | 4.6751e-05
2012-08-14 | 278200 | EMD1 | RURAL | Other | 358.49 | 23 | 8245.27 | 0.024088 | 0.0010473
2012-08-14 | 278202 | SPC2B | RURAL | Third party impacts | 87.98 | 254 | 22346.92 | 0.065285 | 0.00025703
2012-08-14 | 278284 | LWD1 | RURAL | Other | 0.8 | 101 | 80.8 | 0.00023605 | 2.3371e-06
2012-08-15 | 278301 | MTB15A | RURAL | Other | 3 | 31 | 93 | 0.00027165 | 8.7628e-06
2012-08-15 | 278309 | PWC4 | RURAL | Vegetation | 18 | 199 | 3582 | 0.010463 | 5.2577e-05
2012-08-15 | 278435 | ACR5 | RURAL | Equipment failure | 3 | 126 | 378 | 0.0011041 | 8.7628e-06
2012-08-15 | 278464 | RCN10A | URBAN | Animals | 32 | 97 | 3104 | 0.0031165 | 3.2129e-05
2012-08-15 | 278465 | HPE16A | URBAN | Vegetation | 18.5922 | 66 | 1227.0852 | 0.001232 | 1.8667e-05
2012-08-16 | 278320 | QPT21 | URBAN | Equipment failure | 285.5 | 26 | 11642.69 | 0.011689 | 0.00028664
2012-08-16 | 278360 | APMT0 | URBAN | Animals | 1 | 54 | 54 | 5.4216e-05 | 1.004e-06
2012-08-16 | 278360 | APMTR4 | URBAN | Animals | 1 | 54 | 54 | 5.4216e-05 | 1.004e-06
2012-08-16 | 278379 | TWG17 | URBAN | Other | 38.61 | 60 | 2316.6 | 0.0023259 | 3.8764e-05
2012-08-16 | 278424 | BHD31A | URBAN | Other | 93.5 | 19 | 1776.5 | 0.0017836 | 9.3874e-05
2012-08-16 | 278425 | CPC2A | RURAL | Equipment failure | 1511.5 | 41.3333 | 35282.5 | 0.10305 | 0.0044144
2012-08-16 | 278425 | CPC2B | URBAN | Equipment failure | 1786.99 | 56.5625 | 48521.74 | 0.048716 | 0.0017941
2012-08-16 | 278426 | KBR1A | RURAL | Third party impacts | 2 | 504 | 1008 | 0.0029439 | 5.8411e-06
2012-08-16 | 278433 | DBY9 | URBAN | Animals | 45.21 | 53 | 2396.13 | 0.0024057 | 4.5391e-05
2012-08-16 | 278434 | TPT5 | RURAL | Other | 10 | 149 | 1490 | 0.0043517 | 2.9206e-05
2012-08-16 | 278466 | CVL5A | RURAL | Other | 21.78 | 70 | 1524.6 | 0.0044527 | 6.361e-05
2012-08-16 | 278467 | TBV4 | RURAL | Animals | 13.2 | 120 | 1584 | 0.0046262 | 3.8552e-05
2012-08-16 | 282664 | YDA1B | RURAL | Other | 18.8 | 82.5 | 1551 | 0.0045298 | 5.4907e-05
2012-08-16 | 282665 | PWC3 | RURAL | Other | 4.8 | 144.65 | 694.32 | 0.0020278 | 1.4019e-05
2012-08-17 | 278431 | TMH5A | URBAN | Other | 1084.33 | 16 | 17349.28 | 0.017418 | 0.0010886
2012-08-17 | 278461 | WHO1 | RURAL | Other | 7.5 | 17 | 127.5 | 0.00037233 | 2.1902e-05
2012-08-17 | 278463 | NRG9 | RURAL | Other | 20.262 | 10 | 202.62 | 0.0005917 | 5.917e-05
2012-08-17 | 278498 | PGN1B | RURAL | Equipment failure | 19.92 | 254 | 5059.68 | 0.014775 | 5.8171e-05
2012-08-17 | 278977 | AHL12A | URBAN | Animals | 38.61 | 88 | 3397.68 | 0.0034112 | 3.8763e-05
2012-08-18 | 278510 | LLY4 | RURAL | Third party impacts | 25.08 | 20 | 501.6 | 0.0014645 | 7.3227e-05
2012-08-18 | 278516 | WHO2 | RURAL | Other | 297.5 | 2 | 595 | 0.0017372 | 0.00086862
2012-08-18 | 278517 | MTB13A | RURAL | Vegetation | 23 | 82 | 1886 | 0.0055066 | 6.7153e-05
2012-08-18 | 278541 | SMF3A | RURAL | Other | 2.64 | 66 | 174.24 | 0.00050873 | 7.7081e-06
2012-08-18 | 278542 | UPC1 | RURAL | Vegetation | 13 | 141 | 1833 | 0.0053518 | 3.7956e-05
2012-08-19 | 278518 | RST16A | URBAN | Other | 653.5 | 101 | 60248 | 0.060487 | 0.00065609
2012-08-19 | 278526 | BBH8A | URBAN | Equipment failure | 41.58 | 35 | 1455.3 | 0.0014611 | 4.1745e-05
2012-08-19 | 278538 | HTN24B | URBAN | Other | 1 | 102 | 102 | 0.0001024 | 1.004e-06
2012-08-19 | 278543 | SPO60A | URBAN | Equipment failure | 28.545 | 143 | 4081.935 | 0.0040981 | 2.8658e-05
2012-08-20 | 278562 | JBB16A | RURAL | Equipment failure | 14 | 86 | 1204 | 0.0035141 | 4.0862e-05
2012-08-20 | 278564 | BVL10A | URBAN | Third party impacts | 149.064 | 103 | 15353.592 | 0.015414 | 0.00014965
2012-08-20 | 278569 | MHL1B | RURAL | Equipment failure | 897.5655 | 65 | 58341.7575 | 0.17028 | 0.0026197
2012-08-20 | 278571 | BLH9B | URBAN | Other | 81.6 | 11 | 897.6 | 0.00090116 | 8.1923e-05
2012-08-20 | 278581 | WNM2A | URBAN | Equipment failure | 3 | 49 | 147 | 0.00014758 | 3.0119e-06
2012-08-20 | 278584 | KSN2A | RURAL | Equipment failure | 1649.83 | 52.5098 | 128773.6924 | 0.37585 | 0.0048154
2012-08-20 | 278585 | AHD15A | URBAN | Equipment failure | 850.66 | 49 | 41682.34 | 0.041848 | 0.00085403
2012-08-20 | 278585 | AHD15B | URBAN | Equipment failure | 913.08 | 120.1875 | 140801.55 | 0.14136 | 0.0009167
2012-08-21 | 278601 | BRD11A | RURAL | Operational error | 7 | 10 | 70 | 0.00020427 | 2.0427e-05
2012-08-21 | 278606 | KWA4A | URBAN | Equipment failure | 10.64 | 40 | 425.6 | 0.00042729 | 1.0682e-05
2012-08-21 | 278610 | AGE8 | URBAN | Vegetation | 937.33 | 42 | 39367.86 | 0.039524 | 0.00094105
2012-08-21 | 282880 | KRN12 | URBAN | Other | 55.77 | 92 | 5130.84 | 0.0051512 | 5.5991e-05
2012-08-21 | 282884 | NMK7 | URBAN | Other | 39.93 | 95 | 3793.35 | 0.0038084 | 4.0088e-05
2012-08-22 | 278660 | CMV11A | URBAN | Other | 1401.84 | 7 | 9812.88 | 0.0098518 | 0.0014074
2012-08-22 | 278660 | CMV12A | URBAN | Other | 96 | 7 | 672 | 0.00067466 | 9.6381e-05
2012-08-22 | 278675 | RWD1 | RURAL | Equipment failure | 66 | 37 | 2442 | 0.007125 | 0.00019257
2012-08-22 | 278690 | CMV12A | URBAN | Other | 96 | 30 | 2880 | 0.0028914 | 9.6381e-05
2012-08-22 | 278691 | CMV11A | URBAN | Equipment failure | 1401.84 | 2 | 2803.68 | 0.0028148 | 0.0014074
2012-08-22 | 278691 | CMV12A | URBAN | Equipment failure | 0 | 2 | 0 | 0 | 0
2012-08-22 | 278693 | KBR1A | RURAL | Animals | 4.69 | 61 | 286.09 | 0.00083473 | 1.3684e-05
2012-08-22 | 278694 | KBR2A | RURAL | Third party impacts | 0.67 | 80 | 53.6 | 0.00015639 | 1.9549e-06
2012-08-23 | 278695 | BMT1 | RURAL | Third party impacts | 1489.5 | 42 | 62559 | 0.18249 | 0.0043451
2012-08-23 | 278697 | NBR6 | RURAL | Vegetation | 1772.72 | 26.1959 | 47272.92 | 0.1379 | 0.0051713
2012-08-23 | 278721 | CBT13A | URBAN | Third party impacts | 32.5825 | 47 | 1531.3775 | 0.0015375 | 3.2712e-05
2012-08-23 | 278740 | IPL3 | RURAL | Equipment failure | 24 | 235 | 5640 | 0.016453 | 7.0011e-05
2012-08-23 | 278755 | LTN3 | URBAN | Other | 1577.49 | 16 | 25239.84 | 0.02534 | 0.0015838
2012-08-23 | 278759 | IBL2 | RURAL | Third party impacts | 101 | 404.8537 | 40764 | 0.11891 | 0.00029463
2012-08-23 | 278881 | PWC4 | RURAL | Animals | 3 | 214 | 642 | 0.0018728 | 8.7514e-06
2012-08-23 | 278976 | MLS15A | URBAN | Animals | 147 | 92 | 13524 | 0.013578 | 0.00014758
2012-08-23 | 282881 | KRN11 | URBAN | Other | 69.3 | 145 | 10048.5 | 0.010088 | 6.9575e-05
2012-08-24 | 278764 | BBSRDL8 | RURAL | Equipment failure | 12.5 | 53 | 662.5 | 0.0019322 | 3.6456e-05
2012-08-24 | 278781 | RIS1 | RURAL | Vegetation | 709.5 | 137.36 | 107099 | 0.31235 | 0.0020692
2012-08-24 | 278792 | MLS15A | URBAN | Equipment failure | 73.5 | 157 | 11539.5 | 0.011586 | 7.3793e-05
2012-08-24 | 278794 | BTA5A | RURAL | Equipment failure | 15 | 70 | 1050 | 0.0030623 | 4.3747e-05
2012-08-24 | 278823 | CMV12A | URBAN | Equipment failure | 28.5 | 45 | 1282.5 | 0.0012876 | 2.8614e-05
2012-08-24 | 278826 | LTA4B | URBAN | Vegetation | 4 | 97 | 388 | 0.00038955 | 4.016e-06
2012-08-24 | 278831 | SIS2 | RURAL | Vegetation | 109 | 20 | 2180 | 0.0063579 | 0.0003179
2012-08-24 | 278882 | EMD3 | RURAL | Animals | 39.83 | 73 | 2907.59 | 0.0084799 | 0.00011616
2012-08-25 | 278829 | LGL15A | URBAN | Animals | 958.99 | 17 | 16302.83 | 0.016368 | 0.00096282
2012-08-25 | 278836 | GGR3 | RURAL | Animals | 86.99 | 36.0482 | 6470.34 | 0.018867 | 0.00025365
2012-08-25 | 278872 | RWD1 | RURAL | Animals | 1 | 211 | 211 | 0.00061525 | 2.9159e-06
2012-08-25 | 278883 | BMT2 | RURAL | Vegetation | 7 | 56.3833 | 394.6833 | 0.0011509 | 2.0411e-05
2012-08-25 | 278905 | BDL4 | URBAN | Equipment failure | 59.6178 | 126 | 7511.8428 | 0.0075419 | 5.9856e-05
2012-08-26 | 278848 | NDH7 | URBAN | Animals | 1546 | 58.625 | 84195 | 0.084538 | 0.0015523
2012-08-26 | 278851 | BDT4 | RURAL | Equipment failure | 34 | 241 | 8194 | 0.023883 | 9.91e-05
2012-08-26 | 278865 | CBW6 | RURAL | Equipment failure | 15.25 | 20 | 305 | 0.00088899 | 4.4449e-05
2012-08-26 | 278902 | CPB2 | URBAN | Other | 40.5 | 51 | 2065.5 | 0.0020739 | 4.0665e-05
2012-08-27 | 278870 | TBV3 | RURAL | Other | 375 | 66 | 24750 | 0.072111 | 0.0010926
2012-08-27 | 278899 | HPK5A | URBAN | Equipment failure | 40.5 | 71 | 2875.5 | 0.0028875 | 4.0668e-05
2012-08-27 | 278903 | HPE13A | URBAN | Other | 46.695 | 53 | 2474.835 | 0.0024851 | 4.6889e-05
2012-08-27 | 278904 | HPK5A | URBAN | Equipment failure | 26.73 | 112 | 2993.76 | 0.0030062 | 2.6841e-05
2012-08-27 | 278906 | BDL4 | URBAN | Equipment failure | 59.6178 | 143 | 8525.3454 | 0.0085608 | 5.9866e-05
2012-08-28 | 278921 | RIS2 | URBAN | Equipment failure | 649.66 | 48 | 31183.68 | 0.031316 | 0.00065242
2012-08-28 | 278948 | BHL2A | URBAN | Equipment failure | 21 | 95 | 1995 | 0.0020035 | 2.1089e-05
2012-08-28 | 279017 | SRD4A | URBAN | Third party impacts | 34 | 60 | 2040 | 0.0020487 | 3.4144e-05
2012-08-28 | 279018 | EMP23A | URBAN | Third party impacts | 94 | 9 | 846 | 0.00084959 | 9.4399e-05
2012-08-29 | 279016 | MGP13A | RURAL | Other | 12 | 142 | 1704 | 0.0049609 | 3.4936e-05
2012-08-29 | 279020 | EZRRWD4 | RURAL | Equipment failure | 15 | 165 | 2475 | 0.0072055 | 4.3669e-05
2012-08-29 | 279021 | LRE6A | RURAL | Equipment failure | 4 | 169 | 890 | 0.0025911 | 1.1645e-05
2012-08-29 | 279023 | NGE4A | URBAN | Third party impacts | 169 | 87.85 | 15257 | 0.015323 | 0.00016973
2012-08-29 | 279023 | NGE4B | URBAN | Third party impacts | 732.16 | 68.6563 | 51278.2 | 0.0515 | 0.00073533
2012-08-29 | 279026 | KMR17B | URBAN | Equipment failure | 20.199 | 76 | 1535.124 | 0.0015418 | 2.0286e-05
2012-08-29 | 279049 | SFD4 | URBAN | Other | 62.5 | 3 | 187.5 | 0.00018831 | 6.277e-05
2012-08-29 | 279050 | TRP1 | RURAL | Equipment failure | 7 | 79 | 553 | 0.0016099 | 2.0379e-05
2012-08-29 | 279057 | AMR1 | RURAL | Equipment failure | 12 | 119 | 1428 | 0.0041573 | 3.4936e-05
2012-08-29 | 279059 | MCW4 | RURAL | Equipment failure | 13.45 | 486 | 6536.7 | 0.01903 | 3.9157e-05
2012-08-29 | 279060 | BGY17A | URBAN | Other | 1875.51 | 17 | 31883.67 | 0.032022 | 0.0018836
2012-08-29 | 279080 | BVL13A | URBAN | Third party impacts | 41.91 | 54 | 2263.14 | 0.0022729 | 4.2091e-05
2012-08-30 | 279062 | NVL8A | URBAN | Animals | 1 | 122 | 122 | 0.00012254 | 1.0044e-06
2012-08-30 | 279062 | NVL8B | URBAN | Animals | 1933.5 | 157.913 | 323845 | 0.32527 | 0.001942
2012-08-30 | 279063 | CLD20A | RURAL | Equipment failure | 1427.5 | 141.2105 | 194936.5 | 0.56729 | 0.0041542
2012-08-30 | 279082 | ACR2B | URBAN | Other | 101 | 50 | 5050 | 0.0050723 | 0.00010145
2012-08-30 | 279082 | ACR3A | URBAN | Other | 56 | 50 | 2800 | 0.0028123 | 5.6247e-05
2012-08-30 | 279096 | INA9A | URBAN | Other | 1266.99 | 90.56 | 117349.2 | 0.11787 | 0.0012726
2012-08-30 | 279132 | KBN1B | RURAL | Equipment failure | 8.99 | 140 | 1258.6 | 0.0036627 | 2.6162e-05
2012-08-30 | 279133 | PPE16A | RURAL | Equipment failure | 7.5 | 110 | 825 | 0.0024009 | 2.1826e-05
2012-08-30 | 279134 | MGP13A | RURAL | Equipment failure | 1 | 281 | 281 | 0.00081775 | 2.9101e-06
2012-08-30 | 279135 | LTN8 | RURAL | Equipment failure | 598.83 | 4 | 2395.32 | 0.0069707 | 0.0017427
2012-08-30 | 279135 | LTN9 | URBAN | Equipment failure | 84 | 4.2857 | 367 | 0.00036862 | 8.437e-05
2012-08-30 | 279136 | MLY3 | RURAL | Other | 515 | 79.0638 | 39402 | 0.11467 | 0.0014987
2012-08-30 | 279142 | TMH16A | URBAN | Equipment failure | 56 | 87 | 4872 | 0.0048935 | 5.6247e-05
2012-08-30 | 279143 | BMT2 | RURAL | Weather | 7 | 106.9833 | 748.8833 | 0.0021794 | 2.0371e-05
2012-08-31 | 279139 | SHW5A | URBAN | Animals | 88.83 | 160 | 14212.8 | 0.014277 | 8.9229e-05
2012-08-31 | 279140 | MLY3 | RURAL | Vegetation | 515 | 3 | 1545 | 0.0044944 | 0.0014981
2012-08-31 | 279141 | MLY3 | RURAL | Vegetation | 515 | 27 | 13905 | 0.040449 | 0.0014981
2012-08-31 | 279166 | BDB4A | RURAL | Equipment failure | 4 | 104 | 416 | 0.0012101 | 1.1636e-05
2012-08-31 | 279168 | MLT15B | URBAN | Other | 11.487 | 366 | 4204.242 | 0.0042231 | 1.1539e-05
2012-08-31 | 279173 | AMR1 | RURAL | Equipment failure | 109 | 91 | 9919 | 0.028854 | 0.00031708
2012-08-31 | 279222 | TGW1 | RURAL | Third party impacts | 2.68 | 116 | 310.88 | 0.00090434 | 7.796e-06
2012-08-31 | 279223 | BLB8A | URBAN | Equipment failure | 84 | 163 | 13692 | 0.013754 | 8.4377e-05
2012-08-31 | 279224 | CHL11A | RURAL | Equipment failure | 33.5 | 152 | 5092 | 0.014812 | 9.745e-05
2012-08-31 | 279225 | HPK8A | URBAN | Animals | 61.2678 | 71 | 4350.0138 | 0.0043696 | 6.1543e-05
2012-08-31 | 281143 | GLY6 | URBAN | Equipment failure | 16.2 | 146 | 2365.2 | 0.0023758 | 1.6273e-05
2012-09-01 | 279205 | CPC2A | RURAL | Equipment failure | 1511.5 | 45.3077 | 67094.5 | 0.19509 | 0.0043951
2012-09-01 | 279205 | CPC2B | URBAN | Equipment failure | 1786.99 | 16 | 28591.84 | 0.028723 | 0.0017952
2012-09-02 | 279195 | GYM5B | RURAL | Weather | 69.5 | 86 | 5977 | 0.017372 | 0.000202
2012-09-02 | 279204 | GBN4 | RURAL | Other | 35 | 114 | 3995 | 0.011612 | 0.00010173
2012-09-02 | 279226 | RLB13B | RURAL | Equipment failure | 25.08 | 90 | 2257.2 | 0.0065606 | 7.2896e-05
2012-09-02 | 279227 | AHD19 | URBAN | Other | 112.83 | 82 | 9252.06 | 0.0092954 | 0.00011336
2012-09-03 | 279240 | KCY4 | RURAL | Other | 5.5 | 13 | 71.5 | 0.00020773 | 1.5979e-05
2012-09-03 | 279275 | BRT6 | URBAN | Animals | 1131.5 | 68 | 76942 | 0.07731 | 0.0011369
2012-09-03 | 279277 | GBN4 | RURAL | Equipment failure | 35 | 128 | 4480 | 0.013016 | 0.00010169
2012-09-03 | 279278 | GYM7A | RURAL | Other | 86 | 16 | 1376 | 0.0039977 | 0.00024986
2012-09-03 | 279279 | MBG1 | RURAL | Equipment failure | 5 | 150 | 750 | 0.002179 | 1.4527e-05
2012-09-03 | 279282 | MLY6 | RURAL | Other | 1.98 | 278 | 550.44 | 0.0015992 | 5.7525e-06
2012-09-03 | 279283 | PWC3 | RURAL | Operational error | 12.5 | 142 | 1775 | 0.0051569 | 3.6316e-05
2012-09-03 | 279284 | AHD19 | URBAN | Animals | 112.83 | 100 | 11283 | 0.011337 | 0.00011337
2012-09-03 | 279285 | AHD5 | URBAN | Equipment failure | 94.545 | 109 | 10305.405 | 0.010355 | 9.4997e-05
2012-09-03 | 279288 | RBY7A | URBAN | Animals | 0.66 | 47 | 31.02 | 3.1168e-05 | 6.6315e-07
2012-09-03 | 279290 | CVL5A | RURAL | Animals | 21.78 | 81 | 1764.18 | 0.0051255 | 6.3278e-05
2012-09-03 | 279291 | NMC16A | RURAL | Animals | 18.48 | 110 | 2032.8 | 0.0059059 | 5.369e-05
2012-09-04 | 279281 | BNH1B | RURAL | Animals | 163.98 | 101.4568 | 38619.68 | 0.11216 | 0.00047622
2012-09-04 | 279286 | CRY2A | RURAL | Animals | 9.57 | 83 | 794.31 | 0.0023068 | 2.7792e-05
2012-09-04 | 279360 | HPK10 | URBAN | Equipment failure | 63.36 | 25 | 1584 | 0.0015917 | 6.3669e-05
2012-09-04 | 279361 | NRG16A | RURAL | Vegetation | 8.5 | 211 | 1793.5 | 0.0052085 | 2.4685e-05
2012-09-04 | 279486 | CBT12A | RURAL | Equipment failure | 9.24 | 63 | 582.12 | 0.0016905 | 2.6834e-05
2012-09-04 | 281138 | TRG10B | URBAN | Animals | 0.66 | 31 | 20.46 | 2.056e-05 | 6.6322e-07
2012-09-04 | 281141 | TRG5 | URBAN | Equipment failure | 35.25 | 112 | 3948 | 0.0039673 | 3.5422e-05
2012-09-05 | 279351 | CLD28A | RURAL | Equipment failure | 89.56 | 249.8182 | 21597.92 | 0.062697 | 0.00025998
2012-09-05 | 279362 | GAP4A | URBAN | Other | 49.75 | 14 | 696.5 | 0.00069996 | 4.9997e-05
2012-09-05 | 279373 | LBH3A | RURAL | Equipment failure | 11 | 138.5 | 1521.625 | 0.0044171 | 3.1932e-05
2012-09-05 | 279391 | CBT8A | RURAL | Other | 1407.51 | 16 | 22520.16 | 0.065374 | 0.0040859
2012-09-05 | 279406 | NBR6 | RURAL | Other | 6.5 | 55 | 357.5 | 0.0010378 | 1.8869e-05
2012-09-05 | 280022 | NSW22B | URBAN | Equipment failure | 27.67 | 92 | 2545.64 | 0.0025583 | 2.7808e-05
2012-09-05 | 281140 | ENG2 | URBAN | Animals | 76.5 | 65 | 4972.5 | 0.0049972 | 7.688e-05
2012-09-06 | 279403 | HIS5A | URBAN | Other | 13 | 113 | 1469 | 0.0014764 | 1.3066e-05
2012-09-06 | 279440 | BKD16A | URBAN | Equipment failure | 1597.83 | 4 | 6391.32 | 0.0064237 | 0.0016059
2012-09-06 | 279452 | CLM9 | URBAN | Third party impacts | 15.5 | 29 | 449.5 | 0.00045178 | 1.5578e-05
2012-09-06 | 279478 | CCY13A | URBAN | Equipment failure | 6.4 | 549 | 3513.6 | 0.0035314 | 6.4324e-06
2012-09-06 | 279484 | WSE3A | RURAL | Equipment failure | 3 | 159 | 477 | 0.0013841 | 8.7051e-06
2012-09-06 | 279485 | BRD13A | URBAN | Other | 32 | 142 | 4544 | 0.004567 | 3.2162e-05
2012-09-06 | 280023 | WRG1A | URBAN | Equipment failure | 173 | 66 | 11418 | 0.011476 | 0.00017388
2012-09-07 | 279481 | PWC4 | RURAL | Vegetation | 4.2 | 126 | 529.2 | 0.0015349 | 1.2182e-05
2012-09-07 | 279490 | BLH13B | RURAL | Animals | 11 | 68 | 748 | 0.0021696 | 3.1905e-05
2012-09-07 | 279522 | MTG16A | URBAN | Equipment failure | 5.625 | 57 | 320.625 | 0.00032228 | 5.654e-06
2012-09-07 | 279523 | KSN1 | URBAN | Third party impacts | 1 | 269.5 | 179.8 | 0.00018073 | 1.0052e-06
2012-09-07 | 279524 | DRA6 | URBAN | Animals | 813.32 | 56 | 45545.92 | 0.045781 | 0.00081751
2012-09-07 | 279527 | BHD35A | RURAL | Vegetation | 153 | 171.8837 | 30628.5 | 0.088838 | 0.00044378
2012-09-07 | 279586 | MLY6 | RURAL | Vegetation | 15.67 | 81 | 1269.27 | 0.0036815 | 4.5451e-05
2012-09-07 | 279587 | PWC4 | RURAL | Animals | 23.5 | 84 | 1974 | 0.0057256 | 6.8162e-05
2012-09-07 | 280025 | BLH13B | RURAL | Animals | 1 | 128 | 128 | 0.00037126 | 2.9005e-06
2012-09-08 | 279528 | TGP6A | URBAN | Equipment failure | 44.75 | 35 | 1566.25 | 0.0015744 | 4.4984e-05
2012-09-08 | 279536 | BDA12B | URBAN | Vegetation | 111.83 | 181 | 20241.23 | 0.020347 | 0.00011242
2012-09-08 | 279588 | WMD6A | URBAN | Animals | 22 | 63 | 1386 | 0.0013933 | 2.2115e-05
2012-09-08 | 281145 | NMK17A | URBAN | Other | 21.8 | 95 | 2071 | 0.0020818 | 2.1914e-05
2012-09-09 | 279570 | PWC4 | RURAL | Equipment failure | 7 | 10 | 70 | 0.00020288 | 2.0288e-05
2012-09-09 | 279589 | WMD14A | RURAL | Animals | 190 | 61 | 11590 | 0.033591 | 0.00055067
2012-09-09 | 279600 | PWC3 | RURAL | Animals | 28 | 69 | 1932 | 0.0055995 | 8.1152e-05
2012-09-09 | 280026 | HPE12A | URBAN | Animals | 70.95 | 100 | 7095 | 0.0071327 | 7.1327e-05
2012-09-09 | 281146 | AHL6A | URBAN | Other | 66 | 97 | 6402 | 0.006436 | 6.6351e-05
2012-09-10 | 279582 | NDH6 | URBAN | Animals | 1860.01 | 16 | 29760.16 | 0.029921 | 0.0018701
2012-09-10 | 279583 | WRD22B | URBAN | Animals | 753.16 | 92 | 105360.06 | 0.10593 | 0.00075723
2012-09-10 | 279585 | CPL2A | URBAN | Other | 295.17 | 16 | 4722.72 | 0.0047482 | 0.00029676
2012-09-10 | 279640 | ACR2B | URBAN | Other | 1.3 | 145 | 188.5 | 0.00018952 | 1.307e-06
2012-09-10 | 279642 | MHL12A | RURAL | Other | 20 | 313 | 6260 | 0.018136 | 5.7944e-05
2012-09-10 | 279643 | NSW8A | URBAN | Other | 1801.5 | 93.36 | 154252.5 | 0.15509 | 0.0018112
2012-09-10 | 279644 | FDS4 | RURAL | Equipment failure | 4.5 | 204 | 918 | 0.0026596 | 1.3037e-05
2012-09-10 | 279645 | NBR6 | RURAL | Third party impacts | 27.5 | 25 | 687.5 | 0.0019918 | 7.9673e-05
2012-09-10 | 279649 | CLM5 | URBAN | Equipment failure | 365.5 | 46 | 16813 | 0.016904 | 0.00036747
2012-09-10 | 279682 | RWD1 | RURAL | Third party impacts | 7 | 140 | 980 | 0.0028392 | 2.028e-05
2012-09-10 | 279683 | LLY5 | RURAL | Other | 6 | 61 | 366 | 0.0010604 | 1.7383e-05
2012-09-10 | 280027 | CRM16A | RURAL | Equipment failure | 4.62 | 19 | 87.78 | 0.00025432 | 1.3385e-05
2012-09-10 | 280028 | LHM5 | RURAL | Other | 73.5 | 91 | 6688.5 | 0.019378 | 0.00021294
2012-09-10 | 281147 | GLY4 | URBAN | Animals | 60.06 | 51 | 3063.06 | 0.0030796 | 6.0384e-05
2012-09-11 | 279664 | CNB26A | RURAL | Third party impacts | 17 | 51 | 867 | 0.0025109 | 4.9234e-05
2012-09-11 | 279666 | MRB2 | RURAL | Equipment failure | 52.6 | 101.6897 | 5332.6 | 0.015444 | 0.00015234
2012-09-11 | 279681 | NSW33A | URBAN | Animals | 8.5 | 74 | 629 | 0.00063245 | 8.5466e-06
2012-09-11 | 279702 | KLG7A | RURAL | Other | 2477.5 | 70.2687 | 161882.5 | 0.46883 | 0.0071752
2012-09-11 | 279707 | MDR8A | URBAN | Other | 0.1 | 135 | 13.5 | 1.3574e-05 | 1.0055e-07
2012-09-11 | 279708 | BWH8A | RURAL | Other | 0.11 | 48 | 5.28 | 1.5292e-05 | 3.1857e-07
2012-09-11 | 279752 | KBR2A | RURAL | Third party impacts | 433.66 | 17 | 7372.22 | 0.021351 | 0.0012559
2012-09-11 | 279753 | CBW12 | URBAN | Equipment failure | 14.4 | 115 | 1656 | 0.0016651 | 1.4479e-05
2012-09-11 | 279756 | SMF1B | RURAL | Equipment failure | 12.5 | 306 | 3825 | 0.011078 | 3.6202e-05
2012-09-11 | 279798 | GYM7A | RURAL | Other | 55.33 | 60 | 3319.8 | 0.0096146 | 0.00016024
2012-09-12 | 279760 | LHM3 | URBAN | Equipment failure | 372.5 | 96.2353 | 34291.77 | 0.034483 | 0.00037457
2012-09-12 | 279762 | KSN2A | RURAL | Third party impacts | 45.6 | 52 | 2371.2 | 0.0068647 | 0.00013201
2012-09-12 | 279768 | NMK18 | URBAN | Equipment failure | 912.99 | 2.6154 | 2795.98 | 0.0028115 | 0.00091807
2012-09-12 | 279797 | DRD3A | URBAN | Animals | 91.08 | 39 | 3552.12 | 0.0035719 | 9.1587e-05
2012-09-12 | 279799 | GYN6A | RURAL | Other | 6 | 212 | 1272 | 0.0036825 | 1.737e-05
2012-09-12 | 279800 | LRE6A | RURAL | Other | 7 | 121 | 847 | 0.0024521 | 2.0265e-05
2012-09-12 | 280030 | LHM3 | URBAN | Equipment failure | 68.64 | 423 | 29034.72 | 0.029196 | 6.9022e-05
2012-09-12 | 281134 | MLB8A | RURAL | Other | 2.2 | 94.3167 | 207.4967 | 0.00060071 | 6.3691e-06
2012-09-13 | 279820 | THL3 | RURAL | Other | 3.45 | 49 | 169.05 | 0.00048922 | 9.9842e-06
2012-09-13 | 279840 | LBH1B | RURAL | Other | 88.99 | 170 | 15128.3 | 0.043781 | 0.00025753
2012-09-13 | 279851 | HPK3A | URBAN | Other | 83.5 | 66 | 5511 | 0.0055421 | 8.3971e-05
2012-09-13 | 280031 | MTG4B | URBAN | Other | 106 | 33 | 3498 | 0.0035177 | 0.0001066
2012-09-13 | 280033 | LHM5 | RURAL | Animals | 38.445 | 69 | 2652.705 | 0.0076768 | 0.00011126
2012-09-13 | 280074 | SGT3 | URBAN | Other | 27.4362 | 95 | 2606.439 | 0.0026211 | 2.7591e-05
2012-09-13 | 280076 | BRD11A | RURAL | Animals | 22 | 98 | 2156 | 0.0062394 | 6.3667e-05
2012-09-14 | 279872 | LBH5A | RURAL | Animals | 43.83 | 79 | 3462.57 | 0.010017 | 0.00012679
2012-09-14 | 279900 | MRE3 | URBAN | Equipment failure | 27.75 | 107 | 2969.25 | 0.0029862 | 2.7909e-05
2012-09-14 | 279923 | SFD10 | URBAN | Equipment failure | 1343.33 | 153.4737 | 210781.08 | 0.21199 | 0.001351
2012-09-14 | 279941 | BIS12A | URBAN | Other | 1 | 16 | 16 | 1.6092e-05 | 1.0057e-06
2012-09-14 | 279941 | BIS12B | RURAL | Other | 1394.5 | 16 | 22312 | 0.064546 | 0.0040341
2012-09-14 | 279942 | ARG5A | URBAN | Third party impacts | 1522.72 | 17.16 | 27780.48 | 0.02794 | 0.0015314
2012-09-14 | 279947 | MDR33A | URBAN | Other | 1.33 | 99 | 131.67 | 0.00013242 | 1.3376e-06
2012-09-14 | 280000 | NBR1 | RURAL | Animals | 25 | 97 | 2425 | 0.0070152 | 7.2322e-05
2012-09-15 | 279960 | NVL11A | URBAN | Equipment failure | 12.32 | 240 | 2956.8 | 0.002974 | 1.2392e-05
2012-09-15 | 279968 | MCW4 | RURAL | Third party impacts | 1290.99 | 143.2727 | 185587.41 | 0.53665 | 0.0037331
2012-09-15 | 279969 | MCW7 | RURAL | Third party impacts | 407.99 | 290.375 | 81209.32 | 0.23483 | 0.0011798
2012-09-15 | 280021 | LLY3 | RURAL | Other | 41 | 148 | 6068 | 0.017546 | 0.00011856
2012-09-15 | 280034 | WRG9A | URBAN | Animals | 58.74 | 127 | 7459.98 | 0.0075035 | 5.9082e-05
2012-09-15 | 281148 | AHL6A | URBAN | Animals | 38.28 | 61 | 2335.08 | 0.0023487 | 3.8503e-05
2012-09-16 | 279967 | MCW11 | RURAL | Other | 236.5 | 3 | 709.5 | 0.0020507 | 0.00068357
2012-09-16 | 279971 | LBH6A | RURAL | Equipment failure | 847.2 | 30.4884 | 27106.5 | 0.078348 | 0.0024487
2012-09-16 | 279989 | LTA5 | URBAN | Animals | 2030.34 | 88.7778 | 163924.71 | 0.1649 | 0.0020424
2012-09-16 | 280001 | WMD14A | RURAL | Animals | 190 | 72 | 13680 | 0.03954 | 0.00054917
2012-09-16 | 280020 | RBK11B | URBAN | Other | 23.45 | 257 | 6026.65 | 0.0060624 | 2.3589e-05
2012-09-16 | 280035 | LGV3A | RURAL | Equipment failure | 9.57 | 105 | 1004.85 | 0.0029044 | 2.7661e-05
2012-09-17 | 280046 | PWC4 | RURAL | Animals | 304 | 97 | 29488 | 0.0852 | 0.00087835
2012-09-17 | 280047 | SRD19A | URBAN | Equipment failure | 27.15 | 132 | 3796.475 | 0.0038193 | 2.7313e-05
2012-09-17 | 280065 | BMT5 | RURAL | Equipment failure | 328 | 41.4634 | 13600 | 0.039295 | 0.00094769
2012-09-17 | 280068 | MLY3 | RURAL | Other | 226.99 | 16 | 3631.84 | 0.010494 | 0.00065584
2012-09-17 | 280075 | SBH6 | URBAN | Equipment failure | 69 | 300 | 20700 | 0.020824 | 6.9415e-05
2012-09-18 | 280073 | MTG16A | URBAN | Other | 677.76 | 11 | 7455.36 | 0.0075008 | 0.00068189
2012-09-18 | 280160 | BLB4A | URBAN | Equipment failure | 163.83 | 48 | 7863.84 | 0.0079118 | 0.00016483
2012-09-18 | 280163 | SBK10A | URBAN | Third party impacts | 29.8 | 173 | 5155.4 | 0.0051868 | 2.9982e-05
2012-09-18 | 280164 | GAP1A | URBAN | Other | 1.99 | 53 | 105.47 | 0.00010611 | 2.0021e-06
2012-09-18 | 280202 | CLM8 | URBAN | Equipment failure | 127 | 23 | 2921 | 0.0029388 | 0.00012777
2012-09-18 | 280204 | CLM8 | URBAN | Equipment failure | 127 | 351 | 44577 | 0.044849 | 0.00012777
2012-09-18 | 280261 | TGP5B | URBAN | Third party impacts | 31 | 93 | 2883 | 0.0029006 | 3.1189e-05
2012-09-18 | 281160 | NMK17A | URBAN | Equipment failure | 25.635 | 78 | 1999.53 | 0.0020117 | 2.5791e-05
2012-09-19 | 280203 | THL1 | RURAL | Equipment failure | 44.99 | 54 | 2429.46 | 0.0070126 | 0.00012986
2012-09-19 | 280205 | THL1 | RURAL | Equipment failure | 34.99 | 65 | 2274.35 | 0.0065649 | 0.000101
2012-09-19 | 280220 | TGW2 | RURAL | Equipment failure | 60.5 | 99 | 5989.5 | 0.017289 | 0.00017463
2012-09-19 | 280221 | CPB2 | URBAN | Equipment failure | 14.355 | 68 | 976.14 | 0.00098203 | 1.4442e-05
2012-09-19 | 280260 | ACR6 | URBAN | Animals | 49.5 | 79 | 3910.5 | 0.0039341 | 4.9799e-05
2012-09-19 | 280268 | QPT21 | URBAN | Other | 46.42 | 2 | 92.84 | 9.34e-05 | 4.67e-05
2012-09-19 | 280269 | BPN34A | URBAN | Equipment failure | 22.5 | 150 | 3375 | 0.0033954 | 2.2636e-05
2012-09-19 | 280276 | ARL2A | URBAN | Equipment failure | 1 | 65 | 65 | 6.5392e-05 | 1.006e-06
2012-09-19 | 280276 | ARL2B | URBAN | Equipment failure | 176.75 | 207.8571 | 40668.75 | 0.040914 | 0.00017782
2012-09-19 | 280277 | BTA3A | RURAL | Weather | 791.5 | 42.3333 | 79260 | 0.22878 | 0.0022847
2012-09-19 | 280280 | WSE5A | RURAL | Equipment failure | 6 | 225 | 1350 | 0.0038968 | 1.7319e-05
2012-09-19 | 280299 | 321 | URBAN | Other | 1 | 26 | 26 | 2.6157e-05 | 1.006e-06
2012-09-19 | 280303 | LRE6A | RURAL | Weather | 7 | 84 | 588 | 0.0016973 | 2.0205e-05
2012-09-19 | 280304 | THL1 | RURAL | Weather | 4.16 | 225 | 936 | 0.0027018 | 1.2008e-05
2012-09-19 | 280305 | PRG2B | RURAL | Weather | 1 | 176 | 176 | 0.00050802 | 2.8865e-06
2012-09-19 | 280307 | PRG2B | RURAL | Weather | 0.5 | 157 | 78.5 | 0.00022659 | 1.4432e-06
2012-09-19 | 280308 | THL1 | RURAL | Weather | 3.33 | 213 | 709.29 | 0.0020474 | 9.612e-06
2012-09-19 | 280424 | ALY9 | URBAN | Other | 18.15 | 23 | 417.45 | 0.00041997 | 1.826e-05
2012-09-19 | 280425 | CVL3A | URBAN | Animals | 42 | 98 | 4116 | 0.0041408 | 4.2253e-05
2012-09-19 | 280440 | MHL3A | RURAL | Other | 32.01 | 61 | 1952.61 | 0.0056362 | 9.2396e-05
2012-09-19 | 281161 | CSE2 | URBAN | Animals | 34.98 | 248 | 8675.04 | 0.0087274 | 3.5191e-05
2012-09-19 | 281163 | CSE4 | URBAN | Animals | 61.2678 | 305 | 18686.679 | 0.018799 | 6.1637e-05
2012-09-20 | 280362 | YDA1B | RURAL | Equipment failure | 400 | 62.9706 | 30939 | 0.08925 | 0.0011539
2012-09-20 | 280362 | YDA3A | RURAL | Equipment failure | 310.5 | 64 | 19872 | 0.057325 | 0.0008957
2012-09-20 | 280380 | RLA7 | URBAN | Animals | 164.57 | 36 | 5924.52 | 0.0059599 | 0.00016555
2012-09-20 | 280400 | IPL3 | RURAL | Equipment failure | 3 | 36 | 108 | 0.00031155 | 8.6541e-06
2012-09-20 | 280405 | LGV6A | RURAL | Equipment failure | 24.5 | 97 | 2376.5 | 0.0068555 | 7.0675e-05
2012-09-20 | 280406 | SPC2B | RURAL | Animals | 5.5811 | 125 | 697.6375 | 0.0020125 | 1.61e-05
2012-09-20 | 280407 | MLY3 | RURAL | Vegetation | 27 | 59 | 1593 | 0.0045953 | 7.7887e-05
2012-09-20 | 280426 | SBK11 | URBAN | Third party impacts | 9.57 | 29 | 277.53 | 0.00027919 | 9.6272e-06
2012-09-20 | 280427 | CPR7 | URBAN | Other | 104.1678 | 101 | 10520.9478 | 0.010584 | 0.00010479
2012-09-20 | 281164 | AHL6A | URBAN | Animals | 65.01 | 84 | 5460.84 | 0.0054935 | 6.5398e-05
2012-09-20 | 281165 | HWD13A | URBAN | Other | 7.26 | 87 | 631.62 | 0.00063539 | 7.3034e-06
2012-09-21 | 280460 | MLY3 | RURAL | Weather | 227.99 | 25 | 5699.75 | 0.016432 | 0.00065727
2012-09-21 | 280462 | MRB2 | RURAL | Weather | 53.6 | 72.5172 | 3548.4 | 0.01023 | 0.00015452
2012-09-21 | 280464 | KCY2 | RURAL | Weather | 122.5 | 204.5532 | 25823.5 | 0.074447 | 0.00035316
2012-09-21 | 280465 | HPE3A | URBAN | Equipment failure | 49.149 | 57 | 2801.493 | 0.0028181 | 4.944e-05
2012-09-21 | 280466 | PWC3 | RURAL | Weather | 55.5 | 98 | 5439 | 0.01568 | 0.00016
2012-09-21 | 280469 | AMR3 | RURAL | Equipment failure | 170.33 | 233.4531 | 44942.92 | 0.12957 | 0.00049104
2012-09-21 | 280473 | WMD13A | RURAL | Weather | 305 | 146.7143 | 47996 | 0.13837 | 0.00087929
2012-09-21 | 280495 | GVN16A | RURAL | Animals | 1118.75 | 51.25 | 42491.75 | 0.1225 | 0.0032252
2012-09-21 | 280506 | KCY2 | RURAL | Weather | 29 | 98 | 2842 | 0.0081932 | 8.3604e-05
2012-09-21 | 280521 | ARG5A | URBAN | Animals | 1576.72 | 85.1071 | 140473.98 | 0.1413 | 0.001586
2012-09-21 | 280571 | CPK13 | RURAL | Equipment failure | 102 | 396 | 40392 | 0.11645 | 0.00029406
2012-09-21 | 280572 | GGR1 | RURAL | Other | 2 | 109 | 218 | 0.00062847 | 5.7658e-06
2012-09-21 | 280573 | TGW3 | RURAL | Weather | 0.67 | 230 | 154.1 | 0.00044426 | 1.9315e-06
2012-09-21 | 280575 | WMD8B | RURAL | Third party impacts | 24.5 | 81 | 1984.5 | 0.0057211 | 7.0631e-05
2012-09-21 | 280576 | GYS3A | RURAL | Weather | 1 | 26 | 26 | 7.4955e-05 | 2.8829e-06
2012-09-21 | 280579 | PWC4 | RURAL | Weather | 31 | 118 | 3658 | 0.010546 | 8.937e-05
2012-09-21 | 281133 | CLD11 | RURAL | Other | 110.4 | 461.55 | 50955.12 | 0.1469 | 0.00031827
2012-09-22 | 280520 | MRE1 | URBAN | Other | 306.56 | 16 | 4904.96 | 0.0049337 | 0.00030835
2012-09-22 | 280522 | THL3 | RURAL | Third party impacts | 413.85 | 81.6196 | 33384.9 | 0.096188 | 0.0011924
2012-09-22 | 280523 | WSE3A | RURAL | Animals | 310.25 | 115.3182 | 34868.5 | 0.10046 | 0.00089389
2012-09-22 | 280529 | CLD11 | RURAL | Equipment failure | 138 | 150 | 20700 | 0.059641 | 0.0003976
2012-09-22 | 280531 | TRP2 | RURAL | Other | 166.26 | 16 | 2660.16 | 0.0076644 | 0.00047903
2012-09-22 | 280533 | TRP2 | RURAL | Vegetation | 166.26 | 100 | 16626 | 0.047903 | 0.00047903
2012-09-22 | 280534 | AMR3 | RURAL | Other | 1 | 115 | 115 | 0.00033134 | 2.8812e-06
2012-09-22 | 280535 | MFN2A | URBAN | Equipment failure | 518.96 | 73 | 37884.08 | 0.038106 | 0.000522
2012-09-22 | 280535 | MFN2B | RURAL | Equipment failure | 2321.25 | 97.6957 | 220327.25 | 0.63481 | 0.006688
2012-09-22 | 280537 | UMG15B | URBAN | Equipment failure | 22.8655 | 422 | 9649.241 | 0.0097057 | 2.2999e-05
2012-09-22 | 280538 | LLY1 | RURAL | Weather | 207.99 | 194 | 40350.06 | 0.11626 | 0.00059926
2012-09-22 | 280574 | THL3 | RURAL | Other | 2.5 | 151 | 377.5 | 0.0010877 | 7.203e-06
2012-09-22 | 280580 | TWT11A | RURAL | Other | 9 | 135 | 1215 | 0.0035007 | 2.5931e-05
2012-09-22 | 280605 | HTN3B | URBAN | Equipment failure | 80.52 | 56 | 4509.12 | 0.0045355 | 8.0991e-05
2012-09-22 | 280689 | MGP13A | RURAL | Equipment failure | 2.5 | 139 | 347.5 | 0.0010012 | 7.203e-06
2012-09-22 | 280699 | BKD5B | RURAL | Animals | 56.1 | 117 | 6563.7 | 0.018911 | 0.00016164
2012-09-23 | 280547 | LGV6A | RURAL | Third party impacts | 769.5 | 103.7679 | 87623.5 | 0.25231 | 0.0022158
2012-09-23 | 280604 | MFN15A | RURAL | Equipment failure | 2.5 | 102 | 255 | 0.00073427 | 7.1987e-06
2012-09-24 | 280577 | MFD12A | URBAN | Equipment failure | 6.9 | 80 | 552 | 0.00055516 | 6.9395e-06
2012-09-24 | 280578 | BHL5A | URBAN | Other | 1726.75 | 72 | 124326 | 0.12504 | 0.0017366
2012-09-24 | 280603 | NDH7 | URBAN | Equipment failure | 146.85 | 94 | 13803.9 | 0.013883 | 0.00014769
2012-09-24 | 280606 | MRB2 | RURAL | Other | 53.6 | 18 | 964.8 | 0.0027765 | 0.00015425
2012-09-24 | 280608 | BDT1 | RURAL | Weather | 98 | 16 | 1568 | 0.0045124 | 0.00028203
2012-09-24 | 280610 | MLY3 | RURAL | Weather | 227.99 | 17 | 3875.83 | 0.011154 | 0.00065611
2012-09-24 | 280615 | GVN3A | URBAN | Weather | 886 | 44.7 | 82362 | 0.082833 | 0.00089107
2012-09-24 | 280632 | RLB11B | URBAN | Weather | 1926.5 | 113.7742 | 214665 | 0.21589 | 0.0019375
2012-09-24 | 280632 | RLB15A | URBAN | Weather | 121.5 | 30 | 3645 | 0.0036659 | 0.0001222
2012-09-24 | 280638 | YDA1B | RURAL | Weather | 400 | 98.8235 | 44579.5 | 0.12829 | 0.0011511
2012-09-24 | 280649 | NSW16A | URBAN | Weather | 783.33 | 119.2353 | 110757.84 | 0.11139 | 0.00078781
2012-09-24 | 280650 | CMA8A | RURAL | Weather | 59.63 | 237 | 14132.31 | 0.04067 | 0.0001716
2012-09-24 | 280654 | TWT15A | RURAL | Weather | 632.5 | 141.4444 | 89711.5 | 0.25817 | 0.0018202
2012-09-24 | 280657 | GYM2A | RURAL | Weather | 1361.99 | 113.6992 | 198207.93 | 0.5704 | 0.0039195
2012-09-24 | 280660 | TWT12A | RURAL | Equipment failure | 1072.01 | 128.9136 | 145695.06 | 0.41928 | 0.003085
2012-09-24 | 280664 | MRK9 | URBAN | Equipment failure | 95.09 | 10 | 950.9 | 0.00095634 | 9.5634e-05
2012-09-24 | 280672 | ALY8 | URBAN | Third party impacts | 23 | 384 | 8832 | 0.0088825 | 2.3132e-05
2012-09-24 | 280673 | NVL4 | URBAN | Weather | 842 | 127.2353 | 110046 | 0.11068 | 0.00084682
2012-09-24 | 280673 | NVL8B | URBAN | Weather | 450 | 45 | 20250 | 0.020366 | 0.00045258
2012-09-24 | 280674 | BMT1 | RURAL | Weather | 97 | 190 | 18430 | 0.053038 | 0.00027915
2012-09-24 | 280676 | PWC6 | RURAL | Weather | 18.09 | 84 | 1519.56 | 0.004373 | 5.206e-05
2012-09-24 | 280679 | GYN3A | RURAL | Weather | 19.5 | 74 | 1443 | 0.0041527 | 5.6117e-05
2012-09-24 | 280680 | BMT3 | RURAL | Weather | 64.33 | 105 | 6754.65 | 0.019439 | 0.00018513
2012-09-24 | 280682 | GGR1 | RURAL | Weather | 88.49 | 52 | 4601.48 | 0.013242 | 0.00025466
2012-09-24 | 280684 | GGR3 | RURAL | Weather | 4 | 398 | 1592 | 0.0045815 | 1.1511e-05
2012-09-24 | 280688 | GYN3A | RURAL | Weather | 15.6378 | 419 | 6552.2382 | 0.018856 | 4.5003e-05
2012-09-24 | 280690 | MTB15A | RURAL | Weather | 1.65 | 78 | 128.7 | 0.00037037 | 4.7484e-06
2012-09-24 | 280691 | GYN3A | RURAL | Weather | 7.5 | 79 | 592.5 | 0.0017051 | 2.1584e-05
2012-09-24 | 280692 | EMD3 | RURAL | Equipment failure | 11 | 125 | 1375 | 0.003957 | 3.1656e-05
2012-09-24 | 280693 | GYN3A | RURAL | Weather | 19.5 | 338 | 6591 | 0.018968 | 5.6117e-05
2012-09-24 | 280694 | TRP4 | RURAL | Weather | 1 | 164 | 164 | 0.00047196 | 2.8778e-06
2012-09-24 | 280695 | GGR5 | RURAL | Other | 4.7289 | 52 | 245.9028 | 0.00070766 | 1.3609e-05
2012-09-24 | 280696 | MSV1 | RURAL | Weather | 3.685 | 350 | 1289.75 | 0.0037117 | 1.0605e-05
2012-09-24 | 280697 | GGR1 | RURAL | Weather | 3 | 437 | 1311 | 0.0037728 | 8.6334e-06
2012-09-24 | 280698 | BMT2 | RURAL | Weather | 162.5 | 153.3101 | 58104.5 | 0.16721 | 0.00046764
2012-09-24 | 280700 | HPE13A | URBAN | Weather | 46.695 | 149 | 6957.555 | 0.0069974 | 4.6962e-05
2012-09-24 | 280701 | CPD1 | RURAL | Weather | 6.5 | 101 | 656.5 | 0.0018893 | 1.8706e-05
2012-09-24 | 280702 | LLY3 | RURAL | Weather | 6 | 166 | 996 | 0.0028663 | 1.7267e-05
2012-09-24 | 280703 | TGW3 | RURAL | Weather | 0.67 | 143 | 95.81 | 0.00027572 | 1.9281e-06
2012-09-24 | 280704 | BMT1 | RURAL | Weather | 182.01 | 343.6286 | 60789.51 | 0.17494 | 0.00052379
2012-09-24 | 280723 | AMR2 | RURAL | Weather | 208.99 | 16 | 3343.84 | 0.0096229 | 0.00060143
2012-09-24 | 280723 | GYM2A | RURAL | Weather | 1049.49 | 18 | 20705.97 | 0.059588 | 0.0030202
2012-09-24 | 280764 | GTN13A | RURAL | Weather | 4.02 | 101 | 406.02 | 0.0011684 | 1.1569e-05
2012-09-24 | 281166 | NMK5 | URBAN | Other | 4.483 | 30 | 134.49 | 0.00013526 | 4.5087e-06
2012-09-24 | 282786 | OXL11A | URBAN | Other | 41.25 | 116 | 4785 | 0.0048124 | 4.1486e-05
2012-09-25 | 280687 | MDHSWB10 | URBAN | Third party impacts | 4 | 19 | 76 | 7.6425e-05 | 4.0224e-06
2012-09-25 | 280705 | RCN4A | URBAN | Third party impacts | 6 | 10 | 60 | 6.0335e-05 | 6.0335e-06
2012-09-25 | 280709 | RPN8 | RURAL | Vegetation | 82.25 | 80 | 6580 | 0.018929 | 0.00023661
2012-09-25 | 280725 | EMD2 | RURAL | Vegetation | 7 | 129 | 903 | 0.0025977 | 2.0137e-05
2012-09-25 | 280761 | CHL4 | URBAN | Equipment failure | 12.88 | 113 | 1455.44 | 0.0014636 | 1.2952e-05
2012-09-25 | 280762 | MLT15A | URBAN | Equipment failure | 1.1 | 54 | 59.4 | 5.9732e-05 | 1.1061e-06
2012-09-25 | 280780 | SPC2B | RURAL | Other | 1 | 95 | 95 | 0.00027329 | 2.8767e-06
2012-09-25 | 280800 | GYM2A | RURAL | Equipment failure | 1 | 321 | 321 | 0.00092343 | 2.8767e-06
2012-09-25 | 281167 | KMR17A | URBAN | Equipment failure | 57.955 | 70 | 4056.85 | 0.0040795 | 5.8279e-05
2012-09-26 | 280820 | KLG14A | URBAN | Third party impacts | 934 | 213.1818 | 161403 | 0.16228 | 0.00093909
2012-09-26 | 280888 | SIS1 | RURAL | Vegetation | 25.5 | 35 | 892.5 | 0.0025665 | 7.3328e-05
2012-09-26 | 280890 | BKD15A | URBAN | Equipment failure | 11.1 | 95 | 1054.5 | 0.0010602 | 1.1161e-05
2012-09-26 | 280900 | CHBT0 | URBAN | Other | 1 | 2787 | 2787 | 0.0028022 | 1.0055e-06
2012-09-26 | 280903 | AGT23A | URBAN | Equipment failure | 100 | 312 | 31200 | 0.03137 | 0.00010055
2012-09-26 | 280905 | HWD2B | RURAL | Third party impacts | 20 | 83 | 1660 | 0.0047735 | 5.7512e-05
2012-09-27 | 280891 | AHD15B | URBAN | Equipment failure | 4.4966 | 94 | 422.6804 | 0.00042493 | 4.5205e-06
2012-09-27 | 280920 | BIS16A | URBAN | Other | 1320 | 2 | 2640 | 0.002654 | 0.001327
2012-09-27 | 280926 | KMR28A | URBAN | Equipment failure | 10.875 | 183 | 1990.125 | 0.0020007 | 1.0933e-05
2012-09-27 | 280967 | FDS1 | RURAL | Animals | 4 | 33 | 132 | 0.00037943 | 1.1498e-05
2012-09-27 | 280968 | CBW11 | RURAL | Other | 29 | 49 | 1421 | 0.0040847 | 8.336e-05
2012-09-27 | 280969 | CHL5 | URBAN | Equipment failure | 96.815 | 1000 | 96815 | 0.09733 | 9.733e-05
2012-09-27 | 280981 | TGW3 | RURAL | Other | 1 | 74 | 74 | 0.00021271 | 2.8745e-06
2012-09-27 | 281168 | INA10A | URBAN | Other | 22.4575 | 109 | 2447.8675 | 0.0024609 | 2.2577e-05
2012-09-27 | 281169 | GAP6A | URBAN | Other | 38.61 | 48 | 1853.28 | 0.0018631 | 3.8815e-05
2012-09-28 | 280966 | AHL8A | URBAN | Third party impacts | 61.5 | 251 | 15436.5 | 0.015516 | 6.1819e-05
2012-09-28 | 280970 | BRD8A | RURAL | Other | 90 | 27 | 2430 | 0.0069823 | 0.00025861
2012-09-28 | 281040 | SBK10A | URBAN | Other | 722 | 16 | 11552 | 0.011612 | 0.00072574
2012-09-28 | 281083 | GYM2A | RURAL | Other | 4.62 | 94 | 434.28 | 0.0012479 | 1.3275e-05
2012-09-28 | 281102 | TMH15A | URBAN | Third party impacts | 29.04 | 42 | 1219.68 | 0.001226 | 2.919e-05
2012-09-28 | 281170 | MLT21B | URBAN | Other | 53.13 | 52 | 2762.76 | 0.0027771 | 5.3405e-05
2012-09-29 | 281043 | TBV1 | RURAL | Other | 45.17 | 4 | 180.68 | 0.00051897 | 0.00012974
2012-09-29 | 281043 | TBV2 | RURAL | Other | 296 | 4 | 1184 | 0.0034008 | 0.0008502
2012-09-29 | 281043 | TBV3 | RURAL | Other | 379.5 | 4 | 1518 | 0.0043602 | 0.00109
2012-09-29 | 281043 | TBV4 | RURAL | Other | 515.17 | 4 | 2060.68 | 0.0059189 | 0.0014797
2012-09-29 | 281044 | CHL11A | RURAL | Third party impacts | 1877.34 | 107.6154 | 201915.04 | 0.57996 | 0.0053923
2012-09-29 | 281045 | STT1B | RURAL | Equipment failure | 7.5 | 30 | 225 | 0.00064627 | 2.1542e-05
2012-09-29 | 281047 | MLY3 | RURAL | Other | 227.99 | 24 | 5471.76 | 0.015717 | 0.00065486
2012-09-29 | 281048 | NGI2A | URBAN | Weather | 1 | 51 | 51 | 5.1257e-05 | 1.005e-06
2012-09-29 | 281048 | NGI2B | RURAL | Weather | 1931.5 | 53.7692 | 106656.5 | 0.30635 | 0.0055479
2012-09-29 | 281050 | KCY2 | RURAL | Third party impacts | 96 | 70 | 6720 | 0.019302 | 0.00027574
2012-09-29 | 281050 | LTN3 | URBAN | Third party impacts | 56 | 66.5 | 3709.5 | 0.0037282 | 5.6282e-05
2012-09-29 | 281104 | WRD20A | URBAN | Other | 51.0378 | 82 | 4185.0996 | 0.0042062 | 5.1295e-05
2012-09-30 | 281071 | MLY3 | RURAL | Equipment failure | 72.99 | 131 | 9561.69 | 0.027454 | 0.00020957
2012-09-30 | 281074 | GGR2 | RURAL | Equipment failure | 23.49 | 64 | 1503.36 | 0.0043165 | 6.7446e-05
2012-09-30 | 281087 | TGP9A | RURAL | Equipment failure | 21.5 | 148 | 3182 | 0.0091363 | 6.1732e-05
2012-09-30 | 281135 | OXL11A | URBAN | Animals | 41.25 | 101 | 4166.25 | 0.0041867 | 4.1452e-05
2012-09-30 | 281144 | MLT21B | URBAN | Equipment failure | 67.4322 | 103 | 6945.5166 | 0.0069796 | 6.7763e-05
2012-09-30 | 281171 | OXL11A | URBAN | Animals | 41.25 | 46 | 1897.5 | 0.0019068 | 4.1452e-05
2012-10-01 | 281085 | GGR3 | RURAL | Other | 3.35 | 87 | 291.45 | 0.00083658 | 9.6159e-06
2012-10-02 | 281101 | RPN6A | RURAL | Third party impacts | 7.85 | 64 | 502.4 | 0.0014417 | 2.2526e-05
2012-10-02 | 281105 | CPB6 | URBAN | Animals | 4.95 | 31 | 153.45 | 0.00015415 | 4.9726e-06
2012-10-02 | 281106 | CRM13A | URBAN | Equipment failure | 42.9 | 96 | 4118.4 | 0.0041372 | 4.3096e-05
2012-10-02 | 281108 | HPE5A | URBAN | Equipment failure | 36.1 | 35 | 1263.5 | 0.0012693 | 3.6265e-05
2012-10-02 | 281125 | BHL2A | URBAN | Vegetation | 147 | 20 | 2940 | 0.0029534 | 0.00014767
2012-10-02 | 281126 | CMD15A | URBAN | Other | 440.5 | 91 | 40085.5 | 0.040269 | 0.00044251
2012-10-02 | 281127 | KRN10 | URBAN | Equipment failure | 1543 | 89.5 | 135351 | 0.13597 | 0.0015501
2012-10-02 | 281128 | BTN3 | RURAL | Vegetation | 908.83 | 51.5 | 93609.49 | 0.26862 | 0.002608
2012-10-03 | 281174 | NVL10 | URBAN | Equipment failure | 13.375 | 87 | 1163.625 | 0.0011688 | 1.3434e-05
2012-10-03 | 281184 | MDH5A | URBAN | Operational error | 63 | 45 | 2835 | 0.0028475 | 6.3278e-05
2012-10-03 | 281184 | MDH5B | URBAN | Operational error | 43.33 | 45 | 1949.85 | 0.0019584 | 4.3521e-05
2012-10-03 | 281187 | BKD13A | URBAN | Other | 43 | 234 | 10062 | 0.010106 | 4.3189e-05
2012-10-03 | 281187 | RIS2 | URBAN | Other | 2507 | 53 | 132871 | 0.13346 | 0.002518
2012-10-03 | 281208 | NRA16A | RURAL | Equipment failure | 24 | 126 | 3024 | 0.0086751 | 6.885e-05
2012-10-03 | 281209 | SBH4 | URBAN | Other | 55.11 | 63 | 3471.93 | 0.0034872 | 5.5353e-05
2012-10-03 | 281273 | MTG7A | URBAN | Animals | 56 | 34 | 1904 | 0.0019124 | 5.6247e-05
2012-10-03 | 281274 | WED6A | URBAN | Animals | 88.11 | 35 | 3083.85 | 0.0030974 | 8.8498e-05
2012-10-04 | 281210 | LTN7 | URBAN | Equipment failure | 1 | 25 | 25 | 2.5105e-05 | 1.0042e-06
2012-10-04 | 281225 | NBR7 | URBAN | Equipment failure | 1476.25 | 10 | 14762.5 | 0.014824 | 0.0014824
2012-10-04 | 281232 | WMR4 | RURAL | Equipment failure | 48 | 118.2105 | 4760 | 0.013653 | 0.00013768
2012-10-04 | 281233 | NMC1B | RURAL | Equipment failure | 8 | 218 | 1744 | 0.0050022 | 2.2946e-05
2012-10-04 | 281263 | NMK26 | URBAN | Equipment failure | 11.1 | 109 | 1209.9 | 0.001215 | 1.1147e-05
2012-10-04 | 281265 | CLM5 | URBAN | Animals | 1844.5 | 30.2 | 65828 | 0.066104 | 0.0018522
2012-10-04 | 281271 | RBA35A | RURAL | Third party impacts | 162.5 | 334 | 54275 | 0.15567 | 0.00046609
2012-10-04 | 281275 | CHL5 | URBAN | Other | 59.2911 | 100 | 5929.11 | 0.005954 | 5.954e-05
2012-10-04 | 281276 | BLB2A | URBAN | Animals | 39.4878 | 59 | 2329.7802 | 0.0023396 | 3.9654e-05
2012-10-04 | 281277 | BPN3 | URBAN | Animals | 49.5 | 101 | 4999.5 | 0.0050205 | 4.9708e-05
2012-10-04 | 281380 | CLM5 | URBAN | Animals | 35 | 164 | 5740 | 0.0057641 | 3.5147e-05
2012-10-05 | 281266 | 383 | URBAN | Equipment failure | 1 | 15 | 15 | 1.5059e-05 | 1.0039e-06
2012-10-05 | 281266 | LWD1 | RURAL | Equipment failure | 634 | 15 | 9510 | 0.027278 | 0.0018185
2012-10-05 | 281266 | WHO1 | RURAL | Equipment failure | 529 | 15 | 7935 | 0.02276 | 0.0015173
2012-10-05 | 281266 | WHO2 | RURAL | Equipment failure | 837.5 | 15 | 12562.5 | 0.036033 | 0.0024022
2012-10-05 | 281266 | WHO9 | RURAL | Equipment failure | 75.09 | 15 | 1126.35 | 0.0032307 | 0.00021538
2012-10-05 | 281269 | CNB26A | RURAL | Other | 5.36 | 78 | 418.08 | 0.0011992 | 1.5374e-05
2012-10-05 | 281270 | RBY13 | URBAN | Other | 944.5 | 39 | 36835.5 | 0.03698 | 0.00094821
2012-10-05 | 281286 | TRP2 | RURAL | Equipment failure | 23.01 | 160 | 3681.6 | 0.01056 | 6.6e-05
2012-10-05 | 281287 | LRE6A | RURAL | Equipment failure | 1 | 101 | 101 | 0.0002897 | 2.8683e-06
2012-10-05 | 281300 | NBR5 | RURAL | Weather | 200 | 49.6316 | 11822 | 0.033909 | 0.00057367
2012-10-05 | 281381 | LBH1B | RURAL | Vegetation | 18.5 | 121 | 2238.5 | 0.0064208 | 5.3064e-05
2012-10-05 | 281382 | WMD10A | URBAN | Animals | 41 | 64 | 2624 | 0.0026343 | 4.1161e-05
2012-10-05 | 281385 | MTG8A | URBAN | Equipment failure | 101.83 | 76 | 7739.08 | 0.0077694 | 0.00010223
2012-10-05 | 281386 | BVL2A | URBAN | Other | 109.21 | 59 | 6443.39 | 0.0064687 | 0.00010964
2012-10-05 | 281388 | TGW3 | RURAL | Other | 0.67 | 214 | 143.38 | 0.00041126 | 1.9218e-06
2012-10-05 | 281391 | WRD15A | URBAN | Animals | 44.88 | 39 | 1750.32 | 0.0017572 | 4.5056e-05
2012-10-06 | 281322 | KMR24A | URBAN | Other | 749.17 | 15 | 11237.55 | 0.011279 | 0.0007519
2012-10-06 | 281322 | KMR24B | URBAN | Other | 1 | 15 | 15 | 1.5055e-05 | 1.0037e-06
2012-10-06 | 281340 | AMR2 | RURAL | Equipment failure | 208.99 | 195.2222 | 40002.48 | 0.11474 | 0.00059946
2012-10-06 | 281341 | TWT11A | RURAL | Vegetation | 36 | 20 | 720 | 0.0020652 | 0.00010326
2012-10-06 | 281343 | BKD15A | URBAN | Other | 3 | 69 | 207 | 0.00020776 | 3.011e-06
2012-10-06 | 281378 | CBW5 | URBAN | Other | 42.735 | 144 | 6153.84 | 0.0061763 | 4.2891e-05
2012-10-06 | 281379 | NRA13A | RURAL | Other | 37 | 95 | 3515 | 0.010082 | 0.00010613
2012-10-06 | 281383 | CRY3A | RURAL | Animals | 92 | 68 | 6256 | 0.017945 | 0.00026389
2012-10-06 | 281389 | MCW11 | RURAL | Other | 22.445 | 81 | 1818.045 | 0.0052149 | 6.4381e-05
2012-10-06 | 281392 | NSW17 | URBAN | Animals | 40.1478 | 83 | 3332.2674 | 0.0033444 | 4.0294e-05
2012-10-06 | 281393 | BKD15A | URBAN | Operational error | 1.98 | 110 | 217.8 | 0.0002186 | 1.9872e-06
2012-10-07 | 281371 | PWC4 | RURAL | Vegetation | 18 | 128 | 2304 | 0.0066089 | 5.1632e-05
2012-10-07 | 281384 | PWC4 | RURAL | Vegetation | 5 | 130 | 650 | 0.0018645 | 1.4342e-05
2012-10-07 | 281387 | UMG15B | URBAN | Animals | 40.26 | 82 | 3301.32 | 0.0033125 | 4.0396e-05
2012-10-07 | 281390 | WSO13A | RURAL | Animals | 135.5611 | 82 | 11116.0102 | 0.031886 | 0.00038885
2012-10-07 | 281394 | RIS4 | RURAL | Vegetation | 19 | 99 | 1881 | 0.0053955 | 5.45e-05
2012-10-07 | 281500 | MCW11 | RURAL | Vegetation | 3.96 | 79 | 312.84 | 0.00089736 | 1.1359e-05
2012-10-07 | 281501 | MCW11 | RURAL | Vegetation | 12 | 261 | 3132 | 0.0089839 | 3.4421e-05
2012-10-08 | 281375 | MLY1 | RURAL | Equipment failure | 833.01 | 2 | 1666.02 | 0.004779 | 0.0023895
2012-10-08 | 281375 | MLY3 | RURAL | Equipment failure | 2048.48 | 2 | 4096.96 | 0.011752 | 0.0058761
2012-10-08 | 281375 | MLY4 | RURAL | Equipment failure | 626.49 | 2 | 1252.98 | 0.0035942 | 0.0017971
2012-10-08 | 281375 | MLY6 | RURAL | Equipment failure | 611.5 | 2 | 1223 | 0.0035082 | 0.0017541
2012-10-08 | 281377 | AHL8A | URBAN | Animals | 0.99 | 105 | 103.95 | 0.00010427 | 9.9308e-07
2012-10-08 | 281395 | WRD21A | URBAN | Third party impacts | 100.98 | 35 | 3534.3 | 0.0035453 | 0.00010129
2012-10-08 | 281404 | CPB4 | URBAN | Vegetation | 116 | 27 | 3132 | 0.0031417 | 0.00011636
2012-10-08 | 281417 | MDH5A | URBAN | Other | 63 | 16 | 1008 | 0.0010111 | 6.3196e-05
2012-10-08 | 281417 | MDH5B | URBAN | Other | 43.33 | 16 | 693.28 | 0.00069543 | 4.3465e-05
2012-10-08 | 281418 | TGW1 | RURAL | Equipment failure | 50.36 | 9.3636 | 393.58 | 0.001129 | 0.00014446
2012-10-08 | 281420 | PBH6 | URBAN | Equipment failure | 8.5415 | 110 | 939.565 | 0.00094249 | 8.568e-06
2012-10-08 | 281422 | PBH3 | URBAN | Equipment failure | 1126.68 | 52.8 | 72849.24 | 0.073076 | 0.0011302
2012-10-08 | 281429 | MCW4 | RURAL | Animals | 29.7011 | 112 | 3326.5232 | 0.0095421 | 8.5197e-05
2012-10-09 | 281426 | RLA8 | URBAN | Animals | 1 | 449 | 449 | 0.00045027 | 1.0028e-06
2012-10-09 | 281427 | ALY6 | URBAN | Animals | 794 | 23 | 18262 | 0.018314 | 0.00079625
2012-10-09 | 281428 | ZMR7A | URBAN | Equipment failure | 1867.82 | 47.7455 | 173688.89 | 0.17418 | 0.0018731
2012-10-09 | 281440 | ARG5A | URBAN | Other | 1576.22 | 17 | 26795.74 | 0.026872 | 0.0015807
2012-10-09 | 281442 | BTN7 | RURAL | Third party impacts | 72.98 | 120 | 8841.84 | 0.025363 | 0.00020935
2012-10-09 | 281443 | GAP9A | URBAN | Equipment failure | 5 | 127 | 635 | 0.0006368 | 5.0142e-06
2012-10-09 | 281483 | ARG5A | URBAN | Animals | 132 | 46 | 6072 | 0.0060892 | 0.00013237
2012-10-09 | 281496 | HPE3A | URBAN | Equipment failure | 81.915 | 142 | 8928.735 | 0.0089541 | 8.2148e-05
2012-10-09 | 281498 | MMC19B | URBAN | Equipment failure | 31.8 | 257 | 10589.4 | 0.010619 | 3.189e-05
2012-10-09 | 281505 | KRN1 | URBAN | Third party impacts | 50.16 | 64 | 3210.24 | 0.0032194 | 5.0302e-05
2012-10-09 | 281526 | NGI3A | RURAL | Vegetation | 8 | 48 | 384 | 0.0011015 | 2.2949e-05
2012-10-09 | 281842 | MGP12A | RURAL | Other | 7.59 | 64 | 485.76 | 0.0013934 | 2.1772e-05
2012-10-09 | 281880 | HPE5A | URBAN | Other | 40.2039 | 88 | 3537.9432 | 0.003548 | 4.0318e-05
2012-10-10 | 281530 | IPL3 | RURAL | Equipment failure | 12 | 42 | 504 | 0.0014457 | 3.4422e-05
2012-10-10 | 281532 | ARL6B | URBAN | Equipment failure | 57 | 190 | 10830 | 0.010858 | 5.7147e-05
2012-10-10 | 281533 | MFN2B | RURAL | Other | 306.75 | 75 | 23006.25 | 0.065994 | 0.00087992
2012-10-10 | 281537 | RBY3 | URBAN | Other | 68.5 | 85 | 5822.5 | 0.0058375 | 6.8677e-05
2012-10-10 | 281538 | BGY6A | RURAL | Equipment failure | 32.25 | 213.5 | 8074.11 | 0.023161 | 9.251e-05
2012-10-10 | 281581 | ZMR5 | URBAN | Animals | 1956.51 | 19 | 37173.69 | 0.037269 | 0.0019616
2012-10-10 | 281594 | CSE2 | URBAN | Other | 1.545 | 118 | 182.31 | 0.00018278 | 1.549e-06
2012-10-10 | 281745 | MAI11 | URBAN | Equipment failure | 12.67 | 74 | 937.58 | 0.00094 | 1.2703e-05
2012-10-10 | 281881 | BLB4A | URBAN | Other | 63.03 | 36 | 2269.08 | 0.0022749 | 6.3192e-05
2012-10-11 | 281584 | WRD21A | URBAN | Animals | 822.33 | 54 | 44405.82 | 0.044509 | 0.00082423
2012-10-11 | 281589 | SMF2A | RURAL | Other | 927.99 | 31 | 28767.69 | 0.08252 | 0.0026619
2012-10-11 | 281591 | LDR8 | URBAN | Animals | 1147.99 | 108.4706 | 125960.54 | 0.12625 | 0.0011506
2012-10-11 | 281593 | BRD11A | RURAL | Animals | 25.5 | 167 | 4258.5 | 0.012215 | 7.3147e-05
2012-10-11 | 281595 | LBH5A | RURAL | Equipment failure | 105.01 | 193.4 | 18068.51 | 0.051829 | 0.00030122
2012-10-11 | 281602 | IDY9A | URBAN | Animals | 1 | 65 | 130 | 0.0001303 | 1.0023e-06
2012-10-11 | 281602 | IDY9B | URBAN | Animals | 914.66 | 82.6111 | 154116.3 | 0.15447 | 0.00091678
2012-10-11 | 281606 | MLT2B | URBAN | Other | 1236.06 | 2 | 2472.12 | 0.0024778 | 0.0012389
2012-10-11 | 281610 | GTN12A | RURAL | Other | 240.82 | 63.75 | 15253.2 | 0.043754 | 0.00069079
2012-10-11 | 281612 | ARL3A | URBAN | Third party impacts | 25.5 | 49 | 1249.5 | 0.0012524 | 2.5559e-05
2012-10-11 | 281617 | TCB2 | RURAL | Weather | 1257.64 | 131 | 164750.84 | 0.47259 | 0.0036075
2012-10-11 | 281618 | RST18A | URBAN | Equipment failure | 4.3 | 135 | 580.5 | 0.00058184 | 4.31e-06
2012-10-11 | 281621 | MRE8 | URBAN | Equipment failure | 44.5 | 165 | 7342.5 | 0.0073595 | 4.4603e-05
2012-10-11 | 281622 | WMR3 | RURAL | Weather | 367.65 | 71.3765 | 24329.5 | 0.069789 | 0.0010546
2012-10-11 | 281623 | EZRRWD4 | RURAL | Equipment failure | 15 | 60 | 900 | 0.0025816 | 4.3027e-05
2012-10-11 | 281627 | CBW7 | RURAL | Weather | 1376.77 | 41.5918 | 58935.26 | 0.16906 | 0.0039493
2012-10-11 | 281644 | IPL1 | RURAL | Equipment failure | 1.415 | 145 | 205.175 | 0.00058854 | 4.0589e-06
2012-10-11 | 281662 | LLY1 | RURAL | Equipment failure | 207.99 | 241 | 50125.59 | 0.14379 | 0.00059662
2012-10-11 | 281663 | JBB3A | RURAL | Weather | 944.5 | 32.2941 | 29752.5 | 0.085345 | 0.0027093
2012-10-11 | 281664 | TRG10B | URBAN | Other | 507 | 16 | 8112 | 0.0081308 | 0.00050817
2012-10-11 | 281666 | GBG26 | URBAN | Equipment failure | 299.33 | 196 | 61304.29 | 0.061446 | 0.00030002
2012-10-11 | 281668 | AHL14A | URBAN | Equipment failure | 42.24 | 43 | 1816.32 | 0.0018205 | 4.2338e-05
2012-10-11 | 281669 | TGW3 | RURAL | Equipment failure | 3.35 | 148 | 495.8 | 0.0014222 | 9.6095e-06
2012-10-11 | 281805 | MFN13A | RURAL | Weather | 19.14 | 98 | 1875.72 | 0.0053805 | 5.4903e-05
2012-10-11 | 281877 | LRE4A | RURAL | Other | 1 | 143 | 143 | 0.00041019 | 2.8685e-06
2012-10-11 | 281878 | LRE4A | RURAL | Other | 2.4 | 227 | 544.8 | 0.0015628 | 6.8844e-06
2012-10-11 | 281883 | EMP25A | URBAN | Animals | 31.8978 | 108 | 3444.9624 | 0.0034529 | 3.1972e-05
2012-10-11 | 281889 | TWT11A | RURAL | Equipment failure | 29.865 | 76 | 2269.74 | 0.0065107 | 8.5668e-05
2012-10-12 | 281682 | SPO8A | URBAN | Vegetation | 701.76 | 9 | 6315.84 | 0.0063288 | 0.0007032
2012-10-12 | 281701 | CLR8 | RURAL | Vegetation | 58.99 | 84 | 4955.16 | 0.014214 | 0.00016921
2012-10-12 | 281709 | ARL15B | URBAN | Weather | 391 | 99.3333 | 38326 | 0.038405 | 0.0003918
2012-10-12 | 281722 | ABY5A | RURAL | Other | 44.5 | 16 | 712 | 0.0020424 | 0.00012765
2012-10-12 | 281723 | 3702 | URBAN | Other | 1.25 | 17 | 21.25 | 2.1294e-05 | 1.2526e-06
2012-10-12 | 281724 | MGL2A | RURAL | Vegetation | 111 | 277.5 | 25610 | 0.073462 | 0.0003184
2012-10-12 | 281725 | PPE16A | RURAL | Weather | 378.75 | 119.1111 | 42407.5 | 0.12164 | 0.0010864
2012-10-12 | 281726 | VPT1B | URBAN | Weather | 660.99 | 192 | 126910.08 | 0.12717 | 0.00066235
2012-10-12 | 281727 | OXL8B | URBAN | Weather | 30.17 | 175 | 5279.75 | 0.0052906 | 3.0232e-05
2012-10-12 | 281728 | AGE10 | URBAN | Weather | 88 | 165 | 14520 | 0.01455 | 8.8181e-05
2012-10-12 | 281803 | ZMR5 | URBAN | Other | 51.15 | 58 | 2966.7 | 0.0029728 | 5.1255e-05
2012-10-12 | 281804 | TGP8A | URBAN | Weather | 67.98 | 56 | 3806.88 | 0.0038147 | 6.812e-05
2012-10-12 | 281820 | MCW11 | RURAL | Vegetation | 16.415 | 70 | 1149.05 | 0.003296 | 4.7086e-05
2012-10-12 | 281821 | NIP3A | URBAN | Equipment failure | 104.5 | 70 | 7315 | 0.00733 | 0.00010471
2012-10-12 | 281884 | HPK5A | URBAN | Other | 38.0622 | 68 | 2588.2296 | 0.0025935 | 3.814e-05
2012-10-12 | 281885 | BLH12A | RURAL | Other | 4.95 | 81 | 400.95 | 0.0011501 | 1.4199e-05
2012-10-12 | 281890 | NBR6 | RURAL | Other | 4.62 | 43.0667 | 198.968 | 0.00057073 | 1.3252e-05
2012-10-13 | 281763 | GYGGYS6 | RURAL | Other | 6 | 25 | 150 | 0.00043026 | 1.7211e-05
2012-10-13 | 281764 | KMR17A | URBAN | Equipment failure | 578 | 32.2857 | 15680 | 0.015708 | 0.00057904
2012-10-13 | 281764 | KMR17B | URBAN | Equipment failure | 1482 | 66.0714 | 98633 | 0.09881 | 0.0014847
2012-10-13 | 281772 | LLY4 | RURAL | Animals | 1571.31 | 185.3137 | 186732.61 | 0.53563 | 0.0045072
2012-10-13 | 281822 | WHO9 | RURAL | Other | 1.34 | 122 | 163.48 | 0.00046893 | 3.8437e-06
2012-10-13 | 281823 | CPD1 | RURAL | Other | 3 | 96 | 288 | 0.00082611 | 8.6053e-06
2012-10-13 | 281862 | AGT31A | RURAL | Vegetation | 0.66 | 128 | 84.48 | 0.00024232 | 1.8932e-06
2012-10-13 | 281887 | TMH2A | RURAL | Equipment failure | 0.825 | 119 | 98.175 | 0.00028161 | 2.3665e-06
2012-10-13 | 281888 | ALY5 | URBAN | Animals | 38.28 | 77 | 2947.56 | 0.0029528 | 3.8349e-05
2012-10-14 | 281771 | NVL8A | URBAN | Animals | 1 | 47 | 47 | 4.7072e-05 | 1.0015e-06
2012-10-14 | 281771 | NVL8B | URBAN | Animals | 1945.5 | 75.28 | 179924 | 0.1802 | 0.0019485
2012-10-14 | 281777 | MTB15A | RURAL | Weather | 711.5 | 180.25 | 121863.5 | 0.34955 | 0.0020409
2012-10-14 | 281788 | CMV9A | URBAN | Third party impacts | 1473.55 | 133.8095 | 211822.01 | 0.21215 | 0.0014758
2012-10-14 | 281788 | CMV9B | URBAN | Third party impacts | 1012 | 87 | 88044 | 0.088179 | 0.0010136
2012-10-14 | 281863 | MGL2A | RURAL | Other | 31 | 13 | 403 | 0.001156 | 8.892e-05
2012-10-14 | 281894 | NSW16A | URBAN | Animals | 49.5 | 45 | 2227.5 | 0.0022309 | 4.9576e-05
2012-10-15 | 281801 | PWC2 | RURAL | Vegetation | 126.5 | 29 | 3668.5 | 0.010523 | 0.00036285
2012-10-15 | 281848 | AHD10A | URBAN | Other | 13.783 | 92 | 1268.036 | 0.0012697 | 1.3801e-05
2012-10-15 | 281848 | AHD5 | URBAN | Other | 22.3755 | 92 | 2058.546 | 0.0020612 | 2.2404e-05
2012-10-15 | 281874 | WHO9 | RURAL | Equipment failure | 75.09 | 432.1698 | 34617.09 | 0.099294 | 0.00021538
2012-10-15 | 281876 | LLY5 | RURAL | Other | 29 | 41 | 1813.37 | 0.0052014 | 8.3182e-05
2012-10-15 | 281891 | BMT1 | RURAL | Other | 5 | 237 | 1185 | 0.003399 | 1.4342e-05
2012-10-15 | 281892 | AHD21 | URBAN | Equipment failure | 39 | 162 | 6318 | 0.006326 | 3.905e-05
2012-10-15 | 281893 | GYM7A | RURAL | Other | 3.96 | 199.2333 | 788.964 | 0.002263 | 1.1359e-05
2012-10-15 | 281898 | JDL7 | URBAN | Equipment failure | 25.41 | 129 | 3277.89 | 0.0032821 | 2.5442e-05
2012-10-16 | 281895 | HPK9 | URBAN | Other | 75.24 | 136 | 10232.64 | 0.010243 | 7.5316e-05
2012-10-16 | 281928 | IBL2 | RURAL | Other | 757.16 | 17 | 12871.72 | 0.03692 | 0.0021718
2012-10-16 | 281930 | AHD8 | URBAN | Animals | 1142.83 | 116.2727 | 138481.59 | 0.13862 | 0.001144
2012-10-16 | 281940 | HPK3A | URBAN | Animals | 39.8178 | 44 | 1751.9832 | 0.0017538 | 3.9858e-05
2012-10-16 | 281941 | MTB13A | RURAL | Equipment failure | 53.46 | 153 | 8179.38 | 0.023461 | 0.00015334
2012-10-16 | 282257 | YDA1B | RURAL | Other | 9 | 107 | 963 | 0.0027622 | 2.5815e-05
2012-10-17 | 282003 | NDH7 | URBAN | Equipment failure | 2.58 | 95 | 245.1 | 0.00024528 | 2.5819e-06
2012-10-17 | 282028 | VSL10A | URBAN | Third party impacts | 3.27 | 89 | 291.03 | 0.00029125 | 3.2725e-06
2012-10-17 | 282040 | ENG7 | URBAN | Animals | 107 | 26.5 | 2853.5 | 0.0028556 | 0.00010708
2012-10-17 | 282049 | KBN5A | RURAL | Equipment failure | 6 | 127 | 762 | 0.0021856 | 1.721e-05
2012-10-17 | 282051 | HIS5A | URBAN | Other | 9.24 | 56 | 517.44 | 0.00051783 | 9.247e-06
2012-10-17 | 282258 | EMD2 | RURAL | Equipment failure | 8.5 | 54 | 459 | 0.0013165 | 2.438e-05
2012-10-17 | 282259 | MLY1 | RURAL | Other | 1.98 | 70.6667 | 139.92 | 0.00040133 | 5.6792e-06
2012-10-17 | 282260 | CRY3A | RURAL | Animals | 37.62 | 94 | 3536.28 | 0.010143 | 0.0001079
2012-10-17 | 282261 | CLD2 | URBAN | Animals | 90.33 | 71.4 | 6449.562 | 0.0064544 | 9.0398e-05
2012-10-18 | 282046 | SFD10 | URBAN | Animals | 1343 | 63 | 84609 | 0.084651 | 0.0013437
2012-10-18 | 282048 | NSD2B | URBAN | Other | 546.83 | 56 | 30622.48 | 0.030638 | 0.0005471
2012-10-18 | 282082 | TWT11A | RURAL | Vegetation | 1432.99 | 49 | 70216.51 | 0.20139 | 0.0041101
2012-10-18 | 282093 | TWT12A | RURAL | Other | 88.5 | 102 | 9027 | 0.025891 | 0.00025384
2012-10-18 | 282122 | MDR30A | URBAN | Other | 1 | 40 | 40 | 4.002e-05 | 1.0005e-06
2012-10-18 | 282128 | CBT8A | RURAL | Equipment failure | 10.5 | 31 | 325.5 | 0.0009336 | 3.0116e-05
2012-10-18 | 282382 | BMG2A | URBAN | Equipment failure | 0.3 | 20 | 6 | 6.003e-06 | 3.0015e-07
2012-10-18 | 282525 | WFD1B | RURAL | Animals | 0.5 | 174 | 87 | 0.00024953 | 1.4341e-06
2012-10-18 | 282526 | ZMR10 | URBAN | Animals | 33.99 | 95 | 3229.05 | 0.0032306 | 3.4007e-05
2012-10-18 | 284872 | WSE5A | RURAL | Other | 3.33 | 179 | 596.07 | 0.0017096 | 9.5511e-06
2012-10-19 | 282127 | NRA15A | RURAL | Animals | 7.26 | 26 | 188.76 | 0.00054152 | 2.0828e-05
2012-10-19 | 282140 | ARL11A | URBAN | Other | 470 | 35 | 16450 | 0.016456 | 0.00047017
2012-10-19 | 282140 | SPO8A | URBAN | Other | 80.6 | 35 | 2821 | 0.002822 | 8.063e-05
2012-10-19 | 282144 | DRD3A | URBAN | Third party impacts | 126.8 | 155 | 19654 | 0.019661 | 0.00012685
2012-10-19 | 282162 | BRT8 | URBAN | Other | 16.5 | 96 | 1584 | 0.0015846 | 1.6506e-05
2012-10-19 | 282163 | BKD2B | URBAN | Other | 35.6 | 181.5 | 1608.675 | 0.0016093 | 3.5613e-05
2012-10-19 | 282178 | PWC6 | RURAL | Equipment failure | 31 | 55 | 1705 | 0.0048914 | 8.8934e-05
2012-10-19 | 282181 | MMC22A | URBAN | Equipment failure | 81 | 57 | 4617 | 0.0046187 | 8.103e-05
2012-10-19 | 282262 | NBR1 | RURAL | Animals | 14.52 | 92 | 1335.84 | 0.0038323 | 4.1656e-05
2012-10-19 | 282264 | GBN4 | RURAL | Animals | 6 | 64 | 384 | 0.0011016 | 1.7213e-05
2012-10-19 | 282505 | DRD15B | URBAN | Operational error | 129.5 | 77 | 9971.5 | 0.0099752 | 0.00012955
2012-10-19 | 283422 | NDH6 | URBAN | Other | 21.615 | 77 | 1664.355 | 0.001665 | 2.1623e-05
2012-10-20 | 282211 | RHG6 | URBAN | Equipment failure | 822 | 59 | 48498 | 0.04851 | 0.0008222
2012-10-20 | 282220 | RCN3A | URBAN | Equipment failure | 71 | 85.5 | 6674 | 0.0066757 | 7.1018e-05
2012-10-20 | 282220 | RCN8A | URBAN | Equipment failure | 19 | 162 | 3078 | 0.0030788 | 1.9005e-05
2012-10-20 | 282221 | TGW1 | RURAL | Weather | 66 | 88 | 5808 | 0.016666 | 0.00018939
2012-10-20 | 282222 | SBY4 | URBAN | Equipment failure | 12.9789 | 215 | 2790.4635 | 0.0027912 | 1.2982e-05
2012-10-20 | 282223 | HWL6A | URBAN | Third party impacts | 36.75 | 14 | 514.5 | 0.00051463 | 3.6759e-05
2012-10-20 | 282224 | GCLSBY7 | URBAN | Equipment failure | 418.44 | 125.2222 | 48262.16 | 0.048274 | 0.00041854
2012-10-20 | 282227 | SBY4 | URBAN | Equipment failure | 3.933 | 262 | 1030.446 | 0.0010307 | 3.934e-06
2012-10-20 | 282263 | LLY5 | RURAL | Operational error | 5 | 59 | 295 | 0.00084651 | 1.4348e-05
2012-10-20 | 282265 | LBH6A | RURAL | Equipment failure | 82.5 | 122 | 10065 | 0.028882 | 0.00023674
2012-10-21 | 282231 | BHL5A | URBAN | Animals | 1726.75 | 40 | 69070 | 0.069083 | 0.0017271
2012-10-21 | 282241 | GYM8A | RURAL | Equipment failure | 2217.5 | 50 | 110875 | 0.31821 | 0.0063641
2012-10-21 | 282241 | GYM8B | URBAN | Equipment failure | 454.66 | 68 | 30916.88 | 0.030922 | 0.00045474
2012-10-21 | 282246 | GYM7A | RURAL | Other | 87 | 132 | 11484 | 0.032958 | 0.00024969
2012-10-21 | 282252 | LBCVPK5 | URBAN | Equipment failure | 18.213 | 21 | 382.473 | 0.00038254 | 1.8216e-05
2012-10-21 | 282255 | RCF1A | URBAN | Animals | 1888 | 77.9565 | 156438 | 0.15647 | 0.0018883
2012-10-21 | 282266 | GYM8B | URBAN | Other | 82.5 | 39 | 3217.5 | 0.0032181 | 8.2515e-05
2012-10-21 | 282267 | WMD2A | URBAN | Vegetation | 96 | 67.1167 | 6443.2 | 0.0064444 | 9.6017e-05
2012-10-21 | 282268 | KBR1A | RURAL | Weather | 2.01 | 117 | 235.17 | 0.00067493 | 5.7686e-06
2012-10-21 | 282280 | NSW17 | URBAN | Equipment failure | 27.72 | 120 | 3326.4 | 0.003327 | 2.7725e-05
2012-10-21 | 282383 | KMR25A | RURAL | Other | 3.3 | 24 | 79.2 | 0.0002273 | 9.4708e-06
2012-10-22 | 282320 | ADAMAA1 | URBAN | Equipment failure | 25 | 78 | 1950 | 0.00195 | 2.5e-05
2012-10-22 | 282320 | ADAMLS23 | URBAN | Equipment failure | 16.5 | 78 | 1287 | 0.001287 | 1.65e-05
2012-10-22 | 282320 | ADATR1H | URBAN | Equipment failure | 1 | 78 | 78 | 7.8e-05 | 1e-06
2012-10-22 | 282320 | ADATR2H | URBAN | Equipment failure | 1 | 78 | 78 | 7.8e-05 | 1e-06
2012-10-22 | 282320 | GSNMLS6 | URBAN | Equipment failure | 13 | 77 | 1001 | 0.001001 | 1.3e-05
2012-10-22 | 282320 | MAATR1 | URBAN | Equipment failure | 1 | 78 | 78 | 7.8e-05 | 1e-06
2012-10-22 | 282320 | MLS6A | URBAN | Equipment failure | 562 | 77.8 | 43834 | 0.043834 | 0.000562
2012-10-22 | 282321 | PWC6 | RURAL | Third party impacts | 256 | 172.2941 | 31291 | 0.089831 | 0.00073494
2012-10-22 | 282328 | PPE16A | RURAL | Equipment failure | 378.75 | 76.9487 | 42099.75 | 0.12086 | 0.0010873
2012-10-22 | 282330 | TMH13A | URBAN | Equipment failure | 336 | 71.5556 | 17372 | 0.017372 | 0.000336
2012-10-22 | 282348 | RIS2 | URBAN | Vegetation | 659.34 | 127 | 83736.18 | 0.083736 | 0.00065934
2012-10-22 | 282349 | BMT3 | RURAL | Weather | 351 | 16 | 5616 | 0.016123 | 0.0010077
2012-10-22 | 282351 | AHD20 | URBAN | Animals | 1187 | 104.4706 | 127827 | 0.12783 | 0.001187
2012-10-22 | 282352 | HPE16A | URBAN | Equipment failure | 10.4624 | 299 | 3128.2576 | 0.0031283 | 1.0462e-05
2012-10-22 | 282353 | SIS2 | RURAL | Other | 211.5 | 585 | 123727.5 | 0.3552 | 0.00060718
2012-10-22 | 282354 | CRY3A | RURAL | Equipment failure | 80.67 | 90 | 7260.3 | 0.020843 | 0.00023159
2012-10-22 | 282480 | KWH2 | RURAL | Animals | 6.5 | 180 | 1170 | 0.0033589 | 1.866e-05
2012-10-22 | 282481 | AMR2 | RURAL | Other | 8 | 61.5667 | 492.5333 | 0.001414 | 2.2967e-05
2012-10-22 | 282482 | EMD3 | RURAL | Animals | 21.6678 | 107 | 2318.4546 | 0.0066559 | 6.2205e-05
2012-10-22 | 282503 | DRD15B | URBAN | Operational error | 129.5 | 61 | 7899.5 | 0.0078995 | 0.0001295
2012-10-22 | 282504 | DRD15B | URBAN | Operational error | 129.5 | 74 | 9583 | 0.009583 | 0.0001295
2012-10-22 | 282506 | LTN7 | URBAN | Other | 29 | 103 | 2987 | 0.002987 | 2.9e-05
2012-10-22 | 282882 | CMY1 | RURAL | Weather | 3.35 | 78 | 261.3 | 0.00075015 | 9.6173e-06
2012-10-22 | 283124 | HWL10A | URBAN | Other | 38.28 | 268 | 10259.04 | 0.010259 | 3.828e-05
2012-10-22 | 283183 | RLA7 | URBAN | Equipment failure | 9.24 | 192 | 1774.08 | 0.0017741 | 9.24e-06
2012-10-23 | 282355 | TWT15A | RURAL | Weather | 66.5 | 132 | 8778 | 0.025206 | 0.00019096
2012-10-23 | 282360 | SIS1 | RURAL | Weather | 25 | 53 | 1325 | 0.0038047 | 7.1788e-05
2012-10-23 | 282381 | NDH12 | URBAN | Animals | 106.4 | 5 | 532 | 0.00053193 | 0.00010639
2012-10-23 | 282384 | BDL4 | URBAN | Animals | 1725.49 | 125 | 215686.25 | 0.21566 | 0.0017253
2012-10-23 | 282402 | LBH1B | RURAL | Vegetation | 1 | 226 | 226 | 0.00064896 | 2.8715e-06
2012-10-23 | 282403 | MMC32A | URBAN | Other | 9.16 | 24 | 219.84 | 0.00021981 | 9.1589e-06
2012-10-23 | 282405 | BDL4 | URBAN | Animals | 1 | 244 | 244 | 0.00024397 | 9.9988e-07
2012-10-23 | 282431 | MFN15A | RURAL | Other | 8 | 12 | 96 | 0.00027566 | 2.2972e-05
2012-10-23 | 282431 | NGI3A | RURAL | Other | 32 | 12 | 384 | 0.0011027 | 9.1888e-05
2012-10-23 | 282462 | ARG9A | URBAN | Equipment failure | 12.075 | 99 | 1195.425 | 0.0011953 | 1.2074e-05
2012-10-23 | 282467 | BHD21A | URBAN | Equipment failure | 51.25 | 158.6667 | 9225 | 0.0092239 | 5.1244e-05
2012-10-23 | 282500 | MLB13A | URBAN | Equipment failure | 1491 | 101.4286 | 179218 | 0.1792 | 0.0014908
2012-10-23 | 282501 | BGY3A | URBAN | Other | 57 | 90 | 5130 | 0.0051294 | 5.6993e-05
2012-10-23 | 282502 | DBY4 | URBAN | Vegetation | 1 | 88 | 88 | 8.7989e-05 | 9.9988e-07
2012-10-23 | 283184 | CNB21B | URBAN | Animals | 128.25 | 150 | 19237.5 | 0.019235 | 0.00012823
2012-10-24 | 282520 | MLB13A | URBAN | Equipment failure | 129 | 202 | 26058 | 0.026052 | 0.00012897
2012-10-24 | 282521 | SBH6 | URBAN | Equipment failure | 91 | 26 | 2366 | 0.0023654 | 9.0977e-05
2012-10-24 | 282529 | MTB1B | RURAL | Other | 1243.33 | 50.5946 | 67059.58 | 0.19261 | 0.003571
2012-10-24 | 282536 | PPE6A | RURAL | Third party impacts | 11.75 | 203 | 2787.1 | 0.008005 | 3.3748e-05
2012-10-24 | 282566 | KBR1A | RURAL | Other | 115 | 39.5172 | 5259 | 0.015105 | 0.0003303
2012-10-24 | 282660 | ENG3 | URBAN | Third party impacts | 26.4 | 276 | 7286.4 | 0.0072846 | 2.6393e-05
2012-10-24 | 283229 | WSE3A | RURAL | Other | 3.3 | 68 | 224.4 | 0.00064451 | 9.4781e-06
2012-10-25 | 282602 | NBR10 | URBAN | Equipment failure | 20.4 | 34 | 693.6 | 0.00069334 | 2.0392e-05
2012-10-25 | 282635 | YTA1B | RURAL | Equipment failure | 49.5 | 19.1818 | 3409.5 | 0.0097949 | 0.00014221
2012-10-25 | 282760 | MLY3 | RURAL | Equipment failure | 89.5 | 94 | 8413 | 0.024169 | 0.00025712
2012-10-26 | 282661 | CMA8A | RURAL | Other | 24.5 | 10 | 245 | 0.00070401 | 7.0401e-05
2012-10-26 | 282666 | BBH16A | URBAN | Other | 0.67 | 35 | 23.45 | 2.3438e-05 | 6.6966e-07
2012-10-26 | 282667 | MLB3A | RURAL | Third party impacts | 2755 | 75.4 | 190671 | 0.5479 | 0.0079166
2012-10-26 | 282688 | MSV2 | RURAL | Equipment failure | 5 | 43 | 215 | 0.00061781 | 1.4368e-05
2012-10-26 | 282690 | BDT4 | RURAL | Animals | 35 | 253 | 8855 | 0.025445 | 0.00010057
2012-10-26 | 282704 | TMH15A | URBAN | Other | 1735.5 | 70 | 121485 | 0.12142 | 0.0017346
2012-10-26 | 282706 | CRY3A | RURAL | Other | 977.93 | 13.1852 | 9028.44 | 0.025943 | 0.0028101
2012-10-26 | 282761 | GYN6A | RURAL | Equipment failure | 23 | 99 | 2277 | 0.006543 | 6.6091e-05
2012-10-26 | 283185 | RIS2 | URBAN | Third party impacts | 44.88 | 170 | 7629.6 | 0.0076257 | 4.4857e-05
2012-10-26 | 283186 | WED16A | URBAN | Animals | 74.91 | 65 | 4869.15 | 0.0048667 | 7.4872e-05
2012-10-26 | 283228 | SMF3A | RURAL | Equipment failure | 4.29 | 100 | 429 | 0.0012327 | 1.2327e-05
2012-10-27 | 282710 | GBG27 | URBAN | Other | 1202.66 | 57 | 68551.62 | 0.068508 | 0.0012019
2012-10-27 | 282717 | CRY3A | RURAL | Equipment failure | 977.93 | 68.6852 | 59744.01 | 0.17172 | 0.0028108
2012-10-27 | 282725 | MDH5A | URBAN | Animals | 63 | 81 | 5072 | 0.0050688 | 6.296e-05
2012-10-27 | 282725 | MDH5B | URBAN | Animals | 43.33 | 15 | 649.95 | 0.00064953 | 4.3302e-05
2012-10-27 | 282726 | LLY3 | RURAL | Equipment failure | 140 | 117.0732 | 16256 | 0.046723 | 0.00040239
2012-10-27 | 282727 | RWD1 | RURAL | Weather | 4 | 157 | 628 | 0.001805 | 1.1497e-05
2012-10-27 | 282729 | SMF2A | RURAL | Weather | 929.99 | 41.05 | 41361.67 | 0.11888 | 0.002673
2012-10-27 | 282730 | KCY5 | RURAL | Equipment failure | 3 | 826 | 2478 | 0.0071223 | 8.6226e-06
2012-10-27 | 282736 | TGP6A | URBAN | Equipment failure | 21.42 | 56 | 1199.52 | 0.0011988 | 2.1406e-05
2012-10-27 | 282762 | PWC6 | RURAL | Animals | 3.3 | 98.55 | 325.215 | 0.00093473 | 9.4849e-06
2012-10-27 | 282763 | BMT4 | RURAL | Other | 18 | 110 | 1980 | 0.0056909 | 5.1736e-05
2012-10-27 | 282764 | GYM9B | RURAL | Equipment failure | 7 | 320 | 2240 | 0.0064382 | 2.0119e-05
2012-10-27 | 283226 | SMF2A | RURAL | Weather | 8.25 | 57 | 470.25 | 0.0013516 | 2.3712e-05
2012-10-27 | 283227 | WNM7A | URBAN | Other | 46.86 | 95 | 4451.7 | 0.0044488 | 4.683e-05
2012-10-27 | 283427 | BBH12B | URBAN | Equipment failure | 148.17 | 242 | 35857.14 | 0.035834 | 0.00014808
2012-10-28 | 282732 | LBH6A | RURAL | Other | 1698.95 | 63.9756 | 117286.38 | 0.33718 | 0.0048842
2012-10-28 | 282733 | TMH12A | URBAN | Other | 425.25 | 87 | 36996.75 | 0.03697 | 0.00042494
2012-10-28 | 282734 | CRY6A | RURAL | Other | 617.99 | 77.4065 | 44900.27 | 0.12908 | 0.0017766
2012-10-28 | 282735 | BMT2 | RURAL | Weather | 4 | 258 | 1032 | 0.0029668 | 1.1499e-05
2012-10-28 | 282737 | GTN13A | RURAL | Weather | 717.51 | 15 | 10762.65 | 0.030941 | 0.0020627
2012-10-28 | 282739 | LHM3 | URBAN | Equipment failure | 1735.16 | 136.8125 | 248547.76 | 0.24836 | 0.0017339
2012-10-28 | 282741 | RCF2A | URBAN | Equipment failure | 2131.41 | 49.9459 | 157351.12 | 0.15724 | 0.0021298
2012-10-28 | 282765 | GBN4 | RURAL | Vegetation | 18 | 68 | 1224 | 0.0035188 | 5.1747e-05
2012-10-28 | 282766 | GYM8B | URBAN | Operational error | 82.5 | 97 | 8002.5 | 0.0079966 | 8.2439e-05
2012-10-28 | 282767 | GYM8B | URBAN | Weather | 54.45 | 110 | 5989.5 | 0.0059851 | 5.441e-05
2012-10-28 | 282784 | MLT2B | URBAN | Equipment failure | 97.35 | 38 | 3699.3 | 0.0036966 | 9.7278e-05
2012-10-29 | 282768 | THL1 | RURAL | Equipment failure | 4.5 | 10 | 45 | 0.0001294 | 1.294e-05
2012-10-29 | 282769 | CRY5A | RURAL | Equipment failure | 96.49 | 189.8462 | 20529.73 | 0.059035 | 0.00027746
2012-10-29 | 282790 | GTN13A | RURAL | Equipment failure | 43.84 | 46 | 2016.64 | 0.005799 | 0.00012606
2012-10-29 | 282795 | 400 | URBAN | Other | 1 | 2 | 2 | 1.9982e-06 | 9.991e-07
2012-10-29 | 282795 | SIS1 | RURAL | Other | 1197 | 2 | 2394 | 0.0068841 | 0.0034421
2012-10-29 | 282795 | SIS2 | RURAL | Other | 1037 | 2 | 2074 | 0.0059639 | 0.002982
2012-10-29 | 282810 | LTN8 | RURAL | Equipment failure | 7 | 147 | 1029 | 0.002959 | 2.0129e-05
2012-10-29 | 282812 | NRG6 | URBAN | Equipment failure | 6.15 | 182 | 1119.3 | 0.0011183 | 6.1445e-06
2012-10-29 | 282818 | RST8A | URBAN | Animals | 60.635 | 86 | 5214.61 | 0.0052099 | 6.0581e-05
2012-10-29 | 282819 | GGR3 | RURAL | Other | 3 | 103 | 309 | 0.00088855 | 8.6267e-06
2012-10-29 | 282820 | FDS4 | RURAL | Other | 1 | 89 | 89 | 0.00025593 | 2.8756e-06
2012-10-29 | 283182 | WMD14A | RURAL | Other | 88.83 | 199 | 17677.17 | 0.050832 | 0.00025544
2012-10-29 | 283201 | CMV14 | URBAN | Other | 41 | 92 | 3772 | 0.0037686 | 4.0963e-05
2012-10-29 | 283225 | TGP9A | RURAL | Other | 27.5 | 135 | 3712.5 | 0.010676 | 7.9078e-05
2012-10-30 | 282851 | BKD5B | RURAL | Equipment failure | 701 | 8 | 5608 | 0.01613 | 0.0020162
2012-10-30 | 282900 | BTN3 | RURAL | Vegetation | 909.17 | 80 | 72733.6 | 0.2092 | 0.002615
2012-10-30 | 282931 | BGY15A | URBAN | Equipment failure | 80 | 48 | 3840 | 0.0038361 | 7.9918e-05
2012-10-30 | 282932 | TGP9A | RURAL | Equipment failure | 27.5 | 108 | 2970 | 0.0085424 | 7.9097e-05
2012-10-30 | 282934 | CBT8A | RURAL | Third party impacts | 184 | 97 | 17848 | 0.051335 | 0.00052923
2012-10-30 | 283180 | BMT1 | RURAL | Other | 5 | 128 | 640 | 0.0018408 | 1.4381e-05
2012-10-30 | 283181 | MLB13A | URBAN | Other | 23 | 82 | 1886 | 0.0018841 | 2.2977e-05
2012-10-31 | 282940 | EMP23A | URBAN | Equipment failure | 45.5 | 42 | 1911 | 0.001909 | 4.5452e-05
2012-10-31 | 282960 | KBR6A | RURAL | Equipment failure | 2.5 | 123 | 307.5 | 0.00088441 | 7.1903e-06
2012-10-31 | 283046 | AGT23A | URBAN | Animals | 1508.82 | 54 | 81476.28 | 0.08139 | 0.0015072
2012-10-31 | 283047 | KLG11A | URBAN | Equipment failure | 86 | 30 | 2580 | 0.0025773 | 8.5909e-05
2012-10-31 | 283048 | YTA22A | RURAL | Equipment failure | 34 | 76 | 2584 | 0.0074319 | 9.7788e-05
2012-10-31 | 283080 | BVL13A | URBAN | Weather | 41.91 | 173 | 7250.43 | 0.0072428 | 4.1866e-05
2012-10-31 | 283081 | CPD1 | RURAL | Weather | 1 | 102 | 102 | 0.00029336 | 2.8761e-06
2012-10-31 | 283082 | ESK5A | RURAL | Weather | 1 | 75 | 75 | 0.00021571 | 2.8761e-06
2012-10-31 | 283202 | MRK6 | URBAN | Animals | 99.66 | 54 | 5381.64 | 0.005376 | 9.9555e-05
2012-10-31 | 283223 | KLG11A | URBAN | Equipment failure | 86 | 79 | 6794 | 0.0067868 | 8.5909e-05
2012-10-31 | 283224 | CSE4 | URBAN | Third party impacts | 66.5 | 154 | 10241 | 0.01023 | 6.643e-05
2012-10-31 | 283382 | MGL2A | RURAL | Weather | 1.98 | 187 | 370.26 | 0.0010649 | 5.6947e-06
2012-11-01 | 283100 | NBR5 | RURAL | Vegetation | 135 | 110 | 14850 | 0.042708 | 0.00038825
2012-11-01 | 283101 | AHL15B | URBAN | Third party impacts | 1716.46 | 72 | 123585.12 | 0.12345 | 0.0017146
2012-11-01 | 283123 | PBH2B | URBAN | Equipment failure | 2298 | 40.2692 | 91391.93 | 0.091293 | 0.0022955
2012-11-01 | 283141 | QPT5 | URBAN | Other | 1025.5 | 5 | 5127.5 | 0.0051219 | 0.0010244
2012-11-01 | 283147 | SGT22A | URBAN | Equipment failure | 86 | 132 | 11352 | 0.01134 | 8.5907e-05
2012-11-01 | 283221 | CBW5 | URBAN | Equipment failure | 42.735 | 70 | 2991.45 | 0.0029882 | 4.2689e-05
2012-11-01 | 283276 | QGP4 | URBAN | Equipment failure | 12 | 86 | 1032 | 0.0010309 | 1.1987e-05
2012-11-01 | 283276 | WRD13B | URBAN | Equipment failure | 6.5 | 46 | 299 | 0.00029867 | 6.4929e-06
2012-11-01 | 283383 | AHL15B | URBAN | Third party impacts | 14 | 8 | 112 | 0.00011188 | 1.3985e-05
2012-11-02 | 283222 | HDN1 | RURAL | Weather | 624.16 | 43 | 26838.88 | 0.077205 | 0.0017955
2012-11-02 | 283232 | BRD11A | RURAL | Other | 62 | 102 | 6324 | 0.018192 | 0.00017835
2012-11-02 | 283233 | DBY4 | URBAN | Vegetation | 218.5 | 23 | 5025.5 | 0.0050195 | 0.00021824
2012-11-02 | 283235 | SGT3 | URBAN | Animals | 1 | 211 | 211 | 0.00021075 | 9.9881e-07
2012-11-02 | 283236 | TWT11A | RURAL | Weather | 208 | 61 | 12688 | 0.036498 | 0.00059833
2012-11-02 | 283268 | CBW6 | RURAL | Third party impacts | 2175.49 | 48.381 | 104743.52 | 0.30131 | 0.006258
2012-11-02 | 283269 | CBW13 | RURAL | Vegetation | 323 | 57.6905 | 35520 | 0.10218 | 0.00092914
2012-11-02 | 283270 | RLB13B | RURAL | Other | 9.5 | 1142 | 10849 | 0.031208 | 2.7328e-05
2012-11-02 | 283271 | NBR8 | RURAL | Vegetation | 23 | 97 | 2231 | 0.0064177 | 6.6162e-05
2012-11-02 | 283275 | 394 | URBAN | Equipment failure | 1 | 53 | 53 | 5.2937e-05 | 9.9881e-07
2012-11-02 | 283275 | CMA10A | RURAL | Equipment failure | 814 | 53 | 43142 | 0.1241 | 0.0023416
2012-11-02 | 283275 | CMA11A | URBAN | Equipment failure | 537 | 53 | 28461 | 0.028427 | 0.00053636
2012-11-02 | 283275 | CMA15A | URBAN | Equipment failure | 1694 | 53 | 89782 | 0.089675 | 0.001692
2012-11-02 | 283275 | CMA20A | URBAN | Equipment failure | 1336 | 53 | 70808 | 0.070724 | 0.0013344
2012-11-02 | 283275 | CMA8A | RURAL | Equipment failure | 1834.49 | 53 | 97227.97 | 0.27969 | 0.0052771
2012-11-02 | 283275 | CMA9A | URBAN | Equipment failure | 1299.5 | 53 | 68873.5 | 0.068791 | 0.001298
2012-11-02 | 283275 | CMA9B | URBAN | Equipment failure | 1 | 53 | 53 | 5.2937e-05 | 9.9881e-07
2012-11-02 | 283275 | HIS12A | URBAN | Equipment failure | 843 | 3 | 2529 | 0.002526 | 0.00084199
2012-11-02 | 283275 | HIS12B | URBAN | Equipment failure | 956 | 3 | 2868 | 0.0028646 | 0.00095486
2012-11-02 | 283275 | HIS13A | URBAN | Equipment failure | 576.5 | 3 | 1729.5 | 0.0017274 | 0.00057581
2012-11-02 | 283275 | HIS15B | URBAN | Equipment failure | 9 | 3 | 27 | 2.6968e-05 | 8.9893e-06
2012-11-02 | 283275 | HIS1B | URBAN | Equipment failure | 1048.5 | 3 | 3145.5 | 0.0031417 | 0.0010472
2012-11-02 | 283275 | HIS3A | URBAN | Equipment failure | 244.5 | 3 | 733.5 | 0.00073263 | 0.00024421
2012-11-02 | 283275 | HIS5A | URBAN | Equipment failure | 754 | 3 | 2262 | 0.0022593 | 0.0007531
2012-11-02 | 283275 | HIS5B | URBAN | Equipment failure | 871.5 | 3 | 2614.5 | 0.0026114 | 0.00087046
2012-11-02 | 283275 | HISSCV16 | URBAN | Equipment failure | 245.5 | 3 | 736.5 | 0.00073562 | 0.00024521
2012-11-02 | 283275 | HISSCV2 | URBAN | Equipment failure | 206.5 | 3 | 619.5 | 0.00061876 | 0.00020625
2012-11-02 | 283275 | PPE12A | URBAN | Equipment failure | 1 | 53 | 53 | 5.2937e-05 | 9.9881e-07
2012-11-02 | 283275 | PPE12B | RURAL | Equipment failure | 2.75 | 53 | 145.75 | 0.00041927 | 7.9107e-06
2012-11-02 | 283275 | PPE13A | RURAL | Equipment failure | 745.2 | 53 | 39495.6 | 0.11361 | 0.0021436
2012-11-02 | 283275 | PPE15A | URBAN | Equipment failure | 1.4 | 53 | 74.2 | 7.4112e-05 | 1.3983e-06
2012-11-02 | 283275 | PPE16A | RURAL | Equipment failure | 378.75 | 53 | 20073.75 | 0.057744 | 0.0010895
2012-11-02 | 283275 | PPE2A | URBAN | Equipment failure | 1 | 53 | 53 | 5.2937e-05 | 9.9881e-07
2012-11-02 | 283275 | PPE2B | URBAN | Equipment failure | 0.4 | 53 | 21.2 | 2.1175e-05 | 3.9952e-07
2012-11-02 | 283275 | PPE3A | RURAL | Equipment failure | 740 | 53 | 39220 | 0.11282 | 0.0021287
2012-11-02 | 283275 | PPE5A | RURAL | Equipment failure | 1651 | 53 | 87503 | 0.25171 | 0.0047493
2012-11-02 | 283275 | PPE6A | RURAL | Equipment failure | 501 | 53 | 26553 | 0.076383 | 0.0014412
2012-11-02 | 283275 | SCV4 | URBAN | Equipment failure | 389 | 3 | 1167 | 0.0011656 | 0.00038854
2012-11-02 | 283275 | SCV5 | URBAN | Equipment failure | 178 | 3 | 534 | 0.00053336 | 0.00017779
2012-11-02 | 283275 | SCV7 | URBAN | Equipment failure | 386 | 3 | 1158 | 0.0011566 | 0.00038554
2012-11-02 | 283301 | MCN1 | RURAL | Equipment failure | 95.49 | 117.5 | 10787.76 | 0.031032 | 0.00027469
2012-11-02 | 283560 | LGL3A | URBAN | Other | 33.165 | 61 | 2023.065 | 0.0020207 | 3.3125e-05
2012-11-03 | 283294 | CRB25A | RURAL | Other | 0.93 | 125 | 116.25 | 0.00033425 | 2.674e-06
2012-11-03 | 283300 | BWH16A | RURAL | Vegetation | 16 | 130 | 2080 | 0.0059806 | 4.6005e-05
2012-11-03 | 283303 | AHL4A | URBAN | Animals | 869.5 | 77.875 | 72800 | 0.072718 | 0.00086853
2012-11-03 | 283340 | CLD30A | URBAN | Animals | 155 | 61 | 9455 | 0.0094444 | 0.00015483
2012-11-03 | 283426 | BIS16A | URBAN | Other | 2.97 | 114 | 338.58 | 0.0003382 | 2.9667e-06
2012-11-03 | 283561 | BLHSTN16 | RURAL | Other | 11.55 | 74 | 854.7 | 0.0024575 | 3.321e-05
2012-11-03 | 283562 | HPE12A | URBAN | Animals | 78.8568 | 45 | 3548.556 | 0.0035446 | 7.8768e-05
2012-11-04 | 283310 | MHL3A | URBAN | Equipment failure | 1 | 97 | 97 | 9.6892e-05 | 9.9889e-07
2012-11-04 | 283312 | CPD1 | RURAL | Other | 31 | 67 | 4154 | 0.011943 | 8.9125e-05
2012-11-04 | 283328 | SMF2A | RURAL | Other | 9 | 142 | 1278 | 0.0036743 | 2.5875e-05
2012-11-04 | 283341 | CPD1 | RURAL | Other | 1 | 160 | 160 | 0.00046 | 2.875e-06
2012-11-04 | 283384 | CPC2A | RURAL | Other | 24.42 | 60 | 1465.2 | 0.0042125 | 7.0208e-05
2012-11-05 | 283390 | GBN4 | RURAL | Equipment failure | 9 | 41 | 369 | 0.0010602 | 2.5859e-05
2012-11-05 | 283403 | CPD1 | RURAL | Animals | 3 | 117 | 351 | 0.0010085 | 8.6195e-06
2012-11-05 | 283425 | F1173 | URBAN | Other | 11.22 | 72 | 807.84 | 0.00080705 | 1.1209e-05
2012-11-06 | 283428 | YTA22A | RURAL | Other | 1544 | 60 | 92640 | 0.26608 | 0.0044346
2012-11-06 | 283428 | YTA22B | RURAL | Other | 1073.25 | 60 | 64395 | 0.18495 | 0.0030825
2012-11-06 | 283452 | ALY6 | URBAN | Other | 1.33 | 61 | 81.13 | 8.1056e-05 | 1.3288e-06
2012-11-06 | 283455 | HPE13A | URBAN | Third party impacts | 30.3 | 360 | 10908 | 0.010898 | 3.0273e-05
2012-11-06 | 283461 | IBL2 | RURAL | Other | 7.5 | 96 | 720 | 0.002068 | 2.1541e-05
2012-11-06 | 283462 | CLD28A | RURAL | Third party impacts | 6 | 28 | 168 | 0.00048252 | 1.7233e-05
2012-11-06 | 283563 | YTA1B | RURAL | Equipment failure | 9.24 | 8 | 73.92 | 0.00021231 | 2.6539e-05
2012-11-07 | 283485 | IBL2 | RURAL | Equipment failure | 3 | 95 | 285 | 0.00081827 | 8.6134e-06
2012-11-07 | 283495 | 335 | URBAN | Equipment failure | 1 | 2 | 2 | 1.9983e-06 | 9.9916e-07
2012-11-07 | 283526 | RCF12A | URBAN | Other | 139.5 | 95 | 13252.5 | 0.013241 | 0.00013938
2012-11-07 | 283527 | GGR1 | RURAL | Other | 4.62 | 53 | 244.86 | 0.00070302 | 1.3265e-05
2012-11-07 | 283564 | ALY6 | URBAN | Animals | 71.5 | 66 | 4719 | 0.004715 | 7.144e-05
2012-11-08 | 283520 | THL1 | RURAL | Animals | 363.66 | 73 | 26547.18 | 0.076193 | 0.0010437
2012-11-08 | 283520 | THL2 | RURAL | Animals | 206.49 | 73 | 15073.77 | 0.043263 | 0.00059264
2012-11-08 | 283520 | THL3 | RURAL | Animals | 471.66 | 73 | 34431.18 | 0.098821 | 0.0013537
2012-11-08 | 283521 | LBH1B | RURAL | Equipment failure | 14.52 | 75 | 1089 | 0.0031255 | 4.1674e-05
2012-11-08 | 283524 | HDN1 | RURAL | Equipment failure | 624.16 | 65.0342 | 49908.7 | 0.14324 | 0.0017914
2012-11-08 | 283541 | MMC28A | URBAN | Equipment failure | 97.5 | 369.6667 | 46045.2 | 0.04601 | 9.7425e-05
2012-11-08 | 283565 | STT1B | RURAL | Other | 7.26 | 147 | 1067.22 | 0.003063 | 2.0837e-05
2012-11-08 | 283568 | OXL11A | URBAN | Third party impacts | 1493.16 | 91.8182 | 107127.88 | 0.10705 | 0.001492
2012-11-08 | 283575 | GBG27 | URBAN | Equipment failure | 1202.66 | 13 | 15634.58 | 0.015623 | 0.0012017
2012-11-08 | 283583 | GYM8A | RURAL | Third party impacts | 15 | 125 | 1875 | 0.0053814 | 4.3051e-05
2012-11-08 | 283590 | GYN3A | RURAL | Vegetation | 4.5 | 25 | 112.5 | 0.00032288 | 1.2915e-05
2012-11-08 | 283645 | SMR12A | URBAN | Equipment failure | 54.33 | 128 | 6954.24 | 0.0069489 | 5.4288e-05
2012-11-08 | 283764 | AMR2 | RURAL | Other | 8 | 75 | 600 | 0.0017221 | 2.2961e-05
2012-11-08 | 283981 | GBP6 | URBAN | Third party impacts | 101 | 114 | 11514 | 0.011505 | 0.00010092
2012-11-08 | 283982 | HPE5A | URBAN | Vegetation | 14.85 | 35 | 519.75 | 0.00051935 | 1.4839e-05
2012-11-09 | 283649 | FDS1 | RURAL | Equipment failure | 6 | 20 | 120 | 0.0003443 | 1.7215e-05
2012-11-09 | 283667 | AFD6 | URBAN | Equipment failure | 141 | 75 | 11074 | 0.011066 | 0.0001409
2012-11-09 | 283669 | KLG11A | URBAN | Equipment failure | 46.2 | 20 | 924 | 0.00092335 | 4.6167e-05
2012-11-09 | 283670 | CMD3A | RURAL | Equipment failure | 2495.99 | 85.2045 | 194635.11 | 0.55844 | 0.0071614
2012-11-09 | 283678 | GYS3A | RURAL | Animals | 435.99 | 136.7479 | 121537.31 | 0.34871 | 0.0012509
2012-11-09 | 283680 | SPD7B | URBAN | Equipment failure | 2.7864 | 103 | 286.9992 | 0.0002868 | 2.7844e-06
2012-11-09 | 283681 | TBV3 | RURAL | Weather | 377.5 | 146 | 55235 | 0.15848 | 0.0010831
2012-11-09 | 283765 | MLY6 | RURAL | Weather | 28.5 | 8 | 228 | 0.00065417 | 8.1771e-05
2012-11-09 | 283766 | PWC2 | RURAL | Equipment failure | 17.16 | 138 | 2368.08 | 0.0067944 | 4.9235e-05
2012-11-09 | 283768 | LLY5 | RURAL | Weather | 1 | 107 | 107 | 0.000307 | 2.8691e-06
2012-11-10 | 283685 | WNM5 | URBAN | Equipment failure | 2200.5 | 129.6154 | 283474.5 | 0.28329 | 0.0021991
2012-11-10 | 283686 | TGW4 | RURAL | Equipment failure | 16 | 75 | 1200 | 0.0034418 | 4.5891e-05
2012-11-10 | 283687 | VPT3A | RURAL | Other | 1508.17 | 115.2051 | 185848.6 | 0.53305 | 0.0043257
2012-11-10 | 283688 | TWG16 | URBAN | Weather | 383.83 | 48 | 18423.84 | 0.018412 | 0.00038358
2012-11-10 | 283689 | GGR1 | RURAL | Weather | 368.67 | 130.6512 | 42098.42 | 0.12075 | 0.0010574
2012-11-10 | 283691 | RIS1 | RURAL | Weather | 725.5 | 150.84 | 108984.5 | 0.31259 | 0.0020809
2012-11-10 | 283694 | WRG4A | URBAN | Equipment failure | 78 | 94 | 7332 | 0.0073273 | 7.795e-05
2012-11-10 | 283697 | IBL2 | RURAL | Other | 4 | 178 | 710 | 0.0020364 | 1.1473e-05
2012-11-10 | 283699 | CMD7A | RURAL | Equipment failure | 6 | 208 | 1248 | 0.0035795 | 1.7209e-05
2012-11-10 | 283700 | RIS4 | RURAL | Weather | 567 | 161 | 91287 | 0.26183 | 0.0016263
2012-11-10 | 283703 | RCF2A | URBAN | Equipment failure | 2131.41 | 110.3929 | 260653.53 | 0.26049 | 0.00213
2012-11-10 | 283705 | GBN4 | RURAL | Equipment failure | 832.96 | 176.7552 | 159558.97 | 0.45765 | 0.0023891
2012-11-10 | 283709 | CHL4 | URBAN | Equipment failure | 48.5 | 197 | 9554.5 | 0.0095483 | 4.8469e-05
2012-11-10 | 283710 | PBH8 | URBAN | Equipment failure | 19.05 | 7 | 133.35 | 0.00013326 | 1.9038e-05
2012-11-10 | 283769 | FDS1 | RURAL | Third party impacts | 4 | 89 | 356 | 0.0010211 | 1.1473e-05
2012-11-10 | 283770 | MBG1 | RURAL | Other | 1 | 46 | 46 | 0.00013194 | 2.8682e-06
2012-11-10 | 283771 | LDR10A | URBAN | Other | 32.8911 | 103 | 3387.7833 | 0.0033856 | 3.287e-05
2012-11-10 | 283772 | IPL1 | RURAL | Animals | 2.5 | 202 | 505 | 0.0014484 | 7.1705e-06
2012-11-10 | 283800 | HTN24A | URBAN | Other | 44.5 | 111 | 4939.5 | 0.0049363 | 4.4471e-05
2012-11-10 | 283837 | AHL6A | URBAN | Other | 39.4 | 236 | 9298.4 | 0.0092924 | 3.9375e-05
2012-11-10 | 283984 | UMG1B | URBAN | Equipment failure | 56.43 | 189 | 10665.27 | 0.010658 | 5.6394e-05
2012-11-10 | 283985 | RIS1 | RURAL | Other | 38.5 | 184 | 7084 | 0.020318 | 0.00011043
2012-11-11 | 283706 | MLY3 | RURAL | Weather | 138 | 136.7895 | 18260 | 0.052366 | 0.00039576
2012-11-11 | 283708 | RLA4 | URBAN | Animals | 477.5 | 59 | 28172.5 | 0.028155 | 0.0004772
2012-11-11 | 283721 | HPK3A | URBAN | Equipment failure | 60 | 40 | 2400 | 0.0023985 | 5.9962e-05
2012-11-11 | 283722 | BMT3 | RURAL | Weather | 13 | 76 | 988 | 0.0028334 | 3.7282e-05
2012-11-11 | 283723 | SIS1 | RURAL | Equipment failure | 1197 | 271.4545 | 334096 | 0.95813 | 0.0034328
2012-11-11 | 283727 | CVL5A | RURAL | Equipment failure | 1087.33 | 125.2727 | 139492.33 | 0.40004 | 0.0031183
2012-11-11 | 283729 | 375 | URBAN | Other | 1 | 24 | 24 | 2.3985e-05 | 9.9937e-07
2012-11-11 | 283729 | MCN1 | RURAL | Other | 95.49 | 24 | 2291.76 | 0.0065724 | 0.00027385
2012-11-11 | 283729 | MCN2 | RURAL | Other | 79.49 | 24 | 1907.76 | 0.0054711 | 0.00022796
2012-11-11 | 283729 | MCN3 | URBAN | Other | 54.16 | 20 | 2166.4 | 0.002165 | 5.4126e-05
2012-11-11 | 283729 | MCN4 | RURAL | Other | 701.33 | 22.5 | 31559.85 | 0.090508 | 0.0020113
2012-11-11 | 283729 | RLB16A | RURAL | Other | 137.66 | 155.8 | 20378.74 | 0.058443 | 0.00039478
2012-11-11 | 283730 | MRK8 | URBAN | Equipment failure | 5.7 | 89 | 507.3 | 0.00050698 | 5.6964e-06
2012-11-11 | 283731 | CLM6 | URBAN | Equipment failure | 1819.49 | 66.4722 | 119448.99 | 0.11937 | 0.0018183
2012-11-11 | 283733 | HDA13A | URBAN | Other | 308.16 | 364.3333 | 113122.99 | 0.11305 | 0.00030797
2012-11-11 | 283734 | ARG10 | URBAN | Equipment failure | 40.99 | 16.6774 | 1292.0108 | 0.0012912 | 4.0964e-05
2012-11-11 | 283738 | BHL2A | URBAN | Other | 6 | 134.3333 | 811 | 0.00081049 | 5.9962e-06
2012-11-11 | 283761 | BIS1 | RURAL | Equipment failure | 631.5 | 72.25 | 84544.5 | 0.24246 | 0.001811
2012-11-11 | 283767 | GYS3A | RURAL | Vegetation | 5 | 67 | 335 | 0.00096072 | 1.4339e-05
2012-11-11 | 283838 | TRG10B | URBAN | Equipment failure | 30.69 | 71 | 2178.99 | 0.0021776 | 3.0671e-05
2012-11-11 | 283988 | MTG15A | URBAN | Equipment failure | 34.2078 | 167 | 5712.7026 | 0.0057091 | 3.4186e-05
2012-11-12 | 283760 | HDA13A | URBAN | Equipment failure | 2 | 65 | 130 | 0.00012993 | 1.999e-06
2012-11-12 | 283781 | BMT3 | RURAL | Equipment failure | 58 | 64 | 3712 | 0.01064 | 0.00016625
2012-11-12 | 283782 | NDH9 | URBAN | Equipment failure | 0.4 | 39 | 15.6 | 1.5592e-05 | 3.9979e-07
2012-11-12 | 283801 | RCF2A | URBAN | Equipment failure | 124.5 | 70 | 8715 | 0.0087104 | 0.00012443
2012-11-12 | 283802 | PWC6 | RURAL | Equipment failure | 18 | 104 | 1872 | 0.0053657 | 5.1594e-05
2012-11-12 | 283805 | GBN4 | RURAL | Other | 7.33 | 17 | 124.61 | 0.00035717 | 2.101e-05
2012-11-12 | 283806 | MFD13A | RURAL | Equipment failure | 508 | 128.4211 | 54523 | 0.15628 | 0.0014561
2012-11-12 | 283823 | WRG6A | URBAN | Equipment failure | 13.65 | 125 | 1706.25 | 0.0017054 | 1.3643e-05
2012-11-12 | 283841 | NRG6 | URBAN | Other | 27.39 | 52 | 1424.28 | 0.0014235 | 2.7376e-05
2012-11-12 | 283861 | DRD5A | URBAN | Animals | 312 | 62 | 19344 | 0.019334 | 0.00031184
2012-11-12 | 283989 | ARG10 | URBAN | Equipment failure | 0.33 | 78 | 25.74 | 2.5727e-05 | 3.2983e-07
2012-11-12 | 283991 | CNB25A | URBAN | Other | 48.51 | 74 | 3589.74 | 0.0035879 | 4.8485e-05
2012-11-12 | 284176 | CLD17A | URBAN | Other | 74.83 | 64.7667 | 4846.4897 | 0.004844 | 7.4791e-05
2012-11-12 | 286274 | TMH5A | URBAN | Other | 34.98 | 161 | 5631.78 | 0.0056288 | 3.4962e-05
2012-11-12 | 286693 | NMC2A | RURAL | Other | 0.536 | 150 | 80.4 | 0.00023045 | 1.5363e-06
2012-11-13 | 283834 | SMF2A | RURAL | Other | 930.99 | 19.7 | 18616.81 | 0.053344 | 0.0026676
2012-11-13 | 283840 | SIS2 | RURAL | Equipment failure | 48 | 65 | 3120 | 0.00894 | 0.00013754
2012-11-13 | 283842 | MTB2A | RURAL | Equipment failure | 17.5 | 133 | 2327.5 | 0.0066692 | 5.0144e-05
2012-11-13 | 283860 | NIP5B | URBAN | Third party impacts | 78.5 | 107 | 4301.8 | 0.0042998 | 7.8464e-05
2012-11-13 | 283934 | CRY6A | RURAL | Equipment failure | 83.99 | 62 | 5207.38 | 0.014921 | 0.00024066
2012-11-13 | 283980 | AGE5B | URBAN | Equipment failure | 23.5 | 85 | 1997.5 | 0.0019966 | 2.3489e-05
2012-11-14 | 283940 | MAI14 | URBAN | Other | 1 | 11 | 11 | 1.0996e-05 | 9.9961e-07
2012-11-14 | 283961 | CMV9A | URBAN | Third party impacts | 5.5165 | 152 | 838.508 | 0.00083818 | 5.5143e-06
2012-11-14 | 283983 | MLY4 | RURAL | Equipment failure | 1 | 308 | 308 | 0.00088224 | 2.8644e-06
2012-11-14 | 283992 | BTA15A | URBAN | Other | 1234.25 | 16 | 19748 | 0.01974 | 0.0012338
2012-11-14 | 283993 | DBY4 | URBAN | Third party impacts | 212 | 142.8837 | 20226.03 | 0.020218 | 0.00021192
2012-11-14 | 284081 | ENG8 | URBAN | Animals | 88 | 126 | 11088 | 0.011084 | 8.7965e-05
2012-11-15 | 284020 | ENG8 | URBAN | Equipment failure | 110 | 98 | 10780 | 0.01078 | 0.00011
2012-11-15 | 284126 | NRA13A | RURAL | Third party impacts | 17.499 | 114 | 1994.886 | 0.0057149 | 5.0131e-05
2012-11-15 | 284169 | CLD11 | RURAL | Vegetation | 1325.67 | 85.5152 | 104745.86 | 0.30008 | 0.0037978
2012-11-15 | 284170 | LGV6A | RURAL | Equipment failure | 6.6 | 70 | 462 | 0.0013235 | 1.8908e-05
2012-11-15 | 284177 | AHD6 | URBAN | Equipment failure | 9 | 181 | 1629 | 0.001629 | 8.9998e-06
2012-11-15 | 284178 | RWD2 | RURAL | Equipment failure | 5.025 | 50 | 251.25 | 0.00071978 | 1.4396e-05
2012-11-15 | 284180 | ARL3A | URBAN | Third party impacts | 27.72 | 119 | 3298.68 | 0.0032986 | 2.7719e-05
2012-11-16 | 284181 | SMR9A | URBAN | Other | 3.2 | 144 | 460.8 | 0.00046096 | 3.2011e-06
2012-11-16 | 284184 | MRB1 | URBAN | Other | 1 | 2 | 2 | 2.0007e-06 | 1.0004e-06
2012-11-16 | 284223 | HPK8A | URBAN | Equipment failure | 12.7 | 36 | 457.2 | 0.00045736 | 1.2704e-05
2012-11-16 | 284792 | MAI11 | URBAN | Equipment failure | 67.65 | 66 | 4464.9 | 0.0044665 | 6.7674e-05
2012-11-16 | 284794 | MMC19B | URBAN | Equipment failure | 52.14 | 145 | 7560.3 | 0.007563 | 5.2158e-05
2012-11-17 | 284255 | PWC4 | RURAL | Animals | 18 | 116 | 2088 | 0.0059834 | 5.1581e-05
2012-11-17 | 284265 | WNM5 | URBAN | Weather | 2187.5 | 51 | 111562.5 | 0.11164 | 0.0021891
2012-11-17 | 284266 | VPK9A | URBAN | Weather | 567.33 | 258.1333 | 129670.66 | 0.12977 | 0.00056774
2012-11-17 | 284281 | GBP6 | URBAN | Weather | 732.33 | 133 | 97399.89 | 0.097471 | 0.00073287
2012-11-17 | 284284 | MTB15A | RURAL | Weather | 229.5 | 78.8293 | 37047 | 0.10616 | 0.00065766
2012-11-17 | 284287 | NIP1A | URBAN | Weather | 1340.83 | 112.12 | 163445.43 | 0.16356 | 0.0013418
2012-11-17 | 284289 | 355 | URBAN | Weather | 2 | 132 | 264 | 0.00026419 | 2.0015e-06
2012-11-17 | 284290 | HTN22A | URBAN | Weather | 307.5 | 137 | 42127.5 | 0.042158 | 0.00030772
2012-11-17 | 284290 | HTN22B | URBAN | Weather | 207 | 104 | 21528 | 0.021544 | 0.00020715
2012-11-17 | 284291 | CFD1A | URBAN | Other | 1695.33 | 209.45 | 346133.51 | 0.34639 | 0.0016966
2012-11-17 | 284293 | CFD6A | URBAN | Weather | 150 | 33 | 4950 | 0.0049536 | 0.00015011
2012-11-17 | 284298 | CFD6A | URBAN | Weather | 106.5 | 99 | 10543.5 | 0.010551 | 0.00010658
2012-11-17 | 284299 | HDA11A | URBAN | Weather | 1667.16 | 211.8667 | 361616.14 | 0.36188 | 0.0016684
2012-11-17 | 284300 | RST16A | URBAN | Equipment failure | 663.5 | 83 | 55070.5 | 0.055111 | 0.00066398
2012-11-17 | 284301 | HDA3A | URBAN | Weather | 763.5 | 137.75 | 104792 | 0.10487 | 0.00076406
2012-11-17 | 284302 | WRD20A | URBAN | Weather | 50.33 | 38 | 1912.54 | 0.0019139 | 5.0367e-05
2012-11-17 | 284303 | TAB3 | URBAN | Weather | 147.5 | 219 | 32302.5 | 0.032326 | 0.00014761
2012-11-17 | 284304 | TRP1 | RURAL | Weather | 738 | 117.8557 | 71157.35 | 0.20391 | 0.0021148
2012-11-17 | 284305 | NMK17A | URBAN | Weather | 100 | 36 | 3600 | 0.0036026 | 0.00010007
2012-11-17 | 284306 | HTN3B | URBAN | Weather | 764.5 | 216.0909 | 166184 | 0.16631 | 0.00076506
2012-11-17 | 284307 | IPS2A | URBAN | Weather | 1 | 157 | 157 | 0.00015711 | 1.0007e-06
2012-11-17 | 284307 | IPS2B | RURAL | Weather | 1274.17 | 157 | 200044.69 | 0.57325 | 0.0036513
2012-11-17 | 284308 | ENG8 | URBAN | Weather | 163.5 | 7 | 1144.5 | 0.0011453 | 0.00016362
2012-11-17 | 284309 | HMT9A | RURAL | Equipment failure | 192.99 | 223.5 | 42520.89 | 0.12185 | 0.00055304
2012-11-17 | 284310 | NSD9A | URBAN | Weather | 6.25 | 386 | 2412.5 | 0.0024143 | 6.2546e-06
2012-11-17 | 284311 | WED16A | URBAN | Weather | 20.867 | 102 | 2128.434 | 0.00213 | 2.0882e-05
2012-11-17 | 284312 | AGT37A | URBAN | Weather | 1518.96 | 237.9615 | 403753.95 | 0.40405 | 0.0015201
2012-11-17 | 284313 | CPL26A | URBAN | Weather | 331.94 | 49.1579 | 16388.06 | 0.0164 | 0.00033218
2012-11-17 | 284314 | TGP9A | RURAL | Weather | 1748.01 | 121.6607 | 230791.41 | 0.66136 | 0.0050091
2012-11-17 | 284331 | CPD2A | RURAL | Equipment failure | 220 | 149.6098 | 32824 | 0.094061 | 0.00063044
2012-11-17 | 284332 | 691 | URBAN | Weather | 1 | 430 | 430 | 0.00043031 | 1.0007e-06
2012-11-17 | 284332 | RCN10A | URBAN | Weather | 1502.27 | 86.4667 | 140708.23 | 0.14081 | 0.0015034
2012-11-17 | 284334 | TWG18 | URBAN | Equipment failure | 30.893 | 217 | 6703.781 | 0.0067087 | 3.0916e-05
2012-11-17 | 284335 | NSD2B | URBAN | Weather | 241.67 | 137 | 33108.79 | 0.033133 | 0.00024185
2012-11-17 | 284336 | BDT5 | RURAL | Equipment failure | 2 | 105 | 210 | 0.00060178 | 5.7313e-06
2012-11-17 | 284337 | MRB2 | RURAL | Weather | 52.6 | 327.5517 | 16969.4 | 0.048628 | 0.00015073
2012-11-17 | 284338 | GTN12A | RURAL | Weather | 571.66 | 5 | 2858.3 | 0.0081908 | 0.0016382
2012-11-17 | 284338 | GTN13A | RURAL | Weather | 714.51 | 5 | 3572.55 | 0.010238 | 0.0020475
2012-11-17 | 284338 | GTN15A | RURAL | Weather | 1149.95 | 5 | 5749.75 | 0.016477 | 0.0032953
2012-11-17 | 284338 | GTN1B | RURAL | Weather | 284 | 5 | 1420 | 0.0040692 | 0.00081384
2012-11-17 | 284338 | GTN2A | URBAN | Weather | 1 | 5 | 5 | 5.0037e-06 | 1.0007e-06
2012-11-17 | 284338 | GTN3A | URBAN | Weather | 1193.38 | 5 | 5966.9 | 0.0059713 | 0.0011943
2012-11-17 | 284338 | GTN3B | URBAN | Weather | 1 | 5 | 5 | 5.0037e-06 | 1.0007e-06
2012-11-17 | 284338 | GTN5B | RURAL | Weather | 157.15 | 5 | 785.75 | 0.0022517 | 0.00045033
2012-11-17 | 284338 | MSV1 | RURAL | Weather | 135 | 4 | 540 | 0.0015474 | 0.00038686
2012-11-17 | 284338 | MSV2 | RURAL | Weather | 168.01 | 4 | 672.04 | 0.0019258 | 0.00048145
2012-11-17 | 284338 | THL1 | RURAL | Weather | 347.66 | 4 | 1390.64 | 0.0039851 | 0.00099626
2012-11-17 | 284338 | THL2 | RURAL | Weather | 198.49 | 4 | 793.96 | 0.0022752 | 0.0005688
2012-11-17 | 284338 | THL3 | RURAL | Weather | 450.66 | 4 | 1802.64 | 0.0051657 | 0.0012914
2012-11-17 | 284340 | NIP6A | URBAN | Weather | 254.18 | 51 | 12963.18 | 0.012973 | 0.00025437
2012-11-17 | 284340 | NIP6B | URBAN | Weather | 1 | 51 | 51 | 5.1037e-05 | 1.0007e-06
2012-11-17 | 284341 | TWG17 | URBAN | Weather | 1860.1 | 86 | 159968.6 | 0.16009 | 0.0018615
2012-11-17 | 284342 | BHL2A | URBAN | Weather | 721.5 | 55 | 39682.5 | 0.039712 | 0.00072203
2012-11-17 | 284342 | BHL4A | URBAN | Weather | 1395.99 | 28 | 39087.72 | 0.039116 | 0.001397
2012-11-17 | 284342 | BHL5A | URBAN | Weather | 1793.75 | 28 | 50225 | 0.050262 | 0.0017951
2012-11-17 | 284343 | GTN15A | RURAL | Other | 1149.95 | 51 | 58647.45 | 0.16806 | 0.0032953
2012-11-17 | 284344 | LTN2 | RURAL | Operational error | 1680.99 | 63 | 105902.37 | 0.30348 | 0.0048171
2012-11-17 | 284344 | LTN3 | URBAN | Operational error | 1651.84 | 63 | 104065.92 | 0.10414 | 0.001653
2012-11-17 | 284344 | LTN4 | URBAN | Operational error | 1546.67 | 63 | 97440.21 | 0.097511 | 0.0015478
2012-11-17 | 284344 | LTN5 | URBAN | Operational error | 838.16 | 63 | 52804.08 | 0.052843 | 0.00083877
2012-11-17 | 284344 | LTN6 | URBAN | Operational error | 1444.99 | 63 | 91034.37 | 0.091101 | 0.001446
2012-11-17 | 284344 | LTN7 | URBAN | Operational error | 573.5 | 63 | 36130.5 | 0.036157 | 0.00057392
2012-11-17 | 284344 | LTN8 | RURAL | Operational error | 598.33 | 63 | 37694.79 | 0.10802 | 0.0017146
2012-11-17 | 284344 | LTN9 | URBAN | Operational error | 1411 | 63 | 88893 | 0.088958 | 0.001412
2012-11-17 | 284346 | GTN5B | RURAL | Other | 157.15 | 101 | 15872.15 | 0.045484 | 0.00045033
2012-11-17 | 284350 | BVL3A | URBAN | Equipment failure | 1217.33 | 89.3182 | 162674.56 | 0.16279 | 0.0012182
2012-11-17 | 284353 | GTN12A | RURAL | Equipment failure | 571.66 | 168.2333 | 106897.46 | 0.30633 | 0.0016382
2012-11-17 | 284354 | TGP5B | URBAN | Equipment failure | 1519.41 | 73.8043 | 180454.18 | 0.18059 | 0.0015205
2012-11-17 | 284355 | RST5A | URBAN | Weather | 208.035 | 23 | 4784.805 | 0.0047883 | 0.00020819
2012-11-17 | 284355 | RST8A | URBAN | Weather | 94.135 | 23 | 2165.105 | 0.0021667 | 9.4204e-05
2012-11-17 | 284359 | CMY1 | RURAL | Weather | 112.48 | 280 | 31494.4 | 0.090251 | 0.00032233
2012-11-17 | 284360 | GGR2 | RURAL | Weather | 142.65 | 109 | 15548.85 | 0.044557 | 0.00040878
2012-11-17 | 284361 | KCY5 | RURAL | Weather | 111 | 112 | 12432 | 0.035626 | 0.00031808
2012-11-17 | 284362 | WSE5A | RURAL | Equipment failure | 91 | 207.8611 | 18899 | 0.054158 | 0.00026077
2012-11-17 | 284363 | YTA22A | RURAL | Other | 1524 | 63 | 96012 | 0.27513 | 0.0043672
2012-11-17 | 284363 | YTA22B | RURAL | Other | 1056.25 | 63 | 66543.75 | 0.19069 | 0.0030268
2012-11-17 | 284364 | CMY3 | URBAN | Equipment failure | 2 | 484.5 | 1938 | 0.0019394 | 2.0015e-06
2012-11-17 | 284365 | SMR15A | URBAN | Weather | 1401.33 | 128.7778 | 163438.05 | 0.16356 | 0.0014024
2012-11-17 | 284367 | DRA1A | URBAN | Weather | 375.5 | 158.2 | 80645.5 | 0.080704 | 0.00037577
2012-11-17 | 284368 | HPE5A | URBAN | Weather | 170.5 | 256 | 43648 | 0.04368 | 0.00017062
2012-11-17 | 284368 | HPK11 | RURAL | Weather | 194 | 115 | 22310 | 0.063932 | 0.00055593
2012-11-17 | 284370 | BDT1 | RURAL | Other | 468.47 | 109 | 51063.23 | 0.14633 | 0.0013425
2012-11-17 | 284378 | HPE12A | URBAN | Weather | 1453.83 | 3 | 4361.49 | 0.0043647 | 0.0014549
2012-11-17 | 284378 | HPE13A | URBAN | Weather | 1701 | 3 | 5103 | 0.0051067 | 0.0017022
2012-11-17 | 284378 | HPE16A | URBAN | Weather | 1743.63 | 286.7692 | 483580.32 | 0.48393 | 0.0017449
2012-11-17 | 284379 | IBS1 | RURAL | Weather | 260.5 | 266.625 | 68045.5 | 0.19499 | 0.0007465
2012-11-17 | 284383 | MTG16A | URBAN | Weather | 135.67 | 363 | 49248.21 | 0.049284 | 0.00013577
2012-11-17 | 284383 | MTG7A | URBAN | Weather | 1642.82 | 137.1667 | 231180.96 | 0.23135 | 0.001644
2012-11-17 | 284384 | 1129 | URBAN | Weather | 342.5 | 111 | 38017.5 | 0.038045 | 0.00034275
2012-11-17 | 284385 | RPN2A | URBAN | Weather | 1319.49 | 30 | 39584.7 | 0.039614 | 0.0013205
2012-11-17 | 284386 | AMR1 | RURAL | Weather | 20.5 | 283 | 5801.5 | 0.016625 | 5.8745e-05
2012-11-17 | 284388 | RPN2A | URBAN | Weather | 1319.49 | 113.1818 | 139969.46 | 0.14007 | 0.0013205
2012-11-17 | 284390 | HPE3A | URBAN | Weather | 1845.24 | 393.24 | 725402.44 | 0.72593 | 0.0018466
2012-11-17 | 284390 | MTG8A | URBAN | Weather | 100.83 | 72 | 7259.76 | 0.0072651 | 0.0001009
2012-11-17 | 284393 | NRG16A | RURAL | Weather | 17.5 | 550 | 9625 | 0.027582 | 5.0149e-05
2012-11-17 | 284395 | LRE6A | RURAL | Weather | 102.5 | 642 | 65805 | 0.18857 | 0.00029373
2012-11-17 | 284401 | INA1A | URBAN | Equipment failure | 762 | 16.5882 | 12417 | 0.012426 | 0.00076256
2012-11-17 | 284408 | NSW35A | URBAN | Weather | 281 | 169.6923 | 47915 | 0.04795 | 0.00028121
2012-11-17 | 284420 | LRE4A | RURAL | Weather | 324.49 | 233.9459 | 75825.3 | 0.21729 | 0.00092987
2012-11-17 | 284434 | 383 | URBAN | Weather | 1 | 549 | 549 | 0.0005494 | 1.0007e-06
2012-11-17 | 284434 | LWD1 | RURAL | Weather | 615 | 549 | 337635 | 0.96754 | 0.0017624
2012-11-17 | 284434 | TRP4 | RURAL | Weather | 95.5 | 291.3846 | 27470 | 0.078719 | 0.00027367
2012-11-17 | 284434 | WHO1 | RURAL | Weather | 530 | 549 | 290970 | 0.83381 | 0.0015188
2012-11-17 | 284434 | WHO2 | RURAL | Weather | 822.5 | 549 | 451552.5 | 1.294 | 0.002357
2012-11-17 | 284434 | WHO9 | RURAL | Weather | 75.09 | 549 | 41224.41 | 0.11813 | 0.00021518
2012-11-17 | 284518 | CFD2A | URBAN | Weather | 611 | 43 | 26273 | 0.026292 | 0.00061145
2012-11-17 | 284599 | BMT1 | RURAL | Equipment failure | 1.98 | 99.7667 | 197.538 | 0.00056607 | 5.6739e-06
2012-11-17 | 284611 | BSEENG15 | URBAN | Animals | 125.73 | 97 | 12195.81 | 0.012205 | 0.00012582
2012-11-17 | 284612 | NMK17A | URBAN | Vegetation | 66 | 188 | 12408 | 0.012417 | 6.6048e-05
2012-11-17 | 284613 | AGE4B | URBAN | Vegetation | 53.13 | 208 | 11051.04 | 0.011059 | 5.3169e-05
2012-11-17 | 284614 | TWG18 | URBAN | Vegetation | 60.72 | 208 | 12629.76 | 0.012639 | 6.0764e-05
2012-11-17 | 284615 | CGT1 | URBAN | Other | 2.64 | 92 | 242.88 | 0.00024306 | 2.6419e-06
2012-11-17 | 284617 | THL1 | RURAL | Weather | 3 | 40 | 170.7 | 0.00048916 | 8.5969e-06
2012-11-17 | 284620 | LLY3 | RURAL | Weather | 2.01 | 736 | 1479.36 | 0.0042393 | 5.7599e-06
2012-11-17 | 284622 | OXL8B | URBAN | Weather | 46.53 | 202 | 9399.06 | 0.0094059 | 4.6564e-05
2012-11-17 | 284624 | LLY1 | RURAL | Weather | 2.68 | 182 | 487.76 | 0.0013977 | 7.6799e-06
2012-11-17 | 284627 | RST16A | URBAN | Weather | 29.48 | 220 | 6485.6 | 0.0064903 | 2.9502e-05
2012-11-17 | 284629 | MBG4 | RURAL | Weather | 1 | 134 | 134 | 0.00038399 | 2.8656e-06
2012-11-17 | 284631 | LRE8A | RURAL | Weather | 34 | 1604 | 54536 | 0.15628 | 9.7431e-05
2012-11-17 | 284635 | IPS1B | URBAN | Weather | 15.5 | 161 | 2495.5 | 0.0024973 | 1.5511e-05
2012-11-17 | 284636 | RST8A | URBAN | Weather | 29.04 | 34 | 987.36 | 0.00098808 | 2.9061e-05
2012-11-17 | 284637 | KBN5A | RURAL | Weather | 2.31 | 33 | 76.23 | 0.00021845 | 6.6196e-06
2012-11-17 | 284641 | MBG4 | RURAL | Weather | 4.355 | 384 | 1672.32 | 0.0047922 | 1.248e-05
2012-11-17 | 284643 | KBN1B | RURAL | Weather | 12 | 98 | 1176 | 0.00337 | 3.4388e-05
2012-11-17 | 284646 | LWD1 | RURAL | Weather | 0.67 | 139 | 93.13 | 0.00026688 | 1.92e-06
2012-11-17 | 284647 | TGW2 | RURAL | Weather | 1 | 119 | 119 | 0.00034101 | 2.8656e-06
2012-11-17 | 284648 | ESK5A | RURAL | Weather | 1 | 48 | 48 | 0.00013755 | 2.8656e-06
2012-11-17 | 284666 | CMY4 | RURAL | Weather | 6.6 | 227 | 1498.2 | 0.0042933 | 1.8913e-05
2012-11-17 | 284720 | SIS2 | RURAL | Other | 31.02 | 620 | 19232.4 | 0.055113 | 8.8892e-05
2012-11-17 | 284721 | WRD25B | URBAN | Weather | 69.3 | 118 | 8177.4 | 0.0081834 | 6.9351e-05
2012-11-17 | 284722 | BBS11 | URBAN | Equipment failure | 60.72 | 154 | 9350.88 | 0.0093577 | 6.0764e-05
2012-11-17 | 284723 | LTA4B | URBAN | Weather | 22.11 | 289 | 6389.79 | 0.0063945 | 2.2126e-05
2012-11-17 | 284725 | SIS2 | RURAL | Weather | 11.22 | 265 | 2973.3 | 0.0085204 | 3.2152e-05
2012-11-17 | 284738 | BNH1B | RURAL | Weather | 2 | 91 | 182 | 0.00052154 | 5.7313e-06
2012-11-17 | 284739 | FDS1 | RURAL | Weather | 1 | 61 | 61 | 0.0001748 | 2.8656e-06
2012-11-17 | 284742 | BNH6A | RURAL | Weather | 1 | 145 | 145 | 0.00041552 | 2.8656e-06
2012-11-17 | 284759 | MFD13A | RURAL | Equipment failure | 12.5 | 289 | 3612.5 | 0.010352 | 3.582e-05
2012-11-17 | 284761 | HTN24A | URBAN | Weather | 44.5 | 181 | 8054.5 | 0.0080604 | 4.4533e-05
2012-11-17 | 284762 | HTN24A | URBAN | Weather | 79 | 197 | 15563 | 0.015574 | 7.9058e-05
2012-11-17 | 284798 | GGR4 | RURAL | Weather | 6 | 844 | 5064 | 0.014512 | 1.7194e-05
2012-11-17 | 284838 | BDB37A | RURAL | Weather | 16 | 330 | 5280 | 0.015131 | 4.585e-05
2012-11-17 | 284839 | BNH6A | RURAL | Weather | 1 | 251 | 251 | 0.00071927 | 2.8656e-06
2012-11-17 | 284840 | TRP1 | RURAL | Weather | 3 | 133 | 399 | 0.0011434 | 8.5969e-06
2012-11-17 | 284867 | MBG4 | RURAL | Weather | 1 | 1620 | 1620 | 0.0046423 | 2.8656e-06
2012-11-17 | 285161 | SIS2 | RURAL | Weather | 4 | 39 | 156 | 0.00044704 | 1.1463e-05
2012-11-17 | 285840 | LRE6A | RURAL | Weather | 18.76 | 510 | 9567.6 | 0.027417 | 5.3759e-05
2012-11-17 | 285843 | CPD1 | RURAL | Weather | 3 | 1114 | 3342 | 0.0095769 | 8.5969e-06
2012-11-17 | 286282 | WRG19A | URBAN | Other | 45.54 | 809 | 36841.86 | 0.036869 | 4.5573e-05
2012-11-18 | 284358 | OXL8B | URBAN | Weather | 70.5 | 93 | 6556.5 | 0.0065618 | 7.0557e-05
2012-11-18 | 284374 | ACR2A | URBAN | Weather | 1240.5 | 40 | 99240 | 0.09932 | 0.0012415
2012-11-18 | 284374 | ACR2B | URBAN | Weather | 1461.5 | 40 | 116920 | 0.11701 | 0.0014627
2012-11-18 | 284380 | CVL7A | RURAL | Other | 1747.31 | 46.4301 | 79266.44 | 0.22711 | 0.0050064
2012-11-18 | 284382 | SMF3A | RURAL | Weather | 179 | 178.6333 | 69719 | 0.19976 | 0.00051287
2012-11-18 | 284387 | GGR4 | RURAL | Equipment failure | 230 | 123.4706 | 25906 | 0.074226 | 0.000659
2012-11-18 | 284389 | AMR1 | RURAL | Weather | 5.5 | 44 | 242 | 0.00069338 | 1.5759e-05
2012-11-18 | 284391 | WRG4A | URBAN | Equipment failure | 69 | 21 | 1449 | 0.0014502 | 6.9056e-05
2012-11-18 | 284418 | 1129 | URBAN | Weather | 35.5 | 73 | 2591.5 | 0.0025936 | 3.5529e-05
2012-11-18 | 284435 | RCF2A | URBAN | Equipment failure | 2122.91 | 113.3214 | 234451.7 | 0.23464 | 0.0021246
2012-11-18 | 284445 | MCW11 | RURAL | Equipment failure | 238 | 26 | 6188 | 0.01773 | 0.00068192
2012-11-18 | 284461 | LTN4 | URBAN | Equipment failure | 17.25 | 40 | 690 | 0.00069056 | 1.7264e-05
2012-11-18 | 284463 | ENG2 | URBAN | Equipment failure | 66 | 238 | 15708 | 0.015721 | 6.6053e-05
2012-11-18 | 284464 | NIP4A | RURAL | Equipment failure | 7 | 75 | 525 | 0.0015042 | 2.0056e-05
2012-11-18 | 284475 | MGP13A | RURAL | Equipment failure | 97 | 159.3158 | 18046 | 0.051705 | 0.00027792
2012-11-18 | 284479 | RPN2A | URBAN | Equipment failure | 80 | 90 | 7200 | 0.0072058 | 8.0065e-05
2012-11-18 | 284483 | THL3 | RURAL | Equipment failure | 89.82 | 35 | 3143.7 | 0.0090073 | 0.00025735
2012-11-18 | 284486 | KWH3 | RURAL | Weather | 10.99 | 152 | 1670.48 | 0.0047863 | 3.1489e-05
2012-11-18 | 284487 | ACR4 | URBAN | Equipment failure | 6.6 | 92 | 607.2 | 0.00060769 | 6.6053e-06
2012-11-18 | 284489 | TWG13A | URBAN | Equipment failure | 26.235 | 252 | 6611.22 | 0.0066166 | 2.6256e-05
2012-11-18 | 284490 | MFN13A | RURAL | Weather | 1648.5 | 44 | 72534 | 0.20782 | 0.0047233
2012-11-18 | 284492 | MRB2 | RURAL | Weather | 52.6 | 174.2069 | 9120.8 | 0.026133 | 0.00015071
2012-11-18 | 284493 | QPT5 | URBAN | Animals | 80.735 | 76 | 6135.86 | 0.0061408 | 8.08e-05
2012-11-18 | 284495 | TRP2 | RURAL | Weather | 57.66 | 117 | 6746.22 | 0.019329 | 0.00016521
2012-11-18 | 284497 | LTN7 | URBAN | Weather | 573.5 | 39 | 22366.5 | 0.022385 | 0.00057396
2012-11-18 | 284498 | SDM3 | RURAL | Weather | 14 | 257 | 3598 | 0.010309 | 4.0113e-05
2012-11-18 | 284499 | MDH9A | URBAN | Weather | 49.6 | 123.1111 | 5256.8 | 0.005261 | 4.964e-05
2012-11-18 | 284499 | MDH9B | URBAN | Weather | 1 | 77 | 77 | 7.7062e-05 | 1.0008e-06
2012-11-18 | 284500 | SHW4 | URBAN | Weather | 487.83 | 94 | 45856.02 | 0.045893 | 0.00048822
2012-11-18 | 284501 | WSE5A | RURAL | Weather | 694.74 | 23 | 15979.02 | 0.045783 | 0.0019906
2012-11-18 | 284502 | MGL9 | RURAL | Weather | 390 | 209.5385 | 84620 | 0.24245 | 0.0011174
2012-11-18 | 284503 | AGE3 | URBAN | Weather | 2119 | 169.4545 | 362118.5 | 0.36241 | 0.0021207
2012-11-18 | 284504 | WCL19A | RURAL | Weather | 795 | 184.1739 | 116563.5 | 0.33398 | 0.0022778
2012-11-18 | 284505 | CPK9 | RURAL | Weather | 146 | 214 | 31244 | 0.08952 | 0.00041832
2012-11-18 | 284506 | DBS16A | URBAN | Equipment failure | 57.28 | 16 | 916.48 | 0.00091722 | 5.7326e-05
2012-11-18 | 284507 | GLY6 | URBAN | Weather | 1999.66 | 160 | 319945.6 | 0.3202 | 0.0020013
2012-11-18 | 284508 | SMR12A | URBAN | Weather | 1176.33 | 105 | 123514.65 | 0.12361 | 0.0011773
2012-11-18 | 284508 | SMR12B | URBAN | Weather | 89 | 145.5 | 12809.5 | 0.01282 | 8.9072e-05
2012-11-18 | 284509 | AGE9 | URBAN | Weather | 1436.83 | 86.7895 | 127948.79 | 0.12805 | 0.001438
2012-11-18 | 284510 | IDY1A | URBAN | Weather | 1106.16 | 151.8571 | 164488.74 | 0.16462 | 0.0011071
2012-11-18 | 284511 | MRK5A | URBAN | Equipment failure | 85.75 | 226 | 19379.5 | 0.019395 | 8.5819e-05
2012-11-18 | 284512 | NBR4 | RURAL | Weather | 463 | 86.4167 | 36179 | 0.10366 | 0.0013266
2012-11-18 | 284513 | WSE5A | RURAL | Weather | 65.33 | 239 | 15613.87 | 0.044737 | 0.00018718
2012-11-18 | 284514 | AGE9 | URBAN | Weather | 13.208 | 123 | 1624.584 | 0.0016259 | 1.3219e-05
2012-11-18 | 284515 | IDY10A | URBAN | Equipment failure | 57 | 195 | 11115 | 0.011124 | 5.7046e-05
2012-11-18 | 284554 | WRG8A | URBAN | Equipment failure | 55 | 133 | 7315 | 0.0073209 | 5.5044e-05
2012-11-18 | 284588 | MLB6A | RURAL | Weather | 41 | 83 | 3403 | 0.0097503 | 0.00011747
2012-11-18 | 284591 | NBR1 | RURAL | Weather | 1442.83 | 87 | 125526.21 | 0.35966 | 0.004134
2012-11-18 | 284598 | BWH13A | RURAL | Weather | 649.51 | 75.1944 | 36860.05 | 0.10561 | 0.001861
2012-11-18 | 284600 | AMR1 | RURAL | Weather | 7 | 49 | 343 | 0.00098276 | 2.0056e-05
2012-11-18 | 284601 | PWC2 | RURAL | Other | 6.5 | 130 | 845 | 0.0024211 | 1.8624e-05
2012-11-18 | 284602 | AHD10A | URBAN | Equipment failure | 111.67 | 175 | 19542.25 | 0.019558 | 0.00011176
2012-11-18 | 284603 | PWC4 | RURAL | Weather | 2.5 | 239 | 597.5 | 0.001712 | 7.163e-06
2012-11-18 | 284623 | AHL12A | URBAN | Weather | 49.5 | 53 | 2623.5 | 0.0026256 | 4.954e-05
2012-11-18 | 284630 | AGT31A | RURAL | Equipment failure | 7.26 | 451 | 3274.26 | 0.0093814 | 2.0801e-05
2012-11-18 | 284726 | 1129 | URBAN | Weather | 35.5 | 383 | 13596.5 | 0.013607 | 3.5529e-05
2012-11-18 | 284727 | MCN2 | RURAL | Third party impacts | 3.96 | 26 | 102.96 | 0.000295 | 1.1346e-05
2012-11-18 | 284728 | NSW35A | URBAN | Weather | 22.77 | 27 | 614.79 | 0.00061529 | 2.2788e-05
2012-11-18 | 284729 | NSW35A | URBAN | Weather | 54.5 | 152 | 8284 | 0.0082907 | 5.4544e-05
2012-11-18 | 284730 | MRK5A | URBAN | Equipment failure | 127 | 306 | 38862 | 0.038893 | 0.0001271
2012-11-18 | 284744 | WSE3A | RURAL | Weather | 10.89 | 81 | 882.09 | 0.0025274 | 3.1202e-05
2012-11-18 | 284749 | MFD3A | RURAL | Weather | 33 | 72 | 2376 | 0.0068077 | 9.4552e-05
2012-11-18 | 284750 | KLG10A | URBAN | Weather | 1 | 259 | 259 | 0.00025921 | 1.0008e-06
2012-11-18 | 284751 | WSE5A | RURAL | Weather | 1.98 | 187 | 370.26 | 0.0010609 | 5.6731e-06
2012-11-18 | 284753 | WSE5A | RURAL | Weather | 0.66 | 146 | 96.36 | 0.00027609 | 1.891e-06
2012-11-18 | 284756 | WSE6A | RURAL | Weather | 6 | 100 | 600 | 0.0017191 | 1.7191e-05
2012-11-18 | 284757 | WSE6A | RURAL | Weather | 8.58 | 196 | 1681.68 | 0.0048183 | 2.4583e-05
2012-11-18 | 284758 | WSE3A | RURAL | Weather | 4.62 | 48 | 221.76 | 0.00063539 | 1.3237e-05
2012-11-18 | 284784 | NIP4A | RURAL | Weather | 100 | 875 | 87500 | 0.2507 | 0.00028652
2012-11-18 | 284841 | MCW11 | RURAL | Weather | 11 | 598 | 6578 | 0.018847 | 3.1517e-05
2012-11-18 | 284842 | MBG4 | RURAL | Weather | 6.7 | 312 | 2090.4 | 0.0059894 | 1.9197e-05
2012-11-18 | 284843 | MBG4 | RURAL | Weather | 0.4489 | 382 | 171.4798 | 0.00049132 | 1.2862e-06
2012-11-18 | 284860 | MBG4 | RURAL | Weather | 1 | 76 | 76 | 0.00021776 | 2.8652e-06
2012-11-18 | 284861 | HDN1 | RURAL | Weather | 8.71 | 129 | 1123.59 | 0.0032193 | 2.4956e-05
2012-11-18 | 284862 | SPC2B | RURAL | Weather | 0.5 | 90 | 45 | 0.00012893 | 1.4326e-06
2012-11-18 | 284863 | RPN6A | RURAL | Weather | 79.6161 | 163 | 12977.4243 | 0.037183 | 0.00022812
2012-11-18 | 284864 | MBG4 | RURAL | Weather | 5.8089 | 209 | 1214.0601 | 0.0034785 | 1.6644e-05
2012-11-18 | 284865 | SPC2B | RURAL | Weather | 16.5 | 635 | 10477.5 | 0.03002 | 4.7276e-05
2012-11-18 | 284881 | KBN1B | RURAL | Weather | 7 | 237 | 1659 | 0.0047534 | 2.0056e-05
2012-11-18 | 284882 | KBN5A | RURAL | Weather | 6 | 297 | 1782 | 0.0051058 | 1.7191e-05
2012-11-18 | 284883 | MBG1 | RURAL | Weather | 2.5 | 228 | 570 | 0.0016332 | 7.163e-06
2012-11-18 | 284884 | IPS5B | URBAN | Weather | 102 | 125 | 12750 | 0.01276 | 0.00010208
2012-11-18 | 284885 | GGR1 | RURAL | Weather | 0.335 | 30 | 10.05 | 2.8795e-05 | 9.5984e-07
2012-11-18 | 284889 | GGR1 | RURAL | Weather | 7.035 | 38 | 267.33 | 0.00076595 | 2.0157e-05
2012-11-18 | 285026 | LRE6A | RURAL | Weather | 2.01 | 80 | 160.8 | 0.00046072 | 5.759e-06
2012-11-18 | 285027 | BNH6A | RURAL | Weather | 1 | 117 | 117 | 0.00033523 | 2.8652e-06
2012-11-18 | 285028 | FDS1 | RURAL | Weather | 1.32 | 51 | 67.32 | 0.00019289 | 3.7821e-06
2012-11-18 | 285029 | BNH1B | RURAL | Weather | 4 | 104 | 416 | 0.0011919 | 1.1461e-05
2012-11-18 | 285030 | KBR3A | RURAL | Weather | 1 | 123 | 123 | 0.00035242 | 2.8652e-06
2012-11-18 | 285031 | TGW1 | RURAL | Weather | 1.675 | 352 | 589.6 | 0.0016893 | 4.7992e-06
2012-11-18 | 285032 | LWD1 | RURAL | Weather | 0.67 | 252 | 168.84 | 0.00048376 | 1.9197e-06
2012-11-18 | 285033 | WHO1 | RURAL | Weather | 6.03 | 36 | 217.08 | 0.00062198 | 1.7277e-05
2012-11-18 | 285034 | WHO1 | RURAL | Weather | 6 | 361 | 2166 | 0.006206 | 1.7191e-05
2012-11-18 | 285035 | ESK3A | RURAL | Weather | 5 | 99 | 495 | 0.0014183 | 1.4326e-05
2012-11-18 | 285036 | LRE6A | RURAL | Equipment failure | 18.76 | 312 | 5853.12 | 0.01677 | 5.3751e-05
2012-11-18 | 285044 | SMF3A | RURAL | Weather | 0.66 | 606 | 399.96 | 0.001146 | 1.891e-06
2012-11-18 | 285045 | IDY10A | URBAN | Weather | 75.24 | 311 | 23399.64 | 0.023419 | 7.5301e-05
2012-11-18 | 285047 | AGE9 | URBAN | Weather | 132.08 | 266 | 35133.28 | 0.035162 | 0.00013219
2012-11-18 | 285052 | TRP3 | RURAL | Weather | 2.01 | 357 | 717.57 | 0.002056 | 5.759e-06
2012-11-18 | 285160 | LRE6A | RURAL | Weather | 1 | 405 | 405 | 0.0011604 | 2.8652e-06
2012-11-18 | 285180 | NIP5A | URBAN | Weather | 26.13 | 96 | 2508.48 | 0.0025105 | 2.6151e-05
2012-11-18 | 285181 | MCW11 | RURAL | Weather | 2.01 | 90 | 180.9 | 0.00051831 | 5.759e-06
2012-11-18 | 285182 | RBK9A | URBAN | Weather | 31.515 | 184 | 5798.76 | 0.0058034 | 3.154e-05
2012-11-18 | 285183 | LLY4 | RURAL | Weather | 3.35 | 101 | 338.35 | 0.00096944 | 9.5984e-06
2012-11-18 | 285184 | CPD2A | RURAL | Weather | 6.03 | 198 | 1193.94 | 0.0034209 | 1.7277e-05
2012-11-18 | 285185 | CPD2A | RURAL | Weather | 3.35 | 610 | 2043.5 | 0.005855 | 9.5984e-06
2012-11-18 | 285186 | GGR1 | RURAL | Weather | 1 | 498 | 498 | 0.0014269 | 2.8652e-06
2012-11-18 | 285187 | THL3 | RURAL | Weather | 6 | 420 | 2520 | 0.0072203 | 1.7191e-05
2012-11-18 | 285188 | GGR4 | RURAL | Weather | 39 | 214 | 8346 | 0.023913 | 0.00011174
2012-11-18 | 285193 | TRP3 | RURAL | Weather | 1 | 136 | 136 | 0.00038967 | 2.8652e-06
2012-11-18 | 285194 | MBG4 | RURAL | Weather | 1.34 | 71 | 95.14 | 0.00027259 | 3.8394e-06
2012-11-18 | 285196 | GTN15A | RURAL | Weather | 1 | 304 | 304 | 0.00087102 | 2.8652e-06
2012-11-18 | 285240 | GGR3 | RURAL | Weather | 2.68 | 107 | 286.76 | 0.00082162 | 7.6787e-06
2012-11-18 | 285241 | GTN13A | RURAL | Weather | 2.01 | 227 | 456.27 | 0.0013073 | 5.759e-06
2012-11-18 | 285267 | TGW2 | RURAL | Weather | 0.67 | 557 | 373.19 | 0.0010693 | 1.9197e-06
2012-11-18 | 285280 | GGR3 | RURAL | Weather | 2.01 | 380 | 763.8 | 0.0021884 | 5.759e-06
2012-11-18 | 285281 | GGR1 | RURAL | Weather | 1.7889 | 388 | 694.0932 | 0.0019887 | 5.1256e-06
2012-11-18 | 285282 | MBG4 | RURAL | Weather | 1 | 345 | 345 | 0.00098849 | 2.8652e-06
2012-11-18 | 285283 | CPK9 | RURAL | Weather | 92 | 296 | 27232 | 0.078025 | 0.0002636
2012-11-18 | 285384 | CRM15A | URBAN | Other | 20.8 | 169 | 3515.2 | 0.003518 | 2.0817e-05
2012-11-18 | 286218 | CPK9 | RURAL | Other | 146 | 201 | 29346 | 0.084082 | 0.00041832
2012-11-19 | 284516 | NIP4A | RURAL | Equipment failure | 1509.35 | 71.8333 | 101263.31 | 0.29026 | 0.0043264
2012-11-19 | 284517 | SHW4 | URBAN | Weather | 6.75 | 34 | 229.5 | 0.00022984 | 6.76e-06
2012-11-19 | 284519 | SMF3A | RURAL | Weather | 161 | 63 | 10143 | 0.029074 | 0.00046149
2012-11-19 | 284667 | MRK9 | URBAN | Equipment failure | 309.09 | 7 | 2163.63 | 0.0021668 | 0.00030955
2012-11-19 | 284668 | VSL11A | URBAN | Other | 141 | 67 | 9447 | 0.009461 | 0.00014121
2012-11-19 | 284668 | VSL13A | URBAN | Other | 2144.99 | 56.4167 | 123140.04 | 0.12332 | 0.0021482
2012-11-19 | 284669 | NBR1 | RURAL | Equipment failure | 68.4 | 30 | 2052 | 0.0058818 | 0.00019606
2012-11-19 | 284670 | LRE6A | RURAL | Equipment failure | 4.02 | 224 | 900.48 | 0.0025811 | 1.1523e-05
2012-11-19 | 284672 | SHW4 | URBAN | Equipment failure | 487.83 | 143.4444 | 67339.96 | 0.06744 | 0.00048855
2012-11-19 | 284675 | MDRMLD11 | URBAN | Equipment failure | 40 | 10 | 400 | 0.00040059 | 4.0059e-05
2012-11-19 | 284676 | ENG8 | URBAN | Other | 76.065 | 69 | 5248.485 | 0.0052563 | 7.6178e-05
2012-11-19 | 284677 | SPE1 | URBAN | Equipment failure | 204.16 | 2 | 408.32 | 0.00040892 | 0.00020446
2012-11-19 | 284677 | SPE22A | URBAN | Equipment failure | 293.5 | 2 | 587 | 0.00058787 | 0.00029393
2012-11-19 | 284678 | SFD3 | URBAN | Equipment failure | 1171.17 | 80.2273 | 92222.53 | 0.092359 | 0.0011729
2012-11-19 | 284680 | SDM3 | RURAL | Equipment failure | 196 | 2 | 392 | 0.0011236 | 0.00056181
2012-11-19 | 284681 | LTN7 | URBAN | Equipment failure | 573.5 | 69.72 | 43805 | 0.04387 | 0.00057435
2012-11-19 | 284701 | HMT3A | URBAN | Other | 121 | 159.75 | 13165 | 0.013184 | 0.00012118
2012-11-19 | 284702 | BMT5 | RURAL | Other | 4 | 10 | 40 | 0.00011466 | 1.1466e-05
2012-11-19 | 284703 | MLY6 | RURAL | Equipment failure | 272.49 | 135.1212 | 27131.67 | 0.07777 | 0.00078106
2012-11-19 | 284704 | WNM7A | URBAN | Equipment failure | 35 | 5 | 175 | 0.00017526 | 3.5052e-05
2012-11-19 | 284724 | AGE3 | URBAN | Equipment failure | 308.5 | 153 | 47200.5 | 0.04727 | 0.00030896
2012-11-19 | 284731 | FCHQPT2 | URBAN | Other | 18.48 | 47 | 868.56 | 0.00086985 | 1.8507e-05
2012-11-19 | 284732 | ALY5 | URBAN | Equipment failure | 122.5 | 227 | 27807.5 | 0.027849 | 0.00012268
2012-11-19 | 284733 | BPN26A | RURAL | Equipment failure | 26 | 175 | 4550 | 0.013042 | 7.4526e-05
2012-11-19 | 284740 | ZMR10 | URBAN | Equipment failure | 53.79 | 68 | 3657.72 | 0.0036631 | 5.387e-05
2012-11-19 | 284754 | WFD5A | RURAL | Other | 9.24 | 125 | 1155 | 0.0033107 | 2.6486e-05
2012-11-19 | 284799 | SHW10A | URBAN | Other | 29.7 | 191 | 5672.7 | 0.0056811 | 2.9744e-05
2012-11-19 | 285020 | NBR9 | RURAL | Weather | 16 | 21 | 336 | 0.00096311 | 4.5862e-05
2012-11-19 | 285284 | GGR1 | RURAL | Weather | 3.35 | 144 | 482.4 | 0.0013828 | 9.6024e-06
2012-11-19 | 285380 | LRE6A | RURAL | Weather | 6 | 373 | 2238 | 0.006415 | 1.7198e-05
2012-11-19 | 285381 | SPC2B | RURAL | Weather | 2.33 | 126 | 293.58 | 0.00084152 | 6.6787e-06
2012-11-19 | 285382 | LLY3 | RURAL | Weather | 1 | 254 | 254 | 0.00072807 | 2.8664e-06
2012-11-19 | 285403 | HDN1 | RURAL | Weather | 2.68 | 198 | 530.64 | 0.001521 | 7.6819e-06
2012-11-19 | 285404 | FDS4 | RURAL | Weather | 3 | 126 | 378 | 0.0010835 | 8.5992e-06
2012-11-19 | 285406 | TGW2 | RURAL | Weather | 4 | 365 | 1460 | 0.0041849 | 1.1466e-05
2012-11-20 | 284760 | HTN22A | URBAN | Equipment failure | 308.5 | 53.475 | 39169.5 | 0.039242 | 0.00030907
2012-11-20 | 284760 | HTN22B | URBAN | Equipment failure | 207 | 31 | 6417 | 0.0064289 | 0.00020738
2012-11-20 | 284760 | HTN3B | URBAN | Equipment failure | 764.5 | 6 | 4587 | 0.0045955 | 0.00076592
2012-11-20 | 284768 | IBL2 | RURAL | Equipment failure | 8 | 105 | 840 | 0.0024081 | 2.2934e-05
2012-11-20 | 284780 | QEN10 | URBAN | Other | 52.14 | 11 | 573.54 | 0.0005746 | 5.2237e-05
2012-11-20 | 284822 | GYM9B | RURAL | Vegetation | 17 | 76 | 1292 | 0.0037039 | 4.8736e-05
2012-11-20 | 284830 | VPT1B | URBAN | Vegetation | 647.99 | 161 | 104326.39 | 0.10452 | 0.00064919
2012-11-20 | 284831 | BRD8A | RURAL | Other | 44 | 48 | 2112 | 0.0060547 | 0.00012614
2012-11-20 | 284888 | KLG11A | URBAN | Equipment failure | 56.76 | 60 | 3405.6 | 0.0034119 | 5.6865e-05
2012-11-20 | 285386 | SIS2 | RURAL | Equipment failure | 15.51 | 242 | 3753.42 | 0.01076 | 4.4464e-05
2012-11-20 | 285387 | FCHQPT2 | URBAN | Equipment failure | 28 | 325 | 9100 | 0.0091169 | 2.8052e-05
2012-11-20 | 285388 | WRG4A | URBAN | Other | 83.49 | 76 | 6345.24 | 0.006357 | 8.3645e-05
2012-11-20 | 285420 | CNA7A | RURAL | Weather | 0.67 | 161 | 107.87 | 0.00030924 | 1.9208e-06
2012-11-20 | 285421 | NIP1A | URBAN | Animals | 19.2 | 93.6833 | 1798.72 | 0.0018021 | 1.9236e-05
2012-11-20 | 285422 | KBN5A | RURAL | Equipment failure | 4 | 441 | 1764 | 0.005057 | 1.1467e-05
2012-11-20 | 285841 | GYM7A | RURAL | Other | 7.2 | 56 | 403.2 | 0.0011559 | 2.0641e-05
2012-11-21 | 284834 | TGP2A | URBAN | Other | 1262.08 | 18 | 22717.44 | 0.022768 | 0.0012649
2012-11-21 | 284834 | TGP3A | URBAN | Other | 588 | 16 | 9408 | 0.009429 | 0.00058931
2012-11-21 | 284834 | TGP5B | URBAN | Other | 1519.41 | 3 | 4558.23 | 0.0045684 | 0.0015228
2012-11-21 | 284834 | TGP6A | URBAN | Other | 2010.57 | 25 | 50264.25 | 0.050376 | 0.0020151
2012-11-21 | 284834 | TGP8A | URBAN | Other | 831.5 | 14 | 11641 | 0.011667 | 0.00083336
2012-11-21 | 284834 | TGP9A | RURAL | Other | 1749.01 | 6 | 10494.06 | 0.030089 | 0.0050148
2012-11-21 | 284837 | LGL13A | URBAN | Third party impacts | 523 | 221.0909 | 120036.5 | 0.1203 | 0.00052417
2012-11-21 | 284922 | CPD2A | RURAL | Weather | 8 | 11 | 88 | 0.00025231 | 2.2938e-05
2012-11-21 | 285041 | DRA5 | URBAN | Other | 14.025 | 153 | 2145.825 | 0.0021506 | 1.4056e-05
2012-11-21 | 285043 | IDY1A | URBAN | Other | 62.9178 | 49 | 3082.9722 | 0.0030899 | 6.3058e-05
2012-11-21 | 285389 | SBY6 | URBAN | Animals | 34.0494 | 49 | 1668.4206 | 0.0016721 | 3.4125e-05
2012-11-21 | 285424 | HDN1 | RURAL | Other | 3 | 213 | 639 | 0.0018321 | 8.6016e-06
2012-11-21 | 285500 | MSV1 | RURAL | Animals | 1 | 1475 | 1475 | 0.0042291 | 2.8672e-06
2012-11-21 | 285501 | HDN1 | RURAL | Weather | 0.67 | 126 | 84.42 | 0.00024205 | 1.921e-06
2012-11-21 | 285502 | CPD2A | RURAL | Animals | 1 | 189 | 189 | 0.0005419 | 2.8672e-06
2012-11-22 | 284942 | SSSWHI2 | URBAN | Equipment failure | 4 | 52 | 208 | 0.00020854 | 4.0104e-06
2012-11-22 | 284942 | WHITR1H | URBAN | Equipment failure | 82.33 | 37 | 3046.21 | 0.0030542 | 8.2545e-05
2012-11-22 | 284942 | WHITR2H | URBAN | Equipment failure | 186.67 | 37 | 6906.79 | 0.0069248 | 0.00018716
2012-11-22 | 284962 | RBA43A | RURAL | Equipment failure | 1012.83 | 47.0638 | 59430.1966 | 0.17042 | 0.0029044
2012-11-22 | 284965 | MLY1 | RURAL | Equipment failure | 90.5 | 175 | 24351.74 | 0.069831 | 0.00025952
2012-11-22 | 284968 | FDS1 | RURAL | Third party impacts | 2 | 83 | 166 | 0.00047602 | 5.7352e-06
2012-11-22 | 284980 | FDS1 | RURAL | Equipment failure | 49 | 73 | 3577 | 0.010257 | 0.00014051
2012-11-22 | 285013 | MDR33A | URBAN | Other | 85 | 44 | 3740 | 0.0037498 | 8.5222e-05
2012-11-22 | 285021 | TWT3A | RURAL | Vegetation | 13 | 99.5667 | 1294.3667 | 0.0037117 | 3.7279e-05
2012-11-22 | 285022 | BMT1 | RURAL | Animals | 6 | 166 | 996 | 0.0028561 | 1.7206e-05
2012-11-22 | 285024 | NRG16A | RURAL | Vegetation | 72 | 56 | 4032 | 0.011562 | 0.00020647
2012-11-22 | 285190 | DRA6 | URBAN | Animals | 56.5 | 159 | 8983.5 | 0.0090069 | 5.6647e-05
2012-11-22 | 285390 | LGL5A | URBAN | Third party impacts | 22.77 | 92 | 2094.84 | 0.0021003 | 2.2829e-05
2012-11-22 | 285391 | BLH12A | RURAL | Other | 8.91 | 152 | 1354.32 | 0.0038836 | 2.555e-05
2012-11-22 | 285503 | CPD2A | RURAL | Weather | 3 | 61 | 183 | 0.00052477 | 8.6028e-06
2012-11-22 | 285504 | CPD2A | RURAL | Weather | 6.03 | 33 | 198.99 | 0.00057062 | 1.7292e-05
2012-11-22 | 285505 | GGR1 | RURAL | Weather | 6.7 | 84 | 562.8 | 0.0016139 | 1.9213e-05
2012-11-22 | 285506 | BVL2A | URBAN | Other | 105.86 | 64 | 6775.04 | 0.0067927 | 0.00010614
2012-11-22 | 288264 | MMC22A | URBAN | Other | 8.1 | 377 | 3053.7 | 0.0030617 | 8.1211e-06
2012-11-23 | 285025 | CCYUPC17 | URBAN | Equipment failure | 1 | 7 | 7 | 7.0209e-06 | 1.003e-06
2012-11-23 | 285025 | CCYUPC23 | URBAN | Equipment failure | 528.5 | 34 | 17969 | 0.018023 | 0.00053008
2012-11-23 | 285025 | UPC2 | RURAL | Equipment failure | 369.34 | 17 | 6278.78 | 0.018008 | 0.0010593
2012-11-23 | 285039 | TRG3 | URBAN | Equipment failure | 772.67 | 99.6667 | 63436.78 | 0.063626 | 0.00077498
2012-11-23 | 285053 | LLY4 | RURAL | Equipment failure | 5.94 | 60 | 356.4 | 0.0010222 | 1.7036e-05
2012-11-23 | 285076 | WRG19A | URBAN | Equipment failure | 412 | 71 | 29252 | 0.029339 | 0.00041323
2012-11-23 | 285085 | GYS3A | RURAL | Equipment failure | 55 | 294 | 16170 | 0.046375 | 0.00015774
2012-11-23 | 285086 | LGL5A | URBAN | Equipment failure | 0.66 | 152 | 100.32 | 0.00010062 | 6.6197e-07
2012-11-23 | 285087 | SPE5 | URBAN | Equipment failure | 16.25 | 85 | 1381.25 | 0.0013854 | 1.6299e-05
2012-11-23 | 285088 | NBR9 | RURAL | Equipment failure | 10.72 | 39 | 418.08 | 0.0011991 | 3.0745e-05
2012-11-23 | 285089 | KBN5A | RURAL | Equipment failure | 90.5 | 49 | 4434.5 | 0.012718 | 0.00025955
2012-11-23 | 285092 | TWG21 | URBAN | Other | 922.33 | 19 | 17524.27 | 0.017577 | 0.00092509
2012-11-23 | 285093 | LGL5A | URBAN | Equipment failure | 1 | 28 | 28 | 2.8084e-05 | 1.003e-06
2012-11-23 | 285507 | GGR1 | RURAL | Weather | 5.33 | 112 | 596.96 | 0.0017121 | 1.5286e-05
2012-11-23 | 285508 | TGW2 | RURAL | Weather | 2.5 | 131 | 327.5 | 0.00093927 | 7.17e-06
2012-11-24 | 285100 | THL1 | RURAL | Other | 4.69 | 51 | 239.19 | 0.00068608 | 1.3453e-05
2012-11-24 | 285101 | CNB24A | RURAL | Animals | 3 | 208 | 624 | 0.0017899 | 8.6051e-06
2012-11-24 | 285103 | CCY1B | URBAN | Equipment failure | 3.35 | 83 | 278.05 | 0.00027899 | 3.3613e-06
2012-11-24 | 285104 | MRE3 | URBAN | Third party impacts | 8.085 | 137 | 1107.645 | 0.0011114 | 8.1123e-06
2012-11-24 | 285108 | LLY3 | RURAL | Equipment failure | 5 | 46 | 230 | 0.00065972 | 1.4342e-05
2012-11-24 | 285110 | LHM3 | URBAN | Equipment failure | 1712.16 | 94.8158 | 205380.99 | 0.20607 | 0.0017179
2012-11-24 | 285111 | KLG4A | URBAN | Third party impacts | 1851.49 | 18.122 | 35988.39 | 0.03611 | 0.0018577
2012-11-24 | 285116 | NVL12A | URBAN | Animals | 103.18 | 236 | 24350.48 | 0.024433 | 0.00010353
2012-11-24 | 285124 | WED6A | URBAN | Third party impacts | 2343.77 | 99.6667 | 251901.32 | 0.25275 | 0.0023517
2012-11-24 | 285520 | TGW3 | RURAL | Weather | 1 | 152 | 152 | 0.00043599 | 2.8684e-06
2012-11-25 | 285115 | SMR9A | URBAN | Animals | 46 | 80 | 3680 | 0.0036931 | 4.6164e-05
2012-11-25 | 285117 | LLY1 | RURAL | Animals | 570.48 | 119 | 67887.12 | 0.1947 | 0.0016362
2012-11-25 | 285117 | LLY3 | RURAL | Animals | 739.5 | 119 | 88000.5 | 0.25239 | 0.0021209
2012-11-25 | 285117 | LLY4 | RURAL | Animals | 1555.31 | 119 | 185081.89 | 0.53082 | 0.0044607
2012-11-25 | 285117 | LLY5 | RURAL | Animals | 1098.51 | 119 | 130722.69 | 0.37492 | 0.0031506
2012-11-25 | 285120 | RWD1 | RURAL | Animals | 363.99 | 21 | 7643.79 | 0.021923 | 0.0010439
2012-11-25 | 285123 | AMR3 | RURAL | Other | 2 | 145 | 290 | 0.00083173 | 5.7361e-06
2012-11-25 | 285125 | NSW17 | URBAN | Animals | 60 | 252 | 15120 | 0.015174 | 6.0213e-05
2012-11-25 | 285129 | JBB16A | RURAL | Other | 236.5 | 66 | 15609 | 0.044767 | 0.00067829
2012-11-25 | 285144 | JBB12A | URBAN | Vegetation | 1 | 122 | 122 | 0.00012243 | 1.0036e-06
2012-11-25 | 285144 | JBB12B | RURAL | Vegetation | 772 | 137 | 103626.5 | 0.2972 | 0.0022141
2012-11-25 | 285145 | KCY4 | RURAL | Weather | 192.99 | 183.2895 | 29177.16 | 0.083681 | 0.0005535
2012-11-25 | 285146 | NDH10 | URBAN | Animals | 43.55 | 809 | 35231.95 | 0.035357 | 4.3705e-05
2012-11-25 | 285150 | WMD10A | URBAN | Other | 24.3411 | 106 | 2580.1566 | 0.0025893 | 2.4428e-05
2012-11-25 | 285151 | ACR5 | RURAL | Equipment failure | 35 | 272 | 9520 | 0.027304 | 0.00010038
2012-11-26 | 285152 | CCY1B | URBAN | Other | 5 | 15 | 75 | 7.5311e-05 | 5.0208e-06
2012-11-26 | 285162 | RST9A | URBAN | Weather | 47 | 98 | 4606 | 0.0046251 | 4.7195e-05
2012-11-26 | 285192 | ACR5 | RURAL | Equipment failure | 35 | 105 | 3675 | 0.010544 | 0.00010042
2012-11-26 | 285198 | TWG13A | URBAN | Animals | 33.165 | 10 | 331.65 | 0.00033303 | 3.3303e-05
2012-11-26 | 285242 | SGT3 | URBAN | Other | 71 | 7 | 497 | 0.00049906 | 7.1295e-05
2012-11-26 | 285254 | WED5A | URBAN | Equipment failure | 0.5 | 42 | 21 | 2.1087e-05 | 5.0208e-07
2012-11-26 | 285260 | MLY3 | RURAL | Equipment failure | 92 | 217.3939 | 21120 | 0.060594 | 0.00026395
2012-11-26 | 285521 | GGR1 | RURAL | Weather | 0.33 | 110 | 36.3 | 0.00010415 | 9.4678e-07
2012-11-26 | 286272 | PPE13A | RURAL | Other | 2.805 | 147 | 412.335 | 0.001183 | 8.0476e-06
2012-11-26 | 286557 | OXL11A | URBAN | Other | 10.56 | 20 | 211.2 | 0.00021208 | 1.0604e-05
2012-11-26 | 286564 | NSD30B | URBAN | Animals | 44 | 81 | 3564 | 0.0035788 | 4.4183e-05
2012-11-26 | 288265 | MDR24A | URBAN | Other | 39.6 | 42 | 1663.2 | 0.0016701 | 3.9764e-05
2012-11-27 | 285262 | NMC3A | RURAL | Animals | 242 | 79.4 | 19393 | 0.055646 | 0.00069439
2012-11-27 | 285264 | KWH3 | RURAL | Animals | 31.66 | 190 | 6015.4 | 0.01726 | 9.0844e-05
2012-11-27 | 285288 | BDA13A | URBAN | Other | 437.74 | 33 | 14445.42 | 0.014511 | 0.00043973
2012-11-27 | 285289 | BBH12B | URBAN | Third party impacts | 38.81 | 115 | 4463.15 | 0.0044834 | 3.8986e-05
2012-11-27 | 285290 | MGP15A | URBAN | Other | 939.49 | 18 | 16910.82 | 0.016988 | 0.00094375
2012-11-27 | 285291 | MLY3 | RURAL | Equipment failure | 80 | 152 | 12160 | 0.034892 | 0.00022955
2012-11-27 | 285293 | IPL1 | RURAL | Other | 6 | 19 | 114 | 0.00032711 | 1.7216e-05
2012-11-27 | 285302 | CNB24A | RURAL | Third party impacts | 1110.83 | 167.3667 | 99449.25 | 0.28536 | 0.0031874
2012-11-27 | 285304 | WCL19A | RURAL | Other | 45 | 20 | 900 | 0.0025824 | 0.00012912
2012-11-27 | 285339 | CCY13A | URBAN | Third party impacts | 3.875 | 120 | 465 | 0.00046711 | 3.8926e-06
2012-11-27 | 285343 | MTB17A | RURAL | Other | 18 | 107 | 3477.6 | 0.0099785 | 5.1649e-05
2012-11-27 | 286559 | TRG2A | URBAN | Other | 68.5 | 85 | 5822.5 | 0.0058489 | 6.8811e-05
2012-11-27 | 286562 | CBW6 | RURAL | Other | 13.6 | 91 | 1237.6 | 0.0035511 | 3.9023e-05
2012-11-27 | 288267 | NRG14A | RURAL | Other | 9.075 | 51 | 462.825 | 0.001328 | 2.604e-05
2012-11-27 | 288268 | IPL1 | RURAL | Other | 2.4 | 139.35 | 334.44 | 0.00095963 | 6.8865e-06
2012-11-28 | 285342 | KSN3 | URBAN | Animals | 630 | 51 | 32130 | 0.032288 | 0.0006331
2012-11-28 | 285385 | 1129 | URBAN | Equipment failure | 21.3 | 74 | 1576.2 | 0.001584 | 2.1405e-05
2012-11-28 | 285400 | CMD7A | RURAL | Animals | 1276.5 | 17 | 21700.5 | 0.062274 | 0.0036632
2012-11-28 | 285427 | BTN3 | RURAL | Weather | 882.83 | 17 | 15008.11 | 0.043069 | 0.0025335
2012-11-28 | 285429 | BTN4 | URBAN | Weather | 8.66 | 18 | 155.88 | 0.00015665 | 8.7026e-06
2012-11-28 | 285430 | BTN6 | URBAN | Weather | 7 | 18 | 126 | 0.00012662 | 7.0344e-06
2012-11-28 | 285437 | JBB3A | RURAL | Weather | 72 | 91 | 6552 | 0.018802 | 0.00020662
2012-11-28 | 285438 | CNB24A | RURAL | Other | 47.5 | 3 | 142.5 | 0.00040893 | 0.00013631
2012-11-28 | 285439 | 467 | URBAN | Weather | 1 | 135 | 135 | 0.00013566 | 1.0049e-06
2012-11-28 | 285475 | 467 | URBAN | Weather | 1 | 167 | 167 | 0.00016782 | 1.0049e-06
2012-11-28 | 285475 | BTN1 | URBAN | Weather | 28 | 22 | 616 | 0.00061903 | 2.8138e-05
2012-11-28 | 285475 | BTN2 | RURAL | Weather | 158.5 | 22 | 3487 | 0.010007 | 0.00045485
2012-11-28 | 285475 | BTN3 | RURAL | Weather | 882.83 | 157 | 138604.31 | 0.39776 | 0.0025335
2012-11-28 | 285475 | BTN4 | URBAN | Weather | 8.66 | 35 | 303.1 | 0.00030459 | 8.7026e-06
2012-11-28 | 285475 | BTN6 | URBAN | Weather | 7 | 158 | 1106 | 0.0011114 | 7.0344e-06
2012-11-28 | 285475 | BTN7 | RURAL | Weather | 76.98 | 22 | 1693.56 | 0.00486 | 0.00022091
2012-11-28 | 285482 | UPC1 | RURAL | Equipment failure | 531 | 80.7949 | 51366 | 0.14741 | 0.0015238
2012-11-28 | 285522 | HDN1 | RURAL | Vegetation | 8.33 | 79 | 658.07 | 0.0018885 | 2.3905e-05
2012-11-28 | 286271 | NSW35A | URBAN | Other | 0.33 | 134 | 44.22 | 4.4438e-05 | 3.3162e-07
2012-11-28 | 286275 | CNB24A | RURAL | Other | 0.2178 | 7 | 1.5246 | 4.3752e-06 | 6.2502e-07
2012-11-28 | 286283 | BPN29A | URBAN | Animals | 14.85 | 92 | 1366.2 | 0.0013729 | 1.4923e-05
2012-11-28 | 286561 | AHL11A | URBAN | Equipment failure | 73 | 124 | 9052 | 0.0090965 | 7.3359e-05
2012-11-28 | 286563 | AGE4B | URBAN | Other | 87.5 | 108 | 9450 | 0.0094965 | 8.793e-05
2012-11-28 | 286703 | CNB24A | RURAL | Weather | 1.98 | 31.8333 | 63.03 | 0.00018088 | 5.682e-06
2012-11-28 | 288269 | MTB1B | RURAL | Other | 40.26 | 71 | 2858.46 | 0.008203 | 0.00011553
2012-11-29 | 285481 | ZMR9 | URBAN | Equipment failure | 1725 | 96.3462 | 207082.26 | 0.20818 | 0.0017341
2012-11-29 | 285483 | RCN8A | URBAN | Other | 8.15 | 95 | 774.25 | 0.00077836 | 8.1932e-06
2012-11-29 | 285485 | KBN5A | RURAL | Weather | 441.5 | 70.9855 | 26957 | 0.077369 | 0.0012671
2012-11-29 | 285592 | NSW28 | URBAN | Equipment failure | 15.225 | 75 | 1141.875 | 0.0011479 | 1.5306e-05
2012-11-29 | 285594 | NBR6 | RURAL | Equipment failure | 1023.99 | 90.7941 | 83670.51 | 0.24014 | 0.0029389
2012-11-29 | 285595 | ALY6 | URBAN | Other | 1290.99 | 61 | 78750.39 | 0.079168 | 0.0012978
2012-11-29 | 285622 | NIP4A | RURAL | Equipment failure | 8 | 197 | 1576 | 0.0045232 | 2.2961e-05
2012-11-29 | 286560 | BHL2A | URBAN | Other | 115 | 117 | 13455 | 0.013526 | 0.00011561
2012-11-29 | 286565 | AHL6A | URBAN | Animals | 34.65 | 26 | 900.9 | 0.00090568 | 3.4834e-05
2012-11-29 | 286567 | BHL2A | URBAN | Other | 54 | 83 | 4482 | 0.0045058 | 5.4286e-05
2012-11-29 | 287230 | MTB15A | RURAL | Other | 1 | 124 | 124 | 0.00035589 | 2.8701e-06
2012-11-30 | 285602 | CMD7A | RURAL | Equipment failure | 1276.5 | 78.6957 | 94977.5 | 0.2727 | 0.0036651
2012-11-30 | 285604 | KBR3A | RURAL | Third party impacts | 388.32 | 15 | 5824.8 | 0.016724 | 0.001115
2012-11-30 | 285623 | KCY4 | RURAL | Other | 3.5 | 5 | 17.5 | 5.0247e-05 | 1.0049e-05
2012-11-30 | 285640 | RWD2 | RURAL | Equipment failure | 1 | 82 | 82 | 0.00023544 | 2.8712e-06
2012-11-30 | 285646 | CRY5A | RURAL | Equipment failure | 27 | 213 | 5751 | 0.016513 | 7.7523e-05
2012-11-30 | 285676 | GYS5A | RURAL | Animals | 4 | 65 | 260 | 0.00074652 | 1.1485e-05
2012-11-30 | 285677 | BMG2A | URBAN | Animals | 289.5 | 28 | 8106 | 0.0081514 | 0.00029112
2012-11-30 | 285678 | ALYMRK4 | RURAL | Equipment failure | 67 | 44 | 2948 | 0.0084644 | 0.00019237
2012-11-30 | 285678 | MRK1 | URBAN | Equipment failure | 41 | 12 | 492 | 0.00049475 | 4.1229e-05
2012-11-30 | 285678 | MRK2 | URBAN | Equipment failure | 562.58 | 44 | 24753.52 | 0.024892 | 0.00056573
2012-11-30 | 285678 | MRK3 | URBAN | Equipment failure | 1207 | 22 | 26554 | 0.026703 | 0.0012138
2012-11-30 | 285678 | MRK5A | URBAN | Equipment failure | 835.75 | 9 | 7521.75 | 0.0075638 | 0.00084043
2012-11-30 | 285678 | MRK6 | URBAN | Equipment failure | 1730.25 | 44 | 76131 | 0.076557 | 0.0017399
2012-11-30 | 285678 | MRK7A | URBAN | Equipment failure | 71.49 | 7 | 500.43 | 0.00050323 | 7.189e-05
2012-11-30 | 285678 | MRK8 | URBAN | Equipment failure | 164.5 | 16 | 2632 | 0.0026467 | 0.00016542
2012-11-30 | 285678 | MRK9 | URBAN | Equipment failure | 1687.34 | 44 | 74242.96 | 0.074658 | 0.0016968
2012-11-30 | 285679 | ENG7 | URBAN | Animals | 1681 | 85.3158 | 133165 | 0.13391 | 0.0016904
2012-11-30 | 285844 | GGR2 | RURAL | Other | 3 | 137 | 411 | 0.0011801 | 8.6137e-06
2012-11-30 | 286022 | WRG6A | URBAN | Animals | 49.5 | 290 | 14355 | 0.014435 | 4.9777e-05
2012-11-30 | 286023 | CRM15A | URBAN | Other | 41.58 | 167 | 6943.86 | 0.0069827 | 4.1813e-05
2012-11-30 | 286566 | AGE5B | URBAN | Other | 119 | 136 | 16184 | 0.016275 | 0.00011967
2012-12-01 | 285684 | SBY8 | URBAN | Animals | 914.83 | 126.1739 | 170251.83 | 0.17125 | 0.00092022
2012-12-01 | 285685 | TAB3 | URBAN | Animals | 146.5 | 125.5 | 28589.5 | 0.028758 | 0.00014736
2012-12-01 | 285690 | AHL12A | URBAN | Equipment failure | 7.56 | 77 | 582.12 | 0.00058555 | 7.6045e-06
2012-12-01 | 285693 | WSE6A | RURAL | Equipment failure | 5 | 146.5 | 782 | 0.0022463 | 1.4362e-05
2012-12-01 | 285700 | KRN2 | URBAN | Animals | 27.135 | 113 | 3066.255 | 0.0030843 | 2.7295e-05
2012-12-01 | 285846 | LWD1 | RURAL | Equipment failure | 1 | 335 | 335 | 0.00096227 | 2.8724e-06
2012-12-01 | 285847 | CPD2A | RURAL | Other | 4.355 | 90 | 391.95 | 0.0011259 | 1.2509e-05
2012-12-01 | 286012 | NMK7 | URBAN | Animals | 38.19 | 112 | 4277.28 | 0.0043025 | 3.8415e-05
2012-12-01 | 286021 | SBY8 | URBAN | Other | 59.4 | 18 | 1069.2 | 0.0010755 | 5.975e-05
2012-12-01 | 286665 | NMK7 | URBAN | Other | 128.5 | 90 | 11565 | 0.011633 | 0.00012926
2012-12-01 | 287224 | MTB17A | RURAL | Other | 2 | 96 | 192 | 0.00055151 | 5.7449e-06
2012-12-01 | 288271 | SPO16A | URBAN | Other | 12.8 | 23.6667 | 302.9333 | 0.00030472 | 1.2875e-05
2012-12-02 | 285707 | CPR7 | URBAN | Animals | 1632.99 | 84 | 137171.16 | 0.138 | 0.0016429
2012-12-02 | 285710 | EMP21A | RURAL | Vegetation | 1525.48 | 21.1515 | 23909.92 | 0.068697 | 0.0043829
2012-12-02 | 285740 | BVL5A | URBAN | Other | 40.87 | 74 | 3024.38 | 0.0030427 | 4.1118e-05
2012-12-02 | 285848 | MSV1 | RURAL | Other | 2.01 | 138 | 277.38 | 0.00079695 | 5.775e-06
2012-12-02 | 286550 | NBR6 | RURAL | Animals | 34.5 | 82.1667 | 2834.75 | 0.0081447 | 9.9124e-05
2012-12-02 | 287027 | WNM5 | URBAN | Other | 63.6 | 136 | 8649.6 | 0.008702 | 6.3985e-05
2012-12-02 | 288272 | MAI11 | URBAN | Other | 66 | 76 | 5016 | 0.0050464 | 6.64e-05
2012-12-03 | 285723 | KSN7 | RURAL | Equipment failure | 1289.83 | 115.1026 | 141900.33 | 0.40793 | 0.003708
2012-12-03 | 285726 | BSE8 | URBAN | Animals | 2 | 46 | 92 | 9.2596e-05 | 2.013e-06
2012-12-03 | 285726 | BSEENG15 | URBAN | Animals | 1666 | 46 | 76636 | 0.077132 | 0.0016768
2012-12-03 | 285726 | BSET1 | URBAN | Animals | 5 | 46 | 230 | 0.00023149 | 5.0324e-06
2012-12-03 | 285726 | EAC12 | URBAN | Animals | 4 | 6 | 24 | 2.4155e-05 | 4.0259e-06
2012-12-03 | 285726 | EAC2 | URBAN | Animals | 2 | 6 | 12 | 1.2078e-05 | 2.013e-06
2012-12-03 | 285726 | EAC4 | URBAN | Animals | 16 | 6 | 96 | 9.6622e-05 | 1.6104e-05
2012-12-03 | 285726 | EAC6 | URBAN | Animals | 13 | 6 | 78 | 7.8505e-05 | 1.3084e-05
2012-12-03 | 285726 | EAC8 | URBAN | Animals | 2 | 6 | 12 | 1.2078e-05 | 2.013e-06
2012-12-03 | 285726 | ENG2 | URBAN | Animals | 1719.49 | 6 | 10316.94 | 0.010384 | 0.0017306
2012-12-03 | 285726 | ENG3 | URBAN | Animals | 654.5 | 6 | 3927 | 0.0039524 | 0.00065874
2012-12-03 | 285726 | ENG7 | URBAN | Animals | 1681 | 46 | 77326 | 0.077827 | 0.0016919
2012-12-03 | 285726 | ENG8 | URBAN | Animals | 1157.5 | 6 | 6945 | 0.00699 | 0.001165
2012-12-03 | 285726 | ENG9 | URBAN | Animals | 1203.5 | 46 | 55361 | 0.05572 | 0.0012113
2012-12-03 | 285726 | ENGWDL1 | URBAN | Animals | 1 | 6 | 6 | 6.0389e-06 | 1.0065e-06
2012-12-03 | 285726 | GLY6 | URBAN | Animals | 1998.66 | 46 | 91938.36 | 0.092534 | 0.0020116
2012-12-03 | 285726 | TTF9 | RURAL | Animals | 55.5 | 6 | 333 | 0.0009573 | 0.00015955
2012-12-03 | 285726 | WDLT1 | URBAN | Animals | 1 | 6 | 6 | 6.0389e-06 | 1.0065e-06
2012-12-03 | 285726 | WDLT2 | URBAN | Animals | 1 | 6 | 6 | 6.0389e-06 | 1.0065e-06
2012-12-03 | 285762 | HPE13A | URBAN | Equipment failure | 97.5 | 112 | 10920 | 0.010991 | 9.8132e-05
2012-12-03 | 285780 | NBR7 | URBAN | Equipment failure | 373 | 3 | 1119 | 0.0011262 | 0.00037542
2012-12-03 | 285802 | SFD2A | URBAN | Third party impacts | 4.12 | 31 | 127.72 | 0.00012855 | 4.1467e-06
2012-12-03 | 285805 | LTN6 | URBAN | Other | 729 | 34 | 24786 | 0.024947 | 0.00073372
2012-12-03 | 285805 | SPE7 | URBAN | Other | 397 | 34 | 13498 | 0.013585 | 0.00039957
2012-12-03 | 285821 | DBS4A | URBAN | Equipment failure | 3.67 | 28 | 102.76 | 0.00010343 | 3.6938e-06
2012-12-03 | 285823 | NBR8 | RURAL | Equipment failure | 569.25 | 79 | 44970.75 | 0.12928 | 0.0016365
2012-12-03 | 285824 | NRG16A | RURAL | Weather | 17.5 | 252.5 | 3866 | 0.011114 | 5.0308e-05
2012-12-03 | 285825 | ARG5A | URBAN | Animals | 1565.48 | 89.6296 | 144084.93 | 0.14502 | 0.0015756
2012-12-03 | 285829 | MTB15A | RURAL | Weather | 6 | 515 | 3090 | 0.008883 | 1.7249e-05
2012-12-03 | 285849 | BVL5A | URBAN | Equipment failure | 40.87 | 67 | 2738.29 | 0.002756 | 4.1135e-05
2012-12-03 | 286262 | NBR6 | RURAL | Other | 9.6 | 153.9 | 1477.44 | 0.0042473 | 2.7598e-05
2012-12-03 | 286263 | CRY2A | RURAL | Other | 3.2 | 143.7 | 459.84 | 0.0013219 | 9.1992e-06
2012-12-03 | 286549 | BHL4A | URBAN | Other | 46.4 | 79 | 3665.6 | 0.0036893 | 4.6701e-05
2012-12-03 | 286676 | BIS16A | URBAN | Equipment failure | 40.4 | 118 | 4767.2 | 0.0047981 | 4.0662e-05
2012-12-03 | 287024 | CBW13 | RURAL | Other | 20.8 | 127.6167 | 2654.4267 | 0.0076308 | 5.9795e-05
2012-12-04 | 285828 | SFD7A | URBAN | Other | 42.17 | 109 | 4596.53 | 0.0046277 | 4.2456e-05
2012-12-04 | 285830 | BLB4A | URBAN | Animals | 398.5 | 171 | 68143.5 | 0.068605 | 0.0004012
2012-12-04 | 285842 | BDT6 | URBAN | Other | 1 | 12 | 12 | 1.2081e-05 | 1.0068e-06
2012-12-04 | 285922 | KWH1 | RURAL | Weather | 366 | 204.25 | 74628 | 0.21462 | 0.0010526
2012-12-04 | 285923 | EMD1 | RURAL | Animals | 356.49 | 79.3226 | 40045.31 | 0.11517 | 0.0010252
2012-12-04 | 285924 | DBS16A | URBAN | Equipment failure | 57.28 | 56.3333 | 3219.06 | 0.0032409 | 5.7668e-05
2012-12-04 | 285925 | CRY2A | RURAL | Equipment failure | 2.5 | 104 | 260 | 0.00074774 | 7.1898e-06
2012-12-04 | 285928 | INA11A | URBAN | Equipment failure | 50 | 65 | 3250 | 0.003272 | 5.0339e-05
2012-12-04 | 285956 | BTN2 | RURAL | Equipment failure | 6 | 76 | 456 | 0.0013114 | 1.7256e-05
2012-12-04 | 285957 | MLS15A | URBAN | Equipment failure | 1603.33 | 90.1667 | 144534.37 | 0.14551 | 0.0016142
2012-12-04 | 285958 | SPF17B | URBAN | Third party impacts | 98.665 | 29 | 2861.285 | 0.0028807 | 9.9333e-05
2012-12-04 | 285960 | NRG6 | URBAN | Equipment failure | 8.5 | 81 | 688.5 | 0.00069316 | 8.5576e-06
2012-12-04 | 285961 | CBW8 | URBAN | Third party impacts | 3 | 187.6667 | 563 | 0.00056681 | 3.0203e-06
2012-12-04 | 285961 | CBW9 | URBAN | Third party impacts | 2 | 205 | 410 | 0.00041278 | 2.0135e-06
2012-12-04 | 285962 | AGE3 | URBAN | Equipment failure | 2119 | 60.9091 | 108268 | 0.109 | 0.0021334
2012-12-04 | 286000 | KBR3A | RURAL | Animals | 1.5 | 132 | 198 | 0.00056943 | 4.3139e-06
2012-12-04 | 286005 | MBG4 | RURAL | Operational error | 4.62 | 107 | 494.34 | 0.0014217 | 1.3287e-05
2012-12-04 | 286018 | BLB8A | URBAN | Other | 50.536 | 78 | 3941.808 | 0.0039685 | 5.0878e-05
2012-12-04 | 286019 | BPN34A | URBAN | Animals | 44.88 | 140 | 6283.2 | 0.0063258 | 4.5184e-05
2012-12-04 | 286261 | GYN3A | RURAL | Other | 1.2 | 134.9 | 161.88 | 0.00046556 | 3.4511e-06
2012-12-04 | 286264 | GYN3A | RURAL | Other | 6.4 | 82.0833 | 525.3333 | 0.0015108 | 1.8406e-05
2012-12-04 | 286548 | MFD5A | RURAL | Operational error | 4.29 | 62 | 265.98 | 0.00076494 | 1.2338e-05
2012-12-04 | 286666 | AGE7B | URBAN | Operational error | 24.42 | 12 | 293.04 | 0.00029502 | 2.4585e-05
2012-12-04 | 286667 | SFD4 | URBAN | Weather | 76 | 28.5 | 2936.64 | 0.0029565 | 7.6515e-05
2012-12-04 | 286668 | SFD4 | URBAN | Other | 25.08 | 46 | 1153.68 | 0.0011615 | 2.525e-05
2012-12-04 | 286674 | SFD7A | URBAN | Animals | 27.8322 | 106 | 2950.2132 | 0.0029702 | 2.8021e-05
2012-12-04 | 286701 | MFN2A | URBAN | Equipment failure | 1 | 598 | 598 | 0.00060205 | 1.0068e-06
2012-12-04 | 286704 | BTA5A | RURAL | Other | 6 | 117.3333 | 704 | 0.0020247 | 1.7256e-05
2012-12-04 | 287025 | ZMR5 | URBAN | Other | 221.736 | 646.4833 | 143348.6284 | 0.14432 | 0.00022324
2012-12-04 | 287226 | MGP13A | RURAL | Other | 8 | 271.25 | 2170 | 0.0062408 | 2.3007e-05
2012-12-04 | 288273 | BHD35A | RURAL | Other | 2.64 | 149 | 393.36 | 0.0011313 | 7.5925e-06
2012-12-05 | 286001 | 403 | URBAN | Equipment failure | 1 | 9 | 9 | 9.0636e-06 | 1.0071e-06
2012-12-05 | 286001 | 404 | URBAN | Equipment failure | 2 | 7 | 14 | 1.4099e-05 | 2.0141e-06
2012-12-05 | 286001 | BDT1 | RURAL | Equipment failure | 1137.97 | 7 | 7965.79 | 0.022918 | 0.0032741
2012-12-05 | 286001 | BDT2 | RURAL | Equipment failure | 282 | 7 | 1974 | 0.0056794 | 0.00081134
2012-12-05 | 286001 | BDT3 | RURAL | Equipment failure | 699.5 | 7 | 4896.5 | 0.014088 | 0.0020125
2012-12-05 | 286001 | BDT4 | RURAL | Equipment failure | 1355.99 | 7 | 9491.93 | 0.027309 | 0.0039013
2012-12-05 | 286001 | BDT5 | RURAL | Equipment failure | 940.01 | 7 | 6580.07 | 0.018932 | 0.0027045
2012-12-05 | 286001 | BDT6 | URBAN | Equipment failure | 442.5 | 7 | 3097.5 | 0.0031194 | 0.00044563
2012-12-05 | 286001 | IPL1 | RURAL | Equipment failure | 728.97 | 7 | 5102.79 | 0.014681 | 0.0020973
2012-12-05 | 286001 | IPL2 | RURAL | Equipment failure | 327.48 | 7 | 2292.36 | 0.0065954 | 0.00094219
2012-12-05 | 286001 | IPL3 | RURAL | Equipment failure | 498.46 | 7 | 3489.22 | 0.010039 | 0.0014341
2012-12-05 | 286003 | MGL1A | RURAL | Vegetation | 163 | 32 | 10432 | 0.030014 | 0.00046897
2012-12-05 | 286024 | MFN12A | RURAL | Equipment failure | 1101.33 | 36.5581 | 44111.56 | 0.12691 | 0.0031686
2012-12-05 | 286025 | WRG8A | URBAN | Equipment failure | 1290.66 | 50.8696 | 41043.44 | 0.041334 | 0.0012998
2012-12-05 | 286029 | GTN12A | RURAL | Other | 15 | 8 | 120 | 0.00034525 | 4.3157e-05
2012-12-05 | 286030 | TMH12A | URBAN | Equipment failure | 419.25 | 2 | 838.5 | 0.00084443 | 0.00042221
2012-12-05 | 286030 | TMH13A | URBAN | Equipment failure | 328 | 2 | 656 | 0.00066064 | 0.00033032
2012-12-05 | 286030 | TMH15A | URBAN | Equipment failure | 1723.5 | 2 | 3447 | 0.0034714 | 0.0017357
2012-12-05 | 286030 | TMH16A | URBAN | Equipment failure | 531.83 | 2 | 1063.66 | 0.0010712 | 0.00053559
2012-12-05 | 286030 | TMH1B | URBAN | Equipment failure | 6 | 2 | 12 | 1.2085e-05 | 6.0424e-06
2012-12-05 | 286030 | TMH2A | RURAL | Equipment failure | 451.49 | 2 | 902.98 | 0.002598 | 0.001299
2012-12-05 | 286030 | TMH3A | URBAN | Equipment failure | 850.99 | 2 | 1701.98 | 0.001714 | 0.00085701
2012-12-05 | 286030 | TMH5A | URBAN | Equipment failure | 1089.68 | 2 | 2179.36 | 0.0021948 | 0.0010974
2012-12-05 | 286035 | SMR7A | URBAN | Third party impacts | 39.27 | 70 | 2748.9 | 0.0027683 | 3.9548e-05
2012-12-05 | 286036 | BIS1 | RURAL | Equipment failure | 1255 | 107.1538 | 82293 | 0.23677 | 0.0036108
2012-12-05 | 286062 | YTA2A | URBAN | Third party impacts | 1765.5 | 140.9268 | 250507 | 0.25228 | 0.001778
2012-12-05 | 286062 | YTA2B | RURAL | Third party impacts | 1109.5 | 103 | 114278.5 | 0.32879 | 0.0031921
2012-12-05 | 286065 | CSE6 | URBAN | Third party impacts | 3.91 | 140 | 547.4 | 0.00055127 | 3.9376e-06
2012-12-05 | 286066 | PPE13A | RURAL | Operational error | 659 | 91.5185 | 58727 | 0.16896 | 0.001896
2012-12-05 | 286067 | BRD5A | RURAL | Equipment failure | 1679.49 | 101.16 | 180754.26 | 0.52005 | 0.0048321
2012-12-05 | 286075 | RWD2 | RURAL | Animals | 4 | 116 | 464 | 0.001335 | 1.1508e-05
2012-12-05 | 286268 | PWC4 | RURAL | Other | 9.2 | 151.4833 | 1393.6467 | 0.0040097 | 2.6469e-05
2012-12-05 | 286547 | ZMR10 | URBAN | Other | 10 | 2 | 20 | 2.0141e-05 | 1.0071e-05
2012-12-05 | 286670 | AGE10 | URBAN | Vegetation | 65 | 177 | 11505 | 0.011586 | 6.546e-05
2012-12-05 | 286685 | CHL6A | URBAN | Other | 111.21 | 62 | 6895.02 | 0.0069438 | 0.000112
2012-12-05 | 286707 | BPN31A | URBAN | Equipment failure | 41.25 | 69 | 2846.25 | 0.0028664 | 4.1542e-05
2012-12-05 | 287227 | SPO51A | URBAN | Other | 37.855 | 115 | 4353.325 | 0.0043841 | 3.8123e-05
2012-12-06 | 286068 | EMD3 | RURAL | Vegetation | 71 | 118 | 8378 | 0.024114 | 0.00020436
2012-12-06 | 286074 | TRG3 | URBAN | Equipment failure | 772.17 | 16 | 12354.72 | 0.012446 | 0.00077786
2012-12-06 | 286080 | SMF5A | RURAL | Other | 293 | 6 | 1758 | 0.00506 | 0.00084333
2012-12-06 | 286082 | MLY6 | RURAL | Weather | 271.49 | 2 | 542.98 | 0.0015628 | 0.00078142
2012-12-06 | 286093 | MGP13A | RURAL | Other | 98 | 109.6 | 10179 | 0.029298 | 0.00028207
2012-12-06 | 286098 | NSW5A | URBAN | Equipment failure | 96 | 3 | 288 | 0.00029012 | 9.6708e-05
2012-12-06 | 286103 | NRG2A | URBAN | Equipment failure | 24.42 | 70 | 1709.4 | 0.001722 | 2.46e-05
2012-12-06 | 286129 | MRK6 | URBAN | Equipment failure | 1726.25 | 60.8421 | 125478.75 | 0.1264 | 0.001739
2012-12-06 | 286135 | BHD46A | URBAN | Animals | 25.25 | 166 | 4912.25 | 0.0049485 | 2.5436e-05
2012-12-06 | 286135 | BHDRCK29 | URBAN | Animals | 146.74 | 62.3684 | 10263.29 | 0.010339 | 0.00014782
2012-12-06 | 286140 | NMK7 | URBAN | Other | 0.1 | 160 | 16 | 1.6118e-05 | 1.0074e-07
2012-12-06 | 286148 | TRP3 | RURAL | Other | 1 | 70 | 70 | 0.00020148 | 2.8783e-06
2012-12-06 | 286149 | LLY5 | RURAL | Equipment failure | 3 | 305 | 915 | 0.0026336 | 8.6348e-06
2012-12-06 | 286684 | SRD14A | URBAN | Other | 51.15 | 67 | 3427.05 | 0.0034523 | 5.1527e-05
2012-12-06 | 288274 | MDR24A | URBAN | Other | 39.6 | 60 | 2376 | 0.0023935 | 3.9892e-05
2012-12-07 | 286143 | GCLSBY7 | URBAN | Other | 416.44 | 71 | 29567.24 | 0.029794 | 0.00041964
2012-12-07 | 286144 | MTG3A | URBAN | Equipment failure | 4.62 | 49 | 226.38 | 0.00022812 | 4.6555e-06
2012-12-07 | 286150 | RIS1 | RURAL | Weather | 705.5 | 63.24 | 46297.5 | 0.13331 | 0.0020314
2012-12-07 | 286151 | BLH13B | RURAL | Equipment failure | 300.84 | 113.2037 | 34827.56 | 0.10028 | 0.00086625
2012-12-07 | 286153 | MFD3A | RURAL | Animals | 6 | 65 | 158 | 0.00045495 | 1.7277e-05
2012-12-07 | 286156 | HWD5B | URBAN | Third party impacts | 82.9422 | 22 | 1824.7284 | 0.0018387 | 8.3579e-05
2012-12-07 | 286159 | ACR2A | URBAN | Equipment failure | 1237.5 | 62 | 76725 | 0.077314 | 0.001247
2012-12-07 | 286159 | ACR2B | URBAN | Equipment failure | 1461.5 | 131.8966 | 169054 | 0.17035 | 0.0014727
2012-12-07 | 286161 | NVL10 | URBAN | Equipment failure | 554.32 | 74 | 40878.36 | 0.041192 | 0.00055857
2012-12-07 | 286188 | PMBWED19 | URBAN | Equipment failure | 2 | 670 | 1340 | 0.0013503 | 2.0153e-06
2012-12-07 | 286190 | RWD2 | RURAL | Other | 14 | 99 | 1386 | 0.0039909 | 4.0312e-05
2012-12-07 | 286191 | CMD15A | URBAN | Equipment failure | 6.4 | 170 | 1088 | 0.0010963 | 6.4491e-06
2012-12-07 | 286266 | CRY6A | RURAL | Other | 9.6 | 243.7667 | 2340.16 | 0.0067383 | 2.7642e-05
2012-12-07 | 286267 | BMT3 | RURAL | Other | 4 | 126.1667 | 504.6667 | 0.0014531 | 1.1518e-05
2012-12-07 | 286269 | GYGGYS6 | RURAL | Other | 0.8 | 83.5667 | 66.8533 | 0.0001925 | 2.3035e-06
2012-12-07 | 286551 | GYS3A | RURAL | Other | 5 | 67.8333 | 339.1667 | 0.0009766 | 1.4397e-05
2012-12-07 | 286681 | BLHSTN16 | RURAL | Other | 2.1978 | 149 | 327.4722 | 0.00094293 | 6.3284e-06
2012-12-07 | 286682 | LHM5 | RURAL | Other | 44.8 | 147.0333 | 6587.0933 | 0.018967 | 0.000129
2012-12-08 | 286203 | WRG19A | URBAN | Equipment failure | 771 | 87.7778 | 59772 | 0.060249 | 0.00077715
2012-12-08 | 286204 | CNB24A | RURAL | Other | 10.5 | 47 | 493.5 | 0.0014216 | 3.0246e-05
2012-12-08 | 286204 | MCN3 | URBAN | Other | 53.16 | 32 | 1701.12 | 0.0017147 | 5.3584e-05
2012-12-08 | 286205 | TBV4 | RURAL | Equipment failure | 66 | 304 | 20064 | 0.057796 | 0.00019012
2012-12-08 | 286208 | CNB24A | RURAL | Other | 1106.83 | 4 | 4427.32 | 0.012753 | 0.0031883
2012-12-08 | 286211 | WFD5A | RURAL | Equipment failure | 16 | 223 | 3568 | 0.010278 | 4.609e-05
2012-12-08 | 286545 | RCF12A | URBAN | Other | 139.5 | 61 | 8509.5 | 0.0085774 | 0.00014061
2012-12-08 | 286546 | LTN3 | URBAN | Animals | 33 | 99 | 3267 | 0.0032931 | 3.3263e-05
2012-12-08 | 286671 | KMR22A | URBAN | Animals | 22.11 | 82 | 1813.02 | 0.0018275 | 2.2286e-05
2012-12-08 | 286683 | HPK8A | URBAN | Animals | 55.44 | 71 | 3936.24 | 0.0039677 | 5.5882e-05
2012-12-08 | 286708 | CVL17A | URBAN | Other | 46.86 | 108 | 5060.88 | 0.0051013 | 4.7234e-05
2012-12-09 | 286210 | JHDMDH7 | URBAN | Other | 6 | 20 | 120 | 0.00012099 | 6.0494e-06
2012-12-09 | 286216 | LDR3 | URBAN | Third party impacts | 105 | 138 | 14490 | 0.014609 | 0.00010586
2012-12-09 | 286219 | BBH13B | URBAN | Equipment failure | 2059.4 | 59.4545 | 138285.38 | 0.13942 | 0.0020764
2012-12-09 | 286233 | CPD1 | RURAL | Third party impacts | 422.01 | 313.0976 | 135999.33 | 0.3919 | 0.0012161
2012-12-09 | 286242 | RWD2 | RURAL | Equipment failure | 5 | 150 | 750 | 0.0021612 | 1.4408e-05
2012-12-09 | 286243 | MCW11 | RURAL | Equipment failure | 16.08 | 146 | 2347.68 | 0.0067651 | 4.6336e-05
2012-12-09 | 286544 | CLRSRD17 | URBAN | Equipment failure | 32.67 | 74 | 2417.58 | 0.0024375 | 3.2939e-05
2012-12-09 | 286574 | AGT31A | RURAL | Other | 10 | 82 | 820 | 0.0023629 | 2.8816e-05
2012-12-09 | 286692 | MTG7A | URBAN | Other | 37.29 | 284 | 10590.36 | 0.010678 | 3.7597e-05
2012-12-09 | 287102 | BLB2A | URBAN | Animals | 38.8278 | 61 | 2368.4958 | 0.002388 | 3.9148e-05
2012-12-09 | 287146 | GLY2 | URBAN | Other | 50 | 502 | 25100 | 0.025307 | 5.0412e-05
2012-12-10 | 286237 | DBY6 | URBAN | Animals | 2278.16 | 79.6667 | 181639.04 | 0.1832 | 0.0022977
2012-12-10 | 286244 | NRG10 | URBAN | Equipment failure | 99.5 | 70 | 6965 | 0.0070248 | 0.00010035
2012-12-10 | 286260 | MTG11A | URBAN | Third party impacts | 47.5 | 58 | 2755 | 0.0027786 | 4.7908e-05
2012-12-10 | 286276 | QPT5 | URBAN | Other | 154.5 | 67 | 10351.5 | 0.01044 | 0.00015583
2012-12-10 | 286288 | NVL12A | URBAN | Equipment failure | 15.9 | 11 | 174.9 | 0.0001764 | 1.6036e-05
2012-12-10 | 286290 | CRB25A | RURAL | Weather | 142 | 74.8605 | 11690.5 | 0.033703 | 0.00040938
2012-12-10 | 286292 | ABY5A | RURAL | Other | 33.5 | 17 | 569.5 | 0.0016418 | 9.6579e-05
2012-12-10 | 286293 | CMY4 | RURAL | Weather | 700.52 | 92.9512 | 61174.2 | 0.17636 | 0.0020196
2012-12-10 | 286309 | PWC4 | RURAL | Equipment failure | 626.51 | 125.9545 | 65886.79 | 0.18995 | 0.0018062
2012-12-10 | 286310 | GGR1 | RURAL | Animals | 830.83 | 45 | 37387.35 | 0.10779 | 0.0023952
2012-12-10 | 286310 | GGR2 | RURAL | Animals | 139.66 | 32 | 4469.12 | 0.012884 | 0.00040263
2012-12-10 | 286310 | GGR3 | RURAL | Animals | 86.99 | 32 | 2783.68 | 0.0080252 | 0.00025079
2012-12-10 | 286310 | GGR4 | RURAL | Animals | 605.5 | 32 | 19376 | 0.05586 | 0.0017456
2012-12-10 | 286310 | GGR5 | RURAL | Animals | 959.99 | 32 | 30719.68 | 0.088563 | 0.0027676
2012-12-10 | 286341 | THL1 | RURAL | Weather | 2.01 | 94 | 188.94 | 0.00054471 | 5.7947e-06
2012-12-10 | 286369 | GGR1 | RURAL | Animals | 50 | 122.5 | 6050 | 0.017442 | 0.00014415
2012-12-10 | 286552 | LBH5A | RURAL | Weather | 43.83 | 71 | 3111.93 | 0.0089716 | 0.00012636
2012-12-10 | 286694 | BPN35A | URBAN | Other | 35.31 | 84 | 2966.04 | 0.0029915 | 3.5613e-05
2012-12-10 | 287383 | VPT3A | RURAL | Other | 56.1 | 77 | 4319.7 | 0.012454 | 0.00016173
2012-12-10 | 287384 | TMH2A | RURAL | Animals | 35.64 | 72 | 2566.08 | 0.0073979 | 0.00010275
2012-12-11 | 286319 | DBY4 | URBAN | Other | 1 | 218 | 218 | 0.00021994 | 1.0089e-06
2012-12-11 | 286355 | BHL5A | URBAN | Other | 1722.75 | 89.2188 | 155465.25 | 0.15685 | 0.0017381
2012-12-11 | 286358 | SGT24A | URBAN | Equipment failure | 1547.5 | 60.7917 | 107241.5 | 0.10819 | 0.0015612
2012-12-11 | 286372 | QPT5 | URBAN | Equipment failure | 40.25 | 80 | 3220 | 0.0032486 | 4.0607e-05
2012-12-11 | 286374 | KWH2 | RURAL | Equipment failure | 6 | 128 | 768 | 0.002215 | 1.7305e-05
2012-12-11 | 286398 | MTG15A | URBAN | Equipment failure | 8.483 | 389 | 3299.887 | 0.0033292 | 8.5583e-06
2012-12-11 | 286489 | IPS5B | URBAN | Other | 102 | 125 | 12750 | 0.012863 | 0.00010291
2012-12-11 | 286490 | BNH5A | RURAL | Equipment failure | 45.56 | 127 | 5786.12 | 0.016688 | 0.0001314
2012-12-11 | 286543 | NRA1A | RURAL | Animals | 27 | 59 | 1593 | 0.0045945 | 7.7872e-05
2012-12-11 | 286571 | SFD3 | URBAN | Other | 43.56 | 134 | 5837.04 | 0.0058889 | 4.3947e-05
2012-12-11 | 286572 | SFD3 | URBAN | Third party impacts | 42.9 | 44 | 1887.6 | 0.0019044 | 4.3281e-05
2012-12-11 | 286573 | SFD9 | URBAN | Other | 65 | 28 | 2557.1 | 0.0025798 | 6.5577e-05
2012-12-11 | 286710 | MTG15A | URBAN | Equipment failure | 55.9878 | 42 | 2351.4876 | 0.0023724 | 5.6485e-05
2012-12-11 | 286715 | RLB16A | RURAL | Other | 13.5 | 33 | 445.5 | 0.0012849 | 3.8936e-05
2012-12-11 | 287401 | RLB16A | RURAL | Other | 8.91 | 98 | 873.18 | 0.0025184 | 2.5698e-05
2012-12-12 | 286396 | CRB25A | RURAL | Equipment failure | 12 | 73 | 876 | 0.0025276 | 3.4624e-05
2012-12-12 | 286399 | WHO2 | RURAL | Equipment failure | 37 | 125 | 4625 | 0.013345 | 0.00010676
2012-12-12 | 286400 | BBS11 | URBAN | Equipment failure | 1084.5 | 66 | 72154.5 | 0.072817 | 0.0010945
2012-12-12 | 286440 | GLY6 | URBAN | Other | 66.5 | 101 | 6716.5 | 0.0067782 | 6.7111e-05
2012-12-12 | 286449 | MLB12A | RURAL | Weather | 75.5 | 52 | 3926 | 0.011328 | 0.00021784
2012-12-12 | 286452 | BMT2 | RURAL | Equipment failure | 1 | 18 | 18 | 5.1936e-05 | 2.8854e-06
2012-12-12 | 286460 | AHD22A | URBAN | Equipment failure | 17.2 | 173 | 2975.6 | 0.0030029 | 1.7358e-05
2012-12-12 | 286497 | GGR3 | RURAL | Other | 3 | 110 | 330 | 0.00095217 | 8.6561e-06
2012-12-12 | 286554 | CRY2A | RURAL | Other | 9.5 | 77.6667 | 737.8333 | 0.0021289 | 2.7411e-05
2012-12-12 | 286555 | PWC3 | RURAL | Animals | 1.65 | 64.15 | 105.8475 | 0.00030541 | 4.7608e-06
2012-12-12 | 286558 | HTN24A | URBAN | Other | 44.5 | 47 | 2091.5 | 0.0021107 | 4.4909e-05
2012-12-12 | 286570 | GLY6 | URBAN | Equipment failure | 43.89 | 113 | 4959.57 | 0.0050051 | 4.4293e-05
2012-12-12 | 286687 | CHL11A | RURAL | Other | 54.78 | 50 | 2739 | 0.007903 | 0.00015806
2012-12-12 | 287228 | IPL2 | RURAL | Animals | 2.01 | 88 | 176.88 | 0.00051036 | 5.7996e-06
2012-12-13 | 286491 | PRG2A | RURAL | Other | 25 | 11 | 275 | 0.00079381 | 7.2165e-05
2012-12-13 | 286492 | CLR3 | RURAL | Vegetation | 180.67 | 15 | 2710.05 | 0.0078228 | 0.00052152
2012-12-13 | 286496 | SMF2A | RURAL | Other | 15 | 33 | 495 | 0.0014289 | 4.3299e-05
2012-12-13 | 286499 | TCB2 | RURAL | Equipment failure | 408 | 41 | 16728 | 0.048287 | 0.0011777
2012-12-13 | 286505 | BWH12A | RURAL | Equipment failure | 5 | 185 | 925 | 0.0026701 | 1.4433e-05
2012-12-13 | 286542 | DBY6 | URBAN | Equipment failure | 54.4 | 42 | 2284.8 | 0.0023065 | 5.4916e-05
2012-12-13 | 286556 | NVL2 | URBAN | Other | 208.33 | 33.8333 | 7048.4983 | 0.0071153 | 0.0002103
2012-12-13 | 286569 | AHL8A | URBAN | Other | 12.54 | 51 | 639.54 | 0.0006456 | 1.2659e-05
2012-12-14 | 286539 | TGP9A | RURAL | Other | 860 | 57 | 48331.5 | 0.13957 | 0.0024835
2012-12-14 | 286541 | DBY11 | URBAN | Other | 36.96 | 19 | 702.24 | 0.00070911 | 3.7321e-05
2012-12-14 | 286568 | KRN1 | URBAN | Equipment failure | 88.77 | 127 | 11273.79 | 0.011384 | 8.9638e-05
2012-12-14 | 286583 | BLH10A | URBAN | Third party impacts | 1 | 139 | 139 | 0.00014036 | 1.0098e-06
2012-12-14 | 286589 | WSE3A | RURAL | Equipment failure | 265 | 168 | 44520 | 0.12857 | 0.00076528
2012-12-14 | 286591 | AMR2 | RURAL | Weather | 853.31 | 131.1675 | 111940.31 | 0.32327 | 0.0024642
2012-12-14 | 286592 | BHL4A | URBAN | Other | 1392.99 | 15 | 20894.85 | 0.021099 | 0.0014066
2012-12-14 | 286619 | NRA1A | RURAL | Equipment failure | 10 | 87 | 870 | 0.0025124 | 2.8878e-05
2012-12-14 | 286625 | ALY5 | URBAN | Other | 1681.33 | 69.1765 | 116350.44 | 0.11749 | 0.0016978
2012-12-14 | 286625 | BDA12A | URBAN | Other | 1 | 25 | 25 | 2.5244e-05 | 1.0098e-06
2012-12-14 | 286625 | BDA12B | URBAN | Other | 1610.67 | 27.2667 | 52608.75 | 0.053123 | 0.0016264
2012-12-14 | 286672 | KMR25A | RURAL | Equipment failure | 4.62 | 38 | 175.56 | 0.00050699 | 1.3342e-05
2012-12-14 | 286711 | MRK9 | URBAN | Animals | 62 | 48.3333 | 2996.6667 | 0.003026 | 6.2606e-05
2012-12-14 | 286714 | BLB8A | URBAN | Animals | 41.6922 | 9 | 375.2298 | 0.0003789 | 4.21e-05
2012-12-14 | 286807 | BDB36A | RURAL | Other | 20.13 | 134 | 2697.42 | 0.0077897 | 5.8132e-05
2012-12-14 | 286820 | CNB24A | RURAL | Other | 5.3922 | 139 | 749.5158 | 0.0021645 | 1.5572e-05
2012-12-14 | 287389 | KSN7 | RURAL | Other | 2.64 | 85 | 224.4 | 0.00064803 | 7.6239e-06
2012-12-15 | 286627 | TGW1 | RURAL | Other | 67 | 118 | 7906 | 0.02283 | 0.00019347
2012-12-15 | 286638 | SIS1 | RURAL | Equipment failure | 644 | 42 | 27048 | 0.078106 | 0.0018597
2012-12-15 | 286642 | PRG2A | RURAL | Other | 944 | 95 | 89680 | 0.25897 | 0.002726
2012-12-15 | 286642 | PRG2B | RURAL | Other | 161 | 95 | 15295 | 0.044167 | 0.00046491
2012-12-15 | 286673 | NMK23A | URBAN | Animals | 105.7122 | 74 | 7822.7028 | 0.0078991 | 0.00010674
2012-12-15 | 286689 | PWC4 | RURAL | Animals | 3.3 | 105.2667 | 347.38 | 0.0010031 | 9.5293e-06
2012-12-15 | 287140 | NBR6 | RURAL | Other | 6.4 | 69.0833 | 442.1333 | 0.0012767 | 1.8481e-05
2012-12-15 | 287229 | SPD11A | URBAN | Animals | 137 | 78 | 10686 | 0.01079 | 0.00013834
2012-12-16 | 286643 | BDA3A | URBAN | Other | 1140.84 | 17 | 19394.28 | 0.019583 | 0.001152
2012-12-16 | 286645 | CNB24A | RURAL | Other | 76 | 77 | 5852 | 0.016898 | 0.00021946
2012-12-16 | 286646 | BLB4A | URBAN | Other | 67.5 | 99.5 | 3496.5 | 0.0035306 | 6.8158e-05
2012-12-16 | 286648 | JBB13A | RURAL | Vegetation | 223.49 | 79.4444 | 18302.26 | 0.052849 | 0.00064535
2012-12-16 | 286658 | PWC3 | RURAL | Animals | 1293.06 | 27.4159 | 39052.52 | 0.11277 | 0.0037338
2012-12-16 | 286669 | ZMR9 | URBAN | Weather | 122 | 48 | 5856 | 0.0059131 | 0.00012319
2012-12-16 | 286690 | NBR9 | RURAL | Other | 51.5 | 67 | 3450.5 | 0.0099636 | 0.00014871
2012-12-16 | 286691 | CRY5A | RURAL | Other | 6 | 193.1667 | 1159 | 0.0033467 | 1.7325e-05
2012-12-16 | 286712 | CPR5 | URBAN | Animals | 92.07 | 48 | 4419.36 | 0.0044625 | 9.2968e-05
2012-12-16 | 286805 | GTN3A | URBAN | Weather | 65.2 | 147 | 9584.4 | 0.0096779 | 6.5836e-05
2012-12-16 | 286818 | BPN29A | URBAN | Other | 29.7 | 113 | 3356.1 | 0.0033888 | 2.999e-05
2012-12-17 | 286663 | NBR6 | RURAL | Equipment failure | 1025.99 | 106.913 | 130255.385 | 0.37609 | 0.0029623
2012-12-17 | 286664 | CDRSPD12 | URBAN | Equipment failure | 1578 | 58.55 | 132591.5 | 0.13388 | 0.0015934
2012-12-17 | 286664 | SPD12B | URBAN | Equipment failure | 562.99 | 17 | 19141.66 | 0.019328 | 0.00056847
2012-12-17 | 286688 | CMD5A | URBAN | Other | 117.5 | 84 | 9870 | 0.009966 | 0.00011864
2012-12-17 | 286705 | CMA8A | RURAL | Equipment failure | 13 | 167 | 2171 | 0.0062683 | 3.7535e-05
2012-12-17 | 286713 | WED3A | URBAN | Animals | 47.85 | 89 | 4258.65 | 0.0043001 | 4.8316e-05
2012-12-17 | 286730 | IPL3 | RURAL | Vegetation | 156.99 | 208 | 32653.92 | 0.094282 | 0.00045328
2012-12-17 | 286734 | CRB25A | RURAL | Weather | 19.5 | 60 | 937.5 | 0.0027068 | 5.6302e-05
2012-12-17 | 286744 | MMC22A | URBAN | Third party impacts | 94 | 7 | 658 | 0.0006644 | 9.4915e-05
2012-12-17 | 286751 | ESK2A | URBAN | Weather | 1 | 21 | 21 | 2.1204e-05 | 1.0097e-06
2012-12-17 | 286751 | ESK2B | RURAL | Weather | 395.5 | 21 | 8305.5 | 0.02398 | 0.0011419
2012-12-17 | 286751 | ESK3A | RURAL | Weather | 138.59 | 21 | 2910.39 | 0.0084032 | 0.00040015
2012-12-17 | 286751 | ESK5A | RURAL | Weather | 656.49 | 21 | 13786.29 | 0.039805 | 0.0018955
2012-12-17 | 286751 | MRB1 | URBAN | Weather | 1 | 9 | 9 | 9.0876e-06 | 1.0097e-06
2012-12-17 | 286751 | MRB2 | RURAL | Weather | 52.6 | 9 | 473.4 | 0.0013668 | 0.00015187
2012-12-17 | 286751 | SDM1 | RURAL | Weather | 196 | 18 | 3528 | 0.010186 | 0.00056591
2012-12-17 | 286751 | TGW1 | RURAL | Weather | 444.04 | 21 | 9324.84 | 0.026924 | 0.0012821
2012-12-17 | 286751 | TGW2 | RURAL | Weather | 309.49 | 21 | 6499.29 | 0.018765 | 0.00089359
2012-12-17 | 286751 | TGW3 | RURAL | Weather | 667 | 21 | 14007 | 0.040442 | 0.0019258
2012-12-17 | 286751 | TGW4 | RURAL | Weather | 631 | 21 | 13251 | 0.03826 | 0.0018219
2012-12-17 | 286761 | PWC4 | RURAL | Weather | 29.5 | 174.5 | 10295.5 | 0.029726 | 8.5175e-05
2012-12-17 | 286780 | RWD1 | RURAL | Other | 2.31 | 22 | 50.82 | 0.00014673 | 6.6697e-06
2012-12-17 | 286800 | MBG4 | RURAL | Other | 3.2 | 172 | 550.4 | 0.0015892 | 9.2394e-06
2012-12-17 | 286801 | ESK3A | RURAL | Weather | 3.2 | 80 | 256 | 0.00073915 | 9.2394e-06
2012-12-17 | 286802 | BNH1B | RURAL | Weather | 2 | 545 | 1090 | 0.0031472 | 5.7746e-06
2012-12-17 | 286803 | GTN12A | RURAL | Weather | 2.4 | 248 | 595.2 | 0.0017185 | 6.9295e-06
2012-12-17 | 286804 | GTN5B | RURAL | Weather | 6 | 297 | 1782 | 0.0051452 | 1.7324e-05
2012-12-17 | 286812 | KSN1 | URBAN | Other | 29.6 | 79.15 | 2342.84 | 0.0023656 | 2.9888e-05
2012-12-17 | 286815 | NRA15A | RURAL | Animals | 14.52 | 52 | 755.04 | 0.00218 | 4.1924e-05
2012-12-17 | 286816 | MFD2A | URBAN | Operational error | 72 | 48 | 3456 | 0.0034896 | 7.2701e-05
2012-12-17 | 286817 | BPN29A | URBAN | Other | 26.4 | 85 | 2244 | 0.0022658 | 2.6657e-05
2012-12-17 | 286980 | NBR2 | URBAN | Equipment failure | 23 | 75.1667 | 1728.8333 | 0.0017457 | 2.3224e-05
2012-12-17 | 287148 | SHW12 | URBAN | Other | 48.84 | 42 | 2051.28 | 0.0020712 | 4.9315e-05
2012-12-17 | 287149 | GAP1A | URBAN | Equipment failure | 42.57 | 222 | 9450.54 | 0.0095425 | 4.2984e-05
2012-12-17 | 287390 | MRK3 | URBAN | Vegetation | 39.27 | 103 | 4044.81 | 0.0040842 | 3.9652e-05
2012-12-17 | 287391 | LGV6A | RURAL | Other | 8.58 | 80 | 686.4 | 0.0019818 | 2.4773e-05
2012-12-18 | 286776 | CRY5A | RURAL | Equipment failure | 95.49 | 160.7632 | 33955.31 | 0.098033 | 0.00027569
2012-12-18 | 286806 | GBN4 | RURAL | Weather | 23 | 57 | 1311 | 0.003785 | 6.6404e-05
2012-12-18 | 286808 | WMD14A | RURAL | Third party impacts | 1440.58 | 21 | 30252.18 | 0.087342 | 0.0041591
2012-12-18 | 286814 | KCY2 | RURAL | Other | 5 | 16 | 80 | 0.00023097 | 1.4436e-05
2012-12-18 | 286840 | JBB16A | RURAL | Vegetation | 236.5 | 59.9189 | 25549 | 0.073763 | 0.0006828
2012-12-18 | 286844 | KMR27A | URBAN | Other | 21.3 | 186 | 3961.8 | 0.0040003 | 2.1507e-05
2012-12-18 | 286879 | GTN12A | RURAL | Weather | 573.66 | 96.4889 | 48976.5 | 0.1414 | 0.0016562
2012-12-18 | 286880 | LLY3 | RURAL | Weather | 18 | 42 | 756 | 0.0021827 | 5.1968e-05
2012-12-18 | 286898 | CPD1 | RURAL | Weather | 32 | 131.0714 | 3887 | 0.011222 | 9.2388e-05
2012-12-18 | 286926 | RWD1 | RURAL | Weather | 18.76 | 141 | 2645.16 | 0.0076369 | 5.4162e-05
2012-12-18 | 286930 | BTN2 | RURAL | Weather | 56.5 | 26 | 1469 | 0.0042412 | 0.00016312
2012-12-18 | 286931 | FDS1 | RURAL | Weather | 31 | 210 | 6510 | 0.018795 | 8.9501e-05
2012-12-18 | 286932 | LTA4A | URBAN | Equipment failure | 30.525 | 23 | 702.075 | 0.0007089 | 3.0822e-05
2012-12-18 | 286935 | MAI14 | URBAN | Weather | 1738.41 | 190.7647 | 331855.35 | 0.33508 | 0.0017553
2012-12-18 | 286936 | CMA8A | RURAL | Equipment failure | 40 | 73 | 3992 | 0.011525 | 0.00011548
2012-12-18 | 286940 | IPL1 | RURAL | Weather | 1 | 339 | 339 | 0.00097874 | 2.8871e-06
2012-12-18 | 286960 | WMR1 | RURAL | Weather | 3.5 | 258 | 903 | 0.0026071 | 1.0105e-05
2012-12-18 | 286981 | GYGGYS6 | RURAL | Weather | 1.5 | 117.1667 | 175.75 | 0.00050741 | 4.3307e-06
2012-12-18 | 286982 | AMR2 | RURAL | Weather | 3 | 68 | 204 | 0.00058897 | 8.6614e-06
2012-12-18 | 286983 | GBN4 | RURAL | Weather | 9 | 55.6667 | 501 | 0.0014464 | 2.5984e-05
2012-12-18 | 286984 | GBN4 | RURAL | Weather | 8 | 83 | 664 | 0.0019171 | 2.3097e-05
2012-12-18 | 286985 | BMT2 | RURAL | Weather | 8.58 | 168.5 | 1445.73 | 0.004174 | 2.4772e-05
2012-12-18 | 286986 | AMR3 | RURAL | Weather | 8 | 23.5 | 188 | 0.00054278 | 2.3097e-05
2012-12-18 | 286987 | AMR2 | RURAL | Weather | 8.5 | 220.6667 | 1875.6667 | 0.0054153 | 2.4541e-05
2012-12-18 | 286988 | MLY3 | RURAL | Weather | 17 | 162.6667 | 2765.3333 | 0.0079839 | 4.9081e-05
2012-12-18 | 286989 | BMT1 | RURAL | Weather | 6 | 176.5 | 1059 | 0.0030575 | 1.7323e-05
2012-12-18 | 287002 | MSV2 | RURAL | Weather | 0.8 | 190 | 152 | 0.00043884 | 2.3097e-06
2012-12-18 | 287003 | THL1 | RURAL | Weather | 4.62 | 73 | 337.26 | 0.00097371 | 1.3339e-05
2012-12-18 | 287004 | MSV2 | RURAL | Weather | 3 | 242 | 726 | 0.0020961 | 8.6614e-06
2012-12-18 | 287005 | GTN15A | RURAL | Weather | 18.8 | 85 | 1598 | 0.0046136 | 5.4278e-05
2012-12-18 | 287006 | CPD2A | RURAL | Weather | 1 | 184 | 184 | 0.00053123 | 2.8871e-06
2012-12-18 | 287007 | CPD1 | RURAL | Weather | 6 | 81 | 486 | 0.0014031 | 1.7323e-05
2012-12-18 | 287008 | GGR1 | RURAL | Weather | 3.3 | 91 | 300.3 | 0.000867 | 9.5275e-06
2012-12-18 | 287010 | FDS3 | RURAL | Weather | 1 | 153 | 153 | 0.00044173 | 2.8871e-06
2012-12-18 | 287011 | FDS1 | RURAL | Weather | 4 | 197 | 788 | 0.0022751 | 1.1548e-05
2012-12-18 | 287012 | FDS3 | RURAL | Weather | 0.8 | 153 | 122.4 | 0.00035338 | 2.3097e-06
2012-12-18 | 287013 | FDS1 | RURAL | Weather | 0.5 | 243 | 121.5 | 0.00035079 | 1.4436e-06
2012-12-18 | 287014 | KBR6A | RURAL | Weather | 4.8 | 99 | 475.2 | 0.001372 | 1.3858e-05
2012-12-18 | 287015 | BNH6A | RURAL | Weather | 1 | 117 | 117 | 0.00033779 | 2.8871e-06
2012-12-18 | 287016 | TGW3 | RURAL | Weather | 1 | 132 | 132 | 0.0003811 | 2.8871e-06
2012-12-18 | 287017 | TGW2 | RURAL | Weather | 2.4 | 164 | 393.6 | 0.0011364 | 6.9291e-06
2012-12-18 | 287018 | TGW1 | RURAL | Weather | 2.33 | 128 | 298.24 | 0.00086106 | 6.727e-06
2012-12-18 | 287019 | ESK3A | RURAL | Weather | 1 | 41 | 41 | 0.00011837 | 2.8871e-06
2012-12-18 | 287020 | ESK3A | RURAL | Weather | 5 | 81 | 405 | 0.0011693 | 1.4436e-05
2012-12-18 | 287021 | KBN2A | RURAL | Weather | 21.12 | 163 | 3442.56 | 0.0099391 | 6.0976e-05
2012-12-18 | 287022 | RWD1 | RURAL | Weather | 1 | 136 | 136 | 0.00039265 | 2.8871e-06
2012-12-18 | 287023 | RST2A | URBAN | Other | 23.43 | 110 | 2577.3 | 0.0026023 | 2.3658e-05
2012-12-18 | 287026 | FDS4 | RURAL | Other | 418.34 | 20 | 8366.8 | 0.024156 | 0.0012078
2012-12-18 | 287042 | ESK5A | RURAL | Weather | 7 | 18 | 126 | 0.00036378 | 2.021e-05
2012-12-18 | 287043 | BLH9B | URBAN | Third party impacts | 14 | 152 | 2128 | 0.0021487 | 1.4136e-05
2012-12-18 | 287202 | HPE13A | URBAN | Other | 36.465 | 61 | 2224.365 | 0.002246 | 3.6819e-05
2012-12-18 | 287204 | CMA8A | RURAL | Other | 12.8 | 225.9833 | 2892.5867 | 0.0083513 | 3.6955e-05
2012-12-18 | 287223 | FDS3 | RURAL | Other | 5.6 | 103.5667 | 579.9733 | 0.0016745 | 1.6168e-05
2012-12-18 | 287392 | PPE5A | RURAL | Equipment failure | 3 | 122.1667 | 366.5 | 0.0010581 | 8.6614e-06
2012-12-19 | 286938 | CHL11A | RURAL | Equipment failure | 132.5 | 78 | 10335 | 0.029838 | 0.00038254
2012-12-19 | 286939 | CHL3 | URBAN | Equipment failure | 1 | 77 | 77 | 7.7746e-05 | 1.0097e-06
2012-12-19 | 287000 | GTN12A | RURAL | Weather | 0.66 | 107 | 70.62 | 0.00020389 | 1.9055e-06
2012-12-19 | 287001 | CPD1 | RURAL | Weather | 2.8 | 128 | 358.4 | 0.0010347 | 8.0839e-06
2012-12-19 | 287009 | FDS1 | RURAL | Weather | 2 | 161 | 322 | 0.00092965 | 5.7742e-06
2012-12-19 | 287045 | BLBNFM6 | URBAN | Equipment failure | 125 | 95 | 11875 | 0.01199 | 0.00012621
2012-12-19 | 287052 | PWC6 | RURAL | Other | 59.5 | 140 | 8330 | 0.02405 | 0.00017178
2012-12-19 | 287052 | RLB11B | URBAN | Other | 43 | 140 | 6020 | 0.0060783 | 4.3417e-05
2012-12-19 | 287061 | BTA5A | RURAL | Equipment failure | 7 | 71 | 497 | 0.0014349 | 2.021e-05
2012-12-19 | 287079 | ABY5A | RURAL | Equipment failure | 33.5 | 9.4667 | 316.5 | 0.00091377 | 9.6718e-05
2012-12-19 | 287079 | EZRRWD4 | RURAL | Equipment failure | 55 | 10 | 550 | 0.0015879 | 0.00015879
2012-12-19 | 287080 | 436 | URBAN | Equipment failure | 1 | 80 | 80 | 8.0775e-05 | 1.0097e-06
2012-12-19 | 287081 | 1129 | URBAN | Animals | 341.5 | 52 | 17758 | 0.01793 | 0.00034481
2012-12-19 | 287081 | 1255 | URBAN | Animals | 1 | 52 | 52 | 5.2504e-05 | 1.0097e-06
2012-12-19 | 287081 | 1256 | URBAN | Animals | 2 | 52 | 104 | 0.00010501 | 2.0194e-06
2012-12-19 | 287081 | GCLSBY7 | URBAN | Animals | 415.44 | 52 | 21602.88 | 0.021812 | 0.00041946
2012-12-19 | 287081 | GECT0 | URBAN | Animals | 1 | 52 | 52 | 5.2504e-05 | 1.0097e-06
2012-12-19 | 287081 | RLA2 | URBAN | Animals | 255.59 | 52 | 13290.68 | 0.013419 | 0.00025807
2012-12-19 | 287081 | RLA4 | URBAN | Animals | 468.5 | 52 | 24362 | 0.024598 | 0.00047304
2012-12-19 | 287081 | RLA5 | URBAN | Animals | 2018.5 | 52 | 104962 | 0.10598 | 0.0020381
2012-12-19 | 287081 | RLA6 | URBAN | Animals | 511.16 | 52 | 26580.32 | 0.026838 | 0.00051611
2012-12-19 | 287081 | RLA7 | URBAN | Animals | 158 | 52 | 8216 | 0.0082956 | 0.00015953
2012-12-19 | 287081 | RLA8 | URBAN | Animals | 347.16 | 52 | 18052.32 | 0.018227 | 0.00035052
2012-12-19 | 287081 | SBY4 | URBAN | Animals | 509.6 | 52 | 26499.2 | 0.026756 | 0.00051454
2012-12-19 | 287081 | SBY6 | URBAN | Animals | 491.36 | 52 | 25550.72 | 0.025798 | 0.00049612
2012-12-19 | 287081 | SBY8 | URBAN | Animals | 912.83 | 52 | 47467.16 | 0.047927 | 0.00092167
2012-12-19 | 287081 | WDT1 | URBAN | Animals | 12.26 | 52 | 637.52 | 0.0006437 | 1.2379e-05
2012-12-19 | 287081 | WDT2 | URBAN | Animals | 0.71 | 52 | 36.92 | 3.7278e-05 | 7.1688e-07
2012-12-19 | 287120 | FDS3 | RURAL | Other | 1 | 81 | 81 | 0.00023386 | 2.8871e-06
2012-12-19 | 287121 | RWD1 | RURAL | Weather | 2.4 | 342 | 820.8 | 0.0023697 | 6.929e-06
2012-12-19 | 287122 | MCW4 | RURAL | Other | 0.66 | 144 | 95.04 | 0.00027439 | 1.9055e-06
2012-12-19 | 287123 | RWD1 | RURAL | Weather | 1.6 | 211 | 337.6 | 0.00097468 | 4.6194e-06
2012-12-19 | 287220 | YDA5A | RURAL | Equipment failure | 46.33 | 93.7833 | 4344.9818 | 0.012544 | 0.00013376
2012-12-19 | 287620 | YDA5A | RURAL | Equipment failure | 46.33 | 42 | 1945.86 | 0.0056179 | 0.00013376
2012-12-20 | 287128 | SIS2 | RURAL | Other | 17 | 20 | 340 | 0.00098161 | 4.908e-05
2012-12-20 | 287144 | SMF2A | RURAL | Other | 10.5 | 13 | 136.5 | 0.00039409 | 3.0314e-05
2012-12-20 | 287150 | DRA11 | URBAN | Third party impacts | 31.02 | 42 | 1302.84 | 0.0013154 | 3.132e-05
2012-12-20 | 287151 | HPK10 | URBAN | Equipment failure | 985.75 | 5.3333 | 6737.25 | 0.0068023 | 0.00099527
2012-12-20 | 287160 | BLB8A | URBAN | Equipment failure | 1416.32 | 34 | 48154.88 | 0.04862 | 0.00143
2012-12-20 | 287200 | KBN5A | RURAL | Other | 3.795 | 75 | 284.625 | 0.00082173 | 1.0956e-05
2012-12-20 | 287201 | KBR6A | RURAL | Weather | 0.8 | 86 | 68.8 | 0.00019863 | 2.3097e-06
2012-12-20 | 287203 | FDS3 | RURAL | Weather | 3 | 114 | 342 | 0.00098738 | 8.6612e-06
2012-12-20 | 287393 | MTG11A | URBAN | Other | 43 | 30 | 1290 | 0.0013025 | 4.3415e-05
2012-12-20 | 287799 | BHD46A | URBAN | Equipment failure | 45 | 400 | 18000 | 0.018174 | 4.5435e-05
2012-12-21 | 287243 | STL1A | URBAN | Other | 26.1 | 140 | 3654 | 0.0036892 | 2.6351e-05
2012-12-21 | 287244 | BTN7 | RURAL | Weather | 76.98 | 22 | 1693.56 | 0.0048894 | 0.00022225
2012-12-21 | 287247 | BDT1 | RURAL | Weather | 670.5 | 25 | 16762.5 | 0.048394 | 0.0019358
2012-12-21 | 287268 | CPL25B | URBAN | Equipment failure | 14.875 | 140 | 2082.5 | 0.0021025 | 1.5018e-05
2012-12-21 | 287269 | NMC15A | RURAL | Animals | 2 | 168 | 336 | 0.00097005 | 5.7741e-06
2012-12-21 | 287270 | CFD8A | URBAN | Animals | 1249.99 | 60.5385 | 79436.915 | 0.080202 | 0.001262
2012-12-21 | 287271 | CVL15A | URBAN | Equipment failure | 364.66 | 76.1111 | 24200.47 | 0.024433 | 0.00036817
2012-12-21 | 287323 | KBR2A | RURAL | Weather | 1.98 | 167 | 330.66 | 0.00095464 | 5.7164e-06
2012-12-21 | 287324 | KBR2A | RURAL | Weather | 1.98 | 116 | 229.68 | 0.0006631 | 5.7164e-06
2012-12-21 | 287565 | SHW3 | URBAN | Other | 132.5 | 53 | 7022.5 | 0.0070901 | 0.00013378
2012-12-21 | 287796 | BDT1 | RURAL | Other | 8.4 | 30 | 252 | 0.00072754 | 2.4251e-05
2012-12-21 | 287797 | BDT5 | RURAL | Other | 0.8 | 207 | 165.6 | 0.0004781 | 2.3097e-06
2012-12-21 | 288275 | MTB3A | RURAL | Other | 9.2 | 126.6667 | 1165.3333 | 0.0033644 | 2.6561e-05
2012-12-21 | 288276 | MTB3A | RURAL | Other | 3.2 | 350.3 | 1120.96 | 0.0032363 | 9.2386e-06
2012-12-22 | 287274 | CBW11 | RURAL | Other | 1769.23 | 147.1951 | 255499.72 | 0.73764 | 0.0051079
2012-12-22 | 287280 | IPL3 | RURAL | Equipment failure | 499.46 | 45.9721 | 17358.3 | 0.050114 | 0.001442
2012-12-22 | 287281 | BIS1 | RURAL | Animals | 77 | 2 | 154 | 0.00044461 | 0.0002223
2012-12-22 | 287285 | CPL23A | RURAL | Animals | 924.99 | 17 | 15724.83 | 0.045398 | 0.0026705
2012-12-22 | 287285 | CPL26A | URBAN | Animals | 423.94 | 54.4375 | 56633.48 | 0.057177 | 0.00042801
2012-12-22 | 287394 | LHM5 | RURAL | Animals | 38.28 | 32 | 1224.96 | 0.0035365 | 0.00011052
2012-12-22 | 287395 | NMC16A | RURAL | Equipment failure | 25.41 | 122 | 3100.02 | 0.0089499 | 7.336e-05
2012-12-22 | 287621 | CMD15A | URBAN | Other | 71.94 | 19 | 1366.86 | 0.00138 | 7.2631e-05
2012-12-22 | 287794 | PBH3 | URBAN | Other | 1.255 | 185 | 232.175 | 0.0002344 | 1.267e-06
2012-12-23 | 287300 | HIS5A | URBAN | Equipment failure | 736 | 4 | 2944 | 0.0029722 | 0.00074306
2012-12-23 | 287300 | HIS5B | URBAN | Equipment failure | 854 | 103.6875 | 107829 | 0.10886 | 0.00086219
2012-12-23 | 287306 | SPO5A | URBAN | Third party impacts | 680.91 | 113.25 | 73380.24 | 0.074084 | 0.00068744
2012-12-23 | 287321 | TGW2 | RURAL | Weather | 1.98 | 96 | 190.08 | 0.00054876 | 5.7162e-06
2012-12-23 | 287322 | BNH1B | RURAL | Animals | 1 | 80 | 80 | 0.00023096 | 2.887e-06
2012-12-23 | 287396 | ARG10 | URBAN | Other | 40.26 | 66 | 2657.16 | 0.0026826 | 4.0646e-05
2012-12-23 | 287793 | MMC33A | URBAN | Other | 32.8 | 112 | 3673.6 | 0.0037088 | 3.3115e-05
2012-12-24 | 287309 | RPN7A | RURAL | Other | 15 | 59.75 | 1848 | 0.0053351 | 4.3305e-05
2012-12-24 | 287310 | AHD16 | URBAN | Equipment failure | 1341.49 | 35 | 46952.15 | 0.0474 | 0.0013543
2012-12-24 | 287341 | MDR31A | URBAN | Other | 51.67 | 8 | 413.36 | 0.0004173 | 5.2162e-05
2012-12-24 | 287342 | TRP4 | RURAL | Third party impacts | 381.66 | 180.3846 | 68528.13 | 0.19784 | 0.0011018
2012-12-24 | 287566 | IDY6A | URBAN | Other | 41.7611 | 33 | 1378.1163 | 0.0013913 | 4.2159e-05
2012-12-24 | 287623 | LBH5A | RURAL | Other | 12.5 | 50 | 625 | 0.0018044 | 3.6087e-05
2012-12-24 | 287624 | PWC5 | RURAL | Other | 25 | 16 | 400 | 0.0011548 | 7.2175e-05
2012-12-25 | 287348 | MGP4 | RURAL | Equipment failure | 3.5 | 71 | 248.5 | 0.00071742 | 1.0104e-05
2012-12-25 | 287397 | TMH12A | URBAN | Animals | 56.76 | 71 | 4029.96 | 0.0040682 | 5.7299e-05
2012-12-25 | 287403 | SMF2A | RURAL | Animals | 18 | 114 | 2052 | 0.0059241 | 5.1966e-05
2012-12-25 | 287404 | KLG17A | URBAN | Animals | 52 | 83 | 4316 | 0.004357 | 5.2494e-05
2012-12-25 | 287406 | WSE5A | RURAL | Other | 4 | 46 | 184 | 0.00053121 | 1.1548e-05
2012-12-25 | 287625 | WMD10A | URBAN | Animals | 53 | 58.1667 | 3082.8333 | 0.0031121 | 5.3503e-05
2012-12-26 | 287354 | RPN8 | RURAL | Weather | 1823.5 | 93 | 174014 | 0.50237 | 0.0052644
2012-12-26 | 287355 | JBB16A | RURAL | Weather | 692 | 25 | 17300 | 0.049945 | 0.0019978
2012-12-26 | 287357 | KSN3 | URBAN | Equipment failure | 631 | 140.3871 | 88913 | 0.089756 | 0.00063698
2012-12-26 | 287358 | WMD8A | URBAN | Animals | 1 | 85 | 85 | 8.5806e-05 | 1.0095e-06
2012-12-26 | 287358 | WMD8B | RURAL | Animals | 635.91 | 47.3333 | 31170.41 | 0.089988 | 0.0018359
2012-12-26 | 287359 | AHD16 | URBAN | Equipment failure | 1341.49 | 57.619 | 80332.91 | 0.081095 | 0.0013542
2012-12-26 | 287360 | JBB1B | RURAL | Weather | 539 | 3 | 1617 | 0.0046682 | 0.0015561
2012-12-26 | 287363 | KSN7 | RURAL | Third party impacts | 120 | 68 | 8160 | 0.023558 | 0.00034644
2012-12-26 | 287398 | BLH11B | URBAN | Third party impacts | 19 | 44 | 836 | 0.00084393 | 1.918e-05
2012-12-26 | 287399 | KSN1 | URBAN | Animals | 29.7 | 20 | 594 | 0.00059963 | 2.9982e-05
2012-12-26 | 287402 | GBG2A | URBAN | Equipment failure | 53.79 | 36 | 1936.44 | 0.0019548 | 5.43e-05
2012-12-26 | 287405 | MFN15A | RURAL | Third party impacts | 44.5 | 70 | 3115 | 0.0089929 | 0.00012847
2012-12-27 | 287367 | MLT2B | URBAN | Animals | 1231.4 | 15 | 18471 | 0.018645 | 0.001243
2012-12-27 | 287370 | MLT2B | URBAN | Animals | 1231.4 | 8 | 9851.2 | 0.0099441 | 0.001243
2012-12-27 | 287371 | AHL9A | URBAN | Equipment failure | 67.2 | 112 | 7526.4 | 0.0075974 | 6.7834e-05
2012-12-27 | 287400 | QPT21 | URBAN | Animals | 61.71 | 105 | 6479.55 | 0.0065407 | 6.2292e-05
2012-12-27 | 287409 | MRK5A | URBAN | Equipment failure | 11.6 | 110 | 1276 | 0.001288 | 1.1709e-05
2012-12-27 | 287440 | CBW6 | RURAL | Animals | 25.08 | 116 | 2909.28 | 0.0083991 | 7.2406e-05
2012-12-27 | 287441 | ZMR9 | URBAN | Equipment failure | 106.5 | 130 | 13845 | 0.013976 | 0.0001075
2012-12-27 | 287442 | RPN6A | RURAL | Equipment failure | 17.325 | 196 | 3395.7 | 0.0098033 | 5.0017e-05
2012-12-27 | 287569 | TMH3A | URBAN | Other | 21.12 | 166 | 3505.92 | 0.003539 | 2.1319e-05
2012-12-27 | 287626 | CLM9 | URBAN | Other | 13.2 | 64 | 844.8 | 0.00085277 | 1.3325e-05
2012-12-27 | 287788 | KRA3 | URBAN | Other | 101 | 12 | 1212 | 0.0012234 | 0.00010195
2012-12-28 | 287438 | TGP8A | URBAN | Other | 829.5 | 86 | 71337 | 0.072008 | 0.0008373
2012-12-28 | 287452 | EMD2 | RURAL | Other | 493 | 87.5278 | 41514.5 | 0.11985 | 0.0014233
2012-12-28 | 287468 | NRG9 | RURAL | Weather | 1946 | 72 | 140112 | 0.4045 | 0.005618
2012-12-28 | 287471 | NRG16A | RURAL | Weather | 1.98 | 162 | 320.76 | 0.00092603 | 5.7162e-06
2012-12-28 | 287472 | CMA8A | RURAL | Weather | 189.99 | 142.9474 | 28418.76 | 0.082044 | 0.0005485
2012-12-28 | 287473 | RIS2 | URBAN | Equipment failure | 42.83 | 266 | 11392.78 | 0.0115 | 4.3233e-05
2012-12-28 | 287482 | PBH4 | URBAN | Third party impacts | 0.96 | 95 | 91.2 | 9.2058e-05 | 9.6903e-07
2012-12-28 | 287484 | WED3A | URBAN | Animals | 608.33 | 74.3125 | 42449.13 | 0.042848 | 0.00061405
2012-12-28 | 287486 | PPE13A | RURAL | Vegetation | 36 | 54 | 1944 | 0.0056123 | 0.00010393
2012-12-28 | 287534 | KCY5 | RURAL | Equipment failure | 9.5 | 230 | 2185 | 0.006308 | 2.7426e-05
2012-12-28 | 287535 | CPB8 | RURAL | Equipment failure | 9 | 85 | 765 | 0.0022085 | 2.5983e-05
2012-12-28 | 287537 | KCY4 | RURAL | Weather | 3.5 | 118 | 413 | 0.0011923 | 1.0104e-05
2012-12-28 | 287576 | HWD2B | RURAL | Other | 1.98 | 72 | 142.56 | 0.00041157 | 5.7162e-06
2012-12-29 | 287494 | AMR1 | RURAL | Equipment failure | 45.5 | 161 | 7325.5 | 0.021149 | 0.00013136
2012-12-29 | 287497 | HDA10A | URBAN | Animals | 1739.83 | 100 | 173983 | 0.17561 | 0.0017561
2012-12-29 | 287499 | CPL5A | URBAN | Third party impacts | 17.5 | 326 | 5705 | 0.0057585 | 1.7664e-05
2012-12-29 | 287559 | BNH1B | RURAL | Animals | 3 | 72 | 216 | 0.00062359 | 8.661e-06
2012-12-29 | 287627 | GBN4 | RURAL | Weather | 1 | 300 | 300 | 0.0008661 | 2.887e-06
2012-12-29 | 287630 | CRM13A | URBAN | Other | 43.1178 | 119 | 5131.0182 | 0.0051791 | 4.3522e-05
2012-12-29 | 287674 | NSW8A | URBAN | Equipment failure | 67 | 100 | 6700 | 0.0067628 | 6.7628e-05
2012-12-29 | 287784 | JBB13A | RURAL | Other | 15 | 59 | 885 | 0.002555 | 4.3305e-05
2012-12-30 | 287520 | BLH12A | RURAL | Equipment failure | 661.49 | 85.3736 | 58450.25 | 0.16875 | 0.0019097
2012-12-30 | 287523 | NRA1A | RURAL | Animals | 893 | 59.9213 | 56993 | 0.16454 | 0.0025781
2012-12-30 | 287530 | NDH1 | URBAN | Equipment failure | 17.82 | 96 | 1710.72 | 0.0017267 | 1.7986e-05
2012-12-30 | 287531 | SMF3A | RURAL | Other | 2.97 | 100 | 297 | 0.00085744 | 8.5744e-06
2012-12-30 | 287532 | RCF1A | URBAN | Vegetation | 125.5 | 68 | 8534 | 0.0086137 | 0.00012667
2012-12-30 | 287533 | MFD13A | RURAL | Animals | 17.16 | 95 | 1630.2 | 0.0047064 | 4.9541e-05
2012-12-30 | 287560 | PRG2A | RURAL | Other | 0.67 | 81 | 54.27 | 0.00015668 | 1.9343e-06
2012-12-30 | 287567 | INA2A | URBAN | Other | 42.88 | 5 | 214.4 | 0.0002164 | 4.328e-05
2012-12-31 | 287529 | NGI2B | RURAL | Animals | 17.6 | 83 | 1460.8 | 0.0042173 | 5.0811e-05
2012-12-31 | 287539 | WSE6A | RURAL | Vegetation | 20.5 | 19 | 389.5 | 0.0011245 | 5.9183e-05
2012-12-31 | 287541 | MTG15A | URBAN | Equipment failure | 58 | 56 | 3248 | 0.0032782 | 5.854e-05
2012-12-31 | 287544 | PWC6 | RURAL | Equipment failure | 595 | 29 | 17255 | 0.049815 | 0.0017178
2012-12-31 | 287549 | 1129 | URBAN | Animals | 342.5 | 75.9286 | 26149 | 0.026392 | 0.00034569
2012-12-31 | 287550 | BDA12A | URBAN | Other | 1 | 33 | 33 | 3.3307e-05 | 1.0093e-06
2012-12-31 | 287550 | BDA12B | URBAN | Other | 1585.67 | 33 | 52327.11 | 0.052814 | 0.0016004
2012-12-31 | 287551 | WNM1A | URBAN | Animals | 1646 | 159.48 | 257603.5 | 0.26 | 0.0016613
2012-12-31 | 287561 | BNH6A | RURAL | Weather | 1.34 | 62 | 83.08 | 0.00023985 | 3.8686e-06
2012-12-31 | 287562 | LLY5 | RURAL | Weather | 1 | 177 | 177 | 0.000511 | 2.887e-06
2012-12-31 | 287563 | LLY1 | RURAL | Other | 1.34 | 221 | 296.14 | 0.00085495 | 3.8686e-06
2012-12-31 | 287634 | NMC1B | RURAL | Other | 1.98 | 54 | 106.92 | 0.00030868 | 5.7162e-06
2013-01-01 | 287552 | RBY7A | URBAN | Animals | 0.67 | 224 | 150.08 | 0.00015147 | 6.7621e-07
2013-01-01 | 287553 | NMC1B | RURAL | Other | 9.57 | 115 | 1100.55 | 0.0031773 | 2.7629e-05
2013-01-01 | 287554 | MLB8A | RURAL | Equipment failure | 1.225 | 160 | 196 | 0.00056586 | 3.5366e-06
2013-01-01 | 287555 | RHG6 | URBAN | Other | 16.61 | 51 | 847.11 | 0.00085497 | 1.6764e-05
2013-01-01 | 287556 | NVL12A | URBAN | Other | 116 | 76 | 8816 | 0.0088978 | 0.00011708
2013-01-01 | 287622 | THL3 | RURAL | Weather | 1 | 75 | 75 | 0.00021653 | 2.887e-06
2013-01-02 | 287557 | SBH9 | URBAN | Animals | 1188.5 | 130 | 151378.5 | 0.15278 | 0.0011995
2013-01-02 | 287571 | MFD5A | RURAL | Equipment failure | 18 | 82 | 1476 | 0.0042613 | 5.1967e-05
2013-01-02 | 287577 | TGP8A | URBAN | Equipment failure | 67.32 | 138 | 9290.16 | 0.0093761 | 6.7943e-05
2013-01-02 | 287582 | CBW12 | URBAN | Equipment failure | 65.5 | 79.5 | 5218.5 | 0.0052668 | 6.6106e-05
2013-01-02 | 287583 | TWG18 | URBAN | Equipment failure | 50 | 114 | 5700 | 0.0057527 | 5.0462e-05
2013-01-02 | 287600 | NVL8B | URBAN | Animals | 202.5 | 3 | 607.5 | 0.00061312 | 0.00020437
2013-01-02 | 287601 | NBR7 | URBAN | Animals | 46.5 | 108 | 5022 | 0.0050684 | 4.693e-05
2013-01-02 | 287603 | SMF3A | RURAL | Vegetation | 66 | 33 | 2178 | 0.006288 | 0.00019055
2013-01-03 | 287604 | INA1A | URBAN | Animals | 778 | 105.7059 | 81260 | 0.082009 | 0.00078517
2013-01-03 | 287605 | MGP4 | RURAL | Equipment failure | 3 | 155 | 465 | 0.0013425 | 8.6613e-06
2013-01-03 | 287606 | BMT3 | RURAL | Equipment failure | 51 | 168 | 8568 | 0.024737 | 0.00014724
2013-01-03 | 287628 | WFD1B | RURAL | Equipment failure | 29.97 | 51 | 1528.47 | 0.0044129 | 8.6527e-05
2013-01-03 | 287646 | NRG6 | URBAN | Equipment failure | 35 | 70 | 2450 | 0.0024726 | 3.5323e-05
2013-01-03 | 287662 | NSW28 | URBAN | Equipment failure | 104 | 107 | 11128 | 0.011231 | 0.00010496
2013-01-03 | 287663 | SMF6A | RURAL | Vegetation | 20 | 9 | 180 | 0.00051968 | 5.7742e-05
2013-01-03 | 287664 | MAI13 | URBAN | Animals | 7 | 84 | 588 | 0.00059342 | 7.0645e-06
2013-01-03 | 287668 | CBW9 | URBAN | Equipment failure | 421 | 96 | 62364 | 0.062939 | 0.00042488
2013-01-03 | 287677 | CPR7 | URBAN | Third party impacts | 42.4 | 575 | 24380 | 0.024605 | 4.2791e-05
2013-01-03 | 287682 | HPK8A | URBAN | Animals | 54.78 | 91 | 4984.98 | 0.0050309 | 5.5285e-05
2013-01-04 | 287675 | HDA11A | URBAN | Other | 139.92 | 68 | 9514.56 | 0.0096021 | 0.00014121
2013-01-04 | 287679 | CRBTHP14 | URBAN | Equipment failure | 112.5 | 65 | 7312.5 | 0.0073798 | 0.00011353
2013-01-04 | 287685 | CPC2A | RURAL | Vegetation | 1505 | 54 | 81270 | 0.23464 | 0.0043452
2013-01-04 | 287685 | CPC2B | URBAN | Vegetation | 1779.99 | 69.8667 | 138743.46 | 0.14002 | 0.0017964
2013-01-04 | 287686 | 467 | URBAN | Equipment failure | 1 | 159 | 159 | 0.00016046 | 1.0092e-06
2013-01-04 | 287687 | NRG12A | URBAN | Equipment failure | 41.16 | 334 | 14207.55 | 0.014338 | 4.1539e-05
2013-01-04 | 287702 | BBSRDL8 | RURAL | Equipment failure | 8 | 71 | 568 | 0.0016399 | 2.3097e-05
2013-01-04 | 287705 | CHL11A | RURAL | Animals | 74 | 36 | 2664 | 0.0076914 | 0.00021365
2013-01-05 | 287707 | CVL5A | RURAL | Animals | 38.28 | 58 | 2220.24 | 0.0064104 | 0.00011052
2013-01-05 | 287712 | NDH5A | URBAN | Other | 1995 | 41 | 81795 | 0.082546 | 0.0020133
2013-01-05 | 287718 | BLH11B | URBAN | Animals | 20 | 50 | 1000 | 0.0010092 | 2.0184e-05
2013-01-05 | 287719 | BRD2A | URBAN | Third party impacts | 113 | 22 | 2486 | 0.0025088 | 0.00011404
2013-01-05 | 287762 | CPD1 | RURAL | Equipment failure | 3.5 | 136 | 476 | 0.0013743 | 1.0105e-05
2013-01-06 | 287717 | NIP1A | URBAN | Other | 1340.67 | 41 | 54967.47 | 0.055471 | 0.001353
2013-01-06 | 287721 | NIP6A | URBAN | Equipment failure | 255.51 | 26.2857 | 10511.2 | 0.010607 | 0.00025785
2013-01-06 | 287721 | NIP6B | URBAN | Equipment failure | 1 | 20 | 20 | 2.0183e-05 | 1.0092e-06
2013-01-06 | 287722 | MGL2A | RURAL | Third party impacts | 587 | 91.0769 | 58150 | 0.16789 | 0.0016948
2013-01-06 | 287725 | MLS15A | URBAN | Other | 18.5 | 63 | 1165.5 | 0.0011762 | 1.8669e-05
2013-01-06 | 287726 | WNM5 | URBAN | Vegetation | 2186.5 | 35 | 76527.5 | 0.077229 | 0.0022065
2013-01-06 | 287727 | ZMR9 | URBAN | Equipment failure | 1 | 18 | 18 | 1.8165e-05 | 1.0092e-06
2013-01-06 | 287728 | PWC6 | RURAL | Equipment failure | 26 | 146 | 3796 | 0.01096 | 7.5069e-05
2013-01-06 | 287738 | PWC4 | RURAL | Vegetation | 103.5 | 19 | 1966.5 | 0.0056778 | 0.00029883
2013-01-06 | 287740 | RBY15 | URBAN | Animals | 1235.49 | 199.95 | 247082.02 | 0.24935 | 0.0012468
2013-01-06 | 287763 | NIP3A | URBAN | Other | 35.0075 | 137 | 4796.0275 | 0.00484 | 3.5328e-05
2013-01-07 | 287782 | MLS15A | URBAN | Other | 9.25 | 25 | 231.25 | 0.00023336 | 9.3345e-06
2013-01-07 | 287800 | BTA5A | RURAL | Vegetation | 1677.75 | 59 | 98987.25 | 0.28581 | 0.0048443
2013-01-07 | 287805 | HPK3A | URBAN | Other | 20.46 | 72 | 1473.12 | 0.0014866 | 2.0647e-05
2013-01-07 | 287818 | BLB2A | URBAN | Equipment failure | 9.25 | 37 | 342.25 | 0.00034538 | 9.3345e-06
2013-01-07 | 287819 | MGP13A | RURAL | Vegetation | 3.96 | 47 | 186.12 | 0.0005374 | 1.1434e-05
2013-01-07 | 287820 | AFD6 | URBAN | Equipment failure | 5.445 | 67 | 364.815 | 0.00036815 | 5.4948e-06
2013-01-07 | 287847 | WMD13A | RURAL | Equipment failure | 4 | 84 | 336 | 0.00097016 | 1.1549e-05
2013-01-07 | 287848 | NRA1A | RURAL | Animals | 883 | 100.1011 | 91677.5 | 0.26471 | 0.0025495
2013-01-07 | 287850 | GYM3 | URBAN | Third party impacts | 33 | 178 | 5874 | 0.0059277 | 3.3302e-05
2013-01-07 | 287851 | TMH3A | URBAN | Animals | 81 | 117 | 9477 | 0.0095636 | 8.174e-05
2013-01-07 | 287860 | IPL1 | RURAL | Animals | 1 | 127 | 127 | 0.0003667 | 2.8874e-06
2013-01-08 | 287882 | DRD2A | RURAL | Equipment failure | 1840 | 93.7576 | 172453.5 | 0.49795 | 0.0053129
2013-01-08 | 287882 | DRD2B | URBAN | Equipment failure | 1 | 72 | 72 | 7.2657e-05 | 1.0091e-06
2013-01-08 | 287900 | BDT6 | URBAN | Animals | 440.5 | 13 | 5726.5 | 0.0057787 | 0.00044452
2013-01-08 | 287902 | HTN24B | URBAN | Other | 151 | 106 | 16006 | 0.016152 | 0.00015238
2013-01-08 | 287906 | HPE13A | URBAN | Equipment failure | 4.275 | 15 | 64.125 | 6.471e-05 | 4.314e-06
2013-01-08 | 287909 | IPS16A | URBAN | Equipment failure | 61 | 202 | 4331 | 0.0043705 | 6.1557e-05
2013-01-08 | 287930 | GYN7A | RURAL | Other | 148.5 | 96 | 14256 | 0.041164 | 0.00042879
2013-01-08 | 287936 | KLG17A | URBAN | Animals | 34.32 | 69 | 2368.08 | 0.0023897 | 3.4633e-05
2013-01-09 | 287940 | TGW3 | RURAL | Equipment failure | 4 | 211 | 844 | 0.0024371 | 1.155e-05
2013-01-09 | 287943 | AMR3 | RURAL | Equipment failure | 23 | 217 | 4991 | 0.014412 | 6.6413e-05
2013-01-09 | 287944 | TGP8A | URBAN | Other | 67.32 | 58 | 3904.56 | 0.0039401 | 6.7933e-05
2013-01-09 | 287945 | NMK5 | URBAN | Other | 23.5 | 62 | 1457 | 0.0014703 | 2.3714e-05
2013-01-09 | 287947 | BBSRDL8 | RURAL | Equipment failure | 3 | 35 | 105 | 0.00030319 | 8.6625e-06
2013-01-09 | 287952 | CPD2A | RURAL | Equipment failure | 220 | 99.878 | 21089 | 0.060895 | 0.00063525
2013-01-09 | 287954 | MFN15A | RURAL | Equipment failure | 270 | 44 | 16721.1 | 0.048282 | 0.00077963
2013-01-09 | 287955 | NRG16A | RURAL | Third party impacts | 5.28 | 5 | 26.4 | 7.623e-05 | 1.5246e-05
2013-01-09 | 287958 | MFN15A | RURAL | Equipment failure | 7.59 | 57 | 432.63 | 0.0012492 | 2.1916e-05
2013-01-09 | 287959 | MCN3 | URBAN | Equipment failure | 1 | 59 | 59 | 5.9537e-05 | 1.0091e-06
2013-01-09 | 287960 | SFD4 | URBAN | Weather | 129 | 9.3333 | 1229 | 0.0012402 | 0.00013017
2013-01-09 | 287991 | KWA12A | URBAN | Equipment failure | 2363.5 | 82.7692 | 198333 | 0.20014 | 0.002385
2013-01-09 | 287995 | TCB2 | RURAL | Other | 1240.99 | 96 | 119135.04 | 0.344 | 0.0035834
2013-01-09 | 287995 | TCB3 | RURAL | Other | 1364.01 | 96 | 130944.96 | 0.3781 | 0.0039386
2013-01-09 | 287995 | TCBTR3 | URBAN | Other | 1 | 96 | 96 | 9.6874e-05 | 1.0091e-06
2013-01-09 | 287998 | RWD2 | RURAL | Other | 14 | 105 | 1470 | 0.0042446 | 4.0425e-05
2013-01-09 | 287999 | TWT11A | RURAL | Animals | 49.5 | 66 | 3267 | 0.0094335 | 0.00014293
2013-01-09 | 288025 | AMR3 | RURAL | Equipment failure | 1 | 1227 | 1227 | 0.003543 | 2.8875e-06
2013-01-09 | 288033 | CRM15A | URBAN | Equipment failure | 89 | 61 | 5429 | 0.0054784 | 8.981e-05
2013-01-09 | 288042 | ESK5A | RURAL | Operational error | 5.28 | 76 | 401.28 | 0.0011587 | 1.5246e-05
2013-01-09 | 288043 | ABY2A | RURAL | Weather | 8 | 426 | 3408 | 0.0098406 | 2.31e-05
2013-01-09 | 288072 | BDA12B | URBAN | Other | 81.405 | 119 | 9687.195 | 0.0097754 | 8.2146e-05
2013-01-09 | 296567 | BDA12B | URBAN | Other | 40.2 | 27 | 1085.4 | 0.0010953 | 4.0566e-05
2013-01-09 | 296576 | BRD11A | RURAL | Animals | 16.415 | 11 | 180.565 | 0.00052138 | 4.7398e-05
2013-01-09 | 296578 | RBY7A | URBAN | Other | 20.1 | 147 | 2954.7 | 0.0029816 | 2.0283e-05
2013-01-10 | 288001 | LBH1B | RURAL | Weather | 987.5 | 128.7101 | 112767.5 | 0.32563 | 0.0028515
2013-01-10 | 288002 | CFD6A | URBAN | Animals | 97.35 | 110 | 10708.5 | 0.010806 | 9.8235e-05
2013-01-10 | 288020 | LLY3 | RURAL | Weather | 14 | 72 | 1008 | 0.0029107 | 4.0427e-05
2013-01-10 | 288021 | WED16A | URBAN | Animals | 11 | 34 | 374 | 0.0003774 | 1.11e-05
2013-01-10 | 288023 | WRG19A | URBAN | Other | 17 | 10 | 170 | 0.00017155 | 1.7155e-05
2013-01-10 | 288026 | TGW3 | RURAL | Equipment failure | 12 | 575.5 | 6906 | 0.019942 | 3.4651e-05
2013-01-10 | 288027 | GAP6A | URBAN | Equipment failure | 50.05 | 40 | 2002 | 0.0020202 | 5.0505e-05
2013-01-10 | 288031 | TCB2 | RURAL | Other | 25.145 | 32 | 804.64 | 0.0023235 | 7.2609e-05
2013-01-10 | 288034 | KMR25A | RURAL | Weather | 8.5 | 31 | 263.5 | 0.00076089 | 2.4545e-05
2013-01-10 | 288036 | CRY2A | RURAL | Other | 4 | 186 | 744 | 0.0021484 | 1.155e-05
2013-01-10 | 288044 | BRD2A | URBAN | Equipment failure | 26.5 | 140 | 3710 | 0.0037437 | 2.6741e-05
2013-01-10 | 288045 | KBR6A | RURAL | Weather | 1 | 57 | 57 | 0.00016459 | 2.8876e-06
2013-01-10 | 288047 | IPL3 | RURAL | Weather | 3.3 | 321 | 1059.3 | 0.0030589 | 9.5291e-06
2013-01-10 | 288062 | TGW2 | RURAL | Equipment failure | 1 | 51 | 51 | 0.00014727 | 2.8876e-06
2013-01-10 | 288063 | VPT1B | URBAN | Equipment failure | 21.12 | 107 | 1580.8 | 0.0015952 | 2.1312e-05
2013-01-10 | 288065 | MAI13 | URBAN | Equipment failure | 6 | 275 | 1650 | 0.001665 | 6.0545e-06
2013-01-10 | 288073 | TBV4 | RURAL | Other | 2.64 | 72 | 190.08 | 0.00054888 | 7.6233e-06
2013-01-10 | 288074 | NSD3A | URBAN | Equipment failure | 12.5 | 208 | 2600 | 0.0026236 | 1.2614e-05
2013-01-10 | 288075 | GYM7A | RURAL | Equipment failure | 9 | 115 | 1035 | 0.0029887 | 2.5989e-05
2013-01-10 | 288100 | KBR6A | RURAL | Equipment failure | 6.5 | 246 | 1599 | 0.0046173 | 1.877e-05
2013-01-10 | 288101 | PRG2A | RURAL | Other | 5.695 | 215 | 1224.425 | 0.0035357 | 1.6445e-05
2013-01-10 | 288120 | TGW3 | RURAL | Weather | 1 | 231 | 231 | 0.00066704 | 2.8876e-06
2013-01-11 | 288085 | PWC3 | RURAL | Other | 55 | 157 | 8635 | 0.024935 | 0.00015882
2013-01-11 | 288086 | CLD2 | URBAN | Equipment failure | 98.83 | 50 | 4941.5 | 0.0049863 | 9.9727e-05
2013-01-11 | 288087 | GTN13A | RURAL | Equipment failure | 711.51 | 46.7639 | 22543.57 | 0.065099 | 0.0020546
2013-01-11 | 288102 | SBK11 | URBAN | Equipment failure | 15.84 | 102 | 1615.68 | 0.0016303 | 1.5984e-05
2013-01-11 | 288122 | ZMR10 | URBAN | Equipment failure | 1448.18 | 3 | 4344.54 | 0.004384 | 0.0014613
2013-01-11 | 288122 | ZMR11A | URBAN | Equipment failure | 275.5 | 3 | 826.5 | 0.000834 | 0.000278
2013-01-11 | 288122 | ZMR2A | URBAN | Equipment failure | 711.83 | 3 | 2135.49 | 0.0021549 | 0.00071829
2013-01-11 | 288122 | ZMR3 | URBAN | Equipment failure | 1483.67 | 3 | 4451.01 | 0.0044914 | 0.0014971
2013-01-11 | 288122 | ZMR4A | URBAN | Equipment failure | 1934.19 | 3 | 5802.57 | 0.0058552 | 0.0019517
2013-01-11 | 288122 | ZMR5 | URBAN | Equipment failure | 1950.51 | 3 | 5851.53 | 0.0059046 | 0.0019682
2013-01-11 | 288122 | ZMR6A | URBAN | Equipment failure | 815 | 3 | 2445 | 0.0024672 | 0.00082239
2013-01-11 | 288122 | ZMR7A | URBAN | Equipment failure | 1866.49 | 3 | 5599.47 | 0.0056503 | 0.0018834
2013-01-11 | 288122 | ZMR8A | URBAN | Equipment failure | 59 | 3 | 177 | 0.00017861 | 5.9535e-05
2013-01-11 | 288122 | ZMR9 | URBAN | Equipment failure | 1729 | 3 | 5187 | 0.0052341 | 0.0017447
2013-01-11 | 288123 | MSV1 | RURAL | Weather | 2.68 | 230 | 616.4 | 0.00178 | 7.739e-06
2013-01-11 | 288125 | WED3A | URBAN | Equipment failure | 11 | 77 | 847 | 0.00085468 | 1.11e-05
2013-01-11 | 288126 | CPD1 | RURAL | Equipment failure | 4 | 174 | 696 | 0.0020098 | 1.1551e-05
2013-01-11 | 288129 | NVL12A | URBAN | Animals | 116 | 86 | 9976 | 0.010067 | 0.00011705
2013-01-11 | 288132 | GYN3A | RURAL | Equipment failure | 4 | 68 | 272 | 0.00078545 | 1.1551e-05
2013-01-11 | 288133 | SPO5A | URBAN | Operational error | 1 | 144 | 144 | 0.00014531 | 1.0091e-06
2013-01-11 | 288136 | CSE7 | URBAN | Equipment failure | 17.25 | 134 | 2311.5 | 0.0023325 | 1.7407e-05
2013-01-11 | 288137 | MLY6 | RURAL | Equipment failure | 15 | 42 | 630 | 0.0018193 | 4.3316e-05
2013-01-11 | 288162 | ESK5A | RURAL | Vegetation | 186.99 | 74 | 13837.26 | 0.039958 | 0.00053997
2013-01-11 | 288168 | BHD35A | RURAL | Other | 153 | 72 | 11016 | 0.031811 | 0.00044182
2013-01-11 | 288174 | TRG5 | URBAN | Other | 119 | 64.3333 | 7655.6667 | 0.0077251 | 0.00012008
2013-01-11 | 288175 | JBB16A | RURAL | Operational error | 16 | 46.3333 | 741.3333 | 0.0021407 | 4.6203e-05
2013-01-11 | 288320 | CPD1 | RURAL | Weather | 0.67 | 321 | 215.07 | 0.00062106 | 1.9348e-06
2013-01-12 | 288173 | GBP5 | URBAN | Other | 390.08 | 153 | 59682.24 | 0.060223 | 0.00039362
2013-01-12 | 288181 | BGY5A | RURAL | Animals | 37 | 62 | 2294 | 0.0066245 | 0.00010685
2013-01-12 | 288182 | RLB13B | RURAL | Weather | 8.5 | 35 | 297.5 | 0.0008591 | 2.4546e-05
2013-01-12 | 288184 | CRB25A | RURAL | Equipment failure | 69 | 26.5 | 2507.46 | 0.0072409 | 0.00019925
2013-01-12 | 288186 | UMG2B | RURAL | Equipment failure | 986.4 | 73.4118 | 74998 | 0.21657 | 0.0028485
2013-01-12 | 288188 | TGP5B | URBAN | Third party impacts | 150 | 77 | 11550 | 0.011655 | 0.00015136
2013-01-12 | 288189 | IDY6A | URBAN | Other | 109 | 40 | 4360 | 0.0043995 | 0.00010999
2013-01-12 | 288190 | JBB16A | RURAL | Operational error | 5.28 | 72 | 380.16 | 0.0010978 | 1.5247e-05
2013-01-12 | 288191 | JBB13A | RURAL | Operational error | 9.57 | 50 | 478.5 | 0.0013818 | 2.7636e-05
2013-01-12 | 288192 | GLY1 | URBAN | Other | 1 | 81 | 81 | 8.1734e-05 | 1.0091e-06
2013-01-12 | 288194 | RLB11B | URBAN | Equipment failure | 1915.5 | 102.0968 | 194613 | 0.19638 | 0.0019329
2013-01-12 | 288195 | CBW13 | RURAL | Operational error | 14 | 121 | 1694 | 0.0048918 | 4.0428e-05
2013-01-12 | 288196 | KBN5A | RURAL | Other | 14.025 | 67 | 939.675 | 0.0027135 | 4.0501e-05
2013-01-12 | 288197 | NMC16A | RURAL | Equipment failure | 18.48 | 118 | 2180.64 | 0.0062971 | 5.3365e-05
2013-01-12 | 288198 | NBR6 | RURAL | Other | 30 | 372 | 11160 | 0.032227 | 8.6632e-05
2013-01-12 | 288199 | MDRMLD11 | URBAN | Equipment failure | 880.15 | 76.5926 | 80210.18 | 0.080937 | 0.00088813
2013-01-12 | 288200 | NBR5 | RURAL | Vegetation | 1323 | 70.8133 | 115633.5 | 0.33392 | 0.0038205
2013-01-12 | 288200 | NBR6 | RURAL | Vegetation | 1763.98 | 46 | 81143.08 | 0.23432 | 0.0050939
2013-01-12 | 288200 | NBR7 | URBAN | Vegetation | 1466 | 46 | 67436 | 0.068047 | 0.0014793
2013-01-12 | 288200 | NBR8 | RURAL | Vegetation | 566.25 | 46 | 26047.5 | 0.075218 | 0.0016352
2013-01-12 | 288200 | NBR9 | RURAL | Vegetation | 2075 | 46 | 95450 | 0.27564 | 0.0059921
2013-01-12 | 288201 | SHW4 | URBAN | Animals | 489.33 | 45 | 22019.85 | 0.022219 | 0.00049377
2013-01-12 | 288203 | FDS1 | RURAL | Operational error | 226.5 | 73 | 16534.5 | 0.047747 | 0.00065407
2013-01-12 | 288209 | BKD3A | URBAN | Animals | 109 | 71 | 7739 | 0.0078091 | 0.00010999
2013-01-12 | 288214 | KBN5A | RURAL | Operational error | 14.025 | 87 | 1220.175 | 0.0035236 | 4.0501e-05
2013-01-12 | 288260 | KBN5A | RURAL | Operational error | 14.025 | 48 | 673.2 | 0.001944 | 4.0501e-05
2013-01-12 | 288321 | TRP2 | RURAL | Operational error | 8 | 52 | 416 | 0.0012013 | 2.3102e-05
2013-01-13 | 288206 | MAI11 | URBAN | Other | 106 | 54 | 5724 | 0.0057758 | 0.00010696
2013-01-13 | 288208 | KRA3 | URBAN | Equipment failure | 912.5 | 102.9091 | 92192 | 0.093026 | 0.00092075
2013-01-13 | 288210 | BIS15A | URBAN | Vegetation | 39 | 4 | 156 | 0.00015741 | 3.9353e-05
2013-01-13 | 288211 | BDT5 | RURAL | Other | 2 | 110 | 220 | 0.00063532 | 5.7756e-06
2013-01-13 | 288212 | WED21A | URBAN | Animals | 38.28 | 40 | 1531.2 | 0.001545 | 3.8626e-05
2013-01-13 | 288213 | BDA12B | URBAN | Animals | 80.19 | 25 | 2004.75 | 0.0020229 | 8.0915e-05
2013-01-13 | 288216 | VPK8 | URBAN | Vegetation | 61 | 102 | 6222 | 0.0062783 | 6.1552e-05
2013-01-13 | 288217 | CBT12A | RURAL | Vegetation | 14 | 30 | 420 | 0.0012129 | 4.0429e-05
2013-01-13 | 288218 | KRN5A | URBAN | Equipment failure | 2.05 | 195 | 399.75 | 0.00040337 | 2.0685e-06
2013-01-13 | 288225 | IPS1B | URBAN | Operational error | 58.74 | 10 | 587.4 | 0.00059271 | 5.9271e-05
2013-01-13 | 288227 | CRM5A | URBAN | Other | 41.58 | 54 | 2245.32 | 0.0022656 | 4.1956e-05
2013-01-13 | 288228 | SPF15A | URBAN | Equipment failure | 17.16 | 137 | 2350.92 | 0.0023722 | 1.7315e-05
2013-01-13 | 288230 | KBN1B | RURAL | Operational error | 5 | 87 | 435 | 0.0012562 | 1.4439e-05
2013-01-13 | 288231 | KBN5A | RURAL | Other | 14.025 | 144 | 2019.6 | 0.0058322 | 4.0501e-05
2013-01-13 | 288232 | SMR1A | URBAN | Equipment failure | 7.975 | 110 | 877.25 | 0.00088518 | 8.0471e-06
2013-01-13 | 288233 | CCY3B | URBAN | Equipment failure | 1216.99 | 51.3 | 67288.91 | 0.067897 | 0.001228
2013-01-13 | 288234 | BGY5A | RURAL | Equipment failure | 9.57 | 113 | 1081.41 | 0.0031229 | 2.7636e-05
2013-01-13 | 288235 | MDRMLD11 | URBAN | Other | 75.5 | 55 | 3960 | 0.0039958 | 7.6183e-05
2013-01-13 | 288236 | GVN16A | RURAL | Equipment failure | 13.53 | 118 | 1596.54 | 0.0046105 | 3.9072e-05
2013-01-13 | 288239 | JBB12B | RURAL | Operational error | 11 | 164 | 1804 | 0.0052096 | 3.1766e-05
2013-01-13 | 288240 | KWH2 | RURAL | Equipment failure | 501.95 | 66.5882 | 38380.2 | 0.11083 | 0.0014495
2013-01-13 | 288245 | WED6A | URBAN | Other | 138.5 | 96 | 13296 | 0.013416 | 0.00013975
2013-01-13 | 288246 | JBB16A | RURAL | Operational error | 16 | 48.5 | 776 | 0.0022409 | 4.6205e-05
2013-01-13 | 288250 | CCY3B | URBAN | Equipment failure | 3.96 | 74 | 293.04 | 0.00029569 | 3.9958e-06
2013-01-14 | 288266 | TGW3 | RURAL | Equipment failure | 4 | 74 | 296 | 0.00085482 | 1.1552e-05
2013-01-14 | 288278 | JBB16A | RURAL | Other | 17 | 62 | 1054 | 0.0030439 | 4.9095e-05
2013-01-14 | 288284 | AMR2 | RURAL | Third party impacts | 153.99 | 165 | 27600.53 | 0.079708 | 0.00044471
2013-01-14 | 288288 | KRA7 | URBAN | Equipment failure | 1224.67 | 56.4737 | 80529.21 | 0.081257 | 0.0012357
2013-01-14 | 288290 | PBH6 | URBAN | Equipment failure | 2228.34 | 157.4 | 366225.72 | 0.36953 | 0.0022485
2013-01-14 | 288295 | MLY4 | RURAL | Vegetation | 144 | 15 | 2160 | 0.0062379 | 0.00041586
2013-01-14 | 288298 | DRA9 | URBAN | Equipment failure | 31 | 491 | 15221 | 0.015358 | 3.128e-05
2013-01-14 | 288300 | NBR5 | RURAL | Equipment failure | 426 | 327 | 139302 | 0.40229 | 0.0012303
2013-01-14 | 288302 | PWC4 | RURAL | Vegetation | 625.51 | 223.7727 | 123661.17 | 0.35712 | 0.0018064
2013-01-14 | 288308 | LBH6A | RURAL | Vegetation | 1595.87 | 40.4167 | 125657.58 | 0.36289 | 0.0046087
2013-01-14 | 288309 | 322 | URBAN | Equipment failure | 1 | 307 | 307 | 0.00030977 | 1.009e-06
2013-01-14 | 288310 | 332 | URBAN | Equipment failure | 1 | 478 | 478 | 0.00048232 | 1.009e-06
2013-01-14 | 288310 | RCF10A | URBAN | Equipment failure | 630 | 278.2727 | 175644 | 0.17723 | 0.00063569
2013-01-14 | 288312 | MFN2B | RURAL | Animals | 75 | 7.1667 | 537.5 | 0.0015523 | 0.00021659
2013-01-14 | 288313 | DBY6 | URBAN | Weather | 109 | 96.1667 | 10482.1667 | 0.010577 | 0.00010998
2013-01-14 | 288314 | RBY15 | URBAN | Animals | 33.33 | 43.6667 | 1455.41 | 0.0014686 | 3.3631e-05
2013-01-14 | 288315 | BDB27A | RURAL | Animals | 20 | 51.5 | 1030 | 0.0029746 | 5.7758e-05
2013-01-14 | 288322 | PBH2B | URBAN | Other | 161 | 532 | 85652 | 0.086426 | 0.00016245
2013-01-14 | 288343 | GYM8A | RURAL | Animals | 33 | 238 | 7854 | 0.022682 | 9.5301e-05
2013-01-15 | 288311 | MGP13A | RURAL | Other | 3 | 158 | 474 | 0.0013689 | 8.6641e-06
2013-01-15 | 288316 | MGP13A | RURAL | Weather | 4 | 89 | 356 | 0.0010281 | 1.1552e-05
2013-01-15 | 288323 | SIS2 | RURAL | Equipment failure | 46 | 176 | 8096 | 0.023382 | 0.00013285
2013-01-15 | 288324 | RWD1 | RURAL | Other | 5 | 97 | 485 | 0.0014007 | 1.444e-05
2013-01-15 | 288326 | 348 | URBAN | Equipment failure | 1 | 374 | 374 | 0.00037737 | 1.009e-06
2013-01-15 | 288327 | KWA12A | URBAN | Equipment failure | 2.85 | 43 | 122.55 | 0.00012365 | 2.8757e-06
2013-01-15 | 288328 | PWC5 | RURAL | Other | 51.5 | 140 | 7210 | 0.020823 | 0.00014873
2013-01-15 | 288332 | PBH2B | URBAN | Equipment failure | 161 | 260 | 41860 | 0.042237 | 0.00016245
2013-01-15 | 288335 | CMD15A | URBAN | Equipment failure | 267 | 190.75 | 49462 | 0.049908 | 0.00026941
2013-01-15 | 288344 | KMR17A | URBAN | Equipment failure | 45.5 | 122 | 5551 | 0.005601 | 4.591e-05
2013-01-15 | 288346 | GYGGYS6 | RURAL | Equipment failure | 1 | 107 | 107 | 0.00030902 | 2.888e-06
2013-01-15 | 288367 | WMD4A | RURAL | Equipment failure | 36.25 | 80 | 2900 | 0.0083753 | 0.00010469
2013-01-15 | 288368 | IPL1 | RURAL | Animals | 2.31 | 93 | 214.83 | 0.00062044 | 6.6714e-06
2013-01-15 | 288375 | ZMR5 | URBAN | Equipment failure | 1950.51 | 203.7037 | 340601.08 | 0.34367 | 0.0019681
2013-01-15 | 288376 | TGW1 | RURAL | Equipment failure | 0.67 | 168 | 112.56 | 0.00032508 | 1.935e-06
2013-01-15 | 288377 | RWD1 | RURAL | Equipment failure | 5 | 160 | 800 | 0.0023104 | 1.444e-05
2013-01-15 | 288378 | 311 | URBAN | Equipment failure | 1 | 515 | 515 | 0.00051964 | 1.009e-06
2013-01-15 | 288378 | DBY9 | URBAN | Equipment failure | 117 | 130 | 15210 | 0.015347 | 0.00011805
2013-01-16 | 288373 | AHD18B | RURAL | Animals | 159.58 | 23 | 3670.34 | 0.0106 | 0.00046089
2013-01-16 | 288374 | RST5A | URBAN | Animals | 579.33 | 105 | 60829.65 | 0.061377 | 0.00058454
2013-01-16 | 288381 | WRG1A | URBAN | Other | 173 | 95 | 16435 | 0.016583 | 0.00017456
2013-01-16 | 288382 | VPT12A | URBAN | Other | 57 | 127 | 7239 | 0.0073041 | 5.7513e-05
2013-01-16 | 288386 | AMR2 | RURAL | Equipment failure | 12 | 124 | 1488 | 0.0042975 | 3.4658e-05
2013-01-16 | 288414 | MFN12A | RURAL | Animals | 31.35 | 103 | 3229.05 | 0.0093259 | 9.0543e-05
2013-01-16 | 288416 | BLB4A | URBAN | Equipment failure | 67 | 491 | 32897 | 0.033193 | 6.7603e-05
2013-01-16 | 288422 | GGR1 | RURAL | Equipment failure | 2.5 | 110 | 275 | 0.00079423 | 7.2203e-06
2013-01-16 | 288426 | MTB15A | RURAL | Animals | 16.5 | 94 | 1551 | 0.0044795 | 4.7654e-05
2013-01-16 | 288434 | CPB8 | RURAL | Animals | 8.91 | 50 | 445.5 | 0.0012867 | 2.5733e-05
2013-01-16 | 288436 | MSV1 | RURAL | Equipment failure | 6 | 172 | 1032 | 0.0029805 | 1.7329e-05
2013-01-17 | 288435 | AHL14A | URBAN | Animals | 633.5 | 50 | 31675 | 0.031962 | 0.00063924
2013-01-17 | 288438 | ALY5 | URBAN | Other | 165 | 83 | 13695 | 0.013819 | 0.00016649
2013-01-17 | 288460 | BMT1 | RURAL | Equipment failure | 6 | 240 | 1440 | 0.0041581 | 1.7326e-05
2013-01-17 | 288488 | GYS2A | URBAN | Equipment failure | 5 | 26 | 130 | 0.00013118 | 5.0453e-06
2013-01-17 | 288501 | CLM6 | URBAN | Animals | 549 | 4 | 2196 | 0.0022159 | 0.00055397
2013-01-17 | 288521 | RWD1 | RURAL | Other | 28 | 165 | 4620 | 0.013341 | 8.0853e-05
2013-01-17 | 288522 | IBL2 | RURAL | Animals | 735.51 | 57 | 41924.07 | 0.12106 | 0.0021239
2013-01-17 | 288523 | IPS16A | URBAN | Equipment failure | 3.69 | 252 | 929.88 | 0.0009383 | 3.7234e-06
2013-01-17 | 288524 | WED6A | URBAN | Animals | 98.6039 | 41 | 4042.7599 | 0.0040794 | 9.9497e-05
2013-01-17 | 288526 | NRA5A | RURAL | Equipment failure | 13 | 84 | 1092 | 0.0031533 | 3.7539e-05
2013-01-17 | 288585 | AMR1 | RURAL | Equipment failure | 0.66 | 31 | 20.46 | 5.908e-05 | 1.9058e-06
2013-01-18 | 288531 | NIP1A | URBAN | Operational error | 54.605 | 22 | 1201.31 | 0.0012122 | 5.51e-05
2013-01-18 | 288532 | TGW4 | RURAL | Equipment failure | 633 | 108.7027 | 70447.5 | 0.20342 | 0.0018278
2013-01-18 | 288534 | TGW2 | RURAL | Other | 60.5 | 5 | 302.5 | 0.00087348 | 0.0001747
2013-01-18 | 288536 | TRP1 | RURAL | Other | 7 | 58 | 406 | 0.0011723 | 2.0213e-05
2013-01-18 | 288537 | SMF5A | RURAL | Other | 4.29 | 84.5 | 362.505 | 0.0010468 | 1.2388e-05
2013-01-18 | 288540 | SGT7 | URBAN | Equipment failure | 10.95 | 59 | 646.05 | 0.0006519 | 1.1049e-05
2013-01-18 | 288542 | MFN13A | RURAL | Equipment failure | 34 | 81 | 2754 | 0.0079523 | 9.8177e-05
2013-01-18 | 288546 | IPS16A | URBAN | Equipment failure | 2.46 | 30 | 73.8 | 7.4469e-05 | 2.4823e-06
2013-01-18 | 288549 | CPB8 | RURAL | Equipment failure | 13.5 | 215 | 2902.5 | 0.0083811 | 3.8982e-05
2013-01-18 | 288551 | CPB8 | RURAL | Vegetation | 339.49 | 37 | 12561.13 | 0.036271 | 0.00098029
2013-01-18 | 288558 | YTA22A | RURAL | Other | 13 | 167 | 2171 | 0.0062689 | 3.7538e-05
2013-01-18 | 288559 | DBY9 | URBAN | Third party impacts | 18.48 | 47 | 868.56 | 0.00087643 | 1.8647e-05
2013-01-18 | 288581 | NMC1B | RURAL | Vegetation | 1311.5 | 82.5417 | 109129.5 | 0.31512 | 0.003787
2013-01-18 | 288584 | WFD5A | RURAL | Equipment failure | 12.87 | 48 | 617.76 | 0.0017838 | 3.7163e-05
2013-01-18 | 288586 | TSN15A | URBAN | Animals | 334.33 | 90 | 30089.7 | 0.030362 | 0.00033736
2013-01-18 | 288592 | NMC1B | RURAL | Equipment failure | 4 | 80 | 320 | 0.00092402 | 1.155e-05
2013-01-19 | 288593 | BGY17A | URBAN | Equipment failure | 1868.01 | 74.7222 | 160146.92 | 0.16162 | 0.0018852
2013-01-19 | 288594 | GYM8A | RURAL | Animals | 2211.5 | 122.0128 | 269260.5 | 0.77715 | 0.0063829
2013-01-19 | 288595 | INA7A | RURAL | Equipment failure | 40 | 144 | 5220 | 0.015066 | 0.00011545
2013-01-19 | 288596 | AHD18A | URBAN | Equipment failure | 11.8 | 256 | 3020.8 | 0.0030486 | 1.1909e-05
2013-01-19 | 288598 | BPN29A | URBAN | Equipment failure | 5 | 103 | 515 | 0.00051975 | 5.0461e-06
2013-01-19 | 288599 | BRD5A | RURAL | Operational error | 39 | 47 | 1833 | 0.0052905 | 0.00011256
2013-01-19 | 288600 | LLY5 | RURAL | Weather | 27 | 70 | 1890 | 0.005455 | 7.7929e-05
2013-01-19 | 288601 | SMF6A | RURAL | Other | 9 | 22 | 198 | 0.00057148 | 2.5976e-05
2013-01-19 | 288603 | TRP1 | RURAL | Equipment failure | 8.5 | 132 | 1122 | 0.0032384 | 2.4533e-05
2013-01-19 | 288605 | ALY8 | URBAN | Other | 1842.17 | 70 | 128951.9 | 0.13014 | 0.0018592
2013-01-19 | 288605 | HPK5A | URBAN | Other | 1238 | 70 | 86660 | 0.087459 | 0.0012494
2013-01-19 | 288607 | CSE7 | URBAN | Equipment failure | 1097.32 | 63.4 | 68278.78 | 0.068908 | 0.0011074
2013-01-19 | 288608 | JHDMDH7 | URBAN | Other | 6 | 19 | 114 | 0.00011505 | 6.0553e-06
2013-01-19 | 288609 | TBV1 | RURAL | Operational error | 1 | 99 | 99 | 0.00028574 | 2.8862e-06
2013-01-19 | 288611 | CVL7A | RURAL | Equipment failure | 32.5 | 83 | 2697.5 | 0.0077856 | 9.3803e-05
2013-01-19 | 288612 | GYN3A | RURAL | Operational error | 14.5 | 211 | 3059.5 | 0.0088305 | 4.1851e-05
2013-01-19 | 288613 | NRG9 | RURAL | Equipment failure | 5 | 224 | 1120 | 0.0032326 | 1.4431e-05
2013-01-19 | 288614 | MFN12A | RURAL | Equipment failure | 21 | 168 | 3528 | 0.010183 | 6.0611e-05
2013-01-20 | 288617 | CSE2 | URBAN | Third party impacts | 78.5 | 48 | 3768 | 0.0038028 | 7.9224e-05
2013-01-20 | 288618 | NDH7 | URBAN | Other | 0.05 | 75 | 3.75 | 3.7846e-06 | 5.0461e-08
2013-01-20 | 288623 | MLS12B | URBAN | Operational error | 345.5 | 62 | 21421 | 0.021619 | 0.00034869
2013-01-20 | 288633 | CPC2A | RURAL | Third party impacts | 1508 | 103.9231 | 102188 | 0.29493 | 0.0043523
2013-01-20 | 288633 | CPC2B | URBAN | Third party impacts | 1781.99 | 9.1333 | 9157.95 | 0.0092424 | 0.0017984
2013-01-20 | 288635 | HIS12A | URBAN | Equipment failure | 837 | 43.5 | 72819 | 0.073491 | 0.00084472
2013-01-20 | 288635 | HIS12B | URBAN | Equipment failure | 953.5 | 43.5 | 82954.5 | 0.08372 | 0.0009623
2013-01-20 | 288646 | DRD13A | URBAN | Equipment failure | 58 | 73 | 4234 | 0.0042731 | 5.8535e-05
2013-01-21 | 288636 | GBG26 | URBAN | Other | 915.99 | 16 | 14655.84 | 0.014793 | 0.00092456
2013-01-21 | 288637 | CPK13 | RURAL | Weather | 1886.16 | 94.9412 | 169187.52 | 0.48807 | 0.0054412
2013-01-21 | 288640 | IPS12A | URBAN | Other | 1 | 39 | 39 | 3.9365e-05 | 1.0094e-06
2013-01-21 | 288640 | IPS12B | URBAN | Other | 992.5 | 39 | 38707.5 | 0.03907 | 0.0010018
2013-01-21 | 288640 | IPS13A | RURAL | Other | 570 | 39 | 22230 | 0.064129 | 0.0016443
2013-01-21 | 288640 | IPS15B | URBAN | Other | 739.16 | 39 | 28827.24 | 0.029097 | 0.00074607
2013-01-21 | 288640 | IPS16A | URBAN | Other | 1352.17 | 39 | 52734.63 | 0.053228 | 0.0013648
2013-01-21 | 288640 | IPS1B | URBAN | Other | 2477.31 | 39 | 96615.09 | 0.097519 | 0.0025005
2013-01-21 | 288640 | IPS2A | URBAN | Other | 1 | 39 | 39 | 3.9365e-05 | 1.0094e-06
2013-01-21 | 288640 | IPS2B | RURAL | Other | 1270.84 | 39 | 49562.76 | 0.14298 | 0.0036661
2013-01-21 | 288640 | IPS3A | RURAL | Other | 522 | 39 | 20358 | 0.058729 | 0.0015059
2013-01-21 | 288640 | IPS5B | URBAN | Other | 1958.66 | 39 | 76387.74 | 0.077102 | 0.001977
2013-01-21 | 288641 | KSN5 | RURAL | Equipment failure | 8.2 | 61 | 500.2 | 0.001443 | 2.3655e-05
2013-01-21 | 288642 | BGY15A | URBAN | Operational error | 6.35 | 20 | 127 | 0.00012819 | 6.4094e-06
2013-01-21 | 288649 | HPE12A | URBAN | Equipment failure | 131 | 187 | 24497 | 0.024726 | 0.00013223
2013-01-21 | 288650 | LHM2 | URBAN | Animals | 50.5 | 121 | 6110.5 | 0.0061677 | 5.0972e-05
2013-01-21 | 288651 | MFN12A | RURAL | Equipment failure | 14 | 16 | 224 | 0.0006462 | 4.0387e-05
2013-01-21 | 288652 | MTB1B | RURAL | Third party impacts | 41 | 62 | 2542 | 0.0073332 | 0.00011828
2013-01-21 | 288653 | WSE5A | RURAL | Other | 0.99 | 160 | 158.4 | 0.00045695 | 2.856e-06
2013-01-21 | 288654 | GBG1B | URBAN | Other | 31 | 49.5 | 2113.58 | 0.0021334 | 3.129e-05
2013-01-21 | 288657 | GYM8A | RURAL | Equipment failure | 130 | 21 | 2730 | 0.0078755 | 0.00037503
2013-01-21 | 288670 | MLT21B | URBAN | Other | 81.84 | 69 | 5646.96 | 0.0056998 | 8.2606e-05
2013-01-21 | 288671 | MLT21B | URBAN | Other | 40.92 | 44 | 1800.48 | 0.0018173 | 4.1303e-05
2013-01-21 | 288672 | GBN3 | RURAL | Equipment failure | 120.5 | 108 | 13014 | 0.037543 | 0.00034762
2013-01-21 | 288678 | HWL1A | URBAN | Equipment failure | 67.165 | 316 | 21224.14 | 0.021423 | 6.7793e-05
2013-01-21 | 288701 | CLD2 | URBAN | Other | 101.33 | 151 | 15300.83 | 0.015444 | 0.00010228
2013-01-21 | 288709 | MTB1B | RURAL | Other | 26.73 | 145 | 3875.85 | 0.011181 | 7.7111e-05
2013-01-22 | 288700 | NSW22A | URBAN | Equipment failure | 1 | 95 | 95 | 9.5895e-05 | 1.0094e-06
2013-01-22 | 288700 | NSW22B | URBAN | Equipment failure | 1395.01 | 121.9 | 171982.23 | 0.1736 | 0.0014082
2013-01-22 | 288702 | PWC5 | RURAL | Equipment failure | 722.91 | 77.1333 | 81901.13 | 0.23621 | 0.002085
2013-01-22 | 288741 | LTA5 | URBAN | Animals | 1980.35 | 20 | 39607 | 0.03998 | 0.001999
2013-01-22 | 288744 | MTG7A | URBAN | Equipment failure | 2 | 210 | 420 | 0.00042396 | 2.0189e-06
2013-01-22 | 288749 | TGP8A | URBAN | Other | 67.32 | 46.8333 | 3152.82 | 0.0031825 | 6.7954e-05
2013-01-22 | 288750 | CPR5 | URBAN | Animals | 134.5 | 39.5 | 5312.75 | 0.0053628 | 0.00013577
2013-01-22 | 288752 | TGW3 | RURAL | Other | 2.68 | 131 | 351.08 | 0.0010126 | 7.7294e-06
2013-01-22 | 288753 | KBN5A | RURAL | Other | 1 | 136 | 136 | 0.00039224 | 2.8841e-06
2013-01-22 | 296574 | LGV2B | RURAL | Other | 5 | 155 | 775 | 0.0022352 | 1.4421e-05
2013-01-23 | 288746 | TWG21 | URBAN | Animals | 941.5 | 16 | 15064 | 0.015206 | 0.00095039
2013-01-23 | 288751 | LTA4B | URBAN | Equipment failure | 21.78 | 68 | 1481.04 | 0.001495 | 2.1986e-05
2013-01-23 | 288760 | NMC5A | RURAL | Other | 18 | 37 | 666 | 0.0019207 | 5.1911e-05
2013-01-23 | 288785 | SGT22A | URBAN | Third party impacts | 60.39 | 150 | 9058.5 | 0.009144 | 6.096e-05
2013-01-23 | 288791 | MTG7A | URBAN | Equipment failure | 88.33 | 59 | 5211.47 | 0.0052607 | 8.9164e-05
2013-01-23 | 288792 | AHD18A | URBAN | Equipment failure | 672.5 | 75.9412 | 43771.5 | 0.044185 | 0.00067885
2013-01-23 | 288792 | AHD18B | RURAL | Equipment failure | 2009.41 | 91.0571 | 180601.49 | 0.52085 | 0.0057951
2013-01-23 | 288794 | WSE3A | RURAL | Animals | 1126.25 | 89.1667 | 109507.25 | 0.31582 | 0.0032481
2013-01-23 | 288795 | SMF3A | RURAL | Other | 15 | 139 | 2085 | 0.0060131 | 4.326e-05
2013-01-23 | 288796 | WSE6A | RURAL | Animals | 4.02 | 119 | 478.38 | 0.0013796 | 1.1594e-05
2013-01-23 | 288801 | KBR2A | RURAL | Other | 1 | 147 | 147 | 0.00042394 | 2.884e-06
2013-01-24 | 288798 | AGT23A | URBAN | Third party impacts | 62.5 | 131 | 8187.5 | 0.0082659 | 6.3098e-05
2013-01-24 | 288800 | NRA1A | RURAL | Animals | 889 | 97.764 | 89814.5 | 0.25891 | 0.0025627
2013-01-24 | 288802 | LHM1 | URBAN | Other | 1577 | 28 | 44156 | 0.044579 | 0.0015921
2013-01-24 | 288804 | THL1 | RURAL | Weather | 8 | 117 | 936 | 0.0026982 | 2.3062e-05
2013-01-24 | 288866 | CVL7A | RURAL | Animals | 9 | 90 | 810 | 0.002335 | 2.5944e-05
2013-01-24 | 288870 | WMR1 | RURAL | Weather | 424.49 | 103.9429 | 34921.93 | 0.10067 | 0.0012237
2013-01-24 | 288871 | WMD4A | RURAL | Equipment failure | 10.2 | 145 | 1479 | 0.0042635 | 2.9403e-05
2013-01-24 | 288880 | AHD18A | URBAN | Other | 2 | 83 | 166 | 0.00016759 | 2.0191e-06
2013-01-25 | 288883 | KBN1B | RURAL | Equipment failure | 1377 | 101.6327 | 122004 | 0.35162 | 0.0039685
2013-01-25 | 288884 | CFD1A | URBAN | Equipment failure | 83.45 | 198 | 25175.25 | 0.025418 | 8.4255e-05
2013-01-25 | 288900 | KBN2A | RURAL | Other | 14 | 72 | 1008 | 0.0029051 | 4.0348e-05
2013-01-25 | 288903 | ENG2 | URBAN | Equipment failure | 70 | 56 | 3920 | 0.0039578 | 7.0676e-05
2013-01-25 | 288907 | BWH7A | RURAL | Equipment failure | 6 | 69 | 414 | 0.0011931 | 1.7292e-05
2013-01-25 | 288911 | RST9A | URBAN | Third party impacts | 328.99 | 102.9091 | 34654.16 | 0.034989 | 0.00033217
2013-01-25 | 288912 | PWC4 | RURAL | Other | 40 | 157 | 6280 | 0.018099 | 0.00011528
2013-01-25 | 288916 | AGT35A | URBAN | Weather | 3 | 74 | 222 | 0.00022414 | 3.029e-06
2013-01-25 | 288918 | MGP13A | RURAL | Weather | 12 | 21 | 252 | 0.00072626 | 3.4584e-05
2013-01-25 | 288919 | AMR2 | RURAL | Other | 67.5 | 79 | 5332.5 | 0.015368 | 0.00019454
2013-01-25 | 288932 | AMR2 | RURAL | Equipment failure | 811.31 | 75.5412 | 95698.6523 | 0.2758 | 0.0023382
2013-01-25 | 288943 | MLY4 | RURAL | Weather | 144 | 165.6957 | 32227.5 | 0.09288 | 0.00041501
2013-01-25 | 288945 | RST2A | URBAN | Third party impacts | 8.875 | 400 | 3550 | 0.0035843 | 8.9607e-06
2013-01-25 | 288946 | NGI2B | RURAL | Weather | 34.5 | 407 | 14041.5 | 0.040468 | 9.9429e-05
2013-01-25 | 288947 | 311 | URBAN | Equipment failure | 1 | 288 | 288 | 0.00029078 | 1.0097e-06
2013-01-25 | 288949 | GYGGYS6 | RURAL | Equipment failure | 26 | 57 | 1482 | 0.0042711 | 7.4932e-05
2013-01-25 | 288950 | BLB5A | URBAN | Equipment failure | 200 | 239 | 62505 | 0.063108 | 0.00020193
2013-01-25 | 288951 | HPK2 | URBAN | Equipment failure | 76.5 | 129 | 9868.5 | 0.0099638 | 7.7238e-05
2013-01-25 | 288955 | GBN3 | RURAL | Equipment failure | 6.5 | 85 | 552.5 | 0.0015923 | 1.8733e-05
2013-01-25 | 288956 | GYN7A | RURAL | Other | 1 | 94 | 94 | 0.00027091 | 2.882e-06
2013-01-25 | 288958 | GYM2A | RURAL | Other | 4 | 45 | 180 | 0.00051876 | 1.1528e-05
2013-01-25 | 288959 | BWH7A | RURAL | Weather | 5 | 78 | 390 | 0.001124 | 1.441e-05
2013-01-25 | 290730 | NMK7 | URBAN | Other | 57 | 13 | 741 | 0.00074815 | 5.755e-05
2013-01-26 | 288953 | CBW11 | RURAL | Weather | 1096.99 | 45.4342 | 48535.8574 | 0.13985 | 0.0031608
2013-01-26 | 288962 | WRG15A | URBAN | Equipment failure | 430.5 | 168.8333 | 79486 | 0.080259 | 0.00043469
2013-01-26 | 288963 | RCF1A | URBAN | Equipment failure | 107.5 | 34 | 3655 | 0.0036906 | 0.00010855
2013-01-26 | 288964 | 1129 | URBAN | Equipment failure | 9.5 | 47 | 446.5 | 0.00045084 | 9.5924e-06
2013-01-26 | 288965 | NMC16A | RURAL | Weather | 923.32 | 104.3158 | 93693.08 | 0.26996 | 0.0026604
2013-01-26 | 288966 | TWT12A | RURAL | Weather | 906.51 | 102 | 92464.02 | 0.26642 | 0.0026119
2013-01-26 | 288971 | CRY2A | RURAL | Weather | 736 | 70.6477 | 58340 | 0.1681 | 0.0021206
2013-01-26 | 288975 | MCN2 | RURAL | Equipment failure | 20.66 | 175 | 3615.5 | 0.010417 | 5.9528e-05
2013-01-26 | 288979 | WRG15A | URBAN | Equipment failure | 42.24 | 174 | 7349.76 | 0.0074213 | 4.2651e-05
2013-01-26 | 288981 | ZMR10 | URBAN | Equipment failure | 79 | 109 | 8611 | 0.0086948 | 7.9769e-05
2013-01-26 | 288982 | WSE5A | RURAL | Weather | 694.75 | 26.3066 | 18323 | 0.052794 | 0.0020018
2013-01-26 | 288984 | FDS1 | RURAL | Equipment failure | 4 | 45 | 180 | 0.00051863 | 1.1525e-05
2013-01-26 | 288986 | TWT12A | RURAL | Other | 906.51 | 50 | 45325.5 | 0.1306 | 0.0026119
2013-01-26 | 288987 | BMT3 | RURAL | Weather | 23.5 | 140 | 3290 | 0.0094795 | 6.7711e-05
2013-01-26 | 288988 | PWC4 | RURAL | Weather | 18 | 346 | 6228 | 0.017945 | 5.1863e-05
2013-01-26 | 288989 | GYS5A | RURAL | Weather | 178 | 190.8679 | 33501 | 0.096526 | 0.00051287
2013-01-26 | 288990 | NBR4 | RURAL | Weather | 812.66 | 133.4943 | 114454.68 | 0.32978 | 0.0023415
2013-01-26 | 288991 | NBR8 | RURAL | Weather | 22 | 276 | 6072 | 0.017495 | 6.3389e-05
2013-01-26 | 288995 | WMD8B | RURAL | Weather | 36.5 | 32 | 1168 | 0.0033654 | 0.00010517
2013-01-26 | 288996 | JBB12B | RURAL | Weather | 20 | 29 | 580 | 0.0016712 | 5.7626e-05
2013-01-26 | 288997 | JBB12B | RURAL | Weather | 12 | 137 | 1644 | 0.0047369 | 3.4576e-05
2013-01-26 | 288998 | WMD14A | RURAL | Weather | 167 | 7 | 1169 | 0.0033682 | 0.00048118
2013-01-26 | 289000 | MCN3 | URBAN | Equipment failure | 1 | 322 | 322 | 0.00032513 | 1.0097e-06
2013-01-26 | 289005 | NBR8 | RURAL | Weather | 105.75 | 238 | 25168.5 | 0.072518 | 0.0003047
2013-01-26 | 289006 | PWC4 | RURAL | Other | 29.5 | 124 | 3658 | 0.01054 | 8.4998e-05
2013-01-26 | 289008 | IPL1 | RURAL | Weather | 208 | 37.6429 | 7644 | 0.022025 | 0.00059931
2013-01-26 | 289009 | CBW6 | RURAL | Weather | 2140.5 | 34 | 72777 | 0.20969 | 0.0061674
2013-01-26 | 289010 | TGP5B | URBAN | Third party impacts | 1517.41 | 238.6786 | 288150.71 | 0.29095 | 0.0015322
2013-01-26 | 289012 | BWH13A | RURAL | Weather | 654.51 | 92.5926 | 101669.26 | 0.29294 | 0.0018858
2013-01-26 | 289013 | HPK3A | URBAN | Weather | 2542.99 | 104.2813 | 264726.47 | 0.2673 | 0.0025677
2013-01-26 | 289014 | AHD8 | URBAN | Weather | 1129.33 | 135 | 152459.55 | 0.15394 | 0.0011403
2013-01-26 | 289017 | MLY4 | RURAL | Weather | 624.99 | 424.0943 | 273875.32 | 0.78912 | 0.0018008
2013-01-26 | 289018 | MLY6 | RURAL | Weather | 613.49 | 143.2436 | 89794.28 | 0.25872 | 0.0017676
2013-01-26 | 289019 | KCY4 | RURAL | Weather | 88 | 229.7778 | 18736 | 0.053984 | 0.00025355
2013-01-26 | 289020 | NBR4 | RURAL | Weather | 812.66 | 173.7701 | 131809.78 | 0.37978 | 0.0023415
2013-01-26 | 289025 | MTB17A | RURAL | Equipment failure | 562.34 | 170.1667 | 88755.9 | 0.25573 | 0.0016203
2013-01-26 | 289026 | PWC4 | RURAL | Weather | 625.51 | 189.2273 | 109434.95 | 0.31531 | 0.0018023
2013-01-26 | 289501 | GYS5A | RURAL | Weather | 178 | 2026.5283 | 300047 | 0.86453 | 0.00051287
2013-01-26 | 289804 | MLY1 | RURAL | Weather | 818.01 | 6 | 4908.06 | 0.014142 | 0.0023569
2013-01-26 | 289804 | MLY3 | RURAL | Weather | 2042.98 | 6 | 12257.88 | 0.035319 | 0.0058864
2013-01-26 | 289804 | MLY4 | RURAL | Weather | 624.99 | 6 | 3749.94 | 0.010805 | 0.0018008
2013-01-26 | 289804 | MLY6 | RURAL | Weather | 613.49 | 6 | 3680.94 | 0.010606 | 0.0017676
2013-01-26 | 289910 | WFD1B | RURAL | Weather | 344.97 | 1871.1145 | 735004.46 | 2.1178 | 0.00099396
2013-01-26 | 290050 | SMF3A | RURAL | Weather | 1 | 6588 | 6588 | 0.018982 | 2.8813e-06
2013-01-26 | 290134 | MLY1 | RURAL | Weather | 818.01 | 5121.9857 | 3877596.83 | 11.1725 | 0.0023569
2013-01-26 | 290370 | MLY6 | RURAL | Other | 9 | 8190 | 73710 | 0.21238 | 2.5932e-05
2013-01-26 | 290622 | SBH11 | URBAN | Third party impacts | 87.25 | 165 | 14396.25 | 0.014536 | 8.8099e-05
2013-01-26 | 290627 | SMF3A | RURAL | Vegetation | 9 | 438 | 3942 | 0.011358 | 2.5932e-05
2013-01-26 | 290628 | SMF3A | RURAL | Weather | 9 | 41 | 369 | 0.0010632 | 2.5932e-05
2013-01-26 | 290630 | ZMR10 | URBAN | Equipment failure | 58.74 | 188 | 11043.12 | 0.011151 | 5.9312e-05
2013-01-26 | 290736 | BMT3 | RURAL | Other | 2.5 | 312 | 780 | 0.0022474 | 7.2033e-06
2013-01-26 | 290737 | MLB6A | RURAL | Weather | 7.26 | 25 | 181.5 | 0.00052296 | 2.0918e-05
2013-01-26 | 290738 | CMD13A | URBAN | Weather | 84.48 | 84 | 7096.32 | 0.0071654 | 8.5302e-05
2013-01-26 | 290780 | LLY3 | RURAL | Other | 5 | 79 | 395 | 0.0011381 | 1.4407e-05
2013-01-26 | 292394 | MGP13A | RURAL | Weather | 584 | 4658.1 | 3880922 | 11.1821 | 0.0016827
2013-01-27 | 289023 | SMF3A | RURAL | Weather | 161 | 6713 | 1080793 | 3.1139 | 0.00046386
2013-01-27 | 289029 | KMR28A | URBAN | Weather | 951.5 | 101.3889 | 96410 | 0.097351 | 0.00096079
2013-01-27 | 289030 | PWC4 | RURAL | Weather | 625.51 | 20.3182 | 10963.41 | 0.031587 | 0.0018022
2013-01-27 | 289031 | CLD28A | RURAL | Weather | 88.56 | 49 | 4339.44 | 0.012502 | 0.00025515
2013-01-27 | 289040 | WMD8B | RURAL | Weather | 391.75 | 221.1356 | 161473.5 | 0.46522 | 0.0011287
2013-01-27 | 289041 | MRK6 | URBAN | Other | 1742.75 | 29 | 50539.75 | 0.051033 | 0.0017598
2013-01-27 | 289043 | PRG2A | RURAL | Weather | 62.31 | 24 | 1495.44 | 0.0043085 | 0.00017952
2013-01-27 | 289044 | BRD11A | RURAL | Weather | 968.5 | 35.2564 | 64374 | 0.18547 | 0.0027903
2013-01-27 | 289045 | LBH1B | RURAL | Weather | 986.5 | 55 | 54257.5 | 0.15632 | 0.0028422
2013-01-27 | 289045 | LBH2A | URBAN | Weather | 1 | 55 | 55 | 5.5537e-05 | 1.0098e-06
2013-01-27 | 289045 | LBH3A | RURAL | Weather | 782.33 | 55 | 43028.15 | 0.12397 | 0.002254
2013-01-27 | 289045 | LBH5A | RURAL | Weather | 761.07 | 55 | 41858.85 | 0.1206 | 0.0021927
2013-01-27 | 289045 | LBH6A | RURAL | Weather | 1596.87 | 55 | 87827.85 | 0.25304 | 0.0046007
2013-01-27 | 289046 | KWH1 | RURAL | Weather | 52 | 6191 | 321932 | 0.92752 | 0.00014982
2013-01-27 | 289047 | TBV4 | RURAL | Weather | 515.17 | 404 | 208128.68 | 0.59964 | 0.0014843
2013-01-27 | 289048 | NBR2 | URBAN | Weather | 570.41 | 229 | 130623.89 | 0.1319 | 0.00057598
2013-01-27 | 289049 | KWH1 | RURAL | Equipment failure | 574 | 15 | 8610 | 0.024806 | 0.0016537
2013-01-27 | 289049 | KWH2 | RURAL | Equipment failure | 843.95 | 15 | 12659.25 | 0.036472 | 0.0024315
2013-01-27 | 289049 | KWH3 | RURAL | Equipment failure | 418.98 | 15 | 6284.7 | 0.018107 | 0.0012071
2013-01-27 | 289050 | WMR1 | RURAL | Weather | 427.49 | 3344 | 1429526.56 | 4.1186 | 0.0012316
2013-01-27 | 289051 | BWH16A | RURAL | Weather | 281.33 | 328.7813 | 96563.18 | 0.27821 | 0.00081054
2013-01-27 | 289052 | SMF1B | RURAL | Weather | 25.5 | 78 | 1989 | 0.0057305 | 7.3468e-05
2013-01-27 | 289053 | GBG26 | URBAN | Equipment failure | 915.99 | 242 | 221669.58 | 0.22383 | 0.00092493
2013-01-27 | 289054 | SIS2 | RURAL | Weather | 430 | 709 | 304870 | 0.87836 | 0.0012389
2013-01-27 | 289055 | SMF6A | RURAL | Weather | 312.66 | 329.8542 | 69388.66 | 0.19991 | 0.0009008
2013-01-27 | 289056 | EZRRWD4 | RURAL | Weather | 60 | 331.6667 | 19834 | 0.057144 | 0.00017287
2013-01-27 | 289057 | WMR2 | RURAL | Equipment failure | 142.01 | 768.7368 | 122560.13 | 0.35311 | 0.00040914
2013-01-27 | 289058 | TWG16 | URBAN | Weather | 379.83 | 114 | 43300.62 | 0.043723 | 0.00038354
2013-01-27 | 289059 | BDT5 | RURAL | Weather | 115.01 | 207.5882 | 23621.01 | 0.068054 | 0.00033135
2013-01-27 | 289060 | PWC3 | RURAL | Weather | 1013.32 | 751.2128 | 743150.52 | 2.1411 | 0.0029195
2013-01-27 | 289061 | LTA5 | URBAN | Weather | 1980.83 | 227 | 449648.41 | 0.45404 | 0.0020002
2013-01-27 | 289062 | CHL4 | URBAN | Other | 1398.83 | 16 | 22381.28 | 0.0226 | 0.0014125
2013-01-27 | 289063 | RBY6 | URBAN | Weather | 1357.33 | 207 | 280967.31 | 0.28371 | 0.0013706
2013-01-27 | 289064 | SMF6A | RURAL | Weather | 245.99 | 122 | 30010.78 | 0.086464 | 0.00070872
2013-01-27 | 289065 | OXL4A | URBAN | Equipment failure | 445 | 158 | 70310 | 0.070996 | 0.00044934
2013-01-27 | 289066 | WSE3A | RURAL | Weather | 406 | 4532 | 1839992 | 5.3012 | 0.0011697
2013-01-27 | 289067 | AMR3 | RURAL | Weather | 98.01 | 165 | 16171.65 | 0.046592 | 0.00028238
2013-01-27 | 289068 | SMF5A | RURAL | Weather | 692.5 | 600.8788 | 416077 | 1.1988 | 0.0019952
2013-01-27 | 289068 | SMF5B | RURAL | Weather | 477 | 600 | 286200 | 0.82457 | 0.0013743
2013-01-27 | 289069 | SHW4 | URBAN | Weather | 514.82 | 215 | 110686.3 | 0.11177 | 0.00051984
2013-01-27 | 289070 | RCF2A | URBAN | Weather | 2126.08 | 173 | 367811.84 | 0.3714 | 0.0021468
2013-01-27 | 289071 | MTB1B | RURAL | Weather | 33 | 210 | 6930 | 0.019966 | 9.5076e-05
2013-01-27 | 289072 | 1084 | URBAN | Other | 30.66 | 179.1111 | 5493.48 | 0.0055471 | 3.0959e-05
2013-01-27 | 289073 | CCY21A | URBAN | Equipment failure | 1 | 65 | 65 | 6.5634e-05 | 1.0098e-06
2013-01-27 | 289074 | AHD5 | URBAN | Weather | 2037.65 | 174.5714 | 347396.62 | 0.35079 | 0.0020575
2013-01-27 | 289075 | SMF1B | RURAL | Weather | 185 | 201 | 37185 | 0.10713 | 0.000533
2013-01-27 | 289076 | QPT24A | URBAN | Equipment failure | 21 | 171 | 3591 | 0.003626 | 2.1205e-05
2013-01-27 | 289077 | WRD15B | URBAN | Weather | 90.5 | 130 | 11765 | 0.01188 | 9.1383e-05
2013-01-27 | 289078 | MTB15A | RURAL | Weather | 376.5 | 3033.4717 | 1065605.5 | 3.0701 | 0.0010847
2013-01-27 | 289079 | MRK6 | URBAN | Weather | 1742.75 | 315 | 548966.25 | 0.55432 | 0.0017598
2013-01-27 | 289080 | AHD12A | URBAN | Weather | 845.66 | 800 | 676528 | 0.68313 | 0.00085391
2013-01-27 | 289081 | NMC13A | RURAL | Weather | 995.5 | 162 | 161271 | 0.46464 | 0.0028681
2013-01-27 | 289082 | TWT12A | RURAL | Weather | 446.5 | 159.7931 | 89267 | 0.25719 | 0.0012864
2013-01-27 | 289100 | SBY6 | URBAN | Weather | 493.19 | 140 | 69046.6 | 0.06972 | 0.000498
2013-01-27 | 289101 | BHD23A | RURAL | Other | 1206.5 | 758.2759 | 663813.5 | 1.9125 | 0.003476
2013-01-27 | 289102 | GYM7A | RURAL | Weather | 1415 | 637.1789 | 759166.54 | 2.1872 | 0.0040767
2013-01-27 | 289103 | YDA3A | RURAL | Weather | 388.5 | 724.75 | 284152.5 | 0.81867 | 0.0011193
2013-01-27 | 289105 | 332 | URBAN | Weather | 1 | 20 | 20 | 2.0195e-05 | 1.0098e-06
2013-01-27 | 289105 | RCF10A | URBAN | Weather | 643.06 | 20 | 12861.2 | 0.012987 | 0.00064934
2013-01-27 | 289105 | RCF11A | URBAN | Weather | 6 | 20 | 120 | 0.00012117 | 6.0586e-06
2013-01-27 | 289105 | RCF12A | URBAN | Weather | 883.34 | 20 | 17666.8 | 0.017839 | 0.00089196
2013-01-27 | 289105 | RCF1A | URBAN | Weather | 1864 | 20 | 37280 | 0.037644 | 0.0018822
2013-01-27 | 289105 | RCF2A | URBAN | Weather | 2126.08 | 20 | 42521.6 | 0.042937 | 0.0021468
2013-01-27 | 289105 | RCF3A | URBAN | Weather | 369.5 | 20 | 7390 | 0.0074621 | 0.00037311
2013-01-27 | 289105 | RCF5A | URBAN | Weather | 591.25 | 20 | 11825 | 0.01194 | 0.00059702
2013-01-27 | 289105 | RCF9A | URBAN | Weather | 1376.58 | 20 | 27531.6 | 0.0278 | 0.00139
2013-01-27 | 289105 | UNNAMED900 | URBAN | Weather | 406.67 | 20 | 8133.4 | 0.0082128 | 0.00041064
2013-01-27 | 289106 | NMK18 | URBAN | Weather | 988.16 | 314.1429 | 315889.44 | 0.31897 | 0.0009978
2013-01-27 | 289107 | OXL10A | URBAN | Weather | 120.99 | 82 | 9921.18 | 0.010018 | 0.00012217
2013-01-27 | 289107 | OXL4A | URBAN | Weather | 445 | 82 | 36490 | 0.036846 | 0.00044934
2013-01-27 | 289108 | MLB6A | RURAL | Weather | 335 | 623 | 208705 | 0.6013 | 0.00096517
2013-01-27 | 289109 | GAP9A | URBAN | Weather | 1220.49 | 580 | 707884.2 | 0.71479 | 0.0012324
2013-01-27 | 289110 | MLB6A | RURAL | Weather | 436.99 | 624 | 272681.76 | 0.78562 | 0.001259
2013-01-27 | 289111 | BIS15A | URBAN | Weather | 1212.16 | 572 | 693355.52 | 0.70012 | 0.001224
2013-01-27 | 289112 | BDT5 | RURAL | Weather | 937.01 | 49 | 45913.49 | 0.13228 | 0.0026996
2013-01-27 | 289113 | WNM4 | URBAN | Weather | 1343.5 | 403 | 541430.5 | 0.54671 | 0.0013566
2013-01-27 | 289115 | AGE10 | URBAN | Weather | 2241.81 | 2353.2 | 5403124.52 | 5.4559 | 0.0022637
2013-01-27 | 289116 | 373 | URBAN | Weather | 2 | 534 | 1068 | 0.0010784 | 2.0195e-06
2013-01-27 | 289117 | IDY9A | URBAN | Weather | 1 | 345 | 345 | 0.00034837 | 1.0098e-06
2013-01-27 | 289117 | IDY9B | URBAN | Weather | 906.5 | 709.5789 | 1348619 | 1.3618 | 0.00091535
2013-01-27 | 289118 | NBR9 | RURAL | Weather | 2078 | 843.9355 | 1753065 | 5.0507 | 0.0059869
2013-01-27 | 289119 | TSN7A | URBAN | Weather | 10.72 | 484 | 5188.48 | 0.0052391 | 1.0825e-05
2013-01-27 | 289120 | BGY5A | RURAL | Weather | 1007.5 | 884.5536 | 1018368.5 | 2.934 | 0.0029027
2013-01-27 | 289121 | BPN34A | URBAN | Weather | 1606.99 | 734 | 1151545.74 | 1.1628 | 0.0016227
2013-01-27 | 289121 | BPN34B | URBAN | Weather | 1 | 626 | 626 | 0.00063211 | 1.0098e-06
2013-01-27 | 289122 | CCY1B | URBAN | Weather | 840.5 | 389 | 326954.5 | 0.33015 | 0.0008487
2013-01-27 | 289123 | BGY15A | URBAN | Weather | 1458.5 | 866 | 1263061 | 1.2754 | 0.0014727
2013-01-27 | 289124 | LDR3 | URBAN | Weather | 2227.91 | 622.2667 | 2589962.17 | 2.6152 | 0.0022497
2013-01-27 | 289126 | GAP8A | URBAN | Weather | 1534.65 | 868 | 1332076.2 | 1.3451 | 0.0015496
2013-01-27 | 289127 | WCL13A | URBAN | Weather | 97.67 | 285 | 27835.95 | 0.028108 | 9.8623e-05
2013-01-27 | 289129 | TCB1 | RURAL | Weather | 1408.99 | 382.075 | 598357.72 | 1.7239 | 0.0040594
2013-01-27 | 289130 | JBB16A | RURAL | Weather | 700.5 | 1033.5469 | 690000 | 1.988 | 0.0020182
2013-01-27 | 289131 | CLD17A | URBAN | Equipment failure | 1633.15 | 321 | 525294.65 | 0.53042 | 0.0016491
2013-01-27 | 289132 | AHD4A | URBAN | Equipment failure | 607.66 | 341.6176 | 407746.9 | 0.41173 | 0.00061359
2013-01-27 | 289132 | AHD4B | RURAL | Equipment failure | 550 | 357.5 | 393250 | 1.133 | 0.0015846
2013-01-27 | 289132 | AHD9 | URBAN | Equipment failure | 309.17 | 149 | 46066.33 | 0.046516 | 0.00031219
2013-01-27 | 289133 | VPK2A | URBAN | Equipment failure | 274.83 | 2082 | 782869.2 | 0.79051 | 0.00027751
2013-01-27 | 289133 | VPK9A | URBAN | Equipment failure | 564.33 | 21 | 11850.93 | 0.011967 | 0.00056984
2013-01-27 | 289134 | AHL11A | URBAN | Equipment failure | 1705 | 267.6296 | 429966 | 0.43416 | 0.0017216
2013-01-27 | 289134 | AHL11B | URBAN | Equipment failure | 1 | 181 | 181 | 0.00018277 | 1.0098e-06
2013-01-27 | 289135 | EMP21A | RURAL | Equipment failure | 1525.49 | 587.866 | 769800.49 | 2.2179 | 0.0043951
2013-01-27 | 289136 | NGI1B | RURAL | Weather | 1283.5 | 773 | 992145.5 | 2.8585 | 0.0036979
2013-01-27 | 289137 | SIS1 | RURAL | Equipment failure | 697 | 181 | 126157 | 0.36347 | 0.0020081
2013-01-27 | 289138 | SBH4 | URBAN | Weather | 1223.2 | 255.2174 | 310752.1 | 0.31379 | 0.0012351
2013-01-27 | 289138 | SBH6 | URBAN | Weather | 2082.46 | 191 | 397749.86 | 0.40163 | 0.0021028
2013-01-27 | 289140 | AHD21 | URBAN | Weather | 1288 | 973.1111 | 1246732 | 1.2589 | 0.0013006
2013-01-27 | 289142 | CBW6 | RURAL | Weather | 2140.5 | 1419.6381 | 1739673 | 5.0122 | 0.006167
2013-01-27 | 289143 | NSD30A | URBAN | Weather | 1 | 956 | 956 | 0.00096533 | 1.0098e-06
2013-01-27 | 289143 | NSD30B | URBAN | Weather | 741.83 | 1273.5625 | 862694.58 | 0.87111 | 0.00074907
2013-01-27 | 289146 | VPK19A | URBAN | Weather | 274 | 1160.6 | 314476 | 0.31755 | 0.00027667
2013-01-27 | 289147 | MFN12A | RURAL | Weather | 1107.33 | 802 | 888078.66 | 2.5586 | 0.0031903
2013-01-27 | 289148 | CBW11 | RURAL | Weather | 1147.99 | 258.6301 | 446016.53 | 1.285 | 0.0033075
2013-01-27 | 289148 | CBW7 | RURAL | Weather | 76.5 | 28 | 2142 | 0.0061713 | 0.0002204
2013-01-27 | 289150 | LTA6 | URBAN | Weather | 1488.25 | 1031 | 1534385.75 | 1.5494 | 0.0015028
2013-01-27 | 289151 | AHD12A | URBAN | Other | 845.66 | 1780.3125 | 1502985.6 | 1.5177 | 0.00085391
2013-01-27 | 289155 | ARL6B | URBAN | Weather | 201 | 1173 | 235773 | 0.23807 | 0.00020296
2013-01-27 | 289156 | AHD20 | URBAN | Equipment failure | 229.5 | 1888 | 433296 | 0.43752 | 0.00023174
2013-01-27 | 289157 | AHD15A | URBAN | Weather | 853.66 | 1136.8421 | 969684.78 | 0.97915 | 0.00086199
2013-01-27 | 289160 | ACR5 | RURAL | Weather | 1318.5 | 1267 | 1670539.5 | 4.813 | 0.0037987
2013-01-27 | 289161 | BBS6 | URBAN | Weather | 512.5 | 1156 | 592450 | 0.59823 | 0.0005175
2013-01-27 | 289162 | TWG16 | URBAN | Weather | 417.83 | 957.4762 | 399873.31 | 0.40378 | 0.00042191
2013-01-27 | 289164 | KRA7 | URBAN | Equipment failure | 1223.67 | 1088.5263 | 1584981.78 | 1.6005 | 0.0012356
2013-01-27 | 289165 | BRD8A | RURAL | Weather | 1047.99 | 1269.9277 | 1266859.42 | 3.6499 | 0.0030194
2013-01-27 | 289167 | QPT22A | URBAN | Weather | 1127.5 | 911 | 1027152.5 | 1.0372 | 0.0011385
2013-01-27 | 289169 | ACR7 | URBAN | Weather | 435 | 1369 | 595515 | 0.60133 | 0.00043925
2013-01-27 | 289171 | CBT12A | RURAL | Weather | 807.71 | 611.14 | 531507.58 | 1.5313 | 0.0023271
2013-01-27 | 289172 | LHM3 | URBAN | Weather | 1733 | 1606 | 2783198 | 2.8104 | 0.0017499
2013-01-27 | 289173 | LHM1 | URBAN | Weather | 1579 | 1031 | 1627949 | 1.6438 | 0.0015944
2013-01-27 | 289175 | MFN15A | RURAL | Weather | 84.5 | 1608.0833 | 139691 | 0.40246 | 0.00024345
2013-01-27 | 289177 | BKD3A | URBAN | Other | 1789 | 590 | 1055510 | 1.0658 | 0.0018065
2013-01-27 | 289178 | CFD6A | URBAN | Other | 2032.5 | 750 | 1524375 | 1.5393 | 0.0020523
2013-01-27 | 289179 | BTA5A | RURAL | Weather | 1678.75 | 2709.3582 | 4229784 | 12.1864 | 0.0048366
2013-01-27 | 289180 | LGV5B | RURAL | Weather | 625.5 | 3550.7059 | 2195611.5 | 6.3258 | 0.0018021
2013-01-27 | 289181 | BRD11A | RURAL | Equipment failure | 968.5 | 1273.2955 | 1258713.5 | 3.6265 | 0.0027903
2013-01-27 | 289184 | BIS2B | RURAL | Equipment failure | 1068.5 | 1118 | 1194583 | 3.4417 | 0.0030784
2013-01-27 | 289188 | RST8A | URBAN | Weather | 301 | 1312 | 394912 | 0.39877 | 0.00030394
2013-01-27 | 289190 | ACR2A | URBAN | Weather | 1241.5 | 1107 | 1374340.5 | 1.3878 | 0.0012536
2013-01-27 | 289190 | ACR2B | URBAN | Weather | 1462.5 | 1179.6207 | 1711749.5 | 1.7285 | 0.0014768
2013-01-27 | 289199 | TWG17 | URBAN | Weather | 1857.6 | 1473.3158 | 2736556.8 | 2.7633 | 0.0018757
2013-01-27 | 289204 | NSW3A | URBAN | Weather | 1867.16 | 1265 | 2361957.4 | 2.385 | 0.0018854
2013-01-27 | 289208 | HPK8A | URBAN | Other | 1440.49 | 368 | 530100.32 | 0.53527 | 0.0014545
2013-01-27 | 289209 | CRB24B | URBAN | Weather | 2454 | 1090 | 2674860 | 2.701 | 0.002478
2013-01-27 | 289210 | NRA16A | RURAL | Weather | 284 | 1878.6667 | 546277 | 1.5739 | 0.00081823
2013-01-27 | 289211 | BLH13A | URBAN | Weather | 6 | 1835 | 11010 | 0.011117 | 6.0586e-06
2013-01-27 | 289211 | BLH13B | RURAL | Weather | 339.34 | 1835 | 622688.9 | 1.794 | 0.00097767
2013-01-27 | 289212 | AGT23A | URBAN | Weather | 1524.82 | 715 | 1090246.3 | 1.1009 | 0.0015397
2013-01-27 | 289214 | BHL5A | URBAN | Other | 1723.75 | 434 | 748107.5 | 0.75541 | 0.0017406
2013-01-27 | 289218 | AMR3 | RURAL | Weather | 407.49 | 1523 | 620607.27 | 1.788 | 0.001174
2013-01-27 | 289219 | BDA12A | URBAN | Weather | 1 | 1836 | 1836 | 0.0018539 | 1.0098e-06
2013-01-27 | 289219 | BDA12B | URBAN | Weather | 1600.18 | 2035.7 | 3389765.09 | 3.4228 | 0.0016158
2013-01-27 | 289220 | AMR3 | RURAL | Weather | 208.5 | 1539 | 320881.5 | 0.92449 | 0.00060071
2013-01-27 | 289221 | NRA13A | RURAL | Weather | 1924.65 | 736.3409 | 1446688.94 | 4.168 | 0.0055451
2013-01-27 | 289224 | IDY10A | URBAN | Weather | 584 | 984 | 574656 | 0.58026 | 0.0005897
2013-01-27 | 289225 | BLH13A | URBAN | Weather | 6 | 4248 | 25488 | 0.025737 | 6.0586e-06
2013-01-27 | 289225 | BLH13B | RURAL | Weather | 339.34 | 2369.1667 | 842988.9 | 2.4287 | 0.00097767
2013-01-27 | 289227 | SFD10 | URBAN | Weather | 1341.5 | 426 | 571479 | 0.57706 | 0.0013546
2013-01-27 | 289228 | CMV7 | URBAN | Weather | 1709 | 2021 | 3453889 | 3.4876 | 0.0017257
2013-01-27 | 289231 | AGE8 | URBAN | Weather | 938.33 | 2180.4211 | 2113847.52 | 2.1345 | 0.00094749
2013-01-27 | 289251 | SIS1 | RURAL | Weather | 1190 | 785 | 934150 | 2.6914 | 0.0034285
2013-01-27 | 289252 | NRG14A | RURAL | Weather | 308.5 | 685 | 211322.5 | 0.60884 | 0.00088882
2013-01-27 | 289272 | CBW10 | RURAL | Weather | 1046 | 204.4545 | 224547 | 0.64694 | 0.0030136
2013-01-27 | 289291 | SFD7A | URBAN | Weather | 1060.99 | 2632.75 | 2793774.93 | 2.821 | 0.0010713
2013-01-27 | 289291 | SFD7B | URBAN | Weather | 1 | 2617 | 2617 | 0.0026425 | 1.0098e-06
2013-01-27 | 289292 | BPN35A | URBAN | Weather | 2136.5 | 2706 | 5781369 | 5.8378 | 0.0021574
2013-01-27 | 289310 | SFD10 | URBAN | Equipment failure | 1341.5 | 2371.6111 | 3183025.5 | 3.2141 | 0.0013546
2013-01-27 | 289311 | JBB1B | RURAL | Equipment failure | 533 | 2110 | 1124630 | 3.2402 | 0.0015356
2013-01-27 | 289312 | CFD6A | URBAN | Weather | 2032.5 | 833 | 1693072.5 | 1.7096 | 0.0020523
2013-01-27 | 289390 | GYS3A | RURAL | Weather | 428 | 3318 | 1420104 | 4.0914 | 0.0012331
2013-01-27 | 289391 | BLB5A | URBAN | Weather | 1067.33 | 973.6667 | 1014850.35 | 1.0248 | 0.0010777
2013-01-27 | 289392 | LBH6A | RURAL | Weather | 32 | 1394 | 44608 | 0.12852 | 9.2195e-05
2013-01-27 | 289433 | TGP9A | RURAL | Weather | 1767.01 | 2254.1964 | 4246399.66 | 12.2343 | 0.0050909
2013-01-27 | 289434 | BPN34A | URBAN | Weather | 1606.99 | 1334.0571 | 1756278.75 | 1.7734 | 0.0016227
2013-01-27 | 289434 | BPN34B | URBAN | Weather | 1 | 625 | 625 | 0.0006311 | 1.0098e-06
2013-01-27 | 289435 | CRM16A | RURAL | Weather | 2524.47 | 2700 | 6816069 | 19.6377 | 0.0072732
2013-01-27 | 289452 | SMF2A | RURAL | Weather | 932.49 | 3193.8 | 2975378.49 | 8.5723 | 0.0026866
2013-01-27 | 289454 | GAP8A | URBAN | Weather | 1534.65 | 1177.1111 | 1824341.34 | 1.8421 | 0.0015496
2013-01-27 | 289455 | KLG11A | URBAN | Weather | 2378.33 | 2407 | 5724640.31 | 5.7805 | 0.0024015
2013-01-27 | 289456 | KLG5A | RURAL | Weather | 1164.66 | 2582 | 3007152.12 | 8.6639 | 0.0033555
2013-01-27 | 289460 | WSE5A | RURAL | Weather | 694.75 | 2470 | 1716032.5 | 4.944 | 0.0020016
2013-01-27 | 289464 | PPE3A | RURAL | Weather | 729 | 2805 | 2044845 | 5.8914 | 0.0021003
2013-01-27 | 289466 | 312 | URBAN | Equipment failure | 1 | 11020 | 11020 | 0.011128 | 1.0098e-06
2013-01-27 | 289473 | JBB4A | URBAN | Weather | 429 | 3855 | 1653795 | 1.6699 | 0.00043319
2013-01-27 | 289474 | WNM6 | URBAN | Weather | 812 | 1551 | 1259412 | 1.2717 | 0.00081993
2013-01-27 | 289477 | 314 | URBAN | Equipment failure | 1 | 5467 | 5467 | 0.0055204 | 1.0098e-06
2013-01-27 | 289479 | IDY1A | URBAN | Weather | 1104.83 | 1348 | 1489310.84 | 1.5038 | 0.0011156
2013-01-27 | 289480 | 3702 | URBAN | Other | 0.75 | 2871 | 2153.25 | 0.0021743 | 7.5732e-07
2013-01-27 | 289482 | BDT5 | RURAL | Weather | 115.01 | 3228 | 371252.28 | 1.0696 | 0.00033135
2013-01-27 | 289487 | MTB3A | RURAL | Equipment failure | 1001.33 | 3158.6545 | 3109245.52 | 8.958 | 0.0028849
2013-01-27 | 289490 | MTB16A | RURAL | Weather | 385.99 | 2981 | 1150636.19 | 3.3151 | 0.0011121
2013-01-27 | 289492 | RCF9A | URBAN | Weather | 1376.58 | 1271.5333 | 1626563.3 | 1.6424 | 0.00139
2013-01-27 | 289493 | MTB1B | RURAL | Weather | 1222.99 | 4662 | 5701579.38 | 16.4268 | 0.0035235
2013-01-27 | 289494 | MLY3 | RURAL | Weather | 1819.99 | 1083.12 | 1713448.68 | 4.9366 | 0.0052436
2013-01-27 | 289497 | BGY5A | RURAL | Weather | 364.5 | 1023.76 | 377768.5 | 1.0884 | 0.0010502
2013-01-27 | 289498 | MLY3 | RURAL | Weather | 222.99 | 3627 | 808784.73 | 2.3302 | 0.00064245
2013-01-27 | 289500 | NMC5A | RURAL | Weather | 404 | 3606 | 1456824 | 4.1972 | 0.001164
2013-01-27 | 289503 | EMD2 | RURAL | Weather | 110 | 3236.8824 | 357308 | 1.0294 | 0.00031692
2013-01-27 | 289508 | KCY1 | URBAN | Weather | 612 | 6 | 3672 | 0.0037078 | 0.00061797
2013-01-27 | 289508 | KCY2 | RURAL | Weather | 358.26 | 6 | 2149.56 | 0.0061931 | 0.0010322
2013-01-27 | 289508 | KCY3 | URBAN | Weather | 5.65 | 6 | 33.9 | 3.4231e-05 | 5.7051e-06
2013-01-27 | 289508 | KCY4 | RURAL | Weather | 698.12 | 6 | 4188.72 | 0.012068 | 0.0020113
2013-01-27 | 289508 | KCY5 | RURAL | Weather | 524 | 6 | 3144 | 0.0090581 | 0.0015097
2013-01-27 | 289508 | WFD1B | RURAL | Weather | 344.97 | 6 | 2069.82 | 0.0059633 | 0.00099389
2013-01-27 | 289508 | WFD2A | URBAN | Weather | 1 | 6 | 6 | 6.0586e-06 | 1.0098e-06
2013-01-27 | 289508 | WFD2B | RURAL | Weather | 802.78 | 6 | 4816.68 | 0.013877 | 0.0023129
2013-01-27 | 289508 | WFD3A | RURAL | Weather | 245.18 | 6 | 1471.08 | 0.0042383 | 0.00070639
2013-01-27 | 289508 | WFD5A | RURAL | Weather | 549.51 | 6 | 3297.06 | 0.0094991 | 0.0015832
2013-01-27 | 289508 | WFD6A | RURAL | Weather | 357.22 | 6 | 2143.32 | 0.0061751 | 0.0010292
2013-01-27 | 289510 | MTB13A | RURAL | Weather | 1474.99 | 3583.4348 | 5290927.61 | 15.2436 | 0.0042496
2013-01-27 | 289511 | NGI1B | RURAL | Weather | 438 | 3807 | 1667466 | 4.8041 | 0.0012619
2013-01-27 | 289512 | LBH6A | RURAL | Weather | 756.37 | 2195 | 1660232.15 | 4.7833 | 0.0021792
2013-01-27 | 289514 | AGT31A | RURAL | Weather | 390 | 3385.449 | 1326884 | 3.8229 | 0.0011236
2013-01-27 | 289516 | RLA5 | URBAN | Weather | 2021 | 3089.1667 | 6245621 | 6.3066 | 0.0020407
2013-01-27 | 289571 | WNM6 | URBAN | Weather | 812 | 1439 | 1168468 | 1.1799 | 0.00081993
2013-01-27 | 289592 | UNNAMED900 | URBAN | Weather | 406.67 | 654 | 265962.18 | 0.26856 | 0.00041064
2013-01-27 | 289595 | HPK3A | URBAN | Weather | 494 | 8 | 3952 | 0.0039906 | 0.00049882
2013-01-27 | 289612 | MCN1 | RURAL | Equipment failure | 92.99 | 3250 | 296371.01 | 0.85387 | 0.00026791
2013-01-27 | 289671 | LBH5A | RURAL | Weather | 761.07 | 2591.175 | 1981236.69 | 5.7081 | 0.0021927
2013-01-27 | 289690 | LGL13A | URBAN | Weather | 524 | 4157 | 2178268 | 2.1995 | 0.00052911
2013-01-27 | 289692 | LGL5A | URBAN | Weather | 399 | 4202 | 1676598 | 1.693 | 0.00040289
2013-01-27 | 289710 | UPC2 | RURAL | Weather | 373.34 | 3694.4444 | 1377787.64 | 3.9695 | 0.0010756
2013-01-27 | 289754 | CNB26A | RURAL | Weather | 464.49 | 3947 | 1833342.03 | 5.282 | 0.0013382
2013-01-27 | 289756 | KCY2 | RURAL | Weather | 144.5 | 1931.9167 | 280443 | 0.80798 | 0.00041632
2013-01-27 | 289773 | MCW7 | RURAL | Weather | 407 | 2691.3469 | 1087519.5 | 3.1332 | 0.0011726
2013-01-27 | 289778 | VPT12A | URBAN | Weather | 1152.67 | 974 | 1122700.58 | 1.1337 | 0.0011639
2013-01-27 | 289779 | CVL7A | RURAL | Equipment failure | 441 | 867 | 382347 | 1.1016 | 0.0012706
2013-01-27 | 289780 | KMR28A | URBAN | Weather | 951.5 | 1650.3077 | 2342201 | 2.3651 | 0.00096079
2013-01-27 | 289791 | CLD28A | RURAL | Weather | 88.56 | 4213 | 373103.28 | 1.0749 | 0.00025515
2013-01-27 | 289802 | AHL11A | URBAN | Weather | 1705 | 874.8889 | 1130064 | 1.1411 | 0.0017216
2013-01-27 | 289802 | AHL11B | URBAN | Weather | 1 | 234 | 234 | 0.00023628 | 1.0098e-06
2013-01-27 | 289805 | PWC4 | RURAL | Weather | 394.08 | 4183.1864 | 1668343.1 | 4.8066 | 0.0011354
2013-01-27 | 289808 | IPS2A | URBAN | Weather | 1 | 293 | 293 | 0.00029586 | 1.0098e-06
2013-01-27 | 289808 | IPS2B | RURAL | Weather | 1274.84 | 293 | 373528.12 | 1.0762 | 0.0036729
2013-01-27 | 289809 | GYN6A | RURAL | Weather | 709.5 | 2288 | 1623336 | 4.677 | 0.0020441
2013-01-27 | 289811 | IBS1 | RURAL | Equipment failure | 258.5 | 3894 | 1006599 | 2.9001 | 0.00074476
2013-01-27 | 289812 | TRG10B | URBAN | Weather | 505.5 | 1059.1429 | 535477.5 | 0.5407 | 0.00051043
2013-01-27 | 289813 | BMT1 | RURAL | Weather | 130 | 5263.4576 | 682714 | 1.967 | 0.00037454
2013-01-27 | 289815 | CPK13 | RURAL | Weather | 1884.5 | 188 | 354286 | 1.0207 | 0.0054294
2013-01-27 | 289816 | JHDMDH7 | URBAN | Other | 6 | 212 | 1272 | 0.0012844 | 6.0586e-06
2013-01-27 | 289817 | BIS2B | RURAL | Weather | 1068.5 | 227 | 242549.5 | 0.69881 | 0.0030784
2013-01-27 | 289818 | TRG3 | URBAN | Weather | 761.16 | 1362.7619 | 1178623.62 | 1.1901 | 0.00076859
2013-01-27 | 289819 | GYM2A | RURAL | Weather | 3 | 2586 | 7758 | 0.022351 | 8.6433e-06
2013-01-27 | 289822 | KMR19A | URBAN | Weather | 680.83 | 3634.8 | 2309813.72 | 2.3324 | 0.00068747
2013-01-27 | 289826 | KWH3 | RURAL | Other | 27.05 | 5101 | 137982.05 | 0.39754 | 7.7933e-05
2013-01-27 | 289827 | MLY4 | RURAL | Equipment failure | 624.99 | 2364.1887 | 1459655.97 | 4.2054 | 0.0018007
2013-01-27 | 289828 | AHL15B | URBAN | Weather | 1692.97 | 2401.3929 | 4104384.02 | 4.1444 | 0.0017095
2013-01-27 | 289829 | KMR25A | RURAL | Weather | 138 | 4307 | 594366 | 1.7124 | 0.00039759
2013-01-27 | 289831 | STT3A | RURAL | Weather | 53.49 | 4043.4444 | 218701.68 | 0.6301 | 0.00015411
2013-01-27 | 289833 | SBK9 | URBAN | Weather | 1535.5 | 2746.7857 | 4217119 | 4.2583 | 0.0015505
2013-01-27 | 289834 | PRG2A | RURAL | Weather | 20 | 2593 | 51860 | 0.14941 | 5.7622e-05
2013-01-27 | 289850 | BWH13A | RURAL | Weather | 654.51 | 4850.2315 | 3156614.76 | 9.0945 | 0.0018857
2013-01-27 | 289872 | BWH13A | RURAL | Weather | 140 | 6531.1707 | 910725 | 2.6239 | 0.00040335
2013-01-27 | 289912 | CPB6 | URBAN | Weather | 388.16 | 1342 | 520910.72 | 0.52599 | 0.00039195
2013-01-27 | 289913 | AGT31A | RURAL | Weather | 390 | 572.0204 | 266672.5 | 0.76831 | 0.0011236
2013-01-27 | 289915 | SGT4 | URBAN | Weather | 1373.67 | 1089 | 1495926.63 | 1.5105 | 0.0013871
2013-01-27 | 289916 | CPB8 | RURAL | Weather | 336.49 | 1177 | 396048.73 | 1.1411 | 0.00096946
2013-01-27 | 289917 | RLB16A | RURAL | Weather | 136.66 | 1157 | 158115.62 | 0.45555 | 0.00039373
2013-01-27 | 289930 | RLB13B | RURAL | Weather | 1911.47 | 1627 | 3109961.69 | 8.9601 | 0.0055071
2013-01-27 | 289931 | BNH1B | RURAL | Weather | 682.98 | 2989 | 2041427.22 | 5.8815 | 0.0019677
2013-01-27 | 289932 | RIS4 | RURAL | Weather | 537 | 3604 | 1935348 | 5.5759 | 0.0015471
2013-01-27 | 289933 | RIS2 | URBAN | Weather | 2442.98 | 3346.6935 | 8234700.9 | 8.3151 | 0.0024668
2013-01-27 | 289950 | ALY3A | URBAN | Equipment failure | 1368.49 | 1053.5385 | 1440267.11 | 1.4543 | 0.0013818
2013-01-27 | 289990 | TBV3 | RURAL | Weather | 381.5 | 4409 | 1682033.5 | 4.8461 | 0.0010991
2013-01-27 | 290010 | UPC1 | RURAL | Weather | 532 | 4085.5312 | 2184629 | 6.2941 | 0.0015327
2013-01-27 | 290070 | BDB32A | RURAL | Weather | 847 | 2737.0455 | 2312312 | 6.662 | 0.0024403
2013-01-27 | 290135 | SMF6A | RURAL | Weather | 76 | 4985.4091 | 381164 | 1.0982 | 0.00021896
2013-01-27 | 290137 | WMR3 | RURAL | Weather | 160.33 | 675.8667 | 101900.72 | 0.29359 | 0.00046193
2013-01-27 | 290138 | NRG14A | RURAL | Weather | 28 | 5467 | 153076 | 0.44103 | 8.0671e-05
2013-01-27 | 290140 | CRY6A | RURAL | Weather | 327 | 3162 | 1033974 | 2.979 | 0.00094212
2013-01-27 | 290151 | MCW11 | RURAL | Weather | 240 | 2360 | 566400 | 1.6318 | 0.00069146
2013-01-27 | 290152 | MSV1 | RURAL | Equipment failure | 141 | 2896 | 408336 | 1.1765 | 0.00040623
2013-01-27 | 290152 | MSV2 | RURAL | Equipment failure | 170.01 | 2896 | 492348.96 | 1.4185 | 0.00048981
2013-01-27 | 290158 | TBV4 | RURAL | Weather | 515.17 | 4503 | 2319810.51 | 6.6836 | 0.0014843
2013-01-27 | 290159 | PWC6 | RURAL | Weather | 1533.25 | 3207.8824 | 4885773.5 | 14.0764 | 0.0044174
2013-01-27 | 290160 | YDA5A | RURAL | Weather | 357.99 | 2478.2353 | 601599.72 | 1.7333 | 0.0010314
2013-01-27 | 290165 | MLY3 | RURAL | Weather | 515 | 4054.1915 | 2152005 | 6.2001 | 0.0014838
2013-01-27 | 290170 | BMT1 | RURAL | Weather | 172.01 | 6112.9429 | 1040410.61 | 2.9975 | 0.00049558
2013-01-27 | 290171 | WMD13A | RURAL | Weather | 306 | 1022 | 312732 | 0.90101 | 0.00088161
2013-01-27 | 290173 | MLY6 | RURAL | Weather | 273.49 | 569 | 155615.81 | 0.44834 | 0.00078795
2013-01-27 | 290174 | 406 | URBAN | Equipment failure | 1 | 5413 | 5413 | 0.0054658 | 1.0098e-06
2013-01-27 | 290175 | MMC33A | URBAN | Weather | 1575 | 2445 | 3850875 | 3.8885 | 0.0015904
2013-01-27 | 290175 | MMCTR1H | URBAN | Weather |  | 2204
2013-01-27 | 290190 | RBY10 | URBAN | Weather | 622.83 | 2612 | 1626831.96 | 1.6427 | 0.00062891
2013-01-27 | 290191 | PWC4 | RURAL | Weather | 625.51 | 1841 | 1151563.91 | 3.3178 | 0.0018022
2013-01-27 | 290193 | NBR1 | RURAL | Vegetation | 451 | 2859 | 1289409 | 3.7149 | 0.0012994
2013-01-27 | 290210 | UMG1B | URBAN | Equipment failure | 105 | 4893 | 513765 | 0.51878 | 0.00010602
2013-01-27 | 290230 | BMT3 | RURAL | Weather | 581 | 5153.0455 | 3003558 | 8.6535 | 0.0016739
2013-01-27 | 290231 | KWH1 | RURAL | Weather | 52 | 6157 | 320164 | 0.92242 | 0.00014982
2013-01-27 | 290290 | TWT12A | RURAL | Weather | 906.51 | 2987 | 2707745.37 | 7.8013 | 0.0026117
2013-01-27 | 290310 | TWT6B | RURAL | Weather | 157 | 4320 | 678240 | 1.9541 | 0.00045233
2013-01-27 | 290330 | KWH2 | RURAL | Weather | 372.7 | 5373.1412 | 2005100.08 | 5.7769 | 0.0010738
2013-01-27 | 290352 | CRY2A | RURAL | Weather | 190.5 | 4604 | 877062 | 2.5269 | 0.00054885
2013-01-27 | 290390 | CRY6A | RURAL | Weather | 9.38 | 4789 | 44920.82 | 0.12942 | 2.7025e-05
2013-01-27 | 290450 | BMT2 | RURAL | Weather | 792.99 | 3415 | 2708060.85 | 7.8022 | 0.0022847
2013-01-27 | 290491 | EMD3 | RURAL | Weather | 71 | 4721.2857 | 336258 | 0.96879 | 0.00020456
2013-01-27 | 290513 | MLB3A | RURAL | Weather | 2788 | 1593.9756 | 4503323 | 12.9745 | 0.0080325
2013-01-27 | 290530 | WMD4A | RURAL | Weather | 1189 | 1459 | 1734751 | 4.998 | 0.0034256
2013-01-27 | 290533 | WMD14A | RURAL | Weather | 1535.58 | 1630 | 2502995.4 | 7.2114 | 0.0044241
2013-01-27 | 290551 | NBR6 | RURAL | Weather | 467.99 | 1603.3529 | 738009.45 | 2.1263 | 0.0013483
2013-01-27 | 290552 | MGL1A | RURAL | Weather | 90 | 5383.7143 | 485445 | 1.3986 | 0.0002593
2013-01-27 | 290553 | NBR8 | RURAL | Weather | 105.75 | 1903 | 201242.25 | 0.5798 | 0.00030468
2013-01-27 | 290570 | GYN3A | RURAL | Weather | 1421.5 | 1628 | 2314202 | 6.6674 | 0.0040955
2013-01-27 | 290578 | GYN2B | URBAN | Weather | 1 | 5597 | 5597 | 0.0056516 | 1.0098e-06
2013-01-27 | 290579 | GYGGYS6 | RURAL | Weather | 1 | 6245 | 6245 | 0.017992 | 2.8811e-06
2013-01-27 | 290580 | BBSRDL8 | RURAL | Weather | 1287.04 | 400.8146 | 1448019.4 | 4.1719 | 0.0037081
2013-01-27 | 290590 | AHD20 | URBAN | Equipment failure | 2.5 | 8028 | 20070 | 0.020266 | 2.5244e-06
2013-01-27 | 290609 | MTB1B | RURAL | Weather | 65.5 | 108 | 7074 | 0.020381 | 0.00018871
2013-01-27 | 290611 | CRB25A | RURAL | Weather | 22 | 206 | 4532 | 0.013057 | 6.3384e-05
2013-01-27 | 290612 | SPD12B | URBAN | Weather | 50.5 | 132 | 6666 | 0.0067311 | 5.0993e-05
2013-01-27 | 290624 | HPK3A | URBAN | Other | 68.5 | 97 | 6644.5 | 0.0067094 | 6.9169e-05
2013-01-27 | 290626 | MTG15A | URBAN | Equipment failure | 66.5 | 195 | 12967.5 | 0.013094 | 6.7149e-05
2013-01-27 | 290629 | MRK5A | URBAN | Other | 85.75 | 97 | 8317.75 | 0.0083989 | 8.6587e-05
2013-01-27 | 290632 | CBW6 | RURAL | Weather | 11.88 | 339 | 4027.32 | 0.011603 | 3.4227e-05
2013-01-27 | 290634 | SMF3A | RURAL | Other | 2.97 | 77 | 228.69 | 0.00065888 | 8.5568e-06
2013-01-27 | 290635 | HDA11A | URBAN | Other | 140.58 | 529 | 74366.82 | 0.075093 | 0.00014195
2013-01-27 | 290638 | LTA4B | URBAN | Weather | 43.56 | 1626 | 70828.56 | 0.07152 | 4.3985e-05
2013-01-27 | 290639 | MRK9 | URBAN | Equipment failure | 63.5 | 3720 | 236220 | 0.23853 | 6.412e-05
2013-01-27 | 290642 | WSE6A | RURAL | Weather | 19.5 | 1924 | 37518 | 0.10809 | 5.6181e-05
2013-01-27 | 290657 | TMH15A | URBAN | Equipment failure | 64 | 3963 | 253632 | 0.25611 | 6.4625e-05
2013-01-27 | 290663 | ALY9 | URBAN | Vegetation | 99.5 | 2608.5 | 372309.1 | 0.37594 | 0.00010047
2013-01-27 | 290677 | BRT8 | URBAN | Weather | 58.08 | 4166 | 241961.28 | 0.24432 | 5.8647e-05
2013-01-27 | 290696 | KLG13A | URBAN | Other | 55.77 | 3939 | 219678.03 | 0.22182 | 5.6314e-05
2013-01-27 | 290707 | UMG1B | URBAN | Equipment failure | 105 | 4983 | 523215 | 0.52832 | 0.00010602
2013-01-27 | 290717 | LTA2 | URBAN | Equipment failure | 58.08 | 3871 | 224827.68 | 0.22702 | 5.8647e-05
2013-01-27 | 290718 | BKD16A | URBAN | Weather | 87 | 239 | 20793 | 0.020996 | 8.7849e-05
2013-01-27 | 290719 | MTG4A | URBAN | Equipment failure | 1 | 3075 | 3075 | 0.003105 | 1.0098e-06
2013-01-27 | 290719 | MTG4B | URBAN | Equipment failure | 1228.47 | 3075 | 3777545.25 | 3.8144 | 0.0012405
2013-01-27 | 290720 | SMF3A | RURAL | Weather | 2.97 | 4582 | 13608.54 | 0.039207 | 8.5568e-06
2013-01-27 | 290722 | LGV6A | RURAL | Weather | 28 | 120 | 3360 | 0.0096805 | 8.0671e-05
2013-01-27 | 290724 | RPN6A | RURAL | Other | 2184.99 | 316 | 690456.84 | 1.9893 | 0.0062952
2013-01-27 | 290726 | CPB8 | RURAL | Weather | 13.5 | 51 | 688.5 | 0.0019836 | 3.8895e-05
2013-01-27 | 290729 | CVL7A | RURAL | Weather | 18.5 | 892 | 16502 | 0.047544 | 5.33e-05
2013-01-27 | 290732 | AGE10 | URBAN | Weather | 63.69 | 38 | 2420.22 | 0.0024438 | 6.4312e-05
2013-01-27 | 290733 | MLS26B | URBAN | Weather | 75.9 | 915 | 69448.5 | 0.070126 | 7.6641e-05
2013-01-27 | 290735 | BSEENG15 | URBAN | Weather | 190 | 422.9833 | 80366.8333 | 0.081151 | 0.00019185
2013-01-27 | 290740 | MBG2 | RURAL | Weather | 59.5 | 17 | 1011.5 | 0.0029142 | 0.00017142
2013-01-27 | 290741 | AHD8 | URBAN | Vegetation | 32.5578 | 92 | 2995.3176 | 0.0030246 | 3.2876e-05
2013-01-27 | 290754 | LTA3 | URBAN | Vegetation | 70.5 | 4059 | 286159.5 | 0.28895 | 7.1188e-05
2013-01-27 | 290781 | TRP4 | RURAL | Other | 33.83 | 225 | 7611.75 | 0.02193 | 9.7467e-05
2013-01-27 | 290783 | RPN8 | RURAL | Weather | 91.5 | 267 | 24430.5 | 0.070386 | 0.00026362
2013-01-27 | 290811 | TWT3A | RURAL | Weather | 11 | 4462 | 49082 | 0.14141 | 3.1692e-05
2013-01-27 | 290814 | SHW5A | URBAN | Other | 17.33 | 2892 | 50118.36 | 0.050608 | 1.7499e-05
2013-01-27 | 290818 | TWG19 | URBAN | Weather | 150.48 | 3307 | 497637.36 | 0.50249 | 0.00015195
2013-01-27 | 290821 | GYM8A | RURAL | Other | 18 | 1091 | 19638 | 0.056579 | 5.186e-05
2013-01-27 | 290827 | NBR9 | RURAL | Weather | 10 | 2069 | 20690 | 0.05961 | 2.8811e-05
2013-01-27 | 290828 | NBR2 | URBAN | Weather | 81.5 | 1138 | 92747 | 0.093652 | 8.2295e-05
2013-01-27 | 290829 | GAP4A | URBAN | Vegetation | 47.19 | 4227 | 199472.13 | 0.20142 | 4.7651e-05
2013-01-27 | 290830 | WMD2A | URBAN | Weather | 48 | 2874 | 137952 | 0.1393 | 4.8468e-05
2013-01-27 | 290835 | ENG2 | URBAN | Vegetation | 125.4 | 3915 | 490941 | 0.49573 | 0.00012662
2013-01-27 | 290837 | MGL2A | RURAL | Weather | 54 | 2119 | 222074.1 | 0.63982 | 0.00015558
2013-01-27 | 290838 | GBN4 | RURAL | Equipment failure | 6 | 2788 | 16728 | 0.048195 | 1.7287e-05
2013-01-27 | 290839 | CNA7A | RURAL | Weather | 46 | 4733 | 217718 | 0.62727 | 0.00013253
2013-01-27 | 290846 | SPO31A | URBAN | Weather | 12 | 1123 | 13476 | 0.013608 | 1.2117e-05
2013-01-27 | 290849 | ARL15B | URBAN | Weather | 76 | 1155 | 87780 | 0.088637 | 7.6742e-05
2013-01-27 | 290864 | AHD8 | URBAN | Other | 74 | 4302 | 318348 | 0.32146 | 7.4722e-05
2013-01-27 | 290867 | CLM3 | RURAL | Equipment failure | 9 | 4730 | 42570 | 0.12265 | 2.593e-05
2013-01-27 | 290884 | MTB15A | RURAL | Weather | 13 | 5859 | 76167 | 0.21944 | 3.7454e-05
2013-01-27 | 290930 | MTB13A | RURAL | Vegetation | 106 | 6293 | 667058 | 1.9219 | 0.0003054
2013-01-27 | 290934 | BMT1 | RURAL | Weather | 17 | 5966 | 101422 | 0.29221 | 4.8979e-05
2013-01-27 | 290970 | WFD1B | RURAL | Weather | 344.97 | 2997.7786 | 1092719.99 | 3.1482 | 0.00099389
2013-01-27 | 291246 | AGE4B | URBAN | Weather | 27.885 | 27 | 752.895 | 0.00076024 | 2.8157e-05
2013-01-27 | 291247 | KMR17B | URBAN | Weather | 8.06 | 147 | 1184.82 | 0.0011964 | 8.1387e-06
2013-01-27 | 291248 | NGE4B | URBAN | Other | 13.8 | 5730 | 79074 | 0.079846 | 1.3935e-05
2013-01-27 | 291250 | AGE10 | URBAN | Weather | 4.895 | 4165 | 20387.675 | 0.020587 | 4.9428e-06
2013-01-27 | 291251 | TWG18 | URBAN | Weather | 84 | 145 | 12180 | 0.012299 | 8.482e-05
2013-01-27 | 291252 | NDH9 | URBAN | Weather | 153 | 366 | 55998 | 0.056545 | 0.00015449
2013-01-27 | 291253 | WNM3 | URBAN | Other | 22.9 | 5843 | 133804.7 | 0.13511 | 2.3124e-05
2013-01-27 | 291257 | IBL2 | RURAL | Weather | 15 | 4721 | 70815 | 0.20402 | 4.3216e-05
2013-01-27 | 291258 | SGT4 | URBAN | Weather | 55 | 282 | 15510 | 0.015661 | 5.5537e-05
2013-01-27 | 291273 | BRD8A | RURAL | Weather | 32 | 1529 | 48928 | 0.14097 | 9.2195e-05
2013-01-27 | 291276 | DBY6 | URBAN | Weather | 83.5 | 70 | 5845 | 0.005902 | 8.4315e-05
2013-01-27 | 291279 | HTN7A | URBAN | Weather | 42.8 | 6628 | 283678.4 | 0.28645 | 4.3218e-05
2013-01-27 | 291285 | WNM5 | URBAN | Weather | 8.04 | 4320 | 34732.8 | 0.035072 | 8.1185e-06
2013-01-27 | 291287 | GYM9B | RURAL | Weather | 159 | 3255 | 517545 | 1.4911 | 0.00045809
2013-01-27 | 291365 | GBN4 | RURAL | Weather | 198 | 3258 | 645084 | 1.8585 | 0.00057046
2013-01-27 | 291401 | KWH1 | RURAL | Weather | 367 | 5864.2857 | 2213707 | 6.3779 | 0.0010574
2013-01-27 | 291410 | HDA4A | URBAN | Weather | 94 | 1169 | 109886 | 0.11096 | 9.4917e-05
2013-01-27 | 291455 | LGV3A | RURAL | Weather | 219.5 | 4522.9474 | 975735.5 | 2.8112 | 0.0006324
2013-01-27 | 291461 | CPR5 | URBAN | Weather | 135 | 62 | 8370 | 0.0084517 | 0.00013632
2013-01-27 | 291465 | CPR7 | URBAN | Weather | 106 | 5605 | 594130 | 0.59993 | 0.00010703
2013-01-27 | 291510 | MHPWED5 | URBAN | Weather | 17 | 807 | 13719 | 0.013853 | 1.7166e-05
2013-01-27 | 291533 | MTG13A | URBAN | Weather | 14.1 | 25 | 352.5 | 0.00035594 | 1.4238e-05
2013-01-27 | 291545 | MRK5A | URBAN | Weather | 93 | 5592 | 520056 | 0.52513 | 9.3908e-05
2013-01-27 | 291609 | ARG5A | URBAN | Weather | 8.9 | 7396 | 65824.4 | 0.066467 | 8.9869e-06
2013-01-27 | 291617 | GYM3 | URBAN | Weather | 4.5 | 12060 | 54270 | 0.0548 | 4.5439e-06
2013-01-27 | 291633 | GYM8A | RURAL | Weather | 5 | 12210 | 61050 | 0.17589 | 1.4405e-05
2013-01-27 | 291752 | PWC5 | RURAL | Weather | 17.5 | 3906 | 68355 | 0.19694 | 5.0419e-05
2013-01-27 | 291832 | KMR21A | URBAN | Weather | 1047.99 | 1212.3889 | 1269725.29 | 1.2821 | 0.0010582
2013-01-27 | 291832 | KMR21B | URBAN | Weather | 41.68 | 1166 | 48598.88 | 0.049073 | 4.2087e-05
2013-01-27 | 291850 | UMG1B | URBAN | Equipment failure | 7.8 | 5080 | 39624 | 0.040011 | 7.8761e-06
2013-01-27 | 291921 | MTB3A | RURAL | Weather | 58.5 | 937 | 54814.5 | 0.15793 | 0.00016854
2013-01-27 | 292015 | LGV6A | RURAL | Equipment failure | 767.5 | 4568.2679 | 3400142.5 | 9.7961 | 0.0022112
2013-01-27 | 292018 | TWG15A | URBAN | Equipment failure | 630.75 | 1486 | 937294.5 | 0.94644 | 0.00063691
2013-01-27 | 292351 | MBG4 | RURAL | Weather | 199.5 | 3944.717 | 786872 | 2.267 | 0.00057478
2013-01-27 | 292372 | MGP13A | RURAL | Weather | 584 | 1754.8856 | 2552509 | 7.354 | 0.0016826
2013-01-27 | 292430 | BWH12A | RURAL | Weather | 249.17 | 4694.7778 | 1165334.56 | 3.3574 | 0.00071788
2013-01-27 | 292456 | SHW4 | URBAN | Weather | 490.33 | 1355 | 664397.15 | 0.67088 | 0.00049512
2013-01-27 | 292457 | FDS1 | RURAL | Other | 20.5 | 3164 | 64862 | 0.18687 | 5.9062e-05
2013-01-27 | 292532 | OXL10A | URBAN | Weather | 120.99 | 82 | 9921.18 | 0.010018 | 0.00012217
2013-01-27 | 292570 | BMT4 | RURAL | Weather | 700.82 | 974 | 435533.52 | 1.2548 | 0.0020191
2013-01-27 | 292590 | BMT5 | RURAL | Equipment failure | 328.5 | 852.5616 | 901537 | 2.5974 | 0.00094644
2013-01-27 | 292632 | EMP4A | URBAN | Weather | 1391.49 | 760 | 1057532.4 | 1.0679 | 0.0014051
2013-01-27 | 292651 | RCN2A | URBAN | Weather | 1629.33 | 561 | 914054.13 | 0.92298 | 0.0016452
2013-01-27 | 293531 | NDH9 | URBAN | Weather | 1400.99 | 1124 | 1574712.76 | 1.5901 | 0.0014147
2013-01-27 | 293573 | 334 | URBAN | Weather | 1.33 | 156 | 207.48 | 0.00020951 | 1.343e-06
2013-01-27 | 293574 | FGBSGT23 | URBAN | Weather | 1968 | 39 | 76752 | 0.077501 | 0.0019872
2013-01-27 | 293575 | BNH1B | RURAL | Other | 682.98 | 1441 | 984174.18 | 2.8355 | 0.0019677
2013-01-27 | 293611 | BMT1 | RURAL | Weather | 53.6 | 4732 | 253635.2 | 0.73075 | 0.00015443
2013-01-27 | 293630 | UPC1 | RURAL | Weather | 68 | 4369 | 297092 | 0.85595 | 0.00019591
2013-01-27 | 293955 | HPK3A | URBAN | Weather | 2542.99 | 410 | 1042625.9 | 1.0528 | 0.0025678
2013-01-27 | 293971 | GAP4A | URBAN | Weather | 912.5 | 1240 | 1131500 | 1.1425 | 0.00092141
2013-01-27 | 293972 | MMC19A | URBAN | Weather | 1 | 2427 | 2427 | 0.0024507 | 1.0098e-06
2013-01-27 | 293972 | MMC19B | URBAN | Weather | 1095.49 | 2427 | 2658754.23 | 2.6847 | 0.0011062
2013-01-27 | 293973 | NRG16A | RURAL | Weather | 359.5 | 2468 | 887246 | 2.5562 | 0.0010358
2013-01-27 | 293992 | KBN1B | RURAL | Weather | 1377 | 4590 | 6320430 | 18.2097 | 0.0039673
2013-01-27 | 294190 | LBH1B | RURAL | Other | 986.5 | 2 | 1973 | 0.0056844 | 0.0028422
2013-01-27 | 294353 | MLS2A | URBAN | Weather | 225.7 | 168 | 37917.6 | 0.038288 | 0.0002279
2013-01-27 | 294371 | MGL8 | URBAN | Weather | 370.5 | 2737 | 1014058.5 | 1.024 | 0.00037412
2013-01-27 | 294450 | NMC1B | RURAL | Weather | 1314.5 | 2680.7083 | 3529854.09 | 10.1698 | 0.0037872
2013-01-27 | 294634 | LBH3A | RURAL | Weather | 782.33 | 4840 | 3786477.2 | 10.9092 | 0.002254
2013-01-27 | 294635 | BWH7A | RURAL | Weather | 95 | 3181 | 302195 | 0.87065 | 0.0002737
2013-01-27 | 294653 | CBW11 | RURAL | Equipment failure | 1757.49 | 11 | 19332.39 | 0.055698 | 0.0050635
2013-01-27 | 294653 | CBW12 | URBAN | Equipment failure | 922.92 | 11 | 10152.12 | 0.010251 | 0.00093193
2013-01-27 | 294653 | CBW13 | RURAL | Equipment failure | 317 | 11 | 3487 | 0.010046 | 0.00091331
2013-01-27 | 294653 | CBW14 | URBAN | Equipment failure | 556.17 | 11 | 6117.87 | 0.0061776 | 0.0005616
2013-01-27 | 294653 | CBW4 | URBAN | Equipment failure | 88.5 | 11 | 973.5 | 0.000983 | 8.9364e-05
2013-01-27 | 294653 | CBW5 | URBAN | Equipment failure | 755.75 | 11 | 8313.25 | 0.0083944 | 0.00076313
2013-01-27 | 294653 | CBW6 | RURAL | Equipment failure | 2140.5 | 11 | 23545.5 | 0.067837 | 0.006167
2013-01-27 | 294653 | CBW7 | RURAL | Equipment failure | 1352.5 | 11 | 14877.5 | 0.042863 | 0.0038967
2013-01-27 | 294653 | CBW8 | URBAN | Equipment failure | 147 | 11 | 1617 | 0.0016328 | 0.00014843
2013-01-27 | 294653 | CBW9 | URBAN | Equipment failure | 421 | 11 | 4631 | 0.0046762 | 0.00042511
2013-01-27 | 294656 | 448 | URBAN | Weather | 1 | 1346 | 1346 | 0.0013591 | 1.0098e-06
2013-01-27 | 294658 | CLR3 | RURAL | Weather | 179.67 | 170 | 30543.9 | 0.088 | 0.00051765
2013-01-27 | 294683 | STT1B | RURAL | Weather | 92.5 | 496 | 45880 | 0.13218 | 0.0002665
2013-01-27 | 294684 | MGL8 | URBAN | Weather | 370.5 | 2738 | 1014429 | 1.0243 | 0.00037412
2013-01-27 | 294685 | DRA8 | URBAN | Weather | 211 | 1448 | 305528 | 0.30851 | 0.00021306
2013-01-27 | 295050 | CVL7A | RURAL | Weather | 354 | 475 | 168150 | 0.48446 | 0.0010199
2013-01-27 | 295130 | LLY1 | RURAL | Weather | 208.99 | 4033 | 842856.67 | 2.4283 | 0.00060212
2013-01-27 | 295211 | BWH16A | RURAL | Weather | 41.66 | 1141 | 47534.06 | 0.13695 | 0.00012003
2013-01-27 | 295231 | NRA5A | RURAL | Weather | 1570 | 1236 | 1940520 | 5.5908 | 0.0045233
2013-01-27 | 295251 | SMF3A | RURAL | Equipment failure | 179 | 720 | 128880 | 0.37131 | 0.00051572
2013-01-27 | 295290 | BWH12A | RURAL | Equipment failure | 57 | 1645 | 93765 | 0.27015 | 0.00016422
2013-01-27 | 295291 | GBN4 | RURAL | Weather | 301.5 | 1081 | 325921.5 | 0.93901 | 0.00086865
2013-01-27 | 295310 | GBN4 | RURAL | Equipment failure | 66.5 | 1079 | 71753.5 | 0.20673 | 0.00019159
2013-01-27 | 295311 | PWC2 | RURAL | Weather | 1017.98 | 877 | 892768.46 | 2.5721 | 0.0029329
2013-01-27 | 295312 | BHD3A | URBAN | Equipment failure | 1179 | 913 | 1076427 | 1.0869 | 0.0011905
2013-01-27 | 295318 | BMT3 | RURAL | Weather | 943.99 | 1335 | 1260226.65 | 3.6308 | 0.0027197
2013-01-27 | 295344 | BWH12A | RURAL | Equipment failure | 109.11 | 1628 | 177631.08 | 0.51177 | 0.00031436
2013-01-27 | 295450 | TCB3 | RURAL | Equipment failure | 1360 | 134 | 182240 | 0.52505 | 0.0039183
2013-01-27 | 295530 | IBL2 | RURAL | Weather | 735.51 | 3247.2517 | 2421347.38 | 6.9761 | 0.0021191
2013-01-27 | 295531 | JBB1B | RURAL | Weather | 261.5 | 396 | 103554 | 0.29835 | 0.00075341
2013-01-27 | 295591 | WSO12A | URBAN | Weather | 1 | 4419 | 4419 | 0.0044621 | 1.0098e-06
2013-01-27 | 295591 | WSO12B | RURAL | Weather | 854.5 | 4454.3333 | 3783270 | 10.8999 | 0.0024619
2013-01-27 | 296575 | TBV3 | RURAL | Other | 14.07 | 125 | 1758.75 | 0.0050671 | 4.0537e-05
2013-01-28 | 289114 | 390 | URBAN | Weather | 1 | 60 | 60 | 6.0592e-05 | 1.0099e-06
2013-01-28 | 289114 | BDL1 | URBAN | Weather | 100.5 | 60 | 6030 | 0.0060895 | 0.00010149
2013-01-28 | 289114 | BDL2 | URBAN | Weather | 1404.33 | 60 | 84259.8 | 0.085092 | 0.0014182
2013-01-28 | 289114 | BDL3 | URBAN | Weather | 250.5 | 60 | 15030 | 0.015178 | 0.00025297
2013-01-28 | 289114 | BDL4 | URBAN | Weather | 1719.81 | 60 | 103188.6 | 0.10421 | 0.0017368
2013-01-28 | 289114 | BDL5 | URBAN | Weather | 424.66 | 60 | 25479.6 | 0.025731 | 0.00042885
2013-01-28 | 289114 | BDL6 | URBAN | Weather | 251.5 | 60 | 15090 | 0.015239 | 0.00025398
2013-01-28 | 289114 | BDL7 | URBAN | Weather | 264.33 | 60 | 15859.8 | 0.016016 | 0.00026694
2013-01-28 | 289141 | AHD10A | URBAN | Equipment failure | 1592.32 | 35 | 55731.2 | 0.056281 | 0.001608
2013-01-28 | 289141 | AHD10B | URBAN | Equipment failure | 1077.32 | 75.7143 | 108468.26 | 0.10954 | 0.001088
2013-01-28 | 289141 | AHD9 | URBAN | Equipment failure | 309.17 | 35 | 10820.95 | 0.010928 | 0.00031222
2013-01-28 | 289144 | 334 | URBAN | Weather | 1.33 | 400 | 532 | 0.00053725 | 1.3431e-06
2013-01-28 | 289144 | NPD1 | URBAN | Weather | 7 | 466 | 3262 | 0.0032942 | 7.0691e-06
2013-01-28 | 289144 | WSE1B | URBAN | Weather | 5.66 | 422 | 2388.52 | 0.0024121 | 5.7159e-06
2013-01-28 | 289144 | WSE2A | URBAN | Weather | 1 | 422 | 422 | 0.00042617 | 1.0099e-06
2013-01-28 | 289144 | WSE3A | RURAL | Weather | 1135.25 | 422 | 479075.5 | 1.3796 | 0.0032693
2013-01-28 | 289144 | WSE5A | RURAL | Weather | 694.75 | 422 | 293184.5 | 0.84431 | 0.0020007
2013-01-28 | 289144 | WSE6A | RURAL | Weather | 417.38 | 422 | 176134.36 | 0.50723 | 0.001202
2013-01-28 | 289145 | CBW11 | RURAL | Weather | 474.99 | 629 | 298768.71 | 0.86039 | 0.0013679
2013-01-28 | 289145 | CBW7 | RURAL | Weather | 76.5 | 629 | 48118.5 | 0.13857 | 0.0002203
2013-01-28 | 289149 | CVL17A | URBAN | Equipment failure | 2331.34 | 107.6667 | 250663.2 | 0.25314 | 0.0023544
2013-01-28 | 289152 | 335 | URBAN | Weather | 1 | 2177 | 2177 | 0.0021985 | 1.0099e-06
2013-01-28 | 289153 | BDT3 | RURAL | Weather | 178 | 334 | 59452 | 0.17121 | 0.0005126
2013-01-28 | 289154 | AHD21 | URBAN | Other | 1288 | 65 | 83720 | 0.084547 | 0.0013007
2013-01-28 | 289158 | BPN29A | URBAN | Weather | 1388.01 | 755.3333 | 1032462.02 | 1.0427 | 0.0014017
2013-01-28 | 289159 | MFD12A | URBAN | Weather | 1427.17 | 752 | 1073231.84 | 1.0838 | 0.0014413
2013-01-28 | 289166 | WMD6A | URBAN | Weather | 1057 | 1058 | 1118306 | 1.1293 | 0.0010674
2013-01-28 | 289168 | ARG5A | URBAN | Weather | 1554.64 | 225.8148 | 358538.88 | 0.36208 | 0.00157
2013-01-28 | 289170 | WSE6A | RURAL | Equipment failure | 36 | 4451 | 160236 | 0.46144 | 0.00010367
2013-01-28 | 289174 | WMD8B | RURAL | Weather | 391.75 | 237 | 92844.75 | 0.26737 | 0.0011282
2013-01-28 | 289176 | BGY15A | URBAN | Weather | 1458.5 | 754 | 1099709 | 1.1106 | 0.0014729
2013-01-28 | 289182 | BRD11A | RURAL | Equipment failure | 564 | 405 | 228420 | 0.6578 | 0.0016242
2013-01-28 | 289183 | BRD5A | RURAL | Equipment failure | 1684.49 | 830.6552 | 1556287.39 | 4.4818 | 0.004851
2013-01-28 | 289185 | RPN2A | URBAN | Weather | 1320.49 | 466 | 615348.34 | 0.62142 | 0.0013335
2013-01-28 | 289187 | CLD25A | URBAN | Equipment failure | 306.33 | 88 | 26957.04 | 0.027223 | 0.00030935
2013-01-28 | 289189 | FDS1 | RURAL | Weather | 762.53 | 5 | 3812.65 | 0.01098 | 0.0021959
2013-01-28 | 289189 | FDS3 | RURAL | Weather | 567.9 | 5 | 2839.5 | 0.0081771 | 0.0016354
2013-01-28 | 289189 | FDS4 | RURAL | Weather | 418.34 | 5 | 2091.7 | 0.0060236 | 0.0012047
2013-01-28 | 289191 | BVL5A | URBAN | Weather | 1838 | 816 | 1499808 | 1.5146 | 0.0018561
2013-01-28 | 289192 | MLB12A | RURAL | Weather | 1595 | 960 | 3042039 | 8.7604 | 0.0045932
2013-01-28 | 289193 | IPS2A | URBAN | Weather | 1 | 783 | 783 | 0.00079073 | 1.0099e-06
2013-01-28 | 289193 | IPS2B | RURAL | Weather | 1274.84 | 842.3265 | 1024175.72 | 2.9494 | 0.0036713
2013-01-28 | 289194 | MAI17 | URBAN | Weather | 1766.51 | 995 | 1757677.45 | 1.775 | 0.001784
2013-01-28 | 289195 | MAI13 | URBAN | Weather | 1776.6 | 1227 | 2179888.2 | 2.2014 | 0.0017941
2013-01-28 | 289196 | SHW12 | URBAN | Weather | 597.99 | 1088 | 650613.12 | 0.65704 | 0.00060389
2013-01-28 | 289197 | LTA4B | URBAN | Weather | 1911.99 | 299 | 571685.01 | 0.57733 | 0.0019309
2013-01-28 | 289198 | KCY1 | URBAN | Weather | 612 | 205 | 125460 | 0.1267 | 0.00061804
2013-01-28 | 289198 | KCY2 | RURAL | Weather | 358.26 | 205 | 73443.3 | 0.2115 | 0.0010317
2013-01-28 | 289198 | KCY3 | URBAN | Weather | 5.65 | 205 | 1158.25 | 0.0011697 | 5.7058e-06
2013-01-28 | 289198 | KCY4 | RURAL | Weather | 698.12 | 205 | 143114.6 | 0.41214 | 0.0020104
2013-01-28 | 289198 | KCY5 | RURAL | Weather | 524 | 205 | 107420 | 0.30935 | 0.001509
2013-01-28 | 289200 | WSE3A | RURAL | Weather | 1135.25 | 1637.9372 | 1672955.46 | 4.8177 | 0.0032693
2013-01-28 | 289201 | BHD41A | URBAN | Weather | 1700.33 | 781.5263 | 1139423.15 | 1.1507 | 0.0017171
2013-01-28 | 289202 | BDL4 | URBAN | Weather | 1720.81 | 551 | 948166.31 | 0.95753 | 0.0017378
2013-01-28 | 289203 | SPO67B | URBAN | Weather | 1480.33 | 444 | 657266.52 | 0.66376 | 0.0014949
2013-01-28 | 289205 | OXL8A | URBAN | Weather | 82.5 | 1185 | 97762.5 | 0.098728 | 8.3315e-05
2013-01-28 | 289205 | OXL8B | URBAN | Weather | 1635.5 | 1711.6875 | 2899461.07 | 2.9281 | 0.0016516
2013-01-28 | 289206 | DBY5 | URBAN | Weather | 296 | 872 | 258112 | 0.26066 | 0.00029892
2013-01-28 | 289207 | SMR9A | URBAN | Weather | 1061.5 | 1042 | 1106083 | 1.117 | 0.001072
2013-01-28 | 289207 | SMR9B | URBAN | Weather | 1 | 1042 | 1042 | 0.0010523 | 1.0099e-06
2013-01-28 | 289213 | CLM5 | URBAN | Equipment failure | 180.5 | 44 | 7942 | 0.0080204 | 0.00018228
2013-01-28 | 289216 | RLB13B | RURAL | Weather | 1911.47 | 331.7692 | 627040.45 | 1.8057 | 0.0055046
2013-01-28 | 289217 | FGBSGT23 | URBAN | Weather | 1968 | 1319 | 2595792 | 2.6214 | 0.0019874
2013-01-28 | 289222 | BKD5B | RURAL | Weather | 1777.67 | 730.1034 | 1299298.08 | 3.7417 | 0.0051193
2013-01-28 | 289223 | IDY10A | URBAN | Weather | 584 | 697.7273 | 448313 | 0.45274 | 0.00058977
2013-01-28 | 289226 | KWA12A | URBAN | Equipment failure | 2377 | 1038.7241 | 2446941.5 | 2.4711 | 0.0024005
2013-01-28 | 289229 | MFD3A | RURAL | Other | 945 | 841 | 794745 | 2.2887 | 0.0027214
2013-01-28 | 289230 | NRA1A | RURAL | Weather | 895 | 1080 | 966600 | 2.7836 | 0.0025774
2013-01-28 | 289232 | CMV14 | URBAN | Weather | 1186.5 | 1417 | 1681270.5 | 1.6979 | 0.0011982
2013-01-28 | 289233 | WCL19A | RURAL | Weather | 930.34 | 1047.6098 | 1009702.5 | 2.9077 | 0.0026792
2013-01-28 | 289234 | KLG13A | URBAN | Weather | 1532.49 | 1879.76 | 2878517.2 | 2.9069 | 0.0015476
2013-01-28 | 289253 | PBH4 | URBAN | Weather | 1029.49 | 1255 | 1292009.95 | 1.3048 | 0.0010397
2013-01-28 | 289256 | CHL10 | URBAN | Weather | 1011.99 | 459 | 464503.41 | 0.46909 | 0.001022
2013-01-28 | 289270 | WRD21A | URBAN | Weather | 809 | 585 | 473265 | 0.47794 | 0.00081699
2013-01-28 | 289271 | PBH6 | URBAN | Weather | 2226.34 | 1361 | 3030048.74 | 3.06 | 0.0022483
2013-01-28 | 289290 | MRK6 | URBAN | Equipment failure | 1742.75 | 2288.6875 | 3976034.75 | 4.0153 | 0.00176
2013-01-28 | 289331 | MRK3 | URBAN | Weather | 1204 | 1739 | 2093756 | 2.1144 | 0.0012159
2013-01-28 | 289350 | MFD2A | URBAN | Other | 788.98 | 1744 | 1375981.12 | 1.3896 | 0.00079677
2013-01-28 | 289351 | BPN26A | RURAL | Weather | 875 | 1620 | 1417500 | 4.0821 | 0.0025198
2013-01-28 | 289370 | MCW4 | RURAL | Weather | 1286.5 | 1503 | 1933609.5 | 5.5684 | 0.0037048
2013-01-28 | 289371 | NMK26 | URBAN | Weather | 750 | 2086.4286 | 1554329.5 | 1.5697 | 0.0007574
2013-01-28 | 289372 | GTN12A | RURAL | Other | 198.5 | 1794 | 356109 | 1.0255 | 0.00057164
2013-01-28 | 289373 | CRBTHP14 | URBAN | Weather | 122 | 2153 | 262666 | 0.26526 | 0.0001232
2013-01-28 | 289393 | 11THPT2 | URBAN | Weather | 0.25 | 1187 | 296.75 | 0.00029968 | 2.5247e-07
2013-01-28 | 289393 | CRBTHP26 | URBAN | Weather | 1110 | 1206.2727 | 1342373.5 | 1.3556 | 0.001121
2013-01-28 | 289393 | THP2 | URBAN | Weather | 1.5 | 1187 | 1780.5 | 0.0017981 | 1.5148e-06
2013-01-28 | 289394 | WCL13A | URBAN | Other | 97.67 | 1616 | 157834.72 | 0.15939 | 9.8634e-05
2013-01-28 | 289450 | CRM13A | URBAN | Weather | 1792 | 1526 | 2734592 | 2.7616 | 0.0018097
2013-01-28 | 289450 | CRM13B | URBAN | Weather | 24.5 | 1526 | 37387 | 0.037756 | 2.4742e-05
2013-01-28 | 289451 | WRG5A | URBAN | Weather | 710.51 | 2063.9333 | 1457664.38 | 1.4721 | 0.00071753
2013-01-28 | 289458 | NRA1A | RURAL | Other | 97.5 | 1909 | 186127.5 | 0.53601 | 0.00028078
2013-01-28 | 289459 | INA9A | URBAN | Weather | 1277 | 1988.2 | 2541737 | 2.5668 | 0.0012896
2013-01-28 | 289461 | JBB1B | RURAL | Weather | 17 | 836 | 14212 | 0.040927 | 4.8956e-05
2013-01-28 | 289465 | CNA8A | RURAL | Weather | 118 | 362 | 42716 | 0.12301 | 0.00033981
2013-01-28 | 289467 | BLN6A | URBAN | Weather | 363 | 1630 | 591690 | 0.59753 | 0.00036658
2013-01-28 | 289467 | BTA5A | RURAL | Weather | 55.5 | 15 | 832.5 | 0.0023974 | 0.00015983
2013-01-28 | 289469 | KSN6 | URBAN | Weather | 751.49 | 789 | 592925.61 | 0.59878 | 0.00075891
2013-01-28 | 289470 | NMC15A | RURAL | Weather | 278.66 | 1727 | 481245.82 | 1.3859 | 0.00080248
2013-01-28 | 289471 | TRP2 | RURAL | Weather | 103.84 | 1416 | 147037.44 | 0.42343 | 0.00029904
2013-01-28 | 289475 | JBB2A | RURAL | Weather | 793.99 | 3431.1806 | 2721500.15 | 7.8373 | 0.0022865
2013-01-28 | 289478 | CPR6 | URBAN | Weather | 1322 | 2076.6 | 2707447.5 | 2.7342 | 0.0013351
2013-01-28 | 289481 | PBH8 | URBAN | Weather | 1467.49 | 1419 | 2082368.31 | 2.1029 | 0.001482
2013-01-28 | 289483 | KMR22A | URBAN | Weather | 844.16 | 2149 | 1814099.84 | 1.832 | 0.00085249
2013-01-28 | 289483 | KMR22B | URBAN | Weather | 1 | 2149 | 2149 | 0.0021702 | 1.0099e-06
2013-01-28 | 289484 | NRG8B | URBAN | Equipment failure | 268.5 | 2523 | 677425.5 | 0.68411 | 0.00027115
2013-01-28 | 289485 | RWD1 | RURAL | Weather | 177.99 | 2071.3947 | 370100.49 | 1.0658 | 0.00051257
2013-01-28 | 289488 | MDH3A | URBAN | Weather | 89.17 | 2533.9231 | 225935.14 | 0.22817 | 9.005e-05
2013-01-28 | 289489 | HWL11A | URBAN | Weather | 1187 | 2298 | 2727726 | 2.7547 | 0.0011987
2013-01-28 | 289491 | TWG21 | URBAN | Equipment failure | 941.5 | 1793 | 1688109.5 | 1.7048 | 0.0009508
2013-01-28 | 289496 | MLB8A | RURAL | Weather | 167.25 | 2776 | 464286 | 1.337 | 0.00048164
2013-01-28 | 289499 | GYM2B | URBAN | Weather | 32.5 | 2734 | 88855 | 0.089732 | 3.2821e-05
2013-01-28 | 289502 | CPL23A | RURAL | Weather | 924.99 | 2782 | 2573322.18 | 7.4106 | 0.0026638
2013-01-28 | 289504 | MLY6 | RURAL | Weather | 613.49 | 369.7692 | 224039.55 | 0.64518 | 0.0017667
2013-01-28 | 289506 | KMR27A | URBAN | Weather | 938.33 | 2934 | 2753060.22 | 2.7802 | 0.00094759
2013-01-28 | 289507 | CNB26A | RURAL | Weather | 464.49 | 2950 | 1370245.5 | 3.946 | 0.0013376
2013-01-28 | 289509 | MGP16A | URBAN | Weather | 616.5 | 2596.25 | 1593485 | 1.6092 | 0.00062259
2013-01-28 | 289513 | 1129 | URBAN | Weather | 341 | 2698 | 920018 | 0.9291 | 0.00034437
2013-01-28 | 289515 | CMV8 | URBAN | Equipment failure | 952.26 | 2419.3 | 2303800.96 | 2.3265 | 0.00096166
2013-01-28 | 289530 | CBT12A | RURAL | Weather | 807.71 | 2100 | 1696191 | 4.8847 | 0.002326
2013-01-28 | 289531 | BIS15A | URBAN | Weather | 1070.66 | 2038 | 2182005.08 | 2.2035 | 0.0010812
2013-01-28 | 289550 | LLY3 | RURAL | Equipment failure | 133 | 1708 | 227164 | 0.65418 | 0.00038301
2013-01-28 | 289570 | BKD5B | RURAL | Weather | 1776.67 | 1114 | 1979210.38 | 5.6997 | 0.0051164
2013-01-28 | 289590 | ACR5 | RURAL | Weather | 178 | 1143 | 203454 | 0.5859 | 0.0005126
2013-01-28 | 289611 | RCN10A | URBAN | Weather | 1503.27 | 1484 | 2230852.68 | 2.2529 | 0.0015181
2013-01-28 | 289630 | BWH7A | RURAL | Weather | 364.67 | 2187.1471 | 788992.81 | 2.2721 | 0.0010502
2013-01-28 | 289631 | SHW5A | URBAN | Weather | 886.66 | 1490.6842 | 1328501.1 | 1.3416 | 0.00089541
2013-01-28 | 289650 | CMV11A | URBAN | Weather | 301.5 | 2466 | 743499 | 0.75084 | 0.00030448
2013-01-28 | 289755 | JBB3A | RURAL | Weather | 934.5 | 3071.4059 | 3426747 | 9.8683 | 0.0026912
2013-01-28 | 289774 | CVL5A | RURAL | Weather | 1083.33 | 1319 | 1428912.27 | 4.1149 | 0.0031197
2013-01-28 | 289775 | 393 | URBAN | Equipment failure | 1 | 166 | 166 | 0.00016764 | 1.0099e-06
2013-01-28 | 289775 | PBH1 | URBAN | Equipment failure | 1414 | 166 | 234724 | 0.23704 | 0.001428
2013-01-28 | 289775 | PBH2B | URBAN | Equipment failure | 2293.5 | 166 | 380721 | 0.38448 | 0.0023161
2013-01-28 | 289775 | PBH3 | URBAN | Equipment failure | 1115.17 | 166 | 185118.22 | 0.18695 | 0.0011262
2013-01-28 | 289775 | PBH4 | URBAN | Equipment failure | 1029.49 | 166 | 170895.34 | 0.17258 | 0.0010397
2013-01-28 | 289775 | PBH5 | RURAL | Equipment failure | 1 | 166 | 166 | 0.00047804 | 2.8798e-06
2013-01-28 | 289775 | PBH6 | URBAN | Equipment failure | 2226.34 | 166 | 369572.44 | 0.37322 | 0.0022483
2013-01-28 | 289775 | PBH7 | URBAN | Equipment failure | 45.5 | 166 | 7553 | 0.0076276 | 4.5949e-05
2013-01-28 | 289775 | PBH8 | URBAN | Equipment failure | 1467.49 | 166 | 243603.34 | 0.24601 | 0.001482
2013-01-28 | 289776 | WMR1 | RURAL | Equipment failure | 700.5 | 4 | 2802 | 0.0080691 | 0.0020173
2013-01-28 | 289776 | WMR2 | RURAL | Equipment failure | 226.01 | 4 | 904.04 | 0.0026034 | 0.00065086
2013-01-28 | 289776 | WMR3 | RURAL | Equipment failure | 355.33 | 4 | 1421.32 | 0.0040931 | 0.0010233
2013-01-28 | 289776 | WMR4 | RURAL | Equipment failure | 48 | 4 | 192 | 0.00055292 | 0.00013823
2013-01-28 | 289803 | CPB6 | URBAN | Equipment failure | 86 | 1216.625 | 119899.52 | 0.12108 | 8.6849e-05
2013-01-28 | 289810 | KMR17B | URBAN | Weather | 471 | 3296 | 1529027 | 1.5441 | 0.00047565
2013-01-28 | 289814 | BLH12A | RURAL | Weather | 6 | 4063 | 24378 | 0.070203 | 1.7279e-05
2013-01-28 | 289820 | HPK3A | URBAN | Weather | 2542.99 | 1577.1875 | 3938551.05 | 3.9774 | 0.0025681
2013-01-28 | 289823 | MGP15A | RURAL | Weather | 942.49 | 436.3611 | 400785.78 | 1.1542 | 0.0027142
2013-01-28 | 289825 | TGP8A | URBAN | Weather | 828.5 | 37 | 30654.5 | 0.030957 | 0.00083668
2013-01-28 | 289890 | WED3A | URBAN | Weather | 614.33 | 1740.9375 | 1064058.45 | 1.0746 | 0.0006204
2013-01-28 | 289891 | CPB4 | URBAN | Weather | 2445.15 | 419 | 1024517.85 | 1.0346 | 0.0024693
2013-01-28 | 289911 | CPB3 | URBAN | Weather | 1195.82 | 598 | 715100.36 | 0.72216 | 0.0012076
2013-01-28 | 289914 | KMR25A | RURAL | Weather | 409 | 2355 | 963195 | 2.7738 | 0.0011778
2013-01-28 | 289970 | CPL2A | URBAN | Weather | 297.17 | 3094 | 919443.98 | 0.92852 | 0.0003001
2013-01-28 | 290031 | CRB25A | RURAL | Weather | 273.16 | 2577.7065 | 1190936.66 | 3.4296 | 0.00078664
2013-01-28 | 290166 | KSN7 | RURAL | Weather | 1292.5 | 2632.8909 | 3427934.5 | 9.8717 | 0.0037221
2013-01-28 | 290167 | LTA5 | URBAN | Weather | 1980.83 | 226 | 447667.58 | 0.45209 | 0.0020004
2013-01-28 | 290167 | RBY3 | URBAN | Weather | 1568.5 | 532 | 834442 | 0.84268 | 0.001584
2013-01-28 | 290167 | WNM2A | URBAN | Weather | 1977.82 | 380 | 751571.6 | 0.75899 | 0.0019973
2013-01-28 | 290167 | WNM3 | URBAN | Weather | 1256 | 37 | 46472 | 0.046931 | 0.0012684
2013-01-28 | 290167 | WNM4 | URBAN | Weather | 1343.5 | 327 | 439324.5 | 0.44366 | 0.0013568
2013-01-28 | 290167 | WNM7A | URBAN | Weather | 1181.16 | 251 | 296471.16 | 0.2994 | 0.0011928
2013-01-28 | 290192 | NBR9 | RURAL | Weather | 2078 | 643.3011 | 1286350 | 3.7044 | 0.0059842
2013-01-28 | 290512 | KMR17A | URBAN | Weather | 580.5 | 813 | 471946.5 | 0.47661 | 0.00058623
2013-01-28 | 290572 | AMR2 | RURAL | Weather | 153.99 | 1379 | 212352.21 | 0.61153 | 0.00044346
2013-01-28 | 290613 | KRA3 | URBAN | Weather | 79.5 | 3747 | 297886.5 | 0.30083 | 8.0285e-05
2013-01-28 | 290614 | SPO60A | URBAN | Weather | 94 | 115 | 10810 | 0.010917 | 9.4928e-05
2013-01-28 | 290615 | KRA3 | URBAN | Weather | 90.25 | 3623 | 326975.75 | 0.3302 | 9.1141e-05
2013-01-28 | 290617 | JBB13A | RURAL | Weather | 24 | 240 | 5760 | 0.016588 | 6.9115e-05
2013-01-28 | 290618 | BLH10B | URBAN | Weather | 152 | 4900 | 744800 | 0.75215 | 0.0001535
2013-01-28 | 290633 | NSW8A | URBAN | Weather | 54 | 786 | 42444 | 0.042863 | 5.4533e-05
2013-01-28 | 290637 | MTG7A | URBAN | Operational error | 54.78 | 2469 | 135251.82 | 0.13659 | 5.5321e-05
2013-01-28 | 290640 | WSE6A | RURAL | Vegetation | 7.92 | 263 | 2082.96 | 0.0059985 | 2.2808e-05
2013-01-28 | 290641 | HIS12A | URBAN | Weather | 50.4 | 3264.5 | 199858.4 | 0.20183 | 5.0898e-05
2013-01-28 | 290643 | CSE7 | URBAN | Equipment failure | 53.3478 | 1832 | 97733.1696 | 0.098698 | 5.3875e-05
2013-01-28 | 290644 | HPE5A | URBAN | Weather | 23.5 | 2579 | 60606.5 | 0.061205 | 2.3732e-05
2013-01-28 | 290646 | GBG27 | URBAN | Vegetation | 37.95 | 848 | 32181.6 | 0.032499 | 3.8325e-05
2013-01-28 | 290647 | WRD24A | URBAN | Equipment failure | 34 | 427 | 14518 | 0.014661 | 3.4336e-05
2013-01-28 | 290651 | WRD22B | URBAN | Other | 89 | 1953 | 173817 | 0.17553 | 8.9879e-05
2013-01-28 | 290658 | NDH7 | URBAN | Weather | 147.84 | 2048 | 302776.32 | 0.30577 | 0.0001493
2013-01-28 | 290662 | BKD2B | URBAN | Other | 48.18 | 2861 | 137842.98 | 0.1392 | 4.8656e-05
2013-01-28 | 290664 | NSW28 | URBAN | Equipment failure | 105 | 2792 | 293160 | 0.29605 | 0.00010604
2013-01-28 | 290676 | BLB4A | URBAN | Other | 72.83 | 3114 | 226792.62 | 0.22903 | 7.3549e-05
2013-01-28 | 290678 | CLRSRD17 | URBAN | Other | 69 | 1851 | 127719 | 0.12898 | 6.9681e-05
2013-01-28 | 290682 | EMP25A | URBAN | Other | 55.5 | 3557 | 197413.5 | 0.19936 | 5.6048e-05
2013-01-28 | 290683 | SBH11 | URBAN | Other | 139.59 | 3421 | 477537.39 | 0.48225 | 0.00014097
2013-01-28 | 290684 | MRK7A | URBAN | Weather | 26 | 3719 | 96694 | 0.097649 | 2.6257e-05
2013-01-28 | 290685 | BLH11B | URBAN | Weather | 133 | 3719 | 494627 | 0.49951 | 0.00013431
2013-01-28 | 290687 | HPK5A | URBAN | Weather | 64.2378 | 3833 | 246223.4874 | 0.24865 | 6.4872e-05
2013-01-28 | 290692 | NGE4B | URBAN | Equipment failure | 52.47 | 2782 | 145971.54 | 0.14741 | 5.2988e-05
2013-01-28 | 290705 | DRD5A | URBAN | Other | 80.7378 | 2812 | 227034.6936 | 0.22928 | 8.1535e-05
2013-01-28 | 290715 | RLA6 | URBAN | Weather | 88 | 4031 | 354728 | 0.35823 | 8.8869e-05
2013-01-28 | 290723 | NSW17 | URBAN | Other | 51 | 3897 | 198747 | 0.20071 | 5.1504e-05
2013-01-28 | 290746 | MTG15A | URBAN | Weather | 66.5 | 3956 | 263074 | 0.26567 | 6.7157e-05
2013-01-28 | 290749 | BKD2B | URBAN | Weather | 127.5 | 233 | 29707.5 | 0.030001 | 0.00012876
2013-01-28 | 290753 | SBH6 | URBAN | Weather | 79.86 | 2752 | 219774.72 | 0.22194 | 8.0648e-05
2013-01-28 | 290758 | KSN2A | RURAL | Weather | 13.5 | 4294 | 57969 | 0.16694 | 3.8877e-05
2013-01-28 | 290763 | CPC2B | URBAN | Weather | 90 | 60 | 5400 | 0.0054533 | 9.0889e-05
2013-01-28 | 290769 | CPC2B | URBAN | Weather | 90 | 624 | 56160 | 0.056714 | 9.0889e-05
2013-01-28 | 290785 | RST5A | URBAN | Weather | 64.05 | 2041 | 130726.05 | 0.13202 | 6.4682e-05
2013-01-28 | 290787 | CPK9 | RURAL | Weather | 94 | 262 | 24628 | 0.070923 | 0.0002707
2013-01-28 | 290788 | CPC2B | URBAN | Other | 66 | 314 | 20724 | 0.020929 | 6.6652e-05
2013-01-28 | 290790 | WSO13A | RURAL | Equipment failure | 128 | 188 | 24064 | 0.069299 | 0.00036861
2013-01-28 | 290791 | CPK13 | RURAL | Weather | 55 | 240 | 13200 | 0.038013 | 0.00015839
2013-01-28 | 290793 | RBY12 | URBAN | Weather | 106.5 | 562 | 59853 | 0.060444 | 0.00010755
2013-01-28 | 290795 | RBY12 | URBAN | Weather | 4 | 562 | 2248 | 0.0022702 | 4.0395e-06
2013-01-28 | 290798 | MWMRBK11 | RURAL | Weather | 35 | 100 | 3500 | 0.010079 | 0.00010079
2013-01-28 | 290806 | CPC2B | URBAN | Other | 64 | 345 | 22080 | 0.022298 | 6.4632e-05
2013-01-28 | 290807 | BKD15A | URBAN | Weather | 121 | 65 | 7865 | 0.0079427 | 0.00012219
2013-01-28 | 290808 | CPC2B | URBAN | Weather | 90 | 553 | 49770 | 0.050261 | 9.0889e-05
2013-01-28 | 290810 | BDB27A | RURAL | Weather | 29 | 1038 | 30102 | 0.086687 | 8.3514e-05
2013-01-28 | 290812 | GGR3 | RURAL | Weather | 4.33 | 1559 | 6750.47 | 0.01944 | 1.2469e-05
2013-01-28 | 290816 | CPK13 | RURAL | Weather | 33.5 | 1440 | 48240 | 0.13892 | 9.6473e-05
2013-01-28 | 290820 | CPC2B | URBAN | Vegetation | 14 | 1032 | 14448 | 0.014591 | 1.4138e-05
2013-01-28 | 290822 | MCW11 | RURAL | Vegetation | 33 | 2477 | 81741 | 0.2354 | 9.5033e-05
2013-01-28 | 290824 | THL3 | RURAL | Weather | 7 | 2665 | 18655 | 0.053722 | 2.0158e-05
2013-01-28 | 290833 | CLM5 | URBAN | Weather | 35 | 1132 | 39620 | 0.040011 | 3.5346e-05
2013-01-28 | 290845 | KWA12A | URBAN | Equipment failure | 149 | 3160 | 470840 | 0.47549 | 0.00015047
2013-01-28 | 290847 | GYGGYS6 | RURAL | Weather | 3.5 | 2623 | 9180.5 | 0.026438 | 1.0079e-05
2013-01-28 | 290848 | BHD21A | URBAN | Vegetation | 58 | 549 | 31842 | 0.032156 | 5.8573e-05
2013-01-28 | 290850 | KWA12A | URBAN | Weather | 41 | 2402 | 98482 | 0.099454 | 4.1405e-05
2013-01-28 | 290854 | SPD11A | URBAN | Vegetation | 137 | 2195 | 300715 | 0.30368 | 0.00013835
2013-01-28 | 290863 | AHD10A | URBAN | Vegetation | 20.0739 | 531 | 10659.2409 | 0.010764 | 2.0272e-05
2013-01-28 | 290876 | MLB3A | RURAL | Other | 50.16 | 2796 | 140247.36 | 0.40388 | 0.00014445
2013-01-28 | 290889 | SHW3 | URBAN | Other | 62.37 | 2634 | 164282.58 | 0.1659 | 6.2986e-05
2013-01-28 | 290906 | KRN11 | URBAN | Weather | 80 | 3037 | 242960 | 0.24536 | 8.079e-05
2013-01-28 | 290907 | NMK23A | URBAN | Weather | 35.31 | 3055 | 107872.05 | 0.10894 | 3.5659e-05
2013-01-28 | 290916 | INA3A | URBAN | Weather | 36.63 | 3343 | 122454.09 | 0.12366 | 3.6992e-05
2013-01-28 | 290954 | STPT1 | URBAN | Equipment failure | 16.885 | 4036 | 68147.86 | 0.068821 | 1.7052e-05
2013-01-28 | 290961 | MGL1A | RURAL | Weather | 55 | 4252 | 233860 | 0.67346 | 0.00015839
2013-01-28 | 290984 | CPK10 | URBAN | Other | 59 | 165 | 9735 | 0.0098311 | 5.9583e-05
2013-01-28 | 291012 | NMC5A | RURAL | Weather | 16 | 3821 | 61136 | 0.17606 | 4.6076e-05
2013-01-28 | 291013 | MCN2 | RURAL | Weather | 1.2 | 4432 | 5318.4 | 0.015316 | 3.4557e-06
2013-01-28 | 291014 | RST8A | URBAN | Weather | 36.3 | 1410 | 51183 | 0.051688 | 3.6658e-05
2013-01-28 | 291236 | GYN2B | URBAN | Weather | 6 | 2213 | 13278 | 0.013409 | 6.0592e-06
2013-01-28 | 291239 | GYM2B | URBAN | Weather | 19.5 | 2341 | 45649.5 | 0.0461 | 1.9693e-05
2013-01-28 | 291240 | TWT11A | RURAL | Weather | 5 | 182 | 910 | 0.0026206 | 1.4399e-05
2013-01-28 | 291241 | TWT6B | RURAL | Weather | 126.33 | 12 | 1515.96 | 0.0043656 | 0.0003638
2013-01-28 | 291242 | TWT11A | RURAL | Weather | 9 | 33 | 297 | 0.00085529 | 2.5918e-05
2013-01-28 | 291254 | VPT13A | RURAL | Weather | 35.4 | 328 | 11611.2 | 0.033438 | 0.00010194
2013-01-28 | 291295 | LBH6A | RURAL | Weather | 2 | 77 | 154 | 0.00044349 | 5.7596e-06
2013-01-28 | 291310 | TWG16 | URBAN | Weather | 25.5 | 3322 | 84711 | 0.085547 | 2.5752e-05
2013-01-28 | 291319 | DRD16A | URBAN | Weather | 26.5 | 4580 | 121370 | 0.12257 | 2.6762e-05
2013-01-28 | 291347 | TWG18 | URBAN | Weather | 26.31 | 77 | 2025.87 | 0.0020459 | 2.657e-05
2013-01-28 | 291351 | BIS1 | RURAL | Weather | 20.02 | 120 | 2402.4 | 0.0069184 | 5.7653e-05
2013-01-28 | 291354 | TGP9A | RURAL | Weather | 19 | 51 | 969 | 0.0027905 | 5.4716e-05
2013-01-28 | 291355 | NRA5A | RURAL | Weather | 12.5 | 22 | 275 | 0.00079194 | 3.5997e-05
2013-01-28 | 291356 | KMR29A | URBAN | Other | 1.35 | 4629 | 6249.15 | 0.0063108 | 1.3633e-06
2013-01-28 | 291362 | IDY1A | URBAN | Weather | 53.5 | 770 | 41195 | 0.041602 | 5.4028e-05
2013-01-28 | 291393 | GBN4 | RURAL | Weather | 17 | 1435 | 24395 | 0.070252 | 4.8956e-05
2013-01-28 | 291397 | MLT19A | URBAN | Weather | 233.44 | 550 | 128392 | 0.12966 | 0.00023574
2013-01-28 | 291406 | RLB13B | RURAL | Weather | 8.5 | 2195.5 | 36038.3 | 0.10378 | 2.4478e-05
2013-01-28 | 291430 | GAP8A | URBAN | Weather | 52.5 | 92 | 4830 | 0.0048777 | 5.3018e-05
2013-01-28 | 291432 | MGL2A | RURAL | Weather | 22 | 5515 | 121330 | 0.3494 | 6.3355e-05
2013-01-28 | 291548 | CPR7 | URBAN | Weather | 31.4 | 75 | 2355 | 0.0023783 | 3.171e-05
2013-01-28 | 291570 | MRK6 | URBAN | Weather | 49 | 5157 | 252693 | 0.25519 | 4.9484e-05
2013-01-28 | 291574 | ALY8 | URBAN | Weather | 1 | 5180 | 5180 | 0.0052311 | 1.0099e-06
2013-01-28 | 291604 | WSO13A | RURAL | Weather | 126 | 2262 | 285012 | 0.82077 | 0.00036285
2013-01-28 | 291622 | MRK5A | URBAN | Weather | 108.5 | 4585 | 497472.5 | 0.50238 | 0.00010957
2013-01-28 | 291630 | HPE13A | URBAN | Weather | 111 | 59 | 6549 | 0.0066137 | 0.0001121
2013-01-28 | 291667 | SHW3 | URBAN | Weather | 11.8 | 2642 | 31175.6 | 0.031483 | 1.1917e-05
2013-01-28 | 291672 | MLS26B | URBAN | Weather | 3.7275 | 65 | 242.2875 | 0.00024468 | 3.7643e-06
2013-01-28 | 291675 | RBY3 | URBAN | Weather | 1568.5 | 532 | 834442 | 0.84268 | 0.001584
2013-01-28 | 291691 | TRG10B | URBAN | Weather | 82.5 | 901 | 74332.5 | 0.075066 | 8.3315e-05
2013-01-28 | 291717 | ARG5A | URBAN | Weather | 47.5 | 6775 | 321812.5 | 0.32499 | 4.7969e-05
2013-01-28 | 291770 | RLA8 | URBAN | Weather | 4.4 | 3696 | 16262.4 | 0.016423 | 4.4434e-06
2013-01-28 | 291812 | CHL11A | RURAL | Weather | 4.4 | 5244 | 23073.6 | 0.066447 | 1.2671e-05
2013-01-28 | 291899 | INA11A | URBAN | Weather | 1411.25 | 1309.1905 | 1806967.5 | 1.8248 | 0.0014252
2013-01-28 | 291901 | INA7A | RURAL | Weather | 1189.49 | 1462 | 1739034.38 | 5.008 | 0.0034255
2013-01-28 | 291913 | GYN5A | URBAN | Weather | 26 | 3090 | 80340 | 0.081133 | 2.6257e-05
2013-01-28 | 291914 | GYN2B | URBAN | Weather | 27 | 3180 | 85860 | 0.086708 | 2.7267e-05
2013-01-28 | 291915 | GYM2B | URBAN | Weather | 11.1 | 2550 | 28305 | 0.028584 | 1.121e-05
2013-01-28 | 291916 | GYM3 | URBAN | Weather | 77 | 3470 | 267190 | 0.26983 | 7.776e-05
2013-01-28 | 291918 | GYM2B | URBAN | Weather | 32.5 | 3135 | 101887.5 | 0.10289 | 3.2821e-05
2013-01-28 | 292016 | OXL11A | URBAN | Weather | 1479.16 | 1011 | 1495430.76 | 1.5102 | 0.0014938
2013-01-28 | 292017 | OXL10A | URBAN | Weather | 120.99 | 1264 | 152931.36 | 0.15444 | 0.00012218
2013-01-28 | 292017 | OXL4A | URBAN | Weather | 445 | 1264 | 562480 | 0.56803 | 0.00044939
2013-01-28 | 292131 | NIP5A | URBAN | Weather | 1253.5 | 1147.4444 | 1430928.5 | 1.4451 | 0.0012659
2013-01-28 | 292370 | MGP12A | RURAL | Weather | 627 | 1761.5263 | 1397289 | 4.0239 | 0.0018056
2013-01-28 | 292373 | MGP13A | RURAL | Weather | 97 | 3461 | 335717 | 0.96679 | 0.00027934
2013-01-28 | 292450 | BWH16A | RURAL | Weather | 309 | 3677.9474 | 1137673.5 | 3.2762 | 0.00088985
2013-01-28 | 292490 | SMF1B | RURAL | Weather | 24 | 1530 | 36720 | 0.10575 | 6.9115e-05
2013-01-28 | 292531 | MTB15A | RURAL | Weather | 163 | 4355 | 709865 | 2.0443 | 0.0004694
2013-01-28 | 292610 | MTB17A | RURAL | Weather | 721.34 | 4427 | 3193372.18 | 9.1962 | 0.0020773
2013-01-28 | 292630 | 11THPT1 | URBAN | Equipment failure | 0.25 | 3306 | 826.5 | 0.00083466 | 2.5247e-07
2013-01-28 | 292630 | CRBTHP14 | URBAN | Equipment failure | 1304.33 | 3306 | 4312114.98 | 4.3547 | 0.0013172
2013-01-28 | 292630 | THP1 | URBAN | Equipment failure | 1 | 3306 | 3306 | 0.0033386 | 1.0099e-06
2013-01-28 | 292790 | RCN10A | URBAN | Weather | 1503.27 | 1485 | 2232355.95 | 2.2544 | 0.0015181
2013-01-28 | 292792 | GAP4A | URBAN | Equipment failure | 9.5 | 1605 | 15247.5 | 0.015398 | 9.5938e-06
2013-01-28 | 293101 | CRB25A | RURAL | Weather | 56.5 | 3284 | 185546 | 0.53433 | 0.00016271
2013-01-28 | 293530 | MFN13A | RURAL | Weather | 355.5 | 1033 | 367231.5 | 1.0575 | 0.0010238
2013-01-28 | 293591 | BHD23A | RURAL | Weather | 441 | 1193 | 526113 | 1.5151 | 0.00127
2013-01-28 | 293790 | KBR2A | RURAL | Weather | 176.33 | 1647.7391 | 314395.95 | 0.90539 | 0.00050779
2013-01-28 | 293870 | GBP6 | URBAN | Equipment failure | 728.33 | 2747.7273 | 1903363.74 | 1.9222 | 0.00073552
2013-01-28 | 293974 | MAI11 | URBAN | Weather | 1705.83 | 257 | 438398.31 | 0.44273 | 0.0017227
2013-01-28 | 293974 | MAI13 | URBAN | Weather | 1776.6 | 257 | 456586.2 | 0.46109 | 0.0017941
2013-01-28 | 293974 | MAI14 | URBAN | Weather | 1740.41 | 257 | 447285.37 | 0.4517 | 0.0017576
2013-01-28 | 293974 | MAI17 | URBAN | Weather | 1766.51 | 257 | 453993.07 | 0.45848 | 0.001784
2013-01-28 | 293974 | MAI5 | URBAN | Weather | 1735.98 | 257 | 446146.86 | 0.45055 | 0.0017531
2013-01-28 | 293974 | MAI7 | URBAN | Weather | 1423.53 | 257 | 365847.21 | 0.36946 | 0.0014376
2013-01-28 | 293974 | MAI8 | URBAN | Weather | 1256.69 | 257 | 322969.33 | 0.32616 | 0.0012691
2013-01-28 | 293990 | PBH1 | URBAN | Weather | 1414 | 1664 | 2352896 | 2.3761 | 0.001428
2013-01-28 | 294193 | LHM2 | URBAN | Weather | 358.66 | 102 | 36583.32 | 0.036945 | 0.0003622
2013-01-28 | 294636 | BWH7A | RURAL | Weather | 364.67 | 1892 | 689955.64 | 1.9869 | 0.0010502
2013-01-28 | 294638 | GCLSBY7 | URBAN | Weather | 323.44 | 2266 | 732915.04 | 0.74015 | 0.00032663
2013-01-28 | 294670 | ARL11A | URBAN | Weather | 450 | 75 | 33750 | 0.034083 | 0.00045444
2013-01-28 | 294670 | ARL11B | URBAN | Weather | 660.5 | 60 | 39630 | 0.040021 | 0.00066702
2013-01-28 | 294686 | KRA1 | URBAN | Weather | 592.33 | 5 | 2961.65 | 0.0029909 | 0.00059818
2013-01-28 | 294686 | KRA10 | URBAN | Weather | 1081.33 | 5 | 5406.65 | 0.00546 | 0.001092
2013-01-28 | 294686 | KRA2 | URBAN | Weather | 821.16 | 5 | 4105.8 | 0.0041463 | 0.00082927
2013-01-28 | 294686 | KRA3 | URBAN | Weather | 1340.5 | 5 | 6702.5 | 0.0067687 | 0.0013537
2013-01-28 | 294686 | KRA4 | URBAN | Weather | 289.5 | 5 | 1447.5 | 0.0014618 | 0.00029236
2013-01-28 | 294686 | KRA6 | URBAN | Weather | 1 | 5 | 5 | 5.0494e-06 | 1.0099e-06
2013-01-28 | 294687 | 393 | URBAN | Weather | 1 | 1667 | 1667 | 0.0016835 | 1.0099e-06
2013-01-28 | 295052 | LTA4B | URBAN | Equipment failure | 1007.49 | 2545 | 2564062.05 | 2.5894 | 0.0010174
2013-01-28 | 295232 | TWG17 | URBAN | Weather | 1200.55 | 212 | 349768.237 | 0.35322 | 0.0012124
2013-01-28 | 295233 | MRK5A | URBAN | Equipment failure | 749.25 | 421 | 315434.25 | 0.31855 | 0.00075665
2013-01-28 | 295391 | MTG3A | URBAN | Weather | 1152.83 | 608.9259 | 701908.09 | 0.70884 | 0.0011642
2013-01-28 | 295410 | BHD23A | RURAL | Weather | 869 | 1946 | 1691074 | 4.8699 | 0.0025025
2013-01-28 | 296569 | AGE6A | URBAN | Vegetation | 35.175 | 515 | 18115.125 | 0.018294 | 3.5522e-05
2013-01-28 | 296572 | IPS13A | RURAL | Other | 42.88 | 1203 | 51584.64 | 0.14855 | 0.00012348
2013-01-29 | 289254 | TPT5 | RURAL | Weather | 506.5 | 387 | 196015.5 | 0.56433 | 0.0014582
2013-01-29 | 289330 | BDL1 | URBAN | Equipment failure | 100.5 | 54 | 5427 | 0.005481 | 0.0001015
2013-01-29 | 289330 | BDL3 | URBAN | Equipment failure | 250.5 | 54 | 13527 | 0.013662 | 0.00025299
2013-01-29 | 289330 | BDL4 | URBAN | Equipment failure | 1720.81 | 54 | 92923.74 | 0.093848 | 0.0017379
2013-01-29 | 289330 | BDL5 | URBAN | Equipment failure | 424.66 | 54 | 22931.64 | 0.02316 | 0.00042888
2013-01-29 | 289330 | BDL6 | URBAN | Equipment failure | 251.5 | 54 | 13581 | 0.013716 | 0.000254
2013-01-29 | 289330 | BDL7 | URBAN | Equipment failure | 264.33 | 54 | 14273.82 | 0.014416 | 0.00026696
2013-01-29 | 289430 | JBB16A | RURAL | Weather | 236.5 | 434 | 102641 | 0.2955 | 0.00068088
2013-01-29 | 289432 | BDL2 | URBAN | Equipment failure | 1404.33 | 270.7 | 379949.44 | 0.38373 | 0.0014183
2013-01-29 | 289457 | JBB13A | RURAL | Weather | 129 | 808 | 104232 | 0.30008 | 0.00037139
2013-01-29 | 289463 | SBH8 | URBAN | Equipment failure | 754.04 | 761 | 1121042.2 | 1.1322 | 0.00076154
2013-01-29 | 289472 | MAI14 | URBAN | Equipment failure | 394 | 414 | 163116 | 0.16474 | 0.00039792
2013-01-29 | 289486 | SBH13A | URBAN | Equipment failure | 518.04 | 5 | 2590.2 | 0.002616 | 0.00052319
2013-01-29 | 289495 | TWT12A | RURAL | Vegetation | 906.51 | 227.8667 | 413046.52 | 1.1892 | 0.0026098
2013-01-29 | 289505 | CBW11 | RURAL | Weather | 1147.99 | 243.3774 | 400294.97 | 1.1525 | 0.0033051
2013-01-29 | 289517 | BBH10A | URBAN | Equipment failure | 254 | 611 | 209133.44 | 0.21121 | 0.00025653
2013-01-29 | 289610 | JBB1B | RURAL | Weather | 168 | 1375 | 231000 | 0.66505 | 0.00048367
2013-01-29 | 289712 | GVN16A | RURAL | Weather | 156.5 | 1493 | 233654.5 | 0.67269 | 0.00045056
2013-01-29 | 289750 | BHD35A | RURAL | Weather | 1390.5 | 1130.9109 | 1169016 | 3.3656 | 0.0040033
2013-01-29 | 289753 | JBB16A | RURAL | Weather | 30 | 1433 | 42990 | 0.12377 | 8.637e-05
2013-01-29 | 289821 | PWC6 | RURAL | Equipment failure | 254 | 400.5 | 107893 | 0.31062 | 0.00073127
2013-01-29 | 289871 | MLT15A | URBAN | Weather | 35.31 | 104.3333 | 3389.76 | 0.0034235 | 3.5661e-05
2013-01-29 | 289991 | TBV1 | RURAL | Weather | 42.5 | 1552 | 65960 | 0.1899 | 0.00012236
2013-01-29 | 290132 | GGR3 | RURAL | Weather | 86.99 | 1844.5 | 162814.53 | 0.46874 | 0.00025044
2013-01-29 | 290156 | MSV1 | RURAL | Weather | 143 | 2071.3425 | 398847 | 1.1483 | 0.0004117
2013-01-29 | 290164 | BHD35A | RURAL | Equipment failure | 21 | 2507 | 52647 | 0.15157 | 6.0459e-05
2013-01-29 | 290350 | BMT1 | RURAL | Weather | 582.49 | 235 | 136885.15 | 0.39409 | 0.001677
2013-01-29 | 290351 | CRY2A | RURAL | Equipment failure | 736 | 55 | 40480 | 0.11654 | 0.0021189
2013-01-29 | 290351 | CRY3A | RURAL | Equipment failure | 976.69 | 55 | 53717.95 | 0.15465 | 0.0028119
2013-01-29 | 290351 | CRY5A | RURAL | Equipment failure | 96.49 | 55 | 5306.95 | 0.015279 | 0.0002778
2013-01-29 | 290351 | CRY6A | RURAL | Equipment failure | 693.5 | 55 | 38142.5 | 0.10981 | 0.0019966
2013-01-29 | 290490 | JBB4A | URBAN | Equipment failure | 3 | 3956 | 11868 | 0.011986 | 3.0298e-06
2013-01-29 | 290510 | JBB4A | URBAN | Equipment failure | 3 | 4021 | 12063 | 0.012183 | 3.0298e-06
2013-01-29 | 290571 | GYGGYS6 | RURAL | Weather | 157 | 188 | 29516 | 0.084977 | 0.000452
2013-01-29 | 290619 | MTB15A | RURAL | Weather | 29 | 2433 | 70557 | 0.20313 | 8.3491e-05
2013-01-29 | 290621 | CRB25A | RURAL | Weather | 2 | 4920 | 9840 | 0.028329 | 5.758e-06
2013-01-29 | 290623 | HWL8A | URBAN | Equipment failure | 118.5 | 318 | 37683 | 0.038058 | 0.00011968
2013-01-29 | 290625 | HWL8A | URBAN | Equipment failure | 78.5 | 798 | 62643 | 0.063266 | 7.9281e-05
2013-01-29 | 290631 | MDRMLD11 | URBAN | Weather | 67 | 260 | 17420 | 0.017593 | 6.7666e-05
2013-01-29 | 290645 | CRM13A | URBAN | Equipment failure | 69 | 1178 | 81282 | 0.08209 | 6.9686e-05
2013-01-29 | 290649 | SBH6 | URBAN | Equipment failure | 91 | 305 | 27755 | 0.028031 | 9.1905e-05
2013-01-29 | 290650 | KLG11A | URBAN | Weather | 153 | 57 | 8721 | 0.0088077 | 0.00015452
2013-01-29 | 290653 | MHL1B | RURAL | Other | 121.44 | 946 | 114882.24 | 0.33075 | 0.00034963
2013-01-29 | 290655 | MFD9A | URBAN | Weather | 56.5 | 719 | 40623.5 | 0.041027 | 5.7062e-05
2013-01-29 | 290656 | MRK5A | URBAN | Weather | 54.45 | 1104 | 60112.8 | 0.060711 | 5.4991e-05
2013-01-29 | 290659 | SBK9 | URBAN | Equipment failure | 65.01 | 1222 | 79442.22 | 0.080232 | 6.5656e-05
2013-01-29 | 290660 | NDH5A | URBAN | Other | 56.1 | 1841 | 103280.1 | 0.10431 | 5.6658e-05
2013-01-29 | 290661 | TGP9A | RURAL | Weather | 53 | 802 | 42506 | 0.12238 | 0.00015259
2013-01-29 | 290667 | BLB8A | URBAN | Other | 142.17 | 1984 | 282065.28 | 0.28487 | 0.00014358
2013-01-29 | 290668 | LTA4B | URBAN | Equipment failure | 62.33 | 2349 | 146413.17 | 0.14787 | 6.295e-05
2013-01-29 | 290669 | BKD3A | URBAN | Equipment failure | 139 | 1505 | 209195 | 0.21128 | 0.00014038
2013-01-29 | 290672 | CHL4 | URBAN | Other | 94 | 1330 | 125020 | 0.12626 | 9.4935e-05
2013-01-29 | 290674 | GBG28 | URBAN | Other | 1.76 | 1001 | 1761.76 | 0.0017793 | 1.7775e-06
2013-01-29 | 290688 | WNM6 | URBAN | Vegetation | 91.74 | 1313 | 120454.62 | 0.12165 | 9.2652e-05
2013-01-29 | 290690 | SGT7 | URBAN | Other | 64.02 | 877 | 56145.54 | 0.056704 | 6.4657e-05
2013-01-29 | 290691 | TMH16A | URBAN | Weather | 64 | 2700 | 172800 | 0.17452 | 6.4636e-05
2013-01-29 | 290694 | DBY5 | URBAN | Weather | 22.77 | 1322 | 30101.94 | 0.030401 | 2.2996e-05
2013-01-29 | 290697 | MFN2B | RURAL | Other | 3.84 | 2002 | 7687.68 | 0.022133 | 1.1055e-05
2013-01-29 | 290699 | MTB1B | RURAL | Weather | 31.5 | 4740 | 149310 | 0.42986 | 9.0689e-05
2013-01-29 | 290702 | EMP21A | RURAL | Weather | 28.38 | 3184 | 90361.92 | 0.26015 | 8.1706e-05
2013-01-29 | 290713 | LTA2 | URBAN | Equipment failure | 24.915 | 1762 | 43900.23 | 0.044337 | 2.5163e-05
2013-01-29 | 290721 | WMR1 | RURAL | Other | 8.58 | 1025 | 8794.5 | 0.025319 | 2.4702e-05
2013-01-29 | 290725 | RCF5A | URBAN | Weather | 112 | 1396 | 156352 | 0.15791 | 0.00011311
2013-01-29 | 290728 | RCF5A | URBAN | Weather | 71.28 | 2185 | 155746.8 | 0.1573 | 7.1989e-05
2013-01-29 | 290744 | RCF7A | URBAN | Other | 97 | 1457 | 141329 | 0.14273 | 9.7965e-05
2013-01-29 | 290750 | YTA3A | URBAN | Other | 7 | 3306 | 23142 | 0.023372 | 7.0696e-06
2013-01-29 | 290756 | EMP21A | RURAL | Vegetation | 19 | 1683 | 31977 | 0.092062 | 5.4701e-05
2013-01-29 | 290809 | KMR17A | URBAN | Vegetation | 88.77 | 419 | 37194.63 | 0.037564 | 8.9653e-05
2013-01-29 | 290815 | WSO13A | RURAL | Other | 128 | 138 | 17664 | 0.050855 | 0.00036851
2013-01-29 | 290817 | MBG4 | RURAL | Weather | 0.66 | 392 | 258.72 | 0.00074486 | 1.9001e-06
2013-01-29 | 290819 | TWG19 | URBAN | Other | 102.3 | 673 | 68847.9 | 0.069532 | 0.00010332
2013-01-29 | 290823 | NSD1A | URBAN | Weather | 10.23 | 1184 | 12112.32 | 0.012233 | 1.0332e-05
2013-01-29 | 290825 | NSD1A | URBAN | Weather | 16.5 | 1013 | 16714.5 | 0.016881 | 1.6664e-05
2013-01-29 | 290831 | SFD3 | URBAN | Other | 14.355 | 1155 | 16580.025 | 0.016745 | 1.4498e-05
2013-01-29 | 290832 | TRG2A | URBAN | Weather | 56.925 | 2097 | 119371.725 | 0.12056 | 5.7491e-05
2013-01-29 | 290834 | AGE5B | URBAN | Other | 38.94 | 2139 | 83292.66 | 0.084121 | 3.9327e-05
2013-01-29 | 290836 | CLD28A | RURAL | Weather | 43.23 | 162 | 7003.26 | 0.020162 | 0.00012446
2013-01-29 | 290844 | AGT31A | RURAL | Vegetation | 12.87 | 1715 | 22072.05 | 0.063546 | 3.7053e-05
2013-01-29 | 290851 | MAI11 | URBAN | Weather | 135.3 | 561 | 75903.3 | 0.076658 | 0.00013665
2013-01-29 | 290852 | SPD2B | URBAN | Vegetation | 4 | 826 | 3304 | 0.0033369 | 4.0398e-06
2013-01-29 | 290856 | CRB24B | URBAN | Equipment failure | 133 | 1727 | 229691 | 0.23197 | 0.00013432
2013-01-29 | 290858 | BBH10A | URBAN | Weather | 68 | 1703 | 115804 | 0.11696 | 6.8676e-05
2013-01-29 | 290859 | EMD3 | RURAL | Vegetation | 1 | 1075 | 1075 | 0.0030949 | 2.879e-06
2013-01-29 | 290860 | BHD20A | URBAN | Other | 54.83 | 245 | 13433.35 | 0.013567 | 5.5375e-05
2013-01-29 | 290861 | SPO16A | URBAN | Weather | 16 | 958 | 15328 | 0.01548 | 1.6159e-05
2013-01-29 | 290865 | SPO16A | URBAN | Weather | 54.5 | 1047 | 57061.5 | 0.057629 | 5.5042e-05
2013-01-29 | 290866 | SPO61A | URBAN | Weather | 29.5 | 1132 | 33394 | 0.033726 | 2.9793e-05
2013-01-29 | 290868 | YDA1B | RURAL | Weather | 13 | 1969 | 25597 | 0.073694 | 3.7427e-05
2013-01-29 | 290869 | SPO67B | URBAN | Other | 90 | 1321 | 118890 | 0.12007 | 9.0895e-05
2013-01-29 | 290871 | LDR3 | URBAN | Other | 208 | 1303 | 271024 | 0.27372 | 0.00021007
2013-01-29 | 290874 | MAI17 | URBAN | Weather | 225.42 | 1433 | 323026.86 | 0.32624 | 0.00022766
2013-01-29 | 290875 | GBN4 | RURAL | Weather | 7 | 2074 | 14518 | 0.041797 | 2.0153e-05
2013-01-29 | 290878 | MAI5 | URBAN | Other | 137.5 | 2485 | 341687.5 | 0.34509 | 0.00013887
2013-01-29 | 290879 | LDR3 | URBAN | Other | 145 | 1875 | 271875 | 0.27458 | 0.00014644
2013-01-29 | 290880 | MGP2A | URBAN | Weather | 53.5 | 3249 | 173821.5 | 0.17555 | 5.4032e-05
2013-01-29 | 290881 | MMC19B | URBAN | Other | 94 | 2291 | 215354 | 0.2175 | 9.4935e-05
2013-01-29 | 290882 | MMC33A | URBAN | Other | 54 | 2478 | 133812 | 0.13514 | 5.4537e-05
2013-01-29 | 290885 | MDR31A | URBAN | Weather | 10.83 | 2565 | 27778.95 | 0.028055 | 1.0938e-05
2013-01-29 | 290888 | HWL4A | URBAN | Equipment failure | 52 | 2569 | 133588 | 0.13492 | 5.2517e-05
2013-01-29 | 290893 | PBH6 | URBAN | Other | 246.5 | 2550 | 628575 | 0.63483 | 0.00024895
2013-01-29 | 290897 | PBH3 | URBAN | Other | 52.25 | 2652 | 138567 | 0.13994 | 5.277e-05
2013-01-29 | 290901 | BDT2 | RURAL | Vegetation | 9 | 3313 | 29817 | 0.085843 | 2.5911e-05
2013-01-29 | 290905 | OXL11A | URBAN | Other | 51 | 2351 | 119901 | 0.12109 | 5.1507e-05
2013-01-29 | 290910 | MLY3 | RURAL | Vegetation | 6 | 320 | 1920 | 0.0055277 | 1.7274e-05
2013-01-29 | 290912 | INA11A | URBAN | Weather | 35.31 | 2935 | 103634.85 | 0.10467 | 3.5661e-05
2013-01-29 | 290917 | GYM7A | RURAL | Weather | 11 | 2245 | 24695 | 0.071097 | 3.1669e-05
2013-01-29 | 290921 | INA10A | URBAN | Weather | 13 | 2196 | 28548 | 0.028832 | 1.3129e-05
2013-01-29 | 290924 | NMK5 | URBAN | Animals | 121.11 | 2206 | 267168.66 | 0.26983 | 0.00012231
2013-01-29 | 290925 | CPC2A | RURAL | Weather | 34.98 | 2063 | 72163.74 | 0.20776 | 0.00010071
2013-01-29 | 290928 | MTB16A | RURAL | Weather | 6.33 | 1657 | 10488.81 | 0.030197 | 1.8224e-05
2013-01-29 | 290933 | BMT2 | RURAL | Equipment failure | 6 | 2623 | 15738 | 0.04531 | 1.7274e-05
2013-01-29 | 290959 | KWH3 | RURAL | Vegetation | 4.5 | 3903 | 17563.5 | 0.050565 | 1.2956e-05
2013-01-29 | 291009 | BDB32A | RURAL | Weather | 1 | 3782 | 3782 | 0.010888 | 2.879e-06
2013-01-29 | 291031 | RIS2 | URBAN | Weather | 71.5 | 1104 | 78936 | 0.079721 | 7.2211e-05
2013-01-29 | 291190 | ECCT1 | HIGH-DENSITY | Equipment failure | 1.7 | 3554.5 | 12085.3 | 3.1312 | 0.00044046
2013-01-29 | 291245 | THL2 | RURAL | Weather | 3 | 374 | 1122 | 0.0032302 | 8.637e-06
2013-01-29 | 291249 | MCW11 | RURAL | Weather | 6 | 1279 | 7674 | 0.022093 | 1.7274e-05
2013-01-29 | 291357 | STL1A | URBAN | Weather | 200.5 | 521 | 104460.5 | 0.1055 | 0.00020249
2013-01-29 | 291360 | IDY1A | URBAN | Weather | 46.5 | 3785 | 176002.5 | 0.17775 | 4.6962e-05
2013-01-29 | 291368 | STL1A | URBAN | Weather | 76 | 4806 | 365256 | 0.36889 | 7.6756e-05
2013-01-29 | 291390 | HDA3A | URBAN | Weather | 3.27 | 195 | 637.65 | 0.00064399 | 3.3025e-06
2013-01-29 | 291396 | MFD5A | RURAL | Weather | 19.5 | 28 | 546 | 0.0015719 | 5.6141e-05
2013-01-29 | 291450 | WNM2A | URBAN | Weather | 11.4 | 200 | 2280 | 0.0023027 | 1.1513e-05
2013-01-29 | 291451 | KLG5A | RURAL | Weather | 58 | 160 | 9280 | 0.026717 | 0.00016698
2013-01-29 | 291492 | RCF9A | URBAN | Weather | 32.85 | 690 | 22666.5 | 0.022892 | 3.3177e-05
2013-01-29 | 291494 | TGP9A | RURAL | Weather | 34.625 | 46 | 1592.75 | 0.0045855 | 9.9686e-05
2013-01-29 | 291513 | KMR17B | URBAN | Weather | 61.5 | 88 | 5412 | 0.0054658 | 6.2112e-05
2013-01-29 | 291530 | TGP9A | RURAL | Weather | 27.5 | 24 | 660 | 0.0019001 | 7.9173e-05
2013-01-29 | 291532 | SBH6 | URBAN | Equipment failure | 91 | 270 | 24570 | 0.024814 | 9.1905e-05
2013-01-29 | 291591 | HPK8A | URBAN | Weather | 79.42 | 3414 | 271139.88 | 0.27384 | 8.021e-05
2013-01-29 | 291597 | CPR6 | URBAN | Weather | 69.5 | 1181 | 82079.5 | 0.082896 | 7.0191e-05
2013-01-29 | 291657 | MLY3 | RURAL | Weather | 76.5 | 199 | 15223.5 | 0.043829 | 0.00022024
2013-01-29 | 291658 | GBG27 | URBAN | Weather | 60.5 | 46 | 2783 | 0.0028107 | 6.1102e-05
2013-01-29 | 291659 | DRA8 | URBAN | Weather | 17.5 | 210 | 3675 | 0.0037115 | 1.7674e-05
2013-01-29 | 291660 | CBW11 | RURAL | Weather | 7 | 995 | 6965 | 0.020052 | 2.0153e-05
2013-01-29 | 291666 | WNM7A | URBAN | Weather | 23.2 | 1488 | 34521.6 | 0.034865 | 2.3431e-05
2013-01-29 | 291673 | IDY6A | URBAN | Equipment failure | 11.5 | 2638 | 30337 | 0.030639 | 1.1614e-05
2013-01-29 | 291732 | GBN4 | RURAL | Weather | 23 | 42 | 966 | 0.0027811 | 6.6217e-05
2013-01-29 | 291750 | BMT1 | RURAL | Weather | 61.83 | 2583 | 159706.89 | 0.4598 | 0.00017801
2013-01-29 | 291753 | NBR4 | RURAL | Weather | 8 | 78 | 624 | 0.0017965 | 2.3032e-05
2013-01-29 | 291754 | CLM8 | URBAN | Equipment failure | 116 | 47 | 5452 | 0.0055062 | 0.00011715
2013-01-29 | 292132 | KCY1 | URBAN | Equipment failure | 612 | 50 | 30600 | 0.030904 | 0.00061809
2013-01-29 | 292132 | KCY2 | RURAL | Equipment failure | 358.26 | 50 | 17913 | 0.051572 | 0.0010314
2013-01-29 | 292132 | KCY3 | URBAN | Equipment failure | 5.65 | 50 | 282.5 | 0.00028531 | 5.7062e-06
2013-01-29 | 292132 | KCY4 | RURAL | Equipment failure | 698.12 | 50 | 34906 | 0.10049 | 0.0020099
2013-01-29 | 292132 | KCY5 | RURAL | Equipment failure | 524 | 50 | 26200 | 0.07543 | 0.0015086
2013-01-29 | 292350 | CSE7 | URBAN | Weather | 676.83 | 77 | 52115.91 | 0.052634 | 0.00068356
2013-01-29 | 292530 | WFD5A | RURAL | Weather | 92.5 | 782 | 72335 | 0.20825 | 0.00026631
2013-01-29 | 292533 | VPK19A | URBAN | Weather | 11 | 156 | 1716 | 0.0017331 | 1.1109e-05
2013-01-29 | 292534 | MTB17A | RURAL | Weather | 412.34 | 263 | 108445.42 | 0.31222 | 0.0011871
2013-01-29 | 293610 | MTB1B | RURAL | Weather | 1391.32 | 120 | 166958.4 | 0.48067 | 0.0040056
2013-01-29 | 293632 | HPE13A | URBAN | Equipment failure | 339 | 5 | 1695 | 0.0017119 | 0.00034237
2013-01-29 | 294230 | MSV2 | RURAL | Weather | 173.01 | 3097 | 535811.97 | 1.5426 | 0.0004981
2013-01-29 | 294637 | BWH7A | RURAL | Weather | 364.67 | 68 | 24797.56 | 0.071392 | 0.0010499
2013-01-29 | 294639 | SHW5A | URBAN | Weather | 513 | 716 | 367308 | 0.37096 | 0.0005181
2013-01-29 | 295090 | HPE13A | URBAN | Equipment failure | 339 | 5 | 1695 | 0.0017119 | 0.00034237
2013-01-29 | 295091 | HPE13A | URBAN | Equipment failure | 339 | 5 | 1695 | 0.0017119 | 0.00034237
2013-01-29 | 295230 | PBH6 | URBAN | Equipment failure | 2018.67 | 1114 | 2248798.38 | 2.2712 | 0.0020387
2013-01-29 | 295234 | BHD46A | URBAN | Equipment failure | 324.75 | 788 | 255903 | 0.25845 | 0.00032798
2013-01-29 | 296568 | BKD3A | URBAN | Other | 2.01 | 4116 | 8273.16 | 0.0083554 | 2.03e-06
2013-01-29 | 302474 | GTN15A | RURAL | Vegetation | 4.02 | 1396 | 5611.92 | 0.016157 | 1.1574e-05
2013-01-30 | 289670 | LTA2 | URBAN | Equipment failure | 329.25 | 68 | 20736.75 | 0.020944 | 0.00033255
2013-01-30 | 289691 | WMR3 | RURAL | Other | 17 | 141 | 2397 | 0.0068991 | 4.893e-05
2013-01-30 | 289752 | MGP12A | RURAL | Weather | 60 | 402 | 24120 | 0.069423 | 0.00017269
2013-01-30 | 289770 | CPB4 | URBAN | Weather | 1 | 94 | 94 | 9.4941e-05 | 1.01e-06
2013-01-30 | 289783 | MFD3A | RURAL | Other | 945 | 138 | 130410 | 0.37535 | 0.0027199
2013-01-30 | 289790 | SPE24 | URBAN | Equipment failure | 54 | 913 | 49302 | 0.049796 | 5.4541e-05
2013-01-30 | 289801 | 11THPT1 | URBAN | Weather | 0.25 | 444 | 111 | 0.00011211 | 2.525e-07
2013-01-30 | 289801 | CRBTHP14 | URBAN | Weather | 1304.33 | 444 | 579122.52 | 0.58492 | 0.0013174
2013-01-30 | 289801 | THP1 | URBAN | Weather | 1 | 444 | 444 | 0.00044845 | 1.01e-06
2013-01-30 | 289806 | ZMR11A | URBAN | Equipment failure | 17 | 618 | 10506 | 0.010611 | 1.717e-05
2013-01-30 | 289830 | DRD5A | URBAN | Other | 122.33 | 40 | 4893.2 | 0.0049422 | 0.00012356
2013-01-30 | 289835 | LTA4B | URBAN | Equipment failure | 315.66 | 180.1429 | 56851.8 | 0.057421 | 0.00031882
2013-01-30 | 289851 | IPL2 | RURAL | Weather | 333.48 | 293.9371 | 90435.8 | 0.2603 | 0.00095983
2013-01-30 | 290030 | GGR2 | RURAL | Weather | 137.66 | 521.2553 | 67718.25 | 0.19491 | 0.00039622
2013-01-30 | 290136 | RLB16A | RURAL | Other | 26.5 | 1106.8889 | 16833.5 | 0.048451 | 7.6273e-05
2013-01-30 | 290139 | SMF3A | RURAL | Weather | 3 | 1505 | 4515 | 0.012995 | 8.6347e-06
2013-01-30 | 290161 | BBSRDL8 | RURAL | Equipment failure | 1287.04 | 178 | 186776.28 | 0.53759 | 0.0037044
2013-01-30 | 290176 | CLD17A | URBAN | Animals | 1633.15 | 115 | 187812.25 | 0.18969 | 0.0016495
2013-01-30 | 290470 | VPK2A | URBAN | Equipment failure | 85.83 | 164 | 14076.12 | 0.014217 | 8.669e-05
2013-01-30 | 290470 | VPK9A | URBAN | Equipment failure | 564.33 | 134.3333 | 60334.61 | 0.060939 | 0.00056998
2013-01-30 | 290576 | BHD35A | RURAL | Weather | 46.5 | 3372 | 156798 | 0.4513 | 0.00013384
2013-01-30 | 290616 | KRA7 | URBAN | Weather | 64.83 | 360 | 23338.8 | 0.023573 | 6.5479e-05
2013-01-30 | 290636 | MTB17A | RURAL | Weather | 26 | 1700 | 44200 | 0.12722 | 7.4834e-05
2013-01-30 | 290648 | BHD41A | URBAN | Third party impacts | 40 | 152 | 6080 | 0.0061409 | 4.0401e-05
2013-01-30 | 290654 | CVL7A | RURAL | Weather | 63 | 461 | 29043 | 0.083593 | 0.00018133
2013-01-30 | 290671 | ALY9 | URBAN | Weather | 67 | 375 | 25125 | 0.025377 | 6.7671e-05
2013-01-30 | 290673 | IPL3 | RURAL | Weather | 1 | 2545 | 2545 | 0.0073251 | 2.8782e-06
2013-01-30 | 290675 | RBY7A | URBAN | Other | 30.5 | 1087 | 33153.5 | 0.033485 | 3.0805e-05
2013-01-30 | 290680 | PPE16A | RURAL | Equipment failure | 7.5 | 1469 | 11017.5 | 0.031711 | 2.1587e-05
2013-01-30 | 290693 | CVL9A | URBAN | Weather | 33 | 2093 | 69069 | 0.069761 | 3.333e-05
2013-01-30 | 290695 | PPE6A | RURAL | Weather | 2 | 2149 | 4298 | 0.012371 | 5.7565e-06
2013-01-30 | 290698 | BRD5A | RURAL | Vegetation | 3.3 | 345 | 1138.5 | 0.0032769 | 9.4982e-06
2013-01-30 | 290700 | BRD5A | RURAL | Vegetation | 13.86 | 641 | 8884.26 | 0.025571 | 3.9892e-05
2013-01-30 | 290703 | MTB13A | RURAL | Weather | 10 | 2693 | 26930 | 0.077511 | 2.8782e-05
2013-01-30 | 290704 | CPL23A | RURAL | Other | 64 | 1484 | 94976 | 0.27336 | 0.00018421
2013-01-30 | 290706 | SBY4 | URBAN | Other | 94 | 1254 | 117876 | 0.11906 | 9.4941e-05
2013-01-30 | 290711 | RLB13B | RURAL | Weather | 6.6 | 1237 | 8164.2 | 0.023498 | 1.8996e-05
2013-01-30 | 290731 | TMH15A | URBAN | Weather | 53 | 970 | 51410 | 0.051925 | 5.3531e-05
2013-01-30 | 290742 | HTL14A | URBAN | Vegetation | 1.28 | 544 | 696.32 | 0.00070329 | 1.2928e-06
2013-01-30 | 290743 | HDA10A | URBAN | Vegetation | 155 | 592 | 91760 | 0.092679 | 0.00015655
2013-01-30 | 290747 | MFD2A | URBAN | Weather | 11.68 | 896 | 10465.28 | 0.01057 | 1.1797e-05
2013-01-30 | 290751 | RIS4 | RURAL | Weather | 29 | 1082 | 31378 | 0.090313 | 8.3469e-05
2013-01-30 | 290752 | RIS4 | RURAL | Weather | 15 | 1079 | 16185 | 0.046584 | 4.3174e-05
2013-01-30 | 290755 | NGI3A | RURAL | Equipment failure | 10.23 | 963 | 9851.49 | 0.028355 | 2.9444e-05
2013-01-30 | 290759 | BGY5A | RURAL | Weather | 15.18 | 895 | 13586.1 | 0.039104 | 4.3692e-05
2013-01-30 | 290762 | NGE4A | URBAN | Other | 1.5 | 308 | 462 | 0.00046663 | 1.515e-06
2013-01-30 | 290764 | HTN24A | URBAN | Vegetation | 29.37 | 257 | 7548.09 | 0.0076237 | 2.9664e-05
2013-01-30 | 290765 | CBW11 | RURAL | Other | 9.9 | 744 | 7365.6 | 0.0212 | 2.8495e-05
2013-01-30 | 290768 | LTA4B | URBAN | Weather | 43.56 | 486 | 21170.16 | 0.021382 | 4.3996e-05
2013-01-30 | 290771 | MFD2A | URBAN | Other | 48.18 | 675 | 32521.5 | 0.032847 | 4.8662e-05
2013-01-30 | 290773 | GBG27 | URBAN | Other | 4.96 | 1329 | 6591.84 | 0.0066579 | 5.0097e-06
2013-01-30 | 290775 | PPE16A | RURAL | Vegetation | 10 | 4205 | 42050 | 0.12103 | 2.8782e-05
2013-01-30 | 290782 | SBH6 | URBAN | Other | 60.06 | 747 | 44864.82 | 0.045314 | 6.0661e-05
2013-01-30 | 290826 | LRE8A | RURAL | Other | 7.26 | 110 | 798.6 | 0.0022986 | 2.0896e-05
2013-01-30 | 290862 | GYM7A | RURAL | Other | 7.26 | 303 | 2199.78 | 0.0063315 | 2.0896e-05
2013-01-30 | 290872 | MGP4 | RURAL | Vegetation | 3 | 984 | 2952 | 0.0084966 | 8.6347e-06
2013-01-30 | 290873 | MLY3 | RURAL | Other | 4.95 | 398 | 1970.1 | 0.0056704 | 1.4247e-05
2013-01-30 | 290877 | AGT31A | RURAL | Other | 10.56 | 711 | 7508.16 | 0.02161 | 3.0394e-05
2013-01-30 | 290886 | MTB15A | RURAL | Weather | 13.5 | 1441 | 19453.5 | 0.055992 | 3.8856e-05
2013-01-30 | 290900 | KMR17B | URBAN | Vegetation | 43.56 | 94 | 4094.64 | 0.0041356 | 4.3996e-05
2013-01-30 | 290902 | NMK26 | URBAN | Equipment failure | 93 | 936 | 87048 | 0.08792 | 9.3931e-05
2013-01-30 | 290911 | DRA1A | URBAN | Weather | 44.22 | 826 | 36525.72 | 0.036891 | 4.4663e-05
2013-01-30 | 290913 | PWC3 | RURAL | Vegetation | 13 | 1531 | 19903 | 0.057286 | 3.7417e-05
2013-01-30 | 290926 | BMT1 | RURAL | Vegetation | 1 | 1781 | 1781 | 0.0051261 | 2.8782e-06
2013-01-30 | 290932 | NRG10 | URBAN | Equipment failure | 12 | 2206 | 26472 | 0.026737 | 1.212e-05
2013-01-30 | 290936 | STL1A | URBAN | Weather | 130.02 | 422 | 54868.44 | 0.055418 | 0.00013132
2013-01-30 | 290937 | PWC6 | RURAL | Weather | 11.5 | 1661 | 19101.5 | 0.054979 | 3.31e-05
2013-01-30 | 290939 | ACR5 | RURAL | Animals | 28.38 | 796 | 22590.48 | 0.065021 | 8.1684e-05
2013-01-30 | 290940 | PWC6 | RURAL | Weather | 15 | 19 | 285 | 0.0008203 | 4.3174e-05
2013-01-30 | 290945 | TRG3 | URBAN | Vegetation | 58.41 | 1206 | 70442.46 | 0.071148 | 5.8995e-05
2013-01-30 | 290946 | PWC4 | RURAL | Weather | 21.5 | 209 | 4493.5 | 0.012933 | 6.1882e-05
2013-01-30 | 290951 | SMF1B | RURAL | Animals | 19.14 | 966 | 18489.24 | 0.053216 | 5.5089e-05
2013-01-30 | 290956 | KMR22A | URBAN | Other | 7.0928 | 1517 | 10759.7776 | 0.010868 | 7.1638e-06
2013-01-30 | 290957 | IDY6A | URBAN | Vegetation | 75.9 | 466 | 35369.4 | 0.035724 | 7.666e-05
2013-01-30 | 290963 | CLD30A | URBAN | Weather | 48.5 | 2199 | 106651.5 | 0.10772 | 4.8986e-05
2013-01-30 | 290964 | NBR5 | RURAL | Other | 26 | 195 | 5070 | 0.014593 | 7.4834e-05
2013-01-30 | 290965 | PWC3 | RURAL | Other | 4.33 | 1727 | 7477.91 | 0.021523 | 1.2463e-05
2013-01-30 | 291035 | CPB2 | URBAN | Weather | 21.75 | 366 | 7960.5 | 0.0080402 | 2.1968e-05
2013-01-30 | 291039 | VPT3A | RURAL | Weather | 42 | 2080 | 87360 | 0.25144 | 0.00012089
2013-01-30 | 291267 | GYGGYS6 | RURAL | Weather | 15 | 227 | 3405 | 0.0098004 | 4.3174e-05
2013-01-30 | 291431 | SMF1B | RURAL | Weather | 29 | 39 | 1131 | 0.0032553 | 8.3469e-05
2013-01-30 | 291433 | TGP5B | URBAN | Equipment failure | 9.5 | 106 | 1007 | 0.0010171 | 9.5951e-06
2013-01-30 | 291452 | KCY2 | RURAL | Weather | 3 | 185 | 555 | 0.0015974 | 8.6347e-06
2013-01-30 | 291454 | WNM6 | URBAN | Weather | 139 | 164 | 22796 | 0.023024 | 0.00014039
2013-01-30 | 291456 | TRG2A | URBAN | Weather | 417.67 | 12 | 5012.04 | 0.0050622 | 0.00042185
2013-01-30 | 291457 | WNM7A | URBAN | Weather | 19.6 | 200 | 3920 | 0.0039593 | 1.9796e-05
2013-01-30 | 291458 | BIS12B | RURAL | Weather | 31 | 260 | 8060 | 0.023199 | 8.9225e-05
2013-01-30 | 291460 | WNM2A | URBAN | Equipment failure | 5.7 | 319 | 1818.3 | 0.0018365 | 5.7571e-06
2013-01-30 | 291462 | WNM7A | URBAN | Weather | 6 | 285 | 1710 | 0.0017271 | 6.0601e-06
2013-01-30 | 291464 | BYOTR1H | URBAN | Weather | 29.5 | 320 | 9440 | 0.0095345 | 2.9795e-05
2013-01-30 | 291467 | BGY5A | RURAL | Weather | 21 | 156 | 3276 | 0.0094291 | 6.0443e-05
2013-01-30 | 291470 | BIS2B | RURAL | Weather | 147 | 160 | 23520 | 0.067696 | 0.0004231
2013-01-30 | 291471 | SMF6A | RURAL | Weather | 9 | 21 | 189 | 0.00054399 | 2.5904e-05
2013-01-30 | 291472 | MLY1 | RURAL | Weather | 7 | 17 | 119 | 0.00034251 | 2.0148e-05
2013-01-30 | 291476 | MLY4 | RURAL | Weather | 3.9 | 177 | 690.3 | 0.0019868 | 1.1225e-05
2013-01-30 | 291531 | RCF7A | URBAN | Weather | 61 | 428 | 26108 | 0.026369 | 6.1611e-05
2013-01-30 | 291534 | TWG19 | URBAN | Equipment failure | 25.08 | 687 | 17229.96 | 0.017403 | 2.5331e-05
2013-01-30 | 291540 | MTB3A | RURAL | Equipment failure | 110 | 104 | 11440 | 0.032927 | 0.00031661
2013-01-30 | 291634 | 1129 | URBAN | Weather | 62 | 1724 | 106888 | 0.10796 | 6.2621e-05
2013-01-30 | 291663 | HPK3A | URBAN | Weather | 76.5 | 52 | 3978 | 0.0040178 | 7.7266e-05
2013-01-30 | 291671 | HPE13A | URBAN | Weather | 84.5 | 56 | 4732 | 0.0047794 | 8.5346e-05
2013-01-30 | 291711 | BWH12A | RURAL | Weather | 4 | 1091 | 4364 | 0.012561 | 1.1513e-05
2013-01-30 | 291777 | NBR10 | URBAN | Weather | 14 | 2340 | 32760 | 0.033088 | 1.414e-05
2013-01-30 | 292793 | KBN5A | RURAL | Weather | 248 | 99.5714 | 23658 | 0.068093 | 0.0007138
2013-01-30 | 294192 | WSE5A | RURAL | Weather | 41 | 338 | 13858 | 0.039887 | 0.00011801
2013-01-30 | 294640 | 332 | URBAN | Equipment failure | 1 | 173 | 173 | 0.00017473 | 1.01e-06
2013-01-30 | 295190 | WFD1B | RURAL | Weather | 16 | 1263 | 20208 | 0.058163 | 4.6052e-05
2013-01-30 | 295330 | MGP13A | RURAL | Weather | 145 | 1036 | 150220 | 0.43237 | 0.00041734
2013-01-30 | 295349 | BWH12A | RURAL | Weather | 648.28 | 98 | 63531.44 | 0.18286 | 0.0018659
2013-01-30 | 296513 | WSE3A | RURAL | Other | 4.5 | 1363 | 6133.5 | 0.017654 | 1.2952e-05
2013-01-30 | 296571 | MDR4A | URBAN | Equipment failure | 7.8189 | 2403 | 18788.8167 | 0.018977 | 7.8972e-06
2013-01-31 | 289870 | BDT1 | RURAL | Equipment failure | 22.5 | 30 | 675 | 0.0019423 | 6.4743e-05
2013-01-31 | 290090 | BHD23A | RURAL | Vegetation | 225 | 27 | 6075 | 0.017481 | 0.00064743
2013-01-31 | 290110 | LHM3 | URBAN | Weather | 440 | 87 | 38280 | 0.038666 | 0.00044444
2013-01-31 | 290130 | BMT1 | RURAL | Other | 99 | 343 | 33957 | 0.09771 | 0.00028487
2013-01-31 | 290153 | MLB3A | RURAL | Equipment failure | 378 | 40 | 15120 | 0.043507 | 0.0010877
2013-01-31 | 290157 | PWC6 | RURAL | Other | 26 | 37 | 962 | 0.0027681 | 7.4814e-05
2013-01-31 | 290162 | SPD29A | URBAN | Equipment failure | 64 | 156 | 9984 | 0.010085 | 6.4645e-05
2013-01-31 | 290172 | PWC3 | RURAL | Vegetation | 21 | 175 | 3675 | 0.010575 | 6.0426e-05
2013-01-31 | 290250 | YDA1B | RURAL | Equipment failure | 179 | 272 | 48688 | 0.1401 | 0.00051506
2013-01-31 | 290270 | GYN6A | RURAL | Other | 94 | 95 | 8930 | 0.025696 | 0.00027048
2013-01-31 | 290311 | MTB17A | RURAL | Weather | 2 | 1509 | 3018 | 0.0086841 | 5.7549e-06
2013-01-31 | 290652 | LHM3 | URBAN | Weather | 75 | 548 | 41100 | 0.041514 | 7.5756e-05
2013-01-31 | 290679 | MTB13A | RURAL | Weather | 35 | 400 | 14000 | 0.040284 | 0.00010071
2013-01-31 | 290681 | MTB13A | RURAL | Weather | 42 | 277 | 11634 | 0.033476 | 0.00012085
2013-01-31 | 290686 | MAI5 | URBAN | Equipment failure | 137.5 | 35 | 4812.5 | 0.004861 | 0.00013889
2013-01-31 | 290689 | LTA4B | URBAN | Weather | 21.78 | 154 | 3354.12 | 0.0033879 | 2.2e-05
2013-01-31 | 290701 | CPR6 | URBAN | Equipment failure | 311 | 257 | 79927 | 0.080733 | 0.00031413
2013-01-31 | 290709 | CHL3 | URBAN | Weather | 108 | 135 | 14580 | 0.014727 | 0.00010909
2013-01-31 | 290710 | MTB13A | RURAL | Weather | 3.5 | 228 | 798 | 0.0022962 | 1.0071e-05
2013-01-31 | 290712 | EMP21A | RURAL | Weather | 8.58 | 845 | 7250.1 | 0.020862 | 2.4689e-05
2013-01-31 | 290727 | BLN2B | URBAN | Animals | 37.95 | 866 | 32864.7 | 0.033196 | 3.8333e-05
2013-01-31 | 290745 | WRD15B | URBAN | Other | 54.5 | 431 | 23489.5 | 0.023726 | 5.5049e-05
2013-01-31 | 290748 | NMC15A | RURAL | Equipment failure | 11 | 617 | 6787 | 0.019529 | 3.1652e-05
2013-01-31 | 290757 | RBY9A | URBAN | Equipment failure | 58.5 | 640 | 37440 | 0.037817 | 5.909e-05
2013-01-31 | 290776 | NGI1B | RURAL | Equipment failure | 6.27 | 119 | 746.13 | 0.002147 | 1.8042e-05
2013-01-31 | 290778 | NRA1A | RURAL | Weather | 0.33 | 147 | 48.51 | 0.00013959 | 9.4956e-07
2013-01-31 | 290779 | HMT10A | URBAN | Other | 1 | 90 | 90 | 9.0907e-05 | 1.0101e-06
2013-01-31 | 290784 | TGP5B | URBAN | Vegetation | 17 | 56 | 952 | 0.0009616 | 1.7171e-05
2013-01-31 | 290786 | GBG27 | URBAN | Equipment failure | 4.96 | 67 | 332.32 | 0.00033567 | 5.01e-06
2013-01-31 | 290789 | CBW12 | URBAN | Other | 222.17 | 68 | 15107.56 | 0.01526 | 0.00022441
2013-01-31 | 290792 | SGT24A | URBAN | Vegetation | 13.695 | 90 | 1232.55 | 0.001245 | 1.3833e-05
2013-01-31 | 290794 | KCY4 | RURAL | Other | 3 | 114 | 342 | 0.00098409 | 8.6324e-06
2013-01-31 | 290796 | WSE5A | RURAL | Weather | 1.815 | 129 | 234.135 | 0.00067371 | 5.2226e-06
2013-01-31 | 290797 | MHL2A | URBAN | Vegetation | 6.5 | 94 | 611 | 0.00061716 | 6.5655e-06
2013-01-31 | 290799 | HDA14A | URBAN | Operational error | 2.035 | 96 | 195.36 | 0.00019733 | 2.0555e-06
2013-01-31 | 290800 | GBG27 | URBAN | Other | 4.96 | 80 | 396.8 | 0.0004008 | 5.01e-06
2013-01-31 | 290801 | BHL5A | URBAN | Equipment failure | 40.59 | 64 | 2597.76 | 0.0026239 | 4.0999e-05
2013-01-31 | 290802 | LTA5 | URBAN | Other | 68.64 | 283 | 19425.12 | 0.019621 | 6.9332e-05
2013-01-31 | 290803 | BIS12B | RURAL | Equipment failure | 20.46 | 88 | 1800.48 | 0.0051808 | 5.8873e-05
2013-01-31 | 290883 | MTB13A | RURAL | Other | 41 | 420 | 17220 | 0.04955 | 0.00011798
2013-01-31 | 290890 | PBH6 | URBAN | Other | 75 | 34 | 2550 | 0.0025757 | 7.5756e-05
2013-01-31 | 290891 | PBH6 | URBAN | Equipment failure | 244 | 414 | 101016 | 0.10203 | 0.00024646
2013-01-31 | 290892 | MAI7 | URBAN | Weather | 139 | 443 | 61577 | 0.062198 | 0.0001404
2013-01-31 | 290894 | CRY6A | RURAL | Vegetation | 17 | 183 | 3111 | 0.0089518 | 4.8917e-05
2013-01-31 | 290895 | MTB13A | RURAL | Other | 14.5 | 259 | 3755.5 | 0.010806 | 4.1723e-05
2013-01-31 | 290896 | CLD28A | RURAL | Other | 65.5 | 204 | 13362 | 0.038449 | 0.00018847
2013-01-31 | 290898 | AHD8 | URBAN | Other | 74 | 173 | 12802 | 0.012931 | 7.4746e-05
2013-01-31 | 290899 | NRG9 | RURAL | Weather | 10 | 249 | 2490 | 0.0071649 | 2.8775e-05
2013-01-31 | 290903 | BHD35A | RURAL | Animals | 21 | 66 | 1386 | 0.0039881 | 6.0426e-05
2013-01-31 | 290904 | AHD18A | URBAN | Other | 98 | 213 | 20874 | 0.021084 | 9.8988e-05
2013-01-31 | 290919 | NVL8B | URBAN | Weather | 21 | 437 | 9177 | 0.0092695 | 2.1212e-05
2013-01-31 | 290935 | SPO16A | URBAN | Other | 73 | 655 | 47815 | 0.048297 | 7.3736e-05
2013-01-31 | 290941 | JBB2A | RURAL | Equipment failure | 11 | 1017 | 11187 | 0.03219 | 3.1652e-05
2013-01-31 | 290943 | PWC4 | RURAL | Equipment failure | 21 | 26 | 546 | 0.0015711 | 6.0426e-05
2013-01-31 | 290950 | SHW3 | URBAN | Weather | 9.6 | 211 | 2025.6 | 0.002046 | 9.6968e-06
2013-01-31 | 290960 | BMT1 | RURAL | Equipment failure | 1 | 36 | 36 | 0.00010359 | 2.8775e-06
2013-01-31 | 290962 | NBR1 | RURAL | Weather | 12 | 763 | 9156 | 0.026346 | 3.4529e-05
2013-01-31 | 290966 | BWH12A | RURAL | Equipment failure | 12 | 866 | 10392 | 0.029902 | 3.4529e-05
2013-01-31 | 290967 | BWH13A | RURAL | Other | 20 | 673 | 13460 | 0.038731 | 5.7549e-05
2013-01-31 | 290968 | NMK10 | URBAN | Operational error | 25 | 285 | 7125 | 0.0071968 | 2.5252e-05
2013-01-31 | 290969 | BWH12A | RURAL | Other | 5 | 223 | 1115 | 0.0032084 | 1.4387e-05
2013-01-31 | 290971 | AGE5B | URBAN | Weather | 118 | 1042 | 122956 | 0.1242 | 0.00011919
2013-01-31 | 290973 | KMR25A | RURAL | Vegetation | 8.58 | 623 | 5345.34 | 0.015381 | 2.4689e-05
2013-01-31 | 290978 | KMR25A | RURAL | Other | 6 | 888 | 5328 | 0.015331 | 1.7265e-05
2013-01-31 | 290982 | MGL2A | RURAL | Other | 18 | 550 | 9900 | 0.028487 | 5.1794e-05
2013-01-31 | 291274 | KSN2A | RURAL | Weather | 17 | 65 | 1105 | 0.0031796 | 4.8917e-05
2013-01-31 | 291292 | THL3 | RURAL | Weather | 8.5 | 221 | 1878.5 | 0.0054053 | 2.4458e-05
2013-01-31 | 291311 | NSW17 | URBAN | Weather | 14 | 81 | 1134 | 0.0011454 | 1.4141e-05
2013-01-31 | 291316 | BPN26A | RURAL | Weather | 16.5 | 178 | 2937 | 0.0084511 | 4.7478e-05
2013-01-31 | 291324 | VPT16A | URBAN | Equipment failure | 82.5 | 78 | 6435 | 0.0064999 | 8.3332e-05
2013-01-31 | 291400 | CVL9A | URBAN | Weather | 11.8 | 390 | 4602 | 0.0046484 | 1.1919e-05
2013-01-31 | 291661 | ACR2A | URBAN | Equipment failure | 33 | 107 | 3531 | 0.0035666 | 3.3333e-05
2013-01-31 | 291662 | MGL1A | RURAL | Weather | 26 | 249 | 6474 | 0.018629 | 7.4814e-05
2013-01-31 | 291664 | STL1A | URBAN | Weather | 39.4 | 784 | 30889.6 | 0.031201 | 3.9797e-05
2013-01-31 | 291668 | CSE6 | URBAN | Equipment failure | 117.33 | 176 | 20650.08 | 0.020858 | 0.00011851
2013-01-31 | 291669 | WNM7A | URBAN | Equipment failure | 18.566 | 56 | 1039.696 | 0.0010502 | 1.8753e-05
2013-01-31 | 291670 | MLY1 | RURAL | Weather | 1 | 124 | 124 | 0.0003568 | 2.8775e-06
2013-01-31 | 291674 | TRG3 | URBAN | Weather | 43.5 | 72 | 3132 | 0.0031636 | 4.3938e-05
2013-01-31 | 291690 | WNM7A | URBAN | Equipment failure | 3.4 | 172 | 584.8 | 0.00059069 | 3.4343e-06
2013-01-31 | 291712 | STL3 | URBAN | Weather | 90 | 303 | 27270 | 0.027545 | 9.0907e-05
2013-01-31 | 291713 | CPL3A | URBAN | Equipment failure | 3.25 | 2048 | 6656 | 0.0067231 | 3.2828e-06
2013-01-31 | 291731 | WED21B | URBAN | Weather | 47.1 | 301 | 14177.1 | 0.01432 | 4.7575e-05
2013-01-31 | 291751 | MRK9 | URBAN | Vegetation | 31.5 | 128 | 4032 | 0.0040726 | 3.1818e-05
2013-01-31 | 291771 | BMT1 | RURAL | Weather | 1 | 208 | 208 | 0.00059851 | 2.8775e-06
2013-01-31 | 291772 | DRA13A | URBAN | Equipment failure | 3 | 120 | 360 | 0.00036363 | 3.0302e-06
2013-01-31 | 291773 | MLB8A | RURAL | Weather | 19 | 13 | 247 | 0.00071073 | 5.4672e-05
2013-01-31 | 291775 | CRY6A | RURAL | Equipment failure | 13 | 39 | 507 | 0.0014589 | 3.7407e-05
2013-01-31 | 291776 | ALY8 | URBAN | Weather | 18.8 | 73 | 1372.4 | 0.0013862 | 1.899e-05
2013-01-31 | 291790 | HPE3A | URBAN | Equipment failure | 109.5 | 20 | 2190 | 0.0022121 | 0.0001106
2013-01-31 | 291810 | WSO3A | URBAN | Weather | 1 | 49 | 49 | 4.9494e-05 | 1.0101e-06
2013-01-31 | 291813 | HPK8A | URBAN | Weather | 13.8 | 169 | 2332.2 | 0.0023557 | 1.3939e-05
2013-01-31 | 291833 | BMT1 | RURAL | Weather | 3 | 488 | 1464 | 0.0042126 | 8.6324e-06
2013-01-31 | 291834 | NBR6 | RURAL | Equipment failure | 15.33 | 177 | 2713.41 | 0.0078077 | 4.4111e-05
2013-01-31 | 291835 | PWC5 | RURAL | Equipment failure | 16 | 259 | 4144 | 0.011924 | 4.6039e-05
2013-01-31 | 291917 | IDY9B | URBAN | Weather | 3 | 258 | 774 | 0.0007818 | 3.0302e-06
2013-01-31 | 291917 | TRG10B | URBAN | Weather | 290 | 258 | 74820 | 0.075574 | 0.00029292
2013-01-31 | 291917 | TRG3 | URBAN | Weather | 57 | 258 | 14706 | 0.014854 | 5.7575e-05
2013-01-31 | 293285 | MTB17A | RURAL | Weather | 13.5 | 336 | 4536 | 0.013052 | 3.8846e-05
2013-02-01 | 290163 | CSE23A | URBAN | Animals | 134.75 | 164.8333 | 30794.25 | 0.031106 | 0.00013612
2013-02-01 | 290371 | MLY3 | RURAL | Other | 78 | 131 | 10218 | 0.029394 | 0.00022438
2013-02-01 | 290410 | CVL17A | URBAN | Weather | 131.5 | 17 | 2235.5 | 0.0022582 | 0.00013283
2013-02-01 | 290430 | SFD9 | URBAN | Equipment failure | 862 | 126.7692 | 93517 | 0.094465 | 0.00087074
2013-02-01 | 290451 | BWH12A | RURAL | Equipment failure | 5 | 603 | 3015 | 0.0086731 | 1.4383e-05
2013-02-01 | 290511 | GYN3A | RURAL | Vegetation | 677 | 163 | 110351 | 0.31744 | 0.0019475
2013-02-01 | 290514 | WMD8B | RURAL | Other | 30.25 | 59 | 1784.75 | 0.0051341 | 8.7019e-05
2013-02-01 | 290531 | GYN3A | RURAL | Other | 33.5 | 50 | 1675 | 0.0048184 | 9.6368e-05
2013-02-01 | 290532 | BKD12A | URBAN | Weather | 86.5 | 16 | 1384 | 0.001398 | 8.7377e-05
2013-02-01 | 290534 | BMT2 | RURAL | Other | 18.5 | 46 | 851 | 0.002448 | 5.3218e-05
2013-02-01 | 290550 | KCY5 | RURAL | Equipment failure | 100 | 236.5652 | 22171 | 0.063778 | 0.00028767
2013-02-01 | 290574 | MMC28A | URBAN | Equipment failure | 2.5 | 57 | 142.5 | 0.00014394 | 2.5253e-06
2013-02-01 | 290575 | KWH2 | RURAL | Other | 10 | 980 | 9800 | 0.028191 | 2.8767e-05
2013-02-01 | 290577 | LGV6A | RURAL | Equipment failure | 148 | 12 | 1776 | 0.0051089 | 0.00042575
2013-02-01 | 290591 | GBN4 | RURAL | Equipment failure | 12 | 17 | 204 | 0.00058684 | 3.452e-05
2013-02-01 | 290592 | MBG4 | RURAL | Weather | 448.5 | 58 | 26013 | 0.07483 | 0.0012902
2013-02-01 | 290593 | RBA43A | RURAL | Weather | 1015 | 79 | 80185 | 0.23066 | 0.0029198
2013-02-01 | 290594 | TTF81 | URBAN | Weather | 511.5 | 71 | 36316.5 | 0.036685 | 0.00051669
2013-02-01 | 290595 | TRP2 | RURAL | Animals | 157.58 | 121 | 19067.18 | 0.05485 | 0.0004533
2013-02-01 | 290596 | MRK3 | URBAN | Weather | 1204 | 72 | 86688 | 0.087567 | 0.0012162
2013-02-01 | 290597 | TMH15A | URBAN | Weather | 1722.5 | 55.9206 | 191534.5 | 0.19348 | 0.00174
2013-02-01 | 290598 | BDB27A | RURAL | Weather | 976.5 | 41.4444 | 82652 | 0.23776 | 0.0028091
2013-02-01 | 290600 | KLG5A | RURAL | Weather | 1165.66 | 106.2353 | 110007.33 | 0.31645 | 0.0033532
2013-02-01 | 290620 | GGR2 | RURAL | Weather | 39 | 725 | 28275 | 0.081337 | 0.00011219
2013-02-01 | 290665 | MTB13A | RURAL | Weather | 36 | 685 | 24660 | 0.070938 | 0.00010356
2013-02-01 | 290666 | MTB13A | RURAL | Weather | 106 | 640 | 67840 | 0.19515 | 0.00030493
2013-02-01 | 290670 | MTB16A | RURAL | Weather | 6.33 | 152 | 962.16 | 0.0027678 | 1.8209e-05
2013-02-01 | 290760 | NMC2A | RURAL | Animals | 13.2 | 166 | 2191.2 | 0.0063033 | 3.7972e-05
2013-02-01 | 290761 | RLB12B | RURAL | Vegetation | 16.5 | 95 | 1567.5 | 0.0045092 | 4.7465e-05
2013-02-01 | 290766 | BKD3A | URBAN | Other | 84 | 87 | 7308 | 0.0073821 | 8.4852e-05
2013-02-01 | 290767 | CRM16A | RURAL | Equipment failure | 14.33 | 274 | 3926.42 | 0.011295 | 4.1222e-05
2013-02-01 | 290770 | MRK7A | URBAN | Equipment failure | 26 | 554 | 14404 | 0.01455 | 2.6264e-05
2013-02-01 | 290772 | CMA8A | RURAL | Equipment failure | 1 | 700 | 700 | 0.0020137 | 2.8767e-06
2013-02-01 | 290774 | WRD20A | URBAN | Equipment failure | 69 | 683 | 47127 | 0.047605 | 6.97e-05
2013-02-01 | 290777 | CRM16A | RURAL | Weather | 11 | 1066 | 11726 | 0.033732 | 3.1643e-05
2013-02-01 | 290804 | RCF5A | URBAN | Weather | 10.56 | 107 | 1129.92 | 0.0011414 | 1.0667e-05
2013-02-01 | 290840 | GTN13A | RURAL | Other | 14.5 | 146 | 2117 | 0.0060899 | 4.1712e-05
2013-02-01 | 290841 | RBK11B | URBAN | Vegetation | 56 | 86 | 4816 | 0.0048648 | 5.6568e-05
2013-02-01 | 290949 | BBH13B | URBAN | Weather | 62.08 | 36 | 2234.88 | 0.0022575 | 6.2709e-05
2013-02-01 | 290952 | MTB1B | RURAL | Weather | 12 | 499 | 5988 | 0.017225 | 3.452e-05
2013-02-01 | 290955 | BHD35A | RURAL | Equipment failure | 3 | 1170 | 3510 | 0.010097 | 8.63e-06
2013-02-01 | 290972 | GBN3 | RURAL | Other | 1 | 199 | 199 | 0.00057245 | 2.8767e-06
2013-02-01 | 290974 | BWH8A | RURAL | Vegetation | 4 | 26 | 104 | 0.00029917 | 1.1507e-05
2013-02-01 | 290979 | STPT1 | URBAN | Equipment failure | 153.5 | 148 | 22718 | 0.022948 | 0.00015506
2013-02-01 | 290980 | MGL9 | RURAL | Vegetation | 20 | 404 | 8080 | 0.023243 | 5.7533e-05
2013-02-01 | 290981 | SMF5A | RURAL | Vegetation | 16.5 | 278 | 4587 | 0.013195 | 4.7465e-05
2013-02-01 | 291142 | IPS13A | RURAL | Equipment failure | 1.5 | 2580 | 3870 | 0.011133 | 4.315e-06
2013-02-01 | 291346 | NSW17 | URBAN | Equipment failure | 44 | 43 | 1892 | 0.0019112 | 4.4446e-05
2013-02-01 | 291665 | GBG27 | URBAN | Equipment failure | 7.75 | 947 | 7339.25 | 0.0074137 | 7.8286e-06
2013-02-01 | 291710 | MGL9 | RURAL | Weather | 5.5 | 43 | 236.5 | 0.00068033 | 1.5822e-05
2013-02-01 | 291714 | NMK23A | URBAN | Equipment failure | 34.98 | 368 | 12872.64 | 0.013003 | 3.5335e-05
2013-02-01 | 291715 | MLS26B | URBAN | Weather | 6.9 | 114 | 786.6 | 0.00079457 | 6.97e-06
2013-02-01 | 291716 | CLD22A | URBAN | Equipment failure | 4.1516 | 133 | 552.1628 | 0.00055776 | 4.1937e-06
2013-02-01 | 291719 | ENG2 | URBAN | Equipment failure | 26.8 | 145 | 3886 | 0.0039254 | 2.7072e-05
2013-02-01 | 291730 | NMK23A | URBAN | Weather | 10.7 | 25 | 267.5 | 0.00027021 | 1.0808e-05
2013-02-01 | 291774 | CRY2A | RURAL | Equipment failure | 9 | 107 | 963 | 0.0027702 | 2.589e-05
2013-02-01 | 291830 | CHL2 | URBAN | Weather | 92 | 27 | 2484 | 0.0025092 | 9.2933e-05
2013-02-01 | 291831 | DRA6 | URBAN | Weather | 55.5 | 50 | 2775 | 0.0028031 | 5.6063e-05
2013-02-01 | 291836 | BMT2 | RURAL | Weather | 6 | 31 | 186 | 0.00053506 | 1.726e-05
2013-02-01 | 291920 | BDT5 | RURAL | Equipment failure | 8 | 30 | 240 | 0.0006904 | 2.3013e-05
2013-02-02 | 290599 | MAI13 | URBAN | Third party impacts | 1776.6 | 115.48 | 186943.7 | 0.18885 | 0.0017947
2013-02-02 | 290606 | GYN3A | RURAL | Equipment failure | 195.51 | 54 | 10557.54 | 0.030362 | 0.00056226
2013-02-02 | 290607 | WMR1 | RURAL | Vegetation | 194 | 50 | 9700 | 0.027896 | 0.00055791
2013-02-02 | 290714 | TRG10B | URBAN | Vegetation | 505.5 | 50 | 25275 | 0.025533 | 0.00051065
2013-02-02 | 290716 | MGP4 | RURAL | Other | 3 | 366 | 1098 | 0.0031577 | 8.6275e-06
2013-02-02 | 290739 | EMP4A | URBAN | Vegetation | 337.5 | 19 | 6412.5 | 0.0064779 | 0.00034094
2013-02-02 | 290805 | WFD6A | RURAL | Vegetation | 10.56 | 273 | 2882.88 | 0.0082907 | 3.0369e-05
2013-02-02 | 290813 | EMP21A | RURAL | Vegetation | 154 | 60 | 9240 | 0.026573 | 0.00044288
2013-02-02 | 290842 | HDN1 | RURAL | Weather | 7 | 68.3333 | 478.3333 | 0.0013756 | 2.0131e-05
2013-02-02 | 290843 | WHO1 | RURAL | Weather | 3 | 8 | 24 | 6.902e-05 | 8.6275e-06
2013-02-02 | 290870 | YDA5A | RURAL | Weather | 357.99 | 222.1471 | 76231.23 | 0.21923 | 0.0010295
2013-02-02 | 290887 | SPC2B | RURAL | Other | 89.99 | 342 | 30776.58 | 0.088509 | 0.0002588
2013-02-02 | 290958 | CRB25A | RURAL | Other | 16.33 | 107 | 1747.31 | 0.005025 | 4.6963e-05
2013-02-02 | 290975 | WMD3A | URBAN | Equipment failure | 2 | 50 | 100 | 0.00010102 | 2.0204e-06
2013-02-02 | 290976 | BWH13A | RURAL | Weather | 0.5 | 88 | 44 | 0.00012654 | 1.4379e-06
2013-02-02 | 290977 | CLD11 | RURAL | Other | 5 | 244 | 1220 | 0.0035085 | 1.4379e-05
2013-02-02 | 290990 | CFD6A | URBAN | Equipment failure | 105.5 | 115 | 12132.5 | 0.012256 | 0.00010658
2013-02-02 | 291188 | TWG15A | URBAN | Equipment failure | 19.35 | 39 | 754.65 | 0.00076234 | 1.9547e-05
2013-02-02 | 291198 | BLB2A | URBAN | Other | 56.83 | 336 | 19094.88 | 0.019289 | 5.7409e-05
2013-02-02 | 291218 | JBB2A | RURAL | Weather | 6 | 313.8333 | 1883 | 0.0054152 | 1.7255e-05
2013-02-02 | 291219 | RLB15A | URBAN | Other | 99.5 | 64.1667 | 6384.5833 | 0.0064497 | 0.00010051
2013-02-02 | 291220 | BHD31A | URBAN | Weather | 43 | 103.6667 | 4457.6667 | 0.0045031 | 4.3438e-05
2013-02-02 | 291453 | CVL3A | URBAN | Equipment failure | 81 | 66 | 5346 | 0.0054005 | 8.1826e-05
2013-02-02 | 293792 | BKD3A | URBAN | Equipment failure | 74 | 73 | 5402 | 0.0054571 | 7.4754e-05
2013-02-03 | 290991 | TWG15A | URBAN | Equipment failure | 64.5 | 39 | 2515.5 | 0.0025412 | 6.516e-05
2013-02-03 | 290995 | GTN15A | RURAL | Other | 62 | 3 | 186 | 0.00053483 | 0.00017828
2013-02-03 | 290998 | KLG17A | URBAN | Animals | 45 | 57 | 2565 | 0.0025912 | 4.546e-05
2013-02-03 | 291000 | WNM5 | URBAN | Animals | 73.59 | 104 | 7653.36 | 0.0077317 | 7.4343e-05
2013-02-03 | 291138 | MMC19B | URBAN | Third party impacts | 6.5 | 75 | 487.5 | 0.00049249 | 6.5665e-06
2013-02-03 | 291149 | CDRSPD9 | URBAN | Equipment failure | 49 | 233 | 11417 | 0.011534 | 4.9501e-05
2013-02-03 | 291164 | ZMR5 | URBAN | Equipment failure | 12.1 | 52 | 629.2 | 0.00063564 | 1.2224e-05
2013-02-03 | 291229 | ALY6 | URBAN | Other | 788.16 | 16 | 12610.56 | 0.01274 | 0.00079623
2013-02-03 | 291230 | EMD2 | RURAL | Other | 110 | 16 | 1760 | 0.0050607 | 0.0003163
2013-02-03 | 291237 | MLT2B | URBAN | Animals | 359.5 | 92.75 | 30908.5 | 0.031225 | 0.00036318
2013-02-03 | 291650 | CPB5 | URBAN | Equipment failure | 39.83 | 679 | 27044.57 | 0.027321 | 4.0238e-05
2013-02-04 | 291244 | CFD2A | URBAN | Other | 23.7 | 258 | 6114.6 | 0.0061774 | 2.3943e-05
2013-02-04 | 291352 | AHD10A | URBAN | Third party impacts | 112.67 | 47 | 5295.49 | 0.0053499 | 0.00011383
2013-02-04 | 291359 | BMT2 | RURAL | Animals | 4 | 50 | 200 | 0.00057483 | 1.1497e-05
2013-02-04 | 291367 | RCF9A | URBAN | Other | 1367.58 | 17 | 23248.86 | 0.023488 | 0.0013816
2013-02-04 | 291404 | MLB12A | RURAL | Other | 1596 | 46.8378 | 82526 | 0.23719 | 0.0045871
2013-02-04 | 291459 | MAI13 | URBAN | Equipment failure | 1776.6 | 123.36 | 222770.8 | 0.22506 | 0.0017948
2013-02-04 | 291490 | JBB1B | RURAL | Vegetation | 160 | 93 | 14880 | 0.042767 | 0.00045986
2013-02-04 | 291535 | CBW10 | RURAL | Equipment failure | 37 | 55 | 2035 | 0.0058489 | 0.00010634
2013-02-04 | 291590 | TRP2 | RURAL | Other | 45.51 | 83 | 3777.33 | 0.010857 | 0.0001308
2013-02-04 | 291639 | ALY5 | URBAN | Other | 1118 | 41 | 45838 | 0.046309 | 0.0011295
2013-02-04 | 291641 | IBL2 | RURAL | Equipment failure | 8 | 313 | 2504 | 0.0071969 | 2.2993e-05
2013-02-04 | 291645 | RPN6A | RURAL | Weather | 789.66 | 168 | 132662.88 | 0.38129 | 0.0022696
2013-02-04 | 291646 | NMC1B | RURAL | Weather | 71 | 50 | 3550 | 0.010203 | 0.00020406
2013-02-04 | 291647 | DBY11 | URBAN | Animals | 15.18 | 60 | 910.8 | 0.00092015 | 1.5336e-05
2013-02-04 | 291648 | BLB8B | URBAN | Animals | 36.63 | 102 | 3736.26 | 0.0037746 | 3.7006e-05
2013-02-04 | 291649 | CPB3 | URBAN | Animals | 29 | 26 | 754 | 0.00076174 | 2.9298e-05
2013-02-04 | 291652 | NMC3A | RURAL | Equipment failure | 1.32 | 134 | 176.88 | 0.00050838 | 3.7939e-06
2013-02-04 | 291653 | CPB9 | URBAN | Animals | 33.66 | 47 | 1582.02 | 0.0015983 | 3.4006e-05
2013-02-04 | 291654 | KBN5A | RURAL | Other | 7 | 82 | 574 | 0.0016498 | 2.0119e-05
2013-02-04 | 291655 | RBA4A | URBAN | Other | 15.3 | 181 | 2769.3 | 0.0027977 | 1.5457e-05
2013-02-04 | 292452 | BDT4 | RURAL | Other | 4.66 | 431 | 2008.46 | 0.0057726 | 1.3394e-05
2013-02-05 | 291718 | MTB1B | RURAL | Weather | 37.5 | 207 | 7762.5 | 0.022303 | 0.00010775
2013-02-05 | 291851 | CRM16A | RURAL | Other | 46.33 | 9 | 416.97 | 0.0011981 | 0.00013312
2013-02-05 | 291852 | HPK3A | URBAN | Vegetation | 2542.99 | 86 | 218697.14 | 0.22095 | 0.0025692
2013-02-05 | 291870 | CMD13A | URBAN | Equipment failure | 1210.5 | 59.0714 | 72129 | 0.072873 | 0.001223
2013-02-05 | 291871 | MLB12A | RURAL | Weather | 1596 | 29.1892 | 41876 | 0.12032 | 0.0045857
2013-02-05 | 291872 | MSV1 | RURAL | Weather | 64 | 29 | 1856 | 0.0053327 | 0.00018389
2013-02-05 | 291898 | GYM7A | RURAL | Other | 87 | 134 | 11658 | 0.033496 | 0.00024997
2013-02-05 | 291900 | BWH12A | RURAL | Weather | 30.4 | 200 | 6080 | 0.017469 | 8.7346e-05
2013-02-05 | 291902 | NMK5 | URBAN | Other | 66 | 55 | 3630 | 0.0036674 | 6.668e-05
2013-02-05 | 291904 | NRG9 | RURAL | Weather | 2.97 | 110 | 326.7 | 0.00093869 | 8.5335e-06
2013-02-05 | 291905 | MFD3A | RURAL | Equipment failure | 945 | 131.4444 | 101243 | 0.2909 | 0.0027152
2013-02-05 | 291909 | KWA12A | URBAN | Equipment failure | 27.06 | 178 | 4816.68 | 0.0048663 | 2.7339e-05
2013-02-05 | 296511 | CMD13A | URBAN | Other | 85.76 | 118 | 10119.68 | 0.010224 | 8.6644e-05
2013-02-06 | 291906 | LGV6A | RURAL | Weather | 531.5 | 27 | 14350.5 | 0.04122 | 0.0015267
2013-02-06 | 291908 | BHD7A | URBAN | Other | 1163.33 | 3 | 3489.99 | 0.0035261 | 0.0011754
2013-02-06 | 291911 | WSE6A | RURAL | Other | 144 | 230 | 33120 | 0.095132 | 0.00041362
2013-02-06 | 291912 | MLY3 | RURAL | Equipment failure | 515 | 219 | 112785 | 0.32396 | 0.0014793
2013-02-06 | 291919 | BHD3A | URBAN | Third party impacts | 1253 | 130 | 162890 | 0.16458 | 0.001266
2013-02-06 | 291919 | VSL3A | URBAN | Third party impacts | 247 | 99.5385 | 40840 | 0.041263 | 0.00024956
2013-02-06 | 291924 | KWA10A | URBAN | Equipment failure | 575 | 3 | 1725 | 0.0017429 | 0.00058096
2013-02-06 | 291990 | WRD9A | URBAN | Equipment failure | 584.67 | 50.25 | 42048.92 | 0.042484 | 0.00059073
2013-02-06 | 291993 | NBR5 | RURAL | Equipment failure | 1 | 66 | 66 | 0.00018958 | 2.8724e-06
2013-02-06 | 291994 | BPN3 | URBAN | Vegetation | 1953 | 20.5 | 80073 | 0.080902 | 0.0019732
2013-02-06 | 291995 | SHW4 | URBAN | Third party impacts | 100 | 103 | 10300 | 0.010407 | 0.00010104
2013-02-06 | 291997 | NBR6 | RURAL | Other | 131 | 280 | 36680 | 0.10536 | 0.00037628
2013-02-06 | 292000 | HWL2A | URBAN | Other | 58 | 35 | 2030 | 0.002051 | 5.8601e-05
2013-02-06 | 292014 | BDL2 | URBAN | Other | 35.64 | 24 | 855.36 | 0.00086422 | 3.6009e-05
2013-02-06 | 292020 | WRD9A | URBAN | Other | 9.5 | 80 | 760 | 0.00076787 | 9.5984e-06
2013-02-06 | 292022 | HPK5A | URBAN | Other | 38.5 | 121 | 4658.5 | 0.0047068 | 3.8899e-05
2013-02-06 | 292024 | ACR4 | URBAN | Animals | 63.36 | 244 | 15459.84 | 0.01562 | 6.4016e-05
2013-02-06 | 292127 | HDA10A | URBAN | Animals | 69.96 | 100.8333 | 7054.3 | 0.0071274 | 7.0685e-05
2013-02-07 | 292027 | NIP2A | URBAN | Animals | 934.5 | 174.0476 | 128474.5 | 0.12981 | 0.00094423
2013-02-07 | 292030 | JBB16A | RURAL | Animals | 12.21 | 114 | 1391.94 | 0.003997 | 3.5061e-05
2013-02-07 | 292070 | AGE3 | URBAN | Vegetation | 14.3 | 42 | 600.6 | 0.00060685 | 1.4449e-05
2013-02-07 | 292090 | WMR1 | RURAL | Weather | 54 | 114.6154 | 6174 | 0.017729 | 0.00015506
2013-02-07 | 292128 | BRD11A | RURAL | Animals | 11.22 | 136 | 1525.92 | 0.0043817 | 3.2218e-05
2013-02-07 | 292130 | SMF2A | RURAL | Animals | 1.65 | 36 | 59.4 | 0.00017057 | 4.738e-06
2013-02-07 | 292134 | SMF2A | RURAL | Vegetation | 155 | 41.5833 | 11093 | 0.031854 | 0.00044508
2013-02-07 | 292138 | MFN13A | RURAL | Other | 12.54 | 79 | 990.66 | 0.0028447 | 3.6009e-05
2013-02-07 | 292139 | BGY17A | URBAN | Animals | 40.92 | 74 | 3028.08 | 0.0030596 | 4.1346e-05
2013-02-08 | 292210 | KSN14 | URBAN | Other | 10.3 | 59 | 607.7 | 0.00061406 | 1.0408e-05
2013-02-08 | 292262 | RBY7A | URBAN | Other | 74 | 134 | 9916 | 0.01002 | 7.4775e-05
2013-02-08 | 292263 | NBR1 | RURAL | Equipment failure | 126.33 | 82 | 10359.06 | 0.029737 | 0.00036265
2013-02-08 | 292265 | 439 | URBAN | Other | 1 | 59 | 59 | 5.9618e-05 | 1.0105e-06
2013-02-08 | 292266 | SPE20A | URBAN | Vegetation | 1 | 33 | 33 | 3.3346e-05 | 1.0105e-06
2013-02-08 | 292267 | RBY7A | URBAN | Other | 48.84 | 148 | 7228.32 | 0.007304 | 4.9351e-05
2013-02-08 | 292270 | NBR10 | URBAN | Other | 18 | 3 | 54 | 5.4565e-05 | 1.8188e-05
2013-02-08 | 292271 | TRP4 | RURAL | Other | 22.3278 | 72 | 1607.6016 | 0.0046149 | 6.4096e-05
2013-02-08 | 292272 | CHL7 | URBAN | Animals | 1508.5 | 98.4167 | 137309 | 0.13875 | 0.0015243
2013-02-08 | 292298 | VPT12A | URBAN | Other | 60.6078 | 96 | 5818.3488 | 0.0058793 | 6.1242e-05
2013-02-08 | 292299 | MTG7A | URBAN | Other | 32.2278 | 202 | 6510.0156 | 0.0065782 | 3.2565e-05
2013-02-08 | 293090 | LLY3 | RURAL | Other | 4.02 | 167 | 671.34 | 0.0019272 | 1.154e-05
2013-02-09 | 292273 | BLB4A | URBAN | Animals | 51.5 | 100 | 5150 | 0.0052043 | 5.2043e-05
2013-02-09 | 292276 | KRA1 | URBAN | Animals | 591.33 | 18 | 10643.94 | 0.010756 | 0.00059756
2013-02-09 | 292276 | KRA10 | URBAN | Animals | 1083.33 | 18 | 19499.94 | 0.019705 | 0.0010947
2013-02-09 | 292276 | KRA2 | URBAN | Animals | 821.16 | 18 | 14780.88 | 0.014937 | 0.00082981
2013-02-09 | 292276 | KRA3 | URBAN | Animals | 1339.5 | 18 | 24111 | 0.024365 | 0.0013536
2013-02-09 | 292276 | KRA4 | URBAN | Animals | 289.5 | 18 | 5211 | 0.0052659 | 0.00029255
2013-02-09 | 292276 | KRA6 | URBAN | Animals | 1 | 18 | 18 | 1.819e-05 | 1.0105e-06
2013-02-09 | 292276 | KRA7 | URBAN | Animals | 1224.67 | 18 | 22044.06 | 0.022276 | 0.0012376
2013-02-09 | 292278 | BWH7A | RURAL | Vegetation | 95 | 109.6316 | 10663 | 0.030601 | 0.00027263
2013-02-09 | 292279 | NRG10 | URBAN | Other | 1444 | 3 | 4332 | 0.0043776 | 0.0014592
2013-02-09 | 292279 | NRG12A | URBAN | Other | 1318.33 | 3 | 3954.99 | 0.0039967 | 0.0013322
2013-02-09 | 292279 | NRG13A | URBAN | Other | 1448.99 | 3 | 4346.97 | 0.0043928 | 0.0014643
2013-02-09 | 292279 | NRG14A | RURAL | Other | 638 | 3 | 1914 | 0.0054928 | 0.0018309
2013-02-09 | 292279 | NRG15A | URBAN | Other | 1387 | 3 | 4161 | 0.0042048 | 0.0014016
2013-02-09 | 292279 | NRG16A | RURAL | Other | 1910.49 | 3 | 5731.47 | 0.016448 | 0.0054828
2013-02-09 | 292279 | NRG17A | URBAN | Other | 1421 | 3 | 4263 | 0.0043079 | 0.001436
2013-02-09 | 292279 | NRG2A | URBAN | Other | 1302 | 3 | 3906 | 0.0039471 | 0.0013157
2013-02-09 | 292279 | NRG4 | URBAN | Other | 1071 | 3 | 3213 | 0.0032468 | 0.0010823
2013-02-09 | 292279 | NRG5A | URBAN | Other | 359 | 3 | 1077 | 0.0010883 | 0.00036278
2013-02-09 | 292279 | NRG6 | URBAN | Other | 905 | 3 | 2715 | 0.0027436 | 0.00091453
2013-02-09 | 292279 | NRG8B | URBAN | Other | 268.5 | 3 | 805.5 | 0.00081399 | 0.00027133
2013-02-09 | 292279 | NRG9 | RURAL | Other | 1962 | 3 | 5886 | 0.016892 | 0.0056306
2013-02-09 | 292291 | YDA1B | RURAL | Equipment failure | 26 | 78 | 2012 | 0.0057741 | 7.4615e-05
2013-02-09 | 292294 | CLM8 | URBAN | Vegetation | 8.15 | 288 | 2347.2 | 0.0023719 | 8.2359e-06
2013-02-09 | 292295 | LRE6A | RURAL | Animals | 141.17 | 191.0192 | 24949.64 | 0.071601 | 0.00040513
2013-02-09 | 292296 | MSV1 | RURAL | Animals | 141 | 119.1122 | 33613 | 0.096463 | 0.00040464
2013-02-09 | 292300 | BMT1 | RURAL | Weather | 6 | 303 | 1818 | 0.0052173 | 1.7219e-05
2013-02-09 | 292316 | YDA1B | RURAL | Equipment failure | 10.84 | 267.5 | 2939 | 0.0084344 | 3.1109e-05
2013-02-09 | 296506 | LTN5 | RURAL | Animals | 64.32 | 60 | 3859.2 | 0.011075 | 0.00018459
2013-02-10 | 292306 | EMD3 | RURAL | Vegetation | 649 | 61.4222 | 49165 | 0.14106 | 0.0018621
2013-02-10 | 292312 | TWG16 | URBAN | Vegetation | 416.83 | 55.7143 | 21601.5 | 0.02183 | 0.00042124
2013-02-10 | 292314 | NGI1B | RURAL | Other | 43.56 | 16 | 696.96 | 0.0019997 | 0.00012498
2013-02-10 | 292315 | NRA1A | RURAL | Other | 10 | 190 | 1900 | 0.0054514 | 2.8692e-05
2013-02-10 | 292327 | CMY4 | RURAL | Other | 92.83 | 18 | 1670.94 | 0.0047942 | 0.00026635
2013-02-10 | 292333 | KSN4 | URBAN | Vegetation | 94 | 26 | 2444 | 0.0024699 | 9.4995e-05
2013-02-10 | 292334 | CVL7A | RURAL | Animals | 17.16 | 41 | 703.56 | 0.0020186 | 4.9235e-05
2013-02-10 | 292335 | BDB32A | RURAL | Animals | 19.47 | 117 | 2277.99 | 0.006536 | 5.5863e-05
2013-02-10 | 292374 | MDH3A | URBAN | Third party impacts | 2 | 814 | 1628 | 0.0016452 | 2.0212e-06
2013-02-11 | 292352 | BPN29A | URBAN | Animals | 25.74 | 25 | 643.5 | 0.00065035 | 2.6014e-05
2013-02-11 | 292392 | TGW2 | RURAL | Equipment failure | 42 | 161 | 6762 | 0.019394 | 0.00012046
2013-02-11 | 292410 | SHW4 | URBAN | Weather | 1 | 150 | 150 | 0.0001516 | 1.0106e-06
2013-02-11 | 292451 | NIP1A | URBAN | Equipment failure | 1199 | 42.3409 | 82557.1501 | 0.083436 | 0.0012118
2013-02-11 | 292468 | SHW4 | URBAN | Vegetation | 488 | 55 | 26840 | 0.027126 | 0.0004932
2013-02-11 | 292475 | ABY2A | RURAL | Other | 0.66 | 159 | 104.94 | 0.00030098 | 1.893e-06
2013-02-11 | 292510 | LRE6A | RURAL | Equipment failure | 1 | 102 | 102 | 0.00029255 | 2.8681e-06
2013-02-12 | 292470 | CPK13 | RURAL | Vegetation | 1867.5 | 107.2941 | 193751 | 0.55554 | 0.0053546
2013-02-12 | 292473 | BNH6A | RURAL | Other | 21 | 128 | 2688 | 0.0077072 | 6.0213e-05
2013-02-12 | 292474 | CMV11A | URBAN | Equipment failure | 129 | 35 | 4515 | 0.0045633 | 0.00013038
2013-02-12 | 292580 | LGV2B | RURAL | Animals | 16 | 81 | 1296 | 0.003716 | 4.5876e-05
2013-02-12 | 292611 | NVL12A | URBAN | Other | 24.4 | 200 | 4880 | 0.0049322 | 2.4661e-05
2013-02-12 | 292650 | WCL11A | URBAN | Other | 3.5 | 15 | 52.5 | 5.3062e-05 | 3.5375e-06
2013-02-12 | 292748 | CHL7 | URBAN | Equipment failure | 15.045 | 46 | 692.07 | 0.00069948 | 1.5206e-05
2013-02-12 | 292749 | NRA13A | RURAL | Other | 2026.14 | 34.2885 | 84288.66 | 0.24168 | 0.0058095
2013-02-12 | 292750 | YTA22A | RURAL | Other | 172 | 31 | 5332 | 0.015288 | 0.00049317
2013-02-12 | 292752 | MCN2 | RURAL | Equipment failure | 78.49 | 412.2105 | 30183.31 | 0.086544 | 0.00022505
2013-02-12 | 292753 | LTN2 | RURAL | Equipment failure | 1.36 | 149 | 202.64 | 0.00058102 | 3.8995e-06
2013-02-12 | 292754 | GYM8A | RURAL | Third party impacts | 36.5 | 109 | 3978.5 | 0.011407 | 0.00010466
2013-02-12 | 292755 | IBL2 | RURAL | Equipment failure | 1 | 112 | 112 | 0.00032113 | 2.8673e-06
2013-02-12 | 292756 | MGP13A | RURAL | Other | 1 | 170 | 170 | 0.00048744 | 2.8673e-06
2013-02-12 | 292791 | MWMRBK8 | URBAN | Other | 1 | 95 | 95 | 9.6017e-05 | 1.0107e-06
2013-02-12 | 292936 | NVL8B | URBAN | Other | 147 | 63 | 9261 | 0.0093601 | 0.00014857
2013-02-13 | 292757 | ZMR7A | URBAN | Animals | 1868.49 | 152.0714 | 288211.61 | 0.29131 | 0.0018886
2013-02-13 | 292794 | YDA3A | RURAL | Third party impacts | 10.08 | 39 | 393.12 | 0.0011269 | 2.8894e-05
2013-02-13 | 292830 | TBV4 | RURAL | Equipment failure | 66 | 211 | 13926 | 0.039918 | 0.00018919
2013-02-13 | 292831 | LHM3 | URBAN | Other | 26 | 18 | 468 | 0.00047303 | 2.628e-05
2013-02-13 | 292930 | HWD12B | URBAN | Third party impacts | 4.5 | 101 | 454.5 | 0.00045939 | 4.5484e-06
2013-02-13 | 292931 | TRG2A | URBAN | Animals | 113.85 | 85 | 9677.25 | 0.0097813 | 0.00011507
2013-02-13 | 292932 | SFD5 | URBAN | Animals | 116.5 | 131 | 15261.5 | 0.015426 | 0.00011775
2013-02-13 | 292937 | GYN6A | RURAL | Other | 4.29 | 105 | 450.45 | 0.0012912 | 1.2297e-05
2013-02-13 | 292956 | AGE8 | URBAN | Vegetation | 86.5 | 10 | 865 | 0.0008743 | 8.743e-05
2013-02-13 | 292957 | GYN6A | RURAL | Other | 94 | 14.8889 | 1084 | 0.0031072 | 0.00026945
2013-02-13 | 292961 | MLY1 | RURAL | Other | 817.01 | 82 | 66994.82 | 0.19204 | 0.0023419
2013-02-13 | 292961 | MLY3 | RURAL | Other | 2046.48 | 81 | 165764.88 | 0.47516 | 0.0058661
2013-02-13 | 292961 | MLY4 | RURAL | Other | 625.49 | 80 | 50039.2 | 0.14344 | 0.0017929
2013-02-13 | 292961 | MLY6 | RURAL | Other | 613.49 | 20 | 12269.8 | 0.035171 | 0.0017585
2013-02-13 | 292962 | SPO60A | URBAN | Equipment failure | 84 | 296 | 24864 | 0.025131 | 8.4903e-05
2013-02-13 | 292963 | BWH13A | RURAL | Operational error | 49.5 | 62 | 3069 | 0.0087971 | 0.00014189
2013-02-13 | 292966 | GBP6 | URBAN | Equipment failure | 79.6252 | 372 | 32827.6608 | 0.033181 | 8.0482e-05
2013-02-13 | 293091 | RWD1 | RURAL | Other | 2 | 34 | 68 | 0.00019492 | 5.7329e-06
2013-02-13 | 293104 | BLB5A | URBAN | Animals | 58 | 177 | 10266 | 0.010376 | 5.8624e-05
2013-02-14 | 292968 | LGV2B | RURAL | Animals | 32.83 | 120 | 3939.6 | 0.01129 | 9.408e-05
2013-02-14 | 293011 | AGE3 | URBAN | Animals | 2118 | 57.4419 | 240201 | 0.2428 | 0.0021409
2013-02-14 | 293031 | LTN3 | URBAN | Weather | 1639.84 | 7.2105 | 13545.18 | 0.013692 | 0.0016576
2013-02-14 | 293051 | MWMRBK11 | RURAL | Other | 1182.75 | 49.2727 | 59709.75 | 0.17111 | 0.0033894
2013-02-14 | 293051 | RBK11B | URBAN | Other | 726.5 | 45 | 32692.5 | 0.033046 | 0.00073436
2013-02-14 | 293051 | RPN6A | RURAL | Other | 764 | 45 | 34380 | 0.098521 | 0.0021894
2013-02-14 | 293093 | NVL9 | RURAL | Other | 67 | 5 | 335 | 0.00096 | 0.000192
2013-02-14 | 293105 | RLB13B | RURAL | Equipment failure | 9 | 52 | 468 | 0.0013411 | 2.5791e-05
2013-02-14 | 293123 | ALY3A | URBAN | Equipment failure | 77.22 | 84 | 6486.48 | 0.0065566 | 7.8055e-05
2013-02-14 | 293134 | INA3A | URBAN | Animals | 38.61 | 153 | 5907.33 | 0.0059712 | 3.9028e-05
2013-02-14 | 293142 | TBV4 | RURAL | Other | 2.64 | 53 | 139.92 | 0.00040096 | 7.5653e-06
2013-02-14 | 293150 | ESK3A | RURAL | Other | 0.67 | 85 | 56.95 | 0.0001632 | 1.92e-06
2013-02-15 | 293137 | CPB3 | URBAN | Equipment failure | 471.5 | 41 | 19331.5 | 0.019542 | 0.00047663
2013-02-15 | 293137 | CPB5 | URBAN | Equipment failure | 895.99 | 47.5714 | 47361.59 | 0.047877 | 0.00090573
2013-02-15 | 293139 | NMK17A | URBAN | Animals | 7.6 | 120 | 912 | 0.00092192 | 7.6826e-06
2013-02-15 | 293141 | CHL4 | URBAN | Other | 1399.33 | 17 | 23788.61 | 0.024047 | 0.0014145
2013-02-15 | 293172 | MLY3 | RURAL | Other | 38 | 36 | 1368 | 0.0039191 | 0.00010887
2013-02-15 | 293210 | THL3 | RURAL | Equipment failure | 10 | 55 | 550 | 0.0015757 | 2.8649e-05
2013-02-15 | 293286 | HDA10A | URBAN | Equipment failure | 79.53 | 83 | 6600.99 | 0.0066728 | 8.0395e-05
2013-02-15 | 293287 | BLB4A | URBAN | Other | 0.66 | 100 | 66 | 6.6718e-05 | 6.6718e-07
2013-02-16 | 293290 | WRD15A | URBAN | Animals | 12 | 112 | 1344 | 0.0013586 | 1.213e-05
2013-02-16 | 293291 | MTB1B | RURAL | Weather | 288.99 | 106 | 30632.94 | 0.087754 | 0.00082787
2013-02-16 | 293292 | RBY13 | URBAN | Other | 31.02 | 80.1667 | 2486.77 | 0.0025138 | 3.1357e-05
2013-02-16 | 293293 | QPT22A | URBAN | Third party impacts | 41.4711 | 185 | 7672.1535 | 0.0077554 | 4.1921e-05
2013-02-16 | 293294 | GGR1 | RURAL | Equipment failure | 837.66 | 27.1172 | 20654.32 | 0.059168 | 0.0023996
2013-02-16 | 293295 | ESK5A | RURAL | Weather | 659.49 | 56.404 | 36452.44 | 0.10442 | 0.0018892
2013-02-16 | 293297 | RCF2A | URBAN | Equipment failure | 85.6878 | 73 | 6255.2094 | 0.0063231 | 8.6618e-05
2013-02-16 | 293298 | NRA16A | RURAL | Equipment failure | 23.5 | 53 | 1245.5 | 0.003568 | 6.732e-05
2013-02-16 | 293300 | BWH8A | RURAL | Equipment failure | 97.67 | 110 | 10743.7 | 0.030777 | 0.00027979
2013-02-16 | 293301 | CMD5A | URBAN | Equipment failure | 2.625 | 275 | 721.875 | 0.00072971 | 2.6535e-06
2013-02-16 | 293311 | CBW11 | RURAL | Equipment failure | 17 | 61 | 1842.8 | 0.005279 | 4.87e-05
2013-02-16 | 293312 | TGP9A | RURAL | Other | 11.22 | 122 | 1368.84 | 0.0039213 | 3.2142e-05
2013-02-16 | 293313 | KRN1 | URBAN | Other | 56.1 | 65 | 3646.5 | 0.0036861 | 5.6709e-05
2013-02-16 | 293315 | NBR6 | RURAL | Equipment failure | 12 | 91 | 1092 | 0.0031282 | 3.4376e-05
2013-02-16 | 293316 | INA10A | URBAN | Third party impacts | 87.83 | 159.5 | 2235.2735 | 0.0022595 | 8.8783e-05
2013-02-17 | 293307 | CHL7 | URBAN | Animals | 1511.5 | 15 | 22672.5 | 0.022918 | 0.0015279
2013-02-17 | 293322 | HTN24A | URBAN | Animals | 71.5 | 15 | 1072.5 | 0.0010841 | 7.2275e-05
2013-02-17 | 293343 | CMD15A | URBAN | Other | 128 | 53 | 6784 | 0.0068575 | 0.00012939
2013-02-17 | 293345 | WED6A | URBAN | Animals | 97.1322 | 75 | 7284.915 | 0.0073639 | 9.8185e-05
2013-02-17 | 293346 | CMD15A | URBAN | Other | 97.5 | 53 | 5167.5 | 0.0052235 | 9.8557e-05
2013-02-17 | 293351 | MLB6A | RURAL | Weather | 435.99 | 84.7857 | 32780.33 | 0.093901 | 0.0012489
2013-02-17 | 293355 | PBH6 | URBAN | Other | 244 | 53.5 | 18558.64 | 0.01876 | 0.00024664
2013-02-17 | 293363 | PBH6 | URBAN | Other | 80.52 | 147 | 11836.44 | 0.011965 | 8.1393e-05
2013-02-17 | 293376 | MLS26B | URBAN | Weather | 115 | 174 | 20010 | 0.020227 | 0.00011625
2013-02-17 | 293377 | BMT3 | RURAL | Vegetation | 346 | 124.7407 | 55336 | 0.15851 | 0.00099113
2013-02-17 | 293386 | ALY8 | URBAN | Other | 23.6 | 310.5 | 10714.4 | 0.010831 | 2.3856e-05
2013-02-18 | 293430 | MSTSGI11 | HIGH-DENSITY | Equipment failure | 3 | 184 | 552 | 0.14226 | 0.00077315
2013-02-18 | 293450 | BHL3A | URBAN | Equipment failure | 1347.33 | 104.2143 | 116592 | 0.11785 | 0.0013619
2013-02-18 | 293473 | KSN15 | RURAL | Equipment failure | 98 | 104 | 10192 | 0.029192 | 0.0002807
2013-02-18 | 293510 | NRG10 | URBAN | Other | 1445 | 149.9 | 197717 | 0.19985 | 0.0014606
2013-02-18 | 293512 | NRG9 | RURAL | Weather | 1963 | 225.0357 | 339667.63 | 0.97289 | 0.0056225
2013-02-18 | 293518 | TWG17 | URBAN | Equipment failure | 31.4226 | 103 | 3236.5278 | 0.0032715 | 3.1762e-05
2013-02-18 | 293570 | KBN5A | RURAL | Weather | 27 | 129 | 3483 | 0.0099762 | 7.7335e-05
2013-02-18 | 293590 | CRY2A | RURAL | Equipment failure | 47 | 152.1875 | 7946 | 0.022759 | 0.00013462
2013-02-18 | 293592 | CSE3 | URBAN | Third party impacts | 119.5 | 18 | 2151 | 0.0021742 | 0.00012079
2013-02-18 | 293593 | ESK5A | RURAL | Animals | 659.49 | 46 | 30336.54 | 0.086891 | 0.0018889
2013-02-18 | 293594 | CHL8 | URBAN | Equipment failure | 567.5 | 74.3 | 49538.5 | 0.050074 | 0.00057363
2013-02-18 | 293595 | JBB2A | RURAL | Equipment failure | 9 | 62 | 380.34 | 0.0010894 | 2.5778e-05
2013-02-18 | 293597 | MCW11 | RURAL | Equipment failure | 16 | 83.5 | 2002.88 | 0.0057367 | 4.5828e-05
2013-02-18 | 293650 | NSW17 | URBAN | Equipment failure | 34 | 396 | 13464 | 0.013609 | 3.4367e-05
2013-02-18 | 296477 | LDR2B | URBAN | Equipment failure | 179.5 | 59 | 10590.5 | 0.010705 | 0.00018144
2013-02-19 | 293670 | GTN5B | RURAL | Equipment failure | 51.67 | 105.6364 | 5348.04 | 0.015317 | 0.00014799
2013-02-19 | 293690 | DRD16A | URBAN | Other | 543.49 | 46 | 25000.54 | 0.02527 | 0.00054935
2013-02-19 | 293791 | NBR1 | RURAL | Equipment failure | 452 | 99.2581 | 39508.5 | 0.11316 | 0.0012946
2013-02-19 | 293811 | MFN13A | RURAL | Equipment failure | 100 | 317.5 | 32026 | 0.091725 | 0.00028641
2013-02-19 | 293850 | DRD16A | URBAN | Equipment failure | 1 | 365 | 365 | 0.00036894 | 1.0108e-06
2013-02-19 | 293891 | CLD18A | RURAL | Equipment failure | 2 | 267 | 534 | 0.0015294 | 5.7281e-06
2013-02-19 | 293913 | ESK5A | RURAL | Weather | 114 | 36 | 4104 | 0.011754 | 0.0003265
2013-02-19 | 293914 | KMR17A | URBAN | Vegetation | 583.5 | 11.8571 | 1874.5 | 0.0018947 | 0.00058979
2013-02-19 | 293914 | KMR17B | URBAN | Vegetation | 1479 | 66.4138 | 101180 | 0.10227 | 0.0014949
2013-02-19 | 293914 | KMR28A | URBAN | Vegetation | 291 | 65 | 18915 | 0.019119 | 0.00029414
2013-02-19 | 293915 | PWC4 | RURAL | Vegetation | 221 | 38.5 | 17017 | 0.048738 | 0.00063296
2013-02-19 | 293944 | GYM2A | RURAL | Weather | 153 | 87 | 13311 | 0.038124 | 0.0004382
2013-02-19 | 293945 | GBN4 | RURAL | Weather | 24.66 | 60 | 1479.6 | 0.0042377 | 7.0628e-05
2013-02-19 | 293946 | MLY3 | RURAL | Other | 515 | 36.9574 | 21615 | 0.061907 | 0.001475
2013-02-19 | 293947 | TWG11 | URBAN | Weather | 122 | 28 | 3416 | 0.0034528 | 0.00012332
2013-02-19 | 293948 | NMK17A | URBAN | Equipment failure | 5.4 | 101 | 545.4 | 0.00055128 | 5.4582e-06
2013-02-19 | 293949 | NBR9 | RURAL | Weather | 5.94 | 90 | 534.6 | 0.0015311 | 1.7013e-05
2013-02-19 | 293951 | MCN2 | RURAL | Weather | 4.3989 | 56 | 246.3384 | 0.00070553 | 1.2599e-05
2013-02-19 | 293952 | SBY4 | URBAN | Equipment failure | 24.75 | 172 | 4257 | 0.0043029 | 2.5017e-05
2013-02-19 | 293953 | MLY1 | RURAL | Weather | 6.27 | 49 | 307.23 | 0.00087993 | 1.7958e-05
2013-02-19 | 293970 | RPN5A | RURAL | Other | 56.28 | 109 | 6134.52 | 0.01757 | 0.00016119
2013-02-20 | 293954 | CNA9A | RURAL | Equipment failure | 183 | 131 | 23973 | 0.068654 | 0.00052408
2013-02-20 | 294011 | EMD3 | RURAL | Vegetation | 503 | 2 | 1006 | 0.002881 | 0.0014405
2013-02-20 | 294030 | CRB25A | RURAL | Weather | 274.16 | 78.5741 | 21526.48 | 0.061648 | 0.00078515
2013-02-20 | 294050 | TBV4 | RURAL | Vegetation | 515.17 | 25 | 12879.25 | 0.036884 | 0.0014754
2013-02-20 | 294070 | BDT4 | RURAL | Vegetation | 89 | 67 | 5963 | 0.017077 | 0.00025488
2013-02-20 | 294111 | CBT8A | RURAL | Equipment failure | 1409.52 | 100.8317 | 127762.84 | 0.36589 | 0.0040366
2013-02-20 | 294130 | BTN1 | URBAN | Weather | 26 | 55 | 1430 | 0.0014454 | 2.628e-05
2013-02-20 | 294131 | JBB3A | RURAL | Vegetation | 982.5 | 62 | 60915 | 0.17445 | 0.0028137
2013-02-20 | 294139 | BHD41A | URBAN | Weather | 12.332 | 88 | 1085.216 | 0.0010969 | 1.2465e-05
2013-02-20 | 294160 | GBG28 | URBAN | Other | 0.07 | 150 | 10.5 | 1.0613e-05 | 7.0754e-08
2013-02-20 | 294161 | JBB3A | RURAL | Other | 8.58 | 135 | 1158.3 | 0.0033172 | 2.4572e-05
2013-02-20 | 294162 | NRG17A | URBAN | Animals | 4 | 8 | 32 | 3.2345e-05 | 4.0431e-06
2013-02-20 | 294164 | KBN5A | RURAL | Other | 13 | 75.3333 | 979.3333 | 0.0028046 | 3.723e-05
2013-02-20 | 294172 | BPN35A | URBAN | Other | 31.02 | 101 | 3133.02 | 0.0031668 | 3.1354e-05
2013-02-20 | 294173 | YDA1B | RURAL | Other | 8.58 | 80 | 686.4 | 0.0019657 | 2.4572e-05
2013-02-20 | 294366 | ZMR2A | URBAN | Equipment failure | 33.3 | 477 | 15884.1 | 0.016055 | 3.3659e-05
2013-02-21 | 294168 | SBK9 | URBAN | Animals | 1536 | 65.9643 | 98995.5 | 0.10006 | 0.0015525
2013-02-21 | 294171 | RBY12 | URBAN | Equipment failure | 42 | 34 | 1428 | 0.0014434 | 4.2452e-05
2013-02-21 | 294191 | NBR10 | URBAN | Animals | 52 | 9 | 468 | 0.00047303 | 5.2559e-05
2013-02-21 | 294272 | TRP2 | RURAL | Weather | 157.58 | 161.3636 | 24008.18 | 0.068749 | 0.00045124
2013-02-21 | 294310 | BLB4A | URBAN | Equipment failure | 2232.33 | 58.1923 | 119178.99 | 0.12046 | 0.0022563
2013-02-21 | 294331 | BRD8A | RURAL | Weather | 994.99 | 48.4819 | 45789.5 | 0.13112 | 0.0028492
2013-02-21 | 294348 | BRD5A | RURAL | Weather | 47 | 12 | 564 | 0.0016151 | 0.00013459
2013-02-21 | 294365 | BGY17A | URBAN | Animals | 20.46 | 60 | 1227.6 | 0.0012408 | 2.068e-05
2013-02-21 | 294367 | NSW5A | URBAN | Animals | 60.06 | 76 | 4564.56 | 0.0046137 | 6.0706e-05
2013-02-21 | 294368 | KRN11 | URBAN | Other | 106 | 44 | 4664 | 0.0047142 | 0.00010714
2013-02-21 | 294369 | MLB8A | RURAL | Animals | 15.84 | 18 | 285.12 | 0.00081646 | 4.5359e-05
2013-02-21 | 294370 | GGR3 | RURAL | Third party impacts | 7 | 542 | 3794 | 0.010864 | 2.0045e-05
2013-02-21 | 296512 | CPR7 | URBAN | Other | 71.02 | 135 | 9587.7 | 0.0096908 | 7.1784e-05
2013-02-22 | 294362 | BHD23A | RURAL | Weather | 1207.5 | 170.931 | 204735 | 0.58622 | 0.0034574
2013-02-22 | 294364 | 393 | URBAN | Weather | 1 | 200 | 200 | 0.00020215 | 1.0107e-06
2013-02-22 | 294470 | SRD19A | URBAN | Equipment failure | 49.17 | 215 | 10571.55 | 0.010685 | 4.9698e-05
2013-02-22 | 294553 | LLY1 | RURAL | Third party impacts | 290.99 | 113.0357 | 32749 | 0.09377 | 0.00083319
2013-02-22 | 294570 | CMV14 | URBAN | Vegetation | 1188.5 | 41 | 48728.5 | 0.049252 | 0.0012013
2013-02-22 | 294571 | KMR25A | RURAL | Other | 1075 | 76 | 81700 | 0.23393 | 0.0030781
2013-02-22 | 294572 | CRB25A | RURAL | Weather | 142 | 214.871 | 32383 | 0.092722 | 0.00040659
2013-02-22 | 294576 | WNM5 | URBAN | Other | 2198.5 | 55 | 120917.5 | 0.12222 | 0.0022221
2013-02-22 | 294577 | MDR4A | URBAN | Weather | 423.35 | 79 | 33444.65 | 0.033804 | 0.0004279
2013-02-22 | 294590 | CPR4 | URBAN | Equipment failure | 765 | 131.9474 | 98681 | 0.099741 | 0.00077322
2013-02-22 | 294592 | LGV3A | RURAL | Vegetation | 219.5 | 37 | 8121.5 | 0.023254 | 0.0006285
2013-02-22 | 294593 | MTB3A | RURAL | Weather | 994.83 | 41.4909 | 51070.58 | 0.14623 | 0.0028485
2013-02-22 | 294596 | KMR17A | URBAN | Vegetation | 580.5 | 13 | 7546.5 | 0.0076276 | 0.00058674
2013-02-22 | 294599 | HPK3A | URBAN | Weather | 2553 | 105.5625 | 265935 | 0.26879 | 0.0025804
2013-02-22 | 294600 | UPC1 | RURAL | Weather | 100 | 256 | 25600 | 0.073301 | 0.00028633
2013-02-22 | 294607 | BDB27A | RURAL | Equipment failure | 40 | 248 | 9920 | 0.028404 | 0.00011453
2013-02-22 | 294614 | BHD44A | URBAN | Equipment failure | 4.08 | 124 | 505.92 | 0.00051136 | 4.1238e-06
2013-02-22 | 294617 | SPO55A | URBAN | Equipment failure | 27.8289 | 45 | 1252.3005 | 0.0012658 | 2.8128e-05
2013-02-22 | 294620 | IPS13A | RURAL | Other | 8 | 37 | 296 | 0.00084754 | 2.2906e-05
2013-02-22 | 294623 | CBW11 | RURAL | Vegetation | 78.99 | 71 | 5608.29 | 0.016058 | 0.00022617
2013-02-22 | 294627 | MLY1 | RURAL | Other | 40 | 94 | 3760 | 0.010766 | 0.00011453
2013-02-22 | 294628 | MRK3 | URBAN | Vegetation | 121.5 | 15 | 1822.5 | 0.0018421 | 0.00012281
2013-02-22 | 294630 | BRT3 | URBAN | Equipment failure | 7.56 | 460 | 3477.6 | 0.003515 | 7.6412e-06
2013-02-22 | 294647 | SMR7A | URBAN | Other | 89.83 | 55 | 4940.65 | 0.0049937 | 9.0795e-05
2013-02-22 | 294648 | AGE4B | URBAN | Animals | 38 | 63 | 2394 | 0.0024197 | 3.8408e-05
2013-02-22 | 294706 | WNM5 | URBAN | Other | 2198.5 | 82.4615 | 190992.5 | 0.19304 | 0.0022221
2013-02-22 | 294750 | TGW3 | RURAL | Other | 1 | 72 | 72 | 0.00020616 | 2.8633e-06
2013-02-23 | 294631 | 3702 | URBAN | Other | 0.75 | 15 | 11.25 | 1.1371e-05 | 7.5805e-07
2013-02-23 | 294632 | PRG1 | RURAL | Weather | 29 | 25 | 725 | 0.0020757 | 8.3028e-05
2013-02-23 | 294641 | BRT3 | URBAN | Other | 94.5 | 262 | 24759 | 0.025025 | 9.5514e-05
2013-02-23 | 294646 | WSE3A | RURAL | Vegetation | 2 | 166 | 332 | 0.00095053 | 5.7261e-06
2013-02-23 | 294649 | AGE10 | URBAN | Other | 53 | 100 | 5300 | 0.0053569 | 5.3569e-05
2013-02-23 | 294650 | CLM8 | URBAN | Animals | 51.5 | 131 | 6746.5 | 0.0068189 | 5.2053e-05
2013-02-23 | 294651 | LBH3A | RURAL | Weather | 5.3922 | 34 | 183.3348 | 0.0005249 | 1.5438e-05
2013-02-23 | 294652 | EMD2 | RURAL | Animals | 17 | 122 | 2074 | 0.005938 | 4.8672e-05
2013-02-23 | 294659 | BBS11 | URBAN | Other | 1086.5 | 16 | 17384 | 0.017571 | 0.0010982
2013-02-23 | 294661 | TMH15A | URBAN | Vegetation | 1721.5 | 65.125 | 113624.8 | 0.11484 | 0.00174
2013-02-23 | 294674 | WSE5A | RURAL | Other | 31.68 | 107 | 3389.76 | 0.0097051 | 9.0701e-05
2013-02-23 | 294677 | SRD14A | URBAN | Animals | 159.33 | 70 | 11153.1 | 0.011273 | 0.00016104
2013-02-23 | 294678 | WED6A | URBAN | Animals | 97.1322 | 78 | 7576.3116 | 0.0076576 | 9.8175e-05
2013-02-23 | 294679 | TRP1 | RURAL | Animals | 1.98 | 113 | 223.74 | 0.00064058 | 5.6688e-06
2013-02-23 | 294734 | CPD1 | RURAL | Animals | 1 | 300 | 300 | 0.00085891 | 2.863e-06
2013-02-24 | 294663 | MAI5 | URBAN | Weather | 1738.48 | 97.9444 | 176778.96 | 0.17867 | 0.0017571
2013-02-24 | 294671 | KWA3A | URBAN | Other | 1 | 85 | 85 | 8.5911e-05 | 1.0107e-06
2013-02-24 | 294673 | TBV3 | RURAL | Weather | 381.5 | 54 | 20601 | 0.058979 | 0.0010922
2013-02-24 | 294675 | FDS1 | RURAL | Other | 4 | 109 | 436 | 0.0012482 | 1.1452e-05
2013-02-24 | 294676 | CPC2A | RURAL | Weather | 24.09 | 67 | 1614.03 | 0.0046208 | 6.8968e-05
2013-02-24 | 294681 | MAI5 | URBAN | Other | 2.18 | 90 | 196.2 | 0.0001983 | 2.2034e-06
2013-02-24 | 294688 | SMF3A | RURAL | Weather | 66 | 57 | 3762 | 0.01077 | 0.00018895
2013-02-24 | 294689 | MGP13A | RURAL | Vegetation | 8 | 95 | 760 | 0.0021758 | 2.2903e-05
2013-02-24 | 294711 | MTB3A | RURAL | Other | 13 | 157 | 2041 | 0.0058432 | 3.7218e-05
2013-02-24 | 294712 | RBA4A | URBAN | Other | 16.83 | 65 | 1093.95 | 0.0011057 | 1.701e-05
2013-02-24 | 294730 | WED6A | URBAN | Animals | 97.1322 | 96 | 9324.6912 | 0.0094246 | 9.8173e-05
2013-02-24 | 294733 | PWC4 | RURAL | Animals | 5.28 | 110 | 580.8 | 0.0016628 | 1.5116e-05
2013-02-25 | 294704 | NBR6 | RURAL | Equipment failure | 1036.99 | 158.9412 | 101992.33 | 0.29196 | 0.0029684
2013-02-25 | 294705 | TRP2 | RURAL | Animals | 157.58 | 260.9455 | 37488.84 | 0.10731 | 0.00045108
2013-02-25 | 294710 | BHL2A | URBAN | Weather | 8 | 95 | 760 | 0.00076812 | 8.0855e-06
2013-02-25 | 294714 | YTA3A | URBAN | Other | 141.49 | 17 | 2405.33 | 0.002431 | 0.000143
2013-02-25 | 294714 | YTA3B | URBAN | Other | 184.5 | 17 | 3136.5 | 0.00317 | 0.00018647
2013-02-25 | 294735 | CRY6A | RURAL | Equipment failure | 5.28 | 253 | 1335.84 | 0.0038239 | 1.5114e-05
2013-02-25 | 294770 | KCY2 | RURAL | Equipment failure | 358.26 | 16 | 5732.16 | 0.016408 | 0.0010255
2013-02-25 | 294810 | GBG1A | URBAN | Equipment failure | 45.83 | 30 | 1374.9 | 0.0013896 | 4.632e-05
2013-02-25 | 294810 | GBG1B | URBAN | Equipment failure | 104 | 42.2727 | 4200 | 0.0042449 | 0.00010511
2013-02-25 | 294811 | TRP1 | RURAL | Equipment failure | 78.5 | 81 | 6358.5 | 0.018201 | 0.00022471
2013-02-25 | 294830 | GBG23A | URBAN | Equipment failure | 15 | 80 | 1200 | 0.0012128 | 1.516e-05
2013-02-25 | 294876 | CPB5 | URBAN | Equipment failure | 92 | 153 | 14076 | 0.014226 | 9.2983e-05
2013-02-25 | 294877 | MFD9A | URBAN | Weather | 28.65 | 357 | 10228.05 | 0.010337 | 2.8956e-05
2013-02-25 | 294878 | NDH9 | URBAN | Equipment failure | 1402.49 | 147.4444 | 266110.98 | 0.26895 | 0.0014175
2013-02-25 | 294879 | HTN24A | URBAN | Third party impacts | 6.35 | 355 | 2254.25 | 0.0022783 | 6.4179e-06
2013-02-25 | 294880 | MCW4 | RURAL | Weather | 1262.5 | 111 | 140137.5 | 0.40115 | 0.0036139
2013-02-25 | 294882 | GYN3A | RURAL | Equipment failure | 342.5 | 152.8615 | 103588 | 0.29652 | 0.00098042
2013-02-25 | 294883 | KMR25A | RURAL | Weather | 8.5 | 47 | 399.5 | 0.0011436 | 2.4331e-05
2013-02-25 | 294884 | MLB8A | RURAL | Equipment failure | 20 | 138 | 2760 | 0.0079006 | 5.7251e-05
2013-02-25 | 294886 | NBR5 | RURAL | Weather | 134 | 514.6897 | 57054 | 0.16332 | 0.00038358
2013-02-25 | 295072 | KMR29A | URBAN | Equipment failure | 20.5 | 275 | 5637.5 | 0.0056977 | 2.0719e-05
2013-02-25 | 295734 | GYGGYS6 | RURAL | Weather | 1 | 5368 | 5368 | 0.015366 | 2.8625e-06
2013-02-26 | 294885 | CRM15A | URBAN | Equipment failure | 278 | 33 | 9174 | 0.0092719 | 0.00028097
2013-02-26 | 294887 | BDT5 | RURAL | Equipment failure | 109.01 | 314.8235 | 32951.55 | 0.094318 | 0.00031202
2013-02-26 | 294890 | BPN29A | URBAN | Third party impacts | 1320 | 104.0909 | 131391 | 0.13279 | 0.0013341
2013-02-26 | 294910 | MAI17 | URBAN | Animals | 1018.5 | 11 | 11203.5 | 0.011323 | 0.0010294
2013-02-26 | 294970 | WSE1B | URBAN | Animals | 5.75 | 11 | 63.25 | 6.3925e-05 | 5.8113e-06
2013-02-26 | 294991 | RIS2 | URBAN | Equipment failure | 1171.98 | 61.6071 | 72243.78 | 0.073015 | 0.0011845
2013-02-26 | 295051 | MMC22A | URBAN | Equipment failure | 3.2165 | 33 | 106.1445 | 0.00010728 | 3.2508e-06
2013-02-26 | 295070 | CHL6A | URBAN | Equipment failure | 97 | 124 | 12028 | 0.012156 | 9.8035e-05
2013-02-26 | 295075 | FDS1 | RURAL | Equipment failure | 11 | 103 | 1133 | 0.003243 | 3.1486e-05
2013-02-26 | 295088 | GYM2B | URBAN | Weather | 89.5 | 214 | 18829.5 | 0.01903 | 9.0455e-05
2013-02-26 | 295088 | GYN3A | RURAL | Weather | 4 | 235 | 940 | 0.0026906 | 1.1449e-05
2013-02-26 | 295089 | BHL5A | URBAN | Third party impacts | 2.46 | 235 | 578.1 | 0.00058427 | 2.4862e-06
2013-02-26 | 295210 | GYM2B | URBAN | Weather | 31.5 | 1082 | 34083 | 0.034447 | 3.1836e-05
2013-02-26 | 295212 | GYM2B | URBAN | Weather | 31.5 | 49 | 1543.5 | 0.00156 | 3.1836e-05
2013-02-26 | 295359 | GYM3 | URBAN | Weather | 33 | 1400 | 46200 | 0.046693 | 3.3352e-05
2013-02-26 | 295370 | GYM2B | URBAN | Weather | 15 | 884 | 14667 | 0.014823 | 1.516e-05
2013-02-27 | 295110 | KCY1 | URBAN | Equipment failure | 610 | 50 | 30500 | 0.030825 | 0.00061649
2013-02-27 | 295110 | KCY2 | RURAL | Equipment failure | 358.26 | 50 | 17913 | 0.051269 | 0.0010254
2013-02-27 | 295110 | KCY3 | URBAN | Equipment failure | 5.65 | 50 | 282.5 | 0.00028551 | 5.7101e-06
2013-02-27 | 295110 | KCY4 | RURAL | Equipment failure | 700.12 | 50 | 35006 | 0.10019 | 0.0020038
2013-02-27 | 295110 | KCY5 | RURAL | Equipment failure | 526 | 50 | 26300 | 0.075274 | 0.0015055
2013-02-27 | 295131 | GBG1B | URBAN | Equipment failure | 72 | 2 | 144 | 0.00014553 | 7.2766e-05
2013-02-27 | 295150 | EMP4A | URBAN | Equipment failure | 12.975 | 59 | 765.525 | 0.00077367 | 1.3113e-05
2013-02-27 | 295191 | NBR6 | RURAL | Equipment failure | 259 | 75 | 19425 | 0.055597 | 0.00074129
2013-02-27 | 295315 | CPL26A | URBAN | Equipment failure | 5.885 | 77 | 453.145 | 0.00045797 | 5.9476e-06
2013-02-27 | 295316 | BHD35A | RURAL | Other | 2.97 | 224 | 665.28 | 0.0019041 | 8.5005e-06
2013-02-27 | 295352 | KMR27A | URBAN | Other | 21.5 | 102 | 2193 | 0.0022163 | 2.1729e-05
2013-02-27 | 295358 | SCV4 | URBAN | Other | 23.25 | 20 | 465 | 0.00046995 | 2.3497e-05
2013-02-27 | 295360 | GYS3A | RURAL | Other | 12 | 398 | 4776 | 0.01367 | 3.4346e-05
2013-02-27 | 295363 | INA2A | URBAN | Other | 1.215 | 133 | 161.595 | 0.00016331 | 1.2279e-06
2013-02-27 | 295364 | TGW2 | RURAL | Weather | 44.5 | 84 | 3738 | 0.010699 | 0.00012737
2013-02-27 | 295366 | SBH6 | URBAN | Third party impacts | 121.5 | 38 | 4617 | 0.0046661 | 0.00012279
2013-02-27 | 295367 | BISTPT3 | RURAL | Vegetation | 48 | 32.1333 | 1542.4 | 0.0044146 | 0.00013738
2013-02-28 | 295365 | RPN4A | RURAL | Equipment failure | 8 | 101 | 808 | 0.0023125 | 2.2896e-05
2013-02-28 | 295470 | MCN4 | RURAL | Third party impacts | 26.1 | 35 | 913.5 | 0.0026144 | 7.4698e-05
2013-02-28 | 295593 | BHD44A | URBAN | Equipment failure | 22.44 | 95 | 2131.8 | 0.0021544 | 2.2678e-05
2013-02-28 | 295595 | NVL9 | RURAL | Equipment failure | 1 | 73 | 73 | 0.00020892 | 2.862e-06
2013-02-28 | 295596 | TWG18 | URBAN | Third party impacts | 6 | 122 | 732 | 0.00073977 | 6.0637e-06
2013-02-28 | 295610 | ACR2B | URBAN | Equipment failure | 2.5 | 43 | 215 | 0.00021728 | 2.5265e-06
2013-02-28 | 295611 | MCW11 | RURAL | Other | 16.5 | 73 | 1204.5 | 0.0034473 | 4.7223e-05
2013-02-28 | 295612 | WMR3 | RURAL | Weather | 5 | 71 | 355 | 0.001016 | 1.431e-05
2013-02-28 | 295613 | BHD5A | URBAN | Other | 111.33 | 134 | 14918.22 | 0.015077 | 0.00011251
2013-02-28 | 295614 | TWT3A | RURAL | Other | 26.4 | 20.3333 | 536.8 | 0.0015363 | 7.5556e-05
2013-02-28 | 295633 | PBH3 | URBAN | Other | 34.485 | 89 | 3069.165 | 0.0031018 | 3.4851e-05
2013-02-28 | 295634 | SRD14A | URBAN | Equipment failure | 20.1531 | 115 | 1574.3846 | 0.0015911 | 2.0367e-05
2013-02-28 | 295650 | WFD5A | RURAL | Equipment failure | 507.51 | 50.3617 | 12415.49 | 0.035533 | 0.0014525
2013-02-28 | 295744 | CLD20A | RURAL | Other | 41 | 125 | 5125 | 0.014668 | 0.00011734
2013-03-01 | 295635 | MTB2A | RURAL | Vegetation | 180.33 | 92.3922 | 35787.1 | 0.10242 | 0.00051609
2013-03-01 | 295711 | MTB3A | RURAL | Equipment failure | 143.5 | 15 | 2152.5 | 0.0061603 | 0.00041068
2013-03-01 | 295746 | NRG9 | RURAL | Vegetation | 2 | 34 | 68 | 0.00019461 | 5.7238e-06
2013-03-01 | 295768 | IBL2 | RURAL | Animals | 737.51 | 173 | 127589.23 | 0.36515 | 0.0021107
2013-03-01 | 295770 | VPT1B | URBAN | Equipment failure | 58.9578 | 103 | 6072.6534 | 0.0061369 | 5.9582e-05
2013-03-01 | 295773 | MTB13A | RURAL | Weather | 18.5 | 567 | 10489.5 | 0.03002 | 5.2945e-05
2013-03-02 | 295771 | NVL2 | URBAN | Other | 76.38 | 104 | 7943.52 | 0.0080274 | 7.7186e-05
2013-03-02 | 295774 | BDT6 | URBAN | Equipment failure | 33.99 | 85 | 2889.15 | 0.0029196 | 3.4349e-05
2013-03-02 | 295775 | BLH10B | URBAN | Third party impacts | 21.2 | 229 | 4854.8 | 0.004906 | 2.1424e-05
2013-03-02 | 295776 | MTB1B | RURAL | Weather | 1 | 115 | 115 | 0.00032911 | 2.8619e-06
2013-03-02 | 295790 | NBR6 | RURAL | Other | 15.18 | 97 | 1472.46 | 0.004214 | 4.3443e-05
2013-03-02 | 295791 | KRN5A | URBAN | Third party impacts | 46.5 | 154.5 | 3617.7 | 0.0036559 | 4.6991e-05
2013-03-02 | 295792 | BMT1 | RURAL | Equipment failure | 2.64 | 200 | 528 | 0.0015111 | 7.5553e-06
2013-03-02 | 295793 | QPT21 | URBAN | Third party impacts | 953.17 | 61.7143 | 52959.26 | 0.053518 | 0.00096323
2013-03-02 | 295801 | GAP1A | URBAN | Equipment failure | 7.81 | 27 | 210.87 | 0.0002131 | 7.8924e-06
2013-03-02 | 295802 | BLH16A | RURAL | Third party impacts | 4 | 159 | 636 | 0.0018201 | 1.1447e-05
2013-03-02 | 295810 | PRG2A | RURAL | Equipment failure | 1 | 40 | 40 | 0.00011447 | 2.8619e-06
2013-03-02 | 295833 | WRD20A | URBAN | Equipment failure | 47 | 260 | 12220 | 0.012349 | 4.7496e-05
2013-03-02 | 295838 | SMR12A | URBAN | Equipment failure | 108 | 191.5 | 20682 | 0.0209 | 0.00010914
2013-03-03 | 295830 | ZMR6A | URBAN | Equipment failure | 95 | 99 | 9405 | 0.0095043 | 9.6003e-05
2013-03-03 | 295832 | GVN2A | URBAN | Equipment failure | 5 | 167 | 835 | 0.00084381 | 5.0528e-06
2013-03-03 | 295834 | SPF1B | RURAL | Weather | 23.25 | 57 | 1325.25 | 0.0037926 | 6.6536e-05
2013-03-03 | 295835 | BTA5A | RURAL | Weather | 1746 | 50.8806 | 83101 | 0.23782 | 0.0049967
2013-03-03 | 295836 | BWH8A | RURAL | Weather | 5 | 10 | 50 | 0.00014309 | 1.4309e-05
2013-03-03 | 295837 | BKD12A | URBAN | Equipment failure | 17.5 | 159 | 2782.5 | 0.0028119 | 1.7685e-05
2013-03-03 | 295839 | GBN4 | RURAL | Weather | 0.96 | 117 | 112.32 | 0.00032143 | 2.7473e-06
2013-03-03 | 295844 | WSE5A | RURAL | Equipment failure | 29 | 140 | 4060 | 0.011619 | 8.2991e-05
2013-03-03 | 295845 | WMR3 | RURAL | Equipment failure | 2.31 | 78 | 180.18 | 0.00051563 | 6.6107e-06
2013-03-03 | 295846 | SMR12A | URBAN | Equipment failure | 71 | 161 | 11431 | 0.011552 | 7.1749e-05
2013-03-03 | 295847 | AGE10 | URBAN | Other | 34.98 | 68 | 2378.64 | 0.0024037 | 3.5349e-05
2013-03-03 | 295848 | KLG11A | URBAN | Equipment failure | 2356.83 | 64.6857 | 150666.11 | 0.15226 | 0.0023817
2013-03-04 | 295851 | GBG1B | URBAN | Equipment failure | 103 | 155 | 16172 | 0.016341 | 0.00010407
2013-03-04 | 295851 | GBG23A | URBAN | Equipment failure | 15 | 155 | 2325 | 0.0023493 | 1.5156e-05
2013-03-04 | 295890 | MGL2A | RURAL | Weather | 493 | 106.2174 | 47486 | 0.13592 | 0.0014112
2013-03-04 | 295990 | CMV13 | URBAN | Other | 11.8005 | 17 | 200.6085 | 0.0002027 | 1.1924e-05
2013-03-04 | 296011 | CBW7 | RURAL | Equipment failure | 4.62 | 117 | 540.54 | 0.0015472 | 1.3224e-05
2013-03-04 | 296090 | YDA5A | RURAL | Vegetation | 357.99 | 72.5294 | 20287.71 | 0.058071 | 0.0010247
2013-03-04 | 296094 | PPE16A | RURAL | Equipment failure | 16 | 476 | 7616 | 0.0218 | 4.5798e-05
2013-03-04 | 296101 | TGW1 | RURAL | Equipment failure | 49 | 354 | 17346 | 0.049651 | 0.00014026
2013-03-04 | 296106 | ZMR2A | URBAN | Equipment failure | 5.5 | 519 | 2854.5 | 0.0028843 | 5.5574e-06
2013-03-04 | 296108 | SPC2B | RURAL | Weather | 3 | 43 | 129 | 0.00036925 | 8.5871e-06
2013-03-04 | 296109 | PRG2B | RURAL | Other | 11 | 62 | 682 | 0.0019521 | 3.1486e-05
2013-03-04 | 296110 | KBN1B | RURAL | Equipment failure | 4.62 | 167 | 771.54 | 0.0022084 | 1.3224e-05
2013-03-04 | 296111 | MTG16A | URBAN | Vegetation | 135.17 | 111 | 15003.87 | 0.01516 | 0.00013658
2013-03-04 | 296112 | CRM5A | URBAN | Other | 3 | 113 | 339 | 0.00034254 | 3.0313e-06
2013-03-04 | 296113 | CFD8A | URBAN | Equipment failure | 7.59 | 158 | 1199.22 | 0.0012117 | 7.6692e-06
2013-03-04 | 296114 | NRG16A | RURAL | Other | 17.5 | 11.5 | 402.5 | 0.0011521 | 5.0092e-05
2013-03-04 | 296115 | HTN7A | URBAN | Equipment failure | 39 | 80 | 3120 | 0.0031525 | 3.9407e-05
2013-03-04 | 296116 | YDA5A | RURAL | Equipment failure | 12 | 63 | 756 | 0.002164 | 3.4349e-05
2013-03-04 | 296117 | CVL7A | RURAL | Weather | 20 | 37 | 740 | 0.0021182 | 5.7248e-05
2013-03-05 | 296120 | RWD2 | RURAL | Equipment failure | 12 | 115 | 1380 | 0.0039505 | 3.4352e-05
2013-03-05 | 296150 | MLB3A | RURAL | Equipment failure | 2976.5 | 6.2195 | 20532.5 | 0.058778 | 0.0085208
2013-03-05 | 296210 | RBY15 | URBAN | Third party impacts | 22 | 20.5 | 316.8 | 0.00032009 | 2.2228e-05
2013-03-05 | 296216 | NBR9 | RURAL | Vegetation | 32 | 126 | 4032 | 0.011542 | 9.1607e-05
2013-03-05 | 296218 | RBARHP14 | URBAN | Third party impacts | 88 | 219 | 19272 | 0.019472 | 8.8913e-05
2013-03-05 | 296240 | NBR6 | RURAL | Equipment failure | 131 | 66 | 8646 | 0.024751 | 0.00037501
2013-03-05 | 296244 | CBW11 | RURAL | Other | 7 | 390 | 2730 | 0.0078152 | 2.0039e-05
2013-03-05 | 296245 | CBT12A | RURAL | Other | 4.62 | 17 | 78.54 | 0.00022484 | 1.3226e-05
2013-03-05 | 296246 | INA5A | URBAN | Other | 32.8 | 64 | 2099.2 | 0.002121 | 3.314e-05
2013-03-05 | 296247 | IPS1B | URBAN | Other | 15 | 140 | 2100 | 0.0021218 | 1.5156e-05
2013-03-05 | 296251 | PWC6 | RURAL | Weather | 15 | 26 | 390 | 0.0011165 | 4.2941e-05
2013-03-05 | 296252 | STT3A | RURAL | Other | 3.5178 | 156 | 548.7768 | 0.001571 | 1.007e-05
2013-03-05 | 297605 | CMV11A | URBAN | Vegetation | 202.675 | 242 | 49047.35 | 0.049556 | 0.00020478
2013-03-06 | 296248 | RWD2 | RURAL | Other | 12 | 133 | 1596 | 0.0045692 | 3.4355e-05
2013-03-06 | 296253 | OXL4A | URBAN | Weather | 852 | 53 | 45156 | 0.045622 | 0.0008608
2013-03-06 | 296255 | WEL3 | URBAN | Other | 8.8635 | 161 | 1427.0235 | 0.0014418 | 8.955e-06
2013-03-06 | 296264 | JBB13A | RURAL | Other | 224.49 | 39 | 8755.11 | 0.025065 | 0.0006427
2013-03-06 | 296266 | GTN15A | RURAL | Equipment failure | 5.25 | 120 | 630 | 0.0018036 | 1.503e-05
2013-03-06 | 296293 | CPK9 | RURAL | Other | 738.5 | 15 | 11077.5 | 0.031714 | 0.0021143
2013-03-06 | 296298 | LLY1 | RURAL | Other | 3 | 402 | 1206 | 0.0034527 | 8.5888e-06
2013-03-06 | 296341 | AFD7 | URBAN | Animals | 2.5 | 324 | 810 | 0.00081836 | 2.5258e-06
2013-03-07 | 296295 | OXL11A | URBAN | Equipment failure | 16 | 40 | 640 | 0.00064658 | 1.6164e-05
2013-03-07 | 296296 | BRD8A | RURAL | Equipment failure | 63.5 | 90 | 5715 | 0.016363 | 0.00018181
2013-03-07 | 296297 | GSEGSN2 | URBAN | Other | 1 | 39 | 39 | 3.9401e-05 | 1.0103e-06
2013-03-07 | 296299 | F1173 | URBAN | Other | 103.66 | 8 | 829.28 | 0.0008378 | 0.00010473
2013-03-07 | 296299 | WLDT1 | URBAN | Other | 1 | 8 | 8 | 8.0822e-06 | 1.0103e-06
2013-03-07 | 296299 | WLDT2 | URBAN | Other | 1 | 8 | 8 | 8.0822e-06 | 1.0103e-06
2013-03-07 | 296302 | MDR4A | URBAN | Third party impacts | 422.35 | 42 | 17738.7 | 0.017921 | 0.00042669
2013-03-07 | 296305 | SMF3A | RURAL | Equipment failure | 9 | 65 | 585 | 0.001675 | 2.5769e-05
2013-03-07 | 296307 | GBN4 | RURAL | Weather | 16 | 29 | 464 | 0.0013285 | 4.5811e-05
2013-03-07 | 296309 | KCY4 | RURAL | Equipment failure | 7.5 | 83 | 622.5 | 0.0017823 | 2.1474e-05
2013-03-07 | 296311 | IDY6A | URBAN | Vegetation | 186.5 | 27 | 5035.5 | 0.0050873 | 0.00018842
2013-03-07 | 296312 | PRG2A | RURAL | Equipment failure | 1 | 63 | 63 | 0.00018038 | 2.8632e-06
2013-03-07 | 296335 | EMP23A | URBAN | Other | 112.5 | 23 | 2587.5 | 0.0026141 | 0.00011366
2013-03-07 | 296336 | MTB3A | RURAL | Weather | 293.83 | 147.2 | 71925.57 | 0.20594 | 0.00084129
2013-03-07 | 296337 | NRG16A | RURAL | Equipment failure | 708.5 | 12.7925 | 12505.5 | 0.035805 | 0.0020286
2013-03-07 | 296366 | WED3A | URBAN | Animals | 49.83 | 78 | 3886.74 | 0.0039267 | 5.0342e-05
2013-03-08 | 296342 | TWG16 | URBAN | Equipment failure | 416.83 | 48.5714 | 20415.84 | 0.020625 | 0.00042109
2013-03-08 | 296351 | NGE4B | URBAN | Other | 1 | 21 | 21 | 2.1215e-05 | 1.0102e-06
2013-03-08 | 296365 | BHD41A | URBAN | Third party impacts | 31 | 102 | 3162 | 0.0031943 | 3.1317e-05
2013-03-08 | 296386 | SGT5 | URBAN | Equipment failure | 1121 | 48.3 | 55830 | 0.056401 | 0.0011325
2013-03-08 | 296387 | MTB1B | RURAL | Other | 48.51 | 157 | 7616.07 | 0.021808 | 0.0001389
2013-03-09 | 296390 | CNA7A | RURAL | Vegetation | 109.5 | 5 | 547.5 | 0.0015678 | 0.00031357
2013-03-09 | 296391 | AFD8 | URBAN | Equipment failure | 14 | 273 | 3822 | 0.0038609 | 1.4143e-05
2013-03-09 | 296392 | GBN3 | RURAL | Equipment failure | 31.5 | 132 | 4158 | 0.011907 | 9.0204e-05
2013-03-09 | 296393 | WRD17A | URBAN | Third party impacts | 57.75 | 595 | 34361.25 | 0.034711 | 5.8338e-05
2013-03-09 | 296395 | SBH9 | URBAN | Third party impacts | 13 | 243 | 3159 | 0.0031912 | 1.3132e-05
2013-03-09 | 296400 | TWG16 | URBAN | Other | 378.83 | 64 | 24245.12 | 0.024492 | 0.00038269
2013-03-09 | 296401 | BMT2 | RURAL | Animals | 149 | 65 | 9685 | 0.027734 | 0.00042668
2013-03-09 | 296402 | PBH1 | URBAN | Weather | 94 | 29 | 2726 | 0.0027537 | 9.4957e-05
2013-03-10 | 296411 | KRA2 | URBAN | Equipment failure | 37 | 110 | 4070 | 0.0041113 | 3.7376e-05
2013-03-10 | 296424 | GYM2A | RURAL | Weather | 153 | 219.475 | 35787.5 | 0.10248 | 0.00043813
2013-03-10 | 296481 | CRY3A | RURAL | Other | 6.105 | 188 | 1147.74 | 0.0032867 | 1.7482e-05
2013-03-11 | 296425 | MCW4 | RURAL | Equipment failure | 1262.5 | 125.9394 | 131982.5 | 0.378 | 0.0036158
2013-03-11 | 296434 | HIS13A | URBAN | Third party impacts | 572.5 | 59 | 33777.5 | 0.034117 | 0.00057826
2013-03-11 | 296434 | HIS5A | URBAN | Third party impacts | 1.5 | 230 | 345 | 0.00034847 | 1.5151e-06
2013-03-11 | 296436 | GYM2A | RURAL | Other | 84.5 | 94 | 7943 | 0.022749 | 0.00024201
2013-03-11 | 296450 | NRG10 | URBAN | Animals | 1445.5 | 64.2 | 96818 | 0.097791 | 0.00146
2013-03-11 | 296451 | NRG10 | URBAN | Animals | 408 | 61 | 24888 | 0.025138 | 0.0004121
2013-03-11 | 296478 | CFD2A | URBAN | Third party impacts | 169.95 | 107 | 18184.65 | 0.018367 | 0.00017166
2013-03-11 | 296479 | MGL5 | URBAN | Other | 17.16 | 50 | 858 | 0.00086663 | 1.7333e-05
2013-03-12 | 296476 | BMT2 | RURAL | Weather | 1310.99 | 29.3894 | 46491.78 | 0.13317 | 0.0037551
2013-03-12 | 296480 | MLT15B | URBAN | Vegetation | 80.19 | 31 | 2485.89 | 0.0025107 | 8.0991e-05
2013-03-12 | 296484 | WED20A | URBAN | Animals | 77.9922 | 137 | 10684.9314 | 0.010792 | 7.8771e-05
2013-03-12 | 296504 | KLG17A | URBAN | Third party impacts | 1180 | 50.1739 | 61133 | 0.061744 | 0.0011918
2013-03-12 | 296505 | BDT2 | RURAL | Animals | 66.5 | 277.2 | 17267.5 | 0.049459 | 0.00019048
2013-03-12 | 296508 | NMC2A | RURAL | Equipment failure | 2.2 | 270 | 594 | 0.0017014 | 6.3014e-06
2013-03-12 | 296509 | AGE10 | URBAN | Other | 34.98 | 59 | 2063.82 | 0.0020844 | 3.5329e-05
2013-03-13 | 296550 | KMR27A | URBAN | Equipment failure | 935.33 | 73.5417 | 69109.45 | 0.069795 | 0.00094461
2013-03-13 | 296579 | SRD14A | URBAN | Other | 61.07 | 70 | 4274.9 | 0.0043173 | 6.1676e-05
2013-03-13 | 296580 | AGE10 | URBAN | Equipment failure | 53 | 49 | 2597 | 0.0026228 | 5.3526e-05
2013-03-13 | 296584 | CNB24A | RURAL | Equipment failure | 34 | 266.5 | 11849 | 0.033942 | 9.7395e-05
2013-03-13 | 296587 | NRG9 | RURAL | Other | 16.66 | 540 | 8996.4 | 0.025771 | 4.7723e-05
2013-03-14 | 296581 | KMR17A | URBAN | Equipment failure | 580.5 | 84.4167 | 43425.5 | 0.043853 | 0.00058622
2013-03-14 | 296588 | NVL5 | RURAL | Equipment failure | 1262 | 184.9655 | 234781.5 | 0.67262 | 0.0036155
2013-03-14 | 296590 | AMR2 | RURAL | Other | 1 | 79 | 79 | 0.00022632 | 2.8649e-06
2013-03-14 | 296600 | KSN5 | RURAL | Third party impacts | 56 | 73 | 4088 | 0.011712 | 0.00016043
2013-03-14 | 296604 | MLT21B | URBAN | Animals | 50.0478 | 89 | 4454.2542 | 0.0044981 | 5.0541e-05
2013-03-14 | 296606 | MRE8 | URBAN | Equipment failure | 23.5 | 145 | 3407.5 | 0.0034411 | 2.3732e-05
2013-03-14 | 296612 | MGL9 | RURAL | Vegetation | 390 | 23.8125 | 10782 | 0.030889 | 0.0011173
2013-03-14 | 296617 | BDB37A | RURAL | Other | 282 | 584 | 164688 | 0.47181 | 0.00080789
2013-03-14 | 296637 | MAI14 | URBAN | Equipment failure | 4.6464 | 95 | 441.408 | 0.00044576 | 4.6922e-06
2013-03-14 | 296640 | AMR2 | RURAL | Vegetation | 860.31 | 151.6294 | 130814.5 | 0.37477 | 0.0024647
2013-03-14 | 296641 | ARG5A | URBAN | Other | 92 | 141 | 12972 | 0.0131 | 9.2906e-05
2013-03-14 | 296643 | BLB2A | URBAN | Equipment failure | 55.11 | 85 | 4684.35 | 0.0047305 | 5.5653e-05
2013-03-14 | 296644 | CRM16A | RURAL | Equipment failure | 32.67 | 79 | 2580.93 | 0.007394 | 9.3595e-05
2013-03-14 | 296675 | TGP6A | URBAN | Equipment failure | 56 | 204 | 11424 | 0.011537 | 5.6552e-05
2013-03-14 | 296681 | NDH9 | URBAN | Animals | 99.33 | 57 | 5661.81 | 0.0057176 | 0.00010031
2013-03-15 | 296646 | MLT42A | URBAN | Animals | 671.17 | 16 | 10738.72 | 0.010844 | 0.00067774
2013-03-15 | 296648 | CMD11A | RURAL | Other | 20.77 | 81 | 1682.37 | 0.0048203 | 5.951e-05
2013-03-15 | 296649 | JBB4A | URBAN | Third party impacts | 8 | 45 | 360 | 0.00036352 | 8.0783e-06
2013-03-15 | 296650 | AHL9A | URBAN | Other | 102 | 45 | 4590 | 0.0046349 | 0.000103
2013-03-15 | 296651 | WED21A | URBAN | Animals | 76.38 | 95 | 7256.1 | 0.0073271 | 7.7127e-05
2013-03-15 | 296670 | GLY4A | URBAN | Other | 47.2 | 262 | 12366.4 | 0.012487 | 4.7662e-05
2013-03-15 | 296671 | BBSRDL8 | RURAL | Other | 6 | 73 | 438 | 0.001255 | 1.7191e-05
2013-03-15 | 296679 | WRD21A | URBAN | Third party impacts | 3.135 | 43 | 134.805 | 0.00013612 | 3.1657e-06
2013-03-15 | 296682 | NMC2A | RURAL | Equipment failure | 64 | 47.8167 | 3060.2667 | 0.0087683 | 0.00018337
2013-03-15 | 296687 | BWH16A | RURAL | Equipment failure | 16 | 76 | 1216 | 0.0034841 | 4.5843e-05
2013-03-15 | 296689 | RWD1 | RURAL | Equipment failure | 3 | 95 | 285 | 0.00081658 | 8.5956e-06
2013-03-15 | 296712 | MGP13A | RURAL | Vegetation | 28 | 36.8333 | 1031.3333 | 0.002955 | 8.0226e-05
2013-03-15 | 296715 | CLM3 | RURAL | Equipment failure | 1.32 | 58 | 76.56 | 0.00021936 | 3.7821e-06
2013-03-15 | 296716 | NRG8B | URBAN | Other | 238.5 | 90 | 21465 | 0.021675 | 0.00024083
2013-03-15 | 296717 | DRD5A | URBAN | Other | 102.96 | 82 | 8442.72 | 0.0085253 | 0.00010397
2013-03-15 | 296718 | ACR1 | URBAN | Animals | 6.6 | 75 | 495 | 0.00049984 | 6.6646e-06
2013-03-16 | 296719 | MCW4 | RURAL | Other | 411 | 70 | 28770 | 0.082441 | 0.0011777
2013-03-16 | 296721 | BMT3 | RURAL | Equipment failure | 8 | 150 | 1200 | 0.0034386 | 2.2924e-05
2013-03-16 | 296722 | CHL4 | URBAN | Other | 1399.83 | 15 | 20997.45 | 0.021201 | 0.0014134
2013-03-16 | 296730 | EMP21A | RURAL | Vegetation | 51 | 194 | 9894 | 0.028352 | 0.00014614
2013-03-16 | 296731 | PRG2A | RURAL | Other | 2.5 | 217 | 542.5 | 0.0015546 | 7.1638e-06
2013-03-17 | 296729 | MTG12B | URBAN | Third party impacts | 2.3328 | 59 | 137.6352 | 0.00013897 | 2.3554e-06
2013-03-17 | 296736 | JDL4A | URBAN | Vegetation | 39.3 | 19 | 746.7 | 0.00075393 | 3.968e-05
2013-03-17 | 296737 | NRA13A | RURAL | Vegetation | 287.5 | 3 | 862.5 | 0.0024716 | 0.00082386
2013-03-17 | 296738 | CHL5 | URBAN | Third party impacts | 2035.83 | 47.275 | 193766.1 | 0.19564 | 0.0020555
2013-03-17 | 296739 | WED21A | URBAN | Equipment failure | 368 | 74 | 27232 | 0.027496 | 0.00037156
2013-03-17 | 296739 | WED3A | URBAN | Equipment failure | 615 | 74 | 45510 | 0.045951 | 0.00062095
2013-03-17 | 296739 | WED6A | URBAN | Equipment failure | 2426.44 | 81 | 196541.64 | 0.19844 | 0.0024499
2013-03-17 | 296740 | CHL4 | URBAN | Vegetation | 94.5 | 160 | 15120 | 0.015266 | 9.5415e-05
2013-03-17 | 296742 | NRG14A | RURAL | Vegetation | 336.5 | 84.4706 | 28728 | 0.082323 | 0.00096427
2013-03-17 | 296753 | BWH16A | RURAL | Vegetation | 280.34 | 60 | 16820.4 | 0.0482 | 0.00080334
2013-03-17 | 296754 | SGT22A | URBAN | Equipment failure | 9.3 | 171 | 1590.3 | 0.0016057 | 9.39e-06
2013-03-17 | 296756 | EMP4A | URBAN | Equipment failure | 4.183 | 79 | 330.457 | 0.00033366 | 4.2235e-06
2013-03-17 | 296757 | IPS1B | URBAN | Equipment failure | 21 | 45 | 945 | 0.00095415 | 2.1203e-05
2013-03-17 | 296758 | WMD6A | URBAN | Vegetation | 1058 | 42 | 44436 | 0.044866 | 0.0010682
2013-03-17 | 296856 | CVL5A | RURAL | Other | 15.84 | 50 | 792 | 0.0022696 | 4.5391e-05
2013-03-17 | 296857 | KSN7 | RURAL | Other | 14.52 | 76 | 1103.52 | 0.0031622 | 4.1608e-05
2013-03-17 | 296858 | KSN6 | URBAN | Equipment failure | 54 | 23 | 1242 | 0.001254 | 5.4523e-05
2013-03-18 | 296759 | NMK23A | URBAN | Equipment failure | 1502.33 | 19.7273 | 31443.61 | 0.031745 | 0.0015167
2013-03-18 | 296761 | GGR5 | RURAL | Vegetation | 979.5 | 64 | 62688 | 0.17967 | 0.0028074
2013-03-18 | 296777 | NRA16A | RURAL | Vegetation | 114 | 7 | 798 | 0.0022872 | 0.00032674
2013-03-18 | 296783 | PWC4 | RURAL | Equipment failure | 15 | 41 | 615 | 0.0017627 | 4.2992e-05
2013-03-18 | 296800 | GLY4A | URBAN | Equipment failure | 44 | 45 | 1980 | 0.0019989 | 4.4421e-05
2013-03-18 | 296805 | BNH1B | RURAL | Other | 2 | 335 | 670 | 0.0019203 | 5.7322e-06
2013-03-19 | 296806 | TPT5 | RURAL | Equipment failure | 10 | 103 | 1030 | 0.0029525 | 2.8665e-05
2013-03-19 | 296807 | NGI3A | RURAL | Other | 0.33 | 80 | 26.4 | 7.5675e-05 | 9.4593e-07
2013-03-19 | 296809 | AHD10A | URBAN | Equipment failure | 59.5 | 120 | 7140 | 0.0072079 | 6.0065e-05
2013-03-19 | 296810 | GYM2A | RURAL | Other | 59 | 79 | 4661 | 0.013361 | 0.00016912
2013-03-19 | 296813 | RBARHP14 | URBAN | Other | 39 | 4 | 156 | 0.00015748 | 3.9371e-05
2013-03-19 | 296815 | LTN2 | RURAL | Animals | 1707.33 | 39.2857 | 58503.16 | 0.1677 | 0.004894
2013-03-19 | 296848 | CMA15A | URBAN | Other | 18 | 68 | 1224 | 0.0012356 | 1.8171e-05
2013-03-19 | 296850 | PBH1 | URBAN | Vegetation | 9.57 | 53 | 507.21 | 0.00051203 | 9.6609e-06
2013-03-19 | 296853 | PWC4 | RURAL | Weather | 12 | 98 | 1176 | 0.003371 | 3.4398e-05
2013-03-19 | 296861 | BPN28A | RURAL | Other | 92 | 27 | 2484 | 0.0071203 | 0.00026371
2013-03-19 | 296862 | RST20A | URBAN | Other | 72 | 41.5 | 5734.8 | 0.0057893 | 7.2684e-05
2013-03-20 | 296860 | AGT31A | RURAL | Animals | 391 | 192.102 | 86093 | 0.24682 | 0.001121
2013-03-20 | 296871 | CDRSPD12 | URBAN | Equipment failure | 20.995 | 84 | 1763.58 | 0.0017802 | 2.1193e-05
2013-03-20 | 296879 | LLY3 | RURAL | Equipment failure | 1 | 98 | 98 | 0.00028096 | 2.8669e-06
2013-03-20 | 296882 | CPR6 | URBAN | Third party impacts | 326 | 121 | 39446 | 0.039818 | 0.00032907
2013-03-20 | 296885 | NSW28 | URBAN | Animals | 69.3 | 63 | 4365.9 | 0.0044071 | 6.9953e-05
2013-03-20 | 296886 | WSE3A | RURAL | Other | 0.87 | 540 | 469.8 | 0.0013469 | 2.4942e-06
2013-03-20 | 296887 | NRG9 | RURAL | Third party impacts | 149 | 118.5517 | 17679 | 0.050684 | 0.00042717
2013-03-20 | 296912 | 341 | URBAN | Other | 35 | 216.1429 | 8583 | 0.0086639 | 3.533e-05
2013-03-20 | 296912 | TCB1 | RURAL | Other | 1363.49 | 23.925 | 24542.82 | 0.070362 | 0.003909
2013-03-20 | 296914 | RST20A | URBAN | Other | 72 | 38 | 2736 | 0.0027618 | 7.2679e-05
2013-03-21 | 296930 | HTN3A | URBAN | Equipment failure | 39 | 229 | 8931 | 0.0090146 | 3.9365e-05
2013-03-21 | 296932 | PBH4 | URBAN | Equipment failure | 1030.49 | 107.3571 | 98279.1 | 0.099199 | 0.0010401
2013-03-21 | 296933 | HTN24A | URBAN | Third party impacts | 39 | 90 | 3510 | 0.0035429 | 3.9365e-05
2013-03-21 | 296934 | LGV2B | RURAL | Vegetation | 13.86 | 113 | 1566.18 | 0.0044907 | 3.9741e-05
2013-03-21 | 296950 | SARSHW7 | URBAN | Equipment failure | 70.83 | 134 | 9491.22 | 0.0095801 | 7.1493e-05
2013-03-21 | 296960 | CVL15A | URBAN | Equipment failure | 95 | 26 | 2470 | 0.0024931 | 9.5889e-05
2013-03-21 | 296964 | BMT3 | RURAL | Equipment failure | 47 | 117 | 5499 | 0.015767 | 0.00013476
2013-03-21 | 296990 | HDA14A | URBAN | Equipment failure | 17.5 | 45 | 787.5 | 0.00079487 | 1.7664e-05
2013-03-21 | 297010 | TGW1 | RURAL | Equipment failure | 0.335 | 93 | 31.155 | 8.9331e-05 | 9.6055e-07
2013-03-22 | 296991 | 311 | URBAN | Animals | 1 | 142 | 142 | 0.00014332 | 1.0093e-06
2013-03-22 | 297011 | BDB33A | URBAN | Third party impacts | 9 | 47 | 423 | 0.00042692 | 9.0835e-06
2013-03-22 | 297030 | CRM16A | RURAL | Other | 9.63 | 45 | 433.35 | 0.0012428 | 2.7617e-05
2013-03-22 | 297031 | BMT2 | RURAL | Other | 4.29 | 128 | 549.12 | 0.0015748 | 1.2303e-05
2013-03-22 | 297032 | HDA14A | URBAN | Equipment failure | 11.25 | 126 | 1417.5 | 0.0014307 | 1.1354e-05
2013-03-22 | 297063 | WFD1B | RURAL | Other | 79.99 | 20 | 1599.8 | 0.004588 | 0.0002294
2013-03-22 | 297064 | DRD3A | URBAN | Equipment failure | 84 | 84 | 7056 | 0.0071215 | 8.4779e-05
2013-03-22 | 297065 | RLB11B | URBAN | Other | 44 | 27 | 1188 | 0.001199 | 4.4408e-05
2013-03-22 | 297066 | ABY2A | RURAL | Other | 1 | 64 | 64 | 0.00018354 | 2.8678e-06
2013-03-22 | 297087 | IDY1A | URBAN | Animals | 38.94 | 54 | 2102.76 | 0.0021223 | 3.9301e-05
2013-03-23 | 297067 | BRD8A | RURAL | Other | 995.99 | 16 | 15935.84 | 0.04571 | 0.0028569
2013-03-23 | 297070 | PWC4 | RURAL | Other | 4.29 | 82 | 351.78 | 0.001009 | 1.2305e-05
2013-03-23 | 297071 | TGP8A | URBAN | Vegetation | 49.17 | 58 | 2851.86 | 0.0028781 | 4.9622e-05
2013-03-23 | 297072 | GVN16A | RURAL | Equipment failure | 184 | 645 | 118680 | 0.34042 | 0.00052779
2013-03-23 | 297073 | GVN16A | RURAL | Equipment failure | 184 | 10 | 1840 | 0.0052779 | 0.00052779
2013-03-23 | 297074 | SQBT1 | HIGH-DENSITY | Other | 13 | 115 | 1495 | 0.38649 | 0.0033607
2013-03-23 | 297075 | BWH16A | RURAL | Vegetation | 5 | 143 | 715 | 0.0020509 | 1.4342e-05
2013-03-23 | 297082 | MRK7A | URBAN | Equipment failure | 0.3 | 432 | 129.6 | 0.00013079 | 3.0276e-07
2013-03-23 | 297212 | CPK7 | URBAN | Equipment failure | 70.9061 | 277 | 19640.9897 | 0.019822 | 7.1558e-05
2013-03-24 | 297093 | 367 | URBAN | Equipment failure | 2 | 18 | 36 | 3.6329e-05 | 2.0183e-06
2013-03-24 | 297093 | 368 | URBAN | Equipment failure | 2 | 18 | 36 | 3.6329e-05 | 2.0183e-06
2013-03-24 | 297093 | 420 | URBAN | Equipment failure | 1 | 18 | 18 | 1.8165e-05 | 1.0091e-06
2013-03-24 | 297093 | CHBT0 | URBAN | Equipment failure | 1 | 18 | 18 | 1.8165e-05 | 1.0091e-06
2013-03-24 | 297093 | MCW11 | RURAL | Equipment failure | 806.5 | 18 | 14517 | 0.041645 | 0.0023136
2013-03-24 | 297093 | MCW4 | RURAL | Equipment failure | 1263.5 | 18 | 22743 | 0.065244 | 0.0036247
2013-03-24 | 297093 | MCW7 | RURAL | Equipment failure | 386 | 18 | 6948 | 0.019932 | 0.0011073
2013-03-24 | 297093 | WTPT0 | URBAN | Equipment failure | 1 | 18 | 18 | 1.8165e-05 | 1.0091e-06
2013-03-24 | 297107 | GTN12A | RURAL | Weather | 577 | 99.3556 | 49656 | 0.14245 | 0.0016553
2013-03-24 | 297110 | KSN15 | RURAL | Weather | 906.17 | 413 | 379233.49 | 1.0879 | 0.0025996
2013-03-24 | 297111 | LGL5A | URBAN | Weather | 433 | 294 | 127302 | 0.12847 | 0.00043696
2013-03-24 | 297112 | LGL13A | URBAN | Other | 520 | 211 | 109720 | 0.11072 | 0.00052475
2013-03-24 | 297122 | LGL15A | URBAN | Equipment failure | 946 | 777.4286 | 996155 | 1.0053 | 0.00095465
2013-03-24 | 297124 | LGL3A | URBAN | Equipment failure | 668 | 504.8 | 337297 | 0.34038 | 0.00067411
2013-03-24 | 297125 | MRK7A | URBAN | Other | 71.49 | 239 | 17086.11 | 0.017242 | 7.2144e-05
2013-03-24 | 297126 | ALY6 | URBAN | Weather | 788.16 | 346 | 300355.2 | 0.3031 | 0.00079537
2013-03-24 | 297133 | KRN5A | URBAN | Other | 772.5 | 216.3462 | 253305.5 | 0.25562 | 0.00077956
2013-03-24 | 297133 | KRN5B | URBAN | Other | 323.5 | 154 | 49819 | 0.050274 | 0.00032646
2013-03-24 | 297138 | CMV11A | URBAN | Weather | 1437 | 186 | 267282 | 0.26973 | 0.0014501
2013-03-24 | 297140 | HTN22A | URBAN | Weather | 307 | 188 | 57716 | 0.058244 | 0.00030981
2013-03-24 | 297140 | HTN22B | URBAN | Weather | 438.33 | 188 | 82406.04 | 0.083159 | 0.00044234
2013-03-24 | 297141 | MRK6 | URBAN | Weather | 1744.25 | 231 | 402921.75 | 0.40661 | 0.0017602
2013-03-24 | 297144 | EMP21A | RURAL | Weather | 1701.99 | 104 | 177006.96 | 0.50779 | 0.0048826
2013-03-24 | 297144 | EMP22A | URBAN | Weather | 70.99 | 104 | 7382.96 | 0.0074505 | 7.1639e-05
2013-03-24 | 297144 | EMP23A | URBAN | Weather | 1607 | 104 | 167128 | 0.16866 | 0.0016217
2013-03-24 | 297144 | EMP25A | URBAN | Weather | 719 | 104 | 74776 | 0.07546 | 0.00072557
2013-03-24 | 297147 | TRG10B | URBAN | Weather | 505.5 | 145 | 73297.5 | 0.073968 | 0.00051012
2013-03-24 | 297148 | BVL5A | URBAN | Weather | 1836.5 | 436 | 800714 | 0.80803 | 0.0018533
2013-03-24 | 297154 | 452 | URBAN | Weather | 1 | 498 | 498 | 0.00050255 | 1.0091e-06
2013-03-24 | 297156 | MTG3A | URBAN | Weather | 1155.17 | 482 | 556791.94 | 0.56188 | 0.0011657
2013-03-24 | 297158 | LHM2 | URBAN | Weather | 354.66 | 518 | 183713.88 | 0.18539 | 0.0003579
2013-03-24 | 297159 | KSN1 | URBAN | Weather | 1276 | 74.4444 | 153710 | 0.15512 | 0.0012877
2013-03-24 | 297159 | KSN8 | RURAL | Weather | 1445.99 | 570.1 | 1106379.23 | 3.1739 | 0.0041482
2013-03-24 | 297160 | THL1 | RURAL | Weather | 188 | 292.2222 | 59240 | 0.16994 | 0.00053932
2013-03-24 | 297162 | MSV1 | RURAL | Weather | 144 | 37 | 5328 | 0.015285 | 0.0004131
2013-03-24 | 297162 | MSV2 | RURAL | Weather | 168.01 | 37 | 6216.37 | 0.017833 | 0.00048198
2013-03-24 | 297162 | THL1 | RURAL | Weather | 362 | 37 | 13394 | 0.038424 | 0.0010385
2013-03-24 | 297162 | THL2 | RURAL | Weather | 197.49 | 37 | 7307.13 | 0.020962 | 0.00056655
2013-03-24 | 297162 | THL3 | RURAL | Weather | 469.33 | 37 | 17365.21 | 0.049816 | 0.0013464
2013-03-24 | 297165 | NRA13A | RURAL | Equipment failure | 2059.66 | 272.8654 | 553353.56 | 1.5874 | 0.0059086
2013-03-24 | 297172 | SHW3 | URBAN | Weather | 94.5 | 2 | 189 | 0.00019073 | 9.5364e-05
2013-03-24 | 297173 | JBB1B | RURAL | Weather | 1513.5 | 522.4253 | 784687.5 | 2.2511 | 0.0043418
2013-03-24 | 297175 | TRP3 | RURAL | Weather | 3 | 448 | 1344 | 0.0038556 | 8.6062e-06
2013-03-24 | 297176 | CRM13A | URBAN | Weather | 1772 | 482.7143 | 858360.25 | 0.86621 | 0.0017882
2013-03-24 | 297176 | CRM13B | URBAN | Weather | 23.5 | 442 | 10387 | 0.010482 | 2.3715e-05
2013-03-24 | 297178 | TMH15A | URBAN | Weather | 1694.67 | 319.3514 | 627365.73 | 0.6331 | 0.0017102
2013-03-24 | 297179 | TMH16A | URBAN | Weather | 525.83 | 447 | 230848.89 | 0.23296 | 0.00053064
2013-03-24 | 297180 | WRG8A | URBAN | Weather | 1277 | 339 | 432903 | 0.43686 | 0.0012887
2013-03-24 | 297181 | NMC1B | RURAL | Weather | 1320.5 | 465.7188 | 582330.74 | 1.6706 | 0.0037882
2013-03-24 | 297182 | BBSRDL8 | RURAL | Weather | 1298.44 | 240 | 311625.6 | 0.89397 | 0.0037249
2013-03-24 | 297183 | TMH3A | URBAN | Weather | 841.99 | 688.3077 | 579686.52 | 0.58499 | 0.00084969
2013-03-24 | 297184 | BKD5B | RURAL | Weather | 1756.17 | 457.9655 | 785028.8 | 2.252 | 0.005038
2013-03-24 | 297185 | LHM5 | RURAL | Weather | 859.33 | 627.4 | 537489.55 | 1.5419 | 0.0024652
2013-03-24 | 297186 | CMV14 | URBAN | Weather | 1189 | 561 | 641452 | 0.64732 | 0.0011999
2013-03-24 | 297188 | STL1A | URBAN | Vegetation | 247.5 | 22 | 5445 | 0.0054948 | 0.00024976
2013-03-24 | 297189 | TRG10B | URBAN | Weather | 74 | 30 | 2220 | 0.0022403 | 7.4677e-05
2013-03-24 | 297190 | AGT31A | RURAL | Weather | 389 | 395.2857 | 167705 | 0.4811 | 0.0011159
2013-03-24 | 297191 | KCY4 | RURAL | Weather | 10.5 | 203 | 2131.5 | 0.0061147 | 3.0122e-05
2013-03-24 | 297192 | CBW6 | RURAL | Weather | 2147 | 175.8 | 378749 | 1.0865 | 0.0061592
2013-03-24 | 297193 | MTG5A | URBAN | Weather | 489.5 | 455 | 222722.5 | 0.22476 | 0.00049398
2013-03-24 | 297194 | LGV6A | RURAL | Weather | 721.5 | 397 | 286435.5 | 0.82171 | 0.0020698
2013-03-24 | 297195 | NPD1 | URBAN | Weather | 6 | 230 | 1380 | 0.0013926 | 6.0549e-06
2013-03-24 | 297196 | RLB13B | RURAL | Weather | 1892.47 | 606 | 1146836.82 | 3.29 | 0.005429
2013-03-24 | 297197 | BDT5 | RURAL | Weather | 898.01 | 715 | 642077.15 | 1.842 | 0.0025762
2013-03-24 | 297198 | LGV3A | RURAL | Equipment failure | 205.5 | 12 | 2466 | 0.0070743 | 0.00058953
2013-03-24 | 297198 | LGV5B | RURAL | Equipment failure | 601.5 | 231.5636 | 223568 | 0.64136 | 0.0017255
2013-03-24 | 297200 | NMC5A | RURAL | Weather | 403 | 318 | 128154 | 0.36764 | 0.0011561
2013-03-24 | 297201 | KSN4 | URBAN | Weather | 74 | 224 | 16576 | 0.016728 | 7.4677e-05
2013-03-24 | 297202 | CRM5A | URBAN | Weather | 8.25 | 259 | 2136.75 | 0.0021563 | 8.3254e-06
2013-03-24 | 297203 | KBR1A | RURAL | Vegetation | 5.28 | 77 | 406.56 | 0.0011663 | 1.5147e-05
2013-03-24 | 297204 | GGR4 | RURAL | Weather | 27.5 | 66 | 1815 | 0.0052068 | 7.889e-05
2013-03-24 | 297205 | IPS2B | RURAL | Weather | 7.92 | 13 | 102.96 | 0.00029537 | 2.272e-05
2013-03-24 | 297206 | NSW17 | URBAN | Equipment failure | 1293.5 | 577.5 | 724008 | 0.73063 | 0.0013053
2013-03-24 | 297207 | LGV2A | URBAN | Equipment failure | 1 | 189 | 189 | 0.00019073 | 1.0091e-06
2013-03-24 | 297207 | LGV2B | RURAL | Equipment failure | 634 | 722.2841 | 706073 | 2.0255 | 0.0018188
2013-03-24 | 297208 | LLY4 | RURAL | Weather | 10.72 | 123 | 1318.56 | 0.0037826 | 3.0753e-05
2013-03-24 | 297209 | LRE7A | RURAL | Weather | 23 | 34 | 1093.42 | 0.0031367 | 6.5981e-05
2013-03-24 | 297210 | FDS1 | RURAL | Weather | 0.67 | 134 | 89.78 | 0.00025756 | 1.9221e-06
2013-03-24 | 297211 | ALY5 | URBAN | Weather | 325.33 | 326 | 143512.8229 | 0.14482 | 0.0003283
2013-03-24 | 297214 | ABY2A | RURAL | Weather | 1 | 100 | 100 | 0.00028687 | 2.8687e-06
2013-03-24 | 297215 | KBR6A | RURAL | Weather | 1 | 165 | 165 | 0.00047334 | 2.8687e-06
2013-03-24 | 297216 | LLY3 | RURAL | Weather | 2.01 | 269 | 540.69 | 0.0015511 | 5.7662e-06
2013-03-24 | 297217 | JBB2A | RURAL | Weather | 98.5 | 1133 | 111600.5 | 0.32015 | 0.00028257
2013-03-24 | 297218 | BTN7 | RURAL | Weather | 65.99 | 448.9683 | 46338.39 | 0.13293 | 0.00018931
2013-03-24 | 297224 | 357 | URBAN | Weather | 1 | 1062 | 1062 | 0.0010717 | 1.0091e-06
2013-03-24 | 297255 | WRG2A | URBAN | Weather | 1445.25 | 692.5556 | 994980.5 | 1.0041 | 0.0014585
2013-03-24 | 297269 | BPN29A | URBAN | Weather | 17 | 296 | 10064 | 0.010156 | 1.7155e-05
2013-03-24 | 297270 | BDT3 | RURAL | Weather | 667.5 | 304.3151 | 196416 | 0.56347 | 0.0019149
2013-03-24 | 297271 | CPB6 | URBAN | Other | 21 | 1075 | 22575 | 0.022781 | 2.1192e-05
2013-03-24 | 297273 | BDT1 | RURAL | Weather | 1080.97 | 543.8 | 588478.65 | 1.6882 | 0.003101
2013-03-24 | 297275 | CHL9 | RURAL | Equipment failure | 35.97 | 340 | 12229.8 | 0.035084 | 0.00010319
2013-03-24 | 297345 | CMV11A | URBAN | Weather | 301.5 | 1116 | 336474 | 0.33955 | 0.00030426
2013-03-24 | 297355 | SDM1 | RURAL | Equipment failure | 20 | 380 | 7600 | 0.021802 | 5.7375e-05
2013-03-24 | 297374 | BTA5A | RURAL | Weather | 1714 | 974.6418 | 1643418 | 4.7145 | 0.004917
2013-03-24 | 297388 | LGV3A | RURAL | Equipment failure | 4.69 | 1689 | 7921.41 | 0.022724 | 1.3454e-05
2013-03-24 | 297392 | NRG16A | RURAL | Weather | 518.5 | 168.4737 | 110973.5 | 0.31835 | 0.0014874
2013-03-24 | 297413 | CRM16A | RURAL | Weather | 1494.49 | 414.3333 | 555600.98 | 1.5939 | 0.0042873
2013-03-24 | 297420 | JBB3A | RURAL | Weather | 893.5 | 240 | 214440 | 0.61517 | 0.0025632
2013-03-24 | 297427 | 403 | URBAN | Weather | 1 | 4 | 4 | 4.0366e-06 | 1.0091e-06
2013-03-24 | 297427 | 404 | URBAN | Weather | 1 | 4 | 4 | 4.0366e-06 | 1.0091e-06
2013-03-24 | 297427 | 468 | URBAN | Weather | 1 | 342 | 342 | 0.00034513 | 1.0091e-06
2013-03-24 | 297427 | 469 | URBAN | Weather | 1 | 318 | 318 | 0.00032091 | 1.0091e-06
2013-03-24 | 297427 | BDT1 | RURAL | Weather | 1080.97 | 4 | 4323.88 | 0.012404 | 0.003101
2013-03-24 | 297427 | BDT2 | RURAL | Weather | 259 | 4 | 1036 | 0.002972 | 0.000743
2013-03-24 | 297427 | BDT3 | RURAL | Weather | 667.5 | 4 | 2670 | 0.0076595 | 0.0019149
2013-03-24 | 297427 | BDT4 | RURAL | Weather | 1308.49 | 4 | 5233.96 | 0.015015 | 0.0037537
2013-03-24 | 297427 | BDT5 | RURAL | Weather | 898.01 | 4 | 3592.04 | 0.010305 | 0.0025762
2013-03-24 | 297427 | BDT6 | URBAN | Weather | 430.5 | 4 | 1722 | 0.0017377 | 0.00043444
2013-03-24 | 297427 | IPL1 | RURAL | Weather | 599.64 | 4 | 2398.56 | 0.0068808 | 0.0017202
2013-03-24 | 297427 | IPL2A | RURAL | Weather | 284.48 | 4 | 1137.92 | 0.0032644 | 0.0008161
2013-03-24 | 297427 | IPL3 | RURAL | Weather | 429.48 | 4 | 1717.92 | 0.0049283 | 0.0012321
2013-03-24 | 297427 | IPL4A | RURAL | Weather | 29.33 | 4 | 117.32 | 0.00033656 | 8.414e-05
2013-03-24 | 297429 | JBB12A | URBAN | Equipment failure | 1 | 441 | 441 | 0.00044503 | 1.0091e-06
2013-03-24 | 297429 | JBB12B | RURAL | Equipment failure | 754.5 | 441 | 332734.5 | 0.95453 | 0.0021645
2013-03-24 | 297435 | ARL13A | URBAN | Weather | 953 | 49 | 46697 | 0.047124 | 0.00096171
2013-03-24 | 297538 | LDR2B | URBAN | Equipment failure | 1 | 59 | 59 | 5.9539e-05 | 1.0091e-06
2013-03-24 | 297539 | JBB13A | RURAL | Equipment failure | 212.49 | 2 | 424.98 | 0.0012192 | 0.00060958
2013-03-24 | 297539 | JBB16A | RURAL | Equipment failure | 658.5 | 620.987 | 508943.5 | 1.46 | 0.0018891
2013-03-24 | 297539 | TBV4 | RURAL | Equipment failure | 75.5 | 2 | 151 | 0.00043318 | 0.00021659
2013-03-24 | 297540 | JBB13A | RURAL | Weather | 1104.48 | 687.6528 | 774563.78 | 2.222 | 0.0031685
2013-03-25 | 297168 | TMH5A | URBAN | Equipment failure | 1079.68 | 9 | 9717.12 | 0.0098047 | 0.0010894
2013-03-25 | 297199 | SDM1 | RURAL | Weather | 1 | 181 | 181 | 0.00051939 | 2.8696e-06
2013-03-25 | 297221 | LLY4 | RURAL | Weather | 5 | 222 | 1110 | 0.0031852 | 1.4348e-05
2013-03-25 | 297223 | KWA3A | URBAN | Equipment failure | 736.5 | 14 | 10311 | 0.010404 | 0.00074314
2013-03-25 | 297225 | PRG2A | RURAL | Weather | 0.85 | 140 | 119 | 0.00034148 | 2.4391e-06
2013-03-25 | 297226 | LGL11A | URBAN | Other | 35.25 | 750 | 26437.5 | 0.026676 | 3.5568e-05
2013-03-25 | 297228 | GLY3A | URBAN | Weather | 3.5 | 200 | 700 | 0.00070631 | 3.5315e-06
2013-03-25 | 297240 | LLY4 | RURAL | Weather | 3.3 | 107 | 353.1 | 0.0010132 | 9.4696e-06
2013-03-25 | 297241 | DRD2A | RURAL | Equipment failure | 1825 | 242.7576 | 449081 | 1.2887 | 0.005237
2013-03-25 | 297241 | DRD2B | URBAN | Equipment failure | 1 | 180 | 180 | 0.00018162 | 1.009e-06
2013-03-25 | 297248 | GGR2 | RURAL | Weather | 3 | 56 | 168 | 0.00048209 | 8.6087e-06
2013-03-25 | 297249 | CRM16A | RURAL | Weather | 10 | 218 | 2180 | 0.0062556 | 2.8696e-05
2013-03-25 | 297250 | TMH3A | URBAN | Vegetation | 74 | 23 | 1702 | 0.0017173 | 7.4667e-05
2013-03-25 | 297251 | AGT23A | URBAN | Weather | 11.22 | 236 | 2647.92 | 0.0026718 | 1.1321e-05
2013-03-25 | 297253 | KSN7 | RURAL | Vegetation | 18.15 | 189 | 3430.35 | 0.0098436 | 5.2083e-05
2013-03-25 | 297254 | LGL15A | URBAN | Weather | 78.21 | 153 | 11966.13 | 0.012074 | 7.8915e-05
2013-03-25 | 297256 | CFD2A | URBAN | Vegetation | 9.2 | 18 | 165.6 | 0.00016709 | 9.2829e-06
2013-03-25 | 297257 | TMH16A | URBAN | Equipment failure | 131.5 | 73 | 9599.5 | 0.009686 | 0.00013268
2013-03-25 | 297265 | TMH5A | URBAN | Weather | 113 | 129.5 | 14198 | 0.014326 | 0.00011402
2013-03-25 | 297266 | LGV2B | RURAL | Weather | 27 | 453 | 12231 | 0.035098 | 7.7478e-05
2013-03-25 | 297272 | LGV3A | RURAL | Animals | 21 | 167 | 3507 | 0.010064 | 6.0261e-05
2013-03-25 | 297274 | MTG5A | URBAN | Weather | 107.17 | 415 | 44475.55 | 0.044876 | 0.00010814
2013-03-25 | 297276 | BDT5 | RURAL | Weather | 5 | 103 | 515 | 0.0014778 | 1.4348e-05
2013-03-25 | 297278 | MGP13A | RURAL | Weather | 6 | 63 | 378 | 0.0010847 | 1.7217e-05
2013-03-25 | 297281 | BMT2 | RURAL | Equipment failure | 161.5 | 251.8868 | 38175 | 0.10955 | 0.00046343
2013-03-25 | 297282 | CMV14 | URBAN | Weather | 53 | 100 | 5300 | 0.0053478 | 5.3478e-05
2013-03-25 | 297295 | SMF1B | RURAL | Other | 29 | 247 | 7163 | 0.020555 | 8.3217e-05
2013-03-25 | 297299 | KSN8 | RURAL | Other | 20.5 | 352 | 7216 | 0.020707 | 5.8826e-05
2013-03-25 | 297313 | AHL14A | URBAN | Equipment failure | 64.68 | 81 | 5239.08 | 0.0052863 | 6.5263e-05
2013-03-25 | 297316 | NSW17 | URBAN | Other | 63 | 620 | 39060 | 0.039412 | 6.3568e-05
2013-03-25 | 297317 | JBB16A | RURAL | Weather | 7 | 129 | 903 | 0.0025912 | 2.0087e-05
2013-03-25 | 297318 | KSN7 | RURAL | Equipment failure | 10 | 141 | 1410 | 0.0040461 | 2.8696e-05
2013-03-25 | 297319 | CVL7A | RURAL | Equipment failure | 7.5 | 864 | 6480 | 0.018595 | 2.1522e-05
2013-03-25 | 297327 | BDT5 | RURAL | Weather | 9 | 722 | 6498 | 0.018646 | 2.5826e-05
2013-03-25 | 297333 | ABY2A | RURAL | Equipment failure | 1 | 246 | 246 | 0.00070591 | 2.8696e-06
2013-03-25 | 297334 | GTN5B | RURAL | Other | 1 | 132 | 132 | 0.00037878 | 2.8696e-06
2013-03-25 | 297335 | LLY4 | RURAL | Other | 0.67 | 301 | 201.67 | 0.0005787 | 1.9226e-06
2013-03-25 | 297336 | GGR1 | RURAL | Other | 2.01 | 632 | 1270.32 | 0.0036453 | 5.7678e-06
2013-03-25 | 297337 | PRG2B | RURAL | Other | 4 | 235 | 940 | 0.0026974 | 1.1478e-05
2013-03-25 | 297338 | TGW3 | RURAL | Other | 0.67 | 210 | 140.7 | 0.00040375 | 1.9226e-06
2013-03-25 | 297339 | WHO9 | RURAL | Other | 1 | 304 | 304 | 0.00087235 | 2.8696e-06
2013-03-25 | 297389 | WRG9A | URBAN | Other | 718.25 | 145 | 104146.25 | 0.10508 | 0.00072472
2013-03-25 | 297390 | GGR1 | RURAL | Equipment failure | 19 | 115 | 2185 | 0.00627 | 5.4522e-05
2013-03-25 | 297391 | KSN2A | RURAL | Vegetation | 998 | 121 | 120758 | 0.34652 | 0.0028638
2013-03-25 | 297404 | SBH4 | URBAN | Equipment failure | 29.7 | 71 | 2108.7 | 0.0021277 | 2.9968e-05
2013-03-26 | 297321 | WHO1 | RURAL | Equipment failure | 388.5 | 8 | 3108 | 0.0089205 | 0.0011151
2013-03-26 | 297324 | HPE13A | URBAN | Weather | 6.6 | 67 | 442.2 | 0.00044615 | 6.6589e-06
2013-03-26 | 297361 | LGV2B | RURAL | Vegetation | 519.5 | 2 | 1039 | 0.0029821 | 0.001491
2013-03-26 | 297375 | NMC1B | RURAL | Vegetation | 1321.5 | 108.9615 | 158396.15 | 0.45462 | 0.0037929
2013-03-26 | 297378 | LTA4B | URBAN | Weather | 66 | 176 | 11616 | 0.01172 | 6.6589e-05
2013-03-26 | 297386 | ABY2A | RURAL | Equipment failure | 62.5 | 661.375 | 42467.5 | 0.12189 | 0.00017938
2013-03-26 | 297387 | NSD9A | URBAN | Equipment failure | 3.266 | 541 | 1766.906 | 0.0017827 | 3.2951e-06
2013-03-26 | 297405 | RLA5 | URBAN | Third party impacts | 42.24 | 243 | 10264.32 | 0.010356 | 4.2617e-05
2013-03-26 | 297407 | THL4 | URBAN | Equipment failure | 8 | 80 | 640 | 0.00064571 | 8.0714e-06
2013-03-26 | 297408 | YTA2A | URBAN | Other | 5 | 53 | 265 | 0.00026736 | 5.0446e-06
2013-03-26 | 297409 | MFD3A | RURAL | Animals | 21.12 | 101 | 2133.12 | 0.0061224 | 6.0618e-05
2013-03-26 | 297431 | YTA2A | URBAN | Third party impacts | 1761 | 123.9756 | 219438 | 0.2214 | 0.0017767
2013-03-26 | 297431 | YTA2B | RURAL | Third party impacts | 1088.5 | 85 | 92522.5 | 0.26555 | 0.0031242
2013-03-27 | 297417 | SBK9 | URBAN | Equipment failure | 94 | 64 | 6016 | 0.0060691 | 9.483e-05
2013-03-27 | 297430 | MLS90B | URBAN | Third party impacts | 1 | 440 | 440 | 0.00044389 | 1.0088e-06
2013-03-27 | 297433 | MLY1 | RURAL | Vegetation | 205 | 149.0857 | 29186 | 0.083786 | 0.00058851
2013-03-27 | 297437 | BNH6A | RURAL | Equipment failure | 66 | 106.0227 | 6007 | 0.017245 | 0.00018947
2013-03-27 | 297438 | BKD5B | RURAL | Third party impacts | 14.88 | 275 | 4092 | 0.011747 | 4.2717e-05
2013-03-27 | 297439 | BBS6 | URBAN | Equipment failure | 33.825 | 118 | 3991.35 | 0.0040266 | 3.4124e-05
2013-03-27 | 297462 | TWG13A | URBAN | Vegetation | 1045.5 | 119.6 | 259152 | 0.26144 | 0.0010547
2013-03-27 | 297462 | TWG13B | URBAN | Vegetation | 450.01 | 58 | 52201.16 | 0.052662 | 0.00045398
2013-03-27 | 297469 | TWG21 | URBAN | Other | 944.5 | 37 | 34946.5 | 0.035255 | 0.00095284
2013-03-27 | 297472 | CRM16A | RURAL | Other | 4 | 285 | 1140 | 0.0032727 | 1.1483e-05
2013-03-27 | 297473 | KSN2A | RURAL | Equipment failure | 77 | 272 | 20944 | 0.060125 | 0.00022105
2013-03-27 | 297474 | YDA1B | RURAL | Vegetation | 14.85 | 54 | 801.9 | 0.0023021 | 4.2631e-05
2013-03-28 | 297500 | CFD8A | URBAN | Other | 47.5 | 80 | 3800 | 0.0038331 | 4.7913e-05
2013-03-28 | 297503 | TRG10B | URBAN | Equipment failure | 82.5 | 43 | 3547.5 | 0.0035784 | 8.3218e-05
2013-03-28 | 297509 | MLY4 | RURAL | Other | 7.5 | 232 | 1740 | 0.0049967 | 2.1537e-05
2013-03-28 | 297510 | KRN2 | URBAN | Other | 275 | 4 | 1100 | 0.0011096 | 0.00027739
2013-03-28 | 297534 | MGP13A | RURAL | Other | 11 | 193 | 2123 | 0.0060965 | 3.1588e-05
2013-03-28 | 297536 | GAP9A | URBAN | Other | 57.375 | 204 | 6582.6 | 0.0066399 | 5.7874e-05
2013-03-29 | 297541 | SBH4 | URBAN | Equipment failure | 1228.2 | 153 | 187914.6 | 0.18953 | 0.0012388
2013-03-29 | 297541 | SBH6 | URBAN | Equipment failure | 2091.8 | 180.8182 | 354975.3 | 0.35803 | 0.0021098
2013-03-29 | 297542 | KLG5A | RURAL | Third party impacts | 24.42 | 66 | 1611.72 | 0.0046292 | 7.0139e-05
2013-03-29 | 297543 | LGL3A | URBAN | Equipment failure | 669 | 167.6667 | 128140.5 | 0.12924 | 0.00067477
2013-03-29 | 297552 | CHL3 | URBAN | Other | 79.2 | 78 | 6177.6 | 0.0062308 | 7.9883e-05
2013-03-29 | 297554 | MBG1 | RURAL | Equipment failure | 3.96 | 76 | 300.96 | 0.00086442 | 1.1374e-05
2013-03-29 | 297557 | CLM5 | URBAN | Other | 164 | 16 | 2624 | 0.0026466 | 0.00016541
2013-03-30 | 297548 | WSE3A | RURAL | Animals | 292 | 164.5556 | 44848 | 0.12883 | 0.00083881
2013-03-30 | 297550 | NDH10 | URBAN | Equipment failure | 95.33 | 105 | 10009.65 | 0.010095 | 9.6147e-05
2013-03-30 | 297551 | WRD17A | URBAN | Equipment failure | 7.755 | 40 | 310.2 | 0.00031286 | 7.8214e-06
2013-03-30 | 297553 | YTA22B | RURAL | Animals | 65.5 | 56 | 3668 | 0.010537 | 0.00018816
2013-03-30 | 297555 | TGW3 | RURAL | Weather | 0.66 | 93 | 61.38 | 0.00017632 | 1.8959e-06
2013-03-30 | 297556 | BDT1 | RURAL | Other | 1.32 | 101 | 133.32 | 0.00038298 | 3.7919e-06
2013-03-30 | 297563 | STT3A | RURAL | Equipment failure | 4 | 91 | 364 | 0.0010456 | 1.149e-05
2013-03-30 | 297564 | RPN3A | URBAN | Equipment failure | 33.66 | 48 | 1615.68 | 0.0016295 | 3.3948e-05
2013-03-31 | 297561 | NMK18 | URBAN | Other | 758.0722 | 97.8 | 70671.4366 | 0.071274 | 0.00076453
2013-03-31 | 297561 | NMK23A | URBAN | Other | 329.64 | 103 | 33952.92 | 0.034242 | 0.00033245
2013-03-31 | 297565 | LGV6A | RURAL | Weather | 720.5 | 37 | 26658.5 | 0.076589 | 0.00207
2013-03-31 | 297566 | TRP4 | RURAL | Weather | 18 | 94 | 1692 | 0.0048611 | 5.1713e-05
2013-03-31 | 297567 | CPB2 | URBAN | Equipment failure | 44.5 | 173 | 7698.5 | 0.0077641 | 4.4879e-05
2013-03-31 | 297568 | RBA1A | URBAN | Equipment failure | 1547.65 | 125.8621 | 212391.82 | 0.2142 | 0.0015608
2013-03-31 | 297573 | WNM3 | URBAN | Weather | 1281 | 164.8966 | 250690.5 | 0.25283 | 0.0012919
2013-04-01 | 297579 | NDH10 | URBAN | Equipment failure | 102.33 | 46 | 4707.18 | 0.004747 | 0.0001032
2013-04-01 | 297580 | BDT1 | RURAL | Equipment failure | 29.49 | 365 | 10763.85 | 0.030928 | 8.4735e-05
2013-04-01 | 297628 | CPB8 | RURAL | Animals | 20 | 77 | 1540 | 0.004425 | 5.7467e-05
2013-04-01 | 297629 | DRD15B | URBAN | Equipment failure | 129 | 125 | 16125 | 0.016262 | 0.00013009
2013-04-01 | 297631 | SMF3A | RURAL | Animals | 5.94 | 131 | 778.14 | 0.0022359 | 1.7068e-05
2013-04-01 | 297632 | GYGGYS6 | RURAL | Other | 1 | 96 | 96 | 0.00027584 | 2.8733e-06
2013-04-01 | 297633 | MCW11 | RURAL | Equipment failure | 18 | 416 | 7488 | 0.021516 | 5.172e-05
2013-04-02 | 297587 | AHD12A | URBAN | Equipment failure | 843.66 | 73.6875 | 62314.85 | 0.062834 | 0.00085069
2013-04-02 | 297593 | SPO51A | URBAN | Other | 1347.5 | 69.3333 | 92784 | 0.093558 | 0.0013587
2013-04-02 | 297595 | CVL9A | URBAN | Equipment failure | 58 | 84 | 4872 | 0.0049126 | 5.8484e-05
2013-04-02 | 297604 | TRG3 | URBAN | Vegetation | 766.16 | 66 | 50566.56 | 0.050988 | 0.00077255
2013-04-02 | 297607 | CBW11 | RURAL | Equipment failure | 16 | 102 | 1662 | 0.0047762 | 4.598e-05
2013-04-02 | 297609 | THL1 | RURAL | Equipment failure | 3 | 5 | 15 | 4.3106e-05 | 8.6213e-06
2013-04-02 | 297610 | NRG16A | RURAL | Equipment failure | 5 | 194 | 970 | 0.0027875 | 1.4369e-05
2013-04-02 | 297630 | CPB2 | URBAN | Other | 44.5 | 515 | 22917.5 | 0.023109 | 4.4871e-05
2013-04-03 | 297658 | BPN24A | URBAN | Equipment failure | 9 | 95 | 855 | 0.00086208 | 9.0746e-06
2013-04-03 | 297673 | NSW23A | URBAN | Other | 1 | 3 | 3 | 3.0249e-06 | 1.0083e-06
2013-04-03 | 297673 | NSW24 | URBAN | Other | 569.4 | 3 | 1708.2 | 0.0017224 | 0.00057412
2013-04-03 | 297673 | NSW25 | URBAN | Other | 352 | 3 | 1056 | 0.0010647 | 0.00035492
2013-04-03 | 297673 | NSW26 | URBAN | Other | 1156.5 | 3 | 3469.5 | 0.0034982 | 0.0011661
2013-04-03 | 297673 | NSW28 | URBAN | Other | 1061.5 | 3 | 3184.5 | 0.0032109 | 0.0010703
2013-04-03 | 297674 | BGY5A | RURAL | Other | 15.84 | 79 | 1251.36 | 0.0035964 | 4.5524e-05
2013-04-03 | 297684 | NBR8 | RURAL | Equipment failure | 571.25 | 254.9216 | 131113.75 | 0.37682 | 0.0016418
2013-04-03 | 297692 | BDB27A | RURAL | Other | 962.5 | 17 | 16362.5 | 0.047026 | 0.0027662
2013-04-03 | 297693 | ZMR10 | URBAN | Equipment failure | 9.6 | 80 | 768 | 0.00077436 | 9.6795e-06
2013-04-03 | 297694 | 368 | URBAN | Equipment failure | 2 | 209 | 418 | 0.00042146 | 2.0166e-06
2013-04-03 | 297694 | BDB32A | RURAL | Equipment failure | 830 | 188.6 | 143950.5 | 0.41372 | 0.0023854
2013-04-03 | 297704 | RBA43A | RURAL | Equipment failure | 20 | 95 | 1475 | 0.0042392 | 5.748e-05
2013-04-03 | 297706 | BNH1B | RURAL | Weather | 68 | 23 | 1564 | 0.004495 | 0.00019543
2013-04-03 | 297722 | LLY4 | RURAL | Equipment failure | 4 | 51 | 204 | 0.0005863 | 1.1496e-05
2013-04-03 | 297728 | IDY1A | URBAN | Animals | 1110.83 | 93.8571 | 102112.91 | 0.10296 | 0.00112
2013-04-03 | 297730 | WRD21A | URBAN | Other | 814 | 69 | 56166 | 0.056631 | 0.00082074
2013-04-03 | 297733 | KSN1 | URBAN | Animals | 36 | 157 | 5652 | 0.0056988 | 3.6298e-05
2013-04-03 | 297735 | SMF6A | RURAL | Weather | 5.28 | 129 | 681.12 | 0.0019575 | 1.5175e-05
2013-04-03 | 297736 | BDB32A | RURAL | Weather | 22.44 | 96 | 2154.24 | 0.0061913 | 6.4493e-05
2013-04-04 | 297737 | KBR1A | RURAL | Vegetation | 95 | 105 | 9975 | 0.028671 | 0.00027305
2013-04-04 | 297738 | LHM1 | URBAN | Vegetation | 1571 | 36 | 56556 | 0.057022 | 0.0015839
2013-04-04 | 297739 | ZMR5 | URBAN | Equipment failure | 21.6 | 10 | 216 | 0.00021778 | 2.1778e-05
2013-04-04 | 297753 | LBH1B | RURAL | Equipment failure | 994.5 | 11 | 10939.5 | 0.031443 | 0.0028584
2013-04-04 | 297755 | SBH9 | URBAN | Equipment failure | 2.55 | 65 | 165.75 | 0.00016712 | 2.571e-06
2013-04-04 | 297756 | SGT7 | URBAN | Equipment failure | 10.5 | 56 | 588 | 0.00059285 | 1.0587e-05
2013-04-04 | 297758 | ESK5A | RURAL | Equipment failure | 659.49 | 77.101 | 48954.77 | 0.14071 | 0.0018955
2013-04-04 | 297764 | RBY12 | URBAN | Vegetation | 106.5 | 46 | 4899 | 0.0049394 | 0.00010738
2013-04-04 | 297765 | WHO1 | RURAL | Equipment failure | 25.5 | 83 | 2116.5 | 0.0060834 | 7.3294e-05
2013-04-04 | 297768 | BWH8A | RURAL | Vegetation | 97.67 | 40.5 | 7911.27 | 0.022739 | 0.00028073
2013-04-04 | 297770 | MCW4 | RURAL | Equipment failure | 67.5 | 450 | 30375 | 0.087306 | 0.00019401
2013-04-04 | 297803 | BNH1B | RURAL | Other | 6.6 | 74 | 488.4 | 0.0014038 | 1.897e-05
2013-04-04 | 297804 | MLY3 | RURAL | Other | 66.99 | 45 | 3014.55 | 0.0086646 | 0.00019255
2013-04-04 | 297813 | RST20A | URBAN | Animals | 49.915 | 78 | 3893.37 | 0.0039255 | 5.0326e-05
2013-04-05 | 297806 | HPK9 | URBAN | Other | 548.16 | 43 | 23570.88 | 0.023764 | 0.00055265
2013-04-05 | 297807 | GBG2A | URBAN | Other | 927 | 31 | 28737 | 0.028972 | 0.00093459
2013-04-05 | 297809 | GBG2A | URBAN | Equipment failure | 927 | 69 | 63963 | 0.064487 | 0.00093459
2013-04-05 | 297816 | CRY2A | RURAL | Other | 2 | 116.5 | 233 | 0.00066978 | 5.7492e-06
2013-04-05 | 297822 | WMD14A | RURAL | Other | 25.2 | 77 | 1940.4 | 0.0055779 | 7.244e-05
2013-04-05 | 297825 | CPB9 | URBAN | Other | 66 | 73.65 | 4860.9 | 0.0049007 | 6.654e-05
2013-04-05 | 297826 | GBG2A | URBAN | Equipment failure | 927 | 188.1111 | 174244 | 0.17567 | 0.00093459
2013-04-05 | 297834 | WSO2A | URBAN | Animals | 1 | 62 | 62 | 6.2508e-05 | 1.0082e-06
2013-04-05 | 297834 | WSO2B | URBAN | Animals | 5.5 | 62 | 341 | 0.00034379 | 5.545e-06
2013-04-05 | 297838 | MFD8A | RURAL | Animals | 70 | 12 | 840 | 0.0024147 | 0.00020122
2013-04-05 | 297855 | RIS2 | URBAN | Equipment failure | 68.5 | 34 | 2329 | 0.0023481 | 6.9061e-05
2013-04-05 | 297856 | LHM5 | RURAL | Weather | 7.35 | 145 | 1065.75 | 0.0030636 | 2.1128e-05
2013-04-05 | 297857 | TGW2 | RURAL | Other | 31 | 46 | 1426 | 0.0040992 | 8.9113e-05
2013-04-05 | 297858 | RPN2A | URBAN | Third party impacts | 1309.99 | 102.3182 | 131225.07 | 0.1323 | 0.0013207
2013-04-05 | 297868 | WMD10A | URBAN | Equipment failure | 41.5 | 71 | 2946.5 | 0.0029706 | 4.184e-05
2013-04-05 | 297870 | RBA37A | URBAN | Other | 1.32 | 103 | 135.96 | 0.00013707 | 1.3308e-06
2013-04-06 | 297867 | LTN2 | RURAL | Third party impacts | 11.22 | 22 | 246.84 | 0.00070965 | 3.2257e-05
2013-04-06 | 297869 | PWC4 | RURAL | Other | 8 | 44 | 352 | 0.001012 | 2.3e-05
2013-04-06 | 297871 | MRK7A | URBAN | Equipment failure | 0.1 | 286 | 28.6 | 2.8832e-05 | 1.0081e-07
2013-04-06 | 297933 | NRG16A | RURAL | Weather | 27.72 | 109 | 3021.48 | 0.0086866 | 7.9694e-05
2013-04-07 | 297879 | NIP1A | URBAN | Animals | 914.67 | 82.3529 | 79567.32 | 0.080211 | 0.00092207
2013-04-07 | 297901 | TWT15A | RURAL | Other | 65.5 | 40 | 2620 | 0.0075329 | 0.00018832
2013-04-07 | 297934 | BDB32A | RURAL | Other | 22.44 | 83 | 1862.52 | 0.005355 | 6.4518e-05
2013-04-07 | 297935 | BDB32A | RURAL | Equipment failure | 22.44 | 154 | 3455.76 | 0.0099358 | 6.4518e-05
2013-04-07 | 297997 | TCB2 | RURAL | Other | 118 | 169.5 | 9738.54 | 0.028 | 0.00033927
2013-04-08 | 297919 | MLS26B | URBAN | Weather | 114 | 6 | 684 | 0.00068942 | 0.0001149
2013-04-08 | 297936 | BMT1 | RURAL | Equipment failure | 703.49 | 2 | 1406.98 | 0.0040467 | 0.0020233
2013-04-08 | 297936 | BMT2 | RURAL | Equipment failure | 292.5 | 2 | 585 | 0.0016825 | 0.00084127
2013-04-08 | 297936 | BMT3 | RURAL | Equipment failure | 268.5 | 2 | 537 | 0.0015445 | 0.00077224
2013-04-08 | 297936 | BMT4 | RURAL | Equipment failure | 680.82 | 2 | 1361.64 | 0.0039163 | 0.0019581
2013-04-08 | 297936 | BMT5 | RURAL | Equipment failure | 330.5 | 2 | 661 | 0.0019011 | 0.00095056
2013-04-08 | 297937 | BLH12A | RURAL | Other | 109 | 235 | 25615 | 0.073672 | 0.0003135
2013-04-08 | 297938 | BLH11B | URBAN | Other | 68.31 | 107 | 7309.17 | 0.0073671 | 6.8851e-05
2013-04-08 | 297939 | WSE6A | RURAL | Equipment failure | 24.42 | 38 | 927.96 | 0.0026689 | 7.0235e-05
2013-04-08 | 297940 | MFN2A | URBAN | Equipment failure | 505.5 | 55 | 27802.5 | 0.028023 | 0.0005095
2013-04-08 | 297940 | MFN2B | RURAL | Equipment failure | 2306.75 | 60.9565 | 136324.25 | 0.39209 | 0.0066345
2013-04-08 | 297959 | CRY6A | RURAL | Equipment failure | 282 | 113.6429 | 35008.5 | 0.10069 | 0.00081107
2013-04-09 | 297961 | KBR5A | RURAL | Other | 0.66 | 114 | 75.24 | 0.00021645 | 1.8986e-06
2013-04-09 | 297974 | MCW11 | RURAL | Other | 2.5 | 98 | 245 | 0.0007048 | 7.1918e-06
2013-04-09 | 298020 | RBY16 | URBAN | Equipment failure | 335.5 | 144.5 | 48404 | 0.048783 | 0.00033812
2013-04-09 | 298021 | YTA2A | URBAN | Third party impacts | 0.78 | 140 | 109.2 | 0.00011005 | 7.861e-07
2013-04-09 | 298022 | GTN5B | RURAL | Other | 1 | 65 | 65 | 0.00018699 | 2.8767e-06
2013-04-09 | 298023 | KBN13A | RURAL | Equipment failure | 869 | 77.5909 | 79995 | 0.23012 | 0.0024999
2013-04-09 | 298023 | NIP5B | URBAN | Equipment failure | 100.5 | 195 | 19597.5 | 0.019751 | 0.00010129
2013-04-09 | 298024 | SPD12B | URBAN | Other | 5.4 | 690 | 3726 | 0.0037551 | 5.4422e-06
2013-04-09 | 298027 | CRY2A | RURAL | Third party impacts | 13.5 | 145 | 1957.5 | 0.0056312 | 3.8836e-05
2013-04-09 | 298030 | SDM1 | RURAL | Equipment failure | 1 | 449 | 449 | 0.0012917 | 2.8767e-06
2013-04-10 | 298029 | SGT9 | URBAN | Third party impacts | 55 | 165 | 9075 | 0.0091454 | 5.5427e-05
2013-04-10 | 298033 | BRD8A | RURAL | Vegetation | 321.99 | 49 | 15777.51 | 0.045394 | 0.0009264
2013-04-10 | 298034 | RIS2 | URBAN | Equipment failure | 1338.48 | 69.5 | 93465.66 | 0.094191 | 0.0013489
2013-04-10 | 298042 | AHD5 | URBAN | Third party impacts | 1811.49 | 36.2 | 68508 | 0.069039 | 0.0018255
2013-04-10 | 298075 | SPO16A | URBAN | Third party impacts | 54.5 | 155 | 8447.5 | 0.008513 | 5.4923e-05
2013-04-10 | 298076 | CRB25A | RURAL | Weather | 55.5 | 339 | 18814.5 | 0.054131 | 0.00015968
2013-04-10 | 298079 | HTN22A | URBAN | Other | 0.66 | 152 | 100.32 | 0.0001011 | 6.6512e-07
2013-04-10 | 298083 | KWH1 | RURAL | Equipment failure | 57 | 177 | 10089 | 0.029027 | 0.000164
2013-04-11 | 298113 | MLS12B | URBAN | Equipment failure | 2042.5 | 18 | 36765 | 0.037048 | 0.0020582
2013-04-11 | 298113 | MLSQAP12 | URBAN | Equipment failure | 1 | 18 | 18 | 1.8139e-05 | 1.0077e-06
2013-04-11 | 298113 | QAP4 | URBAN | Equipment failure | 13 | 41 | 533 | 0.0005371 | 1.31e-05
2013-04-11 | 298113 | QAPTR1H | URBAN | Equipment failure | 4 | 225 | 900 | 0.00090693 | 4.0308e-06
2013-04-11 | 298118 | RBA34A | URBAN | Third party impacts | 1.32 | 173 | 228.36 | 0.00023012 | 1.3302e-06
2013-04-11 | 298151 | CNB24A | RURAL | Equipment failure | 942.5 | 29.6 | 23063.5 | 0.066364 | 0.002712
2013-04-11 | 298151 | RLB16A | RURAL | Equipment failure | 144.16 | 23 | 3315.68 | 0.0095407 | 0.00041481
2013-04-11 | 298156 | AHL11A | URBAN | Animals | 1714 | 96 | 164544 | 0.16581 | 0.0017272
2013-04-11 | 298156 | AHL11B | URBAN | Animals | 1 | 96 | 96 | 9.6739e-05 | 1.0077e-06
2013-04-11 | 298159 | CVL5A | RURAL | Animals | 1 | 91 | 91 | 0.00026185 | 2.8775e-06
2013-04-11 | 298161 | FDS1 | RURAL | Other | 4 | 211 | 844 | 0.0024286 | 1.151e-05
2013-04-11 | 298833 | BDB27A | RURAL | Equipment failure | 1 | 157 | 157 | 0.00045176 | 2.8775e-06
2013-04-12 | 298157 | BRD8A | RURAL | Equipment failure | 30.5 | 286 | 8723 | 0.025103 | 8.7773e-05
2013-04-12 | 298184 | BTA5A | RURAL | Other | 18.5 | 65 | 1202.5 | 0.0034606 | 5.3239e-05
2013-04-12 | 298185 | LLY4 | RURAL | Other | 1 | 42 | 42 | 0.00012087 | 2.8778e-06
2013-04-12 | 298186 | CMD11A | RURAL | Equipment failure | 78.54 | 36.6667 | 5518.03 | 0.01588 | 0.00022602
2013-04-12 | 298187 | WRG9A | URBAN | Equipment failure | 719.25 | 70.7826 | 53153.5 | 0.05356 | 0.00072475
2013-04-12 | 298188 | RLB13B | RURAL | Weather | 18 | 40 | 720 | 0.002072 | 5.18e-05
2013-04-12 | 298189 | COR23A | RURAL | Equipment failure | 5 | 53 | 265 | 0.00076262 | 1.4389e-05
2013-04-12 | 298217 | CFD8A | URBAN | Equipment failure | 129 | 75 | 9675 | 0.009749 | 0.00012999
2013-04-12 | 298219 | SPC2A | URBAN | Equipment failure | 1 | 79 | 79 | 7.9604e-05 | 1.0076e-06
2013-04-12 | 298219 | SPC2B | RURAL | Equipment failure | 488.99 | 146.0244 | 59698.21 | 0.1718 | 0.0014072
2013-04-12 | 298220 | ALY5 | URBAN | Animals | 1116.5 | 86.3 | 95669.5 | 0.096401 | 0.001125
2013-04-12 | 298222 | GYM7A | RURAL | Vegetation | 80 | 50 | 4000 | 0.011511 | 0.00023022
2013-04-13 | 298224 | PWC6 | RURAL | Weather | 400 | 104.1579 | 21056 | 0.060601 | 0.0011512
2013-04-13 | 298225 | JBB13A | RURAL | Weather | 212.49 | 94.0556 | 20027.45 | 0.057641 | 0.00061156
2013-04-13 | 298226 | WFD3A | RURAL | Equipment failure | 250.18 | 118.7297 | 26866 | 0.077323 | 0.00072004
2013-04-13 | 298227 | LDR3 | URBAN | Equipment failure | 67.2 | 368 | 24729.6 | 0.024917 | 6.771e-05
2013-04-13 | 298228 | WNM5 | URBAN | Third party impacts | 5.85 | 430 | 2515.5 | 0.0025346 | 5.8944e-06
2013-04-13 | 298229 | KLG17A | URBAN | Equipment failure | 40 | 134 | 5360 | 0.0054007 | 4.0304e-05
2013-04-13 | 298230 | RBARHP14 | URBAN | Third party impacts | 21.9 | 248 | 5431.2 | 0.0054725 | 2.2066e-05
2013-04-13 | 298231 | WMR2 | RURAL | Equipment failure | 31 | 86 | 2666 | 0.007673 | 8.9221e-05
2013-04-13 | 298232 | RCN2A | URBAN | Third party impacts | 23.94 | 230 | 5506.2 | 0.005548 | 2.4122e-05
2013-04-13 | 298235 | MLY3 | RURAL | Weather | 214.99 | 328.4615 | 82022.68 | 0.23607 | 0.00061876
2013-04-14 | 298243 | RBA43A | RURAL | Other | 13.2 | 150 | 1980 | 0.0056989 | 3.7993e-05
2013-04-14 | 298244 | MGL1A | RURAL | Third party impacts | 26 | 206 | 5356 | 0.015416 | 7.4834e-05
2013-04-14 | 298245 | MLY4 | RURAL | Equipment failure | 3.96 | 108 | 427.68 | 0.001231 | 1.1398e-05
2013-04-14 | 298246 | IPS2B | RURAL | Animals | 4 | 71 | 284 | 0.00081742 | 1.1513e-05
2013-04-14 | 298254 | CRM16A | RURAL | Third party impacts | 18 | 47 | 846 | 0.002435 | 5.1808e-05
2013-04-14 | 298264 | AHL6A | URBAN | Equipment failure | 46.53 | 213 | 9910.89 | 0.0099858 | 4.6882e-05
2013-04-14 | 298265 | CSE7 | URBAN | Other | 8.7 | 208 | 1809.6 | 0.0018233 | 8.7658e-06
2013-04-14 | 298269 | BDB27A | RURAL | Vegetation | 19 | 23 | 437 | 0.0012578 | 5.4687e-05
2013-04-14 | 298270 | BHD23A | RURAL | Animals | 26 | 140 | 3640 | 0.010477 | 7.4834e-05
2013-04-14 | 298273 | HTN22A | URBAN | Equipment failure | 64 | 209 | 13376 | 0.013477 | 6.4484e-05
2013-04-15 | 298293 | BDB27A | RURAL | Equipment failure | 12.54 | 36 | 451.44 | 0.0012996 | 3.6099e-05
2013-04-15 | 298298 | YTA2A | URBAN | Other | 1.98 | 142 | 281.16 | 0.00028326 | 1.9948e-06
2013-04-15 | 298316 | TRG2A | URBAN | Other | 214 | 82.5 | 17655 | 0.017787 | 0.0002156
2013-04-16 | 298340 | BMT1 | RURAL | Other | 485.49 | 21 | 10195.29 | 0.029351 | 0.0013977
2013-04-16 | 298342 | IPS3A | RURAL | Weather | 530 | 92 | 48760 | 0.14038 | 0.0015258
2013-04-16 | 298344 | LGV6A | RURAL | Weather | 718.5 | 92.1964 | 66675 | 0.19195 | 0.0020685
2013-04-16 | 298345 | RPN6A | RURAL | Weather | 2171 | 90 | 195390 | 0.56251 | 0.0062501
2013-04-16 | 298352 | RST16A | URBAN | Third party impacts | 1 | 91 | 91 | 9.1677e-05 | 1.0074e-06
2013-04-16 | 298400 | KLG16A | RURAL | Animals | 36.3 | 81.3333 | 2952.4 | 0.0084997 | 0.0001045
2013-04-16 | 298401 | NGI1B | RURAL | Weather | 10 | 46.6667 | 466.6667 | 0.0013435 | 2.8789e-05
2013-04-16 | 298402 | CBT12A | RURAL | Other | 4 | 25.6667 | 102.6667 | 0.00029557 | 1.1516e-05
2013-04-16 | 298403 | WNM4 | URBAN | Other | 60 | 44.6667 | 2680 | 0.0026999 | 6.0446e-05
2013-04-16 | 298404 | WNM3 | URBAN | Equipment failure | 125 | 47.6667 | 5958.3333 | 0.0060026 | 0.00012593
2013-04-16 | 298405 | PWC5 | RURAL | Other | 45 | 70 | 3150 | 0.0090685 | 0.00012955
2013-04-16 | 298406 | BDL3 | URBAN | Equipment failure | 87.5 | 99 | 8662.5 | 0.0087269 | 8.8151e-05
2013-04-16 | 298407 | STT1B | RURAL | Equipment failure | 6.27 | 142 | 890.34 | 0.0025632 | 1.8051e-05
2013-04-16 | 298408 | MSV2 | RURAL | Weather | 4 | 84 | 336 | 0.00096731 | 1.1516e-05
2013-04-16 | 298409 | SPC2B | RURAL | Weather | 3 | 111 | 333 | 0.00095867 | 8.6367e-06
2013-04-16 | 298410 | MBG1 | RURAL | Weather | 6 | 116 | 696 | 0.0020037 | 1.7273e-05
2013-04-16 | 298412 | AGE10 | URBAN | Other | 77 | 15 | 1155 | 0.0011636 | 7.7573e-05
2013-04-16 | 298416 | PRG2B | RURAL | Equipment failure | 4 | 81 | 324 | 0.00093276 | 1.1516e-05
2013-04-16 | 298417 | HTN22A | URBAN | Other | 0.1 | 199 | 19.9 | 2.0048e-05 | 1.0074e-07
2013-04-16 | 298417 | HTN3B | URBAN | Other | 0.1 | 199 | 19.9 | 2.0048e-05 | 1.0074e-07
2013-04-16 | 298420 | SPC2B | RURAL | Equipment failure | 0.67 | 184 | 123.28 | 0.00035491 | 1.9289e-06
2013-04-16 | 298421 | ESK3A | RURAL | Other | 3.3 | 143 | 471.9 | 0.0013586 | 9.5004e-06
2013-04-16 | 298422 | GGR4 | RURAL | Weather | 10.05 | 39 | 391.95 | 0.0011284 | 2.8933e-05
2013-04-16 | 298423 | PRG2B | RURAL | Weather | 4 | 89 | 356 | 0.0010249 | 1.1516e-05
2013-04-16 | 298424 | GGR5 | RURAL | Weather | 3.35 | 164 | 549.4 | 0.0015817 | 9.6443e-06
2013-04-16 | 298433 | WMD8B | RURAL | Equipment failure | 8.085 | 193 | 1560.405 | 0.0044923 | 2.3276e-05
2013-04-16 | 298434 | PRG2B | RURAL | Weather | 4 | 215 | 860 | 0.0024759 | 1.1516e-05
2013-04-16 | 298437 | MSV2 | RURAL | Weather | 2.68 | 100 | 268 | 0.00077155 | 7.7155e-06
2013-04-16 | 298438 | SPC2B | RURAL | Weather | 1 | 134 | 134 | 0.00038577 | 2.8789e-06
2013-04-16 | 298542 | GGR4 | RURAL | Weather | 608 | 17 | 10336 | 0.029756 | 0.0017504
2013-04-17 | 298418 | LTN4 | URBAN | Equipment failure | 1712.33 | 74.5 | 119475.11 | 0.12035 | 0.0017249
2013-04-17 | 298419 | NSD6B | URBAN | Equipment failure | 1149 | 77 | 88473 | 0.089124 | 0.0011575
2013-04-17 | 298436 | YDA3A | RURAL | Third party impacts | 2.31 | 131 | 302.61 | 0.00087132 | 6.6513e-06
2013-04-17 | 298454 | ESK5A | RURAL | Vegetation | 661.49 | 61.0101 | 44635.64 | 0.12852 | 0.0019047
2013-04-17 | 298455 | CBT12A | RURAL | Third party impacts | 10 | 62 | 620 | 0.0017852 | 2.8794e-05
2013-04-17 | 298458 | NIP4A | RURAL | Weather | 1492.51 | 66 | 98505.66 | 0.28363 | 0.0042975
2013-04-17 | 298463 | CPC3A | URBAN | Other | 5 | 26 | 130 | 0.00013096 | 5.0368e-06
2013-04-17 | 298463 | CPC3B | URBAN | Other | 34 | 26 | 884 | 0.0008905 | 3.425e-05
2013-04-17 | 298474 | HDN2 | RURAL | Weather | 309 | 146.5231 | 42464 | 0.12227 | 0.00088972
2013-04-17 | 298485 | BBSRDL8 | RURAL | Weather | 1299.44 | 61.3919 | 77986.92 | 0.22455 | 0.0037416
2013-04-17 | 298489 | KRN12 | URBAN | Weather | 88.5 | 25.5 | 2256.75 | 0.0022733 | 8.9151e-05
2013-04-17 | 298495 | CPK11 | URBAN | Other | 34 | 118 | 4012 | 0.0040415 | 3.425e-05
2013-04-17 | 298497 | MBG4 | RURAL | Weather | 2.68 | 163 | 436.84 | 0.0012578 | 7.7167e-06
2013-04-17 | 298498 | CRM13B | URBAN | Other | 5 | 135 | 675 | 0.00067996 | 5.0368e-06
2013-04-17 | 298499 | TRP4 | RURAL | Weather | 5.5 | 198 | 1089 | 0.0031356 | 1.5836e-05
2013-04-17 | 298500 | TRP4 | RURAL | Weather | 1 | 108 | 108 | 0.00031097 | 2.8794e-06
2013-04-17 | 298501 | LLY3 | RURAL | Weather | 1 | 77 | 77 | 0.00022171 | 2.8794e-06
2013-04-17 | 298502 | CPD2A | RURAL | Weather | 0.67 | 113 | 75.71 | 0.000218 | 1.9292e-06
2013-04-17 | 298505 | EMP4A | URBAN | Equipment failure | 585 | 111.2857 | 66324 | 0.066812 | 0.0005893
2013-04-17 | 298506 | KBR1A | RURAL | Weather | 5.83 | 178 | 1037.74 | 0.002988 | 1.6787e-05
2013-04-17 | 298507 | EZRRWD4 | RURAL | Equipment failure | 94.65 | 109.8727 | 26997.93 | 0.077737 | 0.00027253
2013-04-17 | 298523 | IPL2A | RURAL | Weather | 284.49 | 94.3217 | 24686.49 | 0.071081 | 0.00081915
2013-04-17 | 298524 | KRA1 | URBAN | Animals | 590.33 | 7 | 4132.31 | 0.0041627 | 0.00059467
2013-04-17 | 298524 | KRA10 | URBAN | Animals | 1083.33 | 7 | 7583.31 | 0.0076391 | 0.0010913
2013-04-17 | 298524 | KRA2 | URBAN | Animals | 820.16 | 7 | 5741.12 | 0.0057833 | 0.00082619
2013-04-17 | 298524 | KRA3 | URBAN | Animals | 1328.5 | 7 | 9299.5 | 0.0093679 | 0.0013383
2013-04-17 | 298524 | KRA4 | URBAN | Animals | 288.5 | 7 | 2019.5 | 0.0020344 | 0.00029062
2013-04-17 | 298524 | KRA6 | URBAN | Animals | 1 | 7 | 7 | 7.0515e-06 | 1.0074e-06
2013-04-17 | 298524 | KRA7 | URBAN | Animals | 1223.67 | 7 | 8565.69 | 0.0086287 | 0.0012327
2013-04-17 | 298540 | GTN12A | RURAL | Weather | 3 | 46 | 138 | 0.00039735 | 8.6381e-06
2013-04-17 | 298541 | RWD2 | RURAL | Animals | 7 | 24.3333 | 170.3333 | 0.00049045 | 2.0156e-05
2013-04-17 | 298556 | RST5A | URBAN | Weather | 61 | 193 | 11773 | 0.01186 | 6.1449e-05
2013-04-17 | 298581 | KBR6A | RURAL | Weather | 4.02 | 217 | 872.34 | 0.0025118 | 1.1575e-05
2013-04-17 | 298582 | ESK5A | RURAL | Weather | 6.4 | 79.8 | 510.72 | 0.0014705 | 1.8428e-05
2013-04-17 | 298583 | PRG2B | RURAL | Weather | 3 | 144 | 432 | 0.0012439 | 8.6381e-06
2013-04-17 | 298584 | PRG2A | RURAL | Weather | 0.67 | 336 | 225.12 | 0.0006482 | 1.9292e-06
2013-04-17 | 298596 | RWD1 | RURAL | Equipment failure | 3 | 503 | 1509 | 0.004345 | 8.6381e-06
2013-04-18 | 298544 | MLB8A | RURAL | Equipment failure | 481.0575 | 16.2632 | 9149.0125 | 0.026346 | 0.0013853
2013-04-18 | 298545 | MLB8A | RURAL | Other | 315 | 69 | 21735 | 0.062588 | 0.00090708
2013-04-18 | 298548 | SHW12 | URBAN | Third party impacts | 26.07 | 62 | 1616.34 | 0.0016282 | 2.6261e-05
2013-04-18 | 298555 | CRB25A | RURAL | Other | 20 | 215 | 4300 | 0.012382 | 5.7592e-05
2013-04-18 | 298570 | MLT21B | URBAN | Equipment failure | 37.915 | 1034 | 39204.11 | 0.039491 | 3.8192e-05
2013-04-18 | 298585 | HDN2 | RURAL | Other | 4.02 | 212 | 852.24 | 0.0024541 | 1.1576e-05
2013-04-18 | 298586 | RWD2 | RURAL | Equipment failure | 1.98 | 35 | 69.3 | 0.00019956 | 5.7016e-06
2013-04-18 | 298604 | TGW3 | RURAL | Equipment failure | 14 | 468 | 6552 | 0.018867 | 4.0314e-05
2013-04-18 | 298612 | KSN6 | URBAN | Equipment failure | 739.99 | 141.4783 | 96848.72 | 0.097557 | 0.0007454
2013-04-18 | 298633 | CPB4 | URBAN | Equipment failure | 1 | 129 | 129 | 0.00012994 | 1.0073e-06
2013-04-18 | 298637 | PPE13A | RURAL | Equipment failure | 29.7 | 178 | 5286.6 | 0.015223 | 8.5524e-05
2013-04-18 | 300334 | KBR6A | RURAL | Weather | 2.01 | 81 | 162.81 | 0.00046883 | 5.788e-06
2013-04-19 | 298594 | CCYUPC2 | URBAN | Equipment failure | 33.5 | 112 | 3752 | 0.0037792 | 3.3743e-05
2013-04-19 | 298595 | GYM7A | RURAL | Equipment failure | 0.525 | 21 | 11.025 | 3.1752e-05 | 1.512e-06
2013-04-19 | 298599 | GVN16A | RURAL | Equipment failure | 103 | 34 | 3502 | 0.010086 | 0.00029664
2013-04-19 | 298611 | GGR1 | RURAL | Other | 844.66 | 12 | 10135.92 | 0.029191 | 0.0024326
2013-04-19 | 298611 | GGR2 | RURAL | Other | 140.66 | 12 | 1687.92 | 0.0048612 | 0.0004051
2013-04-19 | 298611 | GGR3 | RURAL | Other | 86.99 | 12 | 1043.88 | 0.0030064 | 0.00025053
2013-04-19 | 298638 | CRM13B | URBAN | Equipment failure | 5 | 157 | 785 | 0.00079069 | 5.0362e-06
2013-04-19 | 298641 | KBR3A | RURAL | Weather | 1 | 91 | 91 | 0.00026208 | 2.88e-06
2013-04-19 | 298642 | HPE13A | URBAN | Equipment failure | 100 | 235 | 23500 | 0.02367 | 0.00010072
2013-04-19 | 298645 | PBH1 | URBAN | Equipment failure | 94 | 291.5 | 13456.1 | 0.013554 | 9.4681e-05
2013-04-20 | 298646 | HPE12A | URBAN | Animals | 1458.03 | 63 | 91855.89 | 0.092516 | 0.0014685
2013-04-20 | 298648 | MRE8 | URBAN | Other | 220 | 15 | 3300 | 0.0033237 | 0.00022158
2013-04-20 | 298649 | WEL3 | URBAN | Equipment failure | 37.42 | 11 | 411.62 | 0.00041458 | 3.7689e-05
2013-04-20 | 298743 | BLB5A | URBAN | Animals | 1.98 | 69 | 136.62 | 0.0001376 | 1.9942e-06
2013-04-21 | 298693 | GYM8A | RURAL | Third party impacts | 1590 | 73.3182 | 105031 | 0.30254 | 0.0045799
2013-04-22 | 298713 | CLM9 | URBAN | Equipment failure | 70 | 10 | 700 | 0.00070499 | 7.0499e-05
2013-04-22 | 298741 | KRN12 | URBAN | Equipment failure | 66 | 156 | 10296 | 0.010369 | 6.647e-05
2013-04-22 | 298744 | HPK2 | URBAN | Equipment failure | 180.5 | 32.3333 | 5836.1667 | 0.0058777 | 0.00018179
2013-04-22 | 298745 | BHD23A | RURAL | Vegetation | 12 | 134.1667 | 1610 | 0.0046377 | 3.4567e-05
2013-04-22 | 298746 | TWG17 | URBAN | Equipment failure | 28.2 | 84 | 2368.8 | 0.0023857 | 2.8401e-05
2013-04-23 | 298747 | NSD30B | URBAN | Animals | 29.48 | 68 | 2004.64 | 0.0020188 | 2.9688e-05
2013-04-23 | 298748 | SPO8A | URBAN | Third party impacts | 51 | 107 | 1369.35 | 0.001379 | 5.136e-05
2013-04-23 | 298749 | JBB4A | URBAN | Third party impacts | 8 | 96 | 768 | 0.00077342 | 8.0564e-06
2013-04-23 | 298750 | BHD7A | URBAN | Animals | 9 | 72 | 648 | 0.00065257 | 9.0635e-06
2013-04-23 | 298766 | CMD11A | RURAL | Animals | 2260.99 | 64.4419 | 146793.36 | 0.4229 | 0.0065137
2013-04-23 | 298767 | ZMR9 | URBAN | Third party impacts | 0.717 | 140 | 100.38 | 0.00010109 | 7.2206e-07
2013-04-23 | 298773 | BDT4 | RURAL | Other | 6 | 20 | 120 | 0.00034571 | 1.7285e-05
2013-04-23 | 298811 | MTG13A | URBAN | Equipment failure | 65.17 | 69 | 4496.73 | 0.0045284 | 6.563e-05
2013-04-23 | 298812 | CPR7 | URBAN | Third party impacts | 1654 | 34 | 56236 | 0.056633 | 0.0016657
2013-04-23 | 298813 | GYS3A | RURAL | Third party impacts | 5.445 | 153 | 833.085 | 0.0024 | 1.5686e-05
2013-04-23 | 298814 | CPK13 | RURAL | Equipment failure | 77 | 57 | 4389 | 0.012644 | 0.00022183
2013-04-23 | 298817 | CPL2A | URBAN | Animals | 3.4089 | 58 | 197.7162 | 0.00019911 | 3.4329e-06
2013-04-24 | 298820 | YDA2B | RURAL | Vegetation | 97 | 98 | 9506 | 0.027388 | 0.00027947
2013-04-24 | 298853 | DRD15B | URBAN | Third party impacts | 0.99 | 149 | 147.51 | 0.00014854 | 9.9694e-07
2013-04-24 | 298874 | BLB4A | URBAN | Animals | 1 | 5 | 5 | 5.035e-06 | 1.007e-06
2013-04-24 | 298898 | MDR3A | URBAN | Equipment failure | 51 | 99 | 5049 | 0.0050844 | 5.1357e-05
2013-04-24 | 298903 | HPE13A | URBAN | Equipment failure | 70.25 | 67 | 4706.75 | 0.0047397 | 7.0742e-05
2013-04-24 | 298904 | KMR19A | URBAN | Third party impacts | 51 | 192 | 9792 | 0.0098606 | 5.1357e-05
2013-04-24 | 298908 | BHD35A | RURAL | Other | 15 | 81 | 1215 | 0.0035006 | 4.3217e-05
2013-04-25 | 298914 | CPR5 | URBAN | Equipment failure | 2824 | 143.087 | 424309 | 0.42727 | 0.0028437
2013-04-25 | 298915 | JBB13A | RURAL | Other | 5 | 199 | 995 | 0.0028669 | 1.4406e-05
2013-04-26 | 298917 | GAP1A | URBAN | Animals | 20.79 | 69 | 1434.51 | 0.0014444 | 2.0934e-05
2013-04-26 | 298933 | INA1A | URBAN | Other | 2.31 | 154 | 355.74 | 0.0003582 | 2.326e-06
2013-04-26 | 298950 | GBN4 | RURAL | Other | 699.96 | 17 | 11899.32 | 0.034288 | 0.0020169
2013-04-26 | 298952 | AMR1 | RURAL | Other | 2.5 | 14 | 35 | 0.00010085 | 7.2038e-06
2013-04-26 | 298954 | KBN15A | URBAN | Vegetation | 88 | 58 | 5104 | 0.0051394 | 8.861e-05
2013-04-26 | 298955 | NRG16A | RURAL | Vegetation | 647.5 | 30.9592 | 18065 | 0.052054 | 0.0018658
2013-04-26 | 298959 | SRD18A | URBAN | Equipment failure | 1.9266 | 155 | 298.623 | 0.00030069 | 1.9399e-06
2013-04-26 | 298960 | MAI13 | URBAN | Animals | 7 | 84 | 588 | 0.00059207 | 7.0485e-06
2013-04-26 | 298961 | WNM5 | URBAN | Other | 56.25 | 126 | 7087.5 | 0.0071366 | 5.664e-05
2013-04-26 | 298973 | TTF81 | URBAN | Equipment failure | 512 | 114.125 | 52539 | 0.052903 | 0.00051555
2013-04-27 | 298975 | AHD21 | URBAN | Third party impacts | 16.2 | 160 | 2592 | 0.00261 | 1.6312e-05
2013-04-27 | 298976 | CVL17A | URBAN | Animals | 2419.34 | 22 | 53225.48 | 0.053594 | 0.0024361
2013-04-27 | 298977 | IPS3A | RURAL | Other | 23.1 | 111 | 2564.1 | 0.0073881 | 6.656e-05
2013-04-27 | 298978 | BMG2A | URBAN | Animals | 291.5 | 33 | 9619.5 | 0.0096862 | 0.00029352
2013-04-27 | 298980 | IPS3A | RURAL | Other | 15.84 | 173 | 2740.32 | 0.0078959 | 4.5641e-05
2013-04-27 | 298982 | NIP4A | RURAL | Animals | 16 | 63 | 1008 | 0.0029044 | 4.6102e-05
2013-04-28 | 298979 | SPO16A | URBAN | Equipment failure | 869.5 | 76.3448 | 49402.5 | 0.049743 | 0.0008755
2013-04-28 | 298981 | BDT4 | RURAL | Equipment failure | 25 | 355 | 8875 | 0.025574 | 7.2039e-05
2013-04-28 | 298996 | LHM5 | RURAL | Animals | 858.33 | 55 | 47208.15 | 0.13603 | 0.0024733
2013-04-28 | 299000 | KMR25A | RURAL | Other | 3.3 | 98 | 323.4 | 0.00093189 | 9.5091e-06
2013-04-29 | 298997 | WSO13A | RURAL | Animals | 706.51 | 16 | 11304.16 | 0.032576 | 0.002036
2013-04-29 | 298999 | BSCT5 | URBAN | Equipment failure | 1 | 68 | 68 | 6.8466e-05 | 1.0069e-06
2013-04-29 | 299013 | HIS5B | URBAN | Third party impacts | 10 | 22 | 220 | 0.00022151 | 1.0069e-05
2013-04-29 | 299038 | CVL15A | URBAN | Equipment failure | 9 | 2 | 18 | 1.8123e-05 | 9.0617e-06
2013-04-29 | 299042 | BBSRDL8 | RURAL | Other | 1.6 | 31 | 49.6 | 0.00014293 | 4.6108e-06
2013-04-29 | 299048 | CLD28A | RURAL | Other | 0.66 | 113 | 74.58 | 0.00021492 | 1.902e-06
2013-04-29 | 299049 | LBS12A | URBAN | Equipment failure | 48.99 | 120.5 | 5289.99 | 0.0053262 | 4.9326e-05
2013-04-29 | 299067 | MDR35A | URBAN | Third party impacts | 12 | 86.6667 | 1005 | 0.0010119 | 1.2082e-05
2013-04-29 | 299068 | NDH12 | URBAN | Third party impacts | 51.48 | 197 | 10141.56 | 0.010211 | 5.1833e-05
2013-04-29 | 299069 | KWH1 | RURAL | Other | 6.105 | 234 | 1428.57 | 0.0041168 | 1.7593e-05
2013-04-29 | 299070 | MTG11A | URBAN | Other | 0.87 | 454 | 394.98 | 0.00039769 | 8.7596e-07
2013-04-29 | 299072 | COR25A | URBAN | Animals | 42.5 | 175 | 7437.5 | 0.0074885 | 4.2791e-05
2013-04-29 | 299073 | KBN5A | RURAL | Animals | 19.8 | 60 | 1188 | 0.0034235 | 5.7059e-05
2013-04-29 | 299094 | RPN6A | RURAL | Other | 56.615 | 146 | 8265.79 | 0.02382 | 0.00016315
2013-04-29 | 299100 | NBR6 | RURAL | Equipment failure | 36 | 150 | 5400 | 0.015561 | 0.00010374
2013-04-30 | 299074 | INA1A | URBAN | Animals | 781.5 | 52 | 40638 | 0.040915 | 0.00078683
2013-04-30 | 299093 | GYS5A | RURAL | Equipment failure | 148 | 163.9623 | 26903.5 | 0.077535 | 0.00042653
2013-04-30 | 299097 | BMT2 | RURAL | Equipment failure | 1.4 | 92 | 128.8 | 0.0003712 | 4.0348e-06
2013-04-30 | 299113 | PWC3 | RURAL | Equipment failure | 19 | 275 | 5225 | 0.015058 | 5.4757e-05
2013-04-30 | 299117 | SMR15A | URBAN | Third party impacts | 1403 | 78.0556 | 111805 | 0.11257 | 0.0014126
2013-04-30 | 299143 | PWC6 | RURAL | Other | 23 | 116 | 2668 | 0.0076891 | 6.6285e-05
2013-04-30 | 299145 | KLG13A | URBAN | Equipment failure | 8.35 | 92 | 768.2 | 0.00077344 | 8.4069e-06
2013-04-30 | 299148 | MFN2B | RURAL | Other | 7.9992 | 49 | 391.9608 | 0.0011296 | 2.3053e-05
2013-05-01 | 299153 | MCW11 | RURAL | Equipment failure | 5.94 | 105 | 623.7 | 0.0017976 | 1.712e-05
2013-05-01 | 299164 | WMR1 | RURAL | Vegetation | 36 | 10 | 360 | 0.0010376 | 0.00010376
2013-05-01 | 299177 | WCL3 | URBAN | Third party impacts | 8 | 140 | 1120 | 0.0011276 | 8.0543e-06
2013-05-01 | 299178 | HDA14A | URBAN | Other | 4.25 | 75 | 318.75 | 0.00032091 | 4.2788e-06
2013-05-01 | 299181 | RIS1 | RURAL | Equipment failure | 692.5 | 248.92 | 173896 | 0.5012 | 0.0019959
2013-05-01 | 299206 | RIS2 | URBAN | Other | 6.27 | 160 | 1003.2 | 0.00101 | 6.3125e-06
2013-05-01 | 299207 | MTB1B | RURAL | Other | 29.04 | 89 | 2584.56 | 0.0074492 | 8.3699e-05
2013-05-02 | 299230 | AHL6A | URBAN | Vegetation | 2002 | 62 | 124124 | 0.12496 | 0.0020155
2013-05-03 | 299279 | RST4A | URBAN | Other | 1 | 39 | 39 | 3.9262e-05 | 1.0067e-06
2013-05-03 | 299298 | LGV3A | RURAL | Equipment failure | 8 | 91 | 728 | 0.0020985 | 2.306e-05
2013-05-03 | 299324 | MDH8B | URBAN | Other | 2.4 | 139 | 333.6 | 0.00033584 | 2.4161e-06
2013-05-03 | 299326 | YDA1B | RURAL | Equipment failure | 19.14 | 100 | 1914 | 0.0055172 | 5.5172e-05
2013-05-03 | 299327 | GYM9A | RURAL | Other | 5.0061 | 75 | 375.4575 | 0.0010823 | 1.443e-05
2013-05-03 | 299328 | COR25A | RURAL | Animals | 13.86 | 68 | 942.48 | 0.0027167 | 3.9952e-05
2013-05-04 | 299331 | SGT22A | URBAN | Other | 152 | 58 | 8816 | 0.0088749 | 0.00015302
2013-05-04 | 299332 | CLD30A | URBAN | Other | 24 | 147 | 3528 | 0.0035516 | 2.416e-05
2013-05-04 | 299338 | CPR4 | URBAN | Animals | 4.62 | 82 | 378.84 | 0.00038137 | 4.6509e-06
2013-05-04 | 299339 | BBH8A | URBAN | Equipment failure | 28.545 | 102 | 2911.59 | 0.002931 | 2.8736e-05
2013-05-04 | 299340 | KSN7 | RURAL | Equipment failure | 69.3 | 100 | 6930 | 0.019977 | 0.00019977
2013-05-04 | 299343 | CFD2A | URBAN | Equipment failure | 218.42 | 92 | 20094.64 | 0.020229 | 0.00021988
2013-05-05 | 299342 | LTA5 | URBAN | Animals | 1974.35 | 70.7037 | 142346.15 | 0.14329 | 0.0019875
2013-05-05 | 299342 | WNM2A | URBAN | Animals | 125.5 | 133 | 16685.5 | 0.016797 | 0.00012634
2013-05-05 | 299344 | BMG3B | URBAN | Other | 26.65 | 20 | 533 | 0.00053655 | 2.6828e-05
2013-05-05 | 299359 | CRY2A | RURAL | Equipment failure | 2 | 79.5 | 159 | 0.00045837 | 5.7657e-06
2013-05-05 | 299360 | WSE5A | RURAL | Animals | 80 | 543.9846 | 78464 | 0.2262 | 0.00023063
2013-05-05 | 299363 | NSW22B | URBAN | Other | 13.2 | 129 | 1702.8 | 0.0017142 | 1.3288e-05
2013-05-05 | 299367 | PRG2A | RURAL | Other | 1 | 87 | 87 | 0.00025081 | 2.8828e-06
2013-05-05 | 299368 | MBG1 | RURAL | Animals | 1 | 87 | 87 | 0.00025081 | 2.8828e-06
2013-05-06 | 299366 | ALY3A | URBAN | Animals | 163 | 92 | 14996 | 0.015096 | 0.00016408
2013-05-06 | 299373 | MRK6 | URBAN | Equipment failure | 29.75 | 38 | 1130.5 | 0.001138 | 2.9948e-05
2013-05-06 | 299375 | MDR24A | URBAN | Equipment failure | 47.5 | 228 | 21660 | 0.021804 | 4.7816e-05
2013-05-06 | 299380 | NSW35A | URBAN | Third party impacts | 35 | 89 | 3115 | 0.0031357 | 3.5233e-05
2013-05-06 | 299384 | NBR9 | RURAL | Other | 1 | 66 | 66 | 0.00019027 | 2.8829e-06
2013-05-06 | 299394 | BPN26A | RURAL | Weather | 41 | 50 | 2050 | 0.00591 | 0.0001182
2013-05-06 | 299396 | NDH1 | URBAN | Equipment failure | 1106.99 | 3 | 3320.97 | 0.003343 | 0.0011143
2013-05-06 | 299399 | WSE5A | RURAL | Animals | 16.5 | 192 | 3168 | 0.0091332 | 4.7569e-05
2013-05-06 | 299403 | CMY4 | RURAL | Other | 4 | 100 | 400 | 0.0011532 | 1.1532e-05
2013-05-07 | 299400 | ACR4 | URBAN | Equipment failure | 20.625 | 45 | 928.125 | 0.00093425 | 2.0761e-05
2013-05-07 | 299401 | CFD6A | URBAN | Other | 2277.17 | 16 | 36434.72 | 0.036675 | 0.0022922
2013-05-07 | 299436 | KWA12A | URBAN | Equipment failure | 73.5 | 25 | 1837.5 | 0.0018496 | 7.3985e-05
2013-05-07 | 299440 | MHL13A | URBAN | Equipment failure | 1982.25 | 48.1765 | 98280.5 | 0.098929 | 0.0019953
2013-05-07 | 299442 | BDT5 | RURAL | Third party impacts | 96.01 | 77 | 7392.77 | 0.021313 | 0.00027679
2013-05-07 | 299468 | IPL2A | RURAL | Equipment failure | 37.51 | 96 | 3600.96 | 0.010381 | 0.00010814
2013-05-07 | 299469 | ARG10 | URBAN | Equipment failure | 1.65 | 50 | 82.5 | 8.3044e-05 | 1.6609e-06
2013-05-07 | 299470 | GYN3A | RURAL | Vegetation | 3.3 | 65 | 214.5 | 0.0006184 | 9.5138e-06
2013-05-07 | 299472 | GGR5 | RURAL | Other | 16.5 | 76 | 1254 | 0.0036152 | 4.7569e-05
2013-05-08 | 299474 | CPB6 | URBAN | Equipment failure | 379.16 | 136.6957 | 47098.44 | 0.047409 | 0.00038166
2013-05-08 | 299494 | GYGGYS6 | RURAL | Equipment failure | 146 | 148.9524 | 14472 | 0.041721 | 0.0004209
2013-05-08 | 299500 | GGR4 | RURAL | Equipment failure | 7.5 | 60 | 450 | 0.0012973 | 2.1622e-05
2013-05-08 | 299502 | NIP5B | URBAN | Equipment failure | 10.7 | 90 | 963 | 0.00096935 | 1.0771e-05
2013-05-08 | 299532 | EMD3 | RURAL | Other | 1.32 | 152 | 200.64 | 0.00057842 | 3.8054e-06
2013-05-08 | 299533 | WNM2A | URBAN | Animals | 1973.82 | 169.8846 | 343430.34 | 0.34569 | 0.0019868
2013-05-08 | 299537 | AHD8 | URBAN | Equipment failure | 70 | 84 | 5880 | 0.0059187 | 7.0461e-05
2013-05-08 | 299537 | MLB4A | URBAN | Equipment failure | 62 | 81 | 5022 | 0.0050551 | 6.2409e-05
2013-05-08 | 299538 | TRG2A | URBAN | Equipment failure | 65 | 430 | 27950 | 0.028134 | 6.5428e-05
2013-05-08 | 299540 | MGL8 | URBAN | Equipment failure | 9 | 360 | 3240 | 0.0032613 | 9.0593e-06
2013-05-08 | 299542 | CBW11 | RURAL | Other | 0.33 | 89 | 29.37 | 8.467e-05 | 9.5135e-07
2013-05-08 | 299543 | TRG5 | URBAN | Equipment failure | 12.15 | 113 | 1372.95 | 0.001382 | 1.223e-05
2013-05-08 | 299544 | BLH10B | URBAN | Third party impacts | 37.29 | 188 | 6639.88 | 0.0066836 | 3.7536e-05
2013-05-08 | 299545 | JBB13A | RURAL | Animals | 23 | 95 | 2185 | 0.0062991 | 6.6306e-05
2013-05-08 | 299546 | MTB2A | RURAL | Animals | 29 | 154 | 4466 | 0.012875 | 8.3604e-05
2013-05-09 | 299573 | THL3 | RURAL | Equipment failure | 10 | 69 | 690 | 0.0019891 | 2.8828e-05
2013-05-09 | 299580 | MTN6B | URBAN | Equipment failure | 1 | 75 | 75 | 7.5494e-05 | 1.0066e-06
2013-05-09 | 299580 | MTNQBI9 | URBAN | Equipment failure | 11 | 75 | 825 | 0.00083043 | 1.1072e-05
2013-05-09 | 299580 | MTNWLP5 | RURAL | Equipment failure | 94.99 | 75 | 7124.25 | 0.020538 | 0.00027384
2013-05-09 | 299605 | MFN12A | RURAL | Other | 47.5 | 113 | 5367.5 | 0.015474 | 0.00013693
2013-05-09 | 299619 | BIS16A | URBAN | Other | 23.1 | 101 | 2333.1 | 0.0023485 | 2.3252e-05
2013-05-09 | 299634 | LLY3 | RURAL | Equipment failure | 0.67 | 170 | 113.9 | 0.00032835 | 1.9315e-06
2013-05-09 | 299711 | NSD29A | URBAN | Other | 36.5 | 126 | 4599 | 0.0046293 | 3.674e-05
2013-05-10 | 299674 | KBN1B | RURAL | Other | 26.4 | 35 | 924 | 0.0026639 | 7.6111e-05
2013-05-10 | 299675 | AFD5 | URBAN | Third party impacts | 23 | 135.1 | 4496.1 | 0.0045255 | 2.3151e-05
2013-05-10 | 299677 | PPE6A | RURAL | Other | 1 | 14 | 14 | 4.0362e-05 | 2.883e-06
2013-05-10 | 299679 | CPB6 | URBAN | Vegetation | 380.16 | 116 | 51582.12 | 0.05192 | 0.00038265
2013-05-10 | 299710 | TGP8A | URBAN | Other | 67.32 | 73 | 4914.36 | 0.0049465 | 6.7761e-05
2013-05-10 | 299712 | BMT4 | RURAL | Equipment failure | 4.455 | 92 | 409.86 | 0.0011816 | 1.2844e-05
2013-05-10 | 299713 | BMT4 | RURAL | Equipment failure | 8.91 | 114 | 1015.74 | 0.0029284 | 2.5687e-05
2013-05-11 | 299735 | GVN12A | URBAN | Equipment failure | 7.15 | 71 | 507.65 | 0.00051096 | 7.1966e-06
2013-05-11 | 299736 | NDH1 | URBAN | Equipment failure | 1105.99 | 131.5333 | 123643.37 | 0.12445 | 0.0011132
2013-05-11 | 299753 | KMR17B | URBAN | Other | 29.04 | 70 | 2032.8 | 0.0020461 | 2.9229e-05
2013-05-11 | 299780 | NSW26 | URBAN | Animals | 33 | 29 | 957 | 0.00096324 | 3.3215e-05
2013-05-12 | 299791 | BVL13A | URBAN | Weather | 59 | 114 | 6726 | 0.0067697 | 5.9383e-05
2013-05-12 | 299792 | CPB4 | URBAN | Third party impacts | 82 | 163 | 13366 | 0.013453 | 8.2532e-05
2013-05-12 | 299877 | HPK8A | URBAN | Animals | 55.77 | 57 | 3178.89 | 0.0031995 | 5.6132e-05
2013-05-13 | 299803 | KSN8 | RURAL | Equipment failure | 1439.99 | 90.9 | 203413.45 | 0.58684 | 0.0041543
2013-05-13 | 299824 | PBH1 | URBAN | Other | 1418 | 20 | 28360 | 0.028537 | 0.0014268
2013-05-13 | 299839 | MLY1 | RURAL | Other | 825.01 | 66 | 54450.66 | 0.15709 | 0.0023801
2013-05-13 | 299841 | BNH6A | RURAL | Equipment failure | 92 | 211.069 | 19168 | 0.055299 | 0.00026542
2013-05-13 | 299874 | GGR2 | RURAL | Other | 1.485 | 61 | 90.585 | 0.00026133 | 4.2842e-06
2013-05-14 | 299853 | SHW3 | URBAN | Other | 16.65 | 30 | 499.5 | 0.00050259 | 1.6753e-05
2013-05-14 | 299873 | CCY13A | URBAN | Equipment failure | 35.5 | 89.5 | 3656.5 | 0.0036791 | 3.5719e-05
2013-05-14 | 299875 | GYN6A | RURAL | Equipment failure | 16.5 | 40 | 660 | 0.0019042 | 4.7604e-05
2013-05-14 | 299876 | MBG2 | RURAL | Equipment failure | 69 | 153 | 10557 | 0.030458 | 0.00019907
2013-05-14 | 299879 | CPC25A | URBAN | Equipment failure | 6 | 58 | 348 | 0.00035015 | 6.0371e-06
2013-05-14 | 299904 | CBW5 | URBAN | Equipment failure | 759.75 | 72 | 61607 | 0.061988 | 0.00076444
2013-05-14 | 299927 | CCY13A | URBAN | Equipment failure | 35.5 | 172 | 6106 | 0.0061437 | 3.5719e-05
2013-05-14 | 299930 | NSW26 | URBAN | Animals | 33 | 66 | 2178 | 0.0021915 | 3.3204e-05
2013-05-15 | 299933 | NBR5A | RURAL | Other | 199 | 88 | 17512 | 0.050528 | 0.00057418
2013-05-15 | 300028 | CSE2 | URBAN | Equipment failure | 4.45 | 200 | 890 | 0.00089545 | 4.4773e-06
2013-05-15 | 300035 | ESK5A | RURAL | Other | 1 | 1004 | 1004 | 0.0028969 | 2.8853e-06
2013-05-16 | 300034 | TWG19 | URBAN | Other | 150.48 | 53 | 7975.44 | 0.0080239 | 0.00015139
2013-05-16 | 300038 | GYM7A | RURAL | Equipment failure | 11 | 103 | 1133 | 0.0032694 | 3.1741e-05
2013-05-16 | 300041 | CMY1 | RURAL | Third party impacts | 16 | 210.125 | 3451 | 0.0099581 | 4.6169e-05
2013-05-16 | 300042 | NBR13A | URBAN | Equipment failure | 4 | 114 | 456 | 0.00045877 | 4.0243e-06
2013-05-16 | 300044 | CPR6 | URBAN | Equipment failure | 100 | 153 | 15300 | 0.015393 | 0.00010061
2013-05-16 | 300081 | HWL11A | URBAN | Equipment failure | 2.5 | 196 | 490 | 0.00049297 | 2.5152e-06
2013-05-17 | 300082 | CVL3A | URBAN | Animals | 1778 | 69.0714 | 111773 | 0.11245 | 0.0017887
2013-05-17 | 300083 | CLD20A | RURAL | Equipment failure | 745 | 95 | 70775 | 0.20424 | 0.0021499
2013-05-17 | 300093 | NBR1 | RURAL | Other | 17 | 71 | 1207 | 0.0034832 | 4.9059e-05
2013-05-17 | 300095 | KLG14A | URBAN | Other | 24.42 | 30 | 732.6 | 0.00073701 | 2.4567e-05
2013-05-17 | 300096 | COR23A | RURAL | Vegetation | 38 | 105 | 3990 | 0.011514 | 0.00010966
2013-05-17 | 300108 | BPN2A | URBAN | Equipment failure | 23 | 95 | 2185 | 0.0021981 | 2.3138e-05
2013-05-17 | 300108 | BPN2B | URBAN | Equipment failure | 1 | 95 | 95 | 9.5572e-05 | 1.006e-06
2013-05-17 | 300108 | BPN3 | URBAN | Equipment failure | 1956 | 62 | 121272 | 0.122 | 0.0019678
2013-05-17 | 300108 | BPN4 | URBAN | Equipment failure | 859.1 | 83 | 71305.3 | 0.071734 | 0.00086427
2013-05-17 | 300108 | BPN7B | URBAN | Equipment failure | 21 | 127 | 2667 | 0.002683 | 2.1126e-05
2013-05-17 | 300129 | RCN4A | URBAN | Animals | 1455.66 | 114.32 | 146337.39 | 0.14722 | 0.0014644
2013-05-18 | 300132 | WMD13A | RURAL | Vegetation | 307 | 61 | 18727 | 0.054044 | 0.00088597
2013-05-18 | 300154 | VPT3A | RURAL | Animals | 16.83 | 57 | 959.31 | 0.0027685 | 4.857e-05
2013-05-19 | 300156 | RST8A | URBAN | Other | 323 | 19 | 6137 | 0.0061736 | 0.00032493
2013-05-19 | 300157 | AHL4A | URBAN | Other | 1 | 22 | 22 | 2.2131e-05 | 1.006e-06
2013-05-19 | 300174 | MLY6 | RURAL | Other | 615.5 | 15 | 9232.5 | 0.026645 | 0.0017763
2013-05-19 | 300177 | KLG7A | RURAL | Equipment failure | 76 | 61 | 4636 | 0.013379 | 0.00021933
2013-05-19 | 300178 | CVL3A | URBAN | Other | 67.32 | 84 | 5654.88 | 0.0056886 | 6.7722e-05
2013-05-19 | 300180 | HWL13A | URBAN | Other | 3.96 | 58 | 229.68 | 0.00023105 | 3.9836e-06
2013-05-19 | 300183 | DRD15B | URBAN | Other | 130.5 | 45 | 5872.5 | 0.0059075 | 0.00013128
2013-05-19 | 300183 | DRD5A | URBAN | Other | 22.5 | 42 | 945 | 0.00095064 | 2.2634e-05
2013-05-19 | 300197 | RBY16 | URBAN | Equipment failure | 19.47 | 21 | 408.87 | 0.00041131 | 1.9586e-05
2013-05-19 | 300198 | LRE4A | RURAL | Other | 310.5 | 16 | 4968 | 0.014338 | 0.0008961
2013-05-19 | 300205 | MLY3 | RURAL | Equipment failure | 5.94 | 163 | 968.22 | 0.0027943 | 1.7143e-05
2013-05-19 | 300206 | CNA9A | RURAL | Vegetation | 5 | 41 | 205 | 0.00059163 | 1.443e-05
2013-05-20 | 300200 | PBH3 | URBAN | Other | 52 | 86 | 4472 | 0.0044982 | 5.2305e-05
2013-05-20 | 300203 | NSW8A | URBAN | Animals | 69.96 | 72 | 5037.12 | 0.0050666 | 7.037e-05
2013-05-20 | 300204 | BLB2A | URBAN | Animals | 34.32 | 55 | 1887.6 | 0.0018987 | 3.4521e-05
2013-05-20 | 300219 | VSL13A | URBAN | Other | 4.29 | 40 | 171.6 | 0.00017261 | 4.3151e-06
2013-05-20 | 300232 | COR26A | RURAL | Other | 6 | 82 | 492 | 0.0014201 | 1.7318e-05
2013-05-20 | 300233 | CHL4 | URBAN | Vegetation | 95 | 232 | 22040 | 0.022169 | 9.5557e-05
2013-05-20 | 300234 | CHL2 | URBAN | Equipment failure | 29.37 | 45 | 1321.65 | 0.0013294 | 2.9542e-05
2013-05-20 | 300235 | SDM1 | RURAL | Other | 2 | 68 | 136 | 0.00039255 | 5.7728e-06
2013-05-20 | 300238 | CHL7 | URBAN | Equipment failure | 81.5 | 8 | 652 | 0.00065582 | 8.1977e-05
2013-05-20 | 300239 | GGR3 | RURAL | Animals | 3 | 89 | 267 | 0.00077067 | 8.6592e-06
2013-05-20 | 300241 | SPC2B | RURAL | Equipment failure | 1 | 129 | 129 | 0.00037235 | 2.8864e-06
2013-05-21 | 300253 | MTG7A | URBAN | Equipment failure | 1646.32 | 56.0667 | 87372.08 | 0.087872 | 0.0016557
2013-05-21 | 300257 | WMD2A | URBAN | Equipment failure | 1479 | 9 | 13311 | 0.013387 | 0.0014875
2013-05-21 | 300258 | KBR3A | RURAL | Equipment failure | 2 | 36 | 72 | 0.00020788 | 5.7745e-06
2013-05-21 | 300300 | WNM1A | URBAN | Animals | 59.895 | 100 | 5989.5 | 0.0060238 | 6.0238e-05
2013-05-21 | 300302 | CPK9 | RURAL | Other | 741.5 | 15 | 11122.5 | 0.032113 | 0.0021409
2013-05-21 | 300303 | ARL15B | URBAN | Other | 23 | 140 | 3220 | 0.0032384 | 2.3132e-05
2013-05-21 | 300304 | PBH6 | URBAN | Other | 88.11 | 156 | 13745.16 | 0.013824 | 8.8615e-05
2013-05-21 | 300305 | MLS9A | URBAN | Third party impacts | 434.06 | 80 | 33856.9 | 0.034051 | 0.00043655
2013-05-22 | 300306 | TWG10 | URBAN | Equipment failure | 736 | 7 | 5152 | 0.0051812 | 0.00074017
2013-05-22 | 300306 | TWG13A | URBAN | Equipment failure | 1043 | 7 | 7301 | 0.0073424 | 0.0010489
2013-05-22 | 300306 | TWG13B | URBAN | Equipment failure | 456.99 | 7 | 3198.93 | 0.0032171 | 0.00045958
2013-05-22 | 300313 | NSW17 | URBAN | Animals | 29.7 | 169 | 5019.3 | 0.0050477 | 2.9868e-05
2013-05-22 | 300314 | CLRSRD17 | URBAN | Third party impacts | 29 | 168 | 4872 | 0.0048996 | 2.9164e-05
2013-05-22 | 300355 | IPL3 | RURAL | Equipment failure | 12 | 48 | 576 | 0.0016632 | 3.465e-05
2013-05-22 | 300374 | CPC25A | URBAN | Equipment failure | 6 | 203 | 1218 | 0.0012249 | 6.034e-06
2013-05-22 | 300382 | MLY4 | RURAL | Equipment failure | 95 | 263 | 24985 | 0.072144 | 0.00027431
2013-05-22 | 300384 | HDA3A | URBAN | Equipment failure | 35.64 | 72 | 2566.08 | 0.0025806 | 3.5842e-05
2013-05-22 | 300385 | TRP2 | RURAL | Operational error | 4.95 | 97 | 480.15 | 0.0013864 | 1.4293e-05
2013-05-22 | 300386 | BHL1A | URBAN | Operational error | 116.83 | 30 | 3504.9 | 0.0035248 | 0.00011749
2013-05-22 | 300404 | GYGGYS6 | RURAL | Equipment failure | 568.67 | 58.3191 | 32524.85 | 0.093915 | 0.001642
2013-05-22 | 300414 | GYS5A | RURAL | Other | 8 | 187 | 1496 | 0.0043197 | 2.31e-05
2013-05-22 | 300417 | BIS2B | RURAL | Other | 26.07 | 102 | 2659.14 | 0.0076782 | 7.5277e-05
2013-05-22 | 300418 | MFN15A | RURAL | Equipment failure | 8 | 305 | 2440 | 0.0070454 | 2.31e-05
2013-05-22 | 300419 | MAI17 | URBAN | Operational error | 74.7186 | 142 | 10610.0412 | 0.01067 | 7.5142e-05
2013-05-22 | 300433 | TMH16A | URBAN | Weather | 19.5 | 446 | 8697 | 0.0087463 | 1.961e-05
2013-05-22 | 300693 | BHD35A | RURAL | Other | 29.5 | 241 | 7109.5 | 0.020529 | 8.5181e-05
2013-05-23 | 300453 | RIS4 | RURAL | Vegetation | 527 | 156 | 82212 | 0.2374 | 0.0015218
2013-05-23 | 300493 | SFD7A | URBAN | Other | 5.84 | 85 | 496.4 | 0.00049918 | 5.8727e-06
2013-05-23 | 300510 | BKD16A | URBAN | Other | 164.34 | 130 | 21364.2 | 0.021484 | 0.00016526
2013-05-23 | 300516 | DBY6 | URBAN | Equipment failure | 32 | 130 | 4160 | 0.0041833 | 3.2179e-05
2013-05-23 | 300533 | GGR1 | RURAL | Other | 5 | 59 | 295 | 0.00085187 | 1.4439e-05
2013-05-23 | 300534 | MBG4 | RURAL | Other | 1 | 310 | 310 | 0.00089519 | 2.8877e-06
2013-05-23 | 300654 | JBB3A | RURAL | Animals | 7 | 57 | 399 | 0.0011522 | 2.0214e-05
2013-05-24 | 300553 | STT1B | RURAL | Other | 6 | 78 | 468 | 0.0013518 | 1.733e-05
2013-05-24 | 300555 | THL1 | RURAL | Other | 176 | 16 | 2816 | 0.0081337 | 0.00050836
2013-05-24 | 300599 | CBT12A | RURAL | Weather | 42.72 | 3 | 128.16 | 0.00037018 | 0.00012339
2013-05-24 | 300629 | PPE6A | RURAL | Third party impacts | 32 | 347 | 11104 | 0.032073 | 9.2428e-05
2013-05-24 | 300630 | SPO16A | URBAN | Weather | 52.47 | 59 | 3095.73 | 0.0031127 | 5.2758e-05
2013-05-24 | 300631 | MTG15A | URBAN | Equipment failure | 19.95 | 56 | 1117.2 | 0.0011233 | 2.0059e-05
2013-05-24 | 300632 | MGP12A | RURAL | Weather | 630 | 51.9333 | 18570 | 0.053637 | 0.0018197
2013-05-24 | 300660 | CFD8A | URBAN | Equipment failure | 23.76 | 188 | 4466.88 | 0.0044914 | 2.389e-05
2013-05-25 | 300633 | CNB24A | RURAL | Other | 1155.33 | 47 | 54300.51 | 0.15687 | 0.0033376
2013-05-25 | 300634 | CNB26A | RURAL | Weather | 432.5 | 133.375 | 63869 | 0.18451 | 0.0012494
2013-05-25 | 300636 | PWC6 | RURAL | Vegetation | 402 | 36.8947 | 12162 | 0.035134 | 0.0011613
2013-05-25 | 300639 | BDT1 | RURAL | Vegetation | 83 | 159.6923 | 13327 | 0.0385 | 0.00023977
2013-05-25 | 300655 | CMA8A | RURAL | Third party impacts | 4.95 | 101 | 499.95 | 0.0014443 | 1.43e-05
2013-05-25 | 300662 | AHL6A | URBAN | Third party impacts | 124 | 215.5 | 33216 | 0.033395 | 0.00012467
2013-05-26 | 300663 | NGE4B | URBAN | Weather | 1.8 | 16 | 28.8 | 2.8954e-05 | 1.8096e-06
2013-05-26 | 300666 | BHD33A | URBAN | Other | 85.6 | 196.5 | 16825.6 | 0.016916 | 8.6058e-05
2013-05-26 | 300681 | LLY1 | RURAL | Other | 8 | 108 | 864 | 0.0024962 | 2.3113e-05
2013-05-27 | 300699 | GGR5 | RURAL | Other | 21 | 9 | 189 | 0.00054617 | 6.0685e-05
2013-05-27 | 300720 | TCB1 | RURAL | Equipment failure | 1150.49 | 69 | 79383.81 | 0.2294 | 0.0033247
2013-05-27 | 300721 | MLT21B | URBAN | Animals | 1353.83 | 19 | 25722.77 | 0.025856 | 0.0013609
2013-05-28 | 300733 | LHM2 | URBAN | Other | 31.02 | 86 | 2667.72 | 0.0026813 | 3.1178e-05
2013-05-28 | 300734 | BLN6A | URBAN | Other | 16.5 | 150 | 2475 | 0.0024876 | 1.6584e-05
2013-05-28 | 300735 | BDB32A | RURAL | Animals | 1 | 97 | 97 | 0.00028036 | 2.8903e-06
2013-05-28 | 300765 | MMC19A | URBAN | Third party impacts | 1 | 59 | 59 | 5.93e-05 | 1.0051e-06
2013-05-28 | 300765 | MMC19B | URBAN | Third party impacts | 1094.49 | 118.1667 | 131669.91 | 0.13234 | 0.0011001
2013-05-28 | 300784 | SMF2A | RURAL | Animals | 438.99 | 135.4468 | 94986.42 | 0.27454 | 0.0012688
2013-05-28 | 300792 | TWT12A | RURAL | Other | 11 | 120 | 1320 | 0.0038152 | 3.1793e-05
2013-05-28 | 300793 | CPK9 | RURAL | Equipment failure | 99 | 150 | 14850 | 0.042921 | 0.00028614
2013-05-28 | 300794 | BTN2 | RURAL | Other | 3.3 | 55 | 181.5 | 0.00052459 | 9.5379e-06
2013-05-29 | 300835 | CPL3A | URBAN | Equipment failure | 76 | 70 | 5320 | 0.0053466 | 7.638e-05
2013-05-29 | 300858 | TMH15A | URBAN | Other | 48 | 126 | 6048 | 0.0060782 | 4.824e-05
2013-05-30 | 300893 | NRA16A | RURAL | Weather | 114 | 59 | 6726 | 0.019446 | 0.0003296
2013-05-30 | 300894 | HPK10 | URBAN | Other | 1349.5 | 29 | 39135.5 | 0.039327 | 0.0013561
2013-05-30 | 300896 | TRP2 | RURAL | Weather | 0.66 | 150 | 99 | 0.00028623 | 1.9082e-06
2013-05-30 | 300897 | HPK10 | URBAN | Equipment failure | 154 | 143 | 22022 | 0.02213 | 0.00015476
2013-05-30 | 300922 | DBY11 | URBAN | Animals | 28.38 | 81 | 2298.78 | 0.0023101 | 2.8519e-05
2013-05-30 | 300923 | KLG17A | URBAN | Other | 46.2 | 123 | 5682.6 | 0.0057105 | 4.6427e-05
2013-05-30 | 300924 | VSL3A | URBAN | Operational error | 29.04 | 65 | 1887.6 | 0.0018969 | 2.9182e-05
2013-05-30 | 300982 | KLG17A | URBAN | Equipment failure | 70 | 217 | 15190 | 0.015264 | 7.0343e-05
2013-05-31 | 300957 | ARG9A | URBAN | Other | 23.43 | 173 | 4053.39 | 0.0040729 | 2.3543e-05
2013-05-31 | 300981 | KMR25A | RURAL | Third party impacts | 20 | 32 | 640 | 0.0018507 | 5.7833e-05
2013-05-31 | 300983 | MGL5 | URBAN | Equipment failure | 52 | 329 | 17108 | 0.01719 | 5.225e-05
2013-05-31 | 300984 | CLD11 | RURAL | Other | 9 | 103 | 927 | 0.0026806 | 2.6025e-05
2013-05-31 | 300985 | LTN3 | URBAN | Equipment failure | 30.4 | 70 | 2128 | 0.0021382 | 3.0546e-05
2013-05-31 | 300995 | SGT9 | URBAN | Equipment failure | 174 | 10 | 1740 | 0.0017484 | 0.00017484
2013-06-01 | 300994 | GYM8B | URBAN | Equipment failure | 133.5 | 83 | 11080.5 | 0.011133 | 0.00013413
2013-06-01 | 300996 | MMC24A | URBAN | Equipment failure | 23.43 | 42 | 984.06 | 0.0009887 | 2.354e-05
2013-06-01 | 300997 | MFD2A | URBAN | Equipment failure | 780 | 14 | 10920 | 0.010971 | 0.00078368
2013-06-01 | 300997 | MFD3A | RURAL | Equipment failure | 946 | 14.7286 | 18559 | 0.053675 | 0.0027359
2013-06-01 | 300997 | MFD5A | RURAL | Equipment failure | 514 | 15 | 7710 | 0.022298 | 0.0014865
2013-06-01 | 300998 | GYM7A | RURAL | Equipment failure | 11.5 | 95 | 1092.5 | 0.0031596 | 3.3259e-05
2013-06-01 | 301035 | AGT23A | URBAN | Equipment failure | 31.85 | 176 | 5605.6 | 0.005632 | 3.2e-05
2013-06-02 | 301014 | CBW11 | RURAL | Equipment failure | 1109.5 | 93.0505 | 112876 | 0.32648 | 0.0032091
2013-06-02 | 301021 | NRG16A | RURAL | Third party impacts | 518.5 | 130.0263 | 54989.5 | 0.15905 | 0.0014997
2013-06-02 | 301023 | CBT12A | RURAL | Operational error | 830.9 | 32.9307 | 22906.2 | 0.066254 | 0.0024033
2013-06-02 | 301023 | CBW11 | RURAL | Operational error | 550 | 17.5676 | 9548 | 0.027617 | 0.0015908
2013-06-02 | 301037 | BHD44A | URBAN | Operational error | 31.02 | 87 | 2698.74 | 0.0027113 | 3.1164e-05
2013-06-03 | 301034 | AGE10 | URBAN | Vegetation | 2248.5 | 26 | 58461 | 0.05873 | 0.0022589
2013-06-03 | 301036 | WMD6A | URBAN | Other | 12 | 113 | 1356 | 0.0013623 | 1.2055e-05
2013-06-03 | 301042 | VSL1B | URBAN | Third party impacts | 12 | 430 | 5160 | 0.0051838 | 1.2055e-05
2013-06-03 | 301043 | LWD1 | RURAL | Third party impacts | 647.5 | 6 | 3885 | 0.011238 | 0.001873
2013-06-03 | 301045 | BGY15A | URBAN | Third party impacts | 1436 | 92.5 | 88445.5 | 0.088853 | 0.0014426
2013-06-03 | 301078 | TSN15A | URBAN | Equipment failure | 16.995 | 195 | 3314.025 | 0.0033293 | 1.7073e-05
2013-06-03 | 301079 | SBK11 | URBAN | Third party impacts | 97 | 113 | 10961 | 0.011012 | 9.7447e-05
2013-06-03 | 301080 | SBK11 | URBAN | Equipment failure | 32.01 | 113 | 3617.13 | 0.0036338 | 3.2158e-05
2013-06-03 | 301081 | HIS12A | URBAN | Equipment failure | 11.7 | 56 | 655.2 | 0.00065822 | 1.1754e-05
2013-06-03 | 301082 | WNM3 | URBAN | Equipment failure | 63.69 | 88 | 5604.72 | 0.0056306 | 6.3984e-05
2013-06-03 | 301083 | AHD10A | URBAN | Animals | 77.7678 | 48 | 3732.8544 | 0.0037501 | 7.8126e-05
2013-06-03 | 301095 | CBW7 | RURAL | Animals | 34 | 109 | 3706 | 0.01072 | 9.835e-05
2013-06-04 | 301093 | GLY11A | URBAN | Equipment failure | 2 | 19 | 38 | 3.8169e-05 | 2.0089e-06
2013-06-04 | 301096 | WMR3 | RURAL | Other | 1 | 100 | 100 | 0.00028932 | 2.8932e-06
2013-06-04 | 301115 | RLA6 | URBAN | Equipment failure | 28 | 140 | 3920 | 0.0039374 | 2.8124e-05
2013-06-04 | 301119 | CFD6A | URBAN | Equipment failure | 46.86 | 50 | 2343 | 0.0023534 | 4.7068e-05
2013-06-04 | 301121 | CFD6A | URBAN | Equipment failure | 46.86 | 30 | 1405.8 | 0.001412 | 4.7068e-05
2013-06-04 | 301126 | NBR12A | RURAL | Other | 3.3 | 96 | 316.8 | 0.00091657 | 9.5476e-06
2013-06-04 | 301145 | SBH11 | URBAN | Equipment failure | 164 | 132 | 21648 | 0.021744 | 0.00016473
2013-06-05 | 301144 | NGE4A | URBAN | Other | 167 | 34 | 5678 | 0.0057028 | 0.00016773
2013-06-05 | 301144 | NGE4B | URBAN | Other | 727 | 34 | 24718 | 0.024826 | 0.00073017
2013-06-05 | 301155 | JBB4A | URBAN | Equipment failure | 22 | 72 | 1584 | 0.0015909 | 2.2096e-05
2013-06-05 | 301157 | NGE4B | URBAN | Third party impacts | 12.5 | 72 | 900 | 0.00090392 | 1.2555e-05
2013-06-05 | 301203 | SFD7A | URBAN | Other | 27.9378 | 67 | 1871.8326 | 0.00188 | 2.806e-05
2013-06-05 | 301204 | GAP1A | URBAN | Equipment failure | 102 | 341 | 34782 | 0.034934 | 0.00010244
2013-06-05 | 301206 | RLA5 | URBAN | Equipment failure | 16 | 64 | 1024 | 0.0010285 | 1.607e-05
2013-06-05 | 301207 | LHM1A | URBAN | Third party impacts | 132.5 | 155 | 20537.5 | 0.020627 | 0.00013308
2013-06-05 | 301208 | BTA1A | URBAN | Third party impacts | 15.51 | 78 | 1209.78 | 0.0012151 | 1.5578e-05
2013-06-05 | 301293 | KBR1A | RURAL | Third party impacts | 5 | 40 | 200 | 0.00057871 | 1.4468e-05
2013-06-05 | 301294 | TBV4 | RURAL | Equipment failure | 54 | 70 | 3780 | 0.010938 | 0.00015625
2013-06-06 | 301236 | AGT23A | URBAN | Equipment failure | 45.5 | 226 | 10283 | 0.010327 | 4.5695e-05
2013-06-06 | 301237 | BRD8A | RURAL | Equipment failure | 9 | 152 | 1368 | 0.0039589 | 2.6045e-05
2013-06-06 | 301324 | TWG17 | URBAN | Equipment failure | 136.33 | 57 | 7770.81 | 0.007804 | 0.00013691
2013-06-07 | 301327 | SMR7A | URBAN | Equipment failure | 45 | 113 | 5085 | 0.0051061 | 4.5187e-05
2013-06-07 | 301353 | GBN4 | RURAL | Equipment failure | 20.5 | 17 | 348.5 | 0.0010088 | 5.934e-05
2013-06-07 | 301359 | MDH4A | URBAN | Third party impacts | 139 | 79.7778 | 11611 | 0.011659 | 0.00013958
2013-06-07 | 301359 | MDH4B | URBAN | Third party impacts | 1 | 79 | 79 | 7.9328e-05 | 1.0041e-06
2013-06-07 | 301361 | LBCVPK5 | URBAN | Other | 130.42 | 58 | 7564.36 | 0.0075957 | 0.00013096
2013-06-07 | 301364 | MFN1B | URBAN | Equipment failure | 333 | 49 | 15813 | 0.015879 | 0.00033438
2013-06-07 | 301365 | ACR4 | URBAN | Equipment failure | 750 | 77.4706 | 60020 | 0.060269 | 0.00075311
2013-06-07 | 301366 | VSL12A | URBAN | Equipment failure | 8.1 | 154 | 1247.4 | 0.0012526 | 8.1336e-06
2013-06-07 | 301394 | LGL13A | URBAN | Third party impacts | 521.25 | 256.0909 | 83730.75 | 0.084078 | 0.00052341
2013-06-07 | 301396 | LBCVPK5 | URBAN | Other | 123.42 | 98 | 12095.16 | 0.012145 | 0.00012393
2013-06-07 | 301399 | NSW17 | URBAN | Animals | 29.7 | 82 | 2435.4 | 0.0024455 | 2.9823e-05
2013-06-07 | 301400 | MCW4 | RURAL | Other | 44.55 | 231 | 10291.05 | 0.029789 | 0.00012896
2013-06-08 | 301397 | MTG15A | URBAN | Equipment failure | 5 | 50 | 250 | 0.00025102 | 5.0203e-06
2013-06-08 | 301413 | BKD12A | URBAN | Other | 31.68 | 75 | 2376 | 0.0023857 | 3.1809e-05
2013-06-08 | 301434 | AHD5 | URBAN | Equipment failure | 132 | 64 | 8448 | 0.0084823 | 0.00013254
2013-06-08 | 301436 | RLA7 | URBAN | Third party impacts | 7 | 241 | 1687 | 0.0016939 | 7.0285e-06
2013-06-09 | 301440 | MHL12A | RURAL | Equipment failure | 1.53 | 205 | 313.65 | 0.00090811 | 4.4298e-06
2013-06-09 | 301441 | WCL19A | RURAL | Vegetation | 813 | 95 | 77235 | 0.22362 | 0.0023539
2013-06-09 | 301445 | ADAMLS23 | URBAN | Other | 1 | 277 | 277 | 0.00027811 | 1.004e-06
2013-06-09 | 301448 | TGW1 | RURAL | Animals | 441.98 | 107.9112 | 48108.4 | 0.13929 | 0.0012797
2013-06-09 | 301452 | 341 | URBAN | Animals | 1 | 160 | 160 | 0.00016064 | 1.004e-06
2013-06-10 | 301453 | WMD6A | URBAN | Vegetation | 3.96 | 55 | 217.8 | 0.00021866 | 3.9756e-06
2013-06-10 | 301454 | EMD1 | RURAL | Other | 361.5 | 20 | 7230 | 0.020933 | 0.0010466
2013-06-10 | 301455 | GYM2A | RURAL | Weather | 2 | 216 | 432 | 0.0012507 | 5.7905e-06
2013-06-10 | 301456 | CPK13 | RURAL | Other | 1868 | 16 | 29888 | 0.086533 | 0.0054083
2013-06-10 | 301459 | INA2A | URBAN | Equipment failure | 1790.32 | 84.625 | 151004.74 | 0.1516 | 0.0017974
2013-06-10 | 301460 | BLH10A | URBAN | Equipment failure | 409 | 90.7241 | 34926.5 | 0.035064 | 0.00041061
2013-06-10 | 301460 | BLH10B | URBAN | Equipment failure | 2358.5 | 79 | 186321.5 | 0.18705 | 0.0023678
2013-06-10 | 301461 | BLBNFM6 | URBAN | Animals | 158 | 207 | 32706 | 0.032835 | 0.00015862
2013-06-10 | 301462 | LGL15A | URBAN | Weather | 116.5 | 245 | 28542.5 | 0.028655 | 0.00011696
2013-06-10 | 301463 | BVLNCM7 | URBAN | Equipment failure | 18 | 73 | 1314 | 0.0013192 | 1.8071e-05
2013-06-10 | 301464 | JDL7 | URBAN | Equipment failure | 21.249 | 116 | 2464.884 | 0.0024746 | 2.1333e-05
2013-06-10 | 301465 | INA1A | URBAN | Equipment failure | 5.25 | 142 | 745.5 | 0.00074843 | 5.2707e-06
2013-06-10 | 301466 | SMR7A | URBAN | Equipment failure | 2.295 | 465 | 1067.175 | 0.0010714 | 2.304e-06
2013-06-10 | 301467 | WMR3 | RURAL | Other | 166 | 123 | 20418 | 0.059115 | 0.00048061
2013-06-10 | 301468 | CRM16A | RURAL | Equipment failure | 11 | 101 | 1111 | 0.0032166 | 3.1848e-05
2013-06-10 | 301469 | MGL2A | RURAL | Weather | 1009 | 119.7143 | 121686 | 0.35231 | 0.0029213
2013-06-11 | 301470 | ACFQBI5 | URBAN | Other | 17 | 68 | 1156 | 0.0011605 | 1.7066e-05
2013-06-11 | 301472 | MTB15A | RURAL | Equipment failure | 232.5 | 22 | 5115 | 0.014808 | 0.00067311
2013-06-11 | 301493 | RCN6A | URBAN | Equipment failure | 12.88 | 119 | 1532.72 | 0.0015387 | 1.293e-05
2013-06-11 | 301513 | MTB15A | RURAL | Equipment failure | 232.5 | 90.9118 | 7662.5 | 0.022184 | 0.00067311
2013-06-11 | 301517 | CRB24B | URBAN | Equipment failure | 741.01 | 98.25 | 59987.74 | 0.060222 | 0.0007439
2013-06-11 | 301533 | CMV7 | URBAN | Equipment failure | 3 | 159 | 477 | 0.00047886 | 3.0117e-06
2013-06-11 | 301533 | CMV9B | URBAN | Equipment failure | 3.99 | 159 | 634.41 | 0.00063688 | 4.0056e-06
2013-06-11 | 301534 | OXL5A | URBAN | Equipment failure | 53.26 | 111.381 | 4980.4 | 0.0049998 | 5.3468e-05
2013-06-11 | 301534 | OXL5B | URBAN | Equipment failure | 1 | 81 | 81 | 8.1316e-05 | 1.0039e-06
2013-06-11 | 301535 | HIS1B | URBAN | Equipment failure | 12.8 | 29 | 371.2 | 0.00037265 | 1.285e-05
2013-06-11 | 301564 | PRG2A | RURAL | Equipment failure | 2 | 95 | 190 | 0.00055007 | 5.7902e-06
2013-06-11 | 301565 | NSW8A | URBAN | Equipment failure | 9.36 | 223 | 2087.28 | 0.0020954 | 9.3965e-06
2013-06-11 | 301566 | TWT15A | RURAL | Other | 3.96 | 72 | 285.12 | 0.00082545 | 1.1465e-05
2013-06-11 | 301567 | IPL1 | RURAL | Equipment failure | 12 | 321 | 3852 | 0.011152 | 3.4741e-05
2013-06-11 | 301568 | SPD21A | URBAN | Third party impacts | 51 | 94 | 4794 | 0.0048127 | 5.1199e-05
2013-06-11 | 301568 | SPD21B | URBAN | Third party impacts | 1 | 110.5 | 221 | 0.00022186 | 1.0039e-06
2013-06-11 | 301569 | AGE7A | RURAL | Equipment failure | 18 | 70 | 1260 | 0.0036478 | 5.2112e-05
2013-06-11 | 301569 | AGE7B | URBAN | Equipment failure | 974 | 42 | 40908 | 0.041067 | 0.0009778
2013-06-11 | 301572 | CRB24B | URBAN | Equipment failure | 67.67 | 480 | 32481.6 | 0.032608 | 6.7934e-05
2013-06-11 | 301574 | CPK13 | RURAL | Equipment failure | 66.66 | 77 | 5132.82 | 0.01486 | 0.00019299
2013-06-12 | 301573 | TMH3A | URBAN | Animals | 849 | 116.7692 | 98104 | 0.098483 | 0.00085228
2013-06-12 | 301613 | GYS2A | URBAN | Equipment failure | 7 | 123 | 861 | 0.00086432 | 7.027e-06
2013-06-12 | 301614 | AHL9A | URBAN | Equipment failure | 1637.5 | 148.72 | 153340.5 | 0.15393 | 0.0016438
2013-06-12 | 301614 | AHL9B | URBAN | Equipment failure | 1 | 55 | 55 | 5.5212e-05 | 1.0039e-06
2013-06-12 | 301617 | EMD1 | RURAL | Other | 243.5 | 68.7143 | 24264.5 | 0.070245 | 0.00070492
2013-06-12 | 301618 | SGT7 | URBAN | Other | 901 | 11 | 9911 | 0.0099493 | 0.00090448
2013-06-12 | 301654 | EMD1 | RURAL | Equipment failure | 4 | 83 | 332 | 0.00096113 | 1.158e-05
2013-06-12 | 301657 | AHD5 | URBAN | Equipment failure | 52 | 52 | 2704 | 0.0027144 | 5.2201e-05
2013-06-12 | 301684 | WRG11A | URBAN | Other | 833.25 | 64 | 53328 | 0.053534 | 0.00083647
2013-06-12 | 301685 | BDT3 | RURAL | Weather | 24 | 135 | 3240 | 0.0093797 | 6.9479e-05
2013-06-12 | 301686 | MFD2A | URBAN | Other | 22 | 600 | 13200 | 0.013251 | 2.2085e-05
2013-06-12 | 301687 | IPS15B | URBAN | Other | 11.22 | 91 | 1021.02 | 0.001025 | 1.1263e-05
2013-06-12 | 301688 | GYS2A | URBAN | Equipment failure | 4.62 | 136 | 628.32 | 0.00063075 | 4.6378e-06
2013-06-12 | 301689 | TWT12A | RURAL | Other | 7.92 | 88 | 696.96 | 0.0020177 | 2.2928e-05
2013-06-12 | 301690 | MLB3A | RURAL | Other | 110.55 | 56 | 6190.8 | 0.017922 | 0.00032004
2013-06-12 | 301691 | NIP2A | URBAN | Equipment failure | 25.575 | 80 | 2046 | 0.0020539 | 2.5674e-05
2013-06-13 | 301692 | LBH1B | RURAL | Equipment failure | 341 | 56.7449 | 40117 | 0.11615 | 0.0009873
2013-06-13 | 301693 | MCN1 | RURAL | Other | 7 | 6 | 42 | 0.0001216 | 2.0267e-05
2013-06-13 | 301694 | UPC2 | RURAL | Other | 7.5 | 56 | 420 | 0.001216 | 2.1715e-05
2013-06-13 | 301713 | ENG9 | URBAN | Equipment failure | 1232.5 | 53 | 65322.5 | 0.065569 | 0.0012372
2013-06-13 | 301733 | SFD7A | URBAN | Animals | 27.9378 | 69 | 1927.7082 | 0.001935 | 2.8043e-05
2013-06-13 | 301777 | KBN5A | RURAL | Equipment failure | 21 | 210 | 4410 | 0.012768 | 6.0802e-05
2013-06-13 | 301806 | WMR2 | RURAL | Other | 3 | 92 | 276 | 0.00079911 | 8.686e-06
2013-06-13 | 301807 | AHL6A | URBAN | Equipment failure | 67.32 | 302 | 13635.36 | 0.013687 | 6.7574e-05
2013-06-13 | 301808 | RCF10A | URBAN | Equipment failure | 90 | 53 | 2294.1 | 0.0023028 | 9.034e-05
2013-06-13 | 301809 | TWG13A | URBAN | Animals | 35.64 | 97 | 3457.08 | 0.0034701 | 3.5775e-05
2013-06-13 | 301810 | PBH6 | URBAN | Other | 57.42 | 67 | 3847.14 | 0.0038617 | 5.7637e-05
2013-06-13 | 301811 | TCB1 | RURAL | Equipment failure | 56.5 | 125 | 7062.5 | 0.020448 | 0.00016359
2013-06-13 | 301817 | BLH10B | URBAN | Equipment failure | 41 | 228 | 9348 | 0.0093833 | 4.1155e-05
2013-06-14 | 301813 | UMG3A | URBAN | Equipment failure | 386 | 83.6667 | 32573.5 | 0.032694 | 0.00038743
2013-06-14 | 301814 | SBK11 | URBAN | Third party impacts | 1373.5 | 30.3333 | 41637.5 | 0.041791 | 0.0013786
2013-06-14 | 301816 | RCF1A | URBAN | Other | 181.5 | 77 | 13975.5 | 0.014027 | 0.00018217
2013-06-14 | 301818 | AFD7 | URBAN | Third party impacts | 2 | 422 | 844 | 0.00084712 | 2.0074e-06
2013-06-14 | 301854 | TRP2 | RURAL | Equipment failure | 89.5 | 41 | 3669.5 | 0.010625 | 0.00025916
2013-06-14 | 301895 | CPC2B | URBAN | Other | 42.9 | 97 | 4161.3 | 0.0041767 | 4.3058e-05
2013-06-14 | 301896 | INA1A | URBAN | Equipment failure | 16.8 | 366 | 6148.8 | 0.0061715 | 1.6862e-05
2013-06-14 | 301921 | CNB21B | URBAN | Third party impacts | 1278.75 | 137.2174 | 159029.25 | 0.15962 | 0.0012835
2013-06-14 | 301924 | CLM6 | URBAN | Animals | 60.72 | 113 | 6861.36 | 0.0068867 | 6.0944e-05
2013-06-14 | 301943 | TMH5A | URBAN | Other | 64 | 373 | 23872 | 0.02396 | 6.4236e-05
2013-06-15 | 301925 | CLM4A | URBAN | Third party impacts | 19.5 | 45 | 877.5 | 0.00088067 | 1.9571e-05
2013-06-15 | 301926 | KCY1 | URBAN | Vegetation | 617 | 18 | 11106 | 0.011146 | 0.00061923
2013-06-15 | 301926 | KCY2 | RURAL | Vegetation | 358.26 | 18 | 6448.68 | 0.018674 | 0.0010375
2013-06-15 | 301926 | KCY3 | URBAN | Vegetation | 5.65 | 18 | 101.7 | 0.00010207 | 5.6704e-06
2013-06-15 | 301926 | KCY4 | RURAL | Vegetation | 706.13 | 18 | 12710.34 | 0.036807 | 0.0020449
2013-06-15 | 301926 | KCY5 | RURAL | Vegetation | 525.99 | 18 | 9467.82 | 0.027417 | 0.0015232
2013-06-15 | 301926 | WFD1B | RURAL | Vegetation | 351.97 | 18 | 6335.46 | 0.018347 | 0.0010193
2013-06-15 | 301926 | WFD2A | URBAN | Vegetation | 1 | 18 | 18 | 1.8065e-05 | 1.0036e-06
2013-06-15 | 301926 | WFD2B | RURAL | Vegetation | 814 | 18 | 14652 | 0.04243 | 0.0023572
2013-06-15 | 301926 | WFD3A | RURAL | Vegetation | 261 | 18 | 4698 | 0.013605 | 0.00075582
2013-06-15 | 301926 | WFD5A | RURAL | Vegetation | 555.5 | 18 | 9999 | 0.028956 | 0.0016086
2013-06-15 | 301926 | WFD6A | RURAL | Vegetation | 362 | 18 | 6516 | 0.018869 | 0.0010483
2013-06-15 | 301933 | TBV1 | RURAL | Other | 43.5 | 32 | 1392 | 0.004031 | 0.00012597
2013-06-15 | 301944 | TBV4 | RURAL | Other | 13.5 | 215 | 2902.5 | 0.0084052 | 3.9094e-05
2013-06-15 | 301945 | HWL6A | URBAN | Other | 107 | 228 | 24396 | 0.024484 | 0.00010739
2013-06-15 | 301946 | BDT1 | RURAL | Animals | 404 | 53.0938 | 41464 | 0.12007 | 0.0011699
2013-06-16 | 301950 | CPL25B | URBAN | Equipment failure | 11 | 284 | 3124 | 0.0031351 | 1.1039e-05
2013-06-16 | 301954 | LHM7 | URBAN | Equipment failure | 15.5 | 27 | 418.5 | 0.00041999 | 1.5555e-05
2013-06-16 | 301955 | NSW17 | URBAN | Equipment failure | 44 | 74 | 3256 | 0.0032676 | 4.4157e-05
2013-06-16 | 301965 | HDA10A | URBAN | Animals | 1741 | 78 | 135798 | 0.13628 | 0.0017472
2013-06-16 | 301969 | RCF7A | URBAN | Equipment failure | 38 | 383 | 14554 | 0.014606 | 3.8135e-05
2013-06-17 | 301970 | BHD7A | URBAN | Equipment failure | 1166.5 | 82 | 95653 | 0.095983 | 0.0011705
2013-06-17 | 301973 | NMC3A | RURAL | Animals | 2 | 77 | 154 | 0.00044604 | 5.7927e-06
2013-06-17 | 301974 | MGP13A | RURAL | Equipment failure | 151 | 256.3333 | 37329 | 0.10812 | 0.00043735
2013-06-17 | 301975 | KBN15A | URBAN | Equipment failure | 1 | 185 | 185 | 0.00018564 | 1.0034e-06
2013-06-17 | 301976 | HWL11A | URBAN | Equipment failure | 14.1 | 139.5 | 1690.12 | 0.0016959 | 1.4149e-05
2013-06-17 | 301977 | BTA5A | RURAL | Vegetation | 15 | 20 | 300 | 0.00086891 | 4.3445e-05
2013-06-17 | 301994 | YDA1B | RURAL | Equipment failure | 408 | 4 | 1632 | 0.0047269 | 0.0011817
2013-06-17 | 301994 | YDA2B | RURAL | Equipment failure | 170 | 4 | 680 | 0.0019695 | 0.00049238
2013-06-17 | 301994 | YDA3A | RURAL | Equipment failure | 394.5 | 4 | 1578 | 0.0045705 | 0.0011426
2013-06-17 | 301994 | YDA5A | RURAL | Equipment failure | 886.23 | 4 | 3544.92 | 0.010267 | 0.0025668
2013-06-17 | 301994 | YDA6A | URBAN | Equipment failure | 5 | 4 | 20 | 2.0069e-05 | 5.0172e-06
2013-06-17 | 301999 | BTN2 | RURAL | Equipment failure | 1 | 161 | 161 | 0.00046631 | 2.8964e-06
2013-06-17 | 302001 | PBH6 | URBAN | Operational error | 123.25 | 80 | 9860 | 0.009894 | 0.00012367
2013-06-17 | 302015 | RCF7A | URBAN | Equipment failure | 38 | 205 | 7790 | 0.0078168 | 3.8131e-05
2013-06-17 | 302017 | BLBNFM6 | URBAN | Animals | 23.1 | 72 | 1663.2 | 0.0016689 | 2.318e-05
2013-06-17 | 302018 | YDA3A | RURAL | Third party impacts | 5.36 | 172 | 921.92 | 0.0026702 | 1.5525e-05
2013-06-17 | 302019 | MAI14 | URBAN | Other | 177.83 | 134 | 23829.22 | 0.023911 | 0.00017844
2013-06-18 | 302014 | INA2A | URBAN | Animals | 1792.32 | 126.1667 | 226518.32 | 0.22728 | 0.0017983
2013-06-18 | 302020 | SPD1A | URBAN | Third party impacts | 4.95 | 150 | 742.5 | 0.00074499 | 4.9666e-06
2013-06-18 | 302033 | CBW6 | RURAL | Equipment failure | 2162 | 32.2544 | 210425 | 0.60952 | 0.0062625
2013-06-18 | 302037 | TGW2 | RURAL | Equipment failure | 144 | 93 | 13392 | 0.038792 | 0.00041711
2013-06-18 | 302038 | THL1 | RURAL | Other | 3 | 43 | 129 | 0.00037366 | 8.6899e-06
2013-06-18 | 302041 | INA2A | URBAN | Equipment failure | 68 | 142 | 9656 | 0.0096884 | 6.8228e-05
2013-06-18 | 302042 | INA2A | URBAN | Equipment failure | 28.05 | 24 | 673.2 | 0.00067546 | 2.8144e-05
2013-06-18 | 302045 | MLY1 | RURAL | Equipment failure | 4 | 255 | 1020 | 0.0029546 | 1.1586e-05
2013-06-18 | 302047 | NSW16A | URBAN | Animals | 37.95 | 159 | 6034.05 | 0.0060543 | 3.8077e-05
2013-06-18 | 302048 | BHD23A | RURAL | Other | 3.96 | 83 | 328.68 | 0.00095206 | 1.1471e-05
2013-06-18 | 302053 | CLM3 | RURAL | Equipment failure | 133.33 | 19 | 2533.27 | 0.0073379 | 0.00038621
2013-06-18 | 302076 | WSE5A | RURAL | Other | 1.98 | 153 | 302.94 | 0.0008775 | 5.7353e-06
2013-06-18 | 302079 | GLY12A | URBAN | Other | 34.32 | 43 | 1475.76 | 0.0014807 | 3.4435e-05
2013-06-18 | 302080 | MLY1 | RURAL | Other | 4.29 | 28 | 120.12 | 0.00034794 | 1.2427e-05
2013-06-18 | 302081 | TWT12A | RURAL | Other | 5.94 | 112 | 665.28 | 0.0019271 | 1.7206e-05
2013-06-18 | 302082 | PBH8 | URBAN | Equipment failure | 32 | 20 | 640 | 0.00064215 | 3.2108e-05
2013-06-18 | 302083 | KWH2 | RURAL | Animals | 337.74 | 233.7529 | 77073.12 | 0.22325 | 0.00097831
2013-06-18 | 302087 | RIS4 | RURAL | Other | 20 | 166 | 3320 | 0.0096168 | 5.7932e-05
2013-06-18 | 302149 | BBS11 | URBAN | Equipment failure | 76.5 | 252.5 | 19205 | 0.01927 | 7.6757e-05
2013-06-19 | 302096 | PMBWED19 | URBAN | Third party impacts | 6.5 | 10 | 65 | 6.5214e-05 | 6.5214e-06
2013-06-19 | 302097 | BDT1 | RURAL | Operational error | 278 | 41 | 11398 | 0.033018 | 0.00080531
2013-06-19 | 302097 | MTB15A | RURAL | Operational error | 8 | 41 | 328 | 0.00095014 | 2.3174e-05
2013-06-19 | 302099 | BDT1 | RURAL | Other | 25 | 82 | 2050 | 0.0059384 | 7.242e-05
2013-06-19 | 302099 | BDT2 | RURAL | Other | 1 | 82 | 82 | 0.00023754 | 2.8968e-06
2013-06-19 | 302113 | GBN4 | RURAL | Equipment failure | 165 | 93 | 15345 | 0.044451 | 0.00047797
2013-06-19 | 302146 | TTF81 | URBAN | Equipment failure | 13.8 | 351 | 4843.8 | 0.0048597 | 1.3845e-05
2013-06-19 | 302147 | CNB24A | RURAL | Other | 1 | 212 | 212 | 0.00061412 | 2.8968e-06
2013-06-19 | 302148 | SBK9 | URBAN | Equipment failure | 24.585 | 164 | 4031.94 | 0.0040452 | 2.4666e-05
2013-06-19 | 302150 | CLM3 | RURAL | Equipment failure | 4.95 | 64 | 316.8 | 0.0009177 | 1.4339e-05
2013-06-19 | 302153 | TRP2 | RURAL | Equipment failure | 1 | 149 | 149 | 0.00043162 | 2.8968e-06
2013-06-19 | 302195 | TGP8A | URBAN | Equipment failure | 5.6 | 1053 | 5896.8 | 0.0059162 | 5.6184e-06
2013-06-20 | 302154 | CRM13A | URBAN | Third party impacts | 1779 | 73.2857 | 125960 | 0.12637 | 0.0017849
2013-06-20 | 302154 | CRM13B | URBAN | Third party impacts | 24.5 | 64 | 1568 | 0.0015732 | 2.4581e-05
2013-06-20 | 302173 | NBR7A | RURAL | Equipment failure | 17 | 77 | 1309 | 0.0037913 | 4.9238e-05
2013-06-20 | 302174 | DBY9 | URBAN | Equipment failure | 142 | 109 | 15478 | 0.015529 | 0.00014247
2013-06-20 | 302177 | BHD5A | URBAN | Other | 32.34 | 166 | 5368.44 | 0.0053861 | 3.2446e-05
2013-06-20 | 302196 | COR22A | RURAL | Equipment failure | 1 | 175 | 175 | 0.00050686 | 2.8963e-06
2013-06-20 | 302221 | BDA12B | URBAN | Other | 181.5 | 70 | 12705 | 0.012747 | 0.0001821
2013-06-20 | 302222 | RST2A | URBAN | Other | 15.015 | 133 | 1996.995 | 0.0020036 | 1.5064e-05
2013-06-20 | 302297 | BHD35A | RURAL | Other | 28.5 | 135 | 3847.5 | 0.011144 | 8.2546e-05
2013-06-20 | 302307 | SBK10A | RURAL | Equipment failure | 29.37 | 259 | 7606.83 | 0.022032 | 8.5065e-05
2013-06-21 | 302230 | IDY6A | URBAN | Third party impacts | 1061.33 | 312.7 | 431472.5 | 0.43286 | 0.0010647
2013-06-21 | 302231 | TGW3 | RURAL | Equipment failure | 328 | 62.5702 | 34502 | 0.099939 | 0.00095009
2013-06-21 | 302232 | MCW7 | RURAL | Equipment failure | 723 | 57.7059 | 83892.5 | 0.243 | 0.0020942
2013-06-21 | 302253 | KBN15A | URBAN | Equipment failure | 2.7 | 142 | 383.4 | 0.00038463 | 2.7087e-06
2013-06-21 | 302293 | RBY13 | URBAN | Other | 30.82 | 60 | 1849.2 | 0.0018551 | 3.0919e-05
2013-06-21 | 302294 | ZMR7A | URBAN | Animals | 3 | 101 | 303 | 0.00030397 | 3.0096e-06
2013-06-21 | 302295 | AHD10A | URBAN | Other | 118 | 96 | 11328 | 0.011364 | 0.00011838
2013-06-21 | 302296 | BWH7A | RURAL | Other | 1.32 | 153 | 201.96 | 0.000585 | 3.8235e-06
2013-06-21 | 302299 | HPK2 | URBAN | Third party impacts | 11.533 | 109 | 1257.097 | 0.0012611 | 1.157e-05
2013-06-21 | 302302 | MFN12A | RURAL | Equipment failure | 23.875 | 50 | 1193.75 | 0.0034578 | 6.9157e-05
2013-06-21 | 302308 | BHD44A | URBAN | Equipment failure | 31.02 | 87 | 2698.74 | 0.0027074 | 3.112e-05
2013-06-21 | 302310 | RCN3A | URBAN | Equipment failure | 36.63 | 43 | 1575.09 | 0.0015802 | 3.6748e-05
2013-06-21 | 302311 | TMH15A | URBAN | Equipment failure | 24.09 | 76 | 1830.84 | 0.0018367 | 2.4167e-05
2013-06-22 | 302320 | AJV1 | URBAN | Other | 40 | 58 | 2320 | 0.0023273 | 4.0125e-05
2013-06-22 | 302321 | BMT1 | RURAL | Equipment failure | 11 | 136 | 1496 | 0.0043338 | 3.1866e-05
2013-06-22 | 302322 | NBR15A | RURAL | Equipment failure | 15 | 64 | 960 | 0.002781 | 4.3453e-05
2013-06-23 | 302319 | BRD13A | URBAN | Equipment failure | 2592 | 66.8049 | 170258 | 0.17079 | 0.0026001
2013-06-23 | 302323 | COR26A | RURAL | Equipment failure | 6 | 26 | 156 | 0.00045188 | 1.738e-05
2013-06-23 | 302326 | GYM3 | URBAN | Third party impacts | 31 | 210 | 6510 | 0.0065304 | 3.1097e-05
2013-06-23 | 302341 | HPK6 | URBAN | Animals | 734.5 | 27 | 19831.5 | 0.019894 | 0.00073681
2013-06-23 | 302342 | BRD13A | URBAN | Equipment failure | 1.9 | 258 | 490.2 | 0.00049174 | 1.906e-06
2013-06-23 | 302343 | BKD15A | URBAN | Other | 84.48 | 89 | 7518.72 | 0.0075423 | 8.4745e-05
2013-06-23 | 302344 | CPB3 | URBAN | Third party impacts | 11 | 23 | 253 | 0.00025379 | 1.1035e-05
2013-06-23 | 302345 | CMY4 | RURAL | Operational error | 1.815 | 15 | 27.225 | 7.8862e-05 | 5.2574e-06
2013-06-24 | 302378 | CMY4 | RURAL | Other | 85 | 28 | 2380 | 0.0068941 | 0.00024622
2013-06-24 | 302379 | WMD8B | RURAL | Equipment failure | 21 | 193 | 4053 | 0.01174 | 6.083e-05
2013-06-24 | 302380 | COR25A | RURAL | Equipment failure | 7.92 | 145 | 1148.4 | 0.0033265 | 2.2942e-05
2013-06-24 | 302394 | LBH1B | RURAL | Other | 3.63 | 76 | 275.88 | 0.00079913 | 1.0515e-05
2013-06-24 | 302395 | SPO69A | URBAN | Equipment failure | 18.81 | 170 | 3197.7 | 0.0032075 | 1.8868e-05
2013-06-24 | 302396 | SFD2A | URBAN | Equipment failure | 21 | 125 | 2625 | 0.002633 | 2.1064e-05
2013-06-24 | 302398 | WED6A | URBAN | Operational error | 138.5 | 69 | 9556.5 | 0.0095857 | 0.00013892
2013-06-25 | 302401 | MTG13A | URBAN | Third party impacts | 2.9 | 183 | 530.7 | 0.0005323 | 2.9087e-06
2013-06-25 | 302416 | TRP3 | RURAL | Equipment failure | 1 | 70 | 70 | 0.00020277 | 2.8967e-06
2013-06-25 | 302441 | MLY3 | RURAL | Other | 2.5 | 20 | 50 | 0.00014483 | 7.2417e-06
2013-06-25 | 302469 | BHD23A | RURAL | Operational error | 12 | 73 | 876 | 0.0025375 | 3.476e-05
2013-06-25 | 302549 | CVL3A | URBAN | Equipment failure | 45.5 | 105 | 4777.5 | 0.0047919 | 4.5637e-05
2013-06-26 | 302472 | MLY3 | RURAL | Animals | 55 | 120 | 6600 | 0.019118 | 0.00015932
2013-06-26 | 302518 | KCY4 | RURAL | Third party impacts | 16 | 73 | 1168 | 0.0033834 | 4.6348e-05
2013-06-26 | 302545 | TPT5 | RURAL | Third party impacts | 50 | 211 | 10550 | 0.030561 | 0.00014484
2013-06-26 | 302550 | MLB3A | RURAL | Other | 49.5 | 98 | 4851 | 0.014052 | 0.00014339
2013-06-26 | 302551 | RST20A | URBAN | Other | 57.42 | 45 | 2583.9 | 0.0025916 | 5.759e-05
2013-06-26 | 302555 | MGP13A | RURAL | Equipment failure | 79 | 309 | 24411 | 0.070712 | 0.00022884
2013-06-26 | 302606 | MWMRBK8 | URBAN | Equipment failure | 1 | 2566 | 2566 | 0.0025736 | 1.003e-06
2013-06-26 | 302606 | RBK9A | URBAN | Equipment failure | 292 | 2566 | 749272 | 0.75149 | 0.00029286
2013-06-27 | 302579 | PBH1 | URBAN | Equipment failure | 1419 | 22 | 31218 | 0.031309 | 0.0014231
2013-06-27 | 302579 | PBH2B | URBAN | Equipment failure | 2292 | 17 | 38964 | 0.039078 | 0.0022987
2013-06-27 | 302579 | PBH3 | URBAN | Equipment failure | 1114 | 11 | 12254 | 0.01229 | 0.0011172
2013-06-27 | 302579 | PBH4 | URBAN | Equipment failure | 1032.49 | 8 | 8259.92 | 0.008284 | 0.0010355
2013-06-27 | 302579 | PBH5 | RURAL | Equipment failure | 1 | 9 | 9 | 2.6071e-05 | 2.8968e-06
2013-06-27 | 302579 | PBH6 | URBAN | Equipment failure | 2247 | 13 | 29211 | 0.029296 | 0.0022536
2013-06-27 | 302579 | PBH7 | URBAN | Equipment failure | 45.5 | 59 | 2684.5 | 0.0026923 | 4.5633e-05
2013-06-27 | 302579 | PBH8 | URBAN | Equipment failure | 1465 | 71 | 104015 | 0.10432 | 0.0014693
2013-06-27 | 302580 | COR23A | RURAL | Equipment failure | 730.99 | 144.4121 | 77762.21 | 0.22526 | 0.0021175
2013-06-27 | 302581 | WMD2A | URBAN | Other | 98 | 89 | 8722 | 0.0087474 | 9.8286e-05
2013-06-27 | 302586 | NBR4A | RURAL | Equipment failure | 26.5 | 27 | 715.5 | 0.0020726 | 7.6764e-05
2013-06-27 | 302589 | BPN26A | RURAL | Third party impacts | 890 | 80.1282 | 71241 | 0.20637 | 0.0025781
2013-06-27 | 302607 | LTN9 | URBAN | Equipment failure | 6 | 180 | 1080 | 0.0010831 | 6.0175e-06
2013-06-27 | 302613 | BPN26A | RURAL | Third party impacts | 35 | 250 | 8750 | 0.025347 | 0.00010139
2013-06-27 | 302613 | NMC3A | RURAL | Third party impacts | 22 | 250 | 5500 | 0.015932 | 6.3729e-05
2013-06-27 | 302675 | BHD35A | RURAL | Other | 28.5 | 25 | 712.5 | 0.0020639 | 8.2558e-05
2013-06-27 | 302710 | KMR25A | RURAL | Vegetation | 7.92 | 124 | 982.08 | 0.0028448 | 2.2942e-05
2013-06-27 | 302711 | KSN2A | RURAL | Operational error | 99 | 32 | 3168 | 0.0091769 | 0.00028678
2013-06-27 | 302712 | LGL11A | URBAN | Equipment failure | 37.125 | 107 | 3972.375 | 0.003984 | 3.7233e-05
2013-06-27 | 302739 | LDR2B | URBAN | Other | 128 | 23 | 2944 | 0.0029526 | 0.00012837
2013-06-27 | 302914 | MBG4 | RURAL | Other | 9 | 97 | 873 | 0.0025289 | 2.6071e-05
2013-06-28 | 302633 | RCN8A | URBAN | Third party impacts | 87 | 296 | 24311 | 0.024381 | 8.7249e-05
2013-06-28 | 302709 | CFD1A | URBAN | Equipment failure | 56.76 | 100 | 5676 | 0.0056923 | 5.6923e-05
2013-06-28 | 302718 | KLG7A | RURAL | Third party impacts | 35.64 | 115 | 2795.04 | 0.0080967 | 0.00010324
2013-06-28 | 302719 | YTA22A | RURAL | Other | 347 | 56.6842 | 29250 | 0.084732 | 0.0010052
2013-06-28 | 302761 | CPD1 | RURAL | Other | 1.6 | 74.5833 | 119.3333 | 0.00034569 | 4.6349e-06
2013-06-28 | 302762 | PRG2A | RURAL | Other | 2 | 117 | 234 | 0.00067785 | 5.7936e-06
2013-06-29 | 302733 | BRD5A | RURAL | Equipment failure | 58.41 | 17.5 | 1018.38 | 0.002945 | 0.00016891
2013-06-29 | 302734 | CMY1 | RURAL | Equipment failure | 57 | 70 | 3990 | 0.011539 | 0.00016484
2013-06-29 | 302736 | WMD10A | URBAN | Animals | 1255 | 62.4583 | 79430 | 0.079701 | 0.0012593
2013-06-29 | 302912 | GYS3A | RURAL | Other | 0.99 | 70 | 69.3 | 0.00020041 | 2.863e-06
2013-06-29 | 302913 | KWA1A | URBAN | Weather | 22.77 | 61 | 1388.97 | 0.0013937 | 2.2848e-05
2013-06-29 | 302915 | BDL5 | URBAN | Other | 33.33 | 51 | 1699.83 | 0.0017056 | 3.3444e-05
2013-06-29 | 302916 | SPO41A | URBAN | Equipment failure | 102.96 | 70 | 7207.2 | 0.0072318 | 0.00010331
2013-06-30 | 999999 | Single Loss | Urban | Other | 6328 | 293 | 1855355 | 1.8714 | 0.00637
2013-06-30 | 999999 | Single Loss | Rural short | Other | 3209 | 342 | 1098925 | 3.1668 | 0.00926
2013-06-30 | 999999 | Single Loss | CBD | Other | 9 | 87 | 780 | 0.20231 | 0.00234
Table 2: Planned Outages
Date (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Reason for planned outage | Number of customers interrupted | Duration of interruption (Mins) | Total planned customer minutes off supply (Mins) | Planned SAIDI impact | Planned SAIFI impact
2012-07-01 | 275480 | DRA1A | Urban | LV Transformer SP304-P DRA1A - Planned | 14 | 448 | 6272 | 0.0062716 | 1.3999e-05
2012-07-01 | 275481 | TWT3A | Rural short | LV Transformer SP6877-B TWT3A - Planned | 15.01 | 325 | 4878.25 | 0.014554 | 4.4783e-05
2012-07-01 | 275482 | CBT13A | Urban | LV Transformer SC544695 CBT13A - Planned | 8.82 | 147 | 1296.54 | 0.0012965 | 8.8194e-06
2012-07-01 | 275483 | HDA14A | Urban | LV Transformer SC1050542 HDA14A - Planned | 4.9 | 117 | 573.3 | 0.00057326 | 4.8997e-06
2012-07-01 | 275484 | BLBNFM6 | Urban | LV Transformer SP2362-M BLBNFM6 - Planned | 9.165 | 386 | 3537.69 | 0.0035375 | 9.1644e-06
2012-07-01 | 275485 | MRK9 | Urban | LV Transformer SP763418 MRK9 - Planned | 11.44 | 415 | 4747.6 | 0.0047473 | 1.1439e-05
2012-07-01 | 275486 | NIP3A | Urban | LV Transformer SP3762-C NIP3A - Planned | 16.875 | 326 | 5501.25 | 0.0055009 | 1.6874e-05
2012-07-01 | 275487 | SPF17B | Urban | LV Transformer SC1436136 SPF17B - Planned | 25.93 | 77 | 1996.61 | 0.0019965 | 2.5928e-05
2012-07-01 | 275488 | BVL2A | Urban | LV Transformer SP5268-D BVL2A - Planned | 38.76 | 152 | 5891.52 | 0.0058911 | 3.8758e-05
2012-07-01 | 275489 | BSEENG15 | Urban | LV Transformer SC3693-J BSEENG15 - Planned | 1.135 | 623 | 707.105 | 0.00070706 | 1.1349e-06
2012-07-01 | 275491 | KRA1 | Urban | LV Transformer SP11679-D KRA1 - Planned | 43.29 | 236 | 10216.44 | 0.010216 | 4.3287e-05
2012-07-02 | 275521 | BNH1B | Rural short | LV Transformer SP4306-F BNH1B - Planned | 1 | 141 | 141 | 0.00042096 | 2.9855e-06
2012-07-02 | 275522 | CLM8 | Urban | LV Transformer SP5377-A CLM8 - Planned | 64.505 | 310 | 19996.55 | 0.019989 | 6.4482e-05
2012-07-02 | 275523 | RBA41A | Urban | LV Transformer SC21693-E RBA41A - Planned | 70 | 105 | 7350 | 0.0073474 | 6.9975e-05
2012-07-02 | 275527 | GBN4 | Rural short | Feeder GBN4 - Planned | 9.99 | 290 | 2897.1 | 0.0086493 | 2.9825e-05
2012-07-02 | 275528 | MTB2A | Rural short | Feeder MTB2A - Planned | 73.11 | 285 | 20836.35 | 0.062207 | 0.00021827
2012-07-02 | 275540 | CPC2A | Rural short | LV Transformer SC661354 CPC2A - Planned | 7.65 | 58 | 443.7 | 0.0013247 | 2.2839e-05
2012-07-02 | 275541 | CPC2A | Rural short | LV Transformer SC661354 CPC2A - Planned | 10.2 | 30 | 306 | 0.00091356 | 3.0452e-05
2012-07-02 | 275542 | HTN7A | Urban | LV Transformer SP176-L HTN7A - Planned | 22.8 | 300 | 6840 | 0.0068376 | 2.2792e-05
2012-07-02 | 275543 | BRT8 | Urban | LV Transformer SP3216-G BRT8 - Planned | 12.75 | 275 | 3506.25 | 0.003505 | 1.2745e-05
2012-07-02 | 275544 | WRG11A | Urban | LV Transformer SP5981-H WRG15A - Planned | 35.3559 | 251 | 8874.3309 | 0.0088712 | 3.5343e-05
2012-07-02 | 275544 | WRG15A | Urban | LV Transformer SP5981-H WRG15A - Planned | 25.3346 | 251 | 6358.9846 | 0.0063567 | 2.5326e-05
2012-07-02 | 275545 | FDS1 | Rural short | LV Transformer SP17115-C FDS1 - Planned | 1 | 42 | 42 | 0.00012539 | 2.9855e-06
2012-07-02 | 275546 | LRE8A | Rural short | Feeder LRE8A - Planned | 69 | 470 | 32430 | 0.09682 | 0.000206
2012-07-03 | 275660 | NMC1B | Rural short | Feeder NMC1B - Planned | 26 | 310 | 8060 | 0.024079 | 7.7674e-05
2012-07-03 | 275661 | PWC4 | Rural short | LV Transformer SP5211-A PWC4 - Planned | 9 | 247 | 2223 | 0.0066411 | 2.6887e-05
2012-07-03 | 275662 | CLM3 | Rural short | LV Transformer SP1267-A CLM3 - Planned | 8 | 224 | 1792 | 0.0053535 | 2.39e-05
2012-07-03 | 275663 | BMT5 | Rural short | Feeder BMT5 - Planned | 50 | 126 | 6300 | 0.018821 | 0.00014937
2012-07-03 | 275664 | NPD1 | Urban | Feeder NPD1 - Planned | 2 | 450 | 900 | 0.00089942 | 1.9987e-06
2012-07-03 | 275665 | AMR2 | Rural short | Feeder AMR2 - Planned | 136 | 507 | 68952 | 0.20599 | 0.00040629
2012-07-03 | 275666 | SFD2A | Urban | LV Transformer SP3991-J SFD2A - Planned | 1 | 476 | 476 | 0.00047569 | 9.9936e-07
2012-07-03 | 275667 | LLY4 | Rural short | Feeder LLY4 - Planned | 6.2575 | 544 | 3404.08 | 0.01017 | 1.8694e-05
2012-07-03 | 275669 | SFD3 | Urban | LV Transformer SC4996-J SFD3 - Planned | 29.925 | 456 | 13645.8 | 0.013637 | 2.9906e-05
2012-07-03 | 275670 | MLS15A | Urban | LV Transformer SC23150-F MLS15A - Planned | 1.93 | 220 | 424.6 | 0.00042433 | 1.9288e-06
2012-07-03 | 275671 | SHW10A | Urban | LV Transformer SP1340-K SHW10A - Planned | 23.842 | 188 | 4482.296 | 0.0044794 | 2.3827e-05
2012-07-03 | 275672 | TWG19 | Urban | LV Transformer SC3696-H - Planned | 62.42 | 247 | 15417.74 | 0.015408 | 6.238e-05
2012-07-03 | 275673 | NMK17A | Urban | LV Transformer SP6182-F NMK17A - Planned | 2.8988 | 235 | 681.218 | 0.00068078 | 2.8969e-06
2012-07-03 | 275674 | TRG2A | Urban | LV Transformer SG2949-L TRG2A - Planned | 12.2079 | 370 | 4516.923 | 0.004514 | 1.22e-05
2012-07-03 | 275675 | CLM6 | Urban | LV Transformer SP1007-G CLM6 - Planned | 9.03 | 59 | 532.77 | 0.00053243 | 9.0242e-06
2012-07-03 | 275676 | MLB13A | Urban | LV Transformer SC451931-A MLB13A - Planned | 46.44 | 236 | 10959.84 | 0.010953 | 4.641e-05
2012-07-03 | 275677 | CLD22A | Urban | LV Transformer SG225-A CLD22A - Planned | 1.9834 | 55 | 109.087 | 0.00010902 | 1.9821e-06
2012-07-03 | 275678 | WMR3 | Rural short | LV Transformer SP8301-E WMR3 - Planned | 11.04 | 447 | 4934.88 | 0.014743 | 3.2982e-05
2012-07-03 | 275679 | CLD22A | Urban | LV Transformer SC750799 CLD22A - Planned | 3.28 | 60 | 196.8 | 0.00019667 | 3.2779e-06
2012-07-03 | 275681 | CRB25A | Rural short | LV Transformer SP468679 CRB25A - Planned | 20.99 | 170 | 3568.3 | 0.01066 | 6.2707e-05
2012-07-03 | 275682 | MMC33A | Urban | LV Transformer SC242-K MMC33A - Planned | 26.95 | 492 | 13259.4 | 0.013251 | 2.6933e-05
2012-07-03 | 275683 | BHD23A | Rural short | LV Transformer SP5637-E BHD23A - Planned | 10.175 | 270 | 2747.25 | 0.0082073 | 3.0397e-05
2012-07-03 | 275684 | CRB25A | Rural short | LV Transformer SP760487 CRB25A - Planned | 7.565 | 200 | 1513 | 0.00452 | 2.26e-05
2012-07-03 | 275685 | MAI17 | Urban | LV Transformer SP14034-D MAI17 - Planned | 17.4 | 220 | 3828 | 0.0038255 | 1.7389e-05
2012-07-03 | 275686 | RCF3A | Urban | LV Transformer SP4581-D SBH8 - Planned | 9.8 | 268 | 2626.4 | 0.0026247 | 9.7937e-06
2012-07-03 | 275686 | SBH8 | Urban | LV Transformer SP4581-D SBH8 - Planned | 9.87 | 268 | 2645.16 | 0.0026435 | 9.8637e-06
2012-07-03 | 275687 | SFD7A | Urban | LV Transformer SC6463-H SFD7A - Planned | 34.185 | 365 | 12477.525 | 0.01247 | 3.4163e-05
2012-07-03 | 275688 | EMP23A | Urban | LV Transformer SC1679-H EMP23A - Planned | 11.2462 | 365 | 4104.863 | 0.0041022 | 1.1239e-05
2012-07-03 | 275689 | WED6A | Urban | LV Transformer SP493935 WED6A - Planned | 42.6037 | 197 | 8392.9289 | 0.0083875 | 4.2576e-05
2012-07-03 | 275690 | WRG5A | Urban | LV Transformer SP4043-J WRG5A - Planned | 15.8 | 147 | 2322.6 | 0.0023211 | 1.579e-05
2012-07-03 | 275691 | CPB8 | Rural short | LV Transformer SP526659 CPB8 - Planned | 9.3 | 232 | 2157.6 | 0.0064457 | 2.7783e-05
2012-07-03 | 275692 | BLB8B | Urban | LV Transformer SG1144-I BLB8B - Planned | 11 | 206 | 2266 | 0.0022645 | 1.0993e-05
2012-07-03 | 275693 | IPS1B | Urban | LV Transformer SP2506-G IPS1B - Planned | 13.6146 | 340 | 4628.964 | 0.004626 | 1.3606e-05
2012-07-03 | 275694 | PWC3 | Rural short | LV Transformer SP16357-A PWC3 - Planned | 12 | 19 | 456 | 0.0013623 | 3.585e-05
2012-07-03 | 275813 | BMG2A | Urban | LV Transformer SC484063 BMG2A - Planned | 7.3647 | 320 | 2356.704 | 0.0023552 | 7.36e-06
2012-07-04 | 275740 | GYN7A | Rural short | LV Transformer SP5955-C GYN7A - Planned | 0.4 | 15 | 6 | 1.7937e-05 | 1.1958e-06
2012-07-04 | 275741 | HDN1 | Rural short | LV Transformer SP5935-B HDN1 - Planned | 1 | 27 | 27 | 8.0714e-05 | 2.9894e-06
2012-07-04 | 275760 | EMD3 | Rural short | LV Transformer SP5325-C EMD3 - Planned | 0.4 | 203 | 81.2 | 0.00024274 | 1.1958e-06
2012-07-04 | 275800 | TGW3 | Rural short | Feeder TGW3 - Planned | 38.91 | 428 | 16653.48 | 0.049784 | 0.00011632
2012-07-04 | 275801 | WMR3 | Rural short | Feeder WMR3 - Planned | 9.5 | 392 | 3724 | 0.011133 | 2.84e-05
2012-07-04 | 275802 | AHD18B | Rural short | LV Transformer SP1657-A AHD18B - Planned | 10 | 382 | 3820 | 0.01142 | 2.9894e-05
2012-07-04 | 275803 | LTN6 | Urban | LV Transformer SP2231-F LTN6 - Planned | 5.7 | 370 | 2109 | 0.002107 | 5.6947e-06
2012-07-04 | 275804 | MTB2A | Rural short | Feeder MTB2A - Planned | 11.91 | 404 | 4811.64 | 0.014384 | 3.5604e-05
2012-07-04 | 275805 | BWH12A | Rural short | Feeder BWH12A - Planned | 48.5 | 328 | 15908 | 0.047556 | 0.00014499
2012-07-04 | 275806 | TCB3 | Rural short | Feeder TCB3 - Planned | 136.5 | 383 | 52279.5 | 0.15629 | 0.00040806
2012-07-04 | 275807 | RPN4A | Rural short | Feeder RPN4A - Planned | 7 | 442 | 3094 | 0.0092493 | 2.0926e-05
2012-07-04 | 275808 | MGP4 | Rural short | LV Transformer SC764535 MGP4 - Planned | 0.99 | 90 | 89.1 | 0.00026636 | 2.9595e-06
2012-07-04 | 275809 | PWC3 | Rural short | LV Transformer SP16357-A PWC3 - Planned | 12 | 3.5 | 84 | 0.00025111 | 3.5873e-05
2012-07-04 | 275810 | GBN3 | Rural short | LV Transformer SP15474-B GBN3 - Planned | 1 | 501 | 501 | 0.0014977 | 2.9894e-06
2012-07-04 | 275811 | CMV13 | Urban | LV Transformer SC6650-J CMV13 - Planned | 1.6966 | 136 | 230.7376 | 0.00023052 | 1.695e-06
2012-07-04 | 275812 | SFD4 | Urban | LV Transformer SC3533-J SFD4 - Planned | 16.147 | 330 | 5328.51 | 0.0053235 | 1.6132e-05
2012-07-04 | 275814 | GLY1 | Urban | LV Transformer SP563-S GLY1 - Planned | 0.94 | 200 | 188 | 0.00018782 | 9.3912e-07
2012-07-04 | 275816 | TRG2A | Urban | LV Transformer SG2949-L TRG2A - Planned | 13.9133 | 313 | 4354.8629 | 0.0043508 | 1.39e-05
2012-07-04 | 275817 | AHD18B | Rural short | LV Transformer SP2696-A AHD18B - Planned | 13.11 | 356 | 4667.16 | 0.013952 | 3.9191e-05
2012-07-04 | 275818 | CLM9 | Urban | LV Transformer SP16355-A CLM9 - Planned | 11.71 | 274 | 3208.54 | 0.0032055 | 1.1699e-05
2012-07-04 | 275819 | RBA35A | Rural short | LV Transformer SP4170-G RBA35A - Planned | 30.08 | 456 | 13716.48 | 0.041004 | 8.9922e-05
2012-07-04 | 275820 | BBH8A | Urban | LV Transformer SP1229-F BBH8A - Planned | 49.28 | 458 | 22570.24 | 0.022549 | 4.9234e-05
2012-07-04 | 275821 | PBH1 | Urban | LV Transformer SP5765-F PBH1 - Planned | 23.5 | 320 | 7520 | 0.007513 | 2.3478e-05
2012-07-04 | 275822 | MAI13 | Urban | LV Transformer SC504-H MAI13 - Planned | 35 | 290 | 10150 | 0.010141 | 3.4967e-05
2012-07-04 | 275823 | NDH9 | Urban | LV Transformer SP7742 NDH9 - Planned | 9.1647 | 109 | 998.9523 | 0.00099802 | 9.1561e-06
2012-07-04 | 275824 | SFD7A | Urban | LV Transformer SC6463-H SFD7A - Planned | 4.77 | 390 | 1860.3 | 0.0018586 | 4.7655e-06
2012-07-04 | 275825 | WRG11A | Urban | LV Transformer SP2663-L WRG11A - Planned | 22.325 | 190 | 4241.75 | 0.0042378 | 2.2304e-05
2012-07-04 | 275826 | BLB4A | Urban | LV Transformer SG1144-I BLB8B - Planned | 2.01 | 213 | 428.13 | 0.00042773 | 2.0081e-06
2012-07-04 | 275826 | BLB8B | Urban | LV Transformer SG1144-I BLB8B - Planned | 29.15 | 213 | 6208.95 | 0.0062032 | 2.9123e-05
2012-07-04 | 275827 | BLBNFM6 | Urban | LV Transformer SP1749-I BLBNFM6 - Planned | 9.84 | 28 | 275.52 | 0.00027526 | 9.8308e-06
2012-07-04 | 275828 | BLB2A | Urban | LV Transformer SC1368625 BLB2A - Planned | 4.34 | 19 | 82.46 | 8.2383e-05 | 4.3359e-06
2012-07-04 | 275829 | CHL4 | Urban | LV Transformer SP545-M CHL4 - Planned | 3.675 | 357 | 1311.975 | 0.0013107 | 3.6716e-06
2012-07-04 | 275829 | CHL7 | Urban | LV Transformer SP545-M CHL4 - Planned | 3.225 | 357 | 1151.325 | 0.0011502 | 3.222e-06
2012-07-04 | 275829 | QPT25B | Urban | LV Transformer SP545-M CHL4 - Planned | 2.88 | 357 | 1028.16 | 0.0010272 | 2.8773e-06
2012-07-04 | 275830 | BLB2A | Urban | LV Transformer SC1368625 BLB2A - Planned | 4.34 | 37 | 160.58 | 0.00016043 | 4.3359e-06
2012-07-04 | 275831 | CPB8 | Rural short | LV Transformer SP494076 CPB8 - Planned | 18.07 | 317 | 5728.19 | 0.017124 | 5.4019e-05
2012-07-05 | 275860 | RCN4A | Urban | LV Transformer SC1437567 RCN4A - Planned | 48 | 81 | 3888 | 0.0038845 | 4.7957e-05
2012-07-05 | 275865 | WFD5A | Rural short | Feeder WFD5A - Planned | 32 | 292 | 9344 | 0.027925 | 9.5633e-05
2012-07-05 | 275866 | BKD5B | Rural short | LV Transformer SC741562 BKD5B - Planned | 2 | 385 | 770 | 0.0023012 | 5.9771e-06
2012-07-05 | 275867 | BMT2 | Rural short | Feeder BMT2 - Planned | 43 | 314 | 13502 | 0.040351 | 0.00012851
2012-07-05 | 275868 | BMT1 | Rural short | LV Transformer SP6271-A BMT1 - Planned | 3 | 323 | 969 | 0.0028959 | 8.9656e-06
2012-07-05 | 275869 | GGR4 | Rural short | LV Transformer SP15020-B GGR4 - Planned | 38 | 356 | 13528 | 0.040429 | 0.00011356
2012-07-05 | 275870 | GBN4 | Rural short | Feeder GBN4 - Planned | 63.66 | 370 | 23554.2 | 0.070392 | 0.00019025
2012-07-05 | 275872 | NBR6 | Rural short | Feeder NBR6 - Planned | 264.5 | 80 | 21160 | 0.063237 | 0.00079047
2012-07-05 | 275873 | RBA1A | Urban | Feeder RBA1A - Planned | 1 | 490 | 490 | 0.00048956 | 9.9909e-07
2012-07-05 | 275874 | IDY6A | Urban | LV Transformer SP50449-C IDY6A - Planned | 3.7551 | 365 | 1370.6115 | 0.0013694 | 3.7517e-06
2012-07-05 | 275875 | NSD8A | Urban | LV Transformer SP2271-M NSD8A - Planned | 11.58 | 368 | 4261.44 | 0.0042576 | 1.157e-05
2012-07-05 | 275876 | MLT19A | Urban | LV Transformer SC2000-L MLT19A - Planned | 1.4075 | 94 | 132.305 | 0.00013219 | 1.4062e-06
2012-07-05 | 275877 | CLD25A | Urban | LV Transformer SP2105-B CLD25A - Planned | 38.7885 | 437 | 16950.5745 | 0.016935 | 3.8753e-05
2012-07-05 | 275878 | BHD35A | Rural short | LV Transformer SP5796-E BHD35A - Planned | 18 | 59 | 1062 | 0.0031738 | 5.3794e-05
2012-07-05 | 275879 | MTB13A | Rural short | LV Transformer SP1907-D MTB13A - Planned | 7.12 | 345 | 2456.4 | 0.007341 | 2.1278e-05
2012-07-05 | 275880 | BHL1A | Urban | LV Transformer SC786807 BHL1A - Planned | 16.5068 | 65 | 1072.942 | 0.001072 | 1.6492e-05
2012-07-05 | 275881 | WNM3 | Urban | LV Transformer SP3267-J WNM3 - Planned | 9.52 | 344 | 3274.88 | 0.0032719 | 9.5114e-06
2012-07-05 | 275882 | NDH7 | Urban | LV Transformer SC768975 NDH7 - Planned | 12.475 | 378 | 4715.55 | 0.0047113 | 1.2464e-05
2012-07-05 | 275883 | SBH11 | Urban | LV Transformer SP9115-F SBH11 - Planned | 2.135 | 345 | 736.575 | 0.00073591 | 2.1331e-06
2012-07-05 | 275884 | DRD5A | Urban | LV Transformer SP9268-D DRD15B - Planned | 1.29 | 100 | 129 | 0.00012888 | 1.2888e-06
2012-07-05 | 275885 | HTN24A | Urban | LV Transformer SP3185-I HTN24A - Planned | 2.025 | 147 | 297.675 | 0.00029741 | 2.0232e-06
2012-07-05 | 275887 | YTA23B | Urban | LV Transformer SC739635 YTA23B - Planned | 5.96 | 61 | 363.56 | 0.00036323 | 5.9546e-06
2012-07-05 | 275888 | BLB4A | Urban | LV Transformer SP17984-F BLB4A - Planned | 27.14 | 433 | 11751.62 | 0.011741 | 2.7115e-05
2012-07-05 | 275889 | SBK10A | Urban | LV Transformer SC5197-J SBK10A - Planned | 16.17 | 127 | 2053.59 | 0.0020517 | 1.6155e-05
2012-07-05 | 275890 | HPK8A | Urban | LV Transformer SP24074-F HPK8A - Planned | 8.3226 | 295 | 2455.167 | 0.0024529 | 8.3151e-06
2012-07-05 | 275891 | WED6A | Urban | LV Transformer SP136-N WED6A - Planned | 3.5734 | 271 | 968.3914 | 0.00096751 | 3.5702e-06
2012-07-05 | 275892 | TGW1 | Rural short | LV Transformer SP4767-A TGW1 - Planned | 5.325 | 68 | 362.1 | 0.0010821 | 1.5914e-05
2012-07-05 | 275895 | NDH1 | Urban | LV Transformer SC6150-E NDH9 - Planned | 51.8226 | 195 | 10105.407 | 0.010096 | 5.1776e-05
2012-07-05 | 275895 | NDH5A | Urban | LV Transformer SC6150-E NDH9 - Planned | 1.74 | 195 | 339.3 | 0.00033899 | 1.7384e-06
2012-07-05 | 275896 | CPL23A | Rural short | Feeder CPL23A - Planned | 31.43 | 431 | 13546.33 | 0.040484 | 9.3929e-05
2012-07-06 | 275905 | MGP4 | Rural short | Feeder MGP4 - Planned | 14 | 186 | 2604 | 0.0077798 | 4.1827e-05
2012-07-06 | 275920 | IPL2 | Rural short | LV Transformer SP3932-D IPL2 - Planned | 1 | 285 | 285 | 0.00085147 | 2.9876e-06
2012-07-06 | 275921 | TGW3 | Rural short | LV Transformer SP3332-B TGW3 - Planned | 1 | 316 | 316 | 0.00094409 | 2.9876e-06
2012-07-06 | 275922 | CRB25A | Rural short | LV Transformer SP1988-F CRB25A - Planned | 16.5 | 230 | 3795 | 0.011338 | 4.9296e-05
2012-07-06 | 275925 | TRP2 | Rural short | LV Transformer SP3224-C TRP2 - Planned | 1 | 421 | 421 | 0.0012578 | 2.9876e-06
2012-07-06 | 275927 | GYN6A | Rural short | LV Transformer SP7505-C GYN6A - Planned | 18.05 | 375 | 6768.75 | 0.020222 | 5.3927e-05
2012-07-06 | 275928 | CRY6A | Rural short | Feeder CRY6A - Planned | 13.03 | 382 | 4977.46 | 0.014871 | 3.8929e-05
2012-07-06 | 275930 | IDY6A | Urban | LV Transformer SC751748 IDY6A - Planned | 15.96 | 154 | 2457.84 | 0.0024557 | 1.5946e-05
2012-07-06 | 275931 | BDT3 | Rural short | LV Transformer SC1511235 JBB1B - Planned | 6.41 | 81 | 519.21 | 0.0015512 | 1.9151e-05
2012-07-06 | 275932 | RCN4A | Urban | LV Transformer SC91-V RCN4A - Planned | 8.505 | 180 | 1530.9 | 0.0015296 | 8.4975e-06
2012-07-06 | 275933 | MLT2B | Urban | LV Transformer SC801452 MLT2B - Planned | 36.894 | 339 | 12507.066 | 0.012496 | 3.6862e-05
2012-07-06 | 275934 | CLD17A | Urban | LV Transformer SP4571-A CLD17A - Planned | 26.04 | 250 | 6510 | 0.0065043 | 2.6017e-05
2012-07-06 | 275935 | AHD8 | Urban | LV Transformer SP7722-A AHD8 - Planned | 2.84 | 171 | 485.64 | 0.00048521 | 2.8375e-06
2012-07-06 | 275936 | CLM6 | Urban | LV Transformer SP2301-B CLM6 - Planned | 18.5 | 330 | 6105 | 0.0060996 | 1.8484e-05
2012-07-06 | 275937 | TWT12A | Rural short | LV Transformer SP9295-A TWT12A - Planned | 13.485 | 110 | 1483.35 | 0.0044317 | 4.0288e-05
2012-07-06 | 275938 | BBH16A | Urban | LV Transformer SP2294-F BBH16A - Planned | 38.7192 | 178 | 6892.0176 | 0.006886 | 3.8685e-05
2012-07-06 | 275939 | MMC19B | Urban | LV Transformer SC546-I MMC19B - Planned | 24.51 | 448 | 10980.48 | 0.010971 | 2.4489e-05
2012-07-06 | 275940 | BBH8A | Urban | LV Transformer SP5183-H BBH8A - Planned | 5.76 | 175 | 1008 | 0.0010071 | 5.755e-06
2012-07-06 | 275941 | YTA22A | Rural short | LV Transformer SC1381111 YTA22A - Planned | 25.5628 | 27 | 690.1956 | 0.002062 | 7.6372e-05
2012-07-06 | 275942 | BLH12B | Urban | LV Transformer SP5509-D BLH12B - Planned | 16.1165 | 232 | 3739.028 | 0.0037358 | 1.6102e-05
2012-07-06 | 275943 | NGE4B | Urban | LV Transformer SC4875-H NGE4B - Planned | 6.16 | 270 | 1663.2 | 0.0016617 | 6.1546e-06
2012-07-06 | 275944 | CFD1A | Urban | LV Transformer SC485029 CFD1A - Planned | 22.41 | 185 | 4145.85 | 0.0041422 | 2.239e-05
2012-07-06 | 275946 | SGT4 | Urban | LV Transformer SP50102-J SGT4 - Planned | 5.6348 | 80 | 450.784 | 0.00045039 | 5.6299e-06
2012-07-06 | 275947 | BRT5 | Urban | LV Transformer SP18671-F BRT5 - Planned | 0.715 | 150 | 107.25 | 0.00010716 | 7.1437e-07
2012-07-06 | 275948 | SPE7 | Urban | LV Transformer SP3160-C SPE7 - Planned | 17.175 | 383 | 6578.025 | 0.0065723 | 1.716e-05
2012-07-06 | 275949 | BBS9 | Urban | LV Transformer SC3900-F BBS9 - Planned | 30.249 | 333 | 10072.917 | 0.010064 | 3.0222e-05
2012-07-06 | 275950 | BLB8B | Urban | LV Transformer SG1144-I BLB8B - Planned | 11 | 70 | 770 | 0.00076933 | 1.099e-05
2012-07-06 | 275951 | UMG12A | Urban | LV Transformer SC6310-G UMG12A - Planned | 10.6063 | 354 | 3754.6302 | 0.0037513 | 1.0597e-05
2012-07-06 | 275952 | GBP6 | Urban | LV Transformer SP4319-H GBP6 - Planned | 7.14 | 273 | 1949.22 | 0.0019475 | 7.1337e-06
2012-07-06 | 275953 | BDA5A | Urban | LV Transformer SP55171-C BDA5A - Planned | 7.9875 | 85 | 678.9375 | 0.00067834 | 7.9805e-06
2012-07-06 | 275954 | THL3 | Rural short | LV Transformer SP8403-B THL3 - Planned | 6.05 | 315 | 1905.75 | 0.0056937 | 1.8075e-05
2012-07-06 | 275955 | FDS3 | Rural short | LV Transformer SP3370-B FDS3 - Planned | 6.06 | 207 | 1254.42 | 0.0037477 | 1.8105e-05
2012-07-06 | 275988 | MLB3A | Rural short | Feeder MLB3A - Planned | 1 | 417 | 417 | 0.0012458 | 2.9876e-06
2012-07-06 | 275989 | LBS12A | Urban | LV Transformer SG7220-F LBS12A - Planned | 2.5 | 2463 | 6157.5 | 0.0061521 | 2.4978e-06
2012-07-07 | 275981 | WCL19A | Rural short | LV Transformer SG486-L WCL19A - Planned | 0.33 | 200 | 66 | 0.00019712 | 9.8562e-07
2012-07-07 | 275982 | VPK9A | Urban | LV Transformer SP522158 VPK9A - Planned | 1.05 | 289 | 303.45 | 0.00030319 | 1.0491e-06
2012-07-07 | 275985 | TMH5A | Urban | LV Transformer SP6528-D TMH5A - Planned | 3.3 | 364 | 1201.2 | 0.0012002 | 3.2972e-06
2012-07-07 | 275986 | MTG11A | Urban | LV Transformer SC3584-J MTG11A - Planned | 8 | 386 | 3088 | 0.0030854 | 7.9932e-06
2012-07-07 | 275987 | CPR6 | Urban | LV Transformer SC3355-E CPR6 - Planned | 0.88 | 400 | 352 | 0.0003517 | 8.7925e-07
2012-07-08 | 275991 | MDR31A | Urban | Feeder MDR31A - Planned | 10.17 | 342 | 3478.14 | 0.0034755 | 1.0162e-05
2012-07-08 | 275992 | YTA3A | Urban | Feeder YTA3A - Planned | 21 | 424 | 8904 | 0.0088973 | 2.0984e-05
2012-07-08 | 275993 | KSN7 | Rural short | LV Transformer SP5069-C KSN7 - Planned | 21.42 | 6 | 128.52 | 0.00038366 | 6.3943e-05
2012-07-08 | 275994 | BGY13A | Urban | LV Transformer SP3674-D BGY13A - Planned | 8.45 | 265 | 2239.25 | 0.0022376 | 8.4437e-06
2012-07-08 | 275995 | AHD15B | Urban | LV Transformer SP18212-A AHD15B - Planned | 2.925 | 221 | 646.425 | 0.00064594 | 2.9228e-06
2012-07-08 | 275996 | GBG6A | Urban | LV Transformer SC6343-D GBG6A - Planned | 12.47 | 571 | 7120.37 | 0.007115 | 1.2461e-05
2012-07-08 | 275999 | KLG17A | Urban | LV Transformer SP4995-F KLG17A - Planned | 4.9375 | 331 | 1634.3125 | 0.0016331 | 4.9338e-06
2012-07-09 | 276043 | MBG2 | Rural short | LV Transformer SP2740-F MBG2 - Planned | 12.92 | 270 | 3488.4 | 0.010407 | 3.8544e-05
2012-07-09 | 276047 | GVN13A | Urban | LV Transformer SP5267-G GVN13A - Planned | 44.33 | 418 | 18529.94 | 0.018519 | 4.4304e-05
2012-07-09 | 276049 | KSN5 | Urban | LV Transformer SP808548 KSN5 - Planned | 7.15 | 281 | 2009.15 | 0.002008 | 7.1458e-06
2012-07-09 | 276050 | NBR5 | Rural short | LV Transformer SP5187-A NBR5 - Planned | 32.2952 | 374 | 12078.4048 | 0.036034 | 9.6346e-05
2012-07-09 | 276051 | TWT12A | Rural short | LV Transformer SP3911-B TWT12A - Planned | 24 | 159 | 3816 | 0.011384 | 7.1599e-05
2012-07-09 | 276052 | BHD32B | Urban | LV Transformer SC759-G BHD32B - Planned | 2.535 | 278 | 704.73 | 0.00070431 | 2.5335e-06
2012-07-09 | 276053 | PBH3 | Urban | LV Transformer SP1136-M PBH3 - Planned | 24.115 | 224 | 5401.76 | 0.0053986 | 2.4101e-05
2012-07-09 | 276054 | BHD35A | Rural short | LV Transformer SP610-I BHD35A - Planned | 57.5 | 86 | 4945 | 0.014752 | 0.00017154
2012-07-09 | 276055 | BRT6 | Urban | LV Transformer SP2240-I BRT6 - Planned | 11.16 | 208 | 2321.28 | 0.0023199 | 1.1153e-05
2012-07-09 | 276056 | NRA5A | Rural short | LV Transformer SC2554-F NRA5A - Planned | 6.1 | 45 | 274.5 | 0.00081892 | 1.8198e-05
2012-07-09 | 276057 | LTN4 | Urban | LV Transformer SP1924-G LTN5 - Planned | 9.24 | 330 | 3049.2 | 0.0030474 | 9.2345e-06
2012-07-09 | 276057 | LTN5 | Urban | LV Transformer SP1924-G LTN5 - Planned | 10.66 | 330 | 3517.8 | 0.0035157 | 1.0654e-05
2012-07-09 | 276058 | CPL23A | Rural short | LV Transformer SP2300-F CPL23A - Planned | 33.28 | 116 | 3860.48 | 0.011517 | 9.9284e-05
2012-07-09 | 276059 | OXL8B | Urban | LV Transformer SP949-M OXL8B - Planned | 9.0396 | 382 | 3453.1272 | 0.0034511 | 9.0343e-06
2012-07-09 | 276060 | HPK8A | Urban | LV Transformer SP492472 HPK8A - Planned | 21.5605 | 145 | 3126.2725 | 0.0031244 | 2.1548e-05
2012-07-09 | 276061 | CHL2 | Urban | LV Transformer SP641-K CHL8 - Planned | 16.81 | 375 | 6303.75 | 0.0063 | 1.68e-05
2012-07-09 | 276061 | CHL8 | Urban | LV Transformer SP641-K CHL8 - Planned | 3.955 | 375 | 1483.125 | 0.0014822 | 3.9527e-06
2012-07-09 | 276062 | SPF15A | Urban | LV Transformer SC1412451 SPF15A - Planned | 2.4 | 224 | 537.6 | 0.00053728 | 2.3986e-06
2012-07-09 | 276063 | SPF12B | Urban | LV Transformer SC1412605 STC7 - Planned | 3.4899 | 80 | 279.192 | 0.00027903 | 3.4878e-06
2012-07-09 | 276063 | STC7 | Urban | LV Transformer SC1412605 STC7 - Planned | 6.575 | 80 | 526 | 0.00052569 | 6.5711e-06
2012-07-09 | 276064 | SPF12B | Urban | LV Transformer SC1413061 - Planned | 18.6128 | 135 | 2512.728 | 0.0025112 | 1.8602e-05
2012-07-09 | 276066 | TWT12A | Rural short | Feeder TWT12A - Planned | 17.5 | 325 | 5687.5 | 0.016968 | 5.2208e-05
2012-07-09 | 276067 | GBN4 | Rural short | LV Transformer SP1512-C GBN4 - Planned | 5 | 330 | 1650 | 0.0049225 | 1.4917e-05
2012-07-09 | 276068 | WMD4A | Rural short | Feeder WMD4A - Planned | 5 | 75 | 375 | 0.0011187 | 1.4917e-05
2012-07-09 | 276340 | CCY1B | Urban | Feeder CCY1B - Planned | 126.93 | 628 | 79712.04 | 0.079665 | 0.00012685
2012-07-10 | 276070 | RBA42A | Rural short | LV Transformer SC2287-H RBA42A - Planned | 1.5 | 61 | 91.5 | 0.0002728 | 4.4721e-06
2012-07-10 | 276080 | MCN3 | Urban | LV Transformer SP4364-D MCN3 - Planned | 2.01 | 179 | 359.79 | 0.00035963 | 2.0091e-06
2012-07-10 | 276081 | BTN2 | Rural short | LV Transformer SP418-F BTN2 - Planned | 2.01 | 170 | 341.7 | 0.0010187 | 5.9926e-06
2012-07-10 | 276082 | AMR2 | Rural short | LV Transformer SP64-D AMR2 - Planned | 1 | 77 | 77 | 0.00022957 | 2.9814e-06
2012-07-10 | 276083 | NRG9 | Rural short | Feeder NRG9 - Planned | 232.9284 | 181 | 42160.0404 | 0.1257 | 0.00069445
2012-07-10 | 276086 | GVN16A | Rural short | LV Transformer SP4568-F GVN16A - Planned | 39.06 | 247 | 9647.82 | 0.028764 | 0.00011645
2012-07-10 | 276087 | LTN8 | Rural short | Feeder LTN8 - Planned | 73.98 | 295 | 21824.1 | 0.065066 | 0.00022056
2012-07-10 | 276089 | RWD1 | Rural short | Feeder RWD1 - Planned | 21.02 | 384 | 8071.68 | 0.024065 | 6.2669e-05
2012-07-10 | 276090 | EMP21A | Rural short | LV Transformer SP3158-L EMP21A - Planned | 10 | 286 | 2860 | 0.0085268 | 2.9814e-05
2012-07-10 | 276092 | CRY2A | Rural short | Feeder CRY2A - Planned | 1.4 | 330 | 462 | 0.0013774 | 4.174e-06
2012-07-10 | 276095 | TWG11 | Urban | LV Transformer SC6280-E TWG11 - Planned | 1.845 | 103 | 190.035 | 0.00018995 | 1.8442e-06
2012-07-10 | 276096 | SHW12 | Urban | LV Transformer SC2116-M SHW12 - Planned | 38.76 | 137 | 5310.12 | 0.0053078 | 3.8743e-05
2012-07-10 | 276097 | TWT11A | Rural short | LV Transformer SP6401-B TWT11A - Planned | 3.2 | 72 | 230.4 | 0.00068692 | 9.5405e-06
2012-07-10 | 276098 | CRBTHP14 | Urban | LV Transformer SP4149-H CRBTHP14 - Planned | 155.43 | 435 | 67612.05 | 0.067583 | 0.00015536
2012-07-10 | 276099 | LTA2 | Urban | LV Transformer SP1787-L LTA2 - Planned | 30.91 | 346 | 10694.86 | 0.01069 | 3.0897e-05
2012-07-10 | 276100 | SGT7 | Urban | LV Transformer SP3766-D SGT7 - Planned | 9.9 | 350 | 3465 | 0.0034635 | 9.8957e-06
2012-07-10 | 276101 | BRT8 | Urban | LV Transformer SP228-M BRT8 - Planned | 3.28 | 122 | 400.16 | 0.00039999 | 3.2786e-06
2012-07-10 | 276102 | SBH13A | Urban | LV Transformer SP5750-B SBH13A - Planned | 5.995 | 240 | 1438.8 | 0.0014382 | 5.9924e-06
2012-07-10 | 276103 | SMF5A | Rural short | LV Transformer SP8142-J SMF5A - Planned | 1 | 430 | 430 | 0.001282 | 2.9814e-06
2012-07-10 | 276104 | HPE16A | Urban | LV Transformer SC4059-H HPE16A - Planned | 60.1315 | 445 | 26758.5175 | 0.026747 | 6.0105e-05
2012-07-10 | 276105 | RBY6 | Urban | LV Transformer SP2348-D RBY6 - Planned | 1.25 | 233 | 291.25 | 0.00029112 | 1.2495e-06
2012-07-10 | 276106 | INA7A | Rural short | LV Transformer SP1265-K INA7A - Planned | 16.94 | 359 | 6081.46 | 0.018131 | 5.0505e-05
2012-07-10 | 276107 | RCN3A | Urban | LV Transformer SC3992-I RCN3A - Planned | 22.4998 | 277 | 6232.4446 | 0.0062297 | 2.249e-05
2012-07-10 | 276108 | WED6A | Urban | LV Transformer SP136-N WED6A - Planned | 12.5069 | 226 | 2826.5594 | 0.0028253 | 1.2501e-05
2012-07-10 | 276109 | RBY13 | Urban | LV Transformer SP231763-A RBY13 - Planned | 8.3208 | 218 | 1813.9344 | 0.0018131 | 8.3172e-06
2012-07-10 | 276110 | CPK10 | Urban | LV Transformer SP3417-B CPK10 - Planned | 2.91 | 365 | 1062.15 | 0.0010617 | 2.9087e-06
2012-07-10 | 276111 | BVL5A | Urban | LV Transformer SP3845-D BVL5A - Planned | 19.72 | 242 | 4772.24 | 0.0047702 | 1.9711e-05
2012-07-10 | 276112 | SPF12B | Urban | LV Transformer SC1413061 - Planned | 17.0633 | 145 | 2474.1785 | 0.0024731 | 1.7056e-05
2012-07-10 | 276113 | LLY1 | Rural short | LV Transformer SP4659-B LLY1 - Planned | 1 | 193 | 193 | 0.00057541 | 2.9814e-06
2012-07-10 | 276114 | SPF12B | Urban | LV Transformer SC1413108 SPF12B - Planned | 9.4367 | 77 | 726.6259 | 0.00072631 | 9.4326e-06
2012-07-10 | 276115 | MHL13A | Urban | LV Transformer SC1297467 - Planned | 13.22 | 460 | 6081.2 | 0.0060786 | 1.3214e-05
2012-07-10 | 276116 | LLY1 | Rural short | Feeder LLY1 - Planned | 54.5 | 690 | 37605 | 0.11212 | 0.00016249
2012-07-10 | 276118 | NDH9 | Urban | LV Transformer SC484375 NDH9 - Planned | 2.5921 | 90 | 233.289 | 0.00023319 | 2.591e-06
2012-07-11 | 276123 | RBY6 | Urban | LV Transformer SP2348-D RBY6 - Planned | 5 | 233 | 1165 | 0.0011646 | 4.9983e-06
2012-07-11 | 276124 | RCN2A | Urban | LV Transformer SC1428477 RCN2A - Planned | 18.91 | 116 | 2193.56 | 0.0021928 | 1.8904e-05
2012-07-11 | 276125 | MLY3 | Rural short | LV Transformer SC1451921 MLY3 - Planned | 83.5 | 182 | 15197 | 0.045288 | 0.00024883
2012-07-11 | 276127 | LTN3 | Urban | LV Transformer SC399-F LTN3 - Planned | 53.9 | 410 | 22099 | 0.022091 | 5.3882e-05
2012-07-11 | 276128 | TRP3 | Rural short | Feeder TRP3 - Planned | 32.895 | 419 | 13783.005 | 0.041074 | 9.8029e-05
2012-07-11 | 276141 | TGW2 | Rural short | Feeder TGW2, TGW3 - Planned | 26.785 | 330 | 8839.05 | 0.026341 | 7.9821e-05
2012-07-11 | 276141 | TGW3 | Rural short | Feeder TGW2, TGW3 - Planned | 7.01 | 330 | 2313.3 | 0.0068937 | 2.089e-05
2012-07-11 | 276142 | MTB17A | Rural short | LV Transformer SP6466-F MTB17A - Planned | 1 | 530 | 530 | 0.0015794 | 2.98e-06
2012-07-11 | 276144 | MGL2A | Rural short | LV Transformer SC3746-J MGL2A - Planned | 45.14 | 147 | 6635.58 | 0.019774 | 0.00013452
2012-07-11 | 276145 | CBT7A | Urban | LV Transformer SP3551-F CBT7A - Planned | 4.6749 | 258 | 1206.1242 | 0.0012057 | 4.6733e-06
2012-07-11 | 276146 | KWH2 | Rural short | Feeder KWH2 - Planned | 17.965 | 322 | 5784.73 | 0.017239 | 5.3537e-05
2012-07-11 | 276147 | CLM9 | Urban | Feeder CLM9 - Planned | 79.5 | 383 | 30448.5 | 0.030438 | 7.9473e-05
2012-07-11 | 276148 | CLD17A | Urban | LV Transformer SP1288-B CLD17A - Planned | 70.7101 | 456 | 32243.8056 | 0.032233 | 7.0686e-05
2012-07-11 | 276149 | BMT2 | Rural short | LV Transformer SP11567-B BMT2 - Planned | 14.1 | 191 | 2693.1 | 0.0080256 | 4.2019e-05
2012-07-11 | 276150 | NBR5 | Rural short | LV Transformer SP2692-A NBR5 - Planned | 4.235 | 364 | 1541.54 | 0.0045939 | 1.2621e-05
2012-07-11 | 276151 | SPO5A | Urban | LV Transformer SC1083599 SPO5A - Planned | 1.0325 | 34 | 35.105 | 3.5093e-05 | 1.0321e-06
2012-07-11 | 276153 | HPK8A | Urban | LV Transformer SP1568-H HPK8A - Planned | 6.54 | 325 | 2125.5 | 0.0021248 | 6.5378e-06
2012-07-11 | 276154 | BKD5B | Rural short | LV Transformer SP10518-B BKD5B - Planned | 32.98 | 161 | 5309.78 | 0.015823 | 9.8282e-05
2012-07-11 | 276155 | WED6A | Urban | LV Transformer SP493935 WED6A - Planned | 25.1734 | 270 | 6796.818 | 0.0067945 | 2.5165e-05
2012-07-11 | 276156 | CHL4 | Urban | LV Transformer SG1311-K CHL7 - Planned | 4.9 | 339 | 1661.1 | 0.0016605 | 4.8983e-06
2012-07-11 | 276156 | CHL7 | Urban | LV Transformer SG1311-K CHL7 - Planned | 3.225 | 339 | 1093.275 | 0.0010929 | 3.2239e-06
2012-07-11 | 276156 | QPT25B | Urban | LV Transformer SG1311-K CHL7 - Planned | 2.88 | 339 | 976.32 | 0.00097599 | 2.879e-06
2012-07-11 | 276157 | ABY2A | Rural short | LV Transformer SP1359-E ABY2A - Planned | 7 | 120 | 840 | 0.0025032 | 2.086e-05
2012-07-11 | 276163 | NMK17A | Urban | LV Transformer SP2998-L NMK17A - Planned | 25.635 | 259 | 6639.465 | 0.0066372 | 2.5626e-05
2012-07-12 | 276181 | KBR1A | Rural short | LV Transformer SP3378-B KBR1A - Planned | 5 | 225 | 1125 | 0.003351 | 1.4893e-05
2012-07-12 | 276183 | KWH1 | Rural short | Feeder KWH1 - Planned | 16.445 | 143 | 2351.635 | 0.0070048 | 4.8984e-05
2012-07-12 | 276184 | RWD1 | Rural short | LV Transformer SP1217-H RWD1 - Planned | 7 | 219 | 1533 | 0.0045663 | 2.0851e-05
2012-07-12 | 276185 | IPS1B | Urban | LV Transformer SP763552 IPS1B - Planned | 5 | 144 | 720 | 0.00071982 | 4.9988e-06
2012-07-12 | 276186 | GGR5 | Rural short | LV Transformer SP12078-C GGR5 - Planned | 33.95 | 343 | 11644.85 | 0.034686 | 0.00010113
2012-07-12 | 276188 | MBG4 | Rural short | Feeder MBG4 - Planned | 24.67 | 443 | 10928.81 | 0.032553 | 7.3484e-05
2012-07-12 | 276189 | SRD19A | Urban | LV Transformer SP26206-C SRD19A - Planned | 29.105 | 291 | 8469.555 | 0.0084675 | 2.9098e-05
2012-07-12 | 276191 | TRG2A | Urban | LV Transformer SG2949-L TRG2A - Planned | 15.9882 | 338 | 5404.0116 | 0.0054027 | 1.5984e-05
2012-07-12 | 276192 | SFD4 | Urban | LV Transformer SC3533-J SFD4 - Planned | 5.4835 | 339 | 1858.9065 | 0.0018584 | 5.4822e-06
2012-07-12 | 276193 | INA7A | Rural short | LV Transformer SP16668-F INA7A - Planned | 17.0681 | 329 | 5615.4049 | 0.016726 | 5.084e-05
2012-07-12 | 276194 | PWC4 | Rural short | LV Transformer SP4410-A PWC4 - Planned | 7.04 | 380 | 2675.2 | 0.0079686 | 2.097e-05
2012-07-12 | 276195 | BMT2 | Rural short | LV Transformer SP180-B BMT2 - Planned | 7.04 | 240 | 1689.6 | 0.0050328 | 2.097e-05
2012-07-12 | 276196 | CLD22A | Urban | LV Transformer SP10200-A CLD22A - Planned | 12.6498 | 45 | 569.241 | 0.0005691 | 1.2647e-05
2012-07-12 | 276197 | CLD22A | Urban | LV Transformer SC182-A CLD22A - Planned | 16.9728 | 50 | 848.64 | 0.00084843 | 1.6969e-05
2012-07-12 | 276198 | CLD22A | Urban | LV Transformer SC212-A CLD22A - Planned | 4.095 | 30 | 122.85 | 0.00012282 | 4.094e-06
2012-07-12 | 276200 | GYGGYS6 | Rural short | LV Transformer SP18171-A GYGGYS6 - Planned | 4 | 240 | 960 | 0.0028595 | 1.1915e-05
2012-07-12 | 276201 | MTB1B | Rural short | LV Transformer SP7271-C MTB1B - Planned | 2.09 | 147 | 307.23 | 0.00091514 | 6.2254e-06
2012-07-12 | 276202 | NRG9 | Rural short | LV Transformer SP5170-F NRG9 - Planned | 32.495 | 360 | 11698.2 | 0.034845 | 9.6792e-05
2012-07-12 | 276203 | PBH6 | Urban | LV Transformer SP2754-H PBH6 - Planned | 23.9875 | 94 | 2254.825 | 0.0022543 | 2.3982e-05
2012-07-12 | 276204 | SPO51A | Urban | LV Transformer SP3685-E SPO51A - Planned | 34.905 | 380 | 13263.9 | 0.013261 | 3.4896e-05
2012-07-12 | 276205 | CMA8A | Rural short | LV Transformer SC1367510 CMA8A - Planned | 90.09 | 305 | 27477.45 | 0.081846 | 0.00026835
2012-07-12 | 276206 | ZMR10 | Urban | LV Transformer SP924-K ZMR10 - Planned | 7.82 | 380 | 2971.6 | 0.0029709 | 7.8181e-06
2012-07-12 | 276207 | HTN7A | Urban | LV Transformer SP2289-G HTN7A - Planned | 11.12 | 360 | 4003.2 | 0.0040022 | 1.1117e-05
2012-07-12 | 276208 | SFD10 | Urban | LV Transformer SC1500244 SFD10 - Planned | 2.175 | 277 | 602.475 | 0.00060233 | 2.1745e-06
2012-07-12 | 276209 | CVL5A | Rural short | LV Transformer SP9117-B CVL5A - Planned | 6.93 | 160 | 1108.8 | 0.0033028 | 2.0642e-05
2012-07-12 | 276210 | WRG6A | Urban | LV Transformer SP6663-K WRG6A - Planned | 77.015 | 200 | 15403 | 0.015399 | 7.6996e-05
2012-07-12 | 276211 | HPK8A | Urban | LV Transformer SP492472 HPK8A - Planned | 7.1313 | 390 | 2781.207 | 0.0027805 | 7.1295e-06
2012-07-12 | 276212 | ALY8 | Urban | LV Transformer SC1597-J ALY8 - Planned | 24.32 | 327 | 7952.64 | 0.0079507 | 2.4314e-05
2012-07-12 | 276213 | UMG1B | Urban | LV Transformer SC4905-E UMG1B - Planned | 38.4666 | 350 | 13463.31 | 0.01346 | 3.8457e-05
2012-07-12 | 276214 | UMG1B | Urban | LV Transformer SP2758-H UMG1B - Planned | 12.966 | 218 | 2826.588 | 0.0028259 | 1.2963e-05
2012-07-12 | 276215 | SPF12B | Urban | LV Transformer SC1412271 STC7 - Planned | 1.1633 | 67 | 77.9411 | 7.7922e-05 | 1.163e-06
2012-07-12 | 276215 | STC7 | Urban | LV Transformer SC1412271 STC7 - Planned | 27.985 | 67 | 1874.995 | 0.0018745 | 2.7978e-05
2012-07-12 | 276216 | SPF12B | Urban | LV Transformer SC1414155 - Planned | 9.0531 | 55 | 497.9205 | 0.0004978 | 9.0509e-06
2012-07-12 | 276216 | STC7 | Urban | LV Transformer SC1414155 - Planned | 2.63 | 55 | 144.65 | 0.00014461 | 2.6294e-06
2012-07-12 | 276217 | PRG1 | Rural short | LV Transformer SP4769-B PRG1 - Planned | 0.99 | 186 | 184.14 | 0.00054849 | 2.9489e-06
2012-07-12 | 276219 | BMT2 | Rural short | Feeder BMT2 - Planned | 10 | 447 | 4470 | 0.013315 | 2.9787e-05
2012-07-12 | 276220 | WMR3 | Rural short | LV Transformer SP8301-E WMR3 - Planned | 12 | 363 | 4356 | 0.012975 | 3.5744e-05
2012-07-13 | 276264 | MDR25A | Urban | LV Transformer SG10655-H MDR25A - Planned | 1 | 300 | 300 | 0.00029995 | 9.9985e-07
2012-07-13 | 276281 | SMF2A | Rural short | LV Transformer SP4104-H SMF2A - Planned | 1 | 245 | 245 | 0.00072944 | 2.9773e-06
2012-07-13 | 276282 | NBR7 | Urban | LV Transformer SP4447-A NBR7 - Planned | 61.275 | 375 | 22978.125 | 0.022975 | 6.1266e-05
2012-07-13 | 276283 | PWC4 | Rural short | Feeder PWC4 - Planned | 0.4 | 327 | 130.8 | 0.00038943 | 1.1909e-06
2012-07-13 | 276284 | PWC4 | Rural short | LV Transformer SP9406-A PWC4 - Planned | 2.01 | 342 | 687.42 | 0.0020466 | 5.9844e-06
2012-07-13 | 276285 | MFD8A | Rural short | Feeder MFD8A, WMR3 - Planned | 38 | 317 | 12046 | 0.035864 | 0.00011314
2012-07-13 | 276285 | WMR3 | Rural short | Feeder MFD8A, WMR3 - Planned | 22.9 | 317 | 7259.3 | 0.021613 | 6.818e-05
2012-07-13 | 276286 | GVN5A | Urban | LV Transformer SP4627-H GVN5A - Planned | 16.5 | 367 | 6055.5 | 0.0060546 | 1.6497e-05
2012-07-13 | 276287 | TGW3 | Rural short | Feeder TGW3 - Planned | 16.5 | 458 | 7557 | 0.022499 | 4.9125e-05
2012-07-13 | 276289 | OXL4A | Urban | LV Transformer SP941-M OXL4A - Planned | 45.135 | 359 | 16203.465 | 0.016201 | 4.5128e-05
2012-07-13 | 276290 | BWH12A | Rural short | LV Transformer SP4047-A BWH12A - Planned | 7.04 | 390 | 2745.6 | 0.0081744 | 2.096e-05
2012-07-13 | 276291 | MFD9A | Urban | LV Transformer SP4923-F MFD9A - Planned | 1.7949 | 360 | 646.164 | 0.00064607 | 1.7946e-06
2012-07-13 | 276292 | PWC4 | Rural short | LV Transformer SP4404-A PWC4 - Planned | 0.96 | 242 | 232.32 | 0.00069168 | 2.8582e-06
2012-07-13 | 276293 | CBW6 | Rural short | LV Transformer SP4666-D CBW6 - Planned | 3.8539 | 401 | 1545.4139 | 0.0046011 | 1.1474e-05
2012-07-13 | 276294 | NRG16A | Rural short | LV Transformer SP8709-C NRG16A - Planned | 59.29 | 250 | 14822.5 | 0.044131 | 0.00017652
2012-07-13 | 276295 | MMC19B | Urban | LV Transformer SC546-I MMC19B - Planned | 12.255 | 242 | 2965.71 | 0.0029653 | 1.2253e-05
2012-07-13 | 276296 | CCY8A | Rural short | LV Transformer SP4646-H CCY8A - Planned | 11.04 | 322 | 3554.88 | 0.010584 | 3.2869e-05
2012-07-13 | 276297 | BDT1 | Rural short | LV Transformer SP3527-B BDT1 - Planned | 6 | 228 | 1368 | 0.0040729 | 1.7864e-05
2012-07-13 | 276298 | KLG11A | Urban | LV Transformer SP1913-G KLG11A - Planned | 10.32 | 238 | 2456.16 | 0.0024558 | 1.0318e-05
2012-07-13 | 276299 | WNM7A | Urban | LV Transformer SP5777-H WNM7A - Planned | 4.97 | 305 | 1515.85 | 0.0015156 | 4.9692e-06
2012-07-13 | 276300 | CFD2A | Urban | LV Transformer SP2295-H CFD2A - Planned | 25.745 | 378 | 9731.61 | 0.0097301 | 2.5741e-05
2012-07-13 | 276301 | CHL5 | Urban | LV Transformer SG1031-M CHL5 - Planned | 11.45 | 176 | 2015.2 | 0.0020149 | 1.1448e-05
2012-07-13 | 276301 | SRD19A | Urban | LV Transformer SG1031-M CHL5 - Planned | 4.72 | 176 | 830.72 | 0.00083059 | 4.7193e-06
2012-07-13 | 276302 | CMV12A | Urban | LV Transformer SC534119 CMV12A - Planned | 60.27 | 31 | 1868.37 | 0.0018681 | 6.0261e-05
2012-07-13 | 276304 | MTG13A | Urban | LV Transformer SP1537-K MTG13A - Planned | 4.75 | 256 | 1216 | 0.0012158 | 4.7493e-06
2012-07-13 | 276304 | UMG1B | Urban | LV Transformer SP1537-K MTG13A - Planned | 7.0462 | 256 | 1803.8272 | 0.0018036 | 7.0451e-06
2012-07-13 | 276305 | CHL8 | Urban | LV Transformer SP641-K CHL8 - Planned | 39.265 | 386 | 15156.29 | 0.015154 | 3.9259e-05
2012-07-13 | 276306 | BLB4A | Urban | LV Transformer SP3457-G BLB4A - Planned | 23.115 | 294 | 6795.81 | 0.0067948 | 2.3111e-05
2012-07-13 | 276307 | WRG6A | Urban | LV Transformer SP6663-K WRG6A - Planned | 8.44 | 144 | 1215.36 | 0.0012152 | 8.4387e-06
2012-07-13 | 276308 | SPF12B | Urban | LV Transformer SC1413108 SPF12B - Planned | 28.7065 | 193 | 5540.3545 | 0.0055395 | 2.8702e-05
2012-07-14 | 276312 | CLM6 | Urban | LV Transformer SP2301-B CLM6 - Planned | 53.65 | 333 | 17865.45 | 0.017864 | 5.3647e-05
2012-07-14 | 276314 | PBH6 | Urban | LV Transformer SP383-K PBH6 - Planned | 42.7728 | 344 | 14713.8432 | 0.014713 | 4.277e-05
2012-07-14 | 276315 | TSN15A | Urban | LV Transformer SP3058-L TSN5A - Planned | 1.0813 | 371 | 401.1623 | 0.00040114 | 1.0812e-06
2012-07-14 | 276315 | TSN5A | Urban | LV Transformer SP3058-L TSN5A - Planned | 2.324 | 371 | 862.204 | 0.00086216 | 2.3239e-06
2012-07-14 | 276365 | LTN8 | Rural short | Feeder LTN8, NPD1 - Planned | 6.68 | 485 | 3239.8 | 0.0096412 | 1.9879e-05
2012-07-14 | 276365 | NPD1 | Urban | Feeder LTN8, NPD1 - Planned | 1.824 | 1768 | 3224.832 | 0.0032247 | 1.8239e-06
2012-07-15 | 276320 | ARL11A | Urban | Feeder ARL11A - Planned | 1 | 178 | 178 | 0.00017801 | 1e-06
2012-07-15 | 276321 | INA5A | Urban | Feeder INA5A - Planned | 1.2266 | 295 | 361.847 | 0.00036186 | 1.2266e-06
2012-07-15 | 276323 | MAI17 | Urban | LV Transformer SP4577-G MAI17 - Planned | 52.2634 | 390 | 20382.726 | 0.020383 | 5.2265e-05
2012-07-15 | 276325 | MRD6 | Urban | LV Transformer SC6802-D MRD6 - Planned | 22.425 | 222 | 4978.35 | 0.0049785 | 2.2426e-05
2012-07-15 | 276327 | NBR10 | Urban | LV Transformer SP731556 NBR10 - Planned | 23.1 | 339 | 7830.9 | 0.0078312 | 2.3101e-05
2012-07-15 | 276328 | NRA1A | Rural short | LV Transformer SP581660 NRA1A - Planned | 5.18 | 255 | 1320.9 | 0.0039289 | 1.5408e-05
2012-07-15 | 276329 | WRG6A | Urban | LV Transformer SP5980-H WRG6A - Planned | 1.88 | 365 | 686.2 | 0.00068622 | 1.8801e-06
2012-07-15 | 276330 | YTA3B | Urban | LV Transformer SC567299 YTA3B - Planned | 8.96 | 498 | 4462.08 | 0.0044622 | 8.9603e-06
2012-07-15 | 276331 | WED17A | Urban | LV Transformer SG6357-G WED17A - Planned | 5.285 | 55 | 290.675 | 0.00029069 | 5.2852e-06
2012-07-15 | 276332 | WRD21A | Urban | LV Transformer SC754769 WRD21A - Planned | 19.38 | 47 | 910.86 | 0.00091089 | 1.9381e-05
2012-07-15 | 276333 | TMH15A | Urban | LV Transformer SP2973-C TMH15A - Planned | 54.9081 | 268 | 14715.3708 | 0.014716 | 5.491e-05
2012-07-15 | 276334 | ALY3A | Urban | LV Transformer SP2773-I ALY3A - Planned | 18.975 | 188 | 3567.3 | 0.0035674 | 1.8976e-05
2012-07-15 | 276335 | BLB2A | Urban | LV Transformer SP739805 BLB2A - Planned | 0.6767 | 302 | 204.3634 | 0.00020437 | 6.7672e-07
2012-07-15 | 276335 | BLB9A | Urban | LV Transformer SP739805 BLB2A - Planned | 0.685 | 302 | 206.87 | 0.00020688 | 6.8502e-07
2012-07-15 | 276336 | NIP3A | Urban | LV Transformer SP3762-C NIP3A - Planned | 2.25 | 483 | 1086.75 | 0.0010868 | 2.2501e-06
2012-07-15 | 276390 | BBH2A | Urban | LV Transformer SP27794-C BBH2A - Planned | 7.217 | 379 | 2735.243 | 0.0027353 | 7.2173e-06
2012-07-15 | 276787 | ARL11A | Urban | Feeder ARL11A - Planned | 1 | 125 | 125 | 0.000125 | 1e-06
2012-07-16 | 276361 | IPL3 | Rural short | Feeder IPL3 - Planned | 6.01 | 120 | 721.2 | 0.0021441 | 1.7868e-05
2012-07-16 | 276382 | TGW1 | Rural short | LV Transformer SP985-C TGW1 - Planned | 0.99 | 295 | 292.05 | 0.00086827 | 2.9433e-06
2012-07-16 | 276383 | IPL3 | Rural short | Feeder IPL3 - Planned | 33.49 | 137 | 4588.13 | 0.013641 | 9.9566e-05
2012-07-16 | 276386 | CLM9 | Urban | Feeder CLM9 - Planned | 105.96 | 479 | 50754.84 | 0.050761 | 0.00010597
2012-07-16 | 276388 | CLM8 | Urban | LV Transformer SP4427-A CLM8 - Planned | 9.9 | 469 | 4643.1 | 0.0046437 | 9.9013e-06
2012-07-16 | 276389 | CLD17A | Urban | LV Transformer SC22404-A CLD17A - Planned | 12.5531 | 82 | 1029.3542 | 0.0010295 | 1.2555e-05
2012-07-16 | 276391 | SPD2B | Urban | LV Transformer SG27-J SPD5B - Planned | 1.14 | 30 | 34.2 | 3.4204e-05 | 1.1401e-06
2012-07-16 | 276391 | SPD5B | Urban | LV Transformer SG27-J SPD5B - Planned | 11.625 | 30 | 348.75 | 0.00034879 | 1.1626e-05
2012-07-16 | 276392 | BRT6 | Urban | LV Transformer SP89-L BRT6 - Planned | 12.15 | 269 | 3268.35 | 0.0032688 | 1.2152e-05
2012-07-16 | 276393 | WNM3 | Urban | LV Transformer SP3267-J WNM3 - Planned | 14.96 | 210 | 3141.6 | 0.003142 | 1.4962e-05
2012-07-16 | 276394 | HDN2 | Rural short | LV Transformer SP62196-A HDN2 - Planned | 9.3821 | 117 | 1097.7057 | 0.0032635 | 2.7893e-05
2012-07-16 | 276395 | ESK2B | Rural short | LV Transformer SP115-B ESK2B - Planned | 1.98 | 90 | 178.2 | 0.00052979 | 5.8866e-06
2012-07-16 | 276396 | AGT33A | Urban | LV Transformer SC517711 AGT33A - Planned | 0.99 | 23 | 22.77 | 2.2773e-05 | 9.9013e-07
2012-07-16 | 276788 | RIS2 | Urban | LV Transformer SC795229 RIS2 - Planned | 0.264 | 116 | 30.624 | 3.0628e-05 | 2.6403e-07
2012-07-16 | 277111 | WED22B | Urban | LV Transformer SC2750-I WED22B - Planned | 1.13 | 14649 | 16553.37 | 0.016556 | 1.1301e-06
2012-07-17 | 276440 | SMF2A | Rural short | Feeder SMF2A - Planned | 15.825 | 213 | 3370.725 | 0.010015 | 4.702e-05
2012-07-17 | 276441 | CCY1B | Urban | LV Transformer SP79134-B CCY1B - Planned | 1 | 50 | 50 | 5.0013e-05 | 1.0003e-06
2012-07-17 | 276442 | CRM16A | Rural short | LV Transformer SC1445683 CRM16A - Planned | 39 | 138 | 5382 | 0.015991 | 0.00011588
2012-07-17 | 276443 | GYS3A | Rural short | Feeder GYS3A - Planned | 63.2322 | 232 | 14669.8704 | 0.043588 | 0.00018788
2012-07-17 | 276461 | TGW3 | Rural short | Feeder TGW3 - Planned | 11.01 | 357 | 3930.57 | 0.011679 | 3.2714e-05
2012-07-17 | 276472 | LRE8A | Rural short | Feeder LRE8A - Planned | 53 | 349 | 18497 | 0.054959 | 0.00015748
2012-07-17 | 276473 | GYS3A | Rural short | LV Transformer SP301409 GYS3A - Planned | 1 | 188 | 188 | 0.0005586 | 2.9713e-06
2012-07-17 | 276474 | TWG17 | Urban | LV Transformer SP3047-L TWG17 - Planned | 7.7555 | 180 | 1395.99 | 0.0013964 | 7.7575e-06
2012-07-17 | 276475 | NMK23A | Urban | LV Transformer SP214-Q NMK23A - Planned | 17.27 | 166 | 2866.82 | 0.0028676 | 1.7274e-05
2012-07-17 | 276477 | INA11A | Urban | LV Transformer SP2459-K INA11A - Planned | 9.94 | 280 | 2783.2 | 0.0027839 | 9.9426e-06
2012-07-17 | 276478 | TWT12A | Rural short | LV Transformer SP15359-B TWT12A - Planned | 9.96 | 355 | 3535.8 | 0.010506 | 2.9594e-05
2012-07-17 | 276479 | BWH8A | Rural short | LV Transformer SP493-B BWH8A - Planned | 10.295 | 262 | 2697.29 | 0.0080144 | 3.0589e-05
2012-07-17 | 276480 | WMD6A | Urban | LV Transformer SP6578-A WMD6A - Planned | 8.14 | 73 | 594.22 | 0.00059437 | 8.1421e-06
2012-07-17 | 276481 | AHD4A | Urban | LV Transformer SP2723-A AHD4A - Planned | 3.145 | 20 | 125.8 | 0.00012583 | 3.1458e-06
2012-07-17 | 276482 | MAI11 | Urban | LV Transformer SP2856-E MAI11 - Planned | 30 | 281 | 8430 | 0.0084322 | 3.0008e-05
2012-07-17 | 276483 | CRB24B | Urban | LV Transformer SP17419-D CRB24B - Planned | 79.58 | 120 | 9549.6 | 0.0095521 | 7.9601e-05
2012-07-17 | 276484 | BHD5A | Urban | LV Transformer SG121-L BHD5A - Planned | 6.185 | 190 | 1175.15 | 0.0011755 | 6.1866e-06
2012-07-17 | 276485 | BDL3 | Urban | LV Transformer SP80258-B BDL3 - Planned | 17.64 | 383 | 6756.12 | 0.0067579 | 1.7645e-05
2012-07-17 | 276486 | CFD2A | Urban | LV Transformer SP2295-H CFD2A - Planned | 36.585 | 259 | 9475.515 | 0.009478 | 3.6595e-05
2012-07-17 | 276487 | DRD5A | Urban | LV Transformer SP1575-F DRD5A - Planned | 16.62 | 231 | 3839.22 | 0.0038402 | 1.6624e-05
2012-07-17 | 276488 | BLB4A | Urban | LV Transformer SG1144-I BLB8B - Planned | 3.015 | 184 | 554.76 | 0.0005549 | 3.0158e-06
2012-07-17 | 276488 | BLB8B | Urban | LV Transformer SG1144-I BLB8B - Planned | 6.05 | 184 | 1113.2 | 0.0011135 | 6.0516e-06
2012-07-17 | 276489 | HPE16A | Urban | LV Transformer SC4066-G HPE16A - Planned | 22.7677 | 393 | 8947.7061 | 0.00895 | 2.2774e-05
2012-07-17 | 276490 | YTA3B | Urban | LV Transformer SP13906-B YTA3B - Planned | 1 | 270 | 270 | 0.00027007 | 1.0003e-06
2012-07-17 | 276491 | SRD19A | Urban | LV Transformer SP3347-H SRD19A - Planned | 17.3 | 191 | 3304.3 | 0.0033052 | 1.7304e-05
2012-07-17 | 276492 | HDN2 | Rural short | LV Transformer SP1936-C HDN2 - Planned | 8.1693 | 223 | 1821.7539 | 0.0054129 | 2.4273e-05
2012-07-17 | 276493 | NIP5A | Urban | LV Transformer SP2521-G NIP5A - Planned | 8.475 | 318 | 2695.05 | 0.0026957 | 8.4772e-06
2012-07-17 | 276496 | CLD25A | Urban | LV Transformer SP2086-B CLD25A - Planned | 1.6458 | 30 | 49.374 | 4.9387e-05 | 1.6462e-06
2012-07-18 | 276520 | BDT4 | Rural short | LV Transformer SP10659-D BDT4 - Planned | 4.02 | 178 | 715.56 | 0.0021249 | 1.1937e-05
2012-07-18 | 276521 | MTB15A | Rural short | Feeder MTB15A - Planned | 13.5 | 147 | 1984.5 | 0.005893 | 4.0088e-05
2012-07-18 | 276540 | STT2B | Rural short | Feeder STT2B - Planned | 7 | 342 | 2394 | 0.007109 | 2.0786e-05
2012-07-18 | 276542 | LTN2 | Rural short | LV Transformer SP54309-A LTN8 - Planned | 1.86 | 246 | 457.56 | 0.0013587 | 5.5233e-06
2012-07-18 | 276544 | DRA5 | Urban | LV Transformer SSDRA DRA5 - Planned | 5.1 | 289 | 1473.9 | 0.0014745 | 5.102e-06
2012-07-18 | 276545 | BWH12A | Rural short | LV Transformer SP1282-B BWH12A - Planned | 4 | 344 | 1376 | 0.004086 | 1.1878e-05
2012-07-18 | 276546 | MTB13A | Rural short | LV Transformer SP1794-F MTB13A - Planned | 2.0732 | 129 | 267.4428 | 0.00079417 | 6.1564e-06
2012-07-18 | 276547 | SPD11A | Urban | LV Transformer SP1544-G SPD11A - Planned | 11.34 | 114 | 1292.76 | 0.0012933 | 1.1344e-05
2012-07-18 | 276549 | BBH13B | Urban | LV Transformer SG125-I BBH13B - Planned | 22.716 | 33 | 749.628 | 0.00074992 | 2.2725e-05
2012-07-18 | 276550 | MMC22A | Urban | LV Transformer SC819-I MMC22A - Planned | 9.28 | 111 | 1030.08 | 0.0010305 | 9.2836e-06
2012-07-18 | 276551 | LTN8 | Rural short | LV Transformer SC1439685 LTN8 - Planned | 10.81 | 211 | 2280.91 | 0.0067732 | 3.21e-05
2012-07-18 | 276553 | SBH6 | Urban | LV Transformer SC1913-F SBH6 - Planned | 60.86 | 247 | 15032.42 | 0.015038 | 6.0884e-05
2012-07-18 | 276554 | SBH11 | Urban | LV Transformer SP2610-G SBH11 - Planned | 4.7834 | 122 | 583.5748 | 0.0005838 | 4.7853e-06
2012-07-18 | 276555 | DRD5A | Urban | LV Transformer SP1575-F DRD5A - Planned | 24.93 | 294 | 7329.42 | 0.0073323 | 2.494e-05
2012-07-18 | 276556 | HPE16A | Urban | LV Transformer SC4059-H HPE16A - Planned | 44.8253 | 330 | 14792.349 | 0.014798 | 4.4843e-05
2012-07-18 | 276557 | HPE13A | Urban | LV Transformer SC139-K HPE13A - Planned | 5.985 | 305 | 1825.425 | 0.0018261 | 5.9873e-06
2012-07-18 | 276558 | RLA7 | Urban | LV Transformer SC2536-I RLA7 - Planned | 5.8842 | 135 | 794.367 | 0.00079467 | 5.8865e-06
2012-07-18 | 276559 | BLB4A | Urban | LV Transformer SP3457-G BLB4A - Planned | 15.075 | 160 | 2412 | 0.0024129 | 1.5081e-05
2012-07-18 | 276560 | SRD19A | Urban | LV Transformer SP3348-H SRD19A - Planned | 29.63 | 345 | 10222.35 | 0.010226 | 2.9641e-05
2012-07-18 | 276562 | TWG18 | Urban | LV Transformer SC2194-M TWG18 - Planned | 13.344 | 31 | 413.664 | 0.00041382 | 1.3349e-05
2012-07-18 | 276563 | BDB36A | Urban | LV Transformer SP3396-B BDB36A - Planned | 15.45 | 231 | 3568.95 | 0.0035703 | 1.5456e-05
2012-07-18 | 276564 | HDN1 | Rural short | LV Transformer SP8427-B HDN1 - Planned | 15.8808 | 142 | 2255.0736 | 0.0066964 | 4.7158e-05
2012-07-18 | 276565 | TGW2 | Rural short | LV Transformer SP3138-B TGW2 - Planned | 3.375 | 50 | 168.75 | 0.0005011 | 1.0022e-05
2012-07-18 | 276566 | TGW2 | Rural short | LV Transformer SP3676-B TGW2 - Planned | 4.98 | 151 | 751.98 | 0.002233 | 1.4788e-05
2012-07-18 | 276567 | BVL3A | Urban | LV Transformer SP1375-G BVL3A - Planned | 17.197 | 302 | 5193.494 | 0.0051955 | 1.7204e-05
2012-07-18 | 276569 | CRB22A | Urban | LV Transformer SP3733-E CRB22A - Planned | 41 | 372 | 15252 | 0.015258 | 4.1016e-05
2012-07-18 | 276570 | CCY1B | Urban | Feeder CCY1B - Planned | 74.5 | 503 | 37473.5 | 0.037488 | 7.4529e-05
2012-07-18 | 276571 | CLM3 | Rural short | LV Transformer SP142441 CLM3 - Planned | 0.4 | 502 | 200.8 | 0.00059628 | 1.1878e-06
2012-07-18 | 276572 | BMT3 | Rural short | Feeder BMT3 - Planned | 30.88 | 254 | 7843.52 | 0.023291 | 9.1698e-05
2012-07-18 | 276573 | TWT12A | Rural short | Feeder TWT12A - Planned | 53.14 | 345 | 18333.3 | 0.054441 | 0.0001578
2012-07-18 | 276574 | BMT1 | Rural short | Feeder BMT1 - Planned | 1.871 | 301 | 563.171 | 0.0016723 | 5.5559e-06
2012-07-18 | 276575 | LBH3A | Rural short | Feeder LBH3A - Planned | 71.625 | 202.3125 | 14629.2 | 0.043441 | 0.00021269
2012-07-18 | 276576 | CCY8A | Rural short | Feeder CCY8A - Planned | 2 | 525 | 1050 | 0.003118 | 5.939e-06
2012-07-18 | 276577 | BHD23A | Rural short | LV Transformer SP5779-E BHD23A - Planned | 9.765 | 370 | 3613.05 | 0.010729 | 2.8997e-05
2012-07-18 | 276578 | GYM2A | Rural short | LV Transformer SP4271-B GYM2A - Planned | 11.5 | 75 | 862.5 | 0.0025612 | 3.4149e-05
2012-07-18 | 276579 | BHD35A | Rural short | LV Transformer SP5842-F BHD35A - Planned | 0.5 | 17.5 | 17.5 | 5.1966e-05 | 1.4847e-06
2012-07-18 | 276789 | GYS3A | Rural short | LV Transformer SP5455-C GYS3A - Planned | 2.2311 | 308 | 687.1788 | 0.0020406 | 6.6252e-06
2012-07-19 | 276621 | SMF2A | Rural short | LV Transformer SP4964-E SMF2A - Planned | 6 | 130 | 780 | 0.0023148 | 1.7806e-05
2012-07-19 | 276622 | MDR33A | Urban | LV Transformer SP3395-E MDR33A - Planned | 61 | 196 | 11956 | 0.011962 | 6.1031e-05
2012-07-19 | 276623 | KSN2A | Rural short | LV Transformer SP99515-D KSN2A - Planned | 54 | 192 | 10368 | 0.030769 | 0.00016026
2012-07-19 | 276640 | CMA8A | Rural short | Feeder CMA8A - Planned | 1 | 298 | 298 | 0.00088438 | 2.9677e-06
2012-07-19 | 276641 | MTB13A | Rural short | LV Transformer SC2046726 MTB13A - Planned | 2.5 | 192 | 480 | 0.0014245 | 7.4193e-06
2012-07-19 | 276642 | LHM4 | Urban | LV Transformer SC2139-E - Planned | 10 | 343 | 3430 | 0.0034318 | 1.0005e-05
2012-07-19 | 276646 | EZRRWD4 | Rural short | Feeder EZRRWD4 - Planned | 28.82 | 364 | 10490.48 | 0.031133 | 8.553e-05
2012-07-19 | 276647 | CRB25A | Rural short | Feeder CRB25A - Planned | 72.464 | 460 | 33333.44 | 0.098925 | 0.00021505
2012-07-19 | 276648 | MLB12A | Rural short | LV Transformer SP5408-A MLB12A - Planned | 26.88 | 162 | 4354.56 | 0.012923 | 7.9773e-05
2012-07-19 | 276649 | MLB8A | Rural short | LV Transformer SC1446470 MLB8A - Planned | 15 | 8 | 120 | 0.00035613 | 4.4516e-05
2012-07-19 | 276650 | SHW81 | Urban | LV Transformer SP3674-I SHW81 - Planned | 115.68 | 348 | 40256.64 | 0.040277 | 0.00011574
2012-07-19 | 276651 | TGW3 | Rural short | Feeder TGW3 - Planned | 16 | 508 | 8128 | 0.024122 | 4.7484e-05
2012-07-19 | 276652 | IDY6A | Urban | LV Transformer SC521678-A IDY6A - Planned | 44.7076 | 297 | 13278.1572 | 0.013285 | 4.4731e-05
2012-07-19 | 276652 | TWG21 | Urban | LV Transformer SC521678-A IDY6A - Planned | 4.0716 | 297 | 1209.2652 | 0.0012099 | 4.0737e-06
2012-07-19 | 276653 | NMK17A | Urban | LV Transformer SP2998-L NMK17A - Planned | 13.672 | 318 | 4347.696 | 0.0043499 | 1.3679e-05
2012-07-19 | 276654 | KMR28A | Urban | LV Transformer SC3927-I KMR28A - Planned | 36.575 | 328 | 11996.6 | 0.012003 | 3.6594e-05
2012-07-19 | 276655 | CLD7A | Urban | LV Transformer SG11401-A CLD7A - Planned | 23.7616 | 43 | 1021.7488 | 0.0010223 | 2.3774e-05
2012-07-19 | 276656 | PWC4 | Rural short | LV Transformer SP35-V PWC4 - Planned | 13.02 | 192 | 2499.84 | 0.0074189 | 3.864e-05
2012-07-19 | 276657 | CLD7A | Urban | LV Transformer SG211-A CLD7A - Planned | 1.9766 | 67 | 132.4322 | 0.0001325 | 1.9776e-06
2012-07-19 | 276658 | CRB24B | Urban | LV Transformer SP6823-E CRB24B - Planned | 19.92 | 360 | 7171.2 | 0.0071749 | 1.993e-05
2012-07-19 | 276659 | BDL2 | Urban | LV Transformer SC22776-D BDL2 - Planned | 109.23 | 44 | 4806.12 | 0.0048086 | 0.00010929
2012-07-19 | 276660 | BHD21A | Urban | LV Transformer SP1765-H BHD21A - Planned | 5.9 | 393 | 2318.7 | 0.0023199 | 5.903e-06
2012-07-19 | 276661 | BBH16A | Urban | LV Transformer SC772198 BBH16A - Planned | 94.3149 | 32 | 3018.0768 | 0.0030196 | 9.4364e-05
2012-07-19 | 276662 | BHD21A | Urban | LV Transformer SP3493-E BHD21A - Planned | 60.7 | 456 | 27679.2 | 0.027693 | 6.0731e-05
2012-07-19 | 276663 | SBH6 | Urban | LV Transformer SP3628-E SBH6 - Planned | 10.6664 | 215 | 2293.276 | 0.0022945 | 1.0672e-05
2012-07-19 | 276664 | CFD2A | Urban | LV Transformer SP2295-H CFD2A - Planned | 18.97 | 242 | 4590.74 | 0.0045931 | 1.898e-05
2012-07-19 | 276665 | DRD5A | Urban | LV Transformer SP1575-F DRD5A - Planned | 22.16 | 208 | 4609.28 | 0.0046117 | 2.2171e-05
2012-07-19 | 276666 | BLB4A | Urban | LV Transformer SP3457-G BLB4A - Planned | 8.04 | 238 | 1913.52 | 0.0019145 | 8.0441e-06
2012-07-19 | 276667 | SIS1 | Rural short | LV Transformer SP9063-B SIS1 - Planned | 6.68 | 184 | 1229.12 | 0.0036477 | 1.9824e-05
2012-07-19 | 276668 | NSW25 | Urban | LV Transformer SP6723-G NSW25 - Planned | 10.92 | 395 | 4313.4 | 0.0043156 | 1.0926e-05
2012-07-19 | 276669 | CHL8 | Urban | LV Transformer SP641-K CHL8 - Planned | 43.59 | 479 | 20879.61 | 0.02089 | 4.3612e-05
2012-07-19 | 276670 | ALY6 | Urban | LV Transformer SP798-L ALY6 - Planned | 15.68 | 302 | 4735.36 | 0.0047378 | 1.5688e-05
2012-07-19 | 276671 | WRG6A | Urban | LV Transformer SP5980-H WRG6A - Planned | 1.88 | 16 | 30.08 | 3.0096e-05 | 1.881e-06
2012-07-19 | 276672 | BKD12A | Urban | LV Transformer SC22174-B BKD12A - Planned | 23.75 | 248 | 5890 | 0.005893 | 2.3762e-05
2012-07-19 | 276673 | HDN2 | Rural short | LV Transformer SP62196-A HDN2 - Planned | 14.434 | 231 | 3334.254 | 0.0098952 | 4.2836e-05
2012-07-19 | 276674 | THL3 | Rural short | LV Transformer SP8403-B THL3 - Planned | 6.05 | 193 | 1167.65 | 0.0034653 | 1.7955e-05
2012-07-19 | 276675 | BKD12A | Urban | LV Transformer SC22174-B BKD12A - Planned | 4.1166 | 21 | 86.4486 | 8.6493e-05 | 4.1187e-06
2012-07-19 | 276676 | BPN36A | Urban | LV Transformer SP4332-O BPN36A - Planned | 22.42 | 192 | 4304.64 | 0.0043069 | 2.2432e-05
2012-07-20 | 276723 | SMF2A | Rural short | Feeder SMF2A - Planned | 49.8087 | 231 | 11505.8097 | 0.034119 | 0.0001477
2012-07-20 | 276724 | MTB15A | Rural short | Feeder MTB15A - Planned | 54 | 264 | 14256 | 0.042275 | 0.00016013
2012-07-20 | 276725 | RWD2 | Rural short | LV Transformer SP282772-A RWD2 - Planned | 3 | 271 | 813 | 0.0024109 | 8.8962e-06
2012-07-20 | 276726 | MGP13A | Rural short | Feeder MGP13A - Planned | 13 | 249 | 3237 | 0.009599 | 3.855e-05
2012-07-20 | 276740 | FDS1 | Rural short | Feeder FDS1 - Planned | 10 | 371 | 3710 | 0.011002 | 2.9654e-05
2012-07-20 | 276744 | CMD5A | Urban | LV Transformer SP3463-A CMD5A - Planned | 68.385 | 460 | 31457.1 | 0.03148 | 6.8434e-05
2012-07-20 | 276745 | CMD7A | Rural short | LV Transformer SC1510624 CMD7A - Planned | 2.03 | 342 | 694.26 | 0.0020588 | 6.0198e-06
2012-07-20 | 276746 | LBH6A | Rural short | Feeder LBH6A - Planned | 40.54 | 339 | 13743.06 | 0.040754 | 0.00012022
2012-07-20 | 276747 | EMD3 | Rural short | LV Transformer SP7816-C EMD3 - Planned | 13.05 | 297 | 3875.85 | 0.011493 | 3.8698e-05
2012-07-20 | 276748 | AMR3 | Rural short | LV Transformer SP7513-B AMR3 - Planned | 2.01 | 20 | 40.2 | 0.00011921 | 5.9604e-06
2012-07-20 | 276750 | NSD30B | Urban | LV Transformer SP47445-F NSD30B - Planned | 1.19 | 310 | 368.9 | 0.00036916 | 1.1908e-06
2012-07-20 | 276752 | DRA8 | Urban | LV Transformer SP941-M OXL4A - Planned | 5.06 | 319 | 1614.14 | 0.0016153 | 5.0636e-06
2012-07-20 | 276752 | OXL4A | Urban | LV Transformer SP941-M OXL4A - Planned | 6.92 | 319 | 2207.48 | 0.0022091 | 6.9249e-06
2012-07-20 | 276753 | JDL7 | Urban | LV Transformer SC3921-G JDL7 - Planned | 42.2118 | 265 | 11186.127 | 0.011194 | 4.2242e-05
2012-07-20 | 276755 | INA7A | Rural short | LV Transformer SP28063-F INA7A - Planned | 12.3495 | 185 | 2284.6575 | 0.0067749 | 3.6621e-05
2012-07-20 | 276756 | NMK17A | Urban | LV Transformer SP1373-J NMK17A - Planned | 12.1596 | 254 | 3088.5384 | 0.0030907 | 1.2168e-05
2012-07-20 | 276758 | WCL11A | Urban | LV Transformer SP1093-O WCL11A - Planned | 14.21 | 285 | 4049.85 | 0.0040527 | 1.422e-05
2012-07-20 | 276759 | NBR7 | Urban | LV Transformer SP11510-A NBR7 - Planned | 21.75 | 256 | 5568 | 0.005572 | 2.1765e-05
2012-07-20 | 276760 | GYN7A | Rural short | LV Transformer SP3211-B GYN7A - Planned | 5.84 | 240 | 1401.6 | 0.0041563 | 1.7318e-05
2012-07-20 | 276761 | MFD8A | Rural short | LV Transformer SP3145-H MFD8A - Planned | 12.285 | 330 | 4054.05 | 0.012022 | 3.643e-05
2012-07-20 | 276763 | LBH6A | Rural short | LV Transformer SP2050-B LBH6A - Planned | 13.94 | 322 | 4488.68 | 0.013311 | 4.1338e-05
2012-07-20 | 276764 | HWL6A | Urban | LV Transformer SC786001 HWL6A - Planned | 2.0199 | 70 | 141.393 | 0.00014149 | 2.0213e-06
2012-07-20 | 276765 | PBH2B | Urban | LV Transformer SC743-G PBH2B - Planned | 6.09 | 198 | 1205.82 | 0.0012067 | 6.0943e-06
2012-07-20 | 276766 | BBH12B | Urban | LV Transformer SC192-K BBH12B - Planned | 2.95 | 113 | 333.35 | 0.00033359 | 2.9521e-06
2012-07-20 | 276766 | MAI7 | Urban | LV Transformer SC192-K BBH12B - Planned | 39.36 | 113 | 4447.68 | 0.0044508 | 3.9388e-05
2012-07-20 | 276767 | MAI11 | Urban | LV Transformer SP2856-E MAI11 - Planned | 24 | 107 | 2568 | 0.0025698 | 2.4017e-05
2012-07-20 | 276768 | MAI11 | Urban | LV Transformer SP2856-E MAI11 - Planned | 22 | 115 | 2530 | 0.0025318 | 2.2016e-05
2012-07-20 | 276769 | HWL6A | Urban | LV Transformer SC786154 HWL6A - Planned | 81.8228 | 67 | 5482.1276 | 0.005486 | 8.1881e-05
2012-07-20 | 276770 | MMC19B | Urban | LV Transformer SC196-I MMC19B - Planned | 15.7494 | 350 | 5512.29 | 0.0055162 | 1.5761e-05
2012-07-20 | 276771 | BRT5 | Urban | LV Transformer SP3916-D BRT5 - Planned | 5.04 | 305 | 1537.2 | 0.0015383 | 5.0436e-06
2012-07-20 | 276772 | SBH6 | Urban | LV Transformer SP3415-C SBH6 - Planned | 73.1317 | 236 | 17259.0812 | 0.017271 | 7.3184e-05
2012-07-20 | 276773 | CSE2 | Urban | LV Transformer SC22076-I CSE2 - Planned | 19.89 | 360 | 7160.4 | 0.0071655 | 1.9904e-05
2012-07-20 | 276774 | RLA8 | Urban | LV Transformer SC2972-K RLA8 - Planned | 9.233 | 246 | 2271.318 | 0.0022729 | 9.2396e-06
2012-07-20 | 276775 | BLHSTN16 | Rural short | LV Transformer SC570474 BLHSTN16 - Planned | 8.37 | 44 | 368.28 | 0.0010921 | 2.482e-05
2012-07-20 | 276776 | BLH10B | Urban | LV Transformer SP5433-C BLH10B - Planned | 33.468 | 188 | 6291.984 | 0.0062965 | 3.3492e-05
2012-07-20 | 276777 | HPK8A | Urban | LV Transformer SP492472 HPK8A - Planned | 17.5041 | 380 | 6651.558 | 0.0066563 | 1.7517e-05
2012-07-20 | 276778 | CHL2 | Urban | LV Transformer SP1815-K CHL2 - Planned | 17.825 | 197 | 3511.525 | 0.003514 | 1.7838e-05
2012-07-20 | 276779 | RCN4A | Urban | LV Transformer SC534272 RCN4A - Planned | 4.92 | 36 | 177.12 | 0.00017725 | 4.9235e-06
2012-07-20 | 276780 | RCN10A | Urban | LV Transformer SP1290-P RCN10A - Planned | 12 | 285 | 3420 | 0.0034224 | 1.2009e-05
2012-07-20 | 276781 | AGT37A | Urban | LV Transformer SC6038-G AGT37A - Planned | 1.402 | 45 | 63.09 | 6.3135e-05 | 1.403e-06
2012-07-20 | 276782 | RCN4A | Urban | LV Transformer SC534272 RCN4A - Planned | 13.7 | 54 | 739.8 | 0.00074033 | 1.371e-05
2012-07-20 | 276783 | RCN4A | Urban | LV Transformer SC23006-G RCN4A - Planned | 6.85 | 45 | 308.25 | 0.00030847 | 6.8549e-06
2012-07-20 | 276784 | LWD1 | Rural short | LV Transformer SP3463-B LWD1 - Planned | 10.5 | 63 | 661.5 | 0.0019616 | 3.1137e-05
2012-07-20 | 276785 | TWT5B | Rural short | LV Transformer SC350795 TWT5B - Planned | 7.98 | 92 | 734.16 | 0.0021771 | 2.3664e-05
2012-07-20 | 276790 | MBG1 | Rural short | LV Transformer SP428069 MBG1 - Planned | 1 | 149 | 149 | 0.00044184 | 2.9654e-06
2012-07-21 | 276791 | FDS3 | Rural short | LV Transformer SP4227-E FDS3 - Planned | 2.01 | 270 | 542.7 | 0.001608 | 5.9557e-06
2012-07-22 | 276801 | ARG3 | Urban | Feeder ARG3 - Planned | 4.036 | 240 | 968.64 | 0.00096972 | 4.0405e-06
2012-07-22 | 276802 | SMR7B | Urban | Feeder SMR7B - Planned | 1.0053 | 199 | 200.0547 | 0.00020028 | 1.0064e-06
2012-07-22 | 276803 | PMBWED19 | Urban | LV Transformer SG6457-G PMBWED19 - Planned | 1 | 357 | 357 | 0.0003574 | 1.0011e-06
2012-07-22 | 276804 | UNNAMED842 | CBD | LV Transformer SG6193-E UNNAMED842 - Planned | 1 | 213 | 213 | 0.05663 | 0.00026587
2012-07-22 | 276806 | MGL8 | Urban | Feeder MGL8 - Planned | 1.8 | 435 | 783 | 0.00078387 | 1.802e-06
2012-07-22 | 276807 | GGR1 | Rural short | Feeder GGR1 - Planned | 29.94 | 393 | 11766.42 | 0.034836 | 8.864e-05
2012-07-22 | 276808 | BHD46A | Urban | Feeder BHD46A - Planned | 89.3998 | 358 | 32005.1284 | 0.032041 | 8.9499e-05
2012-07-22 | 276809 | CLD30A | Urban | LV Transformer SP3476-A CLD30A - Planned | 101.365 | 422 | 42776.03 | 0.042824 | 0.00010148
2012-07-22 | 276811 | NSD30B | Urban | LV Transformer SP4226-J NSD30B - Planned | 1.915 | 224 | 428.96 | 0.00042944 | 1.9171e-06
2012-07-22 | 276812 | NMK23A | Urban | LV Transformer SP775683 NMK23A - Planned | 5.1464 | 159 | 818.2776 | 0.00081919 | 5.1521e-06
2012-07-22 | 276813 | CSQSTP5 | Urban | LV Transformer SG3906-K CSQSTP5 - Planned | 2 | 451 | 902 | 0.000903 | 2.0022e-06
2012-07-22 | 276814 | CBW7 | Rural short | LV Transformer SP2603-F CBW7 - Planned | 11.8 | 299 | 3528.2 | 0.010446 | 3.4935e-05
2012-07-22 | 276815 | BHD46A | Urban | LV Transformer SP5114-H BHD46A - Planned | 35.625 | 353 | 12575.625 | 0.01259 | 3.5665e-05
2012-07-22 | 276816 | BHD7A | Urban | LV Transformer SP5815-D BHD7A - Planned | 62.23 | 209 | 13006.07 | 0.013021 | 6.2299e-05
2012-07-22 | 276817 | KLG17A | Urban | LV Transformer SC480091 KLG17A - Planned | 25.53 | 114 | 2910.42 | 0.0029137 | 2.5558e-05
2012-07-22 | 276818 | KLG17A | Urban | LV Transformer SP4995-F KLG17A - Planned | 14.266 | 313 | 4465.258 | 0.0044702 | 1.4282e-05
2012-07-22 | 276819 | BDA5A | Urban | LV Transformer SC3952-G BDA5A - Planned | 29.04 | 124 | 3600.96 | 0.003605 | 2.9072e-05
2012-07-22 | 276820 | CHL5 | Urban | LV Transformer SG1031-M CHL5 - Planned | 3.435 | 136 | 467.16 | 0.00046768 | 3.4388e-06
2012-07-22 | 276821 | BLB9A | Urban | LV Transformer SP24455-E BLB9A - Planned | 0.685 | 282 | 193.17 | 0.00019338 | 6.8576e-07
2012-07-22 | 276822 | BDB35A | Urban | LV Transformer SP36329-B BDB35A - Planned | 17.16 | 396 | 6795.36 | 0.0068029 | 1.7179e-05
2012-07-22 | 276823 | SPF17B | Urban | LV Transformer SC1436136 SPF17B - Planned | 1 | 111 | 111 | 0.00011112 | 1.0011e-06
2012-07-23 | 276862 | IPL3 | Rural short | LV Transformer SP600-F IPL3 - Planned | 7 | 218 | 1526 | 0.0045146 | 2.0709e-05
2012-07-23 | 276863 | FDS1 | Rural short | Feeder FDS1 - Planned | 10 | 211 | 2110 | 0.0062423 | 2.9584e-05
2012-07-23 | 276864 | CLD17A | Urban | LV Transformer SP37505-A CLD17A - Planned | 46.5 | 236 | 10974 | 0.010988 | 4.656e-05
2012-07-23 | 276865 | WFD2B | Rural short | Feeder WFD2B - Planned | 13 | 230 | 2990 | 0.0088457 | 3.846e-05
2012-07-23 | 276867 | UPC1 | Rural short | Feeder UPC1 - Planned | 6.01 | 240 | 1442.4 | 0.0042672 | 1.778e-05
2012-07-23 | 276868 | PWC4 | Rural short | Feeder PWC4 - Planned | 22.5 | 150 | 3375 | 0.0099847 | 6.6565e-05
2012-07-23 | 276871 | RPN4A | Rural short | Feeder RPN4A - Planned | 5 | 372 | 1860 | 0.0055027 | 1.4792e-05
2012-07-23 | 276872 | GBN2 | Rural short | LV Transformer SP869-C GBN2 - Planned | 3 | 360 | 1080 | 0.0031951 | 8.8753e-06
2012-07-23 | 276873 | GYN7A | Rural short | LV Transformer SP3897-B GYN7A - Planned | 16.92 | 333 | 5634.36 | 0.016669 | 5.0057e-05
2012-07-23 | 276874 | SMF2A | Rural short | Feeder SMF2A - Planned | 24.365 | 140 | 3411.1 | 0.010092 | 7.2082e-05
2012-07-23 | 276875 | EMD3 | Rural short | LV Transformer SP460-B EMD3 - Planned | 38.83 | 354 | 13745.82 | 0.040666 | 0.00011488
2012-07-23 | 276876 | MGP13A | Rural short | LV Transformer SP17447-H MGP13A - Planned | 18 | 416 | 7488 | 0.022153 | 5.3252e-05
2012-07-23 | 276877 | KRN12 | Urban | LV Transformer SP12552-E KRN12 - Planned | 19.185 | 429 | 8230.365 | 0.008241 | 1.921e-05
2012-07-23 | 276878 | RBA37A | Urban | LV Transformer SP74071-A RBA37A - Planned | 2.33 | 424 | 987.92 | 0.00098919 | 2.333e-06
2012-07-23 | 276879 | INA7A | Rural short | LV Transformer SP3493-I INA7A - Planned | 2.1 | 216 | 453.6 | 0.0013419 | 6.2127e-06
2012-07-23 | 276880 | WFD2B | Rural short | LV Transformer SP3291-D WFD2B - Planned | 6 | 78 | 468 | 0.0013845 | 1.7751e-05
2012-07-23 | 276881 | WFD1B | Rural short | LV Transformer SP6122-E WFD1B - Planned | 2 | 49 | 98 | 0.00028993 | 5.9169e-06
2012-07-23 | 276882 | SBH6 | Urban | LV Transformer SP17333-E SBH6 - Planned | 18.3495 | 355 | 6514.0725 | 0.0065225 | 1.8373e-05
2012-07-23 | 276883 | HDA10A | Urban | LV Transformer SP2761-I HDA10A - Planned | 24.38 | 250 | 6095 | 0.0061028 | 2.4411e-05
2012-07-23 | 276884 | SBH8 | Urban | LV Transformer SP3309-F SBH8 - Planned | 45.54 | 266 | 12113.64 | 0.012129 | 4.5599e-05
2012-07-23 | 276885 | RBY2A | Urban | LV Transformer SP12058-B RBY2A - Planned | 75.3974 | 210 | 15833.454 | 0.015854 | 7.5495e-05
2012-07-23 | 276886 | HPK8A | Urban | LV Transformer SP1337-K HPK8A - Planned | 11.99 | 212 | 2541.88 | 0.0025452 | 1.2005e-05
2012-07-23 | 276887 | HDN2 | Rural short | LV Transformer SP62196-A HDN2 - Planned | 10.1038 | 200 | 2020.76 | 0.0059783 | 2.9891e-05
2012-07-24 | 276906 | WNM4 | Urban | Feeder WNM4 - Planned | 1 | 346 | 346 | 0.00034654 | 1.0016e-06
2012-07-24 | 276908 | BNH1B | Rural short | Feeder BNH1B - Planned | 40.65 | 349 | 14186.85 | 0.041928 | 0.00012014
2012-07-24 | 276909 | CPD2A | Rural short | LV Transformer SP1808-D CPD2A - Planned | 1 | 375 | 375 | 0.0011083 | 2.9554e-06
2012-07-24 | 276921 | TPT1 | Urban | Feeder TPT1 - Planned | 4 | 335 | 1340 | 0.0013421 | 4.0063e-06
2012-07-24 | 276922 | GBN4 | Rural short | LV Transformer SP1522-C GBN4 - Planned | 5 | 232 | 1160 | 0.0034283 | 1.4777e-05
2012-07-24 | 276923 | BMT3 | Rural short | Feeder BMT3 - Planned | 12 | 338 | 4056 | 0.011987 | 3.5465e-05
2012-07-24 | 276924 | CLM3 | Rural short | Feeder CLM3 - Planned | 56 | 322 | 18032 | 0.053292 | 0.0001655
2012-07-24 | 276925 | BWH13A | Rural short | Feeder BWH13A - Planned | 15.98 | 458 | 7318.84 | 0.02163 | 4.7228e-05
2012-07-24 | 276926 | EMD3 | Rural short | LV Transformer SP6625-C EMD3 - Planned | 11.1964 | 236 | 2642.3504 | 0.0078093 | 3.309e-05
2012-07-24 | 276927 | EMD3 | Rural short | LV Transformer SP4557-C EMD3 - Planned | 23 | 182 | 4186 | 0.012371 | 6.7975e-05
2012-07-24 | 276928 | WMR4 | Rural short | LV Transformer SP1166-I WMR4 - Planned | 4.5 | 221 | 994.5 | 0.0029392 | 1.3299e-05
2012-07-24 | 276929 | AMR2 | Rural short | Feeder AMR2 - Planned | 80.985 | 402 | 32555.97 | 0.096217 | 0.00023935
2012-07-24 | 276930 | BHD23A | Rural short | LV Transformer SP3345-E BHD23A - Planned | 25.5 | 494 | 12597 | 0.03723 | 7.5364e-05
2012-07-24 | 276931 | PWC4 | Rural short | Feeder PWC4 - Planned | 17.69 | 204 | 718.33 | 0.002123 | 5.2282e-05
2012-07-24 | 276932 | MGL1A | Rural short | LV Transformer SP1459-N MGL1A - Planned | 5 | 49 | 245 | 0.00072408 | 1.4777e-05
2012-07-24 | 276933 | CBW5 | Urban | LV Transformer SP3704-D CBW5 - Planned | 39.39 | 369 | 14534.91 | 0.014558 | 3.9452e-05
2012-07-24 | 276934 | KWH2 | Rural short | LV Transformer SP1123-C KWH2 - Planned | 12.255 | 173 | 2120.115 | 0.0062659 | 3.6219e-05
2012-07-24 | 276935 | KWA4A | Urban | LV Transformer SC1389427 KWA4A - Planned | 71.805 | 53 | 3805.665 | 0.0038116 | 7.1917e-05
2012-07-24 | 276936 | KWA10A | Urban | LV Transformer SC456191 KWA10A - Planned | 15.96 | 61 | 973.56 | 0.00097508 | 1.5985e-05
2012-07-24 | 276937 | CLD21A | Rural short | LV Transformer SC456180 CLD21A - Planned | 31.85 | 24 | 764.4 | 0.0022591 | 9.4131e-05
2012-07-24 | 276938 | AMR2 | Rural short | LV Transformer SP1676-C AMR2 - Planned | 1.155 | 307 | 354.585 | 0.001048 | 3.4135e-06
2012-07-24 | 276939 | BHD23A | Rural short | LV Transformer SP3346-E BHD23A - Planned | 2.125 | 461 | 979.625 | 0.0028952 | 6.2803e-06
2012-07-24 | 276940 | NRG6 | Urban | LV Transformer SC363-L NRG6 - Planned | 11.4 | 200 | 2280 | 0.0022836 | 1.1418e-05
2012-07-24 | 276941 | MTB13A | Rural short | LV Transformer SP102337-A MTB13A - Planned | 11.96 | 257 | 3073.72 | 0.0090842 | 3.5347e-05
2012-07-24 | 276942 | TBV4 | Rural short | LV Transformer SC1414215 - Planned | 26.04 | 49 | 1275.96 | 0.003771 | 7.696e-05
2012-07-24 | 276943 | SBH6 | Urban | LV Transformer SP3415-C SBH6 - Planned | 24.6131 | 335 | 8245.3885 | 0.0082583 | 2.4652e-05
2012-07-24 | 276944 | GBG27 | Urban | LV Transformer SP1111-J GBG27 - Planned | 12.8 | 438 | 5606.4 | 0.0056152 | 1.282e-05
2012-07-24 | 276945 | BRT3 | Urban | LV Transformer SP3617-F BRT3 - Planned | 4.075 | 62 | 252.65 | 0.00025305 | 4.0814e-06
2012-07-24 | 276946 | CSE2 | Urban | LV Transformer SC4107-O CSE2 - Planned | 44.085 | 244.5 | 10896.93 | 0.010914 | 4.4154e-05
2012-07-24 | 276948 | CFD1A | Urban | LV Transformer SP3185-I HTN24A - Planned | 1.025 | 30 | 30.75 | 3.0798e-05 | 1.0266e-06
2012-07-24 | 276948 | HTN24A | Urban | LV Transformer SP3185-I HTN24A - Planned | 3.24 | 30 | 97.2 | 9.7352e-05 | 3.2451e-06
2012-07-24 | 276949 | BRT8 | Urban | LV Transformer SP3049-G BRT8 - Planned | 16.39 | 110 | 1802.9 | 0.0018057 | 1.6416e-05
2012-07-24 | 276950 | BRT5 | Urban | LV Transformer SP3916-D BRT5 - Planned | 19.505 | 118 | 2301.59 | 0.0023052 | 1.9535e-05
2012-07-24 | 276951 | BLB8A | Urban | LV Transformer SP29224-C BLB8A - Planned | 16.3163 | 397 | 6477.5711 | 0.0064877 | 1.6342e-05
2012-07-24 | 276952 | BLB5A | Urban | LV Transformer SP1947-I BLB5A - Planned | 11.835 | 562 | 6651.27 | 0.0066617 | 1.1854e-05
2012-07-24 | 276953 | SRD19A | Urban | LV Transformer SP3347-H SRD19A - Planned | 11.83 | 87 | 1029.21 | 0.0010308 | 1.1848e-05
2012-07-24 | 276954 | BLB4A | Urban | LV Transformer SP3457-G BLB4A - Planned | 18.09 | 164 | 2966.76 | 0.0029714 | 1.8118e-05
2012-07-24 | 276955 | BLB5A | Urban | LV Transformer SP1947-I BLB5A - Planned | 43.0693 | 630 | 27133.659 | 0.027176 | 4.3137e-05
2012-07-24 | 276956 | UMG15B | Urban | LV Transformer SP2441-L UMG15B - Planned | 1.64 | 107 | 175.48 | 0.00017575 | 1.6426e-06
2012-07-24 | 276957 | SRD19A | Urban | LV Transformer SP3347-H SRD19A - Planned | 10.54 | 159 | 1675.86 | 0.0016785 | 1.0556e-05
2012-07-24 | 276958 | WRD9A | Urban | LV Transformer SC760382 WRD9A - Planned | 82.5 | 310 | 25575 | 0.025615 | 8.2629e-05
2012-07-24 | 276959 | HDN2 | Rural short | LV Transformer SP62196-A HDN2 - Planned | 29.5897 | 364 | 10770.6508 | 0.031832 | 8.745e-05
2012-07-24 | 276960 | HDN1 | Rural short | LV Transformer SP49366-A HDN1 - Planned | 8.33 | 145 | 1207.85 | 0.0035697 | 2.4619e-05
2012-07-24 | 276961 | BVL3A | Urban | LV Transformer SP1375-G BVL3A - Planned | 10.2402 | 375 | 3840.075 | 0.0038461 | 1.0256e-05
2012-07-24 | 277210 | SMF2A | Rural short | Feeder SMF2A - Planned | 76.76 | 389 | 29859.64 | 0.088248 | 0.00022686
2012-07-25 | 276980 | SMF5A | Rural short | LV Transformer SP5068-M SMF5A - Planned | 17 | 147 | 2499 | 0.0073783 | 5.0193e-05
2012-07-25 | 277000 | CRB25A | Rural short | LV Transformer SP5813-C CRB25A - Planned | 10 | 306 | 3060 | 0.0090347 | 2.9525e-05
2012-07-25 | 277001 | KSN2A | Rural short | Feeder KSN2A - Planned | 22.4 | 325 | 7280 | 0.021494 | 6.6136e-05
2012-07-25 | 277020 | LLY4 | Rural short | Feeder LLY4 - Planned | 36.77 | 428 | 15737.56 | 0.046465 | 0.00010856
2012-07-25 | 277021 | TGW3 | Rural short | Feeder TGW3 - Planned | 314.97 | 5 | 1574.85 | 0.0046498 | 0.00092996
2012-07-25 | 277022 | MTB1B | Rural short | LV Transformer SP2366-D MTB1B - Planned | 14.5 | 340 | 4930 | 0.014556 | 4.2812e-05
2012-07-25 | 277023 | KBR6A | Rural short | Feeder KBR6A - Planned | 17.66 | 374 | 6604.84 | 0.019501 | 5.2142e-05
2012-07-25 | 277024 | WMR3 | Rural short | Feeder WMR3 - Planned | 8.5 | 357 | 3034.5 | 0.0089594 | 2.5096e-05
2012-07-25 | 277025 | BMT3 | Rural short | Feeder BMT3 - Planned | 44 | 340 | 14960 | 0.04417 | 0.00012991
2012-07-25 | 277026 | GBN4 | Rural short | LV Transformer SP1836-E GBN4 - Planned | 4.5 | 24 | 108 | 0.00031887 | 1.3286e-05
2012-07-25 | 277027 | WFD1B | Rural short | Feeder WFD1B - Planned | 42 | 298 | 12516 | 0.036954 | 0.00012401
2012-07-25 | 277028 | EMD3 | Rural short | LV Transformer SP4570-B EMD3 - Planned | 11 | 206 | 2266 | 0.0066904 | 3.2478e-05
2012-07-25 | 277029 | GYS3A | Rural short | LV Transformer SP535-B GYS3A - Planned | 12.5 | 90 | 1125 | 0.0033216 | 3.6907e-05
2012-07-25 | 277030 | GBN4 | Rural short | LV Transformer SP664-B GBN4 - Planned | 6 | 141 | 846 | 0.0024978 | 1.7715e-05
2012-07-25 | 277031 | TRP3 | Rural short | Feeder TRP3 - Planned | 6 | 448 | 2688 | 0.0079364 | 1.7715e-05
2012-07-25 | 277032 | GGR1 | Rural short | Feeder GGR1 - Planned | 112 | 595 | 66640 | 0.19676 | 0.00033068
2012-07-25 | 277033 | NMK10 | Urban | LV Transformer SC484550 NMK10 - Planned | 61.9696 | 328 | 20326.0288 | 0.020363 | 6.2083e-05
2012-07-25 | 277034 | KSN5 | Urban | LV Transformer SP46506-A KSN5 - Planned | 1.99 | 259 | 515.41 | 0.00051635 | 1.9936e-06
2012-07-25 | 277035 | WMR3 | Rural short | LV Transformer SP1885-F WMR3 - Planned | 2.97 | 400 | 1188 | 0.0035076 | 8.769e-06
2012-07-25 | 277036 | WMD11A | Rural short | LV Transformer SC1401482 WMD11A - Planned | 84.5691 | 270 | 22833.657 | 0.067417 | 0.00024969
2012-07-25 | 277037 | NRG13A | Urban | LV Transformer SC198-K NRG13A - Planned | 4.795 | 15 | 71.925 | 7.2056e-05 | 4.8038e-06
2012-07-25 | 277038 | CSE2 | Urban | LV Transformer SC4107-O CSE2 - Planned | 24.8 | 405 | 10044 | 0.010062 | 2.4845e-05
2012-07-25 | 277040 | BLB8A | Urban | LV Transformer SP29224-C BLB8A - Planned | 3.1633 | 270 | 854.091 | 0.00085565 | 3.1691e-06
2012-07-25 | 277041 | BLB4A | Urban | LV Transformer SC5313-H BLB4A - Planned | 14.9766 | 336 | 5032.1376 | 0.0050413 | 1.5004e-05
2012-07-25 | 277042 | CVL17A | Urban | LV Transformer SP18203-A CVL17A - Planned | 19.13 | 42 | 803.46 | 0.00080493 | 1.9165e-05
2012-07-25 | 277043 | HDN1 | Rural short | LV Transformer SP8427-B HDN1 - Planned | 15.8808 | 337 | 5351.8296 | 0.015801 | 4.6888e-05
2012-07-25 | 277044 | CMV7 | Urban | LV Transformer SC1429296 CMV7 - Planned | 27.06 | 37 | 1001.22 | 0.0010031 | 2.7109e-05
2012-07-25 | 277045 | TMH2A | Rural short | LV Transformer SP11696-A TMH2A - Planned | 2.16 | 160 | 345.6 | 0.0010204 | 6.3774e-06
2012-07-25 | 277050 | BHD23A | Rural short | LV Transformer SP3253-E BHD23A - Planned | 11.625 | 363 | 4219.875 | 0.012459 | 3.4323e-05
2012-07-25 | 278021 | RBK12A | Urban | LV Transformer SG10412-D RBK12A - Planned | 1.085 | 23082 | 25043.97 | 0.02509 | 1.087e-06
2012-07-26 | 277065 | GYS5A | Rural short | LV Transformer SP6191-A GYS5A - Planned | 1 | 169 | 169 | 0.00049847 | 2.9495e-06
2012-07-26 | 277066 | SPD11A | Urban | LV Transformer SC608-I SPD11A - Planned | 171.5 | 216 | 37044 | 0.037122 | 0.00017186
2012-07-26 | 277080 | MTNWLP5 | Rural short | LV Transformer SP13946-E MTNWLP5 - Planned | 2.5 | 275 | 687.5 | 0.0020278 | 7.3738e-06
2012-07-26 | 277081 | WMR3 | Rural short | LV Transformer SP1885-F WMR3 - Planned | 9 | 349 | 3141 | 0.0092645 | 2.6546e-05
2012-07-26 | 277083 | GYS3A | Rural short | LV Transformer SP18167-A GYS3A - Planned | 2.01 | 348 | 699.48 | 0.0020631 | 5.9285e-06
2012-07-26 | 277084 | AHD21 | Urban | LV Transformer SP4491-A AHD21 - Planned | 40.33 | 154 | 6210.82 | 0.0062239 | 4.0415e-05
2012-07-26 | 277085 | NMC1B | Rural short | LV Transformer SP6644-I NMC1B - Planned | 13 | 298 | 3874 | 0.011426 | 3.8344e-05
2012-07-26 | 277086 | BMT2 | Rural short | Feeder BMT2 - Planned | 61 | 400 | 24400 | 0.071968 | 0.00017992
2012-07-26 | 277087 | SMF2A | Rural short | LV Transformer SP3695-D SMF2A - Planned | 2 | 150 | 300 | 0.00088486 | 5.8991e-06
2012-07-26 | 277088 | SMF3A | Rural short | Feeder SMF3A - Planned | 166.01 | 95 | 15770.95 | 0.046517 | 0.00048965
2012-07-26 | 277089 | LLY3 | Rural short | Feeder LLY3 - Planned | 45.92 | 509 | 23373.28 | 0.06894 | 0.00013544
2012-07-26 | 277090 | MDR8A | Urban | LV Transformer SP6364-F MDR8A - Planned | 2 | 390 | 780 | 0.00078164 | 2.0042e-06
2012-07-26 | 277091 | BHD23A | Rural short | Feeder BHD23A - Planned | 30.5 | 478 | 14579 | 0.043001 | 8.9961e-05
2012-07-26 | 277092 | KSN5 | Urban | LV Transformer SP46506-A KSN5 - Planned | 29.85 | 165 | 4925.25 | 0.0049356 | 2.9913e-05
2012-07-26 | 277093 | ENG9 | Urban | LV Transformer SP23751-E ENG9 - Planned | 5.265 | 100 | 526.5 | 0.00052761 | 5.2761e-06
2012-07-26 | 277094 | NMK18 | Urban | LV Transformer SP3218-K NMK18 - Planned | 9.1231 | 317 | 2892.0227 | 0.0028981 | 9.1423e-06
2012-07-26 | 277094 | NMK23A | Urban | LV Transformer SP3218-K NMK18 - Planned | 5.52 | 317 | 1749.84 | 0.0017535 | 5.5316e-06
2012-07-26 | 277095 | MLB13A | Urban | LV Transformer SC451931-A MLB13A - Planned | 18.06 | 295 | 5327.7 | 0.0053389 | 1.8098e-05
2012-07-26 | 277096 | AHD10B | Urban | LV Transformer SC265-A AHD10B - Planned | 29.1728 | 90 | 2625.552 | 0.0026311 | 2.9234e-05
2012-07-26 | 277097 | BHD23A | Rural short | LV Transformer SP3847-E BHD23A - Planned | 4.07 | 338 | 1375.66 | 0.0040575 | 1.2005e-05
2012-07-26 | 277098 | BLH12B | Urban | LV Transformer SP738519 BLH12B - Planned | 41.2182 | 182 | 7501.7124 | 0.0075175 | 4.1305e-05
2012-07-26 | 277100 | BDT3 | Rural short | LV Transformer SP6652-F BDT3 - Planned | 1.015 | 54 | 54.81 | 0.00016166 | 2.9938e-06
2012-07-26 | 277101 | PBH8 | Urban | LV Transformer SP9428-D PBH8 - Planned | 35.2 | 497 | 17494.4 | 0.017531 | 3.5274e-05
2012-07-26 | 277102 | NRG2A | Urban | LV Transformer SC1717-G NRG2A - Planned | 49.87 | 250 | 12467.5 | 0.012494 | 4.9975e-05
2012-07-26 | 277103 | MMC33A | Urban | LV Transformer SC417-K MMC33A - Planned | 50.255 | 171 | 8593.605 | 0.0086117 | 5.0361e-05
2012-07-26 | 277104 | SPD11A | Urban | LV Transformer SC1277-I SPD11A - Planned | 106.425 | 215 | 22881.375 | 0.02293 | 0.00010665
2012-07-26 | 277105 | IPL3 | Rural short | LV Transformer SP1912-F IPL3 - Planned | 4 | 299 | 1196 | 0.0035276 | 1.1798e-05
2012-07-26 | 277106 | BRT8 | Urban | LV Transformer SP38983 BRT8 - Planned | 6.25 | 43 | 268.75 | 0.00026932 | 6.2632e-06
2012-07-26 | 277107 | CSE2 | Urban | LV Transformer SC4107-O CSE2 - Planned | 4 | 300 | 1200 | 0.0012025 | 4.0084e-06
2012-07-26 | 277108 | KLG11A | Urban | LV Transformer SP3660-E KLG11A - Planned | 0.7325 | 322 | 235.865 | 0.00023636 | 7.3404e-07
2012-07-26 | 277109 | RCN10A | Urban | LV Transformer SG1625-I RCN10A - Planned | 5.895 | 323 | 1904.085 | 0.0019081 | 5.9074e-06
2012-07-26 | 277110 | BLB4A | Urban | LV Transformer SP3457-G BLB4A - Planned | 21.105 | 159 | 3355.695 | 0.0033628 | 2.1149e-05
2012-07-26 | 277112 | UMG1B | Urban | LV Transformer SC4905-E UMG1B - Planned | 16.6896 | 367 | 6125.0832 | 0.006138 | 1.6725e-05
2012-07-26 | 277113 | WRD15B | Urban | LV Transformer SC6236-C WRD17A - Planned | 3.13 | 98 | 306.74 | 0.00030739 | 3.1366e-06
2012-07-26 | 277113 | WRD17A | Urban | LV Transformer SC6236-C WRD17A - Planned | 26.18 | 98 | 2565.64 | 0.002571 | 2.6235e-05
2012-07-26 | 277114 | FDS3 | Rural short | LV Transformer SP1148-H FDS3 - Planned | 8.215 | 249 | 2045.535 | 0.0060334 | 2.423e-05
2012-07-26 | 277115 | WRG1A | Urban | LV Transformer SP2644-L WRG1A - Planned | 21.71 | 203 | 4407.13 | 0.0044164 | 2.1756e-05
2012-07-27 | 277121 | BNH1B | Rural short | LV Transformer SP5257-C BNH1B - Planned | 25.92 | 9 | 233.28 | 0.00068737 | 7.6375e-05
2012-07-27 | 277123 | TGW4 | Rural short | LV Transformer SP5048-B TGW4 - Planned | 5.395 | 88 | 474.76 | 0.0013989 | 1.5897e-05
2012-07-27 | 277124 | JBB16A | Rural short | LV Transformer SP759369 JBB16A - Planned | 3 | 132 | 396 | 0.0011668 | 8.8397e-06
2012-07-27 | 277141 | BNH3A | Rural short | LV Transformer SP13581-C BNH3A - Planned | 10.01 | 169 | 1691.69 | 0.0049847 | 2.9495e-05
2012-07-27 | 277143 | EZRRWD4 | Rural short | LV Transformer SP4096-F EZRRWD4 - Planned | 2.01 | 165 | 331.65 | 0.00097723 | 5.9226e-06
2012-07-27 | 277144 | KBR2A | Rural short | LV Transformer SP809-E KBR2A - Planned | 4 | 45 | 180 | 0.00053038 | 1.1786e-05
2012-07-27 | 277145 | CPB3 | Urban | LV Transformer SP6158-C CPB3 - Planned | 53.9 | 239 | 12882.1 | 0.012913 | 5.4028e-05
2012-07-27 | 277146 | CLM9 | Urban | LV Transformer SP3968-B CLM9 - Planned | 1 | 289 | 289 | 0.00028969 | 1.0024e-06
2012-07-27 | 277147 | PRG2B | Rural short | Feeder PRG2B - Planned | 2 | 205 | 410 | 0.0012081 | 5.8931e-06
2012-07-27 | 277148 | BHD23A | Rural short | LV Transformer SP11080-F BHD23A - Planned | 0.4 | 289 | 115.6 | 0.00034062 | 1.1786e-06
2012-07-27 | 277160 | LRE6A | Rural short | LV Transformer SP3099-B LRE6A - Planned | 1 | 215 | 215 | 0.00063351 | 2.9466e-06
2012-07-27 | 277161 | WMD1A | Urban | LV Transformer SG146-A WMD1A - Planned | 5.5 | 390 | 2145 | 0.0021501 | 5.5131e-06
2012-07-27 | 277162 | KCY2 | Rural short | Feeder KCY2 - Planned | 52.35 | 365 | 19107.75 | 0.056302 | 0.00015425
2012-07-27 | 277163 | AMR2 | Rural short | LV Transformer SP1498-F AMR2 - Planned | 10 | 343 | 3430 | 0.010107 | 2.9466e-05
2012-07-27 | 277165 | IBL2 | Rural short | LV Transformer SP2949-B IBL2 - Planned | 1 | 448 | 448 | 0.0013201 | 2.9466e-06
2012-07-27 | 277166 | TGW3 | Rural short | Feeder TGW3 - Planned | 17 | 480 | 8160 | 0.024044 | 5.0092e-05
2012-07-27 | 277168 | CDSSRD23 | Urban | LV Transformer SC5223-E CDSSRD23 - Planned | 3.65 | 179 | 653.35 | 0.00065491 | 3.6587e-06
2012-07-27 | 277169 | KMR21A | Urban | LV Transformer SC3927-I KMR28A - Planned | 5.24 | 490 | 2567.6 | 0.0025737 | 5.2525e-06
2012-07-27 | 277169 | KMR28A | Urban | LV Transformer SC3927-I KMR28A - Planned | 31.255 | 490 | 15314.95 | 0.015351 | 3.1329e-05
2012-07-27 | 277170 | NMK17A | Urban | LV Transformer SP4548-L NMK17A - Planned | 22.6993 | 93 | 2111.0349 | 0.0021161 | 2.2753e-05
2012-07-27 | 277171 | IBL2 | Rural short | LV Transformer SP641-C IBL2 - Planned | 5.5 | 271 | 1490.5 | 0.0043919 | 1.6206e-05
2012-07-27 | 277172 | AMR1 | Rural short | LV Transformer SP11581-B AMR1 - Planned | 6.035 | 170 | 1025.95 | 0.003023 | 1.7783e-05
2012-07-27 | 277173 | CMD5A | Urban | LV Transformer SP16416-A CMD5A - Planned | 21.36 | 411 | 8778.96 | 0.0087999 | 2.1411e-05
2012-07-27 | 277174 | NBR5 | Rural short | LV Transformer SP373-A NBR5 - Planned | 18.2 | 281 | 5114.2 | 0.015069 | 5.3627e-05
2012-07-27 | 277175 | LDR8 | Urban | LV Transformer SP1084-E LDR8 - Planned | 18 | 239 | 4302 | 0.0043123 | 1.8043e-05
2012-07-27 | 277176 | MDRMLD11 | Urban | LV Transformer SP14121-D MDRMLD11 - Planned | 6.16 | 289 | 1780.24 | 0.0017845 | 6.1747e-06
2012-07-27 | 277177 | IPL1 | Rural short | LV Transformer SP627-E IPL1 - Planned | 7.04 | 289 | 2034.56 | 0.005995 | 2.0744e-05
2012-07-27 | 277178 | MAI7 | Urban | LV Transformer SC775-I MAI7 - Planned | 39.36 | 144 | 5667.84 | 0.0056813 | 3.9454e-05
2012-07-27 | 277179 | NRG22A | Urban | LV Transformer SC566-I NRG22A - Planned | 29.295 | 69 | 2021.355 | 0.0020262 | 2.9365e-05
2012-07-27 | 277180 | SBH6 | Urban | LV Transformer SP17333-E SBH6 - Planned | 36.0523 | 192 | 6922.0416 | 0.0069385 | 3.6138e-05
2012-07-27 | 277181 | ZMR4A | Urban | LV Transformer SP18387-E ZMR4A - Planned | 16 | 262 | 4192 | 0.004202 | 1.6038e-05
2012-07-27 | 277182 | SFD7A | Urban | LV Transformer SC6463-H SFD7A - Planned | 23.85 | 320 | 7632 | 0.0076502 | 2.3907e-05
2012-07-27 | 277183 | BLB4A | Urban | LV Transformer SC5313-H BLB4A - Planned | 13.725 | 247 | 3390.075 | 0.0033982 | 1.3758e-05
2012-07-27 | 277184 | TSN15A | Urban | LV Transformer SP3528-I TSN15A - Planned | 1.28 | 333 | 426.24 | 0.00042726 | 1.2831e-06
2012-07-27 | 277185 | HPK5A | Urban | LV Transformer SP1375-I HPK5A - Planned | 31.1439 | 300 | 9343.17 | 0.0093654 | 3.1218e-05
2012-07-27 | 277186 | NSW33A | Urban | LV Transformer SC1424764 NSW33A - Planned | 6.1425 | 55 | 337.8375 | 0.00033864 | 6.1571e-06
2012-07-27 | 277187 | UMG12A | Urban | LV Transformer SC6310-G UMG12A - Planned | 2.6799 | 211 | 565.4589 | 0.00056681 | 2.6863e-06
2012-07-27 | 277188 | NMC13A | Rural short | LV Transformer SC523783-A NMC13A - Planned | 9.13 | 22 | 200.86 | 0.00059185 | 2.6902e-05
2012-07-27 | 277189 | BPN4 | Urban | LV Transformer SP3905-J BPN4 - Planned | 15.665 | 207 | 3242.655 | 0.0032504 | 1.5702e-05
2012-07-27 | 277190 | BDB35A | Urban | LV Transformer SP3518-D BDB35A - Planned | 16 | 180 | 2880 | 0.0028869 | 1.6038e-05
2012-07-27 | 277192 | CPD2A | Rural short | LV Transformer SP1815-D CPD2A - Planned | 8.01 | 65 | 520.65 | 0.0015341 | 2.3602e-05
2012-07-28 | 277205 | WCL3 | Urban | LV Transformer SC634041 WCL3 - Planned | 3.0831 | 217 | 669.0327 | 0.00067076 | 3.0911e-06
2012-07-28 | 277206 | BNH2B | Rural short | LV Transformer SP743445 BNH2B - Planned | 8.5 | 226 | 1921 | 0.0056558 | 2.5026e-05
2012-07-29 | 277215 | WFD2B | Rural short | Feeder WFD2B - Planned | 13 | 169 | 2197 | 0.0064616 | 3.8234e-05
2012-07-29 | 277216 | CRB24B | Urban | LV Transformer SP36180-C CRB24B - Planned | 32.7375 | 404 | 13225.95 | 0.013264 | 3.2831e-05
2012-07-29 | 277217 | LGL11A | Urban | LV Transformer SG422-D LGL11A - Planned | 0.99 | 24 | 47.52 | 4.7656e-05 | 9.9284e-07
2012-07-29 | 277219 | CPL23A | Rural short | Feeder CPL23A - Planned | 34.5 | 550 | 18975 | 0.055807 | 0.00010147
2012-07-29 | 277220 | VPK8 | Urban | LV Transformer SC3587-L VPK8 - Planned | 3.3165 | 341 | 1130.9265 | 0.0011342 | 3.326e-06
2012-07-29 | 277221 | TWG14A | Urban | LV Transformer SC6317-F TWG14A - Planned | 2.25 | 409 | 920.25 | 0.00092289 | 2.2565e-06
2012-07-29 | 277223 | MAI17 | Urban | LV Transformer SP4491-F MAI17 - Planned | 4.23 | 320 | 1353.6 | 0.0013575 | 4.2421e-06
2012-07-29 | 277224 | NDH5A | Urban | LV Transformer SP3908-H NDH5A - Planned | 5.48 | 372 | 2038.56 | 0.0020444 | 5.4957e-06
2012-07-29 | 277225 | MTG12B | Urban | LV Transformer SC5180-G MTG12B - Planned | 15.57 | 71 | 1105.47 | 0.0011086 | 1.5615e-05
2012-07-29 | 277226 | NSW33A | Urban | LV Transformer SC1424764 NSW33A - Planned | 0.8775 | 23 | 20.1825 | 2.024e-05 | 8.8002e-07
2012-07-29 | 277227 | NSW33A | Urban | LV Transformer SC1424764 NSW33A - Planned | 6.145 | 250 | 1536.25 | 0.0015407 | 6.1626e-06
2012-07-29 | 277228 | RBK9A | Urban | LV Transformer SP1097-G RBK9A - Planned | 4.9 | 387 | 1896.3 | 0.0019017 | 4.9141e-06
2012-07-30 | 277260 | IPL3 | Rural short | LV Transformer SP603-F IPL3 - Planned | 3 | 115 | 345 | 0.0010136 | 8.8141e-06
2012-07-30 | 277261 | FDS3 | Rural short | LV Transformer SP672-G FDS3 - Planned | 4 | 54 | 216 | 0.00063461 | 1.1752e-05
2012-07-30 | 277262 | KBR1A | Rural short | LV Transformer SP732-E KBR1A - Planned | 6 | 18 | 108 | 0.00031731 | 1.7628e-05
2012-07-30 | 277263 | BTN4 | Urban | Feeder BTN4 - Planned | 2 | 222 | 444 | 0.0004454 | 2.0063e-06
2012-07-30 | 277264 | KBR1A | Rural short | LV Transformer SP730-D KBR1A - Planned | 6.02 | 26 | 156.52 | 0.00045986 | 1.7687e-05
2012-07-30 | 277282 | BMT1 | Rural short | LV Transformer SP12578-B BMT1 - Planned | 11.33 | 185 | 2096.05 | 0.0061583 | 3.3288e-05
2012-07-30 | 277283 | MGP12A | Rural short | LV Transformer SC1457205 MGP12A - Planned | 1.95 | 14 | 27.3 | 8.0208e-05 | 5.7292e-06
2012-07-30 | 277284 | GYM7A | Rural short | LV Transformer SP4803-D GYM7A - Planned | 4.95 | 81 | 400.95 | 0.001178 | 1.4543e-05
2012-07-30 | 277285 | GYN7A | Rural short | LV Transformer SP3932-C GYN7A - Planned | 3.375 | 53 | 178.875 | 0.00052554 | 9.9158e-06
2012-07-30 | 277286 | HDA10A | Urban | LV Transformer SP2761-I HDA10A - Planned | 10.6 | 293 | 3105.8 | 0.0031156 | 1.0633e-05
2012-07-30 | 277287 | ALY8 | Urban | LV Transformer SC2832-G ALY8 - Planned | 39.78 | 267 | 10621.26 | 0.010655 | 3.9905e-05
2012-07-30 | 277288 | NBR5 | Rural short | LV Transformer SP3767-A NBR5 - Planned | 2.01 | 185 | 371.85 | 0.0010925 | 5.9054e-06
2012-07-30 | 277289 | BHD23A | Rural short | LV Transformer SP5771-G BHD23A - Planned | 28 | 470 | 13160 | 0.038664 | 8.2265e-05
2012-07-30 | 277292 | AHD4A | Urban | LV Transformer SP2723-A AHD4A - Planned | 1.11 | 14 | 31.08 | 3.1178e-05 | 1.1135e-06
2012-07-31 | 277322 | KBN5A | Rural short | LV Transformer SP5200-G KBN5A - Planned | 2.01 | 174 | 349.74 | 0.0010265 | 5.8993e-06
2012-07-31 | 277340 | KBR3A | Rural short | LV Transformer SP15535-D KBR3A - Planned | 1 | 306 | 306 | 0.0008981 | 2.935e-06
2012-07-31 | 277341 | TGW1 | Rural short | LV Transformer SP1045-D TGW1 - Planned | 3 | 330 | 990 | 0.0029056 | 8.8049e-06
2012-07-31 | 277344 | IBL2 | Rural short | LV Transformer SP6779-D IBL2 - Planned | 1 | 340 | 340 | 0.00099789 | 2.935e-06
2012-07-31 | 277345 | GYM7A | Rural short | LV Transformer SP865-C GYM7A - Planned | 14 | 357 | 4998 | 0.014669 | 4.109e-05
2012-07-31 | 277346 | WMR3 | Rural short | LV Transformer SP5674-D WMR3 - Planned | 5 | 199 | 995 | 0.0029203 | 1.4675e-05
2012-07-31 | 277347 | NBR6 | Rural short | Feeder NBR6 - Planned | 25.78 | 417 | 10750.26 | 0.031552 | 7.5663e-05
2012-07-31 | 277348 | BHD23A | Rural short | Feeder BHD23A - Planned | 69.5 | 585 | 40657.5 | 0.11933 | 0.00020398
2012-07-31 | 277349 | TWG21 | Urban | LV Transformer SC4041-K TWG21 - Planned | 10.16 | 287 | 2915.92 | 0.0029259 | 1.0195e-05
2012-07-31 | 277350 | NBR5 | Rural short | LV Transformer SP373-A NBR5 - Planned | 16.1 | 297 | 4781.7 | 0.014034 | 4.7253e-05
2012-07-31 | 277351 | CLD2 | Urban | LV Transformer SC245-B CLD2 - Planned | 2.13 | 110 | 234.3 | 0.00023511 | 2.1373e-06
2012-07-31 | 277352 | LLY4 | Rural short | Feeder LLY4 - Planned | 4 | 486 | 1944 | 0.0057056 | 1.174e-05
2012-07-31 | 277353 | CRB22A | Urban | LV Transformer SC1001-K CRB22A - Planned | 5.24 | 24 | 125.76 | 0.00012619 | 5.258e-06
2012-07-31 | 277354 | TWG14A | Urban | LV Transformer SP3285-F TWG14A - Planned | 62.6252 | 339 | 21229.9428 | 0.021303 | 6.2841e-05
2012-07-31 | 277355 | KLG11A | Urban | LV Transformer SP8277-D KLG11A - Planned | 18.25 | 257 | 4690.25 | 0.0047064 | 1.8313e-05
2012-07-31 | 277356 | DRD5A | Urban | LV Transformer SP1575-F DRD5A - Planned | 22.16 | 300 | 6648 | 0.0066709 | 2.2236e-05
2012-07-31 | 277357 | WNM5 | Urban | LV Transformer SP821-N WNM5 - Planned | 2.31 | 89 | 205.59 | 0.0002063 | 2.3179e-06
2012-07-31 | 277358 | HDA10A | Urban | LV Transformer SP2299-E HDA11A - Planned | 2.29 | 310 | 709.9 | 0.00071234 | 2.2979e-06
2012-07-31 | 277358 | HDA11A | Urban | LV Transformer SP2299-E HDA11A - Planned | 24.6598 | 310 | 7644.538 | 0.0076708 | 2.4745e-05
2012-07-31 | 277359 | RCF3A | Urban | LV Transformer SP5750-B SBH13A - Planned | 2.45 | 314 | 769.3 | 0.00077195 | 2.4584e-06
2012-07-31 | 277359 | SBH13A | Urban | LV Transformer SP5750-B SBH13A - Planned | 0.685 | 314 | 215.09 | 0.00021583 | 6.8736e-07
2012-07-31 | 277360 | BKD5B | Rural short | LV Transformer SP10518-B BKD5B - Planned | 4.08 | 57 | 232.56 | 0.00068256 | 1.1975e-05
2012-07-31 | 277361 | BLB4A | Urban | LV Transformer SP4864-D KSN2A - Planned | 14.4 | 184 | 2649.6 | 0.0026587 | 1.445e-05
2012-07-31 | 277361 | BLBNFM6 | Urban | LV Transformer SP4864-D KSN2A - Planned | 1.395 | 184 | 256.68 | 0.00025756 | 1.3998e-06
2012-07-31 | 277362 | KSN2A | Rural short | LV Transformer SP4864-D KSN2A - Planned | 2.94 | 319 | 937.86 | 0.0027526 | 8.6288e-06
2012-07-31 | 277363 | BLB4A | Urban | LV Transformer SP3457-G BLB4A - Planned | 21.21 | 107 | 2269.47 | 0.0022773 | 2.1283e-05
2012-07-31 | 277364 | BVL3A | Urban | LV Transformer SP1375-G BVL3A - Planned | 7.3468 | 318 | 2336.2824 | 0.0023443 | 7.3721e-06
2012-07-31 | 277365 | THL3 | Rural short | LV Transformer SP1845-C THL3 - Planned | 3.105 | 235 | 729.675 | 0.0021416 | 9.1131e-06
2012-07-31 | 277369 | GAP8A | Urban | LV Transformer SP691207 GAP8A - Planned | 4.4165 | 154 | 680.141 | 0.00068248 | 4.4317e-06
2012-07-31 | 277687 | GYN3A | Rural short | Feeder GYN3A - Planned | 6.01 | 394 | 2367.94 | 0.0069498 | 1.7639e-05
2012-07-31 | 277688 | TBV3 | Rural short | Feeder TBV3 - Planned | 19.05 | 484 | 9220.2 | 0.027061 | 5.5911e-05
2012-07-31 | 277689 | KSN2A | Rural short | LV Transformer SP5311-D KSN2A - Planned | 1 | 370 | 370 | 0.0010859 | 2.935e-06
2012-08-01 | 277400 | SGT9 | Urban | LV Transformer SC6275-D SGT9 - Planned | 38 | 153 | 5814 | 0.0058356 | 3.8141e-05
2012-08-01 | 277401 | MBG4 | Rural short | LV Transformer SP13105-C MBG4 - Planned | 1 | 161 | 161 | 0.00047204 | 2.9319e-06
2012-08-01 | 277403 | BHD33A | Urban | Feeder BHD33A - Planned | 339 | 101 | 34239 | 0.034366 | 0.00034026
2012-08-01 | 277420 | MCW7 | Rural short | Feeder MCW7 - Planned | 54.9414 | 276 | 15163.8264 | 0.044459 | 0.00016108
2012-08-01 | 277422 | TRP2 | Rural short | Feeder TRP2 - Planned | 6 | 249 | 1494 | 0.0043803 | 1.7591e-05
2012-08-01 | 277424 | SMF6A | Rural short | Feeder SMF6A - Planned | 50.66 | 415 | 21023.9 | 0.06164 | 0.00014853
2012-08-01 | 277425 | MTB15A | Rural short | Feeder MTB15A - Planned | 119 | 322 | 38318 | 0.11235 | 0.0003489
2012-08-01 | 277426 | TWT11A | Rural short | LV Transformer SP15389-B TWT11A - Planned | 1 | 341 | 341 | 0.00099978 | 2.9319e-06
2012-08-01 | 277427 | WMD4A | Rural short | LV Transformer SP4558-B WMD4A - Planned | 88.11 | 225 | 19824.75 | 0.058124 | 0.00025833
2012-08-01 | 277428 | WMD10A | Urban | LV Transformer SP5158-A WMD10A - Planned | 56.35 | 234 | 13185.9 | 0.013235 | 5.656e-05
2012-08-01 | 277429 | KBN15A | Urban | Feeder KBN15A - Planned | 27.52 | 353 | 9714.56 | 0.0097507 | 2.7622e-05
2012-08-01 | 277430 | EMD1 | Rural short | Feeder EMD1 - Planned | 8.665 | 362 | 3136.73 | 0.0091966 | 2.5405e-05
2012-08-01 | 277431 | NMC16A | Rural short | Feeder NMC16A - Planned | 21 | 311 | 6531 | 0.019148 | 6.157e-05
2012-08-01 | 277432 | LRE8A | Rural short | LV Transformer SP8280-B LRE8A - Planned | 12 | 280 | 3360 | 0.0098512 | 3.5183e-05
2012-08-01 | 277434 | UPC1 | Rural short | LV Transformer SP2041588 UPC1 - Planned | 1 | 44 | 44 | 0.000129 | 2.9319e-06
2012-08-01 | 277435 | GAP1A | Urban | LV Transformer SC4187-I GAP1A - Planned | 24.99 | 310 | 7746.9 | 0.0077757 | 2.5083e-05
2012-08-01 | 277436 | TRG2A | Urban | LV Transformer SC2218-O TRG2A - Planned | 19.3598 | 295 | 5711.141 | 0.0057324 | 1.9432e-05
2012-08-01 | 277437 | CBW7 | Rural short | LV Transformer SP5864-B CBW7 - Planned | 0.98 | 207 | 202.86 | 0.00059477 | 2.8733e-06
2012-08-01 | 277438 | BIS16A | Urban | LV Transformer SP1540-E BIS16A - Planned | 11.4 | 301 | 3431.4 | 0.0034442 | 1.1442e-05
2012-08-01 | 277439 | AHD10B | Urban | LV Transformer SC752861 AHD10B - Planned | 3.3066 | 183 | 605.1078 | 0.00060736 | 3.3189e-06
2012-08-01 | 277440 | GYGGYS6 | Rural short | LV Transformer SP738-C GYGGYS6 - Planned | 22 | 137 | 3014 | 0.0088368 | 6.4502e-05
2012-08-01 | 277441 | AHD10B | Urban | LV Transformer SC265-A AHD10B - Planned | 3.6466 | 72 | 262.5552 | 0.00026353 | 3.6602e-06
2012-08-01 | 277442 | HIS5A | Urban | LV Transformer SC1455849 HIS5A - Planned | 6.975 | 337 | 2350.575 | 0.0023593 | 7.001e-06
2012-08-01 | 277443 | BHD5A | Urban | LV Transformer SP1121-I BHD5A - Planned | 71.82 | 353 | 25352.46 | 0.025447 | 7.2087e-05
2012-08-01 | 277444 | SBH4 | Urban | LV Transformer SP3634-E SBH4 - Planned | 51.8 | 308 | 15954.4 | 0.016014 | 5.1993e-05
2012-08-01 | 277445 | SBH6 | Urban | LV Transformer SP3628-E SBH6 - Planned | 11.9997 | 200 | 2399.94 | 0.0024089 | 1.2044e-05
2012-08-01 | 277446 | BLB4A | Urban | LV Transformer SP1305-O BLB4A - Planned | 22.365 | 295 | 6597.675 | 0.0066222 | 2.2448e-05
2012-08-01 | 277447 | VPT1B | Urban | LV Transformer SC318-D VPT1B - Planned | 7.84 | 220 | 1724.8 | 0.0017312 | 7.8692e-06
2012-08-01 | 277448 | HPE5A | Urban | LV Transformer SP9444-G HPE5A - Planned | 3.53 | 222 | 783.66 | 0.00078658 | 3.5431e-06
2012-08-01 | 277449 | KSN15 | Rural short | LV Transformer SP3955-D KSN15 - Planned | 72.82 | 200 | 14564 | 0.0427 | 0.0002135
2012-08-01 | 277450 | LRE8A | Rural short | LV Transformer SP11244-A LRE8A - Planned | 2.99 | 278 | 831.22 | 0.0024371 | 8.7664e-06
2012-08-01 | 277451 | RBK11B | Urban | LV Transformer SP2729-G RBK11B - Planned | 14.04 | 257 | 3608.28 | 0.0036217 | 1.4092e-05
2012-08-01 | 277452 | BPN36A | Urban | LV Transformer SP4332-O BPN36A - Planned | 14.16 | 207 | 2931.12 | 0.002942 | 1.4213e-05
2012-08-01 | 277454 | AHD15A | Urban | LV Transformer SC200-A AHD15A - Planned | 0.99 | 105 | 103.95 | 0.00010434 | 9.9368e-07
2012-08-01 | 277561 | AGE6A | Urban | LV Transformer SP16064-G AGE6A - Planned | 33.105 | 290 | 9600.45 | 0.0096362 | 3.3228e-05
2012-08-01 | 277561 | MLT2B | Urban | LV Transformer SP16064-G AGE6A - Planned | 3.57 | 290 | 1035.3 | 0.0010392 | 3.5833e-06
2012-08-01 | 277690 | MTB2A | Rural short | Feeder MTB2A - Planned | 32.645 | 420 | 13710.9 | 0.040199 | 9.5712e-05
2012-08-01 | 277691 | GGR1 | Rural short | Feeder GGR1 - Planned | 50 | 450 | 22500 | 0.065968 | 0.0001466
2012-08-02 | 277481 | CPB9 | Urban | LV Transformer SP9016-B CPB9 - Planned | 70.29 | 203 | 14268.87 | 0.014326 | 7.0573e-05
2012-08-02 | 277500 | MBG2 | Rural short | LV Transformer SP759113 MBG2 - Planned | 2 | 210 | 420 | 0.00123 | 5.8574e-06
2012-08-02 | 277520 | HDN1 | Rural short | LV Transformer SP8129-B HDN1 - Planned | 2.01 | 351 | 705.51 | 0.0020662 | 5.8867e-06
2012-08-02 | 277522 | KBR3A | Rural short | LV Transformer SP4336-G KBR3A - Planned | 4 | 390 | 1560 | 0.0045687 | 1.1715e-05
2012-08-02 | 277523 | KBR1A | Rural short | LV Transformer SP1086-E KBR1A - Planned | 4 | 387 | 1548 | 0.0045336 | 1.1715e-05
2012-08-02 | 277524 | GGR1 | Rural short | Feeder GGR1 - Planned | 38.66 | 449 | 17358.34 | 0.050837 | 0.00011322
2012-08-02 | 277540 | KSN3 | Urban | LV Transformer SP3304-A KSN3 - Planned | 1 | 62 | 62 | 6.225e-05 | 1.004e-06
2012-08-02 | 277541 | EMP3 | Urban | LV Transformer SP1243-O EMP3 - Planned | 10.4416 | 98 | 1023.2768 | 0.0010274 | 1.0484e-05
2012-08-02 | 277542 | MTG13A | Urban | LV Transformer SC22667-B MTG13A - Planned | 34.655 | 344 | 11921.32 | 0.011969 | 3.4795e-05
2012-08-02 | 277543 | MTG11A | Urban | LV Transformer SP494008-A MTG11A - Planned | 17.575 | 142 | 2495.65 | 0.0025057 | 1.7646e-05
2012-08-02 | 277544 | HPE16A | Urban | LV Transformer SC4066-G HPE16A - Planned | 10.7847 | 387 | 4173.6789 | 0.0041905 | 1.0828e-05
2012-08-02 | 277545 | DRD3A | Urban | LV Transformer SP778006 DRD3A - Planned | 8.4 | 230 | 1932 | 0.0019398 | 8.4338e-06
2012-08-02 | 277546 | INA7A | Rural short | LV Transformer SP28063-F INA7A - Planned | 8.233 | 259 | 2132.347 | 0.006245 | 2.4112e-05
2012-08-02 | 277547 | MGL9 | Rural short | LV Transformer SP735412 MGL9 - Planned | 2.99 | 26 | 77.74 | 0.00022768 | 8.7568e-06
2012-08-02 | 277548 | SGT7 | Urban | LV Transformer SP882-J SGT7 - Planned | 16 | 205 | 3280 | 0.0032932 | 1.6064e-05
2012-08-02 | 277549 | LTA5 | Urban | LV Transformer SP1843-P LTA5 - Planned | 12.4353 | 11 | 136.7883 | 0.00013734 | 1.2485e-05
2012-08-02 | 277550 | SBH6 | Urban | LV Transformer SP851-E SBH6 - Planned | 12.355 | 271 | 3348.205 | 0.0033617 | 1.2405e-05
2012-08-02 | 277550 | SBH8 | Urban | LV Transformer SP851-E SBH6 - Planned | 0.975 | 271 | 264.225 | 0.00026529 | 9.7893e-07
2012-08-02 | 277551 | RCN4A | Urban | LV Transformer SC2240-M RCN4A - Planned | 1 | 19 | 19 | 1.9077e-05 | 1.004e-06
2012-08-02 | 277552 | ZMR7A | Urban | LV Transformer SC4169-G ZMR7A - Planned | 8.96 | 162 | 1451.52 | 0.0014574 | 8.9961e-06
2012-08-02 | 277553 | MHL12A | Rural short | LV Transformer SC1283436 MHL12A - Planned | 4.18 | 76 | 317.68 | 0.00093038 | 1.2242e-05
2012-08-02 | 277554 | CNA8A | Rural short | LV Transformer SP769095 CNA8A - Planned | 4 | 257 | 1028 | 0.0030107 | 1.1715e-05
2012-08-02 | 277556 | LDR3 | Urban | LV Transformer SP3059-H LDR3 - Planned | 14.6 | 205 | 2993 | 0.0030051 | 1.4659e-05
2012-08-02 | 277557 | LDR3 | Urban | LV Transformer SP4487-E LDR3 - Planned | 8.94 | 93 | 831.42 | 0.00083477 | 8.976e-06
2012-08-02 | 277559 | CLD17A | Urban | LV Transformer SP4387-B CLD17A - Planned | 4.4068 | 450 | 1983.06 | 0.001991 | 4.4245e-06
2012-08-02 | 277560 | BHD23A | Rural short | LV Transformer SP13469-E BHD23A - Planned | 15.04 | 490 | 7369.6 | 0.021583 | 4.4047e-05
2012-08-02 | 277562 | BDT4 | Rural short | LV Transformer SC1458737 BDT4 - Planned | 11.18 | 247 | 2761.46 | 0.0080874 | 3.2743e-05
2012-08-02 | 277563 | BISTPT3 | Rural short | LV Transformer SP8351-E BISTPT3 - Planned | 24.095 | 174 | 4192.53 | 0.012279 | 7.0567e-05
2012-08-02 | 277564 | GYN7A | Rural short | LV Transformer SP3828-B GYN7A - Planned | 4.98 | 235 | 1170.3 | 0.0034274 | 1.4585e-05
2012-08-02 | 277565 | AHD4A | Urban | LV Transformer SP16482-A AHD4A - Planned | 1.72 | 166 | 285.52 | 0.00028667 | 1.7269e-06
2012-08-02 | 277567 | TGW3 | Rural short | Feeder TGW3 - Planned | 129 | 620 | 84462 | 0.24736 | 0.0003778
2012-08-02 | 277627 | PWC3 | Rural short | Feeder PWC3 - Planned | 66.405 | 377 | 25034.685 | 0.073319 | 0.00019448
2012-08-02 | 277628 | AMR2 | Rural short | Feeder AMR2 - Planned | 30.8301 | 310 | 9557.331 | 0.02799 | 9.0292e-05
2012-08-02 | 277629 | YDA5A | Rural short | LV Transformer SP3334-A YDA5A - Planned | 7.04 | 305 | 2147.2 | 0.0062885 | 2.0618e-05
2012-08-02 | 277630 | EMD3 | Rural short | LV Transformer SP5298-A EMD3 - Planned | 4.98 | 260 | 1294.8 | 0.0037921 | 1.4585e-05
2012-08-02 | 277631 | MFN13A | Rural short | LV Transformer SP4719-F MFN13A - Planned | 20 | 150 | 3000 | 0.0087861 | 5.8574e-05
2012-08-03 | 277585 | TGW2 | Rural short | LV Transformer SP15260-A TGW2 - Planned | 5 | 237 | 1185 | 0.0034667 | 1.4627e-05
2012-08-03 | 277586 | TGP8A | Urban | LV Transformer SP9663-I TGP8A - Planned | 39.5 | 278 | 10981 | 0.011029 | 3.9671e-05
2012-08-03 | 277587 | EMD2 | Rural short | Feeder EMD2 - Planned | 15.4 | 61 | 939.4 | 0.0027482 | 4.5052e-05
2012-08-03 | 277600 | NRG9 | Rural short | Feeder NRG9 - Planned | 5.535 | 348 | 1926.18 | 0.005635 | 1.6192e-05
2012-08-03 | 277621 | PWC3 | Rural short | Feeder PWC3 - Planned | 32.51 | 345 | 11215.95 | 0.032812 | 9.5107e-05
2012-08-03 | 277622 | KCY2 | Rural short | Feeder KCY2 - Planned | 38.458 | 277 | 10652.866 | 0.031165 | 0.00011251
2012-08-03 | 277623 | GYM9B | Rural short | Feeder GYM9B - Planned | 39.955 | 322 | 12865.51 | 0.037638 | 0.00011689
2012-08-03 | 277624 | WMD4A | Rural short | Feeder WMD4A - Planned | 21 | 285 | 5985 | 0.017509 | 6.1435e-05
2012-08-03 | 277625 | AMR2 | Rural short | Feeder AMR2 - Planned | 13.08 | 248 | 3243.84 | 0.0094897 | 3.8265e-05
2012-08-03 | 277626 | BWH12A | Rural short | LV Transformer SP2077-D BWH12A - Planned | 3 | 186 | 558 | 0.0016324 | 8.7764e-06
2012-08-03 | 277632 | CNA8A | Rural short | Feeder CNA8A - Planned | 14 | 358 | 5012 | 0.014662 | 4.0956e-05
2012-08-03 | 277633 | LBH6A | Rural short | LV Transformer SP1247-B LBH6A - Planned | 5.33 | 188 | 1002.04 | 0.0029314 | 1.5593e-05
2012-08-03 | 277635 | WCL19A | Rural short | LV Transformer SP70310 WCL19A - Planned | 7.3 | 290 | 2117 | 0.0061932 | 2.1356e-05
2012-08-03 | 277636 | MGL8 | Urban | LV Transformer SC691439 MGL8 - Planned | 6.4 | 111 | 710.4 | 0.00071348 | 6.4277e-06
2012-08-03 | 277637 | AHD5 | Urban | LV Transformer SC744240 AHD5 - Planned | 8.33 | 167 | 1391.11 | 0.0013971 | 8.3661e-06
2012-08-03 | 277638 | BLH12B | Urban | LV Transformer SP4937-B BLH12B - Planned | 80.62 | 265 | 21364.3 | 0.021457 | 8.0969e-05
2012-08-03 | 277639 | BHD44A | Urban | LV Transformer SP15809-D BHD44A - Planned | 10.29 | 318 | 3272.22 | 0.0032864 | 1.0335e-05
2012-08-03 | 277640 | NGE12 | Urban | LV Transformer SC6023-E NGE4A - Planned | 4 | 300 | 1200 | 0.0012052 | 4.0173e-06
2012-08-03 | 277640 | NGE4A | Urban | LV Transformer SC6023-E NGE4A - Planned | 10.2 | 300 | 3060 | 0.0030733 | 1.0244e-05
2012-08-03 | 277641 | WNM1A | Urban | LV Transformer SP16217-G WNM1A - Planned | 2.06 | 187 | 385.22 | 0.00038689 | 2.0689e-06
2012-08-03 | 277642 | HMTPTR5 | Urban | LV Transformer SP5229-K HMTPTR5 - Planned | 7.92 | 146 | 1156.32 | 0.0011613 | 7.9543e-06
2012-08-03 | 277643 | ZMR7A | Urban | LV Transformer SP762298 ZMR7A - Planned | 13.975 | 289 | 4038.775 | 0.0040563 | 1.4036e-05
2012-08-03 | 277644 | WRG1A | Urban | LV Transformer SP2644-L WRG1A - Planned | 20.875 | 305 | 6366.875 | 0.0063945 | 2.0965e-05
2012-08-03 | 277644 | WRG6A | Urban | LV Transformer SP2644-L WRG1A - Planned | 5.06 | 305 | 1543.3 | 0.00155 | 5.0819e-06
2012-08-03 | 277645 | HPK5A | Urban | LV Transformer SP1375-I HPK5A - Planned | 34.5137 | 390 | 13460.343 | 0.013519 | 3.4663e-05
2012-08-03 | 277646 | BLB4A | Urban | LV Transformer SP1305-O BLB4A - Planned | 21.56 | 330 | 7114.8 | 0.0071456 | 2.1653e-05
2012-08-03 | 277647 | BNH5A | Rural short | LV Transformer SP950-D BNH5A - Planned | 18.76 | 345 | 6472.2 | 0.018934 | 5.4882e-05
2012-08-03 | 277648 | RPN5A | Rural short | LV Transformer SP3184-C RPN5A - Planned | 14.06 | 274 | 3852.44 | 0.01127 | 4.1132e-05
2012-08-03 | 277649 | LLY4 | Rural short | LV Transformer SP8078-A LLY4 - Planned | 5.0232 | 164 | 823.8048 | 0.00241 | 1.4695e-05
2012-08-03 | 277651 | MGP2A | Urban | Feeder MGP2A - Planned | 153.84 | 445 | 68458.8 | 0.068755 | 0.00015451
2012-08-04 | 277655 | CCY15A | Urban | Feeder CCY15A - Planned | 0.8 | 120 | 96 | 9.6414e-05 | 8.0345e-07
2012-08-04 | 277663 | LBS10A | Urban | LV Transformer SG11213-I LBS10A - Planned | 1 | 378 | 378 | 0.00037963 | 1.0043e-06
2012-08-04 | 277685 | BHD33A | Urban | LV Transformer SG7253-F BHD33A - Planned | 2 | 270 | 540 | 0.00054233 | 2.0086e-06
2012-08-05 | 277693 | BVLNCM7 | Urban | Feeder BVLNCM7 - Planned | 6.765 | 145 | 980.925 | 0.00098515 | 6.7941e-06
2012-08-05 | 277695 | BDB4A | Rural short | Feeder BDB4A - Planned | 1.5 | 298 | 447 | 0.0013072 | 4.3867e-06
2012-08-05 | 277696 | INA7A | Rural short | LV Transformer SC5526-F INA7A - Planned | 2 | 389 | 778 | 0.0022753 | 5.849e-06
2012-08-05 | 277697 | YTA3A | Urban | Feeder YTA3A - Planned | 20 | 458 | 9160 | 0.0091994 | 2.0086e-05
2012-08-05 | 277698 | CCYUPC23 | Urban | Feeder CCYUPC23 - Planned | 78.5 | 409 | 32106.5 | 0.032245 | 7.8838e-05
2012-08-05 | 277699 | RBA1A | Urban | Feeder RBA1A - Planned | 8.33 | 309 | 2573.97 | 0.0025851 | 8.3659e-06
2012-08-05 | 277700 | INA7A | Rural short | Feeder INA7A - Planned | 2 | 540 | 1080 | 0.0031585 | 5.849e-06
2012-08-05 | 277702 | NMK17A | Urban | LV Transformer SP2630-L NMK17A - Planned | 4.6551 | 281 | 1308.0831 | 0.0013137 | 4.6751e-06
2012-08-05 | 277703 | MRD6 | Urban | LV Transformer SC774945 MRD6 - Planned | 4.8936 | 360 | 1761.696 | 0.0017693 | 4.9147e-06
2012-08-05 | 277704 | LBCVPK5 | Urban | LV Transformer SG3498-J LBCVPK5 - Planned | 2.4284 | 265 | 643.526 | 0.0006463 | 2.4389e-06
2012-08-05 | 277704 | VPK11A | Urban | LV Transformer SG3498-J LBCVPK5 - Planned | 2.3925 | 265 | 634.0125 | 0.00063674 | 2.4028e-06
2012-08-05 | 277704 | VPK8 | Urban | LV Transformer SG3498-J LBCVPK5 - Planned | 7.8 | 265 | 2067 | 0.0020759 | 7.8336e-06
2012-08-05 | 277705 | SHW81 | Urban | LV Transformer SP5512-E SHW81 - Planned | 19.366 | 365 | 7068.59 | 0.007099 | 1.9449e-05
2012-08-05 | 277706 | AHD10B | Urban | LV Transformer SP16027-A AHD5 - Planned | 6.4981 | 373 | 2423.7913 | 0.0024342 | 6.5261e-06
2012-08-05 | 277706 | AHD5 | Urban | LV Transformer SP16027-A AHD5 - Planned | 20 | 373 | 7460 | 0.0074921 | 2.0086e-05
2012-08-05 | 277707 | NGE13 | Urban | LV Transformer SC767161 NGE13 - Planned | 2.02 | 282 | 569.64 | 0.00057209 | 2.0287e-06
2012-08-05 | 277708 | NDH5A | Urban | LV Transformer SP3908-H NDH5A - Planned | 5.48 | 285 | 1561.8 | 0.0015685 | 5.5036e-06
2012-08-05 | 277709 | KLG17A | Urban | LV Transformer SC480091 KLG17A - Planned | 15.805 | 200 | 3161 | 0.0031746 | 1.5873e-05
2012-08-05 | 277710 | NMC3A | Rural short | LV Transformer SP769143 NMC3A - Planned | 5.95 | 263 | 1564.85 | 0.0045764 | 1.7401e-05
2012-08-05 | 277711 | BLB4A | Urban | LV Transformer SP576193 BLB4A - Planned | 11.475 | 329 | 3775.275 | 0.0037915 | 1.1524e-05
2012-08-05 | 277712 | RLA6 | Urban | LV Transformer SC22647-E RLA6 - Planned | 9.2796 | 168 | 1558.9728 | 0.0015657 | 9.3196e-06
2012-08-05 | 277713 | NSW8A | Urban | LV Transformer SP13192-H NSW8A - Planned | 25.16 | 368 | 9258.88 | 0.0092987 | 2.5268e-05
2012-08-05 | 277716 | WCL3 | Urban | LV Transformer SG747684 WCL3 - Planned | 1 | 670 | 670 | 0.00067288 | 1.0043e-06
2012-08-05 | 277717 | VPK8 | Urban | LV Transformer SC520165 VPK8 - Planned | 0.9432 | 817 | 770.5944 | 0.00077391 | 9.4726e-07
2012-08-05 | 277720 | BLCT2 | CBD | LV Transformer SSBLC BLCT1 - Planned | 15 | 10 | 300 | 0.07976 | 0.003988
2012-08-06 | 277740 | CMY1 | Rural short | LV Transformer SP11337-B CMY1 - Planned | 0.5 | 179 | 89.5 | 0.0002617 | 1.462e-06
2012-08-06 | 277766 | JBB16A | Rural short | Feeder JBB16A - Planned | 42 | 364 | 15288 | 0.044702 | 0.00012281
2012-08-06 | 277768 | CPD1 | Rural short | LV Transformer SP8234-B CPD1 - Planned | 5.5 | 334 | 1837 | 0.0053714 | 1.6082e-05
2012-08-06 | 277780 | CRY6A | Rural short | LV Transformer SP15420-C CRY6A - Planned | 2.01 | 131 | 263.31 | 0.00076992 | 5.8772e-06
2012-08-06 | 277781 | WMD6A | Urban | LV Transformer SP6578-A WMD6A - Planned | 35.89 | 391 | 14032.99 | 0.014093 | 3.6044e-05
2012-08-06 | 277782 | BMT2 | Rural short | LV Transformer SP990-C BMT2 - Planned | 5.395 | 196 | 1057.42 | 0.0030919 | 1.5775e-05
2012-08-06 | 277783 | AMR2 | Rural short | LV Transformer SP351-B AMR2 - Planned | 11.05 | 133 | 1469.65 | 0.0042972 | 3.231e-05
2012-08-06 | 277784 | EMD2 | Rural short | Feeder EMD2 - Planned | 71.03 | 385 | 27346.55 | 0.079961 | 0.00020769
2012-08-06 | 277786 | CRBTHP14 | Urban | LV Transformer SP2525-H CRBTHP14 - Planned | 37.8 | 499 | 18862.2 | 0.018943 | 3.7962e-05
2012-08-06 | 277787 | HIS5A | Urban | LV Transformer SP2801-H HIS5A - Planned | 9.625 | 343 | 3301.375 | 0.0033156 | 9.6663e-06
2012-08-06 | 277788 | BRT8 | Urban | LV Transformer SP38983 BRT8 - Planned | 25 | 90 | 2250 | 0.0022597 | 2.5107e-05
2012-08-06 | 277789 | SGT7 | Urban | LV Transformer SP783-L SGT7 - Planned | 16.64 | 300 | 4992 | 0.0050134 | 1.6711e-05
2012-08-06 | 277790 | BRT5 | Urban | LV Transformer SP1386-H BRT5 - Planned | 7.8 | 129 | 1006.2 | 0.0010105 | 7.8335e-06
2012-08-06 | 277791 | HPK8A | Urban | LV Transformer SP1337-K HPK8A - Planned | 13.08 | 330 | 4316.4 | 0.0043349 | 1.3136e-05
2012-08-06 | 277792 | PDB13 | Urban | LV Transformer SC1483552 PDB13 - Planned | 5.3 | 76 | 402.8 | 0.00040453 | 5.3228e-06
2012-08-07 | 277796 | KWA4A | Urban | LV Transformer SC2262-B KWA4A - Planned | 7.53 | 34 | 256.02 | 0.0002571 | 7.5618e-06
2012-08-07 | 277819 | KMR25A | Rural short | LV Transformer SP549451 KMR25A - Planned | 2 | 296 | 592 | 0.0017311 | 5.8482e-06
2012-08-07 | 277820 | IPL1 | Rural short | LV Transformer SP2652-E IPL1 - Planned | 0.99 | 285 | 282.15 | 0.00082503 | 2.8948e-06
2012-08-07 | 277821 | JBB12B | Rural short | LV Transformer SP4479-C JBB12B - Planned | 3 | 162 | 486 | 0.0014211 | 8.7723e-06
2012-08-07 | 277822 | BDT1 | Rural short | LV Transformer SP5402-D BDT1 - Planned | 1 | 71 | 71 | 0.00020761 | 2.9241e-06
2012-08-07 | 277823 | CRB25A | Rural short | Feeder CRB25A - Planned | 1.4 | 420 | 588 | 0.0017194 | 4.0937e-06
2012-08-07 | 277824 | TGW1 | Rural short | Feeder TGW1 - Planned | 15.2676 | 390 | 5954.364 | 0.017411 | 4.4644e-05
2012-08-07 | 277826 | IPS3A | Rural short | Feeder IPS3A - Planned | 5 | 424 | 2120 | 0.0061991 | 1.462e-05
2012-08-07 | 277828 | LLY4 | Rural short | Feeder LLY4 - Planned | 2 | 582 | 1164 | 0.0034036 | 5.8482e-06
2012-08-07 | 277829 | SFD3 | Urban | LV Transformer SC4054-K SFD3 - Planned | 13.395 | 427 | 5719.665 | 0.0057438 | 1.3451e-05
2012-08-07 | 277830 | SFD10 | Urban | LV Transformer SC1500244 SFD10 - Planned | 0.725 | 276 | 200.1 | 0.00020094 | 7.2806e-07
2012-08-07 | 277831 | MRD6 | Urban | LV Transformer SC1050752 MRD6 - Planned | 16.4094 | 307 | 5037.6858 | 0.0050589 | 1.6479e-05
2012-08-07 | 277832 | GYN7A | Rural short | LV Transformer SP4223-C GYN7A - Planned | 4.4 | 157 | 690.8 | 0.00202 | 1.2866e-05
2012-08-07 | 277833 | WMD3A | Urban | LV Transformer SP7726-A WMD3A - Planned | 4.16 | 78 | 324.48 | 0.00032585 | 4.1775e-06
2012-08-07 | 277834 | BWH16A | Rural short | LV Transformer SP16460-A BWH16A - Planned | 13.02 | 40 | 520.8 | 0.0015229 | 3.8072e-05
2012-08-07 | 277835 | EMD3 | Rural short | LV Transformer SP4557-C EMD3 - Planned | 23 | 288 | 6624 | 0.019369 | 6.7254e-05
2012-08-07 | 277836 | WFD5A | Rural short | LV Transformer SP4944-F WFD5A - Planned | 2.01 | 52 | 104.52 | 0.00030563 | 5.8774e-06
2012-08-07 | 277837 | CLD20A | Rural short | LV Transformer SC762435 CLD20A - Planned | 1.105 | 42 | 46.41 | 0.00013571 | 3.2311e-06
2012-08-07 | 277838 | IPL1 | Rural short | LV Transformer SP1477-E IPL1 - Planned | 4.98 | 109 | 542.82 | 0.0015873 | 1.4562e-05
2012-08-07 | 277839 | HWL2A | Urban | LV Transformer SC1387528 HWL2A - Planned | 2.73 | 337 | 920.01 | 0.00092389 | 2.7415e-06
2012-08-07 | 277840 | MDR2A | Urban | LV Transformer SP3339-E MDR2A - Planned | 8.26 | 308 | 2544.08 | 0.0025548 | 8.2948e-06
2012-08-07 | 277841 | BHD5A | Urban | LV Transformer SP1417-L BHD5A - Planned | 0.784 | 405 | 317.52 | 0.00031886 | 7.8731e-07
2012-08-07 | 277842 | CRB25A | Rural short | LV Transformer SP1342-G CRB25A - Planned | 2.145 | 275 | 589.875 | 0.0017248 | 6.2722e-06
2012-08-07 | 277843 | RCN3A | Urban | LV Transformer SC3992-I RCN3A - Planned | 7.2 | 247 | 1778.4 | 0.0017859 | 7.2304e-06
2012-08-07 | 277844 | HPE16A | Urban | LV Transformer SC4059-H HPE16A - Planned | 9.8397 | 320 | 3148.704 | 0.003162 | 9.8812e-06
2012-08-07 | 277845 | RLB13B | Rural short | LV Transformer SC662659 RLB13B - Planned | 3.68 | 61 | 224.48 | 0.0006564 | 1.0761e-05
2012-08-07 | 277846 | BLB4A | Urban | LV Transformer SP1305-O BLB4A - Planned | 2.415 | 250 | 603.75 | 0.0006063 | 2.4252e-06
2012-08-07 | 277847 | RLB13B | Rural short | LV Transformer SC586371 RLB13B - Planned | 14.67 | 70 | 1026.9 | 0.0030027 | 4.2896e-05
2012-08-07 | 277848 | FDS3 | Rural short | LV Transformer SP4085-C FDS3 - Planned | 17.5 | 297 | 5197.5 | 0.015198 | 5.1172e-05
2012-08-07 | 277850 | TRP3 | Rural short | LV Transformer SP1915-F TRP3 - Planned | 10.5 | 376 | 3948 | 0.011544 | 3.0703e-05
2012-08-07 | 277861 | PWC3 | Rural short | Feeder PWC3 - Planned | 86.45 | 356 | 30776.2 | 0.089992 | 0.00025279
2012-08-07 | 277862 | BISTPT3 | Rural short | LV Transformer SP3570-E BISTPT3 - Planned | 33.465 | 370 | 12382.05 | 0.036206 | 9.7855e-05
2012-08-07 | 277863 | CRY6A | Rural short | LV Transformer SP4772-C CRY6A - Planned | 4 | 297 | 1188 | 0.0034738 | 1.1696e-05
2012-08-07 | 278091 | WSE6A | Rural short | LV Transformer SP10276-E WSE6A - Planned | 3 | 148 | 444 | 0.0012983 | 8.7723e-06
2012-08-08 | 277860 | AMR3 | Rural short | LV Transformer SP6318-C AMR3 - Planned | 0.33 | 103 | 33.99 | 9.9392e-05 | 9.6497e-07
2012-08-08 | 277865 | AMR2 | Rural short | LV Transformer SP6845-B AMR2 - Planned | 2.01 | 197 | 395.97 | 0.0011579 | 5.8776e-06
2012-08-08 | 277867 | RWD2 | Rural short | LV Transformer SP8394-C RWD2 - Planned | 2.01 | 108 | 217.08 | 0.00063478 | 5.8776e-06
2012-08-08 | 277869 | BLH13B | Rural short | LV Transformer SP1847-D BLH13B - Planned | 4 | 270 | 1080 | 0.0031581 | 1.1697e-05
2012-08-08 | 277880 | BWH16A | Rural short | LV Transformer SP1759-C BWH16A - Planned | 15.8202 | 296 | 4682.7792 | 0.013693 | 4.6261e-05
2012-08-08 | 277901 | TSN15A | Urban | LV Transformer SC21240-E TSN15A - Planned | 1 | 412 | 412 | 0.00041371 | 1.0041e-06
2012-08-08 | 277902 | HDN1 | Rural short | Feeder HDN1 - Planned | 3 | 417 | 1251 | 0.0036581 | 8.7725e-06
2012-08-08 | 277903 | BTA15A | Urban | LV Transformer SP16340-D BTA15A - Planned | 8 | 305 | 2440 | 0.0024501 | 8.0331e-06
2012-08-08 | 277904 | FDS1 | Rural short | Feeder FDS1 - Planned | 40.71 | 414 | 16853.94 | 0.049284 | 0.00011904
2012-08-08 | 277905 | GGR1 | Rural short | Feeder GGR1 - Planned | 23 | 457 | 10511 | 0.030736 | 6.7256e-05
2012-08-08 | 277906 | CLM3 | Rural short | Feeder CLM3 - Planned | 11.01 | 375 | 4128.75 | 0.012073 | 3.2195e-05
2012-08-08 | 277920 | NRG17A | Urban | LV Transformer SP64176-D NRG17A - Planned | 62.5 | 545 | 34062.5 | 0.034203 | 6.2759e-05
2012-08-08 | 277923 | JDL6 | Urban | LV Transformer SP321-T JDL6 - Planned | 6.27 | 325 | 2037.75 | 0.0020462 | 6.2959e-06
2012-08-08 | 277924 | KMR21A | Urban | LV Transformer SC39-Q BPN34A - Planned | 5.895 | 435 | 2564.325 | 0.0025749 | 5.9194e-06
2012-08-08 | 277924 | KMR28A | Urban | LV Transformer SC39-Q BPN34A - Planned | 9.975 | 435 | 4339.125 | 0.0043571 | 1.0016e-05
2012-08-08 | 277925 | SFD6B | Urban | LV Transformer SP442-P SFD6B - Planned | 7.63 | 292 | 2227.96 | 0.0022372 | 7.6616e-06
2012-08-08 | 277926 | TPT1 | Urban | LV Transformer SC1374456 TPT1 - Planned | 5.37 | 30 | 252.72 | 0.00025377 | 5.3922e-06
2012-08-08 | 277928 | TPT1 | Urban | LV Transformer SC522704-A TPT1 - Planned | 2.66 | 70 | 186.2 | 0.00018697 | 2.671e-06
2012-08-08 | 277929 | KWA10A | Urban | LV Transformer SC456191 KWA10A - Planned | 5.775 | 41 | 236.775 | 0.00023775 | 5.7989e-06
2012-08-08 | 277930 | KWA4A | Urban | LV Transformer SC1440105 KWA4A - Planned | 3.99 | 16 | 63.84 | 6.4104e-05 | 4.0065e-06
2012-08-08 | 277932 | CLM6 | Urban | LV Transformer SP1564-B PGN1B - Planned | 7.4 | 295 | 2183 | 0.002192 | 7.4306e-06
2012-08-08 | 277932 | PGN1B | Rural short | LV Transformer SP1564-B PGN1B - Planned | 10.305 | 295 | 3039.975 | 0.0088894 | 3.0133e-05
2012-08-08 | 277933 | TPT1 | Urban | LV Transformer SC1373278 TPT1 - Planned | 2.4 | 55 | 132 | 0.00013255 | 2.4099e-06
2012-08-08 | 277934 | KWA4A | Urban | LV Transformer SC455047 KWA4A - Planned | 1 | 17 | 17 | 1.707e-05 | 1.0041e-06
2012-08-08 | 277936 | HIS5A | Urban | LV Transformer SP5187-H HIS5A - Planned | 2.94 | 389 | 1143.66 | 0.0011484 | 2.9522e-06
2012-08-08 | 277937 | PBH8 | Urban | LV Transformer SP5645-E PBH8 - Planned | 77.5968 | 519 | 40272.7392 | 0.040439 | 7.7918e-05
2012-08-08 | 277938 | BLH10A | Urban | LV Transformer SC1401774 - Planned | 2.145 | 55 | 117.975 | 0.00011846 | 2.1539e-06
2012-08-08 | 277938 | YTA3B | Urban | LV Transformer SC1401774 - Planned | 3 | 55 | 165 | 0.00016568 | 3.0124e-06
2012-08-08 | 277939 | PBH6 | Urban | LV Transformer SP17408-E PBH6 - Planned | 8.554 | 278 | 2378.012 | 0.0023879 | 8.5894e-06
2012-08-08 | 277940 | MTB13A | Rural short | LV Transformer SP1794-F MTB13A - Planned | 8.3806 | 185 | 1550.411 | 0.0045337 | 2.4506e-05
2012-08-08 | 277941 | NDH7 | Urban | LV Transformer SC768975 NDH7 - Planned | 12.74 | 192 | 2446.08 | 0.0024562 | 1.2793e-05
2012-08-08 | 277942 | WRG8A | Urban | LV Transformer SP3268-A WRG8A - Planned | 4.55 | 280 | 1274 | 0.0012793 | 4.5688e-06
2012-08-08 | 277943 | BTA13A | Urban | LV Transformer SP10360-B BTA13A - Planned | 6.42 | 20 | 128.4 | 0.00012893 | 6.4466e-06
2012-08-08 | 277945 | NIP5A | Urban | LV Transformer SP4257-F NIP5A - Planned | 11.8531 | 378 | 4480.4718 | 0.004499 | 1.1902e-05
2012-08-09 | 277961 | TGW2 | Rural short | LV Transformer SP3227-C TGW2 - Planned | 3 | 268 | 804 | 0.002351 | 8.7724e-06
2012-08-09 | 277980 | TGW1 | Rural short | LV Transformer SP14123-B TGW1 - Planned | 1 | 353 | 353 | 0.0010322 | 2.9241e-06
2012-08-09 | 277981 | MGP4 | Rural short | Feeder MGP4 - Planned | 13 | 360 | 4680 | 0.013685 | 3.8014e-05
2012-08-09 | 277982 | JBB16A | Rural short | LV Transformer SP6014-D JBB16A - Planned | 11.96 | 368 | 4401.28 | 0.01287 | 3.4973e-05
2012-08-09 | 277983 | IPS3A | Rural short | LV Transformer SP3801-D IPS3A - Planned | 3 | 428 | 1284 | 0.0037546 | 8.7724e-06
2012-08-09 | 277984 | CRB25A | Rural short | Feeder CRB25A - Planned | 11.5 | 433 | 4979.5 | 0.014561 | 3.3628e-05
2012-08-09 | 277985 | PWC3 | Rural short | Feeder PWC3 - Planned | 41.405 | 466 | 19294.73 | 0.05642 | 0.00012107
2012-08-09 | 277986 | AHD18B | Rural short | LV Transformer SP1657-A AHD18B - Planned | 9 | 340 | 3060 | 0.0089479 | 2.6317e-05
2012-08-09 | 277987 | GYN7A | Rural short | LV Transformer SP6477-D GYN7A - Planned | 3 | 324 | 972 | 0.0028423 | 8.7724e-06
2012-08-09 | 277989 | TWT5B | Rural short | LV Transformer SP18687-A TWT5B - Planned | 42.5 | 71 | 3017.5 | 0.0088236 | 0.00012428
2012-08-09 | 277990 | BWH16A | Rural short | LV Transformer SP1281-B BWH16A - Planned | 18.5 | 245 | 4532.5 | 0.013254 | 5.4097e-05
2012-08-09 | 277991 | BWH16A | Rural short | LV Transformer SP1758-C BWH16A - Planned | 24.6263 | 184 | 4531.2392 | 0.01325 | 7.2011e-05
2012-08-09 | 277993 | LLY3 | Rural short | Feeder LLY3 - Planned | 45.92 | 528 | 24245.76 | 0.070898 | 0.00013428
2012-08-09 | 277995 | AGE6A | Urban | LV Transformer SP2690-J AGE6A - Planned | 30.42 | 230 | 6996.6 | 0.0070251 | 3.0544e-05
2012-08-09 | 277995 | MLT2B | Urban | LV Transformer SP2690-J AGE6A - Planned | 3.57 | 230 | 821.1 | 0.00082444 | 3.5845e-06
2012-08-09 | 277996 | SHW81 | Urban | LV Transformer SP3674-I SHW81 - Planned | 46.995 | 189 | 8882.055 | 0.0089182 | 4.7186e-05
2012-08-09 | 277997 | KSN5 | Urban | LV Transformer SP62707-C KSN5 - Planned | 12.75 | 458 | 5839.5 | 0.0058633 | 1.2802e-05
2012-08-09 | 277998 | CGT5 | Urban | LV Transformer SP5362-G CGT5 - Planned | 1.215 | 100 | 121.5 | 0.00012199 | 1.2199e-06
2012-08-09 | 277999 | TRG3 | Urban | LV Transformer SP1624-H TRG3 - Planned | 3.375 | 252 | 850.5 | 0.00085396 | 3.3887e-06
2012-08-09 | 278000 | SFD3 | Urban | LV Transformer SC4054-K SFD3 - Planned | 35.25 | 374 | 13183.5 | 0.013237 | 3.5393e-05
2012-08-09 | 278001 | MGL5 | Urban | LV Transformer SC5825-G MGL5 - Planned | 27.74 | 285 | 7905.9 | 0.0079381 | 2.7853e-05
2012-08-09 | 278002 | KMR28A | Urban | LV Transformer SC3927-I KMR28A - Planned | 9.31 | 310 | 2886.1 | 0.0028978 | 9.3479e-06
2012-08-09 | 278003 | AHD18B | Rural short | LV Transformer SP2696-A AHD18B - Planned | 20.3 | 295 | 5988.5 | 0.017511 | 5.936e-05
2012-08-09 | 278004 | CLM9 | Urban | LV Transformer SP42452-A CLM9 - Planned | 14.7 | 217 | 3189.9 | 0.0032029 | 1.476e-05
2012-08-09 | 278005 | SPD12B | Urban | LV Transformer SC22763-G SPD12B - Planned | 2.01 | 41 | 82.41 | 8.2745e-05 | 2.0182e-06
2012-08-09 | 278007 | HIS5A | Urban | LV Transformer SP5187-H HIS5A - Planned | 14.91 | 444 | 6620.04 | 0.006647 | 1.4971e-05
2012-08-09 | 278008 | JBB13A | Rural short | LV Transformer SP5044-E JBB13A - Planned | 5.04 | 357 | 1799.28 | 0.0052613 | 1.4738e-05
2012-08-09 | 278009 | NDH1 | Urban | LV Transformer SP3164-G NDH1 - Planned | 47.5322 | 370 | 17586.914 | 0.017658 | 4.7726e-05
2012-08-09 | 278010 | SBH11 | Urban | LV Transformer SP3150-D SBH11 - Planned | 26.81 | 313 | 8391.53 | 0.0084257 | 2.6919e-05
2012-08-09 | 278012 | QPT22A | Urban | LV Transformer SP3572-I QPT22A - Planned | 6.6031 | 366 | 2416.7346 | 0.0024266 | 6.63e-06
2012-08-09 | 278013 | THL3 | Rural short | LV Transformer SP1341-C THL3 - Planned | 2.01 | 197 | 395.97 | 0.0011579 | 5.8775e-06
2012-08-09 | 278014 | BIS1 | Rural short | LV Transformer SC1366563 - Planned | 3.92 | 60 | 235.2 | 0.00068776 | 1.1463e-05
2012-08-09 | 278016 | MMC24A | Urban | LV Transformer SC398-J MMC24A - Planned | 77.22 | 509 | 39304.98 | 0.039465 | 7.7534e-05
2012-08-09 | 278044 | BIS1 | Rural short | LV Transformer SC791588 BIS1 - Planned | 2.16 | 14447 | 31205.52 | 0.091249 | 6.3161e-06
2012-08-09 | 278045 | BLH10A | Urban | LV Transformer SC1036738 BLH10A - Planned | 5.32 | 59 | 313.88 | 0.00031516 | 5.3416e-06
2012-08-09 | 278092 | KBR3A | Rural short | Feeder KBR3A - Planned | 7.25 | 429 | 3110.25 | 0.0090948 | 2.12e-05
2012-08-10 | 278023 | KBN5A | Rural short | LV Transformer SP3551-E KBN5A - Planned | 4.5 | 53 | 238.5 | 0.00069727 | 1.3156e-05
2012-08-10 | 278042 | BDT1 | Rural short | Feeder BDT1 - Planned | 4 | 190 | 760 | 0.0022219 | 1.1694e-05
2012-08-10 | 278047 | NRG16A | Rural short | LV Transformer SP4579-G NRG16A - Planned | 12.5 | 255 | 3187.5 | 0.0093189 | 3.6545e-05
2012-08-10 | 278060 | MBG2 | Rural short | Feeder MBG2 - Planned | 8 | 385 | 3080 | 0.0090046 | 2.3389e-05
2012-08-10 | 278062 | TRP3 | Rural short | Feeder TRP3 - Planned | 16.1625 | 431 | 6966.0375 | 0.020366 | 4.7252e-05
2012-08-10 | 278063 | RLB13B | Rural short | LV Transformer SP569-G RLB13B - Planned | 4.35 | 393 | 1709.55 | 0.004998 | 1.2718e-05
2012-08-10 | 278064 | GAP9A | Urban | LV Transformer SP2570-K GAP9A - Planned | 0.74 | 295 | 218.3 | 0.00021919 | 7.43e-07
2012-08-10 | 278065 | MFD8A | Rural short | LV Transformer SP14141-C MFD8A - Planned | 46.925 | 266 | 12482.05 | 0.036492 | 0.00013719
2012-08-10 | 278066 | KWA1A | Urban | LV Transformer SP5381-A KWA1A - Planned | 91.5 | 49 | 4483.5 | 0.0045017 | 9.1872e-05
2012-08-10 | 278067 | CBW11 | Rural short | LV Transformer SP9067-F CBW11 - Planned | 4 | 210 | 840 | 0.0024558 | 1.1694e-05
2012-08-10 | 278067 | CBW7 | Rural short | LV Transformer SP9067-F CBW11 - Planned | 0.98 | 210 | 205.8 | 0.00060167 | 2.8651e-06
2012-08-10 | 278068 | BLH10A | Urban | LV Transformer SC714399 BLH10A - Planned | 7.92 | 39 | 308.88 | 0.00031013 | 7.9522e-06
2012-08-10 | 278069 | CRBTHP26 | Urban | LV Transformer SP4207-G CRBTHP26 - Planned | 30.2093 | 374 | 11298.2782 | 0.011344 | 3.0332e-05
2012-08-10 | 278070 | SBH6 | Urban | LV Transformer SP1333-H SBH6 - Planned | 6.26 | 97 | 607.22 | 0.00060969 | 6.2854e-06
2012-08-10 | 278071 | DRD5A | Urban | LV Transformer SP29214-A DRD5A - Planned | 15.2915 | 307 | 4694.4905 | 0.0047136 | 1.5354e-05
2012-08-10 | 278072 | UMG12A | Urban | LV Transformer SC4044-I UMG12A - Planned | 16.38 | 315 | 5159.7 | 0.0051806 | 1.6447e-05
2012-08-10 | 278073 | HPK8A | Urban | LV Transformer SP492472 HPK8A - Planned | 25.2837 | 220 | 5562.414 | 0.005585 | 2.5386e-05
2012-08-10 | 278074 | RBY15 | Urban | LV Transformer SP434-D RBY15 - Planned | 1.3433 | 229 | 307.6157 | 0.00030886 | 1.3488e-06
2012-08-10 | 278075 | RLB13B | Rural short | LV Transformer SP4037-D RLB13B - Planned | 0.935 | 282 | 263.67 | 0.00077086 | 2.7335e-06
2012-08-10 | 278076 | NBR8 | Rural short | Feeder NBR8 - Planned | 22.63 | 305 | 6902.15 | 0.020179 | 6.6161e-05
2012-08-10 | 278077 | GYM2A | Rural short | Feeder GYM2A - Planned | 32.98 | 246 | 8113.08 | 0.023719 | 9.642e-05
2012-08-10 | 278078 | GYM7A | Rural short | Feeder GYM7A - Planned | 10.865 | 377 | 4096.105 | 0.011975 | 3.1765e-05
2012-08-10 | 278079 | BMT4 | Rural short | Feeder BMT4 - Planned | 3.01 | 324 | 975.24 | 0.0028512 | 8.8e-06
2012-08-10 | 278080 | NBR4 | Rural short | Feeder NBR4 - Planned | 91.33 | 328 | 29956.24 | 0.087579 | 0.00026701
2012-08-10 | 278081 | IBL2 | Rural short | LV Transformer SP1819-F IBL2 - Planned | 3 | 3.5 | 21 | 6.1395e-05 | 8.7707e-06
2012-08-11 | 278085 | KBR6A | Rural short | Feeder KBR6A - Planned | 11.01 | 150 | 1651.5 | 0.0048274 | 3.2183e-05
2012-08-11 | 278103 | HDA14A | Urban | LV Transformer SC483957 HDA14A - Planned | 7.5 | 630 | 4725 | 0.0047441 | 7.5304e-06
2012-08-11 | 278104 | CPD1 | Rural short | LV Transformer SP734593 CPD1 - Planned | 6 | 106 | 636 | 0.001859 | 1.7538e-05
2012-08-12 | 278110 | DRA11 | Urban | LV Transformer SG5281-G DRA11 - Planned | 1 | 55 | 55 | 5.5222e-05 | 1.004e-06
2012-08-12 | 278114 | NRA1A | Rural short | Feeder NRA1A - Planned | 1 | 230 | 230 | 0.00067217 | 2.9225e-06
2012-08-12 | 278116 | MLT15B | Urban | LV Transformer SC3118-K MLT15B - Planned | 4.4948 | 333 | 1496.7684 | 0.0015028 | 4.513e-06
2012-08-12 | 278118 | INA1A | Urban | LV Transformer SP28640-D INA2A - Planned | 6.45 | 388 | 2502.6 | 0.0025127 | 6.4761e-06
2012-08-12 | 278118 | INA2A | Urban | LV Transformer SP28640-D INA2A - Planned | 3.48 | 388 | 1350.24 | 0.0013557 | 3.4941e-06
2012-08-12 | 278119 | DRA5 | Urban | LV Transformer SC5531-F DRA5 - Planned | 1.0538 | 35 | 36.883 | 3.7032e-05 | 1.0581e-06
2012-08-12 | 278120 | AHD7 | Urban | LV Transformer SP1286-A AHD7 - Planned | 1.0033 | 311 | 312.0263 | 0.00031329 | 1.0074e-06
2012-08-12 | 278121 | MRE3 | Urban | LV Transformer SC494776-A MRE3 - Planned | 2.0625 | 234 | 482.625 | 0.00048458 | 2.0708e-06
2012-08-12 | 278122 | HTN7A | Urban | LV Transformer SP176-L HTN7A - Planned | 25.65 | 411 | 10542.15 | 0.010585 | 2.5754e-05
2012-08-12 | 278123 | NDH7 | Urban | LV Transformer SC4377-G NDH7 - Planned | 5.12 | 319 | 1633.28 | 0.0016399 | 5.1407e-06
2012-08-12 | 278124 | BLB4A | Urban | LV Transformer SP5423-F BLB8B - Planned | 18.0825 | 257 | 4647.2025 | 0.004666 | 1.8156e-05
2012-08-12 | 278124 | BLB8B | Urban | LV Transformer SP5423-F BLB8B - Planned | 2.125 | 257 | 546.125 | 0.00054833 | 2.1336e-06
2012-08-12 | 278125 | WRD17A | Urban | LV Transformer SC6236-C WRD17A - Planned | 38.475 | 165 | 6348.375 | 0.006374 | 3.8631e-05
2012-08-12 | 278126 | TSN15A | Urban | LV Transformer SG3876-G TSN15A - Planned | 20.6274 | 39 | 804.4686 | 0.00080772 | 2.0711e-05
2012-08-13 | 278180 | IBL2 | Rural short | LV Transformer SP735487 IBL2 - Planned | 1 | 217 | 217 | 0.00063406 | 2.9219e-06
2012-08-13 | 278181 | RBA41A | Urban | LV Transformer SC2096439 RBA41A - Planned | 1.6417 | 356 | 584.4452 | 0.0005868 | 1.6483e-06
2012-08-13 | 278182 | INA7A | Rural short | LV Transformer SP28063-F INA7A - Planned | 8.333 | 270 | 2249.91 | 0.0065741 | 2.4349e-05
2012-08-13 | 278183 | LTN3 | Urban | LV Transformer SP2373-F LTN3 - Planned | 11.635 | 330 | 3839.55 | 0.003855 | 1.1682e-05
2012-08-13 | 278184 | BRT8 | Urban | LV Transformer SP50490-K BRT8 - Planned | 5.5 | 233 | 1281.5 | 0.0012867 | 5.5222e-06
2012-08-13 | 278185 | NGE2A | Urban | LV Transformer SP764119 NGE2A - Planned | 4.58 | 230 | 1053.4 | 0.0010576 | 4.5985e-06
2012-08-13 | 278186 | CHL11A | Rural short | LV Transformer SP3936-G CHL11A - Planned | 10.26 | 169 | 1733.94 | 0.0050665 | 2.9979e-05
2012-08-13 | 278186 | WRD20A | Urban | LV Transformer SP3936-G CHL11A - Planned | 0.7733 | 169 | 130.6877 | 0.00013121 | 7.7642e-07
2012-08-13 | 278187 | MGP13A | Rural short | Feeder MGP13A - Planned | 10 | 265 | 2650 | 0.0077432 | 2.9219e-05
2012-08-13 | 278188 | BRD5A | Rural short | LV Transformer SP763286 BRD5A - Planned | 1 | 475 | 475 | 0.0013879 | 2.9219e-06
2012-08-13 | 278362 | PTR1 | Urban | Feeder HMTPTR5, HMTPTR7 - Planned | 2.5 | 4640 | 11600 | 0.011647 | 2.5101e-06
2012-08-13 | 278362 | PTR3 | Urban | Feeder HMTPTR5, HMTPTR7 - Planned | 2 | 4640 | 9280 | 0.0093174 | 2.0081e-06
2012-08-14 | 278221 | LGV2B | Rural short | LV Transformer SP1196-H LGV2B - Planned | 2.01 | 214 | 430.14 | 0.0012566 | 5.8721e-06
2012-08-14 | 278242 | CPD2A | Rural short | LV Transformer SP1816-D CPD2A - Planned | 4 | 352 | 1408 | 0.0041134 | 1.1686e-05
2012-08-14 | 278243 | CRB25A | Rural short | Feeder CRB25A - Planned | 1.4 | 474 | 663.6 | 0.0019387 | 4.09e-06
2012-08-14 | 278245 | PPE6A | Rural short | Feeder PPE6A - Planned | 2 | 515 | 1030 | 0.0030091 | 5.8429e-06
2012-08-14 | 278246 | BHD23A | Rural short | LV Transformer SP3237-E BHD23A - Planned | 18.5 | 549 | 10156.5 | 0.029672 | 5.4047e-05
2012-08-14 | 278248 | GYN2B | Urban | LV Transformer SP5546-B GYN2B - Planned | 3 | 295 | 885 | 0.00088857 | 3.0121e-06
2012-08-14 | 278249 | TCB3 | Rural short | Feeder TCB3 - Planned | 2.675 | 325 | 869.375 | 0.0025398 | 7.8148e-06
2012-08-14 | 278250 | GYN6A | Rural short | Feeder GYN6A - Planned | 28.345 | 331 | 9382.195 | 0.027409 | 8.2808e-05
2012-08-14 | 278251 | AMR2 | Rural short | Feeder AMR2 - Planned | 11.01 | 218 | 2400.18 | 0.007012 | 3.2165e-05
2012-08-14 | 278252 | MLY6 | Rural short | LV Transformer SP2461-C MLY6 - Planned | 18.525 | 170 | 3149.25 | 0.0092003 | 5.412e-05
2012-08-14 | 278255 | PPE6A | Rural short | LV Transformer SP5967-C PPE6A - Planned | 13.23 | 484 | 6403.32 | 0.018707 | 3.8651e-05
2012-08-14 | 278256 | NDH12 | Urban | LV Transformer SP758852 NDH12 - Planned | 17.145 | 220 | 3771.9 | 0.0037871 | 1.7214e-05
2012-08-14 | 278257 | UPC2 | Rural short | LV Transformer SP485-J UPC2 - Planned | 7.5 | 124 | 930 | 0.0027169 | 2.1911e-05
2012-08-14 | 278258 | RBA4A | Urban | LV Transformer SC2096439 RBA41A - Planned | 1.01 | 58 | 58.58 | 5.8816e-05 | 1.0141e-06
2012-08-14 | 278259 | IPL1 | Rural short | LV Transformer SP2125-C IPL1 - Planned | 3 | 256 | 768 | 0.0022437 | 8.7643e-06
2012-08-14 | 278261 | KRNQNP7 | Urban | LV Transformer SP2678-M KRNQNP7 - Planned | 5.1 | 83 | 423.3 | 0.00042501 | 5.1205e-06
2012-08-14 | 278262 | BMG2A | Urban | LV Transformer SC6720-G BMG2A - Planned | 2.9664 | 126 | 373.7664 | 0.00037527 | 2.9784e-06
2012-08-14 | 278263 | OXL4A | Urban | LV Transformer SP16675-H OXL4A - Planned | 23.78 | 244 | 5802.32 | 0.0058257 | 2.3876e-05
2012-08-14 | 278264 | BLH10A | Urban | LV Transformer SC1083128 YTA3B - Planned | 1.08 | 35 | 37.8 | 3.7952e-05 | 1.0844e-06
2012-08-14 | 278264 | YTA3B | Urban | LV Transformer SC1083128 YTA3B - Planned | 0.99 | 35 | 34.65 | 3.479e-05 | 9.9399e-07
2012-08-14 | 278265 | ENG7 | Urban | LV Transformer SP2133-K ENG7 - Planned | 14.82 | 219 | 3245.58 | 0.0032587 | 1.488e-05
2012-08-14 | 278266 | CLM7 | Urban | LV Transformer SP2256-B CLM7 - Planned | 10.575 | 360 | 3807 | 0.0038223 | 1.0618e-05
2012-08-14 | 278267 | SBH4 | Urban | LV Transformer SP4645-D SBH4 - Planned | 8.14 | 166 | 1351.24 | 0.0013567 | 8.1728e-06
2012-08-14 | 278268 | CLM6 | Urban | LV Transformer SP1007-G CLM6 - Planned | 43 | 129 | 5547 | 0.0055693 | 4.3173e-05
2012-08-14 | 278270 | EMD3 | Rural short | LV Transformer SP2869-C EMD3 - Planned | 6.5 | 58 | 377 | 0.0011014 | 1.8989e-05
2012-08-14 | 278271 | HDA3A | Urban | LV Transformer SP2760-J HDA3A - Planned | 18.84 | 320 | 6028.8 | 0.0060531 | 1.8916e-05
2012-08-14 | 278272 | EMD3 | Rural short | LV Transformer SP3774-B EMD3 - Planned | 8.455 | 90 | 760.95 | 0.0022231 | 2.4701e-05
2012-08-14 | 278273 | HPK5A | Urban | LV Transformer SP621-L HPK5A - Planned | 20.7683 | 300 | 6230.49 | 0.0062556 | 2.0852e-05
2012-08-14 | 278274 | CMD5A | Urban | LV Transformer SP5361-A CMD5A - Planned | 14.16 | 212 | 3001.92 | 0.003014 | 1.4217e-05
2012-08-14 | 278275 | RLB13B | Rural short | LV Transformer SP569-G RLB13B - Planned | 4.35 | 287 | 1248.45 | 0.0036473 | 1.2708e-05
2012-08-14 | 278276 | YDA5A | Rural short | LV Transformer SC1424108 YDA5A - Planned | 61 | 126 | 7686 | 0.022454 | 0.00017821
2012-08-14 | 278277 | HPE16A | Urban | LV Transformer SC4028-I SRD19A - Planned | 5.4665 | 360 | 1967.94 | 0.0019759 | 5.4885e-06
2012-08-14 | 278277 | SRD19A | Urban | LV Transformer SC4028-I SRD19A - Planned | 3.2665 | 360 | 1175.94 | 0.0011807 | 3.2797e-06
2012-08-14 | 278505 | GYGGYS6 | Rural short | LV Transformer SP1035-D GYGGYS6 - Planned | 2.345 | 12 | 28.14 | 8.2209e-05 | 6.8508e-06
2012-08-15 | 278281 | RIS2 | Urban | LV Transformer SP6177-C RIS2 - Planned | 43 | 20 | 860 | 0.00086346 | 4.3173e-05
2012-08-15 | 278282 | RIS2 | Urban | LV Transformer SP11622-C RIS2 - Planned | 26 | 11 | 286 | 0.00028715 | 2.6105e-05
2012-08-15 | 278283 | RIS2 | Urban | LV Transformer SP6889-B RIS2 - Planned | 19 | 11 | 209 | 0.00020984 | 1.9076e-05
2012-08-15 | 278286 | RIS1 | Rural short | LV Transformer SP493050 RIS1 - Planned | 11 | 13 | 143 | 0.00041769 | 3.213e-05
2012-08-15 | 278287 | CRB25A | Rural short | LV Transformer SC1386008 CRB25A - Planned | 23 | 160 | 3680 | 0.010749 | 6.7181e-05
2012-08-15 | 278288 | MBG2 | Rural short | LV Transformer SP3839-B MBG2 - Planned | 3 | 191 | 573 | 0.0016737 | 8.7628e-06
2012-08-15 | 278289 | BTA1A | Urban | Feeder BTA1A, TMH2A - Planned | 17.5 | 26 | 455 | 0.00045683 | 1.757e-05
2012-08-15 | 278289 | TMH2A | Rural short | Feeder BTA1A, TMH2A - Planned | 1 | 26 | 26 | 7.5944e-05 | 2.9209e-06
2012-08-15 | 278290 | KBR6A | Rural short | Feeder KBR6A - Planned | 48.49 | 308 | 14934.92 | 0.043624 | 0.00014164
2012-08-15 | 278291 | BDT1 | Rural short | LV Transformer SP2382-E BDT1 - Planned | 3 | 152 | 456 | 0.0013319 | 8.7628e-06
2012-08-15 | 278292 | BLH10B | Urban | LV Transformer SP1821-E BLH10B - Planned | 11.5 | 309 | 3553.5 | 0.0035678 | 1.1546e-05
2012-08-15 | 278293 | TGW1 | Rural short | Feeder TGW1 - Planned | 20.86 | 361 | 7530.46 | 0.021996 | 6.093e-05
2012-08-15 | 278294 | LLY1 | Rural short | LV Transformer SP4659-B LLY1 - Planned | 1 | 225 | 225 | 0.00065721 | 2.9209e-06
2012-08-15 | 278295 | MLB4A | Urban | LV Transformer SP12348-A MLB4A - Planned | 79.38 | 267 | 21194.46 | 0.02128 | 7.9699e-05
2012-08-15 | 278296 | CBW6 | Rural short | LV Transformer SP4122-F CBW6 - Planned | 3 | 303 | 909 | 0.0026551 | 8.7628e-06
2012-08-15 | 278297 | SMF3A | Rural short | Feeder SMF3A - Planned | 33.94 | 402 | 13643.88 | 0.039853 | 9.9136e-05
2012-08-15 | 278298 | BWH13A | Rural short | Feeder BWH13A - Planned | 15.98 | 362 | 5784.76 | 0.016897 | 4.6676e-05
2012-08-15 | 278300 | BHD23A | Rural short | LV Transformer SP5705-F BHD23A - Planned | 20.425 | 492 | 10049.1 | 0.029353 | 5.966e-05
2012-08-15 | 278302 | TWT12A | Rural short | LV Transformer SP5490-A TWT12A - Planned | 3 | 170 | 510 | 0.0014897 | 8.7628e-06
2012-08-15 | 278303 | GYM7A | Rural short | LV Transformer SP3527-A GYM7A - Planned | 3.1165 | 312 | 972.348 | 0.0028402 | 9.103e-06
2012-08-15 | 278304 | HIS5A | Urban | LV Transformer SP5187-H HIS5A - Planned | 11.13 | 424 | 4719.12 | 0.0047381 | 1.1175e-05
2012-08-15 | 278305 | YTA1B | Rural short | LV Transformer SP758612 YTA1B - Planned | 1 | 255 | 255 | 0.00074483 | 2.9209e-06
2012-08-15 | 278306 | CNB21B | Urban | LV Transformer SP4033-E LHM5 - Planned | 1.96 | 297 | 582.12 | 0.00058446 | 1.9679e-06
2012-08-15 | 278306 | LHM5 | Rural short | LV Transformer SP4033-E LHM5 - Planned | 8.85 | 297 | 2628.45 | 0.0076775 | 2.585e-05
2012-08-15 | 278307 | LRE8A | Rural short | LV Transformer SP11244-A LRE8A - Planned | 3.91 | 274 | 1071.34 | 0.0031293 | 1.1421e-05
2012-08-15 | 278308 | MSV1 | Rural short | LV Transformer SP1919-D MSV1 - Planned | 1 | 70 | 70 | 0.00020446 | 2.9209e-06
2012-08-15 | 278310 | RIS1 | Rural short | LV Transformer SP2556-F RIS1 - Planned | 41.5 | 13 | 539.5 | 0.0015758 | 0.00012122
2012-08-15 | 278311 | RIS1 | Rural short | LV Transformer SP11509-E RIS1 - Planned | 10.5 | 22 | 231 | 0.00067473 | 3.067e-05
2012-08-16 | 278340 | RIS4 | Rural short | LV Transformer SP11707-A RIS4 - Planned | 4 | 21 | 84 | 0.00024533 | 1.1682e-05
2012-08-16 | 278341 | RIS4 | Rural short | LV Transformer SP8902-B RIS4 - Planned | 37 | 28 | 1036 | 0.0030257 | 0.00010806
2012-08-16 | 278342 | RIS4 | Rural short | LV Transformer SP13732-A RIS4 - Planned | 28 | 15 | 420 | 0.0012266 | 8.1776e-05
2012-08-16 | 278343 | RIS4 | Rural short | LV Transformer SP7930-C RIS4 - Planned | 13 | 12 | 156 | 0.00045561 | 3.7967e-05
2012-08-16 | 278345 | RIS1 | Rural short | LV Transformer SP3982-D RIS1 - Planned | 70 | 11 | 770 | 0.0022488 | 0.00020444
2012-08-16 | 278346 | RIS1 | Rural short | LV Transformer SP13752-B RIS1 - Planned | 26.5 | 12 | 318 | 0.00092874 | 7.7395e-05
2012-08-16 | 278347 | RIS1 | Rural short | LV Transformer SP11161-D RIS1 - Planned | 37.5 | 11 | 412.5 | 0.0012047 | 0.00010952
2012-08-16 | 278348 | RIS1 | Rural short | LV Transformer SP760850 RIS1 - Planned | 16 | 8 | 128 | 0.00037383 | 4.6729e-05
2012-08-16 | 278349 | RIS1 | Rural short | LV Transformer SP2563-F RIS1 - Planned | 36.5 | 12 | 438 | 0.0012792 | 0.0001066
2012-08-16 | 278350 | RIS1 | Rural short | LV Transformer SP9091-B RIS1 - Planned | 17 | 9 | 153 | 0.00044685 | 4.965e-05
2012-08-16 | 278352 | RIS4 | Rural short | LV Transformer SP233448 RIS4 - Planned | 9 | 5 | 45 | 0.00013143 | 2.6285e-05
2012-08-16 | 278361 | WSE5A | Rural short | LV Transformer SP3651-G WSE5A - Planned | 9 | 7 | 63 | 0.000184 | 2.6285e-05
2012-08-16 | 278363 | RIS4 | Rural short | LV Transformer SP9113-B RIS4 - Planned | 4 | 25 | 100 | 0.00029206 | 1.1682e-05
2012-08-16 | 278364 | RIS4 | Rural short | LV Transformer SP8904-B RIS4 - Planned | 15 | 22 | 330 | 0.00096379 | 4.3809e-05
2012-08-16 | 278365 | RIS4 | Rural short | LV Transformer SP16194-A RIS4 - Planned | 1 | 9 | 9 | 2.6285e-05 | 2.9206e-06
2012-08-16 | 278366 | RIS1 | Rural short | LV Transformer SP9024-A RIS1 - Planned | 5.395 | 21 | 113.295 | 0.00033089 | 1.5756e-05
2012-08-16 | 278367 | RIS1 | Rural short | LV Transformer SP9023-A RIS1 - Planned | 43 | 71 | 3053 | 0.0089165 | 0.00012558
2012-08-16 | 278368 | RIS1 | Rural short | LV Transformer SP15022-C RIS1 - Planned | 13 | 18 | 234 | 0.00068341 | 3.7967e-05
2012-08-16 | 278369 | RIS1 | Rural short | LV Transformer SP7420-C RIS1 - Planned | 20.5 | 25 | 512.5 | 0.0014968 | 5.9872e-05
2012-08-16 | 278370 | RIS4 | Rural short | LV Transformer SP6227-C RIS4 - Planned | 10.01 | 8 | 80.08 | 0.00023388 | 2.9235e-05
2012-08-16 | 278371 | RIS4 | Rural short | LV Transformer SP9011-B RIS4 - Planned | 20 | 16 | 320 | 0.00093458 | 5.8411e-05
2012-08-16 | 278372 | RIS4 | Rural short | LV Transformer SP6128-C RIS4 - Planned | 3 | 8 | 24 | 7.0094e-05 | 8.7617e-06
2012-08-16 | 278373 | RIS4 | Rural short | LV Transformer SP9019-C RIS4 - Planned | 16 | 12 | 192 | 0.00056075 | 4.6729e-05
2012-08-16 | 278374 | IBS1 | Rural short | LV Transformer SP773908 IBS1 - Planned | 12.5 | 13 | 162.5 | 0.00047459 | 3.6507e-05
2012-08-16 | 278375 | IBS1 | Rural short | LV Transformer SP11621-C IBS1 - Planned | 35.5 | 13 | 461.5 | 0.0013478 | 0.00010368
2012-08-16 | 278376 | MGP4 | Rural short | LV Transformer SP17435-E MGP4 - Planned | 1.6 | 195 | 312 | 0.00091122 | 4.6729e-06
2012-08-16 | 278377 | WSE3A | Rural short | Feeder WSE3A - Planned | 40.1 | 259 | 10385.9 | 0.030333 | 0.00011711
2012-08-16 | 278378 | CMY1 | Rural short | Feeder CMY1 - Planned | 10.309 | 356 | 3670.004 | 0.010719 | 3.0108e-05
2012-08-16 | 278386 | TGW1 | Rural short | Feeder TGW1 - Planned | 2 | 337 | 674 | 0.0019685 | 5.8411e-06
2012-08-16 | 278387 | CRB25A | Rural short | Feeder CRB25A - Planned | 49 | 396 | 19404 | 0.056671 | 0.00014311
2012-08-16 | 278400 | GGR1 | Rural short | Feeder GGR1 - Planned | 15.94 | 468 | 7459.92 | 0.021787 | 4.6554e-05
2012-08-16 | 278401 | GYS2A | Urban | LV Transformer SP4252-B GYS2A - Planned | 4 | 308 | 1232 | 0.0012369 | 4.016e-06
2012-08-16 | 278403 | PWC3 | Rural short | Feeder PWC3 - Planned | 43.45 | 330 | 14338.5 | 0.041877 | 0.0001269
2012-08-16 | 278404 | PWC3 | Rural short | LV Transformer SP17926-A PWC3 - Planned | 8.5 | 322 | 2737 | 0.0079936 | 2.4825e-05
2012-08-16 | 278405 | PWC3 | Rural short | LV Transformer SP2855-A PWC3 - Planned | 25.11 | 281 | 7055.91 | 0.020607 | 7.3336e-05
2012-08-16 | 278406 | AMR2 | Rural short | LV Transformer SP430-D AMR2 - Planned | 6 | 145 | 870 | 0.0025409 | 1.7523e-05
2012-08-16 | 278407 | RBY9A | Urban | LV Transformer SC1182-C RBY9A - Planned | 2.1 | 177 | 371.7 | 0.00037319 | 2.1084e-06
2012-08-16 | 278408 | IDY9B | Urban | LV Transformer SP3177-K IDY9B - Planned | 19.6 | 227 | 4449.2 | 0.004467 | 1.9678e-05
2012-08-16 | 278409 | KMR21A | Urban | LV Transformer SC6051-H KMR21A - Planned | 14.41 | 375 | 5403.75 | 0.0054253 | 1.4468e-05
2012-08-16 | 278410 | SFD6B | Urban | LV Transformer SP1540-K SFD6B - Planned | 6.08 | 441 | 2681.28 | 0.002692 | 6.1043e-06
2012-08-16 | 278411 | NMK23A | Urban | LV Transformer SC3162-L NMK23A - Planned | 1.5917 | 211 | 335.8487 | 0.00033719 | 1.5981e-06
2012-08-16 | 278412 | TWT11A | Rural short | LV Transformer SP6011-B TWT11A - Planned | 9.45 | 261 | 2466.45 | 0.0072034 | 2.7599e-05
2012-08-16 | 278413 | CBW12 | Urban | LV Transformer SP3631-E CBW12 - Planned | 6.5901 | 320 | 2108.832 | 0.0021173 | 6.6164e-06
2012-08-16 | 278414 | CMD5A | Urban | LV Transformer SP767-B CMD5A - Planned | 3.54 | 305 | 1079.7 | 0.001084 | 3.5541e-06
2012-08-16 | 278415 | BHD44A | Urban | LV Transformer SP3389-D BHD44A - Planned | 13.9005 | 200 | 2780.1 | 0.0027912 | 1.3956e-05
2012-08-16 | 278416 | MTB13A | Rural short | LV Transformer SP6581-D MTB13A - Planned | 8.05 | 314 | 2527.7 | 0.0073823 | 2.3511e-05
2012-08-16 | 278418 | HDA11A | Urban | LV Transformer SP1804-I HDA3A - Planned | 5.9751 | 302 | 1804.4802 | 0.0018117 | 5.999e-06
2012-08-16 | 278418 | HDA3A | Urban | LV Transformer SP1804-I HDA3A - Planned | 20.85 | 302 | 6296.7 | 0.0063219 | 2.0933e-05
2012-08-16 | 278420 | NSW26 | Urban | LV Transformer SP5435-D WRG8A - Planned | 17.58 | 166 | 2918.28 | 0.0029299 | 1.765e-05
2012-08-16 | 278420 | WRG8A | Urban | LV Transformer SP5435-D WRG8A - Planned | 8.4 | 166 | 1394.4 | 0.0014 | 8.4336e-06
2012-08-16 | 278421 | BLB4A | Urban | LV Transformer SP17984-F BLB4A - Planned | 5.9 | 42 | 247.8 | 0.00024879 | 5.9236e-06
2012-08-16 | 278422 | MTG11A | Urban | LV Transformer SP494008-A MTG11A - Planned | 16.2495 | 286 | 4647.357 | 0.0046659 | 1.6314e-05
2012-08-16 | 278423 | UMG1B | Urban | LV Transformer SC4905-E UMG1B - Planned | 15.2988 | 341 | 5216.8908 | 0.0052377 | 1.536e-05
2012-08-16 | 278430 | DRA9 | Urban | LV Transformer SC1433452 DRA9 - Planned | 9.198 | 181 | 1664.838 | 0.0016715 | 9.2348e-06
2012-08-16 | 278441 | RIS4 | Rural short | LV Transformer SP9014-B RIS4 - Planned | 4 | 19 | 76 | 0.00022196 | 1.1682e-05
2012-08-16 | 278442 | RIS4 | Rural short | LV Transformer SP9020-C RIS4 - Planned | 21 | 15 | 315 | 0.00091998 | 6.1332e-05
2012-08-16 | 278443 | RIS4 | Rural short | LV Transformer SP6199-C RIS4 - Planned | 13.95 | 18 | 251.1 | 0.00073336 | 4.0742e-05
2012-08-16 | 278444 | RIS4 | Rural short | LV Transformer SP9012-B RIS4 - Planned | 3 | 10 | 30 | 8.7617e-05 | 8.7617e-06
2012-08-16 | 278445 | RIS4 | Rural short | LV Transformer SP763444 RIS4 - Planned | 21.5 | 20 | 430 | 0.0012558 | 6.2792e-05
2012-08-16 | 278446 | RIS4 | Rural short | LV Transformer SP9027-B RIS4 - Planned | 30.5 | 30 | 915 | 0.0026723 | 8.9077e-05
2012-08-16 | 278447 | RIS4 | Rural short | LV Transformer SP7924-B RIS4 - Planned | 50.5 | 15 | 757.5 | 0.0022123 | 0.00014749
2012-08-16 | 278448 | RIS4 | Rural short | LV Transformer SP9042-B RIS4 - Planned | 4 | 25 | 100 | 0.00029206 | 1.1682e-05
2012-08-16 | 278507 | RPN4A | Rural short | LV Transformer SP3874-D RPN4A - Planned | 1 | 279 | 279 | 0.00081484 | 2.9206e-06
2012-08-17 | 278429 | DRA9 | Urban | LV Transformer SC515069 DRA9 - Planned | 1.066 | 101 | 107.666 | 0.00010809 | 1.0702e-06
2012-08-17 | 278460 | KBN5A | Rural short | LV Transformer SP3539-E KBN5A - Planned | 13.5 | 250 | 3375 | 0.0098558 | 3.9423e-05
2012-08-17 | 278462 | TGW1 | Rural short | Feeder TGW1 - Planned | 65 | 305 | 19825 | 0.057894 | 0.00018982
2012-08-17 | 278468 | JBB16A | Rural short | Feeder JBB16A - Planned | 15 | 283 | 4245 | 0.012396 | 4.3804e-05
2012-08-17 | 278469 | NRG16A | Rural short | Feeder NRG16A - Planned | 28 | 239 | 6692 | 0.019542 | 8.1767e-05
2012-08-17 | 278470 | MTB15A | Rural short | Feeder MTB15A - Planned | 10.4 | 246 | 2558.4 | 0.0074711 | 3.037e-05
2012-08-17 | 278471 | FDS1 | Rural short | Feeder FDS1 - Planned | 28.5 | 369 | 10516.5 | 0.030711 | 8.3227e-05
2012-08-17 | 278472 | CPD1 | Rural short | Feeder CPD1 - Planned | 25 | 385 | 9625 | 0.028107 | 7.3006e-05
2012-08-17 | 278473 | KBN5A | Rural short | LV Transformer SP2501-G KBN5A - Planned | 1 | 240 | 240 | 0.00070086 | 2.9202e-06
2012-08-17 | 278475 | GYN7A | Rural short | Feeder GYN7A - Planned | 34.79 | 366 | 12733.14 | 0.037184 | 0.00010159
2012-08-17 | 278476 | EMD2 | Rural short | Feeder EMD2 - Planned | 26.99 | 303 | 8177.97 | 0.023882 | 7.8817e-05
2012-08-17 | 278477 | MTG4B | Urban | LV Transformer SP6411-D MTG4B - Planned | 16.345 | 145 | 2370.025 | 0.0023794 | 1.641e-05
2012-08-17 | 278478 | TRG2A | Urban | LV Transformer SC2218-O TRG2A - Planned | 19.95 | 226 | 4508.7 | 0.0045266 | 2.0029e-05
2012-08-17 | 278479 | AMR2 | Rural short | LV Transformer SP425-D AMR2 - Planned | 7.41 | 190 | 1407.9 | 0.0041114 | 2.1639e-05
2012-08-17 | 278480 | PWC3 | Rural short | LV Transformer SP3806-B PWC3 - Planned | 6.095 | 94 | 572.93 | 0.0016731 | 1.7799e-05
2012-08-17 | 278481 | EMD3 | Rural short | LV Transformer SP2241-D EMD3 - Planned | 8.01 | 343 | 2747.43 | 0.0080231 | 2.3391e-05
2012-08-17 | 278482 | SBH4 | Urban | LV Transformer SP3634-E SBH4 - Planned | 33.3 | 240 | 7992 | 0.0080237 | 3.3432e-05
2012-08-17 | 278483 | BRT5 | Urban | LV Transformer SP1207-P BRT5 - Planned | 7.375 | 135 | 995.625 | 0.00099958 | 7.4043e-06
2012-08-17 | 278484 | AHD5 | Urban | LV Transformer SP4060-A AHD5 - Planned | 35.775 | 295 | 10553.625 | 0.010596 | 3.5917e-05
2012-08-17 | 278485 | CMD5A | Urban | LV Transformer SP3762-B CMD5A - Planned | 10 | 181 | 1810 | 0.0018172 | 1.004e-05
2012-08-17 | 278486 | CDRSPD12 | Urban | LV Transformer SP1428-I CDRSPD12 - Planned | 90.56 | 283 | 25628.48 | 0.02573 | 9.092e-05
2012-08-17 | 278487 | BRT6 | Urban | LV Transformer SP3975-G BRT6 - Planned | 18.9 | 342 | 6463.8 | 0.0064895 | 1.8975e-05
2012-08-17 | 278487 | BRT8 | Urban | LV Transformer SP3975-G BRT6 - Planned | 12.5 | 342 | 4275 | 0.004292 | 1.255e-05
2012-08-17 | 278488 | YTA26A | Urban | LV Transformer SC2393-D YTA26A - Planned | 11.55 | 121 | 1397.55 | 0.0014031 | 1.1596e-05
2012-08-17 | 278489 | WNM5 | Urban | LV Transformer SP6708-G WNM5 - Planned | 14.625 | 42 | 614.25 | 0.00061669 | 1.4683e-05
2012-08-17 | 278490 | JBB13A | Rural short | LV Transformer SP4857-E JBB13A - Planned | 14 | 245 | 3430 | 0.010016 | 4.0883e-05
2012-08-17 | 278491 | UMG15B | Urban | LV Transformer SP2201-J UMG15B - Planned | 20.88 | 75 | 1566 | 0.0015722 | 2.0963e-05
2012-08-17 | 278492 | LTN8 | Rural short | LV Transformer SP11275-D LTN8 - Planned | 3.015 | 437 | 1317.555 | 0.0038476 | 8.8045e-06
2012-08-17 | 278493 | HPE3A | Urban | LV Transformer SC3657-F HPE3A - Planned | 30.6373 | 347 | 10631.1431 | 0.010673 | 3.0759e-05
2012-08-17 | 278494 | HPK8A | Urban | LV Transformer SP1337-K HPK8A - Planned | 43.9343 | 458 | 20121.9094 | 0.020202 | 4.4109e-05
2012-08-17 | 278495 | WRD22B | Urban | LV Transformer SG4488-G WRD22B - Planned | 52.02 | 144 | 7490.88 | 0.0075206 | 5.2227e-05
2012-08-17 | 278496 | TMH15A | Urban | LV Transformer SP72731-A TMH15A - Planned | 20.355 | 256 | 5210.88 | 0.0052316 | 2.0436e-05
2012-08-17 | 278502 | BDA13A | Urban | LV Transformer SC1894-K BDA13A - Planned | 10.835 | 272 | 2947.12 | 0.0029588 | 1.0878e-05
2012-08-18 | 278508 | WCL11A | Urban | LV Transformer SG1734836 WCL11A - Planned | 1 | 98 | 98 | 9.8389e-05 | 1.004e-06
2012-08-18 | 278509 | NGE13 | Urban | LV Transformer SG2446-H NGE13 - Planned | 1 | 270 | 270 | 0.00027107 | 1.004e-06
2012-08-18 | 278511 | FDS3 | Rural short | Feeder FDS3 - Planned | 63.01 | 204 | 12854.04 | 0.03753 | 0.00018397
2012-08-18 | 278513 | WSO15A | Urban | LV Transformer SC6632-G WSO15A - Planned | 16.08 | 102 | 1640.16 | 0.0016467 | 1.6144e-05
2012-08-18 | 278514 | WCL11A | Urban | LV Transformer SG738826 WCL11A - Planned | 1.5 | 82 | 123 | 0.00012349 | 1.506e-06
2012-08-18 | 278515 | NSD30B | Urban | LV Transformer SP16062-H NSD30B - Planned | 5 | 580 | 2900 | 0.0029115 | 5.0198e-06
2012-08-18 | 278531 | NDH9 | Urban | LV Transformer SP481884 NDH9 - Planned | 2.93 | 416 | 1218.88 | 0.0012237 | 2.9416e-06
2012-08-19 | 278520 | TWG10 | Urban | LV Transformer SG7082-H TWG10 - Planned | 1 | 241 | 241 | 0.00024195 | 1.004e-06
2012-08-19 | 278524 | WCL17A | Urban | LV Transformer SP11603-H WCL17A - Planned | 17.5 | 293 | 5127.5 | 0.0051478 | 1.7569e-05
2012-08-19 | 278525 | NGE4A | Urban | Feeder NGE4A - Planned | 4 | 377 | 1508 | 0.001514 | 4.0159e-06
2012-08-19 | 278527 | CRBTHP14 | Urban | LV Transformer SP5641-E CRBTHP14 - Planned | 24.08 | 553 | 13316.24 | 0.013369 | 2.4175e-05
2012-08-19 | 278528 | SFD4 | Urban | LV Transformer SC6781-J SFD4 - Planned | 12.7621 | 189 | 2412.0369 | 0.0024216 | 1.2813e-05
2012-08-19 | 278529 | CLD16A | Urban | LV Transformer SP2996-B CLD16A - Planned | 17.425 | 264 | 4600.2 | 0.0046184 | 1.7494e-05
2012-08-19 | 278530 | SPE9 | Urban | LV Transformer SC1513000 SPE9 - Planned | 2.09 | 170 | 355.3 | 0.00035671 | 2.0983e-06
2012-08-19 | 278532 | ACR3A | Urban | LV Transformer SC619301 ACR3A - Planned | 2.0961 | 46 | 96.4206 | 9.6803e-05 | 2.1044e-06
2012-08-19 | 278533 | NRA5A | Rural short | LV Transformer SP37847-B NRA5A - Planned | 12.83 | 290 | 3720.7 | 0.010861 | 3.7453e-05
2012-08-19 | 278534 | NGE13 | Urban | LV Transformer SC581869 NGE13 - Planned | 7.1299 | 166 | 1183.5634 | 0.0011883 | 7.1582e-06
2012-08-19 | 278535 | SPE9 | Urban | LV Transformer SP581134 SPE9 - Planned | 1.04 | 50 | 52 | 5.2206e-05 | 1.0441e-06
2012-08-19 | 278536 | EMP2A | Urban | LV Transformer SC784727 EMP2A - Planned | 5.12 | 521 | 2667.52 | 0.0026781 | 5.1403e-06
2012-08-19 | 278537 | WRG8A | Urban | LV Transformer SP813805 WRG8A - Planned | 3.38 | 407 | 1375.66 | 0.0013811 | 3.3934e-06
2012-08-20 | 278560 | GGR1 | Rural short | LV Transformer SP11077-B GGR1 - Planned | 1 | 159 | 159 | 0.00046407 | 2.9187e-06
2012-08-20 | 278561 | KSN7 | Rural short | LV Transformer SP1017-H KSN7 - Planned | 7 | 195 | 1365 | 0.003984 | 2.0431e-05
2012-08-20 | 278565 | MLY4 | Rural short | LV Transformer SP4417-B MLY4 - Planned | 24.38 | 210 | 5119.8 | 0.014943 | 7.1158e-05
2012-08-20 | 278566 | BWH16A | Rural short | LV Transformer SP6636-C BWH16A - Planned | 32 | 36 | 1152 | 0.0033623 | 9.3398e-05
2012-08-20 | 278567 | TGW3 | Rural short | Feeder TGW3 - Planned | 43 | 342 | 14706 | 0.042922 | 0.0001255
2012-08-20 | 278568 | GBN3 | Rural short | LV Transformer SP3528-B GBN3 - Planned | 1 | 91 | 91 | 0.0002656 | 2.9187e-06
2012-08-20 | 278570 | ARLSNT3 | Urban | Feeder ARLSNT3 - Planned | 4 | 457 | 1828 | 0.0018352 | 4.0159e-06
2012-08-20 | 278572 | AHL6A | Urban | LV Transformer SC4032-L AHL6A - Planned | 2.2268 | 333 | 741.5244 | 0.00074446 | 2.2356e-06
2012-08-20 | 278573 | PGN1B | Rural short | LV Transformer SP1566-A PGN1B - Planned | 3.5925 | 163 | 585.5775 | 0.0017091 | 1.0485e-05
2012-08-20 | 278574 | MTB1B | Rural short | LV Transformer SP5033-E MTB1B - Planned | 23.04 | 342 | 7879.68 | 0.022998 | 6.7247e-05
2012-08-20 | 278575 | MAI14 | Urban | LV Transformer SP8864-C MAI14 - Planned | 29.415 | 240 | 7059.6 | 0.0070876 | 2.9532e-05
2012-08-20 | 278576 | CRB24B | Urban | LV Transformer SP11807-D CRB24B - Planned | 1.8075 | 286 | 516.945 | 0.00051899 | 1.8147e-06
2012-08-20 | 278577 | BGY5A | Rural short | LV Transformer SP4722-E BGY5A - Planned | 3.08 | 348 | 1071.84 | 0.0031284 | 8.9896e-06
2012-08-20 | 278578 | NDH6 | Urban | LV Transformer SP4282-H NDH6 - Planned | 7.115 | 325 | 2312.375 | 0.0023215 | 7.1432e-06
2012-08-20 | 278579 | BGY15A | Urban | LV Transformer SP8626-B BGY15A - Planned | 14.99 | 255 | 3822.45 | 0.0038376 | 1.5049e-05
2012-08-20 | 278580 | HPK8A | Urban | LV Transformer SP1568-H HPK8A - Planned | 16.1694 | 295 | 4769.973 | 0.0047889 | 1.6233e-05
2012-08-20 | 278582 | CPD2A | Rural short | LV Transformer SP1811-D CPD2A - Planned | 2.345 | 233 | 546.385 | 0.0015947 | 6.8443e-06
2012-08-20 | 278586 | TGP5B | Urban | LV Transformer SP22546-E WNM1A - Planned | 16.76 | 350 | 5866 | 0.0058892 | 1.6826e-05
2012-08-20 | 278586 | WNM1A | Urban | LV Transformer SP22546-E WNM1A - Planned | 25.2 | 350 | 8820 | 0.0088549 | 2.53e-05
2012-08-21 | 278600 | BDT1 | Rural short | LV Transformer SP5598-D BDT1 - Planned | 9 | 120 | 1080 | 0.0031517 | 2.6264e-05
2012-08-21 | 278602 | FDS1 | Rural short | LV Transformer SP743620 FDS1 - Planned | 1 | 180 | 180 | 0.00052528 | 2.9182e-06
2012-08-21 | 278603 | KCY2 | Rural short | Feeder KCY2 - Planned | 51.35 | 158 | 8113.3 | 0.023676 | 0.00014985
2012-08-21 | 278604 | AMR3 | Rural short | Feeder AMR3 - Planned | 29.55 | 195 | 5762.25 | 0.016815 | 8.6233e-05
2012-08-21 | 278605 | EMD3 | Rural short | Feeder EMD3 - Planned | 40.805 | 195 | 7956.975 | 0.02322 | 0.00011908
2012-08-21 | 278607 | NRA16A | Rural short | LV Transformer SP3643-F NRA16A - Planned | 10.5 | 228 | 2394 | 0.0069862 | 3.0641e-05
2012-08-21 | 278608 | NRA16A | Rural short | LV Transformer SP1369-E NRA16A - Planned | 15.51 | 266 | 4125.66 | 0.01204 | 4.5261e-05
2012-08-21 | 278609 | JBB16A | Rural short | LV Transformer SP7360-C JBB16A - Planned | 14.52 | 331 | 4806.12 | 0.014025 | 4.2372e-05
2012-08-21 | 278611 | LRE8A | Rural short | Feeder LRE8A - Planned | 12 | 374 | 4488 | 0.013097 | 3.5018e-05
2012-08-21 | 278612 | LLY4 | Rural short | Feeder LLY4 - Planned | 1 | 445 | 445 | 0.0012986 | 2.9182e-06
2012-08-21 | 278613 | WSE3A | Rural short | Feeder WSE3A - Planned | 62.757 | 465 | 29182.005 | 0.085159 | 0.00018314
2012-08-21 | 278614 | CRM16A | Rural short | LV Transformer SP56234-B CRM16A - Planned | 2.9697 | 298 | 884.9706 | 0.0025825 | 8.6662e-06
2012-08-21 | 278615 | BKD3A | Urban | LV Transformer SC1487432 BKD3A - Planned | 10.08 | 209 | 2106.72 | 0.0021151 | 1.012e-05
2012-08-21 | 278616 | SHW4 | Urban | LV Transformer SP2539-I SHW4 - Planned | 7.81 | 185 | 1444.85 | 0.0014506 | 7.841e-06
2012-08-21 | 278617 | MLS12B | Urban | LV Transformer SC2500-L MLS12B - Planned | 8.1 | 377 | 3053.7 | 0.0030658 | 8.1321e-06
2012-08-21 | 278618 | NBR5 | Rural short | LV Transformer SP373-A NBR5 - Planned | 14.7 | 145 | 2131.5 | 0.0062202 | 4.2898e-05
2012-08-21 | 278619 | PGN1B | Rural short | LV Transformer SP2152-B PGN1B - Planned | 11.0997 | 161 | 1787.0517 | 0.005215 | 3.2391e-05
2012-08-21 | 278620 | KWA4A | Urban | LV Transformer SC456698 KWA4A - Planned | 203.04 | 60 | 12182.4 | 0.012231 | 0.00020385
2012-08-21 | 278621 | CRB25A | Rural short | LV Transformer SP3004-E CRB25A - Planned | 1 | 262 | 262 | 0.00076457 | 2.9182e-06
2012-08-21 | 278622 | BDL2 | Urban | LV Transformer SP4213-F MDR33A - Planned | 2.92 | 382 | 1115.44 | 0.0011199 | 2.9316e-06
2012-08-21 | 278622 | MDR33A | Urban | LV Transformer SP4213-F MDR33A - Planned | 3.96 | 382 | 1512.72 | 0.0015187 | 3.9757e-06
2012-08-21 | 278623 | BHD35A | Rural short | LV Transformer SP5088-H BHD35A - Planned | 14.06 | 50 | 703 | 0.0020515 | 4.103e-05
2012-08-21 | 278624 | BHD44A | Urban | LV Transformer SP1065-I BHD44A - Planned | 4.4166 | 382 | 1687.1412 | 0.0016938 | 4.4341e-06
2012-08-21 | 278626 | DRD5A | Urban | LV Transformer SP2228-G RCF1A - Planned | 0.9425 | 275 | 259.1875 | 0.00026022 | 9.4624e-07
2012-08-21 | 278626 | RCF1A | Urban | LV Transformer SP2228-G RCF1A - Planned | 6.6399 | 275 | 1825.9725 | 0.0018332 | 6.6662e-06
2012-08-21 | 278627 | LTN3 | Urban | LV Transformer SP3181-D LTN3 - Planned | 5.9464 | 343 | 2039.6152 | 0.0020477 | 5.97e-06
2012-08-21 | 278628 | HDA13A | Urban | LV Transformer SP1853-I HDA3A - Planned | 1.18 | 336 | 396.48 | 0.00039805 | 1.1847e-06
2012-08-21 | 278628 | HDA3A | Urban | LV Transformer SP1853-I HDA3A - Planned | 27.905 | 336 | 9376.08 | 0.0094133 | 2.8016e-05
2012-08-21 | 278629 | UMG12A | Urban | LV Transformer SC4057-I UMG12A - Planned | 5.11 | 260 | 1328.6 | 0.0013339 | 5.1303e-06
2012-08-21 | 278630 | JBB16A | Rural short | LV Transformer SP1194-F JBB16A - Planned | 10 | 303 | 3030 | 0.0088422 | 2.9182e-05
2012-08-21 | 278631 | HPE3A | Urban | LV Transformer SP274-M HPE3A - Planned | 25.185 | 260 | 6548.1 | 0.0065741 | 2.5285e-05
2012-08-21 | 278632 | HPK8A | Urban | LV Transformer SP492472 HPK8A - Planned | 32.3416 | 322 | 10413.9952 | 0.010455 | 3.247e-05
2012-08-21 | 278633 | SBY4 | Urban | LV Transformer SC1036892 SBY4 - Planned | 46.8384 | 229 | 10725.9936 | 0.010769 | 4.7024e-05
2012-08-21 | 278634 | BVL10A | Urban | LV Transformer SP8572-A BVL10A - Planned | 3.7366 | 76 | 283.9816 | 0.00028511 | 3.7514e-06
2012-08-21 | 278635 | WHO2 | Rural short | LV Transformer SP4107-A WHO2 - Planned | 3.12 | 207 | 645.84 | 0.0018847 | 9.1048e-06
2012-08-21 | 278636 | WMD8B | Rural short | Feeder WMD8B - Planned | 75.49 | 462 | 34876.38 | 0.10178 | 0.0002203
2012-08-21 | 278638 | LBH1B | Rural short | Feeder LBH1B - Planned | 79.2372 | 447 | 35419.0284 | 0.10336 | 0.00023123
2012-08-21 | 278639 | IBL2 | Rural short | Feeder IBL2 - Planned | 77.585 | 386 | 29947.81 | 0.087394 | 0.00022641
2012-08-22 | 278661 | SMF3A | Rural short | LV Transformer SP532-D SMF3A - Planned | 11 | 208 | 2288 | 0.0066757 | 3.2095e-05
2012-08-22 | 278662 | BNH6A | Rural short | Feeder BNH6A - Planned | 29 | 258 | 7482 | 0.02183 | 8.4613e-05
2012-08-22 | 278663 | MGL8 | Urban | LV Transformer SC691439 MGL8 - Planned | 64 | 267 | 17088 | 0.017156 | 6.4254e-05
2012-08-22 | 278664 | RWD1 | Rural short | LV Transformer SP763243 RWD1 - Planned | 3 | 390 | 1170 | 0.0034137 | 8.7531e-06
2012-08-22 | 278666 | WMD10A | Urban | LV Transformer SP5158-A WMD10A - Planned | 56.35 | 400 | 22540 | 0.022629 | 5.6573e-05
2012-08-22 | 278667 | PWC4 | Rural short | Feeder PWC4 - Planned | 30.36 | 394 | 11961.84 | 0.034901 | 8.8582e-05
2012-08-22 | 278668 | WMR1 | Rural short | LV Transformer SP17042-D WMR1 - Planned | 4 | 326 | 1304 | 0.0038047 | 1.1671e-05
2012-08-22 | 278669 | GBN3 | Rural short | Feeder GBN3 - Planned | 71.415 | 313 | 22352.895 | 0.065219 | 0.00020837
2012-08-22 | 278670 | WMD6A | Urban | Feeder WMD6A - Planned | 0.528 | 133 | 70.224 | 7.0502e-05 | 5.3009e-07
2012-08-22 | 278671 | LBH3A | Rural short | LV Transformer SP3991-B LBH3A - Planned | 20.9 | 39 | 815.1 | 0.0023782 | 6.098e-05
2012-08-22 | 278672 | SPO11A | Urban | Feeder SPO11A - Planned | 223 | 399 | 88977 | 0.08933 | 0.00022388
2012-08-22 | 278673 | BMT1 | Rural short | Feeder BMT1 - Planned | 11.99 | 338 | 4052.62 | 0.011824 | 3.4983e-05
2012-08-22 | 278674 | LLY4 | Rural short | Feeder LLY4 - Planned | 3 | 475 | 1425 | 0.0041577 | 8.7531e-06
2012-08-22 | 278676 | OXL10A | Urban | LV Transformer SP13931-E OXL10A - Planned | 12.425 | 189 | 2348.325 | 0.0023576 | 1.2474e-05
2012-08-22 | 278677 | AGE10 | Urban | LV Transformer SP733335 AGE10 - Planned | 19.6392 | 355 | 6971.916 | 0.0069996 | 1.9717e-05
2012-08-22 | 278678 | KRA7 | Urban | LV Transformer SP17443-H KRA7 - Planned | 1.1883 | 282 | 335.1006 | 0.00033643 | 1.193e-06
2012-08-22 | 278679 | BHD35A | Rural short | LV Transformer SP5818-D BHD35A - Planned | 8.06 | 176 | 1418.56 | 0.0041389 | 2.3517e-05
2012-08-22 | 278680 | NDH7 | Urban | LV Transformer SC5302-H NDH7 - Planned | 4.875 | 243 | 1184.625 | 0.0011893 | 4.8943e-06
2012-08-22 | 278681 | SBH11 | Urban | LV Transformer SP16791-C SBH11 - Planned | 16.77 | 238 | 3991.26 | 0.0040071 | 1.6837e-05
2012-08-22 | 278682 | BRT8 | Urban | LV Transformer SP38983 BRT8 - Planned | 18.875 | 251 | 4737.625 | 0.0047564 | 1.895e-05
2012-08-22 | 278683 | SBH6 | Urban | LV Transformer SP76-F SBH6 - Planned | 6.4915 | 258 | 1674.807 | 0.0016814 | 6.5172e-06
2012-08-22 | 278684 | NDH6 | Urban | LV Transformer SP1936-I NDH6 - Planned | 7.8536 | 305 | 2395.348 | 0.0024048 | 7.8847e-06
2012-08-22 | 278685 | HPE3A | Urban | LV Transformer SP1710-M HPE3A - Planned | 17.16 | 211 | 3620.76 | 0.0036351 | 1.7228e-05
2012-08-22 | 278686 | WNM5 | Urban | LV Transformer SP821-N WNM5 - Planned | 23.1 | 295 | 6814.5 | 0.0068415 | 2.3192e-05
2012-08-22 | 278688 | CRB25A | Rural short | Feeder CRB25A - Planned | 17 | 601 | 10217 | 0.02981 | 4.9601e-05
2012-08-22 | 278723 | NMK18 | Urban | LV Transformer SP1963-N NMK18 - Planned | 2.5167 | 346 | 870.7782 | 0.00087423 | 2.5267e-06
2012-08-22 | 278832 | GYS3A | Rural short | LV Transformer SP83-B GYS3A - Planned | 4 | 269 | 1076 | 0.0031395 | 1.1671e-05
2012-08-22 | 278833 | RWD1 | Rural short | LV Transformer SP31307-B RWD1 - Planned | 3 | 17 | 51 | 0.0001488 | 8.7531e-06
2012-08-22 | 278834 | CPD2A | Rural short | Feeder CPD2A - Planned | 7.5 | 390 | 2925 | 0.0085343 | 2.1883e-05
2012-08-23 | 278696 | BNH5A | Rural short | Feeder BNH5A - Planned | 8.92 | 192 | 1712.64 | 0.004996 | 2.6021e-05
2012-08-23 | 278698 | UPC1 | Rural short | LV Transformer SP8735-D UPC1 - Planned | 13 | 176 | 2288 | 0.0066744 | 3.7923e-05
2012-08-23 | 278699 | SMF3A | Rural short | Feeder SMF3A - Planned | 13.9 | 254 | 3530.6 | 0.010299 | 4.0548e-05
2012-08-23 | 278700 | TGW1 | Rural short | Feeder TGW1 - Planned | 9.1973 | 205 | 1885.4465 | 0.0055001 | 2.683e-05
2012-08-23 | 278701 | BTN2 | Rural short | LV Transformer SP6669-E BTN2 - Planned | 18.05 | 270 | 4873.5 | 0.014217 | 5.2654e-05
2012-08-23 | 278702 | MDR33A | Urban | LV Transformer SC375-I MDR33A - Planned | 46 | 280 | 12880 | 0.012931 | 4.6183e-05
2012-08-23 | 278703 | YTA2B | Rural short | Feeder YTA2B - Planned | 424.83 | 177 | 75194.91 | 0.21935 | 0.0012393
2012-08-23 | 278720 | TBV4 | Rural short | Feeder TBV4 - Planned | 61.15 | 317 | 19384.55 | 0.056547 | 0.00017838
2012-08-23 | 278722 | GAP9A | Urban | LV Transformer SP2547-M GAP9A - Planned | 8.22 | 216 | 1775.52 | 0.0017826 | 8.2527e-06
2012-08-23 | 278724 | THL3 | Rural short | Feeder THL3 - Planned | 1 | 430 | 430 | 0.0012544 | 2.9171e-06
2012-08-23 | 278725 | BMT1 | Rural short | LV Transformer SP7589-B BMT1 - Planned | 17.39 | 278 | 4834.42 | 0.014103 | 5.0729e-05
2012-08-23 | 278726 | CBT13A | Urban | LV Transformer SP9269-E CBT13A - Planned | 1.02 | 266 | 271.32 | 0.0002724 | 1.0241e-06
2012-08-23 | 278727 | NBR8 | Rural short | LV Transformer SP118389-A NBR8 - Planned | 0.99 | 97 | 96.03 | 0.00028013 | 2.888e-06
2012-08-23 | 278728 | MLY3 | Rural short | LV Transformer SP1763-C MLY3 - Planned | 4.94 | 367 | 1812.98 | 0.0052887 | 1.4411e-05
2012-08-23 | 278729 | YDA3A | Rural short | LV Transformer SP148036 YDA3A - Planned | 3 | 236 | 708 | 0.0020653 | 8.7514e-06
2012-08-23 | 278730 | GGR1 | Rural short | Feeder GGR1 - Planned | 31.439 | 510 | 16033.89 | 0.046773 | 9.1712e-05
2012-08-23 | 278731 | CRB25A | Rural short | Feeder CRB25A - Planned | 37.21 | 441 | 16409.61 | 0.047869 | 0.00010855
2012-08-23 | 278733 | MAI14 | Urban | LV Transformer SP2220-H MAI14 - Planned | 10.56 | 270 | 2851.2 | 0.0028625 | 1.0602e-05
2012-08-23 | 278735 | HDA3A | Urban | LV Transformer SP2760-J HDA3A - Planned | 16.485 | 240 | 3956.4 | 0.0039721 | 1.655e-05
2012-08-23 | 278736 | ZMR10 | Urban | LV Transformer SP18-Q ZMR10 - Planned | 17.07 | 238 | 4062.66 | 0.0040788 | 1.7138e-05
2012-08-23 | 278737 | HPE3A | Urban | LV Transformer SP1710-M HPE3A - Planned | 13.725 | 163 | 2237.175 | 0.0022461 | 1.378e-05
2012-08-23 | 278738 | NDH6 | Urban | LV Transformer SP6105-G NDH6 - Planned | 8.52 | 312 | 2658.24 | 0.0026688 | 8.5539e-06
2012-08-23 | 278739 | RLB15A | Urban | LV Transformer SP4344-E RLB15A - Planned | 2.88 | 222 | 639.36 | 0.0006419 | 2.8914e-06
2012-08-23 | 278741 | WRG15A | Urban | LV Transformer SP3249-E WRG15A - Planned | 21.685 | 285 | 6180.225 | 0.0062048 | 2.1771e-05
2012-08-23 | 278742 | THL3 | Rural short | LV Transformer SP4765-B THL3 - Planned | 3.375 | 368 | 1242 | 0.0036231 | 9.8453e-06
2012-08-23 | 278743 | WSE3A | Rural short | Feeder WSE3A - Planned | 6.9 | 378 | 2608.2 | 0.0076085 | 2.0128e-05
2012-08-23 | 278744 | THL3 | Rural short | LV Transformer SP1845-C THL3 - Planned | 3.105 | 119 | 369.495 | 0.0010779 | 9.0577e-06
2012-08-23 | 278745 | LTN6 | Urban | LV Transformer SP3259-E LTN6 - Planned | 4.98 | 375 | 1867.5 | 0.0018749 | 4.9998e-06
2012-08-23 | 278746 | MLT15B | Urban | LV Transformer SP6199-E MLT15B - Planned | 37.651 | 293 | 11031.743 | 0.011076 | 3.7801e-05
2012-08-23 | 278746 | MLT2B | Urban | LV Transformer SP6199-E MLT15B - Planned | 4.74 | 293 | 1388.82 | 0.0013943 | 4.7588e-06
2012-08-23 | 278747 | TWG13A | Urban | LV Transformer SP1043-N TWG13A - Planned | 2.905 | 395 | 1147.475 | 0.001152 | 2.9165e-06
2012-08-23 | 278748 | CRY6A | Rural short | Feeder CRY6A - Planned | 5 | 365 | 1825 | 0.0053238 | 1.4586e-05
2012-08-23 | 278749 | GYS5A | Rural short | LV Transformer SP6004-C GYS5A - Planned | 4 | 166 | 664 | 0.001937 | 1.1669e-05
2012-08-23 | 278750 | MLY3 | Rural short | LV Transformer SP36301-A MLY3 - Planned | 0.4 | 360 | 144 | 0.00042007 | 1.1669e-06
2012-08-23 | 278751 | TCB3 | Rural short | LV Transformer SP14201-B TCB3 - Planned | 77.5 | 111 | 8602.5 | 0.025095 | 0.00022608
2012-08-23 | 278752 | AMR3 | Rural short | LV Transformer SP2329-F AMR3 - Planned | 4 | 142 | 568 | 0.0016569 | 1.1669e-05
2012-08-24 | 278774 | IPL3 | Rural short | LV Transformer SP777083 IPL3 - Planned | 4 | 149 | 596 | 0.0017382 | 1.1666e-05
2012-08-24 | 278778 | IPL1 | Rural short | Feeder IPL1 - Planned | 2 | 205 | 410 | 0.0011958 | 5.833e-06
2012-08-24 | 278790 | BRD8A | Rural short | Feeder BRD8A - Planned | 44.56 | 200 | 8912 | 0.025992 | 0.00012996
2012-08-24 | 278793 | BNH5A | Rural short | Feeder BNH5A - Planned | 14.01 | 260 | 3642.6 | 0.010624 | 4.086e-05
2012-08-24 | 278795 | MLB6A | Rural short | Feeder MLB6A - Planned | 37.03 | 402 | 14886.06 | 0.043415 | 0.000108
2012-08-24 | 278796 | GYM2A | Rural short | LV Transformer SP352-C GYM2A - Planned | 9.02 | 184 | 1659.68 | 0.0048404 | 2.6307e-05
2012-08-24 | 278797 | EMD3 | Rural short | LV Transformer SP5359-C EMD3 - Planned | 6 | 220 | 1320 | 0.0038497 | 1.7499e-05
2012-08-24 | 278798 | BPN3 | Urban | LV Transformer SP6536-H BPN3 - Planned | 5.1133 | 227 | 1160.7191 | 0.0011654 | 5.1337e-06
2012-08-24 | 278800 | TWG21 | Urban | LV Transformer SC1323-R TWG21 - Planned | 7.72 | 208 | 1605.76 | 0.0016122 | 7.7508e-06
2012-08-24 | 278801 | MFN13A | Rural short | LV Transformer SC1492740 MFN13A - Planned | 2.94 | 185 | 543.9 | 0.0015863 | 8.5744e-06
2012-08-24 | 278802 | MLY3 | Rural short | LV Transformer SP161890 MLY3 - Planned | 5 | 279 | 1395 | 0.0040685 | 1.4582e-05
2012-08-24 | 278803 | TWT13A | Urban | LV Transformer SC124-B TWT13A - Planned | 1.015 | 109 | 110.635 | 0.00011108 | 1.019e-06
2012-08-24 | 278804 | CCYUPC23 | Urban | LV Transformer SC1489-J CCYUPC23 - Planned | 28.08 | 189 | 5307.12 | 0.0053283 | 2.8192e-05
2012-08-24 | 278805 | MAI14 | Urban | LV Transformer SP273-K MAI14 - Planned | 12.4306 | 328 | 4077.2368 | 0.0040935 | 1.248e-05
2012-08-24 | 278806 | SPD4A | Urban | LV Transformer SC622-J SPD4A - Planned | 1.6908 | 175 | 295.89 | 0.00029707 | 1.6975e-06
2012-08-24 | 278807 | HIS5A | Urban | LV Transformer SP5187-H HIS5A - Planned | 13.23 | 211 | 2791.53 | 0.0028027 | 1.3283e-05
2012-08-24 | 278808 | LTN6 | Urban | LV Transformer SP17313-D LTN6 - Planned | 21.51 | 339 | 7291.89 | 0.007321 | 2.1596e-05
2012-08-24 | 278808 | SPE7 | Urban | LV Transformer SP17313-D LTN6 - Planned | 1.155 | 339 | 391.545 | 0.00039311 | 1.1596e-06
2012-08-24 | 278809 | DRD5A | Urban | LV Transformer SP4091-H RCF1A - Planned | 1.4233 | 300 | 426.99 | 0.00042869 | 1.429e-06
2012-08-24 | 278810 | DRD13A | Urban | LV Transformer SP13757-C DRD13A - Planned | 5.1 | 14 | 71.4 | 7.1685e-05 | 5.1203e-06
2012-08-24 | 278811 | WNM5 | Urban | LV Transformer SP2987-K WNM5 - Planned | 21 | 222 | 4662 | 0.0046806 | 2.1084e-05
2012-08-24 | 278812 | BRT5 | Urban | LV Transformer SP1852-J BRT5 - Planned | 8.55 | 110 | 940.5 | 0.00094425 | 8.5841e-06
2012-08-24 | 278813 | HPE3A | Urban | LV Transformer SP1710-M HPE3A - Planned | 3.66 | 160 | 585.6 | 0.00058794 | 3.6746e-06
2012-08-24 | 278814 | WNM5 | Urban | LV Transformer SP821-N WNM5 - Planned | 20.79 | 155 | 3222.45 | 0.0032353 | 2.0873e-05
2012-08-24 | 278815 | BLB4A | Urban | LV Transformer SP1933-H BLB4A - Planned | 7.28 | 256 | 1863.68 | 0.0018711 | 7.309e-06
2012-08-24 | 278816 | UMG1B | Urban | LV Transformer SC517792 UMG1B - Planned | 3.225 | 320 | 1032 | 0.0010361 | 3.2379e-06
2012-08-24 | 278817 | EMP21A | Rural short | LV Transformer SP2592-J EMP21A - Planned | 71.2 | 56 | 3987.2 | 0.011629 | 0.00020765
2012-08-24 | 278818 | CHL10 | Urban | LV Transformer SP595-M CHL10 - Planned | 11.6745 | 301 | 3514.0245 | 0.003528 | 1.1721e-05
2012-08-24 | 278819 | HPK5A | Urban | LV Transformer SP72-K HPK5A - Planned | 22.275 | 420 | 9355.5 | 0.0093928 | 2.2364e-05
2012-08-24 | 278820 | LWD1 | Rural short | LV Transformer SP3463-B LWD1 - Planned | 10.5 | 285 | 2992.5 | 0.0087276 | 3.0623e-05
2012-08-24 | 278821 | BDB35A | Urban | LV Transformer SP3518-D BDB35A - Planned | 8.955 | 308 | 2758.14 | 0.0027691 | 8.9907e-06
2012-08-25 | 278835 | TGW1 | Rural short | Feeder TGW1 - Planned | 4.8 | 189 | 907.2 | 0.0026453 | 1.3996e-05
2012-08-25 | 278837 | DBS4A | Urban | Feeder DBS4A - Planned | 2.5 | 181 | 452.5 | 0.00045431 | 2.51e-06
2012-08-25 | 278838 | SARSHW7 | Urban | LV Transformer SG3378-H SARSHW7 - Planned | 1 | 85 | 85 | 8.534e-05 | 1.004e-06
2012-08-25 | 278839 | KBR3A | Rural short | Feeder KBR3A - Planned | 8.01 | 390 | 3123.9 | 0.009109 | 2.3356e-05
2012-08-25 | 278841 | LLY1 | Rural short | LV Transformer SP17526-B LLY1 - Planned | 5.88 | 178 | 1046.64 | 0.0030519 | 1.7145e-05
2012-08-26 | 278850 | WED15B | Urban | LV Transformer SG11552-F WED15B - Planned | 1 | 111 | 111 | 0.00011145 | 1.0041e-06
2012-08-26 | 278852 | SMR12B | Urban | LV Transformer SP25797-E SMR12B - Planned | 7.02 | 42 | 294.84 | 0.00029604 | 7.0486e-06
2012-08-26 | 278853 | BHDRCK29 | Urban | Feeder BHDRCK29 - Planned | 9.094 | 198 | 1800.612 | 0.0018079 | 9.131e-06
2012-08-26 | 278856 | CRB15A | Urban | LV Transformer SP15837-D CRB15A - Planned | 1 | 180 | 180 | 0.00018073 | 1.0041e-06
2012-08-26 | 278857 | MLT2B | Urban | LV Transformer SC774394 MLT15B - Planned | 8.7683 | 384 | 3367.0272 | 0.0033807 | 8.804e-06
2012-08-26 | 278859 | NBR10 | Urban | LV Transformer SP1770-A NBR10 - Planned | 9.28 | 359 | 3331.52 | 0.0033451 | 9.3178e-06
2012-08-26 | 278860 | BHD20A | Urban | LV Transformer SP1414-J BHD20A - Planned | 12.85 | 250 | 3212.5 | 0.0032256 | 1.2902e-05
2012-08-26 | 278861 | BTA15A | Urban | LV Transformer SP4004-D BTA15A - Planned | 1.05 | 313 | 328.65 | 0.00032999 | 1.0543e-06
2012-08-26 | 278862 | NDH6 | Urban | LV Transformer SSSBY 598 - Planned | 20.545 | 290 | 5958.05 | 0.0059823 | 2.0629e-05
2012-08-26 | 278863 | CPR5 | Urban | LV Transformer SP736808 CPR5 - Planned | 34.5132 | 334 | 11527.4088 | 0.011574 | 3.4654e-05
2012-08-26 | 278864 | RST5A | Urban | LV Transformer SP565-G RST5A - Planned | 6.14 | 410 | 2517.4 | 0.0025277 | 6.165e-06
2012-08-26 | 278864 | RST8A | Urban | LV Transformer SP565-G RST5A - Planned | 0.895 | 410 | 366.95 | 0.00036844 | 8.9865e-07
2012-08-27 | 278871 | HTL6A | Urban | LV Transformer SG81-L HTL6A - Planned | 1 | 75 | 75 | 7.5312e-05 | 1.0042e-06
2012-08-27 | 278880 | FDS1 | Rural short | LV Transformer SP2946-B FDS1 - Planned | 0.4 | 197 | 78.8 | 0.00022959 | 1.1654e-06
2012-08-27 | 278884 | SDM3 | Rural short | Feeder SDM3 - Planned | 6 | 435 | 2610 | 0.0076044 | 1.7481e-05
2012-08-27 | 278887 | BDL4 | Urban | Feeder BDL4 - Planned | 90.2567 | 510 | 46030.917 | 0.046222 | 9.0632e-05
2012-08-27 | 278889 | CMD5A | Urban | LV Transformer SP53940-A CMD5A - Planned | 17.25 | 210 | 3622.5 | 0.0036376 | 1.7322e-05
2012-08-27 | 278890 | LDR3 | Urban | LV Transformer SP4487-E LDR3 - Planned | 138.57 | 285 | 39492.45 | 0.039657 | 0.00013915
2012-08-27 | 278891 | BRD5A | Rural short | LV Transformer SP17265-D BRD5A - Planned | 4 | 60 | 240 | 0.00069926 | 1.1654e-05
2012-08-27 | 278892 | WNM3 | Urban | LV Transformer SP6708-G WNM5 - Planned | 9.6 | 218 | 2092.8 | 0.0021015 | 9.6399e-06
2012-08-27 | 278892 | WNM5 | Urban | LV Transformer SP6708-G WNM5 - Planned | 3.375 | 218 | 735.75 | 0.00073881 | 3.389e-06
2012-08-27 | 278893 | NDH6 | Urban | LV Transformer SP1341-J NDH6 - Planned | 5.04 | 256 | 1290.24 | 0.0012956 | 5.061e-06
2012-08-27 | 278894 | SGT4 | Urban | LV Transformer SP483956 SGT4 - Planned | 5.25 | 98 | 514.5 | 0.00051664 | 5.2718e-06
2012-08-27 | 278895 | WRD22B | Urban | LV Transformer SG4488-G WRD22B - Planned | 29.07 | 240 | 6976.8 | 0.0070058 | 2.9191e-05
2012-08-27 | 278895 | WRD9A | Urban | LV Transformer SG4488-G WRD22B - Planned | 16.39 | 240 | 3933.6 | 0.00395 | 1.6458e-05
2012-08-27 | 278896 | RBY2A | Urban | LV Transformer SP1600-C RBY2A - Planned | 72.8957 | 179 | 13048.3303 | 0.013103 | 7.3199e-05
2012-08-27 | 278897 | CMV13 | Urban | LV Transformer SC2514-N CMV13 - Planned | 2.57 | 115 | 295.55 | 0.00029678 | 2.5807e-06
2012-08-27 | 278898 | RBK9A | Urban | LV Transformer SP3797-C RBK9A - Planned | 8.48 | 180 | 1526.4 | 0.0015327 | 8.5153e-06
2012-08-28 | 278920 | IPL3 | Rural short | LV Transformer SP599-E IPL3 - Planned | 11.04 | 99 | 1092.96 | 0.0031832 | 3.2153e-05
2012-08-28 | 278922 | RWD2 | Rural short | Feeder RWD2 - Planned | 70 | 183.0435 | 13388 | 0.038992 | 0.00020387
2012-08-28 | 278940 | LBH5A | Rural short | LV Transformer SP2737-B LBH5A - Planned | 9.02 | 204 | 1840.08 | 0.0053591 | 2.627e-05
2012-08-28 | 278941 | GYM8A | Rural short | Feeder GYM8A - Planned | 43 | 271 | 11653 | 0.033939 | 0.00012524
2012-08-28 | 278942 | MFN15A | Rural short | LV Transformer SP5755-D MFN15A - Planned | 22 | 313 | 6886 | 0.020055 | 6.4074e-05
2012-08-28 | 278943 | AMR2 | Rural short | Feeder AMR2 - Planned | 42.123 | 288 | 12131.424 | 0.035332 | 0.00012268
2012-08-28 | 278944 | BMT1 | Rural short | LV Transformer SP1783-D BMT1 - Planned | 1 | 152 | 152 | 0.00044269 | 2.9124e-06
2012-08-28 | 278945 | SIS2 | Rural short | LV Transformer SP1502295 SIS2 - Planned | 1 | 385 | 385 | 0.0011213 | 2.9124e-06
2012-08-28 | 278946 | GBN2 | Rural short | Feeder GBN2 - Planned | 5.01 | 379 | 1898.79 | 0.0055301 | 1.4591e-05
2012-08-28 | 278947 | KCY5 | Rural short | Feeder KCY5 - Planned | 2 | 325 | 650 | 0.0018931 | 5.8249e-06
2012-08-28 | 278949 | GBN3 | Rural short | Feeder GBN3 - Planned | 34.77 | 375 | 13038.75 | 0.037975 | 0.00010127
2012-08-28 | 278950 | SHW12 | Urban | LV Transformer SP6408-C SHW12 - Planned | 5.83 | 264 | 1539.12 | 0.0015456 | 5.8547e-06
2012-08-28 | 278951 | LTN3 | Urban | LV Transformer SP446-G LTN3 - Planned | 13.12 | 370 | 4854.4 | 0.004875 | 1.3176e-05
2012-08-28 | 278952 | TRG2A | Urban | LV Transformer SP4206-I TRG2A - Planned | 17.9582 | 305 | 5477.251 | 0.0055005 | 1.8034e-05
2012-08-28 | 278953 | CMD5A | Urban | LV Transformer SP3804-B CMD5A - Planned | 12.45 | 241 | 3000.45 | 0.0030132 | 1.2503e-05
2012-08-28 | 278954 | MLB13A | Urban | LV Transformer SC451931-A MLB13A - Planned | 7.74 | 273 | 2113.02 | 0.002122 | 7.7728e-06
2012-08-28 | 278955 | KCY2 | Rural short | LV Transformer SP4699-E KCY2 - Planned | 2 | 285 | 570 | 0.0016601 | 5.8249e-06
2012-08-28 | 278956 | TWT12A | Rural short | LV Transformer SP5435-B TWT12A - Planned | 26.4 | 23 | 607.2 | 0.0017684 | 7.6889e-05
2012-08-28 | 278957 | KRA3 | Urban | LV Transformer SC1950-I KRA3 - Planned | 62.225 | 399 | 24827.775 | 0.024933 | 6.2489e-05
2012-08-28 | 278958 | MGP13A | Rural short | LV Transformer SP17424-D MGP13A - Planned | 2 | 190 | 380 | 0.0011067 | 5.8249e-06
2012-08-28 | 278959 | BTN2 | Rural short | LV Transformer SP263-D BTN2 - Planned | 8.01 | 218 | 1746.18 | 0.0050857 | 2.3329e-05
2012-08-28 | 278960 | BHD5A | Urban | LV Transformer SP1121-I BHD5A - Planned | 13.3 | 280 | 3724 | 0.0037398 | 1.3356e-05
2012-08-28 | 278961 | ZMR6A | Urban | LV Transformer SP2142-G ZMR6A - Planned | 5.625 | 261 | 1468.125 | 0.0014744 | 5.6489e-06
2012-08-28 | 278962 | CSE2 | Urban | LV Transformer SC4107-O CSE2 - Planned | 21.91 | 363 | 7953.33 | 0.0079871 | 2.2003e-05
2012-08-28 | 278963 | CFD8A | Urban | LV Transformer SP552045 CFD8A - Planned | 8.22 | 235 | 1931.7 | 0.0019399 | 8.2549e-06
2012-08-28 | 278964 | NRA13A | Rural short | LV Transformer SP10440-D NRA13A - Planned | 7.0786 | 30 | 212.358 | 0.00061848 | 2.0616e-05
2012-08-28 | 278965 | BPN29A | Urban | LV Transformer SP6686-I BPN29A - Planned | 18.9 | 300 | 5670 | 0.0056941 | 1.898e-05
2012-08-28 | 278966 | CNB21B | Urban | LV Transformer SP4033-E LHM5 - Planned | 0.98 | 209 | 204.82 | 0.00020569 | 9.8416e-07
2012-08-28 | 278966 | LHM5 | Rural short | LV Transformer SP4033-E LHM5 - Planned | 8.26 | 209 | 1726.34 | 0.0050279 | 2.4057e-05
2012-08-28 | 278967 | CPB4 | Urban | LV Transformer SP619-E CPB4 - Planned | 80.64 | 240 | 19353.6 | 0.019436 | 8.0982e-05
2012-08-28 | 278968 | MTG11A | Urban | LV Transformer SP494008-A MTG11A - Planned | 13.4745 | 201 | 2708.3745 | 0.0027199 | 1.3532e-05
2012-08-28 | 278969 | GGR1 | Rural short | LV Transformer SP2283-D GGR1 - Planned | 1 | 344 | 344 | 0.0010019 | 2.9124e-06
2012-08-28 | 278970 | WHO2 | Rural short | LV Transformer SP17224-A WHO2 - Planned | 7.475 | 38.5 | 558.35 | 0.0016262 | 2.1771e-05
2012-08-28 | 278971 | WFD1B | Rural short | Feeder WFD1B - Planned | 9 | 364 | 3276 | 0.0095412 | 2.6212e-05
2012-08-28 | 278972 | MCW11 | Rural short | LV Transformer SP1445806 MCW11 - Planned | 15 | 348 | 5220 | 0.015203 | 4.3687e-05
2012-08-28 | 278973 | MGP4 | Rural short | LV Transformer SP466642 MGP4 - Planned | 1 | 420 | 420 | 0.0012232 | 2.9124e-06
2012-08-28 | 278975 | OXL11A | Urban | LV Transformer SG6143-E OXL11A - Planned | 519 | 43.5 | 45153 | 0.045345 | 0.0005212
2012-08-29 | 279008 | MGP13A | Rural short | LV Transformer SP4572-G MGP13A - Planned | 2 | 49 | 98 | 0.00028531 | 5.8226e-06
2012-08-29 | 279009 | NMC2A | Rural short | LV Transformer SC513491 NMC2A - Planned | 32 | 147 | 4704 | 0.013695 | 9.3162e-05
2012-08-29 | 279015 | MGP13A | Rural short | LV Transformer SP5231-F MGP13A - Planned | 1 | 18 | 18 | 5.2403e-05 | 2.9113e-06
2012-08-29 | 279019 | LGV5B | Rural short | LV Transformer SP16343-C LGV5B - Planned | 10 | 381 | 3810 | 0.011092 | 2.9113e-05
2012-08-29 | 279022 | MTB1B | Rural short | LV Transformer SP2366-D MTB1B - Planned | 14.5 | 430 | 6235 | 0.018152 | 4.2214e-05
2012-08-29 | 279024 | LLY4 | Rural short | Feeder LLY4 - Planned | 11 | 495 | 5445 | 0.015852 | 3.2024e-05
2012-08-29 | 279025 | SHW12 | Urban | LV Transformer SP5437-H SHW12 - Planned | 5.925 | 318 | 1884.15 | 0.0018923 | 5.9506e-06
2012-08-29 | 279027 | CMD5A | Urban | LV Transformer SP805-C CMD5A - Planned | 27.945 | 335 | 9361.575 | 0.0094021 | 2.8066e-05
2012-08-29 | 279028 | BHD1A | Urban | LV Transformer SP2223-F BHD1A - Planned | 75.9561 | 340 | 25825.074 | 0.025937 | 7.6285e-05
2012-08-29 | 279029 | MAI17 | Urban | LV Transformer SP12565-C MAI17 - Planned | 4.9915 | 280 | 1397.62 | 0.0014037 | 5.0131e-06
2012-08-29 | 279030 | SPO5A | Urban | LV Transformer SC789009-A SPO5A - Planned | 6.825 | 355 | 2422.875 | 0.0024334 | 6.8545e-06
2012-08-29 | 279032 | BHD20A | Urban | LV Transformer SC21681-E BHD20A - Planned | 5.37 | 314 | 1686.18 | 0.0016935 | 5.3932e-06
2012-08-29 | 279033 | BHD23A | Rural short | LV Transformer SP5705-F BHD23A - Planned | 7.125 | 136 | 969 | 0.002821 | 2.0743e-05
2012-08-29 | 279034 | CRB25A | Rural short | LV Transformer SP796211 CRB25A - Planned | 20.4198 | 367 | 7494.0666 | 0.021817 | 5.9448e-05
2012-08-29 | 279035 | BHD23A | Rural short | LV Transformer SP18901-E BHD23A - Planned | 9.075 | 145 | 1315.875 | 0.0038309 | 2.642e-05
2012-08-29 | 279036 | BHL5A | Urban | LV Transformer SP929-K BHL5A - Planned | 2 | 264 | 528 | 0.00053028 | 2.0087e-06
2012-08-29 | 279037 | HTN7A | Urban | LV Transformer SP378-J HTN7A - Planned | 15.06 | 390 | 5873.4 | 0.0058988 | 1.5125e-05
2012-08-29 | 279038 | HDA13A | Urban | LV Transformer SP1853-I HDA3A - Planned | 1.18 | 365 | 430.7 | 0.00043256 | 1.1851e-06
2012-08-29 | 279038 | HDA3A | Urban | LV Transformer SP1853-I HDA3A - Planned | 13.575 | 365 | 4954.875 | 0.0049763 | 1.3634e-05
2012-08-29 | 279039 | RCF1A | Urban | LV Transformer SP2228-G RCF1A - Planned | 2.2133 | 40 | 88.532 | 8.8915e-05 | 2.2229e-06
2012-08-29 | 279040 | NDH6 | Urban | LV Transformer SC1397-K NDH9 - Planned | 44.83 | 289 | 12955.87 | 0.013012 | 4.5024e-05
2012-08-29 | 279040 | NDH9 | Urban | LV Transformer SC1397-K NDH9 - Planned | 1.39 | 289 | 401.71 | 0.00040345 | 1.396e-06
2012-08-29 | 279041 | WNM2A | Urban | LV Transformer SP988-P WNM2A - Planned | 3.495 | 437 | 1527.315 | 0.0015339 | 3.5101e-06
2012-08-29 | 279041 | WNM5 | Urban | LV Transformer SP988-P WNM2A - Planned | 2.1 | 437 | 917.7 | 0.00092167 | 2.1091e-06
2012-08-29 | 279042 | RCF1A | Urban | LV Transformer SP2228-G RCF1A - Planned | 2.2133 | 51 | 112.8783 | 0.00011337 | 2.2229e-06
2012-08-29 | 279043 | WNM4 | Urban | LV Transformer SP5426-F WNM4 - Planned | 3.26 | 409 | 1333.34 | 0.0013391 | 3.2741e-06
2012-08-29 | 279044 | GBP5 | Urban | LV Transformer SP2065-G GBP5 - Planned | 24.09 | 273 | 6576.57 | 0.006605 | 2.4194e-05
2012-08-29 | 279045 | RLB12B | Rural short | LV Transformer SP9130-B RLB12B - Planned | 0.93 | 154 | 143.22 | 0.00041696 | 2.7075e-06
2012-08-29 | 279046 | WED16A | Urban | LV Transformer SP135-O WED16A - Planned | 23.4396 | 110 | 2578.356 | 0.0025895 | 2.3541e-05
2012-08-29 | 279047 | PDB13 | Urban | LV Transformer SC2052903 PDB13 - Planned | 2.82 | 196 | 552.72 | 0.00055511 | 2.8322e-06
2012-08-29 | 279048 | FDS1 | Rural short | LV Transformer SP948-E FDS1 - Planned | 10.95 | 251 | 2748.45 | 0.0080016 | 3.1879e-05
2012-08-29 | 279051 | AGE10 | Urban | LV Transformer SG4221-H AGE10 - Planned | 1 | 670 | 670 | 0.0006729 | 1.0043e-06
2012-08-29 | 279052 | MFD3A | Rural short | LV Transformer SP3129-G MFD3A - Planned | 14.335 | 362 | 5189.27 | 0.015108 | 4.1733e-05
2012-08-29 | 279053 | NBR6 | Rural short | Feeder NBR6 - Planned | 21.975 | 305.2 | 8393.405 | 0.024436 | 6.3976e-05
2012-08-29 | 279054 | YDA3A | Rural short | Feeder YDA3A - Planned | 17.02 | 411 | 6995.22 | 0.020365 | 4.955e-05
2012-08-29 | 279055 | PWC4 | Rural short | Feeder PWC4 - Planned | 28.35 | 383 | 10858.05 | 0.031611 | 8.2535e-05
2012-08-29 | 279056 | PGN6A | Urban | LV Transformer SC1471112 PGN6A - Planned | 3 | 226 | 678 | 0.00068093 | 3.013e-06
2012-08-30 | 279081 | BNH5A | Rural short | LV Transformer SP14008-B BNH5A - Planned | 2.01 | 70 | 140.7 | 0.00040946 | 5.8494e-06
2012-08-30 | 279083 | BLH12A | Rural short | LV Transformer SP12945-B BLH12A - Planned | 6.02 | 156 | 939.12 | 0.002733 | 1.7519e-05
2012-08-30 | 279084 | BDT2 | Rural short | LV Transformer SP759-C BDT2 - Planned | 4.98 | 95 | 473.1 | 0.0013768 | 1.4493e-05
2012-08-30 | 279085 | YTA2A | Urban | LV Transformer SP17126-C YTA2A - Planned | 7 | 208 | 1456 | 0.0014624 | 7.0308e-06
2012-08-30 | 279086 | BNH5A | Rural short | LV Transformer SP4155-B BNH5A - Planned | 1 | 242 | 242 | 0.00070426 | 2.9101e-06
2012-08-30 | 279087 | JBB16A | Rural short | Feeder JBB16A - Planned | 37 | 105 | 3885 | 0.011306 | 0.00010768
2012-08-30 | 279088 | IPL2 | Rural short | LV Transformer SP17333-H IPL2 - Planned | 2 | 117 | 234 | 0.00068097 | 5.8203e-06
2012-08-30 | 279089 | BBSRDL8 | Rural short | LV Transformer SP2537-G BBSRDL8 - Planned | 15.67 | 266 | 4168.22 | 0.01213 | 4.5602e-05
2012-08-30 | 279090 | CRM16A | Rural short | LV Transformer SP7972-D CRM16A - Planned | 56 | 278 | 15568 | 0.045305 | 0.00016297
2012-08-30 | 279093 | TRP4 | Rural short | Feeder TRP4 - Planned | 16.1 | 368 | 5924.8 | 0.017242 | 4.6853e-05
2012-08-30 | 279094 | BTN7 | Rural short | LV Transformer SP3163-C BTN7 - Planned | 2.2311 | 270 | 602.397 | 0.0017531 | 6.4928e-06
2012-08-30 | 279097 | BHD1A | Urban | LV Transformer SP3495-E BHD1A - Planned | 23.25 | 360 | 8370 | 0.0084069 | 2.3352e-05
2012-08-30 | 279097 | BHD21A | Urban | LV Transformer SP3495-E BHD1A - Planned | 3.45 | 360 | 1242 | 0.0012475 | 3.4652e-06
2012-08-30 | 279098 | NMK17A | Urban | LV Transformer SP1884-O NMK17A - Planned | 21.7712 | 288 | 6270.1056 | 0.0062977 | 2.1867e-05
2012-08-30 | 279100 | NRG9 | Rural short | LV Transformer SC943-J NRG9 - Planned | 16.874 | 58 | 978.692 | 0.0028481 | 4.9106e-05
2012-08-30 | 279101 | SPD4A | Urban | LV Transformer SC607-K SPD4A - Planned | 1.08 | 108 | 116.64 | 0.00011715 | 1.0848e-06
2012-08-30 | 279102 | PWC2 | Rural short | Feeder PWC2 - Planned | 2.01 | 317 | 637.17 | 0.0018543 | 5.8494e-06
2012-08-30 | 279103 | MGP17A | Urban | LV Transformer SC1447275 MGP17A - Planned | 92.41 | 108 | 9980.28 | 0.010024 | 9.2817e-05
2012-08-30 | 279104 | NGI3A | Rural short | Feeder NGI3A - Planned | 5 | 362 | 1810 | 0.0052674 | 1.4551e-05
2012-08-30 | 279105 | NBR6 | Rural short | Feeder NBR6 - Planned | 5.01 | 420 | 2104.2 | 0.0061235 | 1.458e-05
2012-08-30 | 279106 | BBH16A | Urban | LV Transformer SC763704 BBH16A - Planned | 11.8 | 149 | 1758.2 | 0.0017659 | 1.1852e-05
2012-08-30 | 279107 | GYM2A | Rural short | LV Transformer SP974-C GYM2A - Planned | 8.3037 | 294 | 2441.2878 | 0.0071045 | 2.4165e-05
2012-08-30 | 279108 | GYN7A | Rural short | LV Transformer SP745507 GYN7A - Planned | 0.8 | 13 | 20.8 | 6.0531e-05 | 2.3281e-06
2012-08-30 | 279109 | BRT5 | Urban | LV Transformer SP3049-G BRT8 - Planned | 1.385 | 315 | 436.275 | 0.0004382 | 1.3911e-06
2012-08-30 | 279109 | BRT8 | Urban | LV Transformer SP3049-G BRT8 - Planned | 15.75 | 315 | 4961.25 | 0.0049831 | 1.5819e-05
2012-08-30 | 279110 | SGT4 | Urban | LV Transformer SP5493-E SGT4 - Planned | 1.695 | 5 | 8.475 | 8.5123e-06 | 1.7025e-06
2012-08-30 | 279111 | AMR2 | Rural short | LV Transformer SP15481-A AMR2 - Planned | 18.05 | 182 | 3285.1 | 0.0095601 | 5.2528e-05
2012-08-30 | 279112 | DRD16A | Urban | LV Transformer SP5896-B DRD16A - Planned | 2.7 | 85 | 229.5 | 0.00023051 | 2.7119e-06
2012-08-30 | 279114 | NDH6 | Urban | LV Transformer SP12548-D NDH6 - Planned | 16.7521 | 377 | 6315.5417 | 0.0063434 | 1.6826e-05
2012-08-30 | 279115 | CRB25A | Rural short | Feeder CRB25A - Planned | 42.5 | 528 | 22440 | 0.065304 | 0.00012368
2012-08-30 | 279117 | RCN10A | Urban | LV Transformer SP4178-M RCN10A - Planned | 23.18 | 335 | 7765.3 | 0.0077995 | 2.3282e-05
2012-08-30 | 279118 | UMG12A | Urban | LV Transformer SC4044-I UMG12A - Planned | 6.24 | 263 | 1641.12 | 0.0016484 | 6.2675e-06
2012-08-30 | 279119 | HPE13A | Urban | LV Transformer SC139-K HPE13A - Planned | 4.225 | 385 | 1626.625 | 0.0016338 | 4.2436e-06
2012-08-30 | 279120 | RBY3 | Urban | LV Transformer SP5413-D RBY3 - Planned | 4.9581 | 256 | 1269.2736 | 0.0012749 | 4.98e-06
2012-08-30 | 279121 | GBP5 | Urban | LV Transformer SP2065-G GBP5 - Planned | 48.18 | 258 | 12430.44 | 0.012485 | 4.8392e-05
2012-08-30 | 279122 | HPE3A | Urban | LV Transformer SC3657-F HPE3A - Planned | 20.6493 | 335 | 6917.5155 | 0.006948 | 2.074e-05
2012-08-30 | 279123 | MTG11A | Urban | LV Transformer SC5136-H MTG11A - Planned | 4.8 | 177 | 849.6 | 0.00085334 | 4.8212e-06
2012-08-30 | 279124 | MSV2 | Rural short | LV Transformer SP12547-A MSV2 - Planned | 1 | 279 | 279 | 0.00081193 | 2.9101e-06
2012-08-30 | 279125 | BDB27A | Rural short | LV Transformer SP3159-C BDB27A - Planned | 10.235 | 288 | 2947.68 | 0.0085782 | 2.9785e-05
2012-08-30 | 279126 | RST8A | Urban | LV Transformer SP2471-F RST8A - Planned | 8.9 | 155 | 1379.5 | 0.0013856 | 8.9392e-06
2012-08-30 | 279127 | SFD3 | Urban | LV Transformer SC4054-K SFD3 - Planned | 25.38 | 370 | 9390.6 | 0.009432 | 2.5492e-05
2012-08-30 | 279128 | CLD20A | Rural short | LV Transformer SP4364-B CLD20A - Planned | 29.04 | 362 | 10512.48 | 0.030593 | 8.4511e-05
2012-08-30 | 279129 | GGR1 | Rural short | Feeder GGR1 - Planned | 27.1 | 512 | 13875.2 | 0.040379 | 7.8865e-05
2012-08-30 | 279130 | SMF3A | Rural short | Feeder SMF3A - Planned | 185.02 | 368 | 68087.36 | 0.19814 | 0.00053844
2012-08-30 | 279131 | YDA1B | Rural short | Feeder YDA1B - Planned | 96.88 | 542 | 52508.96 | 0.15281 | 0.00028194
2012-08-31 | 279144 | IPL3 | Rural short | LV Transformer SP817-D IPL3 - Planned | 4.98 | 94 | 468.12 | 0.0013617 | 1.4487e-05
2012-08-31 | 279145 | PRG1 | Rural short | LV Transformer SP2978-B PRG1 - Planned | 0.4 | 102 | 40.8 | 0.00011869 | 1.1636e-06
2012-08-31 | 279146 | BLH12A | Rural short | LV Transformer SP781-C BLH12A - Planned | 16.45 | 132 | 2171.4 | 0.0063165 | 4.7853e-05
2012-08-31 | 279147 | IPL1 | Rural short | LV Transformer SP624-E IPL1 - Planned | 3 | 170 | 510 | 0.0014836 | 8.7269e-06
2012-08-31 | 279148 | BLH12A | Rural short | LV Transformer SP2578-P BLH12A - Planned | 12 | 259 | 3108 | 0.0090411 | 3.4908e-05
2012-08-31 | 279149 | MWMRBK11 | Rural short | Feeder MWMRBK11 - Planned | 2 | 312 | 624 | 0.0018152 | 5.8179e-06
2012-08-31 | 279150 | TGW2 | Rural short | Feeder TGW2 - Planned | 32.96 | 310 | 10217.6 | 0.029723 | 9.588e-05
2012-08-31 | 279151 | FDS3 | Rural short | Feeder FDS3 - Planned | 28 | 256 | 7168 | 0.020851 | 8.1451e-05
2012-08-31 | 279152 | BLB5A | Urban | LV Transformer SC2187-F BLB5A - Planned | 0.67 | 380 | 254.6 | 0.00025574 | 6.7301e-07
2012-08-31 | 279153 | GAP9A | Urban | LV Transformer SP2578-N GAP9A - Planned | 7.7 | 281 | 2163.7 | 0.0021734 | 7.7346e-06
2012-08-31 | 279154 | KRN18A | Urban | LV Transformer SC799525 KRN18A - Planned | 6.7835 | 218 | 1478.803 | 0.0014854 | 6.814e-06
2012-08-31 | 279155 | CMD13A | Urban | LV Transformer SP3474-A CMD13A - Planned | 6.2 | 272 | 1686.4 | 0.001694 | 6.2279e-06
2012-08-31 | 279156 | LRE4A | Rural short | Feeder LRE4A - Planned | 17 | 430 | 7310 | 0.021265 | 4.9452e-05
2012-08-31 | 279157 | BMT4 | Rural short | LV Transformer SP9255-A BMT4 - Planned | 10.5 | 21 | 220.5 | 0.00064143 | 3.0544e-05
2012-08-31 | 279158 | MFN15A | Rural short | LV Transformer SP5762-D MFN15A - Planned | 8.1 | 192 | 1555.2 | 0.004524 | 2.3563e-05
2012-08-31 | 279159 | BDT4 | Rural short | LV Transformer SP1170-I BDT4 - Planned | 5 | 125 | 625 | 0.0018181 | 1.4545e-05
2012-08-31 | 279160 | BDT5 | Rural short | LV Transformer SP573-G BDT5 - Planned | 1 | 72 | 72 | 0.00020945 | 2.909e-06
2012-08-31 | 279161 | HTN7A | Urban | LV Transformer SP378-J HTN7A - Planned | 17.57 | 320 | 5622.4 | 0.0056477 | 1.7649e-05
2012-08-31 | 279162 | NDH6 | Urban | LV Transformer SP8719-D NDH6 - Planned | 52.58 | 350 | 18403 | 0.018486 | 5.2816e-05
2012-08-31 | 279163 | RBY13 | Urban | LV Transformer SP808601 RBY13 - Planned | 6.05 | 270 | 1633.5 | 0.0016408 | 6.0772e-06
2012-08-31 | 279164 | CHL9 | Rural short | LV Transformer SP7807-E CHL9 - Planned | 8.701 | 287 | 2497.187 | 0.0072642 | 2.5311e-05
2012-08-31 | 279165 | MTG13A | Urban | LV Transformer SP5128-G MTG7A - Planned | 9.23 | 214 | 1975.22 | 0.0019841 | 9.2715e-06
2012-08-31 | 279165 | MTG7A | Urban | LV Transformer SP5128-G MTG7A - Planned | 1.12 | 214 | 239.68 | 0.00024076 | 1.125e-06
2012-08-31 | 279167 | BHL2A | Urban | LV Transformer SP2414-L BHL2A - Planned | 20.24 | 411 | 8318.64 | 0.008356 | 2.0331e-05
2012-08-31 | 279169 | GYM7A | Rural short | Feeder GYM7A - Planned | 8.1 | 334 | 2705.4 | 0.0078699 | 2.3563e-05
2012-08-31 | 279170 | CRY5A | Rural short | Feeder CRY5A - Planned | 51.663 | 340 | 17565.42 | 0.051097 | 0.00015029
2012-08-31 | 279171 | KCY4 | Rural short | LV Transformer SP2615-F KCY4 - Planned | 4 | 212 | 848 | 0.0024668 | 1.1636e-05
2012-08-31 | 279172 | AMR1 | Rural short | Feeder AMR1 - Planned | 48.26 | 499 | 24081.74 | 0.070053 | 0.00014039
2012-08-31 | 279182 | MLY6 | Rural short | Feeder MLY6 - Planned | 8.855 | 286 | 2532.53 | 0.007367 | 2.5759e-05
2012-08-31 | 279203 | WSO3A | Urban | LV Transformer SG11609-G WSO3A - Planned | 1 | 2815 | 2815 | 0.0028276 | 1.0045e-06
2012-09-01 | 279183 | MLY4 | Rural short | Feeder MLY4, TMH3A - Planned | 14.69 | 97 | 1424.93 | 0.0041433 | 4.2715e-05
2012-09-01 | 279184 | KBR6A | Rural short | Feeder KBR6A - Planned | 9.99 | 314 | 3136.86 | 0.0091212 | 2.9048e-05
2012-09-01 | 279185 | TGW3 | Rural short | Feeder TGW3 - Planned | 7.5 | 259 | 1942.5 | 0.0056483 | 2.1808e-05
2012-09-01 | 279189 | CPL23A | Rural short | LV Transformer SG771750 CPL23A - Planned | 0.5 | 393 | 196.5 | 0.00057137 | 1.4539e-06
2012-09-01 | 279190 | CPL23A | Rural short | LV Transformer SP1023-Q CPL23A - Planned | 4.32 | 265 | 1144.8 | 0.0033288 | 1.2561e-05
2012-09-01 | 279191 | DRA9 | Urban | LV Transformer SC762238 - Planned | 0.96 | 43 | 41.28 | 4.1469e-05 | 9.644e-07
2012-09-01 | 279193 | RST8A | Urban | LV Transformer SP4386-E RST8A - Planned | 5.37 | 314 | 1686.18 | 0.0016939 | 5.3946e-06
2012-09-02 | 279198 | ARG4 | Urban | LV Transformer SG2702-L ARG4 - Planned | 1 | 251 | 251 | 0.00025218 | 1.0047e-06
2012-09-02 | 279199 | MLT21B | Urban | LV Transformer SP4557-K MLT21B - Planned | 0.89 | 347 | 308.83 | 0.00031028 | 8.9417e-07
2012-09-02 | 279200 | AGE10 | Urban | LV Transformer SP26963-D AGE10 - Planned | 16.2894 | 285 | 4642.479 | 0.0046642 | 1.6366e-05
2012-09-03 | 279228 | TBV3 | Rural short | LV Transformer SP2055-E TBV3 - Planned | 2.5 | 195 | 487.5 | 0.0014163 | 7.2633e-06
2012-09-03 | 279241 | TGW2 | Rural short | LV Transformer SP13942-A TGW2 - Planned | 3 | 382 | 1146 | 0.0033295 | 8.7159e-06
2012-09-03 | 279242 | PPE16A | Rural short | LV Transformer SP3521-C PPE16A - Planned | 9.5 | 325 | 3087.5 | 0.0089701 | 2.76e-05
2012-09-03 | 279260 | NBR6 | Rural short | Feeder NBR6 - Planned | 15.475 | 259.75 | 3597.695 | 0.010452 | 4.496e-05
2012-09-03 | 279261 | BWH16A | Rural short | LV Transformer SP14475-A BWH16A - Planned | 17 | 374 | 6358 | 0.018472 | 4.939e-05
2012-09-03 | 279262 | EMD3 | Rural short | LV Transformer SP5184-B EMD3 - Planned | 0.4 | 120 | 48 | 0.00013945 | 1.1621e-06
2012-09-03 | 279263 | OXL4A | Urban | LV Transformer SP2036-J OXL4A - Planned | 9.88 | 409 | 4040.92 | 0.0040602 | 9.9272e-06
2012-09-03 | 279264 | WCL17A | Urban | LV Transformer SP5524-G WCL17A - Planned | 6.02 | 262 | 1577.24 | 0.0015848 | 6.0488e-06
2012-09-03 | 279265 | MFN15A | Rural short | LV Transformer SP9281-F MFN15A - Planned | 3 | 275 | 825 | 0.0023969 | 8.7159e-06
2012-09-03 | 279266 | AHD19 | Urban | LV Transformer SP4454-A AHD19 - Planned | 6.64 | 319 | 2118.16 | 0.0021283 | 6.6717e-06
2012-09-03 | 279268 | ARG5A | Urban | LV Transformer SP2472-M ARG5A - Planned | 24.91 | 195 | 4857.45 | 0.0048807 | 2.5029e-05
2012-09-03 | 279269 | HPK8A | Urban | LV Transformer SP492472 HPK8A - Planned | 32.415 | 390 | 12641.85 | 0.012702 | 3.257e-05
2012-09-03 | 279270 | BDA5A | Urban | LV Transformer SP3023-J BDA5A - Planned | 15.0792 | 272 | 4101.5424 | 0.0041211 | 1.5151e-05
2012-09-03 | 279271 | GGR1 | Rural short | LV Transformer SP2283-D GGR1 - Planned | 11.5 | 300 | 3450 | 0.010023 | 3.3411e-05
2012-09-03 | 279272 | CRB24B | Urban | Feeder CRB24B - Planned | 117.5 | 562 | 66035 | 0.066351 | 0.00011806
2012-09-03 | 279273 | BWH16A | Rural short | LV Transformer SP2248-C BWH16A - Planned | 2.01 | 389 | 781.89 | 0.0022716 | 5.8397e-06
2012-09-03 | 279301 | AHD8 | Urban | LV Transformer SP5394-A AHD8 - Planned | 3.42 | 339 | 1159.38 | 0.0011649 | 3.4363e-06
2012-09-04 | 279287 | MCW7 | Rural short | LV Transformer SP244428 MCW7 - Planned | 5 | 26 | 130 | 0.00037753 | 1.4521e-05
2012-09-04 | 279300 | ABY2A | Rural short | LV Transformer SP739363 ABY2A - Planned | 6 | 31 | 186 | 0.00054016 | 1.7425e-05
2012-09-04 | 279302 | EMD2 | Rural short | LV Transformer SP28-C EMD2 - Planned | 13.95 | 177 | 2469.15 | 0.0071707 | 4.0512e-05
2012-09-04 | 279303 | GBN4 | Rural short | Feeder GBN4 - Planned | 12.554 | 189 | 2372.706 | 0.0068906 | 3.6458e-05
2012-09-04 | 279304 | BLH13B | Rural short | LV Transformer SP5519-D BLH13B - Planned | 9 | 179 | 1611 | 0.0046785 | 2.6137e-05
2012-09-04 | 279320 | CBW13 | Rural short | LV Transformer SP2443-E CBW13 - Planned | 6 | 329 | 1974 | 0.0057327 | 1.7425e-05
2012-09-04 | 279321 | KLG14A | Urban | LV Transformer SP5086-F KLG14A - Planned | 38 | 381 | 14478 | 0.014549 | 3.8185e-05
2012-09-04 | 279322 | GGR4 | Rural short | Feeder GGR4 - Planned | 75.06 | 351 | 26346.06 | 0.076512 | 0.00021798
2012-09-04 | 279323 | BDT5 | Rural short | LV Transformer SP576-F BDT5 - Planned | 6.02 | 400 | 2408 | 0.0069931 | 1.7483e-05
2012-09-04 | 279324 | GVN16A | Rural short | Feeder GVN16A - Planned | 47.31 | 290 | 13719.9 | 0.039844 | 0.00013739
2012-09-04 | 279325 | EMD2 | Rural short | Feeder EMD2 - Planned | 15.4 | 252 | 3880.8 | 0.01127 | 4.4723e-05
2012-09-04 | 279326 | MFN15A | Rural short | Feeder MFN15A - Planned | 34.5 | 497 | 17146.5 | 0.049795 | 0.00010019
2012-09-04 | 279327 | CRB25A | Rural short | Feeder CRB25A - Planned | 38.21 | 406 | 15513.26 | 0.045052 | 0.00011097
2012-09-04 | 279328 | HIS13A | Urban | LV Transformer SP468670 HIS13A - Planned | 1.5 | 615 | 922.5 | 0.000927 | 1.5073e-06
2012-09-04 | 279329 | MLT42A | Urban | LV Transformer SC83-N MLT42A - Planned | 34.2 | 370 | 12654 | 0.012716 | 3.4367e-05
2012-09-04 | 279330 | NMK17A | Urban | LV Transformer SP3301-M NMK17A - Planned | 13.5633 | 375.5 | 4914.5103 | 0.0049385 | 1.3629e-05
2012-09-04 | 279332 | MLY3 | Rural short | LV Transformer SP7809-A MLY3 - Planned | 2 | 140 | 280 | 0.00081315 | 5.8082e-06
2012-09-04 | 279333 | CMD13A | Urban | LV Transformer SP4383-B CMD13A - Planned | 31.625 | 356 | 11258.5 | 0.011313 | 3.1779e-05
2012-09-04 | 279334 | AHD10B | Urban | LV Transformer SC265-A AHD10B - Planned | 9.1165 | 146 | 1331.009 | 0.0013375 | 9.161e-06
2012-09-04 | 279335 | AHD4A | Urban | LV Transformer SP16482-A AHD4A - Planned | 1.72 | 367 | 631.24 | 0.00063432 | 1.7284e-06
2012-09-04 | 279336 | GYN7A | Rural short | LV Transformer SP3115-C GYN7A - Planned | 19.6742 | 282 | 5548.1244 | 0.016112 | 5.7136e-05
2012-09-04 | 279337 | HWL8A | Urban | LV Transformer SP2178-H LDR1 - Planned | 0.81 | 387 | 313.47 | 0.000315 | 8.1395e-07
2012-09-04 | 279337 | LDR1 | Urban | LV Transformer SP2178-H LDR1 - Planned | 23.2332 | 387 | 8991.2484 | 0.0090351 | 2.3346e-05
2012-09-04 | 279337 | LDR3 | Urban | LV Transformer SP2178-H LDR1 - Planned | 31.93 | 387 | 12356.91 | 0.012417 | 3.2086e-05
2012-09-04 | 279338 | NDH6 | Urban | LV Transformer SC4670-E NDH6 - Planned | 16.47 | 315 | 5188.05 | 0.0052133 | 1.655e-05
2012-09-04 | 279339 | SGT4 | Urban | LV Transformer SP2063-H SGT4 - Planned | 4.0456 | 57 | 230.5992 | 0.00023172 | 4.0653e-06
2012-09-04 | 279340 | BRT3 | Urban | LV Transformer SP2862-H BRT3 - Planned | 51.83 | 306 | 15859.98 | 0.015937 | 5.2083e-05
2012-09-04 | 279341 | BRT5 | Urban | LV Transformer SP1852-J BRT5 - Planned | 5.835 | 82 | 478.47 | 0.0004808 | 5.8635e-06
2012-09-04 | 279342 | BRT5 | Urban | LV Transformer SP4049-H BRT5 - Planned | 6.72 | 75 | 504 | 0.00050646 | 6.7528e-06
2012-09-04 | 279343 | BLB5A | Urban | LV Transformer SP1057-K BLB5A - Planned | 10.32 | 45 | 464.4 | 0.00046666 | 1.037e-05
2012-09-04 | 279344 | BLB5A | Urban | LV Transformer SC491380 BLB5A - Planned | 37.02 | 70 | 2591.4 | 0.002604 | 3.7201e-05
2012-09-04 | 279345 | CPR4 | Urban | LV Transformer SP3805-G CPR4 - Planned | 31.6392 | 273 | 8637.5016 | 0.0086796 | 3.1793e-05
2012-09-04 | 279345 | CPR6 | Urban | LV Transformer SP3805-G CPR4 - Planned | 2.985 | 273 | 814.905 | 0.00081888 | 2.9996e-06
2012-09-04 | 279346 | SBK9 | Urban | LV Transformer SP2224-J SBK9 - Planned | 0.7275 | 237 | 172.4175 | 0.00017326 | 7.3105e-07
2012-09-04 | 279347 | BKD13A | Urban | LV Transformer SP6110-C BKD13A - Planned | 12.92 | 271 | 3501.32 | 0.0035184 | 1.2983e-05
2012-09-04 | 279347 | CVL3A | Urban | LV Transformer SP6110-C BKD13A - Planned | 7.14 | 271 | 1934.94 | 0.0019444 | 7.1748e-06
2012-09-04 | 279348 | BVL3A | Urban | LV Transformer SP3273-C BVL3A - Planned | 10.26 | 192 | 1969.92 | 0.0019795 | 1.031e-05
2012-09-04 | 279349 | BVL10A | Urban | LV Transformer SP8572-A BVL10A - Planned | 16.8147 | 190 | 3194.793 | 0.0032104 | 1.6897e-05
2012-09-04 | 279350 | LLY3 | Rural short | Feeder LLY3, LLY4 - Planned | 45.92 | 578 | 26541.76 | 0.07708 | 0.00013336
2012-09-04 | 279350 | LLY4 | Rural short | Feeder LLY3, LLY4 - Planned | 2 | 578 | 1156 | 0.0033571 | 5.8082e-06
2012-09-05 | 279363 | MTB16A | Rural short | LV Transformer SP113742-A MTB16A - Planned | 2.01 | 170 | 341.7 | 0.00099192 | 5.8348e-06
2012-09-05 | 279364 | IPL3 | Rural short | LV Transformer SP23731-A IPL3 - Planned | 5 | 160 | 800 | 0.0023223 | 1.4515e-05
2012-09-05 | 279365 | MTB2A | Rural short | LV Transformer SP902-G MTB2A - Planned | 16.45 | 163 | 2681.35 | 0.0077837 | 4.7753e-05
2012-09-05 | 279367 | KLG7A | Rural short | LV Transformer SC1461653 KLG7A - Planned | 29.14 | 110 | 3205.4 | 0.009305 | 8.4591e-05
2012-09-05 | 279368 | CMA8A | Rural short | LV Transformer SP4813-C CMA8A - Planned | 12.33 | 318 | 3920.94 | 0.011382 | 3.5793e-05
2012-09-05 | 279369 | NMC1B | Rural short | Feeder NMC1B - Planned | 81.45 | 253 | 20606.85 | 0.05982 | 0.00023644
2012-09-05 | 279370 | TRP3 | Rural short | Feeder TRP3 - Planned | 30 | 232 | 6960 | 0.020204 | 8.7087e-05
2012-09-05 | 279371 | TGW3 | Rural short | Feeder TGW3 - Planned | 14 | 394 | 5516 | 0.016012 | 4.0641e-05
2012-09-05 | 279372 | GGR1 | Rural short | Feeder GGR1, LLY4 - Planned | 23.66 | 581 | 13746.46 | 0.039905 | 6.8683e-05
2012-09-05 | 279372 | LLY4 | Rural short | Feeder GGR1, LLY4 - Planned | 2 | 581 | 1162 | 0.0033732 | 5.8058e-06
2012-09-05 | 279374 | CRBTHP26 | Urban | LV Transformer SP737244 - Planned | 0.5 | 639 | 319.5 | 0.00032109 | 5.0248e-07
2012-09-05 | 279375 | SFD10 | Urban | LV Transformer SG1013-Q SFD4 - Planned | 1.035 | 231 | 239.085 | 0.00024027 | 1.0401e-06
2012-09-05 | 279375 | SFD4 | Urban | LV Transformer SG1013-Q SFD4 - Planned | 29.44 | 231 | 6800.64 | 0.0068344 | 2.9586e-05
2012-09-05 | 279376 | WSO3A | Urban | LV Transformer SP32519-C WSO3A - Planned | 9 | 390 | 3510 | 0.0035274 | 9.0447e-06
2012-09-05 | 279377 | MGL5 | Urban | LV Transformer SC6202-E MGL5 - Planned | 6 | 202 | 1212 | 0.001218 | 6.0298e-06
2012-09-05 | 279377 | WCL19A | Rural short | LV Transformer SC6202-E MGL5 - Planned | 3 | 202 | 606 | 0.0017592 | 8.7087e-06
2012-09-05 | 279378 | MFD8A | Rural short | LV Transformer SP9404-C MFD8A - Planned | 3.19 | 245 | 781.55 | 0.0022688 | 9.2603e-06
2012-09-05 | 279379 | CMD15A | Urban | LV Transformer SP5291-A CMD15A - Planned | 6.09 | 121 | 736.89 | 0.00074055 | 6.1203e-06
2012-09-05 | 279380 | AHD10B | Urban | LV Transformer SP724-A AHD10B - Planned | 1.8566 | 101 | 187.5166 | 0.00018845 | 1.8658e-06
2012-09-05 | 279381 | CMD13A | Urban | LV Transformer SP4377-B CMD13A - Planned | 17.9854 | 255 | 4586.277 | 0.0046091 | 1.8075e-05
2012-09-05 | 279382 | BWH16A | Rural short | LV Transformer SP7704-A BWH16A - Planned | 26.88 | 111 | 2983.68 | 0.0086613 | 7.803e-05
2012-09-05 | 279383 | LDR8 | Urban | LV Transformer SP8781-D LDR8 - Planned | 18.4759 | 233 | 4304.8847 | 0.0043263 | 1.8568e-05
2012-09-05 | 279384 | CRBTHP26 | Urban | LV Transformer SP5638-D CRBTHP26 - Planned | 27 | 477 | 12879 | 0.012943 | 2.7134e-05
2012-09-05 | 279385 | PBH1 | Urban | LV Transformer SP3206-H PBH1 - Planned | 16.31 | 420 | 6850.2 | 0.0068842 | 1.6391e-05
2012-09-05 | 279386 | BHD23A | Rural short | LV Transformer SP5812-E BHD23A - Planned | 6 | 317 | 1902 | 0.0055213 | 1.7417e-05
2012-09-05 | 279387 | SPD7B | Urban | LV Transformer SG788-J SPD7B - Planned | 24.525 | 243 | 5959.575 | 0.0059892 | 2.4647e-05
2012-09-05 | 279388 | HDA3A | Urban | LV Transformer SP1853-I HDA3A - Planned | 15.96 | 287 | 4580.52 | 0.0046033 | 1.6039e-05
2012-09-05 | 279389 | NDH6 | Urban | LV Transformer SP741834 NDH6 - Planned | 7.84 | 298 | 2336.32 | 0.0023479 | 7.879e-06
2012-09-05 | 279390 | LTN3 | Urban | LV Transformer SP446-G LTN3 - Planned | 12.96 | 260 | 3369.6 | 0.0033863 | 1.3024e-05
2012-09-05 | 279392 | WNM5 | Urban | LV Transformer SP2987-K WNM5 - Planned | 28.21 | 390 | 11001.9 | 0.011057 | 2.835e-05
2012-09-05 | 279393 | MTG11A | Urban | LV Transformer SC5136-H MTG11A - Planned | 30.4 | 251 | 7630.4 | 0.0076683 | 3.0551e-05
2012-09-05 | 279394 | CHL11A | Rural short | LV Transformer SP3936-G CHL11A - Planned | 8.55 | 314 | 2684.7 | 0.0077934 | 2.482e-05
2012-09-05 | 279395 | FDS1 | Rural short | LV Transformer SP1761-E FDS1 - Planned | 4.98 | 309 | 1538.82 | 0.004467 | 1.4456e-05
2012-09-05 | 279396 | EMD3 | Rural short | LV Transformer SP3774-B EMD3 - Planned | 8.455 | 170 | 1437.35 | 0.0041725 | 2.4544e-05
2012-09-05 | 279397 | AMR2 | Rural short | LV Transformer SP1478-D AMR2 - Planned | 7 | 166 | 1162 | 0.0033732 | 2.032e-05
2012-09-05 | 279398 | CBW13 | Rural short | LV Transformer SP161-M CBW13 - Planned | 15 | 187 | 2805 | 0.0081426 | 4.3544e-05
2012-09-05 | 279399 | BWH16A | Rural short | LV Transformer SP17916-B BWH16A - Planned | 16 | 298 | 4768 | 0.013841 | 4.6446e-05
2012-09-05 | 279400 | MFD8A | Rural short | LV Transformer SP9235-E MFD8A - Planned | 17.5 | 356 | 6230 | 0.018085 | 5.0801e-05
2012-09-05 | 279401 | MFN15A | Rural short | Feeder MFN15A - Planned | 8 | 404 | 3232 | 0.0093822 | 2.3223e-05
2012-09-05 | 279532 | AMR2 | Rural short | Feeder AMR2 - Planned | 11.02 | 377 | 4154.54 | 0.01206 | 3.199e-05
2012-09-06 | 279407 | TBV2 | Rural short | LV Transformer SP880-D TBV2 - Planned | 2.01 | 54 | 108.54 | 0.00031495 | 5.8324e-06
2012-09-06 | 279421 | GGR4 | Rural short | LV Transformer SP5114-B GGR4 - Planned | 2.01 | 184 | 369.84 | 0.0010732 | 5.8324e-06
2012-09-06 | 279423 | MGL1A | Rural short | LV Transformer SP2017-O MGL1A - Planned | 21 | 191 | 4011 | 0.011639 | 6.0936e-05
2012-09-06 | 279425 | MCW11 | Rural short | Feeder MCW11 - Planned | 51.56 | 353 | 18200.68 | 0.052813 | 0.00014961
2012-09-06 | 279426 | TGW3 | Rural short | Feeder TGW3 - Planned | 9.5 | 295 | 2802.5 | 0.008132 | 2.7566e-05
2012-09-06 | 279441 | MTB15A | Rural short | Feeder MTB15A - Planned | 16.4 | 446 | 7314.4 | 0.021224 | 4.7588e-05
2012-09-06 | 279442 | GGR1 | Rural short | Feeder GGR1 - Planned | 14.95 | 425 | 6353.75 | 0.018437 | 4.338e-05
2012-09-06 | 279443 | RBA1A | Urban | LV Transformer SP3007-F RBA1A - Planned | 8 | 457 | 3656 | 0.0036745 | 8.0405e-06
2012-09-06 | 279445 | CBW10 | Rural short | LV Transformer SP3601-E CBW10 - Planned | 19 | 356 | 6764 | 0.019627 | 5.5132e-05
2012-09-06 | 279446 | KWH1 | Rural short | Feeder KWH1 - Planned | 6.732 | 299 | 2012.868 | 0.0058407 | 1.9534e-05
2012-09-06 | 279447 | MLY3 | Rural short | Feeder MLY3 - Planned | 58.87 | 342 | 20133.54 | 0.058421 | 0.00017082
2012-09-06 | 279448 | BWH12A | Rural short | LV Transformer SP2276-C BWH12A - Planned | 10 | 295 | 2950 | 0.00856 | 2.9017e-05
2012-09-06 | 279449 | KCY4 | Rural short | LV Transformer SP12548-A KCY4 - Planned | 5.5 | 154 | 847 | 0.0024577 | 1.5959e-05
2012-09-06 | 279450 | AMR2 | Rural short | Feeder AMR2 - Planned | 20.109 | 241 | 4846.269 | 0.014062 | 5.835e-05
2012-09-06 | 279451 | TRP3 | Rural short | Feeder TRP3 - Planned | 4.02 | 322 | 1294.44 | 0.0037561 | 1.1665e-05
2012-09-06 | 279454 | ARG9A | Urban | LV Transformer SP5610-I ARG9A - Planned | 5.0004 | 95 | 475.038 | 0.00047744 | 5.0257e-06
2012-09-06 | 279455 | MLT15B | Urban | LV Transformer SP425-Q MLT15B - Planned | 3.675 | 180 | 661.5 | 0.00066485 | 3.6936e-06
2012-09-06 | 279456 | MLS11A | Urban | LV Transformer SG4783-H MLS15A - Planned | 18.26 | 324 | 5916.24 | 0.0059462 | 1.8352e-05
2012-09-06 | 279456 | MLS15A | Urban | LV Transformer SG4783-H MLS15A - Planned | 66.15 | 324 | 21432.6 | 0.021541 | 6.6485e-05
2012-09-06 | 279457 | BSEENG15 | Urban | LV Transformer SP2542-J BSEENG15 - Planned | 9.52 | 159 | 1513.68 | 0.0015213 | 9.5682e-06
2012-09-06 | 279458 | CMD5A | Urban | LV Transformer SP3804-B CMD5A - Planned | 29.5085 | 151 | 4455.7835 | 0.0044783 | 2.9658e-05
2012-09-06 | 279459 | GYGGYS6 | Rural short | LV Transformer SP738-C GYGGYS6 - Planned | 22 | 240 | 5280 | 0.015321 | 6.3837e-05
2012-09-06 | 279460 | BHD5A | Urban | LV Transformer SP651-G BHD5A - Planned | 12.56 | 183 | 2298.48 | 0.0023101 | 1.2624e-05
2012-09-06 | 279461 | MTB15A | Rural short | LV Transformer SP1675-F MTB15A - Planned | 3 | 360 | 1080 | 0.0031338 | 8.7051e-06
2012-09-06 | 279462 | YTA3B | Urban | LV Transformer SC1401791 - Planned | 2 | 54 | 108 | 0.00010855 | 2.0101e-06
2012-09-06 | 279463 | WSE6A | Rural short | LV Transformer SP12314-D WSE6A - Planned | 1 | 105 | 105 | 0.00030468 | 2.9017e-06
2012-09-06 | 279464 | GAP9A | Urban | LV Transformer SP2570-K GAP9A - Planned | 17.415 | 357 | 6217.155 | 0.0062486 | 1.7503e-05
2012-09-06 | 279465 | HTN24A | Urban | LV Transformer SP767-L HTN24A - Planned | 7.92 | 320 | 2534.4 | 0.0025472 | 7.9601e-06
2012-09-06 | 279466 | WNM3 | Urban | LV Transformer SP3267-J WNM3 - Planned | 1.35 | 35 | 47.25 | 4.7489e-05 | 1.3568e-06
2012-09-06 | 279467 | CFD6A | Urban | LV Transformer SP618-P CFD6A - Planned | 19.78 | 256 | 5063.68 | 0.0050893 | 1.988e-05
2012-09-06 | 279468 | BHL4A | Urban | LV Transformer SC1427101 BHL4A - Planned | 1.01 | 334 | 337.34 | 0.00033905 | 1.0151e-06
2012-09-06 | 279469 | HPE3A | Urban | LV Transformer SC3657-F HPE3A - Planned | 10.8163 | 355 | 3839.7865 | 0.0038592 | 1.0871e-05
2012-09-06 | 279470 | CHL10 | Urban | LV Transformer SP740760 CHL10 - Planned | 4.6 | 283 | 1301.8 | 0.0013084 | 4.6233e-06
2012-09-06 | 279471 | WED6A | Urban | LV Transformer SG3759-E WED6A - Planned | 8.28 | 156 | 1291.68 | 0.0012982 | 8.3219e-06
2012-09-06 | 279472 | LGL11A | Urban | LV Transformer SP3597-A LGL11A - Planned | 4.95 | 304 | 1504.8 | 0.0015124 | 4.9751e-06
2012-09-06 | 279473 | BDB4A | Rural short | LV Transformer SP18003-B BDB4A - Planned | 1.095 | 298 | 326.31 | 0.00094685 | 3.1774e-06
2012-09-06 | 279474 | MCW11 | Rural short | LV Transformer SP3415-B MCW11 - Planned | 5.115 | 465 | 2378.475 | 0.0069016 | 1.4842e-05
2012-09-06 | 279534 | THL3 | Rural short | Feeder THL3 - Planned | 7 | 285 | 1995 | 0.0057889 | 2.0312e-05
2012-09-07 | 279482 | ABY2A | Rural short | Feeder ABY2A - Planned | 10.45 | 122 | 1274.9 | 0.0036978 | 3.031e-05
2012-09-07 | 279483 | HMT3A | Urban | LV Transformer SC736245 HMT3A - Planned | 1.05 | 104 | 109.2 | 0.00010976 | 1.0554e-06
2012-09-07 | 279487 | KBR6A | Rural short | Feeder KBR6A - Planned | 23.2075 | 374 | 8679.605 | 0.025175 | 6.7313e-05
2012-09-07 | 279489 | SFD11 | Urban | LV Transformer SC2110-M SFD11 - Planned | 1 | 469 | 469 | 0.00047142 | 1.0052e-06
2012-09-07 | 279491 | PWC4 | Rural short | LV Transformer SP4401-B PWC4 - Planned | 13 | 296 | 3848 | 0.011161 | 3.7706e-05
2012-09-07 | 279492 | MLY6 | Rural short | Feeder PWC3, MLY6 - Planned | 15.77 | 382 | 6024.14 | 0.017473 | 4.5741e-05
2012-09-07 | 279492 | PWC3 | Rural short | Feeder PWC3, MLY6 - Planned | 82.395 | 382 | 31474.89 | 0.091293 | 0.00023899
2012-09-07 | 279493 | MFN15A | Rural short | Feeder MFN15A - Planned | 34.5 | 386 | 13317 | 0.038626 | 0.00010007
2012-09-07 | 279494 | YDA5A | Rural short | Feeder YDA5A - Planned | 8.04 | 309 | 2484.36 | 0.0072059 | 2.332e-05
2012-09-07 | 279495 | NMK23A | Urban | LV Transformer SP484248 NMK23A - Planned | 9.695 | 198 | 1919.61 | 0.0019295 | 9.745e-06
2012-09-07 | 279496 | AGE9 | Urban | LV Transformer SP2742-K AGE9 - Planned | 19.44 | 233 | 4529.52 | 0.0045529 | 1.954e-05
2012-09-07 | 279497 | CBW5 | Urban | LV Transformer SP3104-G CBW5 - Planned | 9.261 | 278 | 2574.558 | 0.0025878 | 9.3087e-06
2012-09-07 | 279498 | KCY2 | Rural short | LV Transformer SP4699-E KCY2 - Planned | 2 | 246 | 492 | 0.001427 | 5.801e-06
2012-09-07 | 279499 | GYN7A | Rural short | LV Transformer SP3115-C GYN7A - Planned | 6.0536 | 233 | 1410.4888 | 0.0040911 | 1.7558e-05
2012-09-07 | 279500 | YDA5A | Rural short | LV Transformer SP2847-A YDA5A - Planned | 11.04 | 197 | 2174.88 | 0.0063082 | 3.2021e-05
2012-09-07 | 279501 | CMD15A | Urban | LV Transformer SP5349-A CMD15A - Planned | 24.575 | 251 | 6168.325 | 0.0062001 | 2.4702e-05
2012-09-07 | 279502 | BTN2 | Rural short | LV Transformer SP5405-E BTN2 - Planned | 9.96 | 64 | 637.44 | 0.0018489 | 2.8889e-05
2012-09-07 | 279503 | MTB1B | Rural short | LV Transformer SP7191-E MTB1B - Planned | 15.12 | 109 | 1648.08 | 0.0047802 | 4.3856e-05
2012-09-07 | 279504 | BTN2 | Rural short | LV Transformer SP762250 BTN2 - Planned | 6 | 85 | 510 | 0.0014793 | 1.7403e-05
2012-09-07 | 279505 | PBH3 | Urban | LV Transformer SC750-H PBH3 - Planned | 6.7203 | 376 | 2526.8328 | 0.0025399 | 6.7549e-06
2012-09-07 | 279506 | BRT5 | Urban | LV Transformer SP1207-P BRT5 - Planned | 7.325 | 290 | 2124.25 | 0.0021352 | 7.3627e-06
2012-09-07 | 279507 | RCF1A | Urban | LV Transformer SP2228-G RCF1A - Planned | 6.6699 | 285 | 1900.9215 | 0.0019107 | 6.7043e-06
2012-09-07 | 279508 | MHL25A | Urban | LV Transformer SC581007 MHL25A - Planned | 1.125 | 25 | 28.125 | 2.827e-05 | 1.1308e-06
2012-09-07 | 279509 | SBH4 | Urban | LV Transformer SP3557-D SBH4 - Planned | 22.815 | 257 | 5863.455 | 0.0058937 | 2.2933e-05
2012-09-07 | 279510 | LTA5 | Urban | LV Transformer SC6246-F LTA5 - Planned | 1.1301 | 15 | 16.9515 | 1.7039e-05 | 1.1359e-06
2012-09-07 | 279511 | SBH4 | Urban | LV Transformer SP2620-G SBH4 - Planned | 17.1 | 330 | 5643 | 0.0056721 | 1.7188e-05
2012-09-07 | 279512 | MLT2B | Urban | LV Transformer SC801452 MLT2B - Planned | 13.416 | 217 | 2911.272 | 0.0029263 | 1.3485e-05
2012-09-07 | 279513 | HDA3A | Urban | LV Transformer SP3613-G HDA3A - Planned | 6.04 | 89 | 537.56 | 0.00054033 | 6.0711e-06
2012-09-07 | 279514 | SGT4 | Urban | LV Transformer SP2593-I SGT4 - Planned | 6.965 | 174 | 1211.91 | 0.0012182 | 7.0009e-06
2012-09-07 | 279515 | SBH4 | Urban | LV Transformer SP9052-D SBH6 - Planned | 4.575 | 202 | 924.15 | 0.00092891 | 4.5986e-06
2012-09-07 | 279515 | SBH6 | Urban | LV Transformer SP9052-D SBH6 - Planned | 14.025 | 202 | 2833.05 | 0.0028476 | 1.4097e-05
2012-09-07 | 279518 | HPK8A | Urban | LV Transformer SP24074-F HPK8A - Planned | 1.1349 | 100 | 113.49 | 0.00011407 | 1.1407e-06
2012-09-07 | 279519 | RCN3A | Urban | LV Transformer SC6116-J RCN3A - Planned | 22.44 | 365 | 8190.6 | 0.0082328 | 2.2556e-05
2012-09-07 | 279520 | HDN1 | Rural short | LV Transformer SP1171-C HDN1 - Planned | 3.0825 | 305 | 940.1625 | 0.0027269 | 8.9408e-06
2012-09-07 | 279521 | BDB28A | Urban | LV Transformer SC2457-G BDB28A - Planned | 0.74 | 264 | 195.36 | 0.00019637 | 7.4381e-07
2012-09-07 | 279533 | NRG16A | Rural short | Feeder NRG16A - Planned | 15 | 314 | 4710 | 0.013661 | 4.3507e-05
2012-09-08 | 279529 | LBS2A | Urban | Feeder LBS2A - Planned | 4 | 460 | 1840 | 0.0018496 | 4.0209e-06
2012-09-08 | 279530 | TGW3 | Rural short | LV Transformer SP2807-C TGW3 - Planned | 1 | 134 | 134 | 0.00038852 | 2.8994e-06
2012-09-08 | 279539 | MRK9 | Urban | LV Transformer SP2049080 MRK9 - Planned | 3.5625 | 112 | 399 | 0.00040109 | 3.5811e-06
2012-09-09 | 279541 | WCL17A | Urban | LV Transformer SP5524-G WCL17A - Planned | 12.04 | 295 | 3551.8 | 0.0035707 | 1.2104e-05
2012-09-09 | 279542 | FIS5A | Urban | LV Transformer SC793483 FIS5A - Planned | 1.056 | 309 | 326.304 | 0.00032804 | 1.0616e-06
2012-09-09 | 279544 | RPN6A | Rural short | LV Transformer SP1790-G RPN6A - Planned | 13.485 | 360 | 4854.6 | 0.01407 | 3.9083e-05
2012-09-09 | 279560 | MLT8B | Urban | LV Transformer SG1734770 MLT8B - Planned | 1.0197 | 165 | 168.2505 | 0.00016915 | 1.0251e-06
2012-09-09 | 279561 | NSD2B | Urban | LV Transformer SC3081-L NSD2B - Planned | 5.85 | 202 | 1181.7 | 0.001188 | 5.8811e-06
2012-09-09 | 279562 | AGE7B | Urban | LV Transformer SP1007-U AGE7B - Planned | 13.975 | 272 | 3801.2 | 0.0038214 | 1.4049e-05
2012-09-09 | 279563 | BMG44A | Urban | LV Transformer SG7206-H BMG44A - Planned | 0.798 | 103 | 82.194 | 8.2631e-05 | 8.0224e-07
2012-09-09 | 279564 | BHD31A | Urban | LV Transformer SP188-J BHD31A - Planned | 17.1612 | 384 | 6589.9008 | 0.0066249 | 1.7252e-05
2012-09-09 | 279565 | MDH3A | Urban | LV Transformer SC549498 MDH3A - Planned | 3.04 | 116 | 352.64 | 0.00035451 | 3.0562e-06
2012-09-09 | 279566 | NGE13 | Urban | LV Transformer SC6569-G NGE13 - Planned | 5.0076 | 94 | 470.7144 | 0.00047322 | 5.0342e-06
2012-09-09 | 279567 | HDA14A | Urban | LV Transformer SC547369 HDA14A - Planned | 6.125 | 59 | 361.375 | 0.0003633 | 6.1576e-06
2012-09-09 | 279568 | DRD5A | Urban | LV Transformer SP4179-E DRD5A - Planned | 24.3425 | 296 | 7205.38 | 0.0072437 | 2.4472e-05
2012-09-09 | 279569 | EMP22A | Urban | LV Transformer SC757368 EMP22A - Planned | 0.966 | 393 | 379.638 | 0.00038166 | 9.7114e-07
2012-09-09 | 279571 | LBS10A | Urban | LV Transformer SG11213-I LBS10A - Planned | 1 | 570 | 570 | 0.00057303 | 1.0053e-06
2012-09-10 | 279620 | CPD1 | Rural short | LV Transformer SP3296-A CPD1 - Planned | 1 | 290 | 290 | 0.00084018 | 2.8972e-06
2012-09-10 | 279641 | MTB15A | Rural short | Feeder MTB15A - Planned | 52.99 | 354 | 18758.46 | 0.054347 | 0.00015352
2012-09-10 | 279647 | CBW9 | Urban | LV Transformer SP5082-G CBW9 - Planned | 5 | 294 | 1470 | 0.0014779 | 5.027e-06
2012-09-10 | 279650 | LTA4A | Urban | LV Transformer SC1366822 - Planned | 13.3089 | 187 | 2488.7643 | 0.0025022 | 1.3381e-05
2012-09-10 | 279651 | SHW10A | Urban | LV Transformer SP23702-D SHW10A - Planned | 8.719 | 224 | 1953.056 | 0.0019636 | 8.7661e-06
2012-09-10 | 279652 | YDA5A | Rural short | LV Transformer SP3333-A YDA5A - Planned | 5.98 | 82 | 490.36 | 0.0014207 | 1.7325e-05
2012-09-10 | 279653 | CLM8 | Urban | LV Transformer SP41315-A CLM8 - Planned | 1.155 | 352 | 406.56 | 0.00040876 | 1.1612e-06
2012-09-10 | 279654 | BBH8A | Urban | LV Transformer SP43611-B BBH8A - Planned | 21.2 | 289 | 6126.8 | 0.0061599 | 2.1314e-05
2012-09-10 | 279655 | BHD3A | Urban | LV Transformer SP6394-D BHD3A - Planned | 42.795 | 71 | 3038.445 | 0.0030549 | 4.3026e-05
2012-09-10 | 279656 | SPO16A | Urban | LV Transformer SP3780-G SPO16A - Planned | 9.3 | 189 | 1757.7 | 0.0017672 | 9.3502e-06
2012-09-10 | 279657 | CPR6 | Urban | LV Transformer SP494969 CPR6 - Planned | 3.42 | 6 | 20.52 | 2.0631e-05 | 3.4385e-06
2012-09-10 | 279658 | NIP5B | Urban | LV Transformer SP12938-B NIP5B - Planned | 4.97 | 73 | 362.81 | 0.00036477 | 4.9968e-06
2012-09-10 | 279659 | PRG2A | Rural short | LV Transformer SP110-B PRG2A - Planned | 4.085 | 45 | 183.825 | 0.00053258 | 1.1835e-05
2012-09-11 | 279701 | KSN7 | Rural short | LV Transformer SP8647-B KSN7 - Planned | 13.5 | 212 | 2862 | 0.0082887 | 3.9098e-05
2012-09-11 | 279703 | IPL1 | Rural short | LV Transformer SP4095-D IPL1 - Planned | 5.2043 | 244 | 1269.8492 | 0.0036776 | 1.5072e-05
2012-09-11 | 279704 | IPL3 | Rural short | LV Transformer SP586-G IPL3 - Planned | 3 | 212 | 636 | 0.0018419 | 8.6884e-06
2012-09-11 | 279705 | KMR25A | Rural short | Feeder KMR25A - Planned | 34.99 | 345 | 12071.55 | 0.034961 | 0.00010134
2012-09-11 | 279706 | KMR25A | Rural short | Feeder KMR25A - Planned | 18 | 365 | 6570 | 0.019028 | 5.213e-05
2012-09-11 | 279720 | GBN4 | Rural short | LV Transformer SP6200-A GBN4 - Planned | 1.25 | 319 | 398.75 | 0.0011548 | 3.6202e-06
2012-09-11 | 279721 | MFN15A | Rural short | Feeder MFN15A - Planned | 7 | 278 | 1946 | 0.0056359 | 2.0273e-05
2012-09-11 | 279723 | BMT3 | Rural short | LV Transformer SP1495590 BMT3 - Planned | 2 | 161 | 322 | 0.00093255 | 5.7923e-06
2012-09-11 | 279724 | CBW6 | Rural short | LV Transformer SP1317-K CBW6 - Planned | 10 | 230 | 2300 | 0.0066611 | 2.8961e-05
2012-09-11 | 279726 | BVL5A | Urban | LV Transformer SP14087-B BVL5A - Planned | 1 | 420 | 420 | 0.0004223 | 1.0055e-06
2012-09-11 | 279727 | CRB25A | Rural short | Feeder CRB25A - Planned | 38.21 | 480 | 18340.8 | 0.053117 | 0.00011066
2012-09-11 | 279728 | SFD3 | Urban | LV Transformer SC4054-K SFD3 - Planned | 9.57 | 416 | 3981.12 | 0.0040029 | 9.6225e-06
2012-09-11 | 279729 | MGL5 | Urban | LV Transformer SC2561-M MGL5 - Planned | 4.2 | 46 | 193.2 | 0.00019426 | 4.223e-06
2012-09-11 | 279730 | MGL5 | Urban | LV Transformer SC2537-I MGL5 - Planned | 2.08 | 98 | 203.84 | 0.00020496 | 2.0914e-06
2012-09-11 | 279731 | AGE3 | Urban | LV Transformer SP13704-H - Planned | 17.4 | 289 | 5028.6 | 0.0050562 | 1.7495e-05
2012-09-11 | 279732 | NMK17A | Urban | LV Transformer SP2924-J NMK17A - Planned | 24.025 | 212 | 5093.3 | 0.0051212 | 2.4157e-05
2012-09-11 | 279733 | AHD10A | Urban | LV Transformer SP4019-A AHD10A - Planned | 7.8869 | 94 | 741.3686 | 0.00074543 | 7.9301e-06
2012-09-11 | 279734 | NBR8 | Rural short | LV Transformer SP4403-A NBR8 - Planned | 1 | 375 | 375 | 0.001086 | 2.8961e-06
2012-09-11 | 279735 | GYM8A | Rural short | LV Transformer SP10366-B GYM8A - Planned | 5.98 | 303 | 1811.94 | 0.0052476 | 1.7319e-05
2012-09-11 | 279736 | AHD19 | Urban | LV Transformer SP3786-A AHD19 - Planned | 7.8 | 56 | 436.8 | 0.00043919 | 7.8428e-06
2012-09-11 | 279737 | BHD23A | Rural short | LV Transformer SP5705-F BHD23A - Planned | 6.235 | 60 | 374.1 | 0.0010834 | 1.8057e-05
2012-09-11 | 279738 | SPO32A | Urban | LV Transformer SP40515-A SPO32A - Planned | 3.275 | 330 | 1080.75 | 0.0010867 | 3.293e-06
2012-09-11 | 279739 | MDR8A | Urban | LV Transformer SP3180-G MDR8A - Planned | 3 | 195 | 585 | 0.00058821 | 3.0164e-06
2012-09-11 | 279740 | MTB1B | Rural short | LV Transformer SP6074-B MTB1B - Planned | 22.5 | 183 | 4117.5 | 0.011925 | 6.5163e-05
2012-09-11 | 279741 | SBH4 | Urban | LV Transformer SP5046-G SBH4 - Planned | 4.03 | 234 | 943.02 | 0.00094819 | 4.0521e-06
2012-09-11 | 279741 | SBH8 | Urban | LV Transformer SP5046-G SBH4 - Planned | 19 | 234 | 4446 | 0.0044704 | 1.9104e-05
2012-09-11 | 279742 | SBH4 | Urban | LV Transformer SP1306-I SBH4 - Planned | 13.775 | 223 | 3071.825 | 0.0030887 | 1.3851e-05
2012-09-11 | 279743 | BRT6 | Urban | LV Transformer SP2443-G BRT6 - Planned | 33 | 108 | 3564 | 0.0035835 | 3.3181e-05
2012-09-11 | 279744 | HDA3A | Urban | LV Transformer SP1050781 HDA3A - Planned | 17.59 | 368 | 6473.12 | 0.0065086 | 1.7686e-05
2012-09-11 | 279745 | DRD2A | Rural short | LV Transformer SP4636-D DRD2A - Planned | 3.4449 | 54 | 186.0246 | 0.00053875 | 9.9769e-06
2012-09-11 | 279746 | RCN3A | Urban | LV Transformer SC5216-M RCN6A - Planned | 1.32 | 328 | 432.96 | 0.00043533 | 1.3272e-06
2012-09-11 | 279746 | RCN6A | Urban | LV Transformer SC5216-M RCN6A - Planned | 6.89 | 328 | 2259.92 | 0.0022723 | 6.9278e-06
2012-09-11 | 279747 | SBY4 | Urban | LV Transformer SC1036892 SBY4 - Planned | 57.8592 | 220 | 12729.024 | 0.012799 | 5.8176e-05
2012-09-11 | 279748 | HPK8A | Urban | LV Transformer SP2864-G HPK8A - Planned | 6.8 | 240 | 1632 | 0.0016409 | 6.8373e-06
2012-09-11 | 279749 | MWMRBK11 | Rural short | LV Transformer SP13034-C MWMRBK11 - Planned | 3.5 | 272 | 952 | 0.0027571 | 1.0136e-05
2012-09-12 | 279761 | BBSRDL8 | Rural short | LV Transformer SP6205-D BBSRDL8 - Planned | 11 | 355 | 3905 | 0.011305 | 3.1846e-05
2012-09-12 | 279763 | BHD5A | Urban | LV Transformer SG761353 BHD5A - Planned | 2 | 275 | 550 | 0.00055306 | 2.0111e-06
2012-09-12 | 279764 | TGW2 | Rural short | Feeder TGW2 - Planned | 22.56 | 405 | 9136.8 | 0.026451 | 6.5312e-05
2012-09-12 | 279765 | BNH6A | Rural short | Feeder BNH6A - Planned | 55 | 433 | 23815 | 0.068946 | 0.00015923
2012-09-12 | 279766 | EMD3 | Rural short | Feeder EMD3 - Planned | 3.436 | 378 | 1298.808 | 0.0037601 | 9.9474e-06
2012-09-12 | 279767 | GYN7A | Rural short | LV Transformer SP7620-C GYN7A - Planned | 1 | 132 | 132 | 0.00038215 | 2.895e-06
2012-09-12 | 279769 | NRA5A | Rural short | LV Transformer SP7018-F NRA5A - Planned | 1.5 | 485 | 727.5 | 0.0021061 | 4.3426e-06
2012-09-12 | 279770 | LLY1 | Rural short | Feeder LLY3, LLY1 - Planned | 54.5 | 535 | 29157.5 | 0.084412 | 0.00015778
2012-09-12 | 279770 | LLY3 | Rural short | Feeder LLY3, LLY1 - Planned | 58 | 535 | 31030 | 0.089833 | 0.00016791
2012-09-12 | 279771 | MGL5 | Urban | LV Transformer SC22107-F MGL5 - Planned | 14.16 | 120 | 1699.2 | 0.0017087 | 1.4239e-05
2012-09-12 | 279772 | MGL5 | Urban | LV Transformer SC5053-J MGL5 - Planned | 1.04 | 83 | 86.32 | 8.68e-05 | 1.0458e-06
2012-09-12 | 279773 | PGN1B | Rural short | LV Transformer SP2158-C PGN1B - Planned | 76.36 | 146 | 11148.56 | 0.032276 | 0.00022107
2012-09-12 | 279774 | CMD13A | Urban | LV Transformer SP3474-A CMD13A - Planned | 27.06 | 227 | 6142.62 | 0.0061768 | 2.7211e-05
2012-09-12 | 279776 | BLH10B | Urban | LV Transformer SP78764 BLH10B - Planned | 14.8126 | 230 | 3406.898 | 0.0034259 | 1.4895e-05
2012-09-12 | 279777 | BHD3A | Urban | LV Transformer SP5169-G BHD3A - Planned | 26.2 | 345 | 9039 | 0.0090893 | 2.6346e-05
2012-09-12 | 279778 | MAI11 | Urban | LV Transformer SP11978-D MAI11 - Planned | 58.32 | 400 | 23328 | 0.023458 | 5.8644e-05
2012-09-12 | 279779 | MTB1B | Rural short | LV Transformer SP7271-C MTB1B - Planned | 9.5 | 298 | 2831 | 0.0081959 | 2.7503e-05
2012-09-12 | 279780 | HMT10A | Urban | LV Transformer SP16227-D HMT10A - Planned | 22.05 | 179 | 3946.95 | 0.0039689 | 2.2173e-05
2012-09-12 | 279782 | BRT3 | Urban | LV Transformer SP2862-H BRT3 - Planned | 5.11 | 297 | 1517.67 | 0.0015261 | 5.1384e-06
2012-09-12 | 279783 | ZMR4A | Urban | LV Transformer SC581934 ZMR4A - Planned | 1.445 | 35 | 50.575 | 5.0856e-05 | 1.453e-06
2012-09-12 | 279784 | CSE6 | Urban | LV Transformer SP11109-E CSE6 - Planned | 6.606 | 376 | 2483.856 | 0.0024977 | 6.6428e-06
2012-09-12 | 279785 | SBH11 | Urban | LV Transformer SP16790-D SBH11 - Planned | 6.93 | 335 | 2321.55 | 0.0023345 | 6.9686e-06
2012-09-12 | 279786 | HPK8A | Urban | LV Transformer SP1923-I HPK8A - Planned | 2.78 | 352 | 978.56 | 0.000984 | 2.7955e-06
2012-09-12 | 279787 | ARG9A | Urban | LV Transformer SP3318-M ARG9A - Planned | 15.0423 | 304 | 4572.8592 | 0.0045983 | 1.5126e-05
2012-09-12 | 279788 | BDB28A | Urban | LV Transformer SP3865-D BDB28A - Planned | 8.96 | 376 | 3368.96 | 0.0033877 | 9.0098e-06
2012-09-12 | 279788 | MWMRBK11 | Rural short | LV Transformer SP3865-D BDB28A - Planned | 18.76 | 376 | 7053.76 | 0.020421 | 5.4311e-05
2012-09-12 | 279789 | NIP1A | Urban | LV Transformer SP1606-D NIP1A - Planned | 23.1 | 250 | 5775 | 0.0058071 | 2.3229e-05
2012-09-12 | 279790 | THL3 | Rural short | LV Transformer SP1341-C THL3 - Planned | 2.01 | 388 | 779.88 | 0.0022578 | 5.819e-06
2012-09-12 | 279791 | CPD2A | Rural short | LV Transformer SP2808-D CPD2A - Planned | 3 | 385 | 1155 | 0.0033438 | 8.6851e-06
2012-09-12 | 279792 | SPF12B | Urban | LV Transformer SC1413108 SPF12B - Planned | 8.37 | 155 | 1297.35 | 0.0013046 | 8.4166e-06
2012-09-12 | 280927 | TCB1 | Rural short | LV Transformer SP95125-A TCB1 - Planned | 7.905 | 129 | 1019.745 | 0.0029522 | 2.2885e-05
2012-09-13 | 279821 | MCW7 | Rural short | LV Transformer SP14018-B MCW7 - Planned | 1 | 240 | 240 | 0.00069455 | 2.894e-06
2012-09-13 | 279841 | CRB25A | Rural short | Feeder CRB25A - Planned | 5.594 | 445 | 2489.33 | 0.007204 | 1.6189e-05
2012-09-13 | 279842 | THL3 | Rural short | LV Transformer SP775234 THL3 - Planned | 2 | 402 | 804 | 0.0023267 | 5.7879e-06
2012-09-13 | 279843 | GGR1 | Rural short | Feeder GGR1 - Planned | 18 | 502 | 9036 | 0.02615 | 5.2091e-05
2012-09-13 | 279844 | YDA3A | Rural short | LV Transformer SP16515-A YDA3A - Planned | 2.01 | 419 | 842.19 | 0.0024373 | 5.8169e-06
2012-09-13 | 279845 | CBW11 | Rural short | Feeder CBW11 - Planned | 4 | 480 | 1920 | 0.0055564 | 1.1576e-05
2012-09-13 | 279846 | NGI3A | Rural short | Feeder NGI3A - Planned | 9 | 404 | 3636 | 0.010522 | 2.6046e-05
2012-09-13 | 279847 | BWH16A | Rural short | LV Transformer SP9554-A BWH16A - Planned | 33.575 | 318 | 10676.85 | 0.030898 | 9.7165e-05
2012-09-13 | 279848 | AMR3 | Rural short | LV Transformer SP307-D AMR3 - Planned | 3.67 | 273 | 1001.91 | 0.0028995 | 1.0621e-05
2012-09-13 | 279850 | KMR25A | Rural short | Feeder KMR25A - Planned | 130.7 | 8 | 1045.6 | 0.0030259 | 0.00037824
2012-09-13 | 279853 | MLT21B | Urban | LV Transformer SP4436-J MLT21B - Planned | 29.8325 | 267 | 7965.2775 | 0.0080102 | 3.0001e-05
2012-09-13 | 279854 | SFD10 | Urban | LV Transformer SP14089-G SFD3 - Planned | 1.2 | 281 | 337.2 | 0.0003391 | 1.2068e-06
2012-09-13 | 279854 | SFD4 | Urban | LV Transformer SP14089-G SFD3 - Planned | 6.7002 | 281 | 1882.7562 | 0.0018934 | 6.738e-06
2012-09-13 | 279855 | CSE2 | Urban | LV Transformer SP2227-Q CSE2 - Planned | 1.8 | 278 | 500.4 | 0.00050322 | 1.8102e-06
2012-09-13 | 279856 | TCB1 | Rural short | LV Transformer SP2328-C TCB1 - Planned | 3.0532 | 185 | 564.842 | 0.0016346 | 8.8358e-06
2012-09-13 | 279857 | TCB1 | Rural short | LV Transformer SP6745-C TCB1 - Planned | 1.9566 | 90 | 176.094 | 0.00050961 | 5.6623e-06
2012-09-13 | 279858 | GBN4 | Rural short | LV Transformer SP9357-B GBN4 - Planned | 2.125 | 41 | 87.125 | 0.00025214 | 6.1497e-06
2012-09-13 | 279859 | BBH8A | Urban | LV Transformer SP4560-G BBH8A - Planned | 24.6 | 492 | 12103.2 | 0.012172 | 2.4739e-05
2012-09-13 | 279860 | SPO16A | Urban | LV Transformer SP1433-K SPO16A - Planned | 12.485 | 200 | 2497 | 0.0025111 | 1.2555e-05
2012-09-13 | 279861 | MTB1B | Rural short | LV Transformer SP5539-B MTB1B - Planned | 48.22 | 318 | 15333.96 | 0.044376 | 0.00013955
2012-09-13 | 279862 | SGT3 | Urban | LV Transformer SP4493-M SGT3 - Planned | 3.3256 | 121 | 402.3976 | 0.00040467 | 3.3444e-06
2012-09-13 | 279863 | DRD13A | Urban | LV Transformer SP2764-F DRD5A - Planned | 1.14 | 298 | 339.72 | 0.00034164 | 1.1464e-06
2012-09-13 | 279863 | DRD5A | Urban | LV Transformer SP2764-F DRD5A - Planned | 41.5156 | 298 | 12371.6488 | 0.012441 | 4.175e-05
2012-09-13 | 279864 | SFD9 | Urban | LV Transformer SC3203-L SFD9 - Planned | 15.95 | 243 | 3875.85 | 0.0038977 | 1.604e-05
2012-09-13 | 279865 | NDH6 | Urban | LV Transformer SP2821-I NDH6 - Planned | 23.885 | 368 | 8789.68 | 0.0088393 | 2.402e-05
2012-09-13 | 279866 | UMG12A | Urban | LV Transformer SC4058-G UMG12A - Planned | 79.2 | 295 | 23364 | 0.023496 | 7.9647e-05
2012-09-13 | 279867 | TMH15A | Urban | LV Transformer SP5525-E TMH15A - Planned | 23.76 | 214 | 5084.64 | 0.0051133 | 2.3894e-05
2012-09-13 | 279868 | KMR25A | Rural short | LV Transformer SP5071-K KMR25A - Planned | 11 | 545 | 5995 | 0.017349 | 3.1834e-05
2012-09-13 | 279938 | NSW3A | Urban | LV Transformer SP9471-F NSW3A - Planned | 0.885 | 1638 | 1449.63 | 0.0014578 | 8.8999e-07
2012-09-14 | 279880 | BMT2 | Rural short | LV Transformer SP996-C BMT2 - Planned | 11.96 | 155 | 1853.8 | 0.0053628 | 3.4599e-05
2012-09-14 | 279901 | TGW2 | Rural short | Feeder TGW2 - Planned | 29.71 | 259 | 7694.89 | 0.02226 | 8.5947e-05
2012-09-14 | 279902 | MGP2A | Urban | LV Transformer SP6328-D MGP2A - Planned | 28 | 204 | 5712 | 0.0057447 | 2.816e-05
2012-09-14 | 279903 | MLY6 | Rural short | LV Transformer SP4367-B MLY6 - Planned | 12 | 270 | 3240 | 0.0093729 | 3.4714e-05
2012-09-14 | 279904 | IPL1 | Rural short | Feeder IPL1 - Planned | 36.77 | 228 | 8383.56 | 0.024253 | 0.00010637
2012-09-14 | 279905 | GBN4 | Rural short | Feeder GBN4 - Planned | 6.02 | 266 | 1601.32 | 0.0046324 | 1.7415e-05
2012-09-14 | 279906 | GYN7A | Rural short | LV Transformer SP3826-B GYN7A - Planned | 0.4 | 348 | 139.2 | 0.00040269 | 1.1571e-06
2012-09-14 | 279907 | PWC4 | Rural short | LV Transformer SP2059-C PWC4 - Planned | 30.07 | 273 | 8209.11 | 0.023748 | 8.6989e-05
2012-09-14 | 279908 | KCY2 | Rural short | Feeder KCY2 - Planned | 51.35 | 295 | 15148.25 | 0.043822 | 0.00014855
2012-09-14 | 279909 | KLG16A | Rural short | LV Transformer SP5083-F KLG16A - Planned | 45.5 | 384 | 17472 | 0.050544 | 0.00013163
2012-09-14 | 279924 | HTL2A | Urban | LV Transformer SG6469-H HTL2A - Planned | 1.0974 | 433 | 475.1742 | 0.00047789 | 1.1037e-06
2012-09-14 | 279925 | SFD6B | Urban | LV Transformer SP442-P SFD6B - Planned | 3.27 | 275 | 899.25 | 0.0009044 | 3.2887e-06
2012-09-14 | 279926 | AHL8A | Urban | LV Transformer SP548710 AHL8A - Planned | 46.53 | 350 | 16285.5 | 0.016379 | 4.6796e-05
2012-09-14 | 279927 | GAP4A | Urban | LV Transformer SP199-R GAP4A - Planned | 4.94 | 295 | 1457.3 | 0.0014656 | 4.9683e-06
2012-09-14 | 279928 | GYN7A | Rural short | LV Transformer SP3932-C GYN7A - Planned | 3.375 | 273 | 921.375 | 0.0026654 | 9.7634e-06
2012-09-14 | 279929 | MDR12B | Urban | LV Transformer SP3498-E MDR12B - Planned | 34.89 | 129 | 4500.81 | 0.0045266 | 3.509e-05
2012-09-14 | 279929 | MDR24A | Urban | LV Transformer SP3498-E MDR12B - Planned | 3.8664 | 129 | 498.7656 | 0.00050162 | 3.8885e-06
2012-09-14 | 279930 | BHD35A | Rural short | LV Transformer SP610-I BHD35A - Planned | 6.265 | 127 | 795.655 | 0.0023017 | 1.8124e-05
2012-09-14 | 279931 | PBH2B | Urban | LV Transformer SP3503-E PBH2B - Planned | 46.06 | 230 | 10593.8 | 0.010654 | 4.6324e-05
2012-09-14 | 279932 | HTL6A | Urban | LV Transformer SC1512817 HTL6A - Planned | 5 | 245 | 1225 | 0.001232 | 5.0286e-06
2012-09-14 | 279933 | SMF2A | Rural short | LV Transformer SP3574-D SMF2A - Planned | 3.375 | 70 | 236.25 | 0.00068344 | 9.7634e-06
2012-09-14 | 279934 | CPR4 | Urban | LV Transformer SP3805-G CPR4 - Planned | 23.7294 | 97 | 2301.7518 | 0.0023149 | 2.3865e-05
2012-09-14 | 279935 | GBP6 | Urban | LV Transformer SC798383 GBP6 - Planned | 22.56 | 265 | 5978.4 | 0.0060126 | 2.2689e-05
2012-09-14 | 279936 | GCLSBK5 | Urban | LV Transformer SP4255-J GCLSBK5 - Planned | 3.4875 | 232 | 809.1 | 0.00081373 | 3.5075e-06
2012-09-14 | 279937 | HPK8A | Urban | LV Transformer SP2864-G HPK8A - Planned | 13.44 | 330 | 4435.2 | 0.0044606 | 1.3517e-05
2012-09-14 | 279939 | CPD2A | Rural short | LV Transformer SP1810-C CPD2A - Planned | 4.98 | 134 | 667.32 | 0.0019305 | 1.4407e-05
2012-09-14 | 279940 | FDS3 | Rural short | LV Transformer SP4382-F FDS3 - Planned | 4.11 | 362 | 1487.82 | 0.0043041 | 1.189e-05
2012-09-14 | 280161 | FDS3 | Rural short | LV Transformer SP4227-E FDS3 - Planned | 2.01 | 450 | 904.5 | 0.0026166 | 5.8147e-06
2012-09-15 | 279946 | LWD1 | Rural short | LV Transformer SP3129-B LWD1 - Planned | 5 | 77 | 385 | 0.0011133 | 1.4458e-05
2012-09-15 | 279988 | HPK3A | Urban | LV Transformer SP3312-I HPK3A - Planned | 4.04 | 206 | 832.24 | 0.00083709 | 4.0635e-06
2012-09-15 | 279988 | HPK8A | Urban | LV Transformer SP3312-I HPK3A - Planned | 2.07 | 206 | 426.42 | 0.0004289 | 2.0821e-06
2012-09-16 | 279970 | LBH6A | Rural short | LV Transformer SP178-B LBH6A - Planned | 16.1 | 80 | 1288 | 0.0037228 | 4.6535e-05
2012-09-16 | 279972 | CMD15A | Urban | LV Transformer SP16431-A CMD15A - Planned | 8 | 215 | 1720 | 0.0017302 | 8.0474e-06
2012-09-16 | 279974 | CBT13A | Urban | Feeder CBT13A - Planned | 42 | 355 | 14910 | 0.014998 | 4.2249e-05
2012-09-16 | 279975 | BWH8A | Rural short | Feeder BWH8A - Planned | 4.11 | 276 | 1134.36 | 0.0032787 | 1.1879e-05
2012-09-16 | 279976 | BHD41A | Urban | LV Transformer SP11986-E BHD41A - Planned | 18.05 | 363 | 6552.15 | 0.006591 | 1.8157e-05
2012-09-16 | 279977 | HMT10A | Urban | LV Transformer SP16227-D HMT10A - Planned | 45 | 395 | 17775 | 0.01788 | 4.5267e-05
2012-09-16 | 279978 | TWT15A | Rural short | Feeder TWT15A - Planned | 21.05 | 350 | 7367.5 | 0.021295 | 6.0842e-05
2012-09-16 | 279979 | BWH13A | Rural short | LV Transformer SP12054-B BWH13A - Planned | 0.4 | 225 | 90 | 0.00026013 | 1.1561e-06
2012-09-16 | 279980 | NMK18 | Urban | LV Transformer SG1009-P NMK18 - Planned | 2.033 | 394 | 801.002 | 0.00080575 | 2.0451e-06
2012-09-16 | 279981 | NMK5 | Urban | LV Transformer SP6595-I NMK5 - Planned | 40.6885 | 386 | 15705.761 | 0.015799 | 4.093e-05
2012-09-16 | 279982 | HDA14A | Urban | LV Transformer SC581325 HDA14A - Planned | 1.02 | 33 | 33.66 | 3.386e-05 | 1.026e-06
2012-09-16 | 279983 | NDH6 | Urban | LV Transformer SP1341-J NDH6 - Planned | 37.8 | 349 | 13192.2 | 0.01327 | 3.8024e-05
2012-09-16 | 279984 | HDA14A | Urban | LV Transformer SC581325 HDA14A - Planned | 1.02 | 44 | 44.88 | 4.5146e-05 | 1.026e-06
2012-09-16 | 279985 | NDH6 | Urban | LV Transformer SG1939-I NDH6 - Planned | 5.42 | 323 | 1750.66 | 0.001761 | 5.4521e-06
2012-09-16 | 279986 | ARG5A | Urban | LV Transformer SP2138-L ARG5A - Planned | 18 | 195 | 3510 | 0.0035308 | 1.8107e-05
2012-09-16 | 279987 | UMG2B | Rural short | LV Transformer SP3990-G UMG2B - Planned | 23.9133 | 247 | 5906.5851 | 0.017072 | 6.9118e-05
2012-09-17 | 280024 | RWD1 | Rural short | LV Transformer SP1203-H RWD1 - Planned | 6 | 66 | 396 | 0.0011442 | 1.7336e-05
2012-09-17 | 280029 | BDB32A | Rural short | LV Transformer SP4066-D BDB32A - Planned | 1 | 85 | 85 | 0.00024559 | 2.8893e-06
2012-09-17 | 280032 | LLY3 | Rural short | LV Transformer SP15610-B LLY3 - Planned | 14 | 197 | 2758 | 0.0079687 | 4.045e-05
2012-09-17 | 280040 | IPL3 | Rural short | Feeder IPL3 - Planned | 14 | 291 | 4074 | 0.011771 | 4.045e-05
2012-09-17 | 280041 | BNH1B | Rural short | LV Transformer SP895-F BNH1B - Planned | 4 | 322 | 1288 | 0.0037214 | 1.1557e-05
2012-09-17 | 280042 | CMA8A | Rural short | LV Transformer SP5300-C CMA8A - Planned | 11.04 | 376 | 4151.04 | 0.011994 | 3.1898e-05
2012-09-17 | 280043 | CRB25A | Rural short | Feeder CRB25A - Planned | 3 | 525 | 1575 | 0.0045507 | 8.6679e-06
2012-09-17 | 280044 | GBN4 | Rural short | Feeder GBN4 - Planned | 13.03 | 385 | 5016.55 | 0.014494 | 3.7648e-05
2012-09-17 | 280045 | NBR7 | Urban | LV Transformer SP4489-A NBR7 - Planned | 88.35 | 391 | 34544.85 | 0.034753 | 8.8881e-05
2012-09-17 | 280048 | TRG2A | Urban | LV Transformer SP16127-F TRG2A - Planned | 16.4906 | 187 | 3083.7422 | 0.0031023 | 1.659e-05
2012-09-17 | 280049 | WMR1 | Rural short | LV Transformer SP17618-D WMR1 - Planned | 1 | 110 | 110 | 0.00031782 | 2.8893e-06
2012-09-17 | 280049 | WMR2 | Rural short | LV Transformer SP17618-D WMR1 - Planned | 2 | 110 | 220 | 0.00063565 | 5.7786e-06
2012-09-17 | 280050 | SFD4 | Urban | LV Transformer SC3533-J SFD4 - Planned | 5.5835 | 290 | 1619.215 | 0.001629 | 5.6171e-06
2012-09-17 | 280051 | NRG16A | Rural short | LV Transformer SP1491-I NRG16A - Planned | 1.04 | 551 | 573.04 | 0.0016557 | 3.0049e-06
2012-09-17 | 280052 | AHD5 | Urban | LV Transformer SP4060-A AHD5 - Planned | 22.525 | 142 | 3198.55 | 0.0032178 | 2.266e-05
2012-09-17 | 280053 | MAI11 | Urban | LV Transformer SP1583-G MAI11 - Planned | 19.7397 | 301 | 5941.6497 | 0.0059774 | 1.9858e-05
2012-09-17 | 280054 | NRG2A | Urban | LV Transformer SC919-I NRG2A - Planned | 30.1 | 55 | 1655.5 | 0.0016655 | 3.0281e-05
2012-09-17 | 280055 | BRT5 | Urban | LV Transformer SP1207-P BRT5 - Planned | 7.325 | 198 | 1450.35 | 0.0014591 | 7.369e-06
2012-09-17 | 280056 | DRD15B | Urban | LV Transformer SP429-G DRD15B - Planned | 7.0625 | 360 | 2542.5 | 0.0025578 | 7.105e-06
2012-09-17 | 280058 | CSE4 | Urban | LV Transformer SP3569-G CSE4 - Planned | 6.37 | 335 | 2133.95 | 0.0021468 | 6.4083e-06
2012-09-17 | 280059 | ZMR9 | Urban | LV Transformer SP28442-A ZMR9 - Planned | 20.57 | 220 | 4525.4 | 0.0045526 | 2.0694e-05
2012-09-17 | 280060 | RLA2 | Urban | LV Transformer SP5126-H RLA2 - Planned | 11.13 | 277 | 3083.01 | 0.0031015 | 1.1197e-05
2012-09-17 | 280060 | RLA5 | Urban | LV Transformer SP5126-H RLA2 - Planned | 0.9433 | 277 | 261.2941 | 0.00026287 | 9.4897e-07
2012-09-17 | 280061 | LLY3 | Rural short | LV Transformer SP2222-D LLY3 - Planned | 7.04 | 319 | 2245.76 | 0.0064887 | 2.0341e-05
2012-09-17 | 280063 | NRG16A | Rural short | Feeder NRG16A - Planned | 39 | 614 | 23946 | 0.069187 | 0.00011268
2012-09-18 | 280080 | CCYUPC2 | Urban | Feeder CCYUPC2 - Planned | 3.5 | 164 | 574 | 0.0005775 | 3.5213e-06
2012-09-18 | 280100 | NBR1 | Rural short | LV Transformer SP9901-A NBR1 - Planned | 18.9 | 148 | 2797.2 | 0.008079 | 5.4588e-05
2012-09-18 | 280120 | MTB1B | Rural short | Feeder MTB1B - Planned | 29.51 | 351 | 10358.01 | 0.029916 | 8.5232e-05
2012-09-18 | 280140 | BTA1A | Urban | LV Transformer SP6640-C BTA1A - Planned | 17.5 | 335 | 5862.5 | 0.0058982 | 1.7607e-05
2012-09-18 | 280141 | MGP13A | Rural short | Feeder MGP13A - Planned | 12 | 374 | 4488 | 0.012962 | 3.4659e-05
2012-09-18 | 280162 | LLY4 | Rural short | Feeder LLY4 - Planned | 9.01 | 595 | 5360.95 | 0.015484 | 2.6023e-05
2012-09-18 | 280166 | EMD3 | Rural short | Feeder EMD3 - Planned | 8 | 415 | 3320 | 0.009589 | 2.3106e-05
2012-09-18 | 280168 | NMK18 | Urban | LV Transformer SP3218-K NMK18 - Planned | 69.0749 | 385 | 26593.8365 | 0.026756 | 6.9496e-05
2012-09-18 | 280169 | ZMR4A | Urban | LV Transformer SC4483-H ZMR4A - Planned | 4.98 | 207 | 1030.86 | 0.0010371 | 5.0104e-06
2012-09-18 | 280170 | KRN18A | Urban | LV Transformer SP881-M KRN18A - Planned | 5.23 | 310 | 1621.3 | 0.0016312 | 5.2619e-06
2012-09-18 | 280171 | MGL5 | Urban | LV Transformer SC5451-H MGL5 - Planned | 39.02 | 263 | 10262.26 | 0.010325 | 3.9258e-05
2012-09-18 | 280172 | NMK17A | Urban | LV Transformer SP3301-M NMK17A - Planned | 12.54 | 203 | 2545.62 | 0.0025611 | 1.2616e-05
2012-09-18 | 280173 | KRN10 | Urban | LV Transformer SP1515-P KRN10 - Planned | 32.67 | 246 | 8036.82 | 0.0080858 | 3.2869e-05
2012-09-18 | 280174 | JDL7 | Urban | LV Transformer SC4755-G JDL7 - Planned | 41.23 | 220 | 9070.6 | 0.0091259 | 4.1481e-05
2012-09-18 | 280175 | EMD2 | Rural short | LV Transformer SP11395-A EMD2 - Planned | 11.96 | 129 | 1542.84 | 0.0044561 | 3.4543e-05
2012-09-18 | 280176 | GYM7A | Rural short | LV Transformer SP1044-E GYM7A - Planned | 1.04 | 194 | 201.76 | 0.00058273 | 3.0038e-06
2012-09-18 | 280177 | CLD25A | Urban | LV Transformer SP415-A CLD25A - Planned | 16.3761 | 430 | 7041.723 | 0.0070847 | 1.6476e-05
2012-09-18 | 280178 | MLB3A | Rural short | LV Transformer SP4562-B MLB3A - Planned | 2.65 | 248 | 657.2 | 0.0018982 | 7.6538e-06
2012-09-18 | 280179 | MMC20A | Urban | LV Transformer SC1641-F MMC20A - Planned | 1.83 | 82 | 150.06 | 0.00015098 | 1.8412e-06
2012-09-18 | 280180 | MTB1B | Rural short | LV Transformer SP5538-B MTB1B - Planned | 1.21 | 293 | 354.53 | 0.001024 | 3.4948e-06
2012-09-18 | 280181 | MMC30A | Urban | LV Transformer SC741448 MMC30A - Planned | 13.115 | 125 | 1639.375 | 0.0016494 | 1.3195e-05
2012-09-18 | 280182 | SGT22A | Urban | LV Transformer SP3157-F SGT22A - Planned | 6.935 | 271 | 1879.385 | 0.0018908 | 6.9773e-06
2012-09-18 | 280183 | DRD5A | Urban | LV Transformer SP4991-F DRD5A - Planned | 15.46 | 120 | 1855.2 | 0.0018665 | 1.5554e-05
2012-09-18 | 280184 | DRD13A | Urban | LV Transformer SP5093-E DRD13A - Planned | 9.525 | 209 | 1990.725 | 0.0020029 | 9.5831e-06
2012-09-18 | 280185 | ACR2B | Urban | LV Transformer SC23103-D ACR2B - Planned | 7.07 | 76 | 537.32 | 0.0005406 | 7.1131e-06
2012-09-18 | 280186 | RCF1A | Urban | LV Transformer SP1303-H RCF1A - Planned | 25.5 | 340 | 8670 | 0.0087229 | 2.5655e-05
2012-09-18 | 280187 | RCN3A | Urban | LV Transformer SC6116-J RCN3A - Planned | 2.64 | 137 | 361.68 | 0.00036389 | 2.6561e-06
2012-09-18 | 280188 | LGL3A | Urban | LV Transformer SP4898-B LGL3A - Planned | 15.075 | 236 | 3557.7 | 0.0035794 | 1.5167e-05
2012-09-18 | 280189 | RLB15A | Urban | LV Transformer SP4344-E RLB15A - Planned | 12.36 | 68 | 840.48 | 0.00084561 | 1.2435e-05
2012-09-18 | 280190 | SBK9 | Urban | LV Transformer SG1976-H SBK9 - Planned | 6.93 | 61 | 422.73 | 0.00042531 | 6.9723e-06
2012-09-18 | 280191 | BKD13A | Urban | LV Transformer SP10654-A BKD13A - Planned | 1.95 | 210 | 409.5 | 0.000412 | 1.9619e-06
2012-09-18 | 280192 | TRP2 | Rural short | LV Transformer SP4003-B TRP2 - Planned | 8.455 | 49 | 414.295 | 0.0011966 | 2.442e-05
2012-09-18 | 280193 | NIP1A | Urban | LV Transformer SP15559-B NIP1A - Planned | 38.625 | 330 | 12746.25 | 0.012824 | 3.8861e-05
2012-09-18 | 280194 | NIP1A | Urban | LV Transformer SP1606-D NIP1A - Planned | 17.535 | 155 | 2717.925 | 0.0027345 | 1.7642e-05
2012-09-18 | 280200 | SQBT1 | CBD | LV Transformer SSSQB SQBT1 - Planned | 2.6 | 299 | 777.4 | 0.20634 | 0.00069011
2012-09-18 | 280284 | NMK23A | Urban | LV Transformer SC3162-L NMK23A - Planned | 4.8051 | 265 | 1273.3515 | 0.0012811 | 4.8344e-06
2012-09-18 | 280548 | KWH1 | Rural short | Feeder KWH1 - Planned | 18.02 | 202 | 3640.04 | 0.010513 | 5.2046e-05
2012-09-19 | 280198 | HTN7B | Urban | LV Transformer SG1734708 HTN7B - Planned | 11 | 150 | 1650 | 0.00166 | 1.1066e-05
2012-09-19 | 280222 | MCW7 | Rural short | LV Transformer SP14018-B MCW7 - Planned | 1 | 130 | 130 | 0.00037524 | 2.8865e-06
2012-09-19 | 280223 | MTB15A | Rural short | Feeder MTB15A - Planned | 2.01 | 149 | 299.49 | 0.00086447 | 5.8018e-06
2012-09-19 | 280240 | FDS3 | Rural short | LV Transformer SP3803-C FDS3 - Planned | 3 | 185 | 555 | 0.001602 | 8.6595e-06
2012-09-19 | 280241 | MLY1 | Rural short | LV Transformer SP6130-A MLY1 - Planned | 3 | 182 | 546 | 0.001576 | 8.6595e-06
2012-09-19 | 280262 | CLM3 | Rural short | Feeder CLM3 - Planned | 17.01 | 315 | 5358.15 | 0.015466 | 4.9099e-05
2012-09-19 | 280263 | WMR1 | Rural short | LV Transformer SP17042-D WMR1 - Planned | 4 | 235 | 940 | 0.0027133 | 1.1546e-05
2012-09-19 | 280264 | HDN2 | Rural short | Feeder HDN2 - Planned | 11.02 | 351 | 3868.02 | 0.011165 | 3.1809e-05
2012-09-19 | 280265 | CRM15A | Urban | LV Transformer SP4032-E CRM15A - Planned | 10.5 | 337 | 3538.5 | 0.0035598 | 1.0563e-05
2012-09-19 | 280266 | BDT1 | Rural short | LV Transformer SP2065-E BDT1 - Planned | 2.01 | 341 | 685.41 | 0.0019784 | 5.8018e-06
2012-09-19 | 280270 | GYN3A | Rural short | Feeder GYN3A - Planned | 4.01 | 463 | 1856.63 | 0.0053591 | 1.1575e-05
2012-09-19 | 280272 | LBH3A | Rural short | LV Transformer SP3991-B LBH3A - Planned | 20.9 | 317 | 6625.3 | 0.019124 | 6.0328e-05
2012-09-19 | 280273 | CNB24A | Rural short | Feeder CNB24A - Planned | 11.43 | 473 | 5406.39 | 0.015605 | 3.2993e-05
2012-09-19 | 280274 | CRB25A | Rural short | Feeder CRB25A - Planned | 9.8 | 513 | 5027.4 | 0.014512 | 2.8288e-05
2012-09-19 | 280275 | GGR1 | Rural short | Feeder GGR1 - Planned | 95.17 | 540 | 51391.8 | 0.14834 | 0.00027471
2012-09-19 | 280281 | NMK18 | Urban | LV Transformer SP3218-K NMK18 - Planned | 9.1231 | 360 | 3284.316 | 0.0033041 | 9.1781e-06
2012-09-19 | 280282 | KMR29A | Urban | LV Transformer SP3484-I KMR29A - Planned | 7.7187 | 259 | 1999.1433 | 0.0020112 | 7.7653e-06
2012-09-19 | 280283 | NMK23A | Urban | LV Transformer SP484248 NMK23A - Planned | 1.385 | 120 | 166.2 | 0.0001672 | 1.3934e-06
2012-09-19 | 280285 | BISTPT3 | Rural short | LV Transformer SP3264-C BISTPT3 - Planned | 16.875 | 195 | 3290.625 | 0.0094983 | 4.8709e-05
2012-09-19 | 280286 | CMD15A | Urban | LV Transformer SP5349-A CMD15A - Planned | 27.83 | 181 | 5037.23 | 0.0050676 | 2.7998e-05
2012-09-19 | 280286 | CMD7A | Rural short | LV Transformer SP5349-A CMD15A - Planned | 5.34 | 181 | 966.54 | 0.0027899 | 1.5414e-05
2012-09-19 | 280287 | MLB3A | Rural short | LV Transformer SP4563-B MLB3A - Planned | 31.64 | 175 | 5537 | 0.015982 | 9.1328e-05
2012-09-19 | 280288 | MLB13A | Urban | LV Transformer SC451931-A MLB13A - Planned | 11.61 | 320 | 3715.2 | 0.0037376 | 1.168e-05
2012-09-19 | 280289 | CNB24A | Rural short | LV Transformer SP2839-E CNB24A - Planned | 6.45 | 455 | 2934.75 | 0.0084711 | 1.8618e-05
2012-09-19 | 280290 | BDL4 | Urban | LV Transformer SP4162-H BDL4 - Planned | 7.2264 | 177 | 1279.0728 | 0.0012868 | 7.27e-06
2012-09-19 | 280291 | HWL10A | Urban | LV Transformer SP3032-F HWL10A - Planned | 45.244 | 220 | 9953.68 | 0.010014 | 4.5517e-05
2012-09-19 | 280292 | LDR8 | Urban | LV Transformer SP1122-K LDR8 - Planned | 16.1263 | 192 | 3096.2496 | 0.0031149 | 1.6224e-05
2012-09-19 | 280293 | HPE3A | Urban | LV Transformer SC3657-F HPE3A - Planned | 17.6994 | 376 | 6654.9744 | 0.0066951 | 1.7806e-05
2012-09-19 | 280294 | BKD13A | Urban | LV Transformer SP10654-A BKD13A - Planned | 25.91 | 402 | 10415.82 | 0.010479 | 2.6066e-05
2012-09-19 | 280295 | BDB35A | Urban | LV Transformer SP5304-D BDB35A - Planned | 19 | 516 | 9804 | 0.0098632 | 1.9115e-05
2012-09-19 | 280296 | KBR6A | Rural short | LV Transformer SP3549-C KBR6A - Planned | 5.29 | 405 | 2142.45 | 0.0061842 | 1.527e-05
2012-09-19 | 280297 | RPN8 | Rural short | LV Transformer SC1409197 RPN8 - Planned | 1.16 | 234 | 271.44 | 0.00078351 | 3.3483e-06
2012-09-19 | 280402 | MFN13A | Rural short | LV Transformer SC448710 MFN13A - Planned | 1.045 | 291 | 304.095 | 0.00087777 | 3.0164e-06
2012-09-20 | 280322 | BNH6A | Rural short | LV Transformer SP2714-E BNH6A - Planned | 2.01 | 170 | 341.7 | 0.0009857 | 5.7982e-06
2012-09-20 | 280340 | MBG2 | Rural short | Feeder MBG2 - Planned | 11.98 | 275 | 3294.5 | 0.0095036 | 3.4559e-05
2012-09-20 | 280341 | KWA2A | Urban | LV Transformer SP5415-A KWA2A - Planned | 106.5 | 178 | 18957 | 0.01907 | 0.00010714
2012-09-20 | 280342 | PWC4 | Rural short | LV Transformer SP12827-A PWC4 - Planned | 18 | 252 | 4536 | 0.013085 | 5.1924e-05
2012-09-20 | 280343 | PWC4 | Rural short | LV Transformer SP1783-C PWC4 - Planned | 17.5 | 210 | 3675 | 0.010601 | 5.0482e-05
2012-09-20 | 280344 | ARL15B | Urban | LV Transformer SP8711-D ARL15B - Planned | 1 | 277 | 277 | 0.00027865 | 1.006e-06
2012-09-20 | 280345 | GGR1 | Rural short | Feeder GGR1 - Planned | 25.66 | 305 | 7826.3 | 0.022576 | 7.4021e-05
2012-09-20 | 280346 | TGW2 | Rural short | Feeder TGW2 - Planned | 16.76 | 369 | 6184.44 | 0.01784 | 4.8347e-05
2012-09-20 | 280347 | KBR6A | Rural short | Feeder KBR6A - Planned | 10.99 | 400 | 4396 | 0.012681 | 3.1703e-05
2012-09-20 | 280360 | YDA3A | Rural short | LV Transformer SP16515-A YDA3A - Planned | 2.01 | 450 | 904.5 | 0.0026092 | 5.7982e-06
2012-09-20 | 280361 | MTB1B | Rural short | LV Transformer SP5538-B MTB1B - Planned | 58.685 | 418 | 24530.33 | 0.070762 | 0.00016929
2012-09-20 | 280363 | RWD1 | Rural short | Feeder RWD1 - Planned | 48.84 | 503 | 24566.52 | 0.070867 | 0.00014089
2012-09-20 | 280381 | CRB25A | Rural short | Feeder CRB25A - Planned | 5.594 | 678 | 3792.732 | 0.010941 | 1.6137e-05
2012-09-20 | 280382 | STT3A | Rural short | LV Transformer SP10102-C STT3A - Planned | 0.4 | 330 | 132 | 0.00038078 | 1.1539e-06
2012-09-20 | 280383 | IDY5A | Urban | LV Transformer SP3257-I IDY5A - Planned | 6.36 | 310 | 1971.6 | 0.0019834 | 6.398e-06
2012-09-20 | 280384 | SFD10 | Urban | LV Transformer SC1500244 SFD10 - Planned | 2.82 | 318 | 896.76 | 0.00090212 | 2.8368e-06
2012-09-20 | 280384 | SFD3 | Urban | LV Transformer SC1500244 SFD10 - Planned | 0.855 | 318 | 271.89 | 0.00027351 | 8.6011e-07
2012-09-20 | 280385 | KMR21A | Urban | LV Transformer SC6051-H KMR21A - Planned | 9.31 | 325 | 3025.75 | 0.0030438 | 9.3656e-06
2012-09-20 | 280386 | GAP6A | Urban | LV Transformer SC2300-H GAP6A - Planned | 18.75 | 339 | 6356.25 | 0.0063942 | 1.8862e-05
2012-09-20 | 280387 | MLB13A | Urban | LV Transformer SC451931-A MLB13A - Planned | 6.45 | 274 | 1767.3 | 0.0017779 | 6.4885e-06
2012-09-20 | 280388 | CMD15A | Urban | LV Transformer SP5290-A CMD15A - Planned | 11.97 | 214 | 2561.58 | 0.0025769 | 1.2041e-05
2012-09-20 | 280389 | CRB25A | Rural short | LV Transformer SP11263-E CRB25A - Planned | 12.375 | 472 | 5841 | 0.016849 | 3.5698e-05
2012-09-20 | 280390 | MAI11 | Urban | LV Transformer SP3055-E MAI11 - Planned | 11.4621 | 382 | 4378.5222 | 0.0044047 | 1.1531e-05
2012-09-20 | 280391 | DRD5A | Urban | LV Transformer SP3405-A DRD5A - Planned | 19.475 | 360 | 7011 | 0.0070529 | 1.9591e-05
2012-09-20 | 280392 | CFD2A | Urban | LV Transformer SP7107-G CFD2A - Planned | 24.75 | 327 | 8093.25 | 0.0081416 | 2.4898e-05
2012-09-20 | 280393 | DRD5A | Urban | LV Transformer SP237-L DRD5A - Planned | 46.65 | 360 | 16794 | 0.016894 | 4.6929e-05
2012-09-20 | 280394 | WNM5 | Urban | LV Transformer SC3395-K WNM5 - Planned | 22.135 | 229 | 5068.915 | 0.0050992 | 2.2267e-05
2012-09-20 | 280395 | KSN4 | Urban | LV Transformer SP4863-D KSN4 - Planned | 23.44 | 328 | 7688.32 | 0.0077342 | 2.358e-05
2012-09-20 | 280396 | RPN8 | Rural short | LV Transformer SP3774-D RPN8 - Planned | 23.7825 | 275 | 6540.1875 | 0.018866 | 6.8605e-05
2012-09-20 | 280397 | IPS2B | Rural short | LV Transformer SC1390592 IPS2B - Planned | 5.82 | 60 | 349.2 | 0.0010073 | 1.6789e-05
2012-09-20 | 280398 | IPS2B | Rural short | LV Transformer SC1439636 IPS2B - Planned | 8.02 | 75 | 601.5 | 0.0017351 | 2.3135e-05
2012-09-20 | 280549 | KWH3 | Rural short | Feeder KWH3 - Planned | 26.4472 | 239 | 6320.8808 | 0.018234 | 7.6292e-05
2012-09-21 | 280420 | MGP13A | Rural short | Feeder MGP13A - Planned | 13 | 200 | 2600 | 0.0074955 | 3.7478e-05
2012-09-21 | 280421 | CPD1 | Rural short | LV Transformer SP2083-D CPD1 - Planned | 3 | 161 | 483 | 0.0013924 | 8.6487e-06
2012-09-21 | 280422 | TGW1 | Rural short | Feeder TGW1 - Planned | 25 | 201 | 5025 | 0.014487 | 7.2073e-05
2012-09-21 | 280423 | PWC3 | Rural short | Feeder PWC3 - Planned | 30 | 228 | 6840 | 0.019719 | 8.6487e-05
2012-09-21 | 280428 | GYN7A | Rural short | Feeder GYN7A - Planned | 136 | 315 | 42840 | 0.1235 | 0.00039207
2012-09-21 | 280429 | ACR5 | Rural short | LV Transformer SP4958-E ACR5 - Planned | 10.25 | 240 | 2460 | 0.0070919 | 2.955e-05
2012-09-21 | 280430 | CPD1 | Rural short | LV Transformer SP3474-B CPD1 - Planned | 1 | 187 | 187 | 0.0005391 | 2.8829e-06
2012-09-21 | 280431 | CBW6 | Rural short | LV Transformer SP37790-B CBW6 - Planned | 5 | 61 | 305 | 0.00087929 | 1.4415e-05
2012-09-21 | 280441 | MTB13A | Rural short | Feeder MTB13A - Planned | 13.95 | 330 | 4603.5 | 0.013271 | 4.0216e-05
2012-09-21 | 280442 | CRY5A | Rural short | Feeder CRY5A, TWT12A - Planned | 21.04 | 355 | 7469.2 | 0.021533 | 6.0656e-05
2012-09-21 | 280442 | TWT12A | Rural short | Feeder CRY5A, TWT12A - Planned | 19.3 | 355 | 6851.5 | 0.019752 | 5.564e-05
2012-09-21 | 280443 | IPS2B | Rural short | LV Transformer SC748683 IPS2B - Planned | 0.99 | 324 | 320.76 | 0.00092472 | 2.8541e-06
2012-09-21 | 280444 | FDS3 | Rural short | LV Transformer SP4227-E FDS3 - Planned | 2.01 | 390 | 783.9 | 0.0022599 | 5.7946e-06
2012-09-21 | 280445 | LBH1B | Rural short | LV Transformer SP3015-A LBH1B - Planned | 8 | 321 | 2568 | 0.0074033 | 2.3063e-05
2012-09-21 | 280446 | BWH13A | Rural short | LV Transformer SP420-B BWH13A - Planned | 0.99 | 339 | 335.61 | 0.00096753 | 2.8541e-06
2012-09-21 | 280463 | GYN3A | Rural short | Feeder GYN3A - Planned | 2 | 471 | 942 | 0.0027157 | 5.7658e-06
2012-09-21 | 280472 | NSD30B | Urban | LV Transformer SP42702-C NSD30B - Planned | 13.14 | 315 | 4139.1 | 0.0041636 | 1.3218e-05
2012-09-21 | 280474 | SFD11 | Urban | LV Transformer SC3175-M SFD11 - Planned | 26.5644 | 256 | 6800.4864 | 0.0068407 | 2.6721e-05
2012-09-21 | 280475 | MLT15B | Urban | LV Transformer SP6199-E MLT15B - Planned | 15.834 | 182 | 2881.788 | 0.0028988 | 1.5928e-05
2012-09-21 | 280476 | OXL4A | Urban | LV Transformer SP2894-L OXL4A - Planned | 11.775 | 255 | 3002.625 | 0.0030204 | 1.1845e-05
2012-09-21 | 280477 | CLD9A | Urban | LV Transformer SP591-B CLD9A - Planned | 33.66 | 187 | 6294.42 | 0.0063316 | 3.3859e-05
2012-09-21 | 280478 | MFD5A | Rural short | LV Transformer SP4904-E MFD5A - Planned | 3.01 | 313 | 942.13 | 0.0027161 | 8.6775e-06
2012-09-21 | 280479 | MDR25A | Urban | LV Transformer SP1089-H MDR25A - Planned | 5.88 | 365 | 2146.2 | 0.0021589 | 5.9148e-06
2012-09-21 | 280480 | NRG12A | Urban | LV Transformer SC1076-J NRG12A - Planned | 6.6 | 69 | 455.4 | 0.00045809 | 6.639e-06
2012-09-21 | 280481 | BHD7A | Urban | LV Transformer SC2361-J BHD7A - Planned | 130.47 | 315 | 41098.05 | 0.041341 | 0.00013124
2012-09-21 | 280482 | JBB2A | Rural short | LV Transformer SP3656-B JBB2A - Planned | 3.22 | 254 | 817.88 | 0.0023579 | 9.2829e-06
2012-09-21 | 280483 | LDR8 | Urban | LV Transformer SP468825 LDR8 - Planned | 32.75 | 269 | 8809.75 | 0.0088618 | 3.2944e-05
2012-09-21 | 280484 | BDT4 | Rural short | LV Transformer SP419-F BDT4 - Planned | 6.02 | 105 | 632.1 | 0.0018223 | 1.7355e-05
2012-09-21 | 280485 | ARL3A | Urban | LV Transformer SP6262-C ARL3A - Planned | 34.85 | 129 | 4495.65 | 0.0045222 | 3.5056e-05
2012-09-21 | 280486 | MTB13A | Rural short | LV Transformer SP5499-D MTB13A - Planned | 18.04 | 240 | 4329.6 | 0.012482 | 5.2008e-05
2012-09-21 | 280487 | NDH6 | Urban | LV Transformer SP4282-H NDH6 - Planned | 81.31 | 363 | 29515.53 | 0.02969 | 8.1791e-05
2012-09-21 | 280487 | NDH9 | Urban | LV Transformer SP4282-H NDH6 - Planned | 7.8 | 363 | 2831.4 | 0.0028481 | 7.8461e-06
2012-09-21 | 280488 | BHL4A | Urban | LV Transformer SC1427101 BHL4A - Planned | 11.11 | 65 | 722.15 | 0.00072642 | 1.1176e-05
2012-09-21 | 280488 | BHL5A | Urban | LV Transformer SC1427101 BHL4A - Planned | 1.12 | 65 | 72.8 | 7.323e-05 | 1.1266e-06
2012-09-21 | 280489 | SBH6 | Urban | LV Transformer SP17272-A SBH6 - Planned | 4.425 | 228 | 1008.9 | 0.0010149 | 4.4512e-06
2012-09-21 | 280490 | BGY15A | Urban | LV Transformer SC483871 BGY15A - Planned | 17.86 | 80 | 1428.8 | 0.0014372 | 1.7966e-05
2012-09-21 | 280491 | HDA10A | Urban | LV Transformer SP2294-G HDA10A - Planned | 7.17 | 212 | 1520.04 | 0.001529 | 7.2124e-06
2012-09-21 | 280492 | KRN2 | Urban | LV Transformer SP2274-F KRN2 - Planned | 4.44 | 241 | 1070.04 | 0.0010764 | 4.4663e-06
2012-09-21 | 280493 | BRT5 | Urban | LV Transformer SP37-L BRT5 - Planned | 2.74 | 155 | 424.7 | 0.00042721 | 2.7562e-06
2012-09-21 | 280494 | BRT8 | Urban | LV Transformer SP1186-J BRT8 - Planned | 1.27 | 182 | 231.14 | 0.00023251 | 1.2775e-06
2012-09-21 | 280496 | QPT25B | Urban | LV Transformer SC518181-A QPT25B - Planned | 14.03 | 24 | 336.72 | 0.00033871 | 1.4113e-05
2012-09-21 | 280497 | CHL6A | Urban | LV Transformer SP1065-N CHL6A - Planned | 6.42 | 194 | 1245.48 | 0.0012528 | 6.458e-06
2012-09-21 | 280498 | TMH16A | Urban | LV Transformer SP6646-E TMH16A - Planned | 16.71 | 269 | 4494.99 | 0.0045216 | 1.6809e-05
2012-09-21 | 280499 | RCN3A | Urban | LV Transformer SC6116-J RCN3A - Planned | 14.52 | 304 | 4414.08 | 0.0044402 | 1.4606e-05
2012-09-21 | 280500 | VPT13A | Rural short | LV Transformer SC2307-E VPT13A - Planned | 6.25 | 32 | 200 | 0.00057658 | 1.8018e-05
2012-09-21 | 280500 | VPT2A | Urban | LV Transformer SC2307-E VPT13A - Planned | 0.73 | 32 | 23.36 | 2.3498e-05 | 7.3432e-07
2012-09-21 | 280501 | IPS2B | Rural short | LV Transformer SC1439636 IPS2B - Planned | 12.25 | 43 | 526.75 | 0.0015186 | 3.5316e-05
2012-09-21 | 280502 | BVL13A | Urban | LV Transformer SP4231-F BVL13A - Planned | 22.08 | 233 | 5144.64 | 0.0051751 | 2.2211e-05
2012-09-21 | 280503 | FDS3 | Rural short | LV Transformer SP3370-B FDS3 - Planned | 8.88 | 345 | 3063.6 | 0.0088321 | 2.56e-05
2012-09-21 | 280504 | IPS2B | Rural short | LV Transformer SC1390592 IPS2B - Planned | 9.93 | 39 | 387.27 | 0.0011165 | 2.8627e-05
2012-09-22 | 280524 | VPT5B | Urban | LV Transformer SC735107 VPT5B - Planned | 1.386 | 155 | 214.83 | 0.00021609 | 1.3941e-06
2012-09-22 | 280542 | KMR19A | Urban | LV Transformer SC484166 KMR21B - Planned | 3 | 465 | 1395 | 0.0014032 | 3.0175e-06
2012-09-22 | 280542 | KMR21B | Urban | LV Transformer SC484166 KMR21B - Planned | 9.984 | 465 | 4642.56 | 0.0046697 | 1.0042e-05
2012-09-22 | 280543 | FDS3 | Rural short | LV Transformer SP4382-F FDS3 - Planned | 4.11 | 143 | 587.73 | 0.0016934 | 1.1842e-05
2012-09-22 | 280544 | RST9A | Urban | LV Transformer SP3754-C RST9A - Planned | 3.911 | 240 | 938.64 | 0.00094413 | 3.9339e-06
2012-09-23 | 280550 | TGP9A | Rural short | Feeder TGP9A - Planned | 27.192 | 324 | 8810.208 | 0.025369 | 7.8299e-05
2012-09-23 | 280552 | KWH3 | Rural short | Feeder KWH3 - Planned | 10.4141 | 319 | 3322.0979 | 0.009566 | 2.9987e-05
2012-09-23 | 280553 | MWMRBK11 | Rural short | Feeder MWMRBK11 - Planned | 72 | 312 | 22464 | 0.064685 | 0.00020732
2012-09-23 | 280554 | SPO8A | Urban | LV Transformer SC472971 SPO8A - Planned | 1 | 418 | 418 | 0.00042042 | 1.0058e-06
2012-09-23 | 280555 | MLT40A | Urban | Feeder MLT40A, MLT6A - Planned | 1 | 562 | 562 | 0.00056525 | 1.0058e-06
2012-09-23 | 280560 | MLT21B | Urban | LV Transformer SP4557-K MLT21B - Planned | 7.12 | 270 | 1922.4 | 0.0019335 | 7.1612e-06
2012-09-23 | 280562 | SPO11A | Urban | LV Transformer SP6432-E SPO47A - Planned | 21.615 | 450 | 9726.75 | 0.009783 | 2.174e-05
2012-09-23 | 280562 | SPO47A | Urban | LV Transformer SP6432-E SPO47A - Planned | 22.366 | 450 | 10064.7 | 0.010123 | 2.2495e-05
2012-09-23 | 280563 | HTN7A | Urban | LV Transformer SC6814-F HTN7A - Planned | 1.03 | 369 | 380.07 | 0.00038227 | 1.036e-06
2012-09-23 | 280564 | GBG23A | Urban | LV Transformer SG3830-F GBG23A - Planned | 3.145 | 120 | 377.4 | 0.00037958 | 3.1632e-06
2012-09-23 | 280565 | HTN7A | Urban | LV Transformer SC1664-K HTN7A - Planned | 5.56 | 260 | 1445.6 | 0.001454 | 5.5922e-06
2012-09-23 | 280566 | NDH6 | Urban | LV Transformer SC810173 NDH6 - Planned | 3.045 | 345 | 1050.525 | 0.0010566 | 3.0626e-06
2012-09-23 | 280567 | WSE3A | Rural short | LV Transformer SP17323-C WSE3A - Planned | 1.125 | 229 | 257.625 | 0.00074183 | 3.2394e-06
2012-09-23 | 280568 | WRD9A | Urban | LV Transformer SC2105-J WRD9A - Planned | 7.525 | 303 | 2280.075 | 0.0022933 | 7.5685e-06
2012-09-23 | 280569 | RBK9A | Urban | LV Transformer SP1097-G RBK9A - Planned | 10.88 | 288 | 3133.44 | 0.0031516 | 1.0943e-05
2012-09-23 | 280570 | RST5A | Urban | LV Transformer SP8367-C RST5A - Planned | 25.95 | 345 | 8952.75 | 0.0090045 | 2.61e-05
2012-09-23 | 280941 | LTA5 | Urban | LV Transformer SC779031 LTA5 - Planned | 2.9037 | 174.5 | 54.1725 | 5.4486e-05 | 2.9205e-06
2012-09-23 | 281062 | SPO16A | Urban | Feeder SPO16A - Planned | 245.5 | 363 | 89116.5 | 0.089632 | 0.00024692
2012-09-24 | 280601 | MCN3 | Urban | Feeder MCN3 - Planned | 0.264 | 386 | 101.904 | 0.00010249 | 2.6551e-07
2012-09-24 | 280602 | FDS1 | Rural short | LV Transformer SP4189-C FDS1 - Planned | 7.04 | 380 | 2675.2 | 0.0076987 | 2.026e-05
2012-09-24 | 280607 | CPK9 | Rural short | LV Transformer SG776896 CPK9 - Planned | 1 | 368 | 368 | 0.001059 | 2.8778e-06
2012-09-24 | 280611 | EMD2 | Rural short | Feeder EMD2 - Planned | 91.175 | 420 | 38293.5 | 0.1102 | 0.00026238
2012-09-24 | 280612 | NBR8 | Rural short | Feeder NBR8 - Planned | 18.98 | 220 | 4175.6 | 0.012017 | 5.4621e-05
2012-09-24 | 280613 | GBN4 | Rural short | LV Transformer SP5941-B GBN4 - Planned | 3 | 225 | 675 | 0.0019425 | 8.6334e-06
2012-09-24 | 280614 | MTB1B | Rural short | Feeder MTB1B - Planned | 34 | 433 | 14722 | 0.042367 | 9.7845e-05
2012-09-24 | 280655 | ZMR10 | Urban | LV Transformer SP143-M ZMR10 - Planned | 19.98 | 187 | 3736.26 | 0.0037576 | 2.0094e-05
2012-09-24 | 280656 | NMK17A | Urban | LV Transformer SP2924-J NMK17A - Planned | 16.94 | 301 | 5098.94 | 0.0051281 | 1.7037e-05
2012-09-24 | 280658 | ENG7 | Urban | LV Transformer SP768909 ENG7 - Planned | 15.39 | 295 | 4540.05 | 0.004566 | 1.5478e-05
2012-09-24 | 280659 | CSE10 | Urban | LV Transformer SP6701-K CSE10 - Planned | 12.0402 | 327 | 3937.1454 | 0.0039597 | 1.2109e-05
2012-09-24 | 280661 | GBN4 | Rural short | LV Transformer SP2933-C GBN4 - Planned | 3 | 45 | 135 | 0.0003885 | 8.6334e-06
2012-09-24 | 280662 | NBR4 | Rural short | LV Transformer SP4351-A NBR4 - Planned | 7.175 | 323 | 2317.525 | 0.0066694 | 2.0648e-05
2012-09-24 | 280663 | MFD9A | Urban | LV Transformer SP3586-E MFD9A - Planned | 12.4632 | 385 | 4798.332 | 0.0048258 | 1.2535e-05
2012-09-24 | 280665 | SPO16A | Urban | LV Transformer SP3780-G SPO16A - Planned | 9.3 | 392 | 3645.6 | 0.0036665 | 9.3532e-06
2012-09-24 | 280666 | SPO60A | Urban | LV Transformer SP1434-J SPO60A - Planned | 15.98 | 464 | 7414.72 | 0.0074572 | 1.6071e-05
2012-09-24 | 280667 | BSC3 | Urban | LV Transformer SC6402-C BSC3 - Planned | 8 | 40 | 320 | 0.00032183 | 8.0458e-06
2012-09-24 | 280668 | HDA3A | Urban | LV Transformer SP6607-I HDA3A - Planned | 2.57 | 153 | 393.21 | 0.00039546 | 2.5847e-06
2012-09-24 | 280669 | CHL3 | Urban | LV Transformer SP494875 CHL3 - Planned | 22.115 | 230 | 5086.45 | 0.0051156 | 2.2242e-05
2012-09-24 | 280670 | BVL13A | Urban | LV Transformer SP4231-F BVL13A - Planned | 20.24 | 178 | 3602.72 | 0.0036233 | 2.0356e-05
2012-09-24 | 280671 | PRG2A | Rural short | LV Transformer SP1696-B PRG2A - Planned | 6.02 | 280 | 1685.6 | 0.0048508 | 1.7324e-05
2012-09-25 | 280706 | FDS3 | Rural short | Feeder FDS3 - Planned | 5 | 227 | 1135 | 0.0032651 | 1.4384e-05
2012-09-25 | 280707 | BDT2 | Rural short | LV Transformer SP18431-B BDT2 - Planned | 4.1339 | 199 | 822.6461 | 0.0023665 | 1.1892e-05
2012-09-25 | 280720 | CPC2B | Urban | LV Transformer SP10493-D CPC2B - Planned | 33.95 | 357 | 12120.15 | 0.012188 | 3.414e-05
2012-09-25 | 280721 | CBW11 | Rural short | LV Transformer SP4578-E CBW11 - Planned | 1 | 406 | 406 | 0.0011679 | 2.8767e-06
2012-09-25 | 280722 | CMY1 | Rural short | LV Transformer SP8282-A CMY1 - Planned | 5.5 | 371 | 2040.5 | 0.0058699 | 1.5822e-05
2012-09-25 | 280724 | IPL1 | Rural short | Feeder IPL1 - Planned | 28.05 | 330 | 9256.5 | 0.026628 | 8.0692e-05
2012-09-25 | 280726 | CLD28A | Rural short | Feeder CLD28A - Planned | 3.71 | 427 | 1584.17 | 0.0045572 | 1.0673e-05
2012-09-25 | 280727 | BWH12A | Rural short | Feeder BWH16A, BWH12A, BWH8A - Planned | 23.5 | 522 | 12267 | 0.035289 | 6.7603e-05
2012-09-25 | 280727 | BWH16A | Rural short | Feeder BWH16A, BWH12A, BWH8A - Planned | 1 | 522 | 522 | 0.0015016 | 2.8767e-06
2012-09-25 | 280727 | BWH8A | Rural short | Feeder BWH16A, BWH12A, BWH8A - Planned | 37.83 | 522 | 19747.26 | 0.056807 | 0.00010883
2012-09-25 | 280728 | NMK18 | Urban | LV Transformer SP2640-L NMK18 - Planned | 6.471 | 275 | 1779.525 | 0.0017895 | 6.5072e-06
2012-09-25 | 280729 | MHL3A | Rural short | LV Transformer SP3649-E MHL3A - Planned | 28.96 | 462 | 13379.52 | 0.038489 | 8.331e-05
2012-09-25 | 280731 | STL2 | Urban | LV Transformer SP776405 STL2 - Planned | 15.2946 | 302 | 4618.9692 | 0.0046448 | 1.538e-05
2012-09-25 | 280732 | ENG7 | Urban | LV Transformer SP596-O ENG7 - Planned | 19.8 | 205 | 4059 | 0.0040817 | 1.9911e-05
2012-09-25 | 280733 | KMR19A | Urban | LV Transformer SP2123-N KMR19A - Planned | 9 | 273 | 2457 | 0.0024707 | 9.0503e-06
2012-09-25 | 280734 | EMD2 | Rural short | LV Transformer SP2282-E EMD2 - Planned | 3.1875 | 79 | 251.8125 | 0.00072439 | 9.1695e-06
2012-09-25 | 280735 | PBH1 | Urban | LV Transformer SP2757-F PBH1 - Planned | 18.375 | 375 | 6890.625 | 0.0069291 | 1.8478e-05
2012-09-25 | 280736 | MAI11 | Urban | LV Transformer SP4636-E MAI11 - Planned | 45.635 | 65 | 2966.275 | 0.0029828 | 4.589e-05
2012-09-25 | 280737 | BBH4A | Urban | LV Transformer SC707-F BBH4A - Planned | 2.25 | 21 | 47.25 | 4.7514e-05 | 2.2626e-06
2012-09-25 | 280738 | SPO41A | Urban | LV Transformer SP1086-I SPO41A - Planned | 8.61 | 395 | 3400.95 | 0.00342 | 8.6581e-06
2012-09-25 | 280739 | SPO5A | Urban | LV Transformer SC569-N SPO5A - Planned | 1.035 | 27 | 27.945 | 2.8101e-05 | 1.0408e-06
2012-09-25 | 280740 | NDH6 | Urban | LV Transformer SP2821-I NDH6 - Planned | 11.85 | 162 | 1919.7 | 0.0019304 | 1.1916e-05
2012-09-25 | 280741 | ACR5 | Rural short | LV Transformer SP5880-H ACR5 - Planned | 2 | 348 | 696 | 0.0020022 | 5.7534e-06
2012-09-25 | 280742 | HDA11A | Urban | LV Transformer SC5007-F HDA11A - Planned | 5.337 | 34 | 181.458 | 0.00018247 | 5.3668e-06
2012-09-25 | 280743 | WNM5 | Urban | LV Transformer SP2947-L WNM5 - Planned | 13.065 | 185 | 2417.025 | 0.0024305 | 1.3138e-05
2012-09-25 | 280744 | BRT3 | Urban | LV Transformer SP2345-H BRT3 - Planned | 5.225 | 172 | 898.7 | 0.00090372 | 5.2542e-06
2012-09-25 | 280745 | SRD19A | Urban | LV Transformer SC4771-F SRD19A - Planned | 9.31 | 275 | 2560.25 | 0.0025746 | 9.362e-06
2012-09-25 | 280746 | CHL3 | Urban | LV Transformer SP494875 CHL3 - Planned | 22.115 | 278 | 6147.97 | 0.0061823 | 2.2239e-05
2012-09-25 | 280747 | BNH1B | Rural short | LV Transformer SP3083-D BNH1B - Planned | 3 | 194 | 582 | 0.0016742 | 8.6301e-06
2012-09-25 | 280748 | BVL13A | Urban | LV Transformer SP1785-G BVL13A - Planned | 28.635 | 239 | 6843.765 | 0.006882 | 2.8795e-05
2012-09-25 | 280749 | RST9A | Urban | LV Transformer SP4908-C RST9A - Planned | 18.132 | 335 | 6074.22 | 0.0061082 | 1.8233e-05
2012-09-25 | 280750 | BNH1B | Rural short | LV Transformer SP112-G BNH1B - Planned | 2.01 | 153 | 307.53 | 0.00088468 | 5.7822e-06
2012-09-25 | 280751 | RPN8 | Rural short | LV Transformer SP3854-D RPN8 - Planned | 2.88 | 225 | 648 | 0.0018641 | 8.2849e-06
2012-09-25 | 280752 | RPN8 | Rural short | LV Transformer SP3525-E RPN8 - Planned | 7.2 | 433 | 3117.6 | 0.0089684 | 2.0712e-05
2012-09-25 | 280874 | CSE2 | Urban | LV Transformer SC4116-J CSE2 - Planned | 10.2141 | 350 | 3574.935 | 0.0035949 | 1.0271e-05
2012-09-26 | 280801 | BVL13A | Urban | LV Transformer SP40148-A BVL13A - Planned | 16 | 195 | 3120 | 0.003137 | 1.6087e-05
2012-09-26 | 280802 | MBG4 | Rural short | LV Transformer SP8567-B MBG4 - Planned | 4.02 | 61 | 245.22 | 0.00070516 | 1.156e-05
2012-09-26 | 280803 | AMR3 | Rural short | LV Transformer SP13952-B AMR3 - Planned | 1.25 | 204 | 255 | 0.00073328 | 3.5945e-06
2012-09-26 | 280804 | WMR1 | Rural short | Feeder WMR1 - Planned | 30.91 | 250 | 7727.5 | 0.022221 | 8.8885e-05
2012-09-26 | 280821 | EMD3 | Rural short | Feeder EMD3 - Planned | 45.4684 | 305 | 13867.862 | 0.039879 | 0.00013075
2012-09-26 | 280822 | MTB15A | Rural short | LV Transformer SP7347-D MTB15A - Planned | 18.525 | 303 | 5613.075 | 0.016141 | 5.3271e-05
2012-09-26 | 280840 | BGY15A | Urban | LV Transformer SC483871 BGY15A - Planned | 19 | 330 | 6270 | 0.0063042 | 1.9104e-05
2012-09-26 | 280841 | GGR1 | Rural short | LV Transformer SP2283-D GGR1 - Planned | 11.5 | 408 | 4692 | 0.013492 | 3.307e-05
2012-09-26 | 280860 | CNB24A | Rural short | LV Transformer SP526694 CNB24A - Planned | 9 | 473 | 4257 | 0.012241 | 2.588e-05
2012-09-26 | 280862 | NBR9 | Rural short | LV Transformer SP5366-A NBR9 - Planned | 1 | 340 | 340 | 0.00097771 | 2.8756e-06
2012-09-26 | 280863 | EMD2 | Rural short | Feeder EMD2 - Planned | 81 | 395 | 31995 | 0.092005 | 0.00023292
2012-09-26 | 280865 | NRG16A | Rural short | Feeder NRG16A - Planned | 39 | 375 | 14625 | 0.042056 | 0.00011215
2012-09-26 | 280867 | CRB24B | Urban | LV Transformer SP6823-E CRB24B - Planned | 38.18 | 502 | 19166.36 | 0.019271 | 3.8388e-05
2012-09-26 | 280868 | WCL19A | Rural short | LV Transformer SC1502222 WCL19A - Planned | 17.08 | 213 | 3638.04 | 0.010462 | 4.9115e-05
2012-09-26 | 280869 | FGBSGT23 | Urban | LV Transformer SC2056418 FGBSGT23 - Planned | 1 | 348 | 348 | 0.0003499 | 1.0055e-06
2012-09-26 | 280870 | AMR2 | Rural short | LV Transformer SP168-E AMR2 - Planned | 27 | 365 | 9855 | 0.028339 | 7.7641e-05
2012-09-26 | 280871 | MLT15B | Urban | LV Transformer SP5229-J MLT15B - Planned | 28.8677 | 273 | 7880.8821 | 0.0079238 | 2.9025e-05
2012-09-26 | 280872 | CFD6A | Urban | LV Transformer SC781255 CFD6A - Planned | 6.7 | 361 | 2418.7 | 0.0024319 | 6.7365e-06
2012-09-26 | 280873 | AGE7B | Urban | LV Transformer SP1420-P AGE7B - Planned | 17.6 | 370 | 6512 | 0.0065475 | 1.7696e-05
2012-09-26 | 280875 | NBR4 | Rural short | LV Transformer SP4350-A NBR4 - Planned | 5.04 | 374 | 1884.96 | 0.0054204 | 1.4493e-05
2012-09-26 | 280876 | SPO16A | Urban | LV Transformer SP1433-K SPO16A - Planned | 10.395 | 167 | 1735.965 | 0.0017454 | 1.0452e-05
2012-09-26 | 280877 | SPO60A | Urban | LV Transformer SP26979-B SPO60A - Planned | 21.275 | 201 | 4276.275 | 0.0042996 | 2.1391e-05
2012-09-26 | 280878 | SPD7B | Urban | LV Transformer SG7064-D SPD7B - Planned | 8.04 | 208 | 1672.32 | 0.0016814 | 8.0838e-06
2012-09-26 | 280879 | MTB3A | Rural short | LV Transformer SP238-D MTB3A - Planned | 1.815 | 260 | 471.9 | 0.001357 | 5.2192e-06
2012-09-26 | 280880 | MDR24A | Urban | LV Transformer SC1047-H MDR24A - Planned | 21.35 | 203 | 4334.05 | 0.0043577 | 2.1466e-05
2012-09-26 | 280881 | DRD15B | Urban | LV Transformer SP429-G DRD15B - Planned | 46.9425 | 230 | 10796.775 | 0.010856 | 4.7198e-05
2012-09-26 | 280882 | HTN7A | Urban | LV Transformer SP176-L HTN7A - Planned | 15.675 | 240 | 3762 | 0.0037825 | 1.576e-05
2012-09-26 | 280883 | SBH4 | Urban | LV Transformer SP1306-I SBH4 - Planned | 2.76 | 308 | 850.08 | 0.00085471 | 2.775e-06
2012-09-26 | 280884 | NSW5A | Urban | LV Transformer SP4704-H NSW5A - Planned | 4.875 | 229 | 1116.375 | 0.0011225 | 4.9016e-06
2012-09-26 | 280885 | HPE3A | Urban | LV Transformer SC3657-F HPE3A - Planned | 7.8664 | 337 | 2650.9768 | 0.0026654 | 7.9093e-06
2012-09-26 | 280886 | CHL3 | Urban | LV Transformer SP45538-E CHL3 - Planned | 0.82 | 225 | 184.5 | 0.00018551 | 8.2447e-07
2012-09-26 | 280887 | BKD13A | Urban | LV Transformer SP6110-C BKD13A - Planned | 19.05 | 195 | 3714.75 | 0.003735 | 1.9154e-05
2012-09-26 | 280889 | BWH8A | Rural short | Feeder BWH8A - Planned | 37.83 | 708 | 26783.64 | 0.077019 | 0.00010878
2012-09-27 | 280901 | BWH12A | Rural short | Feeder BWH12A - Planned | 40.47 | 59 | 2387.73 | 0.0068635 | 0.00011633
2012-09-27 | 280902 | SGT7 | Urban | LV Transformer SP5477-F SGT7 - Planned | 35.5 | 86 | 3053 | 0.0030692 | 3.5689e-05
2012-09-27 | 280904 | BNH6A | Rural short | Feeder BNH6A - Planned | 4.9 | 153 | 749.7 | 0.002155 | 1.4085e-05
2012-09-27 | 280906 | BNH6A | Rural short | Feeder BNH6A - Planned | 16 | 178 | 2848 | 0.0081866 | 4.5992e-05
2012-09-27 | 280921 | CPK9 | Rural short | LV Transformer SG776896 CPK9 - Planned | 1 | 360 | 360 | 0.0010348 | 2.8745e-06
2012-09-27 | 280922 | GYM4 | Urban | Feeder GYM4 - Planned | 57.45 | 209 | 12007.05 | 0.012071 | 5.7755e-05
2012-09-27 | 280923 | AMR3 | Rural short | LV Transformer SP301692 AMR3 - Planned | 3.5 | 178 | 623 | 0.0017908 | 1.0061e-05
2012-09-27 | 280924 | BTN2 | Rural short | LV Transformer SP263-D BTN2 - Planned | 9 | 130 | 1170 | 0.0033632 | 2.587e-05
2012-09-27 | 280925 | TWT3A | Rural short | LV Transformer SC740400-B TWT3A - Planned | 12 | 29 | 348 | 0.0010003 | 3.4494e-05
2012-09-27 | 280928 | QPT5 | Urban | LV Transformer SP747248 QPT5 - Planned | 1 | 382 | 382 | 0.00038403 | 1.0053e-06
2012-09-27 | 280940 | GYN3A | Rural short | Feeder GYN3A - Planned | 3.01 | 462 | 1390.62 | 0.0039973 | 8.6522e-06
2012-09-27 | 280942 | MLT15B | Urban | LV Transformer SP2234-N MLT15B - Planned | 24.571 | 415 | 10196.965 | 0.010251 | 2.4702e-05
2012-09-27 | 280943 | BPN28A | Rural short | LV Transformer SP15107-G BPN28A - Planned | 1.9 | 247 | 469.3 | 0.001349 | 5.4615e-06
2012-09-27 | 280944 | SFD4 | Urban | LV Transformer SC3533-J SFD4 - Planned | 16.4503 | 258 | 4244.1774 | 0.0042667 | 1.6538e-05
2012-09-27 | 280945 | STL2 | Urban | LV Transformer SG5070-J STL2 - Planned | 16.56 | 320 | 5299.2 | 0.0053274 | 1.6648e-05
2012-09-27 | 280946 | GAP6A | Urban | LV Transformer SC7914-E GAP6A - Planned | 51 | 139 | 7089 | 0.0071267 | 5.1271e-05
2012-09-27 | 280947 | MAI5 | Urban | LV Transformer SP3801-E MAI5 - Planned | 23.03 | 400 | 9212 | 0.009261 | 2.3152e-05
2012-09-27 | 280948 | GVN3A | Urban | LV Transformer SP6343-C GVN3A - Planned | 14.1 | 381 | 5372.1 | 0.0054007 | 1.4175e-05
2012-09-27 | 280949 | BHD35A | Rural short | LV Transformer SP395-J BHD35A - Planned | 15.08 | 83 | 1251.64 | 0.0035978 | 4.3347e-05
2012-09-27 | 280950 | PBH6 | Urban | LV Transformer SP3012-F PBH6 - Planned | 11.165 | 284 | 3170.86 | 0.0031877 | 1.1224e-05
2012-09-27 | 280951 | SGT22A | Urban | LV Transformer SP303-N SGT22A - Planned | 5.805 | 183 | 1062.315 | 0.001068 | 5.8359e-06
2012-09-27 | 280952 | HTN3B | Urban | LV Transformer SP714256 HTN3B - Planned | 7.12 | 182 | 1295.84 | 0.0013027 | 7.1578e-06
2012-09-27 | 280953 | RCN10A | Urban | LV Transformer SP3092-M RCN10A - Planned | 2.9981 | 338 | 1013.3578 | 0.0010187 | 3.014e-06
2012-09-27 | 280954 | WED20A | Urban | LV Transformer SP161-Q WED6A - Planned | 2.82 | 269 | 758.58 | 0.00076261 | 2.835e-06
2012-09-27 | 280954 | WED6A | Urban | LV Transformer SP161-Q WED6A - Planned | 36.48 | 269 | 9813.12 | 0.0098653 | 3.6674e-05
2012-09-27 | 280955 | GGR1 | Rural short | Feeder GGR1 - Planned | 65.16 | 523 | 34078.68 | 0.097959 | 0.0001873
2012-09-27 | 280956 | RCN10A | Urban | LV Transformer SP5611-G RCN10A - Planned | 1.96 | 73 | 143.08 | 0.00014384 | 1.9704e-06
2012-09-27 | 280957 | RBK11B | Urban | LV Transformer SP2729-G RBK11B - Planned | 31.2 | 365 | 11388 | 0.011449 | 3.1366e-05
2012-09-27 | 280958 | KBR6A | Rural short | LV Transformer SP4147-C KBR6A - Planned | 7.04 | 299 | 2104.96 | 0.0060507 | 2.0236e-05
2012-09-27 | 280959 | BVL10A | Urban | LV Transformer SP3782-D BVL10A - Planned | 6.12 | 185 | 1132.2 | 0.0011382 | 6.1525e-06
2012-09-27 | 281021 | MHL25A | Urban | LV Transformer SC782539 MHL25A - Planned | 23 | 312 | 7176 | 0.0072141 | 2.3122e-05
2012-09-27 | 281063 | BWH13A | Rural short | Feeder BWH13A - Planned | 64.33 | 218 | 14023.94 | 0.040312 | 0.00018492
2012-09-28 | 280971 | SMF5A | Rural short | LV Transformer SP1604-L SMF5A - Planned | 11 | 45 | 495 | 0.0014223 | 3.1607e-05
2012-09-28 | 280980 | WSE3A | Rural short | LV Transformer SP238-H WSE3A - Planned | 7.04 | 202 | 1422.08 | 0.0040862 | 2.0229e-05
2012-09-28 | 280982 | WSE3A | Rural short | LV Transformer SP759597 WSE3A - Planned | 8 | 158 | 1264 | 0.003632 | 2.2987e-05
2012-09-28 | 280983 | KBN2A | Rural short | LV Transformer SP4192-E KBN2A - Planned | 19.08 | 66 | 1259.28 | 0.0036184 | 5.4824e-05
2012-09-28 | 280984 | TGW2 | Rural short | LV Transformer SP3090-B TGW2 - Planned | 0.5 | 70 | 35 | 0.00010057 | 1.4367e-06
2012-09-28 | 280985 | KBN5A | Rural short | LV Transformer SP5275-D KBN5A - Planned | 7.04 | 250 | 1760 | 0.0050572 | 2.0229e-05
2012-09-28 | 280986 | TGW2 | Rural short | LV Transformer SP2349-B TGW2 - Planned | 3 | 191 | 573 | 0.0016465 | 8.6202e-06
2012-09-28 | 281000 | GBN4 | Rural short | Feeder GBN4 - Planned | 15 | 371 | 5565 | 0.01599 | 4.3101e-05
2012-09-28 | 281001 | MTB13A | Rural short | LV Transformer SP3080-C MTB13A - Planned | 14.5 | 337 | 4886.5 | 0.014041 | 4.1664e-05
2012-09-28 | 281002 | MWMRBK11 | Rural short | LV Transformer SP801824 MWMRBK11 - Planned | 1 | 490 | 490 | 0.001408 | 2.8734e-06
2012-09-28 | 281004 | ENG8 | Urban | LV Transformer SP1965-L ENG8 - Planned | 2.335 | 195 | 455.325 | 0.00045768 | 2.3471e-06
2012-09-28 | 281005 | NMK18 | Urban | LV Transformer SP522463 NMK18 - Planned | 11.1 | 316 | 3507.6 | 0.0035258 | 1.1157e-05
2012-09-28 | 281006 | GLY6 | Urban | LV Transformer SP4744-K GLY6 - Planned | 7.02 | 112 | 786.24 | 0.00079031 | 7.0564e-06
2012-09-28 | 281007 | SHW12 | Urban | LV Transformer SP367-R SHW12 - Planned | 23.495 | 164 | 3853.18 | 0.0038731 | 2.3617e-05
2012-09-28 | 281008 | PWC3 | Rural short | LV Transformer SP6659-B PWC3 - Planned | 3 | 225 | 675 | 0.0019395 | 8.6202e-06
2012-09-28 | 281009 | LBH1B | Rural short | LV Transformer SP4074-A LBH1B - Planned | 30.94 | 310 | 9591.4 | 0.02756 | 8.8903e-05
2012-09-28 | 281010 | NGI2B | Rural short | LV Transformer SP9094-F NGI2B - Planned | 2.97 | 140 | 415.8 | 0.0011948 | 8.534e-06
2012-09-28 | 281011 | PWC2 | Rural short | LV Transformer SP9905-A PWC2 - Planned | 22 | 134 | 2948 | 0.0084708 | 6.3215e-05
2012-09-28 | 281012 | BHD23A | Rural short | LV Transformer SP5771-G BHD23A - Planned | 28 | 283 | 7924 | 0.022769 | 8.0455e-05
2012-09-28 | 281013 | CCY26A | Urban | LV Transformer SC791051 CCY26A - Planned | 73.74 | 59 | 4350.66 | 0.0043732 | 7.4122e-05
2012-09-28 | 281014 | MTB13A | Rural short | LV Transformer SP9165-C MTB13A - Planned | 19.505 | 364 | 7099.82 | 0.020401 | 5.6046e-05
2012-09-28 | 281015 | BHD44A | Urban | LV Transformer SP1065-I BHD44A - Planned | 15.5981 | 438 | 6831.9678 | 0.0068674 | 1.5679e-05
2012-09-28 | 281016 | BRD8A | Rural short | LV Transformer SP7051-C BRD8A - Planned | 16.4 | 439 | 7199.6 | 0.020687 | 4.7124e-05
2012-09-28 | 281017 | BRD8A | Rural short | LV Transformer SP7124-E BRD8A - Planned | 2.07 | 463 | 958.41 | 0.0027539 | 5.9479e-06
2012-09-28 | 281018 | MHL3A | Rural short | LV Transformer SC1430330 MHL3A - Planned | 8.58 | 55 | 471.9 | 0.001356 | 2.4654e-05
2012-09-28 | 281019 | MHL3A | Rural short | LV Transformer SC1444516 MHL3A - Planned | 9.45 | 60 | 567 | 0.0016292 | 2.7154e-05
2012-09-28 | 281020 | NGE12 | Urban | LV Transformer SP10892-H NGE12 - Planned | 3.27 | 300 | 981 | 0.00098608 | 3.2869e-06
2012-09-28 | 281022 | CHL3 | Urban | LV Transformer SP494875 CHL3 - Planned | 22.115 | 231 | 5108.565 | 0.005135 | 2.223e-05
2012-09-28 | 281023 | ARG5A | Urban | LV Transformer SP3588-H ARG5A - Planned | 12.72 | 55 | 699.6 | 0.00070322 | 1.2786e-05
2012-09-28 | 281024 | RBY7A | Urban | LV Transformer SP5517-C RBY7A - Planned | 26.7525 | 39 | 1043.3475 | 0.0010488 | 2.6891e-05
2012-09-28 | 281025 | TGW2 | Rural short | LV Transformer SP7987-A TGW2 - Planned | 3.33 | 91 | 303.03 | 0.00087072 | 9.5684e-06
2012-09-28 | 281026 | BVL13A | Urban | LV Transformer SP1785-G BVL13A - Planned | 27.39 | 310 | 8490.9 | 0.0085349 | 2.7532e-05
2012-09-28 | 281027 | MWMRBK11 | Rural short | LV Transformer SP13034-C MWMRBK11 - Planned | 3.5 | 233 | 815.5 | 0.0023433 | 1.0057e-05
2012-09-28 | 281028 | TGW1 | Rural short | LV Transformer SP8349-A TGW1 - Planned | 2.0703 | 46 | 95.2338 | 0.00027364 | 5.9488e-06
2012-09-28 | 281064 | BRD8A | Rural short | Feeder BRD8A - Planned | 94.945 | 504 | 47852.28 | 0.1375 | 0.00027281
2012-09-29 | 281051 | NSD30B | Urban | LV Transformer SP16062-H NSD30B - Planned | 5.2 | 530 | 2756 | 0.0027699 | 5.2262e-06
2012-09-29 | 281052 | BDA3A | Urban | LV Transformer SP108-P BDA3A - Planned | 2.08 | 276 | 574.08 | 0.00057698 | 2.0905e-06
2012-09-30 | 281061 | CPR4 | Urban | LV Transformer SP8658-E CPR4 - Planned | 1.8 | 80 | 144 | 0.00014471 | 1.8088e-06
2012-09-30 | 281069 | MDR24A | Urban | LV Transformer SC364-M MDR24A - Planned | 42.77 | 339 | 14499.03 | 0.01457 | 4.298e-05
2012-09-30 | 281070 | RCF10A | Urban | LV Transformer SP374-J RCF10A - Planned | 1.64 | 349 | 572.36 | 0.00057517 | 1.648e-06
2012-10-02 | 281086 | KBR2A | Rural short | LV Transformer SP2124-C KBR2A - Planned | 3 | 9 | 27 | 7.7479e-05 | 8.6087e-06
2012-10-02 | 281088 | KBR2A | Rural short | LV Transformer SP425444 KBR2A - Planned | 1 | 21 | 21 | 6.0261e-05 | 2.8696e-06
2012-10-02 | 281100 | AMR2 | Rural short | LV Transformer SP6869-C AMR2 - Planned | 3.35 | 202 | 676.7 | 0.0019418 | 9.6131e-06
2012-10-02 | 281103 | RWD1 | Rural short | LV Transformer SP1204-H RWD1 - Planned | 2.01 | 229 | 460.29 | 0.0013208 | 5.7679e-06
2012-10-02 | 281107 | CBW13 | Rural short | LV Transformer SP9641-D CBW13 - Planned | 2 | 63 | 126 | 0.00036157 | 5.7392e-06
2012-10-02 | 281109 | NRG16A | Rural short | Feeder NRG16A - Planned | 66.8 | 257 | 17167.6 | 0.049264 | 0.00019169
2012-10-02 | 281110 | FDS3 | Rural short | LV Transformer SP4293-G FDS3 - Planned | 35 | 258 | 9030 | 0.025912 | 0.00010044
2012-10-02 | 281111 | AHD22A | Urban | LV Transformer SP6627-A AHD22A - Planned | 41.325 | 419 | 17315.175 | 0.017394 | 4.1514e-05
2012-10-02 | 281112 | JBB16A | Rural short | Feeder JBB16A - Planned | 29 | 468 | 13572 | 0.038946 | 8.3218e-05
2012-10-02 | 281113 | LLY4 | Rural short | Feeder LLY4 - Planned | 18 | 531 | 9558 | 0.027427 | 5.1652e-05
2012-10-02 | 281114 | BHL2A | Urban | LV Transformer SP458-K BHL2A - Planned | 1.98 | 352 | 696.96 | 0.00070015 | 1.9891e-06
2012-10-02 | 281115 | NSD30B | Urban | LV Transformer SP4226-J NSD30B - Planned | 4.625 | 226 | 1045.25 | 0.00105 | 4.6462e-06
2012-10-02 | 281116 | MGL5 | Urban | LV Transformer SC122-Q MGL5 - Planned | 2.04 | 83 | 169.32 | 0.00017009 | 2.0493e-06
2012-10-02 | 281117 | GYN3A | Rural short | LV Transformer SP1723-C GYN3A - Planned | 4 | 230 | 920 | 0.00264 | 1.1478e-05
2012-10-02 | 281118 | BWH16A | Rural short | LV Transformer SP14475-A BWH16A - Planned | 2.04 | 125 | 255 | 0.00073174 | 5.8539e-06
2012-10-02 | 281119 | TCB3 | Rural short | LV Transformer SP6381-C TCB3 - Planned | 2.24 | 299 | 669.76 | 0.0019219 | 6.4279e-06
2012-10-02 | 281120 | LDR1 | Urban | LV Transformer SP2861-F LDR1 - Planned | 1.68 | 205 | 344.4 | 0.00034597 | 1.6877e-06
2012-10-02 | 281121 | TGP9A | Rural short | LV Transformer SP1622-J TGP9A - Planned | 11.375 | 284 | 3230.5 | 0.0092702 | 3.2641e-05
2012-10-02 | 281122 | LLY4 | Rural short | LV Transformer SP3949-C LLY4 - Planned | 3 | 79 | 237 | 0.00068009 | 8.6087e-06
2012-10-02 | 281123 | CRB24B | Urban | LV Transformer SP11807-D CRB24B - Planned | 1.8375 | 457 | 839.7375 | 0.00084358 | 1.8459e-06
2012-10-03 | 281162 | BDT1 | Rural short | LV Transformer SP1820-G BDT1 - Planned | 8.01 | 180 | 1441.8 | 0.0041362 | 2.2979e-05
2012-10-03 | 281172 | MTB15A | Rural short | Feeder MTB15A - Planned | 1 | 158 | 158 | 0.00045326 | 2.8688e-06
2012-10-03 | 281173 | CRY6A | Rural short | Feeder CRY6A - Planned | 14 | 253 | 3542 | 0.010161 | 4.0163e-05
2012-10-03 | 281181 | MBG1 | Rural short | Feeder MBG1 - Planned | 16.51 | 325 | 5365.75 | 0.015393 | 4.7363e-05
2012-10-03 | 281182 | CVL7A | Rural short | Feeder CVL7A - Planned | 20.96 | 350 | 7336 | 0.021045 | 6.0129e-05
2012-10-03 | 281183 | CRB25A | Rural short | Feeder CRB25A - Planned | 15 | 365 | 5475 | 0.015706 | 4.3031e-05
2012-10-03 | 281185 | GBN4 | Rural short | LV Transformer SP4801-B GBN4 - Planned | 3 | 381 | 1143 | 0.003279 | 8.6063e-06
2012-10-03 | 281186 | GYN3A | Rural short | Feeder GYN3A - Planned | 3.01 | 400 | 1204 | 0.003454 | 8.6349e-06
2012-10-03 | 281188 | BGY3A | Urban | Feeder BGY3A - Planned | 1.306 | 526 | 686.956 | 0.00068998 | 1.3118e-06
2012-10-03 | 281189 | STL2 | Urban | LV Transformer SP3004-M STL2 - Planned | 12.8681 | 299 | 3847.5619 | 0.0038645 | 1.2925e-05
2012-10-03 | 281190 | NMK10 | Urban | LV Transformer SP2667-K NMK17A - Planned | 0.8266 | 400 | 330.64 | 0.0003321 | 8.3024e-07
2012-10-03 | 281190 | NMK17A | Urban | LV Transformer SP2667-K NMK17A - Planned | 15.385 | 400 | 6154 | 0.0061811 | 1.5453e-05
2012-10-03 | 281191 | NBR4 | Rural short | LV Transformer SP5132-A NBR4 - Planned | 1 | 218 | 218 | 0.00062539 | 2.8688e-06
2012-10-03 | 281192 | CMD5A | Urban | LV Transformer SP805-C CMD5A - Planned | 27.3 | 325 | 8872.5 | 0.0089116 | 2.742e-05
2012-10-03 | 281193 | AMR1 | Rural short | LV Transformer SP11581-B AMR1 - Planned | 3.195 | 243 | 776.385 | 0.0022273 | 9.1657e-06
2012-10-03 | 281194 | LDR8 | Urban | LV Transformer SP468825 LDR8 - Planned | 3.93 | 400 | 1572 | 0.0015789 | 3.9473e-06
2012-10-03 | 281196 | GVN12A | Urban | LV Transformer SP6382-C GVN12A - Planned | 17 | 422 | 7174 | 0.0072056 | 1.7075e-05
2012-10-03 | 281198 | BHD23A | Rural short | LV Transformer SP17420-D BHD23A - Planned | 26.4 | 246 | 6494.4 | 0.018631 | 7.5735e-05
2012-10-03 | 281199 | DRD15B | Urban | LV Transformer SP429-G DRD15B - Planned | 18.6225 | 176 | 3277.56 | 0.003292 | 1.8705e-05
2012-10-03 | 281199 | DRD5A | Urban | LV Transformer SP429-G DRD15B - Planned | 1.1325 | 176 | 199.32 | 0.0002002 | 1.1375e-06
2012-10-03 | 281200 | WED6A | Urban | LV Transformer SP5406-G WED6A - Planned | 16.02 | 247 | 3956.94 | 0.0039744 | 1.6091e-05
2012-10-03 | 281201 | ALY8 | Urban | LV Transformer SP3396-G ALY8 - Planned | 45.26 | 353 | 15976.78 | 0.016047 | 4.5459e-05
2012-10-03 | 281202 | ALY6 | Urban | LV Transformer SP1610-I ALY6 - Planned | 11.895 | 248 | 2949.96 | 0.002963 | 1.1947e-05
2012-10-03 | 281203 | WED6A | Urban | LV Transformer SC4124-I WED6A - Planned | 10.4419 | 30 | 313.257 | 0.00031464 | 1.0488e-05
2012-10-03 | 281204 | BLB8B | Urban | LV Transformer SP1674-H BLB8B - Planned | 6.225 | 14 | 87.15 | 8.7534e-05 | 6.2524e-06
2012-10-03 | 281206 | FDS3 | Rural short | LV Transformer SP8216-B FDS3 - Planned | 25.27 | 384 | 9703.68 | 0.027837 | 7.2493e-05
2012-10-03 | 281207 | LLY1 | Rural short | LV Transformer SP2318-C LLY1 - Planned | 35.88 | 289 | 10369.32 | 0.029747 | 0.00010293
2012-10-03 | 281397 | BTN2 | Rural short | LV Transformer SP286-E BTN2 - Planned | 4.5 | 130 | 585 | 0.0016782 | 1.2909e-05
2012-10-04 | 281220 | GYS5A | Rural short | LV Transformer SP3091-D GYS5A - Planned | 3 | 153 | 459 | 0.0013165 | 8.6048e-06
2012-10-04 | 281221 | GBN3 | Rural short | LV Transformer SP2554-D GBN3 - Planned | 6 | 30 | 180 | 0.00051629 | 1.721e-05
2012-10-04 | 281223 | PWC3 | Rural short | Feeder PWC3 - Planned | 78 | 124 | 9672 | 0.027742 | 0.00022372
2012-10-04 | 281224 | BWH16A | Rural short | LV Transformer SP1670-B BWH16A - Planned | 4.5 | 144 | 648 | 0.0018586 | 1.2907e-05
2012-10-04 | 281226 | WMR3 | Rural short | LV Transformer SP11841-D WMR3 - Planned | 3 | 92 | 276 | 0.00079164 | 8.6048e-06
2012-10-04 | 281227 | NBR7 | Urban | LV Transformer SC329-A NBR7 - Planned | 3 | 337 | 1011 | 0.0010152 | 3.0126e-06
2012-10-04 | 281228 | LBH1B | Rural short | Feeder LBH1B - Planned | 95.5 | 313 | 29891.5 | 0.085737 | 0.00027392
2012-10-04 | 281229 | RWD1 | Rural short | LV Transformer SP270920 RWD1 - Planned | 1 | 174 | 174 | 0.00049908 | 2.8683e-06
2012-10-04 | 281230 | GGR1 | Rural short | Feeder GGR1 - Planned | 18 | 386 | 6948 | 0.019929 | 5.1629e-05
2012-10-04 | 281231 | PPE6A | Rural short | LV Transformer SP9730-A PPE6A - Planned | 1 | 293 | 293 | 0.0008404 | 2.8683e-06
2012-10-04 | 281234 | GBN4 | Rural short | Feeder GBN4 - Planned | 17.5 | 365 | 6387.5 | 0.018321 | 5.0195e-05
2012-10-04 | 281235 | GYN3A | Rural short | Feeder GYN3A - Planned | 2 | 516 | 1032 | 0.00296 | 5.7365e-06
2012-10-04 | 281236 | HPK2 | Urban | LV Transformer SP4166-G HPK2 - Planned | 0.765 | 218 | 166.77 | 0.00016747 | 7.6821e-07
2012-10-04 | 281237 | NMK17A | Urban | LV Transformer SP1331-O NMK17A - Planned | 1.898 | 245 | 465.01 | 0.00046696 | 1.906e-06
2012-10-04 | 281238 | SFD3 | Urban | LV Transformer SC4054-K SFD3 - Planned | 16.215 | 342 | 5545.53 | 0.0055688 | 1.6283e-05
2012-10-04 | 281239 | NMK26 | Urban | LV Transformer SP4338-K VPK19A - Planned | 57.75 | 386 | 22291.5 | 0.022385 | 5.7992e-05
2012-10-04 | 281239 | VPK19A | Urban | LV Transformer SP4338-K VPK19A - Planned | 2.72 | 386 | 1049.92 | 0.0010543 | 2.7314e-06
2012-10-04 | 281240 | TWG17 | Urban | LV Transformer SP3382-G TWG17 - Planned | 7.72 | 241 | 1860.52 | 0.0018683 | 7.7524e-06
2012-10-04 | 281241 | YDA3A | Rural short | LV Transformer SP119074 YDA3A - Planned | 6.9 | 305 | 2104.5 | 0.0060362 | 1.9791e-05
2012-10-04 | 281242 | CBT7A | Urban | LV Transformer SC21090-C CBT7A - Planned | 1.1611 | 283 | 328.5913 | 0.00032997 | 1.166e-06
2012-10-04 | 281243 | LBH1B | Rural short | LV Transformer SP2098-B LBH1B - Planned | 5.18 | 277 | 1434.86 | 0.0041155 | 1.4858e-05
2012-10-04 | 281244 | MGP13A | Rural short | LV Transformer SP4612-D MGP13A - Planned | 3.105 | 317 | 984.285 | 0.0028232 | 8.9059e-06
2012-10-04 | 281245 | PBH6 | Urban | LV Transformer SP383-K PBH6 - Planned | 24.3747 | 337 | 8214.2739 | 0.0082488 | 2.4477e-05
2012-10-04 | 281246 | CRBTHP14 | Urban | LV Transformer SP2526-H CRBTHP14 - Planned | 9.895 | 296 | 2928.92 | 0.0029412 | 9.9365e-06
2012-10-04 | 281247 | HIS12A | Urban | LV Transformer SC1527-F HIS12A - Planned | 13.225 | 150 | 1983.75 | 0.0019921 | 1.3281e-05
2012-10-04 | 281247 | HISSCV16 | Urban | LV Transformer SC1527-F HIS12A - Planned | 1.15 | 150 | 172.5 | 0.00017322 | 1.1548e-06
2012-10-04 | 281248 | SGT7 | Urban | LV Transformer SP3057-G SGT7 - Planned | 14.3728 | 198 | 2845.8144 | 0.0028578 | 1.4433e-05
2012-10-04 | 281249 | TGP9A | Rural short | LV Transformer SP3464-J TGP9A - Planned | 5.16 | 120 | 619.2 | 0.001776 | 1.48e-05
2012-10-04 | 281250 | NGE4B | Urban | LV Transformer SP589-L NGE4B - Planned | 7.81 | 360 | 2811.6 | 0.0028234 | 7.8428e-06
2012-10-04 | 281251 | CPL25B | Urban | LV Transformer SC23502-E CPL25B - Planned | 3.0096 | 19 | 57.1824 | 5.7423e-05 | 3.0222e-06
2012-10-04 | 281252 | CPL3A | Urban | LV Transformer SC5522-G CPL3A - Planned | 1.04 | 24 | 24.96 | 2.5065e-05 | 1.0444e-06
2012-10-04 | 281254 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 16.383 | 265 | 4341.495 | 0.0043597 | 1.6452e-05
2012-10-04 | 281255 | TGW4 | Rural short | LV Transformer SP8173-A TGW4 - Planned | 2.96 | 175 | 518 | 0.0014858 | 8.49e-06
2012-10-04 | 281257 | BNH3A | Rural short | LV Transformer SP1064-E BNH3A - Planned | 2.01 | 235 | 472.35 | 0.0013548 | 5.7652e-06
2012-10-04 | 281258 | MWMRBK11 | Rural short | LV Transformer SP5196-E MWMRBK11 - Planned | 1.14 | 275 | 313.5 | 0.0008992 | 3.2698e-06
2012-10-04 | 281259 | NIP1A | Urban | LV Transformer SP8573-C NIP1A - Planned | 4.55 | 325 | 1478.75 | 0.001485 | 4.5691e-06
2012-10-04 | 281396 | BHD33A | Urban | LV Transformer SC1423-G BHD33A - Planned | 143 | 39 | 5577 | 0.0056004 | 0.0001436
2012-10-05 | 281278 | IPL1 | Rural short | LV Transformer SP626-E IPL1 - Planned | 8 | 165 | 1320 | 0.0037862 | 2.2947e-05
2012-10-05 | 281279 | PWC6 | Rural short | LV Transformer SP5108-A PWC6 - Planned | 36 | 261 | 9396 | 0.026951 | 0.00010326
2012-10-05 | 281280 | AHD18B | Rural short | LV Transformer SC169615 AHD18B - Planned | 28.5 | 85 | 2422.5 | 0.0069485 | 8.1748e-05
2012-10-05 | 281281 | GYM9B | Rural short | LV Transformer SP5932-B GYM9B - Planned | 6 | 77 | 462 | 0.0013252 | 1.721e-05
2012-10-05 | 281282 | PWC6 | Rural short | Feeder PWC6 - Planned | 47.55 | 295 | 14027.25 | 0.040235 | 0.00013639
2012-10-05 | 281283 | GYN3A | Rural short | LV Transformer SP1728-D GYN3A - Planned | 3 | 122 | 366 | 0.0010498 | 8.605e-06
2012-10-05 | 281284 | AHD21 | Urban | LV Transformer SP4491-A AHD21 - Planned | 40 | 245 | 9800 | 0.0098384 | 4.0157e-05
2012-10-05 | 281285 | AMR2 | Rural short | Feeder AMR2 - Planned | 23.99 | 251 | 6021.49 | 0.017272 | 6.8811e-05
2012-10-05 | 281288 | FDS3 | Rural short | Feeder FDS3 - Planned | 15.43 | 346 | 5338.78 | 0.015313 | 4.4258e-05
2012-10-05 | 281289 | TGW2 | Rural short | LV Transformer SP12637-B TGW2 - Planned | 2.01 | 366 | 735.66 | 0.0021101 | 5.7654e-06
2012-10-05 | 281301 | MGP16A | Urban | LV Transformer SC757920 MGP16A - Planned | 1.5 | 398 | 597 | 0.00059934 | 1.5059e-06
2012-10-05 | 281302 | BVL3A | Urban | LV Transformer SP695-E BVL3A - Planned | 9.7881 | 308 | 3014.7348 | 0.0030266 | 9.8265e-06
2012-10-05 | 281303 | KLG7A | Rural short | LV Transformer SP1287764 KLG7A - Planned | 1 | 33 | 33 | 9.4655e-05 | 2.8683e-06
2012-10-05 | 281304 | BMT4 | Rural short | LV Transformer SP173789 BMT4 - Planned | 71.5 | 46 | 3289 | 0.009434 | 0.00020509
2012-10-05 | 281305 | ENG3 | Urban | LV Transformer SP1066-N ENG3 - Planned | 22.92 | 220 | 5042.4 | 0.0050622 | 2.301e-05
2012-10-05 | 281306 | KRN18A | Urban | LV Transformer SP6708-H KRN18A - Planned | 15.61 | 373 | 5822.53 | 0.0058454 | 1.5671e-05
2012-10-05 | 281307 | AGE10 | Urban | LV Transformer SG794-N AGE10 - Planned | 6.075 | 281 | 1707.075 | 0.0017138 | 6.0988e-06
2012-10-05 | 281308 | NMK26 | Urban | LV Transformer SP952-M NMK26 - Planned | 33.3 | 189 | 6293.7 | 0.0063184 | 3.3431e-05
2012-10-05 | 281309 | BWH8A | Rural short | LV Transformer SP355-B BWH8A - Planned | 2.05 | 85 | 174.25 | 0.00049981 | 5.8801e-06
2012-10-05 | 281310 | CRB25A | Rural short | LV Transformer SP11263-E CRB25A - Planned | 2.145 | 217 | 465.465 | 0.0013351 | 6.1526e-06
2012-10-05 | 281311 | NDH6 | Urban | LV Transformer SP8719-D NDH6 - Planned | 3.88 | 194 | 752.72 | 0.00075567 | 3.8952e-06
2012-10-05 | 281312 | DRD15B | Urban | LV Transformer SP4179-E DRD5A - Planned | 34.38 | 331 | 11379.78 | 0.011424 | 3.4515e-05
2012-10-05 | 281312 | DRD5A | Urban | LV Transformer SP4179-E DRD5A - Planned | 12.4575 | 331 | 4123.4325 | 0.0041396 | 1.2506e-05
2012-10-05 | 281313 | SBH6 | Urban | LV Transformer SC772820 SBH6 - Planned | 3.675 | 242 | 889.35 | 0.00089284 | 3.6894e-06
2012-10-05 | 281314 | DRD16A | Urban | LV Transformer SP5896-B DRD16A - Planned | 19.18 | 203 | 3893.54 | 0.0039088 | 1.9255e-05
2012-10-05 | 281315 | CSE7 | Urban | LV Transformer SC779126 CSE7 - Planned | 12.375 | 284 | 3514.5 | 0.0035283 | 1.2424e-05
2012-10-05 | 281316 | BWH8A | Rural short | LV Transformer SC798006 BWH8A - Planned | 1.5 | 350 | 525 | 0.0015059 | 4.3025e-06
2012-10-05 | 281317 | WED10 | Urban | LV Transformer SP12025-E WED10 - Planned | 8.22 | 235 | 1931.7 | 0.0019393 | 8.2522e-06
2012-10-05 | 281318 | RCN6A | Urban | LV Transformer SC5216-M RCN6A - Planned | 6.89 | 345 | 2377.05 | 0.0023864 | 6.917e-06
2012-10-05 | 281320 | NIP1A | Urban | LV Transformer SP3202-E NIP1A - Planned | 1.2733 | 233 | 296.6789 | 0.00029784 | 1.2783e-06
2012-10-05 | 281321 | FDS3 | Rural short | LV Transformer SP4382-F FDS3 - Planned | 3.96 | 348 | 1378.08 | 0.0039528 | 1.1359e-05
2012-10-05 | 281323 | CDSSRD23 | Urban | LV Transformer SG11652-G CDSSRD23 - Planned | 5 | 150 | 750 | 0.00075294 | 5.0196e-06
2012-10-06 | 281327 | KRN12 | Urban | LV Transformer SP12552-E KRN12 - Planned | 4.225 | 5 | 21.125 | 2.1202e-05 | 4.2404e-06
2012-10-06 | 281344 | NDH10 | Urban | LV Transformer SP995-L NDH10 - Planned | 1.86 | 310 | 576.6 | 0.0005787 | 1.8668e-06
2012-10-06 | 281347 | BLB8A | Urban | LV Transformer SP2486-K BLB8A - Planned | 2.1 | 324 | 680.4 | 0.00068288 | 2.1077e-06
2012-10-06 | 281348 | CPR4 | Urban | LV Transformer SP773397 CPR4 - Planned | 18.9 | 271 | 5121.9 | 0.0051406 | 1.8969e-05
2012-10-07 | 281362 | CRB24B | Urban | Feeder CRB24B - Planned | 185.85 | 360 | 66906 | 0.067132 | 0.00018648
2012-10-07 | 281364 | BSEENG15 | Urban | LV Transformer SP733239-A BSEENG15 - Planned | 1.155 | 413 | 477.015 | 0.00047863 | 1.1589e-06
2012-10-07 | 281364 | ENG2 | Urban | LV Transformer SP733239-A BSEENG15 - Planned | 1.895 | 413 | 782.635 | 0.00078528 | 1.9014e-06
2012-10-07 | 281365 | CDRSPD12 | Urban | LV Transformer SP4212-E CDRSPD12 - Planned | 2.57 | 515 | 1323.55 | 0.001328 | 2.5787e-06
2012-10-07 | 281366 | LTN7 | Urban | LV Transformer SP15158-B LTN7 - Planned | 5.2 | 393 | 2043.6 | 0.0020505 | 5.2176e-06
2012-10-07 | 281367 | HMT10A | Urban | LV Transformer SC771014 HMT10A - Planned | 10.07 | 118 | 1188.26 | 0.0011923 | 1.0104e-05
2012-10-07 | 281368 | CPL6A | Urban | LV Transformer SG4477-G CPL6A - Planned | 1.225 | 375 | 459.375 | 0.00046093 | 1.2291e-06
2012-10-07 | 281369 | RST8A | Urban | LV Transformer SP3358-B RST8A - Planned | 6.76 | 405 | 2737.8 | 0.002747 | 6.7828e-06
2012-10-08 | 281400 | BDT4 | Rural short | LV Transformer SP419-F BDT4 - Planned | 6.02 | 383 | 2305.66 | 0.0066138 | 1.7268e-05
2012-10-08 | 281401 | GYM2A | Rural short | LV Transformer SP1040-G GYM2A - Planned | 5 | 112 | 560 | 0.0016064 | 1.4342e-05
2012-10-08 | 281402 | GYS3A | Rural short | LV Transformer SP5988-A GYS3A - Planned | 7 | 195 | 1365 | 0.0039155 | 2.0079e-05
2012-10-08 | 281403 | MDR8A | Urban | LV Transformer SP6372-B MDR8A - Planned | 2 | 379 | 758 | 0.00076036 | 2.0062e-06
2012-10-08 | 281405 | CVL17A | Urban | LV Transformer SP10324-C CVL17A - Planned | 2.1549 | 249 | 536.5701 | 0.00053824 | 2.1616e-06
2012-10-08 | 281407 | KRN18A | Urban | LV Transformer SP2652-K KRN18A - Planned | 6.93 | 316 | 2189.88 | 0.0021967 | 6.9515e-06
2012-10-08 | 281408 | TWG18 | Urban | Feeder TWG18 - Planned | 22.18 | 325 | 7208.5 | 0.0072309 | 2.2249e-05
2012-10-08 | 281409 | NMK18 | Urban | LV Transformer SP243-Q NMK18 - Planned | 2.8683 | 180 | 516.294 | 0.0005179 | 2.8772e-06
2012-10-08 | 281410 | NBR4 | Rural short | LV Transformer SP4350-A NBR4 - Planned | 11.04 | 235 | 2594.4 | 0.007442 | 3.1668e-05
2012-10-08 | 281412 | HTN22A | Urban | LV Transformer SG2030-J HTN22A - Planned | 0.99 | 428 | 423.72 | 0.00042504 | 9.9308e-07
2012-10-08 | 281413 | ZMR3 | Urban | LV Transformer SP2197-J ZMR3 - Planned | 7.6181 | 210 | 1599.801 | 0.0016048 | 7.6418e-06
2012-10-08 | 281414 | CVL17A | Urban | LV Transformer SP10324-C CVL17A - Planned | 15.0843 | 322 | 4857.1446 | 0.0048722 | 1.5131e-05
2012-10-08 | 281415 | GGR4 | Rural short | LV Transformer SP4050-B GGR4 - Planned | 0.98 | 190 | 186.2 | 0.00053411 | 2.8111e-06
2012-10-09 | 281441 | WSE3A | Rural short | Feeder WSE3A - Planned | 13.91 | 260 | 3616.6 | 0.010374 | 3.9902e-05
2012-10-09 | 281460 | MCW4 | Rural short | Feeder MCW4 - Planned | 25.04 | 340 | 8513.6 | 0.024422 | 7.1829e-05
2012-10-09 | 281461 | KBR6A | Rural short | Feeder KBR6A - Planned | 18.66 | 410 | 7650.6 | 0.021946 | 5.3528e-05
2012-10-09 | 281462 | NRG9 | Rural short | LV Transformer SP6449-F NRG9 - Planned | 7 | 304 | 2128 | 0.0061043 | 2.008e-05
2012-10-09 | 281463 | RWD1 | Rural short | LV Transformer SP2150-E RWD1 - Planned | 0.5 | 445 | 222.5 | 0.00063826 | 1.4343e-06
2012-10-09 | 281464 | RBA35A | Rural short | Feeder RBA35A - Planned | 2 | 341 | 682 | 0.0019564 | 5.7371e-06
2012-10-09 | 281465 | KCY5 | Rural short | LV Transformer SP15054-A KCY5 - Planned | 1 | 330 | 330 | 0.00094663 | 2.8686e-06
2012-10-09 | 281466 | YDA3A | Rural short | Feeder YDA3A - Planned | 25.475 | 414 | 10546.65 | 0.030254 | 7.3077e-05
2012-10-09 | 281469 | TRG2A | Urban | LV Transformer SP3749-I TRG2A - Planned | 12.1464 | 181 | 2198.4984 | 0.0022047 | 1.2181e-05
2012-10-09 | 281471 | GGR1 | Rural short | Feeder GGR4, GGR1 - Planned | 77 | 455 | 35035 | 0.1005 | 0.00022088
2012-10-09 | 281471 | GGR4 | Rural short | Feeder GGR4, GGR1 - Planned | 4 | 455 | 1820 | 0.0052208 | 1.1474e-05
2012-10-09 | 281472 | SFD10 | Urban | Feeder SFD4, SFD10 - Planned | 18.775 | 293 | 5501.075 | 0.0055167 | 1.8828e-05
2012-10-09 | 281472 | SFD4 | Urban | Feeder SFD4, SFD10 - Planned | 7.68 | 293 | 2250.24 | 0.0022566 | 7.7018e-06
2012-10-09 | 281473 | AGE9 | Urban | LV Transformer SP2339-L AGE9 - Planned | 9.0747 | 310 | 2813.157 | 0.0028211 | 9.1005e-06
2012-10-09 | 281474 | CLD7A | Urban | LV Transformer SC219-A CLD7A - Planned | 21.3629 | 284 | 6067.0636 | 0.0060843 | 2.1424e-05
2012-10-09 | 281475 | MFD3A | Rural short | LV Transformer SP12088-D MFD3A - Planned | 3.15 | 185 | 582.75 | 0.0016717 | 9.036e-06
2012-10-09 | 281476 | CMD13A | Urban | LV Transformer SP4383-B CMD13A - Planned | 27.83 | 296 | 8237.68 | 0.0082611 | 2.7909e-05
2012-10-09 | 281477 | CMD13A | Urban | LV Transformer SP3474-A CMD13A - Planned | 15.99 | 297 | 4749.03 | 0.0047625 | 1.6035e-05
2012-10-09 | 281478 | BMT1 | Rural short | LV Transformer SP1682-D BMT1 - Planned | 4.98 | 232 | 1155.36 | 0.0033142 | 1.4285e-05
2012-10-09 | 281479 | HIS12A | Urban | Feeder HIS12A - Planned | 11.92 | 128 | 1525.76 | 0.0015301 | 1.1954e-05
2012-10-09 | 281480 | LDR1 | Urban | Feeder LDR8, LDR1 - Planned | 23.52 | 349 | 8208.48 | 0.0082318 | 2.3587e-05
2012-10-09 | 281480 | LDR8 | Urban | Feeder LDR8, LDR1 - Planned | 2.62 | 349 | 914.38 | 0.00091698 | 2.6274e-06
2012-10-09 | 281481 | MTB1B | Rural short | Feeder MTB1B - Planned | 33.275 | 406 | 13509.65 | 0.038753 | 9.5452e-05
2012-10-09 | 281482 | MAI11 | Urban | LV Transformer SP1583-G MAI11 - Planned | 6.5799 | 195 | 1283.0805 | 0.0012867 | 6.5986e-06
2012-10-09 | 281484 | HTN24B | Urban | LV Transformer SC1179-T HTN24B - Planned | 13.855 | 346 | 4793.83 | 0.0048074 | 1.3894e-05
2012-10-09 | 281485 | ZMR4A | Urban | LV Transformer SC816933 ZMR4A - Planned | 0.98 | 202 | 197.96 | 0.00019852 | 9.8278e-07
2012-10-09 | 281486 | QPT24A | Urban | LV Transformer SP2881-J QPT24A - Planned | 6.0431 | 143 | 864.1633 | 0.00086662 | 6.0603e-06
2012-10-09 | 281487 | MTG11A | Urban | Feeder MTG11A - Planned | 6.275 | 262 | 1644.05 | 0.0016487 | 6.2928e-06
2012-10-09 | 281488 | SBK12 | Urban | LV Transformer SG2003-N SBK12 - Planned | 4.355 | 32 | 139.36 | 0.00013976 | 4.3674e-06
2012-10-09 | 281489 | BVL13A | Urban | LV Transformer SP4231-F BVL13A - Planned | 22.08 | 283 | 6248.64 | 0.0062664 | 2.2143e-05
2012-10-09 | 281490 | SPF12B | Urban | Feeder SPF12B - Planned | 89.37 | 71 | 6345.27 | 0.0063633 | 8.9624e-05
2012-10-09 | 281491 | SPF12B | Urban | LV Transformer SC1434958 SPF12B - Planned | 89.38 | 47 | 4200.86 | 0.0042128 | 8.9634e-05
2012-10-09 | 281492 | GGR4 | Rural short | LV Transformer SP5342-C GGR4 - Planned | 2.12 | 349 | 739.88 | 0.0021224 | 6.0814e-06
2012-10-09 | 281493 | LLY1 | Rural short | LV Transformer SP1930-C LLY1 - Planned | 1 | 309 | 309 | 0.00088639 | 2.8686e-06
2012-10-10 | 281502 | MGP13A | Rural short | LV Transformer SP1657-I MGP13A - Planned | 2 | 25 | 50 | 0.00014343 | 5.7371e-06
2012-10-10 | 281503 | BTA13A | Urban | LV Transformer SC567763 BTA13A - Planned | 98 | 70 | 6860 | 0.0068777 | 9.8253e-05
2012-10-10 | 281504 | MGP13A | Rural short | LV Transformer SP5197-H MGP13A - Planned | 1 | 12 | 12 | 3.4422e-05 | 2.8685e-06
2012-10-10 | 281520 | MGP13A | Rural short | LV Transformer SP1660-F MGP13A - Planned | 4 | 15 | 60 | 0.00017211 | 1.1474e-05
2012-10-10 | 281521 | WSE3A | Rural short | Feeder WSE3A - Planned | 34.22 | 260 | 8897.2 | 0.025522 | 9.8161e-05
2012-10-10 | 281522 | CVL7A | Rural short | Feeder CVL7A - Planned | 46.915 | 276 | 12948.54 | 0.037143 | 0.00013458
2012-10-10 | 281523 | MGP13A | Rural short | LV Transformer SP1658-H MGP13A - Planned | 1 | 50 | 50 | 0.00014343 | 2.8685e-06
2012-10-10 | 281524 | MFN15A | Rural short | LV Transformer SP3185-F MFN15A - Planned | 15.5 | 176 | 2728 | 0.0078254 | 4.4462e-05
2012-10-10 | 281525 | AMR3 | Rural short | Feeder AMR3 - Planned | 26 | 232 | 6032 | 0.017303 | 7.4582e-05
2012-10-10 | 281527 | GTN12A | Rural short | LV Transformer SP2287-E GTN12A - Planned | 2.732 | 370 | 1010.84 | 0.0028996 | 7.8368e-06
2012-10-10 | 281528 | BGY15A | Urban | LV Transformer SP16776-D BGY15A - Planned | 10.01 | 320 | 3203.2 | 0.0032115 | 1.0036e-05
2012-10-10 | 281529 | KBR6A | Rural short | Feeder KBR6A - Planned | 73 | 357 | 26061 | 0.074757 | 0.0002094
2012-10-10 | 281531 | GVN12A | Urban | LV Transformer SP125287 GVN12A - Planned | 8 | 397 | 3176 | 0.0031842 | 8.0206e-06
2012-10-10 | 281534 | YDA3A | Rural short | LV Transformer SP16515-A YDA3A - Planned | 2.01 | 350 | 703.5 | 0.002018 | 5.7658e-06
2012-10-10 | 281535 | WMD8B | Rural short | LV Transformer SP1237-B WMD8B - Planned | 6.02 | 478 | 2877.56 | 0.0082544 | 1.7269e-05
2012-10-10 | 281536 | GBN4 | Rural short | LV Transformer SP880-B GBN4 - Planned | 3.5 | 67 | 234.5 | 0.00067267 | 1.004e-05
2012-10-10 | 281543 | GAP9A | Urban | LV Transformer SP57243-B MCW11 - Planned | 5.975 | 231 | 1380.225 | 0.0013838 | 5.9904e-06
2012-10-10 | 281544 | TRG2A | Urban | LV Transformer SP4206-I TRG2A - Planned | 17.17 | 337 | 5786.29 | 0.0058012 | 1.7214e-05
2012-10-10 | 281545 | GLY6 | Urban | LV Transformer SP4744-K GLY6 - Planned | 3.78 | 205 | 774.9 | 0.0007769 | 3.7897e-06
2012-10-10 | 281546 | KRN12 | Urban | LV Transformer SP2710-I KRN12 - Planned | 6.86 | 221 | 1516.06 | 0.00152 | 6.8777e-06
2012-10-10 | 281547 | KRN1 | Urban | LV Transformer SP761254 KRN1 - Planned | 13.68 | 426 | 5827.68 | 0.0058427 | 1.3715e-05
2012-10-10 | 281547 | KRN18A | Urban | LV Transformer SP761254 KRN1 - Planned | 16.055 | 426 | 6839.43 | 0.0068571 | 1.6096e-05
2012-10-10 | 281548 | CMD13A | Urban | LV Transformer SP4383-B CMD13A - Planned | 36.685 | 211 | 7740.535 | 0.0077605 | 3.678e-05
2012-10-10 | 281549 | CMD13A | Urban | LV Transformer SP3807-A CMD13A - Planned | 15.62 | 270 | 4217.4 | 0.0042283 | 1.566e-05
2012-10-10 | 281550 | AHD21 | Urban | LV Transformer SP4491-A AHD21 - Planned | 11.2 | 370 | 4144 | 0.0041547 | 1.1229e-05
2012-10-10 | 281551 | WMD14A | Rural short | LV Transformer SC455388 WMD14A - Planned | 37.49 | 52 | 1949.48 | 0.0055922 | 0.00010754
2012-10-10 | 281552 | GVN3A | Urban | LV Transformer SP6343-C GVN3A - Planned | 16.45 | 335 | 5510.75 | 0.0055249 | 1.6492e-05
2012-10-10 | 281555 | SPO60A | Urban | LV Transformer SP10017-E SPO60A - Planned | 1.1 | 262 | 288.2 | 0.00028894 | 1.1028e-06
2012-10-10 | 281556 | CNB24A | Rural short | LV Transformer SP2656-E CNB24A - Planned | 11.31 | 435 | 4919.85 | 0.014113 | 3.2443e-05
2012-10-10 | 281557 | LDR3 | Urban | LV Transformer SP10515-D LDR3 - Planned | 92.625 | 288 | 26676 | 0.026745 | 9.2864e-05
2012-10-10 | 281559 | CSE2 | Urban | LV Transformer SC4431-L CSE2 - Planned | 24.3342 | 461 | 11218.0662 | 0.011247 | 2.4397e-05
2012-10-10 | 281560 | HDA3A | Urban | LV Transformer SP3613-G HDA3A - Planned | 22.2 | 315 | 6993 | 0.007011 | 2.2257e-05
2012-10-10 | 281561 | DRD3A | Urban | LV Transformer SC466-H DRD3A - Planned | 2.175 | 265 | 576.375 | 0.00057786 | 2.1806e-06
2012-10-10 | 281562 | NRA1A | Rural short | LV Transformer SP5702-E NRA1A - Planned | 6 | 151 | 906 | 0.0025989 | 1.7211e-05
2012-10-10 | 281563 | MTG3A | Urban | LV Transformer SP2662-M MTG3A - Planned | 3.6866 | 287 | 1058.0542 | 0.0010608 | 3.6961e-06
2012-10-10 | 281564 | ALY8 | Urban | LV Transformer SP3396-G ALY8 - Planned | 45.26 | 290 | 13125.4 | 0.013159 | 4.5377e-05
2012-10-10 | 281566 | RCN3A | Urban | LV Transformer SC6116-J RCN3A - Planned | 7.92 | 285 | 2257.2 | 0.002263 | 7.9404e-06
2012-10-10 | 281567 | LLY3 | Rural short | LV Transformer SP13480-B LLY3 - Planned | 8.91 | 122 | 1087.02 | 0.0031182 | 2.5559e-05
2012-10-10 | 281568 | MCW11 | Rural short | LV Transformer SP3647-D MCW11 - Planned | 3.9 | 165 | 643.5 | 0.0018459 | 1.1187e-05
2012-10-10 | 281570 | BVL13A | Urban | LV Transformer SP4231-F BVL13A - Planned | 20.24 | 213 | 4311.12 | 0.0043222 | 2.0292e-05
2012-10-10 | 281572 | MCW4 | Rural short | LV Transformer SP4311-I MCW4 - Planned | 2.88 | 275 | 792 | 0.0022719 | 8.2614e-06
2012-10-10 | 281780 | KBN1B | Rural short | LV Transformer SP794059 KBN1B - Planned | 6.02 | 374 | 2251.48 | 0.0064585 | 1.7269e-05
2012-10-10 | 281781 | CNB24A | Rural short | Feeder CNB24A - Planned | 8.8 | 521 | 4584.8 | 0.013152 | 2.5243e-05
2012-10-11 | 281600 | MGP13A | Rural short | LV Transformer SP470343 MGP13A - Planned | 3 | 29 | 87 | 0.00024956 | 8.6055e-06
2012-10-11 | 281601 | MGP13A | Rural short | LV Transformer SP15823-C MGP13A - Planned | 0.4 | 25 | 10 | 2.8685e-05 | 1.1474e-06
2012-10-11 | 281604 | MGP13A | Rural short | LV Transformer SP1655-F MGP13A - Planned | 7 | 64 | 448 | 0.0012851 | 2.0079e-05
2012-10-11 | 281608 | MGP13A | Rural short | LV Transformer SP12652-C MGP13A - Planned | 2 | 45 | 90 | 0.00025816 | 5.737e-06
2012-10-11 | 281609 | MGP13A | Rural short | LV Transformer SP1656-G MGP13A - Planned | 6.5 | 15 | 97.5 | 0.00027968 | 1.8645e-05
2012-10-11 | 281613 | MGP13A | Rural short | LV Transformer SP15297-B MGP13A - Planned | 2 | 47 | 94 | 0.00026964 | 5.737e-06
2012-10-11 | 281616 | PPE6A | Rural short | LV Transformer SP9730-A PPE6A - Planned | 1 | 395 | 395 | 0.0011331 | 2.8685e-06
2012-10-11 | 281619 | MCW11 | Rural short | Feeder MCW11 - Planned | 2 | 425 | 850 | 0.0024382 | 5.737e-06
2012-10-11 | 281620 | GGR3 | Rural short | Feeder GGR3, LRE7A, GGR5 - Planned | 6 | 486 | 2916 | 0.0083645 | 1.7211e-05
2012-10-11 | 281620 | GGR5 | Rural short | Feeder GGR3, LRE7A, GGR5 - Planned | 4.5 | 486 | 2187 | 0.0062734 | 1.2908e-05
2012-10-11 | 281620 | LRE7A | Rural short | Feeder GGR3, LRE7A, GGR5 - Planned | 11.04 | 486 | 5365.44 | 0.015391 | 3.1668e-05
2012-10-11 | 281624 | CRBTHP14 | Urban | Feeder CRBTHP26, CRBTHP14 - Planned | 21 | 459 | 9639 | 0.0096613 | 2.1049e-05
2012-10-11 | 281624 | CRBTHP26 | Urban | Feeder CRBTHP26, CRBTHP14 - Planned | 103.1283 | 459 | 47335.8897 | 0.047445 | 0.00010337
2012-10-11 | 281628 | KRN18A | Urban | LV Transformer SP2674-M KRN18A - Planned | 34.56 | 276 | 9538.56 | 0.0095606 | 3.464e-05
2012-10-11 | 281629 | KMR21A | Urban | LV Transformer SC6333-E KMR21A - Planned | 19.71 | 425 | 8376.75 | 0.0083961 | 1.9756e-05
2012-10-11 | 281630 | AGE10 | Urban | LV Transformer SP794408 AGE10 - Planned | 16.625 | 307 | 5103.875 | 0.0051157 | 1.6663e-05
2012-10-11 | 281630 | AGE9 | Urban | LV Transformer SP794408 AGE10 - Planned | 1.15 | 307 | 353.05 | 0.00035387 | 1.1527e-06
2012-10-11 | 281631 | SMR12A | Urban | LV Transformer SC3700-H SMR12A - Planned | 12.12 | 227 | 2751.24 | 0.0027576 | 1.2148e-05
2012-10-11 | 281632 | CSE10 | Urban | LV Transformer SP6701-K CSE10 - Planned | 48.0792 | 315 | 15144.948 | 0.01518 | 4.819e-05
2012-10-11 | 281633 | CBW12 | Urban | LV Transformer SC133-G CBW12 - Planned | 2.42 | 18 | 43.56 | 4.3661e-05 | 2.4256e-06
2012-10-11 | 281634 | GYM4 | Urban | LV Transformer SP171-C GYM4 - Planned | 0.87 | 130 | 113.1 | 0.00011336 | 8.7201e-07
2012-10-11 | 281635 | NBR4 | Rural short | LV Transformer SP4351-A NBR4 - Planned | 4.2 | 204 | 856.8 | 0.0024577 | 1.2048e-05
2012-10-11 | 281636 | CMD15A | Urban | LV Transformer SP5349-A CMD15A - Planned | 22.77 | 166 | 3779.82 | 0.0037886 | 2.2823e-05
2012-10-11 | 281637 | WMD8B | Rural short | LV Transformer SP2713-A WMD8B - Planned | 14.85 | 220 | 3267 | 0.0093714 | 4.2597e-05
2012-10-11 | 281638 | CMD13A | Urban | LV Transformer SP7754-C CMD13A - Planned | 45.66 | 226 | 10319.16 | 0.010343 | 4.5766e-05
2012-10-11 | 281639 | BLH11B | Urban | LV Transformer SP6935-C BLH11B - Planned | 35.145 | 241 | 8469.945 | 0.0084896 | 3.5226e-05
2012-10-11 | 281640 | MDR24A | Urban | LV Transformer SC1035-H MDR24A - Planned | 1.25 | 57 | 71.25 | 7.1415e-05 | 1.2529e-06
2012-10-11 | 281641 | BBH3A | Urban | LV Transformer SP2247-I BBH3A - Planned | 10.795 | 308 | 3324.86 | 0.0033326 | 1.082e-05
2012-10-11 | 281642 | SGT4 | Urban | LV Transformer SP1051297 SGT4 - Planned | 14.95 | 223 | 3333.85 | 0.0033416 | 1.4985e-05
2012-10-11 | 281643 | BRT5 | Urban | LV Transformer SP14156-E BRT5 - Planned | 6.96 | 134 | 932.64 | 0.0009348 | 6.9761e-06
2012-10-11 | 281643 | BRT8 | Urban | LV Transformer SP14156-E BRT5 - Planned | 5.13 | 134 | 687.42 | 0.00068901 | 5.1419e-06
2012-10-11 | 281645 | DRD2A | Rural short | LV Transformer SP3560-E DRD2A - Planned | 17.475 | 255 | 4456.125 | 0.012782 | 5.0127e-05
2012-10-11 | 281646 | DRD5A | Urban | LV Transformer SP4179-E DRD5A - Planned | 1.1325 | 170 | 192.525 | 0.00019297 | 1.1351e-06
2012-10-11 | 281647 | DRD3A | Urban | LV Transformer SC466-H DRD3A - Planned | 3.045 | 57 | 173.565 | 0.00017397 | 3.052e-06
2012-10-11 | 281648 | NSW3A | Urban | LV Transformer SC509000 NSW3A - Planned | 2.04 | 60 | 122.4 | 0.00012268 | 2.0447e-06
2012-10-11 | 281649 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 36.0426 | 275 | 9911.715 | 0.0099347 | 3.6126e-05
2012-10-11 | 281650 | HPE16A | Urban | LV Transformer SP1448-M HPE16A - Planned | 9.035 | 320 | 2891.2 | 0.0028979 | 9.0559e-06
2012-10-11 | 281650 | HPE3A | Urban | LV Transformer SP1448-M HPE16A - Planned | 0.88 | 320 | 281.6 | 0.00028225 | 8.8204e-07
2012-10-11 | 281651 | RBY2A | Urban | LV Transformer SP12058-B RBY2A - Planned | 29.7825 | 153 | 4556.7225 | 0.0045673 | 2.9851e-05
2012-10-11 | 281652 | UMG2B | Rural short | LV Transformer SP522-J UMG2B - Planned | 6.7398 | 329 | 2217.3942 | 0.0063606 | 1.9333e-05
2012-10-11 | 281653 | HPE12A | Urban | LV Transformer SP28994-E HPE12A - Planned | 34.526 | 244 | 8424.344 | 0.0084438 | 3.4606e-05
2012-10-11 | 281654 | MCW4 | Rural short | LV Transformer SP4420-E MCW4 - Planned | 19.32 | 344 | 6646.08 | 0.019064 | 5.5419e-05
2012-10-11 | 281655 | BVL13A | Urban | LV Transformer SP1785-G BVL13A - Planned | 27.39 | 257 | 7039.23 | 0.0070555 | 2.7453e-05
2012-10-11 | 281655 | BVL3A | Urban | LV Transformer SP1785-G BVL13A - Planned | 9.2213 | 257 | 2369.8741 | 0.0023754 | 9.2426e-06
2012-10-11 | 281656 | RST8A | Urban | LV Transformer SP756697 RST8A - Planned | 6.04 | 292 | 1763.68 | 0.0017678 | 6.054e-06
2012-10-11 | 281658 | CMD15A | Urban | LV Transformer SP10853-A CMD15A - Planned | 118.34 | 387 | 45797.58 | 0.045904 | 0.00011861
2012-10-11 | 281659 | WMD13A | Rural short | LV Transformer SP4422-A WMD13A - Planned | 0.99 | 299 | 296.01 | 0.0008491 | 2.8398e-06
2012-10-11 | 281660 | AMR3 | Rural short | LV Transformer SP5456-B AMR3 - Planned | 1 | 240 | 240 | 0.00068844 | 2.8685e-06
2012-10-11 | 281661 | KWH2 | Rural short | LV Transformer SP219383 KWH2 - Planned | 2 | 208 | 416 | 0.0011933 | 5.737e-06
2012-10-11 | 281785 | LBH5A | Rural short | Feeder LBH5A - Planned | 2.01 | 260 | 522.6 | 0.0014991 | 5.7657e-06
2012-10-12 | 281680 | BTN2 | Rural short | LV Transformer SP6752-E BTN2 - Planned | 3 | 58 | 174 | 0.00049911 | 8.6054e-06
2012-10-12 | 281681 | MGP13A | Rural short | LV Transformer SP230833-B MGP13A - Planned | 5 | 26 | 130 | 0.0003729 | 1.4342e-05
2012-10-12 | 281683 | MGP13A | Rural short | LV Transformer SP8749-C MGP13A - Planned | 1 | 33 | 33 | 9.466e-05 | 2.8685e-06
2012-10-12 | 281702 | MGP13A | Rural short | LV Transformer SP470064 MGP13A - Planned | 2 | 13 | 26 | 7.458e-05 | 5.7369e-06
2012-10-12 | 281704 | MGP13A | Rural short | LV Transformer SP1519-H MGP13A - Planned | 5 | 22 | 110 | 0.00031553 | 1.4342e-05
2012-10-12 | 281705 | BDT1 | Rural short | Feeder BDT1 - Planned | 6.985 | 118 | 824.23 | 0.0023643 | 2.0036e-05
2012-10-12 | 281708 | WSE3A | Rural short | Feeder WSE3A - Planned | 78.96 | 320 | 25267.2 | 0.072478 | 0.00022649
2012-10-12 | 281710 | BDT3 | Rural short | LV Transformer SP2383-D BDT3 - Planned | 12 | 410 | 4920 | 0.014113 | 3.4422e-05
2012-10-12 | 281713 | MCW11 | Rural short | LV Transformer SP3274-C MCW11 - Planned | 2.01 | 310 | 623.1 | 0.0017873 | 5.7656e-06
2012-10-12 | 281717 | TGW2 | Rural short | Feeder TGW2 - Planned | 118.8336 | 416 | 49434.7776 | 0.1418 | 0.00034087
2012-10-12 | 281718 | GBN4 | Rural short | LV Transformer SP6210-B GBN4 - Planned | 15.04 | 369 | 5549.76 | 0.015919 | 4.3142e-05
2012-10-12 | 281719 | EMD3 | Rural short | LV Transformer SP2886-C EMD3 - Planned | 2.01 | 266 | 534.66 | 0.0015337 | 5.7656e-06
2012-10-12 | 281720 | GBN4 | Rural short | Feeder GBN4 - Planned | 12 | 220 | 2640 | 0.0075728 | 3.4422e-05
2012-10-12 | 281721 | CNA9A | Rural short | Feeder CNA9A - Planned | 5.5 | 442 | 2431 | 0.0069733 | 1.5777e-05
2012-10-12 | 281729 | MFD13A | Rural short | LV Transformer SP307938 MFD13A - Planned | 28.275 | 251 | 7097.025 | 0.020358 | 8.1106e-05
2012-10-12 | 281730 | GAP6A | Urban | LV Transformer SC5227-J GAP6A - Planned | 5.5998 | 295 | 1651.941 | 0.0016553 | 5.6113e-06
2012-10-12 | 281731 | GLY6 | Urban | LV Transformer SP664073 GLY6 - Planned | 15.84 | 234 | 3706.56 | 0.0037142 | 1.5873e-05
2012-10-12 | 281732 | KMR17B | Urban | LV Transformer SP3625-L KMR17B - Planned | 29.75 | 194 | 5771.5 | 0.0057834 | 2.9811e-05
2012-10-12 | 281733 | KMR28A | Urban | LV Transformer SC3927-I KMR28A - Planned | 4.565 | 250 | 1141.25 | 0.0011436 | 4.5744e-06
2012-10-12 | 281734 | MLB6A | Rural short | LV Transformer SP9929-A MLB6A - Planned | 9 | 81 | 729 | 0.0020911 | 2.5816e-05
2012-10-12 | 281735 | MFD3A | Rural short | LV Transformer SP12088-D MFD3A - Planned | 3.15 | 350 | 1102.5 | 0.0031625 | 9.0357e-06
2012-10-12 | 281736 | SPO9A | Urban | LV Transformer SG1299-H SPO9A - Planned | 1.98 | 31 | 61.38 | 6.1506e-05 | 1.9841e-06
2012-10-12 | 281737 | MAI11 | Urban | LV Transformer SP14624-C MAI11 - Planned | 26.38 | 250 | 6595 | 0.0066085 | 2.6434e-05
2012-10-12 | 281738 | UPC1 | Rural short | LV Transformer SP8793-D UPC1 - Planned | 7 | 32 | 224 | 0.00064254 | 2.0079e-05
2012-10-12 | 281739 | HWL11A | Urban | LV Transformer SP10034-E HWL11A - Planned | 42.51 | 192 | 8161.92 | 0.0081787 | 4.2597e-05
2012-10-12 | 281740 | DRD16A | Urban | LV Transformer SP5896-B DRD16A - Planned | 28.085 | 137 | 3847.645 | 0.0038555 | 2.8143e-05
2012-10-12 | 281741 | SBH4 | Urban | LV Transformer SP3634-E SBH4 - Planned | 17.86 | 222 | 3964.92 | 0.0039731 | 1.7897e-05
2012-10-12 | 281742 | HMTPTR5 | Urban | LV Transformer SP5229-K HMTPTR5 - Planned | 10.12 | 130 | 1315.6 | 0.0013183 | 1.0141e-05
2012-10-12 | 281743 | MTG13A | Urban | LV Transformer SC5090-J MTG13A - Planned | 1.43 | 145 | 207.35 | 0.00020778 | 1.4329e-06
2012-10-12 | 281744 | CPR4 | Urban | LV Transformer SP756296 CPR4 - Planned | 1.64 | 241 | 395.24 | 0.00039605 | 1.6434e-06
2012-10-13 | 281760 | CPC25A | Urban | LV Transformer SG176-F CPC25A - Planned | 1 | 125 | 125 | 0.00012522 | 1.0018e-06
2012-10-13 | 281774 | BBH12B | Urban | LV Transformer SP16179-E BBH12B - Planned | 36.17 | 264 | 9548.88 | 0.009566 | 3.6235e-05
2012-10-13 | 281775 | BHD32B | Urban | LV Transformer SG165-L BHD32B - Planned | 86.23 | 295 | 25437.85 | 0.025483 | 8.6385e-05
2012-10-14 | 281778 | WSO3A | Urban | Feeder WSO3A - Planned | 1.5 | 310 | 465 | 0.00046571 | 1.5023e-06
2012-10-14 | 281779 | GARTR5H | Urban | LV Transformer SSCHA GARTR5H - Planned | 1 | 250 | 250 | 0.00025038 | 1.0015e-06
2012-10-14 | 281782 | WRD17A | Urban | LV Transformer SC22553-E WRD17A - Planned | 1 | 212 | 212 | 0.00021232 | 1.0015e-06
2012-10-14 | 281786 | DRD16A | Urban | LV Transformer SP9188-D DRD16A - Planned | 36.2101 | 374 | 13542.5774 | 0.013563 | 3.6266e-05
2012-10-14 | 281787 | BDT4 | Rural short | Feeder BDT4 - Planned | 20 | 380 | 7600 | 0.0218 | 5.7368e-05
2012-10-14 | 281789 | 585 | Urban | LV Transformer SSGAP 585 - Planned | 1 | 271 | 271 | 0.00027142 | 1.0015e-06
2012-10-14 | 281790 | DRA8 | Urban | LV Transformer SP1527-K DRA8 - Planned | 32.13 | 365 | 11727.45 | 0.011745 | 3.2179e-05
2012-10-14 | 281791 | MLY3 | Rural short | LV Transformer SP1658-B MLY3 - Planned | 2.685 | 243 | 652.455 | 0.0018715 | 7.7016e-06
2012-10-14 | 281792 | SPO11A | Urban | LV Transformer SP40561-B SPO11A - Planned | 37.335 | 276 | 10304.46 | 0.01032 | 3.7392e-05
2012-10-14 | 281793 | BDT4 | Rural short | Feeder BDT4 - Planned | 2.02 | 372 | 751.44 | 0.0021554 | 5.7941e-06
2012-10-14 | 281794 | NDH6 | Urban | Feeder NDH6 - Planned | 9.71 | 286 | 2777.06 | 0.0027813 | 9.7249e-06
2012-10-14 | 281795 | DRD16A | Urban | Feeder DRD16A - Planned | 11.9915 | 341 | 4089.1015 | 0.0040954 | 1.201e-05
2012-10-15 | 281840 | LBH1B | Rural short | LV Transformer SP17919-A LBH1B - Planned | 23.92 | 159 | 3803.28 | 0.010909 | 6.8611e-05
2012-10-15 | 281841 | WSE5A | Rural short | LV Transformer SP5629-B WSE5A - Planned | 4.5 | 139 | 625.5 | 0.0017941 | 1.2908e-05
2012-10-15 | 281843 | BGY5A | Rural short | LV Transformer SP2595-G BGY5A - Planned | 36.375 | 242 | 8802.75 | 0.025249 | 0.00010434
2012-10-15 | 281844 | AMR3 | Rural short | LV Transformer SP2344-D AMR3 - Planned | 7.6296 | 240 | 1831.104 | 0.0052522 | 2.1884e-05
2012-10-15 | 281845 | LBH1B | Rural short | LV Transformer SP192-C LBH1B - Planned | 13.95 | 162 | 2259.9 | 0.0064822 | 4.0013e-05
2012-10-15 | 281847 | JBB3A | Rural short | Feeder JBB3A - Planned | 36.89 | 222 | 8189.58 | 0.023491 | 0.00010581
2012-10-15 | 281864 | GBN4 | Rural short | LV Transformer SP1500-F GBN4 - Planned | 1 | 153 | 153 | 0.00043886 | 2.8683e-06
2012-10-15 | 281865 | CMD5A | Urban | LV Transformer SP4473-B CMD5A - Planned | 184.14 | 360 | 66290.4 | 0.066375 | 0.00018437
2012-10-15 | 281866 | CRB24B | Urban | LV Transformer SP6823-E CRB24B - Planned | 14.11 | 320 | 4515.2 | 0.0045209 | 1.4128e-05
2012-10-15 | 281867 | BRD8A | Rural short | Feeder BRD8A - Planned | 52.49 | 557 | 29236.93 | 0.083861 | 0.00015056
2012-10-15 | 281875 | NDH9 | Urban | LV Transformer SP481884 NDH9 - Planned | 2.4736 | 358 | 885.5488 | 0.00088668 | 2.4767e-06
2012-10-16 | 281882 | CDKQPT25 | Urban | LV Transformer SG4545-H CDKQPT25 - Planned | 0.99 | 22 | 21.78 | 2.1802e-05 | 9.91e-07
2012-10-16 | 281886 | SGT5 | Urban | LV Transformer SP2836-I SGT5 - Planned | 71 | 277 | 19667 | 0.019687 | 7.1072e-05
2012-10-16 | 281896 | MTB15A | Rural short | Feeder MTB15A - Planned | 53.99 | 298 | 16089.02 | 0.046149 | 0.00015486
2012-10-16 | 281897 | MTB1B | Rural short | Feeder MTB1B - Planned | 84.6 | 367 | 31048.2 | 0.089056 | 0.00024266
2012-10-16 | 281899 | JBB16A | Rural short | Feeder JBB16A - Planned | 20.9 | 430 | 8987 | 0.025778 | 5.9948e-05
2012-10-16 | 281900 | WMR1 | Rural short | LV Transformer SP17618-D WMR1 - Planned | 11.38 | 324 | 3687.12 | 0.010576 | 3.2642e-05
2012-10-16 | 281901 | KRN10 | Urban | LV Transformer SP1515-P KRN10 - Planned | 15 | 304 | 4560 | 0.0045646 | 1.5015e-05
2012-10-16 | 281902 | KRN1 | Urban | LV Transformer SP3264-J KRN18A - Planned | 1.52 | 393 | 597.36 | 0.00059796 | 1.5215e-06
2012-10-16 | 281902 | KRN18A | Urban | LV Transformer SP3264-J KRN18A - Planned | 9.77 | 393 | 3839.61 | 0.0038435 | 9.7799e-06
2012-10-16 | 281903 | JDL4A | Urban | LV Transformer SP46-M JDL4A - Planned | 4.04 | 277 | 1119.08 | 0.0011202 | 4.0441e-06
2012-10-16 | 281904 | BHD35A | Rural short | Feeder BHD35A - Planned | 18 | 530 | 9540 | 0.027364 | 5.163e-05
2012-10-16 | 281905 | AGE10 | Urban | LV Transformer SP2325-L AGE10 - Planned | 2.5166 | 277 | 697.0982 | 0.0006978 | 2.5191e-06
2012-10-16 | 281906 | AGE3 | Urban | LV Transformer SP2531-F AGE3 - Planned | 39.785 | 301 | 11975.285 | 0.011987 | 3.9825e-05
2012-10-16 | 281907 | CLD25A | Urban | LV Transformer SP4423-A CLD25A - Planned | 3.99 | 75 | 299.25 | 0.00029955 | 3.994e-06
2012-10-16 | 281908 | AHD21 | Urban | LV Transformer SP2831-A AHD21 - Planned | 27 | 395 | 10665 | 0.010676 | 2.7027e-05
2012-10-16 | 281909 | CMD5A | Urban | LV Transformer SP3804-B CMD5A - Planned | 15 | 208 | 3120 | 0.0031232 | 1.5015e-05
2012-10-16 | 281910 | AHD18B | Rural short | LV Transformer SC169714 AHD18B - Planned | 118.86 | 57 | 6775.02 | 0.019433 | 0.00034093
2012-10-16 | 281911 | GYN7A | Rural short | LV Transformer SP3828-B GYN7A - Planned | 4.98 | 148 | 737.04 | 0.0021141 | 1.4284e-05
2012-10-16 | 281912 | CLD18A | Rural short | LV Transformer SC1423470 CLD18A - Planned | 1 | 66 | 66 | 0.00018931 | 2.8683e-06
2012-10-16 | 281913 | CMD5A | Urban | LV Transformer SP71750 CMD5A - Planned | 57 | 266 | 15162 | 0.015177 | 5.7058e-05
2012-10-16 | 281914 | BHD35A | Rural short | LV Transformer SP395-J BHD35A - Planned | 11.96 | 430 | 5142.8 | 0.014751 | 3.4305e-05
2012-10-16 | 281915 | MGP13A | Rural short | LV Transformer SP3834-D MGP13A - Planned | 5.265 | 420 | 2211.3 | 0.0063427 | 1.5102e-05
2012-10-16 | 281916 | NRG12A | Urban | LV Transformer SC946-H NRG12A - Planned | 5.28 | 182 | 960.96 | 0.00096193 | 5.2853e-06
2012-10-16 | 281917 | HTN24A | Urban | LV Transformer SP740267 HTN24A - Planned | 28.89 | 358 | 10342.62 | 0.010353 | 2.8919e-05
2012-10-16 | 281919 | BRT6 | Urban | LV Transformer SP3896-F BRT6 - Planned | 13.32 | 320 | 4262.4 | 0.0042667 | 1.3333e-05
2012-10-16 | 281920 | ALY5 | Urban | LV Transformer SP4170-I ALY5 - Planned | 45.35 | 358 | 16235.3 | 0.016252 | 4.5396e-05
2012-10-16 | 281921 | VPT13A | Rural short | LV Transformer SC1369041 VPT13A - Planned | 4.28 | 95 | 406.6 | 0.0011663 | 1.2276e-05
2012-10-16 | 281922 | MSV2 | Rural short | LV Transformer SP1301-D MSV2 - Planned | 5 | 161 | 805 | 0.002309 | 1.4342e-05
2012-10-16 | 281923 | RST16A | Urban | LV Transformer SP426068 RST8A - Planned | 1.13 | 310 | 350.3 | 0.00035065 | 1.1311e-06
2012-10-16 | 281923 | RST8A | Urban | LV Transformer SP426068 RST8A - Planned | 3.04 | 310 | 942.4 | 0.00094335 | 3.0431e-06
2012-10-16 | 281924 | JBB16A | Rural short | LV Transformer SP7871-B JBB16A - Planned | 6.02 | 439 | 2642.78 | 0.0075803 | 1.7267e-05
2012-10-16 | 281926 | NBR4 | Rural short | Feeder NBR4 - Planned | 28.54 | 384 | 10959.36 | 0.031435 | 8.1862e-05
2012-10-16 | 281933 | NMK5 | Urban | LV Transformer SC4550-I NMK5 - Planned | 20.57 | 300 | 6171 | 0.0061772 | 2.0591e-05
2012-10-17 | 281980 | BNH2B | Rural short | LV Transformer SP5305-C BNH2B - Planned | 3 | 217 | 651 | 0.0018672 | 8.6048e-06
2012-10-17 | 281981 | SMF2A | Rural short | LV Transformer SP3154-E SMF2A - Planned | 12.2 | 214 | 2610.8 | 0.0074885 | 3.4993e-05
2012-10-17 | 282000 | MTB16A | Rural short | LV Transformer SP12757-B MTB16A - Planned | 26 | 340 | 8840 | 0.025355 | 7.4575e-05
2012-10-17 | 282001 | GGR4 | Rural short | Feeder GGR4 - Planned | 28.315 | 420 | 11892.3 | 0.03411 | 8.1215e-05
2012-10-17 | 282002 | GVN12A | Urban | LV Transformer SP125287 GVN12A - Planned | 6.88 | 454 | 3123.52 | 0.0031259 | 6.8852e-06
2012-10-17 | 282004 | MCN3 | Urban | LV Transformer SP4878-D MCN3 - Planned | 1 | 600 | 600 | 0.00060045 | 1.0008e-06
2012-10-17 | 282005 | SMF5A | Rural short | LV Transformer SP3676-G SMF5A - Planned | 1.1 | 70 | 77 | 0.00022086 | 3.1551e-06
2012-10-17 | 282006 | NMC1B | Rural short | LV Transformer SP7964-F NMC1B - Planned | 1 | 158 | 158 | 0.00045318 | 2.8683e-06
2012-10-17 | 282007 | INA7A | Rural short | Feeder INA7A - Planned | 15.9994 | 308 | 4927.8152 | 0.014134 | 4.589e-05
2012-10-17 | 282008 | AGE10 | Urban | Feeder AGE3, AGE10 - Planned | 0.7583 | 225 | 170.6175 | 0.00017075 | 7.5887e-07
2012-10-17 | 282008 | AGE3 | Urban | Feeder AGE3, AGE10 - Planned | 42.47 | 225 | 9555.75 | 0.0095629 | 4.2502e-05
2012-10-17 | 282009 | KRN18A | Urban | Feeder KRN12, KRN18A - Planned | 27.29 | 410 | 11188.9 | 0.011197 | 2.7311e-05
2012-10-17 | 282010 | EMD2 | Rural short | LV Transformer SP2282-E EMD2 - Planned | 3.1875 | 195 | 621.5625 | 0.0017828 | 9.1426e-06
2012-10-17 | 282011 | EMD2 | Rural short | LV Transformer SP1253-B EMD2 - Planned | 7.04 | 68 | 478.72 | 0.0013731 | 2.0193e-05
2012-10-17 | 282012 | GVN12A | Urban | LV Transformer SP6382-C GVN12A - Planned | 17.34 | 370 | 6415.8 | 0.0064206 | 1.7353e-05
2012-10-17 | 282013 | BHD44A | Urban | Feeder BHD44A - Planned | 19.4771 | 376 | 7323.3896 | 0.0073289 | 1.9492e-05
2012-10-17 | 282014 | BHD35A | Rural short | LV Transformer SP1117-L BHD35A - Planned | 2 | 359 | 718 | 0.0020594 | 5.7365e-06
2012-10-17 | 282015 | HIS5A | Urban | Feeder HIS5A, HWL10A - Planned | 3.99 | 207 | 825.93 | 0.00082655 | 3.993e-06
2012-10-17 | 282015 | HWL10A | Urban | Feeder HIS5A, HWL10A - Planned | 26.655 | 207 | 5517.585 | 0.0055217 | 2.6675e-05
2012-10-17 | 282016 | SBH6 | Urban | LV Transformer SC742283 SBH6 - Planned | 1.225 | 115 | 140.875 | 0.00014098 | 1.2259e-06
2012-10-17 | 282017 | HTN22A | Urban | Feeder HTN22A - Planned | 11.125 | 368 | 4094 | 0.0040971 | 1.1133e-05
2012-10-17 | 282018 | WSE3A | Rural short | LV Transformer SP9399-E WSE3A - Planned | 6.02 | 219 | 1318.38 | 0.0037815 | 1.7267e-05
2012-10-17 | 282019 | BRT6 | Urban | LV Transformer SP665-I BRT6 - Planned | 12 | 385 | 4620 | 0.0046235 | 1.2009e-05
2012-10-17 | 282020 | NRA5A | Rural short | LV Transformer SC2554-F NRA5A - Planned | 2.44 | 222 | 541.68 | 0.0015537 | 6.9986e-06
2012-10-17 | 282021 | QPT22A | Urban | Feeder QPT22A - Planned | 88.6816 | 446 | 39551.9936 | 0.039582 | 8.8748e-05
2012-10-17 | 282022 | CPL3A | Urban | Feeder CPL3A - Planned | 0.92 | 54 | 49.68 | 4.9717e-05 | 9.2069e-07
2012-10-17 | 282023 | NMC2A | Rural short | Feeder NMC2A - Planned | 4.44 | 69 | 306.36 | 0.00087872 | 1.2735e-05
2012-10-17 | 282024 | WRG6A | Urban | LV Transformer SP3148-J WRG6A - Planned | 29.12 | 271 | 7891.52 | 0.0078975 | 2.9142e-05
2012-10-17 | 282026 | NIP1A | Urban | Feeder NIP1A - Planned | 34.3633 | 242 | 8315.9186 | 0.0083222 | 3.4389e-05
2012-10-17 | 282027 | GGR4 | Rural short | LV Transformer SP744995 GGR4 - Planned | 6 | 340 | 2040 | 0.0058512 | 1.721e-05
2012-10-17 | 282029 | TCB3 | Rural short | Feeder TCB3 - Planned | 117.9 | 441 | 51993.9 | 0.14913 | 0.00033817
2012-10-17 | 282030 | EMD2 | Rural short | Feeder EMD2 - Planned | 91.59 | 435 | 39841.65 | 0.11428 | 0.0002627
2012-10-17 | 282031 | CBW11 | Rural short | LV Transformer SP4728-G CBW11 - Planned | 5 | 165 | 825 | 0.0023663 | 1.4341e-05
2012-10-17 | 282032 | TCB3 | Rural short | Feeder TCB3 - Planned | 139.5 | 245 | 34177.5 | 0.09803 | 0.00040012
2012-10-17 | 282033 | WFD1B | Rural short | Feeder WFD1B - Planned | 3 | 359 | 1077 | 0.0030891 | 8.6048e-06
2012-10-17 | 282035 | AHD5 | Urban | LV Transformer SP3501-B AHD5 - Planned | 141.8175 | 327 | 46374.3225 | 0.046409 | 0.00014192
2012-10-17 | 282036 | BWH8A | Rural short | LV Transformer SP5368-A BWH8A - Planned | 3.11 | 140 | 435.4 | 0.0012488 | 8.9203e-06
2012-10-17 | 282037 | TWT3A | Rural short | LV Transformer SP7578-C TWT3A - Planned | 18.05 | 186 | 3357.3 | 0.0096296 | 5.1772e-05
2012-10-17 | 282038 | BMT1 | Rural short | LV Transformer SP2354-D BMT1 - Planned | 13.02 | 164 | 2135.28 | 0.0061245 | 3.7345e-05
2012-10-17 | 282039 | CBW11 | Rural short | LV Transformer SP8361-D CBW11 - Planned | 8 | 46 | 368 | 0.0010555 | 2.2946e-05
2012-10-17 | 282044 | NRG12A | Urban | LV Transformer SC946-H NRG12A - Planned | 2.64 | 15 | 39.6 | 3.963e-05 | 2.642e-06
2012-10-18 | 282060 | LLY3 | Rural short | LV Transformer SP3979-C LLY3 - Planned | 2.01 | 154 | 309.54 | 0.00088782 | 5.7651e-06
2012-10-18 | 282080 | IPL1 | Rural short | Feeder IPL1 - Planned | 10 | 350 | 3500 | 0.010039 | 2.8682e-05
2012-10-18 | 282081 | GTN12A | Rural short | LV Transformer SP2049-C GTN12A - Planned | 3 | 382 | 1146 | 0.003287 | 8.6046e-06
2012-10-18 | 282083 | WSE3A | Rural short | Feeder WSE3A - Planned | 41.99 | 367 | 15410.33 | 0.0442 | 0.00012044
2012-10-18 | 282084 | NMC5A | Rural short | Feeder NMC5A - Planned | 80.95 | 412 | 33351.4 | 0.095658 | 0.00023218
2012-10-18 | 282085 | CNB24A | Rural short | Feeder CNB24A, MCN2 - Planned | 45.609 | 119 | 8444.158 | 0.024219 | 0.00013082
2012-10-18 | 282085 | MCN2 | Rural short | Feeder CNB24A, MCN2 - Planned | 1 | 62 | 62 | 0.00017783 | 2.8682e-06
2012-10-18 | 282086 | MCN3 | Urban | Feeder MCN3 - Planned | 0.264 | 406 | 107.184 | 0.00010724 | 2.6413e-07
2012-10-18 | 282087 | GYN3A | Rural short | Feeder GYN3A - Planned | 3.01 | 470 | 1414.7 | 0.0040576 | 8.6333e-06
2012-10-18 | 282088 | CMD13A | Urban | LV Transformer SP3474-A CMD13A - Planned | 21.25 | 370 | 7862.5 | 0.0078664 | 2.126e-05
2012-10-18 | 282089 | CBW11 | Rural short | LV Transformer SP3588-E CBW11 - Planned | 7 | 94 | 658 | 0.0018873 | 2.0077e-05
2012-10-18 | 282090 | BMT1 | Rural short | LV Transformer SP2153-C BMT1 - Planned | 14 | 223 | 3122 | 0.0089545 | 4.0155e-05
2012-10-18 | 282091 | AMR2 | Rural short | LV Transformer SP2654-E AMR2 - Planned | 9 | 115 | 1035 | 0.0029686 | 2.5814e-05
2012-10-18 | 282092 | MLY1 | Rural short | LV Transformer SP162324 MLY1 - Planned | 6 | 14 | 84 | 0.00024093 | 1.7209e-05
2012-10-18 | 282094 | BVL3A | Urban | LV Transformer SP811223 BVL3A - Planned | 19.2809 | 339 | 6536.2251 | 0.0065394 | 1.929e-05
2012-10-18 | 282095 | JDL8A | Urban | LV Transformer SC426346 JDL8A - Planned | 2.7 | 311 | 839.7 | 0.00084011 | 2.7013e-06
2012-10-18 | 282096 | JDL8A | Urban | LV Transformer SC518309-A JDL8A - Planned | 1.89 | 279 | 527.31 | 0.00052757 | 1.8909e-06
2012-10-18 | 282097 | SFD10 | Urban | LV Transformer SC4996-J SFD3 - Planned | 0.95 | 362 | 343.9 | 0.00034407 | 9.5047e-07
2012-10-18 | 282097 | SFD3 | Urban | LV Transformer SC4996-J SFD3 - Planned | 22.1 | 362 | 8000.2 | 0.0080041 | 2.2111e-05
2012-10-18 | 282098 | KRN18A | Urban | LV Transformer SP484728 KRN18A - Planned | 32.835 | 443 | 14545.905 | 0.014553 | 3.2851e-05
2012-10-18 | 282099 | KRN18A | Urban | LV Transformer SP2674-M KRN18A - Planned | 3.84 | 342 | 1313.28 | 0.0013139 | 3.8419e-06
2012-10-18 | 282100 | MLS15A | Urban | LV Transformer SG6239-D MLS15A - Planned | 4.4166 | 268 | 1183.6488 | 0.0011842 | 4.4188e-06
2012-10-18 | 282101 | CBW14 | Urban | LV Transformer SP5713-E CBW14 - Planned | 27.7675 | 372 | 10329.51 | 0.010335 | 2.7781e-05
2012-10-18 | 282102 | CRY6A | Rural short | LV Transformer SP272454 CRY6A - Planned | 3.375 | 294 | 992.25 | 0.002846 | 9.6802e-06
2012-10-18 | 282104 | CBW11 | Rural short | LV Transformer SP151-J CBW11 - Planned | 6.132 | 205 | 1257.06 | 0.0036055 | 1.7588e-05
2012-10-18 | 282105 | BHD23A | Rural short | LV Transformer SC1385938 BHD23A - Planned | 20.06 | 62 | 1243.72 | 0.0035672 | 5.7536e-05
2012-10-18 | 282107 | CRBTHP26 | Urban | LV Transformer SP2527-G CRBTHP26 - Planned | 155.67 | 462 | 71919.54 | 0.071955 | 0.00015575
2012-10-18 | 282108 | CNB24A | Rural short | LV Transformer SP472182 CNB24A - Planned | 3 | 330 | 990 | 0.0028395 | 8.6046e-06
2012-10-18 | 282109 | BHD23A | Rural short | LV Transformer SC1385938 BHD23A - Planned | 14.935 | 44 | 657.14 | 0.0018848 | 4.2837e-05
2012-10-18 | 282110 | JBB16A | Rural short | LV Transformer SP5422-D JBB16A - Planned | 5.075 | 196 | 994.7 | 0.002853 | 1.4556e-05
2012-10-18 | 282111 | DRD13A | Urban | LV Transformer SP5093-E DRD13A - Planned | 13.93 | 315 | 4387.95 | 0.0043901 | 1.3937e-05
2012-10-18 | 282112 | HTN24A | Urban | LV Transformer SC796369 HTN24A - Planned | 5.005 | 338 | 1691.69 | 0.0016925 | 5.0075e-06
2012-10-18 | 282113 | SBH6 | Urban | LV Transformer SC742283 SBH6 - Planned | 11.025 | 206 | 2271.15 | 0.0022723 | 1.103e-05
2012-10-18 | 282114 | BLB8A | Urban | LV Transformer SP1064381-A BLB8A - Planned | 6.8983 | 305 | 2103.9815 | 0.002105 | 6.9017e-06
2012-10-18 | 282115 | CPR5 | Urban | LV Transformer SP400-M CPR5 - Planned | 23.833 | 217 | 5171.761 | 0.0051743 | 2.3845e-05
2012-10-18 | 282116 | MTG3A | Urban | LV Transformer SP2602-J MTG3A - Planned | 19.9456 | 300 | 5983.68 | 0.0059866 | 1.9955e-05
2012-10-18 | 282117 | HPK3A | Urban | LV Transformer SP832-L HPK3A - Planned | 4.955 | 334 | 1654.97 | 0.0016558 | 4.9574e-06
2012-10-18 | 282118 | GTN12A | Rural short | LV Transformer SP2854-C GTN12A - Planned | 6 | 215 | 1290 | 0.0037 | 1.7209e-05
2012-10-18 | 282119 | NMC5A | Rural short | LV Transformer SP10793-G NMC5A - Planned | 16 | 363 | 5808 | 0.016658 | 4.5891e-05
2012-10-18 | 282120 | GGR1 | Rural short | LV Transformer SP8151-B GGR1 - Planned | 28 | 265 | 7420 | 0.021282 | 8.0309e-05
2012-10-18 | 282169 | CBT13A | Urban | LV Transformer SC2707-F CBT13A - Planned | 1 | 62 | 62 | 6.2031e-05 | 1.0005e-06
2012-10-18 | 282179 | CMD11A | Rural short | LV Transformer SP2094-A CMD11A - Planned | 23.5 | 195 | 4582.5 | 0.013144 | 6.7403e-05
2012-10-18 | 283540 | TPT1 | Urban | Feeder TPT1 - Planned | 2.76 | 315 | 869.4 | 0.00086983 | 2.7614e-06
2012-10-19 | 282143 | NBR6 | Rural short | LV Transformer SP17729-A NBR6 - Planned | 10.465 | 10 | 104.65 | 0.00030022 | 3.0022e-05
2012-10-19 | 282160 | MCW4 | Rural short | LV Transformer SP4955-C MCW4 - Planned | 23.04 | 251 | 5783.04 | 0.016591 | 6.6098e-05
2012-10-19 | 282161 | CRM13A | Urban | Feeder CRM13A - Planned | 241.25 | 235 | 56693.75 | 0.056715 | 0.00024134
2012-10-19 | 282164 | FDS3 | Rural short | Feeder KBR6A, FDS3 - Planned | 15.33 | 390 | 5978.7 | 0.017152 | 4.3979e-05
2012-10-19 | 282164 | KBR6A | Rural short | Feeder KBR6A, FDS3 - Planned | 18.66 | 390 | 7277.4 | 0.020878 | 5.3533e-05
2012-10-19 | 282165 | NBR8 | Rural short | Feeder NBR8 - Planned | 3.65 | 327 | 1193.55 | 0.0034241 | 1.0471e-05
2012-10-19 | 282166 | MLB8A | Rural short | Feeder MLB8A - Planned | 49.08 | 179 | 8785.32 | 0.025204 | 0.0001408
2012-10-19 | 282167 | GYN3A | Rural short | Feeder GYN3A - Planned | 77.962 | 386 | 30093.332 | 0.086333 | 0.00022366
2012-10-19 | 282168 | LBH1B | Rural short | Feeder LBH1B - Planned | 83.9472 | 383 | 32151.7776 | 0.092239 | 0.00024083
2012-10-19 | 282170 | WMR2 | Rural short | Feeder WMR2 - Planned | 30.9 | 190 | 5871 | 0.016843 | 8.8647e-05
2012-10-19 | 282171 | AMR2 | Rural short | LV Transformer SP356-C AMR2 - Planned | 3 | 28 | 84 | 0.00024098 | 8.6065e-06
2012-10-19 | 282172 | GYM2A | Rural short | LV Transformer SP735-B GYM2A - Planned | 20.425 | 66 | 1348.05 | 0.0038673 | 5.8596e-05
2012-10-19 | 282173 | AHD21 | Urban | LV Transformer SP9906-A AHD21 - Planned | 59.85 | 238 | 14244.3 | 0.01425 | 5.9872e-05
2012-10-19 | 282176 | WHO1 | Rural short | Feeder WHO1 - Planned | 11.38 | 353 | 4017.14 | 0.011525 | 3.2647e-05
2012-10-19 | 282177 | WMR2 | Rural short | Feeder WMR2 - Planned | 28.88 | 515 | 14873.2 | 0.042669 | 8.2852e-05
2012-10-19 | 282180 | KMR27A | Urban | LV Transformer SP2566-O KMR27A - Planned | 6.1947 | 80 | 495.576 | 0.00049576 | 6.197e-06
2012-10-19 | 282182 | SMR7A | Urban | LV Transformer SC3775-I SMR7A - Planned | 89.83 | 186 | 16708.38 | 0.016715 | 8.9863e-05
2012-10-19 | 282183 | AGE3 | Urban | LV Transformer SP1600-M AGE3 - Planned | 1.395 | 211 | 294.345 | 0.00029445 | 1.3955e-06
2012-10-19 | 282184 | MLB6A | Rural short | LV Transformer SP9776-A MLB6A - Planned | 3.33 | 184 | 612.72 | 0.0017578 | 9.5533e-06
2012-10-19 | 282185 | CMD13A | Urban | LV Transformer SP7754-C CMD13A - Planned | 31.32 | 210 | 6577.2 | 0.0065796 | 3.1332e-05
2012-10-19 | 282186 | AHD10A | Urban | LV Transformer SP3789-A AHD10A - Planned | 12.14 | 208 | 2525.12 | 0.0025261 | 1.2145e-05
2012-10-19 | 282187 | CBW12 | Urban | LV Transformer SP12670-C CBW12 - Planned | 13.015 | 360 | 4685.4 | 0.0046871 | 1.302e-05
2012-10-19 | 282188 | GYN3A | Rural short | LV Transformer SP1151-D GYN3A - Planned | 15.98 | 360 | 5752.8 | 0.016504 | 4.5844e-05
2012-10-19 | 282189 | MMC33A | Urban | LV Transformer SP2340-H MMC33A - Planned | 19.2 | 284 | 5452.8 | 0.0054548 | 1.9207e-05
2012-10-19 | 282190 | MMC33A | Urban | LV Transformer SP2865-G MMC33A - Planned | 18.72 | 410 | 7675.2 | 0.0076781 | 1.8727e-05
2012-10-19 | 282191 | HIS12A | Urban | LV Transformer SC1527-F HIS12A - Planned | 26.465 | 71 | 1879.015 | 0.0018797 | 2.6475e-05
2012-10-19 | 282192 | BHD35A | Rural short | LV Transformer SP5770-F BHD35A - Planned | 33.33 | 200 | 6666 | 0.019124 | 9.5619e-05
2012-10-19 | 282193 | CSE9 | Urban | LV Transformer SP2273-G CSE9 - Planned | 6.24 | 311 | 1940.64 | 0.0019414 | 6.2423e-06
2012-10-19 | 282194 | BRT3 | Urban | LV Transformer SP3095-H BRT3 - Planned | 20.02 | 135 | 2702.7 | 0.0027037 | 2.0027e-05
2012-10-19 | 282195 | BRT5 | Urban | LV Transformer SP37-L BRT5 - Planned | 12.42 | 237 | 2943.54 | 0.0029446 | 1.2425e-05
2012-10-19 | 282196 | HDA10A | Urban | LV Transformer SP2761-I HDA10A - Planned | 5.3 | 280 | 1484 | 0.0014846 | 5.302e-06
2012-10-19 | 282197 | NDH6 | Urban | LV Transformer SP741834 NDH6 - Planned | 8.515 | 270 | 2299.05 | 0.0022999 | 8.5182e-06
2012-10-19 | 282198 | DRD13A | Urban | LV Transformer SP3689-E DRD13A - Planned | 25.38 | 283 | 7182.54 | 0.0071852 | 2.5389e-05
2012-10-19 | 282199 | HPE12A | Urban | LV Transformer SP542-I HPE12A - Planned | 34.455 | 252 | 8682.66 | 0.0086859 | 3.4468e-05
2012-10-19 | 282200 | CVL17A | Urban | LV Transformer SP4839-F CVL17A - Planned | 4.98 | 136 | 677.28 | 0.00067753 | 4.9819e-06
2012-10-19 | 282201 | NMC2A | Rural short | LV Transformer SP4317-N NMC2A - Planned | 10.5825 | 272 | 2878.44 | 0.0082578 | 3.036e-05
2012-10-19 | 282202 | RCN3A | Urban | LV Transformer SC4800-J RCN3A - Planned | 9.9 | 300 | 2970 | 0.0029711 | 9.9037e-06
2012-10-19 | 282203 | BVL3A | Urban | LV Transformer SP3207-D BVL3A - Planned | 4.5268 | 240 | 1086.432 | 0.0010868 | 4.5285e-06
2012-10-19 | 282204 | IPS1B | Urban | LV Transformer SP1615-F IPS1B - Planned | 16.0995 | 261 | 4201.9695 | 0.0042035 | 1.6105e-05
2012-10-19 | 282205 | CSE9 | Urban | LV Transformer SP2196-J CSE9 - Planned | 1.9266 | 159 | 306.3294 | 0.00030644 | 1.9273e-06
2012-10-20 | 282214 | KRN12 | Urban | LV Transformer SP12552-E KRN12 - Planned | 38.025 | 233 | 8859.825 | 0.008862 | 3.8034e-05
2012-10-20 | 282215 | MCN3 | Urban | LV Transformer SP755395 MCN3 - Planned | 0.8 | 300 | 240 | 0.00024006 | 8.002e-07
2012-10-21 | 282233 | WSO3A | Urban | LV Transformer SP766017 WSO3A - Planned | 14.5 | 358 | 5191 | 0.0051919 | 1.4503e-05
2012-10-21 | 282234 | NSD1A | Urban | LV Transformer SC3669-J NSD1A - Planned | 34.59 | 347 | 12002.73 | 0.012005 | 3.4596e-05
2012-10-21 | 282235 | DRD16A | Urban | LV Transformer SP737737 DRD16A - Planned | 14.25 | 281 | 4004.25 | 0.004005 | 1.4253e-05
2012-10-21 | 282235 | DRD3A | Urban | LV Transformer SP737737 DRD16A - Planned | 2.05 | 281 | 576.05 | 0.00057615 | 2.0504e-06
2012-10-21 | 282236 | HDA10A | Urban | LV Transformer SP10781-E HDA10A - Planned | 4.34 | 242 | 1050.28 | 0.0010505 | 4.3408e-06
2012-10-21 | 282237 | UMG1B | Urban | LV Transformer SC5146-H UMG1B - Planned | 1.2134 | 149 | 180.7966 | 0.00018083 | 1.2136e-06
2012-10-21 | 282239 | RBK9A | Urban | LV Transformer SC811241 RBK9A - Planned | 23.04 | 460 | 10598.4 | 0.0106 | 2.3044e-05
2012-10-21 | 282240 | TBV4 | Rural short | Feeder TBV4 - Planned | 80.435 | 473 | 38045.755 | 0.10919 | 0.00023084
2012-10-21 | 282244 | SPO47A | Urban | LV Transformer SP6432-E SPO47A - Planned | 11.183 | 338 | 3779.854 | 0.0037805 | 1.1185e-05
2012-10-21 | 282338 | AHD21 | Urban | LV Transformer SP13576-A AHD21 - Planned | 17.16 | 395 | 6778.2 | 0.0067794 | 1.7163e-05
2012-10-21 | 282341 | BHD32B | Urban | LV Transformer SG165-L BHD32B - Planned | 82.7808 | 398 | 32946.7584 | 0.032953 | 8.2796e-05
2012-10-22 | 282300 | PRG2A | Rural short | Feeder PRG2A - Planned | 40.36 | 83 | 3349.88 | 0.009617 | 0.00011587
2012-10-22 | 282323 | SIS2 | Rural short | Feeder SIS2 - Planned | 20.01 | 198 | 3961.98 | 0.011374 | 5.7446e-05
2012-10-22 | 282324 | BRD5A | Rural short | LV Transformer SP13733-C BRD5A - Planned | 18.05 | 335 | 6046.75 | 0.017359 | 5.1819e-05
2012-10-22 | 282325 | MTB2A | Rural short | LV Transformer SP7197-F MTB2A - Planned | 2.01 | 332 | 667.32 | 0.0019158 | 5.7704e-06
2012-10-22 | 282326 | NRG9 | Rural short | Feeder NRG9 - Planned | 28.9075 | 335 | 9684.0125 | 0.027801 | 8.2989e-05
2012-10-22 | 282335 | MLT2B | Urban | LV Transformer SP758047 MLT2B - Planned | 26.5194 | 251 | 6656.3694 | 0.0066564 | 2.6519e-05
2012-10-22 | 282336 | KRN18A | Urban | LV Transformer SC799525 KRN18A - Planned | 13.567 | 307 | 4165.069 | 0.0041651 | 1.3567e-05
2012-10-22 | 282337 | INA3A | Urban | LV Transformer SG1205-N INA3A - Planned | 1.17 | 70 | 81.9 | 8.19e-05 | 1.17e-06
2012-10-22 | 282339 | CMD5A | Urban | LV Transformer SP53940-A CMD5A - Planned | 1.96 | 326 | 638.96 | 0.00063896 | 1.96e-06
2012-10-22 | 282340 | YDA5A | Rural short | LV Transformer SP7420-A YDA5A - Planned | 5.9381 | 145 | 861.0245 | 0.0024719 | 1.7047e-05
2012-10-22 | 282342 | CRBTHP26 | Urban | LV Transformer SP4207-G CRBTHP26 - Planned | 5.2085 | 282 | 1468.797 | 0.0014688 | 5.2085e-06
2012-10-22 | 282343 | NDH6 | Urban | LV Transformer SP1936-I NDH6 - Planned | 4.8835 | 148 | 722.758 | 0.00072276 | 4.8835e-06
2012-10-22 | 282344 | DRD13A | Urban | LV Transformer SP5770-D DRD13A - Planned | 9.945 | 55 | 546.975 | 0.00054698 | 9.945e-06
2012-10-22 | 282345 | SGT24A | Urban | LV Transformer SP3192-I SGT24A - Planned | 16.25 | 70 | 1137.5 | 0.0011375 | 1.625e-05
2012-10-22 | 282346 | MCW11 | Rural short | LV Transformer SP8232-D MCW11 - Planned | 9.92 | 95 | 942.4 | 0.0027055 | 2.8479e-05
2012-10-23 | 282385 | BDT1 | Rural short | LV Transformer SP7235-G BDT1 - Planned | 4 | 85 | 340 | 0.00097631 | 1.1486e-05
2012-10-23 | 282386 | BDT5 | Rural short | LV Transformer SP15333-C BDT5 - Planned | 2.01 | 105 | 211.05 | 0.00060603 | 5.7717e-06
2012-10-23 | 282404 | KBN5A | Rural short | Feeder KBN5A - Planned | 36 | 286 | 10296 | 0.029565 | 0.00010337
2012-10-23 | 282420 | TGW3 | Rural short | LV Transformer SP12951-A TGW3 - Planned | 1 | 373 | 373 | 0.0010711 | 2.8715e-06
2012-10-23 | 282421 | CBW6 | Rural short | LV Transformer SP4132-G CBW6 - Planned | 3 | 120 | 360 | 0.0010337 | 8.6145e-06
2012-10-23 | 282422 | MFD5A | Rural short | LV Transformer SP13450-C MFD5A - Planned | 37.5 | 350 | 13125 | 0.037688 | 0.00010768
2012-10-23 | 282423 | CBW11 | Rural short | LV Transformer SP5711-D CBW11 - Planned | 1 | 345 | 345 | 0.00099067 | 2.8715e-06
2012-10-23 | 282424 | MLY6 | Rural short | LV Transformer SP15737-A MLY6 - Planned | 13 | 242 | 3146 | 0.0090338 | 3.733e-05
2012-10-23 | 282425 | MLY1 | Rural short | LV Transformer SP2512-D MLY1 - Planned | 12.04 | 139 | 1673.56 | 0.0048056 | 3.4573e-05
2012-10-23 | 282426 | CBW13 | Rural short | LV Transformer SP1582-G CBW13 - Planned | 5.5 | 229 | 1259.5 | 0.0036167 | 1.5793e-05
2012-10-23 | 282427 | GYM8A | Rural short | LV Transformer SP9265-B GYM8A - Planned | 15.98 | 179 | 2860.42 | 0.0082137 | 4.5887e-05
2012-10-23 | 282428 | GYM7A | Rural short | LV Transformer SP6544-D GYM7A - Planned | 4.98 | 157 | 781.86 | 0.0022451 | 1.43e-05
2012-10-23 | 282429 | CNB24A | Rural short | LV Transformer SP2656-E CNB24A - Planned | 17.355 | 420 | 7289.1 | 0.020931 | 4.9835e-05
2012-10-23 | 282430 | GGR4 | Rural short | Feeder GGR4 - Planned | 5.69 | 335 | 1906.15 | 0.0054735 | 1.6339e-05
2012-10-23 | 282432 | MFN15A | Rural short | Feeder MFN15A, NGI3A - Planned | 8 | 240 | 1920 | 0.0055133 | 2.2972e-05
2012-10-23 | 282432 | NGI3A | Rural short | Feeder MFN15A, NGI3A - Planned | 9 | 240 | 2160 | 0.0062025 | 2.5844e-05
2012-10-23 | 282433 | MLY6 | Rural short | LV Transformer SP5340-A MLY6 - Planned | 17 | 417 | 7089 | 0.020356 | 4.8816e-05
2012-10-23 | 282434 | RWD2 | Rural short | Feeder RWD2 - Planned | 46 | 443 | 20378 | 0.058516 | 0.00013209
2012-10-23 | 282435 | EZRRWD4 | Rural short | Feeder EZRRWD4 - Planned | 2 | 455 | 910 | 0.0026131 | 5.743e-06
2012-10-23 | 282436 | MCN3 | Urban | Feeder MCN3 - Planned | 2.745 | 554 | 1520.73 | 0.0015205 | 2.7447e-06
2012-10-23 | 282437 | MGP13A | Rural short | Feeder MGP13A - Planned | 252.49 | 387 | 97713.63 | 0.28059 | 0.00072503
2012-10-23 | 282438 | NBR4 | Rural short | LV Transformer SP4350-A NBR4 - Planned | 5.04 | 365 | 1839.6 | 0.0052824 | 1.4472e-05
2012-10-23 | 282439 | MGL5 | Urban | LV Transformer SC6821-I MGL5 - Planned | 1.24 | 294 | 364.56 | 0.00036451 | 1.2398e-06
2012-10-23 | 282440 | PGN1B | Rural short | LV Transformer SP1566-A PGN1B - Planned | 50 | 315 | 15750 | 0.045226 | 0.00014358
2012-10-23 | 282441 | TRG2A | Urban | LV Transformer SP3749-I TRG2A - Planned | 31.1833 | 225 | 7016.2425 | 0.0070154 | 3.1179e-05
2012-10-23 | 282442 | CMA8A | Rural short | LV Transformer SC1428342 CMA8A - Planned | 9.6 | 175 | 1680 | 0.0048241 | 2.7566e-05
2012-10-23 | 282443 | NMK17A | Urban | LV Transformer SP3303-L NMK17A - Planned | 34.1994 | 384 | 13132.5696 | 0.013131 | 3.4195e-05
2012-10-23 | 282444 | LDR8 | Urban | LV Transformer SP1122-K LDR8 - Planned | 66.664 | 448 | 29865.472 | 0.029862 | 6.6656e-05
2012-10-23 | 282445 | NMK26 | Urban | LV Transformer SP1734900 NMK26 - Planned | 1.39 | 212 | 294.68 | 0.00029464 | 1.3898e-06
2012-10-23 | 282445 | VPK19A | Urban | LV Transformer SP1734900 NMK26 - Planned | 1.08 | 212 | 228.96 | 0.00022893 | 1.0799e-06
2012-10-23 | 282446 | INA10A | Urban | LV Transformer SC2764-K INA10A - Planned | 145.25 | 212 | 59311 | 0.059304 | 0.00014523
2012-10-23 | 282447 | MMC33A | Urban | LV Transformer SP2865-G MMC33A - Planned | 19.76 | 346 | 6836.96 | 0.0068361 | 1.9758e-05
2012-10-23 | 282448 | CMD13A | Urban | LV Transformer SP3807-A CMD13A - Planned | 11.36 | 141 | 1601.76 | 0.0016016 | 1.1359e-05
2012-10-23 | 282449 | MGP13A | Rural short | LV Transformer SP1710-I MGP13A - Planned | 1.92 | 240 | 460.8 | 0.0013232 | 5.5133e-06
2012-10-23 | 282450 | TCB1 | Rural short | LV Transformer SP6221-B TCB1 - Planned | 3.01 | 210 | 632.1 | 0.0018151 | 8.6432e-06
2012-10-23 | 282451 | CLD20A | Rural short | LV Transformer SP5369-A CLD20A - Planned | 37.8 | 294 | 11113.2 | 0.031912 | 0.00010854
2012-10-23 | 282452 | WNM3 | Urban | LV Transformer SP2168-K WNM3 - Planned | 27.72 | 244 | 6763.68 | 0.0067628 | 2.7717e-05
2012-10-23 | 282453 | BRT8 | Urban | LV Transformer SP1186-J BRT8 - Planned | 11.43 | 177 | 2023.11 | 0.0020229 | 1.1429e-05
2012-10-23 | 282454 | SMF6A | Rural short | LV Transformer SP2209-M SMF6A - Planned | 8.05 | 335 | 2696.75 | 0.0077437 | 2.3116e-05
2012-10-23 | 282455 | BRT5 | Urban | LV Transformer SP3916-D BRT5 - Planned | 17 | 178 | 3026 | 0.0030256 | 1.6998e-05
2012-10-23 | 282456 | BHL4A | Urban | LV Transformer SP635-I BHL4A - Planned | 11.27 | 69 | 777.63 | 0.00077753 | 1.1269e-05
2012-10-23 | 282457 | WRG6A | Urban | LV Transformer SP3148-J WRG6A - Planned | 5.6 | 275 | 1540 | 0.0015398 | 5.5993e-06
2012-10-23 | 282458 | CNB24A | Rural short | LV Transformer SP4859-E CNB24A - Planned | 2.1 | 517 | 1085.7 | 0.0031176 | 6.0302e-06
2012-10-23 | 282459 | HPE5A | Urban | LV Transformer SP2052035 HPE5A - Planned | 1.125 | 223 | 501.75 | 0.00050169 | 1.1249e-06
2012-10-23 | 282460 | WED20A | Urban | LV Transformer SP2466-K WED20A - Planned | 25.845 | 255 | 6590.475 | 0.0065897 | 2.5842e-05
2012-10-24 | 282507 | WSE3A | Rural short | LV Transformer SP6141-D WSE3A - Planned | 1 | 24 | 24 | 6.8932e-05 | 2.8721e-06
2012-10-24 | 282508 | BDB37A | Rural short | LV Transformer SP739741-A BDB37A - Planned | 19 | 98 | 1862 | 0.0053479 | 5.4571e-05
2012-10-24 | 282522 | TGW2 | Rural short | Feeder TGW2 - Planned | 4 | 298 | 1192 | 0.0034236 | 1.1489e-05
2012-10-24 | 282524 | TRP1 | Rural short | LV Transformer SP1042-S TRP1 - Planned | 11.96 | 355 | 4245.8 | 0.012195 | 3.4351e-05
2012-10-24 | 282527 | IPL1 | Rural short | Feeder IPL1 - Planned | 15 | 261 | 3915 | 0.011244 | 4.3082e-05
2012-10-24 | 282530 | KBR5A | Rural short | Feeder KBR5A - Planned | 8 | 428 | 3424 | 0.0098342 | 2.2977e-05
2012-10-24 | 282531 | BWH8A | Rural short | Feeder BWH8A - Planned | 39.097 | 529 | 20682.313 | 0.059403 | 0.00011229
2012-10-24 | 282532 | GYN3A | Rural short | Feeder GYN3A - Planned | 32.34 | 480 | 15523.2 | 0.044585 | 9.2885e-05
2012-10-24 | 282533 | NBR4 | Rural short | LV Transformer SP4351-A NBR4 - Planned | 17.5 | 323 | 5652.5 | 0.016235 | 5.0263e-05
2012-10-24 | 282534 | AMR2 | Rural short | Feeder AMR2 - Planned | 54.69 | 239 | 13070.91 | 0.037542 | 0.00015708
2012-10-24 | 282535 | CBW11 | Rural short | Feeder CBW11 - Planned | 8.05 | 256 | 2060.8 | 0.0059189 | 2.3121e-05
2012-10-24 | 282537 | NMK17A | Urban | LV Transformer SP758160 NMK17A - Planned | 14.9592 | 352 | 5265.6384 | 0.0052643 | 1.4955e-05
2012-10-24 | 282538 | NMK26 | Urban | LV Transformer SP952-M NMK26 - Planned | 23.23 | 279 | 6481.17 | 0.0064796 | 2.3224e-05
2012-10-24 | 282539 | NMK17A | Urban | LV Transformer SP1884-O NMK17A - Planned | 7.2955 | 380 | 2772.29 | 0.0027716 | 7.2937e-06
2012-10-24 | 282540 | ENG8 | Urban | LV Transformer SP521841 ENG8 - Planned | 6.15 | 286 | 1758.9 | 0.0017585 | 6.1485e-06
2012-10-24 | 282541 | GYM9A | Rural short | LV Transformer SC824724 GYM9A - Planned | 1 | 285 | 285 | 0.00081856 | 2.8721e-06
2012-10-24 | 282542 | GYN3A | Rural short | LV Transformer SP1151-D GYN3A - Planned | 3.06 | 499 | 1526.94 | 0.0043856 | 8.7888e-06
2012-10-24 | 282543 | NGI2B | Rural short | LV Transformer SC1387669 NGI2B - Planned | 57 | 320 | 18240 | 0.052388 | 0.00016371
2012-10-24 | 282544 | WMD14A | Rural short | LV Transformer SP144704 WMD14A - Planned | 23.9841 | 110 | 2638.251 | 0.0075775 | 6.8886e-05
2012-10-24 | 282545 | BHD23A | Rural short | LV Transformer SC1435630 BHD23A - Planned | 2 | 50 | 100 | 0.00028721 | 5.7443e-06
2012-10-24 | 282546 | BHD23A | Rural short | LV Transformer SP5758-E BHD23A - Planned | 17 | 115 | 1955 | 0.0056151 | 4.8827e-05
2012-10-24 | 282547 | HIS5A | Urban | LV Transformer SC513-H HIS5A - Planned | 29.26 | 120 | 3511.2 | 0.0035103 | 2.9253e-05
2012-10-24 | 282548 | SPO5A | Urban | LV Transformer SP3850-D SPO5A - Planned | 12.638 | 387 | 4890.906 | 0.0048897 | 1.2635e-05
2012-10-24 | 282550 | LDR3 | Urban | LV Transformer SP10515-D LDR3 - Planned | 97.92 | 278 | 27221.76 | 0.027215 | 9.7896e-05
2012-10-24 | 282551 | CRB25A | Rural short | LV Transformer SP5646-E CRB25A - Planned | 2.145 | 150 | 321.75 | 0.00092411 | 6.1608e-06
2012-10-24 | 282552 | MAI11 | Urban | LV Transformer SP14624-C MAI11 - Planned | 21.505 | 207 | 4451.535 | 0.0044504 | 2.15e-05
2012-10-24 | 282553 | CRB22A | Urban | LV Transformer SC1001-K CRB22A - Planned | 7.115 | 60 | 426.9 | 0.00042679 | 7.1132e-06
2012-10-24 | 282554 | DRD13A | Urban | LV Transformer SP5770-D DRD13A - Planned | 9.36 | 105 | 982.8 | 0.00098256 | 9.3577e-06
2012-10-24 | 282555 | SGT7 | Urban | LV Transformer SP1432-K SGT7 - Planned | 16.13 | 382 | 6161.66 | 0.0061601 | 1.6126e-05
2012-10-24 | 282556 | LTA3 | Urban | LV Transformer SP1682-K LTA5 - Planned | 1.785 | 167 | 298.095 | 0.00029802 | 1.7846e-06
2012-10-24 | 282556 | LTA5 | Urban | LV Transformer SP1682-K LTA5 - Planned | 1.56 | 167 | 260.52 | 0.00026046 | 1.5596e-06
2012-10-24 | 282556 | WNM1A | Urban | LV Transformer SP1682-K LTA5 - Planned | 7.81 | 167 | 1304.27 | 0.0013039 | 7.8081e-06
2012-10-24 | 282557 | DRD16A | Urban | LV Transformer SP4718-G DRD3A - Planned | 1.25 | 313 | 391.25 | 0.00039115 | 1.2497e-06
2012-10-24 | 282557 | DRD3A | Urban | LV Transformer SP4718-G DRD3A - Planned | 34.01 | 313 | 10645.13 | 0.010642 | 3.4002e-05
2012-10-24 | 282558 | WRG6A | Urban | LV Transformer SP3148-J WRG6A - Planned | 14.56 | 188 | 2737.28 | 0.0027366 | 1.4556e-05
2012-10-24 | 282559 | NMC3A | Rural short | LV Transformer SP6946-I NMC3A - Planned | 5.98 | 205 | 1225.9 | 0.003521 | 1.7175e-05
2012-10-24 | 282560 | QPT22A | Urban | LV Transformer SP21918-E QPT22A - Planned | 35.6362 | 400 | 14254.48 | 0.014251 | 3.5627e-05
2012-10-24 | 282561 | RCN3A | Urban | LV Transformer SC4800-J RCN3A - Planned | 5.94 | 200 | 1188 | 0.0011877 | 5.9385e-06
2012-10-24 | 282562 | CPB9 | Urban | LV Transformer SP3547-C CPB9 - Planned | 10.7 | 324 | 3466.8 | 0.0034659 | 1.0697e-05
2012-10-24 | 282563 | CPR5 | Urban | LV Transformer SG740-K CPR5 - Planned | 16.645 | 406 | 6757.87 | 0.0067562 | 1.6641e-05
2012-10-24 | 282564 | AGE3 | Urban | LV Transformer SP1600-M AGE3 - Planned | 5.58 | 11 | 61.38 | 6.1365e-05 | 5.5786e-06
2012-10-24 | 282565 | BVL13A | Urban | LV Transformer SP1785-G BVL13A - Planned | 26.04 | 114 | 2968.56 | 0.0029678 | 2.6034e-05
2012-10-25 | 282600 | MTB15A | Rural short | Feeder MTB15A - Planned | 40.45 | 131 | 5298.95 | 0.015223 | 0.00011621
2012-10-25 | 282603 | LRE7A | Rural short | Feeder LRE7A - Planned | 8.98 | 252 | 2262.96 | 0.0065011 | 2.5798e-05
2012-10-25 | 282604 | TGW2 | Rural short | LV Transformer SP8279-A TGW2 - Planned | 1 | 166 | 166 | 0.00047689 | 2.8728e-06
2012-10-25 | 282605 | BNH6A | Rural short | LV Transformer SP4364-E BNH6A - Planned | 2.01 | 227 | 456.27 | 0.0013108 | 5.7744e-06
2012-10-25 | 282606 | TRP3 | Rural short | LV Transformer SP2649-D TRP3 - Planned | 2.01 | 283 | 568.83 | 0.0016342 | 5.7744e-06
2012-10-25 | 282607 | UPC1 | Rural short | LV Transformer SP15921-D UPC1 - Planned | 0.4 | 338 | 135.2 | 0.00038841 | 1.1491e-06
2012-10-25 | 282608 | TRP1 | Rural short | LV Transformer SP2337-C TRP1 - Planned | 7 | 329 | 2303 | 0.0066161 | 2.011e-05
2012-10-25 | 282609 | TGW2 | Rural short | LV Transformer SP10911-A TGW2 - Planned | 1 | 100 | 100 | 0.00028728 | 2.8728e-06
2012-10-25 | 282610 | BMT1 | Rural short | LV Transformer SP7490-C BMT1 - Planned | 36 | 275 | 9900 | 0.028441 | 0.00010342
2012-10-25 | 282611 | GYGGYS6 | Rural short | LV Transformer SP6204-B GYGGYS6 - Planned | 6 | 233 | 1398 | 0.0040162 | 1.7237e-05
2012-10-25 | 282612 | MLY3 | Rural short | LV Transformer SP3797-A MLY3 - Planned | 11 | 195 | 2145 | 0.0061622 | 3.1601e-05
2012-10-25 | 282613 | KWH2 | Rural short | LV Transformer SP3356-A KWH2 - Planned | 6 | 76 | 456 | 0.00131 | 1.7237e-05
2012-10-25 | 282614 | BDT1 | Rural short | Feeder BDT1 - Planned | 11 | 400 | 4400 | 0.01264 | 3.1601e-05
2012-10-25 | 282615 | LBH1B | Rural short | Feeder LBH1B - Planned | 65.9072 | 479 | 31569.5488 | 0.090694 | 0.00018934
2012-10-25 | 282616 | GBN4 | Rural short | Feeder GBN4 - Planned | 208.1651 | 353 | 73482.2803 | 0.2111 | 0.00059802
2012-10-25 | 282617 | MCN3 | Urban | LV Transformer SP2954-C MCN3 - Planned | 3.5 | 382 | 1337 | 0.0013365 | 3.4987e-06
2012-10-25 | 282618 | MAI7 | Urban | LV Transformer SP656824 MAI7 - Planned | 18 | 465 | 8370 | 0.0083668 | 1.7993e-05
2012-10-25 | 282619 | SMF5A | Rural short | LV Transformer SP3285-H SMF5A - Planned | 1.075 | 308 | 331.1 | 0.0009512 | 3.0883e-06
2012-10-25 | 282620 | NMK17A | Urban | LV Transformer SP1884-O NMK17A - Planned | 29.4147 | 345 | 10148.0715 | 0.010144 | 2.9404e-05
2012-10-25 | 282621 | SFD3 | Urban | LV Transformer SC4054-K SFD3 - Planned | 4.2 | 265 | 1113 | 0.0011126 | 4.1984e-06
2012-10-25 | 282622 | TRG2A | Urban | LV Transformer SP3749-I TRG2A - Planned | 44.974 | 453 | 20373.222 | 0.020365 | 4.4957e-05
2012-10-25 | 282623 | WMD11A | Rural short | LV Transformer SG2097-A WMD11A - Planned | 50.16 | 42 | 2106.72 | 0.0060523 | 0.0001441
2012-10-25 | 282624 | BHD7A | Urban | LV Transformer SC1438-I BHD7A - Planned | 7.875 | 26 | 204.75 | 0.00020467 | 7.872e-06
2012-10-25 | 282625 | CRB24B | Urban | LV Transformer SP764699 CRB24B - Planned | 28.305 | 492 | 13926.06 | 0.013921 | 2.8294e-05
2012-10-25 | 282626 | DRD16A | Urban | LV Transformer SP5896-B DRD16A - Planned | 6.9 | 298 | 2056.2 | 0.0020554 | 6.8974e-06
2012-10-25 | 282626 | DRD3A | Urban | LV Transformer SP5896-B DRD16A - Planned | 34.01 | 298 | 10134.98 | 0.010131 | 3.3997e-05
2012-10-25 | 282627 | HDA3A | Urban | LV Transformer SP1853-I HDA3A - Planned | 22.68 | 246 | 5579.28 | 0.0055772 | 2.2671e-05
2012-10-25 | 282628 | NDH7 | Urban | LV Transformer SP1434-L NDH7 - Planned | 66.04 | 225 | 14859 | 0.014853 | 6.6015e-05
2012-10-25 | 282629 | HPE3A | Urban | LV Transformer SP64816-D HPE3A - Planned | 34.0429 | 232 | 7897.9528 | 0.007895 | 3.403e-05
2012-10-25 | 282630 | ALY5 | Urban | LV Transformer SP4170-I ALY5 - Planned | 38.93 | 326 | 12691.18 | 0.012686 | 3.8915e-05
2012-10-25 | 282631 | CNB24A | Rural short | LV Transformer SP4859-E CNB24A - Planned | 2.1 | 360 | 756 | 0.0021719 | 6.033e-06
2012-10-25 | 282632 | PDB13 | Urban | LV Transformer SC2055782 PDB13 - Planned | 8.88 | 275 | 2442 | 0.0024411 | 8.8766e-06
2012-10-25 | 282633 | BDB27A | Rural short | LV Transformer SP3159-C BDB27A - Planned | 13.53 | 268 | 3626.04 | 0.010417 | 3.8869e-05
2012-10-25 | 282634 | NIP1A | Urban | LV Transformer SP1606-D NIP1A - Planned | 10.855 | 168 | 1823.64 | 0.0018229 | 1.0851e-05
2012-10-26 | 282640 | AHD6 | Urban | LV Transformer SP47083-A AHD6 - Planned | 12.83 | 130 | 1667.9 | 0.001667 | 1.2823e-05
2012-10-26 | 282662 | KBN15A | Urban | Feeder KBN15A - Planned | 24.84 | 235 | 5837.4 | 0.0058344 | 2.4827e-05
2012-10-26 | 282680 | GYN3A | Rural short | Feeder GYN3A - Planned | 32.34 | 487 | 15749.58 | 0.045257 | 9.293e-05
2012-10-26 | 282681 | CLD28A | Rural short | Feeder CLD28A - Planned | 29.475 | 440 | 12969 | 0.037267 | 8.4697e-05
2012-10-26 | 282682 | WMR1 | Rural short | LV Transformer SP1379500 WMR1 - Planned | 1 | 333 | 333 | 0.00095688 | 2.8735e-06
2012-10-26 | 282683 | NBR8 | Rural short | LV Transformer SP5169-A NBR8 - Planned | 51.36 | 331 | 17000.16 | 0.04885 | 0.00014758
2012-10-26 | 282684 | BMT3 | Rural short | LV Transformer SP4221-B BMT3 - Planned | 3 | 124 | 372 | 0.001069 | 8.6206e-06
2012-10-26 | 282685 | CBW11 | Rural short | LV Transformer SP3124-H CBW11 - Planned | 1 | 257 | 257 | 0.0007385 | 2.8735e-06
2012-10-26 | 282686 | TWT11A | Rural short | LV Transformer SC1394453 TWT11A - Planned | 31 | 162 | 5022 | 0.014431 | 8.9079e-05
2012-10-26 | 282687 | KWH2 | Rural short | LV Transformer SP1114-D KWH2 - Planned | 3 | 143 | 429 | 0.0012327 | 8.6206e-06
2012-10-26 | 282689 | HPK3A | Urban | LV Transformer SP3319-G HPK3A - Planned | 2.4 | 265 | 636 | 0.00063568 | 2.3988e-06
2012-10-26 | 282691 | WNM5 | Urban | LV Transformer SP2143-K WNM5 - Planned | 2.07 | 119 | 246.33 | 0.0002462 | 2.0689e-06
2012-10-26 | 282692 | GAP8A | Urban | LV Transformer SP3703-J GAP8A - Planned | 2.15 | 48 | 103.2 | 0.00010315 | 2.1489e-06
2012-10-26 | 282693 | OXL4A | Urban | LV Transformer SP941-M OXL4A - Planned | 0.96 | 198 | 190.08 | 0.00018998 | 9.5951e-07
2012-10-26 | 282694 | NMK26 | Urban | LV Transformer SP952-M NMK26 - Planned | 26.58 | 221 | 5874.18 | 0.0058712 | 2.6566e-05
2012-10-26 | 282695 | INA7A | Rural short | LV Transformer SP5119-H INA7A - Planned | 1 | 410 | 410 | 0.0011781 | 2.8735e-06
2012-10-26 | 282696 | CMD5A | Urban | LV Transformer SP16416-A CMD5A - Planned | 16.8 | 322 | 5409.6 | 0.0054068 | 1.6791e-05
2012-10-26 | 282697 | MMC33A | Urban | LV Transformer SP18527-D MMC33A - Planned | 19.74 | 385 | 7599.9 | 0.007596 | 1.973e-05
2012-10-26 | 282698 | MMC19B | Urban | LV Transformer SP3475-C MMC19B - Planned | 33.39 | 170 | 5676.3 | 0.0056734 | 3.3373e-05
2012-10-26 | 282699 | CRB25A | Rural short | LV Transformer SP796211 CRB25A - Planned | 14.3 | 81 | 1158.3 | 0.0033284 | 4.1091e-05
2012-10-26 | 282700 | BRT5 | Urban | LV Transformer SP1574-H BRT5 - Planned | 18.18 | 265 | 4817.7 | 0.0048152 | 1.8171e-05
2012-10-26 | 282701 | DRD13A | Urban | LV Transformer SP5093-E DRD13A - Planned | 10.16 | 78 | 792.48 | 0.00079208 | 1.0155e-05
2012-10-26 | 282702 | SGT7 | Urban | LV Transformer SP1432-K SGT7 - Planned | 16.13 | 241 | 3887.33 | 0.0038853 | 1.6122e-05
2012-10-26 | 282703 | WRD11A | Urban | LV Transformer SP118-N WRD15A - Planned | 1.41 | 223 | 314.43 | 0.00031427 | 1.4093e-06
2012-10-26 | 282703 | WRD15A | Urban | LV Transformer SP118-N WRD15A - Planned | 22.575 | 223 | 5034.225 | 0.0050317 | 2.2563e-05
2012-10-27 | 282728 | KBR2A | Rural short | LV Transformer SP4157-C KBR2A - Planned | 6.09 | 170 | 1035.3 | 0.0029757 | 1.7504e-05
2012-10-28 | 282747 | NRG6 | Urban | LV Transformer SP10207-E NRG6 - Planned | 3.1875 | 201 | 640.6875 | 0.00064022 | 3.1852e-06
2012-10-28 | 282748 | NDH6 | Urban | LV Transformer SC765161 NDH6 - Planned | 48.855 | 308 | 15047.34 | 0.015036 | 4.8819e-05
2012-10-28 | 282749 | HPK2 | Urban | LV Transformer SG2298-H HPK2 - Planned | 1.075 | 60 | 64.5 | 6.4453e-05 | 1.0742e-06
2012-10-28 | 282750 | RST16A | Urban | LV Transformer SP8542-B RST16A - Planned | 16.38 | 82 | 1343.16 | 0.0013422 | 1.6368e-05
2012-10-28 | 282751 | RST16A | Urban | LV Transformer SP8542-B RST16A - Planned | 2.73 | 23 | 62.79 | 6.2744e-05 | 2.728e-06
2012-10-28 | 282752 | RST5A | Urban | LV Transformer SP565-G RST5A - Planned | 27.405 | 355 | 9728.775 | 0.0097216 | 2.7385e-05
2012-10-28 | 284886 | BPN34A | Urban | LV Transformer SC807019 BPN34A - Planned | 0.96 | 319 | 306.24 | 0.00030601 | 9.5929e-07
2012-10-29 | 282781 | NMC1B | Rural short | LV Transformer SP4819-K NMC1B - Planned | 10 | 209 | 2090 | 0.0060099 | 2.8756e-05
2012-10-29 | 282783 | TGW1 | Rural short | LV Transformer SP3717-B TGW1 - Planned | 0.4 | 54 | 21.6 | 6.2112e-05 | 1.1502e-06
2012-10-29 | 282785 | BNH2B | Rural short | Feeder BNH2B - Planned | 12 | 272 | 3264 | 0.0093858 | 3.4507e-05
2012-10-29 | 282787 | TGW1 | Rural short | LV Transformer SP2437-B TGW1 - Planned | 1 | 180 | 180 | 0.0005176 | 2.8756e-06
2012-10-29 | 282788 | LLY1 | Rural short | Feeder LLY1 - Planned | 5 | 358 | 1790 | 0.0051473 | 1.4378e-05
2012-10-29 | 282791 | LBH1B | Rural short | Feeder LBH1B - Planned | 43.37 | 213 | 9237.81 | 0.026564 | 0.00012471
2012-10-29 | 282792 | GYN3A | Rural short | LV Transformer SP1722-C GYN3A - Planned | 4 | 248 | 992 | 0.0028526 | 1.1502e-05
2012-10-29 | 282793 | AMR1 | Rural short | LV Transformer SP2911-C AMR1 - Planned | 7.04 | 234 | 1647.36 | 0.0047371 | 2.0244e-05
2012-10-29 | 282794 | LBH6A | Rural short | LV Transformer SP4510-B LBH6A - Planned | 8.455 | 185 | 1564.175 | 0.0044979 | 2.4313e-05
2012-10-29 | 282796 | AGE10 | Urban | LV Transformer SP522276 AGE10 - Planned | 35.6833 | 222 | 7921.6926 | 0.0079146 | 3.5651e-05
2012-10-29 | 282797 | KRN10 | Urban | LV Transformer SP525-O KRN10 - Planned | 2.91 | 315 | 916.65 | 0.00091583 | 2.9074e-06
2012-10-29 | 282798 | SMR7A | Urban | LV Transformer SC2346-H SMR7A - Planned | 9.12 | 251 | 2289.12 | 0.0022871 | 9.1118e-06
2012-10-29 | 282799 | CLD2 | Urban | LV Transformer SC245-B CLD2 - Planned | 4.3 | 252 | 1083.6 | 0.0010826 | 4.2962e-06
2012-10-29 | 282800 | BLH10B | Urban | LV Transformer SP5433-C BLH10B - Planned | 5.0202 | 245 | 1229.949 | 0.0012288 | 5.0157e-06
2012-10-29 | 282801 | SPO41A | Urban | LV Transformer SP986-I SPO41A - Planned | 24.4206 | 389 | 9499.6134 | 0.0094911 | 2.4399e-05
2012-10-29 | 282802 | CRB25A | Rural short | LV Transformer SP5763-E CRB25A - Planned | 18.83 | 327 | 6157.41 | 0.017706 | 5.4147e-05
2012-10-29 | 282803 | NRA15A | Rural short | LV Transformer SP4135-E NRA15A - Planned | 11.1 | 448 | 4972.8 | 0.0143 | 3.1919e-05
2012-10-29 | 282804 | SGT5 | Urban | LV Transformer SP2684-G SGT5 - Planned | 6.7 | 84 | 562.8 | 0.0005623 | 6.694e-06
2012-10-29 | 282805 | WNM6 | Urban | LV Transformer SP6516-F WNM6 - Planned | 3.6 | 270 | 972 | 0.00097113 | 3.5968e-06
2012-10-29 | 282806 | ALY5 | Urban | LV Transformer SP4170-I ALY5 - Planned | 52.51 | 280 | 14702.8 | 0.01469 | 5.2463e-05
2012-10-29 | 282807 | RBY13 | Urban | LV Transformer SP808601 RBY13 - Planned | 28.9 | 267 | 7716.3 | 0.0077094 | 2.8874e-05
2012-10-29 | 282808 | NIP1A | Urban | LV Transformer SP1606-D NIP1A - Planned | 17.47 | 102 | 1781.94 | 0.0017803 | 1.7454e-05
2012-10-29 | 282809 | MCW11 | Rural short | LV Transformer SP5181-F MCW11 - Planned | 8.16 | 193 | 1574.88 | 0.0045287 | 2.3465e-05
2012-10-29 | 283037 | WNM6 | Urban | LV Transformer SC4406-J - Planned | 1.38 | 270 | 372.6 | 0.00037227 | 1.3788e-06
2012-10-30 | 282841 | GTN12A | Rural short | LV Transformer SP7978-C GTN12A - Planned | 60.27 | 17 | 1024.59 | 0.002947 | 0.00017335
2012-10-30 | 282842 | GTN12A | Rural short | LV Transformer SP3017-C GTN12A - Planned | 4.4 | 12 | 52.8 | 0.00015187 | 1.2655e-05
2012-10-30 | 282843 | GTN12A | Rural short | LV Transformer SP8143-B GTN12A - Planned | 1 | 11 | 11 | 3.1639e-05 | 2.8762e-06
2012-10-30 | 282846 | THL3 | Rural short | LV Transformer SP244483-A THL3 - Planned | 1 | 19 | 19 | 5.4649e-05 | 2.8762e-06
2012-10-30 | 282847 | GTN12A | Rural short | LV Transformer SP4679-A GTN12A - Planned | 1 | 15 | 15 | 4.3144e-05 | 2.8762e-06
2012-10-30 | 282849 | GTN12A | Rural short | LV Transformer SP16840-A GTN12A - Planned | 9 | 13 | 117 | 0.00033652 | 2.5886e-05
2012-10-30 | 282852 | GTN12A | Rural short | LV Transformer SP3458-B GTN12A - Planned | 4.4 | 84 | 369.6 | 0.0010631 | 1.2655e-05
2012-10-30 | 282853 | THL3 | Rural short | LV Transformer SP2085-D THL3 - Planned | 1 | 27 | 27 | 7.7659e-05 | 2.8762e-06
2012-10-30 | 282854 | THL3 | Rural short | LV Transformer SP16823-A THL3 - Planned | 0.536 | 9 | 4.824 | 1.3875e-05 | 1.5417e-06
2012-10-30 | 282855 | GTN12A | Rural short | LV Transformer SP8016-C GTN12A - Planned | 5.16 | 4 | 20.64 | 5.9366e-05 | 1.4841e-05
2012-10-30 | 282856 | GTN12A | Rural short | LV Transformer SP10472-A GTN12A - Planned | 13 | 13 | 169 | 0.00048609 | 3.7391e-05
2012-10-30 | 282857 | THL3 | Rural short | LV Transformer SP12669-A THL3 - Planned | 0.536 | 5 | 2.68 | 7.7083e-06 | 1.5417e-06
2012-10-30 | 282858 | GTN12A | Rural short | LV Transformer SP8017-C GTN12A - Planned | 4.264 | 5 | 21.32 | 6.1322e-05 | 1.2264e-05
2012-10-30 | 282859 | THL3 | Rural short | LV Transformer SP8096-B THL3 - Planned | 0.536 | 4 | 2.144 | 6.1667e-06 | 1.5417e-06
2012-10-30 | 282860 | GTN12A | Rural short | LV Transformer SP8371-A GTN12A - Planned | 15.98 | 12 | 191.76 | 0.00055155 | 4.5962e-05
2012-10-30 | 282862 | THL3 | Rural short | LV Transformer SP1339-C THL3 - Planned | 4 | 39 | 156 | 0.00044869 | 1.1505e-05
2012-10-30 | 282863 | KBN2A | Rural short | LV Transformer SP3574-C KBN2A - Planned | 13 | 203 | 2639 | 0.0075904 | 3.7391e-05
2012-10-30 | 282864 | THL3 | Rural short | LV Transformer SP3109-C THL3 - Planned | 2.01 | 9 | 18.09 | 5.2031e-05 | 5.7813e-06
2012-10-30 | 282866 | THL3 | Rural short | LV Transformer SP1853-B THL3 - Planned | 0.5 | 13 | 6.5 | 1.8696e-05 | 1.4381e-06
2012-10-30 | 282868 | MBG2 | Rural short | Feeder MBG2 - Planned | 5.9 | 134 | 790.6 | 0.002274 | 1.697e-05
2012-10-30 | 282869 | TGW4 | Rural short | LV Transformer SP8064-A TGW4 - Planned | 3 | 238 | 714 | 0.0020536 | 8.6287e-06
2012-10-30 | 282870 | THL3 | Rural short | LV Transformer SP5417-A THL3 - Planned | 2.01 | 19 | 38.19 | 0.00010984 | 5.7813e-06
2012-10-30 | 282883 | THL3 | Rural short | LV Transformer SP4621-B THL3 - Planned | 0.4 | 19 | 7.6 | 2.1859e-05 | 1.1505e-06
2012-10-30 | 282886 | JBB12B | Rural short | LV Transformer SP2967-C JBB12B - Planned | 5.395 | 357 | 1926.015 | 0.0055397 | 1.5517e-05
2012-10-30 | 282887 | THL3 | Rural short | LV Transformer SP1342-C THL3 - Planned | 3 | 8 | 24 | 6.903e-05 | 8.6287e-06
2012-10-30 | 282888 | TGW3 | Rural short | LV Transformer SP2604-C TGW3 - Planned | 2.01 | 269 | 540.69 | 0.0015552 | 5.7813e-06
2012-10-30 | 282889 | MCN3 | Urban | Feeder MCN3 - Planned | 0.4 | 485 | 194 | 0.0001938 | 3.9959e-07
2012-10-30 | 282901 | CNB24A | Rural short | LV Transformer SP3523-C CNB24A - Planned | 11.5 | 536 | 6164 | 0.017729 | 3.3077e-05
2012-10-30 | 282902 | SMF6A | Rural short | Feeder SMF6A - Planned | 124.94 | 594 | 74214.36 | 0.21346 | 0.00035936
2012-10-30 | 282903 | EMD3 | Rural short | LV Transformer SP3774-B EMD3 - Planned | 8.455 | 380 | 3212.9 | 0.0092411 | 2.4319e-05
2012-10-30 | 282904 | YDA3A | Rural short | Feeder YDA3A - Planned | 10 | 414 | 4140 | 0.011908 | 2.8762e-05
2012-10-30 | 282905 | LBH6A | Rural short | LV Transformer SP3020-A LBH6A - Planned | 29.5 | 118 | 3481 | 0.010012 | 8.4849e-05
2012-10-30 | 282906 | BWH16A | Rural short | LV Transformer SP17942-A BWH16A - Planned | 5 | 154 | 770 | 0.0022147 | 1.4381e-05
2012-10-30 | 282907 | SMF6A | Rural short | LV Transformer SP2209-M SMF6A - Planned | 17.21 | 575 | 9895.75 | 0.028463 | 4.95e-05
2012-10-30 | 282908 | KMR19A | Urban | LV Transformer SP2123-N KMR19A - Planned | 2.975 | 295 | 877.625 | 0.00087673 | 2.972e-06
2012-10-30 | 282908 | KMR21B | Urban | LV Transformer SP2123-N KMR19A - Planned | 6.88 | 295 | 2029.6 | 0.0020275 | 6.873e-06
2012-10-30 | 282909 | KMR21A | Urban | LV Transformer SC4346-K KMR21A - Planned | 4.345 | 565 | 2454.925 | 0.0024524 | 4.3406e-06
2012-10-30 | 282910 | NMK17A | Urban | LV Transformer SP758160 NMK17A - Planned | 36.6116 | 324 | 11862.1584 | 0.01185 | 3.6574e-05
2012-10-30 | 282911 | AGE9 | Urban | LV Transformer SP644-K AGE9 - Planned | 6.37 | 179 | 1140.23 | 0.0011391 | 6.3635e-06
2012-10-30 | 282912 | AGE5B | Urban | LV Transformer SP2604-L AGE5B - Planned | 2.38 | 242 | 575.96 | 0.00057537 | 2.3776e-06
2012-10-30 | 282913 | GAP9A | Urban | LV Transformer SP4331-M GAP9A - Planned | 25.2175 | 62 | 1563.485 | 0.0015619 | 2.5192e-05
2012-10-30 | 282914 | GBN2 | Rural short | LV Transformer SP1223-E GBN2 - Planned | 11.04 | 256 | 2826.24 | 0.008129 | 3.1754e-05
2012-10-30 | 282915 | MLY3 | Rural short | LV Transformer SP2833-B MLY4 - Planned | 14.32 | 383 | 5484.56 | 0.015775 | 4.1188e-05
2012-10-30 | 282915 | MLY4 | Rural short | LV Transformer SP2833-B MLY4 - Planned | 36.985 | 383 | 14165.255 | 0.040743 | 0.00010638
2012-10-30 | 282916 | PWC4 | Rural short | LV Transformer SP82458-A PWC4 - Planned | 2.5 | 160 | 400 | 0.0011505 | 7.1906e-06
2012-10-30 | 282917 | CMD5A | Urban | LV Transformer SP4473-B CMD5A - Planned | 7.44 | 50 | 372 | 0.00037162 | 7.4324e-06
2012-10-30 | 282918 | BHD35A | Rural short | LV Transformer SP472181 BHD35A - Planned | 9 | 216 | 1944 | 0.0055914 | 2.5886e-05
2012-10-30 | 282919 | BHD1A | Urban | LV Transformer SP1143-K BHD1A - Planned | 8.683 | 397 | 3447.151 | 0.0034436 | 8.6741e-06
2012-10-30 | 282920 | BBH10A | Urban | LV Transformer SP2683-E BBH10A - Planned | 16.79 | 264 | 4432.56 | 0.004428 | 1.6773e-05
2012-10-30 | 282921 | MMC33A | Urban | LV Transformer SP1227-J MMC33A - Planned | 19.25 | 435 | 8373.75 | 0.0083652 | 1.923e-05
2012-10-30 | 282922 | BHD23A | Rural short | LV Transformer SP5812-E BHD23A - Planned | 2.04 | 300 | 612 | 0.0017603 | 5.8675e-06
2012-10-30 | 282923 | SGT6 | Urban | LV Transformer SP5470-G SGT6 - Planned | 10.8 | 320 | 3456 | 0.0034525 | 1.0789e-05
2012-10-30 | 282924 | DRD16A | Urban | LV Transformer SP3723-D DRD16A - Planned | 20 | 243 | 4860 | 0.004855 | 1.998e-05
2012-10-30 | 282925 | SGT7 | Urban | LV Transformer SP1612-J SGT7 - Planned | 5.48 | 357 | 1956.36 | 0.0019544 | 5.4744e-06
2012-10-30 | 282926 | WSE3A | Rural short | LV Transformer SP238-H WSE3A - Planned | 7.04 | 352 | 2478.08 | 0.0071276 | 2.0249e-05
2012-10-30 | 282927 | WRG6A | Urban | LV Transformer SP4105-M WRG6A - Planned | 29.12 | 360 | 10483.2 | 0.010472 | 2.909e-05
2012-10-30 | 282928 | CNB24A | Rural short | LV Transformer SP4859-E CNB24A - Planned | 2.1 | 425 | 892.5 | 0.002567 | 6.0401e-06
2012-10-30 | 282929 | CPB9 | Urban | LV Transformer SP3547-C CPB9 - Planned | 33.015 | 336 | 11093.04 | 0.011082 | 3.2981e-05
2012-10-30 | 282930 | BVL2A | Urban | LV Transformer SP2106-G BVL2A - Planned | 11.41 | 327 | 3731.07 | 0.0037273 | 1.1398e-05
2012-10-30 | 282982 | GYN5A | Urban | LV Transformer SP13103-C GYN5A - Planned | 29.1 | 12 | 349.2 | 0.00034884 | 2.907e-05
2012-10-31 | 282980 | KWH3 | Rural short | LV Transformer SP2586-E KWH3 - Planned | 7 | 95 | 665 | 0.0019126 | 2.0133e-05
2012-10-31 | 282981 | PWC4 | Rural short | LV Transformer SP202466 PWC4 - Planned | 48 | 181 | 8688 | 0.024988 | 0.00013805
2012-10-31 | 282983 | WSE3A | Rural short | Feeder WSE3A - Planned | 12.755 | 280 | 3571.4 | 0.010272 | 3.6685e-05
2012-10-31 | 283000 | BNH1B | Rural short | LV Transformer SP115-H BNH1B - Planned | 6.02 | 376 | 2263.52 | 0.0065101 | 1.7314e-05
2012-10-31 | 283001 | BHD23A | Rural short | LV Transformer SP3693-D BHD23A - Planned | 0.4 | 295 | 118 | 0.00033938 | 1.1504e-06
2012-10-31 | 283020 | IPL2 | Rural short | Feeder IPL2 - Planned | 7.5 | 335 | 2512.5 | 0.0072262 | 2.1571e-05
2012-10-31 | 283022 | NBR4 | Rural short | Feeder NBR4 - Planned | 10 | 427 | 4270 | 0.012281 | 2.8761e-05
2012-10-31 | 283023 | PGN1B | Rural short | Feeder PGN1B - Planned | 28.04 | 205 | 5748.2 | 0.016532 | 8.0646e-05
2012-10-31 | 283024 | 341 | Urban | Feeder 341 - Planned | 29.01 | 397 | 11516.97 | 0.011505 | 2.8979e-05
2012-10-31 | 283025 | CMA8A | Rural short | LV Transformer SC1502950 CMA8A - Planned | 20.3 | 305 | 6191.5 | 0.017807 | 5.8385e-05
2012-10-31 | 283026 | AGE5B | Urban | LV Transformer SP3446-J AGE5B - Planned | 1.77 | 104 | 184.08 | 0.00018389 | 1.7681e-06
2012-10-31 | 283027 | DRA6 | Urban | LV Transformer SP284-Q DRA6 - Planned | 2.98 | 60 | 178.8 | 0.00017861 | 2.9769e-06
2012-10-31 | 283028 | AGE7B | Urban | LV Transformer SP1420-P AGE7B - Planned | 8 | 285 | 2280 | 0.0022776 | 7.9916e-06
2012-10-31 | 283029 | LBH1B | Rural short | LV Transformer SP6676-A LBH1B - Planned | 25.74 | 440 | 11325.6 | 0.032574 | 7.4031e-05
2012-10-31 | 283030 | MMC33A | Urban | LV Transformer SP1227-J MMC33A - Planned | 18.75 | 416 | 7800 | 0.0077918 | 1.873e-05
2012-10-31 | 283031 | SPO5A | Urban | LV Transformer SP3850-D SPO5A - Planned | 1.17 | 243 | 284.31 | 0.00028401 | 1.1688e-06
2012-10-31 | 283032 | BHD33A | Urban | LV Transformer SC1020-J BHD33A - Planned | 91.89 | 295 | 27107.55 | 0.027079 | 9.1793e-05
2012-10-31 | 283033 | CRB25A | Rural short | LV Transformer SP796211 CRB25A - Planned | 13.2 | 250 | 3300 | 0.0094912 | 3.7965e-05
2012-10-31 | 283035 | NRA5A | Rural short | LV Transformer SP1380-G NRA5A - Planned | 6.9 | 366 | 2525.4 | 0.0072633 | 1.9845e-05
2012-10-31 | 283036 | CSE7 | Urban | LV Transformer SP13528-F NDH6 - Planned | 7.8 | 361 | 2815.8 | 0.0028128 | 7.7918e-06
2012-10-31 | 283036 | NDH6 | Urban | LV Transformer SP13528-F NDH6 - Planned | 34.6881 | 361 | 12522.4041 | 0.012509 | 3.4652e-05
2012-10-31 | 283038 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 98.298 | 326 | 32045.148 | 0.032011 | 9.8194e-05
2012-10-31 | 283039 | CPB4 | Urban | LV Transformer SP4973-D CPB4 - Planned | 7.36 | 333 | 2450.88 | 0.0024483 | 7.3522e-06
2012-10-31 | 283040 | ARG9A | Urban | LV Transformer SP3318-M ARG9A - Planned | 7.245 | 310 | 2245.95 | 0.0022436 | 7.2374e-06
2012-10-31 | 283041 | TGW1 | Rural short | LV Transformer SP5080-A TGW1 - Planned | 9 | 219 | 1971 | 0.0056688 | 2.5885e-05
2012-10-31 | 283042 | NIP2A | Urban | LV Transformer SP358-F NIP2A - Planned | 19.22 | 227 | 4362.94 | 0.0043583 | 1.92e-05
2012-10-31 | 283043 | BNH1B | Rural short | LV Transformer SP25671-B BNH1B - Planned | 2 | 317 | 634 | 0.0018235 | 5.7522e-06
2012-10-31 | 283044 | NIP1A | Urban | LV Transformer SP15559-B NIP1A - Planned | 17.535 | 170 | 2980.95 | 0.0029778 | 1.7517e-05
2012-10-31 | 283045 | TGW1 | Rural short | LV Transformer SP8146-A TGW1 - Planned | 1 | 93 | 93 | 0.00026748 | 2.8761e-06
2012-10-31 | 283302 | UPC1 | Rural short | Feeder UPC1 - Planned | 20 | 366 | 7320 | 0.021053 | 5.7522e-05
2012-11-01 | 283102 | PRG2A | Rural short | Feeder PRG2A - Planned | 3 | 178 | 534 | 0.0015358 | 8.6278e-06
2012-11-01 | 283103 | BDT1 | Rural short | LV Transformer SP7179-D BDT1 - Planned | 2.5 | 96 | 240 | 0.00069023 | 7.1899e-06
2012-11-01 | 283120 | WFD1B | Rural short | LV Transformer SP13427-E WFD1B - Planned | 3.99 | 122 | 486.78 | 0.0014 | 1.1475e-05
2012-11-01 | 283121 | MFN12A | Rural short | LV Transformer SP13586-C MFN12A - Planned | 22.5 | 125 | 2812.5 | 0.0080886 | 6.4709e-05
2012-11-01 | 283122 | YTA1B | Rural short | LV Transformer SP7841-C YTA1B - Planned | 1.25 | 213 | 266.25 | 0.00076572 | 3.5949e-06
2012-11-01 | 283125 | LGV6A | Rural short | LV Transformer SP5442-F LGV6A - Planned | 13.02 | 301 | 3919.02 | 0.011271 | 3.7445e-05
2012-11-01 | 283140 | FDS1 | Rural short | Feeder FDS1 - Planned | 10.02 | 397 | 3977.94 | 0.01144 | 2.8817e-05
2012-11-01 | 283142 | LBH1B | Rural short | Feeder LBH1B - Planned | 80.9472 | 477 | 38611.8144 | 0.11105 | 0.0002328
2012-11-01 | 283143 | NBR4 | Rural short | LV Transformer SP4351-A NBR4 - Planned | 17.5 | 439 | 7682.5 | 0.022094 | 5.0329e-05
2012-11-01 | 283144 | GYN3A | Rural short | Feeder GYN3A - Planned | 45.622 | 396 | 18066.312 | 0.051958 | 0.00013121
2012-11-01 | 283145 | CBW7 | Rural short | LV Transformer SP3133-E CBW7 - Planned | 4 | 32 | 128 | 0.00036812 | 1.1504e-05
2012-11-01 | 283146 | EMD2 | Rural short | LV Transformer SP3219-B EMD2 - Planned | 6 | 3.5 | 42 | 0.00012079 | 1.7256e-05
2012-11-01 | 283148 | CRBTHP14 | Urban | Feeder CRBTHP14 - Planned | 56.29 | 630 | 35462.7 | 0.035424 | 5.6229e-05
2012-11-01 | 283150 | INA10A | Urban | LV Transformer SP2845-I INA10A - Planned | 5.28 | 287 | 1515.36 | 0.0015137 | 5.2743e-06
2012-11-01 | 283151 | KMR22A | Urban | LV Transformer SC4943-G KMR22A - Planned | 5.4102 | 73 | 394.9446 | 0.00039452 | 5.4043e-06
2012-11-01 | 283152 | AGE5B | Urban | LV Transformer SP2604-L AGE5B - Planned | 7.14 | 247 | 1763.58 | 0.0017617 | 7.1322e-06
2012-11-01 | 283153 | DRA8 | Urban | LV Transformer SP799214 DRA8 - Planned | 89.5 | 231 | 20674.5 | 0.020652 | 8.9403e-05
2012-11-01 | 283154 | AGE6A | Urban | LV Transformer SP1322-O AGE6A - Planned | 5.38 | 300 | 1614 | 0.0016122 | 5.3742e-06
2012-11-01 | 283155 | EMD3 | Rural short | LV Transformer SP6625-C EMD3 - Planned | 12.17 | 319 | 3882.23 | 0.011165 | 3.5e-05
2012-11-01 | 283156 | GYN3A | Rural short | LV Transformer SP1151-D GYN3A - Planned | 4.08 | 365 | 1489.2 | 0.0042829 | 1.1734e-05
2012-11-01 | 283157 | MLY1 | Rural short | LV Transformer SP1075-A MLY1 - Planned | 3 | 70 | 210 | 0.00060395 | 8.6278e-06
2012-11-01 | 283158 | LDR8 | Urban | LV Transformer SP1084-E LDR8 - Planned | 15 | 228 | 3420 | 0.0034163 | 1.4984e-05
2012-11-01 | 283159 | BBH10A | Urban | LV Transformer SP2887-H BBH10A - Planned | 11.235 | 334 | 3752.49 | 0.0037484 | 1.1223e-05
2012-11-01 | 283160 | KLG10A | Urban | LV Transformer SC784215 KLG10A - Planned | 3.9 | 45 | 175.5 | 0.00017531 | 3.8958e-06
2012-11-01 | 283161 | SPE7 | Urban | LV Transformer SP266-H SPE7 - Planned | 0.64 | 160 | 102.4 | 0.00010229 | 6.393e-07
2012-11-01 | 283162 | KLG10A | Urban | LV Transformer SC784215 KLG10A - Planned | 10.86 | 32 | 347.52 | 0.00034714 | 1.0848e-05
2012-11-01 | 283163 | DRD13A | Urban | LV Transformer SP3689-E DRD13A - Planned | 18.8 | 360 | 6768 | 0.0067606 | 1.878e-05
2012-11-01 | 283164 | SGT7 | Urban | LV Transformer SP813851 SGT7 - Planned | 0.8 | 171 | 136.8 | 0.00013665 | 7.9913e-07
2012-11-01 | 283165 | KLG11A | Urban | LV Transformer SC788402 KLG11A - Planned | 5.02 | 45 | 225.9 | 0.00022565 | 5.0145e-06
2012-11-01 | 283166 | KLG11A | Urban | LV Transformer SC546692 KLG11A - Planned | 23.98 | 52 | 1246.96 | 0.0012456 | 2.3954e-05
2012-11-01 | 283167 | KLG11A | Urban | LV Transformer SP8296-E NRA13A - Planned | 5.56 | 60 | 333.6 | 0.00033324 | 5.554e-06
2012-11-01 | 283167 | NRA13A | Rural short | LV Transformer SP8296-E NRA13A - Planned | 1.96 | 60 | 117.6 | 0.00033821 | 5.6369e-06
2012-11-01 | 283168 | BBS9 | Urban | LV Transformer SC3900-F BBS9 - Planned | 19.1577 | 307 | 5881.4139 | 0.005875 | 1.9137e-05
2012-11-01 | 283169 | WRG6A | Urban | LV Transformer SP3150-J WRG6A - Planned | 2.67 | 293 | 782.31 | 0.00078146 | 2.6671e-06
2012-11-01 | 283170 | WRG1A | Urban | LV Transformer SP2419-M WRG1A - Planned | 18.9 | 253 | 4781.7 | 0.0047765 | 1.8879e-05
2012-11-01 | 283171 | CNB24A | Rural short | LV Transformer SP4859-E CNB24A - Planned | 5.25 | 441 | 2315.25 | 0.0066585 | 1.5099e-05
2012-11-01 | 283172 | GGR4 | Rural short | LV Transformer SP5342-C GGR4 - Planned | 5.12 | 464 | 2375.68 | 0.0068323 | 1.4725e-05
2012-11-01 | 283173 | THL2 | Rural short | LV Transformer SP3346-B THL2 - Planned | 1 | 63 | 63 | 0.00018118 | 2.8759e-06
2012-11-01 | 283304 | MCN3 | Urban | Feeder MCN3 - Planned | 3.745 | 444 | 1662.78 | 0.001661 | 3.7409e-06
2012-11-02 | 283230 | UPC1 | Rural short | Feeder UPC1 - Planned | 16.46 | 256 | 4213.76 | 0.012121 | 4.7349e-05
2012-11-02 | 283231 | WSE3A | Rural short | Feeder WSE3A - Planned | 19 | 270 | 5130 | 0.014757 | 5.4656e-05
2012-11-02 | 283240 | CRB25A | Rural short | LV Transformer SP5759-E CRB25A - Planned | 8.5 | 243 | 2065.5 | 0.0059416 | 2.4451e-05
2012-11-02 | 283262 | TRP4 | Rural short | Feeder TRP4 - Planned | 5 | 350 | 1750 | 0.0050341 | 1.4383e-05
2012-11-02 | 283263 | MGP15A | Urban | Feeder MGP15A - Planned | 32 | 404 | 12928 | 0.012913 | 3.1962e-05
2012-11-02 | 283264 | GGR1 | Rural short | Feeder GGR1 - Planned | 24 | 415 | 9960 | 0.028651 | 6.9039e-05
2012-11-02 | 283265 | IPL2 | Rural short | Feeder IPL2 - Planned | 7.5 | 305 | 2287.5 | 0.0065802 | 2.1575e-05
2012-11-02 | 283266 | MCW4 | Rural short | Feeder MCW4 - Planned | 2 | 387 | 774 | 0.0022265 | 5.7532e-06
2012-11-02 | 283272 | CRY6A | Rural short | Feeder CRY6A - Planned | 3.41 | 369 | 1258.29 | 0.0036196 | 9.8092e-06
2012-11-02 | 283273 | NBR4 | Rural short | Feeder NBR4 - Planned | 10 | 260 | 2600 | 0.0074792 | 2.8766e-05
2012-11-02 | 283274 | PWC4 | Rural short | LV Transformer SP2460-C PWC4 - Planned | 4.98 | 117 | 582.66 | 0.0016761 | 1.4326e-05
2012-11-02 | 283278 | KRN18A | Urban | LV Transformer SP2674-M KRN18A - Planned | 20.16 | 354 | 7136.64 | 0.0071281 | 2.0136e-05
2012-11-02 | 283279 | GBN4 | Rural short | LV Transformer SP879-D GBN4 - Planned | 3 | 150 | 450 | 0.0012945 | 8.6298e-06
2012-11-02 | 283280 | LBH1B | Rural short | LV Transformer SP6676-A LBH1B - Planned | 63.83 | 259 | 16531.97 | 0.047556 | 0.00018361
2012-11-02 | 283281 | PGN1B | Rural short | LV Transformer SP2158-C PGN1B - Planned | 6.6 | 180 | 1188 | 0.0034174 | 1.8986e-05
2012-11-02 | 283282 | MMC33A | Urban | LV Transformer SP2865-G MMC33A - Planned | 18.72 | 205 | 3837.6 | 0.003833 | 1.8698e-05
2012-11-02 | 283284 | BRD11A | Rural short | LV Transformer SC583834 BRD11A - Planned | 42.7 | 284 | 12126.8 | 0.034884 | 0.00012283
2012-11-02 | 283285 | QPT21 | Urban | LV Transformer SC1436022 QPT21 - Planned | 6.3196 | 77 | 486.6092 | 0.00048603 | 6.3121e-06
2012-11-02 | 283286 | RCF2A | Urban | LV Transformer SP4918-F RCF2A - Planned | 30.6 | 191 | 5844.6 | 0.0058376 | 3.0564e-05
2012-11-02 | 283287 | WRG11A | Urban | LV Transformer SP6538-J WRG11A - Planned | 9.425 | 380 | 3581.5 | 0.0035772 | 9.4138e-06
2012-11-02 | 283287 | WRG15A | Urban | LV Transformer SP6538-J WRG11A - Planned | 1.32 | 380 | 501.6 | 0.000501 | 1.3184e-06
2012-11-02 | 283288 | SBK4 | Urban | LV Transformer SC5352-H SBK4 - Planned | 0.73 | 69 | 50.37 | 5.031e-05 | 7.2913e-07
2012-11-02 | 283289 | THL3 | Rural short | LV Transformer SP1470-D THL3 - Planned | 0.4 | 89 | 35.6 | 0.00010241 | 1.1506e-06
2012-11-02 | 283290 | MSV1 | Rural short | LV Transformer SP3131-C MSV1 - Planned | 2.2 | 212 | 466.4 | 0.0013417 | 6.3285e-06
2012-11-03 | 283293 | BDA3A | Urban | LV Transformer SC2780-I BDA3A - Planned | 1 | 106 | 106 | 0.00010588 | 9.9888e-07
2012-11-03 | 283296 | SPF1B | Rural short | LV Transformer SC2055274 RPN8 - Planned | 0.94 | 182 | 171.08 | 0.00049191 | 2.7028e-06
2012-11-03 | 283318 | WRG4A | Urban | LV Transformer SC1314-O WRG4A - Planned | 1.755 | 160 | 280.8 | 0.00028049 | 1.753e-06
2012-11-03 | 283318 | WRG9A | Urban | LV Transformer SC1314-O WRG4A - Planned | 19 | 85 | 1615 | 0.0016132 | 1.8979e-05
2012-11-04 | 283313 | MRE7A | Urban | LV Transformer SC744206 MRE7A - Planned | 5.5 | 290 | 1595 | 0.0015932 | 5.4939e-06
2012-11-04 | 283314 | SMR10A | Urban | Feeder SMR10A - Planned | 55.077 | 270 | 14870.79 | 0.014854 | 5.5016e-05
2012-11-04 | 283315 | GBG26 | Urban | LV Transformer SP1765-L GBG26 - Planned | 6.965 | 301 | 2096.465 | 0.0020941 | 6.9573e-06
2012-11-04 | 283316 | DRD2A | Rural short | LV Transformer SC768834 DRD2A - Planned | 3 | 120 | 360 | 0.001035 | 8.625e-06
2012-11-04 | 283317 | NDH6 | Urban | LV Transformer SP757901 NDH6 - Planned | 28.36 | 315 | 8933.4 | 0.0089235 | 2.8328e-05
2012-11-04 | 283319 | HPK2 | Urban | LV Transformer SP1992-N HPK2 - Planned | 18.9328 | 269 | 5092.9232 | 0.0050873 | 1.8912e-05
2012-11-04 | 283320 | GTN15A | Rural short | LV Transformer SP2457-D GTN15A - Planned | 4.125 | 21 | 86.625 | 0.00024905 | 1.1859e-05
2012-11-04 | 283321 | SPF1B | Rural short | LV Transformer SC1433981 SPF1B - Planned | 0.94 | 65 | 61.1 | 0.00017566 | 2.7025e-06
2012-11-04 | 283322 | BDB4A | Rural short | LV Transformer SP18003-B BDB4A - Planned | 9 | 28 | 252 | 0.0007245 | 2.5875e-05
2012-11-04 | 283323 | BHDRCK29 | Urban | Feeder BHDRCK29 - Planned | 2 | 425 | 850 | 0.00084906 | 1.9978e-06
2012-11-04 | 283324 | TGP9A | Rural short | Feeder TGP9A - Planned | 26.392 | 604 | 15940.768 | 0.04583 | 7.5877e-05
2012-11-05 | 283360 | GPSTR1H | Urban | LV Transformer SSGPS GPSTR1H - Planned | 1 | 52 | 52 | 5.1949e-05 | 9.9902e-07
2012-11-05 | 283360 | GPSTR2H | Urban | LV Transformer SSGPS GPSTR1H - Planned | 1 | 52 | 52 | 5.1949e-05 | 9.9902e-07
2012-11-05 | 283381 | BDT1 | Rural short | LV Transformer SP7295-E BDT1 - Planned | 3 | 333 | 999 | 0.0028703 | 8.6195e-06
2012-11-05 | 283385 | GGR4 | Rural short | Feeder GGR4 - Planned | 6 | 353 | 2118 | 0.0060854 | 1.7239e-05
2012-11-05 | 283386 | NGI1B | Rural short | Feeder NGI1B - Planned | 2.65 | 404 | 1070.6 | 0.003076 | 7.6139e-06
2012-11-05 | 283387 | MFD3A | Rural short | LV Transformer SC1632-F MFD3A - Planned | 1 | 396 | 396 | 0.0011378 | 2.8732e-06
2012-11-05 | 283388 | NBR4 | Rural short | LV Transformer SP4351-A NBR4 - Planned | 17.5 | 2 | 70 | 0.00020112 | 5.0281e-05
2012-11-05 | 283391 | NMK5 | Urban | LV Transformer SP3032-O NMK5 - Planned | 15.875 | 145 | 2301.875 | 0.0022996 | 1.5859e-05
2012-11-05 | 283392 | ENG3 | Urban | LV Transformer SP750-P ENG3 - Planned | 13.35 | 237 | 3163.95 | 0.0031609 | 1.3337e-05
2012-11-05 | 283393 | NMK5 | Urban | LV Transformer SP2423-K NMK5 - Planned | 19.78 | 339 | 6705.42 | 0.0066989 | 1.9761e-05
2012-11-05 | 283394 | GYM2A | Rural short | LV Transformer SP547-C GYM2A - Planned | 1 | 255 | 255 | 0.00073266 | 2.8732e-06
2012-11-05 | 283395 | MDRMLD11 | Urban | LV Transformer SP14121-D MDRMLD11 - Planned | 7.8 | 323 | 2519.4 | 0.0025169 | 7.7924e-06
2012-11-05 | 283396 | DBY9 | Urban | LV Transformer SP8137-C DBY9 - Planned | 10.15 | 290 | 2943.5 | 0.0029406 | 1.014e-05
2012-11-05 | 283397 | SGT7 | Urban | LV Transformer SP50044-F SGT7 - Planned | 2.0866 | 225 | 469.485 | 0.00046903 | 2.0846e-06
2012-11-05 | 283398 | GGR4 | Rural short | LV Transformer SP3464-B GGR4 - Planned | 14.06 | 384 | 5399.04 | 0.015512 | 4.0397e-05
2012-11-06 | 283423 | RWD1 | Rural short | LV Transformer SP1208-G RWD1 - Planned | 3 | 123 | 369 | 0.0010598 | 8.6165e-06
2012-11-06 | 283424 | TGW2 | Rural short | Feeder TGW2 - Planned | 27.02 | 177 | 4782.54 | 0.013736 | 7.7606e-05
2012-11-06 | 283429 | LLY1 | Rural short | Feeder LLY1 - Planned | 14.02 | 325 | 4556.5 | 0.013087 | 4.0268e-05
2012-11-06 | 283430 | AGT31A | Rural short | Feeder AGT31A - Planned | 4 | 322 | 1288 | 0.0036993 | 1.1489e-05
2012-11-06 | 283431 | MLB8A | Rural short | LV Transformer SP479-A MLB8A - Planned | 8.01 | 15 | 240.3 | 0.00069018 | 2.3006e-05
2012-11-06 | 283432 | GYN7A | Rural short | Feeder GYN7A - Planned | 4 | 59 | 236 | 0.00067783 | 1.1489e-05
2012-11-06 | 283433 | PWC4 | Rural short | LV Transformer SP2075-C PWC4 - Planned | 26.88 | 273 | 7338.24 | 0.021077 | 7.7203e-05
2012-11-06 | 283434 | BWH16A | Rural short | LV Transformer SP11342-B BWH16A - Planned | 32.01 | 321 | 10275.21 | 0.029512 | 9.1938e-05
2012-11-06 | 283435 | GYS3A | Rural short | Feeder GYS3A - Planned | 72.9122 | 262 | 19102.9964 | 0.054867 | 0.00020942
2012-11-06 | 283436 | BMT2 | Rural short | LV Transformer SP5-E BMT2 - Planned | 7 | 271 | 1897 | 0.0054485 | 2.0105e-05
2012-11-06 | 283437 | GBN3 | Rural short | LV Transformer SP2558-D GBN3 - Planned | 1 | 221 | 221 | 0.00063475 | 2.8722e-06
2012-11-06 | 283438 | YDA2B | Rural short | LV Transformer SP4002-A YDA2B - Planned | 0.8 | 191 | 152.8 | 0.00043887 | 2.2977e-06
2012-11-06 | 283439 | CRY6A | Rural short | LV Transformer SP6803-B CRY6A - Planned | 21.375 | 156 | 3334.5 | 0.0095772 | 6.1392e-05
2012-11-06 | 283440 | MCW7 | Rural short | Feeder MCW7 - Planned | 42.86 | 434 | 18601.24 | 0.053426 | 0.0001231
2012-11-06 | 283441 | ALY8 | Urban | LV Transformer SP30341-B ALY8 - Planned | 20.1085 | 316 | 6354.286 | 0.0063485 | 2.009e-05
2012-11-06 | 283442 | TWG21 | Urban | LV Transformer SP4311-M TWG21 - Planned | 38.349 | 228 | 8743.572 | 0.0087356 | 3.8314e-05
2012-11-06 | 283443 | NBR8 | Rural short | LV Transformer SP5364-A NBR8 - Planned | 3.96 | 118 | 467.28 | 0.0013421 | 1.1374e-05
2012-11-06 | 283444 | MMC33A | Urban | LV Transformer SP2865-G MMC33A - Planned | 18.72 | 303 | 5672.16 | 0.005667 | 1.8703e-05
2012-11-06 | 283445 | IPL1 | Rural short | LV Transformer SP627-E IPL1 - Planned | 7.04 | 200 | 1408 | 0.004044 | 2.022e-05
2012-11-06 | 283446 | SGT7 | Urban | LV Transformer SP813851 SGT7 - Planned | 0.8 | 210 | 168 | 0.00016785 | 7.9927e-07
2012-11-06 | 283447 | BGY15A | Urban | LV Transformer SP13774-D BGY15A - Planned | 6.4 | 410 | 2624 | 0.0026216 | 6.3942e-06
2012-11-06 | 283448 | CPB4 | Urban | LV Transformer SP4973-D CPB4 - Planned | 11.96 | 279 | 3336.84 | 0.0033338 | 1.1949e-05
2012-11-06 | 283449 | BPN29A | Urban | LV Transformer SP4834-J BPN29A - Planned | 9.12 | 155 | 1413.6 | 0.0014123 | 9.1117e-06
2012-11-06 | 283450 | MWMRBK11 | Rural short | LV Transformer SP4221-E MWMRBK11 - Planned | 12.22 | 465 | 5682.3 | 0.01632 | 3.5098e-05
2012-11-06 | 283741 | CPL23A | Rural short | Feeder CPL23A - Planned | 2.94 | 195 | 573.3 | 0.0016466 | 8.4441e-06
2012-11-06 | 284935 | CPL23A | Rural short | Feeder CPL23A - Planned | 2.94 | 195 | 573.3 | 0.0016466 | 8.4441e-06
2012-11-07 | 283460 | RWD1 | Rural short | LV Transformer SP734398 RWD1 - Planned | 1 | 153 | 153 | 0.00043928 | 2.8711e-06
2012-11-07 | 283463 | KBR2A | Rural short | LV Transformer SP740844 KBR2A - Planned | 3 | 234 | 702 | 0.0020155 | 8.6134e-06
2012-11-07 | 283480 | BHD23A | Rural short | LV Transformer SP5779-E BHD23A - Planned | 15.5 | 373 | 5781.5 | 0.016599 | 4.4503e-05
2012-11-07 | 283481 | UPC1 | Rural short | Feeder UPC1 - Planned | 18.465 | 325 | 6001.125 | 0.01723 | 5.3015e-05
2012-11-07 | 283482 | LLY1 | Rural short | Feeder LLY1 - Planned | 2.99 | 395 | 1181.05 | 0.0033909 | 8.5847e-06
2012-11-07 | 283483 | WSE3A | Rural short | Feeder WSE3A - Planned | 42.925 | 355 | 15238.375 | 0.043751 | 0.00012324
2012-11-07 | 283484 | JBB4A | Urban | Feeder JBB4A - Planned | 27.01 | 360 | 9723.6 | 0.0097154 | 2.6987e-05
2012-11-07 | 283486 | GYN3A | Rural short | Feeder GYN3A - Planned | 23.642 | 462 | 10922.604 | 0.03136 | 6.7879e-05
2012-11-07 | 283487 | BWH13A | Rural short | LV Transformer SP17904-B BWH13A - Planned | 20 | 331 | 6620 | 0.019007 | 5.7423e-05
2012-11-07 | 283488 | BWH12A | Rural short | LV Transformer SP2700-C BWH12A - Planned | 26.5 | 312 | 8268 | 0.023739 | 7.6085e-05
2012-11-07 | 283489 | WFD2B | Rural short | LV Transformer SP12044-D WFD2B - Planned | 1.25 | 226 | 282.5 | 0.00081109 | 3.5889e-06
2012-11-07 | 283490 | GBN4 | Rural short | Feeder GBN4 - Planned | 22.81 | 152 | 3467.12 | 0.0099546 | 6.549e-05
2012-11-07 | 283491 | WFD2B | Rural short | Feeder WFD2B - Planned | 2.168 | 134 | 290.512 | 0.0008341 | 6.2246e-06
2012-11-07 | 283492 | PGN6A | Urban | LV Transformer SC759448 PGN6A - Planned | 1 | 86 | 86 | 8.5928e-05 | 9.9916e-07
2012-11-07 | 283494 | CNB24A | Rural short | Feeder CNB24A - Planned | 17.1988 | 627 | 10783.6476 | 0.030961 | 4.938e-05
2012-11-07 | 283496 | ALY8 | Urban | LV Transformer SP2940-H ALY8 - Planned | 21.7168 | 554 | 12031.1072 | 0.012021 | 2.1699e-05
2012-11-07 | 283497 | ENG8 | Urban | LV Transformer SP4307-N ENG8 - Planned | 44.37 | 375 | 16638.75 | 0.016625 | 4.4333e-05
2012-11-07 | 283498 | SMF6A | Rural short | LV Transformer SP2209-M SMF6A - Planned | 11.96 | 296 | 3540.16 | 0.010164 | 3.4339e-05
2012-11-07 | 283499 | YDA5A | Rural short | LV Transformer SP2847-A YDA5A - Planned | 0.96 | 65 | 62.4 | 0.00017916 | 2.7563e-06
2012-11-07 | 283500 | NBR8 | Rural short | LV Transformer SP4403-A NBR8 - Planned | 1 | 63 | 63 | 0.00018088 | 2.8711e-06
2012-11-07 | 283501 | LDR8 | Urban | LV Transformer SP2853-E LDR8 - Planned | 32.56 | 114 | 3711.84 | 0.0037087 | 3.2533e-05
2012-11-07 | 283502 | PBH1 | Urban | LV Transformer SP15834-C PBH1 - Planned | 27.2 | 338 | 9193.6 | 0.0091859 | 2.7177e-05
2012-11-07 | 283503 | MMC33A | Urban | LV Transformer SP2865-G MMC33A - Planned | 18.72 | 360 | 6739.2 | 0.0067336 | 1.8704e-05
2012-11-07 | 283504 | RBA43A | Rural short | LV Transformer SP467144 RBA43A - Planned | 6.225 | 233 | 1450.425 | 0.0041644 | 1.7873e-05
2012-11-07 | 283505 | BHD45B | Urban | LV Transformer SC909-I BHD45B - Planned | 7.7864 | 124 | 965.5136 | 0.0009647 | 7.7799e-06
2012-11-07 | 283506 | SGT7 | Urban | LV Transformer SP813851 SGT7 - Planned | 0.8 | 189 | 151.2 | 0.00015107 | 7.9933e-07
2012-11-07 | 283507 | DRD16A | Urban | LV Transformer SP3723-D DRD16A - Planned | 18.91 | 295 | 5578.45 | 0.0055738 | 1.8894e-05
2012-11-07 | 283508 | CPB4 | Urban | LV Transformer SP4973-D CPB4 - Planned | 22.08 | 264 | 5829.12 | 0.0058242 | 2.2061e-05
2012-11-07 | 283509 | BBS9 | Urban | LV Transformer SC3900-F BBS9 - Planned | 17.1411 | 313 | 5365.1643 | 0.0053607 | 1.7127e-05
2012-11-07 | 283523 | HTN7A | Urban | LV Transformer SP2052-G HTN7A - Planned | 21.375 | 280 | 5985 | 0.00598 | 2.1357e-05
2012-11-07 | 283525 | MCW7 | Rural short | LV Transformer SP18005-C MCW7 - Planned | 31 | 297 | 9207 | 0.026434 | 8.9005e-05
2012-11-07 | 283742 | TGW2 | Rural short | Feeder TGW2 - Planned | 4 | 410 | 1640 | 0.0047087 | 1.1485e-05
2012-11-08 | 283566 | SPC2B | Rural short | LV Transformer SG7197-C SPC2B - Planned | 1 | 351 | 351 | 0.0010074 | 2.8701e-06
2012-11-08 | 283567 | BMT2 | Rural short | LV Transformer SP5427-B BMT2 - Planned | 18.5 | 344 | 6364 | 0.018265 | 5.3097e-05
2012-11-08 | 283570 | FDS1 | Rural short | Feeder FDS1 - Planned | 3.01 | 386 | 1161.86 | 0.0033346 | 8.639e-06
2012-11-08 | 283571 | MTB15A | Rural short | Feeder MTB15A - Planned | 10.01 | 327 | 3273.27 | 0.0093946 | 2.873e-05
2012-11-08 | 283573 | TGW2 | Rural short | Feeder TGW2 - Planned | 4 | 401 | 1604 | 0.0046036 | 1.148e-05
2012-11-08 | 283574 | MGL9 | Rural short | Feeder MGL9 - Planned | 22 | 470 | 10340 | 0.029677 | 6.3142e-05
2012-11-08 | 283576 | CBT8A | Rural short | Feeder CBT8A - Planned | 20.5409 | 386 | 7928.7874 | 0.022756 | 5.8954e-05
2012-11-08 | 283577 | WFD2B | Rural short | Feeder WFD2B - Planned | 4.8 | 78 | 374.4 | 0.0010746 | 1.3776e-05
2012-11-08 | 283578 | GBN3 | Rural short | LV Transformer SP2555-D GBN3 - Planned | 3.5 | 233 | 815.5 | 0.0023406 | 1.0045e-05
2012-11-08 | 283579 | GBN4 | Rural short | Feeder GBN4 - Planned | 21.845 | 193 | 4216.085 | 0.012101 | 6.2697e-05
2012-11-08 | 283580 | NBR6 | Rural short | Feeder NBR6 - Planned | 147.425 | 200 | 29485 | 0.084625 | 0.00042312
2012-11-08 | 283581 | CBT12A | Rural short | LV Transformer SP4675-E CBT12A - Planned | 4 | 144 | 576 | 0.0016532 | 1.148e-05
2012-11-08 | 283582 | PWC3 | Rural short | LV Transformer SP521-A PWC3 - Planned | 8.04 | 108 | 868.32 | 0.0024922 | 2.3076e-05
2012-11-08 | 283584 | AHL5A | Rural short | Feeder AHL5A - Planned | 1 | 438 | 438 | 0.0012571 | 2.8701e-06
2012-11-08 | 283587 | JBB16A | Rural short | LV Transformer SP6014-D JBB16A - Planned | 11.96 | 407 | 4867.72 | 0.013971 | 3.4326e-05
2012-11-08 | 283588 | RLB16A | Rural short | Feeder RLB16A - Planned | 0.66 | 511 | 337.26 | 0.00096797 | 1.8943e-06
2012-11-08 | 283589 | TBV2 | Rural short | Feeder TBV2 - Planned | 37.34 | 300 | 11202 | 0.032151 | 0.00010717
2012-11-08 | 283591 | WMD4A | Rural short | Feeder WMD4A - Planned | 45.1 | 593 | 26744.3 | 0.076759 | 0.00012944
2012-11-08 | 283592 | TGP9A | Rural short | LV Transformer SP9324-G TGP9A - Planned | 6.435 | 240 | 1544.4 | 0.0044326 | 1.8469e-05
2012-11-08 | 283593 | WMD4A | Rural short | LV Transformer SP4360-A WMD4A - Planned | 45.1 | 595 | 26834.5 | 0.077017 | 0.00012944
2012-11-08 | 283594 | ALY8 | Urban | LV Transformer SC2832-G ALY8 - Planned | 4.59 | 56 | 257.04 | 0.00025684 | 4.5865e-06
2012-11-08 | 283595 | KLG14A | Urban | LV Transformer SC1489829 KLG14A - Planned | 1 | 582 | 582 | 0.00058155 | 9.9923e-07
2012-11-08 | 283596 | ENG7 | Urban | LV Transformer SP768909 ENG7 - Planned | 20.88 | 320 | 6681.6 | 0.0066765 | 2.0864e-05
2012-11-08 | 283597 | AGE8 | Urban | LV Transformer SP2171-I AGE8 - Planned | 2.655 | 282 | 748.71 | 0.00074813 | 2.653e-06
2012-11-08 | 283598 | KMR21A | Urban | LV Transformer SC4346-K KMR21A - Planned | 18.36 | 345 | 6334.2 | 0.0063293 | 1.8346e-05
2012-11-08 | 283599 | CMD7A | Rural short | LV Transformer SP4362-B CMD7A - Planned | 46.28 | 363 | 16799.64 | 0.048216 | 0.00013283
2012-11-08 | 283600 | WMD14A | Rural short | LV Transformer SP3763-B WMD14A - Planned | 29.9 | 91 | 2720.9 | 0.0078092 | 8.5816e-05
2012-11-08 | 283601 | IBL2 | Rural short | LV Transformer SP705-C IBL2 - Planned | 8.01 | 133 | 1065.33 | 0.0030576 | 2.2989e-05
2012-11-08 | 283602 | CMD15A | Urban | LV Transformer SP10853-A CMD15A - Planned | 6.1 | 231 | 1409.1 | 0.001408 | 6.0953e-06
2012-11-08 | 283603 | GBN4 | Rural short | LV Transformer SP1507-F GBN4 - Planned | 4.98 | 44 | 219.12 | 0.00062889 | 1.4293e-05
2012-11-08 | 283604 | CRBTHP14 | Urban | LV Transformer SP4149-H CRBTHP14 - Planned | 43.96 | 374 | 16441.04 | 0.016428 | 4.3926e-05
2012-11-08 | 283605 | BLH15B | Urban | LV Transformer SP9714-C BLH15B - Planned | 25.4214 | 116 | 2948.8824 | 0.0029466 | 2.5402e-05
2012-11-08 | 283606 | MMC33A | Urban | LV Transformer SP2340-H MMC33A - Planned | 18.96 | 295 | 5593.2 | 0.0055889 | 1.8945e-05
2012-11-08 | 283607 | BHD45B | Urban | LV Transformer SC909-I BHD45B - Planned | 7.7864 | 457 | 3558.3848 | 0.0035556 | 7.7804e-06
2012-11-08 | 283608 | MDRMLD11 | Urban | LV Transformer SP564323 MDRMLD11 - Planned | 42 | 18 | 756 | 0.00075542 | 4.1968e-05
2012-11-08 | 283609 | SGT5 | Urban | LV Transformer SP2684-G SGT5 - Planned | 16.08 | 177 | 2846.16 | 0.002844 | 1.6068e-05
2012-11-08 | 283610 | DBY7A | Urban | LV Transformer SP17269-B DBY7A - Planned | 5.545 | 32.3333 | 188.915 | 0.00018877 | 5.5407e-06
2012-11-08 | 283611 | BHL4A | Urban | LV Transformer SP5771-I BHL4A - Planned | 8.85 | 37 | 327.45 | 0.0003272 | 8.8432e-06
2012-11-08 | 283612 | DBY10 | Urban | LV Transformer SP17269-B DBY7A - Planned | 4.03 | 40 | 161.2 | 0.00016108 | 4.0269e-06
2012-11-08 | 283612 | DBY7A | Urban | LV Transformer SP17269-B DBY7A - Planned | 3.21 | 15 | 48.15 | 4.8113e-05 | 3.2075e-06
2012-11-08 | 283613 | DBY10 | Urban | LV Transformer SP17269-B DBY7A - Planned | 1.86 | 20 | 37.2 | 3.7171e-05 | 1.8586e-06
2012-11-08 | 283613 | DBY7A | Urban | LV Transformer SP17269-B DBY7A - Planned | 107 | 27 | 3723.6 | 0.0037207 | 0.00010692
2012-11-08 | 283614 | WRG1A | Urban | LV Transformer SP2419-M WRG1A - Planned | 39.92 | 157.3333 | 5536.22 | 0.005532 | 3.9889e-05
2012-11-08 | 283615 | WED6A | Urban | LV Transformer SG3759-E WED6A - Planned | 12.6783 | 415 | 5261.4945 | 0.0052574 | 1.2669e-05
2012-11-08 | 283616 | MWMRBK11 | Rural short | LV Transformer SP3603-G MWMRBK11 - Planned | 9.18 | 212 | 1946.16 | 0.0055857 | 2.6347e-05
2012-11-08 | 283618 | KBN1B | Rural short | LV Transformer SC1825963 KBN1B - Planned | 1 | 128 | 128 | 0.00036737 | 2.8701e-06
2012-11-08 | 283621 | UPC1 | Rural short | Feeder UPC1 - Planned | 62.48 | 479 | 29927.92 | 0.085896 | 0.00017932
2012-11-08 | 283626 | ANAT2 | Urban | LV Transformer SSANA ANAT1 - Planned | 0.536 | 462 | 247.632 | 0.00024744 | 5.3559e-07
2012-11-08 | 283659 | TGP9A | Rural short | LV Transformer SP23648-E TGP9A - Planned | 6.435 | 240 | 1544.4 | 0.0044326 | 1.8469e-05
2012-11-09 | 283640 | SMF6A | Rural short | LV Transformer SP2816-M SMF6A - Planned | 12 | 191 | 2292 | 0.0065761 | 3.443e-05
2012-11-09 | 283641 | CCY8A | Rural short | LV Transformer SP4646-H CCY8A - Planned | 12 | 289 | 3468 | 0.0099502 | 3.443e-05
2012-11-09 | 283642 | PPE13A | Rural short | LV Transformer SP6725-D PPE13A - Planned | 1.25 | 211 | 263.75 | 0.00075674 | 3.5864e-06
2012-11-09 | 283643 | TGW2 | Rural short | Feeder TGW2 - Planned | 4.8 | 369 | 1771.2 | 0.0050818 | 1.3772e-05
2012-11-09 | 283644 | BNH1B | Rural short | Feeder BNH1B - Planned | 35.94 | 274 | 9847.56 | 0.028254 | 0.00010312
2012-11-09 | 283647 | CCYUPC2 | Urban | Feeder CCYUPC2 - Planned | 1.5 | 417 | 625.5 | 0.00062506 | 1.4989e-06
2012-11-09 | 283648 | LTN2 | Rural short | LV Transformer SP753666 LTN2 - Planned | 1.9866 | 255 | 506.583 | 0.0014535 | 5.6999e-06
2012-11-09 | 283651 | TRG2A | Urban | LV Transformer SP484584-A TRG2A - Planned | 3.15 | 280 | 882 | 0.00088138 | 3.1478e-06
2012-11-09 | 283653 | NSD8A | Urban | LV Transformer SP2271-M NSD8A - Planned | 11.7 | 178 | 2082.6 | 0.0020811 | 1.1692e-05
2012-11-09 | 283654 | CMD15A | Urban | LV Transformer SP6572-B CMD15A - Planned | 68.805 | 361 | 24838.605 | 0.024821 | 6.8756e-05
2012-11-09 | 283655 | BLN2B | Urban | LV Transformer SP5024-E BLN2B - Planned | 10.99 | 224 | 2461.76 | 0.00246 | 1.0982e-05
2012-11-09 | 283656 | CCY7A | Rural short | LV Transformer SC1502707 CCY7A - Planned | 0.944 | 65 | 61.36 | 0.00017605 | 2.7085e-06
2012-11-09 | 283657 | LDR8 | Urban | LV Transformer SP13669-B LDR8 - Planned | 10.71 | 227 | 2431.17 | 0.0024294 | 1.0702e-05
2012-11-09 | 283658 | MMC19B | Urban | LV Transformer SC482-L MMC19B - Planned | 42.3 | 243 | 10278.9 | 0.010272 | 4.227e-05
2012-11-09 | 283658 | MMC22A | Urban | LV Transformer SC482-L MMC19B - Planned | 4.05 | 243 | 984.15 | 0.00098345 | 4.0471e-06
2012-11-09 | 283660 | DBY7A | Urban | LV Transformer SC1389051 DBY7A - Planned | 3.99 | 90 | 359.1 | 0.00035885 | 3.9872e-06
2012-11-09 | 283661 | SGT7 | Urban | LV Transformer SP813851 SGT7 - Planned | 0.8 | 94 | 75.2 | 7.5147e-05 | 7.9943e-07
2012-11-09 | 283662 | DBY7A | Urban | LV Transformer SC1389051 DBY7A - Planned | 1.53 | 60 | 91.8 | 9.1735e-05 | 1.5289e-06
2012-11-09 | 283663 | CPB4 | Urban | LV Transformer SP4973-D CPB4 - Planned | 20.24 | 338 | 6841.12 | 0.0068363 | 2.0226e-05
2012-11-09 | 283664 | AGT37A | Urban | LV Transformer SC6038-G AGT37A - Planned | 28.04 | 231 | 6477.24 | 0.0064727 | 2.802e-05
2012-11-09 | 283665 | GTN12A | Rural short | LV Transformer SP5090-A GTN12A - Planned | 1.96 | 240 | 470.4 | 0.0013496 | 5.6235e-06
2012-11-09 | 283671 | AMR2 | Rural short | Feeder AMR2 - Planned | 14.03 | 300 | 4209 | 0.012076 | 4.0254e-05
2012-11-09 | 283672 | PWC5 | Rural short | LV Transformer SP15501-A PWC5 - Planned | 20.9 | 284 | 5935.6 | 0.01703 | 5.9965e-05
2012-11-09 | 283673 | WFD2B | Rural short | LV Transformer SP3715-D WFD2B - Planned | 23.5 | 234 | 5499 | 0.015777 | 6.7425e-05
2012-11-09 | 283674 | PWC3 | Rural short | LV Transformer SP520-A PWC3 - Planned | 10.01 | 148 | 1481.48 | 0.0042506 | 2.872e-05
2012-11-09 | 283675 | AMR3 | Rural short | LV Transformer SP7513-B AMR3 - Planned | 2.01 | 200 | 402 | 0.0011534 | 5.767e-06
2012-11-09 | 283676 | PWC3 | Rural short | LV Transformer SP3806-B PWC3 - Planned | 25.44 | 157 | 3994.08 | 0.01146 | 7.2991e-05
2012-11-09 | 283677 | GBN4 | Rural short | LV Transformer SP7523-C GBN4 - Planned | 2 | 12 | 24 | 6.886e-05 | 5.7383e-06
2012-11-09 | 283696 | MTG3A | Urban | LV Transformer SC2957-J MTG3A - Planned | 1.96 | 235 | 460.6 | 0.00046027 | 1.9586e-06
2012-11-11 | 283724 | WSE3A | Rural short | Feeder WSE3A - Planned | 64.006 | 218 | 13953.308 | 0.040016 | 0.00018356
2012-11-11 | 283732 | TRG3 | Urban | LV Transformer SG3305-K TRG3 - Planned | 3.5 | 327 | 1144.5 | 0.0011438 | 3.4978e-06
2012-11-11 | 283735 | SBY4 | Urban | Feeder SBY4 - Planned | 4 | 374 | 1496 | 0.0014951 | 3.9975e-06
2012-11-11 | 283739 | HTN22A | Urban | Feeder HTN22A - Planned | 4 | 530 | 2120 | 0.0021187 | 3.9975e-06
2012-11-11 | 283740 | NDH7 | Urban | Feeder NDH7 - Planned | 14.75 | 565 | 8333.75 | 0.0083285 | 1.4741e-05
2012-11-11 | 283743 | MFD9A | Urban | LV Transformer SP3647-E MFD9A - Planned | 18.8573 | 299 | 5638.3327 | 0.0056348 | 1.8845e-05
2012-11-11 | 283744 | MDRMLD11 | Urban | LV Transformer SC562136 MDRMLD11 - Planned | 19.3056 | 42 | 810.8352 | 0.00081033 | 1.9293e-05
2012-11-11 | 283745 | CRB24B | Urban | LV Transformer SP3458-F CRB24B - Planned | 17.55 | 485 | 8511.75 | 0.0085064 | 1.7539e-05
2012-11-11 | 283746 | CRB15A | Urban | LV Transformer SC762992 CRB15A - Planned | 15.17 | 184 | 2791.28 | 0.0027895 | 1.516e-05
2012-11-11 | 283747 | MDRMLD11 | Urban | LV Transformer SC562136 MDRMLD11 - Planned | 10.8594 | 37 | 401.7978 | 0.00040155 | 1.0853e-05
2012-11-11 | 283748 | MDRMLD11 | Urban | LV Transformer SC562136 MDRMLD11 - Planned | 4.2231 | 36 | 152.0316 | 0.00015194 | 4.2204e-06
2012-11-11 | 283749 | KRN2 | Urban | LV Transformer SP1371-I KRN2 - Planned | 4.2415 | 345 | 1463.3175 | 0.0014624 | 4.2388e-06
2012-11-11 | 283750 | DRD15B | Urban | LV Transformer SP796423 DRD15B - Planned | 3.0999 | 192 | 595.1808 | 0.00059481 | 3.098e-06
2012-11-11 | 283751 | ALY5 | Urban | LV Transformer SP1850-L ALY5 - Planned | 28.56 | 536 | 15308.16 | 0.015299 | 2.8542e-05
2012-11-11 | 283751 | BDA13A | Urban | LV Transformer SP1850-L ALY5 - Planned | 9.95 | 536 | 5333.2 | 0.0053299 | 9.9438e-06
2012-11-11 | 283753 | NMC1B | Rural short | LV Transformer SP753091 NMC1B - Planned | 3 | 405 | 1215 | 0.0034844 | 8.6035e-06
2012-11-11 | 283754 | RST8A | Urban | LV Transformer SP3358-B RST8A - Planned | 5.2 | 330 | 1716 | 0.0017149 | 5.1967e-06
2012-11-11 | 283763 | NMK17A | Urban | LV Transformer SP2630-L NMK17A - Planned | 34.1968 | 335 | 11455.928 | 0.011449 | 3.4175e-05
2012-11-12 | 283780 | JBB3A | Rural short | LV Transformer SP16272-C JBB3A - Planned | 1 | 230 | 230 | 0.00065925 | 2.8663e-06
2012-11-12 | 283803 | BDT3 | Rural short | LV Transformer SP2383-D BDT3 - Planned | 12 | 414 | 4968 | 0.01424 | 3.4396e-05
2012-11-12 | 283804 | SMF3A | Rural short | LV Transformer SP15752-E SMF3A - Planned | 2 | 120 | 240 | 0.00068791 | 5.7326e-06
2012-11-12 | 283807 | LLY1 | Rural short | Feeder LLY1 - Planned | 6 | 452 | 2712 | 0.0077734 | 1.7198e-05
2012-11-12 | 283808 | JDL5 | Urban | LV Transformer SP16652-F JDL5 - Planned | 1.5 | 413 | 619.5 | 0.00061918 | 1.4992e-06
2012-11-12 | 283810 | WFD5A | Rural short | LV Transformer SP5700-E WFD5A - Planned | 5.5 | 310 | 1705 | 0.0048871 | 1.5765e-05
2012-11-12 | 283811 | GYGGYS6 | Rural short | Feeder GYGGYS6 - Planned | 47.575 | 281 | 13368.575 | 0.038318 | 0.00013636
2012-11-12 | 283812 | ALY8 | Urban | LV Transformer SC2832-G ALY8 - Planned | 46.83 | 439 | 20558.37 | 0.020548 | 4.6806e-05
2012-11-12 | 283813 | MGL9 | Rural short | LV Transformer SP16118-G MGL9 - Planned | 2.97 | 95 | 282.15 | 0.00080873 | 8.5129e-06
2012-11-12 | 283814 | ENG7 | Urban | LV Transformer SP325-Q ENG7 - Planned | 26.33 | 341 | 8978.53 | 0.0089738 | 2.6316e-05
2012-11-12 | 283815 | SMR15A | Urban | LV Transformer SC22615-D SMR15A - Planned | 6.12 | 161 | 985.32 | 0.0009848 | 6.1168e-06
2012-11-12 | 283816 | CMD15A | Urban | LV Transformer SP7743-B CMD15A - Planned | 4.45 | 79 | 351.55 | 0.00035137 | 4.4477e-06
2012-11-12 | 283817 | GBN4 | Rural short | LV Transformer SP9357-B GBN4 - Planned | 2.125 | 60 | 127.5 | 0.00036545 | 6.0909e-06
2012-11-12 | 283818 | CMD15A | Urban | LV Transformer SP5349-A CMD15A - Planned | 2.55 | 242 | 617.1 | 0.00061678 | 2.5487e-06
2012-11-12 | 283818 | CMD7A | Rural short | LV Transformer SP5349-A CMD15A - Planned | 9 | 242 | 2178 | 0.0062428 | 2.5797e-05
2012-11-12 | 283819 | CMD15A | Urban | LV Transformer SP6574-A CMD15A - Planned | 5.705 | 70 | 399.35 | 0.00039914 | 5.702e-06
2012-11-12 | 283820 | LBH1B | Rural short | LV Transformer SP16491-B LBH1B - Planned | 6.83 | 338 | 2308.54 | 0.006617 | 1.9577e-05
2012-11-12 | 283824 | BHD35A | Rural short | LV Transformer SP5088-H BHD35A - Planned | 20 | 379 | 7580 | 0.021727 | 5.7326e-05
2012-11-12 | 283825 | MMC33A | Urban | LV Transformer SP2340-H MMC33A - Planned | 19.2 | 367 | 7046.4 | 0.0070427 | 1.919e-05
2012-11-12 | 283826 | SPO32A | Urban | LV Transformer SP2000-G SPO32A - Planned | 23.67 | 412 | 9752.04 | 0.0097469 | 2.3658e-05
2012-11-12 | 283827 | SGT24A | Urban | LV Transformer SP3873-D SGT24A - Planned | 25.91 | 242 | 6270.22 | 0.0062669 | 2.5896e-05
2012-11-12 | 283828 | BHL5A | Urban | LV Transformer SP3191-G BHL5A - Planned | 8.82 | 388 | 3422.16 | 0.0034204 | 8.8154e-06
2012-11-12 | 283829 | MTG13A | Urban | LV Transformer SC4045-I MTG13A - Planned | 4.7306 | 128 | 605.5168 | 0.0006052 | 4.7281e-06
2012-11-12 | 283830 | SPF12B | Urban | LV Transformer SC1413255 SPF12B - Planned | 11.08 | 60 | 664.8 | 0.00066445 | 1.1074e-05
2012-11-12 | 283831 | SPF12B | Urban | LV Transformer SC1376954 SPF12B - Planned | 26.64 | 91 | 2424.24 | 0.002423 | 2.6626e-05
2012-11-13 | 283862 | NIP4A | Rural short | LV Transformer SP4453-D NIP4A - Planned | 6.02 | 242 | 1456.84 | 0.0041744 | 1.725e-05
2012-11-13 | 283865 | MLY3 | Rural short | Feeder MLY3 - Planned | 45.01 | 312 | 14043.12 | 0.040239 | 0.00012897
2012-11-13 | 283866 | PWC4 | Rural short | LV Transformer SP504-A PWC4 - Planned | 11.04 | 50 | 552 | 0.0015817 | 3.1634e-05
2012-11-13 | 283867 | PWC4 | Rural short | LV Transformer SP4405-A PWC4 - Planned | 24 | 2 | 48 | 0.00013754 | 6.8769e-05
2012-11-13 | 283868 | CMD11A | Rural short | LV Transformer SP765796 CMD11A - Planned | 12.33 | 206 | 2539.98 | 0.007278 | 3.533e-05
2012-11-13 | 283869 | GBN2 | Rural short | LV Transformer SP6828-C GBN2 - Planned | 4 | 31 | 124 | 0.00035531 | 1.1462e-05
2012-11-13 | 283870 | KWH2 | Rural short | LV Transformer SP777838 KWH2 - Planned | 14.71 | 262 | 3854.02 | 0.011043 | 4.215e-05
2012-11-13 | 283871 | BDT4 | Rural short | Feeder BDT4 - Planned | 8.74 | 231 | 2018.94 | 0.005785 | 2.5043e-05
2012-11-13 | 283880 | MSV1 | Rural short | LV Transformer SP2805-C MSV1 - Planned | 6.02 | 325 | 1956.5 | 0.0056061 | 1.725e-05
2012-11-13 | 283881 | MSV1 | Rural short | Feeder MSV1 - Planned | 9.67 | 395 | 3819.65 | 0.010945 | 2.7708e-05
2012-11-13 | 283882 | CNB24A | Rural short | Feeder CNB24A - Planned | 25.755 | 386 | 9941.43 | 0.028486 | 7.3798e-05
2012-11-13 | 283883 | BRD8A | Rural short | LV Transformer SP5892-B BRD8A - Planned | 20.5 | 330 | 6765 | 0.019384 | 5.874e-05
2012-11-13 | 283900 | UPC1 | Rural short | Feeder UPC1 - Planned | 29 | 439 | 12731 | 0.036479 | 8.3096e-05
2012-11-13 | 283901 | GGR5 | Rural short | Feeder GGR5 - Planned | 4.5 | 565 | 2542.5 | 0.0072852 | 1.2894e-05
2012-11-13 | 283902 | ALY8 | Urban | LV Transformer SP2627-J HPK5A - Planned | 17.86 | 337 | 6018.82 | 0.0060161 | 1.7852e-05
2012-11-13 | 283902 | HPK5A | Urban | LV Transformer SP2627-J HPK5A - Planned | 8.4 | 337 | 2830.8 | 0.0028295 | 8.3961e-06
2012-11-13 | 283903 | ALY8 | Urban | LV Transformer SP1567-I ALY8 - Planned | 3.76 | 235 | 883.6 | 0.00088319 | 3.7583e-06
2012-11-13 | 283904 | ENG8 | Urban | LV Transformer SP1965-L ENG8 - Planned | 6.975 | 231 | 1611.225 | 0.0016105 | 6.9718e-06
2012-11-13 | 283905 | ENG9 | Urban | LV Transformer SP23751-E ENG9 - Planned | 8.9 | 160 | 1424 | 0.0014233 | 8.8959e-06
2012-11-13 | 283906 | VPK14A | Urban | LV Transformer SP4279-K VPK14A - Planned | 1.04 | 370 | 384.8 | 0.00038462 | 1.0395e-06
2012-11-13 | 283907 | CSE2 | Urban | LV Transformer SC4431-L CSE2 - Planned | 23.9876 | 410 | 9834.916 | 0.0098304 | 2.3977e-05
2012-11-13 | 283908 | BIS13A | Urban | LV Transformer SC1412540 BIS13A - Planned | 0.78 | 166 | 129.48 | 0.00012942 | 7.7964e-07
2012-11-13 | 283909 | TCB1 | Rural short | LV Transformer SP942-B TCB1 - Planned | 11.43 | 292 | 3337.56 | 0.0095634 | 3.2751e-05
2012-11-13 | 283910 | PWC6 | Rural short | LV Transformer SP3996-B PWC6 - Planned | 60.825 | 103 | 6264.975 | 0.017952 | 0.00017429
2012-11-13 | 283911 | LBH1B | Rural short | LV Transformer SP205069 LBH1B - Planned | 84.92 | 44 | 3736.48 | 0.010706 | 0.00024333
2012-11-13 | 283912 | JBB12B | Rural short | LV Transformer SP1377-F JBB12B - Planned | 1.155 | 355 | 410.025 | 0.0011749 | 3.3095e-06
2012-11-13 | 283913 | CRB25A | Rural short | LV Transformer SP5677-F CRB25A - Planned | 12.56 | 420 | 5275.2 | 0.015115 | 3.5989e-05
2012-11-13 | 283914 | BBH10A | Urban | LV Transformer SP2683-E BBH10A - Planned | 15.33 | 365 | 5595.45 | 0.0055929 | 1.5323e-05
2012-11-13 | 283915 | ARL13A | Urban | LV Transformer SC1437318 ARL13A - Planned | 6.13 | 72 | 441.36 | 0.00044116 | 6.1272e-06
2012-11-13 | 283916 | UPC1 | Rural short | LV Transformer SP4896-G UPC1 - Planned | 1.05 | 349 | 366.45 | 0.00105 | 3.0087e-06
2012-11-13 | 283917 | SMF3A | Rural short | LV Transformer SP5721-D SMF3A - Planned | 6 | 44 | 264 | 0.00075646 | 1.7192e-05
2012-11-13 | 283918 | DRD3A | Urban | LV Transformer SP4140-D DRD3A - Planned | 42.46 | 270 | 11464.2 | 0.011459 | 4.244e-05
2012-11-13 | 283919 | SGT24A | Urban | LV Transformer SC760407 SGT24A - Planned | 43.5 | 288 | 12528 | 0.012522 | 4.348e-05
2012-11-13 | 283920 | NDH7 | Urban | LV Transformer SP1294-L NDH7 - Planned | 2.88 | 280 | 806.4 | 0.00080603 | 2.8787e-06
2012-11-13 | 283921 | WSE3A | Rural short | LV Transformer SP240-H WSE3A - Planned | 4.98 | 300 | 1494 | 0.0042809 | 1.427e-05
2012-11-13 | 283922 | SGT6 | Urban | LV Transformer SP5470-G SGT6 - Planned | 9.9 | 360 | 3564 | 0.0035624 | 9.8954e-06
2012-11-13 | 283923 | HDA3A | Urban | LV Transformer SP1050781 HDA3A - Planned | 16.07 | 351 | 5640.57 | 0.005638 | 1.6063e-05
2012-11-13 | 283925 | CVL3A | Urban | LV Transformer SP4852-C CVL3A - Planned | 15.3 | 195 | 2983.5 | 0.0029821 | 1.5293e-05
2012-11-13 | 283926 | WRG6A | Urban | LV Transformer SP3614-J WRG6A - Planned | 32.9 | 274 | 9014.6 | 0.0090105 | 3.2885e-05
2012-11-13 | 283927 | MSV1 | Rural short | LV Transformer SP1919-D MSV1 - Planned | 1 | 52 | 52 | 0.000149 | 2.8654e-06
2012-11-13 | 283928 | SPF17B | Urban | LV Transformer SC21463-D SPF17B - Planned | 7.8932 | 40 | 315.728 | 0.00031558 | 7.8896e-06
2012-11-13 | 283929 | MWMRBK11 | Rural short | LV Transformer SP5149-F MWMRBK11 - Planned | 19.36 | 72 | 1393.92 | 0.0039941 | 5.5474e-05
2012-11-13 | 283930 | SPF17B | Urban | LV Transformer SC21465-C STC7 - Planned | 3.9466 | 105 | 414.393 | 0.0004142 | 3.9448e-06
2012-11-13 | 283930 | STC7 | Urban | LV Transformer SC21465-C STC7 - Planned | 5.4999 | 105 | 577.4895 | 0.00057722 | 5.4974e-06
2012-11-13 | 283931 | TGW3 | Rural short | LV Transformer SP4790-B TGW3 - Planned | 2.01 | 143 | 287.43 | 0.0008236 | 5.7594e-06
2012-11-13 | 283932 | MSV2 | Rural short | LV Transformer SP1301-D MSV2 - Planned | 5 | 120 | 600 | 0.0017192 | 1.4327e-05
2012-11-13 | 283935 | GYN3A | Rural short | Feeder GYN3A - Planned | 24.23 | 488 | 11824.24 | 0.033881 | 6.9428e-05
2012-11-13 | 283936 | NBR4 | Rural short | Feeder YDA3A, NBR4 - Planned | 38.54 | 560 | 21582.4 | 0.061842 | 0.00011043
2012-11-13 | 283936 | YDA3A | Rural short | Feeder YDA3A, NBR4 - Planned | 17.02 | 560 | 9531.2 | 0.027311 | 4.8769e-05
2012-11-14 | 283941 | IPL3 | Rural short | LV Transformer SP3667-A IPL3 - Planned | 3 | 187 | 561 | 0.0016069 | 8.5932e-06
2012-11-14 | 283960 | NRG13A | Urban | LV Transformer SP657830 NRG13A - Planned | 1 | 195 | 195 | 0.00019492 | 9.9961e-07
2012-11-14 | 283986 | MDR33A | Urban | LV Transformer SP733486 MDR33A - Planned | 47 | 285 | 13395 | 0.01339 | 4.6981e-05
2012-11-14 | 283990 | JBB3A | Rural short | LV Transformer SP4382-E JBB3A - Planned | 8.01 | 130 | 1041.3 | 0.0029827 | 2.2944e-05
2012-11-14 | 283994 | AGE8 | Urban | LV Transformer SP522108 AGE8 - Planned | 5.9815 | 176 | 1052.744 | 0.0010523 | 5.9791e-06
2012-11-14 | 283995 | AGE6A | Urban | LV Transformer SP13157-E AGE6A - Planned | 17.55 | 237 | 4159.35 | 0.0041577 | 1.7543e-05
2012-11-14 | 283996 | MLT2B | Urban | LV Transformer SP758047 MLT2B - Planned | 5.9 | 218 | 1286.2 | 0.0012857 | 5.8977e-06
2012-11-14 | 283997 | KRN18A | Urban | LV Transformer SC799525 KRN18A - Planned | 25.9672 | 354 | 9192.3888 | 0.0091888 | 2.5957e-05
2012-11-14 | 283997 | NMK17A | Urban | LV Transformer SC799525 KRN18A - Planned | 1.3907 | 354 | 492.3078 | 0.00049211 | 1.3902e-06
2012-11-14 | 283998 | CLM6 | Urban | LV Transformer SP3351-B CLM6 - Planned | 90.39 | 273 | 24676.47 | 0.024667 | 9.0354e-05
2012-11-14 | 283999 | CCY26A | Urban | LV Transformer SC1379997 CCY26A - Planned | 3.14 | 34 | 106.76 | 0.00010672 | 3.1388e-06
2012-11-14 | 284000 | MAI17 | Urban | LV Transformer SP4491-F MAI17 - Planned | 1.405 | 317 | 445.385 | 0.00044521 | 1.4044e-06
2012-11-14 | 284001 | JBB12B | Rural short | LV Transformer SP3965-D JBB12B - Planned | 0.96 | 60 | 57.6 | 0.00016499 | 2.7498e-06
2012-11-14 | 284002 | RCF2A | Urban | LV Transformer SP3418-B RCF2A - Planned | 43.065 | 340 | 14642.1 | 0.014636 | 4.3048e-05
2012-11-14 | 284003 | SGT7 | Urban | LV Transformer SP813851 SGT7 - Planned | 0.8 | 213 | 170.4 | 0.00017033 | 7.9968e-07
2012-11-14 | 284004 | ZMR5 | Urban | LV Transformer SP703-J ZMR5 - Planned | 4.96 | 221 | 1096.16 | 0.0010957 | 4.958e-06
2012-11-14 | 284005 | WRG6A | Urban | LV Transformer SP2113-M WRG6A - Planned | 10.665 | 160 | 1706.4 | 0.0017057 | 1.0661e-05
2012-11-14 | 284006 | ALY5 | Urban | LV Transformer SP676-L ALY5 - Planned | 20.16 | 354 | 7136.64 | 0.0071338 | 2.0152e-05
2012-11-14 | 284007 | KBR2A | Rural short | LV Transformer SP807-E KBR2A - Planned | 8.33 | 109 | 907.97 | 0.0026008 | 2.3861e-05
2012-11-14 | 284008 | YDA3A | Rural short | Feeder YDA3A - Planned | 64.505 | 405 | 26124.525 | 0.074831 | 0.00018477
2012-11-14 | 284009 | MLY1 | Rural short | Feeder MLY1 - Planned | 31.505 | 190 | 5985.95 | 0.017146 | 9.0243e-05
2012-11-14 | 284010 | GYN3A | Rural short | LV Transformer SP1174-C GYN3A - Planned | 7 | 74 | 518 | 0.0014838 | 2.0051e-05
2012-11-14 | 284012 | CMA8A | Rural short | Feeder CMA8A - Planned | 12 | 630 | 7560 | 0.021655 | 3.4373e-05
2012-11-14 | 284040 | JBB12B | Rural short | LV Transformer SP1376-G JBB12B - Planned | 0.4 | 333 | 133.2 | 0.00038154 | 1.1458e-06
2012-11-15 | 284060 | TGW3 | Rural short | LV Transformer SP4583-B TGW3 - Planned | 3 | 65 | 195 | 0.00055863 | 8.5944e-06
2012-11-15 | 284100 | CMY1 | Rural short | LV Transformer SP12648-A CMY1 - Planned | 2.345 | 194 | 454.93 | 0.0013033 | 6.7179e-06
2012-11-15 | 284101 | MCW7 | Rural short | LV Transformer SP2024-H MCW7 - Planned | 0.5 | 235 | 117.5 | 0.00033661 | 1.4324e-06
2012-11-15 | 284120 | TGW1 | Rural short | LV Transformer SP8061-A TGW1 - Planned | 6.02 | 111 | 668.22 | 0.0019143 | 1.7246e-05
2012-11-15 | 284121 | KLG10A | Urban | LV Transformer SP5879-B KLG10A - Planned | 1 | 375 | 375 | 0.00037499 | 9.9998e-07
2012-11-15 | 284122 | FDS1 | Rural short | Feeder FDS1 - Planned | 46.99 | 400 | 18796 | 0.053847 | 0.00013462
2012-11-15 | 284123 | MTB15A | Rural short | Feeder MTB15A - Planned | 13 | 345 | 4485 | 0.012849 | 3.7242e-05
2012-11-15 | 284125 | CNB24A | Rural short | Feeder CNB24A - Planned | 11 | 410 | 4510 | 0.01292 | 3.1513e-05
2012-11-15 | 284127 | MHL12A | Rural short | LV Transformer SC1827506 MHL12A - Planned | 4.1 | 272 | 1115.2 | 0.0031948 | 1.1746e-05
2012-11-15 | 284128 | ALY8 | Urban | LV Transformer SC2832-G ALY8 - Planned | 43.55 | 419 | 18247.45 | 0.018247 | 4.3549e-05
2012-11-15 | 284129 | AGE8 | Urban | LV Transformer SC2172-N - Planned | 20.8 | 325 | 6760 | 0.0067599 | 2.08e-05
2012-11-15 | 284130 | OXL8B | Urban | LV Transformer SP1264-H OXL8B - Planned | 14.95 | 230 | 3438.5 | 0.0034384 | 1.495e-05
2012-11-15 | 284131 | NMK7 | Urban | LV Transformer SP13798-H NMK7 - Planned | 1.96 | 356 | 697.76 | 0.00069775 | 1.96e-06
2012-11-15 | 284132 | KMR21A | Urban | LV Transformer SC1881-P KMR21A - Planned | 17.485 | 408 | 7133.88 | 0.0071337 | 1.7485e-05
2012-11-15 | 284133 | SMF5A | Rural short | LV Transformer SP3285-H SMF5A - Planned | 2.15 | 417 | 896.55 | 0.0025684 | 6.1593e-06
2012-11-15 | 284134 | GAP4A | Urban | LV Transformer SC22137-I GAP4A - Planned | 2.43 | 149 | 362.07 | 0.00036206 | 2.43e-06
2012-11-15 | 284135 | ENG9 | Urban | LV Transformer SP2412-N ENG9 - Planned | 21.45 | 230 | 4933.5 | 0.0049334 | 2.145e-05
2012-11-15 | 284136 | YDA5A | Rural short | LV Transformer SP3332-A YDA5A - Planned | 3.41 | 358 | 1220.78 | 0.0034973 | 9.7689e-06
2012-11-15 | 284137 | GYM2A | Rural short | LV Transformer SP4200-A GYM2A - Planned | 11.96 | 130 | 1554.8 | 0.0044542 | 3.4263e-05
2012-11-15 | 284138 | MLY1 | Rural short | LV Transformer SP13533-C MLY1 - Planned | 3 | 364 | 1092 | 0.0031284 | 8.5944e-06
2012-11-15 | 284139 | CMD15A | Urban | LV Transformer SP5228-A CMD15A - Planned | 111.72 | 269 | 30052.68 | 0.030052 | 0.00011172
2012-11-15 | 284140 | CNB24A | Rural short | LV Transformer SP3523-C CNB24A - Planned | 1.035 | 280 | 289.8 | 0.00083022 | 2.9651e-06
2012-11-15 | 284141 | LDR8 | Urban | LV Transformer SP468825 LDR8 - Planned | 19.05 | 396 | 7543.8 | 0.0075437 | 1.905e-05
2012-11-15 | 284142 | CRB25A | Rural short | LV Transformer SP5764-F CRB25A - Planned | 43.575 | 357 | 15556.275 | 0.044566 | 0.00012483
2012-11-15 | 284143 | BBH16A | Urban | LV Transformer SP8787-E BBH16A - Planned | 1.4933 | 58 | 86.6114 | 8.661e-05 | 1.4933e-06
2012-11-15 | 284144 | MDR3A | Urban | LV Transformer SC1270-I MDR3A - Planned | 2.16 | 26 | 56.16 | 5.6159e-05 | 2.16e-06
2012-11-15 | 284145 | BBH10A | Urban | LV Transformer SP61074-D BBH10A - Planned | 20.14 | 430 | 8660.2 | 0.00866 | 2.014e-05
2012-11-15 | 284146 | DRD3A | Urban | LV Transformer SP17290-C DRD3A - Planned | 15.55 | 210 | 3265.5 | 0.0032654 | 1.555e-05
2012-11-15 | 284147 | DRD3A | Urban | LV Transformer SP17290-C DRD3A - Planned | 15.55 | 320 | 4976 | 0.0049759 | 1.555e-05
2012-11-15 | 284148 | HDA3A | Urban | LV Transformer SP2760-J HDA3A - Planned | 40.29 | 324 | 13053.96 | 0.013054 | 4.0289e-05
2012-11-15 | 284150 | DRD3A | Urban | LV Transformer SP3418-B RCF2A - Planned | 8.715 | 392 | 3416.28 | 0.0034162 | 8.7148e-06
2012-11-15 | 284150 | RCF2A | Urban | LV Transformer SP3418-B RCF2A - Planned | 39.15 | 392 | 15346.8 | 0.015346 | 3.9149e-05
2012-11-15 | 284151 | HPE16A | Urban | LV Transformer SC4410-I HPE16A - Planned | 20.7648 | 330 | 6852.384 | 0.0068522 | 2.0764e-05
2012-11-15 | 284152 | BLBNFM6 | Urban | LV Transformer SP15-Q BLBNFM6 - Planned | 29.4 | 268 | 7879.2 | 0.007879 | 2.9399e-05
2012-11-15 | 284153 | NMC3A | Rural short | LV Transformer SP2927-L NMC3A - Planned | 17.15 | 268 | 4596.2 | 0.013167 | 4.9131e-05
2012-11-15 | 284154 | HPE5A | Urban | LV Transformer SP3420-I HPE5A - Planned | 6.7064 | 245 | 1643.068 | 0.001643 | 6.7063e-06
2012-11-15 | 284155 | TGW1 | Rural short | LV Transformer SP15671-B TGW1 - Planned | 6.02 | 126 | 758.52 | 0.002173 | 1.7246e-05
2012-11-15 | 284156 | MSV1 | Rural short | LV Transformer SP3013-C MSV1 - Planned | 3 | 327 | 981 | 0.0028104 | 8.5944e-06
2012-11-15 | 284157 | WSO13A | Rural short | LV Transformer SP3257-C WSO13A - Planned | 26.1637 | 475 | 12427.7575 | 0.035603 | 7.4954e-05
2012-11-15 | 284158 | FDS1 | Rural short | LV Transformer SP4189-C FDS1 - Planned | 7.04 | 401 | 2823.04 | 0.0080874 | 2.0168e-05
2012-11-15 | 284159 | THL3 | Rural short | LV Transformer SP1845-C THL3 - Planned | 2.625 | 319 | 837.375 | 0.0023989 | 7.5201e-06
2012-11-15 | 284160 | 341 | Urban | LV Transformer SP2306-D 341 - Planned | 0.75 | 11 | 16.5 | 1.65e-05 | 7.4999e-07
2012-11-15 | 284161 | KCY4 | Rural short | LV Transformer SP3175-D KCY4 - Planned | 1 | 90 | 90 | 0.00025783 | 2.8648e-06
2012-11-15 | 284162 | KCY2 | Rural short | Feeder KCY2 - Planned | 2.9 | 162 | 469.8 | 0.0013459 | 8.3079e-06
2012-11-15 | 284163 | KCY2 | Rural short | LV Transformer SP4695-E KCY2 - Planned | 1.25 | 42 | 52.5 | 0.0001504 | 3.581e-06
2012-11-15 | 284164 | PGN1B | Rural short | LV Transformer SP13447-C PGN1B - Planned | 7.04 | 227 | 1598.08 | 0.0045782 | 2.0168e-05
2012-11-15 | 284165 | KCY4 | Rural short | LV Transformer SP8267-E KCY4 - Planned | 9.5 | 80 | 760 | 0.0021772 | 2.7216e-05
2012-11-15 | 284166 | KCY4 | Rural short | Feeder KCY4 - Planned | 36 | 60 | 2160 | 0.006188 | 0.00010313
2012-11-16 | 284182 | NRA1A | Rural short | LV Transformer SP5657-C NRA1A - Planned | 1 | 80 | 80 | 0.00022922 | 2.8652e-06
2012-11-16 | 284183 | WSE5A | Rural short | Feeder WSE5A - Planned | 4 | 150 | 600 | 0.0017191 | 1.1461e-05
2012-11-16 | 284200 | GGR4 | Rural short | LV Transformer SP2088-E GGR4 - Planned | 1 | 244 | 244 | 0.00069911 | 2.8652e-06
2012-11-16 | 284201 | BTN2 | Rural short | Feeder BTN2 - Planned | 2 | 191 | 382 | 0.0010945 | 5.7304e-06
2012-11-16 | 284202 | PRG2B | Rural short | LV Transformer SP17576-A PRG2B - Planned | 3 | 208 | 624 | 0.0017879 | 8.5957e-06
2012-11-16 | 284203 | NIP5B | Urban | LV Transformer SP8563-B NIP5B - Planned | 23.43 | 136 | 3186.48 | 0.0031876 | 2.3438e-05
2012-11-16 | 284220 | KBR2A | Rural short | Feeder KBR2A - Planned | 30.42 | 336 | 10221.12 | 0.029286 | 8.716e-05
2012-11-16 | 284221 | PWC4 | Rural short | LV Transformer SP37555-A PWC4 - Planned | 16.5 | 83 | 1369.5 | 0.0039239 | 4.7276e-05
2012-11-16 | 284222 | WMR1 | Rural short | Feeder WMR1 - Planned | 62.476 | 196 | 12245.296 | 0.035085 | 0.00017901
2012-11-16 | 284224 | WMR3 | Rural short | Feeder WMR3 - Planned | 7.15 | 375 | 2681.25 | 0.0076824 | 2.0486e-05
2012-11-16 | 284225 | GYN7A | Rural short | LV Transformer SP12420-A GYN7A - Planned | 3.5 | 288 | 1008 | 0.0028881 | 1.0028e-05
2012-11-16 | 284227 | GBN4 | Rural short | LV Transformer SP11051-C GBN4 - Planned | 0.4 | 247 | 98.8 | 0.00028308 | 1.1461e-06
2012-11-16 | 284228 | NBR1 | Rural short | Feeder NBR1 - Planned | 18.93 | 198 | 3748.14 | 0.010739 | 5.4239e-05
2012-11-16 | 284229 | GBN4 | Rural short | LV Transformer SP2933-C GBN4 - Planned | 3 | 224 | 672 | 0.0019254 | 8.5957e-06
2012-11-16 | 284230 | WMR3 | Rural short | LV Transformer SP11841-D WMR3 - Planned | 1.5 | 81 | 121.5 | 0.00034812 | 4.2978e-06
2012-11-16 | 284231 | SMF5A | Rural short | Feeder SMF5A - Planned | 155.15 | 484 | 75092.6 | 0.21516 | 0.00044454
2012-11-16 | 284232 | ENG3 | Urban | LV Transformer SP6060-H ENG3 - Planned | 36 | 187 | 6732 | 0.0067344 | 3.6013e-05
2012-11-16 | 284233 | SMF5A | Rural short | LV Transformer SP3285-H SMF5A - Planned | 1.075 | 482 | 518.15 | 0.0014846 | 3.0801e-06
2012-11-16 | 284234 | NBR5 | Rural short | LV Transformer SP2837-A NBR5 - Planned | 24.96 | 201 | 5016.96 | 0.014375 | 7.1516e-05
2012-11-16 | 284235 | CMD5A | Urban | LV Transformer SP3463-A CMD5A - Planned | 7.47 | 86 | 642.42 | 0.00064265 | 7.4726e-06
2012-11-16 | 284236 | BBH10A | Urban | LV Transformer SP61074-D BBH10A - Planned | 18.02 | 299 | 5387.98 | 0.0053899 | 1.8026e-05
2012-11-16 | 284237 | CRBTHP14 | Urban | LV Transformer SC741-G CRBTHP14 - Planned | 9.35 | 92 | 860.2 | 0.0008605 | 9.3533e-06
2012-11-16 | 284238 | BLH12A | Rural short | LV Transformer SP4917-C BLH12A - Planned | 14.96 | 82 | 1226.72 | 0.0035148 | 4.2864e-05
2012-11-16 | 284239 | CRBTHP14 | Urban | LV Transformer SC741-G CRBTHP14 - Planned | 16.83 | 84 | 1413.72 | 0.0014142 | 1.6836e-05
2012-11-16 | 284240 | LDR8 | Urban | LV Transformer SP468825 LDR8 - Planned | 25.4 | 248 | 6299.2 | 0.0063014 | 2.5409e-05
2012-11-16 | 284241 | HDA3A | Urban | LV Transformer SP1050781 HDA3A - Planned | 36.18 | 301 | 10890.18 | 0.010894 | 3.6193e-05
2012-11-16 | 284242 | DRD13A | Urban | LV Transformer SP3177-D DRD13A - Planned | 74.755 | 261 | 19511.055 | 0.019518 | 7.4781e-05
2012-11-16 | 284243 | ACR3B | Urban | LV Transformer SC22704-B ACR3B - Planned | 42.57 | 86 | 3661.02 | 0.0036623 | 4.2585e-05
2012-11-16 | 284244 | RCF2A | Urban | LV Transformer SP4918-F RCF2A - Planned | 9.225 | 297 | 2739.825 | 0.0027408 | 9.2283e-06
2012-11-16 | 284245 | SGT5 | Urban | LV Transformer SP4392-F SGT5 - Planned | 55.07 | 241 | 13271.87 | 0.013277 | 5.5089e-05
2012-11-16 | 284246 | HPE5A | Urban | LV Transformer SP3420-I HPE5A - Planned | 19.2809 | 234 | 4511.7306 | 0.0045133 | 1.9288e-05
2012-11-16 | 284247 | CMV14 | Urban | LV Transformer SP2409-O CMV14 - Planned | 24.93 | 200 | 4986 | 0.0049878 | 2.4939e-05
2012-11-16 | 284254 | SFD6B | Urban | LV Transformer SP2811-J SFD6B - Planned | 8.82 | 257 | 2266.74 | 0.0022675 | 8.8231e-06
2012-11-17 | 284357 | AFD3A | Urban | LV Transformer SG11614-J AFD3A - Planned | 0.16 | 112 | 17.92 | 1.7933e-05 | 1.6012e-07
2012-11-19 | 284671 | MWMRBK11 | Rural short | LV Transformer SP1386-F MWMRBK11 - Planned | 70.5 | 182 | 12831 | 0.036779 | 0.00020208
2012-11-19 | 284673 | NGE4B | Urban | LV Transformer SP3130-E NGE4B - Planned | 28 | 385 | 10780 | 0.010796 | 2.8041e-05
2012-11-19 | 284683 | NMK17A | Urban | LV Transformer SP773473 NMK17A - Planned | 4.8283 | 239 | 1153.9637 | 0.0011557 | 4.8355e-06
2012-11-19 | 284684 | MLB6A | Rural short | LV Transformer SP9776-A MLB6A - Planned | 3.33 | 228 | 759.24 | 0.0021763 | 9.5451e-06
2012-11-19 | 284685 | DRD3A | Urban | LV Transformer SP5772-C DRD3A - Planned | 35.2 | 195 | 6864 | 0.0068742 | 3.5252e-05
2012-11-19 | 284685 | SBH13A | Urban | LV Transformer SP5772-C DRD3A - Planned | 16.38 | 195 | 3194.1 | 0.0031988 | 1.6404e-05
2012-11-19 | 284686 | NGE4B | Urban | LV Transformer SP678-L NGE4B - Planned | 21.36 | 397 | 8479.92 | 0.0084925 | 2.1392e-05
2012-11-19 | 284687 | ALY8 | Urban | LV Transformer SC796205-A ALY8 - Planned | 20.295 | 426 | 8645.67 | 0.0086585 | 2.0325e-05
2012-11-19 | 284688 | HPE5A | Urban | LV Transformer SP3350-G HPE5A - Planned | 1.935 | 207 | 400.545 | 0.00040114 | 1.9379e-06
2012-11-19 | 284689 | ALY8 | Urban | LV Transformer SP2940-H ALY8 - Planned | 5.61 | 346 | 1941.06 | 0.0019439 | 5.6183e-06
2012-11-19 | 284690 | CHL8 | Urban | LV Transformer SC1063943 CHL8 - Planned | 7.44 | 308 | 2291.52 | 0.0022949 | 7.451e-06
2012-11-19 | 284700 | GYM7A | Rural short | Feeder GYM7A - Planned | 28.94 | 261 | 7553.34 | 0.021651 | 8.2954e-05
2012-11-20 | 284734 | MFD12A | Urban | LV Transformer SC1366463 MFD12A - Planned | 57 | 96 | 5472 | 0.0054822 | 5.7106e-05
2012-11-20 | 284735 | MBG2 | Rural short | LV Transformer SP425084 MBG2 - Planned | 5 | 76 | 380 | 0.0010894 | 1.4334e-05
2012-11-20 | 284746 | DRD3A | Urban | LV Transformer SP4998-E DRD3A - Planned | 3.8019 | 156 | 593.0964 | 0.0005942 | 3.809e-06
2012-11-20 | 284766 | AMR2 | Rural short | LV Transformer SP9340-A AMR2 - Planned | 2.01 | 158 | 317.58 | 0.00091044 | 5.7623e-06
2012-11-20 | 284767 | LBH6A | Rural short | Feeder LBH6A - Planned | 93 | 268 | 24924 | 0.071452 | 0.00026661
2012-11-20 | 284769 | NRA16A | Rural short | LV Transformer SP4144-E NRA16A - Planned | 23.04 | 256 | 5898.24 | 0.016909 | 6.6051e-05
2012-11-20 | 284774 | SMF2A | Rural short | LV Transformer SP2811-E SMF2A - Planned | 16 | 64 | 1024 | 0.0029356 | 4.5869e-05
2012-11-20 | 284776 | LWD1 | Rural short | LV Transformer SP7990-A LWD1 - Planned | 1 | 180 | 180 | 0.00051603 | 2.8668e-06
2012-11-20 | 284786 | LLY1 | Rural short | LV Transformer SP1895-C LLY1 - Planned | 0.99 | 309 | 305.91 | 0.00087699 | 2.8381e-06
2012-11-20 | 284793 | SMF2A | Rural short | Feeder SMF2A - Planned | 108.759 | 186 | 20229.174 | 0.057993 | 0.00031179
2012-11-20 | 284795 | WSE3A | Rural short | LV Transformer SP4988-G WSE3A - Planned | 4.15 | 68 | 282.2 | 0.00080901 | 1.1897e-05
2012-11-20 | 284796 | JBB16A | Rural short | LV Transformer SP6086-C JBB16A - Planned | 0.4 | 358 | 143.2 | 0.00041053 | 1.1467e-06
2012-11-20 | 284800 | ALY8 | Urban | LV Transformer SP30341-B ALY8 - Planned | 27.9419 | 333 | 9304.6527 | 0.0093219 | 2.7994e-05
2012-11-20 | 284801 | GAP9A | Urban | LV Transformer SP2887-N GAP9A - Planned | 12.49 | 309 | 3859.41 | 0.0038666 | 1.2513e-05
2012-11-20 | 284802 | CLD28A | Rural short | LV Transformer SP3467-A CLD28A - Planned | 19.52 | 367 | 7163.84 | 0.020537 | 5.596e-05
2012-11-20 | 284803 | CBT8A | Rural short | LV Transformer SC21073-C CBT8A - Planned | 9.17 | 171 | 1568.07 | 0.0044954 | 2.6289e-05
2012-11-20 | 284804 | WMD14A | Rural short | LV Transformer SP2819-A WMD14A - Planned | 15.93 | 232 | 3695.76 | 0.010595 | 4.5668e-05
2012-11-20 | 284805 | BBH10A | Urban | LV Transformer SP2684-E BBH10A - Planned | 19.04 | 390 | 7425.6 | 0.0074394 | 1.9075e-05
2012-11-20 | 284806 | JBB16A | Rural short | LV Transformer SP5422-D JBB16A - Planned | 17.5 | 367 | 6422.5 | 0.018412 | 5.0169e-05
2012-11-20 | 284807 | LDR8 | Urban | LV Transformer SP2853-E LDR8 - Planned | 29.4 | 370 | 10878 | 0.010898 | 2.9455e-05
2012-11-20 | 284808 | BHD35A | Rural short | LV Transformer SP4557-E BHD35A - Planned | 5.075 | 293 | 1486.975 | 0.0042629 | 1.4549e-05
2012-11-20 | 284809 | MGP13A | Rural short | Feeder MGP13A - Planned | 2 | 398 | 796 | 0.002282 | 5.7336e-06
2012-11-20 | 284810 | CRB25A | Rural short | LV Transformer SP5797-E CRB25A - Planned | 6.2054 | 272 | 1687.8688 | 0.0048388 | 1.779e-05
2012-11-20 | 284812 | SMF2A | Rural short | LV Transformer SP3567-E SMF2A - Planned | 8.01 | 95 | 760.95 | 0.0021815 | 2.2963e-05
2012-11-20 | 284813 | SMF2A | Rural short | LV Transformer SP1368803 SMF2A - Planned | 2.016 | 142 | 286.272 | 0.00082069 | 5.7795e-06
2012-11-20 | 284814 | SGT24A | Urban | LV Transformer SP39457-D SGT24A - Planned | 15.36 | 242 | 3717.12 | 0.003724 | 1.5388e-05
2012-11-20 | 284815 | CVL3A | Urban | LV Transformer SC1516-E CVL3A - Planned | 106.56 | 337 | 35910.72 | 0.035977 | 0.00010676
2012-11-20 | 284816 | CPB4 | Urban | LV Transformer SP3547-C CPB9 - Planned | 24.215 | 281 | 6804.415 | 0.006817 | 2.426e-05
2012-11-20 | 284817 | QEN10 | Urban | LV Transformer SC4802-I QEN10 - Planned | 28.595 | 290 | 8292.55 | 0.0083079 | 2.8648e-05
2012-11-20 | 284818 | SPF15A | Urban | LV Transformer SC635008 SPF15A - Planned | 5 | 62 | 310 | 0.00031058 | 5.0093e-06
2012-11-20 | 284819 | SPF17B | Urban | LV Transformer SC428194 SPF17B - Planned | 0.8666 | 40 | 34.664 | 3.4728e-05 | 8.6821e-07
2012-11-20 | 284820 | KBR1A | Rural short | LV Transformer SP1068-G KBR1A - Planned | 8.01 | 249 | 1994.49 | 0.0057178 | 2.2963e-05
2012-11-20 | 284821 | LGV6A | Rural short | LV Transformer SP5429-C LGV6A - Planned | 3.185 | 100 | 318.5 | 0.00091308 | 9.1308e-06
2012-11-20 | 284823 | CRB25A | Rural short | Feeder CRB25A - Planned | 48.625 | 480 | 23340 | 0.066911 | 0.0001394
2012-11-20 | 284825 | PPE5A | Rural short | Feeder PPE5A - Planned | 7.98 | 423 | 3375.54 | 0.009677 | 2.2877e-05
2012-11-20 | 284827 | KBN13A | Rural short | Feeder KBN13A - Planned | 18.02 | 450 | 8109 | 0.023247 | 5.166e-05
2012-11-20 | 284866 | BMT2 | Rural short | LV Transformer SP2889-C BMT2 - Planned | 3.32 | 80 | 265.6 | 0.00076142 | 9.5178e-06
2012-11-20 | 284869 | EMD2 | Rural short | LV Transformer SP2263-A EMD2 - Planned | 0.335 | 345 | 115.575 | 0.00033133 | 9.6038e-07
2012-11-20 | 284870 | MLY3 | Rural short | LV Transformer SP2998-B MLY3 - Planned | 16.92 | 130 | 2199.6 | 0.0063058 | 4.8506e-05
2012-11-20 | 284871 | GYGGYS6 | Rural short | LV Transformer SP553-B GYGGYS6 - Planned | 3 | 217 | 651 | 0.0018663 | 8.6004e-06
2012-11-20 | 284912 | HDA11A | Urban | LV Transformer SC6523-E HDA11A - Planned | 12.1 | 340 | 4114 | 0.0041216 | 1.2122e-05
2012-11-21 | 284873 | WMR1 | Rural short | Feeder WMR1 - Planned | 11.2 | 188 | 2105.6 | 0.0060372 | 3.2113e-05
2012-11-21 | 284874 | WMR1 | Rural short | Feeder WMR1 - Planned | 8.01 | 187 | 1497.87 | 0.0042947 | 2.2966e-05
2012-11-21 | 284880 | BNH1B | Rural short | Feeder BNH1B - Planned | 40.65 | 216 | 8780.4 | 0.025175 | 0.00011655
2012-11-21 | 284890 | SMF5A | Rural short | LV Transformer SP16054-F SMF5A - Planned | 1 | 103 | 103 | 0.00029532 | 2.8672e-06
2012-11-21 | 284900 | NDH9 | Urban | LV Transformer SC2076316 NDH9 - Planned | 2.067 | 225 | 465.075 | 0.00046611 | 2.0716e-06
2012-11-21 | 284901 | HPE16A | Urban | LV Transformer SC4410-I HPE16A - Planned | 20.9248 | 355 | 7428.304 | 0.0074449 | 2.0971e-05
2012-11-21 | 284902 | HPE5A | Urban | LV Transformer SP3350-G HPE5A - Planned | 17.415 | 108 | 1880.82 | 0.001885 | 1.7454e-05
2012-11-21 | 284903 | RCN8A | Urban | LV Transformer SC5207-N RCN8A - Planned | 1.9 | 143 | 271.7 | 0.00027231 | 1.9042e-06
2012-11-21 | 284904 | KBN1B | Rural short | LV Transformer SC1825963 KBN1B - Planned | 1 | 55 | 55 | 0.0001577 | 2.8672e-06
2012-11-21 | 284905 | KMR21A | Urban | LV Transformer SC4346-K KMR21A - Planned | 6.885 | 80 | 550.8 | 0.00055203 | 6.9004e-06
2012-11-21 | 284906 | KMR21A | Urban | LV Transformer SC6333-E KMR21A - Planned | 15.84 | 320 | 5068.8 | 0.0050801 | 1.5875e-05
2012-11-21 | 284907 | DRA9 | Urban | LV Transformer SP11467-F DRA9 - Planned | 26.27 | 192 | 5043.84 | 0.0050551 | 2.6329e-05
2012-11-21 | 284908 | GYN2B | Urban | LV Transformer SP2159-C GYN2B - Planned | 1.08 | 91 | 98.28 | 9.8499e-05 | 1.0824e-06
2012-11-21 | 284909 | KWA2A | Urban | LV Transformer SP5266-A KWA2A - Planned | 24.75 | 80 | 1980 | 0.0019844 | 2.4805e-05
2012-11-21 | 284910 | AMR3 | Rural short | LV Transformer SP776685 AMR3 - Planned | 2.5 | 165 | 412.5 | 0.0011827 | 7.168e-06
2012-11-21 | 284911 | CNB24A | Rural short | LV Transformer SP2656-E CNB24A - Planned | 4.095 | 243 | 995.085 | 0.0028531 | 1.1741e-05
2012-11-21 | 284913 | NIP1A | Urban | LV Transformer SP3202-E NIP1A - Planned | 39.4723 | 185 | 7302.3755 | 0.0073187 | 3.956e-05
2012-11-21 | 284914 | WRG15A | Urban | LV Transformer SP3249-E WRG15A - Planned | 29.42 | 253 | 7443.26 | 0.0074599 | 2.9486e-05
2012-11-21 | 284915 | MLY6 | Rural short | Feeder MLY6 - Planned | 38.52 | 308 | 11864.16 | 0.034017 | 0.00011044
2012-11-21 | 284916 | AMR2 | Rural short | LV Transformer SP1422-E AMR2 - Planned | 2.01 | 310 | 623.1 | 0.0017866 | 5.7631e-06
2012-11-21 | 284917 | PWC4 | Rural short | Feeder PWC4 - Planned | 54.67 | 396 | 21649.32 | 0.062073 | 0.00015675
2012-11-21 | 284918 | NBR8 | Rural short | LV Transformer SP2514-A NBR8 - Planned | 17 | 40 | 680 | 0.0019497 | 4.8742e-05
2012-11-21 | 284919 | NVL3 | Rural short | LV Transformer SC1370682 NVL3 - Planned | 44 | 190 | 8360 | 0.02397 | 0.00012616
2012-11-21 | 284920 | GYM2A | Rural short | Feeder GYM2A - Planned | 64.895 | 143 | 9279.985 | 0.026608 | 0.00018607
2012-11-21 | 284921 | MLY1 | Rural short | LV Transformer SP988-B MLY1 - Planned | 0.4 | 317 | 126.8 | 0.00036356 | 1.1469e-06
2012-11-21 | 284924 | BHD23A | Rural short | LV Transformer SP5771-G BHD23A - Planned | 28 | 480 | 13440 | 0.038535 | 8.0282e-05
2012-11-21 | 284925 | MGP13A | Rural short | LV Transformer SP5168-F MGP13A - Planned | 6 | 390 | 2340 | 0.0067093 | 1.7203e-05
2012-11-21 | 284926 | CNB24A | Rural short | Feeder CNB24A - Planned | 22.5 | 431 | 9697.5 | 0.027805 | 6.4512e-05
2012-11-21 | 284928 | NMK5 | Urban | LV Transformer SP11193-G NMK5 - Planned | 3.84 | 250 | 960 | 0.00096214 | 3.8486e-06
2012-11-21 | 284929 | ALY8 | Urban | LV Transformer SC2832-G ALY8 - Planned | 13.725 | 455 | 6244.875 | 0.0062588 | 1.3756e-05
2012-11-21 | 284930 | KRN10 | Urban | LV Transformer SP1515-P KRN10 - Planned | 19.37 | 294 | 5694.78 | 0.0057075 | 1.9413e-05
2012-11-21 | 284931 | PGN1B | Rural short | LV Transformer SP6733-A PGN1B - Planned | 34.32 | 276 | 9472.32 | 0.027159 | 9.8402e-05
2012-11-21 | 284932 | BBH8A | Urban | LV Transformer SP2869-H BBH8A - Planned | 17.8 | 385 | 6853 | 0.0068683 | 1.784e-05
2012-11-21 | 284933 | MBG2 | Rural short | Feeder MBG2 - Planned | 34.03 | 640 | 21779.2 | 0.062445 | 9.7571e-05
2012-11-21 | 284934 | WSE6A | Rural short | LV Transformer SP8356-D WSE6A - Planned | 27.16 | 217 | 5893.72 | 0.016898 | 7.7873e-05
2012-11-21 | 284964 | DBS16A | Urban | LV Transformer SC493979 MRE1 - Planned | 3.16 | 262 | 827.92 | 0.00082977 | 3.1671e-06
2012-11-21 | 284964 | MRE1 | Urban | LV Transformer SC493979 MRE1 - Planned | 1.0598 | 262 | 277.6676 | 0.00027829 | 1.0622e-06
2012-11-21 | 284989 | DBS16A | Urban | LV Transformer SC751473 DBS16A - Planned | 3.16 | 262 | 827.92 | 0.00082977 | 3.1671e-06
2012-11-21 | 284989 | MRE1 | Urban | LV Transformer SC751473 DBS16A - Planned | 1.0598 | 262 | 277.6676 | 0.00027829 | 1.0622e-06
2012-11-21 | 285042 | THL2 | Rural short | LV Transformer SP2269-D THL2 - Planned | 0.75 | 379 | 284.25 | 0.000815 | 2.1504e-06
2012-11-21 | 285046 | KCY5 | Rural short | Feeder KCY5 - Planned | 121.54 | 27.5385 | 1944.64 | 0.0055757 | 0.00034848
2012-11-21 | 285048 | JBB12B | Rural short | Feeder JBB12B - Planned | 52.09 | 355 | 18491.95 | 0.05302 | 0.00014935
2012-11-22 | 284963 | SMF2A | Rural short | LV Transformer SP5705-D SMF2A - Planned | 17.39 | 66 | 1147.74 | 0.0032912 | 4.9867e-05
2012-11-22 | 284966 | CNB24A | Rural short | LV Transformer SP10852-B CNB24A - Planned | 0.5 | 144 | 72 | 0.00020647 | 1.4338e-06
2012-11-22 | 284967 | BBSRDL8 | Rural short | LV Transformer SP2939-I BBSRDL8 - Planned | 3 | 130 | 390 | 0.0011184 | 8.6028e-06
2012-11-22 | 284969 | IPL2 | Rural short | LV Transformer SP6747-C IPL2 - Planned | 2.5 | 372 | 930 | 0.0026669 | 7.169e-06
2012-11-22 | 284970 | TGW1 | Rural short | Feeder TGW1 - Planned | 49 | 409 | 20041 | 0.057469 | 0.00014051
2012-11-22 | 284971 | SMF2A | Rural short | Feeder SMF2A - Planned | 11 | 220 | 2420 | 0.0069396 | 3.1544e-05
2012-11-22 | 284972 | GYM7A | Rural short | Feeder GYM7A - Planned | 26.1 | 408 | 10648.8 | 0.030536 | 7.4844e-05
2012-11-22 | 284973 | NBR8 | Rural short | Feeder NBR8 - Planned | 27.8 | 336 | 9340.8 | 0.026786 | 7.9719e-05
2012-11-22 | 284974 | NVL10 | Urban | LV Transformer SP5994-B NVL10 - Planned | 46.725 | 107 | 4999.575 | 0.0050126 | 4.6847e-05
2012-11-22 | 284975 | KCY2 | Rural short | Feeder KCY2 - Planned | 59.4775 | 433 | 25753.7575 | 0.073851 | 0.00017056
2012-11-22 | 284981 | KSN5 | Rural short | LV Transformer SP808548 KSN5 - Planned | 7.02 | 238 | 1670.76 | 0.0047911 | 2.013e-05
2012-11-22 | 284983 | MFD8A | Rural short | LV Transformer SP1466271 MFD8A - Planned | 3.24 | 75 | 243 | 0.00069682 | 9.291e-06
2012-11-22 | 284984 | NMK7 | Urban | LV Transformer SP4089-K NMK7 - Planned | 15.3 | 348 | 5324.4 | 0.0053383 | 1.534e-05
2012-11-22 | 284985 | HDA3A | Urban | LV Transformer SP1050781 HDA3A - Planned | 12.06 | 240 | 2894.4 | 0.002902 | 1.2091e-05
2012-11-22 | 284986 | CMD15A | Urban | LV Transformer SP5226-A CMD15A - Planned | 34.88 | 177 | 6173.76 | 0.0061899 | 3.4971e-05
2012-11-22 | 284987 | DRD3A | Urban | LV Transformer SP778006 DRD3A - Planned | 63.14 | 275 | 17363.5 | 0.017409 | 6.3305e-05
2012-11-22 | 284988 | LBH1B | Rural short | LV Transformer SP782127 LBH1B - Planned | 54.18 | 398 | 21563.64 | 0.061836 | 0.00015537
2012-11-22 | 284990 | NGI2B | Rural short | LV Transformer SP17098-D NGI2B - Planned | 22.035 | 164 | 3613.74 | 0.010363 | 6.3187e-05
2012-11-22 | 284991 | HPE5A | Urban | LV Transformer SP3350-G HPE5A - Planned | 15.41 | 75 | 1155.75 | 0.0011588 | 1.545e-05
2012-11-22 | 284992 | HPE5A | Urban | LV Transformer SP493148 HPE5A - Planned | 9.6664 | 368 | 3557.2352 | 0.0035665 | 9.6916e-06
2012-11-22 | 284993 | OXL8B | Urban | LV Transformer SP1264-H OXL8B - Planned | 2.99 | 345 | 1031.55 | 0.0010342 | 2.9978e-06
2012-11-22 | 284994 | QGP4 | Urban | LV Transformer SC763568-A QGP4 - Planned | 20.24 | 108 | 2185.92 | 0.0021916 | 2.0293e-05
2012-11-22 | 284994 | WRD13B | Urban | LV Transformer SC763568-A QGP4 - Planned | 10.01 | 108 | 1081.08 | 0.0010839 | 1.0036e-05
2012-11-22 | 284995 | PDB13 | Urban | LV Transformer SC2052903 PDB13 - Planned | 6.24 | 100 | 624 | 0.00062563 | 6.2563e-06
2012-11-22 | 284996 | WHO1 | Rural short | LV Transformer SP68267-A WHO1 - Planned | 12.4 | 120 | 1488 | 0.004267 | 3.5558e-05
2012-11-22 | 284997 | BBH10A | Urban | LV Transformer SP2684-E BBH10A - Planned | 17.68 | 415 | 7337.2 | 0.0073563 | 1.7726e-05
2012-11-22 | 284997 | MMC33A | Urban | LV Transformer SP2684-E BBH10A - Planned | 0.84 | 415 | 348.6 | 0.00034951 | 8.4219e-07
2012-11-22 | 284998 | GVN16A | Rural short | LV Transformer SP6422-C GVN16A - Planned | 9.9 | 340 | 3366 | 0.0096523 | 2.8389e-05
2012-11-22 | 284999 | MDR33A | Urban | LV Transformer SP3712-F MDR33A - Planned | 13.6 | 434 | 5902.4 | 0.0059178 | 1.3635e-05
2012-11-22 | 285000 | BHD7A | Urban | LV Transformer SC2336-E BHD7A - Planned | 19.855 | 80 | 1588.4 | 0.0015925 | 1.9907e-05
2012-11-22 | 285001 | CRBTHP14 | Urban | LV Transformer SP567555 CRBTHP14 - Planned | 19.0753 | 397 | 7572.8941 | 0.0075927 | 1.9125e-05
2012-11-22 | 285001 | CRBTHP26 | Urban | LV Transformer SP567555 CRBTHP14 - Planned | 38.321 | 397 | 15213.437 | 0.015253 | 3.8421e-05
2012-11-22 | 285002 | WNM5 | Urban | LV Transformer SC759826 WNM5 - Planned | 5 | 125.5 | 852.62 | 0.00085484 | 5.013e-06
2012-11-22 | 285003 | CSE21A | Urban | LV Transformer SC743459 CSE21A - Planned | 7.8866 | 100 | 788.66 | 0.00079072 | 7.9072e-06
2012-11-22 | 285049 | GBN4 | Rural short | LV Transformer SP998-D GBN4 - Planned | 9 | 230 | 2070 | 0.0059359 | 2.5808e-05
2012-11-22 | 285050 | WMR2 | Rural short | LV Transformer SP2374-H WMR2 - Planned | 1 | 69 | 69 | 0.00019786 | 2.8676e-06
2012-11-22 | 285075 | HDA11A | Urban | LV Transformer SC5007-F HDA11A - Planned | 9.845 | 122 | 1201.09 | 0.0012042 | 9.8707e-06
2012-11-23 | 285038 | WFD2B | Rural short | Feeder WFD2B - Planned | 13 | 229 | 2977 | 0.008538 | 3.7284e-05
2012-11-23 | 285051 | TGW1 | Rural short | LV Transformer SP2267-D TGW1 - Planned | 1 | 209 | 209 | 0.00059941 | 2.868e-06
2012-11-23 | 285060 | MCN3 | Urban | LV Transformer SP5527-D MCN3 - Planned | 0.5 | 350 | 175 | 0.00017552 | 5.0149e-07
2012-11-23 | 285061 | KBR6A | Rural short | LV Transformer SP8217-B KBR6A - Planned | 3 | 360 | 1080 | 0.0030974 | 8.604e-06
2012-11-23 | 285062 | HPK5A | Urban | LV Transformer SP2622-N HPK5A - Planned | 5.25 | 131 | 687.75 | 0.00068981 | 5.2657e-06
2012-11-23 | 285063 | ALY8 | Urban | LV Transformer SP3426-E ALY8 - Planned | 6.03 | 313 | 1887.39 | 0.001893 | 6.048e-06
2012-11-23 | 285064 | MFD8A | Rural short | LV Transformer SP1466271 MFD8A - Planned | 4.92 | 153 | 752.76 | 0.0021589 | 1.4111e-05
2012-11-23 | 285065 | GAP1A | Urban | LV Transformer SC4187-I GAP1A - Planned | 15.95 | 36 | 574.2 | 0.00057592 | 1.5998e-05
2012-11-23 | 285066 | MLB12A | Rural short | LV Transformer SP57408-A MLB12A - Planned | 57.78 | 64 | 3697.92 | 0.010606 | 0.00016571
2012-11-23 | 285067 | AHD8 | Urban | LV Transformer SC175726 AHD8 - Planned | 1 | 32 | 32 | 3.2096e-05 | 1.003e-06
2012-11-23 | 285068 | PGN1B | Rural short | LV Transformer SP3531-A PGN1B - Planned | 13.09 | 174 | 2277.66 | 0.0065323 | 3.7542e-05
2012-11-23 | 285069 | GYM7A | Rural short | LV Transformer SP3930-C GYM7A - Planned | 7.5 | 64 | 480 | 0.0013766 | 2.151e-05
2012-11-23 | 285070 | AHD20 | Urban | LV Transformer SG264-A AHD20 - Planned | 50.05 | 60 | 3003 | 0.003012 | 5.02e-05
2012-11-23 | 285071 | BBH10A | Urban | LV Transformer SP61074-D BBH10A - Planned | 19.08 | 374 | 7135.92 | 0.0071573 | 1.9137e-05
2012-11-23 | 285072 | LDR5 | Urban | LV Transformer SP2198-I LDR5 - Planned | 25.11 | 121 | 3038.31 | 0.0030474 | 2.5185e-05
2012-11-23 | 285073 | CBW10 | Rural short | LV Transformer SC2765-H CBW10 - Planned | 3.92 | 300 | 1176 | 0.0033728 | 1.1243e-05
2012-11-23 | 285074 | HTN24A | Urban | LV Transformer SP740267 HTN24A - Planned | 20.33 | 271 | 5509.43 | 0.0055259 | 2.0391e-05
2012-11-23 | 285077 | HDA3A | Urban | LV Transformer SP1410448 HDA3A - Planned | 2 | 335 | 670 | 0.000672 | 2.006e-06
2012-11-23 | 285078 | CVL3A | Urban | LV Transformer SP6786-D CVL3A - Planned | 9 | 110 | 990 | 0.00099296 | 9.0269e-06
2012-11-23 | 285079 | RCN3A | Urban | LV Transformer SC4800-J RCN3A - Planned | 19.14 | 330 | 6316.2 | 0.0063351 | 1.9197e-05
2012-11-23 | 285080 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 44.2341 | 293 | 12960.5913 | 0.012999 | 4.4366e-05
2012-11-23 | 285081 | TGW1 | Rural short | LV Transformer SP1346-C TGW1 - Planned | 1.25 | 247 | 308.75 | 0.00088549 | 3.585e-06
2012-11-23 | 285082 | CBW10 | Rural short | Feeder CBW10 - Planned | 4.5 | 413 | 1858.5 | 0.0053302 | 1.2906e-05
2012-11-23 | 285083 | GBN3 | Rural short | LV Transformer SP2558-D GBN3 - Planned | 1 | 70 | 70 | 0.00020076 | 2.868e-06
2012-11-23 | 285084 | EMD3 | Rural short | Feeder EMD3 - Planned | 38 | 286 | 10868 | 0.031169 | 0.00010898
2012-11-23 | 285095 | BPN4 | Urban | LV Transformer SP493453 BPN4 - Planned | 3 | 346 | 1038 | 0.0010411 | 3.009e-06
2012-11-23 | 287525 | SMF2A | Rural short | Feeder SMF2A - Planned | 111.7619 | 39 | 4358.7141 | 0.012501 | 0.00032053
2012-11-24 | 285102 | KBR6A | Rural short | Feeder KBR6A - Planned | 9.15 | 275 | 2516.25 | 0.0072175 | 2.6245e-05
2012-11-24 | 285105 | VPK9A | Urban | LV Transformer SP522158 VPK9A - Planned | 1.96 | 135 | 264.6 | 0.00026549 | 1.9666e-06
2012-11-24 | 285106 | GYM2A | Rural short | LV Transformer SP4206-A GYM2A - Planned | 3.375 | 44 | 148.5 | 0.00042595 | 9.6807e-06
2012-11-24 | 285107 | HDA14A | Urban | LV Transformer SP1080-I HDA14A - Planned | 1.02 | 464 | 473.28 | 0.00047488 | 1.0234e-06
2012-11-24 | 285121 | CRB24B | Urban | LV Transformer SC741-G CRB24B - Planned | 9.35 | 555 | 5189.25 | 0.0052068 | 9.3816e-06
2012-11-24 | 285122 | KBR6A | Rural short | Feeder KBR6A - Planned | 9.15 | 275 | 2516.25 | 0.0072175 | 2.6245e-05
2012-11-25 | 285119 | NDH6 | Urban | LV Transformer SP3891-E NDH6 - Planned | 3.56 | 289 | 1028.84 | 0.0010325 | 3.5727e-06
2012-11-25 | 285130 | AGE10 | Urban | LV Transformer SP757861 AGE10 - Planned | 8.05 | 79 | 635.95 | 0.00063821 | 8.0786e-06
2012-11-25 | 285131 | MDR31A | Urban | LV Transformer SC560852 MDR31A - Planned | 2.0668 | 36 | 74.4048 | 7.4669e-05 | 2.0741e-06
2012-11-25 | 285132 | MDR31A | Urban | LV Transformer SC560852 MDR31A - Planned | 3.1002 | 31 | 96.1062 | 9.6448e-05 | 3.1112e-06
2012-11-25 | 285133 | MDR31A | Urban | LV Transformer SC560610 MDR31A - Planned | 17.4245 | 63 | 1097.7435 | 0.0011016 | 1.7486e-05
2012-11-25 | 285134 | MDR31A | Urban | LV Transformer SC560610 MDR31A - Planned | 11.8107 | 27 | 318.8889 | 0.00032002 | 1.1853e-05
2012-11-25 | 285135 | MDR31A | Urban | LV Transformer SC560610 MDR31A - Planned | 10.134 | 34 | 344.556 | 0.00034578 | 1.017e-05
2012-11-25 | 285136 | RCF10A | Urban | LV Transformer SP3439-B RCF10A - Planned | 12.825 | 296 | 3796.2 | 0.0038097 | 1.2871e-05
2012-11-25 | 285137 | MRE3 | Urban | LV Transformer SC5194-K MRE3 - Planned | 8.79 | 120 | 1054.8 | 0.0010585 | 8.8212e-06
2012-11-25 | 285138 | ACR4 | Urban | LV Transformer SP4170-E ACR4 - Planned | 7.2 | 350 | 2520 | 0.002529 | 7.2256e-06
2012-11-25 | 285139 | CHL11A | Rural short | LV Transformer SP493623 CHL11A - Planned | 2.785 | 116 | 323.06 | 0.00092655 | 7.9875e-06
2012-11-25 | 285143 | LHM5 | Rural short | Feeder LHM5 - Planned | 89.9 | 326 | 29307.4 | 0.084055 | 0.00025784
2012-11-26 | 285163 | SMF2A | Rural short | Feeder SMF2A - Planned | 16.51 | 26 | 429.26 | 0.0012316 | 4.7368e-05
2012-11-26 | 285189 | BIS2B | Rural short | LV Transformer SP4177-F BIS2B - Planned | 0.264 | 47 | 12.408 | 3.5599e-05 | 7.5742e-07
2012-11-26 | 285191 | CBW7 | Rural short | LV Transformer SP2238-F CBW7 - Planned | 9.5 | 264 | 2508 | 0.0071955 | 2.7256e-05
2012-11-26 | 285197 | KBR2A | Rural short | Feeder KBR2A - Planned | 10 | 327 | 3270 | 0.0093817 | 2.869e-05
2012-11-26 | 285220 | BDB33A | Urban | LV Transformer SP4302-C BDB33A - Planned | 1 | 360 | 360 | 0.00036149 | 1.0042e-06
2012-11-26 | 285243 | ALY8 | Urban | LV Transformer SP8649-H ALY8 - Planned | 18.785 | 409 | 7683.065 | 0.0077149 | 1.8863e-05
2012-11-26 | 285244 | OXL11A | Urban | LV Transformer SP49963-D OXL11A - Planned | 16.8423 | 207 | 3486.3561 | 0.0035008 | 1.6912e-05
2012-11-26 | 285245 | NVL9 | Rural short | LV Transformer SC365-B NVL9 - Planned | 9.63 | 283 | 2725.29 | 0.0078189 | 2.7629e-05
2012-11-26 | 285246 | CRB24B | Urban | LV Transformer SP11395-D CRB24B - Planned | 48.41 | 532 | 25754.12 | 0.025861 | 4.8611e-05
2012-11-26 | 285247 | MDRMLD11 | Urban | LV Transformer SP567459 MDRMLD11 - Planned | 9 | 213 | 1917 | 0.001925 | 9.0374e-06
2012-11-26 | 285248 | BBH8A | Urban | LV Transformer SP45061-B BBH8A - Planned | 29.96 | 453 | 13571.88 | 0.013628 | 3.0084e-05
2012-11-26 | 285249 | SGT4 | Urban | LV Transformer SP50044-F SGT7 - Planned | 7.5736 | 13 | 98.4568 | 9.8865e-05 | 7.605e-06
2012-11-26 | 285249 | SGT7 | Urban | LV Transformer SP50044-F SGT7 - Planned | 13.5629 | 13 | 176.3177 | 0.00017705 | 1.3619e-05
2012-11-26 | 285250 | SGT24A | Urban | LV Transformer SP5299-H SGT24A - Planned | 16.14 | 109 | 1759.26 | 0.0017666 | 1.6207e-05
2012-11-26 | 285251 | SGT5 | Urban | LV Transformer SP3758-G SGT5 - Planned | 6.84 | 170 | 1162.8 | 0.0011676 | 6.8684e-06
2012-11-26 | 285252 | CHL11A | Rural short | LV Transformer SC794294 CHL11A - Planned | 15.705 | 241 | 3784.905 | 0.010859 | 4.5058e-05
2012-11-26 | 285253 | RPN2A | Urban | LV Transformer SP8229-D RPN2A - Planned | 16.205 | 147 | 2382.135 | 0.002392 | 1.6272e-05
2012-11-27 | 285285 | KMR25A | Rural short | LV Transformer SP509-N KMR25A - Planned | 20 | 108 | 2160 | 0.0061978 | 5.7387e-05
2012-11-27 | 285286 | MFN13A | Rural short | LV Transformer SP4719-F MFN13A - Planned | 20 | 208 | 4160 | 0.011937 | 5.7387e-05
2012-11-27 | 285287 | CBW11 | Rural short | LV Transformer SP4952-E CBW11 - Planned | 20 | 217 | 4340 | 0.012453 | 5.7387e-05
2012-11-27 | 285292 | JBB16A | Rural short | LV Transformer SP4783-D JBB16A - Planned | 3 | 245 | 735 | 0.002109 | 8.6081e-06
2012-11-27 | 285300 | MSV1 | Rural short | Feeder MSV1 - Planned | 7 | 335 | 2345 | 0.0067287 | 2.0086e-05
2012-11-27 | 285301 | FDS3 | Rural short | Feeder FDS3 - Planned | 22.805 | 354 | 8072.97 | 0.023164 | 6.5436e-05
2012-11-27 | 285303 | MGP13A | Rural short | LV Transformer SP5209-I MGP13A - Planned | 2 | 447 | 894 | 0.0025652 | 5.7387e-06
2012-11-27 | 285305 | RLB16A | Rural short | Feeder RLB16A - Planned | 17.5 | 412 | 7210 | 0.020688 | 5.0214e-05
2012-11-27 | 285306 | PWC4 | Rural short | Feeder PWC4 - Planned | 58.748 | 365 | 21443.02 | 0.061528 | 0.00016857
2012-11-27 | 285307 | NBR1 | Rural short | LV Transformer SP6677-A NBR1 - Planned | 22 | 366 | 8052 | 0.023104 | 6.3126e-05
2012-11-27 | 285308 | GBN4 | Rural short | LV Transformer SP5610-B GBN4 - Planned | 4.98 | 155 | 771.9 | 0.0022149 | 1.4289e-05
2012-11-27 | 285309 | GYGGYS6 | Rural short | LV Transformer SP39532 GYGGYS6 - Planned | 2.5 | 20 | 50 | 0.00014347 | 7.1734e-06
2012-11-27 | 285310 | NBR1 | Rural short | LV Transformer SP15015-A NBR1 - Planned | 1.5 | 113 | 169.5 | 0.00048636 | 4.3041e-06
2012-11-27 | 285311 | GBN2 | Rural short | LV Transformer SP9342-B GBN2 - Planned | 4 | 20 | 80 | 0.00022955 | 1.1477e-05
2012-11-27 | 285312 | GYM7A | Rural short | LV Transformer SP2653-C GYM7A - Planned | 4.98 | 115 | 572.7 | 0.0016433 | 1.4289e-05
2012-11-27 | 285313 | NBR8 | Rural short | Feeder NBR8 - Planned | 22.63 | 534 | 12084.42 | 0.034675 | 6.4934e-05
2012-11-27 | 285314 | ALY8 | Urban | LV Transformer SP3456-H ALY8 - Planned | 26.64 | 309 | 8231.76 | 0.0082691 | 2.6761e-05
2012-11-27 | 285315 | AGE8 | Urban | LV Transformer SP2171-I AGE8 - Planned | 6.125 | 342 | 2094.75 | 0.0021042 | 6.1528e-06
2012-11-27 | 285316 | KRN18A | Urban | LV Transformer SP773473 NMK17A - Planned | 0.99 | 416 | 411.84 | 0.00041371 | 9.9449e-07
2012-11-27 | 285316 | NMK17A | Urban | LV Transformer SP773473 NMK17A - Planned | 15.5475 | 416 | 6467.76 | 0.0064971 | 1.5618e-05
2012-11-27 | 285317 | INA9A | Urban | LV Transformer SP1970-K INA9A - Planned | 6.95 | 297 | 2064.15 | 0.0020735 | 6.9815e-06
2012-11-27 | 285318 | WMD14A | Rural short | LV Transformer SP3763-B WMD14A - Planned | 3.81 | 40 | 152.4 | 0.00043729 | 1.0932e-05
2012-11-27 | 285319 | GBN4 | Rural short | LV Transformer SP879-D GBN4 - Planned | 3 | 165 | 495 | 0.0014203 | 8.6081e-06
2012-11-27 | 285320 | KWA6A | Urban | LV Transformer SC7823-A KWA6A - Planned | 9 | 148 | 1332 | 0.001338 | 9.0408e-06
2012-11-27 | 285321 | WMD14A | Rural short | LV Transformer SC175593 WMD14A - Planned | 31.115 | 44 | 1369.06 | 0.0039283 | 8.928e-05
2012-11-27 | 285322 | PWC4 | Rural short | LV Transformer SP206-C PWC4 - Planned | 3.0121 | 310 | 933.751 | 0.0026793 | 8.6428e-06
2012-11-27 | 285323 | AMR1 | Rural short | LV Transformer SP546-B AMR1 - Planned | 2.49 | 68 | 169.32 | 0.00048584 | 7.1447e-06
2012-11-27 | 285324 | BMT1 | Rural short | LV Transformer SP444-C BMT1 - Planned | 6 | 94 | 564 | 0.0016183 | 1.7216e-05
2012-11-27 | 285325 | SPO31A | Urban | LV Transformer SP985-H SPO31A - Planned | 20.475 | 100 | 2047.5 | 0.0020568 | 2.0568e-05
2012-11-27 | 285325 | SPO69A | Urban | LV Transformer SP985-H SPO31A - Planned | 1.17 | 100 | 117 | 0.00011753 | 1.1753e-06
2012-11-27 | 285326 | MGP13A | Rural short | LV Transformer SP1062-I MGP13A - Planned | 9 | 380 | 3420 | 0.0098132 | 2.5824e-05
2012-11-27 | 285327 | LDR1 | Urban | LV Transformer SP468825 LDR8 - Planned | 20.28 | 354 | 7179.12 | 0.0072117 | 2.0372e-05
2012-11-27 | 285327 | LDR8 | Urban | LV Transformer SP468825 LDR8 - Planned | 16.51 | 354 | 5844.54 | 0.005871 | 1.6585e-05
2012-11-27 | 285328 | MAI5 | Urban | LV Transformer SP3801-E MAI5 - Planned | 19.11 | 119 | 2274.09 | 0.0022844 | 1.9197e-05
2012-11-27 | 285329 | KRA3 | Urban | LV Transformer SP11973-D KRA3 - Planned | 28.105 | 374 | 10511.27 | 0.010559 | 2.8232e-05
2012-11-27 | 285330 | SGT24A | Urban | LV Transformer SP3702-G SGT24A - Planned | 67.84 | 207 | 14042.88 | 0.014107 | 6.8148e-05
2012-11-27 | 285331 | DBS4A | Urban | LV Transformer SP723-M DBS4A - Planned | 14.7852 | 303 | 4479.9156 | 0.0045002 | 1.4852e-05
2012-11-27 | 285332 | KWA6A | Urban | LV Transformer SP99134-A KWA6A - Planned | 9.1225 | 150 | 1368.375 | 0.0013746 | 9.1639e-06
2012-11-27 | 285333 | LTA6 | Urban | LV Transformer SC5129-I LTA6 - Planned | 15.3621 | 250 | 3840.525 | 0.0038579 | 1.5432e-05
2012-11-27 | 285334 | ALY5 | Urban | LV Transformer SP1850-L ALY5 - Planned | 33.565 | 114 | 3826.41 | 0.0038438 | 3.3717e-05
2012-11-27 | 285335 | HPE5A | Urban | LV Transformer SP2237-M HPE5A - Planned | 13.2849 | 364 | 4835.7036 | 0.0048576 | 1.3345e-05
2012-11-27 | 285336 | RCN3A | Urban | LV Transformer SC4707-K RCN3A - Planned | 1.95 | 178 | 347.1 | 0.00034867 | 1.9588e-06
2012-11-27 | 285337 | RLA5 | Urban | LV Transformer SP494056 RLA5 - Planned | 11.2666 | 140 | 1577.324 | 0.0015845 | 1.1318e-05
2012-11-27 | 285338 | TGW1 | Rural short | LV Transformer SP15671-B TGW1 - Planned | 0.98 | 129 | 126.42 | 0.00036275 | 2.812e-06
2012-11-28 | 285383 | LBH6A | Rural short | LV Transformer SP16411-A LBH6A - Planned | 64.68 | 213 | 13776.84 | 0.039536 | 0.00018561
2012-11-28 | 285401 | MGL9 | Rural short | LV Transformer SP4927-H MGL9 - Planned | 1 | 287 | 287 | 0.00082361 | 2.8697e-06
2012-11-28 | 285405 | SMF6A | Rural short | Feeder SMF6A - Planned | 6.9 | 345 | 2380.5 | 0.0068314 | 1.9801e-05
2012-11-28 | 285425 | FDS1 | Rural short | Feeder FDS1 - Planned | 53.4 | 389 | 20772.6 | 0.059611 | 0.00015324
2012-11-28 | 285426 | JBB16A | Rural short | Feeder JBB16A - Planned | 20.9 | 393 | 8213.7 | 0.023571 | 5.9977e-05
2012-11-28 | 285431 | GYN3A | Rural short | Feeder GYN3A - Planned | 22.03 | 486 | 10706.58 | 0.030725 | 6.322e-05
2012-11-28 | 285432 | AMR2 | Rural short | LV Transformer SP350479 AMR2 - Planned | 7 | 307 | 2149 | 0.006167 | 2.0088e-05
2012-11-28 | 285433 | BMT2 | Rural short | Feeder BMT2 - Planned | 25.85 | 253 | 6540.05 | 0.018768 | 7.4182e-05
2012-11-28 | 285434 | NBR9 | Rural short | Feeder NBR9 - Planned | 13.04 | 259 | 3377.36 | 0.0096921 | 3.7421e-05
2012-11-28 | 285436 | CNB24A | Rural short | Feeder CNB24A - Planned | 46.62 | 472 | 22004.64 | 0.063147 | 0.00013379
2012-11-28 | 285440 | AGE6A | Urban | LV Transformer SP3693-H AGE6A - Planned | 26.1 | 270 | 7047 | 0.0070817 | 2.6228e-05
2012-11-28 | 285441 | ENG8 | Urban | LV Transformer SP1965-L ENG8 - Planned | 41.49 | 175 | 7260.75 | 0.0072965 | 4.1694e-05
2012-11-28 | 285442 | ENG9 | Urban | LV Transformer SP2412-N ENG9 - Planned | 11.44 | 284 | 3248.96 | 0.0032649 | 1.1496e-05
2012-11-28 | 285443 | KMR25A | Rural short | LV Transformer SP2148-L KMR25A - Planned | 18.04 | 477 | 8605.08 | 0.024694 | 5.177e-05
2012-11-28 | 285444 | TRG2A | Urban | LV Transformer SC4879-G TRG2A - Planned | 8.4232 | 280 | 2358.496 | 0.0023701 | 8.4646e-06
2012-11-28 | 285445 | NBR7 | Urban | LV Transformer SP5327-A NBR7 - Planned | 14.875 | 265 | 3941.875 | 0.0039613 | 1.4948e-05
2012-11-28 | 285446 | CLM8 | Urban | LV Transformer SC1426052 CLM9 - Planned | 14.385 | 85 | 1222.725 | 0.0012287 | 1.4456e-05
2012-11-28 | 285446 | CLM9 | Urban | LV Transformer SC1426052 CLM9 - Planned | 20.79 | 85 | 1767.15 | 0.0017758 | 2.0892e-05
2012-11-28 | 285447 | BBH8A | Urban | LV Transformer SP31569-C BBH8A - Planned | 19.08 | 310 | 5914.8 | 0.0059439 | 1.9174e-05
2012-11-28 | 285448 | VSL10A | Urban | LV Transformer SC1367623 VSL10A - Planned | 47.67 | 107 | 5100.69 | 0.0051258 | 4.7904e-05
2012-11-28 | 285449 | KRA10 | Urban | LV Transformer SP4539-F KRA10 - Planned | 43.29 | 255 | 11038.95 | 0.011093 | 4.3503e-05
2012-11-28 | 285451 | LDR8 | Urban | LV Transformer SC758262 LDR8 - Planned | 3.6266 | 225 | 815.985 | 0.00082 | 3.6444e-06
2012-11-28 | 285452 | TGP9A | Rural short | LV Transformer SP1954-I TGP9A - Planned | 5.83 | 162 | 944.46 | 0.0027103 | 1.673e-05
2012-11-28 | 285453 | CFD2A | Urban | LV Transformer SP7107-G CFD2A - Planned | 28.685 | 323 | 9265.255 | 0.0093108 | 2.8826e-05
2012-11-28 | 285454 | KWA12A | Urban | LV Transformer SP4412-B KWA12A - Planned | 17.03 | 244 | 4155.32 | 0.0041758 | 1.7114e-05
2012-11-28 | 285455 | WFD5A | Rural short | LV Transformer SP1631-F WFD5A - Planned | 6.03 | 83 | 500.49 | 0.0014363 | 1.7304e-05
2012-11-28 | 285456 | BHL2A | Urban | LV Transformer SC769096 BHL2A - Planned | 6.75 | 184 | 1242 | 0.0012481 | 6.7832e-06
2012-11-28 | 285457 | KWA12A | Urban | LV Transformer SP4412-B KWA12A - Planned | 20.96 | 219 | 4590.24 | 0.0046128 | 2.1063e-05
2012-11-28 | 285458 | BKD15A | Urban | LV Transformer SP4826-D BKD15A - Planned | 9.03 | 118 | 1065.54 | 0.0010708 | 9.0744e-06
2012-11-28 | 285459 | HPE5A | Urban | LV Transformer SP196-N HPE5A - Planned | 1.8468 | 338 | 624.2184 | 0.00062729 | 1.8559e-06
2012-11-28 | 285460 | CHL3 | Urban | LV Transformer SP1651-K CHL3 - Planned | 0.745 | 110 | 81.95 | 8.2353e-05 | 7.4866e-07
2012-11-28 | 285461 | IPS1B | Urban | LV Transformer SP2506-G IPS1B - Planned | 7.8498 | 287 | 2252.8926 | 0.002264 | 7.8884e-06
2012-11-28 | 285462 | THL2 | Rural short | LV Transformer SP244291 THL2 - Planned | 3 | 170 | 510 | 0.0014636 | 8.6092e-06
2012-11-28 | 285463 | WSO13A | Rural short | LV Transformer SP3260-E WSO13A - Planned | 33.2403 | 335 | 11135.5005 | 0.031956 | 9.539e-05
2012-11-28 | 285464 | CRB24B | Urban | LV Transformer SP11103-F CRB24B - Planned | 22.835 | 495 | 11303.325 | 0.011359 | 2.2947e-05
2012-11-28 | 285473 | WMD8B | Rural short | LV Transformer SC1461475 WMD8B - Planned | 2.9 | 69 | 200.1 | 0.00057423 | 8.3222e-06
2012-11-29 | 285509 | WFD2B | Rural short | LV Transformer SP1927-F WFD2B - Planned | 1 | 96 | 96 | 0.00027553 | 2.8701e-06
2012-11-29 | 285523 | NGI1B | Rural short | LV Transformer SP3252-F NGI1B - Planned | 22 | 78 | 1716 | 0.0049251 | 6.3142e-05
2012-11-29 | 285524 | LBH1B | Rural short | LV Transformer SP3033-A LBH1B - Planned | 8 | 190 | 1520 | 0.0043625 | 2.2961e-05
2012-11-29 | 285540 | KCY2 | Rural short | LV Transformer SP4665-B KCY2 - Planned | 1.17 | 83 | 97.11 | 0.00027871 | 3.358e-06
2012-11-29 | 285560 | NIP4A | Rural short | Feeder NIP4A - Planned | 9.04 | 415 | 3751.6 | 0.010767 | 2.5946e-05
2012-11-29 | 285561 | LBH1B | Rural short | LV Transformer SP16435-A LBH1B - Planned | 39.99 | 423 | 16915.77 | 0.04855 | 0.00011477
2012-11-29 | 285562 | ACR5 | Rural short | LV Transformer SP1975-K ACR5 - Planned | 1 | 429 | 429 | 0.0012313 | 2.8701e-06
2012-11-29 | 285563 | RLB16A | Rural short | Feeder RLB16A - Planned | 19.28 | 418 | 8059.04 | 0.02313 | 5.5335e-05
2012-11-29 | 285564 | MWMRBK11 | Rural short | LV Transformer SP798844 MWMRBK11 - Planned | 1 | 90 | 90 | 0.00025831 | 2.8701e-06
2012-11-29 | 285565 | SDM3 | Rural short | Feeder SDM3, FHYPO - Planned | 12 | 161 | 1932 | 0.005545 | 3.4441e-05
2012-11-29 | 285566 | LLY3 | Rural short | Feeder LLY3 - Planned | 5.78 | 355 | 2051.9 | 0.0058891 | 1.6589e-05
2012-11-29 | 285567 | AGE8 | Urban | LV Transformer SP748724 AGE8 - Planned | 4.37 | 335 | 1463.95 | 0.0014717 | 4.3932e-06
2012-11-29 | 285568 | MGL2A | Rural short | LV Transformer SC3746-J MGL2A - Planned | 12 | 273 | 3276 | 0.0094024 | 3.4441e-05
2012-11-29 | 285569 | KMR24A | Urban | LV Transformer SP2928-L KMR24A - Planned | 10.81 | 233 | 2518.73 | 0.0025321 | 1.0867e-05
2012-11-29 | 285570 | AGE6A | Urban | LV Transformer SP1322-O AGE6A - Planned | 6.66 | 302 | 2011.32 | 0.002022 | 6.6953e-06
2012-11-29 | 285571 | MLY3 | Rural short | LV Transformer SP1245-B MLY3 - Planned | 8.01 | 267 | 2138.67 | 0.0061382 | 2.2989e-05
2012-11-29 | 285572 | JBB16A | Rural short | LV Transformer SP6023-C JBB16A - Planned | 4.98 | 247 | 1230.06 | 0.0035304 | 1.4293e-05
2012-11-29 | 285573 | BBH16A | Urban | LV Transformer SP2722-J BBH16A - Planned | 22.32 | 454 | 10133.28 | 0.010187 | 2.2438e-05
2012-11-29 | 285574 | BHD3A | Urban | LV Transformer SP6394-D BHD3A - Planned | 34.87 | 279 | 9728.73 | 0.0097803 | 3.5055e-05
2012-11-29 | 285575 | GVN16A | Rural short | LV Transformer SP10014-F GVN16A - Planned | 19.68 | 422 | 8304.96 | 0.023836 | 5.6483e-05
2012-11-29 | 285576 | BBH8A | Urban | LV Transformer SP45061-B BBH8A - Planned | 31.785 | 440 | 13985.4 | 0.01406 | 3.1954e-05
2012-11-29 | 285577 | BLN6A | Urban | LV Transformer SP734505 BLN6A - Planned | 6.08 | 75 | 456 | 0.00045842 | 6.1122e-06
2012-11-29 | 285578 | RCF2A | Urban | LV Transformer SP2212-F RCF2A - Planned | 4.365 | 96 | 419.04 | 0.00042126 | 4.3882e-06
2012-11-29 | 285579 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 4.26 | 101 | 430.26 | 0.00043254 | 4.2826e-06
2012-11-29 | 285580 | HDA3A | Urban | LV Transformer SP1050781 HDA3A - Planned | 32.83 | 378 | 12409.74 | 0.012476 | 3.3004e-05
2012-11-29 | 285581 | CSE2 | Urban | LV Transformer SC4431-L CSE2 - Planned | 28.3239 | 316 | 8950.3524 | 0.0089978 | 2.8474e-05
2012-11-29 | 285582 | MHL25A | Urban | LV Transformer SC620235 MHL25A - Planned | 0.825 | 86 | 70.95 | 7.1326e-05 | 8.2938e-07
2012-11-29 | 285584 | NBR8 | Rural short | Feeder NBR8 - Planned | 65.59 | 401 | 26301.59 | 0.075488 | 0.00018825
2012-11-29 | 285585 | BBS9 | Urban | LV Transformer SC3900-F BBS9 - Planned | 7.0581 | 227 | 1602.1887 | 0.0016107 | 7.0955e-06
2012-11-29 | 285586 | GYN3A | Rural short | Feeder GYN3A - Planned | 77.132 | 382 | 29464.424 | 0.084565 | 0.00022137
2012-11-29 | 285587 | NBR5 | Rural short | Feeder NBR5 - Planned | 62.745 | 50 | 3137.25 | 0.0090042 | 0.00018008
2012-11-29 | 285588 | UMG2B | Rural short | LV Transformer SP2448-J UMG2B - Planned | 37.7056 | 234 | 8823.1104 | 0.025323 | 0.00010822
2012-11-29 | 285589 | KBR2A | Rural short | LV Transformer SP4157-C KBR2A - Planned | 29.58 | 151 | 4466.58 | 0.012819 | 8.4897e-05
2012-11-29 | 285590 | NIP1A | Urban | LV Transformer SP1606-D NIP1A - Planned | 28.525 | 180 | 5134.5 | 0.0051617 | 2.8676e-05
2012-11-30 | 285620 | NGI1B | Rural short | LV Transformer SP7055-F NGI1B - Planned | 51 | 121 | 6171 | 0.017718 | 0.00014643
2012-11-30 | 285621 | BNH2B | Rural short | LV Transformer SP69140-B BNH2B - Planned | 3 | 175 | 525 | 0.0015074 | 8.6137e-06
2012-11-30 | 285641 | TGW1 | Rural short | Feeder TGW1 - Planned | 10 | 193 | 1930 | 0.0055415 | 2.8712e-05
2012-11-30 | 285642 | PPE13A | Rural short | LV Transformer SP3093-E PPE13A - Planned | 7.48 | 237 | 1772.76 | 0.00509 | 2.1477e-05
2012-11-30 | 285643 | PPE13A | Rural short | LV Transformer SP6725-D PPE13A - Planned | 1 | 259 | 259 | 0.00074365 | 2.8712e-06
2012-11-30 | 285644 | JBB12B | Rural short | Feeder JBB12B - Planned | 8.5 | 305 | 2592.5 | 0.0074437 | 2.4406e-05
2012-11-30 | 285645 | RWD1 | Rural short | Feeder RWD1 - Planned | 12 | 360 | 4320 | 0.012404 | 3.4455e-05
2012-11-30 | 285647 | MLY3 | Rural short | LV Transformer SP161890 MLY3 - Planned | 65.17 | 350 | 22809.5 | 0.065492 | 0.00018712
2012-11-30 | 285648 | GYGGYS6 | Rural short | LV Transformer SP5498-B GYGGYS6 - Planned | 1 | 252 | 252 | 0.00072355 | 2.8712e-06
2012-11-30 | 285650 | NBR1 | Rural short | Feeder NBR1 - Planned | 43.06 | 271 | 11669.26 | 0.033505 | 0.00012364
2012-11-30 | 285651 | GBN4 | Rural short | Feeder GBN4 - Planned | 12.818 | 213 | 2730.234 | 0.0078392 | 3.6804e-05
2012-11-30 | 285652 | ALY8 | Urban | LV Transformer SP8649-H ALY8 - Planned | 50.4 | 429 | 21621.6 | 0.021743 | 5.0682e-05
2012-11-30 | 285654 | VPT13A | Rural short | LV Transformer SP232621 VPT13A - Planned | 2.07 | 234 | 484.38 | 0.0013908 | 5.9435e-06
2012-11-30 | 285655 | ALY8 | Urban | LV Transformer SP3750-E ALY8 - Planned | 12.5 | 116 | 1450 | 0.0014581 | 1.257e-05
2012-11-30 | 285656 | SMR15A | Urban | LV Transformer SP5518-F SMR15A - Planned | 2.22 | 400 | 888 | 0.00089297 | 2.2324e-06
2012-11-30 | 285657 | TRG2A | Urban | LV Transformer SP484584-A TRG2A - Planned | 6.86 | 250 | 1715 | 0.0017246 | 6.8984e-06
2012-11-30 | 285658 | GAP9A | Urban | LV Transformer SP2887-N GAP9A - Planned | 13.95 | 332 | 4631.4 | 0.0046573 | 1.4028e-05
2012-11-30 | 285659 | KMR27A | Urban | LV Transformer SP2205-K KMR27A - Planned | 9.23 | 301 | 2778.23 | 0.0027938 | 9.2817e-06
2012-11-30 | 285660 | DRA9 | Urban | LV Transformer SP1547-I DRA9 - Planned | 7.75 | 282 | 2185.5 | 0.0021977 | 7.7934e-06
2012-11-30 | 285661 | KMR19A | Urban | LV Transformer SP32153-E KMR19A - Planned | 7 | 252 | 1764 | 0.0017739 | 7.0392e-06
2012-11-30 | 285662 | BMT1 | Rural short | LV Transformer SP548-B BMT1 - Planned | 29.1 | 82 | 2386.2 | 0.0068514 | 8.3553e-05
2012-11-30 | 285663 | BWH7A | Rural short | LV Transformer SP6661-B BWH7A - Planned | 1 | 185 | 185 | 0.00053118 | 2.8712e-06
2012-11-30 | 285664 | MDR31A | Urban | LV Transformer SP330089-A MDR31A - Planned | 2.8188 | 360 | 1014.768 | 0.0010204 | 2.8346e-06
2012-11-30 | 285665 | GVN16A | Rural short | LV Transformer SP14121-D MDRMLD11 - Planned | 3.08 | 445 | 1370.6 | 0.0039353 | 8.8434e-06
2012-11-30 | 285665 | MDRMLD11 | Urban | LV Transformer SP14121-D MDRMLD11 - Planned | 7.7 | 445 | 3426.5 | 0.0034457 | 7.7431e-06
2012-11-30 | 285666 | BBH8A | Urban | LV Transformer SP1229-F BBH8A - Planned | 50.16 | 440 | 22070.4 | 0.022194 | 5.0441e-05
2012-11-30 | 285666 | MMC33A | Urban | LV Transformer SP1229-F BBH8A - Planned | 0.77 | 440 | 338.8 | 0.0003407 | 7.7431e-07
2012-11-30 | 285667 | SPO49A | Urban | LV Transformer SG1082591 SPO49A - Planned | 3.83 | 70 | 268.1 | 0.0002696 | 3.8514e-06
2012-11-30 | 285668 | TPT4 | Rural short | LV Transformer SP2963-F TPT4 - Planned | 29.7 | 67 | 1989.9 | 0.0057135 | 8.5276e-05
2012-11-30 | 285669 | HTN7A | Urban | LV Transformer SP378-J HTN7A - Planned | 14.49 | 315 | 4564.35 | 0.0045899 | 1.4571e-05
2012-11-30 | 285670 | SGT5 | Urban | LV Transformer SP3313-F SGT5 - Planned | 67.915 | 219 | 14873.385 | 0.014957 | 6.8295e-05
2012-11-30 | 285671 | NDH7 | Urban | LV Transformer SP1294-L NDH7 - Planned | 0.94 | 78 | 73.32 | 7.373e-05 | 9.4526e-07
2012-11-30 | 285672 | VPT16A | Urban | LV Transformer SC2384-D VPT16A - Planned | 4.16 | 102 | 424.32 | 0.00042669 | 4.1833e-06
2012-11-30 | 285673 | GGR4 | Rural short | LV Transformer SP8690-B GGR4 - Planned | 3 | 235 | 705 | 0.0020242 | 8.6137e-06
2012-12-01 | 285687 | BNH1B | Rural short | Feeder BNH1B - Planned | 17 | 200 | 3400 | 0.0097663 | 4.8832e-05
2012-12-01 | 285691 | QPT22A | Urban | LV Transformer SP21918-E QPT22A - Planned | 75.1227 | 352 | 26443.1904 | 0.026599 | 7.5565e-05
2012-12-01 | 285701 | BHD20A | Urban | LV Transformer SC657952 BHD20A - Planned | 23.79 | 268 | 6375.72 | 0.0064133 | 2.393e-05
2012-12-02 | 285703 | WRG12A | Urban | LV Transformer SC492747 WRG12A - Planned | 3.5 | 145 | 507.5 | 0.00051058 | 3.5212e-06
2012-12-02 | 285709 | SPE12 | Urban | LV Transformer SG138-F SPE12 - Planned | 1 | 243 | 243 | 0.00024447 | 1.0061e-06
2012-12-02 | 285711 | BGY5A | Rural short | Feeder BGY5A - Planned | 25.5 | 324 | 8262 | 0.023738 | 7.3265e-05
2012-12-02 | 285713 | NMK5 | Urban | LV Transformer SP6595-I - Planned | 5.985 | 222 | 1328.67 | 0.0013367 | 6.0213e-06
2012-12-02 | 285713 | NMK7 | Urban | LV Transformer SP6595-I - Planned | 0.85 | 222 | 188.7 | 0.00018984 | 8.5515e-07
2012-12-02 | 285713 | TRG5 | Urban | LV Transformer SP6595-I - Planned | 1.545 | 222 | 342.99 | 0.00034507 | 1.5544e-06
2012-12-02 | 285714 | NBR10 | Urban | LV Transformer SP1285-A NBR10 - Planned | 12.15 | 347 | 4216.05 | 0.0042416 | 1.2224e-05
2012-12-02 | 285715 | NBR8 | Rural short | LV Transformer SG232-A NBR8 - Planned | 0.975 | 529 | 515.775 | 0.0014819 | 2.8013e-06
2012-12-02 | 285717 | CFD2A | Urban | LV Transformer SP7107-G CFD2A - Planned | 19.765 | 330 | 6522.45 | 0.006562 | 1.9885e-05
2012-12-02 | 285718 | UMG1A | Urban | LV Transformer SC4399-F UMG1A - Planned | 49.245 | 426 | 20978.37 | 0.021105 | 4.9543e-05
2012-12-02 | 285719 | WRG12A | Urban | LV Transformer SP4021-L WRG12A - Planned | 21.84 | 135 | 2948.4 | 0.0029663 | 2.1972e-05
2012-12-02 | 285725 | BHD32B | Urban | LV Transformer SP8965-C BHD32B - Planned | 4.4061 | 164 | 722.6004 | 0.00072698 | 4.4328e-06
2012-12-03 | 285760 | BHD35A | Rural short | Feeder BHD35A - Planned | 28.5 | 188 | 5358 | 0.015403 | 8.1931e-05
2012-12-03 | 285782 | TRP3 | Rural short | LV Transformer SP3124-B TRP3 - Planned | 1 | 325 | 325 | 0.0009343 | 2.8748e-06
2012-12-03 | 285800 | KWH3 | Rural short | LV Transformer SP700-D KWH3 - Planned | 2.01 | 195 | 391.95 | 0.0011268 | 5.7783e-06
2012-12-03 | 285801 | BBH13B | Urban | LV Transformer SG1100-J BBH13B - Planned | 45 | 303 | 13635 | 0.013723 | 4.5291e-05
2012-12-03 | 285803 | JBB16A | Rural short | Feeder JBB16A - Planned | 34.88 | 440 | 15347.2 | 0.04412 | 0.00010027
2012-12-03 | 285804 | HPK9 | Urban | LV Transformer SP6125-F HPK9 - Planned | 17.085 | 297 | 5074.245 | 0.0051071 | 1.7196e-05
2012-12-03 | 285806 | KMR24A | Urban | LV Transformer SP802206 KMR24A - Planned | 14.85 | 323 | 4796.55 | 0.0048276 | 1.4946e-05
2012-12-03 | 285807 | AGE9 | Urban | LV Transformer SP2742-K AGE9 - Planned | 37.355 | 401 | 14979.355 | 0.015076 | 3.7597e-05
2012-12-03 | 285808 | KMR19A | Urban | LV Transformer SP2205-K KMR27A - Planned | 1.19 | 306 | 364.14 | 0.0003665 | 1.1977e-06
2012-12-03 | 285808 | KMR27A | Urban | LV Transformer SP2205-K KMR27A - Planned | 21.3 | 306 | 6517.8 | 0.00656 | 2.1438e-05
2012-12-03 | 285809 | SFD8 | Urban | LV Transformer SC5375-H SFD8 - Planned | 12.24 | 265 | 3243.6 | 0.0032646 | 1.2319e-05
2012-12-03 | 285810 | GAP9A | Urban | LV Transformer SP1350-L GAP9A - Planned | 46.18 | 206 | 9513.08 | 0.0095747 | 4.6479e-05
2012-12-03 | 285811 | STL2 | Urban | LV Transformer SP3004-M STL2 - Planned | 14.7064 | 252 | 3706.0128 | 0.00373 | 1.4802e-05
2012-12-03 | 285812 | KWA6A | Urban | LV Transformer SP7711-A KWA6A - Planned | 9.15 | 78 | 713.7 | 0.00071832 | 9.2093e-06
2012-12-03 | 285813 | NBR7 | Urban | LV Transformer SP17730-A NBR7 - Planned | 12.78 | 357 | 4562.46 | 0.004592 | 1.2863e-05
2012-12-03 | 285814 | GVN15A | Urban | LV Transformer SC788743 - Planned | 0.99 | 50 | 49.5 | 4.9821e-05 | 9.9641e-07
2012-12-03 | 285815 | SGT24A | Urban | LV Transformer SP50-L SGT24A - Planned | 18.835 | 266 | 5010.11 | 0.0050426 | 1.8957e-05
2012-12-03 | 285816 | DRD3A | Urban | LV Transformer SP17290-C DRD3A - Planned | 3.13 | 279 | 873.27 | 0.00087893 | 3.1503e-06
2012-12-03 | 285817 | SGT24A | Urban | LV Transformer SP144-M SGT24A - Planned | 16.16 | 261 | 4217.76 | 0.0042451 | 1.6265e-05
2012-12-03 | 285818 | DRD3A | Urban | LV Transformer SP5667-C DRD3A - Planned | 26.55 | 150 | 3982.5 | 0.0040083 | 2.6722e-05
2012-12-03 | 285819 | MTG13A | Urban | LV Transformer SP3045-K UMG1B - Planned | 16.2192 | 242 | 3925.0464 | 0.0039505 | 1.6324e-05
2012-12-03 | 285819 | UMG1B | Urban | LV Transformer SP3045-K UMG1B - Planned | 3.955 | 242 | 957.11 | 0.00096331 | 3.9806e-06
2012-12-03 | 285820 | HPE16A | Urban | LV Transformer SC4410-I HPE16A - Planned | 4.9116 | 30 | 147.348 | 0.0001483 | 4.9434e-06
2012-12-04 | 285860 | BWH7A | Rural short | LV Transformer SP176102 BWH7A - Planned | 9 | 132 | 1188 | 0.0034166 | 2.5883e-05
2012-12-04 | 285901 | RPN6A | Rural short | LV Transformer SP11772-D RPN6A - Planned | 53.5 | 87 | 4654.5 | 0.013386 | 0.00015386
2012-12-04 | 285920 | TGW3 | Rural short | LV Transformer SP43660-A TGW3 - Planned | 1 | 268 | 268 | 0.00077075 | 2.8759e-06
2012-12-04 | 285921 | CNB24A | Rural short | LV Transformer SP4859-E CNB24A - Planned | 10.5 | 444 | 4662 | 0.013408 | 3.0197e-05
2012-12-04 | 285926 | GYN7A | Rural short | Feeder GYN7A - Planned | 4 | 215 | 860 | 0.0024733 | 1.1504e-05
2012-12-04 | 285929 | HPE12A | Urban | LV Transformer SP51-O HPE12A - Planned | 31.0648 | 356 | 11059.0688 | 0.011134 | 3.1275e-05
2012-12-04 | 285930 | NSW3A | Urban | LV Transformer SC1366381 NSW3A - Planned | 10.8 | 177 | 1911.6 | 0.0019245 | 1.0873e-05
2012-12-04 | 285931 | IDY6A | Urban | LV Transformer SP961-J TRG2A - Planned | 1.21 | 359 | 434.39 | 0.00043733 | 1.2182e-06
2012-12-04 | 285931 | TRG2A | Urban | LV Transformer SP961-J TRG2A - Planned | 32.3441 | 359 | 11611.5319 | 0.01169 | 3.2563e-05
2012-12-04 | 285932 | SMR12A | Urban | LV Transformer SG4143-H SMR12A - Planned | 20.09 | 303 | 6087.27 | 0.0061285 | 2.0226e-05
2012-12-04 | 285933 | NBR2 | Urban | LV Transformer SP3250-A NBR2 - Planned | 18.48 | 40 | 739.2 | 0.00074421 | 1.8605e-05
2012-12-04 | 285934 | PGN1B | Rural short | LV Transformer SP6733-A PGN1B - Planned | 5.2 | 123 | 639.6 | 0.0018394 | 1.4955e-05
2012-12-04 | 285935 | NBR5 | Rural short | LV Transformer SP4031-A NBR5 - Planned | 5.2251 | 233 | 1217.4483 | 0.0035013 | 1.5027e-05
2012-12-04 | 285936 | NBR2 | Urban | LV Transformer SP3025-A NBR2 - Planned | 7.05 | 24 | 169.2 | 0.00017035 | 7.0978e-06
2012-12-04 | 285937 | JBB16A | Rural short | LV Transformer SP99765-B JBB16A - Planned | 12.105 | 248 | 3002.04 | 0.0086337 | 3.4813e-05
2012-12-04 | 285938 | BBH8A | Urban | LV Transformer SP43611-B BBH8A - Planned | 27.04 | 440 | 11897.6 | 0.011978 | 2.7223e-05
2012-12-04 | 285939 | LDR10A | Urban | LV Transformer SP34040-D LDR10A - Planned | 11.28 | 370 | 4173.6 | 0.0042019 | 1.1356e-05
2012-12-04 | 285939 | SPO11A | Urban | LV Transformer SP34040-D LDR10A - Planned | 85.55 | 370 | 31653.5 | 0.031868 | 8.6129e-05
2012-12-04 | 285940 | CRB24B | Urban | LV Transformer SP17419-D CRB24B - Planned | 167.34 | 458 | 76641.72 | 0.077161 | 0.00016847
2012-12-04 | 285941 | LDR1 | Urban | LV Transformer SP2861-F LDR1 - Planned | 25.35 | 318 | 8061.3 | 0.0081159 | 2.5522e-05
2012-12-04 | 285942 | DRD16A | Urban | LV Transformer SP5896-B DRD16A - Planned | 28.23 | 341 | 9626.43 | 0.0096916 | 2.8421e-05
2012-12-04 | 285943 | HDA11A | Urban | LV Transformer SP5166-G HDA11A - Planned | 10.68 | 179 | 1911.72 | 0.0019247 | 1.0752e-05
2012-12-04 | 285944 | BHL2A | Urban | LV Transformer SP1446-N BHL2A - Planned | 5.95 | 265 | 1576.75 | 0.0015874 | 5.9903e-06
2012-12-04 | 285945 | BIS1 | Rural short | LV Transformer SC743661 BIS16A - Planned | 14.44 | 35.5 | 847.4 | 0.0024371 | 4.1528e-05
2012-12-04 | 285945 | BIS16A | Urban | LV Transformer SC743661 BIS16A - Planned | 5.12 | 47.6667 | 349.42 | 0.00035179 | 5.1547e-06
2012-12-04 | 285946 | ZMR10 | Urban | LV Transformer SP2254-I ZMR10 - Planned | 8.03 | 345 | 2770.35 | 0.0027891 | 8.0844e-06
2012-12-04 | 285947 | LBH1B | Rural short | LV Transformer SP3803-B LBH1B - Planned | 0.78 | 175 | 136.5 | 0.00039256 | 2.2432e-06
2012-12-04 | 285948 | CLR3 | Rural short | LV Transformer SP864-L CLR3 - Planned | 5.32 | 128 | 680.96 | 0.0019584 | 1.53e-05
2012-12-04 | 285949 | QPT5 | Urban | LV Transformer SP2341-K QPT5 - Planned | 15.605 | 349 | 5446.145 | 0.005483 | 1.5711e-05
2012-12-04 | 285950 | CNB24A | Rural short | LV Transformer SP2838-D CNB24A - Planned | 6.375 | 425 | 2709.375 | 0.007792 | 1.8334e-05
2012-12-04 | 285951 | HPE5A | Urban | LV Transformer SP2237-M HPE5A - Planned | 1.255 | 131 | 164.405 | 0.00016552 | 1.2635e-06
2012-12-04 | 285952 | LLY4 | Rural short | LV Transformer SP8078-A LLY4 - Planned | 28.9351 | 211 | 6105.3061 | 0.017558 | 8.3215e-05
2012-12-04 | 285953 | SPF1B | Rural short | LV Transformer SC1485570 SPF1B - Planned | 28.2 | 235 | 6627 | 0.019059 | 8.1101e-05
2012-12-04 | 285954 | MWMRBK11 | Rural short | LV Transformer SP1386-F MWMRBK11 - Planned | 5.48 | 317 | 1737.16 | 0.004996 | 1.576e-05
2012-12-04 | 285955 | NIP4A | Rural short | LV Transformer SP3631-D NIP4A - Planned | 3.04 | 382 | 1161.28 | 0.0033398 | 8.7428e-06
2012-12-05 | 285980 | NBR8 | Rural short | Feeder NBR8 - Planned | 96.6525 | 64 | 6185.76 | 0.017797 | 0.00027808
2012-12-05 | 285981 | CPD1 | Rural short | LV Transformer SP4543-D CPD1 - Planned | 1 | 36 | 36 | 0.00010358 | 2.8771e-06
2012-12-05 | 285982 | GBN2 | Rural short | LV Transformer SP2568-E GBN2 - Planned | 1.335 | 62 | 82.77 | 0.00023814 | 3.8409e-06
2012-12-05 | 286002 | MGP15A | Urban | Feeder MGP15A - Planned | 58 | 189 | 10962 | 0.01104 | 5.841e-05
2012-12-05 | 286004 | GYGGYS6 | Rural short | LV Transformer SP13636-C GYGGYS6 - Planned | 1 | 100 | 100 | 0.00028771 | 2.8771e-06
2012-12-05 | 286008 | IBL2 | Rural short | LV Transformer SP2942-B IBL2 - Planned | 1.32 | 198 | 261.36 | 0.00075196 | 3.7978e-06
2012-12-05 | 286009 | JBB12B | Rural short | Feeder JBB12B - Planned | 7.195 | 303 | 2180.085 | 0.0062723 | 2.0701e-05
2012-12-05 | 286011 | BDT2 | Rural short | Feeder BDT2 - Planned | 20.365 | 283 | 5763.295 | 0.016582 | 5.8592e-05
2012-12-05 | 286016 | GBN4 | Rural short | Feeder GBN4 - Planned | 23.81 | 304 | 7238.24 | 0.020825 | 6.8504e-05
2012-12-05 | 286027 | FDS4 | Rural short | Feeder FDS4 - Planned | 10.01 | 382 | 3823.82 | 0.011002 | 2.88e-05
2012-12-05 | 286028 | SPC2B | Rural short | Feeder SPC2B - Planned | 10.41 | 362 | 3768.42 | 0.010842 | 2.9951e-05
2012-12-05 | 286031 | MLY6 | Rural short | LV Transformer SP175151 MLY6 - Planned | 0.5 | 358 | 179 | 0.000515 | 1.4386e-06
2012-12-05 | 286032 | GYS3A | Rural short | LV Transformer SP7628-A GYS3A - Planned | 3 | 408 | 1224 | 0.0035216 | 8.6313e-06
2012-12-05 | 286033 | GBN4 | Rural short | LV Transformer SP1510-E GBN4 - Planned | 4.1781 | 30 | 125.343 | 0.00036062 | 1.2021e-05
2012-12-05 | 286034 | MLB6A | Rural short | Feeder MLB6A - Planned | 2.01 | 424 | 852.24 | 0.002452 | 5.783e-06
2012-12-05 | 286037 | HPE12A | Urban | LV Transformer SP164-O HPE12A - Planned | 13.53 | 162 | 2191.86 | 0.0022074 | 1.3626e-05
2012-12-05 | 286038 | JDL7 | Urban | LV Transformer SC3921-G JDL7 - Planned | 23.87 | 330 | 7877.1 | 0.0079328 | 2.4039e-05
2012-12-05 | 286039 | TWG16 | Urban | LV Transformer SP1977-K TWG16 - Planned | 8.16 | 229 | 1868.64 | 0.0018819 | 8.2177e-06
2012-12-05 | 286040 | AHL9A | Urban | LV Transformer SC1693-N AHL9A - Planned | 27.675 | 341 | 9437.175 | 0.0095039 | 2.7871e-05
2012-12-05 | 286041 | AGE8 | Urban | LV Transformer SP6254-F AGE8 - Planned | 20.16 | 348 | 7015.68 | 0.0070653 | 2.0303e-05
2012-12-05 | 286042 | NVL9 | Rural short | LV Transformer SP3354-A NVL9 - Planned | 26.88 | 240 | 6451.2 | 0.018561 | 7.7336e-05
2012-12-05 | 286043 | AHD7 | Urban | LV Transformer SP9950-A AHD7 - Planned | 18.0596 | 45 | 812.682 | 0.00081843 | 1.8187e-05
2012-12-05 | 286044 | MLY3 | Rural short | LV Transformer SP3977-B MLY3 - Planned | 0.99 | 352 | 348.48 | 0.0010026 | 2.8483e-06
2012-12-05 | 286045 | AHD15B | Urban | LV Transformer SP7811-A AHD15B - Planned | 16.2747 | 29 | 471.9663 | 0.0004753 | 1.639e-05
2012-12-05 | 286046 | AHD25A | Urban | LV Transformer SP3805-A AHD25A - Planned | 6.57 | 52 | 341.64 | 0.00034406 | 6.6165e-06
2012-12-05 | 286047 | MLY3 | Rural short | LV Transformer SP9549-A MLY3 - Planned | 0.98 | 247 | 242.06 | 0.00069643 | 2.8196e-06
2012-12-05 | 286048 | SGT24A | Urban | LV Transformer SP39457-D SGT24A - Planned | 13 | 151 | 1963 | 0.0019769 | 1.3092e-05
2012-12-05 | 286049 | NBR1 | Rural short | LV Transformer SP5207-A NBR1 - Planned | 11.97 | 280 | 3351.6 | 0.0096429 | 3.4439e-05
2012-12-05 | 286050 | WFD2B | Rural short | LV Transformer SP1630-F WFD2B - Planned | 24.895 | 348 | 8663.46 | 0.024926 | 7.1625e-05
2012-12-05 | 286051 | HDA3A | Urban | LV Transformer SP1050781 HDA3A - Planned | 10.05 | 250 | 2512.5 | 0.0025303 | 1.0121e-05
2012-12-05 | 286052 | CNB24A | Rural short | LV Transformer SP6783-E CNB24A - Planned | 4.05 | 455 | 1842.75 | 0.0053018 | 1.1652e-05
2012-12-05 | 286053 | RCF10A | Urban | LV Transformer SP3392-C RCF10A - Planned | 16.2 | 327 | 5297.4 | 0.0053349 | 1.6315e-05
2012-12-05 | 286054 | LDR8 | Urban | LV Transformer SP1084-E LDR8 - Planned | 31.28 | 398 | 12449.44 | 0.012537 | 3.1501e-05
2012-12-05 | 286055 | MRE3 | Urban | LV Transformer SP517-N MRE3 - Planned | 2.6533 | 152 | 403.3016 | 0.00040615 | 2.6721e-06
2012-12-05 | 286056 | ZMR10 | Urban | LV Transformer SP18-Q ZMR10 - Planned | 15.07 | 315 | 4747.05 | 0.0047806 | 1.5177e-05
2012-12-05 | 286057 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 37.6809 | 390 | 14695.551 | 0.014799 | 3.7947e-05
2012-12-05 | 286058 | LBH1B | Rural short | LV Transformer SP9685-A LBH1B - Planned | 31.415 | 42 | 1319.43 | 0.0037961 | 9.0384e-05
2012-12-05 | 286059 | RPN3A | Urban | LV Transformer SP8213-C RPN3A - Planned | 20.21 | 98 | 1980.58 | 0.0019946 | 2.0353e-05
2012-12-05 | 286060 | RPN3A | Urban | LV Transformer SP5005-E RPN3A - Planned | 20.76 | 255 | 5293.8 | 0.0053312 | 2.0907e-05
2012-12-05 | 286061 | BHL2A | Urban | LV Transformer SP2753-H BHL2A - Planned | 18.96 | 274 | 5195.04 | 0.0052318 | 1.9094e-05
2012-12-05 | 286063 | WMR3 | Rural short | LV Transformer SP5061-H WMR3 - Planned | 2.5 | 137 | 342.5 | 0.00098541 | 7.1928e-06
2012-12-05 | 286064 | CBW11 | Rural short | LV Transformer SP2383-G CBW11 - Planned | 4.98 | 74 | 368.52 | 0.0010603 | 1.4328e-05
2012-12-06 | 286083 | MSV1 | Rural short | LV Transformer SP8682-B MSV1 - Planned | 3 | 185 | 555 | 0.0015974 | 8.6348e-06
2012-12-06 | 286084 | SMF6A | Rural short | LV Transformer SP4716-J SMF6A - Planned | 7 | 4 | 28 | 8.0591e-05 | 2.0148e-05
2012-12-06 | 286086 | NBR6 | Rural short | LV Transformer SP3004-A NBR6 - Planned | 16.91 | 198 | 3348.18 | 0.0096369 | 4.8671e-05
2012-12-06 | 286087 | LBH3A | Rural short | LV Transformer SP206101 LBH3A - Planned | 21.5 | 233 | 5009.5 | 0.014419 | 6.1883e-05
2012-12-06 | 286088 | TGW1 | Rural short | LV Transformer SP2617-C TGW1 - Planned | 5 | 221 | 1105 | 0.0031805 | 1.4391e-05
2012-12-06 | 286089 | AMR1 | Rural short | Feeder AMR1 - Planned | 9.4 | 327 | 3073.8 | 0.0088472 | 2.7056e-05
2012-12-06 | 286090 | KCY4 | Rural short | LV Transformer SP12548-A KCY4 - Planned | 5 | 203 | 1015 | 0.0029214 | 1.4391e-05
2012-12-06 | 286092 | KBR6A | Rural short | Feeder KBR6A - Planned | 13.2175 | 324 | 4282.47 | 0.012326 | 3.8043e-05
2012-12-06 | 286094 | CBW13 | Rural short | LV Transformer SP161-M CBW13 - Planned | 15 | 230 | 3450 | 0.00993 | 4.3174e-05
2012-12-06 | 286095 | CNB24A | Rural short | LV Transformer SP4859-E CNB24A - Planned | 8.4 | 371 | 3116.4 | 0.0089698 | 2.4177e-05
2012-12-06 | 286096 | SPC2B | Rural short | LV Transformer SP8028-B SPC2B - Planned | 22.08 | 395 | 8721.6 | 0.025103 | 6.3552e-05
2012-12-06 | 286097 | PWC4 | Rural short | Feeder PWC4 - Planned | 28.2632 | 383 | 10824.8056 | 0.031157 | 8.1349e-05
2012-12-06 | 286099 | TGW1 | Rural short | Feeder TGW1 - Planned | 12.67 | 401 | 5080.67 | 0.014623 | 3.6468e-05
2012-12-06 | 286100 | JBB16A | Rural short | LV Transformer SP6023-C JBB16A - Planned | 4.98 | 375 | 1867.5 | 0.0053752 | 1.4334e-05
2012-12-06 | 286101 | GTN5B | Rural short | LV Transformer SG773363 GTN5B - Planned | 1.5 | 206 | 309 | 0.00088938 | 4.3174e-06
2012-12-06 | 286102 | WMD8B | Rural short | LV Transformer SP1237-B WMD8B - Planned | 6.02 | 500 | 3010 | 0.0086636 | 1.7327e-05
2012-12-06 | 286105 | CRBTHP26 | Urban | LV Transformer SC362-J CRBTHP26 - Planned | 24.25 | 343 | 8317.75 | 0.0083791 | 2.4429e-05
2012-12-06 | 286106 | HPE12A | Urban | LV Transformer SP164-O HPE12A - Planned | 10.32 | 434 | 4478.88 | 0.0045119 | 1.0396e-05
2012-12-06 | 286107 | ENG7 | Urban | LV Transformer SP596-O ENG7 - Planned | 3.96 | 135 | 534.6 | 0.00053854 | 3.9892e-06
2012-12-06 | 286108 | DRA6 | Urban | LV Transformer SP31850-E DRA6 - Planned | 10.03 | 340 | 3410.2 | 0.0034353 | 1.0104e-05
2012-12-06 | 286109 | AGE8 | Urban | LV Transformer SP522108 AGE8 - Planned | 7.8396 | 190 | 1489.524 | 0.0015005 | 7.8974e-06
2012-12-06 | 286110 | KMR18A | Urban | LV Transformer SP23670-D KMR18A - Planned | 6.615 | 423 | 2798.145 | 0.0028188 | 6.6638e-06
2012-12-06 | 286111 | BWH8A | Rural short | LV Transformer SP13372-A BWH8A - Planned | 30.86 | 87 | 2684.82 | 0.0077276 | 8.8823e-05
2012-12-06 | 286112 | LBH6A | Rural short | LV Transformer SP6874-A LBH6A - Planned | 24.5 | 132 | 3234 | 0.0093083 | 7.0517e-05
2012-12-06 | 286113 | GYS3A | Rural short | LV Transformer SP563-C GYS3A - Planned | 2.345 | 137 | 321.265 | 0.00092468 | 6.7495e-06
2012-12-06 | 286114 | MDRMLD11 | Urban | LV Transformer SP6422-C MDRMLD11 - Planned | 0.99 | 239 | 236.61 | 0.00023835 | 9.973e-07
2012-12-06 | 286115 | BBH12B | Urban | LV Transformer SP4628-G BBH12B - Planned | 148.279 | 158 | 23428.082 | 0.023601 | 0.00014937
2012-12-06 | 286116 | BHD44A | Urban | LV Transformer SC278-J BHD44A - Planned | 0.8083 | 262 | 211.7746 | 0.00021334 | 8.1426e-07
2012-12-06 | 286117 | CRB24B | Urban | LV Transformer SP1108-J CRB24B - Planned | 126.43 | 558 | 70547.94 | 0.071068 | 0.00012736
2012-12-06 | 286118 | SGT5 | Urban | LV Transformer SP4392-F SGT5 - Planned | 7.865 | 218 | 1714.57 | 0.0017272 | 7.923e-06
2012-12-06 | 286119 | BHL2A | Urban | LV Transformer SP16003-B BHL2A - Planned | 15.425 | 290 | 4473.25 | 0.0045062 | 1.5539e-05
2012-12-06 | 286120 | HDA11A | Urban | LV Transformer SP5166-G HDA11A - Planned | 21.36 | 263 | 5617.68 | 0.0056591 | 2.1517e-05
2012-12-06 | 286121 | DRD3A | Urban | LV Transformer SP434843 DRD3A - Planned | 26.56 | 315 | 8366.4 | 0.0084281 | 2.6756e-05
2012-12-06 | 286122 | WSE3A | Rural short | LV Transformer SP5756-C WSE3A - Planned | 0.4 | 91 | 36.4 | 0.00010477 | 1.1513e-06
2012-12-06 | 286123 | BLB8B | Urban | LV Transformer SP3101-I QPT22A - Planned | 9.05 | 325 | 2941.25 | 0.0029629 | 9.1167e-06
2012-12-06 | 286123 | QPT22A | Urban | LV Transformer SP3101-I QPT22A - Planned | 7.77 | 325 | 2525.25 | 0.0025439 | 7.8273e-06
2012-12-06 | 286124 | CRM16A | Rural short | LV Transformer SP5321-D CRM16A - Planned | 10.36 | 293 | 3035.48 | 0.0087369 | 2.9819e-05
2012-12-06 | 286124 | KSN6 | Urban | LV Transformer SP5321-D CRM16A - Planned | 4.7532 | 293 | 1392.6876 | 0.001403 | 4.7882e-06
2012-12-06 | 286125 | BLBNFM6 | Urban | LV Transformer SP40370-C BLBNFM6 - Planned | 13.94 | 210 | 2927.4 | 0.002949 | 1.4043e-05
2012-12-06 | 286126 | HPE16A | Urban | LV Transformer SC4587-G HPE16A - Planned | 23.8342 | 280 | 6673.576 | 0.0067228 | 2.401e-05
2012-12-06 | 286127 | EMP4A | Urban | LV Transformer SP755-N EMP4A - Planned | 22.62 | 300 | 6786 | 0.006836 | 2.2787e-05
2012-12-06 | 286128 | WHO1 | Rural short | LV Transformer SP2309-D WHO1 - Planned | 4.5 | 382 | 1719 | 0.0049477 | 1.2952e-05
2012-12-06 | 286130 | SPC2B | Rural short | LV Transformer SP8135-B SPC2B - Planned | 1.98 | 325 | 643.5 | 0.0018522 | 5.699e-06
2012-12-06 | 286131 | WSO13A | Rural short | LV Transformer SP3259-D WSO13A - Planned | 56.97 | 413 | 23528.61 | 0.067721 | 0.00016397
2012-12-06 | 286146 | SPE12 | Urban | LV Transformer SC484388 SPE12 - Planned | 5.2 | 73 | 522.08 | 0.00052593 | 5.2383e-06
2012-12-07 | 286152 | MSV1 | Rural short | LV Transformer SP2806-C MSV1 - Planned | 5 | 95 | 475 | 0.0013677 | 1.4397e-05
2012-12-07 | 286154 | GBN3 | Rural short | LV Transformer SP6201-A GBN3 - Planned | 4 | 130 | 520 | 0.0014973 | 1.1518e-05
2012-12-07 | 286155 | RLB13B | Rural short | Feeder RLB13B - Planned | 10 | 233 | 2330 | 0.0067091 | 2.8794e-05
2012-12-07 | 286157 | YDA3A | Rural short | LV Transformer SP16354-A YDA3A - Planned | 13 | 209 | 2717 | 0.0078234 | 3.7432e-05
2012-12-07 | 286158 | GYN7A | Rural short | LV Transformer SP6520-D GYN7A - Planned | 2.01 | 255 | 512.55 | 0.0014758 | 5.7876e-06
2012-12-07 | 286160 | TGW1 | Rural short | Feeder TGW1 - Planned | 56.46 | 228 | 12872.88 | 0.037066 | 0.00016257
2012-12-07 | 286162 | IPL3 | Rural short | Feeder IPL3 - Planned | 17.2 | 287 | 4936.4 | 0.014214 | 4.9526e-05
2012-12-07 | 286163 | MLY1 | Rural short | LV Transformer SP5333-A MLY1 - Planned | 2.01 | 354 | 711.54 | 0.0020488 | 5.7876e-06
2012-12-07 | 286164 | MLY3 | Rural short | LV Transformer SP7817-A MLY3 - Planned | 0.4 | 370 | 148 | 0.00042615 | 1.1518e-06
2012-12-07 | 286165 | FDS4 | Rural short | Feeder FDS4 - Planned | 5.01 | 405 | 2029.05 | 0.0058425 | 1.4426e-05
2012-12-07 | 286166 | MCW7 | Rural short | Feeder MCW7 - Planned | 13.465 | 336 | 4524.24 | 0.013027 | 3.8771e-05
2012-12-07 | 286168 | TRG2A | Urban | LV Transformer SP961-J TRG2A - Planned | 27.342 | 169 | 4620.798 | 0.0046563 | 2.7552e-05
2012-12-07 | 286169 | AGE4B | Urban | LV Transformer SP484056 AGE4B - Planned | 24.465 | 213 | 5211.045 | 0.005251 | 2.4653e-05
2012-12-07 | 286170 | GYM7A | Rural short | LV Transformer SP6437-D GYM7A - Planned | 5.04 | 178 | 897.12 | 0.0025832 | 1.4512e-05
2012-12-07 | 286171 | GYM7A | Rural short | LV Transformer SP9319-B GYM7A - Planned | 10.01 | 53 | 530.53 | 0.0015276 | 2.8823e-05
2012-12-07 | 286172 | GYM7A | Rural short | LV Transformer SP9320-A GYM7A - Planned | 4.98 | 61 | 303.78 | 0.00087471 | 1.434e-05
2012-12-07 | 286173 | GBN3 | Rural short | LV Transformer SP2555-D GBN3 - Planned | 3.5 | 175 | 612.5 | 0.0017636 | 1.0078e-05
2012-12-07 | 286174 | MLY3 | Rural short | LV Transformer SP1245-B MLY3 - Planned | 8.01 | 230 | 1842.3 | 0.0053048 | 2.3064e-05
2012-12-07 | 286175 | GYM7A | Rural short | LV Transformer SP9318-B GYM7A - Planned | 5.2539 | 49 | 257.4411 | 0.00074128 | 1.5128e-05
2012-12-07 | 286176 | BBH8A | Urban | LV Transformer SP2693-G BBH8A - Planned | 38.925 | 503 | 19579.275 | 0.01973 | 3.9224e-05
2012-12-07 | 286177 | JBB16A | Rural short | LV Transformer SP6495-E JBB16A - Planned | 4 | 352 | 1408 | 0.0040542 | 1.1518e-05
2012-12-07 | 286179 | LDR8 | Urban | LV Transformer SP13669-B LDR8 - Planned | 17.245 | 273 | 4707.885 | 0.004744 | 1.7377e-05
2012-12-07 | 286180 | BHL2A | Urban | LV Transformer SP710-J BHL3A - Planned | 3.16 | 329 | 1039.64 | 0.0010476 | 3.1842e-06
2012-12-07 | 286180 | BHL3A | Urban | LV Transformer SP710-J BHL3A - Planned | 19 | 329 | 6251 | 0.006299 | 1.9146e-05
2012-12-07 | 286181 | SGT24A | Urban | LV Transformer SP3793-D SGT24A - Planned | 8.03 | 120 | 963.6 | 0.00097099 | 8.0916e-06
2012-12-07 | 286181 | SGT5 | Urban | LV Transformer SP3793-D SGT24A - Planned | 3.99 | 120 | 478.8 | 0.00048247 | 4.0206e-06
2012-12-07 | 286182 | KWA10A | Urban | LV Transformer SP4408-B KWA10A - Planned | 3.8 | 141 | 535.8 | 0.00053991 | 3.8292e-06
2012-12-07 | 286183 | BLB8B | Urban | LV Transformer SP946-J BLB8B - Planned | 19.475 | 331 | 6446.225 | 0.0064957 | 1.9624e-05
2012-12-07 | 286184 | BLBNFM6 | Urban | LV Transformer SP3112-H BLBNFM6 - Planned | 2.3466 | 273 | 640.6218 | 0.00064554 | 2.3646e-06
2012-12-07 | 286185 | RLA5 | Urban | LV Transformer SP3421-I RLA5 - Planned | 5.2375 | 250 | 1309.375 | 0.0013194 | 5.2777e-06
2012-12-07 | 286186 | KLG7A | Rural short | Feeder KLG7A - Planned | 10.5 | 593 | 6226.5 | 0.017929 | 3.0234e-05
2012-12-07 | 286207 | AGE5B | Urban | LV Transformer SP2754-N AGE5B - Planned | 50.04 | 419 | 20966.76 | 0.021128 | 5.0424e-05
2012-12-08 | 286214 | CNB24A | Rural short | LV Transformer SP2838-D CNB24A - Planned | 12.92 | 367 | 4741.64 | 0.013659 | 3.7217e-05
2012-12-08 | 286215 | UMG2B | Rural short | LV Transformer SP2445-J UMG2B - Planned | 18 | 155 | 2790 | 0.0080369 | 5.1851e-05
2012-12-09 | 286220 | NDH7 | Urban | LV Transformer SC621096 NDH7 - Planned | 4.5 | 488 | 2196 | 0.0022141 | 4.5371e-06
2012-12-09 | 286221 | MDR25A | Urban | Feeder MDR25A, MDR3A - Planned | 4 | 448 | 1792 | 0.0018068 | 4.0329e-06
2012-12-09 | 286221 | MDR3A | Urban | Feeder MDR25A, MDR3A - Planned | 60 | 448 | 26880 | 0.027101 | 6.0494e-05
2012-12-09 | 286224 | SHW4 | Urban | LV Transformer SP2506-N SHW4 - Planned | 8.16 | 410 | 3345.6 | 0.0033732 | 8.2272e-06
2012-12-09 | 286225 | MLS10B | Urban | LV Transformer SG7133-I MLS10B - Planned | 2.375 | 32 | 76 | 7.6626e-05 | 2.3946e-06
2012-12-09 | 286226 | AGE4B | Urban | LV Transformer SG1086-N AGE4B - Planned | 14.49 | 329 | 4767.21 | 0.0048065 | 1.4609e-05
2012-12-09 | 286227 | MDR25A | Urban | LV Transformer SP11109-D MDR25A - Planned | 4.0362 | 301 | 1214.8962 | 0.0012249 | 4.0694e-06
2012-12-09 | 286228 | GBG1A | Urban | LV Transformer SC783551 GBG23A - Planned | 0.98 | 167 | 163.66 | 0.00016501 | 9.8807e-07
2012-12-09 | 286228 | GBG1B | Urban | LV Transformer SC783551 GBG23A - Planned | 9.92 | 167 | 1656.64 | 0.0016703 | 1.0002e-05
2012-12-09 | 286228 | GBG23A | Urban | LV Transformer SC783551 GBG23A - Planned | 1 | 167 | 167 | 0.00016838 | 1.0082e-06
2012-12-09 | 286229 | WNM3 | Urban | LV Transformer SP375789 WNM3 - Planned | 2.145 | 264 | 566.28 | 0.00057094 | 2.1627e-06
2012-12-09 | 286230 | PMBWED19 | Urban | LV Transformer SC22568-C PMBWED19 - Planned | 4 | 47 | 188 | 0.00018955 | 4.0329e-06
2012-12-09 | 286277 | ENG8 | Urban | LV Transformer SC480438 ENG8 - Planned | 16.5433 | 276 | 4565.9508 | 0.0046036 | 1.668e-05
2012-12-09 | 286298 | ENG8 | Urban | LV Transformer SC772973 ENG8 - Planned | 16.5433 | 276 | 4565.9508 | 0.0046036 | 1.668e-05
2012-12-10 | 286241 | MFN3B | Urban | Feeder MFN3B - Planned | 1.92 | 149 | 286.08 | 0.00028854 | 1.9365e-06
2012-12-10 | 286265 | BNH5A | Rural short | LV Transformer SP9460-D BNH5A - Planned | 1 | 194 | 194 | 0.00055929 | 2.883e-06
2012-12-10 | 286270 | MLY3 | Rural short | LV Transformer SP4344-B MLY3 - Planned | 2.01 | 234 | 470.34 | 0.001356 | 5.7947e-06
2012-12-10 | 286273 | NBR1 | Rural short | LV Transformer SP9502-A NBR1 - Planned | 28.13 | 175 | 4922.75 | 0.014192 | 8.1098e-05
2012-12-10 | 286280 | JBB16A | Rural short | Feeder JBB16A - Planned | 17.98 | 327 | 5879.46 | 0.01695 | 5.1836e-05
2012-12-10 | 286291 | LLY1 | Rural short | LV Transformer SP2584-D LLY1 - Planned | 3.375 | 403 | 1360.125 | 0.0039212 | 9.73e-06
2012-12-10 | 286295 | HPE12A | Urban | LV Transformer SP164-O HPE12A - Planned | 1.23 | 527 | 648.21 | 0.00065377 | 1.2406e-06
2012-12-10 | 286295 | HPK9 | Urban | LV Transformer SP164-O HPE12A - Planned | 4.02 | 527 | 2118.54 | 0.0021367 | 4.0545e-06
2012-12-10 | 286296 | BLB8A | Urban | LV Transformer SP3446-G BLB8A - Planned | 9.283 | 369 | 3425.427 | 0.0034548 | 9.3627e-06
2012-12-10 | 286297 | SHW12 | Urban | LV Transformer SC1390545 SHW12 - Planned | 3.083 | 64 | 197.312 | 0.00019901 | 3.1095e-06
2012-12-10 | 286299 | SHW12 | Urban | LV Transformer SP920-L SHW12 - Planned | 44.0409 | 297 | 13080.1473 | 0.013192 | 4.4419e-05
2012-12-10 | 286300 | MLB6A | Rural short | LV Transformer SP4567-B MLB6A - Planned | 7.02 | 217 | 1523.34 | 0.0043917 | 2.0238e-05
2012-12-10 | 286301 | PGN1B | Rural short | LV Transformer SP1001-F PGN1B - Planned | 13 | 231 | 3003 | 0.0086575 | 3.7478e-05
2012-12-10 | 286302 | AMR3 | Rural short | LV Transformer SP307-D AMR3 - Planned | 3.67 | 92 | 337.64 | 0.0009734 | 1.058e-05
2012-12-10 | 286303 | BBH12B | Urban | LV Transformer SP4628-G BBH12B - Planned | 30.537 | 114 | 3481.218 | 0.0035111 | 3.0799e-05
2012-12-10 | 286304 | LDR8 | Urban | LV Transformer SG7089-F LDR8 - Planned | 9.9 | 220 | 2178 | 0.0021967 | 9.985e-06
2012-12-10 | 286305 | BBH8A | Urban | LV Transformer SC732642 BBH8A - Planned | 81.94 | 365 | 29908.1 | 0.030165 | 8.2643e-05
2012-12-10 | 286306 | SGT5 | Urban | LV Transformer SP2836-I SGT5 - Planned | 71.72 | 278 | 19938.16 | 0.020109 | 7.2336e-05
2012-12-10 | 286307 | DRD3A | Urban | LV Transformer SP2777-G DRD3A - Planned | 8.775 | 235 | 2062.125 | 0.0020798 | 8.8503e-06
2012-12-10 | 286308 | SPF17B | Urban | LV Transformer SC21463-D SPF17B - Planned | 9.8665 | 91 | 897.8515 | 0.00090556 | 9.9512e-06
2012-12-10 | 286312 | QEN10 | Urban | LV Transformer SC1835294 QEN10 - Planned | 0.99 | 85 | 84.15 | 8.4872e-05 | 9.985e-07
2012-12-10 | 286629 | MFN3B | Urban | Feeder MFN3B - Planned | 1.92 | 149 | 286.08 | 0.00028854 | 1.9365e-06
2012-12-10 | 286630 | BPN28A | Rural short | LV Transformer SP17970-E BPN28A - Planned | 0.424 | 90 | 38.16 | 0.00011001 | 1.2224e-06
2012-12-10 | 286631 | BHD35A | Rural short | Feeder BHD35A - Planned | 29.5 | 179 | 5280.5 | 0.015223 | 8.5047e-05
2012-12-11 | 286348 | CCY3B | Urban | LV Transformer SC720-G CCY3B - Planned | 70 | 87 | 6090 | 0.0061441 | 7.0622e-05
2012-12-11 | 286349 | PPE13A | Rural short | LV Transformer SP388-I PPE13A - Planned | 11.5 | 199 | 2288.5 | 0.0066004 | 3.3168e-05
2012-12-11 | 286353 | PRG2A | Rural short | LV Transformer SP5424-A PRG2A - Planned | 7 | 215 | 1505 | 0.0043407 | 2.0189e-05
2012-12-11 | 286356 | MCW11 | Rural short | LV Transformer SP4213-D MCW11 - Planned | 24.5 | 265 | 6492.5 | 0.018725 | 7.0662e-05
2012-12-11 | 286357 | CRM16A | Rural short | LV Transformer SP13837-B CRM16A - Planned | 4 | 299 | 1196 | 0.0034495 | 1.1537e-05
2012-12-11 | 286359 | GGR1 | Rural short | LV Transformer SP781802 GGR1 - Planned | 0.4 | 316 | 126.4 | 0.00036456 | 1.1537e-06
2012-12-11 | 286360 | CRM13A | Urban | LV Transformer SP5029-E CRM13A - Planned | 6 | 86 | 516 | 0.00052058 | 6.0533e-06
2012-12-11 | 286361 | BHD23A | Rural short | LV Transformer SP467670 BHD23A - Planned | 31.04 | 342 | 10615.68 | 0.030617 | 8.9524e-05
2012-12-11 | 286362 | MBG2 | Rural short | LV Transformer SP14024-D MBG2 - Planned | 1 | 379 | 379 | 0.0010931 | 2.8842e-06
2012-12-11 | 286363 | MRB1 | Urban | Feeder MRB1, MRB2 - Planned | 1 | 343 | 343 | 0.00034605 | 1.0089e-06
2012-12-11 | 286363 | MRB2 | Rural short | Feeder MRB1, MRB2 - Planned | 7.072 | 343 | 2425.696 | 0.0069961 | 2.0397e-05
2012-12-11 | 286364 | CRB25A | Rural short | Feeder CRB25A - Planned | 67.96 | 403 | 27387.88 | 0.078991 | 0.00019601
2012-12-11 | 286365 | KWA2A | Urban | Feeder KWA2A - Planned | 143 | 400 | 57200 | 0.057708 | 0.00014427
2012-12-11 | 286366 | NBR9 | Rural short | LV Transformer SP3955-B NBR9 - Planned | 31.04 | 219 | 6797.76 | 0.019606 | 8.9524e-05
2012-12-11 | 286367 | MLB6A | Rural short | Feeder MLB6A - Planned | 2.01 | 355 | 713.55 | 0.002058 | 5.7972e-06
2012-12-11 | 286368 | KWH3 | Rural short | Feeder KWH3 - Planned | 6.99 | 338 | 2362.62 | 0.0068142 | 2.016e-05
2012-12-11 | 286370 | KBR2A | Rural short | Feeder KBR2A - Planned | 10 | 400 | 4000 | 0.011537 | 2.8842e-05
2012-12-11 | 286371 | SMF3A | Rural short | Feeder SMF3A - Planned | 116 | 470 | 54520 | 0.15724 | 0.00033456
2012-12-11 | 286373 | MWMRBK11 | Rural short | LV Transformer SP7943-C MWMRBK11 - Planned | 2.5 | 430 | 1075 | 0.0031005 | 7.2104e-06
2012-12-11 | 286375 | MLB12A | Rural short | LV Transformer SP13939-A MLB12A - Planned | 32.255 | 553 | 17837.015 | 0.051445 | 9.3028e-05
2012-12-11 | 286377 | BBSRDL8 | Rural short | LV Transformer SC1299410 - Planned | 2 | 347 | 694 | 0.0020016 | 5.7683e-06
2012-12-11 | 286378 | HPE12A | Urban | LV Transformer SP164-O HPE12A - Planned | 29.52 | 440 | 12988.8 | 0.013104 | 2.9782e-05
2012-12-11 | 286379 | KMR17A | Urban | LV Transformer SP2566-O KMR27A - Planned | 1.365 | 205 | 279.825 | 0.00028231 | 1.3771e-06
2012-12-11 | 286379 | KMR27A | Urban | LV Transformer SP2566-O KMR27A - Planned | 18.5724 | 205 | 3807.342 | 0.0038412 | 1.8737e-05
2012-12-11 | 286381 | GYM7A | Rural short | LV Transformer SP301120-A GYM7A - Planned | 3.04 | 217 | 659.68 | 0.0019026 | 8.7678e-06
2012-12-11 | 286382 | CLD1A | Urban | LV Transformer SP13846-B CLD1A - Planned | 191.5 | 98 | 18767 | 0.018934 | 0.0001932
2012-12-11 | 286382 | CMD11A | Rural short | LV Transformer SP13846-B CLD1A - Planned | 321.16 | 98 | 31473.68 | 0.090775 | 0.00092628
2012-12-11 | 286383 | HWL2A | Urban | LV Transformer SC1247-H HWL2A - Planned | 8 | 80 | 640 | 0.00064568 | 8.071e-06
2012-12-11 | 286384 | CNB24A | Rural short | LV Transformer SP2838-D CNB24A - Planned | 25.5 | 396 | 10098 | 0.029124 | 7.3546e-05
2012-12-11 | 286385 | LDR8 | Urban | LV Transformer SP2853-E LDR8 - Planned | 52.92 | 392 | 20744.64 | 0.020929 | 5.339e-05
2012-12-11 | 286386 | CRB25A | Rural short | LV Transformer SP12821-B CRB25A - Planned | 48.41 | 506 | 24495.46 | 0.070649 | 0.00013962
2012-12-11 | 286387 | BHD23A | Rural short | LV Transformer SP17420-D BHD23A - Planned | 26.4 | 350 | 9240 | 0.02665 | 7.6142e-05
2012-12-11 | 286388 | BHL2A | Urban | LV Transformer SP2401-J BHL2A - Planned | 27.05 | 267 | 7222.35 | 0.0072865 | 2.729e-05
2012-12-11 | 286388 | BHL3A | Urban | LV Transformer SP2401-J BHL2A - Planned | 6.08 | 267 | 1623.36 | 0.0016378 | 6.134e-06
2012-12-11 | 286389 | DRD3A | Urban | LV Transformer SP4688-D DRD3A - Planned | 22.94 | 311 | 7134.34 | 0.0071977 | 2.3144e-05
2012-12-11 | 286390 | SGT7 | Urban | LV Transformer SP3057-G SGT7 - Planned | 89.83 | 174 | 15630.42 | 0.015769 | 9.0628e-05
2012-12-11 | 286391 | QPT5 | Urban | LV Transformer SP388-Q QPT5 - Planned | 1.11 | 344 | 381.84 | 0.00038523 | 1.1199e-06
2012-12-11 | 286392 | RPN3A | Urban | LV Transformer SP3888-B RPN3A - Planned | 36.65 | 310 | 11361.5 | 0.011462 | 3.6975e-05
2012-12-11 | 286632 | LLY1 | Rural short | LV Transformer SP17529-B LLY1 - Planned | 3 | 490 | 1470 | 0.0042397 | 8.6525e-06
2012-12-12 | 286420 | SMF3A | Rural short | LV Transformer SP1545-F SMF3A - Planned | 31 | 79 | 2449 | 0.0070662 | 8.9446e-05
2012-12-12 | 286422 | MSV1 | Rural short | LV Transformer SP2372-C MSV1 - Planned | 0.4 | 205 | 82 | 0.0002366 | 1.1541e-06
2012-12-12 | 286441 | ZMR7A | Urban | LV Transformer SC692044 ZMR7A - Planned | 5 | 71 | 355 | 0.00035826 | 5.0459e-06
2012-12-12 | 286442 | CBW11 | Rural short | LV Transformer SP4980-E CBW11 - Planned | 6 | 322 | 1932 | 0.0055745 | 1.7312e-05
2012-12-12 | 286443 | FDS4 | Rural short | Feeder FDS4 - Planned | 12 | 348 | 4176 | 0.012049 | 3.4624e-05
2012-12-12 | 286444 | NBR1 | Rural short | Feeder NBR1 - Planned | 19.05 | 349 | 6648.45 | 0.019183 | 5.4966e-05
2012-12-12 | 286445 | BMT2 | Rural short | LV Transformer SP980-D BMT2 - Planned | 6 | 253 | 1518 | 0.00438 | 1.7312e-05
2012-12-12 | 286446 | GBN4 | Rural short | Feeder GBN4 - Planned | 15.04 | 311 | 4677.44 | 0.013496 | 4.3396e-05
2012-12-12 | 286447 | BMT4 | Rural short | LV Transformer SP5431-C BMT4 - Planned | 15.04 | 149 | 2240.96 | 0.006466 | 4.3396e-05
2012-12-12 | 286450 | WHO1 | Rural short | Feeder WHO1 - Planned | 26.97 | 379 | 10221.63 | 0.029493 | 7.7818e-05
2012-12-12 | 286451 | TGW1 | Rural short | Feeder TGW1 - Planned | 11.325 | 402 | 4552.65 | 0.013136 | 3.2677e-05
2012-12-12 | 286462 | HPK9 | Urban | LV Transformer SP6125-F HPK9 - Planned | 18.09 | 371 | 6711.39 | 0.006773 | 1.8256e-05
2012-12-12 | 286463 | BBSRDL8 | Rural short | LV Transformer SC1299410 - Planned | 2 | 131 | 262 | 0.00075596 | 5.7707e-06
2012-12-12 | 286464 | AGE8 | Urban | LV Transformer SP2171-I AGE8 - Planned | 4.375 | 232 | 1015 | 0.0010243 | 4.4152e-06
2012-12-12 | 286465 | AHL8A | Urban | LV Transformer SP4649-M AHL8A - Planned | 9.01 | 73 | 657.73 | 0.00066377 | 9.0927e-06
2012-12-12 | 286466 | AGE10 | Urban | LV Transformer SG794-N AGE10 - Planned | 2.7 | 352 | 950.4 | 0.00095913 | 2.7248e-06
2012-12-12 | 286467 | KMR27A | Urban | LV Transformer SP671-N KMR27A - Planned | 13.32 | 240 | 3196.8 | 0.0032262 | 1.3442e-05
2012-12-12 | 286468 | AGE3 | Urban | LV Transformer SP2531-F AGE3 - Planned | 41.85 | 266 | 11132.1 | 0.011234 | 4.2234e-05
2012-12-12 | 286469 | CLD20A | Rural short | LV Transformer SC1563-A CLD20A - Planned | 80.2 | 40 | 3208 | 0.0092562 | 0.00023141
2012-12-12 | 286470 | BWH7A | Rural short | LV Transformer SP9554-A BWH7A - Planned | 26.685 | 231 | 6164.235 | 0.017786 | 7.6996e-05
2012-12-12 | 286471 | CNB24A | Rural short | LV Transformer SP6783-E CNB24A - Planned | 3.75 | 493 | 1848.75 | 0.0053343 | 1.082e-05
2012-12-12 | 286472 | CRB25A | Rural short | LV Transformer SP5677-F CRB25A - Planned | 10.58 | 115 | 1216.7 | 0.0035106 | 3.0527e-05
2012-12-12 | 286473 | PBH8 | Urban | LV Transformer SP5738-D PBH8 - Planned | 11.76 | 195 | 2293.2 | 0.0023143 | 1.1868e-05
2012-12-12 | 286474 | LDR8 | Urban | LV Transformer SP468825 LDR8 - Planned | 31.75 | 348 | 11049 | 0.01115 | 3.2042e-05
2012-12-12 | 286475 | TGP2A | Urban | LV Transformer SC1383861 TGP2A - Planned | 3.12 | 52 | 162.24 | 0.00016373 | 3.1486e-06
2012-12-12 | 286476 | HDA10A | Urban | LV Transformer SP2299-E HDA11A - Planned | 1.205 | 348 | 419.34 | 0.00042319 | 1.2161e-06
2012-12-12 | 286476 | HDA11A | Urban | LV Transformer SP2299-E HDA11A - Planned | 24.6026 | 348 | 8561.7048 | 0.0086403 | 2.4828e-05
2012-12-12 | 286477 | DRD3A | Urban | LV Transformer SP2777-G DRD3A - Planned | 31.2 | 332 | 10358.4 | 0.010454 | 3.1486e-05
2012-12-12 | 286478 | TGP2A | Urban | LV Transformer SC516588 TGP2A - Planned | 11 | 70 | 770 | 0.00077707 | 1.1101e-05
2012-12-12 | 286479 | MRK9 | Urban | LV Transformer SP1486-L MRK9 - Planned | 20.4256 | 396 | 8088.5376 | 0.0081628 | 2.0613e-05
2012-12-12 | 286480 | MRK9 | Urban | LV Transformer SP1486-L MRK9 - Planned | 14.0426 | 443 | 6220.8718 | 0.006278 | 1.4172e-05
2012-12-12 | 286481 | WSO13A | Rural short | LV Transformer SP3259-D WSO13A - Planned | 65.77 | 300 | 19731 | 0.056931 | 0.00018977
2012-12-12 | 286482 | WED4B | Urban | LV Transformer SC164-N WED4B - Planned | 4.2699 | 262 | 1118.7138 | 0.001129 | 4.3091e-06
2012-12-12 | 286483 | BKD2B | Urban | LV Transformer SP2399-E BKD2B - Planned | 4.76 | 77 | 366.52 | 0.00036989 | 4.8037e-06
2012-12-12 | 286484 | GTN12A | Rural short | LV Transformer SP17515-A GTN12A - Planned | 2.2 | 80 | 176 | 0.00050782 | 6.3478e-06
2012-12-12 | 286485 | THL2 | Rural short | LV Transformer SP3024-B THL2 - Planned | 0.99 | 105 | 103.95 | 0.00029993 | 2.8565e-06
2012-12-12 | 286488 | QEN10 | Urban | LV Transformer SC1835294 QEN10 - Planned | 0.99 | 114 | 112.86 | 0.0001139 | 9.9909e-07
2012-12-13 | 286493 | SGT9 | Urban | LV Transformer SC6275-D SGT9 - Planned | 38 | 64 | 2432 | 0.002455 | 3.836e-05
2012-12-13 | 286494 | GBN2 | Rural short | LV Transformer SP63-B GBN2 - Planned | 1 | 25 | 25 | 7.2165e-05 | 2.8866e-06
2012-12-13 | 286498 | KBR2A | Rural short | Feeder KBR2A - Planned | 7 | 380 | 2660 | 0.0076783 | 2.0206e-05
2012-12-13 | 286500 | 341 | Urban | Feeder 341 - Planned | 29.01 | 352 | 10211.52 | 0.010308 | 2.9285e-05
2012-12-13 | 286501 | ESK2B | Rural short | Feeder ESK2B - Planned | 4.01 | 388 | 1555.88 | 0.0044912 | 1.1575e-05
2012-12-13 | 286502 | WSE5A | Rural short | Feeder GTN12A, WSE5A - Planned | 51.01 | 425 | 21679.25 | 0.062579 | 0.00014725
2012-12-13 | 286503 | BDT1 | Rural short | Feeder BDT1 - Planned | 6 | 413 | 2478 | 0.007153 | 1.732e-05
2012-12-13 | 286504 | ARL6B | Urban | LV Transformer SP12496-C ARL6B - Planned | 2 | 530 | 1060 | 0.00107 | 2.019e-06
2012-12-13 | 286506 | AHD18B | Rural short | LV Transformer SC2084200 AHD18B - Planned | 0.99 | 170 | 168.3 | 0.00048581 | 2.8577e-06
2012-12-13 | 286507 | MRD6 | Urban | LV Transformer SC1050752 MRD6 - Planned | 19.1936 | 438 | 8406.7968 | 0.0084865 | 1.9375e-05
2012-12-13 | 286508 | TRG5 | Urban | LV Transformer SC2804-K TRG5 - Planned | 3.09 | 357 | 1103.13 | 0.0011136 | 3.1193e-06
2012-12-13 | 286509 | CSE2 | Urban | LV Transformer SC4431-L CSE2 - Planned | 16.4977 | 368 | 6071.1536 | 0.0061287 | 1.6654e-05
2012-12-13 | 286510 | GAP9A | Urban | LV Transformer SP2127-I GAP9A - Planned | 56.16 | 447 | 25103.52 | 0.025341 | 5.6692e-05
2012-12-13 | 286511 | PWC4 | Rural short | LV Transformer SP12827-A PWC4 - Planned | 27.2603 | 365 | 9950.0095 | 0.028722 | 7.8689e-05
2012-12-13 | 286512 | IPL1 | Rural short | LV Transformer SP1474-G IPL1 - Planned | 4.98 | 78 | 388.44 | 0.0011213 | 1.4375e-05
2012-12-13 | 286513 | BHD44A | Urban | LV Transformer SP3831-E BHD44A - Planned | 25.64 | 318 | 8153.52 | 0.0082308 | 2.5883e-05
2012-12-13 | 286514 | RBA43A | Rural short | LV Transformer SP743382 RBA43A - Planned | 24.48 | 223 | 5459.04 | 0.015758 | 7.0664e-05
2012-12-13 | 286515 | IPL3 | Rural short | LV Transformer SP3534-B IPL3 - Planned | 2.01 | 153 | 307.53 | 0.00088771 | 5.8021e-06
2012-12-13 | 286516 | SPO51A | Urban | LV Transformer SP1112-G SPO51A - Planned | 11.935 | 512 | 6110.72 | 0.0061686 | 1.2048e-05
2012-12-13 | 286517 | LDR8 | Urban | LV Transformer SP468825 LDR8 - Planned | 39.37 | 197 | 7755.89 | 0.0078294 | 3.9743e-05
2012-12-13 | 286518 | KCY1 | Urban | LV Transformer SP1329-H KCY1 - Planned | 0.77 | 74 | 56.98 | 5.752e-05 | 7.773e-07
2012-12-13 | 286519 | ZMR9 | Urban | LV Transformer SP28442-A ZMR9 - Planned | 1.27 | 145 | 184.15 | 0.0001859 | 1.282e-06
2012-12-13 | 286520 | KWA12A | Urban | LV Transformer SP4413-B KWA12A - Planned | 143.5 | 278 | 39893 | 0.040271 | 0.00014486
2012-12-13 | 286521 | SGT24A | Urban | LV Transformer SC3910-F SGT24A - Planned | 11.31 | 318 | 3596.58 | 0.0036307 | 1.1417e-05
2012-12-13 | 286522 | SGT26A | Urban | LV Transformer SP2510-I SGT9 - Planned | 2.31 | 32 | 147.84 | 0.00014924 | 2.3319e-06
2012-12-13 | 286522 | SGT9 | Urban | LV Transformer SP2510-I SGT9 - Planned | 24.2658 | 32 | 433.0512 | 0.00043716 | 2.4496e-05
2012-12-13 | 286523 | HTN3B | Urban | LV Transformer SP2353-K HTN3B - Planned | 13.91 | 386 | 5369.26 | 0.0054201 | 1.4042e-05
2012-12-13 | 286524 | SGT24A | Urban | LV Transformer SP50-L SGT24A - Planned | 73.94 | 192 | 14196.48 | 0.014331 | 7.4641e-05
2012-12-13 | 286525 | CNB24A | Rural short | LV Transformer SP4859-E CNB24A - Planned | 3.15 | 333 | 1048.95 | 0.0030279 | 9.0928e-06
2012-12-13 | 286526 | BLB4A | Urban | LV Transformer SP39074-D BLB4A - Planned | 16.8 | 275 | 4620 | 0.0046638 | 1.6959e-05
2012-12-13 | 286527 | HPE16A | Urban | LV Transformer SC4066-G HPE16A - Planned | 20.5149 | 370 | 7590.513 | 0.0076624 | 2.0709e-05
2012-12-13 | 286528 | AGT25A | Urban | LV Transformer SP1469-L AGT25A - Planned | 9.1 | 205 | 1865.5 | 0.0018832 | 9.1862e-06
2012-12-13 | 286529 | HPK8A | Urban | LV Transformer SP1923-I HPK8A - Planned | 13.995 | 175 | 2449.125 | 0.0024723 | 1.4128e-05
2012-12-13 | 286530 | KBN1B | Rural short | LV Transformer SP5236-D KBN1B - Planned | 3 | 97 | 291 | 0.00084 | 8.6598e-06
2012-12-13 | 286531 | WHO1 | Rural short | LV Transformer SP2309-D WHO1 - Planned | 3 | 130 | 390 | 0.0011258 | 8.6598e-06
2012-12-13 | 286532 | ESK2B | Rural short | LV Transformer SP115-B ESK2B - Planned | 3.96 | 364 | 1441.44 | 0.0041609 | 1.1431e-05
2012-12-13 | 286581 | MLB6A | Rural short | Feeder MLB6A - Planned | 2.01 | 1230 | 2472.3 | 0.0071365 | 5.8021e-06
2012-12-13 | 286634 | NMC5A | Rural short | LV Transformer SP7945-F NMC5A - Planned | 3.04 | 277 | 842.08 | 0.0024307 | 8.7752e-06
2012-12-14 | 286575 | CBW11 | Rural short | LV Transformer SP8165-F CBW11 - Planned | 12 | 175 | 2100 | 0.0060645 | 3.4654e-05
2012-12-14 | 286576 | KBR2A | Rural short | Feeder KBR2A - Planned | 9.5 | 247 | 2346.5 | 0.0067763 | 2.7434e-05
2012-12-14 | 286577 | BMT3 | Rural short | LV Transformer SP49-A BMT3 - Planned | 1 | 18 | 18 | 5.1981e-05 | 2.8878e-06
2012-12-14 | 286578 | CBW11 | Rural short | LV Transformer SP7058-E CBW11 - Planned | 21 | 266 | 5586 | 0.016131 | 6.0645e-05
2012-12-14 | 286579 | RWD1 | Rural short | Feeder RWD1 - Planned | 82.5 | 170 | 14025 | 0.040502 | 0.00023825
2012-12-14 | 286580 | IPL1 | Rural short | LV Transformer SP2552-F IPL1 - Planned | 4.264 | 183 | 780.312 | 0.0022534 | 1.2314e-05
2012-12-14 | 286584 | LLY4 | Rural short | LV Transformer SP3949-C LLY4 - Planned | 1 | 23 | 23 | 6.642e-05 | 2.8878e-06
2012-12-14 | 286585 | CBW13 | Rural short | LV Transformer SP8135-D CBW13 - Planned | 26 | 150 | 3900 | 0.011263 | 7.5084e-05
2012-12-14 | 286586 | BMT3 | Rural short | LV Transformer SP4753-C BMT3 - Planned | 3 | 65 | 195 | 0.00056313 | 8.6635e-06
2012-12-14 | 286587 | BMT1 | Rural short | LV Transformer SP119-B BMT1 - Planned | 15.04 | 277 | 4166.08 | 0.012031 | 4.3433e-05
2012-12-14 | 286588 | MLB6A | Rural short | Feeder MLB6A - Planned | 37.22 | 233 | 8672.26 | 0.025044 | 0.00010749
2012-12-14 | 286590 | MRB2 | Rural short | Feeder TRP2, MRB2 - Planned | 13.59 | 406 | 5517.54 | 0.015934 | 3.9246e-05
2012-12-14 | 286590 | TRP2 | Rural short | Feeder TRP2, MRB2 - Planned | 1 | 406 | 406 | 0.0011725 | 2.8878e-06
2012-12-14 | 286594 | MRD6 | Urban | LV Transformer SC1050752 MRD6 - Planned | 7.1976 | 299 | 2152.0824 | 0.0021731 | 7.268e-06
2012-12-14 | 286595 | NMK7 | Urban | LV Transformer SP1174-P NMK7 - Planned | 6.425 | 151 | 970.175 | 0.00097966 | 6.4878e-06
2012-12-14 | 286596 | KMR27A | Urban | LV Transformer SP671-N KMR27A - Planned | 14.8 | 344 | 5091.2 | 0.005141 | 1.4945e-05
2012-12-14 | 286597 | GYM7A | Rural short | LV Transformer SP4803-D GYM7A - Planned | 15 | 160 | 2400 | 0.0069308 | 4.3318e-05
2012-12-14 | 286598 | NVL3 | Rural short | LV Transformer SP3206-C NVL3 - Planned | 6.55 | 154 | 1008.7 | 0.002913 | 1.8915e-05
2012-12-14 | 286599 | KWA2A | Urban | LV Transformer SP5265-A KWA2A - Planned | 83.025 | 265 | 22001.625 | 0.022217 | 8.3837e-05
2012-12-14 | 286600 | NVL5 | Rural short | LV Transformer SP3884-B NVL5 - Planned | 11.25 | 134 | 1507.5 | 0.0043534 | 3.2488e-05
2012-12-14 | 286601 | AHD4A | Urban | LV Transformer SP16482-A AHD4A - Planned | 5.1 | 77 | 392.7 | 0.00039654 | 5.1499e-06
2012-12-14 | 286602 | LDR8 | Urban | LV Transformer SG7089-F LDR8 - Planned | 11.88 | 170 | 2019.6 | 0.0020393 | 1.1996e-05
2012-12-14 | 286603 | LDR8 | Urban | LV Transformer SP8781-D LDR8 - Planned | 31.16 | 169 | 5266.04 | 0.0053175 | 3.1465e-05
2012-12-14 | 286604 | MTB3A | Rural short | LV Transformer SP4437-D MTB3A - Planned | 13.05 | 254 | 3314.7 | 0.0095723 | 3.7686e-05
2012-12-14 | 286605 | LDR1 | Urban | LV Transformer SP2178-H LDR1 - Planned | 10.665 | 117 | 1247.805 | 0.00126 | 1.0769e-05
2012-12-14 | 286606 | CMA9A | Urban | LV Transformer SP15906-B CMA9A - Planned | 3 | 244 | 732 | 0.00073916 | 3.0293e-06
2012-12-14 | 286607 | BBH8A | Urban | LV Transformer SP2869-H BBH8A - Planned | 19.6 | 342 | 6703.2 | 0.0067687 | 1.9792e-05
2012-12-14 | 286608 | PBH8 | Urban | LV Transformer SP13301-D PBH8 - Planned | 50.02 | 291 | 14555.82 | 0.014698 | 5.0509e-05
2012-12-14 | 286610 | DRD3A | Urban | LV Transformer SP4688-D DRD3A - Planned | 3 | 352 | 1056 | 0.0010663 | 3.0293e-06
2012-12-14 | 286611 | CBW11 | Rural short | LV Transformer SP9068-E CBW11 - Planned | 4.5 | 70 | 315 | 0.00090967 | 1.2995e-05
2012-12-14 | 286612 | BHL5A | Urban | LV Transformer SC5164-H SGT5 - Planned | 10.7 | 37 | 271.78 | 0.00027444 | 1.0805e-05
2012-12-14 | 286612 | SGT5 | Urban | LV Transformer SC5164-H SGT5 - Planned | 4.8 | 20 | 96 | 9.6939e-05 | 4.8469e-06
2012-12-14 | 286612 | SGT6 | Urban | LV Transformer SC5164-H SGT5 - Planned | 0.83 | 20 | 16.6 | 1.6762e-05 | 8.3811e-07
2012-12-14 | 286613 | WRG11A | Urban | LV Transformer SP3241-I WRG11A - Planned | 2.94 | 190 | 558.6 | 0.00056406 | 2.9687e-06
2012-12-14 | 286614 | HPK8A | Urban | LV Transformer SP30988-C HPK8A - Planned | 11.505 | 319 | 3670.095 | 0.003706 | 1.1617e-05
2012-12-14 | 286615 | HPE5A | Urban | LV Transformer SP2237-M HPE5A - Planned | 27.3397 | 95 | 2597.2715 | 0.0026227 | 2.7607e-05
2012-12-14 | 286616 | RPN8 | Rural short | LV Transformer SC2057229 RPN8 - Planned | 12.48 | 155 | 1934.4 | 0.0055862 | 3.604e-05
2012-12-14 | 286617 | MRB2 | Rural short | LV Transformer SP3102-B MRB2 - Planned | 4 | 324 | 1296 | 0.0037426 | 1.1551e-05
2012-12-15 | 286636 | MLB6A | Rural short | LV Transformer SC737528 MLB6A - Planned | 1 | 354 | 354 | 0.0010222 | 2.8877e-06
2012-12-15 | 286639 | BNH5A | Rural short | LV Transformer SP4132-D BNH5A - Planned | 6.0664 | 180 | 1091.952 | 0.0031532 | 1.7518e-05
2012-12-16 | 286647 | MDH9A | Urban | Feeder MDH9A - Planned | 2 | 600 | 1200 | 0.0012117 | 2.0195e-06
2012-12-16 | 286649 | KMR21B | Urban | LV Transformer SC484166 KMR21B - Planned | 2.87 | 165 | 473.55 | 0.00047817 | 2.898e-06
2012-12-16 | 286650 | CNB24A | Rural short | LV Transformer SP6783-E CNB24A - Planned | 13.5 | 346 | 4671 | 0.013488 | 3.8982e-05
2012-12-16 | 286651 | RCF10A | Urban | LV Transformer SP3392-C RCF10A - Planned | 9 | 186 | 1674 | 0.0016903 | 9.0878e-06
2012-12-16 | 286652 | HDA11A | Urban | LV Transformer SP5166-G HDA11A - Planned | 41.21 | 375 | 15453.75 | 0.015604 | 4.1612e-05
2012-12-16 | 286653 | SPE9 | Urban | LV Transformer SC1513000 SPE9 - Planned | 5.98 | 334 | 1997.32 | 0.0020168 | 6.0383e-06
2012-12-16 | 286654 | ZMR5 | Urban | LV Transformer SP63921-D ZMR5 - Planned | 4.05 | 343 | 1389.15 | 0.0014027 | 4.0895e-06
2012-12-16 | 286655 | WED21A | Urban | LV Transformer SC6759-G WED21A - Planned | 1.9599 | 270 | 529.173 | 0.00053433 | 1.979e-06
2012-12-17 | 286680 | GBN3 | Rural short | LV Transformer SP2563-E GBN3 - Planned | 3 | 72 | 216 | 0.00062366 | 8.6619e-06
2012-12-17 | 286686 | CBW11 | Rural short | LV Transformer SP4133-G CBW11 - Planned | 2 | 153 | 306 | 0.00088351 | 5.7746e-06
2012-12-17 | 286695 | MCW7 | Rural short | LV Transformer SP18005-C MCW7 - Planned | 30.07 | 228 | 6855.96 | 0.019795 | 8.6821e-05
2012-12-17 | 286700 | NMC5A | Rural short | Feeder NMC5A - Planned | 79 | 351 | 27729 | 0.080062 | 0.0002281
2012-12-17 | 286722 | SMF5A | Rural short | Feeder SMF5A - Planned | 24 | 525 | 12600 | 0.03638 | 6.9295e-05
2012-12-17 | 286731 | CLM9 | Urban | LV Transformer SP3968-B CLM9 - Planned | 1 | 522 | 522 | 0.00052708 | 1.0097e-06
2012-12-17 | 286735 | BMG2A | Urban | LV Transformer SC6159-G BMG2A - Planned | 18.601 | 92 | 1711.292 | 0.0017279 | 1.8782e-05
2012-12-17 | 286736 | SPO60A | Urban | LV Transformer SP53327-D SPO60A - Planned | 6.92 | 385 | 2664.2 | 0.0026901 | 6.9873e-06
2012-12-17 | 286737 | NGE4B | Urban | LV Transformer SP1905-I NGE4B - Planned | 10.3129 | 355 | 3661.0795 | 0.0036967 | 1.0413e-05
2012-12-17 | 286738 | NDH9 | Urban | LV Transformer SC772163 NDH9 - Planned | 1 | 394 | 394 | 0.00039783 | 1.0097e-06
2012-12-17 | 286739 | DBY7A | Urban | LV Transformer SC176130 DBY7A - Planned | 2.54 | 10 | 25.4 | 2.5647e-05 | 2.5647e-06
2012-12-17 | 286739 | DBY9 | Urban | LV Transformer SC176130 DBY7A - Planned | 1.86 | 10 | 18.6 | 1.8781e-05 | 1.8781e-06
2012-12-17 | 286740 | RBY15 | Urban | LV Transformer SP434-D RBY15 - Planned | 8.1198 | 230 | 1867.554 | 0.0018857 | 8.1988e-06
2012-12-17 | 286741 | WED20A | Urban | LV Transformer SP2466-K WED20A - Planned | 18.5233 | 361 | 6686.9113 | 0.006752 | 1.8704e-05
2012-12-17 | 286742 | BKD12A | Urban | LV Transformer SP4507-E BKD12A - Planned | 1.28 | 198 | 253.44 | 0.00025591 | 1.2925e-06
2012-12-17 | 286743 | QEN10 | Urban | LV Transformer SC1835294 QEN10 - Planned | 0.99 | 72 | 71.28 | 7.1974e-05 | 9.9963e-07
2012-12-17 | 286888 | CMD5A | Urban | LV Transformer SC550212 CMD5A - Planned | 1.005 | 32.5 | 65.325 | 6.5961e-05 | 1.0148e-06
2012-12-17 | 287237 | CRB25A | Rural short | Feeder CRB25A - Planned | 49.48 | 228 | 11281.44 | 0.032573 | 0.00014286
2012-12-18 | 286809 | KCY4 | Rural short | LV Transformer SP7111-C KCY4 - Planned | 11 | 169 | 1859 | 0.0053672 | 3.1758e-05
2012-12-18 | 286810 | PPE16A | Rural short | LV Transformer SP1614-D PPE16A - Planned | 12.5 | 192 | 2400 | 0.0069291 | 3.6089e-05
2012-12-18 | 286811 | NRA13A | Rural short | LV Transformer SP5642-C NRA13A - Planned | 5.5 | 248 | 1364 | 0.003938 | 1.5879e-05
2012-12-18 | 286819 | KBR2A | Rural short | Feeder KBR2A - Planned | 8.41 | 267 | 2245.47 | 0.006483 | 2.4281e-05
2012-12-18 | 286842 | BTN2 | Rural short | Feeder BTN2 - Planned | 32.25 | 307 | 9900.75 | 0.028585 | 9.311e-05
2012-12-18 | 286843 | BDT5 | Rural short | Feeder BDT5 - Planned | 4.01 | 318 | 1275.18 | 0.0036816 | 1.1577e-05
2012-12-18 | 286848 | GBN4 | Rural short | LV Transformer SP6283-B GBN4 - Planned | 3 | 365 | 1095 | 0.0031614 | 8.6614e-06
2012-12-18 | 286849 | MLY3 | Rural short | Feeder MLY3 - Planned | 35.24 | 278 | 9796.72 | 0.028284 | 0.00010174
2012-12-18 | 286850 | CLD22A | Urban | LV Transformer SC738194 CLD22A - Planned | 1 | 81 | 81 | 8.1787e-05 | 1.0097e-06
2012-12-18 | 286851 | NBR6 | Rural short | LV Transformer SP4071-A NBR6 - Planned | 16.92 | 245 | 4145.4 | 0.011968 | 4.885e-05
2012-12-18 | 286852 | BMT1 | Rural short | LV Transformer SP4256-B BMT1 - Planned | 4 | 119 | 476 | 0.0013743 | 1.1548e-05
2012-12-18 | 286853 | KWH2 | Rural short | LV Transformer SP42-E KWH2 - Planned | 5 | 142 | 710 | 0.0020499 | 1.4436e-05
2012-12-18 | 286854 | GYM7A | Rural short | Feeder GYM7A - Planned | 13.34 | 197 | 2627.98 | 0.0075873 | 3.8514e-05
2012-12-18 | 286855 | MLY6 | Rural short | Feeder MLY6 - Planned | 14.52 | 213 | 3092.76 | 0.0089292 | 4.1921e-05
2012-12-18 | 286872 | GGR1 | Rural short | Feeder GGR1 - Planned | 6 | 410 | 2460 | 0.0071023 | 1.7323e-05
2012-12-18 | 286882 | HPE12A | Urban | LV Transformer SC2582-K HPE12A - Planned | 1.0414 | 407 | 423.8498 | 0.00042797 | 1.0515e-06
2012-12-18 | 286883 | CRM16A | Rural short | LV Transformer SP2833-E CRM16A - Planned | 0.78 | 116 | 90.48 | 0.00026123 | 2.252e-06
2012-12-18 | 286884 | GAP9A | Urban | LV Transformer SP2578-N GAP9A - Planned | 8.97 | 180 | 1614.6 | 0.0016303 | 9.0572e-06
2012-12-18 | 286886 | JDL7 | Urban | LV Transformer SC3921-G JDL7 - Planned | 19.25 | 312 | 6006 | 0.0060644 | 1.9437e-05
2012-12-18 | 286890 | KWA6A | Urban | LV Transformer SP5414-A KWA6A - Planned | 16.905 | 208 | 3516.24 | 0.0035504 | 1.7069e-05
2012-12-18 | 286891 | CMD15A | Urban | LV Transformer SP5350-A CMD7A - Planned | 26.88 | 294 | 7902.72 | 0.0079795 | 2.7141e-05
2012-12-18 | 286891 | CMD7A | Rural short | LV Transformer SP5350-A CMD7A - Planned | 21.875 | 294 | 6431.25 | 0.018568 | 6.3156e-05
2012-12-18 | 286892 | MLY3 | Rural short | LV Transformer SC2048518 MLY3 - Planned | 75.17 | 42 | 3157.14 | 0.0091151 | 0.00021703
2012-12-18 | 286892 | MLY4 | Rural short | LV Transformer SC2048518 MLY3 - Planned | 38.7 | 42 | 1625.4 | 0.0046927 | 0.00011173
2012-12-18 | 286894 | LDR8 | Urban | LV Transformer SP468825 LDR8 - Planned | 26.88 | 381 | 10241.28 | 0.010341 | 2.7141e-05
2012-12-18 | 286895 | SPO32A | Urban | LV Transformer SP1771-I SPO32A - Planned | 9.9996 | 447 | 4469.8212 | 0.0045133 | 1.0097e-05
2012-12-18 | 286896 | BBH12B | Urban | LV Transformer SP3376-F BBH12B - Planned | 12.3 | 261 | 3210.3 | 0.0032415 | 1.242e-05
2012-12-18 | 286897 | CDRSPD12 | Urban | LV Transformer SP2685-E CDRSPD12 - Planned | 67.32 | 155 | 10434.6 | 0.010536 | 6.7974e-05
2012-12-18 | 286899 | BHL2A | Urban | LV Transformer SP1580-H BHL2A - Planned | 19.415 | 375 | 7280.625 | 0.0073514 | 1.9604e-05
2012-12-18 | 286900 | HTN24A | Urban | LV Transformer SP20476-F HTN24A - Planned | 8 | 315 | 2520 | 0.0025445 | 8.0777e-06
2012-12-18 | 286901 | SGT24A | Urban | LV Transformer SP3239-H SGT24A - Planned | 4.675 | 44 | 205.7 | 0.0002077 | 4.7204e-06
2012-12-18 | 286903 | SGT24A | Urban | LV Transformer SP3239-H SGT24A - Planned | 37.4 | 82 | 3066.8 | 0.0030966 | 3.7763e-05
2012-12-18 | 286904 | DRD13A | Urban | LV Transformer SP5770-D DRD13A - Planned | 27.76 | 230 | 6384.8 | 0.0064468 | 2.803e-05
2012-12-18 | 286905 | BLBNFM6 | Urban | LV Transformer SP3429-G BLBNFM6 - Planned | 11.91 | 213 | 2536.83 | 0.0025615 | 1.2026e-05
2012-12-18 | 286906 | RBY7A | Urban | LV Transformer SP11631-B RBY7A - Planned | 16.1675 | 230 | 3718.525 | 0.0037547 | 1.6325e-05
2012-12-18 | 286908 | RLA8 | Urban | LV Transformer SP392-R RLA8 - Planned | 6.2881 | 122.3333 | 1815.4643 | 0.0018331 | 6.3492e-06
2012-12-18 | 286912 | RLA8 | Urban | LV Transformer SP950-O RLA8 - Planned | 5.28 | 316 | 1668.48 | 0.0016847 | 5.3313e-06
2012-12-18 | 286914 | KBR2A | Rural short | LV Transformer SP3640-C KBR2A - Planned | 2.83 | 259 | 732.97 | 0.0021162 | 8.1706e-06
2012-12-18 | 286915 | BDB28A | Urban | LV Transformer SP3371-C MWMRBK11 - Planned | 4.59 | 280 | 1285.2 | 0.0012977 | 4.6346e-06
2012-12-18 | 286915 | MWMRBK11 | Rural short | LV Transformer SP3371-C MWMRBK11 - Planned | 1.33 | 280 | 372.4 | 0.0010752 | 3.8399e-06
2012-12-18 | 286916 | RST8A | Urban | LV Transformer SP4386-E RST8A - Planned | 12.39 | 361 | 4472.79 | 0.0045163 | 1.251e-05
2012-12-18 | 286941 | TMH12A | Urban | Feeder TMH12A, TMH13A - Planned | 1 | 377 | 377 | 0.00038066 | 1.0097e-06
2012-12-18 | 286941 | TMH13A | Urban | Feeder TMH12A, TMH13A - Planned | 1 | 377 | 377 | 0.00038066 | 1.0097e-06
2012-12-18 | 287242 | TMH12A | Urban | Feeder TMH12A, TMH13A - Planned | 1 | 377 | 377 | 0.00038066 | 1.0097e-06
2012-12-19 | 287028 | TGW1 | Rural short | Feeder TGW1 - Planned | 10.489 | 243 | 2548.827 | 0.0073587 | 3.0283e-05
2012-12-19 | 287040 | SPO5A | Urban | LV Transformer SG561257 SPO5A - Planned | 1 | 300 | 300 | 0.00030291 | 1.0097e-06
2012-12-19 | 287044 | WFD3A | Rural short | LV Transformer SP14192-B WFD3A - Planned | 25 | 160 | 4000 | 0.011548 | 7.2177e-05
2012-12-19 | 287046 | GBN3 | Rural short | Feeder GBN3 - Planned | 96.965 | 367 | 35586.155 | 0.10274 | 0.00027995
2012-12-19 | 287047 | BMT2 | Rural short | LV Transformer SP5618-B BMT2 - Planned | 3 | 266 | 798 | 0.0023039 | 8.6613e-06
2012-12-19 | 287049 | GYS5A | Rural short | LV Transformer SP2628-D GYS5A - Planned | 3 | 162 | 486 | 0.0014031 | 8.6613e-06
2012-12-19 | 287050 | BMT5 | Rural short | LV Transformer SP3943-C BMT5 - Planned | 16.5 | 145 | 2392.5 | 0.0069074 | 4.7637e-05
2012-12-19 | 287051 | BDB37A | Rural short | Feeder BDB37A - Planned | 4 | 420 | 1680 | 0.0048503 | 1.1548e-05
2012-12-19 | 287053 | PWC6 | Rural short | Feeder PWC6 - Planned | 20.55 | 427 | 8774.85 | 0.025334 | 5.933e-05
2012-12-19 | 287060 | CRB25A | Rural short | LV Transformer SP5732-E CRB25A - Planned | 43.12 | 525 | 22638 | 0.065358 | 0.00012449
2012-12-19 | 287062 | HWD5B | Urban | LV Transformer SC525892 HWD5B - Planned | 1.4867 | 61 | 90.6887 | 9.1567e-05 | 1.5011e-06
2012-12-19 | 287063 | HWD5B | Urban | LV Transformer SC1377097 HWD5B - Planned | 2.5851 | 85 | 219.7335 | 0.00022186 | 2.6101e-06
2012-12-19 | 287064 | AGE8 | Urban | LV Transformer SC2172-N - Planned | 13 | 300 | 3900 | 0.0039378 | 1.3126e-05
2012-12-19 | 287065 | GLY6 | Urban | LV Transformer SC1883-M GLY6 - Planned | 5.585 | 320 | 1787.2 | 0.0018045 | 5.6391e-06
2012-12-19 | 287066 | AGE10 | Urban | LV Transformer SG794-N AGE10 - Planned | 10.8 | 240 | 2592 | 0.0026171 | 1.0905e-05
2012-12-19 | 287067 | YDA5A | Rural short | LV Transformer SP7430-B CPB6 - Planned | 47 | 322 | 15134 | 0.043693 | 0.00013569
2012-12-19 | 287068 | GBN3 | Rural short | LV Transformer SP2555-D GBN3 - Planned | 3.5 | 130 | 455 | 0.0013136 | 1.0105e-05
2012-12-19 | 287069 | LDR1 | Urban | LV Transformer SP2861-F LDR1 - Planned | 25.2 | 435 | 10962 | 0.011068 | 2.5444e-05
2012-12-19 | 287069 | LDR8 | Urban | LV Transformer SP2861-F LDR1 - Planned | 3.84 | 435 | 1670.4 | 0.0016866 | 3.8772e-06
2012-12-19 | 287070 | JBB16A | Rural short | LV Transformer SP9748-B JBB16A - Planned | 7.04 | 387 | 2724.48 | 0.0078658 | 2.0325e-05
2012-12-19 | 287071 | MGP13A | Rural short | LV Transformer SP1713-F MGP13A - Planned | 2 | 295 | 590 | 0.0017034 | 5.7742e-06
2012-12-19 | 287072 | CNB24A | Rural short | LV Transformer SP6783-E CNB24A - Planned | 1.95 | 385 | 750.75 | 0.0021675 | 5.6298e-06
2012-12-19 | 287073 | NDH5A | Urban | LV Transformer SP2071-G NDH5A - Planned | 9.415 | 392 | 3690.68 | 0.0037264 | 9.5062e-06
2012-12-19 | 287074 | DRD3A | Urban | LV Transformer SC466-H DRD3A - Planned | 1.0875 | 415 | 451.3125 | 0.00045568 | 1.098e-06
2012-12-19 | 287075 | MRK9 | Urban | LV Transformer SP855-K MRK9 - Planned | 18.7714 | 381 | 7151.9034 | 0.0072212 | 1.8953e-05
2012-12-19 | 287076 | RBY15 | Urban | LV Transformer SP434-D RBY15 - Planned | 8.1198 | 172 | 1396.6056 | 0.0014101 | 8.1985e-06
2012-12-19 | 287077 | BLBNFM6 | Urban | LV Transformer SP5394-E BLBNFM6 - Planned | 6.915 | 299 | 2067.585 | 0.0020876 | 6.982e-06
2012-12-19 | 287078 | UMG2B | Rural short | LV Transformer SP2448-J UMG2B - Planned | 29.4811 | 328 | 9669.8008 | 0.027918 | 8.5115e-05
2012-12-20 | 287124 | FDS1 | Rural short | LV Transformer SP427506 FDS1 - Planned | 2 | 54 | 108 | 0.0003118 | 5.7742e-06
2012-12-20 | 287126 | WMR3 | Rural short | LV Transformer SP12646-C WMR3 - Planned | 1 | 55 | 55 | 0.00015879 | 2.8871e-06
2012-12-20 | 287127 | CBW11 | Rural short | LV Transformer SP8165-F CBW11 - Planned | 12 | 89 | 1068 | 0.0030834 | 3.4645e-05
2012-12-20 | 287129 | CBW7 | Rural short | LV Transformer SP7128-F CBW7 - Planned | 3.5 | 193 | 675.5 | 0.0019502 | 1.0105e-05
2012-12-20 | 287142 | PPE13A | Rural short | LV Transformer SP1613-E PPE13A - Planned | 8 | 240 | 1920 | 0.0055432 | 2.3097e-05
2012-12-20 | 287143 | CRM13A | Urban | LV Transformer SP17769-B CRM13A - Planned | 25.44 | 266 | 6767.04 | 0.0068324 | 2.5686e-05
2012-12-20 | 287145 | CBW13 | Rural short | LV Transformer SP9280-E CBW13 - Planned | 26 | 143 | 3718 | 0.010734 | 7.5064e-05
2012-12-20 | 287147 | TGW3 | Rural short | LV Transformer SP3018-C TGW3 - Planned | 1 | 337 | 337 | 0.00097295 | 2.8871e-06
2012-12-20 | 287161 | BDT1 | Rural short | Feeder BDT1 - Planned | 3.1875 | 304 | 969 | 0.0027976 | 9.2026e-06
2012-12-20 | 287162 | NBR4 | Rural short | Feeder NBR4 - Planned | 30.54 | 393 | 12002.22 | 0.034651 | 8.8171e-05
2012-12-20 | 287163 | GYM9B | Rural short | Feeder GYM9B - Planned | 28.44 | 275 | 7821 | 0.02258 | 8.2108e-05
2012-12-20 | 287164 | MLY3 | Rural short | Feeder MLY3 - Planned | 65.8289 | 381 | 25080.8109 | 0.07241 | 0.00019005
2012-12-20 | 287165 | MCN3 | Urban | Feeder MCN3, MCN4 - Planned | 2 | 313 | 626 | 0.00063205 | 2.0193e-06
2012-12-20 | 287165 | MCN4 | Rural short | Feeder MCN3, MCN4 - Planned | 55.5 | 313 | 17371.5 | 0.050153 | 0.00016023
2012-12-20 | 287167 | KMR19A | Urban | LV Transformer SP1867-M KMR19A - Planned | 8 | 279 | 2232 | 0.0022536 | 8.0773e-06
2012-12-20 | 287168 | MLT2B | Urban | LV Transformer SP1597-M MLT2B - Planned | 18.603 | 97 | 1804.491 | 0.0018219 | 1.8783e-05
2012-12-20 | 287169 | KWA2A | Urban | LV Transformer SP6571-A KWA2A - Planned | 73.08 | 210 | 15346.8 | 0.015495 | 7.3786e-05
2012-12-20 | 287170 | BHD35A | Rural short | LV Transformer SP5735-C BHD35A - Planned | 8.1 | 215 | 1741.5 | 0.0050278 | 2.3385e-05
2012-12-20 | 287171 | CCY13A | Urban | LV Transformer SP472468 CCY13A - Planned | 7.02 | 275 | 1930.5 | 0.0019491 | 7.0878e-06
2012-12-20 | 287172 | MTB15A | Rural short | LV Transformer SP744226 MTB15A - Planned | 17.5 | 200 | 3500 | 0.010105 | 5.0524e-05
2012-12-20 | 287173 | CRB25A | Rural short | LV Transformer SP5737-D CRB25A - Planned | 99.47 | 173 | 17208.31 | 0.049682 | 0.00028718
2012-12-20 | 287174 | SPO51A | Urban | LV Transformer SP1435-H SPO51A - Planned | 11.375 | 423 | 4811.625 | 0.0048581 | 1.1485e-05
2012-12-20 | 287175 | SGT7 | Urban | LV Transformer SP5891-F SGT7 - Planned | 9.41 | 303 | 2851.23 | 0.0028788 | 9.5009e-06
2012-12-20 | 287176 | SGT24A | Urban | LV Transformer SP39457-D SGT24A - Planned | 67.84 | 230 | 15603.2 | 0.015754 | 6.8495e-05
2012-12-20 | 287177 | CBW12 | Urban | LV Transformer SP6129-F CBW12 - Planned | 1.9725 | 115 | 226.8375 | 0.00022903 | 1.9915e-06
2012-12-20 | 287178 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 14.91 | 73 | 1088.43 | 0.0010989 | 1.5054e-05
2012-12-20 | 287179 | MTG3A | Urban | LV Transformer SP2869-J MTG3A - Planned | 11.97 | 145 | 1735.65 | 0.0017524 | 1.2086e-05
2012-12-20 | 287180 | BLB4A | Urban | LV Transformer SP5423-F BLB8B - Planned | 0.7283 | 240 | 174.792 | 0.00017648 | 7.3533e-07
2012-12-20 | 287180 | BLB8B | Urban | LV Transformer SP5423-F BLB8B - Planned | 7.225 | 240 | 1734 | 0.0017507 | 7.2948e-06
2012-12-20 | 287181 | HPE16A | Urban | LV Transformer SC3657-F HPE3A - Planned | 14.3796 | 265 | 3810.594 | 0.0038474 | 1.4518e-05
2012-12-20 | 287181 | HPE3A | Urban | LV Transformer SC3657-F HPE3A - Planned | 30.144 | 265 | 7988.16 | 0.0080653 | 3.0435e-05
2012-12-20 | 287182 | NIP5A | Urban | LV Transformer SP8560-B NIP5A - Planned | 23.925 | 365 | 8732.625 | 0.008817 | 2.4156e-05
2012-12-20 | 287183 | BNH1B | Rural short | LV Transformer SP4129-C BNH1B - Planned | 0.655 | 102 | 66.81 | 0.00019289 | 1.891e-06
2012-12-20 | 287185 | DRD3A | Urban | LV Transformer SC466-H DRD3A - Planned | 2.175 | 430 | 935.25 | 0.00094428 | 2.196e-06
2012-12-20 | 287245 | NIP1A | Urban | LV Transformer SP4942-C NIP1A - Planned | 0.975 | 1832 | 1786.2 | 0.0018034 | 9.8442e-07
2012-12-20 | 287246 | JBB16A | Rural short | LV Transformer SP4785-D JBB16A - Planned | 7.04 | 403 | 2837.12 | 0.008191 | 2.0325e-05
2012-12-21 | 287222 | CRB25A | Rural short | LV Transformer SP5766-F CRB25A - Planned | 5 | 174 | 870 | 0.0025117 | 1.4435e-05
2012-12-21 | 287225 | JBB12B | Rural short | LV Transformer SP6052-C JBB12B - Planned | 0.4 | 191 | 76.4 | 0.00022057 | 1.1548e-06
2012-12-21 | 287231 | GYN6A | Rural short | Feeder GYN6A - Planned | 36.03 | 210 | 7566.3 | 0.021844 | 0.00010402
2012-12-21 | 287232 | BMT2 | Rural short | LV Transformer SP3192-B BMT2 - Planned | 1 | 128 | 128 | 0.00036954 | 2.8871e-06
2012-12-21 | 287233 | TWT12A | Rural short | LV Transformer SP6755-C TWT12A - Planned | 4 | 101 | 404 | 0.0011664 | 1.1548e-05
2012-12-21 | 287234 | GYN6A | Rural short | LV Transformer SP396-C GYN6A - Planned | 1 | 182 | 182 | 0.00052545 | 2.8871e-06
2012-12-21 | 287235 | MLB6A | Rural short | LV Transformer SP5133-A MLB6A - Planned | 11.04 | 163 | 1799.52 | 0.0051953 | 3.1873e-05
2012-12-21 | 287236 | RBA43A | Rural short | LV Transformer SP6247-D RBA43A - Planned | 19.475 | 123 | 2395.425 | 0.0069157 | 5.6226e-05
2012-12-21 | 287241 | GYN6A | Rural short | Feeder GYN6A - Planned | 47.725 | 237 | 11310.825 | 0.032655 | 0.00013779
2012-12-21 | 287261 | CMD11A | Rural short | LV Transformer SP4419-B CMD11A - Planned | 4.2339 | 370 | 1566.543 | 0.0045227 | 1.2224e-05
2012-12-21 | 287262 | MLB11A | Urban | LV Transformer SC337-A MLB3A - Planned | 8 | 83 | 664 | 0.00067039 | 8.077e-06
2012-12-21 | 287262 | MLB3A | Rural short | LV Transformer SC337-A MLB3A - Planned | 54.57 | 83 | 4529.31 | 0.013076 | 0.00015755
2012-12-21 | 287263 | SPO60A | Urban | LV Transformer SP352-J SPO60A - Planned | 1.67 | 235 | 392.45 | 0.00039623 | 1.6861e-06
2012-12-21 | 287264 | SPO41A | Urban | LV Transformer SP6431-D SPO47A - Planned | 3.085 | 27 | 83.295 | 8.4097e-05 | 3.1147e-06
2012-12-21 | 287264 | SPO47A | Urban | LV Transformer SP6431-D SPO47A - Planned | 2.4983 | 27 | 67.4541 | 6.8103e-05 | 2.5224e-06
2012-12-21 | 287265 | SGT7 | Urban | LV Transformer SP5991-F SGT7 - Planned | 73.0794 | 222 | 16223.6268 | 0.01638 | 7.3783e-05
2012-12-21 | 287266 | HWD5B | Urban | LV Transformer SC1377097 HWD5B - Planned | 2.5851 | 51 | 131.8401 | 0.00013311 | 2.61e-06
2012-12-21 | 287267 | HDN1 | Rural short | LV Transformer SP8293-B HDN1 - Planned | 3.06 | 202 | 618.12 | 0.0017846 | 8.8344e-06
2012-12-23 | 287301 | BRD14B | Urban | LV Transformer SC1050350 BRD14B - Planned | 1 | 259 | 259 | 0.00026148 | 1.0096e-06
2012-12-23 | 287303 | CPK9 | Rural short | LV Transformer SP4205-D CPK9 - Planned | 1.32 | 82 | 108.24 | 0.00031249 | 3.8108e-06
2012-12-23 | 287304 | CPK11 | Urban | LV Transformer SC585828 CPK11 - Planned | 1 | 278 | 278 | 0.00028067 | 1.0096e-06
2012-12-24 | 287343 | WMR3 | Rural short | Feeder WMR3 - Planned | 7.5 | 225 | 1687.5 | 0.0048718 | 2.1652e-05
2012-12-24 | 287344 | NBR4 | Rural short | LV Transformer SP4402-A NBR4 - Planned | 1.165 | 94 | 109.51 | 0.00031615 | 3.3633e-06
2012-12-24 | 287345 | NMK7 | Urban | LV Transformer SP5061-M NMK7 - Planned | 0.605 | 86 | 52.03 | 5.2526e-05 | 6.1077e-07
2012-12-24 | 287346 | KWA2A | Urban | LV Transformer SP4519-B KWA2A - Planned | 20.9475 | 219 | 4587.5025 | 0.0046312 | 2.1147e-05
2012-12-27 | 287407 | JBB16A | Rural short | Feeder JBB16A - Planned | 15 | 237 | 3555 | 0.010263 | 4.3305e-05
2012-12-27 | 287410 | HMT9A | Rural short | LV Transformer SP3718-I HMT9A - Planned | 1 | 195 | 195 | 0.00056296 | 2.887e-06
2012-12-27 | 287422 | EMD3 | Rural short | LV Transformer SP732165 EMD3 - Planned | 1 | 117 | 117 | 0.00033778 | 2.887e-06
2012-12-27 | 287423 | AMR3 | Rural short | Feeder AMR3 - Planned | 20.42 | 291 | 5942.22 | 0.017155 | 5.8952e-05
2012-12-27 | 287424 | KWH2 | Rural short | LV Transformer SP2338-D KWH2 - Planned | 6.45 | 386 | 2489.7 | 0.0071877 | 1.8621e-05
2012-12-27 | 287425 | WED21A | Urban | LV Transformer SP6404-C WED21A - Planned | 11.1 | 410 | 4551 | 0.0045939 | 1.1205e-05
2012-12-27 | 287426 | CPB2 | Urban | LV Transformer SC1444998 CPB2 - Planned | 0.79 | 40 | 31.6 | 3.1898e-05 | 7.9745e-07
2012-12-27 | 287427 | CNB26A | Rural short | LV Transformer SP2654-F CNB26A - Planned | 4.95 | 55 | 272.25 | 0.00078598 | 1.4291e-05
2012-12-27 | 287428 | RBY15 | Urban | LV Transformer SP434-D RBY15 - Planned | 1.3433 | 112 | 150.4496 | 0.00015187 | 1.356e-06
2012-12-27 | 287475 | TWG13B | Urban | LV Transformer SG2964-M TWG13B - Planned | 1.1669 | 1706 | 1990.7314 | 0.0020095 | 1.1779e-06
2012-12-28 | 287443 | RWD2 | Rural short | LV Transformer SP3886-C RWD2 - Planned | 4 | 65 | 260 | 0.00075061 | 1.1548e-05
2012-12-28 | 287444 | KMR25A | Rural short | LV Transformer SP6637-H KMR25A - Planned | 7.02 | 84 | 589.68 | 0.0017024 | 2.0267e-05
2012-12-28 | 287445 | RWD1 | Rural short | LV Transformer SP4963-C RWD1 - Planned | 30 | 60 | 1800 | 0.0051965 | 8.6609e-05
2012-12-28 | 287447 | GYN1B | Urban | LV Transformer SC449011 GYN1B - Planned | 0.32 | 122 | 39.04 | 3.9407e-05 | 3.2301e-07
2012-12-28 | 287448 | WMR3 | Rural short | LV Transformer SP4729-G WMR3 - Planned | 1.5 | 135 | 202.5 | 0.00058461 | 4.3305e-06
2012-12-28 | 287449 | GYN7A | Rural short | LV Transformer SP3941-B GYN7A - Planned | 2.01 | 180 | 361.8 | 0.0010445 | 5.8028e-06
2012-12-28 | 287450 | KWH2 | Rural short | LV Transformer SP4793-B KWH2 - Planned | 1 | 192 | 192 | 0.0005543 | 2.887e-06
2012-12-28 | 287453 | EMD3 | Rural short | LV Transformer SP3228-C EMD3 - Planned | 3 | 286 | 858 | 0.002477 | 8.6609e-06
2012-12-28 | 287454 | ACR5 | Rural short | LV Transformer SP11453-D ACR5 - Planned | 13 | 270 | 3510 | 0.010133 | 3.7531e-05
2012-12-28 | 287455 | CBW13 | Rural short | Feeder CBW13 - Planned | 23 | 308 | 7084 | 0.020451 | 6.64e-05
2012-12-28 | 287456 | MTG4B | Urban | LV Transformer SG752675 MTG4B - Planned | 0.112 | 343 | 38.416 | 3.8777e-05 | 1.1305e-07
2012-12-28 | 287457 | MBG4 | Rural short | LV Transformer SP3626-D MBG4 - Planned | 5 | 40 | 200 | 0.00057739 | 1.4435e-05
2012-12-28 | 287458 | GBN4 | Rural short | LV Transformer SP1500-F GBN4 - Planned | 1 | 18 | 18 | 5.1965e-05 | 2.887e-06
2012-12-28 | 287474 | ENG7 | Urban | LV Transformer SP802367 ENG7 - Planned | 4 | 280 | 1120 | 0.0011305 | 4.0376e-06
2012-12-28 | 287476 | NVL12A | Urban | LV Transformer SP2166-C NVL12A - Planned | 61.48 | 90 | 5533.2 | 0.0055852 | 6.2058e-05
2012-12-28 | 287477 | CCY13A | Urban | LV Transformer SP6362-F CCY13A - Planned | 0.92 | 216 | 198.72 | 0.00020059 | 9.2865e-07
2012-12-28 | 287478 | CCY8A | Rural short | LV Transformer SC753573 GVN15A - Planned | 1 | 38 | 38 | 0.0001097 | 2.887e-06
2012-12-28 | 287478 | GVN15A | Urban | LV Transformer SC753573 GVN15A - Planned | 22.285 | 38 | 846.83 | 0.00085479 | 2.2495e-05
2012-12-28 | 287479 | WRG2A | Urban | LV Transformer SP2953-D WRG2A - Planned | 1.16 | 81 | 93.96 | 9.4843e-05 | 1.1709e-06
2012-12-28 | 287480 | RBY15 | Urban | LV Transformer SP434-D RBY15 - Planned | 11.7564 | 191 | 2245.4724 | 0.0022666 | 1.1867e-05
2012-12-30 | 287528 | SPE12 | Urban | LV Transformer SP15189-E SPE12 - Planned | 1 | 185 | 185 | 0.00018673 | 1.0093e-06
2012-12-31 | 287538 | BNH1B | Rural short | LV Transformer SP3644-C BNH1B - Planned | 6 | 76 | 456 | 0.0013165 | 1.7322e-05
2012-12-31 | 287540 | PPE13A | Rural short | LV Transformer SP5436-C PPE13A - Planned | 6.5 | 177 | 1150.5 | 0.0033215 | 1.8765e-05
2012-12-31 | 287542 | MLB6A | Rural short | LV Transformer SC737528 MLB6A - Planned | 1 | 148 | 148 | 0.00042727 | 2.887e-06
2012-12-31 | 287543 | WMD8B | Rural short | LV Transformer SP5360-A WMD8B - Planned | 10.01 | 257 | 2572.57 | 0.007427 | 2.8899e-05
2012-12-31 | 287545 | PWC6 | Rural short | Feeder PWC6 - Planned | 27.96 | 281 | 7856.76 | 0.022682 | 8.072e-05
2012-12-31 | 287546 | WFD3A | Rural short | Feeder WFD3A - Planned | 5 | 227 | 1135 | 0.0032767 | 1.4435e-05
2012-12-31 | 287547 | WFD2B | Rural short | LV Transformer SP12529-C WFD2B - Planned | 6 | 188 | 1128 | 0.0032565 | 1.7322e-05
2013-01-02 | 287564 | BDT1 | Rural short | LV Transformer SP16260-D BDT1 - Planned | 1 | 54 | 54 | 0.0001559 | 2.8871e-06
2013-01-02 | 287570 | MBG4 | Rural short | LV Transformer SP8567-B MBG4 - Planned | 6 | 185 | 1110 | 0.0032046 | 1.7322e-05
2013-01-02 | 287572 | IPL3 | Rural short | LV Transformer SP1943-G IPL3 - Planned | 3 | 155 | 465 | 0.0013425 | 8.6612e-06
2013-01-02 | 287573 | LLY1 | Rural short | LV Transformer SP103-B LLY1 - Planned | 4.98 | 214 | 1065.72 | 0.0030768 | 1.4378e-05
2013-01-02 | 287574 | GYM7A | Rural short | LV Transformer SP9311-B GYM7A - Planned | 1 | 104 | 104 | 0.00030025 | 2.8871e-06
2013-01-02 | 287575 | CLM6 | Urban | LV Transformer SC384-D CLM6 - Planned | 2.01 | 276 | 554.76 | 0.00055989 | 2.0286e-06
2013-01-02 | 287578 | KBR3A | Rural short | Feeder KBR3A - Planned | 20.33 | 360 | 7318.8 | 0.02113 | 5.8694e-05
2013-01-02 | 287579 | TGW3 | Rural short | LV Transformer SP2807-C TGW3 - Planned | 1 | 318 | 318 | 0.00091809 | 2.8871e-06
2013-01-02 | 287584 | SMF1B | Rural short | LV Transformer SP6184-F SMF1B - Planned | 6.6 | 576 | 3801.6 | 0.010975 | 1.9055e-05
2013-01-02 | 287585 | TRG2A | Urban | LV Transformer SP961-J TRG2A - Planned | 11.3594 | 204 | 2317.3176 | 0.0023387 | 1.1464e-05
2013-01-02 | 287586 | NSD8A | Urban | LV Transformer SG2572-N NSD8A - Planned | 2.5 | 235 | 587.5 | 0.00059293 | 2.5231e-06
2013-01-02 | 287587 | MLY3 | Rural short | LV Transformer SP4561-C MLY3 - Planned | 11.21 | 240 | 2690.4 | 0.0077674 | 3.2364e-05
2013-01-02 | 287588 | PGN1B | Rural short | LV Transformer SP1825-D PGN1B - Planned | 25.375 | 182 | 4618.25 | 0.013333 | 7.3259e-05
2013-01-02 | 287589 | HWL11A | Urban | LV Transformer SP10034-E HWL11A - Planned | 78.48 | 292 | 22916.16 | 0.023128 | 7.9206e-05
2013-01-02 | 287590 | CRB25A | Rural short | LV Transformer SP5764-F CRB25A - Planned | 17.325 | 265 | 4591.125 | 0.013255 | 5.0018e-05
2013-01-02 | 287591 | CRB15A | Urban | LV Transformer SC22931-F CRB15A - Planned | 0.2283 | 226 | 51.5958 | 5.2073e-05 | 2.3041e-07
2013-01-02 | 287592 | DRD13A | Urban | LV Transformer SP2609-F DRD13A - Planned | 0.955 | 145 | 138.475 | 0.00013976 | 9.6383e-07
2013-01-02 | 287593 | CNB24A | Rural short | LV Transformer SP2838-D CNB24A - Planned | 6.12 | 290 | 1774.8 | 0.005124 | 1.7669e-05
2013-01-02 | 287594 | BLBNFM6 | Urban | LV Transformer SP3429-G BLBNFM6 - Planned | 17.94 | 318 | 5704.92 | 0.0057577 | 1.8106e-05
2013-01-02 | 287595 | THL1 | Rural short | LV Transformer SP2658-C THL1 - Planned | 2.01 | 52 | 104.52 | 0.00030176 | 5.803e-06
2013-01-02 | 287596 | THL3 | Rural short | LV Transformer SP3039-C THL3 - Planned | 4 | 119 | 476 | 0.0013742 | 1.1548e-05
2013-01-02 | 287597 | CPD1 | Rural short | LV Transformer SP1853-B CPD1 - Planned | 1 | 62 | 62 | 0.000179 | 2.8871e-06
2013-01-02 | 287724 | FIS13A | Urban | Feeder FIS13A - Planned | 3.4 | 145 | 493 | 0.00049756 | 3.4314e-06
2013-01-03 | 287629 | GYN6A | Rural short | LV Transformer SP1711-D GYN6A - Planned | 3 | 216 | 648 | 0.0018708 | 8.6613e-06
2013-01-03 | 287631 | MCN1 | Rural short | LV Transformer SP4396-D MCN1 - Planned | 0.5 | 269 | 134.5 | 0.00038832 | 1.4436e-06
2013-01-03 | 287632 | WSE3A | Rural short | Feeder WSE3A - Planned | 16 | 245 | 3920 | 0.011317 | 4.6194e-05
2013-01-03 | 287633 | GYM7A | Rural short | LV Transformer SP6540-D GYM7A - Planned | 1 | 346 | 346 | 0.00099894 | 2.8871e-06
2013-01-03 | 287636 | WFD1B | Rural short | LV Transformer SP13596-C WFD1B - Planned | 2 | 260 | 520 | 0.0015013 | 5.7742e-06
2013-01-03 | 287640 | MLY3 | Rural short | Feeder MLY3 - Planned | 58.12 | 360 | 20923.2 | 0.060408 | 0.0001678
2013-01-03 | 287641 | BTN6 | Urban | Feeder BTN6 - Planned | 7 | 325 | 2275 | 0.002296 | 7.0645e-06
2013-01-03 | 287642 | GBG2A | Urban | LV Transformer SP16016-D GBG2A - Planned | 1 | 215 | 215 | 0.00021698 | 1.0092e-06
2013-01-03 | 287643 | TGW3 | Rural short | LV Transformer SP4701-B TGW3 - Planned | 1 | 355 | 355 | 0.0010249 | 2.8871e-06
2013-01-03 | 287644 | GTN12A | Rural short | Feeder GTN12A - Planned | 12.75 | 359 | 4577.25 | 0.013215 | 3.6811e-05
2013-01-03 | 287645 | FDS4 | Rural short | Feeder FDS4 - Planned | 18.99 | 418 | 7937.82 | 0.022917 | 5.4826e-05
2013-01-03 | 287647 | KMR27A | Urban | LV Transformer SP2566-O KMR27A - Planned | 4.1199 | 85 | 350.1915 | 0.00035342 | 4.1579e-06
2013-01-03 | 287648 | DRA8 | Urban | LV Transformer SP799214 DRA8 - Planned | 23.625 | 65 | 1535.625 | 0.0015498 | 2.3843e-05
2013-01-03 | 287649 | DRA8 | Urban | LV Transformer SG798487 DRA8 - Planned | 2.1 | 265 | 556.5 | 0.00056163 | 2.1194e-06
2013-01-03 | 287650 | PKW7A | Urban | LV Transformer SC811675 PKW7A - Planned | 1 | 133 | 133 | 0.00013423 | 1.0092e-06
2013-01-03 | 287651 | MGP1 | Rural short | LV Transformer SP4580-G MGP1 - Planned | 12.16 | 128 | 1556.48 | 0.0044937 | 3.5107e-05
2013-01-03 | 287652 | HWL11A | Urban | LV Transformer SP10034-E HWL11A - Planned | 3.27 | 213 | 696.51 | 0.00070293 | 3.3002e-06
2013-01-03 | 287653 | BHD35A | Rural short | LV Transformer SP5805-F BHD35A - Planned | 17.415 | 325 | 5659.875 | 0.016341 | 5.0279e-05
2013-01-03 | 287654 | SGT7 | Urban | LV Transformer SC6190-E SGT7 - Planned | 3.6399 | 256 | 931.8144 | 0.00094041 | 3.6735e-06
2013-01-03 | 287655 | LTA5 | Urban | LV Transformer SC6246-F LTA5 - Planned | 19.5063 | 69 | 1345.9347 | 0.0013583 | 1.9686e-05
2013-01-03 | 287656 | RCF2A | Urban | LV Transformer SP3418-B RCF2A - Planned | 2.61 | 185 | 482.85 | 0.0004873 | 2.6341e-06
2013-01-03 | 287657 | MFD8A | Rural short | LV Transformer SC787379 MFD8A - Planned | 0.9 | 46 | 41.4 | 0.00011953 | 2.5984e-06
2013-01-03 | 287658 | NMC15A | Rural short | LV Transformer SP744331 NMC15A - Planned | 17 | 271 | 4607 | 0.013301 | 4.9081e-05
2013-01-03 | 287659 | BLH13B | Rural short | LV Transformer SP7937-A BLH13B - Planned | 4.98 | 105 | 522.9 | 0.0015097 | 1.4378e-05
2013-01-03 | 287660 | BLBNFM6 | Urban | LV Transformer SP5394-E BLBNFM6 - Planned | 6.915 | 291 | 2012.265 | 0.0020308 | 6.9788e-06
2013-01-03 | 287661 | THL1 | Rural short | LV Transformer SP4734-A THL1 - Planned | 1 | 200 | 200 | 0.00057742 | 2.8871e-06
2013-01-04 | 287678 | THL3 | Rural short | LV Transformer SP2055-D THL3 - Planned | 1 | 174 | 174 | 0.00050237 | 2.8872e-06
2013-01-04 | 287680 | TGW3 | Rural short | LV Transformer SP4700-A TGW3 - Planned | 1 | 199 | 199 | 0.00057455 | 2.8872e-06
2013-01-04 | 287681 | CVL7A | Rural short | LV Transformer SP3589-B CVL7A - Planned | 26 | 260 | 6760 | 0.019517 | 7.5066e-05
2013-01-04 | 287683 | TGW3 | Rural short | LV Transformer SP3018-C TGW3 - Planned | 1 | 269 | 269 | 0.00077665 | 2.8872e-06
2013-01-04 | 287684 | WHO1 | Rural short | Feeder WHO1 - Planned | 30 | 442 | 13260 | 0.038284 | 8.6615e-05
2013-01-04 | 287688 | AGE10 | Urban | LV Transformer SP2588-M AGE10 - Planned | 5.79 | 240 | 1389.6 | 0.0014024 | 5.8433e-06
2013-01-04 | 287689 | AHL9A | Urban | LV Transformer SP4194-K AHL9A - Planned | 1.28 | 59 | 75.52 | 7.6215e-05 | 1.2918e-06
2013-01-04 | 287690 | AHL6A | Urban | LV Transformer SC4300-N AHL6A - Planned | 1.0267 | 203 | 208.4201 | 0.00021034 | 1.0361e-06
2013-01-04 | 287690 | GLY2 | Urban | LV Transformer SC4300-N AHL6A - Planned | 24.375 | 203 | 4948.125 | 0.0049936 | 2.4599e-05
2013-01-04 | 287691 | BWH16A | Rural short | LV Transformer SP1759-C BWH16A - Planned | 5.2173 | 307 | 1601.7111 | 0.0046244 | 1.5063e-05
2013-01-04 | 287692 | MLY1 | Rural short | LV Transformer SP10071-A MLY1 - Planned | 3 | 176 | 528 | 0.0015244 | 8.6615e-06
2013-01-04 | 287693 | IPL1 | Rural short | LV Transformer SP5315-E IPL1 - Planned | 4 | 150 | 600 | 0.0017323 | 1.1549e-05
2013-01-04 | 287694 | PPE5A | Rural short | LV Transformer SP4800-E PPE5A - Planned | 10.44 | 277 | 2891.88 | 0.0083493 | 3.0142e-05
2013-01-04 | 287695 | CRBTHP26 | Urban | LV Transformer SP17403-E CRBTHP26 - Planned | 23.64 | 203 | 4798.92 | 0.0048431 | 2.3857e-05
2013-01-04 | 287696 | HWL11A | Urban | LV Transformer SP10034-E HWL11A - Planned | 22.89 | 157 | 3593.73 | 0.0036268 | 2.3101e-05
2013-01-04 | 287697 | MRE3 | Urban | LV Transformer SC808031-A MRE3 - Planned | 12.54 | 205 | 2570.7 | 0.0025943 | 1.2655e-05
2013-01-04 | 287698 | WED16A | Urban | LV Transformer SP53863-D WED16A - Planned | 20.6001 | 216 | 4449.6216 | 0.0044905 | 2.079e-05
2013-01-04 | 287698 | WED20A | Urban | LV Transformer SP53863-D WED16A - Planned | 1.16 | 216 | 250.56 | 0.00025286 | 1.1707e-06
2013-01-04 | 287699 | SBK11 | Urban | LV Transformer SP25912-F SBK11 - Planned | 25.725 | 298 | 7666.05 | 0.0077366 | 2.5962e-05
2013-01-04 | 287700 | BNH1B | Rural short | LV Transformer SP1521-F BNH1B - Planned | 6.02 | 138 | 830.76 | 0.0023985 | 1.7381e-05
2013-01-06 | 287729 | DRA8 | Urban | LV Transformer SP799214 DRA8 - Planned | 29.75 | 290 | 8627.5 | 0.0087065 | 3.0023e-05
2013-01-06 | 287730 | KWA10A | Urban | LV Transformer SP5203-A KWA10A - Planned | 22.56 | 113 | 2549.28 | 0.0025726 | 2.2767e-05
2013-01-06 | 287731 | KWA10A | Urban | LV Transformer SP202892 KWA10A - Planned | 32.78 | 298 | 9768.44 | 0.0098579 | 3.308e-05
2013-01-06 | 287732 | HTN7A | Urban | LV Transformer SC1664-K HTN7A - Planned | 7.02 | 240 | 1684.8 | 0.0017002 | 7.0843e-06
2013-01-06 | 287733 | MDH4A | Urban | LV Transformer SP1839-L MDH4A - Planned | 1.71 | 117 | 200.07 | 0.0002019 | 1.7257e-06
2013-01-06 | 287734 | HDA11A | Urban | LV Transformer SP5166-G HDA11A - Planned | 13.35 | 62 | 827.7 | 0.00083528 | 1.3472e-05
2013-01-07 | 287780 | BNH1B | Rural short | LV Transformer SP3913-D BNH1B - Planned | 5 | 212 | 1060 | 0.0030606 | 1.4437e-05
2013-01-07 | 287789 | BGY5A | Rural short | LV Transformer SP11532-D BGY5A - Planned | 2.01 | 273 | 548.73 | 0.0015844 | 5.8036e-06
2013-01-07 | 287790 | GYN7A | Rural short | LV Transformer SP6520-D GYN7A - Planned | 2.01 | 245 | 492.45 | 0.0014219 | 5.8036e-06
2013-01-07 | 287791 | YDA3A | Rural short | LV Transformer SP9899-A YDA3A - Planned | 4.98 | 68 | 338.64 | 0.00097778 | 1.4379e-05
2013-01-07 | 287792 | BMT1 | Rural short | LV Transformer SP6288-B BMT1 - Planned | 1 | 242 | 242 | 0.00069874 | 2.8874e-06
2013-01-07 | 287798 | TRP1 | Rural short | LV Transformer SP5082-A TRP1 - Planned | 11 | 335 | 3685 | 0.01064 | 3.1761e-05
2013-01-07 | 287802 | JBB12B | Rural short | LV Transformer SP5540-C JBB12B - Planned | 0.5 | 325 | 162.5 | 0.0004692 | 1.4437e-06
2013-01-07 | 287803 | WMR2 | Rural short | Feeder WMR2 - Planned | 2.6521 | 382 | 1013.1022 | 0.0029252 | 7.6576e-06
2013-01-07 | 287804 | TGW3 | Rural short | LV Transformer SP2801-C TGW3 - Planned | 3 | 350 | 1050 | 0.0030317 | 8.6621e-06
2013-01-07 | 287810 | AMR2 | Rural short | LV Transformer SP2903-C AMR2 - Planned | 9 | 185 | 1665 | 0.0048075 | 2.5986e-05
2013-01-07 | 287811 | OXL5A | Urban | LV Transformer SP16661-E OXL5A - Planned | 1 | 538 | 538 | 0.00054292 | 1.0091e-06
2013-01-07 | 287812 | MGP12A | Rural short | LV Transformer SP10106-F MGP12A - Planned | 26 | 266 | 6916 | 0.019969 | 7.5072e-05
2013-01-07 | 287813 | SPO51A | Urban | LV Transformer SP38163-B SPO51A - Planned | 0.865 | 123 | 106.395 | 0.00010737 | 8.7291e-07
2013-01-07 | 287814 | LDR8 | Urban | LV Transformer SP8781-D LDR8 - Planned | 16.4 | 225 | 3690 | 0.0037237 | 1.655e-05
2013-01-07 | 287815 | MRE3 | Urban | LV Transformer SP1921-J MRE3 - Planned | 14.752 | 193 | 2847.136 | 0.0028732 | 1.4887e-05
2013-01-07 | 287816 | SGT22A | Urban | LV Transformer SP303-N SGT22A - Planned | 8.385 | 123 | 1031.355 | 0.0010408 | 8.4616e-06
2013-01-07 | 287817 | CMV8 | Urban | LV Transformer SP2016-K CMV8 - Planned | 1.056 | 152 | 160.512 | 0.00016198 | 1.0657e-06
2013-01-08 | 287883 | WSE5A | Rural short | Feeder WSE5A - Planned | 37.37 | 188 | 7025.56 | 0.020286 | 0.0001079
2013-01-08 | 287885 | WSE5A | Rural short | Feeder WSE5A - Planned | 36.55 | 235 | 8589.25 | 0.024801 | 0.00010554
2013-01-08 | 287886 | MTB13A | Rural short | LV Transformer SP3080-C MTB13A - Planned | 13.5 | 213 | 2875.5 | 0.0083029 | 3.8981e-05
2013-01-08 | 287887 | MLY3 | Rural short | Feeder MLY3 - Planned | 37.9 | 126 | 4775.4 | 0.013789 | 0.00010943
2013-01-08 | 287901 | NGI1B | Rural short | LV Transformer SP9087-F NGI1B - Planned | 15.98 | 357 | 5704.86 | 0.016473 | 4.6142e-05
2013-01-08 | 287903 | GGR1 | Rural short | Feeder GGR1 - Planned | 5.955 | 425 | 2530.875 | 0.0073078 | 1.7195e-05
2013-01-08 | 287904 | STT3A | Rural short | LV Transformer SP4797-D STT3A - Planned | 0.8 | 442 | 353.6 | 0.001021 | 2.31e-06
2013-01-08 | 287910 | CRB24B | Urban | LV Transformer SP53609-C CRB24B - Planned | 43.12 | 495 | 21344.4 | 0.021539 | 4.3513e-05
2013-01-08 | 287910 | CRBTHP14 | Urban | LV Transformer SP53609-C CRB24B - Planned | 15.39 | 495 | 7618.05 | 0.0076876 | 1.553e-05
2013-01-08 | 287911 | GAP8A | Urban | LV Transformer SP2779-K GAP8A - Planned | 38.4 | 185 | 7104 | 0.0071688 | 3.875e-05
2013-01-08 | 287912 | TWG19 | Urban | LV Transformer SP18034-G TWG19 - Planned | 0.695 | 253 | 175.835 | 0.00017744 | 7.0134e-07
2013-01-08 | 287913 | TRG2A | Urban | LV Transformer SP4206-I TRG2A - Planned | 14.3 | 164 | 2345.2 | 0.0023666 | 1.443e-05
2013-01-08 | 287914 | GYM2A | Rural short | LV Transformer SP4243-C GYM2A - Planned | 4.98 | 141 | 702.18 | 0.0020275 | 1.438e-05
2013-01-08 | 287915 | AMR3 | Rural short | LV Transformer SP5495-B AMR3 - Planned | 2.01 | 147 | 295.47 | 0.00085316 | 5.8038e-06
2013-01-08 | 287916 | NVL5 | Rural short | LV Transformer SC761206 NVL5 - Planned | 9 | 25 | 225 | 0.00064968 | 2.5987e-05
2013-01-08 | 287917 | HWL2A | Urban | LV Transformer SC563880 HWL2A - Planned | 1 | 18 | 18 | 1.8164e-05 | 1.0091e-06
2013-01-08 | 287918 | PPE13A | Rural short | LV Transformer SC788594 PPE13A - Planned | 5.72 | 135 | 772.2 | 0.0022297 | 1.6516e-05
2013-01-08 | 287919 | HWL2A | Urban | LV Transformer SC1387528 HWL2A - Planned | 0.02 | 62 | 1.24 | 1.2513e-06 | 2.0182e-08
2013-01-08 | 287920 | GBG27 | Urban | LV Transformer SP1686-H GBG27 - Planned | 9.9 | 194 | 1920.6 | 0.0019381 | 9.9903e-06
2013-01-08 | 287920 | SGT22A | Urban | LV Transformer SP1686-H GBG27 - Planned | 11.97 | 194 | 2322.18 | 0.0023434 | 1.2079e-05
2013-01-08 | 287921 | KCY1 | Urban | LV Transformer SP16595-E KCY1 - Planned | 6.84 | 375 | 2565 | 0.0025884 | 6.9024e-06
2013-01-08 | 287922 | NGI1B | Rural short | LV Transformer SP7055-F NGI1B - Planned | 4.08 | 294 | 1199.52 | 0.0034636 | 1.1781e-05
2013-01-08 | 287923 | MBG2 | Rural short | Feeder MBG2 - Planned | 16.02 | 505 | 8090.1 | 0.02336 | 4.6257e-05
2013-01-08 | 287924 | DRD3A | Urban | LV Transformer SP778006 DRD3A - Planned | 22.96 | 227 | 5211.92 | 0.0052595 | 2.3169e-05
2013-01-08 | 287925 | AFD1A | Urban | LV Transformer SC5759-G AFD1A - Planned | 12.92 | 20 | 258.4 | 0.00026076 | 1.3038e-05
2013-01-08 | 287926 | BBSRDL8 | Rural short | LV Transformer SP3960-E BBSRDL8 - Planned | 0.5833 | 390 | 227.487 | 0.00065686 | 1.6843e-06
2013-01-08 | 287927 | BMT1 | Rural short | Feeder BMT1 - Planned | 32.52 | 410 | 13333.2 | 0.038499 | 9.39e-05
2013-01-08 | 287928 | GYM2A | Rural short | Feeder GYM2A - Planned | 8 | 330 | 2640 | 0.0076229 | 2.31e-05
2013-01-08 | 287931 | FDS1 | Rural short | Feeder FDS1 - Planned | 23.245 | 355 | 8251.975 | 0.023827 | 6.7119e-05
2013-01-08 | 288179 | GVN16A | Rural short | Feeder GVN16A - Planned | 26.46 | 420 | 11113.2 | 0.032089 | 7.6402e-05
2013-01-09 | 287941 | NRA1A | Rural short | LV Transformer SG202-J NRA1A - Planned | 1 | 45 | 45 | 0.00012994 | 2.8875e-06
2013-01-09 | 287942 | ACFQBI5 | Urban | LV Transformer SG970-I ACFQBI5 - Planned | 1 | 115 | 115 | 0.00011605 | 1.0091e-06
2013-01-09 | 287946 | SMF2A | Rural short | Feeder SMF2A - Planned | 16.27 | 167 | 2717.09 | 0.0078456 | 4.698e-05
2013-01-09 | 287948 | BHD35A | Rural short | LV Transformer SP5097-H BHD35A - Planned | 9.5 | 233 | 2213.5 | 0.0063915 | 2.7431e-05
2013-01-09 | 287949 | IPL3 | Rural short | LV Transformer SP5072-D IPL3 - Planned | 1 | 92 | 92 | 0.00026565 | 2.8875e-06
2013-01-09 | 287950 | BNH1B | Rural short | Feeder BNH1B - Planned | 35.02 | 246 | 8614.92 | 0.024876 | 0.00010112
2013-01-09 | 287953 | HDN1 | Rural short | Feeder HDN1 - Planned | 3 | 378 | 1134 | 0.0032744 | 8.6625e-06
2013-01-09 | 287957 | SMF2A | Rural short | Feeder SMF2A - Planned | 113.8 | 315 | 35847 | 0.10351 | 0.0003286
2013-01-09 | 287961 | CRM16A | Rural short | LV Transformer SP2833-E CRM16A - Planned | 2.97 | 270 | 801.9 | 0.0023155 | 8.5759e-06
2013-01-09 | 287962 | TRG2A | Urban | LV Transformer SP961-J TRG2A - Planned | 12.1316 | 235 | 2850.926 | 0.0028769 | 1.2242e-05
2013-01-09 | 287963 | NMK5 | Urban | LV Transformer SP1463-N NMK5 - Planned | 3.75 | 308 | 1155 | 0.0011655 | 3.7841e-06
2013-01-09 | 287964 | GAP8A | Urban | LV Transformer SP2779-K GAP8A - Planned | 6.4 | 203 | 1299.2 | 0.001311 | 6.4583e-06
2013-01-09 | 287965 | TWT5B | Rural short | LV Transformer SC759000 TWT5B - Planned | 1 | 38 | 38 | 0.00010973 | 2.8875e-06
2013-01-09 | 287967 | TWT3A | Rural short | LV Transformer SP302238 TWT3A - Planned | 12.88 | 54 | 695.52 | 0.0020083 | 3.7191e-05
2013-01-09 | 287968 | AHD15A | Urban | LV Transformer SC85-A AHD15A - Planned | 77.1168 | 29 | 2236.3872 | 0.0022568 | 7.7819e-05
2013-01-09 | 287969 | NBR6 | Rural short | LV Transformer SP4386-A NBR6 - Planned | 9 | 125 | 1125 | 0.0032484 | 2.5988e-05
2013-01-09 | 287970 | CRY3A | Rural short | Feeder CRY3A - Planned | 5.98 | 280 | 1674.4 | 0.0048348 | 1.7267e-05
2013-01-09 | 287971 | MLY1 | Rural short | LV Transformer SP7725-A MLY1 - Planned | 5.04 | 56 | 282.24 | 0.00081497 | 1.4553e-05
2013-01-09 | 287973 | LDR3 | Urban | LV Transformer SP958-G LDR3 - Planned | 34.68 | 272 | 9432.96 | 0.0095189 | 3.4996e-05
2013-01-09 | 287974 | CRY2A | Rural short | Feeder CRY2A - Planned | 25.88 | 146 | 3778.48 | 0.01091 | 7.4729e-05
2013-01-09 | 287976 | BHD31A | Urban | LV Transformer SC22908-B BHD31A - Planned | 0.93 | 54 | 50.22 | 5.0677e-05 | 9.3847e-07
2013-01-09 | 287976 | BHD35A | Rural short | LV Transformer SC22908-B BHD31A - Planned | 3.99 | 54 | 215.46 | 0.00062214 | 1.1521e-05
2013-01-09 | 287977 | YTA22A | Rural short | LV Transformer SC1400942 YTA2A - Planned | 16.74 | 60 | 1004.4 | 0.0029002 | 4.8337e-05
2013-01-09 | 287977 | YTA2A | Urban | LV Transformer SC1400942 YTA2A - Planned | 1.02 | 60 | 61.2 | 6.1757e-05 | 1.0293e-06
2013-01-09 | 287978 | GYGGYS6 | Rural short | LV Transformer SP5578-B GYGGYS6 - Planned | 1 | 140 | 140 | 0.00040425 | 2.8875e-06
2013-01-09 | 287979 | BHL2A | Urban | LV Transformer SP1580-H BHL2A - Planned | 2 | 184 | 368 | 0.00037135 | 2.0182e-06
2013-01-09 | 287980 | SGT7 | Urban | LV Transformer SP5991-F SGT7 - Planned | 7.5481 | 55 | 415.1455 | 0.00041893 | 7.6168e-06
2013-01-09 | 287981 | BHL2A | Urban | LV Transformer SP2401-J BHL2A - Planned | 27.05 | 266 | 7195.3 | 0.0072608 | 2.7296e-05
2013-01-09 | 287981 | BHL3A | Urban | LV Transformer SP2401-J BHL2A - Planned | 6.08 | 266 | 1617.28 | 0.001632 | 6.1354e-06
2013-01-09 | 287982 | CRB25A | Rural short | LV Transformer SP5732-E CRB25A - Planned | 16.02 | 413 | 6616.26 | 0.019104 | 4.6258e-05
2013-01-09 | 287983 | WNM2A | Urban | LV Transformer SP5927-F WNM2A - Planned | 1.775 | 210 | 372.75 | 0.00037614 | 1.7912e-06
2013-01-09 | 287984 | DBY7A | Urban | LV Transformer SP17269-B DBY7A - Planned | 20.74 | 10.3333 | 197.42 | 0.00019922 | 2.0929e-05
2013-01-09 | 287985 | BKD12A | Urban | LV Transformer SP4410-D BKD2B - Planned | 1.7 | 327 | 555.9 | 0.00056096 | 1.7155e-06
2013-01-09 | 287985 | BKD2B | Urban | LV Transformer SP4410-D BKD2B - Planned | 11.22 | 327 | 3668.94 | 0.0037023 | 1.1322e-05
2013-01-09 | 287986 | RCN2A | Urban | LV Transformer SC4570-J RCN2A - Planned | 19.8091 | 404 | 8002.8764 | 0.0080758 | 1.9989e-05
2013-01-09 | 287987 | MRE2 | Urban | LV Transformer SC2747-J MRE2 - Planned | 8.25 | 325 | 2681.25 | 0.0027057 | 8.3251e-06
2013-01-09 | 287988 | WED6A | Urban | LV Transformer SP161-Q WED6A - Planned | 5.675 | 418 | 2372.15 | 0.0023938 | 5.7267e-06
2013-01-09 | 287989 | GTN12A | Rural short | LV Transformer SP2854-C GTN12A - Planned | 7.04 | 95 | 668.8 | 0.0019312 | 2.0328e-05
2013-01-09 | 287990 | GTN12A | Rural short | LV Transformer SP4608-B GTN12A - Planned | 7.98 | 72 | 574.56 | 0.001659 | 2.3042e-05
2013-01-09 | 288135 | GGR4 | Rural short | LV Transformer SC244369 - Planned | 1 | 3483 | 3483 | 0.010057 | 2.8875e-06
2013-01-10 | 288022 | CBW11 | Rural short | Feeder CBW11 - Planned | 52 | 239 | 12428 | 0.035887 | 0.00015016
2013-01-10 | 288024 | JBB16A | Rural short | Feeder JBB16A - Planned | 100.9 | 267 | 26940.3 | 0.077793 | 0.00029136
2013-01-10 | 288028 | LLY3 | Rural short | Feeder LLY3 - Planned | 7.02 | 361 | 2534.22 | 0.0073179 | 2.0271e-05
2013-01-10 | 288029 | MCW11 | Rural short | Feeder MCW11 - Planned | 89.05 | 329 | 29297.45 | 0.0846 | 0.00025714
2013-01-10 | 288030 | BHD35A | Rural short | Feeder BHD35A - Planned | 27.98 | 360 | 10072.8 | 0.029086 | 8.0796e-05
2013-01-10 | 288032 | SPO31A | Urban | Feeder SPO31A, SPO51A - Planned | 2.09 | 595 | 1243.55 | 0.0012549 | 2.109e-06
2013-01-10 | 288032 | SPO51A | Urban | Feeder SPO31A, SPO51A - Planned | 1 | 595 | 595 | 0.00060041 | 1.0091e-06
2013-01-10 | 288035 | NRG16A | Rural short | LV Transformer SP5211-G NRG16A - Planned | 18.05 | 430 | 7761.5 | 0.022412 | 5.2121e-05
2013-01-10 | 288037 | BMT1 | Rural short | Feeder BMT1 - Planned | 47.8 | 247 | 11806.6 | 0.034093 | 0.00013803
2013-01-10 | 288038 | GYS3A | Rural short | LV Transformer SP7662-B GYS3A - Planned | 4 | 218 | 872 | 0.002518 | 1.155e-05
2013-01-10 | 288039 | GYGGYS6 | Rural short | LV Transformer SP13636-C GYGGYS6 - Planned | 1 | 101 | 101 | 0.00029165 | 2.8876e-06
2013-01-10 | 288040 | GGR5 | Rural short | Feeder GGR5 - Planned | 4.5 | 554 | 2493 | 0.0071988 | 1.2994e-05
2013-01-10 | 288048 | DRA6 | Urban | LV Transformer SP10554-F DRA6 - Planned | 6.02 | 77 | 463.54 | 0.00046775 | 6.0747e-06
2013-01-10 | 288049 | GAP8A | Urban | LV Transformer SP3196-L GAP8A - Planned | 11.02 | 394 | 4341.88 | 0.0043813 | 1.112e-05
2013-01-10 | 288050 | ENG7 | Urban | LV Transformer SP802367 ENG7 - Planned | 22.8 | 241 | 5494.8 | 0.0055447 | 2.3007e-05
2013-01-10 | 288051 | LDR8 | Urban | LV Transformer SP1122-K LDR8 - Planned | 20.75 | 225 | 4668.75 | 0.0047112 | 2.0939e-05
2013-01-10 | 288052 | BHD31A | Urban | LV Transformer SC22921-C BHD31A - Planned | 2.17 | 10 | 21.7 | 2.1897e-05 | 2.1897e-06
2013-01-10 | 288053 | CRBTHP26 | Urban | LV Transformer SP4207-G CRBTHP26 - Planned | 27.375 | 310 | 8486.25 | 0.0085634 | 2.7624e-05
2013-01-10 | 288054 | SPD11A | Urban | LV Transformer SP3797-E SPD11A - Planned | 17.4897 | 377 | 6593.6169 | 0.0066536 | 1.7649e-05
2013-01-10 | 288055 | DRD13A | Urban | LV Transformer SP2609-F DRD13A - Planned | 25.785 | 220 | 5672.7 | 0.0057243 | 2.6019e-05
2013-01-10 | 288055 | DRD2A | Rural short | LV Transformer SP2609-F DRD13A - Planned | 0.84 | 220 | 184.8 | 0.00053363 | 2.4256e-06
2013-01-10 | 288055 | DRD3A | Urban | LV Transformer SP2609-F DRD13A - Planned | 8.905 | 220 | 1959.1 | 0.0019769 | 8.9859e-06
2013-01-10 | 288056 | BLBNFM6 | Urban | LV Transformer SP3429-G BLBNFM6 - Planned | 25.29 | 253 | 6398.37 | 0.0064565 | 2.552e-05
2013-01-10 | 288057 | ALY9 | Urban | LV Transformer SP5265-H ALY9 - Planned | 21.08 | 246 | 5185.68 | 0.0052328 | 2.1272e-05
2013-01-10 | 288057 | MRK3 | Urban | LV Transformer SP5265-H ALY9 - Planned | 2.34 | 246 | 575.64 | 0.00058087 | 2.3613e-06
2013-01-10 | 288058 | CPR7 | Urban | LV Transformer SP26255-D CPR7 - Planned | 6.39 | 20 | 127.8 | 0.00012896 | 6.4481e-06
2013-01-10 | 288059 | HDA10A | Urban | LV Transformer SP11233-E HDA10A - Planned | 5.445 | 10 | 54.45 | 5.4945e-05 | 5.4945e-06
2013-01-10 | 288060 | SPF17B | Urban | LV Transformer SC21463-D SPF17B - Planned | 1.9733 | 280 | 552.524 | 0.00055755 | 1.9912e-06
2013-01-10 | 288061 | RWD2 | Rural short | LV Transformer SP3503-D RWD2 - Planned | 11.505 | 340 | 3911.7 | 0.011295 | 3.3222e-05
2013-01-10 | 288081 | TVCT1 | Urban | LV Transformer SSTVC TVCT4 - Planned | 4 | 301 | 1204 | 0.0012149 | 4.0364e-06
2013-01-10 | 288083 | LBH1B | Rural short | LV Transformer SP202341 LBH1B - Planned | 2.94 | 163 | 479.22 | 0.0013838 | 8.4896e-06
2013-01-10 | 288180 | KWA2A | Urban | LV Transformer SC2451-B KWA2A - Planned | 2.01 | 308 | 619.08 | 0.00062471 | 2.0283e-06
2013-01-11 | 288103 | THL3 | Rural short | LV Transformer SP3017-C THL3 - Planned | 5.5 | 105 | 577.5 | 0.0016676 | 1.5882e-05
2013-01-11 | 288121 | RBA43A | Rural short | LV Transformer SP6448-F RBA43A - Planned | 18 | 184 | 3312 | 0.0095641 | 5.1979e-05
2013-01-11 | 288124 | FDS1 | Rural short | Feeder FDS1 - Planned | 22 | 192 | 4224 | 0.012198 | 6.3529e-05
2013-01-11 | 288127 | FDS1 | Rural short | Feeder FDS1 - Planned | 16.8 | 329 | 5527.2 | 0.015961 | 4.8513e-05
2013-01-11 | 288128 | MGL2A | Rural short | LV Transformer SP446-P MGL2A - Planned | 3 | 272 | 816 | 0.0023564 | 8.6631e-06
2013-01-11 | 288130 | CPD2A | Rural short | LV Transformer SP1972-C CPD2A - Planned | 2.5 | 285 | 712.5 | 0.0020575 | 7.2193e-06
2013-01-11 | 288131 | WFD5A | Rural short | Feeder WFD5A - Planned | 8 | 263 | 2104 | 0.0060757 | 2.3102e-05
2013-01-11 | 288134 | GYM9B | Rural short | LV Transformer SP3-H GYM9B - Planned | 3 | 301 | 903 | 0.0026076 | 8.6631e-06
2013-01-11 | 288138 | ENG2 | Urban | LV Transformer SP4744-K GLY6 - Planned | 1.91 | 206 | 393.46 | 0.00039703 | 1.9273e-06
2013-01-11 | 288138 | GLY6 | Urban | LV Transformer SP4744-K GLY6 - Planned | 7.02 | 206 | 1446.12 | 0.0014592 | 7.0837e-06
2013-01-11 | 288139 | GLY2 | Urban | LV Transformer SC736389 - Planned | 6.25 | 187 | 1168.75 | 0.0011794 | 6.3067e-06
2013-01-11 | 288140 | AGE3 | Urban | LV Transformer SC714533 AGE3 - Planned | 1.755 | 180 | 315.9 | 0.00031877 | 1.7709e-06
2013-01-11 | 288141 | GAP8A | Urban | LV Transformer SP4703-H GAP8A - Planned | 30.1 | 368 | 11076.8 | 0.011177 | 3.0373e-05
2013-01-11 | 288142 | BMT3 | Rural short | LV Transformer SP18309-A BMT3 - Planned | 2.07 | 45 | 93.15 | 0.00026899 | 5.9775e-06
2013-01-11 | 288143 | KWA2A | Urban | LV Transformer SP4519-B KWA2A - Planned | 28.405 | 335 | 9515.675 | 0.009602 | 2.8663e-05
2013-01-11 | 288145 | CLD8 | Urban | LV Transformer SP1665-B CLD8 - Planned | 18.87 | 221 | 4170.27 | 0.0042081 | 1.9041e-05
2013-01-11 | 288146 | MMC20A | Urban | LV Transformer SC1444-I MMC20A - Planned | 26.54 | 83 | 2202.82 | 0.0022228 | 2.6781e-05
2013-01-11 | 288147 | UPC2 | Rural short | LV Transformer SP2929-E UPC2 - Planned | 3.96 | 324 | 1283.04 | 0.003705 | 1.1435e-05
2013-01-11 | 288148 | CRB25A | Rural short | LV Transformer SP120497 CRB25A - Planned | 5.52 | 567 | 3129.84 | 0.009038 | 1.594e-05
2013-01-11 | 288149 | DRD13A | Urban | LV Transformer SP3177-D DRD13A - Planned | 26.24 | 270 | 7084.8 | 0.0071491 | 2.6478e-05
2013-01-11 | 288150 | DRD3A | Urban | LV Transformer SP4140-D DRD3A - Planned | 15.12 | 312 | 4717.44 | 0.0047602 | 1.5257e-05
2013-01-11 | 288151 | CFD2A | Urban | LV Transformer SP7107-G CFD2A - Planned | 14.235 | 313 | 4455.555 | 0.004496 | 1.4364e-05
2013-01-11 | 288152 | MRE8 | Urban | LV Transformer SP3430-H MRE8 - Planned | 0.935 | 107 | 100.045 | 0.00010095 | 9.4348e-07
2013-01-11 | 288153 | KCY1 | Urban | LV Transformer SP4099-H KCY1 - Planned | 40.12 | 310 | 12437.2 | 0.01255 | 4.0484e-05
2013-01-11 | 288154 | ARG5A | Urban | LV Transformer SP2764-J ARG5A - Planned | 6.3 | 208 | 1310.4 | 0.0013223 | 6.3572e-06
2013-01-11 | 288155 | SBY4 | Urban | LV Transformer SP2087-I SBY4 - Planned | 11.31 | 90 | 1017.9 | 0.0010271 | 1.1413e-05
2013-01-11 | 288156 | CVL17A | Urban | LV Transformer SP10324-C CVL17A - Planned | 31.6393 | 143 | 4524.4199 | 0.0045655 | 3.1926e-05
2013-01-11 | 288157 | BLH12B | Urban | LV Transformer SP4073-C BLH12B - Planned | 15.4 | 215 | 3311 | 0.003341 | 1.554e-05
2013-01-11 | 288159 | IPS5B | Urban | LV Transformer SP46915-B IPS5B - Planned | 0.87 | 25 | 21.75 | 2.1947e-05 | 8.7789e-07
2013-01-11 | 288160 | CPD1 | Rural short | LV Transformer SP8234-B CPD1 - Planned | 4.98 | 40 | 199.2 | 0.00057523 | 1.4381e-05
2013-01-11 | 288161 | RST2A | Urban | LV Transformer SC127-G RST2A - Planned | 21.76 | 52 | 1131.52 | 0.0011418 | 2.1957e-05
2013-01-12 | 288177 | BPN2A | Urban | LV Transformer SG808004 BPN2A - Planned | 1 | 250 | 250 | 0.00025227 | 1.0091e-06
2013-01-12 | 288178 | BLH10A | Urban | LV Transformer SC1327-E BLH10A - Planned | 23 | 319 | 7337 | 0.0074035 | 2.3208e-05
2013-01-12 | 288223 | AFD1A | Urban | LV Transformer SP16661-E - Planned | 1 | 266 | 266 | 0.00026841 | 1.0091e-06
2013-01-13 | 288220 | SPE20A | Urban | Feeder SPE20A - Planned | 49.12 | 391 | 19205.92 | 0.01938 | 4.9564e-05
2013-01-13 | 288222 | NMK18 | Urban | LV Transformer SP1771-O NMK18 - Planned | 25.935 | 348 | 9025.38 | 0.009107 | 2.617e-05
2013-01-13 | 288224 | GBG1A | Urban | LV Transformer SC6400-D GBG1A - Planned | 4 | 537 | 2148 | 0.0021674 | 4.0362e-06
2013-01-13 | 288224 | GBG1B | Urban | LV Transformer SC6400-D GBG1A - Planned | 0.93 | 537 | 499.41 | 0.00050393 | 9.3841e-07
2013-01-13 | 288226 | CFD1A | Urban | LV Transformer SP2086-I CFD1A - Planned | 15.825 | 455 | 7200.375 | 0.0072655 | 1.5968e-05
2013-01-13 | 288242 | HTN22A | Urban | Feeder HTN22A - Planned | 3 | 389 | 1167 | 0.0011776 | 3.0271e-06
2013-01-13 | 288247 | RBA37A | Urban | Feeder RBA43A, RBA37A - Planned | 1 | 363 | 363 | 0.00036628 | 1.009e-06
2013-01-13 | 288249 | CFD1A | Urban | LV Transformer SG845-L CFD1A - Planned | 15.825 | 455 | 7200.375 | 0.0072655 | 1.5968e-05
2013-01-13 | 288261 | BDL1 | Urban | LV Transformer SG7160-G BDL1 - Planned | 3 | 246 | 738 | 0.00074467 | 3.0271e-06
2013-01-14 | 288262 | IPL2 | Rural short | Feeder IPL2 - Planned | 23.02 | 139 | 3199.78 | 0.0092407 | 6.648e-05
2013-01-14 | 288281 | GBN4 | Rural short | LV Transformer SP2636-E GBN4 - Planned | 1 | 60 | 60 | 0.00017327 | 2.8879e-06
2013-01-14 | 288282 | MLY3 | Rural short | LV Transformer SP5147-B MLY3 - Planned | 1 | 207 | 207 | 0.0005978 | 2.8879e-06
2013-01-14 | 288285 | LGV2B | Rural short | LV Transformer SP7856-B LGV2B - Planned | 31.96 | 321 | 10259.16 | 0.029628 | 9.2298e-05
2013-01-14 | 288287 | KCY5 | Rural short | Feeder KCY5 - Planned | 62.34 | 366 | 22816.44 | 0.065892 | 0.00018003
2013-01-14 | 288289 | DRD13A | Urban | LV Transformer SP3177-D DRD13A - Planned | 7.38 | 196 | 1446.48 | 0.0014595 | 7.4467e-06
2013-01-14 | 288291 | BHL2A | Urban | LV Transformer SP2753-H BHL2A - Planned | 3.9 | 160 | 624 | 0.00062964 | 3.9352e-06
2013-01-14 | 288292 | LHM3 | Urban | LV Transformer SC266-C LHM3 - Planned | 9.3 | 147 | 1367.1 | 0.0013794 | 9.384e-06
2013-01-14 | 288294 | RLA8 | Urban | LV Transformer SP392-R RLA8 - Planned | 2.7549 | 96 | 264.4704 | 0.00026686 | 2.7798e-06
2013-01-15 | 288325 | RWD2 | Rural short | LV Transformer SP1523-H RWD2 - Planned | 44 | 70 | 3080 | 0.0088952 | 0.00012707
2013-01-15 | 288330 | KBR1A | Rural short | Feeder KBR1A - Planned | 11.02 | 197 | 2170.94 | 0.0062698 | 3.1826e-05
2013-01-15 | 288331 | SMF1B | Rural short | LV Transformer SP3313-J SMF1B - Planned | 9 | 158 | 1422 | 0.0041068 | 2.5992e-05
2013-01-15 | 288334 | UPC1 | Rural short | LV Transformer SP11800-G UPC1 - Planned | 11.96 | 355 | 4245.8 | 0.012262 | 3.4541e-05
2013-01-15 | 288336 | TGW3 | Rural short | Feeder TGW3 - Planned | 34.167 | 449 | 15340.983 | 0.044305 | 9.8676e-05
2013-01-15 | 288337 | CNB24A | Rural short | Feeder CNB24A - Planned | 31.1488 | 360 | 11213.568 | 0.032385 | 8.9959e-05
2013-01-15 | 288338 | LLY1 | Rural short | LV Transformer SP1634-C LLY1 - Planned | 3 | 325 | 975 | 0.0028158 | 8.6641e-06
2013-01-15 | 288339 | MGP13A | Rural short | Feeder MGP13A - Planned | 31 | 470 | 14570 | 0.042079 | 8.9529e-05
2013-01-15 | 288340 | BMT1 | Rural short | Feeder BMT1 - Planned | 43.48 | 415 | 18044.2 | 0.052112 | 0.00012557
2013-01-15 | 288342 | CNB24A | Rural short | Feeder CNB24A - Planned | 34.33 | 360 | 12358.8 | 0.035693 | 9.9146e-05
2013-01-15 | 288345 | AGE10 | Urban | LV Transformer SG4221-H AGE10 - Planned | 1 | 643 | 643 | 0.0006488 | 1.009e-06
2013-01-15 | 288347 | CNB24A | Rural short | LV Transformer SP6783-E CNB24A - Planned | 31.1488 | 360 | 11213.568 | 0.032385 | 8.9959e-05
2013-01-15 | 288348 | BMT1 | Rural short | LV Transformer SP3909-B BMT1 - Planned | 43.48 | 415 | 18044.2 | 0.052112 | 0.00012557
2013-01-15 | 288349 | MGP13A | Rural short | LV Transformer SP4506-F MGP13A - Planned | 31 | 470 | 14570 | 0.042079 | 8.9529e-05
2013-01-15 | 288350 | NMK7 | Urban | LV Transformer SP4089-K NMK7 - Planned | 3.06 | 274 | 838.44 | 0.000846 | 3.0876e-06
2013-01-15 | 288351 | AGE10 | Urban | LV Transformer SP26943-F AGE10 - Planned | 23.8146 | 335 | 7977.891 | 0.0080498 | 2.4029e-05
2013-01-15 | 288351 | TWG11 | Urban | LV Transformer SP26943-F AGE10 - Planned | 1.33 | 335 | 445.55 | 0.00044957 | 1.342e-06
2013-01-15 | 288352 | AGE10 | Urban | LV Transformer SC772751-A AGE10 - Planned | 13.625 | 396 | 5395.5 | 0.0054441 | 1.3748e-05
2013-01-15 | 288353 | OXL11A | Urban | LV Transformer SP12494-F OXL11A - Planned | 10.1166 | 288 | 2913.5808 | 0.0029398 | 1.0208e-05
2013-01-15 | 288354 | BMT3 | Rural short | LV Transformer SC1370758 BMT3 - Planned | 75.18 | 47 | 3533.46 | 0.010205 | 0.00021712
2013-01-15 | 288355 | TCB1 | Rural short | LV Transformer SP48392-A TCB1 - Planned | 11.2 | 278 | 3113.6 | 0.0089922 | 3.2346e-05
2013-01-15 | 288356 | CRB25A | Rural short | LV Transformer SP5764-F CRB25A - Planned | 24.055 | 368 | 8852.24 | 0.025566 | 6.9472e-05
2013-01-15 | 288357 | BHD45B | Urban | LV Transformer SC22908-B BHD31A - Planned | 56.96 | 55 | 3132.8 | 0.003161 | 5.7473e-05
2013-01-15 | 288357 | MAI13 | Urban | LV Transformer SC22908-B BHD31A - Planned | 1.01 | 55 | 55.55 | 5.6051e-05 | 1.0191e-06
2013-01-15 | 288358 | BRD2A | Urban | LV Transformer SC103-J BRD2A - Planned | 4.24 | 380 | 1611.2 | 0.0016257 | 4.2782e-06
2013-01-15 | 288359 | DBY6 | Urban | LV Transformer SP484292 DBY6 - Planned | 5.15 | 229 | 1179.35 | 0.00119 | 5.1964e-06
2013-01-15 | 288360 | BISTPT3 | Rural short | LV Transformer SP3264-C BISTPT3 - Planned | 7.98 | 304 | 2425.92 | 0.0070061 | 2.3047e-05
2013-01-15 | 288361 | DRD13A | Urban | LV Transformer SP10719-C DRD13A - Planned | 7.325 | 265 | 1941.125 | 0.0019586 | 7.391e-06
2013-01-15 | 288362 | SGT5 | Urban | LV Transformer SP5170-G SGT5 - Planned | 8.1 | 247 | 2000.7 | 0.0020187 | 8.173e-06
2013-01-15 | 288363 | SBK11 | Urban | LV Transformer SP713-K SBK11 - Planned | 15.51 | 295 | 4575.45 | 0.0046167 | 1.565e-05
2013-01-15 | 288364 | DRA11 | Urban | LV Transformer SP10554-F DRA6 - Planned | 0.885 | 282 | 249.57 | 0.00025182 | 8.9298e-07
2013-01-15 | 288364 | DRA6 | Urban | LV Transformer SP10554-F DRA6 - Planned | 23.22 | 282 | 6548.04 | 0.0066071 | 2.3429e-05
2013-01-15 | 288364 | DRA8 | Urban | LV Transformer SP10554-F DRA6 - Planned | 9.625 | 282 | 2714.25 | 0.0027387 | 9.7118e-06
2013-01-15 | 288365 | RPN3A | Urban | LV Transformer SC1457814 RPN3A - Planned | 8.19 | 20 | 163.8 | 0.00016528 | 8.2638e-06
2013-01-15 | 288366 | WHO2 | Rural short | LV Transformer SP1252-C WHO2 - Planned | 2.07 | 323 | 668.61 | 0.001931 | 5.9782e-06
2013-01-16 | 288380 | PRG2B | Rural short | LV Transformer SP11735-A PRG2B - Planned | 1 | 19 | 19 | 5.4874e-05 | 2.8881e-06
2013-01-16 | 288383 | TGW1 | Rural short | Feeder TGW1 - Planned | 6.01 | 222 | 1334.22 | 0.0038534 | 1.7358e-05
2013-01-16 | 288384 | SPD7B | Urban | Feeder SPO49B, SPD7B - Planned | 0.74 | 135 | 99.9 | 0.0001008 | 7.4666e-07
2013-01-16 | 288384 | SPO49B | Urban | Feeder SPO49B, SPD7B - Planned | 1.6858 | 135 | 227.583 | 0.00022963 | 1.701e-06
2013-01-16 | 288385 | JBB16A | Rural short | Feeder JBB16A - Planned | 100.9 | 252 | 25426.8 | 0.073436 | 0.00029141
2013-01-16 | 288388 | HDN1 | Rural short | LV Transformer SP5010-B HDN1 - Planned | 3 | 225 | 675 | 0.0019495 | 8.6644e-06
2013-01-16 | 288389 | TGW3 | Rural short | LV Transformer SP8888-A TGW3 - Planned | 2.01 | 260 | 522.6 | 0.0015093 | 5.8051e-06
2013-01-16 | 288390 | WSE3A | Rural short | Feeder WSE3A - Planned | 57.76 | 328 | 18945.28 | 0.054716 | 0.00016682
2013-01-16 | 288391 | KBR2A | Rural short | LV Transformer SP8606-B KBR2A - Planned | 1 | 445 | 445 | 0.0012852 | 2.8881e-06
2013-01-16 | 288392 | MLY3 | Rural short | Feeder MLY3 - Planned | 133.885 | 447 | 59846.595 | 0.17284 | 0.00038668
2013-01-16 | 288393 | GYGGYS6 | Rural short | Feeder GYGGYS6 - Planned | 10.01 | 393 | 3933.93 | 0.011362 | 2.891e-05
2013-01-16 | 288394 | MLY4 | Rural short | LV Transformer SP3959-B MLY4 - Planned | 16.45 | 271 | 4457.95 | 0.012875 | 4.751e-05
2013-01-16 | 288395 | MLY1 | Rural short | LV Transformer SP5171-B MLY1 - Planned | 0.536 | 359 | 192.424 | 0.00055574 | 1.548e-06
2013-01-16 | 288396 | PWC4 | Rural short | Feeder PWC4 - Planned | 12.51 | 111 | 1388.61 | 0.0040105 | 3.613e-05
2013-01-16 | 288397 | CRY5A | Rural short | Feeder CRY5A - Planned | 34.9288 | 172 | 6007.7536 | 0.017351 | 0.00010088
2013-01-16 | 288402 | UPC1 | Rural short | Feeder UPC1 - Planned | 21.7 | 620 | 13454 | 0.038857 | 6.2672e-05
2013-01-16 | 288404 | AGE10 | Urban | LV Transformer SP2588-M AGE10 - Planned | 4.825 | 128 | 617.6 | 0.00062316 | 4.8684e-06
2013-01-16 | 288405 | KRN10 | Urban | LV Transformer SC531869-A KRN10 - Planned | 2.015 | 288 | 580.32 | 0.00058554 | 2.0331e-06
2013-01-16 | 288406 | AHL6A | Urban | LV Transformer SC4984-K AHL6A - Planned | 3.8132 | 90 | 343.188 | 0.00034627 | 3.8475e-06
2013-01-16 | 288407 | KMR28A | Urban | LV Transformer SP2070-J KMR28A - Planned | 20.74 | 301 | 6242.74 | 0.0062989 | 2.0927e-05
2013-01-16 | 288408 | KMR27A | Urban | LV Transformer SP2205-K KMR27A - Planned | 4.26 | 197 | 839.22 | 0.00084677 | 4.2983e-06
2013-01-16 | 288409 | AMR1 | Rural short | LV Transformer SP546-B AMR1 - Planned | 3 | 370 | 1110 | 0.0032058 | 8.6644e-06
2013-01-16 | 288410 | KWH1 | Rural short | LV Transformer SC1426000 KWH1 - Planned | 2.09 | 58 | 121.22 | 0.0003501 | 6.0362e-06
2013-01-16 | 288411 | HIS12A | Urban | LV Transformer SP5152-H HIS12A - Planned | 16.62 | 191 | 3174.42 | 0.003203 | 1.6769e-05
2013-01-16 | 288412 | MAI5 | Urban | LV Transformer SP4586-H MAI5 - Planned | 6.57 | 306 | 2010.42 | 0.0020285 | 6.6291e-06
2013-01-16 | 288413 | RBARHP14 | Urban | LV Transformer SP4625-D RBARHP14 - Planned | 14.01 | 62 | 868.62 | 0.00087643 | 1.4136e-05
2013-01-16 | 288415 | SPO51A | Urban | LV Transformer SP38163-B SPO51A - Planned | 25.085 | 383 | 9607.555 | 0.009694 | 2.5311e-05
2013-01-16 | 288417 | MRE3 | Urban | LV Transformer SP517-N MRE3 - Planned | 27.15 | 225 | 6108.75 | 0.0061637 | 2.7394e-05
2013-01-16 | 288418 | BISTPT3 | Rural short | LV Transformer SP3264-C BISTPT3 - Planned | 5.985 | 334 | 1998.99 | 0.0057733 | 1.7285e-05
2013-01-16 | 288419 | WNM2A | Urban | LV Transformer SP807686 WNM2A - Planned | 18.92 | 342 | 6470.64 | 0.0065288 | 1.909e-05
2013-01-16 | 288420 | KCY1 | Urban | LV Transformer SP1329-H KCY1 - Planned | 22.04 | 310 | 6832.4 | 0.0068939 | 2.2238e-05
2013-01-16 | 288421 | AHL4A | Urban | LV Transformer SP11497-G AHL4A - Planned | 1.005 | 111 | 111.555 | 0.00011256 | 1.014e-06
2013-01-16 | 288423 | SGT5 | Urban | LV Transformer SP39152-D SGT5 - Planned | 17.25 | 212 | 3657 | 0.0036899 | 1.7405e-05
2013-01-16 | 288424 | SGT5 | Urban | LV Transformer SP2190-I SGT5 - Planned | 7.98 | 110 | 877.8 | 0.0008857 | 8.0518e-06
2013-01-16 | 288425 | MTG15A | Urban | LV Transformer SP1208-Q MTG15A - Planned | 3.1098 | 276 | 858.3048 | 0.00086603 | 3.1378e-06
2013-01-16 | 288427 | TMH16A | Urban | LV Transformer SP6646-E TMH16A - Planned | 7.175 | 250 | 1793.75 | 0.0018099 | 7.2395e-06
2013-01-16 | 288428 | BLBNFM6 | Urban | LV Transformer SP5394-E BLBNFM6 - Planned | 6.915 | 228 | 1576.62 | 0.0015908 | 6.9772e-06
2013-01-16 | 288429 | BKD2B | Urban | LV Transformer SP5414-D BKD2B - Planned | 14.04 | 162 | 2274.48 | 0.0022949 | 1.4166e-05
2013-01-16 | 288430 | RST9A | Urban | LV Transformer SP4908-C RST9A - Planned | 13.1397 | 468 | 6149.3796 | 0.0062047 | 1.3258e-05
2013-01-16 | 288431 | RCN2A | Urban | LV Transformer SC4570-J RCN2A - Planned | 23.9122 | 266 | 6360.6452 | 0.0064179 | 2.4127e-05
2013-01-16 | 288432 | HDN1 | Rural short | LV Transformer SP2289-D HDN1 - Planned | 2.1294 | 392 | 834.7248 | 0.0024108 | 6.15e-06
2013-01-16 | 288433 | CPD1 | Rural short | LV Transformer SP1342-C CPD1 - Planned | 3 | 226 | 678 | 0.0019581 | 8.6644e-06
2013-01-17 | 288440 | TGW1 | Rural short | LV Transformer SP4766-B TGW1 - Planned | 4 | 248 | 992 | 0.0028645 | 1.155e-05
2013-01-17 | 288441 | NRA3B | Rural short | LV Transformer SP17337-D NRA3B - Planned | 1 | 232 | 232 | 0.00066992 | 2.8876e-06
2013-01-17 | 288461 | WHO1 | Rural short | LV Transformer SP3738-B WHO1 - Planned | 4.98 | 388 | 1932.24 | 0.0055795 | 1.438e-05
2013-01-17 | 288462 | MLY3 | Rural short | LV Transformer SP2997-C MLY3 - Planned | 7.04 | 337 | 2372.48 | 0.0068508 | 2.0329e-05
2013-01-17 | 288463 | NBR1 | Rural short | LV Transformer SP3511-B NBR1 - Planned | 13.5 | 366 | 4941 | 0.014268 | 3.8983e-05
2013-01-17 | 288464 | MLY1 | Rural short | LV Transformer SP2088-C - Planned | 13.67 | 189 | 2583.63 | 0.0074605 | 3.9473e-05
2013-01-17 | 288465 | TGP5B | Urban | LV Transformer SC518087 TGP5B - Planned | 1.12 | 50 | 56 | 5.6507e-05 | 1.1301e-06
2013-01-17 | 288466 | DRD3A | Urban | LV Transformer SP3054-F DRD3A - Planned | 32.94 | 303 | 9980.82 | 0.010071 | 3.3238e-05
2013-01-17 | 288467 | NSW3A | Urban | LV Transformer SC1429938 NSW3A - Planned | 0.86 | 332 | 285.52 | 0.00028811 | 8.6779e-07
2013-01-17 | 288468 | DRD15B | Urban | LV Transformer SP3741-C DRD15B - Planned | 22.8 | 187 | 4263.6 | 0.0043022 | 2.3006e-05
2013-01-17 | 288469 | SBY8 | Urban | LV Transformer SP473-L SBY8 - Planned | 3.8332 | 190 | 728.308 | 0.0007349 | 3.8679e-06
2013-01-17 | 288470 | AGE8 | Urban | LV Transformer SP660-L AGE8 - Planned | 18.88 | 291 | 5494.08 | 0.0055438 | 1.9051e-05
2013-01-17 | 288471 | BLB4A | Urban | LV Transformer SP3470-G BLB4A - Planned | 14.49 | 245 | 3550.05 | 0.0035822 | 1.4621e-05
2013-01-17 | 288472 | KWA12A | Urban | LV Transformer SP85364-A KWA12A - Planned | 10.14 | 269 | 2727.66 | 0.0027524 | 1.0232e-05
2013-01-17 | 288473 | WRD25B | Urban | LV Transformer SP51770-D WRD25B - Planned | 2.1 | 240 | 504 | 0.00050856 | 2.119e-06
2013-01-17 | 288474 | NBR9 | Rural short | LV Transformer SP2021-A NBR9 - Planned | 30.07 | 365 | 10975.55 | 0.031693 | 8.683e-05
2013-01-17 | 288475 | LLY4 | Rural short | LV Transformer SP26534-B LLY4 - Planned | 3 | 280 | 840 | 0.0024256 | 8.6628e-06
2013-01-17 | 288476 | GYM8B | Urban | LV Transformer SP4842-B GYM8B - Planned | 0.6833 | 35 | 23.9155 | 2.4132e-05 | 6.8949e-07
2013-01-17 | 288477 | BDB28A | Urban | LV Transformer SP2698-F BDB28A - Planned | 4.62 | 250 | 1155 | 0.0011655 | 4.6618e-06
2013-01-17 | 288477 | MWMRBK11 | Rural short | LV Transformer SP2698-F BDB28A - Planned | 2.68 | 250 | 670 | 0.0019347 | 7.7388e-06
2013-01-17 | 288478 | TCB3 | Rural short | LV Transformer SP588951 TCB3 - Planned | 6 | 28 | 168 | 0.00048512 | 1.7326e-05
2013-01-17 | 288479 | NBR9 | Rural short | Feeder NBR9 - Planned | 19.01 | 2 | 38.02 | 0.00010979 | 5.4893e-05
2013-01-17 | 288480 | CLM9 | Urban | LV Transformer SP5388-A CLM9 - Planned | 14.3 | 187 | 2674.1 | 0.0026983 | 1.4429e-05
2013-01-17 | 288481 | LDR3 | Urban | LV Transformer SP958-G LDR3 - Planned | 44.88 | 346 | 15528.48 | 0.015669 | 4.5286e-05
2013-01-17 | 288482 | CRB25A | Rural short | LV Transformer SP5797-E CRB25A - Planned | 6.2054 | 402 | 2494.5708 | 0.0072033 | 1.7919e-05
2013-01-17 | 288483 | SPO3A | Urban | LV Transformer SP6440-G SPO3A - Planned | 14.69 | 340 | 4994.6 | 0.0050398 | 1.4823e-05
2013-01-17 | 288484 | ACR3A | Urban | LV Transformer SC7878-E ACR3A - Planned | 9 | 253 | 2277 | 0.0022976 | 9.0815e-06
2013-01-17 | 288485 | HTN7A | Urban | LV Transformer SC484256 HTN7A - Planned | 16.055 | 31 | 497.705 | 0.00050221 | 1.62e-05
2013-01-17 | 288486 | SGT24A | Urban | LV Transformer SP3702-G SGT24A - Planned | 12.35 | 302 | 3729.7 | 0.0037635 | 1.2462e-05
2013-01-17 | 288487 | NDH5A | Urban | LV Transformer SP310-J NDH5A - Planned | 12.84 | 48 | 616.32 | 0.0006219 | 1.2956e-05
2013-01-17 | 288500 | CRB25A | Rural short | Feeder CRB25A - Planned | 52.83 | 425 | 22452.75 | 0.064834 | 0.00015255
2013-01-17 | 288565 | AGE10 | Urban | LV Transformer SP2911-K AGE10 - Planned | 11.395 | 269 | 3065.255 | 0.003093 | 1.1498e-05
2013-01-17 | 288616 | RLB16A | Rural short | LV Transformer SP3577-B RLB16A - Planned | 0.264 | 512 | 135.168 | 0.00039031 | 7.6233e-07
2013-01-18 | 288538 | BNH2B | Rural short | Feeder BNH2B - Planned | 8.99 | 94 | 845.06 | 0.0024402 | 2.5959e-05
2013-01-18 | 288543 | SMF3A | Rural short | LV Transformer SP12066-G SMF3A - Planned | 1 | 230 | 230 | 0.00066414 | 2.8876e-06
2013-01-18 | 288544 | JBB1B | Rural short | Feeder JBB1B - Planned | 84.86 | 257 | 21809.02 | 0.062975 | 0.00024504
2013-01-18 | 288545 | WSE5A | Rural short | LV Transformer SC522784-A WSE5A - Planned | 19 | 323 | 6137 | 0.017721 | 5.4863e-05
2013-01-18 | 288552 | MCW4 | Rural short | LV Transformer SP1510-H MCW4 - Planned | 1 | 283 | 283 | 0.00081718 | 2.8876e-06
2013-01-18 | 288553 | CRB25A | Rural short | Feeder CRB25A - Planned | 26.3704 | 476 | 12552.3104 | 0.036245 | 7.6146e-05
2013-01-18 | 288554 | NBR9 | Rural short | Feeder NBR9 - Planned | 19.01 | 18 | 684.36 | 0.0019761 | 5.4892e-05
2013-01-18 | 288555 | WMD8B | Rural short | LV Transformer SP417-A WMD8B - Planned | 33 | 297 | 9801 | 0.028301 | 9.5289e-05
2013-01-18 | 288556 | CRY2A | Rural short | LV Transformer SP6446-C CRY2A - Planned | 6 | 177 | 1062 | 0.0030666 | 1.7325e-05
2013-01-18 | 288560 | AMR1 | Rural short | LV Transformer SP2911-C AMR1 - Planned | 6 | 419 | 2514 | 0.0072593 | 1.7325e-05
2013-01-18 | 288561 | TRP1 | Rural short | Feeder TRP1 - Planned | 25.98 | 440 | 11431.2 | 0.033008 | 7.5019e-05
2013-01-18 | 288562 | MHL1B | Rural short | LV Transformer SC759276 MHL1B - Planned | 4.08 | 439 | 1791.12 | 0.005172 | 1.1781e-05
2013-01-18 | 288563 | DRA1A | Urban | LV Transformer SP11041-E DRA1A - Planned | 8.88 | 295 | 2619.6 | 0.0026433 | 8.9605e-06
2013-01-18 | 288564 | ENG2 | Urban | LV Transformer SP867-L ENG2 - Planned | 19.63 | 250 | 4907.5 | 0.004952 | 1.9808e-05
2013-01-18 | 288566 | NBR9 | Rural short | LV Transformer SP3050-A NBR9 - Planned | 8.01 | 288 | 2306.88 | 0.0066612 | 2.3129e-05
2013-01-18 | 288567 | NVL9 | Rural short | LV Transformer SP6285-A NVL9 - Planned | 8.88 | 185 | 1642.8 | 0.0047437 | 2.5641e-05
2013-01-18 | 288568 | WMD8B | Rural short | LV Transformer SP2713-A WMD8B - Planned | 6.08 | 249 | 1513.92 | 0.0043715 | 1.7556e-05
2013-01-18 | 288569 | MLY3 | Rural short | LV Transformer SP7774-A MLY3 - Planned | 8.1 | 181 | 1466.1 | 0.0042334 | 2.3389e-05
2013-01-18 | 288570 | BLH12B | Urban | LV Transformer SP4937-B BLH12B - Planned | 23.46 | 206 | 4832.76 | 0.0048765 | 2.3673e-05
2013-01-18 | 288571 | CCY13A | Urban | LV Transformer SP6376-E CCY13A - Planned | 12.07 | 191 | 2305.37 | 0.0023263 | 1.2179e-05
2013-01-18 | 288572 | SPO51A | Urban | LV Transformer SP3885-E SPO51A - Planned | 20.8 | 210 | 4368 | 0.0044076 | 2.0988e-05
2013-01-18 | 288573 | MLY4 | Rural short | LV Transformer SP9506-A MLY4 - Planned | 20.475 | 197 | 4033.575 | 0.011647 | 5.9123e-05
2013-01-18 | 288574 | DRD13A | Urban | LV Transformer SP2609-F DRD13A - Planned | 42.975 | 253 | 10872.675 | 0.010971 | 4.3364e-05
2013-01-18 | 288575 | MTG12B | Urban | LV Transformer SP2018-L MTG12B - Planned | 25.7844 | 263 | 6781.2972 | 0.0068427 | 2.6018e-05
2013-01-18 | 288575 | MTG4B | Urban | LV Transformer SP2018-L MTG12B - Planned | 1.71 | 263 | 449.73 | 0.0004538 | 1.7255e-06
2013-01-18 | 288576 | BLB4A | Urban | LV Transformer SP1933-H BLB4A - Planned | 14.16 | 219 | 3101.04 | 0.0031291 | 1.4288e-05
2013-01-18 | 288577 | VPT16A | Urban | LV Transformer SP3612-B VPT16A - Planned | 3.255 | 164 | 533.82 | 0.00053866 | 3.2845e-06
2013-01-18 | 288578 | SBY8 | Urban | LV Transformer SP495153 SBY8 - Planned | 20.925 | 295 | 6172.875 | 0.0062288 | 2.1115e-05
2013-01-18 | 288579 | IPS1B | Urban | LV Transformer SP1615-F IPS1B - Planned | 3.2349 | 260 | 841.074 | 0.00084869 | 3.2642e-06
2013-01-18 | 288580 | BNH2B | Rural short | LV Transformer SP1833586 BNH2B - Planned | 8 | 107 | 856 | 0.0024717 | 2.31e-05
2013-01-18 | 288583 | CNA7A | Rural short | LV Transformer SP39663-B CNA7A - Planned | 10 | 564 | 5640 | 0.016286 | 2.8876e-05
2013-01-18 | 288597 | EMP2A | Urban | LV Transformer SC2781-J EMP2A - Planned | 4 | 21 | 168 | 0.00016952 | 4.0362e-06
2013-01-19 | 288604 | MTG8A | Urban | LV Transformer SP794561 MTG8A - Planned | 4.98 | 343 | 1708.14 | 0.0017239 | 5.0259e-06
2013-01-19 | 288615 | WRD19A | Urban | LV Transformer SC6120-H WRD19A - Planned | 1 | 476 | 476 | 0.00048039 | 1.0092e-06
2013-01-19 | 288631 | GCLSBY7 | Urban | LV Transformer SP1493-N GCLSBY7 - Planned | 13.86 | 320 | 4435.2 | 0.0044761 | 1.3988e-05
2013-01-20 | 288619 | CBW11 | Rural short | LV Transformer SP4935-D CBW11 - Planned | 2 | 176 | 352 | 0.0010159 | 5.7723e-06
2013-01-20 | 288620 | ARG4 | Urban | Feeder ARG4 - Planned | 1 | 206 | 206 | 0.0002079 | 1.0092e-06
2013-01-20 | 288621 | NDH7 | Urban | Feeder NDH7 - Planned | 12 | 494 | 5928 | 0.0059827 | 1.2111e-05
2013-01-20 | 288624 | CRB22A | Urban | LV Transformer SP1386227 CRB22A - Planned | 33 | 137 | 4521 | 0.0045627 | 3.3304e-05
2013-01-20 | 288625 | NDH12 | Urban | LV Transformer SC744776 NDH12 - Planned | 5.395 | 140 | 755.3 | 0.00076227 | 5.4448e-06
2013-01-20 | 288626 | MDH3A | Urban | LV Transformer SP484301 MDH8B - Planned | 1.02 | 374 | 381.48 | 0.000385 | 1.0294e-06
2013-01-20 | 288626 | MDH8B | Urban | LV Transformer SP484301 MDH8B - Planned | 1 | 374 | 374 | 0.00037745 | 1.0092e-06
2013-01-20 | 288627 | WNM2A | Urban | LV Transformer SP5927-F WNM2A - Planned | 20.895 | 290 | 6059.55 | 0.0061155 | 2.1088e-05
2013-01-20 | 288628 | NDH7 | Urban | LV Transformer SP799732 NDH7 - Planned | 33.345 | 300 | 10003.5 | 0.010096 | 3.3653e-05
2013-01-20 | 288629 | NGE2B | Urban | LV Transformer SC484720 NGE2B - Planned | 5.03 | 85 | 427.55 | 0.00043149 | 5.0764e-06
2013-01-20 | 288630 | ARG4 | Urban | LV Transformer SC6273-I ARG4 - Planned | 8 | 210 | 1680 | 0.0016955 | 8.0738e-06
2013-01-20 | 288632 | WED4B | Urban | LV Transformer SC164-N WED4B - Planned | 25.8993 | 104 | 2693.5272 | 0.0027184 | 2.6138e-05
2013-01-21 | 288639 | MCW11 | Rural short | LV Transformer SP5171-E MCW11 - Planned | 10 | 76 | 760 | 0.0021925 | 2.8848e-05
2013-01-21 | 288643 | MLY1 | Rural short | LV Transformer SP9558-A MLY1 - Planned | 3 | 264 | 792 | 0.0022848 | 8.6544e-06
2013-01-21 | 288644 | WFD2B | Rural short | LV Transformer SP9615-C WFD2B - Planned | 9 | 280 | 2520 | 0.0072697 | 2.5963e-05
2013-01-21 | 288647 | LBH5A | Rural short | LV Transformer SP2737-B LBH5A - Planned | 9.02 | 409 | 3689.18 | 0.010643 | 2.6021e-05
2013-01-21 | 288648 | BDT5 | Rural short | Feeder BDT5 - Planned | 4.1339 | 427 | 1765.1753 | 0.0050922 | 1.1926e-05
2013-01-21 | 288655 | MTB13A | Rural short | Feeder MTB13A - Planned | 40.95 | 500 | 20475 | 0.059067 | 0.00011813
2013-01-21 | 288656 | ZMR10 | Urban | LV Transformer SP143-M ZMR10 - Planned | 20.72 | 82 | 1699.04 | 0.0017149 | 2.0914e-05
2013-01-21 | 288658 | ENG7 | Urban | LV Transformer SP596-O ENG7 - Planned | 14.2 | 332 | 4714.4 | 0.0047585 | 1.4333e-05
2013-01-21 | 288659 | HIS12A | Urban | LV Transformer SP2804-G HIS12A - Planned | 19.11 | 415 | 7930.65 | 0.0080048 | 1.9289e-05
2013-01-21 | 288660 | MAI11 | Urban | LV Transformer SP14624-C MAI11 - Planned | 85.905 | 450 | 38657.25 | 0.039019 | 8.6709e-05
2013-01-21 | 288661 | RBA35A | Urban | LV Transformer SC589048 RBA35A - Planned | 4 | 17 | 68 | 6.8636e-05 | 4.0374e-06
2013-01-21 | 288662 | BRD13A | Urban | LV Transformer SC2726-G BRD13A - Planned | 6.3 | 328 | 2066.4 | 0.0020857 | 6.3589e-06
2013-01-21 | 288663 | MRE1 | Urban | LV Transformer SC4832-J MRE1 - Planned | 2.9742 | 43 | 127.8906 | 0.00012909 | 3.002e-06
2013-01-21 | 288664 | MRE2 | Urban | LV Transformer SC732203 MRE2 - Planned | 1.0731 | 31 | 33.2661 | 3.3577e-05 | 1.0831e-06
2013-01-21 | 288665 | HTN3B | Urban | LV Transformer SP3955-H HTN3B - Planned | 6.75 | 279 | 1883.25 | 0.0019009 | 6.8131e-06
2013-01-21 | 288666 | NDH1 | Urban | LV Transformer SP8549-D NDH1 - Planned | 28.0686 | 182 | 5108.4852 | 0.0051563 | 2.8331e-05
2013-01-21 | 288667 | ARG5A | Urban | LV Transformer SP912-K ARG5A - Planned | 4.6 | 210 | 966 | 0.00097504 | 4.643e-06
2013-01-21 | 288668 | MCW11 | Rural short | LV Transformer SP3647-D MCW11 - Planned | 6.24 | 177 | 1104.48 | 0.0031862 | 1.8001e-05
2013-01-21 | 288669 | RPN8 | Rural short | LV Transformer SP3666-D RPN8 - Planned | 15.225 | 279 | 4247.775 | 0.012254 | 4.3921e-05
2013-01-22 | 288703 | BMT1 | Rural short | Feeder BMT1 - Planned | 18.91 | 228 | 4311.48 | 0.012435 | 5.4539e-05
2013-01-22 | 288704 | CRY3A | Rural short | Feeder CRY3A - Planned | 35.9 | 391 | 14036.9 | 0.040484 | 0.00010354
2013-01-22 | 288705 | GYM7A | Rural short | Feeder GYM7A - Planned | 3 | 363 | 1089 | 0.0031408 | 8.6523e-06
2013-01-22 | 288706 | BMT1 | Rural short | LV Transformer SP444-C BMT1 - Planned | 6 | 297 | 1782 | 0.0051395 | 1.7305e-05
2013-01-22 | 288707 | PWC6 | Rural short | LV Transformer SP3996-B PWC6 - Planned | 27.36 | 270 | 7387.2 | 0.021305 | 7.8909e-05
2013-01-22 | 288708 | JBB3A | Rural short | Feeder JBB3A - Planned | 25 | 409 | 10225 | 0.02949 | 7.2103e-05
2013-01-22 | 288710 | CPD1 | Rural short | Feeder CPD1 - Planned | 4.01 | 409 | 1640.09 | 0.0047302 | 1.1565e-05
2013-01-22 | 288711 | CNB24A | Rural short | Feeder CNB24A - Planned | 54.31 | 420 | 22810.2 | 0.065787 | 0.00015664
2013-01-22 | 288712 | CBT8A | Rural short | Feeder CBT8A - Planned | 2 | 266 | 532 | 0.0015343 | 5.7682e-06
2013-01-22 | 288713 | SMF6A | Rural short | Feeder SMF6A - Planned | 31.34 | 430 | 13476.2 | 0.038867 | 9.0388e-05
2013-01-22 | 288714 | MLY3 | Rural short | Feeder MLY3 - Planned | 58.495 | 415 | 24275.425 | 0.070013 | 0.00016871
2013-01-22 | 288715 | RBA43A | Rural short | Feeder RBA43A - Planned | 82 | 432 | 35424 | 0.10217 | 0.0002365
2013-01-22 | 288716 | WFD1B | Rural short | LV Transformer SP4917-F WFD1B - Planned | 6 | 418 | 2508 | 0.0072333 | 1.7305e-05
2013-01-22 | 288717 | MBG1 | Rural short | Feeder RWD2, MBG1, MBG2 - Planned | 5.02 | 578 | 2901.56 | 0.0083684 | 1.4478e-05
2013-01-22 | 288717 | MBG2 | Rural short | Feeder RWD2, MBG1, MBG2 - Planned | 2.01 | 578 | 1161.78 | 0.0033507 | 5.7971e-06
2013-01-22 | 288717 | RWD2 | Rural short | Feeder RWD2, MBG1, MBG2 - Planned | 7 | 578 | 4046 | 0.011669 | 2.0189e-05
2013-01-22 | 288718 | CRB25A | Rural short | Feeder CRB25A - Planned | 26 | 453 | 11778 | 0.033969 | 7.4987e-05
2013-01-22 | 288719 | BHL2A | Urban | LV Transformer SP16003-B BHL2A - Planned | 9.5 | 121 | 1149.5 | 0.0011603 | 9.5895e-06
2013-01-22 | 288720 | RCN10A | Urban | LV Transformer SC5881-I RCN10A - Planned | 20.14 | 307 | 6182.98 | 0.0062413 | 2.033e-05
2013-01-22 | 288721 | AGE10 | Urban | LV Transformer SP2326-I AGE10 - Planned | 24.7081 | 316 | 7807.7596 | 0.0078813 | 2.4941e-05
2013-01-22 | 288722 | SFD4 | Urban | LV Transformer SC3533-J SFD4 - Planned | 10.967 | 253 | 2774.651 | 0.0028008 | 1.107e-05
2013-01-22 | 288723 | MLY1 | Rural short | LV Transformer SP205084 MLY1 - Planned | 6 | 70 | 420 | 0.0012113 | 1.7305e-05
2013-01-22 | 288724 | MLY4 | Rural short | LV Transformer SP204684 MLY4 - Planned | 15.04 | 65 | 977.6 | 0.0028195 | 4.3377e-05
2013-01-22 | 288725 | BHD2A | Urban | LV Transformer SP6394-D BHD3A - Planned | 0.9 | 382 | 343.8 | 0.00034704 | 9.0848e-07
2013-01-22 | 288725 | BHD3A | Urban | LV Transformer SP6394-D BHD3A - Planned | 29.925 | 382 | 11431.35 | 0.011539 | 3.0207e-05
2013-01-22 | 288726 | LDR3 | Urban | LV Transformer SP958-G LDR3 - Planned | 25.5 | 324 | 8262 | 0.0083399 | 2.574e-05
2013-01-22 | 288727 | MDR24A | Urban | LV Transformer SP3348-F MDR24A - Planned | 27.465 | 200 | 5493 | 0.0055448 | 2.7724e-05
2013-01-22 | 288728 | CRB25A | Rural short | LV Transformer SP3822-F CRB25A - Planned | 0.975 | 120 | 117 | 0.00033744 | 2.812e-06
2013-01-22 | 288729 | AHL8A | Urban | LV Transformer SC789953 AHL8A - Planned | 7.98 | 212 | 1691.76 | 0.0017077 | 8.0552e-06
2013-01-22 | 288730 | DRD3A | Urban | LV Transformer SP1928-G DRD3A - Planned | 32.64 | 375 | 12240 | 0.012355 | 3.2948e-05
2013-01-22 | 288731 | NGE4B | Urban | LV Transformer SP3130-E NGE4B - Planned | 10.92 | 215 | 2347.8 | 0.0023699 | 1.1023e-05
2013-01-22 | 288732 | GCLSBY7 | Urban | LV Transformer SP1493-N GCLSBY7 - Planned | 1.155 | 235 | 271.425 | 0.00027398 | 1.1659e-06
2013-01-22 | 288733 | RLB15A | Urban | LV Transformer SP3664-B RLB15A - Planned | 36.07 | 200 | 7214 | 0.007282 | 3.641e-05
2013-01-22 | 288734 | UMG2B | Rural short | LV Transformer SP2448-J UMG2B - Planned | 3.8332 | 233 | 893.1356 | 0.0025759 | 1.1055e-05
2013-01-22 | 288735 | NSW28 | Urban | LV Transformer SP3638-J NSW28 - Planned | 6.24 | 330 | 2059.2 | 0.0020786 | 6.2988e-06
2013-01-22 | 288735 | NSW5A | Urban | LV Transformer SP3638-J NSW28 - Planned | 16.992 | 330 | 5607.36 | 0.0056602 | 1.7152e-05
2013-01-22 | 288736 | RLB11B | Urban | LV Transformer SP4113-D RLB11B - Planned | 4.06 | 70 | 284.2 | 0.00028688 | 4.0983e-06
2013-01-22 | 288737 | HPK5A | Urban | LV Transformer SP3436-D HPK5A - Planned | 14.6538 | 198 | 2901.4524 | 0.0029288 | 1.4792e-05
2013-01-22 | 288738 | NMC2A | Rural short | LV Transformer SC512763 NMC2A - Planned | 11.62 | 31 | 360.22 | 0.0010389 | 3.3513e-05
2013-01-22 | 288739 | CPD1 | Rural short | LV Transformer SP1834773 CPD1 - Planned | 2 | 188 | 376 | 0.0010844 | 5.7682e-06
2013-01-23 | 288780 | CBT8A | Rural short | Feeder CBT8A - Planned | 4 | 325 | 1300 | 0.0037492 | 1.1536e-05
2013-01-23 | 288781 | ABY2A | Rural short | Feeder ABY2A - Planned | 2 | 210 | 420 | 0.0012113 | 5.7679e-06
2013-01-23 | 288782 | RLB16A | Rural short | Feeder RLB16A - Planned | 17.5 | 304 | 5320 | 0.015343 | 5.047e-05
2013-01-23 | 288783 | WHO1 | Rural short | Feeder WHO1 - Planned | 1.5 | 385 | 577.5 | 0.0016655 | 4.326e-06
2013-01-23 | 288784 | TGW1 | Rural short | Feeder TGW1 - Planned | 8.25 | 387 | 3192.75 | 0.0092078 | 2.3793e-05
2013-01-23 | 288786 | MLY3 | Rural short | LV Transformer SP6664-B MLY3 - Planned | 24.96 | 292 | 7288.32 | 0.021019 | 7.1984e-05
2013-01-23 | 288787 | CLD11 | Rural short | LV Transformer SP16447-A CLD11 - Planned | 40 | 204 | 8160 | 0.023533 | 0.00011536
2013-01-23 | 288788 | AMR1 | Rural short | Feeder AMR1 - Planned | 17.44 | 150 | 2616 | 0.0075445 | 5.0296e-05
2013-01-23 | 288789 | MLY3 | Rural short | LV Transformer SP6647-B MLY3 - Planned | 55 | 328 | 18040 | 0.052027 | 0.00015862
2013-01-23 | 288790 | CRB25A | Rural short | Feeder CRB25A - Planned | 50.33 | 456 | 22950.48 | 0.066189 | 0.00014515
2013-01-23 | 288829 | SHW10A | Urban | LV Transformer SP2432-J SHW10A - Planned | 22.815 | 366 | 8350.29 | 0.0084292 | 2.303e-05
2013-01-23 | 288853 | KMR19A | Urban | LV Transformer SP2244-L KMR19A - Planned | 5.1 | 252 | 1285.2 | 0.0012973 | 5.1482e-06
2013-01-23 | 288854 | OXL11A | Urban | LV Transformer SP12494-F OXL11A - Planned | 10.1166 | 421 | 4259.0886 | 0.0042993 | 1.0212e-05
2013-01-23 | 288855 | SFD3 | Urban | LV Transformer SC4054-K SFD3 - Planned | 21.7 | 259 | 5620.3 | 0.0056734 | 2.1905e-05
2013-01-23 | 288856 | AMR1 | Rural short | LV Transformer SP546-B AMR1 - Planned | 3 | 416 | 1248 | 0.0035992 | 8.6519e-06
2013-01-23 | 288857 | WMD8B | Rural short | LV Transformer SP10315-A WMD8B - Planned | 6.18 | 389 | 2404.02 | 0.0069331 | 1.7823e-05
2013-01-23 | 288858 | BHD46A | Urban | LV Transformer SC568855 BHD46A - Planned | 26.4 | 31 | 818.4 | 0.00082613 | 2.6649e-05
2013-01-23 | 288859 | LDR1 | Urban | LV Transformer SP2178-H LDR1 - Planned | 10.665 | 335 | 3572.775 | 0.0036065 | 1.0766e-05
2013-01-23 | 288860 | BHD31A | Urban | LV Transformer SC656903 BHD31A - Planned | 0.99 | 22 | 21.78 | 2.1986e-05 | 9.9935e-07
2013-01-23 | 288861 | LDR10A | Urban | LV Transformer SP34040-D LDR10A - Planned | 7.05 | 381 | 2686.05 | 0.0027114 | 7.1166e-06
2013-01-23 | 288861 | SPO11A | Urban | LV Transformer SP34040-D LDR10A - Planned | 29.1 | 381 | 11087.1 | 0.011192 | 2.9375e-05
2013-01-23 | 288863 | WNM2A | Urban | LV Transformer SP2088-J WNM2A - Planned | 10.725 | 265 | 2842.125 | 0.002869 | 1.0826e-05
2013-01-23 | 288864 | LTA3 | Urban | LV Transformer SC5821-H LTA3 - Planned | 2.295 | 300 | 688.5 | 0.000695 | 2.3167e-06
2013-01-23 | 288865 | MRE1 | Urban | LV Transformer SP723-M MRE2 - Planned | 12.6514 | 271 | 3428.5294 | 0.0034609 | 1.2771e-05
2013-01-23 | 288865 | MRE2 | Urban | LV Transformer SP723-M MRE2 - Planned | 13.3688 | 271 | 3622.9448 | 0.0036572 | 1.3495e-05
2013-01-23 | 288867 | DRD13A | Urban | LV Transformer SP2609-F DRD13A - Planned | 2.865 | 304 | 870.96 | 0.00087919 | 2.8921e-06
2013-01-23 | 288868 | HTN24B | Urban | LV Transformer SP4122-H HTN24B - Planned | 11.4 | 195 | 2223 | 0.002244 | 1.1508e-05
2013-01-23 | 288869 | WED6A | Urban | LV Transformer SP5406-G WED6A - Planned | 29.415 | 202 | 5941.83 | 0.0059979 | 2.9693e-05
2013-01-23 | 288872 | TSN15A | Urban | LV Transformer SC1419247 TSN15A - Planned | 0.4 | 100 | 40 | 4.0378e-05 | 4.0378e-07
2013-01-23 | 288873 | WED6A | Urban | LV Transformer SP136-N WED6A - Planned | 3.5234 | 326 | 1148.6284 | 0.0011595 | 3.5567e-06
2013-01-23 | 288874 | ARG9A | Urban | LV Transformer SP1553-M ARG9A - Planned | 14.2 | 325 | 4615 | 0.0046586 | 1.4334e-05
2013-01-23 | 288875 | HPK5A | Urban | LV Transformer SP115-Q HPK5A - Planned | 13.915 | 311 | 4327.565 | 0.0043684 | 1.4046e-05
2013-01-23 | 288876 | HDA3A | Urban | LV Transformer SP6607-I HDA3A - Planned | 1.29 | 45 | 58.05 | 5.8598e-05 | 1.3022e-06
2013-01-23 | 288878 | KCY1 | Urban | LV Transformer SP2788-G KCY1 - Planned | 27.16 | 292 | 7930.72 | 0.0080056 | 2.7417e-05
2013-01-23 | 288879 | ABY2A | Rural short | LV Transformer SP11033-D ABY2A - Planned | 6 | 2 | 12 | 3.4608e-05 | 1.7304e-05
2013-01-24 | 288803 | LLY1 | Rural short | LV Transformer SP970-A LLY1 - Planned | 0.99 | 78 | 77.22 | 0.0002226 | 2.8539e-06
2013-01-24 | 288805 | LLY1 | Rural short | LV Transformer SP2824-B LLY1 - Planned | 1 | 105 | 105 | 0.00030268 | 2.8827e-06
2013-01-24 | 288807 | THL1 | Rural short | LV Transformer SP1377564 THL1 - Planned | 24 | 350 | 8400 | 0.024215 | 6.9185e-05
2013-01-24 | 288820 | MLY1 | Rural short | Feeder MLY1 - Planned | 39.5 | 375 | 14812.5 | 0.0427 | 0.00011387
2013-01-24 | 288821 | MLY1 | Rural short | Feeder MLY1 - Planned | 20.01 | 403 | 8064.03 | 0.023246 | 5.7683e-05
2013-01-24 | 288822 | AMR2 | Rural short | Feeder AMR2 - Planned | 23.35 | 250 | 5837.5 | 0.016828 | 6.7311e-05
2013-01-24 | 288823 | MBG1 | Rural short | Feeder MBG1 - Planned | 23.02 | 468 | 10773.36 | 0.031056 | 6.6359e-05
2013-01-24 | 288824 | VPT13A | Rural short | LV Transformer SP232621 VPT13A - Planned | 3.105 | 210 | 652.05 | 0.0018797 | 8.9507e-06
2013-01-24 | 288825 | BHL3A | Urban | LV Transformer SC1442949 BHL3A - Planned | 13.68 | 267 | 3652.56 | 0.0036875 | 1.3811e-05
2013-01-24 | 288826 | SHW12 | Urban | LV Transformer SP367-R SHW12 - Planned | 5.12 | 158 | 808.96 | 0.0008167 | 5.169e-06
2013-01-24 | 288827 | GAP8A | Urban | LV Transformer SP2779-K GAP8A - Planned | 1.92 | 80 | 153.6 | 0.00015507 | 1.9384e-06
2013-01-24 | 288828 | TRG2A | Urban | LV Transformer SP7616-F TRG2A - Planned | 35.6867 | 410 | 14631.547 | 0.014772 | 3.6028e-05
2013-01-24 | 288830 | BWH16A | Rural short | LV Transformer SP1759-C BWH16A - Planned | 5.0623 | 383 | 1938.8609 | 0.0055891 | 1.4593e-05
2013-01-24 | 288831 | YDA5A | Rural short | LV Transformer SP2847-A YDA5A - Planned | 13.92 | 337 | 4691.04 | 0.013523 | 4.0127e-05
2013-01-24 | 288832 | BMT4 | Rural short | LV Transformer SC1440435 - Planned | 4.895 | 44 | 215.38 | 0.00062087 | 1.4111e-05
2013-01-24 | 288833 | SPO3A | Urban | LV Transformer SP6440-G SPO3A - Planned | 12.54 | 427 | 5354.58 | 0.0054058 | 1.266e-05
2013-01-24 | 288834 | LDR1 | Urban | LV Transformer SP2861-F LDR1 - Planned | 20.28 | 233 | 4725.24 | 0.0047705 | 2.0474e-05
2013-01-24 | 288835 | CRBTHP14 | Urban | LV Transformer SP2484-G CRBTHP14 - Planned | 85.03 | 430 | 36562.9 | 0.036913 | 8.5844e-05
2013-01-24 | 288836 | NRG9 | Rural short | LV Transformer SC1401284 - Planned | 96 | 330 | 31680 | 0.091324 | 0.00027674
2013-01-24 | 288837 | HIS12A | Urban | LV Transformer SP5152-H HIS12A - Planned | 14.905 | 270 | 4024.35 | 0.0040629 | 1.5048e-05
2013-01-24 | 288838 | WNM2A | Urban | LV Transformer SP807686 WNM2A - Planned | 3.87 | 282 | 1091.34 | 0.0011018 | 3.907e-06
2013-01-24 | 288839 | DRD13A | Urban | LV Transformer SP3086-F DRD13A - Planned | 6.0431 | 323 | 1951.9213 | 0.0019706 | 6.101e-06
2013-01-24 | 288839 | DRD5A | Urban | LV Transformer SP3086-F DRD13A - Planned | 0.915 | 323 | 295.545 | 0.00029837 | 9.2376e-07
2013-01-24 | 288840 | DRD13A | Urban | LV Transformer SP4120-H DRD13A - Planned | 5.04 | 265 | 1335.6 | 0.0013484 | 5.0882e-06
2013-01-24 | 288841 | KRN2 | Urban | LV Transformer SP2567-K KRN2 - Planned | 8.46 | 333 | 2817.18 | 0.0028441 | 8.541e-06
2013-01-24 | 288842 | HDA3A | Urban | LV Transformer SP20425-D HDA3A - Planned | 7.05 | 335 | 2361.75 | 0.0023844 | 7.1175e-06
2013-01-24 | 288843 | CSE9 | Urban | LV Transformer SP2161-I CSE9 - Planned | 17.02 | 179 | 3046.58 | 0.0030757 | 1.7183e-05
2013-01-24 | 288844 | BLB4A | Urban | LV Transformer SP5396-F BLB4A - Planned | 13.965 | 234 | 3267.81 | 0.0032991 | 1.4099e-05
2013-01-24 | 288845 | SBY4 | Urban | LV Transformer SP495153 SBY8 - Planned | 4.65 | 266 | 1236.9 | 0.0012487 | 4.6945e-06
2013-01-24 | 288845 | SBY8 | Urban | LV Transformer SP495153 SBY8 - Planned | 11.8848 | 266 | 3161.3568 | 0.0031916 | 1.1999e-05
2013-01-24 | 288846 | WED6A | Urban | LV Transformer SP136-N WED6A - Planned | 8.5185 | 270 | 2299.995 | 0.002322 | 8.6e-06
2013-01-24 | 288847 | CVL17A | Urban | LV Transformer SP10824-B CVL17A - Planned | 34.65 | 230 | 7969.5 | 0.0080458 | 3.4982e-05
2013-01-24 | 288848 | SPD11A | Urban | LV Transformer SP3797-E SPD11A - Planned | 1.9433 | 12 | 23.3196 | 2.3543e-05 | 1.9619e-06
2013-01-24 | 288849 | LLY3 | Rural short | LV Transformer SP2339-D LLY3 - Planned | 2 | 175 | 350 | 0.0010089 | 5.7654e-06
2013-01-24 | 288850 | VPT12A | Urban | LV Transformer SP11050-C VPT12A - Planned | 2.9035 | 55 | 159.6925 | 0.00016122 | 2.9313e-06
2013-01-24 | 288851 | LLY3 | Rural short | LV Transformer SP11758-A LLY3 - Planned | 2.01 | 50 | 100.5 | 0.00028971 | 5.7942e-06
2013-01-24 | 288921 | HWD2B | Rural short | LV Transformer SC1379758 HWD2B - Planned | 2 | 223 | 446 | 0.0012857 | 5.7654e-06
2013-01-25 | 288904 | CVL7A | Rural short | Feeder CVL7A - Planned | 23.02 | 275 | 6330.5 | 0.018245 | 6.6344e-05
2013-01-25 | 288905 | CMY4 | Rural short | LV Transformer SP1495218 CMY4 - Planned | 1 | 167 | 167 | 0.00048129 | 2.882e-06
2013-01-25 | 288908 | MDH3A | Urban | LV Transformer SG5023-J MDH3A - Planned | 1 | 327 | 327 | 0.00033016 | 1.0097e-06
2013-01-25 | 288910 | UPC2 | Rural short | Feeder UPC2 - Planned | 19.4 | 208 | 4035.2 | 0.011629 | 5.5911e-05
2013-01-25 | 288917 | PWC2 | Rural short | Feeder PWC2 - Planned | 36.51 | 172 | 6279.72 | 0.018098 | 0.00010522
2013-01-25 | 288922 | SHW10A | Urban | LV Transformer SP755153 SHW10A - Planned | 10.115 | 240 | 2427.6 | 0.002451 | 1.0213e-05
2013-01-25 | 288922 | SHW6 | Urban | LV Transformer SP755153 SHW10A - Planned | 1.79 | 240 | 429.6 | 0.00043375 | 1.8073e-06
2013-01-25 | 288923 | NSD2B | Urban | LV Transformer SC1734706 NSD2B - Planned | 1.28 | 325 | 416 | 0.00042002 | 1.2924e-06
2013-01-25 | 288924 | SFD9 | Urban | LV Transformer SP1888-K SFD9 - Planned | 23.805 | 122 | 2904.21 | 0.0029322 | 2.4035e-05
2013-01-25 | 288925 | AHL15B | Urban | LV Transformer SP2406-J AHL15B - Planned | 14.44 | 225 | 3249 | 0.0032804 | 1.4579e-05
2013-01-25 | 288926 | AGE8 | Urban | LV Transformer SP34098-E AGE8 - Planned | 11.88 | 259 | 3076.92 | 0.0031066 | 1.1995e-05
2013-01-25 | 288927 | PGN1B | Rural short | LV Transformer SP6733-A PGN1B - Planned | 10.4 | 155 | 1612 | 0.0046458 | 2.9973e-05
2013-01-25 | 288929 | BBH12B | Urban | LV Transformer SP4628-G BBH12B - Planned | 31.987 | 410 | 13114.67 | 0.013241 | 3.2296e-05
2013-01-25 | 288930 | BHD31A | Urban | LV Transformer SC560539-B BHD31A - Planned | 13 | 40 | 520 | 0.00052502 | 1.3125e-05
2013-01-25 | 288931 | LDR8 | Urban | LV Transformer SP1122-K LDR8 - Planned | 4.98 | 204 | 1015.92 | 0.0010257 | 5.0281e-06
2013-01-25 | 288933 | DRD13A | Urban | LV Transformer SP10719-C DRD13A - Planned | 3.6625 | 252 | 922.95 | 0.00093186 | 3.6979e-06
2013-01-25 | 288934 | WNM2A | Urban | LV Transformer SP807686 WNM2A - Planned | 9.89 | 222 | 2195.58 | 0.0022168 | 9.9855e-06
2013-01-25 | 288935 | DRD13A | Urban | LV Transformer SP3553-F DRD13A - Planned | 20.125 | 310 | 6238.75 | 0.006299 | 2.0319e-05
2013-01-25 | 288936 | CMD13A | Urban | LV Transformer SP3807-A CMD13A - Planned | 8.52 | 200 | 1704 | 0.0017204 | 8.6022e-06
2013-01-25 | 288937 | MRE1 | Urban | LV Transformer SC4832-J MRE1 - Planned | 35.6904 | 296 | 10564.3584 | 0.010666 | 3.6035e-05
2013-01-25 | 288938 | UMG2B | Rural short | LV Transformer SC1835195 UMG2B - Planned | 1 | 155 | 155 | 0.00044671 | 2.882e-06
2013-01-25 | 288939 | HPE5A | Urban | LV Transformer SP3420-I HPE5A - Planned | 5.8681 | 238 | 1396.6078 | 0.0014101 | 5.9247e-06
2013-01-25 | 288940 | QEN10 | Urban | LV Transformer SC494965 QEN10 - Planned | 0.96 | 130 | 124.8 | 0.000126 | 9.6927e-07
2013-01-25 | 288941 | MTG7A | Urban | LV Transformer SP2637-J MTG7A - Planned | 15.255 | 180 | 2745.9 | 0.0027724 | 1.5402e-05
2013-01-25 | 289002 | PQSRGA85 | CBD | LV Transformer SG5031-J PQSRGA85 - Planned | 0.98 | 1081 | 1059.38 | 0.27587 | 0.0002552
2013-01-25 | 289003 | AGE9 | Urban | LV Transformer SP1117-Q AGE9 - Planned | 16.17 | 310 | 5012.7 | 0.0050611 | 1.6326e-05
2013-01-25 | 293470 | ESK5A | Rural short | LV Transformer SP9388-A ESK5A - Planned | 10 | 325 | 3250 | 0.0093665 | 2.882e-05
2013-01-29 | 291002 | LDR3 | Urban | Feeder LDR3 - Planned | 274.8992 | 404 | 111059.2768 | 0.11216 | 0.00027763
2013-01-29 | 291005 | BDB32A | Rural short | Feeder BDB32A - Planned | 44.74 | 202 | 9037.48 | 0.026019 | 0.00012881
2013-02-03 | 291228 | LLY4 | Rural short | LV Transformer SC21504-B LLY4 - Planned | 26.33 | 362 | 9531.46 | 0.027407 | 7.571e-05
2013-02-04 | 291542 | CBT8A | Rural short | LV Transformer SP11442-E CBT8A - Planned | 2 | 325 | 650 | 0.0018682 | 5.7483e-06
2013-02-04 | 291595 | RWD2 | Rural short | Feeder RWD2 - Planned | 3 | 360 | 1080 | 0.0031041 | 8.6224e-06
2013-02-04 | 291635 | NVL8B | Urban | LV Transformer SP892-B NVL8B - Planned | 1.465 | 124 | 181.66 | 0.00018353 | 1.48e-06
2013-02-04 | 291636 | MGP4 | Rural short | LV Transformer SP10234-D MGP4 - Planned | 0.95 | 342 | 324.9 | 0.00093381 | 2.7304e-06
2013-02-04 | 291637 | BHL4A | Urban | LV Transformer SP2966-H BHL4A - Planned | 9.8 | 191 | 1871.8 | 0.001891 | 9.9006e-06
2013-02-04 | 291638 | WNM3 | Urban | LV Transformer SP2168-K WNM3 - Planned | 16.31 | 225 | 3669.75 | 0.0037074 | 1.6477e-05
2013-02-05 | 291811 | GBN2 | Rural short | LV Transformer SP867-B GBN2 - Planned | 2.01 | 20 | 40.2 | 0.0001155 | 5.7752e-06
2013-02-05 | 291890 | CRM16A | Rural short | LV Transformer SP8957-A CRM16A - Planned | 3.8664 | 198 | 765.5472 | 0.0021996 | 1.1109e-05
2013-02-05 | 291891 | GYM2A | Rural short | LV Transformer SP441-C - Planned | 1 | 52 | 52 | 0.00014941 | 2.8732e-06
2013-02-05 | 291892 | GYM2A | Rural short | LV Transformer SP5459-C GYM2A - Planned | 6 | 50 | 300 | 0.00086197 | 1.7239e-05
2013-02-05 | 291893 | GLY6 | Urban | LV Transformer SC4743-J GLY6 - Planned | 10.26 | 285 | 2924.1 | 0.0029542 | 1.0366e-05
2013-02-05 | 291894 | WNM1A | Urban | LV Transformer SP6437-G WNM2A - Planned | 11.01 | 217 | 2389.17 | 0.0024138 | 1.1124e-05
2013-02-05 | 291894 | WNM2A | Urban | LV Transformer SP6437-G WNM2A - Planned | 19.86 | 217 | 4309.62 | 0.004354 | 2.0065e-05
2013-02-05 | 291895 | CFD1A | Urban | LV Transformer SC23107-F CFD1A - Planned | 24.83 | 315 | 7821.45 | 0.0079021 | 2.5086e-05
2013-02-05 | 291896 | KRN2 | Urban | LV Transformer SP32988-C KRN2 - Planned | 8.69 | 89 | 773.41 | 0.00078138 | 8.7796e-06
2013-02-05 | 291897 | DRD13A | Urban | LV Transformer SP3177-D DRD13A - Planned | 17.82 | 264 | 4704.48 | 0.004753 | 1.8004e-05
2013-02-06 | 291950 | BTN2 | Rural short | Feeder BTN2 - Planned | 17 | 18 | 306 | 0.00087894 | 4.883e-05
2013-02-06 | 291970 | WFD2B | Rural short | LV Transformer SP5074-G WFD2B - Planned | 18 | 287 | 5166 | 0.014839 | 5.1702e-05
2013-02-06 | 291971 | CBW11 | Rural short | LV Transformer SP1963-G CBW11 - Planned | 10 | 213 | 2130 | 0.0061181 | 2.8724e-05
2013-02-06 | 291991 | BHD35A | Rural short | LV Transformer SP5748-D BHD35A - Planned | 0.5 | 478 | 239 | 0.00068649 | 1.4362e-06
2013-02-06 | 291992 | WCL17A | Urban | LV Transformer SC734313 WCL17A - Planned | 1 | 166 | 166 | 0.00016772 | 1.0104e-06
2013-02-06 | 291998 | YDA5A | Rural short | LV Transformer SP3336-A YDA5A - Planned | 10.5 | 331 | 3475.5 | 0.0099829 | 3.016e-05
2013-02-06 | 291999 | YDA5A | Rural short | Feeder YDA5A - Planned | 66.844 | 175 | 11697.7 | 0.0336 | 0.000192
2013-02-06 | 292001 | AGE3 | Urban | LV Transformer SP2531-F AGE3 - Planned | 5.54 | 148 | 819.92 | 0.00082841 | 5.5974e-06
2013-02-06 | 292002 | ENG2 | Urban | LV Transformer SP763994 ENG2 - Planned | 10.395 | 336 | 3492.72 | 0.0035289 | 1.0503e-05
2013-02-06 | 292003 | ENG2 | Urban | LV Transformer SP4744-K GLY6 - Planned | 1.93 | 57 | 110.01 | 0.00011115 | 1.95e-06
2013-02-06 | 292003 | GLY6 | Urban | LV Transformer SP4744-K GLY6 - Planned | 8.1 | 57 | 461.7 | 0.00046648 | 8.1839e-06
2013-02-06 | 292004 | AGE7B | Urban | LV Transformer SP6279-E AGE7B - Planned | 3.04 | 202 | 614.08 | 0.00062044 | 3.0715e-06
2013-02-06 | 292005 | RBA34A | Urban | LV Transformer SC466210-B RBA34A - Planned | 1 | 248 | 248 | 0.00025057 | 1.0104e-06
2013-02-06 | 292007 | DRD5A | Urban | LV Transformer SP2764-F DRD5A - Planned | 13.575 | 379 | 5144.925 | 0.0051982 | 1.3716e-05
2013-02-06 | 292008 | CFD2A | Urban | LV Transformer SP12927-D HDA11A - Planned | 1.365 | 348 | 475.02 | 0.00047994 | 1.3791e-06
2013-02-06 | 292008 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 17.12 | 348 | 5957.76 | 0.0060195 | 1.7297e-05
2013-02-06 | 292009 | DRD13A | Urban | LV Transformer SP3177-D DRD13A - Planned | 13.79 | 283 | 3902.57 | 0.003943 | 1.3933e-05
2013-02-06 | 292010 | WRD20A | Urban | LV Transformer SP146-Q WRD20A - Planned | 26.79 | 358 | 9590.82 | 0.0096902 | 2.7067e-05
2013-02-06 | 292011 | LGL15A | Urban | LV Transformer SP6539-F LGL15A - Planned | 9.48 | 344 | 3261.12 | 0.0032949 | 9.5782e-06
2013-02-06 | 292012 | MRK6 | Urban | LV Transformer SP317-S MRK6 - Planned | 2.08 | 371 | 771.68 | 0.00077967 | 2.1015e-06
2013-02-06 | 292013 | CHL3 | Urban | LV Transformer SP45538-E CHL3 - Planned | 7.8 | 371 | 2893.8 | 0.0029238 | 7.8808e-06
2013-02-07 | 292050 | NMC1B | Rural short | LV Transformer SP12388-D NMC1B - Planned | 23 | 186 | 4278 | 0.012284 | 6.6045e-05
2013-02-07 | 292091 | KLG7A | Rural short | Feeder KLG7A - Planned | 8 | 334 | 2672 | 0.0076727 | 2.2972e-05
2013-02-07 | 292092 | TBV2 | Rural short | LV Transformer SP404381 TBV2 - Planned | 1 | 380 | 380 | 0.0010912 | 2.8715e-06
2013-02-07 | 292110 | RLB16A | Rural short | Feeder RLB16A - Planned | 17.5 | 400 | 7000 | 0.020101 | 5.0251e-05
2013-02-07 | 292111 | CCY7A | Rural short | LV Transformer SP1500379 CCY7A - Planned | 1 | 438 | 438 | 0.0012577 | 2.8715e-06
2013-02-07 | 292112 | KRN12 | Urban | LV Transformer SP2628-L KRN12 - Planned | 29 | 396 | 11484 | 0.011604 | 2.9302e-05
2013-02-07 | 292113 | SHW10A | Urban | LV Transformer SP2824-I SHW10A - Planned | 12.495 | 271 | 3386.145 | 0.0034214 | 1.2625e-05
2013-02-07 | 292114 | LBH3A | Rural short | LV Transformer SP5182-A LBH3A - Planned | 60.047 | 195 | 11709.165 | 0.033623 | 0.00017243
2013-02-07 | 292115 | MGP1 | Rural short | LV Transformer SP81083-B MGP1 - Planned | 17.285 | 61 | 1054.385 | 0.0030277 | 4.9634e-05
2013-02-07 | 292116 | DRD13A | Urban | LV Transformer SP13757-C DRD13A - Planned | 36.96 | 309 | 11420.64 | 0.01154 | 3.7345e-05
2013-02-07 | 292117 | WNM2A | Urban | LV Transformer SP6437-G WNM2A - Planned | 12.75 | 289 | 3684.75 | 0.0037231 | 1.2883e-05
2013-02-07 | 292118 | KLG7A | Rural short | LV Transformer SP13731-D KLG7A - Planned | 1 | 300 | 300 | 0.00086145 | 2.8715e-06
2013-02-07 | 292119 | MRE3 | Urban | LV Transformer SP764155 MRE3 - Planned | 23.595 | 86 | 2029.17 | 0.0020503 | 2.3841e-05
2013-02-07 | 292120 | CHL3 | Urban | LV Transformer SP18667-G CHL3 - Planned | 4.15 | 300 | 1245 | 0.001258 | 4.1932e-06
2013-02-07 | 292121 | MTG4B | Urban | LV Transformer SP1607-J MTG4B - Planned | 12.975 | 123 | 1595.925 | 0.0016125 | 1.311e-05
2013-02-07 | 292122 | RLB16A | Rural short | LV Transformer SP2400-F RLB16A - Planned | 5.04 | 306 | 1542.24 | 0.0044286 | 1.4472e-05
2013-02-07 | 292123 | CVL17A | Urban | LV Transformer SP2104-D CVL17A - Planned | 20.43 | 345 | 7048.35 | 0.0071217 | 2.0643e-05
2013-02-07 | 292124 | MCW11 | Rural short | LV Transformer SP16984-B MCW11 - Planned | 7.56 | 249 | 1882.44 | 0.0054054 | 2.1709e-05
2013-02-07 | 292125 | WHO2 | Rural short | LV Transformer SC2097024 WHO2 - Planned | 3.64 | 381 | 1386.84 | 0.0039823 | 1.0452e-05
2013-02-07 | 292151 | GYM7A | Rural short | Feeder GYM7A - Planned | 55.1244 | 352 | 19403.7888 | 0.055718 | 0.00015829
2013-02-07 | 292261 | LLY4 | Rural short | LV Transformer SP10055-A LLY4 - Planned | 9.8928 | 316 | 3126.1248 | 0.0089767 | 2.8407e-05
2013-02-08 | 292150 | MLY3 | Rural short | LV Transformer SP5147-B MLY3 - Planned | 1 | 58 | 58 | 0.0001665 | 2.8707e-06
2013-02-08 | 292170 | MLY1 | Rural short | LV Transformer SP16471-A MLY1 - Planned | 1 | 130 | 130 | 0.00037319 | 2.8707e-06
2013-02-08 | 292251 | AGE2 | Urban | LV Transformer SP1239-M AGE2 - Planned | 7.1053 | 253 | 1797.6409 | 0.0018165 | 7.1797e-06
2013-02-08 | 292252 | GYM9B | Rural short | LV Transformer SP10600-C GYM9B - Planned | 3.01 | 235 | 707.35 | 0.0020306 | 8.6407e-06
2013-02-08 | 292253 | BLH12B | Urban | LV Transformer SP4937-B BLH12B - Planned | 23.29 | 217 | 5053.93 | 0.0051068 | 2.3534e-05
2013-02-08 | 292254 | MGP13A | Rural short | LV Transformer SP4506-F MGP13A - Planned | 3.105 | 260 | 807.3 | 0.0023175 | 8.9134e-06
2013-02-08 | 292255 | HDA4A | Urban | LV Transformer SP1782-K HDA4A - Planned | 2.82 | 230 | 648.6 | 0.00065539 | 2.8495e-06
2013-02-08 | 292256 | KCY5 | Rural short | LV Transformer SP4038-G KCY5 - Planned | 9.9 | 193 | 1910.7 | 0.005485 | 2.842e-05
2013-02-08 | 292257 | LTA2 | Urban | LV Transformer SP1916-P LTA2 - Planned | 42.28 | 270 | 11415.6 | 0.011535 | 4.2723e-05
2013-02-08 | 292258 | MRE3 | Urban | LV Transformer SP5418-E MRE3 - Planned | 28.475 | 262 | 7460.45 | 0.0075386 | 2.8773e-05
2013-02-08 | 292259 | AFD7 | Urban | LV Transformer SC6322-D AFD7 - Planned | 0.92 | 35 | 32.2 | 3.2537e-05 | 9.2963e-07
2013-02-08 | 292260 | AGT23A | Urban | LV Transformer SC1467834 AGT23A - Planned | 13.0622 | 245 | 3200.239 | 0.0032337 | 1.3199e-05
2013-02-09 | 292290 | MRE3 | Urban | LV Transformer SC808031-A MRE3 - Planned | 7.08 | 359 | 2541.72 | 0.0025685 | 7.1546e-06
2013-02-09 | 292325 | SBK11 | Urban | LV Transformer SP1842-M SBK11 - Planned | 8.34 | 409 | 3411.06 | 0.003447 | 8.4279e-06
2013-02-10 | 292310 | PAST1 | CBD | LV Transformer SSPAS PAST1 - Planned | 1 | 120 | 120 | 0.030891 | 0.00025742
2013-02-10 | 292310 | PAST2 | CBD | LV Transformer SSPAS PAST1 - Planned | 1 | 120 | 120 | 0.030891 | 0.00025742
2013-02-10 | 292317 | DRD13A | Urban | LV Transformer SP3671-D DRD13A - Planned | 18.525 | 185 | 3427.125 | 0.0034634 | 1.8721e-05
2013-02-10 | 292318 | CLD3 | Urban | LV Transformer SC2345-A CLD3 - Planned | 24 | 272 | 6528 | 0.0065971 | 2.4254e-05
2013-02-10 | 292319 | HTL6A | Urban | LV Transformer SC757207 HTL6A - Planned | 10.469 | 129 | 1350.501 | 0.0013648 | 1.058e-05
2013-02-10 | 292320 | SGT4 | Urban | LV Transformer SC6206-F SGT4 - Planned | 0.96 | 384 | 368.64 | 0.00037254 | 9.7016e-07
2013-02-10 | 292321 | MRE8 | Urban | LV Transformer SP3430-H MRE8 - Planned | 0.945 | 260 | 245.7 | 0.0002483 | 9.55e-07
2013-02-10 | 292323 | MDH3A | Urban | LV Transformer SC2238-H MDH3A - Planned | 1 | 556 | 556 | 0.00056188 | 1.0106e-06
2013-02-10 | 292324 | WED16A | Urban | LV Transformer SP3659-I WED16A - Planned | 1.05 | 295 | 309.75 | 0.00031303 | 1.0611e-06
2013-02-10 | 292324 | WED20A | Urban | LV Transformer SP3659-I WED16A - Planned | 12.76 | 295 | 3764.2 | 0.003804 | 1.2895e-05
2013-02-10 | 293318 | F1220 | Urban | Feeder F1220 - Planned | 1 | 801 | 801 | 0.00080948 | 1.0106e-06
2013-02-10 | 293492 | GLY2 | Urban | LV Transformer SP2961-L GLY2 - Planned | 23.44 | 476 | 11157.44 | 0.011276 | 2.3688e-05
2013-02-11 | 292371 | MGP4 | Rural short | LV Transformer SP4504-D MGP4 - Planned | 24 | 67 | 1608 | 0.0046119 | 6.8835e-05
2013-02-11 | 292454 | WMD13A | Rural short | LV Transformer SP5162-A WMD13A - Planned | 25.92 | 183 | 4743.36 | 0.013604 | 7.4341e-05
2013-02-11 | 292455 | GYGGYS6 | Rural short | Feeder GYGGYS6 - Planned | 37.565 | 70 | 2629.55 | 0.0075418 | 0.00010774
2013-02-11 | 292459 | NVL8B | Urban | LV Transformer SP11682-B NVL8B - Planned | 2.385 | 45 | 107.325 | 0.00010847 | 2.4104e-06
2013-02-11 | 292460 | CPL3A | Urban | LV Transformer SC5522-G CPL3A - Planned | 6.96 | 20 | 139.2 | 0.00014068 | 7.0341e-06
2013-02-11 | 292461 | PWC3 | Rural short | LV Transformer SP794-A PWC3 - Planned | 4 | 351 | 1404 | 0.0040268 | 1.1472e-05
2013-02-11 | 292462 | AGE9 | Urban | LV Transformer SP5442-H AGE9 - Planned | 20.5418 | 453 | 9305.4354 | 0.0094045 | 2.0761e-05
2013-02-11 | 292463 | DRD5A | Urban | LV Transformer SP2764-F DRD5A - Planned | 9.05 | 60 | 543 | 0.00054878 | 9.1464e-06
2013-02-11 | 292464 | BHD7A | Urban | LV Transformer SC2361-J BHD7A - Planned | 12.24 | 141 | 1725.84 | 0.0017442 | 1.237e-05
2013-02-11 | 292465 | BRD13A | Urban | LV Transformer SC788469 BRD13A - Planned | 14.995 | 19.6667 | 717.575 | 0.00072522 | 1.5155e-05
2013-02-12 | 292550 | RLB13B | Rural short | LV Transformer SP1839-F RLB13B - Planned | 2.01 | 83 | 166.83 | 0.00047835 | 5.7632e-06
2013-02-12 | 292571 | KBR1A | Rural short | LV Transformer SP4092-D KBR1A - Planned | 1 | 179 | 179 | 0.00051324 | 2.8673e-06
2013-02-12 | 292572 | BLB8A | Urban | LV Transformer SP13869-E BLB8A - Planned | 0.4 | 232 | 92.8 | 9.3793e-05 | 4.0428e-07
2013-02-12 | 292574 | BDT1 | Rural short | LV Transformer SP4308-G BDT1 - Planned | 11.04 | 95 | 1048.8 | 0.0030072 | 3.1655e-05
2013-02-12 | 292631 | ABY2A | Rural short | LV Transformer SP12942-B ABY2A - Planned | 1.34 | 302 | 404.68 | 0.0011603 | 3.8421e-06
2013-02-12 | 292652 | MSV2 | Rural short | LV Transformer SP13623-A MSV2 - Planned | 1 | 259 | 259 | 0.00074262 | 2.8673e-06
2013-02-12 | 292670 | IPL1 | Rural short | LV Transformer SP4433-D IPL1 - Planned | 1.675 | 378 | 633.15 | 0.0018154 | 4.8027e-06
2013-02-12 | 292671 | MGP1 | Rural short | LV Transformer SP15833-B MGP1 - Planned | 21 | 324 | 6804 | 0.019509 | 6.0213e-05
2013-02-12 | 292690 | MLY3 | Rural short | LV Transformer SP6781-D MLY3 - Planned | 1 | 267 | 267 | 0.00076556 | 2.8673e-06
2013-02-12 | 292691 | GBN3 | Rural short | LV Transformer SP2554-D GBN3 - Planned | 4.98 | 212 | 1055.76 | 0.0030271 | 1.4279e-05
2013-02-12 | 292692 | TGW1 | Rural short | Feeder TGW1 - Planned | 55.42 | 388 | 21502.96 | 0.061655 | 0.0001589
2013-02-12 | 292694 | GYS2A | Urban | LV Transformer SP4252-B GYS2A - Planned | 4.98 | 349 | 1738.02 | 0.0017566 | 5.0333e-06
2013-02-12 | 292710 | ABY5A | Rural short | Feeder ABY5A - Planned | 19.5 | 503 | 9808.5 | 0.028124 | 5.5912e-05
2013-02-12 | 292711 | RBY12 | Urban | LV Transformer SC2059727 RBY12 - Planned | 3.9 | 155 | 604.5 | 0.00061097 | 3.9417e-06
2013-02-12 | 292712 | AGE7B | Urban | LV Transformer SP329-R AGE7B - Planned | 1.33 | 322 | 428.26 | 0.00043284 | 1.3442e-06
2013-02-12 | 292713 | SFD3 | Urban | LV Transformer SC4054-K SFD3 - Planned | 9.8 | 316 | 3096.8 | 0.0031299 | 9.9049e-06
2013-02-12 | 292714 | MGL5 | Urban | LV Transformer SC5451-H MGL5 - Planned | 7.95 | 350 | 2782.5 | 0.0028123 | 8.0351e-06
2013-02-12 | 292715 | SHW10A | Urban | LV Transformer SP246-Q SHW10A - Planned | 22.08 | 215 | 4747.2 | 0.004798 | 2.2316e-05
2013-02-12 | 292716 | ENG7 | Urban | LV Transformer SP596-O ENG7 - Planned | 14.14 | 266 | 3761.24 | 0.0038015 | 1.4291e-05
2013-02-12 | 292717 | LBH6A | Rural short | LV Transformer SP4516-A LBH6A - Planned | 24.96 | 78 | 1946.88 | 0.0055822 | 7.1567e-05
2013-02-12 | 292718 | MGP13A | Rural short | LV Transformer SP1708-G MGP13A - Planned | 7.98 | 330 | 2633.4 | 0.0075507 | 2.2881e-05
2013-02-12 | 292719 | SPO67B | Urban | LV Transformer SP3691-F SPO67B - Planned | 31.366 | 167 | 5238.122 | 0.0052942 | 3.1702e-05
2013-02-12 | 292720 | BLH10A | Urban | LV Transformer SC1401799 - Planned | 9 | 51 | 459 | 0.00046391 | 9.0963e-06
2013-02-12 | 292721 | SPO67B | Urban | LV Transformer SP1769-H SPO67B - Planned | 23.85 | 137 | 3267.45 | 0.0033024 | 2.4105e-05
2013-02-12 | 292722 | SFD2A | Urban | LV Transformer SC760629 SFD2A - Planned | 14.05 | 35 | 491.75 | 0.00049701 | 1.42e-05
2013-02-12 | 292723 | BRD2A | Urban | LV Transformer SC103-J BRD2A - Planned | 12.6 | 325 | 4095 | 0.0041388 | 1.2735e-05
2013-02-12 | 292724 | DRD13A | Urban | LV Transformer SP5770-D DRD13A - Planned | 7.98 | 259 | 2066.82 | 0.0020889 | 8.0654e-06
2013-02-12 | 292725 | HDA4A | Urban | LV Transformer SP748326 HDA4A - Planned | 5.37 | 352 | 1890.24 | 0.0019105 | 5.4275e-06
2013-02-12 | 292726 | DRD13A | Urban | LV Transformer SP6155-D DRD13A - Planned | 21.2075 | 309 | 6553.1175 | 0.0066233 | 2.1435e-05
2013-02-12 | 292727 | MHL3A | Urban | LV Transformer SC584517 MHL3A - Planned | 10.4 | 20 | 208 | 0.00021023 | 1.0511e-05
2013-02-12 | 292728 | WFD2B | Rural short | LV Transformer SP808-H WFD2B - Planned | 9 | 145 | 1305 | 0.0037418 | 2.5805e-05
2013-02-12 | 292729 | CFD2A | Urban | LV Transformer SP12927-D HDA11A - Planned | 2.21 | 230 | 508.3 | 0.00051374 | 2.2337e-06
2013-02-12 | 292729 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 17.12 | 230 | 3937.6 | 0.0039797 | 1.7303e-05
2013-02-12 | 292731 | DRD3A | Urban | LV Transformer SP1928-G DRD3A - Planned | 5.44 | 150 | 816 | 0.00082473 | 5.4982e-06
2013-02-12 | 292732 | CBT13A | Urban | LV Transformer SC21075-C CBT13A - Planned | 2 | 55 | 110 | 0.00011118 | 2.0214e-06
2013-02-12 | 292733 | WFD2B | Rural short | LV Transformer SP5025-F WFD2B - Planned | 7.05 | 186 | 1311.3 | 0.0037598 | 2.0214e-05
2013-02-12 | 292735 | WFD2B | Rural short | LV Transformer SP110-L WFD2B - Planned | 1.02 | 398 | 405.96 | 0.001164 | 2.9246e-06
2013-02-12 | 292736 | MCN2 | Rural short | LV Transformer SP5380-D MCN2 - Planned | 4.98 | 151 | 751.98 | 0.0021561 | 1.4279e-05
2013-02-12 | 292737 | WED6A | Urban | LV Transformer SC3591-H WED6A - Planned | 68.665 | 179 | 12291.035 | 0.012423 | 6.94e-05
2013-02-12 | 292738 | CHL3 | Urban | LV Transformer SP45538-E CHL3 - Planned | 0.78 | 270 | 210.6 | 0.00021285 | 7.8835e-07
2013-02-12 | 292739 | CMV14 | Urban | LV Transformer SC6466-J CMV14 - Planned | 1 | 140 | 140 | 0.0001415 | 1.0107e-06
2013-02-12 | 292741 | OXL8A | Urban | LV Transformer SG6285-D OXL8A - Planned | 1.05 | 45 | 47.25 | 4.7756e-05 | 1.0612e-06
2013-02-12 | 292742 | BLB2A | Urban | LV Transformer SC1368624 BLB2A - Planned | 9.77 | 402 | 3927.54 | 0.0039696 | 9.8746e-06
2013-02-12 | 292743 | CHL5 | Urban | LV Transformer SP716-L CHL5 - Planned | 26.67 | 363 | 9681.21 | 0.0097848 | 2.6955e-05
2013-02-12 | 292743 | SRD14A | Urban | LV Transformer SP716-L CHL5 - Planned | 53.32 | 363 | 19355.16 | 0.019562 | 5.3891e-05
2013-02-12 | 292744 | BDB32A | Rural short | LV Transformer SP3538-D BDB32A - Planned | 21.06 | 321 | 6760.26 | 0.019383 | 6.0385e-05
2013-02-12 | 292745 | RLB13B | Rural short | LV Transformer SP2925-D RLB13B - Planned | 2.125 | 172 | 365.5 | 0.001048 | 6.0929e-06
2013-02-12 | 292746 | LGL15A | Urban | LV Transformer SP2461-H LGL15A - Planned | 8.425 | 149 | 1255.325 | 0.0012688 | 8.5152e-06
2013-02-12 | 293319 | ABY5A | Rural short | Feeder ABY5A - Planned | 19.5 | 503 | 9808.5 | 0.028124 | 5.5912e-05
2013-02-12 | 293320 | RLB13B | Rural short | LV Transformer SP4875-C RLB13B - Planned | 9.2 | 97 | 892.4 | 0.0025587 | 2.6379e-05
2013-02-12 | 293321 | MSV2 | Rural short | LV Transformer SP8413-A MSV2 - Planned | 0.8 | 12 | 9.6 | 2.7526e-05 | 2.2938e-06
2013-02-12 | 293490 | MLY4 | Rural short | LV Transformer SP3038-A MLY4 - Planned | 22.08 | 239 | 5277.12 | 0.015131 | 6.3309e-05
2013-02-13 | 292811 | GGR1 | Rural short | LV Transformer SP758265 GGR1 - Planned | 1 | 176 | 176 | 0.0005045 | 2.8665e-06
2013-02-13 | 292832 | KBR2A | Rural short | Feeder KBR2A - Planned | 4 | 252 | 1008 | 0.0028894 | 1.1466e-05
2013-02-13 | 292870 | RIS4 | Rural short | LV Transformer SP11707-A RIS4 - Planned | 3 | 296 | 888 | 0.0025454 | 8.5994e-06
2013-02-13 | 292871 | BNH1B | Rural short | LV Transformer SP1550-E BNH1B - Planned | 5 | 340 | 1700 | 0.004873 | 1.4332e-05
2013-02-13 | 292890 | KLG7A | Rural short | Feeder KLG7A - Planned | 8 | 392 | 3136 | 0.0089892 | 2.2932e-05
2013-02-13 | 292910 | CRY6A | Rural short | Feeder CRY6A - Planned | 54.02 | 332 | 17934.64 | 0.051409 | 0.00015485
2013-02-13 | 292911 | MLY3 | Rural short | LV Transformer SP4575-A MLY3 - Planned | 9 | 384 | 3456 | 0.0099065 | 2.5798e-05
2013-02-13 | 292912 | MLY3 | Rural short | LV Transformer SP4561-C MLY3 - Planned | 29.1 | 68 | 1978.8 | 0.0056721 | 8.3414e-05
2013-02-13 | 292933 | CCY26A | Urban | LV Transformer SC2061889 CCY26A - Planned | 0.4 | 532 | 212.8 | 0.00021509 | 4.043e-07
2013-02-13 | 292938 | ENG2 | Urban | LV Transformer SP783372 ENG2 - Planned | 40.92 | 158 | 6465.36 | 0.0065349 | 4.136e-05
2013-02-13 | 292939 | AGE9 | Urban | LV Transformer SP1117-Q AGE9 - Planned | 1.48 | 455 | 673.4 | 0.00068064 | 1.4959e-06
2013-02-13 | 292940 | GBN4 | Rural short | LV Transformer SP6825-D GBN4 - Planned | 3.375 | 71 | 239.625 | 0.00068687 | 9.6743e-06
2013-02-13 | 292941 | BBH16A | Urban | LV Transformer SP8787-E BBH16A - Planned | 1.4933 | 63 | 94.0779 | 9.509e-05 | 1.5094e-06
2013-02-13 | 292942 | MAI11 | Urban | LV Transformer SP11978-D MAI11 - Planned | 0.825 | 71 | 58.575 | 5.9205e-05 | 8.3387e-07
2013-02-13 | 292943 | GVN13A | Urban | LV Transformer SC568131 GVN13A - Planned | 1.32 | 109 | 143.88 | 0.00014543 | 1.3342e-06
2013-02-13 | 292944 | CCY26A | Urban | LV Transformer SP6405-B CCY26A - Planned | 17.15 | 262 | 4493.3 | 0.0045416 | 1.7334e-05
2013-02-13 | 292945 | MGP12A | Rural short | LV Transformer SP12065-D MGP12A - Planned | 41 | 286 | 11726 | 0.033612 | 0.00011752
2013-02-13 | 292946 | BDT1 | Rural short | LV Transformer SP13303-B BDT1 - Planned | 20.475 | 519 | 10626.525 | 0.03046 | 5.8691e-05
2013-02-13 | 292948 | ZMR5 | Urban | LV Transformer SP441482 ZMR5 - Planned | 32.76 | 45 | 1474.2 | 0.0014901 | 3.3112e-05
2013-02-13 | 292949 | CFD1A | Urban | LV Transformer SP2086-I CFD1A - Planned | 2.325 | 306 | 711.45 | 0.0007191 | 2.35e-06
2013-02-13 | 292950 | KLG7A | Rural short | LV Transformer SP13731-D KLG7A - Planned | 1 | 373 | 373 | 0.0010692 | 2.8665e-06
2013-02-13 | 292951 | BRD13A | Urban | LV Transformer SC2296-D BRD13A - Planned | 12 | 205 | 2460 | 0.0024865 | 1.2129e-05
2013-02-13 | 292952 | RBY9A | Urban | LV Transformer SC1160-E RBY9A - Planned | 5.265 | 238 | 1253.07 | 0.0012665 | 5.3216e-06
2013-02-13 | 292953 | EMP23A | Urban | LV Transformer SP3997-F EMP23A - Planned | 2.79 | 263 | 733.77 | 0.00074166 | 2.82e-06
2013-02-13 | 292954 | WED6A | Urban | LV Transformer SC3591-H WED6A - Planned | 22.15 | 330 | 7309.5 | 0.0073881 | 2.2388e-05
2013-02-13 | 292955 | LGL15A | Urban | LV Transformer SP803247 LGL15A - Planned | 23.94 | 210 | 5027.4 | 0.0050815 | 2.4197e-05
2013-02-13 | 292958 | GBN3 | Rural short | LV Transformer SP7516-B GBN3 - Planned | 2.01 | 121 | 243.21 | 0.00069715 | 5.7616e-06
2013-02-13 | 292959 | NBR4 | Rural short | LV Transformer SP5117-A NBR4 - Planned | 5 | 186 | 930 | 0.0026658 | 1.4332e-05
2013-02-13 | 292960 | GBN4 | Rural short | LV Transformer SP3830-A GBN4 - Planned | 2.345 | 166 | 389.27 | 0.0011158 | 6.7218e-06
2013-02-13 | 293491 | BMT1 | Rural short | LV Transformer SP1453-E BMT1 - Planned | 8.5 | 235 | 1997.5 | 0.0057257 | 2.4365e-05
2013-02-14 | 292970 | BNH1B | Rural short | LV Transformer SP1545-D BNH1B - Planned | 2 | 62 | 124 | 0.00035534 | 5.7313e-06
2013-02-14 | 293030 | WFD2B | Rural short | LV Transformer SP4978-E WFD2B - Planned | 23.5 | 268 | 6298 | 0.018048 | 6.7343e-05
2013-02-14 | 293032 | WNM2A | Urban | LV Transformer SG2806-I WNM2A - Planned | 23.04 | 298 | 6865.92 | 0.0069402 | 2.3289e-05
2013-02-14 | 293050 | CMV9B | Urban | LV Transformer SC10110-I CMV9B - Planned | 21 | 10.5 | 441 | 0.00044577 | 2.1227e-05
2013-02-14 | 293052 | BTN2 | Rural short | Feeder BTN2 - Planned | 21.5 | 125 | 2687.5 | 0.0077015 | 6.1612e-05
2013-02-14 | 293070 | TGW2 | Rural short | Feeder TGW2 - Planned | 5.98 | 392 | 2344.16 | 0.0067176 | 1.7137e-05
2013-02-14 | 293092 | RWD2 | Rural short | Feeder RWD2 - Planned | 6.68 | 357 | 2384.76 | 0.0068339 | 1.9143e-05
2013-02-14 | 293094 | WMD8B | Rural short | Feeder WMD8B - Planned | 42.32 | 395 | 16716.4 | 0.047903 | 0.00012127
2013-02-14 | 293095 | BMT1 | Rural short | Feeder BMT1 - Planned | 20.96 | 380 | 7964.8 | 0.022824 | 6.0064e-05
2013-02-14 | 293096 | MLY3 | Rural short | Feeder MLY3 - Planned | 39.95 | 295 | 11785.25 | 0.033772 | 0.00011448
2013-02-14 | 293097 | GBN3 | Rural short | LV Transformer SP2560-D GBN3 - Planned | 6 | 385 | 2310 | 0.0066197 | 1.7194e-05
2013-02-14 | 293098 | GBN4 | Rural short | Feeder GBN4 - Planned | 21.27 | 257 | 5466.39 | 0.015665 | 6.0953e-05
2013-02-14 | 293099 | PWC5 | Rural short | LV Transformer SP3952-B PWC5 - Planned | 14.08 | 315 | 4435.2 | 0.01271 | 4.0348e-05
2013-02-14 | 293100 | MTB17A | Rural short | Feeder MTB17A - Planned | 13.2596 | 520 | 6894.992 | 0.019759 | 3.7997e-05
2013-02-14 | 293102 | KLG7A | Rural short | Feeder KLG7A - Planned | 26 | 610 | 15860 | 0.045449 | 7.4507e-05
2013-02-14 | 293103 | MGP13A | Rural short | Feeder MGP13A - Planned | 5.5 | 155 | 559.5 | 0.0016033 | 1.5761e-05
2013-02-14 | 293106 | AGE10 | Urban | LV Transformer SC806580 AGE10 - Planned | 12.63 | 234 | 2955.42 | 0.0029874 | 1.2767e-05
2013-02-14 | 293107 | AGE10 | Urban | LV Transformer SP26943-F AGE10 - Planned | 28.1181 | 295 | 8294.8395 | 0.0083845 | 2.8422e-05
2013-02-14 | 293107 | TWG11 | Urban | LV Transformer SP26943-F AGE10 - Planned | 1.33 | 295 | 392.35 | 0.00039659 | 1.3444e-06
2013-02-14 | 293108 | INA7A | Rural short | LV Transformer SC4922-H INA7A - Planned | 8.8 | 263 | 2314.4 | 0.0066323 | 2.5218e-05
2013-02-14 | 293109 | NVL10 | Urban | LV Transformer SP9430-B NVL10 - Planned | 6.3 | 54 | 340.2 | 0.00034388 | 6.3681e-06
2013-02-14 | 293110 | GYM2A | Rural short | LV Transformer SP735-B GYM2A - Planned | 3.01 | 231 | 695.31 | 0.0019925 | 8.6256e-06
2013-02-14 | 293111 | NVL9 | Rural short | LV Transformer SC1919-E NVL9 - Planned | 0.81 | 381 | 308.61 | 0.00088437 | 2.3212e-06
2013-02-14 | 293112 | LDR6 | Urban | LV Transformer SC568193 LDR6 - Planned | 3.19 | 103 | 328.57 | 0.00033212 | 3.2245e-06
2013-02-14 | 293112 | SPO11A | Urban | LV Transformer SC568193 LDR6 - Planned | 0.92 | 103 | 94.76 | 9.5785e-05 | 9.2995e-07
2013-02-14 | 293113 | BLH10B | Urban | LV Transformer SP5433-C BLH10B - Planned | 22.14 | 81 | 1793.34 | 0.0018127 | 2.2379e-05
2013-02-14 | 293114 | SPO11A | Urban | LV Transformer SP40561-B SPO11A - Planned | 1.92 | 48 | 92.16 | 9.3157e-05 | 1.9408e-06
2013-02-14 | 293115 | JBB1B | Rural short | LV Transformer SP5352-D JBB1B - Planned | 20 | 80 | 1600 | 0.0045851 | 5.7313e-05
2013-02-14 | 293116 | MGP12A | Rural short | LV Transformer SP15841-C - Planned | 23 | 305 | 7015 | 0.020103 | 6.591e-05
2013-02-14 | 293117 | DRD13A | Urban | LV Transformer SP3400-C RCF2A - Planned | 11.76 | 93 | 1093.68 | 0.0011055 | 1.1887e-05
2013-02-14 | 293117 | RCF2A | Urban | LV Transformer SP3400-C RCF2A - Planned | 1.52 | 93 | 141.36 | 0.00014289 | 1.5364e-06
2013-02-14 | 293118 | BHL4A | Urban | LV Transformer SP2966-H BHL4A - Planned | 6.86 | 250 | 1715 | 0.0017335 | 6.9342e-06
2013-02-14 | 293119 | CMD5A | Urban | LV Transformer SP805-C CMD5A - Planned | 15.6 | 265 | 4134 | 0.0041787 | 1.5769e-05
2013-02-14 | 293120 | CFD1A | Urban | LV Transformer SP2086-I CFD1A - Planned | 10.32 | 219 | 2260.08 | 0.0022845 | 1.0432e-05
2013-02-14 | 293122 | CPB9 | Urban | LV Transformer SP7923-D CPB9 - Planned | 2 | 138 | 276 | 0.00027898 | 2.0216e-06
2013-02-14 | 293124 | WRD25A | Urban | LV Transformer SC5419-E WRD25A - Planned | 20 | 352 | 7040 | 0.0071161 | 2.0216e-05
2013-02-14 | 293125 | EMP21A | Rural short | LV Transformer SP5587-I EMP21A - Planned | 0.815 | 184 | 149.96 | 0.00042973 | 2.3355e-06
2013-02-14 | 293126 | BLB8A | Urban | LV Transformer SP3446-G BLB8A - Planned | 16.2061 | 253 | 4100.1433 | 0.0041445 | 1.6381e-05
2013-02-14 | 293127 | WED16A | Urban | LV Transformer SP135-O WED16A - Planned | 25.0404 | 390 | 9765.756 | 0.0098714 | 2.5311e-05
2013-02-14 | 293128 | ALY3A | Urban | LV Transformer SP2773-I ALY3A - Planned | 7.65 | 308 | 2356.2 | 0.0023817 | 7.7327e-06
2013-02-14 | 293129 | FDS1 | Rural short | LV Transformer SP3200-D FDS1 - Planned | 0.9 | 175 | 157.5 | 0.00045134 | 2.5791e-06
2013-02-14 | 293370 | NGE12 | Urban | LV Transformer SC3247-G NGE12 - Planned | 9.57 | 1615 | 3493.05 | 0.0035308 | 9.6735e-06
2013-02-14 | 293471 | BNH1B | Rural short | LV Transformer SP1549-E BNH1B - Planned | 3 | 132 | 396 | 0.0011348 | 8.597e-06
2013-02-15 | 293170 | MLY3 | Rural short | LV Transformer SP7774-A MLY3 - Planned | 25.11 | 285 | 7156.35 | 0.020502 | 7.1937e-05
2013-02-15 | 293171 | JBB1B | Rural short | LV Transformer SP5354-D JBB1B - Planned | 15.04 | 245 | 3684.8 | 0.010556 | 4.3088e-05
2013-02-15 | 293190 | IPS1B | Urban | LV Transformer SP763552 IPS1B - Planned | 4 | 118 | 472 | 0.00047713 | 4.0435e-06
2013-02-15 | 293191 | THL3 | Rural short | LV Transformer SP3458-B THL3 - Planned | 4 | 284 | 1136 | 0.0032545 | 1.1459e-05
2013-02-15 | 293192 | WMR3 | Rural short | Feeder WMR3 - Planned | 1 | 370 | 370 | 0.00106 | 2.8649e-06
2013-02-15 | 293193 | GBN3 | Rural short | Feeder GBN3 - Planned | 8.01 | 324 | 2595.24 | 0.007435 | 2.2948e-05
2013-02-15 | 293194 | NBR9 | Rural short | LV Transformer SP586-A NBR9 - Planned | 9 | 42 | 378 | 0.0010829 | 2.5784e-05
2013-02-15 | 293195 | PWC3 | Rural short | LV Transformer SP16357-A PWC3 - Planned | 11.04 | 25 | 276 | 0.0007907 | 3.1628e-05
2013-02-15 | 293222 | MLY3 | Rural short | Feeder MLY3 - Planned | 86.05 | 439 | 37775.95 | 0.10822 | 0.00024652
2013-02-15 | 293259 | AGE2 | Urban | LV Transformer SP1239-M AGE2 - Planned | 9.1849 | 167 | 1533.8783 | 0.0015506 | 9.2848e-06
2013-02-15 | 293260 | AGE10 | Urban | LV Transformer SC772751-A AGE10 - Planned | 12.21 | 190 | 2319.9 | 0.0023451 | 1.2343e-05
2013-02-15 | 293261 | GLY2 | Urban | LV Transformer SP779957 GLY2 - Planned | 17.85 | 245 | 4373.25 | 0.0044208 | 1.8044e-05
2013-02-15 | 293262 | AGE2 | Urban | LV Transformer SP13258-H AGE2 - Planned | 9.8 | 379 | 3714.2 | 0.0037546 | 9.9066e-06
2013-02-15 | 293263 | NBR4 | Rural short | LV Transformer SP5157-A NBR4 - Planned | 2.04 | 135 | 275.4 | 0.00078898 | 5.8443e-06
2013-02-15 | 293264 | AMR2 | Rural short | LV Transformer SP576-B AMR2 - Planned | 8.01 | 63 | 504.63 | 0.0014457 | 2.2948e-05
2013-02-15 | 293265 | NBR5 | Rural short | LV Transformer SP2692-A NBR5 - Planned | 4.27 | 114 | 486.78 | 0.0013946 | 1.2233e-05
2013-02-15 | 293267 | YTA23B | Urban | LV Transformer SC567457 YTA23B - Planned | 3 | 43 | 129 | 0.0001304 | 3.0326e-06
2013-02-15 | 293269 | MGP15A | Rural short | LV Transformer SP11262-D MGP15A - Planned | 12.255 | 208 | 2549.04 | 0.0073027 | 3.5109e-05
2013-02-15 | 293270 | MTB17A | Rural short | LV Transformer SP5265-G MTB17A - Planned | 1.04 | 264 | 274.56 | 0.00078658 | 2.9795e-06
2013-02-15 | 293273 | DRD13A | Urban | LV Transformer SP3553-F DRD13A - Planned | 5.565 | 190 | 1057.35 | 0.0010688 | 5.6255e-06
2013-02-15 | 293274 | SGT4 | Urban | LV Transformer SC3544-G SGT4 - Planned | 0.99 | 43 | 42.57 | 4.3033e-05 | 1.0008e-06
2013-02-15 | 293275 | SGT7 | Urban | LV Transformer SP5175-I SGT7 - Planned | 13.11 | 77 | 1009.47 | 0.0010204 | 1.3253e-05
2013-02-15 | 293276 | MTG7A | Urban | LV Transformer SP5128-G MTG7A - Planned | 10.17 | 123 | 1250.91 | 0.0012645 | 1.0281e-05
2013-02-15 | 293277 | LGL11A | Urban | LV Transformer SP3261-C LGL11A - Planned | 4.44 | 159 | 705.96 | 0.00071364 | 4.4883e-06
2013-02-15 | 293277 | WRG11A | Urban | LV Transformer SP3261-C LGL11A - Planned | 5 | 159 | 795 | 0.00080364 | 5.0544e-06
2013-02-15 | 293278 | UMG1A | Urban | LV Transformer SC758128 - Planned | 43.8648 | 435 | 19081.188 | 0.019289 | 4.4342e-05
2013-02-15 | 293279 | WED6A | Urban | LV Transformer SC3591-H WED6A - Planned | 21.21 | 251 | 5323.71 | 0.0053816 | 2.1441e-05
2013-02-15 | 293281 | WRG19A | Urban | LV Transformer SP759220 WRG19A - Planned | 1.04 | 48 | 49.92 | 5.0463e-05 | 1.0513e-06
2013-02-15 | 293282 | MBG1 | Rural short | LV Transformer SP4109-G MBG1 - Planned | 1.34 | 174 | 233.16 | 0.00066797 | 3.8389e-06
2013-02-16 | 293308 | GCLSBY7 | Urban | LV Transformer SC766334 GCLSBY7 - Planned | 4.4844 | 334 | 1497.7896 | 0.001514 | 4.5331e-06
2013-02-16 | 293309 | CMV8 | Urban | LV Transformer SC1941-M CMV8 - Planned | 2.002 | 125 | 250.25 | 0.00025297 | 2.0237e-06
2013-02-16 | 293374 | GCLSBY7 | Urban | LV Transformer SP834377 GCLSBY7 - Planned | 1 | 334 | 334 | 0.00033763 | 1.0109e-06
2013-02-17 | 293356 | ENG3 | Urban | LV Transformer SG1148-N ENG3 - Planned | 6 | 376 | 2256 | 0.0022805 | 6.065e-06
2013-02-17 | 293359 | CBW11 | Rural short | Feeder CBW11 - Planned | 42.5 | 441 | 18742.5 | 0.053689 | 0.00012174
2013-02-17 | 293360 | ZMR9 | Urban | LV Transformer SG4677-G ZMR9 - Planned | 1 | 498 | 498 | 0.0005034 | 1.0108e-06
2013-02-17 | 293364 | ENG8 | Urban | LV Transformer SP1418275 ENG7 - Planned | 10.0331 | 370 | 3712.247 | 0.0037525 | 1.0142e-05
2013-02-17 | 293365 | HTN22A | Urban | LV Transformer SG2195-I HTN22A - Planned | 1 | 415 | 415 | 0.0004195 | 1.0108e-06
2013-02-17 | 293366 | NDH7 | Urban | LV Transformer SC5302-H NDH7 - Planned | 24.04 | 255 | 6130.2 | 0.0061966 | 2.4301e-05
2013-02-17 | 293367 | CBT13A | Urban | LV Transformer SC774435 CBT13A - Planned | 18.44 | 81.5 | 758.48 | 0.0007667 | 1.864e-05
2013-02-17 | 293368 | NDH7 | Urban | LV Transformer SP2162-J NDH7 - Planned | 15.52 | 287 | 4454.24 | 0.0045025 | 1.5688e-05
2013-02-17 | 293371 | CPR4 | Urban | LV Transformer SP116-O CPR4 - Planned | 15.9864 | 387 | 6186.7368 | 0.0062538 | 1.616e-05
2013-02-17 | 293372 | WED16A | Urban | LV Transformer SP3659-I WED16A - Planned | 1.05 | 207 | 217.35 | 0.00021971 | 1.0614e-06
2013-02-17 | 293373 | WED21A | Urban | LV Transformer SP74-O WED21A - Planned | 2.9 | 553 | 1603.7 | 0.0016211 | 2.9314e-06
2013-02-18 | 293519 | KCY5 | Rural short | LV Transformer SP5826-C KCY5 - Planned | 0.5 | 180 | 90 | 0.00025778 | 1.4321e-06
2013-02-18 | 293571 | KCY1 | Urban | LV Transformer SP3440-A KCY1 - Planned | 8 | 420 | 3360 | 0.0033963 | 8.0864e-06
2013-02-18 | 293576 | AHL4A | Urban | LV Transformer SP772352 AHL4A - Planned | 26.68 | 171 | 4562.28 | 0.0046116 | 2.6968e-05
2013-02-18 | 293577 | ENG2 | Urban | LV Transformer SP18533-F ENG2 - Planned | 12.06 | 285 | 3437.1 | 0.0034742 | 1.219e-05
2013-02-18 | 293578 | PGN1B | Rural short | LV Transformer SP6733-A PGN1B - Planned | 30.45 | 240 | 7308 | 0.020932 | 8.7216e-05
2013-02-18 | 293579 | PGN1B | Rural short | LV Transformer SP3531-A PGN1B - Planned | 14.245 | 223 | 3176.635 | 0.0090987 | 4.0801e-05
2013-02-18 | 293580 | PGN1B | Rural short | LV Transformer SP2158-C PGN1B - Planned | 21.45 | 121 | 2595.45 | 0.007434 | 6.1438e-05
2013-02-18 | 293581 | NVL9 | Rural short | LV Transformer SP2914-B NVL9 - Planned | 18.785 | 182 | 3418.87 | 0.0097925 | 5.3805e-05
2013-02-18 | 293582 | IPL1 | Rural short | LV Transformer SP834316 IPL1 - Planned | 1 | 210 | 210 | 0.00060149 | 2.8642e-06
2013-02-18 | 293583 | GVN15A | Urban | LV Transformer SP6305-F GVN15A - Planned | 3 | 56 | 168 | 0.00016981 | 3.0324e-06
2013-02-18 | 293584 | LTN5 | Rural short | LV Transformer SP3126-F LTN5 - Planned | 3.92 | 333 | 1305.36 | 0.0037389 | 1.1228e-05
2013-02-18 | 293585 | CVL5A | Rural short | LV Transformer SP766701 CVL5A - Planned | 1.96 | 87 | 170.52 | 0.00048841 | 5.6139e-06
2013-02-18 | 293586 | NSW16A | Urban | LV Transformer SP3279-K NSW16A - Planned | 4.8 | 325 | 1560 | 0.0015768 | 4.8518e-06
2013-02-18 | 293587 | LLY1 | Rural short | LV Transformer SP1637-B LLY1 - Planned | 10.5 | 171 | 1795.5 | 0.0051428 | 3.0075e-05
2013-02-18 | 293588 | NIP5A | Urban | LV Transformer SP1446-H NIP5A - Planned | 11.83 | 192 | 2271.36 | 0.0022959 | 1.1958e-05
2013-02-18 | 293589 | NIP4A | Rural short | LV Transformer SP4145-C NIP4A - Planned | 4.21 | 51 | 214.71 | 0.00061498 | 1.2058e-05
2013-02-18 | 294642 | WMR3 | Rural short | LV Transformer SP4948-D WMR3 - Planned | 1 | 239 | 239 | 0.00068456 | 2.8642e-06
2013-02-19 | 293710 | STT3A | Rural short | LV Transformer SP4737-C STT3A - Planned | 22.08 | 91 | 2009.28 | 0.0057547 | 6.3239e-05
2013-02-19 | 293730 | PWC5 | Rural short | LV Transformer SP3509-B PWC5 - Planned | 12.04 | 161 | 1938.44 | 0.0055518 | 3.4483e-05
2013-02-19 | 293810 | MGL1A | Rural short | LV Transformer SP741771 MGL1A - Planned | 1 | 196 | 196 | 0.00056136 | 2.8641e-06
2013-02-19 | 293890 | WHO1 | Rural short | Feeder WHO1 - Planned | 26.97 | 301 | 8117.97 | 0.02325 | 7.7244e-05
2013-02-19 | 293892 | NVL9 | Rural short | LV Transformer SP6774-B NVL9 - Planned | 1 | 109 | 109 | 0.00031218 | 2.8641e-06
2013-02-19 | 293911 | JBB13A | Rural short | LV Transformer SP5546-D JBB13A - Planned | 5 | 409 | 2045 | 0.005857 | 1.432e-05
2013-02-19 | 293912 | MGP4 | Rural short | Feeder MGP4 - Planned | 85 | 468 | 39780 | 0.11393 | 0.00024345
2013-02-19 | 293919 | SMR15A | Urban | LV Transformer SP5518-F SMR15A - Planned | 1.8 | 76 | 136.8 | 0.00013827 | 1.8194e-06
2013-02-19 | 293920 | TWG17 | Urban | LV Transformer SP4164-K TWG17 - Planned | 28.08 | 145 | 4071.6 | 0.0041155 | 2.8383e-05
2013-02-19 | 293922 | NBR5 | Rural short | LV Transformer SP4046-A NBR5 - Planned | 23.04 | 89 | 2050.56 | 0.005873 | 6.5988e-05
2013-02-19 | 293924 | GYM2A | Rural short | LV Transformer SP974-C GYM2A - Planned | 8.83 | 79 | 697.57 | 0.0019979 | 2.529e-05
2013-02-19 | 293925 | YDA5A | Rural short | LV Transformer SP2847-A YDA5A - Planned | 13.92 | 300 | 4176 | 0.01196 | 3.9868e-05
2013-02-19 | 293926 | PPE5A | Rural short | LV Transformer SP5025-G PPE5A - Planned | 6.075 | 256 | 1555.2 | 0.0044542 | 1.7399e-05
2013-02-19 | 293927 | YTA22B | Rural short | LV Transformer SC1433033 YTA22B - Planned | 4.25 | 55 | 233.75 | 0.00066948 | 1.2172e-05
2013-02-19 | 293928 | NRG16A | Rural short | LV Transformer SP1665-H NRG16A - Planned | 21 | 120 | 2520 | 0.0072175 | 6.0146e-05
2013-02-19 | 293929 | CMA11A | Urban | LV Transformer SP467667 CMA11A - Planned | 2 | 97 | 194 | 0.00019609 | 2.0216e-06
2013-02-19 | 293930 | MAI7 | Urban | LV Transformer SC239-J MAI7 - Planned | 24.655 | 247 | 6089.785 | 0.0061554 | 2.4921e-05
2013-02-19 | 293931 | CCY26A | Urban | LV Transformer SC1401949 CCY26A - Planned | 0.5 | 176 | 88 | 8.8949e-05 | 5.0539e-07
2013-02-19 | 293932 | YTA22B | Rural short | LV Transformer SC1433033 YTA22B - Planned | 25.07 | 31 | 777.17 | 0.0022259 | 7.1802e-05
2013-02-19 | 293933 | WNM2A | Urban | LV Transformer SP2088-J WNM2A - Planned | 23.705 | 320 | 7585.6 | 0.0076674 | 2.3961e-05
2013-02-19 | 293934 | CFD1A | Urban | LV Transformer SG845-L CFD1A - Planned | 39.89 | 330 | 13163.7 | 0.013306 | 4.032e-05
2013-02-19 | 293935 | DRD5A | Urban | LV Transformer SP2764-F DRD5A - Planned | 4.525 | 184 | 832.6 | 0.00084158 | 4.5738e-06
2013-02-19 | 293936 | AGE8 | Urban | LV Transformer SP14717-E GAP8A - Planned | 2.13 | 126 | 268.38 | 0.00027127 | 2.153e-06
2013-02-19 | 293936 | GAP8A | Urban | LV Transformer SP14717-E GAP8A - Planned | 6.05 | 126 | 762.3 | 0.00077052 | 6.1152e-06
2013-02-19 | 293937 | KLG13A | Urban | LV Transformer SP5647-C KLG13A - Planned | 8.19 | 233 | 1908.27 | 0.0019288 | 8.2783e-06
2013-02-19 | 293938 | AGE5B | Urban | LV Transformer SP4179-K AGE5B - Planned | 5.91 | 347 | 2050.77 | 0.0020729 | 5.9737e-06
2013-02-19 | 293939 | HPE5A | Urban | LV Transformer SP9444-G HPE5A - Planned | 43.435 | 291 | 12639.585 | 0.012776 | 4.3903e-05
2013-02-19 | 293940 | MTG8A | Urban | LV Transformer SP801861 MTG8A - Planned | 10.395 | 188 | 1954.26 | 0.0019753 | 1.0507e-05
2013-02-19 | 293942 | WED16A | Urban | LV Transformer SP135-O WED16A - Planned | 10.4665 | 313 | 3276.0145 | 0.0033113 | 1.0579e-05
2013-02-19 | 293943 | WMD13A | Rural short | LV Transformer SP5379-A WMD13A - Planned | 19.95 | 390 | 7780.5 | 0.022284 | 5.7138e-05
2013-02-19 | 294643 | CLD18A | Rural short | LV Transformer SP765223 CLD18A - Planned | 2 | 267 | 534 | 0.0015294 | 5.7281e-06
2013-02-20 | 294010 | WMR2 | Rural short | Feeder WMR2 - Planned | 9 | 86 | 774 | 0.0022166 | 2.5774e-05
2013-02-20 | 294090 | MTB17A | Rural short | Feeder MTB17A - Planned | 19 | 310 | 5890 | 0.016868 | 5.4413e-05
2013-02-20 | 294110 | IPL1 | Rural short | Feeder IPL1 - Planned | 2 | 73 | 146 | 0.00041812 | 5.7276e-06
2013-02-20 | 294133 | CBW11 | Rural short | LV Transformer SP5795-D CBW11 - Planned | 1 | 270 | 270 | 0.00077323 | 2.8638e-06
2013-02-20 | 294134 | PWC4 | Rural short | Feeder PWC4 - Planned | 76.45 | 412 | 31497.4 | 0.090203 | 0.00021894
2013-02-20 | 294135 | CLM9 | Urban | LV Transformer SP5388-A CLM9 - Planned | 130 | 355 | 46150 | 0.046647 | 0.0001314
2013-02-20 | 294136 | GBN4 | Rural short | LV Transformer SP1515-B GBN4 - Planned | 3.5 | 95 | 332.5 | 0.00095222 | 1.0023e-05
2013-02-20 | 294137 | PWC5 | Rural short | LV Transformer SP260-A PWC5 - Planned | 10.12 | 111 | 1123.32 | 0.003217 | 2.8982e-05
2013-02-20 | 294140 | KSN5 | Rural short | LV Transformer SP10502-C KSN5 - Planned | 6.3 | 164 | 1033.2 | 0.0029589 | 1.8042e-05
2013-02-20 | 294141 | PPE6A | Rural short | LV Transformer SC1821425 PPE6A - Planned | 21.08 | 390 | 8221.2 | 0.023544 | 6.0369e-05
2013-02-20 | 294142 | MAI14 | Urban | LV Transformer SP15340-B MAI14 - Planned | 79 | 355 | 28045 | 0.028347 | 7.9851e-05
2013-02-20 | 294143 | AGE10 | Urban | LV Transformer SC772751-A AGE10 - Planned | 8.275 | 181 | 1497.775 | 0.0015139 | 8.3641e-06
2013-02-20 | 294144 | SARSHW9 | Urban | LV Transformer SP3804-I SHW6 - Planned | 11.11 | 295 | 3277.45 | 0.0033127 | 1.123e-05
2013-02-20 | 294144 | SHW6 | Urban | LV Transformer SP3804-I SHW6 - Planned | 4.6751 | 295 | 1379.1545 | 0.001394 | 4.7254e-06
2013-02-20 | 294145 | NVL9 | Rural short | LV Transformer SP6211-B NVL9 - Planned | 17.94 | 352 | 6314.88 | 0.018085 | 5.1377e-05
2013-02-20 | 294146 | RBA1A | Urban | LV Transformer SP3758-E RBA1A - Planned | 53 | 220 | 11660 | 0.011786 | 5.3571e-05
2013-02-20 | 294147 | MGP15A | Rural short | LV Transformer SP5863-D MGP15A - Planned | 4.1 | 392 | 1607.2 | 0.0046027 | 1.1742e-05
2013-02-20 | 294148 | BHL4A | Urban | LV Transformer SP2976-H BHL4A - Planned | 14.98 | 294 | 4404.12 | 0.0044515 | 1.5141e-05
2013-02-20 | 294149 | CFD2A | Urban | LV Transformer SP9353-F CFD2A - Planned | 2.235 | 320 | 715.2 | 0.0007229 | 2.2591e-06
2013-02-20 | 294149 | HDA11A | Urban | LV Transformer SP9353-F CFD2A - Planned | 25.68 | 320 | 8217.6 | 0.0083061 | 2.5957e-05
2013-02-20 | 294150 | DRD5A | Urban | LV Transformer SP2764-F DRD5A - Planned | 4.525 | 185 | 837.125 | 0.00084614 | 4.5737e-06
2013-02-20 | 294151 | WNM2A | Urban | LV Transformer SP2088-J WNM2A - Planned | 17.24 | 320 | 5516.8 | 0.0055762 | 1.7426e-05
2013-02-20 | 294152 | SGT22A | Urban | LV Transformer SC4503-G SGT22A - Planned | 6.12 | 256 | 1566.72 | 0.0015836 | 6.1859e-06
2013-02-20 | 294153 | RBY15 | Urban | LV Transformer SP434-D RBY15 - Planned | 9.4381 | 235 | 2217.9535 | 0.0022418 | 9.5397e-06
2013-02-20 | 294154 | WED21A | Urban | LV Transformer SP6404-C WED21A - Planned | 7.03 | 368 | 2587.04 | 0.0026149 | 7.1057e-06
2013-02-20 | 294155 | BLB2A | Urban | LV Transformer SC2978-H BLB2A - Planned | 1.77 | 290 | 513.3 | 0.00051883 | 1.7891e-06
2013-02-20 | 294156 | HPE5A | Urban | LV Transformer SP2237-M HPE5A - Planned | 2.51 | 322 | 808.22 | 0.00081692 | 2.537e-06
2013-02-20 | 294157 | KSN8 | Rural short | LV Transformer SP6618-E KSN8 - Planned | 11.06 | 95 | 1050.7 | 0.003009 | 3.1674e-05
2013-02-20 | 294158 | TMH15A | Urban | LV Transformer SP3665-D TMH15A - Planned | 5.68 | 330 | 1874.4 | 0.0018946 | 5.7412e-06
2013-02-20 | 294159 | LLY4 | Rural short | LV Transformer SP26534-B LLY4 - Planned | 3 | 375 | 1125 | 0.0032218 | 8.5915e-06
2013-02-21 | 294273 | BTN2 | Rural short | Feeder BTN2 - Planned | 12.04 | 312 | 3756.48 | 0.010757 | 3.4477e-05
2013-02-21 | 294274 | YTA22A | Rural short | Feeder YTA22A - Planned | 25.02 | 145 | 3627.9 | 0.010389 | 7.1647e-05
2013-02-21 | 294275 | ARL13A | Urban | Feeder ARL13A - Planned | 33.49 | 115 | 3851.35 | 0.0038928 | 3.385e-05
2013-02-21 | 294290 | BNH2B | Rural short | Feeder BNH2B - Planned | 6.25 | 254 | 1587.5 | 0.0045459 | 1.7897e-05
2013-02-21 | 294291 | CRB25A | Rural short | Feeder CRB25A - Planned | 29.435 | 275 | 8094.625 | 0.02318 | 8.4289e-05
2013-02-21 | 294292 | BDT3 | Rural short | Feeder BDT3 - Planned | 28.29 | 381 | 10778.49 | 0.030865 | 8.1011e-05
2013-02-21 | 294293 | BHD35A | Rural short | LV Transformer SP5728-E BHD35A - Planned | 4.5 | 51 | 229.5 | 0.00065719 | 1.2886e-05
2013-02-21 | 294330 | CMA8A | Rural short | Feeder CMA8A - Planned | 4 | 499 | 1996 | 0.0057157 | 1.1454e-05
2013-02-21 | 294333 | BMT1 | Rural short | Feeder BMT1 - Planned | 22.73 | 267 | 6068.91 | 0.017379 | 6.5089e-05
2013-02-21 | 294334 | CLM3 | Rural short | Feeder CLM3 - Planned | 18.01 | 369 | 6645.69 | 0.01903 | 5.1573e-05
2013-02-21 | 294335 | GYN3A | Rural short | LV Transformer SP6870-C GYN3A - Planned | 6.45 | 318 | 2051.1 | 0.0058735 | 1.847e-05
2013-02-21 | 294336 | GYGGYS6 | Rural short | LV Transformer SP2634-D GYGGYS6 - Planned | 2.345 | 61 | 143.045 | 0.00040962 | 6.7151e-06
2013-02-21 | 294337 | GBN4 | Rural short | LV Transformer SP5591-B GBN4 - Planned | 6.02 | 24 | 144.48 | 0.00041373 | 1.7239e-05
2013-02-21 | 294338 | GLY1 | Urban | LV Transformer SC1284325 GLY1 - Planned | 10 | 397 | 3970 | 0.0040127 | 1.0108e-05
2013-02-21 | 294339 | BHL2A | Urban | LV Transformer SP2401-J BHL2A - Planned | 26.5 | 248 | 6572 | 0.0066427 | 2.6785e-05
2013-02-21 | 294340 | CBW10 | Rural short | LV Transformer SC2765-H CBW10 - Planned | 52.08 | 345 | 17967.6 | 0.051452 | 0.00014913
2013-02-21 | 294341 | AGE5B | Urban | LV Transformer SP4179-K AGE5B - Planned | 8.865 | 299 | 2650.635 | 0.0026791 | 8.9604e-06
2013-02-21 | 294342 | NBR9 | Rural short | LV Transformer SP2021-A NBR9 - Planned | 4.96 | 107 | 530.72 | 0.0015198 | 1.4203e-05
2013-02-21 | 294343 | GYS5A | Rural short | LV Transformer SP7534-C GYS5A - Planned | 9 | 73 | 657 | 0.0018814 | 2.5772e-05
2013-02-21 | 294344 | CRB25A | Rural short | LV Transformer SP9426-F CRB25A - Planned | 3.105 | 255 | 791.775 | 0.0022673 | 8.8914e-06
2013-02-21 | 294345 | MGP12A | Rural short | LV Transformer SP11265-G MGP12A - Planned | 32.04 | 287 | 9195.48 | 0.026332 | 9.1749e-05
2013-02-21 | 294346 | MTB17A | Rural short | LV Transformer SP5265-G MTB17A - Planned | 5.98 | 399 | 2386.02 | 0.0068325 | 1.7124e-05
2013-02-21 | 294347 | BHL4A | Urban | LV Transformer SP5771-I BHL4A - Planned | 8.85 | 255 | 2256.75 | 0.002281 | 8.9452e-06
2013-02-21 | 294349 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 10.7 | 339 | 3627.3 | 0.0036663 | 1.0815e-05
2013-02-21 | 294350 | DRD13A | Urban | LV Transformer SP3086-F DRD13A - Planned | 13.8128 | 269 | 3715.6432 | 0.0037556 | 1.3961e-05
2013-02-21 | 294351 | WRD20A | Urban | LV Transformer SC5829-E WRD20A - Planned | 59.29 | 400 | 23716 | 0.023971 | 5.9928e-05
2013-02-21 | 294352 | HPE5A | Urban | LV Transformer SP37841-D HPE5A - Planned | 14.655 | 272 | 3986.16 | 0.004029 | 1.4813e-05
2013-02-21 | 294354 | CPL5A | Urban | LV Transformer SG6545-I CPL5A - Planned | 12.96 | 123 | 1594.08 | 0.0016112 | 1.3099e-05
2013-02-21 | 294355 | NIP5A | Urban | LV Transformer SP1446-H NIP5A - Planned | 23.76 | 343 | 8149.68 | 0.0082373 | 2.4016e-05
2013-02-21 | 294356 | GGR1 | Rural short | LV Transformer SP3021-C GGR1 - Planned | 3.35 | 295 | 988.25 | 0.0028299 | 9.593e-06
2013-02-21 | 294357 | LLY1 | Rural short | LV Transformer SP1327-C LLY1 - Planned | 5.395 | 207 | 1116.765 | 0.0031979 | 1.5449e-05
2013-02-21 | 294603 | GAP8A | Urban | LV Transformer SP775351 GAP8A - Planned | 25.415 | 287 | 7294.105 | 0.0073726 | 2.5688e-05
2013-02-21 | 294612 | SPD11A | Urban | LV Transformer SP2310-G SPD11A - Planned | 70.67 | 636 | 44946.12 | 0.04543 | 7.143e-05
2013-02-21 | 294644 | MTB17A | Rural short | Feeder MTB17A - Planned | 23.5 | 434 | 10199 | 0.029206 | 6.7294e-05
2013-02-22 | 294390 | MTB1B | Rural short | LV Transformer SP6074-B MTB1B - Planned | 21.5 | 60 | 1290 | 0.0036937 | 6.1561e-05
2013-02-22 | 294510 | BNH6A | Rural short | LV Transformer SP2513-F BNH6A - Planned | 2 | 310 | 620 | 0.0017753 | 5.7266e-06
2013-02-22 | 294511 | KCY4 | Rural short | LV Transformer SP3582-D KCY4 - Planned | 3 | 266 | 798 | 0.0022849 | 8.5899e-06
2013-02-22 | 294530 | WSO12B | Rural short | Feeder WSO12B - Planned | 27 | 207 | 5589 | 0.016003 | 7.7309e-05
2013-02-22 | 294550 | TGW2 | Rural short | Feeder TGW2 - Planned | 5.98 | 280 | 1674.4 | 0.0047943 | 1.7123e-05
2013-02-22 | 294551 | KBR6A | Rural short | Feeder KBR6A - Planned | 9.54 | 322 | 3071.88 | 0.0087957 | 2.7316e-05
2013-02-22 | 294552 | RLB16A | Rural short | Feeder RLB16A - Planned | 19.28 | 360 | 6940.8 | 0.019874 | 5.5205e-05
2013-02-22 | 294601 | ENG2 | Urban | LV Transformer SP763994 ENG2 - Planned | 23.1 | 180 | 4158 | 0.0042027 | 2.3348e-05
2013-02-22 | 294604 | TCB2 | Rural short | LV Transformer SP5939-A TCB2 - Planned | 0.87 | 272 | 236.64 | 0.00067757 | 2.4911e-06
2013-02-22 | 294605 | TCB1 | Rural short | LV Transformer SP6553-B TCB1 - Planned | 41.695 | 201 | 8380.695 | 0.023997 | 0.00011939
2013-02-22 | 294608 | MAI17 | Urban | LV Transformer SP2244-F MAI17 - Planned | 13.5852 | 311 | 4224.9972 | 0.0042704 | 1.3731e-05
2013-02-22 | 294609 | SPD7B | Urban | LV Transformer SC22758-C SPD7B - Planned | 3.2799 | 22 | 72.1578 | 7.2933e-05 | 3.3151e-06
2013-02-22 | 294610 | SPO55A | Urban | LV Transformer SC1063981 SPO55A - Planned | 21.9 | 109 | 2387.1 | 0.0024128 | 2.2135e-05
2013-02-22 | 294611 | MMC19B | Urban | LV Transformer SP1110-K MMC19B - Planned | 3.8664 | 27 | 104.3928 | 0.00010551 | 3.9079e-06
2013-02-22 | 294613 | HWL1A | Urban | LV Transformer SP2885-F HWL1A - Planned | 29.915 | 82 | 2453.03 | 0.0024794 | 3.0236e-05
2013-02-22 | 294615 | BHD1A | Urban | LV Transformer SP59315-B PBH6 - Planned | 5.775 | 336 | 1940.4 | 0.0019613 | 5.8371e-06
2013-02-22 | 294615 | PBH6 | Urban | LV Transformer SP59315-B PBH6 - Planned | 4.095 | 336 | 1375.92 | 0.0013907 | 4.139e-06
2013-02-22 | 294616 | BHL4A | Urban | LV Transformer SP1753-I BHL4A - Planned | 3.7 | 258 | 954.6 | 0.00096486 | 3.7398e-06
2013-02-22 | 294618 | DRD13A | Urban | LV Transformer SP3553-F DRD13A - Planned | 3.975 | 76 | 302.1 | 0.00030535 | 4.0177e-06
2013-02-22 | 294619 | MCW11 | Rural short | LV Transformer SP3647-D MCW11 - Planned | 5 | 290 | 1450 | 0.0041518 | 1.4317e-05
2013-02-22 | 294624 | IBL2 | Rural short | Feeder IBL2 - Planned | 34.447 | 381 | 13124.307 | 0.037579 | 9.8632e-05
2013-02-22 | 294626 | GYM2A | Rural short | Feeder GYM2A - Planned | 39.455 | 249 | 9824.295 | 0.02813 | 0.00011297
2013-02-22 | 294696 | HTL14A | Urban | LV Transformer SC4578-I HTL14A - Planned | 1 | 2910 | 2910 | 0.0029413 | 1.0107e-06
2013-02-23 | 294657 | HMT10A | Urban | LV Transformer SP2505-M HMT10A - Planned | 13.2 | 53 | 699.6 | 0.00070711 | 1.3342e-05
2013-02-24 | 294691 | BBH10A | Urban | LV Transformer SC741233 BBH10A - Planned | 10.74 | 130 | 1396.2 | 0.0014112 | 1.0855e-05
2013-02-24 | 294692 | BHD41A | Urban | LV Transformer SP2488-H BHD41A - Planned | 2.28 | 468 | 1067.04 | 0.0010785 | 2.3044e-06
2013-02-24 | 294693 | BGY15A | Urban | LV Transformer SP10350-D BGY15A - Planned | 25.11 | 213 | 5348.43 | 0.0054057 | 2.5379e-05
2013-02-24 | 294694 | WFD6A | Rural short | LV Transformer SP3665-G WFD6A - Planned | 2 | 343 | 686 | 0.001964 | 5.7258e-06
2013-02-24 | 294695 | NDH7 | Urban | LV Transformer SC22036-E NDH7 - Planned | 2.1 | 51 | 107.1 | 0.00010825 | 2.1225e-06
2013-02-24 | 294697 | SPE9 | Urban | LV Transformer SC737524 SPE9 - Planned | 2 | 61 | 122 | 0.00012331 | 2.0214e-06
2013-02-24 | 294698 | HTN22B | Urban | LV Transformer SC818501 HTN22B - Planned | 2.03 | 221 | 448.63 | 0.00045344 | 2.0518e-06
2013-02-24 | 294699 | NGE13 | Urban | LV Transformer SC22009-G NGE13 - Planned | 7 | 44 | 308 | 0.0003113 | 7.075e-06
2013-02-24 | 294700 | DRD3A | Urban | LV Transformer SP3552-F DRD3A - Planned | 53.745 | 383 | 20584.335 | 0.020805 | 5.4321e-05
2013-02-24 | 294703 | ABT7 | Urban | Feeder ABTQPT95, ABTQPT3 - Planned | 2 | 937 | 1874 | 0.0018941 | 2.0214e-06
2013-02-24 | 294703 | ABT8 | Urban | Feeder ABTQPT95, ABTQPT3 - Planned | 3 | 937 | 2811 | 0.0028411 | 3.0321e-06
2013-02-24 | 295777 | MDH9A | Urban | LV Transformer SC5743-E MDH9A - Planned | 1 | 515 | 515 | 0.00052052 | 1.0107e-06
2013-02-25 | 294790 | MTB3A | Rural short | LV Transformer SP10024-E MTB3A - Planned | 21.33 | 226 | 4820.58 | 0.013799 | 6.1058e-05
2013-02-25 | 294850 | MMC28A | Urban | LV Transformer SP6396-C MMC28A - Planned | 2.5 | 399 | 997.5 | 0.0010082 | 2.5267e-06
2013-02-25 | 294870 | GBN3 | Rural short | Feeder GBN3 - Planned | 100.465 | 424 | 42597.16 | 0.12194 | 0.00028758
2013-02-25 | 294872 | SPD2B | Urban | LV Transformer SC735097 SPD2B - Planned | 21.06 | 42 | 884.52 | 0.00089397 | 2.1285e-05
2013-02-25 | 294873 | BDL4 | Urban | LV Transformer SP15885-D BDL4 - Planned | 10.3998 | 60 | 623.988 | 0.00063066 | 1.0511e-05
2013-02-25 | 294874 | DBS4A | Urban | LV Transformer SP1921-J MRE3 - Planned | 9.024 | 350 | 3158.4 | 0.0031922 | 9.1204e-06
2013-02-25 | 294874 | MRE3 | Urban | LV Transformer SP1921-J MRE3 - Planned | 2.766 | 350 | 968.1 | 0.00097845 | 2.7956e-06
2013-02-25 | 294875 | MTG13A | Urban | LV Transformer SC7922-D MTG13A - Planned | 3.45 | 69 | 238.05 | 0.00024059 | 3.4869e-06
2013-02-25 | 294930 | DRA1A | Urban | LV Transformer SG1107-L DRA1A - Planned | 1 | 8 | 8 | 8.0855e-06 | 1.0107e-06
2013-02-26 | 294990 | PPE5A | Rural short | LV Transformer SP6286-E PPE5A - Planned | 2 | 91 | 182 | 0.00052094 | 5.7246e-06
2013-02-26 | 295030 | BMT1 | Rural short | LV Transformer SP9363-B BMT1 - Planned | 9 | 230 | 2070 | 0.005925 | 2.5761e-05
2013-02-26 | 295074 | NVL12A | Urban | LV Transformer SP1040-F NVL12A - Planned | 155.5 | 168 | 26124 | 0.026403 | 0.00015716
2013-02-26 | 295076 | AHL4A | Urban | LV Transformer SC1059-S AHL4A - Planned | 18.055 | 251 | 4531.805 | 0.0045802 | 1.8248e-05
2013-02-26 | 295077 | WCL10A | Urban | LV Transformer SP698-J WCL10A - Planned | 33.565 | 152 | 5101.88 | 0.0051563 | 3.3923e-05
2013-02-26 | 295078 | NBR9 | Rural short | LV Transformer SP4534-B NBR9 - Planned | 6.08 | 290 | 1763.2 | 0.0050468 | 1.7403e-05
2013-02-26 | 295079 | MAI11 | Urban | LV Transformer SP2886-F MAI11 - Planned | 56.5 | 360 | 20340 | 0.020557 | 5.7103e-05
2013-02-26 | 295080 | BDL2 | Urban | LV Transformer SC758109 BDL2 - Planned | 1 | 40 | 40 | 4.0427e-05 | 1.0107e-06
2013-02-26 | 295081 | SPD29A | Urban | LV Transformer SC22771-E SPD29A - Planned | 10.88 | 20 | 217.6 | 0.00021992 | 1.0996e-05
2013-02-26 | 295082 | MAI17 | Urban | LV Transformer SP4622-F MAI17 - Planned | 16.0404 | 392 | 6287.8368 | 0.0063549 | 1.6212e-05
2013-02-26 | 295083 | MRE3 | Urban | LV Transformer SP1921-J MRE3 - Planned | 4.61 | 265 | 1221.65 | 0.0012347 | 4.6592e-06
2013-02-26 | 295084 | CBW7 | Rural short | LV Transformer SC2446-G CBW7 - Planned | 1.12 | 41 | 45.92 | 0.00013144 | 3.2058e-06
2013-02-26 | 295085 | BHL4A | Urban | LV Transformer SP1753-I BHL4A - Planned | 0.74 | 345 | 255.3 | 0.00025802 | 7.479e-07
2013-02-26 | 295086 | EMP21A | Rural short | LV Transformer SP3655-M EMP21A - Planned | 27.73 | 190 | 5268.7 | 0.015081 | 7.9372e-05
2013-02-26 | 295087 | KSN8 | Rural short | LV Transformer SP4929-D KSN8 - Planned | 15.81 | 150 | 2371.5 | 0.006788 | 4.5253e-05
2013-02-27 | 295193 | CPD2A | Rural short | LV Transformer SP647-B CPD2A - Planned | 4.98 | 140 | 697.2 | 0.0019955 | 1.4253e-05
2013-02-27 | 295313 | PWC4 | Rural short | Feeder PWC4 - Planned | 7.5 | 420 | 3150 | 0.0090157 | 2.1466e-05
2013-02-27 | 295314 | BHD35A | Rural short | Feeder BHD35A - Planned | 21 | 376 | 7896 | 0.022599 | 6.0105e-05
2013-02-27 | 295317 | MTB3A | Rural short | LV Transformer SP6520-E MTB3A - Planned | 13 | 405 | 5265 | 0.015069 | 3.7208e-05
2013-02-27 | 295319 | BHD35A | Rural short | Feeder BHD35A - Planned | 30.4 | 273 | 8299.2 | 0.023753 | 8.7009e-05
2013-02-27 | 295332 | NBR5 | Rural short | LV Transformer SP2504-A NBR5 - Planned | 16.425 | 330 | 5420.25 | 0.015514 | 4.7011e-05
2013-02-27 | 295333 | SPO3A | Urban | LV Transformer SP3485-E SPO3A - Planned | 8.9463 | 216 | 1932.4008 | 0.001953 | 9.0415e-06
2013-02-27 | 295334 | NRG8B | Urban | LV Transformer SC657335 NRG8B - Planned | 1.9625 | 60 | 117.75 | 0.000119 | 1.9834e-06
2013-02-27 | 295335 | MTB3A | Rural short | LV Transformer SP1835-F MTB3A - Planned | 12.42 | 392 | 4868.64 | 0.013935 | 3.5548e-05
2013-02-27 | 295336 | MHL13A | Urban | LV Transformer SC580939-A MHL13A - Planned | 6.3275 | 60 | 379.65 | 0.00038369 | 6.3948e-06
2013-02-27 | 295337 | NGE4A | Urban | LV Transformer SC1050855 NGE4A - Planned | 2.03 | 51 | 103.53 | 0.00010463 | 2.0516e-06
2013-02-27 | 295338 | DRD13A | Urban | LV Transformer SP5770-D DRD13A - Planned | 18.24 | 50 | 912 | 0.00092171 | 1.8434e-05
2013-02-27 | 295339 | DRD13A | Urban | LV Transformer SP3086-F DRD13A - Planned | 10.3596 | 113 | 1170.6348 | 0.0011831 | 1.047e-05
2013-02-27 | 295340 | HWD5A | Rural short | LV Transformer SC2059718 HWD5A - Planned | 2.88 | 126 | 362.88 | 0.0010386 | 8.243e-06
2013-02-27 | 295341 | LHM5 | Rural short | LV Transformer SP13851-A LHM5 - Planned | 9.02 | 248 | 2236.96 | 0.0064025 | 2.5816e-05
2013-02-27 | 295342 | TWG17 | Urban | LV Transformer SC475-R TWG17 - Planned | 20.02 | 237 | 4744.74 | 0.0047952 | 2.0233e-05
2013-02-27 | 295343 | GAP8A | Urban | LV Transformer SP3703-J GAP8A - Planned | 6.02 | 434 | 2612.68 | 0.0026405 | 6.0841e-06
2013-02-27 | 295345 | MLY3 | Rural short | LV Transformer SP781316 MLY3 - Planned | 9 | 160 | 1440 | 0.0041215 | 2.5759e-05
2013-02-27 | 295346 | CLD2 | Urban | LV Transformer SP4038-A CLD2 - Planned | 25.0124 | 115 | 2876.426 | 0.002907 | 2.5279e-05
2013-02-27 | 295347 | BHL1A | Urban | LV Transformer SC4276-J BHL1A - Planned | 36.08 | 145 | 5231.6 | 0.0052873 | 3.6464e-05
2013-02-27 | 295348 | CBT13A | Urban | LV Transformer SC21075-C CBT13A - Planned | 10.92 | 60 | 655.2 | 0.00066217 | 1.1036e-05
2013-02-27 | 295350 | AHL4A | Urban | LV Transformer SP4979-I AHL4A - Planned | 12.21 | 330 | 4029.3 | 0.0040722 | 1.234e-05
2013-02-27 | 295351 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 2.14 | 318 | 680.52 | 0.00068776 | 2.1628e-06
2013-02-27 | 295353 | MHL13A | Urban | LV Transformer SC583323 MHL13A - Planned | 13.08 | 73 | 954.84 | 0.000965 | 1.3219e-05
2013-02-27 | 295354 | DRD5A | Urban | LV Transformer SC509-F DRD5A - Planned | 20.43 | 125 | 2553.75 | 0.0025809 | 2.0647e-05
2013-02-27 | 295355 | CHL5 | Urban | LV Transformer SP716-L CHL5 - Planned | 30.48 | 252 | 7680.96 | 0.0077627 | 3.0804e-05
2013-02-27 | 295355 | SRD14A | Urban | LV Transformer SP716-L CHL5 - Planned | 21.08 | 252 | 5312.16 | 0.0053687 | 2.1304e-05
2013-02-27 | 295356 | LGL15A | Urban | LV Transformer SP6539-F LGL15A - Planned | 66.36 | 340 | 22562.4 | 0.022803 | 6.7066e-05
2013-02-27 | 295357 | CPD2A | Rural short | LV Transformer SP647-B CPD2A - Planned | 4.98 | 224 | 1115.52 | 0.0031928 | 1.4253e-05
2013-02-28 | 295430 | CVL7A | Rural short | LV Transformer SP1800-F CVL7A - Planned | 8 | 221 | 1768 | 0.00506 | 2.2896e-05
2013-02-28 | 295452 | JBB12B | Rural short | LV Transformer SP6836-D JBB12B - Planned | 2.25 | 70 | 157.5 | 0.00045076 | 6.4395e-06
2013-02-28 | 295490 | MCW11 | Rural short | LV Transformer SP5171-E MCW11 - Planned | 9 | 285 | 2565 | 0.007341 | 2.5758e-05
2013-02-28 | 295510 | WHO1 | Rural short | LV Transformer SP25604-A WHO1 - Planned | 7 | 325 | 2275 | 0.006511 | 2.0034e-05
2013-02-28 | 295532 | IPL1 | Rural short | LV Transformer SP4413-D IPL1 - Planned | 1.34 | 180 | 241.2 | 0.00069031 | 3.8351e-06
2013-02-28 | 295550 | MLY1 | Rural short | Feeder MLY1 - Planned | 45.722 | 217 | 9921.674 | 0.028396 | 0.00013086
2013-02-28 | 295570 | BDT1 | Rural short | Feeder BDT1 - Planned | 64 | 225 | 14400 | 0.041213 | 0.00018317
2013-02-28 | 295590 | MCN2 | Rural short | Feeder MCN2 - Planned | 18.505 | 410 | 7587.05 | 0.021714 | 5.2961e-05
2013-02-28 | 295594 | CBT12A | Rural short | Feeder CBT12A - Planned | 45 | 450 | 20250 | 0.057955 | 0.00012879
2013-02-28 | 295615 | CRB25A | Rural short | LV Transformer SP760627 CRB25A - Planned | 20.9 | 655 | 13689.5 | 0.039179 | 5.9815e-05
2013-02-28 | 295616 | LGV2B | Rural short | LV Transformer SP105401 - Planned | 26.87 | 319 | 8571.53 | 0.024532 | 7.6901e-05
2013-02-28 | 295617 | MTB3A | Rural short | LV Transformer SC560171 MTB3A - Planned | 7.92 | 310 | 2455.2 | 0.0070267 | 2.2667e-05
2013-02-28 | 295618 | SFD10 | Urban | LV Transformer SC1500244 SFD10 - Planned | 13.395 | 272 | 3643.44 | 0.0036821 | 1.3537e-05
2013-02-28 | 295618 | SFD3 | Urban | LV Transformer SC1500244 SFD10 - Planned | 0.855 | 272 | 232.56 | 0.00023503 | 8.6408e-07
2013-02-28 | 295618 | SFD5 | Urban | LV Transformer SC1500244 SFD10 - Planned | 1.155 | 272 | 314.16 | 0.0003175 | 1.1673e-06
2013-02-28 | 295619 | KRN12 | Urban | LV Transformer SC1980-L KRN12 - Planned | 61.46 | 552 | 33925.92 | 0.034286 | 6.2113e-05
2013-02-28 | 295620 | NMK7 | Urban | LV Transformer SP15029-F NMK7 - Planned | 6.9 | 281 | 1938.9 | 0.0019595 | 6.9733e-06
2013-02-28 | 295621 | MTB17A | Rural short | LV Transformer SP5265-G MTB17A - Planned | 7.02 | 435 | 3053.7 | 0.0087396 | 2.0091e-05
2013-02-28 | 295622 | BBH3A | Urban | LV Transformer SC1258-F BBH3A - Planned | 1.13 | 217 | 245.21 | 0.00024781 | 1.142e-06
2013-02-28 | 295623 | MTB17A | Rural short | LV Transformer SP4995-G MTB17A - Planned | 10.72 | 263 | 2819.36 | 0.008069 | 3.068e-05
2013-02-28 | 295624 | BLH13B | Rural short | LV Transformer SP4088-C BLH13B - Planned | 3 | 157 | 471 | 0.001348 | 8.5859e-06
2013-02-28 | 295625 | MHL13A | Urban | LV Transformer SC583504 MHL13A - Planned | 4.01 | 65 | 260.65 | 0.00026342 | 4.0526e-06
2013-02-28 | 295626 | SGT7 | Urban | LV Transformer SP4735-E SGT7 - Planned | 5.1983 | 346 | 1798.6118 | 0.0018177 | 5.2535e-06
2013-02-28 | 295627 | FGBSGT23 | Urban | LV Transformer SP5008-I FGBSGT23 - Planned | 1 | 68 | 68 | 6.8722e-05 | 1.0106e-06
2013-02-28 | 295628 | BHL4A | Urban | LV Transformer SP972-H BHL4A - Planned | 7.36 | 215 | 1582.4 | 0.0015992 | 7.4381e-06
2013-02-28 | 295629 | MHL13A | Urban | LV Transformer SC583323 MHL13A - Planned | 8.48 | 62.5 | 826.8 | 0.00083558 | 8.57e-06
2013-02-28 | 295630 | ALY6 | Urban | LV Transformer SC4738-F ALY6 - Planned | 8.96 | 273 | 2446.08 | 0.0024721 | 9.0551e-06
2013-02-28 | 295631 | MHL3A | Urban | LV Transformer SC584137 MHL3A - Planned | 5.67 | 35 | 220.02 | 0.00022236 | 5.7302e-06
2013-02-28 | 295632 | WCL11A | Urban | LV Transformer SP3526-I WCL19A - Planned | 7.92 | 275 | 2178 | 0.0022011 | 8.0041e-06
2013-02-28 | 295632 | WCL19A | Rural short | LV Transformer SP3526-I WCL19A - Planned | 19.02 | 275 | 5230.5 | 0.01497 | 5.4435e-05
2013-02-28 | 295763 | SGT22A | Urban | LV Transformer SP762623 SGT22A - Planned | 0.96 | 383 | 367.68 | 0.00037158 | 9.7019e-07
2013-03-01 | 295690 | GGR1 | Rural short | LV Transformer SP492-B GGR1 - Planned | 1.165 | 21 | 24.465 | 7.0017e-05 | 3.3341e-06
2013-03-01 | 295691 | CVL7A | Rural short | LV Transformer SP9006-B CVL7A - Planned | 18 | 249 | 4482 | 0.012827 | 5.1514e-05
2013-03-01 | 295710 | MTB3A | Rural short | Feeder MTB3A - Planned | 65 | 378 | 24570 | 0.070317 | 0.00018602
2013-03-01 | 295731 | WCL5A | Urban | LV Transformer SP3926-G WCL5A - Planned | 1 | 103 | 103 | 0.00010409 | 1.0106e-06
2013-03-01 | 295735 | MLY1 | Rural short | LV Transformer SP4604-A MLY1 - Planned | 4.4 | 195 | 858 | 0.0024555 | 1.2592e-05
2013-03-01 | 295736 | NBR5 | Rural short | LV Transformer SP3810-A NBR5 - Planned | 18 | 50 | 900 | 0.0025757 | 5.1514e-05
2013-03-01 | 295737 | NSW5A | Urban | LV Transformer SP3553-L NSW5A - Planned | 15.01 | 285 | 4277.85 | 0.0043231 | 1.5169e-05
2013-03-01 | 295738 | CHL2 | Urban | LV Transformer SP540-I CHL2 - Planned | 8.64 | 264 | 2280.96 | 0.0023051 | 8.7314e-06
2013-03-01 | 295739 | CHL7 | Urban | LV Transformer SP2881-J MRE2 - Planned | 1.27 | 208 | 264.16 | 0.00026696 | 1.2834e-06
2013-03-01 | 295739 | MRE2 | Urban | LV Transformer SP2881-J MRE2 - Planned | 5.1798 | 208 | 1077.3984 | 0.0010888 | 5.2346e-06
2013-03-01 | 295740 | NMC1B | Rural short | LV Transformer SC2772-I NMC1B - Planned | 1.11 | 225 | 249.75 | 0.00071476 | 3.1767e-06
2013-03-01 | 295741 | WED21A | Urban | LV Transformer SP6404-C WED21A - Planned | 1.11 | 25 | 27.75 | 2.8044e-05 | 1.1217e-06
2013-03-01 | 295742 | HPK3A | Urban | LV Transformer SP5225-K HPK3A - Planned | 6.93 | 298 | 2065.14 | 0.002087 | 7.0033e-06
2013-03-01 | 295742 | MTG4B | Urban | LV Transformer SP5225-K HPK3A - Planned | 10.505 | 298 | 3130.49 | 0.0031636 | 1.0616e-05
2013-03-01 | 295743 | WED6A | Urban | LV Transformer SC3413-G WED6A - Planned | 2.68 | 248 | 664.64 | 0.00067167 | 2.7084e-06
2013-03-01 | 295745 | GLY6 | Urban | LV Transformer SC1883-M GLY6 - Planned | 16.1 | 178 | 2865.8 | 0.0028961 | 1.627e-05
2013-03-01 | 295747 | YDA5A | Rural short | LV Transformer SP2847-A YDA5A - Planned | 7.2 | 207 | 1490.4 | 0.0042654 | 2.0606e-05
2013-03-01 | 295748 | MLY1 | Rural short | LV Transformer SP162324 MLY1 - Planned | 6 | 146 | 876 | 0.002507 | 1.7171e-05
2013-03-01 | 295749 | KWA6A | Urban | LV Transformer SP4470-B KWA6A - Planned | 22.3125 | 363 | 8099.4375 | 0.0081852 | 2.2549e-05
2013-03-01 | 295750 | CRB24B | Urban | LV Transformer SP11103-F CRB24B - Planned | 0.94 | 35 | 32.9 | 3.3248e-05 | 9.4995e-07
2013-03-01 | 295751 | CRB24B | Urban | LV Transformer SP2525-H CRB24B - Planned | 10.5 | 40 | 420 | 0.00042444 | 1.0611e-05
2013-03-01 | 295752 | KRA7 | Urban | LV Transformer SP2995-G KRA7 - Planned | 1.86 | 70 | 130.2 | 0.00013158 | 1.8797e-06
2013-03-01 | 295753 | MHL13A | Urban | LV Transformer SC581252 MHL13A - Planned | 127.36 | 49 | 6240.64 | 0.0063067 | 0.00012871
2013-03-01 | 295755 | MHL13A | Urban | LV Transformer SC585097 MHL3A - Planned | 3.64 | 19 | 78.26 | 7.9088e-05 | 3.6785e-06
2013-03-01 | 295755 | MHL3A | Urban | LV Transformer SC585097 MHL3A - Planned | 1.71 | 5 | 8.55 | 8.6405e-06 | 1.7281e-06
2013-03-01 | 295756 | MDH5A | Urban | LV Transformer SC23665-G MDH5A - Planned | 1 | 30 | 30 | 3.0317e-05 | 1.0106e-06
2013-03-01 | 295757 | SGT7 | Urban | LV Transformer SC6190-E SGT7 - Planned | 2.4066 | 370 | 890.442 | 0.00089987 | 2.4321e-06
2013-03-01 | 295758 | MHL13A | Urban | LV Transformer SC585097 MHL3A - Planned | 0.91 | 70 | 63.7 | 6.4374e-05 | 9.1963e-07
2013-03-01 | 295758 | MHL3A | Urban | LV Transformer SC585097 MHL3A - Planned | 6.84 | 70 | 478.8 | 0.00048387 | 6.9124e-06
2013-03-01 | 295759 | DBS4A | Urban | LV Transformer SP43959-D DBS4A - Planned | 12.096 | 311 | 3761.856 | 0.0038017 | 1.2224e-05
2013-03-01 | 295759 | MRE3 | Urban | LV Transformer SP43959-D DBS4A - Planned | 2.766 | 311 | 860.226 | 0.00086933 | 2.7953e-06
2013-03-01 | 295760 | MHL3A | Urban | LV Transformer SC585097 MHL3A - Planned | 6.84 | 63 | 430.92 | 0.00043548 | 6.9124e-06
2013-03-01 | 295761 | HTN7B | Urban | LV Transformer SC22025-F HTN7B - Planned | 1.83 | 42 | 76.86 | 7.7673e-05 | 1.8494e-06
2013-03-01 | 295762 | MHL13A | Urban | LV Transformer SC587067 MHL13A - Planned | 17.97 | 40.6667 | 982.66 | 0.00099306 | 1.816e-05
2013-03-01 | 295764 | MHL13A | Urban | LV Transformer SC587067 MHL13A - Planned | 5.98 | 48 | 287.04 | 0.00029008 | 6.0433e-06
2013-03-01 | 295765 | RPN6A | Rural short | LV Transformer SP11771-D RPN6A - Planned | 36.295 | 269 | 9763.355 | 0.027942 | 0.00010387
2013-03-02 | 295796 | JDL4A | Urban | LV Transformer SC4809-I JDL4A - Planned | 8.7996 | 295 | 2595.882 | 0.0026233 | 8.8925e-06
2013-03-02 | 295798 | WRD21A | Urban | LV Transformer SC809978 WRD21A - Planned | 1 | 335 | 335 | 0.00033854 | 1.0106e-06
2013-03-02 | 295812 | WFD3A | Rural short | Feeder WFD3A - Planned | 8 | 124 | 992 | 0.002839 | 2.2895e-05
2013-03-03 | 295840 | AGE2 | Urban | LV Transformer SP1239-M AGE2 - Planned | 16.33 | 128 | 2090.24 | 0.0021123 | 1.6502e-05
2013-03-03 | 295841 | DRD5A | Urban | LV Transformer SP17310-E DRD5A - Planned | 2.22 | 276 | 612.72 | 0.00061919 | 2.2434e-06
2013-03-03 | 295842 | BDA12B | Urban | LV Transformer SP123-N BDA12B - Planned | 16.45 | 340 | 5593 | 0.005652 | 1.6624e-05
2013-03-03 | 295843 | MDH5A | Urban | LV Transformer SG1531-G MDH5A - Planned | 1 | 549 | 549 | 0.00055479 | 1.0106e-06
2013-03-03 | 295849 | HTL3A | Urban | Feeder HTL3A, MDH3A - Planned | 0.4 | 232.5 | 186 | 0.00018796 | 4.0422e-07
2013-03-03 | 295849 | MDH3A | Urban | Feeder HTL3A, MDH3A - Planned | 6.67 | 530 | 3535.1 | 0.0035724 | 6.7404e-06
2013-03-04 | 295910 | BNH6A | Rural short | LV Transformer SP2918-F BNH6A - Planned | 1 | 42 | 42 | 0.00012022 | 2.8624e-06
2013-03-04 | 295911 | TGW2 | Rural short | LV Transformer SP8350-A TGW2 - Planned | 5 | 85 | 425 | 0.0012165 | 1.4312e-05
2013-03-04 | 295971 | WHO1 | Rural short | LV Transformer SP3738-B WHO1 - Planned | 4.98 | 162 | 806.76 | 0.0023093 | 1.4255e-05
2013-03-04 | 296030 | WMD8B | Rural short | LV Transformer SP2259-A WMD8B - Planned | 29.61 | 318 | 9415.98 | 0.026952 | 8.4755e-05
2013-03-04 | 296050 | KMR19A | Urban | LV Transformer SP32153-E KMR19A - Planned | 7 | 95 | 665 | 0.00067194 | 7.073e-06
2013-03-04 | 296051 | KCY5 | Rural short | Feeder KCY5 - Planned | 6.9 | 308 | 2125.2 | 0.0060831 | 1.975e-05
2013-03-04 | 296070 | FDS3 | Rural short | Feeder FDS3 - Planned | 13 | 311 | 4043 | 0.011573 | 3.7211e-05
2013-03-04 | 296091 | NRA13A | Rural short | LV Transformer SP5850-B NRA13A - Planned | 3 | 391 | 1173 | 0.0033576 | 8.5871e-06
2013-03-04 | 296092 | NSD9A | Urban | LV Transformer SP10731-J NSD9A - Planned | 3.3 | 110 | 363 | 0.00036679 | 3.3344e-06
2013-03-04 | 296093 | DRA8 | Urban | LV Transformer SG798487 DRA8 - Planned | 13.49 | 272 | 3669.28 | 0.0037076 | 1.3631e-05
2013-03-04 | 296095 | CLM9 | Urban | LV Transformer SP2718-A CLM9 - Planned | 119.295 | 405 | 48314.475 | 0.048818 | 0.00012054
2013-03-04 | 296096 | NBR6 | Rural short | LV Transformer SP2110-A NBR6 - Planned | 5.28 | 185 | 976.8 | 0.002796 | 1.5113e-05
2013-03-04 | 296097 | GYM7A | Rural short | LV Transformer SP3378-A GYM7A - Planned | 12 | 266 | 3192 | 0.0091367 | 3.4349e-05
2013-03-04 | 296098 | BMT2 | Rural short | LV Transformer SP85-C BMT2 - Planned | 8.1 | 246 | 1992.6 | 0.0057036 | 2.3185e-05
2013-03-04 | 296099 | MAI14 | Urban | LV Transformer SP9972-D MAI14 - Planned | 9.2 | 308 | 2833.6 | 0.0028632 | 9.296e-06
2013-03-04 | 296100 | QPT21 | Urban | LV Transformer SC517665-B QPT21 - Planned | 9.1875 | 47 | 431.8125 | 0.00043632 | 9.2833e-06
2013-03-04 | 296102 | BHL4A | Urban | LV Transformer SP1753-I BHL4A - Planned | 5.46 | 264 | 1441.44 | 0.0014565 | 5.517e-06
2013-03-04 | 296103 | DRD15B | Urban | LV Transformer SP2203-E DRD15B - Planned | 16.15 | 128 | 2067.2 | 0.0020888 | 1.6318e-05
2013-03-04 | 296104 | NSW5A | Urban | LV Transformer SP4412-J NSW5A - Planned | 47.11 | 370 | 17430.7 | 0.017613 | 4.7601e-05
2013-03-04 | 296105 | BNH1B | Rural short | LV Transformer SP3778-C BNH1B - Planned | 3 | 67 | 201 | 0.00057534 | 8.5871e-06
2013-03-04 | 296119 | DBS4A | Urban | LV Transformer SG3405-I DBS4A - Planned | 1 | 125 | 125 | 0.0001263 | 1.0104e-06
2013-03-04 | 296407 | MGP15A | Rural short | LV Transformer SP5847-C MGP15A - Planned | 9 | 49 | 441 | 0.0012623 | 2.5761e-05
2013-03-05 | 296170 | LBH6A | Rural short | LV Transformer SP6582-A LBH6A - Planned | 30.555 | 58 | 1772.19 | 0.0050733 | 8.747e-05
2013-03-05 | 296190 | GBN4 | Rural short | LV Transformer SP1517-E GBN4 - Planned | 1.25 | 198 | 247.5 | 0.00070852 | 3.5784e-06
2013-03-05 | 296211 | MTB17A | Rural short | Feeder MTB17A - Planned | 37 | 320 | 11840 | 0.033894 | 0.00010592
2013-03-05 | 296212 | NBR5 | Rural short | Feeder NBR5 - Planned | 2 | 193 | 386 | 0.001105 | 5.7254e-06
2013-03-05 | 296213 | MLY1 | Rural short | LV Transformer SP7786-A MLY1 - Planned | 4.98 | 90 | 448.2 | 0.0012831 | 1.4256e-05
2013-03-05 | 296214 | NBR6 | Rural short | LV Transformer SP3002-A NBR6 - Planned | 4.98 | 311 | 1548.78 | 0.0044337 | 1.4256e-05
2013-03-05 | 296215 | WMR1 | Rural short | LV Transformer SP9664-D WMR1 - Planned | 1 | 30 | 30 | 8.5881e-05 | 2.8627e-06
2013-03-05 | 296217 | CBW11 | Rural short | LV Transformer SP7094-F CBW11 - Planned | 6.5 | 139 | 903.5 | 0.0025865 | 1.8608e-05
2013-03-05 | 296219 | TRG2A | Urban | LV Transformer SC2218-O TRG2A - Planned | 66 | 147 | 9702 | 0.0098026 | 6.6685e-05
2013-03-05 | 296220 | AHL4A | Urban | LV Transformer SP11497-G AHL4A - Planned | 22.075 | 125 | 2759.375 | 0.002788 | 2.2304e-05
2013-03-05 | 296221 | AHL4A | Urban | LV Transformer SP772352 AHL4A - Planned | 23.28 | 217 | 5051.76 | 0.0051042 | 2.3521e-05
2013-03-05 | 296222 | AHL4A | Urban | LV Transformer SC1059-S AHL4A - Planned | 48.8 | 131 | 6392.8 | 0.0064591 | 4.9306e-05
2013-03-05 | 296223 | AHL4A | Urban | LV Transformer SC1059-S AHL4A - Planned | 14.11 | 116 | 1636.76 | 0.0016537 | 1.4256e-05
2013-03-05 | 296224 | DRA6 | Urban | LV Transformer SP746-L DRA6 - Planned | 26.695 | 286 | 7634.77 | 0.007714 | 2.6972e-05
2013-03-05 | 296225 | CFD6A | Urban | LV Transformer SP1330-O CFD6A - Planned | 10.34 | 300 | 3102 | 0.0031342 | 1.0447e-05
2013-03-05 | 296226 | AHL11A | Urban | LV Transformer SC2383-M AHL11A - Planned | 5.15 | 54 | 278.1 | 0.00028098 | 5.2034e-06
2013-03-05 | 296227 | GYM7A | Rural short | LV Transformer SP9317-B GYM7A - Planned | 12 | 140 | 1680 | 0.0048093 | 3.4352e-05
2013-03-05 | 296228 | MTB17A | Rural short | LV Transformer SP8773-B MTB17A - Planned | 5.04 | 305 | 1537.2 | 0.0044006 | 1.4428e-05
2013-03-05 | 296229 | BTA5A | Rural short | LV Transformer SP3529-C BTA5A - Planned | 15.51 | 292 | 4528.92 | 0.012965 | 4.4401e-05
2013-03-05 | 296230 | GVN3A | Urban | LV Transformer SC22777-D GVN3A - Planned | 45.51 | 27 | 1228.77 | 0.0012415 | 4.5982e-05
2013-03-05 | 296231 | SGT22A | Urban | LV Transformer SP3157-F SGT22A - Planned | 20 | 225 | 4500 | 0.0045467 | 2.0207e-05
2013-03-05 | 296232 | SGT7 | Urban | LV Transformer SP227-K SGT7 - Planned | 14.7 | 352 | 5174.4 | 0.0052281 | 1.4852e-05
2013-03-05 | 296233 | DRD15B | Urban | LV Transformer SP3424-C DRD15B - Planned | 24.12 | 306 | 7380.72 | 0.0074573 | 2.437e-05
2013-03-05 | 296234 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 13.735 | 299 | 4106.765 | 0.0041494 | 1.3877e-05
2013-03-05 | 296235 | KCY1 | Urban | LV Transformer SP2385-I KCY1 - Planned | 5 | 333 | 1665 | 0.0016823 | 5.0519e-06
2013-03-05 | 296236 | WRG1A | Urban | LV Transformer SP3643-L WRG1A - Planned | 19.72 | 270 | 5324.4 | 0.0053796 | 1.9925e-05
2013-03-05 | 296237 | BLBNFM6 | Urban | LV Transformer SP3429-G BLBNFM6 - Planned | 18.17 | 202 | 3670.34 | 0.0037084 | 1.8358e-05
2013-03-05 | 296238 | CPK13 | Rural short | LV Transformer SP3746-D CPK13 - Planned | 10.64 | 183 | 1947.12 | 0.005574 | 3.0459e-05
2013-03-05 | 296239 | CRB25A | Rural short | Feeder CRB25A - Planned | 43.5 | 599 | 26056.5 | 0.074592 | 0.00012453
2013-03-05 | 296408 | CBW11 | Rural short | Feeder CBW11 - Planned | 7 | 198 | 1386 | 0.0039677 | 2.0039e-05
2013-03-06 | 296254 | FDS4 | Rural short | LV Transformer SP6855-D FDS4 - Planned | 2 | 380 | 760 | 0.0021758 | 5.7258e-06
2013-03-06 | 296256 | WMD13A | Rural short | Feeder WMD8B, WMD13A - Planned | 31.04 | 303 | 9405.12 | 0.026926 | 8.8865e-05
2013-03-06 | 296256 | WMD8B | Rural short | Feeder WMD8B, WMD13A - Planned | 5.325 | 303 | 1613.475 | 0.0046192 | 1.5245e-05
2013-03-06 | 296257 | PWC4 | Rural short | Feeder PWC4 - Planned | 32.825 | 394 | 12933.05 | 0.037026 | 9.3975e-05
2013-03-06 | 296258 | GYM7A | Rural short | Feeder GYM7A - Planned | 23 | 271 | 6233 | 0.017845 | 6.5847e-05
2013-03-06 | 296259 | GBN4 | Rural short | LV Transformer SP1534-B GBN4 - Planned | 23 | 25 | 575 | 0.0016462 | 6.5847e-05
2013-03-06 | 296260 | GBN4 | Rural short | LV Transformer SP74-E GBN4 - Planned | 5 | 26 | 130 | 0.00037218 | 1.4315e-05
2013-03-06 | 296261 | RLB16A | Rural short | Feeder RLB16A - Planned | 21.55 | 414 | 8921.7 | 0.025542 | 6.1696e-05
2013-03-06 | 296262 | MTB17A | Rural short | LV Transformer SP6466-F MTB17A - Planned | 1 | 352 | 352 | 0.0010077 | 2.8629e-06
2013-03-06 | 296263 | SMF3A | Rural short | LV Transformer SP16769-C SMF3A - Planned | 3 | 553 | 1659 | 0.0047496 | 8.5888e-06
2013-03-06 | 296265 | JBB16A | Rural short | LV Transformer SP4856-E JBB16A - Planned | 20 | 490 | 9800 | 0.028057 | 5.7258e-05
2013-03-06 | 296267 | SHW6 | Urban | LV Transformer SP12359-F SHW6 - Planned | 9.77 | 261 | 2549.97 | 0.0025763 | 9.8709e-06
2013-03-06 | 296268 | CLM5 | Urban | LV Transformer SP1751-A CLM5 - Planned | 41.475 | 263 | 10907.925 | 0.011021 | 4.1903e-05
2013-03-06 | 296269 | GBN3 | Rural short | LV Transformer SP2555-D GBN3 - Planned | 3.5 | 85 | 297.5 | 0.00085172 | 1.002e-05
2013-03-06 | 296270 | GBN4 | Rural short | LV Transformer SP6737-B GBN4 - Planned | 6.02 | 258 | 1553.16 | 0.0044466 | 1.7235e-05
2013-03-06 | 296271 | PWC4 | Rural short | LV Transformer SP4532-B PWC4 - Planned | 9.1818 | 377 | 3461.5386 | 0.0099101 | 2.6287e-05
2013-03-06 | 296272 | EMD3 | Rural short | LV Transformer SP166513 EMD3 - Planned | 29.25 | 347 | 10149.75 | 0.029058 | 8.374e-05
2013-03-06 | 296273 | CMD5A | Urban | LV Transformer SP3463-A CMD5A - Planned | 4.98 | 252 | 1254.96 | 0.0012679 | 5.0314e-06
2013-03-06 | 296274 | SPO47A | Urban | LV Transformer SP964-E SPO47A - Planned | 14.55 | 239 | 3477.45 | 0.0035134 | 1.47e-05
2013-03-06 | 296275 | SPO3A | Urban | LV Transformer SP730-G SPO3A - Planned | 38.15 | 273 | 10414.95 | 0.010522 | 3.8544e-05
2013-03-06 | 296276 | CCYUPC23 | Urban | LV Transformer SC1577-G CCYUPC23 - Planned | 33 | 223 | 7359 | 0.007435 | 3.3341e-05
2013-03-06 | 296277 | BHD1A | Urban | LV Transformer SP3031-G BHD1A - Planned | 19.95 | 241 | 4807.95 | 0.0048576 | 2.0156e-05
2013-03-06 | 296278 | PPE5A | Rural short | LV Transformer SP5025-G PPE5A - Planned | 14.58 | 8 | 116.64 | 0.00033393 | 4.1741e-05
2013-03-06 | 296279 | CCY13A | Urban | LV Transformer SP8739-C CCY13A - Planned | 6.97 | 73 | 508.81 | 0.00051406 | 7.042e-06
2013-03-06 | 296280 | SGT22A | Urban | LV Transformer SP882-J SGT7 - Planned | 2.73 | 350 | 955.5 | 0.00096537 | 2.7582e-06
2013-03-06 | 296280 | SGT7 | Urban | LV Transformer SP882-J SGT7 - Planned | 25.25 | 350 | 8837.5 | 0.0089288 | 2.5511e-05
2013-03-06 | 296281 | ZMR7A | Urban | LV Transformer SP2713-H ZMR7A - Planned | 14.8033 | 188 | 2783.0204 | 0.0028118 | 1.4956e-05
2013-03-06 | 296282 | ZMR7A | Urban | LV Transformer SP731997-B ZMR7A - Planned | 36.7787 | 185 | 6804.0595 | 0.0068743 | 3.7158e-05
2013-03-06 | 296283 | CFD2A | Urban | LV Transformer SP2295-H CFD2A - Planned | 13.65 | 212 | 2893.8 | 0.0029237 | 1.3791e-05
2013-03-06 | 296284 | WNM2A | Urban | LV Transformer SP807686 WNM2A - Planned | 4.05 | 227 | 919.35 | 0.00092884 | 4.0918e-06
2013-03-06 | 296285 | KCY1 | Urban | LV Transformer SP31131-B KCY1 - Planned | 5.88 | 307 | 1805.16 | 0.0018238 | 5.9407e-06
2013-03-06 | 296286 | DRD15B | Urban | LV Transformer SP329-J DRD15B - Planned | 18.5 | 155 | 2867.5 | 0.0028971 | 1.8691e-05
2013-03-06 | 296287 | CHL7 | Urban | LV Transformer SP2788-H CHL7 - Planned | 11.935 | 260 | 3103.1 | 0.0031351 | 1.2058e-05
2013-03-06 | 296288 | HPE13A | Urban | LV Transformer SP27-O HPE13A - Planned | 13.26 | 385 | 5105.1 | 0.0051578 | 1.3397e-05
2013-03-06 | 296289 | KSN2A | Rural short | LV Transformer SP4713-B KSN2A - Planned | 8.625 | 269 | 2320.125 | 0.0066423 | 2.4693e-05
2013-03-06 | 296290 | NIP4A | Rural short | LV Transformer SP3362-C NIP4A - Planned | 12.61 | 286 | 3606.46 | 0.010325 | 3.6101e-05
2013-03-07 | 296300 | BDB36A | Rural short | LV Transformer SP3813-D BDB36A - Planned | 38.5 | 60 | 2310 | 0.0066139 | 0.00011023
2013-03-07 | 296301 | LLY1 | Rural short | LV Transformer SP1876-C LLY1 - Planned | 3 | 292 | 876 | 0.0025081 | 8.5895e-06
2013-03-07 | 296303 | VSL13A | Urban | LV Transformer SC754495 VSL13A - Planned | 1.04 | 202 | 210.08 | 0.00021224 | 1.0507e-06
2013-03-07 | 296304 | DRA6 | Urban | LV Transformer SG4030-I DRA6 - Planned | 0.5 | 417 | 208.5 | 0.00021064 | 5.0514e-07
2013-03-07 | 296306 | KCY5 | Rural short | LV Transformer SP1801-I KCY5 - Planned | 2 | 185 | 370 | 0.0010594 | 5.7263e-06
2013-03-07 | 296308 | BHD35A | Rural short | Feeder BHD35A - Planned | 34.145 | 190 | 6487.55 | 0.018575 | 9.7763e-05
2013-03-07 | 296310 | RLB16A | Rural short | Feeder RLB16A - Planned | 9.528 | 443 | 4220.904 | 0.012085 | 2.728e-05
2013-03-07 | 296313 | NSD30B | Urban | LV Transformer SC22083-G NSD30B - Planned | 17.795 | 300 | 5338.5 | 0.0053934 | 1.7978e-05
2013-03-07 | 296314 | EMP21A | Rural short | LV Transformer SP2315-J EMP21A - Planned | 3 | 357 | 1071 | 0.0030665 | 8.5895e-06
2013-03-07 | 296315 | AHL4A | Urban | LV Transformer SC1059-S AHL4A - Planned | 12.97 | 444 | 5758.68 | 0.0058179 | 1.3103e-05
2013-03-07 | 296316 | OXL4A | Urban | LV Transformer SP4491-I OXL4A - Planned | 7.215 | 423 | 3051.945 | 0.0030833 | 7.2892e-06
2013-03-07 | 296317 | TRG2A | Urban | LV Transformer SP4206-I TRG2A - Planned | 15.4 | 227 | 3495.8 | 0.0035317 | 1.5558e-05
2013-03-07 | 296318 | GAP1A | Urban | LV Transformer SC760402 GAP1A - Planned | 12.04 | 62 | 746.48 | 0.00075415 | 1.2164e-05
2013-03-07 | 296318 | GAP6A | Urban | LV Transformer SC760402 GAP1A - Planned | 5.22 | 62 | 323.64 | 0.00032697 | 5.2737e-06
2013-03-07 | 296319 | AHL14A | Urban | LV Transformer SP4604-K AHL14A - Planned | 21 | 304 | 6384 | 0.0064496 | 2.1216e-05
2013-03-07 | 296320 | SHW81 | Urban | LV Transformer SP5515-E SHW81 - Planned | 25.23 | 383 | 9663.09 | 0.0097624 | 2.5489e-05
2013-03-07 | 296321 | GYM7A | Rural short | LV Transformer SP16882-B GYM7A - Planned | 17 | 219 | 3723 | 0.01066 | 4.8674e-05
2013-03-07 | 296322 | NVL5 | Rural short | LV Transformer SP3884-B NVL5 - Planned | 5.95 | 207 | 1231.65 | 0.0035264 | 1.7036e-05
2013-03-07 | 296323 | BTA5A | Rural short | LV Transformer SP78983-A BTA5A - Planned | 11 | 350 | 3850 | 0.011023 | 3.1495e-05
2013-03-07 | 296324 | CRB25A | Rural short | LV Transformer SP5646-E CRB25A - Planned | 16.07 | 404 | 6492.28 | 0.018589 | 4.6011e-05
2013-03-07 | 296325 | BTA5A | Rural short | LV Transformer SP3566-C BTA5A - Planned | 2.08 | 420 | 873.6 | 0.0025013 | 5.9554e-06
2013-03-07 | 296326 | HIS12B | Urban | LV Transformer SC21714-E HIS12B - Planned | 0.7 | 66 | 46.2 | 4.6675e-05 | 7.072e-07
2013-03-07 | 296327 | CBW11 | Rural short | LV Transformer SP2396-G CBW11 - Planned | 10.33 | 237 | 2448.21 | 0.0070096 | 2.9577e-05
2013-03-07 | 296328 | WNM2A | Urban | LV Transformer SP807686 WNM2A - Planned | 15.75 | 230 | 3622.5 | 0.0036597 | 1.5912e-05
2013-03-07 | 296329 | SGT7 | Urban | LV Transformer SP5891-F SGT7 - Planned | 58.755 | 549 | 32256.495 | 0.032588 | 5.9359e-05
2013-03-07 | 296330 | ALY6 | Urban | LV Transformer SC4738-F ALY6 - Planned | 6.3 | 433 | 2727.9 | 0.0027559 | 6.3648e-06
2013-03-07 | 296331 | BLB5A | Urban | LV Transformer SP520-I BLB5A - Planned | 24.335 | 318 | 7738.53 | 0.0078181 | 2.4585e-05
2013-03-07 | 296332 | CHL6A | Urban | LV Transformer SC4470-G CHL6A - Planned | 6.79 | 355 | 2410.45 | 0.0024352 | 6.8598e-06
2013-03-07 | 296333 | EMP21A | Rural short | LV Transformer SP5331-K EMP21A - Planned | 17.25 | 330 | 5692.5 | 0.016299 | 4.939e-05
2013-03-07 | 296334 | NIP4A | Rural short | LV Transformer SP4388-F NIP4A - Planned | 1.74 | 244 | 424.56 | 0.0012156 | 4.9819e-06
2013-03-07 | 296409 | MLY4 | Rural short | Feeder MLY4 - Planned | 150.1 | 318 | 47731.8 | 0.13666 | 0.00042976
2013-03-08 | 296350 | WLDT1 | Urban | LV Transformer SSWLD WLDT1 - Planned | 1 | 108 | 108 | 0.0001091 | 1.0102e-06
2013-03-08 | 296352 | CRM5A | Urban | LV Transformer SC588822 CRM5A - Planned | 40.15 | 117 | 4697.55 | 0.0047456 | 4.0561e-05
2013-03-08 | 296356 | SMF1B | Rural short | Feeder SMF1B - Planned | 20.5 | 108 | 2214 | 0.0063396 | 5.87e-05
2013-03-08 | 296357 | WFD2B | Rural short | Feeder WFD2B - Planned | 13 | 384 | 4992 | 0.014294 | 3.7224e-05
2013-03-08 | 296358 | MLY6 | Rural short | Feeder MLY6 - Planned | 15.77 | 349 | 5503.73 | 0.015759 | 4.5156e-05
2013-03-08 | 296360 | MLY1 | Rural short | LV Transformer SP9558-A MLY1 - Planned | 3 | 251 | 753 | 0.0021561 | 8.5902e-06
2013-03-08 | 296361 | GVN5A | Urban | LV Transformer SP474178 GVN5A - Planned | 24.455 | 379 | 9268.445 | 0.0093633 | 2.4705e-05
2013-03-08 | 296362 | CVL5A | Rural short | LV Transformer SP3930-D CVL5A - Planned | 0.4 | 205 | 82 | 0.0002348 | 1.1454e-06
2013-03-08 | 296363 | MGP1 | Rural short | Feeder MGP1 - Planned | 89.5 | 390 | 34905 | 0.099947 | 0.00025627
2013-03-08 | 296364 | AMR3 | Rural short | Feeder AMR3 - Planned | 22.5 | 379 | 8527.5 | 0.024418 | 6.4426e-05
2013-03-08 | 296368 | HIS13A | Urban | LV Transformer SP468670 HIS13A - Planned | 1.5 | 260 | 390 | 0.00039399 | 1.5153e-06
2013-03-08 | 296369 | AHL4A | Urban | LV Transformer SC1059-S AHL4A - Planned | 29.95 | 255 | 7637.25 | 0.0077154 | 3.0256e-05
2013-03-08 | 296370 | SMR4A | Urban | LV Transformer SC766899 SMR4A - Planned | 0.99 | 101 | 99.99 | 0.00010101 | 1.0001e-06
2013-03-08 | 296371 | ENG2 | Urban | LV Transformer SP773186 ENG2 - Planned | 31.46 | 87 | 2737.02 | 0.002765 | 3.1782e-05
2013-03-08 | 296372 | RBA4A | Urban | LV Transformer SC570473 RBA4A - Planned | 144.54 | 30 | 4336.2 | 0.0043806 | 0.00014602
2013-03-08 | 296374 | VSL13A | Urban | LV Transformer SC791123 VSL13A - Planned | 25.0124 | 26 | 650.3224 | 0.00065697 | 2.5268e-05
2013-03-08 | 296375 | CFD2A | Urban | LV Transformer SP12927-D HDA11A - Planned | 1.365 | 186 | 253.89 | 0.00025649 | 1.379e-06
2013-03-08 | 296375 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 17.12 | 186 | 3184.32 | 0.0032169 | 1.7295e-05
2013-03-08 | 296376 | SGT7 | Urban | LV Transformer SP5477-F SGT7 - Planned | 19.17 | 330 | 6326.1 | 0.0063908 | 1.9366e-05
2013-03-08 | 296377 | SGT7 | Urban | LV Transformer SP5175-I SGT7 - Planned | 21.09 | 439 | 9258.51 | 0.0093532 | 2.1306e-05
2013-03-08 | 296378 | WNM2A | Urban | LV Transformer SP807686 WNM2A - Planned | 7.2 | 188 | 1353.6 | 0.0013674 | 7.2737e-06
2013-03-08 | 296379 | SGT22A | Urban | LV Transformer SP1111-J GBG27 - Planned | 5.965 | 244 | 1455.46 | 0.0014703 | 6.026e-06
2013-03-08 | 296380 | RCF1A | Urban | LV Transformer SP763672 RCF1A - Planned | 20.6867 | 370 | 7654.079 | 0.0077324 | 2.0898e-05
2013-03-08 | 296381 | BIS1 | Rural short | LV Transformer SP6093-D BIS1 - Planned | 14.96 | 297 | 4443.12 | 0.012722 | 4.2836e-05
2013-03-08 | 296382 | WED16A | Urban | LV Transformer SP135-O WED16A - Planned | 10.5165 | 37 | 389.1105 | 0.00039309 | 1.0624e-05
2013-03-08 | 296383 | RLB16A | Rural short | LV Transformer SP9037-B RLB16A - Planned | 3.07 | 150 | 460.5 | 0.0013186 | 8.7906e-06
2013-03-08 | 296384 | HPK3A | Urban | LV Transformer SP4198-G HPK3A - Planned | 11.53 | 212 | 2444.36 | 0.0024694 | 1.1648e-05
2013-03-08 | 296385 | EMP21A | Rural short | LV Transformer SP4365-O EMP21A - Planned | 4.08 | 257 | 1048.56 | 0.0030024 | 1.1683e-05
2013-03-08 | 296394 | MTB3A | Rural short | LV Transformer SP5497-E MTB3A - Planned | 1 | 177 | 177 | 0.00050682 | 2.8634e-06
2013-03-09 | 296396 | NVL10 | Urban | LV Transformer SG388-E NVL10 - Planned | 7.1907 | 70 | 503.349 | 0.00050847 | 7.2639e-06
2013-03-09 | 296397 | NVL8B | Urban | LV Transformer SC734336 NVL8B - Planned | 15.13 | 60 | 907.8 | 0.00091704 | 1.5284e-05
2013-03-09 | 296403 | KSN1 | Urban | LV Transformer SC2708-D KSN1 - Planned | 1 | 440 | 440 | 0.00044448 | 1.0102e-06
2013-03-09 | 296406 | CRB24B | Urban | LV Transformer SP14119-C CRB24B - Planned | 43.5 | 500 | 21750 | 0.021971 | 4.3943e-05
2013-03-09 | 296422 | KSN2A | Rural short | LV Transformer SP3586-B KSN2A - Planned | 3.38 | 295 | 997.1 | 0.0028553 | 9.679e-06
2013-03-10 | 296410 | BTN7 | Rural short | Feeder BTN7 - Planned | 1 | 210 | 210 | 0.00060136 | 2.8636e-06
2013-03-10 | 296412 | BPN29A | Urban | Feeder BPN29A - Planned | 6 | 295 | 1770 | 0.001788 | 6.0609e-06
2013-03-10 | 296413 | DRA8 | Urban | LV Transformer SG520558 DRA8 - Planned | 2 | 415 | 830 | 0.00083843 | 2.0203e-06
2013-03-10 | 296414 | HTL3A | Urban | LV Transformer SC4818-F HTL3A - Planned | 0.536 | 445 | 238.52 | 0.00024094 | 5.4144e-07
2013-03-10 | 296415 | NDH7 | Urban | Feeder NDH7 - Planned | 9.5 | 498 | 4731 | 0.004779 | 9.5965e-06
2013-03-10 | 296416 | BBH12B | Urban | LV Transformer SP3698-F BBH12B - Planned | 29.3241 | 355 | 10410.0555 | 0.010516 | 2.9622e-05
2013-03-10 | 296417 | MDH3A | Urban | LV Transformer SG5472-G MDH3A - Planned | 2.01 | 258 | 518.58 | 0.00052385 | 2.0304e-06
2013-03-10 | 296418 | NDH7 | Urban | LV Transformer SC4377-G NDH7 - Planned | 1.845 | 310 | 571.95 | 0.00057776 | 1.8637e-06
2013-03-10 | 296420 | CPL26A | Urban | LV Transformer SC3947-H CPL3A - Planned | 12.92 | 425 | 5491 | 0.0055468 | 1.3051e-05
2013-03-10 | 296420 | CPL3A | Urban | LV Transformer SC3947-H CPL3A - Planned | 4.97 | 425 | 2112.25 | 0.0021337 | 5.0205e-06
2013-03-11 | 296430 | BNH6A | Rural short | LV Transformer SP2495-G BNH6A - Planned | 2 | 165 | 330 | 0.00094513 | 5.7281e-06
2013-03-11 | 296431 | GYS5A | Rural short | LV Transformer SP3518-B GYS5A - Planned | 4 | 204 | 816 | 0.002337 | 1.1456e-05
2013-03-11 | 296432 | NBR5 | Rural short | LV Transformer SP790-A NBR5 - Planned | 3.78 | 221 | 835.38 | 0.0023926 | 1.0826e-05
2013-03-11 | 296433 | ABY2A | Rural short | LV Transformer SP12942-B ABY2A - Planned | 2 | 335 | 670 | 0.0019189 | 5.7281e-06
2013-03-11 | 296435 | CLM3 | Rural short | LV Transformer SP12657-A CLM3 - Planned | 2.01 | 413 | 830.13 | 0.0023775 | 5.7567e-06
2013-03-11 | 296437 | BHL2A | Urban | LV Transformer SC1494710 BHL2A - Planned | 22.4 | 431 | 9654.4 | 0.0097515 | 2.2625e-05
2013-03-11 | 296438 | GYM9A | Rural short | LV Transformer SP18155-A GYM9A - Planned | 5.0127 | 240 | 1203.048 | 0.0034456 | 1.4357e-05
2013-03-11 | 296439 | CMD13A | Urban | LV Transformer SP3807-A CMD13A - Planned | 32.43 | 160 | 5188.8 | 0.005241 | 3.2756e-05
2013-03-11 | 296440 | SPO51A | Urban | LV Transformer SP2246-G SPO51A - Planned | 18.02 | 94 | 1693.88 | 0.0017109 | 1.8201e-05
2013-03-11 | 296441 | HIS12A | Urban | LV Transformer SP5152-H HIS12A - Planned | 21.68 | 170 | 3685.6 | 0.0037227 | 2.1898e-05
2013-03-11 | 296442 | SGT7 | Urban | LV Transformer SP714524 SGT7 - Planned | 24.84 | 340 | 8445.6 | 0.0085305 | 2.509e-05
2013-03-11 | 296443 | WNM2A | Urban | LV Transformer SP807686 WNM2A - Planned | 18.9 | 246 | 4649.4 | 0.0046961 | 1.909e-05
2013-03-11 | 296444 | GBG27 | Urban | LV Transformer SP1111-J GBG27 - Planned | 8.05 | 286 | 2302.3 | 0.0023254 | 8.1309e-06
2013-03-11 | 296445 | RCF1A | Urban | LV Transformer SP3566-D RCF1A - Planned | 5.3601 | 108 | 578.8908 | 0.00058471 | 5.414e-06
2013-03-11 | 296446 | CFD2A | Urban | LV Transformer SP2295-H CFD2A - Planned | 36.855 | 154 | 5675.67 | 0.0057327 | 3.7226e-05
2013-03-11 | 296447 | DRD15B | Urban | LV Transformer SP3602-E DRD15B - Planned | 6 | 230 | 1380 | 0.0013939 | 6.0603e-06
2013-03-11 | 296448 | TMH15A | Urban | LV Transformer SP17753-B TMH15A - Planned | 0.99 | 627 | 620.73 | 0.00062697 | 9.9995e-07
2013-03-12 | 296471 | WFD6A | Rural short | LV Transformer SP4622-E WFD6A - Planned | 7 | 269 | 1883 | 0.0053935 | 2.005e-05
2013-03-12 | 296472 | NRG16A | Rural short | LV Transformer SP5167-I NRG16A - Planned | 19.5 | 270 | 5265 | 0.01508 | 5.5854e-05
2013-03-12 | 296473 | MBG1 | Rural short | LV Transformer SP1079-E MBG1 - Planned | 5 | 285 | 1425 | 0.0040816 | 1.4321e-05
2013-03-12 | 296474 | WMR3 | Rural short | LV Transformer SP9685-E WMR3 - Planned | 1 | 39 | 39 | 0.00011171 | 2.8643e-06
2013-03-12 | 296475 | MLY1 | Rural short | Feeder MLY1 - Planned | 55.76 | 403 | 22471.28 | 0.064364 | 0.00015971
2013-03-12 | 296482 | GTN12A | Rural short | Feeder GTN12A - Planned | 12.75 | 440 | 5610 | 0.016069 | 3.652e-05
2013-03-12 | 296483 | BNH6A | Rural short | LV Transformer SP2703-E BNH6A - Planned | 4 | 425 | 1700 | 0.0048693 | 1.1457e-05
2013-03-12 | 296485 | JBB16A | Rural short | LV Transformer SP4856-E JBB16A - Planned | 20 | 382 | 7640 | 0.021883 | 5.7286e-05
2013-03-12 | 296486 | SRD19A | Urban | LV Transformer SP16707-D SRD19A - Planned | 20.72 | 239 | 4952.08 | 0.0050015 | 2.0927e-05
2013-03-12 | 296487 | KRN10 | Urban | LV Transformer SP1523-O KRN10 - Planned | 23.73 | 372 | 8827.56 | 0.0089157 | 2.3967e-05
2013-03-12 | 296488 | GLY15A | Urban | LV Transformer SP4397-J GLY15A - Planned | 29.26 | 121 | 3540.46 | 0.0035758 | 2.9552e-05
2013-03-12 | 296489 | DRA6 | Urban | LV Transformer SP2666-K DRA6 - Planned | 15.6 | 286 | 4461.6 | 0.0045062 | 1.5756e-05
2013-03-12 | 296490 | TCB3 | Rural short | LV Transformer SP6740-C TCB3 - Planned | 9.99 | 125 | 1248.75 | 0.0035768 | 2.8614e-05
2013-03-12 | 296491 | TCB3 | Rural short | LV Transformer SP6380-C TCB3 - Planned | 2.07 | 49 | 101.43 | 0.00029052 | 5.9291e-06
2013-03-12 | 296492 | GYM9B | Rural short | LV Transformer SP1060-D GYM9B - Planned | 1 | 81 | 81 | 0.00023201 | 2.8643e-06
2013-03-12 | 296493 | GBN2 | Rural short | LV Transformer SP871-C GBN2 - Planned | 11.04 | 126 | 1391.04 | 0.0039843 | 3.1622e-05
2013-03-12 | 296494 | SPD12B | Urban | LV Transformer SC22763-G SPD12B - Planned | 41.41 | 384 | 15901.44 | 0.01606 | 4.1824e-05
2013-03-12 | 296495 | BBH8A | Urban | LV Transformer SP4566-H BBH8A - Planned | 24.725 | 292 | 7219.7 | 0.0072918 | 2.4972e-05
2013-03-12 | 296496 | DRD15B | Urban | LV Transformer SP3741-C DRD15B - Planned | 37.8 | 246 | 9298.8 | 0.0093917 | 3.8178e-05
2013-03-12 | 296497 | SGT24A | Urban | LV Transformer SP50-L SGT24A - Planned | 6.375 | 255 | 1625.625 | 0.0016419 | 6.4387e-06
2013-03-12 | 296498 | MRE2 | Urban | LV Transformer SP5846-G MRE2 - Planned | 24.48 | 209 | 5116.32 | 0.0051674 | 2.4724e-05
2013-03-12 | 296499 | NMC13A | Rural short | LV Transformer SC21122-G NMC13A - Planned | 38.69 | 90 | 3482.1 | 0.0099737 | 0.00011082
2013-03-12 | 296500 | NSW3A | Urban | LV Transformer SC1366381 NSW3A - Planned | 8.56 | 215 | 1840.4 | 0.0018588 | 8.6455e-06
2013-03-12 | 296501 | CPL5A | Urban | LV Transformer SG6545-I CPL5A - Planned | 15.12 | 270 | 4082.4 | 0.0041232 | 1.5271e-05
2013-03-12 | 296502 | BVL2A | Urban | LV Transformer SP3255-E BVL2A - Planned | 10.98 | 247 | 2712.06 | 0.0027391 | 1.109e-05
2013-03-12 | 296515 | IDY9B | Urban | LV Transformer SC6566-G IDY9B - Planned | 12.06 | 237 | 2858.22 | 0.0028868 | 1.218e-05
2013-03-12 | 296516 | MGP17A | Urban | LV Transformer SC764535 MGP17A - Planned | 0.99 | 79 | 78.21 | 7.8991e-05 | 9.9989e-07
2013-03-12 | 296732 | KWA6A | Urban | LV Transformer SP4470-B KWA6A - Planned | 5.355 | 375 | 2008.125 | 0.0020282 | 5.4085e-06
2013-03-13 | 296530 | MGP13A | Rural short | LV Transformer SP1717-F MGP13A - Planned | 8 | 236 | 1888 | 0.0054083 | 2.2916e-05
2013-03-13 | 296531 | WMR3 | Rural short | Feeder WMR3 - Planned | 22.308 | 341 | 7607.028 | 0.021791 | 6.3902e-05
2013-03-13 | 296533 | RPN6A | Rural short | LV Transformer SP5210-E RPN6A - Planned | 2 | 247 | 494 | 0.0014151 | 5.7291e-06
2013-03-13 | 296534 | KMR27A | Urban | Feeder KMR27A - Planned | 28 | 344 | 9632 | 0.0097276 | 2.8278e-05
2013-03-13 | 296535 | BTA1A | Urban | LV Transformer SP2101-D BTA1A - Planned | 10.01 | 425 | 4254.25 | 0.0042965 | 1.0109e-05
2013-03-13 | 296537 | BTA5A | Rural short | LV Transformer SP3566-C BTA5A - Planned | 25 | 386 | 9650 | 0.027643 | 7.1614e-05
2013-03-13 | 296538 | TBV2 | Rural short | Feeder TBV2 - Planned | 85.238 | 379.6667 | 33439.148 | 0.095788 | 0.00024417
2013-03-13 | 296540 | BMT1 | Rural short | LV Transformer SP9347-B BMT1 - Planned | 4 | 80 | 320 | 0.00091666 | 1.1458e-05
2013-03-13 | 296541 | NBR6 | Rural short | Feeder NBR6 - Planned | 139.43 | 356 | 49637.08 | 0.14219 | 0.0003994
2013-03-13 | 296542 | AMR2 | Rural short | Feeder AMR2 - Planned | 38.05 | 263 | 10007.15 | 0.028666 | 0.000109
2013-03-13 | 296543 | MTB17A | Rural short | LV Transformer SP439840 MTB17A - Planned | 2 | 510 | 1020 | 0.0029218 | 5.7291e-06
2013-03-13 | 296545 | CRB15A | Urban | LV Transformer SP3014-E CRBTHP14 - Planned | 2.7 | 110 | 297 | 0.00029995 | 2.7268e-06
2013-03-13 | 296546 | TWT6B | Rural short | LV Transformer SP15358-B TWT6B - Planned | 53 | 414 | 21942 | 0.062854 | 0.00015182
2013-03-13 | 296547 | SHW10A | Urban | LV Transformer SP1340-K SHW10A - Planned | 27.3 | 197 | 5378.1 | 0.0054315 | 2.7571e-05
2013-03-13 | 296548 | KMR22A | Urban | LV Transformer SP3929-J KMR22A - Planned | 5.18 | 87 | 450.66 | 0.00045513 | 5.2314e-06
2013-03-13 | 296549 | SFD9 | Urban | LV Transformer SP3038-L SFD9 - Planned | 23.23 | 287 | 6667.01 | 0.0067332 | 2.346e-05
2013-03-13 | 296551 | NVL3 | Rural short | LV Transformer SP2353-E NVL3 - Planned | 33.84 | 208 | 7038.72 | 0.020163 | 9.6937e-05
2013-03-13 | 296552 | GBN3 | Rural short | LV Transformer SP6533-B GBN3 - Planned | 5 | 27 | 135 | 0.00038671 | 1.4323e-05
2013-03-13 | 296553 | GYM7A | Rural short | LV Transformer SP6830-D GYM7A - Planned | 6.02 | 78 | 469.56 | 0.0013451 | 1.7245e-05
2013-03-13 | 296554 | CLM4A | Urban | LV Transformer SP2832-A CLM4A - Planned | 11.115 | 345 | 3834.675 | 0.0038727 | 1.1225e-05
2013-03-13 | 296555 | GYM2A | Rural short | LV Transformer SP1040-G GYM2A - Planned | 3 | 98 | 294 | 0.00084218 | 8.5937e-06
2013-03-13 | 296556 | MTB17A | Rural short | LV Transformer SP5265-G MTB17A - Planned | 4.94 | 389 | 1921.66 | 0.0055047 | 1.4151e-05
2013-03-13 | 296557 | BHD21A | Urban | LV Transformer SC340-G BHD21A - Planned | 30.75 | 178 | 5473.5 | 0.0055278 | 3.1055e-05
2013-03-13 | 296558 | DRD15B | Urban | LV Transformer SP3424-C DRD15B - Planned | 25.46 | 235 | 5983.1 | 0.0060425 | 2.5713e-05
2013-03-13 | 296559 | BRD13A | Urban | LV Transformer SC22723-B LTN9 - Planned | 3.9 | 95 | 370.5 | 0.00037418 | 3.9387e-06
2013-03-13 | 296559 | LTN9 | Urban | LV Transformer SC22723-B LTN9 - Planned | 5.53 | 95 | 525.35 | 0.00053056 | 5.5849e-06
2013-03-13 | 296560 | GBG27 | Urban | LV Transformer SP1671-F GBG27 - Planned | 4.305 | 319 | 1373.295 | 0.0013869 | 4.3477e-06
2013-03-13 | 296561 | WED6A | Urban | LV Transformer SC4124-I WED6A - Planned | 35.3208 | 449 | 15859.0392 | 0.016016 | 3.5671e-05
2013-03-13 | 296562 | CHL7 | Urban | LV Transformer SG2038-K CHL7 - Planned | 23.65 | 308 | 7284.2 | 0.0073565 | 2.3885e-05
2013-03-13 | 296563 | NIP5A | Urban | LV Transformer SP1446-H NIP5A - Planned | 25.2 | 302 | 7610.4 | 0.0076859 | 2.545e-05
2013-03-13 | 296564 | CPB8 | Rural short | LV Transformer SP777492 CPB8 - Planned | 1 | 363 | 363 | 0.0010398 | 2.8646e-06
2013-03-13 | 296565 | RST20A | Urban | LV Transformer SP15560-C RST20A - Planned | 3.78 | 132 | 498.96 | 0.00050391 | 3.8175e-06
2013-03-13 | 296582 | WMR3 | Rural short | Feeder WMR3 - Planned | 25.33 | 341 | 8637.53 | 0.024743 | 7.2559e-05
2013-03-14 | 296591 | CPD2A | Rural short | LV Transformer SP2810-B CPD2A - Planned | 1 | 170 | 170 | 0.00048703 | 2.8649e-06
2013-03-14 | 296592 | BBH10A | Urban | LV Transformer SP48468-C BBH10A - Planned | 77 | 231 | 17787 | 0.017962 | 7.7759e-05
2013-03-14 | 296594 | CBW11 | Rural short | Feeder CBW11 - Planned | 20 | 267 | 5340 | 0.015298 | 5.7297e-05
2013-03-14 | 296595 | SIS2 | Rural short | LV Transformer SP2570-E SIS2 - Planned | 11 | 270 | 2970 | 0.0085087 | 3.1514e-05
2013-03-14 | 296597 | THL2 | Rural short | Feeder THL2 - Planned | 10.95 | 343 | 3755.85 | 0.01076 | 3.137e-05
2013-03-14 | 296598 | TGW3 | Rural short | Feeder TGW3 - Planned | 5.02 | 336 | 1686.72 | 0.0048322 | 1.4382e-05
2013-03-14 | 296599 | BDT3 | Rural short | Feeder BDT3 - Planned | 8.68 | 339 | 2942.52 | 0.0084299 | 2.4867e-05
2013-03-14 | 296601 | BNH1B | Rural short | Feeder BNH1B - Planned | 59.9 | 418 | 25038.2 | 0.071731 | 0.00017161
2013-03-14 | 296602 | JBB13A | Rural short | Feeder JBB13A - Planned | 67.99 | 271 | 18425.29 | 0.052786 | 0.00019478
2013-03-14 | 296603 | KLG16A | Rural short | Feeder KLG16A - Planned | 5 | 471 | 2355 | 0.0067468 | 1.4324e-05
2013-03-14 | 296605 | BDT1 | Rural short | LV Transformer SP11653-C BDT1 - Planned | 2 | 358 | 716 | 0.0020512 | 5.7297e-06
2013-03-14 | 296607 | TWG11 | Urban | LV Transformer SP397-N TWG11 - Planned | 12.155 | 382 | 4643.21 | 0.004689 | 1.2275e-05
2013-03-14 | 296608 | GAP9A | Urban | LV Transformer SC4269-M GAP9A - Planned | 35.2 | 6 | 211.2 | 0.00021328 | 3.5547e-05
2013-03-14 | 296609 | GAP9A | Urban | LV Transformer SC2481-L GAP9A - Planned | 4.83 | 113 | 545.79 | 0.00055117 | 4.8776e-06
2013-03-14 | 296610 | AGE8 | Urban | LV Transformer SP660-L AGE8 - Planned | 11.8 | 354 | 4177.2 | 0.0042184 | 1.1916e-05
2013-03-14 | 296611 | AGE10 | Urban | LV Transformer SP522276 AGE10 - Planned | 30.12 | 343 | 10331.16 | 0.010433 | 3.0417e-05
2013-03-14 | 296613 | NBR9 | Rural short | LV Transformer SP4434-A NBR9 - Planned | 2.04 | 406 | 828.24 | 0.0023728 | 5.8443e-06
2013-03-14 | 296614 | NVL9 | Rural short | LV Transformer SP3544-C NVL9 - Planned | 1.37 | 307 | 420.59 | 0.0012049 | 3.9249e-06
2013-03-14 | 296615 | GYN3A | Rural short | LV Transformer SP80035-A GYN3A - Planned | 5 | 190 | 950 | 0.0027216 | 1.4324e-05
2013-03-14 | 296616 | GYS5A | Rural short | LV Transformer SP1401-E GYS5A - Planned | 0.4 | 152 | 60.8 | 0.00017418 | 1.1459e-06
2013-03-14 | 296618 | LDR1 | Urban | LV Transformer SP2178-H LDR1 - Planned | 33.18 | 339 | 11248.02 | 0.011359 | 3.3507e-05
2013-03-14 | 296619 | BBH10A | Urban | LV Transformer SC741313 BBH10A - Planned | 9.98 | 46 | 459.08 | 0.0004636 | 1.0078e-05
2013-03-14 | 296620 | CRB25A | Rural short | LV Transformer SP5646-E CRB25A - Planned | 2.145 | 372 | 797.94 | 0.002286 | 6.1451e-06
2013-03-14 | 296621 | MAI11 | Urban | LV Transformer SP2886-F MAI11 - Planned | 30.75 | 219 | 6734.25 | 0.0068006 | 3.1053e-05
2013-03-14 | 296622 | VSL3A | Urban | LV Transformer SC791281-A VSL3A - Planned | 44.46 | 64 | 2845.44 | 0.0028735 | 4.4898e-05
2013-03-14 | 296623 | MRE2 | Urban | LV Transformer SP5846-G MRE2 - Planned | 5.44 | 298 | 1621.12 | 0.0016371 | 5.4936e-06
2013-03-14 | 296623 | MRE3 | Urban | LV Transformer SP5846-G MRE2 - Planned | 0.93 | 298 | 277.14 | 0.00027987 | 9.3916e-07
2013-03-14 | 296624 | SGT7 | Urban | LV Transformer SP1612-J SGT7 - Planned | 28.455 | 383 | 10898.265 | 0.011006 | 2.8735e-05
2013-03-14 | 296625 | KWA12A | Urban | LV Transformer SP4412-B KWA12A - Planned | 6.75 | 291 | 1964.25 | 0.0019836 | 6.8165e-06
2013-03-14 | 296626 | BHL5A | Urban | LV Transformer SP1357-I BHL5A - Planned | 6.15 | 220 | 1353 | 0.0013663 | 6.2106e-06
2013-03-14 | 296627 | HDA11A | Urban | LV Transformer SP12927-D HDA11A - Planned | 13.735 | 223 | 3062.905 | 0.0030931 | 1.387e-05
2013-03-14 | 296628 | DRD5A | Urban | LV Transformer SP3059-F DRD5A - Planned | 34.19 | 429 | 14667.51 | 0.014812 | 3.4527e-05
2013-03-14 | 296629 | MTG7A | Urban | LV Transformer SP1892-L MTG7A - Planned | 2.97 | 303 | 899.91 | 0.00090878 | 2.9993e-06
2013-03-14 | 296630 | MTG8A | Urban | LV Transformer SP16706-D MTG8A - Planned | 21.0474 | 193 | 4062.1482 | 0.0041022 | 2.1255e-05
2013-03-14 | 296631 | RLB11B | Urban | LV Transformer SP9129-C RLB11B - Planned | 2.62 | 260 | 681.2 | 0.00068791 | 2.6458e-06
2013-03-14 | 296632 | CHL6A | Urban | LV Transformer SC4470-G CHL6A - Planned | 6.79 | 386 | 2620.94 | 0.0026468 | 6.8569e-06
2013-03-14 | 296633 | CVL5A | Rural short | LV Transformer SP4462-B CVL5A - Planned | 1.95 | 90 | 175.5 | 0.00050278 | 5.5865e-06
2013-03-14 | 296634 | ARG5A | Urban | LV Transformer SP4181-G ARG5A - Planned | 48.175 | 223 | 10743.025 | 0.010849 | 4.865e-05
2013-03-14 | 296635 | LLY1 | Rural short | LV Transformer SP1638-B LLY1 - Planned | 1 | 85 | 85 | 0.00024351 | 2.8649e-06
2013-03-14 | 296636 | BDB37A | Rural short | LV Transformer SP4151-C BDB37A - Planned | 8.74 | 381 | 3329.94 | 0.0095399 | 2.5039e-05
2013-03-14 | 296638 | GBN3 | Rural short | LV Transformer SP2561-E GBN3 - Planned | 1 | 222 | 222 | 0.000636 | 2.8649e-06
2013-03-14 | 296733 | BDB37A | Rural short | Feeder BDB37A - Planned | 161 | 451 | 72611 | 0.20802 | 0.00046124
2013-03-15 | 296672 | BLH12A | Rural short | Feeder BLH12A - Planned | 5 | 145 | 725 | 0.0020773 | 1.4326e-05
2013-03-15 | 296673 | BBSRDL8 | Rural short | Feeder BBSRDL8 - Planned | 11.98 | 172 | 2060.56 | 0.0059039 | 3.4325e-05
2013-03-15 | 296674 | TGW3 | Rural short | Feeder TGW3 - Planned | 1 | 151 | 151 | 0.00043265 | 2.8652e-06
2013-03-15 | 296676 | NRG10 | Urban | LV Transformer SP3803-F NRG10 - Planned | 36 | 172 | 6192 | 0.0062526 | 3.6352e-05
2013-03-15 | 296677 | BNH3A | Rural short | LV Transformer SP5265-C BNH3A - Planned | 2 | 80 | 160 | 0.00045843 | 5.7304e-06
2013-03-15 | 296678 | CBW7 | Rural short | Feeder CBW7 - Planned | 39.33 | 215 | 8455.95 | 0.024228 | 0.00011269
2013-03-15 | 296680 | BVL2A | Urban | Feeder BVL2A - Planned | 1 | 290 | 290 | 0.00029284 | 1.0098e-06
2013-03-15 | 296683 | GTN12A | Rural short | Feeder GTN12A - Planned | 2 | 345 | 690 | 0.001977 | 5.7304e-06
2013-03-15 | 296684 | WMD3A | Urban | Feeder WMD4A, WMD3A - Planned | 1 | 303 | 303 | 0.00030596 | 1.0098e-06
2013-03-15 | 296684 | WMD4A | Rural short | Feeder WMD4A, WMD3A - Planned | 2.25 | 303 | 681.75 | 0.0019534 | 6.4467e-06
2013-03-15 | 296685 | RCN4A | Urban | LV Transformer SP1125-P RCN4A - Planned | 2.33 | 393 | 915.69 | 0.00092465 | 2.3528e-06
2013-03-15 | 296686 | KBR1A | Rural short | Feeder KBR1A - Planned | 12 | 243 | 2916 | 0.0083549 | 3.4382e-05
2013-03-15 | 296688 | WMR3 | Rural short | Feeder WMR3 - Planned | 26.9 | 369 | 9926.1 | 0.02844 | 7.7074e-05
2013-03-15 | 296690 | JBB16A | Rural short | Feeder JBB16A - Planned | 40.855 | 503 | 20550.065 | 0.05888 | 0.00011706
2013-03-15 | 296692 | KMR21A | Urban | LV Transformer SC7759-G KMR21A - Planned | 4.72 | 22 | 103.84 | 0.00010486 | 4.7662e-06
2013-03-15 | 296693 | AGE9 | Urban | LV Transformer SP1117-Q AGE9 - Planned | 17.76 | 306 | 5434.56 | 0.0054877 | 1.7934e-05
2013-03-15 | 296694 | GBN4 | Rural short | LV Transformer SP5454-C GBN4 - Planned | 2.01 | 91 | 182.91 | 0.00052407 | 5.7591e-06
2013-03-15 | 296695 | GBN4 | Rural short | LV Transformer SP12684-B GBN4 - Planned | 7.775 | 150 | 1166.25 | 0.0033415 | 2.2277e-05
2013-03-15 | 296697 | NBR5 | Rural short | LV Transformer SP4031-A NBR5 - Planned | 11.76 | 143 | 1681.68 | 0.0048184 | 3.3695e-05
2013-03-15 | 296698 | NBR1 | Rural short | LV Transformer SP765-A NBR1 - Planned | 38.7 | 105 | 4063.5 | 0.011643 | 0.00011088
2013-03-15 | 296699 | BHD20A | Urban | LV Transformer SC420-J BHD32B - Planned | 5.355 | 36 | 192.78 | 0.00019467 | 5.4074e-06
2013-03-15 | 296699 | BHD32B | Urban | LV Transformer SC420-J BHD32B - Planned | 3.65 | 36 | 131.4 | 0.00013269 | 3.6857e-06
2013-03-15 | 296700 | JBB16A | Rural short | LV Transformer SP4855-D JBB16A - Planned | 4.9 | 446 | 2185.4 | 0.0062616 | 1.4039e-05
2013-03-15 | 296701 | HIS5A | Urban | LV Transformer SP2801-H HIS5A - Planned | 25.375 | 185 | 4694.375 | 0.0047403 | 2.5623e-05
2013-03-15 | 296702 | BHD20A | Urban | LV Transformer SC570-J BHD20A - Planned | 9.12 | 50 | 456 | 0.00046046 | 9.2092e-06
2013-03-15 | 296703 | SPO60A | Urban | LV Transformer SP26979-B SPO60A - Planned | 8.935 | 146 | 1304.51 | 0.0013173 | 9.0224e-06
2013-03-15 | 296704 | SPO69A | Urban | LV Transformer SP10030-E SPO69A - Planned | 15.72 | 30 | 471.6 | 0.00047621 | 1.5874e-05
2013-03-15 | 296705 | BHD35A | Rural short | LV Transformer SP5743-D BHD35A - Planned | 24.5 | 181 | 4434.5 | 0.012706 | 7.0197e-05
2013-03-15 | 296706 | PBH6 | Urban | LV Transformer SP17408-E PBH6 - Planned | 16.8 | 266 | 4468.8 | 0.0045125 | 1.6964e-05
2013-03-15 | 296707 | WNM2A | Urban | LV Transformer SP807686 WNM2A - Planned | 6.3 | 207 | 1304.1 | 0.0013169 | 6.3616e-06
2013-03-15 | 296708 | SRD14A | Urban | LV Transformer SC4361-I SRD14A - Planned | 45.8025 | 240 | 10992.6 | 0.0111 | 4.6251e-05
2013-03-15 | 296709 | WED16A | Urban | LV Transformer SP135-O WED16A - Planned | 35.7561 | 338 | 12085.5618 | 0.012204 | 3.6106e-05
2013-03-15 | 296709 | WED20A | Urban | LV Transformer SP135-O WED16A - Planned | 5.615 | 338 | 1897.87 | 0.0019164 | 5.6699e-06
2013-03-15 | 296710 | WHO1 | Rural short | LV Transformer SP25604-A WHO1 - Planned | 7 | 246 | 1722 | 0.0049339 | 2.0056e-05
2013-03-15 | 296711 | GTN12A | Rural short | LV Transformer SP2397-D GTN12A - Planned | 2.01 | 334 | 671.34 | 0.0019235 | 5.7591e-06
2013-03-16 | 296725 | WMD2A | Urban | LV Transformer SC771774 WMD6A - Planned | 111 | 114 | 12654 | 0.012777 | 0.00011208
2013-03-16 | 296725 | WMD6A | Urban | LV Transformer SC771774 WMD6A - Planned | 55 | 114 | 6270 | 0.0063309 | 5.5534e-05
2013-03-16 | 296728 | AGT37A | Urban | LV Transformer SP45949-C AGT37A - Planned | 2.003 | 175 | 350.525 | 0.00035393 | 2.0225e-06
2013-03-17 | 296741 | WED21A | Urban | LV Transformer SG6454-F WED21A - Planned | 18 | 235 | 4230 | 0.0042709 | 1.8174e-05
2013-03-17 | 296743 | DRA6 | Urban | LV Transformer SP746-L DRA6 - Planned | 7 | 297 | 2079 | 0.0020991 | 7.0678e-06
2013-03-17 | 296744 | BHDRCK29 | Urban | LV Transformer SC568855 BHD46A - Planned | 2 | 455 | 910 | 0.00091881 | 2.0194e-06
2013-03-17 | 296745 | KCY5 | Rural short | LV Transformer SP4038-G KCY5 - Planned | 4.14 | 304 | 1258.56 | 0.0036065 | 1.1864e-05
2013-03-17 | 296746 | BHL5A | Urban | LV Transformer SP929-K BHL5A - Planned | 27.8 | 320 | 8896 | 0.0089821 | 2.8069e-05
2013-03-17 | 296748 | HTL3A | Urban | LV Transformer SC5162-H HTL3A - Planned | 2.2011 | 176 | 387.3936 | 0.00039114 | 2.2224e-06
2013-03-17 | 296749 | RST18A | Urban | LV Transformer SG111-K RST18A - Planned | 4.6 | 370 | 1702 | 0.0017185 | 4.6445e-06
2013-03-17 | 296750 | BHD46A | Urban | Feeder BHD46A - Planned | 61 | 509 | 31049 | 0.03135 | 6.159e-05
2013-03-18 | 296770 | WFD2B | Rural short | Feeder WFD2B - Planned | 71 | 149 | 10579 | 0.030321 | 0.00020349
2013-03-18 | 296771 | LLY1 | Rural short | LV Transformer SP2803-C LLY1 - Planned | 2 | 153 | 306 | 0.00087703 | 5.7322e-06
2013-03-18 | 296772 | FDS3 | Rural short | Feeder FDS3 - Planned | 10.15 | 245 | 2486.75 | 0.0071273 | 2.9091e-05
2013-03-18 | 296773 | BNH1B | Rural short | Feeder BNH1B - Planned | 19.5 | 270 | 5265 | 0.01509 | 5.5889e-05
2013-03-18 | 296774 | WMR3 | Rural short | Feeder WMR3 - Planned | 15 | 310 | 4650 | 0.013327 | 4.2992e-05
2013-03-18 | 296775 | BDT5 | Rural short | LV Transformer SP649-E BDT5 - Planned | 2 | 368 | 736 | 0.0021095 | 5.7322e-06
2013-03-18 | 296778 | EMD3 | Rural short | Feeder EMD3 - Planned | 65.99 | 274 | 18081.26 | 0.051823 | 0.00018914
2013-03-18 | 296779 | MLY3 | Rural short | Feeder MLY3 - Planned | 2 | 324 | 648 | 0.0018572 | 5.7322e-06
2013-03-18 | 296781 | MLY3 | Rural short | Feeder MLY3 - Planned | 17.01 | 380 | 6463.8 | 0.018526 | 4.8753e-05
2013-03-18 | 296782 | LLY1 | Rural short | LV Transformer SP774146 LLY1 - Planned | 1 | 85 | 85 | 0.00024362 | 2.8661e-06
2013-03-18 | 296784 | SFD9 | Urban | LV Transformer SP3038-L SFD9 - Planned | 7.07 | 283 | 2000.81 | 0.00202 | 7.1377e-06
2013-03-18 | 296785 | NBR9 | Rural short | LV Transformer SP3993-B NBR9 - Planned | 3.04 | 344 | 1045.76 | 0.0029973 | 8.713e-06
2013-03-18 | 296786 | GYM7A | Rural short | LV Transformer SP1044-E GYM7A - Planned | 6.02 | 57 | 343.14 | 0.00098348 | 1.7254e-05
2013-03-18 | 296787 | GBN2 | Rural short | LV Transformer SP1227-E GBN2 - Planned | 2.01 | 117 | 235.17 | 0.00067403 | 5.7609e-06
2013-03-18 | 296788 | SPO41A | Urban | LV Transformer SP3236-D SPO41A - Planned | 3.24 | 263 | 852.12 | 0.00086028 | 3.271e-06
2013-03-18 | 296789 | HIS12A | Urban | LV Transformer SC21746-D HIS12A - Planned | 27.88 | 56 | 1561.28 | 0.0015762 | 2.8147e-05
2013-03-18 | 296790 | MGP13A | Rural short | LV Transformer SP6369-C MGP13A - Planned | 0.99 | 85 | 84.15 | 0.00024118 | 2.8375e-06
2013-03-18 | 296791 | BHD35A | Rural short | LV Transformer SP2512-I BHD35A - Planned | 7 | 125 | 875 | 0.0025079 | 2.0063e-05
2013-03-18 | 296792 | HWL10A | Urban | LV Transformer SC733273 HWL10A - Planned | 25.08 | 29 | 727.32 | 0.00073428 | 2.532e-05
2013-03-18 | 296794 | MGP4 | Rural short | LV Transformer SP317-L MGP4 - Planned | 86.58 | 245 | 21212.1 | 0.060797 | 0.00024815
2013-03-18 | 296795 | LTA2 | Urban | LV Transformer SP764753 LTA2 - Planned | 8.05 | 138 | 1110.9 | 0.0011215 | 8.127e-06
2013-03-18 | 296796 | ZMR7A | Urban | LV Transformer SP5865-G ZMR7A - Planned | 22.266 | 152 | 3384.432 | 0.0034168 | 2.2479e-05
2013-03-18 | 296796 | ZMR9 | Urban | LV Transformer SP5865-G ZMR7A - Planned | 13.7064 | 152 | 2083.3728 | 0.0021033 | 1.3838e-05
2013-03-18 | 296797 | MRE2 | Urban | LV Transformer SC2747-J MRE2 - Planned | 13.64 | 352 | 4801.28 | 0.0048472 | 1.3771e-05
2013-03-18 | 296798 | BKD3A | Urban | LV Transformer SP6116-C BKD3A - Planned | 19.91 | 160 | 3185.6 | 0.0032161 | 2.0101e-05
2013-03-18 | 296799 | SRD18A | Urban | LV Transformer SC4400-J SRD18A - Planned | 7.3 | 266 | 1941.8 | 0.0019604 | 7.3699e-06
2013-03-19 | 296804 | AHD9 | Urban | LV Transformer SC737071 AHD9 - Planned | 5 | 10 | 50 | 5.0475e-05 | 5.0475e-06
2013-03-19 | 296808 | GTN1B | Rural short | LV Transformer SP5457-B GTN1B - Planned | 19.475 | 88 | 1713.8 | 0.0049125 | 5.5824e-05
2013-03-19 | 296811 | LLY1 | Rural short | Feeder LLY1 - Planned | 13.4075 | 183 | 2453.5725 | 0.0070331 | 3.8432e-05
2013-03-19 | 296812 | SIS2 | Rural short | Feeder SIS2 - Planned | 33.98 | 151 | 5130.98 | 0.014708 | 9.7402e-05
2013-03-19 | 296814 | CPD2A | Rural short | LV Transformer SP3690-C CPD2A - Planned | 2.345 | 212 | 497.14 | 0.001425 | 6.7219e-06
2013-03-19 | 296817 | BNH6A | Rural short | Feeder BNH6A - Planned | 16 | 475 | 7600 | 0.021785 | 4.5863e-05
2013-03-19 | 296818 | TWG17 | Urban | LV Transformer SP758641 TWG17 - Planned | 27.5288 | 425 | 11699.74 | 0.011811 | 2.779e-05
2013-03-19 | 296819 | GAP6A | Urban | LV Transformer SC4383-J GAP6A - Planned | 22.94 | 245 | 5620.3 | 0.0056737 | 2.3158e-05
2013-03-19 | 296820 | GYN3A | Rural short | LV Transformer SP1173-C GYN3A - Planned | 4 | 65 | 260 | 0.00074528 | 1.1466e-05
2013-03-19 | 296821 | GYN3A | Rural short | LV Transformer SP4207-B GYN3A - Planned | 1 | 199 | 199 | 0.00057043 | 2.8665e-06
2013-03-19 | 296822 | NVL3 | Rural short | LV Transformer SP2352-C NVL3 - Planned | 4.58 | 240 | 1099.2 | 0.0031508 | 1.3128e-05
2013-03-19 | 296823 | CLM5 | Urban | LV Transformer SP34586-F CLM5 - Planned | 30.14 | 330 | 9946.2 | 0.010041 | 3.0426e-05
2013-03-19 | 296824 | MAI14 | Urban | LV Transformer SP26323-E MAI14 - Planned | 9.0112 | 41 | 369.4592 | 0.00037297 | 9.0968e-06
2013-03-19 | 296825 | BBH16A | Urban | LV Transformer SP2722-J BBH16A - Planned | 11.22 | 68 | 762.96 | 0.00077021 | 1.1327e-05
2013-03-19 | 296826 | BTA5A | Rural short | LV Transformer SC2055163 BTA5A - Planned | 40.85 | 348 | 14215.8 | 0.040749 | 0.0001171
2013-03-19 | 296827 | MRE2 | Urban | LV Transformer SP517-N MRE3 - Planned | 28.35 | 315 | 8930.25 | 0.0090151 | 2.8619e-05
2013-03-19 | 296827 | MRE3 | Urban | LV Transformer SP517-N MRE3 - Planned | 26.97 | 315 | 8495.55 | 0.0085763 | 2.7226e-05
2013-03-19 | 296828 | DBS4A | Urban | LV Transformer SP43959-D DBS4A - Planned | 7.07 | 218 | 1541.26 | 0.0015559 | 7.1372e-06
2013-03-19 | 296828 | MRE3 | Urban | LV Transformer SP43959-D DBS4A - Planned | 2.796 | 218 | 609.528 | 0.00061532 | 2.8226e-06
2013-03-19 | 296829 | DRD15B | Urban | LV Transformer SP3602-E DRD15B - Planned | 12 | 245 | 2940 | 0.0029679 | 1.2114e-05
2013-03-19 | 296830 | SGT7 | Urban | LV Transformer SP882-J SGT7 - Planned | 12.24 | 277 | 3390.48 | 0.0034227 | 1.2356e-05
2013-03-19 | 296831 | MFN13A | Rural short | LV Transformer SC1388253 MFN13A - Planned | 1.95 | 56 | 109.2 | 0.00031302 | 5.5896e-06
2013-03-19 | 296832 | BHL5A | Urban | LV Transformer SP3192-I SGT24A - Planned | 26.64 | 112 | 2983.68 | 0.003012 | 2.6893e-05
2013-03-19 | 296832 | SGT24A | Urban | LV Transformer SP3192-I SGT24A - Planned | 3.42 | 112 | 383.04 | 0.00038668 | 3.4525e-06
2013-03-19 | 296833 | HPE13A | Urban | LV Transformer SC5851-G HPE16A - Planned | 2.24 | 176 | 394.24 | 0.00039799 | 2.2613e-06
2013-03-19 | 296834 | BPN35A | Urban | LV Transformer SP12635-F BPN35A - Planned | 4.16 | 57 | 237.12 | 0.00023937 | 4.1995e-06
2013-03-19 | 296835 | TMH15A | Urban | LV Transformer SP7326-C TMH15A - Planned | 46.46 | 290 | 13473.4 | 0.013601 | 4.6902e-05
2013-03-19 | 296837 | RPN6A | Rural short | LV Transformer SP10788-D RPN6A - Planned | 11.73 | 160 | 1876.8 | 0.0053798 | 3.3624e-05
2013-03-19 | 296838 | RST16A | Urban | LV Transformer SP4185-D RST16A - Planned | 10.32 | 312 | 3219.84 | 0.0032504 | 1.0418e-05
2013-03-19 | 296839 | ACR5 | Rural short | Feeder ACR5 - Planned | 95.5 | 528 | 50424 | 0.14454 | 0.00027375
2013-03-19 | 296840 | PPE5A | Rural short | Feeder PPE5A - Planned | 8.15 | 488 | 3977.2 | 0.011401 | 2.3362e-05
2013-03-19 | 296841 | CRB25A | Rural short | Feeder CRB25A - Planned | 19 | 562 | 10678 | 0.030608 | 5.4463e-05
2013-03-19 | 296842 | GBN2 | Rural short | LV Transformer SP2568-E GBN2 - Planned | 1.335 | 347 | 463.245 | 0.0013279 | 3.8267e-06
2013-03-19 | 296843 | MLY3 | Rural short | Feeder MLY3 - Planned | 55.545 | 291 | 16163.595 | 0.046332 | 0.00015922
2013-03-19 | 296845 | NBR6 | Rural short | Feeder NBR6 - Planned | 94.97 | 399 | 37893.03 | 0.10862 | 0.00027223
2013-03-19 | 296846 | GBN2 | Rural short | Feeder GBN2 - Planned | 99.61 | 265 | 26396.65 | 0.075665 | 0.00028553
2013-03-19 | 296847 | GYGGYS6 | Rural short | LV Transformer SP2634-D GYGGYS6 - Planned | 2.345 | 155 | 363.475 | 0.0010419 | 6.7219e-06
2013-03-19 | 297108 | KBR2A | Rural short | Feeder KBR2A - Planned | 15.5 | 187 | 2898.5 | 0.0083084 | 4.443e-05
2013-03-19 | 297414 | NRG10 | Urban | LV Transformer SP15881-C NRG10 - Planned | 32.5 | 198 | 6435 | 0.0064962 | 3.2809e-05
2013-03-19 | 297415 | NMC3A | Rural short | Feeder NMC3A - Planned | 2 | 323 | 646 | 0.0018517 | 5.7329e-06
2013-03-20 | 296873 | LLY1 | Rural short | LV Transformer SP5073-A LLY1 - Planned | 0.99 | 185 | 183.15 | 0.00052507 | 2.8382e-06
2013-03-20 | 296875 | WMR1 | Rural short | Feeder WMR1 - Planned | 12 | 351 | 4212 | 0.012075 | 3.4403e-05
2013-03-20 | 296876 | TRP1 | Rural short | Feeder TRP1 - Planned | 7.98 | 346 | 2761.08 | 0.0079157 | 2.2878e-05
2013-03-20 | 296877 | LLY1 | Rural short | Feeder LLY1 - Planned | 3.01 | 312 | 939.12 | 0.0026924 | 8.6294e-06
2013-03-20 | 296878 | KBR1A | Rural short | Feeder KBR1A - Planned | 11.9 | 407 | 4843.3 | 0.013885 | 3.4116e-05
2013-03-20 | 296880 | NMC1B | Rural short | Feeder NMC1B - Planned | 20.435 | 378 | 7724.43 | 0.022145 | 5.8585e-05
2013-03-20 | 296881 | MGL8 | Urban | LV Transformer SP4447-K MGL8 - Planned | 22 | 363 | 7986 | 0.0080613 | 2.2207e-05
2013-03-20 | 296883 | BGY5A | Rural short | Feeder BGY5A - Planned | 27 | 380 | 10260 | 0.029414 | 7.7406e-05
2013-03-20 | 296884 | MBG2 | Rural short | Feeder MBG2 - Planned | 19.055 | 505 | 9622.775 | 0.027588 | 5.4629e-05
2013-03-20 | 296888 | PWC6 | Rural short | LV Transformer SP3970-B PWC6 - Planned | 16.92 | 323 | 5465.16 | 0.015668 | 4.8508e-05
2013-03-20 | 296889 | BMT2 | Rural short | Feeder BMT2 - Planned | 14.46 | 234 | 3383.64 | 0.0097006 | 4.1455e-05
2013-03-20 | 296890 | MLY3 | Rural short | LV Transformer SP6529-C MLY3 - Planned | 2.01 | 69 | 138.69 | 0.00039761 | 5.7625e-06
2013-03-20 | 296891 | MLY3 | Rural short | LV Transformer SP9549-A MLY3 - Planned | 6.02 | 33 | 198.66 | 0.00056954 | 1.7259e-05
2013-03-20 | 296893 | OXL4A | Urban | LV Transformer SP2894-L OXL4A - Planned | 8.825 | 391 | 3450.575 | 0.0034831 | 8.9082e-06
2013-03-20 | 296894 | AGE10 | Urban | LV Transformer SP733335 AGE10 - Planned | 20.8058 | 315 | 6553.827 | 0.0066156 | 2.1002e-05
2013-03-20 | 296895 | AGE10 | Urban | LV Transformer SP733334 AGE10 - Planned | 0.9233 | 190 | 175.427 | 0.00017708 | 9.32e-07
2013-03-20 | 296896 | MLY4 | Rural short | LV Transformer SP94068-A MLY4 - Planned | 9.03 | 136 | 1228.08 | 0.0035208 | 2.5888e-05
2013-03-20 | 296897 | NBR4 | Rural short | LV Transformer SP886-A NBR4 - Planned | 10.25 | 252 | 2583 | 0.0074052 | 2.9386e-05
2013-03-20 | 296898 | HWL1A | Urban | LV Transformer SP2885-F HWL1A - Planned | 29.915 | 315 | 9423.225 | 0.009512 | 3.0197e-05
2013-03-20 | 296899 | HIS12B | Urban | LV Transformer SC760180 HIS12B - Planned | 1.02 | 17 | 17.34 | 1.7503e-05 | 1.0296e-06
2013-03-20 | 296900 | NRG10 | Urban | LV Transformer SP74321-A NRG10 - Planned | 4.13 | 191 | 788.83 | 0.00079627 | 4.1689e-06
2013-03-20 | 296901 | BBH16A | Urban | LV Transformer SC193-J MAI7 - Planned | 2.0067 | 180 | 361.206 | 0.00036461 | 2.0256e-06
2013-03-20 | 296901 | MAI7 | Urban | LV Transformer SC193-J MAI7 - Planned | 39.9483 | 180 | 7190.694 | 0.0072585 | 4.0325e-05
2013-03-20 | 296902 | BHD35A | Rural short | LV Transformer SP678-I BHD35A - Planned | 1.105 | 336 | 371.28 | 0.0010644 | 3.1679e-06
2013-03-20 | 296903 | KWA6A | Urban | LV Transformer SP4470-B KWA6A - Planned | 2.0825 | 434 | 903.805 | 0.00091232 | 2.1021e-06
2013-03-20 | 296904 | DRD15B | Urban | LV Transformer SP3602-E DRD15B - Planned | 4 | 270 | 1080 | 0.0010902 | 4.0377e-06
2013-03-20 | 296905 | SGT7 | Urban | LV Transformer SP3766-D SGT7 - Planned | 5.365 | 261 | 1400.265 | 0.0014135 | 5.4156e-06
2013-03-20 | 296906 | BHL5A | Urban | LV Transformer SP3785-F BHL5A - Planned | 46.8875 | 285 | 13362.9375 | 0.013489 | 4.7329e-05
2013-03-20 | 296907 | CHL11A | Rural short | LV Transformer SC1063598 CHL11A - Planned | 13.085 | 365 | 4776.025 | 0.013692 | 3.7513e-05
2013-03-20 | 296908 | HPE13A | Urban | LV Transformer SP3148-G HPE13A - Planned | 13.86 | 345 | 4781.7 | 0.0048268 | 1.3991e-05
2013-03-20 | 296909 | MTG4B | Urban | LV Transformer SP6411-D MTG4B - Planned | 35.175 | 189 | 6648.075 | 0.0067107 | 3.5507e-05
2013-03-20 | 296910 | NMC13A | Rural short | LV Transformer SP6036-I NMC13A - Planned | 18 | 407 | 7326 | 0.021003 | 5.1604e-05
2013-03-20 | 296911 | BVL10A | Urban | LV Transformer SP8466-C BVL10A - Planned | 10.24 | 205 | 2099.2 | 0.002119 | 1.0337e-05
2013-03-21 | 296935 | IPL1 | Rural short | LV Transformer SP2548-F IPL1 - Planned | 1 | 113 | 113 | 0.00032401 | 2.8673e-06
2013-03-21 | 296936 | KCY5 | Rural short | Feeder KCY5 - Planned | 202 | 86 | 17372 | 0.049811 | 0.0005792
2013-03-21 | 296937 | NRG9 | Rural short | Feeder NRG9 - Planned | 44 | 240 | 10560 | 0.030279 | 0.00012616
2013-03-21 | 296951 | TGW1 | Rural short | Feeder TGW1 - Planned | 15.26 | 353 | 5386.78 | 0.015446 | 4.3755e-05
2013-03-21 | 296953 | MBG1 | Rural short | Feeder MBG1 - Planned | 2 | 340 | 680 | 0.0019498 | 5.7346e-06
2013-03-21 | 296954 | BNH6A | Rural short | Feeder BNH6A - Planned | 20.01 | 369 | 7383.69 | 0.021171 | 5.7375e-05
2013-03-21 | 296955 | BMT1 | Rural short | Feeder BMT1 - Planned | 113.54 | 341 | 38717.14 | 0.11101 | 0.00032555
2013-03-21 | 296956 | KCY5 | Rural short | Feeder KCY5 - Planned | 5.9 | 364 | 2147.6 | 0.0061578 | 1.6917e-05
2013-03-21 | 296957 | CLD18A | Rural short | LV Transformer SP152288 CLD18A - Planned | 1 | 281 | 281 | 0.00080571 | 2.8673e-06
2013-03-21 | 296958 | GYM2A | Rural short | LV Transformer SP2299-C GYM2A - Planned | 0.4 | 206 | 82.4 | 0.00023627 | 1.1469e-06
2013-03-21 | 296959 | PWC4 | Rural short | LV Transformer SP2992-B PWC4 - Planned | 4.98 | 154 | 766.92 | 0.002199 | 1.4279e-05
2013-03-21 | 296962 | RLB16A | Rural short | Feeder RLB16A - Planned | 6.25 | 585 | 3656.25 | 0.010484 | 1.7921e-05
2013-03-21 | 296965 | SPO5A | Urban | LV Transformer SG1798-G SPO5A - Planned | 1 | 597 | 597 | 0.00060259 | 1.0094e-06
2013-03-21 | 296966 | CRB25A | Rural short | LV Transformer SP5677-F CRB25A - Planned | 7.5 | 538 | 4035 | 0.01157 | 2.1505e-05
2013-03-21 | 296967 | AGE7B | Urban | LV Transformer SP1007-U AGE7B - Planned | 1.085 | 87 | 94.395 | 9.5279e-05 | 1.0952e-06
2013-03-21 | 296968 | DRA11 | Urban | LV Transformer SP7193-F DRA11 - Planned | 12.15 | 438 | 5321.7 | 0.0053715 | 1.2264e-05
2013-03-21 | 296969 | AHL9A | Urban | LV Transformer SC2942-I AHL9A - Planned | 14.175 | 347 | 4918.725 | 0.0049648 | 1.4308e-05
2013-03-21 | 296970 | GAP9A | Urban | LV Transformer SP2570-K GAP9A - Planned | 8.76 | 186 | 1629.36 | 0.0016446 | 8.842e-06
2013-03-21 | 296971 | MLY4 | Rural short | LV Transformer SP3959-B MLY4 - Planned | 1.05 | 227 | 238.35 | 0.00068342 | 3.0107e-06
2013-03-21 | 296972 | KWA2A | Urban | LV Transformer SP4519-B KWA2A - Planned | 12.1275 | 93 | 1127.8575 | 0.0011384 | 1.2241e-05
2013-03-21 | 296973 | GYM2A | Rural short | LV Transformer SP2571-E GYM2A - Planned | 7 | 111 | 777 | 0.0022279 | 2.0071e-05
2013-03-21 | 296974 | AHD6 | Urban | LV Transformer SP13762-A AHD6 - Planned | 32.19 | 90 | 2897.1 | 0.0029242 | 3.2491e-05
2013-03-21 | 296975 | GYS3A | Rural short | LV Transformer SP1741-C GYS3A - Planned | 6 | 61 | 366 | 0.0010494 | 1.7204e-05
2013-03-21 | 296976 | SPD29A | Urban | LV Transformer SC766764 SPD29A - Planned | 96.57 | 49 | 4731.93 | 0.0047762 | 9.7474e-05
2013-03-21 | 296977 | SPO51A | Urban | LV Transformer SP764179 SPO51A - Planned | 14.85 | 228 | 3385.8 | 0.0034175 | 1.4989e-05
2013-03-21 | 296978 | SPD29A | Urban | LV Transformer SC370-J SPD3A - Planned | 6.66 | 44 | 293.04 | 0.00029578 | 6.7223e-06
2013-03-21 | 296979 | CRB25A | Rural short | LV Transformer SP760627 CRB25A - Planned | 3.08 | 537 | 1653.96 | 0.0047424 | 8.8313e-06
2013-03-21 | 296980 | HWL11A | Urban | LV Transformer SP10034-E HWL11A - Planned | 35.97 | 35 | 1258.95 | 0.0012707 | 3.6307e-05
2013-03-21 | 296981 | DRD15B | Urban | LV Transformer SP3742-D DRD15B - Planned | 17.175 | 281 | 4826.175 | 0.0048714 | 1.7336e-05
2013-03-21 | 296982 | MTG8A | Urban | LV Transformer SC1063720 MTG8A - Planned | 18.27 | 362 | 6613.74 | 0.0066756 | 1.8441e-05
2013-03-21 | 296983 | RLB16A | Rural short | LV Transformer SP9033-B RLB16A - Planned | 0.75 | 10 | 7.5 | 2.1505e-05 | 2.1505e-06
2013-03-21 | 296984 | HPE13A | Urban | LV Transformer SP12142-E HPE13A - Planned | 27.565 | 312 | 8600.28 | 0.0086808 | 2.7823e-05
2013-03-21 | 296986 | AGT37A | Urban | LV Transformer SC4473-I AGT37A - Planned | 22.95 | 99 | 2272.05 | 0.0022933 | 2.3165e-05
2013-03-21 | 296987 | MBG1 | Rural short | LV Transformer SP1079-E MBG1 - Planned | 3 | 313 | 939 | 0.0026924 | 8.6019e-06
2013-03-21 | 296988 | VPT3A | Rural short | LV Transformer SP6190-C VPT3A - Planned | 1.34 | 262 | 351.08 | 0.0010067 | 3.8422e-06
2013-03-21 | 297104 | RWD2 | Rural short | Feeder RWD2 - Planned | 11 | 365 | 4015 | 0.011512 | 3.154e-05
2013-03-22 | 297012 | GYM7A | Rural short | LV Transformer SP6248-A GYM7A - Planned | 0.536 | 54 | 28.944 | 8.3007e-05 | 1.5372e-06
2013-03-22 | 297033 | LHM3 | Urban | LV Transformer SP4930-B LHM3 - Planned | 22.08 | 342 | 7551.36 | 0.0076214 | 2.2285e-05
2013-03-22 | 297034 | JBB16A | Rural short | LV Transformer SP15335-B JBB16A - Planned | 0.4 | 367 | 146.8 | 0.000421 | 1.1471e-06
2013-03-22 | 297035 | MFN12A | Rural short | LV Transformer SP4931-G MFN12A - Planned | 0.4 | 403 | 161.2 | 0.0004623 | 1.1471e-06
2013-03-22 | 297036 | MBG1 | Rural short | LV Transformer SP1078-F MBG1 - Planned | 6 | 330 | 1980 | 0.0056783 | 1.7207e-05
2013-03-22 | 297037 | GAP9A | Urban | LV Transformer SC2481-L GAP9A - Planned | 4.025 | 276 | 1110.9 | 0.0011212 | 4.0623e-06
2013-03-22 | 297038 | ENG2 | Urban | LV Transformer SP773186 ENG2 - Planned | 19.14 | 155 | 2966.7 | 0.0029942 | 1.9318e-05
2013-03-22 | 297039 | AHL4A | Urban | LV Transformer SP609-R AHL4A - Planned | 10.83 | 127 | 1375.41 | 0.0013882 | 1.093e-05
2013-03-22 | 297040 | AHL11A | Urban | LV Transformer SC621781 AHL11A - Planned | 6.14 | 85 | 521.9 | 0.00052674 | 6.197e-06
2013-03-22 | 297041 | MLY3 | Rural short | LV Transformer SP1162-D MLY3 - Planned | 1 | 69 | 69 | 0.00019788 | 2.8678e-06
2013-03-22 | 297042 | KWH2 | Rural short | LV Transformer SP31197-G KWH2 - Planned | 4 | 119 | 476 | 0.0013651 | 1.1471e-05
2013-03-22 | 297043 | JBB16A | Rural short | LV Transformer SP4855-D JBB16A - Planned | 17.5 | 372 | 6510 | 0.01867 | 5.0187e-05
2013-03-22 | 297044 | GYM7A | Rural short | Feeder GYM7A - Planned | 47.395 | 140 | 6635.3 | 0.019029 | 0.00013592
2013-03-22 | 297045 | BMT1 | Rural short | Feeder BMT1 - Planned | 126.49 | 350 | 44271.5 | 0.12696 | 0.00036275
2013-03-22 | 297046 | KRA3 | Urban | LV Transformer SC725-G KRA3 - Planned | 3.61 | 102 | 368.22 | 0.00037164 | 3.6435e-06
2013-03-22 | 297047 | TGW3 | Rural short | Feeder TGW3 - Planned | 17.5 | 337 | 5897.5 | 0.016913 | 5.0187e-05
2013-03-22 | 297048 | MTB16A | Rural short | LV Transformer SP113742-A MTB16A - Planned | 16.02 | 42 | 672.84 | 0.0019296 | 4.5943e-05
2013-03-22 | 297048 | TBV1 | Rural short | LV Transformer SP113742-A MTB16A - Planned | 0.99 | 42 | 41.58 | 0.00011924 | 2.8392e-06
2013-03-22 | 297049 | MAI5 | Urban | LV Transformer SP14793-D MAI5 - Planned | 1.23 | 53 | 65.19 | 6.5795e-05 | 1.2414e-06
2013-03-22 | 297050 | SPO67B | Urban | LV Transformer SP3051-G SPO67B - Planned | 6.895 | 261 | 1799.595 | 0.0018163 | 6.959e-06
2013-03-22 | 297051 | MTB16A | Rural short | LV Transformer SP568232 MTB16A - Planned | 27.85 | 74 | 2060.9 | 0.0059103 | 7.9869e-05
2013-03-22 | 297053 | MTB16A | Rural short | LV Transformer SP560344 MTB16A - Planned | 38.28 | 63 | 2411.64 | 0.0069162 | 0.00010978
2013-03-22 | 297054 | BHD5A | Urban | LV Transformer SP1766-P BHD5A - Planned | 25.6059 | 275 | 7041.6225 | 0.007107 | 2.5843e-05
2013-03-22 | 297055 | BHD35A | Rural short | LV Transformer SP5770-F BHD35A - Planned | 13.13 | 370 | 4858.1 | 0.013932 | 3.7655e-05
2013-03-22 | 297056 | SPO32A | Urban | LV Transformer SP1972-I SPO32A - Planned | 4.88 | 147 | 717.36 | 0.00072402 | 4.9253e-06
2013-03-22 | 297057 | CFD1A | Urban | LV Transformer SC754888 CFD1A - Planned | 0.02 | 55 | 1.1 | 1.1102e-06 | 2.0186e-08
2013-03-22 | 297058 | MFN12A | Rural short | LV Transformer SP7139-E MFN12A - Planned | 1.98 | 410 | 811.8 | 0.0023281 | 5.6783e-06
2013-03-22 | 297059 | BHL5A | Urban | LV Transformer SP3191-G BHL5A - Planned | 16.18 | 91 | 1472.38 | 0.001486 | 1.633e-05
2013-03-22 | 297060 | DRD3A | Urban | LV Transformer SP434843 DRD3A - Planned | 24.36 | 188 | 4579.68 | 0.0046222 | 2.4586e-05
2013-03-22 | 297061 | RLB11B | Urban | LV Transformer SP13426-B RLB11B - Planned | 0.84 | 234 | 196.56 | 0.00019838 | 8.4779e-07
2013-03-22 | 297062 | NIP4A | Rural short | LV Transformer SP3179-D NIP4A - Planned | 13.32 | 220 | 2930.4 | 0.0084039 | 3.82e-05
2013-03-22 | 297062 | NIP5A | Urban | LV Transformer SP3179-D NIP4A - Planned | 3.36 | 220 | 739.2 | 0.00074606 | 3.3912e-06
2013-03-23 | 297076 | GYGGYS6 | Rural short | LV Transformer SP5957-C GYGGYS6 - Planned | 1 | 120 | 120 | 0.00034421 | 2.8684e-06
2013-03-23 | 297078 | TWG14A | Urban | LV Transformer SC2093-I TWG14A - Planned | 1.145 | 373 | 427.085 | 0.00043101 | 1.1555e-06
2013-03-23 | 297079 | PGN1B | Rural short | LV Transformer SP3531-A PGN1B - Planned | 6.16 | 159 | 979.44 | 0.0028094 | 1.7669e-05
2013-03-23 | 297081 | BNH6A | Rural short | LV Transformer SP753035 BNH6A - Planned | 4 | 44 | 176 | 0.00050484 | 1.1474e-05
2013-03-23 | 297084 | CPL2A | Urban | Feeder CPL2A - Planned | 3.58 | 269 | 963.02 | 0.00097188 | 3.6129e-06
2013-03-24 | 297088 | EHSTR1H | CBD | LV Transformer SSEHS EHSTR1H - Planned | 1 | 45 | 45 | 0.011633 | 0.00025851
2013-03-24 | 297088 | EHSTR2H | CBD | LV Transformer SSEHS EHSTR1H - Planned | 1 | 41 | 41 | 0.010599 | 0.00025851
2013-03-24 | 297088 | EHSTR3H | CBD | LV Transformer SSEHS EHSTR1H - Planned | 1 | 73 | 73 | 0.018871 | 0.00025851
2013-03-24 | 297089 | CPL5A | Urban | LV Transformer SG737059 CPL5A - Planned | 2 | 334 | 668 | 0.00067411 | 2.0183e-06
2013-03-24 | 297090 | GBN3 | Rural short | Feeder GBN3 - Planned | 28.395 | 430 | 12209.85 | 0.035027 | 8.1458e-05
2013-03-24 | 297091 | MBG1 | Rural short | LV Transformer SP11690-D MBG1 - Planned | 2 | 259 | 518 | 0.001486 | 5.7375e-06
2013-03-24 | 297092 | IPL2A | Rural short | LV Transformer SP2812-E IPL2A - Planned | 8 | 263 | 2104 | 0.0060358 | 2.295e-05
2013-03-24 | 297094 | WSO13A | Rural short | LV Transformer SP733907 WSO13A - Planned | 2 | 445 | 890 | 0.0025532 | 5.7375e-06
2013-03-24 | 297095 | SFD9 | Urban | LV Transformer SP2096-H SFD9 - Planned | 3.96 | 179 | 1417.68 | 0.0014306 | 3.9962e-06
2013-03-24 | 297096 | ENG7 | Urban | LV Transformer SP325-Q ENG7 - Planned | 12.18 | 151 | 1839.18 | 0.001856 | 1.2291e-05
2013-03-24 | 297097 | BWSTR1H | Urban | LV Transformer SSBWS BWSTR1H - Planned | 1 | 307 | 307 | 0.00030981 | 1.0091e-06
2013-03-24 | 297098 | TGP9A | Rural short | LV Transformer SC794487 TGP9A - Planned | 2 | 334 | 668 | 0.0019163 | 5.7375e-06
2013-03-24 | 297099 | HTN22B | Urban | LV Transformer SP481109 HTN22B - Planned | 3.8 | 285 | 1083 | 0.0010929 | 3.8347e-06
2013-03-24 | 297100 | SPE9 | Urban | LV Transformer SC1513000 SPE9 - Planned | 3.91 | 210 | 821.1 | 0.00082861 | 3.9457e-06
2013-03-24 | 297101 | ARG4 | Urban | LV Transformer SP626770-A ARG4 - Planned | 1.05 | 100 | 105 | 0.00010596 | 1.0596e-06
2013-03-24 | 297102 | CPB2 | Urban | LV Transformer SP88420-A CPB2 - Planned | 9.36 | 201 | 1881.36 | 0.0018986 | 9.4456e-06
2013-03-24 | 297103 | CPB2 | Urban | LV Transformer SP88420-A CPB2 - Planned | 3.12 | 229 | 714.48 | 0.00072101 | 3.1485e-06
2013-03-25 | 297242 | AHD6 | Urban | LV Transformer SC22365-A AHD6 - Planned | 12.735 | 340 | 4329.9 | 0.0043689 | 1.285e-05
2013-03-25 | 297243 | GYN3A | Rural short | LV Transformer SP6265-B GYN3A - Planned | 16.5 | 123 | 2029.5 | 0.0058238 | 4.7348e-05
2013-03-25 | 297244 | MLY4 | Rural short | LV Transformer SP3038-A MLY4 - Planned | 13.11 | 255 | 3343.05 | 0.0095931 | 3.762e-05
2013-03-25 | 297246 | SBH4 | Urban | LV Transformer SP2961-E SBH4 - Planned | 43.855 | 104 | 4560.92 | 0.004602 | 4.425e-05
2013-03-25 | 297247 | DBY6 | Urban | LV Transformer SP4965-E DBY6 - Planned | 22.05 | 297 | 6548.85 | 0.0066079 | 2.2249e-05
2013-03-25 | 297267 | GYGGYS6 | Rural short | Feeder GYGGYS6 - Planned | 32.685 | 80 | 2614.8 | 0.0075033 | 9.3792e-05
2013-03-25 | 297268 | MLB6A | Rural short | Feeder MLB6A - Planned | 63.03 | 126 | 7941.78 | 0.022789 | 0.00018087
2013-03-26 | 297362 | NMC1B | Rural short | LV Transformer SP11344-H NMC1B - Planned | 1 | 148 | 148 | 0.00042478 | 2.8702e-06
2013-03-26 | 297373 | KCY5 | Rural short | Feeder KCY5 - Planned | 5.9 | 221 | 1303.9 | 0.0037424 | 1.6934e-05
2013-03-26 | 297377 | THL1 | Rural short | Feeder THL1 - Planned | 22.02 | 375 | 8257.5 | 0.0237 | 6.3201e-05
2013-03-26 | 297379 | GYGGYS6 | Rural short | Feeder GYGGYS6 - Planned | 10 | 378 | 3780 | 0.010849 | 2.8702e-05
2013-03-26 | 297380 | NBR6 | Rural short | Feeder NBR6 - Planned | 28.33 | 310 | 8782.3 | 0.025207 | 8.1312e-05
2013-03-26 | 297381 | COR26A | Urban | LV Transformer SP49-A COR26A - Planned | 1 | 38 | 38 | 3.8339e-05 | 1.0089e-06
2013-03-26 | 297382 | MLY3 | Rural short | LV Transformer SP751032 MLY3 - Planned | 1 | 36 | 36 | 0.00010333 | 2.8702e-06
2013-03-26 | 297383 | MLY3 | Rural short | LV Transformer SP792-B MLY3 - Planned | 2.01 | 156 | 313.56 | 0.00089997 | 5.769e-06
2013-03-26 | 297384 | GYS3A | Rural short | Feeder GYS3A - Planned | 17.01 | 199 | 3384.99 | 0.0097155 | 4.8821e-05
2013-03-26 | 297385 | PGN1B | Rural short | Feeder PGN1B - Planned | 2 | 438 | 876 | 0.0025143 | 5.7403e-06
2013-03-26 | 297394 | GLY4A | Urban | LV Transformer SP4520-K GLY4A - Planned | 1 | 62 | 62 | 6.2553e-05 | 1.0089e-06
2013-03-26 | 297395 | TWG17 | Urban | LV Transformer SP758641 TWG17 - Planned | 30.9699 | 112 | 3468.6288 | 0.0034996 | 3.1246e-05
2013-03-26 | 297396 | EMD3 | Rural short | LV Transformer SP166513 EMD3 - Planned | 4.225 | 177 | 747.825 | 0.0021464 | 1.2126e-05
2013-03-26 | 297397 | MDR8A | Urban | LV Transformer SP3180-G MDR8A - Planned | 0.96 | 36 | 34.56 | 3.4868e-05 | 9.6856e-07
2013-03-26 | 297398 | MRE3 | Urban | LV Transformer SC808031-A MRE3 - Planned | 21.195 | 213 | 4514.535 | 0.0045548 | 2.1384e-05
2013-03-26 | 297399 | CSE6 | Urban | LV Transformer SP22674-D CSE6 - Planned | 22.96 | 266 | 6107.36 | 0.0061618 | 2.3165e-05
2013-03-26 | 297400 | HPE13A | Urban | LV Transformer SP3148-G HPE13A - Planned | 39.3 | 324 | 12733.2 | 0.012847 | 3.9651e-05
2013-03-26 | 297400 | HPK6 | Urban | LV Transformer SP3148-G HPE13A - Planned | 0.83 | 324 | 268.92 | 0.00027132 | 8.374e-07
2013-03-26 | 297401 | WED16A | Urban | LV Transformer SP135-O WED16A - Planned | 6.3099 | 205 | 1293.5295 | 0.0013051 | 6.3662e-06
2013-03-26 | 297402 | ARG5A | Urban | LV Transformer SP14342-F ARG5A - Planned | 6.9 | 334 | 2304.6 | 0.0023252 | 6.9616e-06
2013-03-26 | 297406 | BHD35A | Rural short | Feeder BHD35A - Planned | 71.5 | 743 | 53124.5 | 0.15248 | 0.00020522
2013-03-27 | 297416 | LLY5 | Rural short | LV Transformer SP5320-C LLY5 - Planned | 2.01 | 184 | 369.84 | 0.0010617 | 5.7702e-06
2013-03-27 | 297418 | IPL3 | Rural short | LV Transformer SP1919-G IPL3 - Planned | 2 | 200 | 400 | 0.0011483 | 5.7415e-06
2013-03-27 | 297419 | MBG1 | Rural short | Feeder MBG1 - Planned | 24.45 | 333 | 8141.85 | 0.023373 | 7.019e-05
2013-03-27 | 297423 | IPL3 | Rural short | LV Transformer SP6012-E IPL3 - Planned | 2 | 90 | 180 | 0.00051674 | 5.7415e-06
2013-03-27 | 297424 | LLY5 | Rural short | LV Transformer SP1800-C LLY5 - Planned | 1 | 55 | 55 | 0.00015789 | 2.8708e-06
2013-03-27 | 297425 | MSV1 | Rural short | LV Transformer SP2806-C MSV1 - Planned | 5 | 358 | 1790 | 0.0051387 | 1.4354e-05
2013-03-27 | 297426 | TGW3 | Rural short | LV Transformer SP244047 TGW3 - Planned | 1 | 223 | 223 | 0.00064018 | 2.8708e-06
2013-03-27 | 297428 | BDT3 | Rural short | LV Transformer SP440-F BDT3 - Planned | 4 | 390 | 1560 | 0.0044784 | 1.1483e-05
2013-03-27 | 297432 | TBV2 | Rural short | Feeder TBV2 - Planned | 28.89 | 456 | 13173.84 | 0.037819 | 8.2936e-05
2013-03-27 | 297434 | UPC1 | Rural short | Feeder UPC1 - Planned | 32 | 400 | 12800 | 0.036746 | 9.1864e-05
2013-03-27 | 297441 | AMR2 | Rural short | Feeder AMR2 - Planned | 37.1115 | 228 | 8461.422 | 0.024291 | 0.00010654
2013-03-27 | 297442 | AMR2 | Rural short | Feeder AMR2 - Planned | 2.01 | 227 | 456.27 | 0.0013098 | 5.7702e-06
2013-03-27 | 297443 | GBN4 | Rural short | Feeder GBN4 - Planned | 2.01 | 89 | 178.89 | 0.00051355 | 5.7702e-06
2013-03-27 | 297444 | ENG7 | Urban | LV Transformer SP32413-F ENG7 - Planned | 6.15 | 311 | 1912.65 | 0.0019295 | 6.2043e-06
2013-03-27 | 297445 | NBR6 | Rural short | LV Transformer SP5292-A NBR6 - Planned | 1.85 | 399 | 738.15 | 0.0021191 | 5.3109e-06
2013-03-27 | 297446 | KLG7A | Rural short | LV Transformer SP2224-F KLG7A - Planned | 3.15 | 220 | 693 | 0.0019894 | 9.0429e-06
2013-03-27 | 297447 | BHL4A | Urban | LV Transformer SP1753-I BHL4A - Planned | 5.92 | 45 | 266.4 | 0.00026875 | 5.9723e-06
2013-03-27 | 297448 | BHL1A | Urban | LV Transformer SP3329-G BHL1A - Planned | 10.25 | 191 | 1957.75 | 0.001975 | 1.0341e-05
2013-03-27 | 297449 | BRT5 | Urban | LV Transformer SP1852-J BRT5 - Planned | 3.975 | 237 | 942.075 | 0.00095039 | 4.0101e-06
2013-03-27 | 297450 | AGE8 | Urban | LV Transformer SP522108 AGE8 - Planned | 1.3266 | 257 | 340.9362 | 0.00034395 | 1.3383e-06
2013-03-27 | 297451 | MTG7A | Urban | LV Transformer SG2509-I MTG7A - Planned | 6.5132 | 261 | 1699.9452 | 0.001715 | 6.5707e-06
2013-03-27 | 297452 | WED16A | Urban | LV Transformer SP135-O WED16A - Planned | 16.8264 | 220 | 3701.808 | 0.0037345 | 1.6975e-05
2013-03-27 | 297453 | AGT25A | Urban | LV Transformer SP2374-M AGT25A - Planned | 6.82 | 222 | 1514.04 | 0.0015274 | 6.8802e-06
2013-03-27 | 297454 | PPE5A | Rural short | LV Transformer SP5025-G PPE5A - Planned | 14.46 | 201 | 2906.46 | 0.0083437 | 4.1511e-05
2013-03-27 | 297455 | CRB25A | Rural short | LV Transformer SP4493-F CRB25A - Planned | 27.075 | 405 | 10965.375 | 0.031479 | 7.7726e-05
2013-03-27 | 297456 | NMC5A | Rural short | LV Transformer SP4946-K NMC5A - Planned | 14.5 | 432 | 6264 | 0.017982 | 4.1626e-05
2013-03-27 | 297457 | SGT22A | Urban | LV Transformer SP2529-G SGT22A - Planned | 7.26 | 176 | 1277.76 | 0.001289 | 7.3241e-06
2013-03-27 | 297458 | NDH7 | Urban | LV Transformer SP2162-J NDH7 - Planned | 21.23 | 63 | 1337.49 | 0.0013493 | 2.1417e-05
2013-03-27 | 297459 | WNM1A | Urban | LV Transformer SP1333-M WNM1A - Planned | 4.58 | 50 | 229 | 0.00023102 | 4.6204e-06
2013-03-27 | 297459 | WNM2A | Urban | LV Transformer SP1333-M WNM1A - Planned | 11.52 | 50 | 576 | 0.00058109 | 1.1622e-05
2013-03-27 | 297460 | BHL4A | Urban | LV Transformer SP635-I BHL4A - Planned | 6.9 | 37 | 255.3 | 0.00025755 | 6.9609e-06
2013-03-27 | 297461 | KBN2A | Rural short | LV Transformer SP1777-F KBN2A - Planned | 1.928 | 79 | 152.312 | 0.00043725 | 5.5348e-06
2013-03-27 | 297463 | MLY4 | Rural short | Feeder MLY4 - Planned | 57.265 | 537 | 30751.305 | 0.08828 | 0.00016439
2013-03-28 | 297494 | IPS1B | Urban | Feeder IPS1B - Planned | 6 | 175 | 1050 | 0.0010591 | 6.0522e-06
2013-03-28 | 297495 | MBG1 | Rural short | Feeder MBG1 - Planned | 5 | 174 | 870 | 0.0024983 | 1.4358e-05
2013-03-28 | 297496 | BDT1 | Rural short | LV Transformer SP7200-C BDT1 - Planned | 3 | 180 | 540 | 0.0015507 | 8.615e-06
2013-03-28 | 297497 | TGW1 | Rural short | Feeder TGW1 - Planned | 20.5 | 274 | 5617 | 0.01613 | 5.8869e-05
2013-03-28 | 297498 | MGP13A | Rural short | LV Transformer SP1655-F MGP13A - Planned | 6 | 313 | 1878 | 0.005393 | 1.723e-05
2013-03-28 | 297499 | GGR2 | Rural short | LV Transformer SP13990-A GGR2 - Planned | 6.5 | 179 | 1163.5 | 0.0033412 | 1.8666e-05
2013-03-28 | 297501 | IPL1 | Rural short | LV Transformer SP2429-D IPL1 - Planned | 2 | 52 | 104 | 0.00029865 | 5.7433e-06
2013-03-28 | 297502 | CNA8A | Rural short | Feeder CNA8A - Planned | 5 | 236 | 1180 | 0.0033886 | 1.4358e-05
2013-03-28 | 297504 | MCW4 | Rural short | LV Transformer SP1510-H MCW4 - Planned | 1 | 377 | 377 | 0.0010826 | 2.8717e-06
2013-03-28 | 297505 | MLY1 | Rural short | Feeder MLY1 - Planned | 77.17 | 307 | 23691.19 | 0.068033 | 0.00022161
2013-03-28 | 297506 | KWH2 | Rural short | Feeder KWH2 - Planned | 20.505 | 181 | 3711.405 | 0.010658 | 5.8883e-05
2013-03-28 | 297507 | GBN2 | Rural short | LV Transformer SP15469-B GBN2 - Planned | 4 | 16 | 64 | 0.00018379 | 1.1487e-05
2013-03-28 | 297508 | KCY4 | Rural short | Feeder KCY4 - Planned | 10.2 | 148 | 1509.6 | 0.0043351 | 2.9291e-05
2013-03-28 | 297513 | MTB17A | Rural short | Feeder MTB17A - Planned | 23.8 | 440 | 10472 | 0.030072 | 6.8345e-05
2013-03-28 | 297514 | BHD35A | Rural short | Feeder BHD35A - Planned | 48.98 | 498 | 24392.04 | 0.070046 | 0.00014065
2013-03-28 | 297515 | GAP9A | Urban | LV Transformer SC2481-L GAP9A - Planned | 3.22 | 5 | 16.1 | 1.624e-05 | 3.248e-06
2013-03-28 | 297516 | INA9A | Urban | LV Transformer SP1980-I INA9A - Planned | 14.08 | 212 | 2984.96 | 0.0030109 | 1.4203e-05
2013-03-28 | 297517 | AGE10 | Urban | LV Transformer SP522276 AGE10 - Planned | 23.4133 | 253 | 5923.5649 | 0.0059751 | 2.3617e-05
2013-03-28 | 297518 | ENG7 | Urban | LV Transformer SC4185-L ENG7 - Planned | 50.96 | 14 | 713.44 | 0.00071965 | 5.1403e-05
2013-03-28 | 297519 | SPO41A | Urban | LV Transformer SP16689-D SPO41A - Planned | 14.345 | 168 | 2409.96 | 0.0024309 | 1.447e-05
2013-03-28 | 297520 | SPO16A | Urban | LV Transformer SC563185 SPO16A - Planned | 1.96 | 23 | 45.08 | 4.5472e-05 | 1.9771e-06
2013-03-28 | 297521 | MGP16A | Urban | LV Transformer SP6299-E MGP16A - Planned | 43.605 | 71 | 3095.955 | 0.0031229 | 4.3984e-05
2013-03-28 | 297522 | SPO60A | Urban | LV Transformer SC1042-L SPO60A - Planned | 8.96 | 13 | 116.48 | 0.00011749 | 9.038e-06
2013-03-28 | 297523 | GVN15A | Urban | LV Transformer SC754335 GVN5A - Planned | 13.5 | 55 | 742.5 | 0.00074896 | 1.3617e-05
2013-03-28 | 297523 | GVN5A | Urban | LV Transformer SC754335 GVN5A - Planned | 4.69 | 55 | 257.95 | 0.00026019 | 4.7308e-06
2013-03-28 | 297524 | SPO41A | Urban | LV Transformer SP3236-D SPO41A - Planned | 8.1 | 67 | 542.7 | 0.00054742 | 8.1705e-06
2013-03-28 | 297525 | BHD35A | Rural short | LV Transformer SP4557-E BHD35A - Planned | 8.5 | 517 | 4394.5 | 0.01262 | 2.4409e-05
2013-03-28 | 297526 | SGT22A | Urban | LV Transformer SP2996-I SGT22A - Planned | 12.96 | 250 | 3240 | 0.0032682 | 1.3073e-05
2013-03-28 | 297527 | SGT7 | Urban | LV Transformer SP227-K SGT7 - Planned | 21.34 | 305 | 6508.7 | 0.0065653 | 2.1526e-05
2013-03-28 | 297528 | KRN2 | Urban | LV Transformer SP1973-H KRN2 - Planned | 5.28 | 224 | 1182.72 | 0.001193 | 5.3259e-06
2013-03-28 | 297529 | HPE13A | Urban | LV Transformer SP1626-D STT1B - Planned | 23.53 | 304 | 7153.12 | 0.0072154 | 2.3735e-05
2013-03-28 | 297530 | WRG5A | Urban | LV Transformer SP2143-N WRG5A - Planned | 7.567 | 148 | 1119.916 | 0.0011297 | 7.6328e-06
2013-03-28 | 297531 | EMP21A | Rural short | LV Transformer SP5212-M NSW5A - Planned | 6.21 | 291 | 1807.11 | 0.0051894 | 1.7833e-05
2013-03-28 | 297531 | NSW5A | Urban | LV Transformer SP5212-M NSW5A - Planned | 4.9 | 291 | 1425.9 | 0.0014383 | 4.9426e-06
2013-03-28 | 297532 | BNH1B | Rural short | LV Transformer SP895-F BNH1B - Planned | 4 | 205 | 820 | 0.0023548 | 1.1487e-05
2013-03-28 | 297533 | KLG16A | Rural short | Feeder KLG16A - Planned | 17 | 304 | 5168 | 0.014841 | 4.8818e-05
2013-03-28 | 297535 | GAP9A | Urban | LV Transformer SP797524 GAP9A - Planned | 6.075 | 199 | 1208.925 | 0.0012194 | 6.1279e-06
2013-04-02 | 297594 | LLY1 | Rural short | LV Transformer SP714-C LLY1 - Planned | 9 | 97 | 873 | 0.0025088 | 2.5864e-05
2013-04-02 | 297596 | AMR1 | Rural short | LV Transformer SP1551-D AMR1 - Planned | 4.4 | 12 | 52.8 | 0.00015173 | 1.2645e-05
2013-04-02 | 297597 | KBR2A | Rural short | Feeder KBR2A - Planned | 6 | 235 | 1410 | 0.004052 | 1.7243e-05
2013-04-02 | 297598 | KBR5A | Rural short | Feeder KBR5A - Planned | 7 | 178 | 1246 | 0.0035807 | 2.0116e-05
2013-04-02 | 297599 | CPB4 | Urban | LV Transformer SP2794-D CPB4 - Planned | 1 | 278 | 278 | 0.00028032 | 1.0083e-06
2013-04-02 | 297600 | THL1 | Rural short | LV Transformer SP1855-B THL1 - Planned | 3 | 96 | 288 | 0.00082764 | 8.6213e-06
2013-04-02 | 297601 | MCW4 | Rural short | Feeder MCW4 - Planned | 2 | 273 | 546 | 0.0015691 | 5.7475e-06
2013-04-02 | 297603 | MBG1 | Rural short | Feeder MBG1 - Planned | 17.8 | 361 | 6425.8 | 0.018466 | 5.1153e-05
2013-04-02 | 297606 | KLG10A | Urban | LV Transformer SP5879-B KLG10A - Planned | 1 | 465 | 465 | 0.00046888 | 1.0083e-06
2013-04-02 | 297611 | HDA3A | Urban | LV Transformer SP6607-I HDA3A - Planned | 6.48 | 344 | 2229.12 | 0.0022477 | 6.534e-06
2013-04-02 | 297612 | AGE3 | Urban | LV Transformer SP4000-J AGE3 - Planned | 9.48 | 220 | 2085.6 | 0.002103 | 9.559e-06
2013-04-02 | 297613 | KLG11A | Urban | LV Transformer SP3660-E KLG11A - Planned | 17.76 | 158 | 2806.08 | 0.0028295 | 1.7908e-05
2013-04-02 | 297614 | SGT22A | Urban | LV Transformer SC6371-F SGT22A - Planned | 10.29 | 290 | 2984.1 | 0.003009 | 1.0376e-05
2013-04-02 | 297615 | CLM5 | Urban | LV Transformer SP11518-A CLM5 - Planned | 34 | 380 | 12920 | 0.013028 | 3.4284e-05
2013-04-02 | 297616 | CLM5 | Urban | LV Transformer SP4465-A CLM5 - Planned | 54.5 | 430 | 23435 | 0.02363 | 5.4954e-05
2013-04-02 | 297617 | WNM3 | Urban | LV Transformer SP684-R WNM3 - Planned | 12.58 | 321 | 4038.18 | 0.0040719 | 1.2685e-05
2013-04-02 | 297618 | KBR2A | Rural short | LV Transformer SP5151-D KBR2A - Planned | 1 | 216 | 216 | 0.00062073 | 2.8738e-06
2013-04-02 | 297619 | CRBTHP14 | Urban | LV Transformer SP1408-L CRBTHP14 - Planned | 64.8 | 277 | 17949.6 | 0.018099 | 6.534e-05
2013-04-02 | 297620 | GGR1 | Rural short | LV Transformer SP5435-A GGR1 - Planned | 2 | 70 | 140 | 0.00040233 | 5.7475e-06
2013-04-02 | 297621 | HWL1A | Urban | LV Transformer SP5138-G HWL1A - Planned | 21.4928 | 327 | 7028.1456 | 0.0070867 | 2.1672e-05
2013-04-02 | 297622 | MGP4 | Rural short | LV Transformer SP3770-E MGP4 - Planned | 55.08 | 449 | 24730.92 | 0.071071 | 0.00015829
2013-04-02 | 297623 | NRG22A | Urban | LV Transformer SP3398-E NRG22A - Planned | 7.84 | 238 | 1865.92 | 0.0018815 | 7.9054e-06
2013-04-02 | 297625 | MLY3 | Rural short | Feeder MLY3 - Planned | 23.02 | 285 | 6560.7 | 0.018854 | 6.6154e-05
2013-04-02 | 297626 | GBN4 | Rural short | Feeder GBN4 - Planned | 44.529 | 243 | 10820.547 | 0.031096 | 0.00012797
2013-04-02 | 297627 | AMR2 | Rural short | Feeder AMR2 - Planned | 36.0315 | 317 | 11421.9855 | 0.032824 | 0.00010355
2013-04-02 | 297850 | CFD1A | Urban | LV Transformer SG899-K CFD1A - Planned | 1.275 | 337 | 429.675 | 0.00043326 | 1.2856e-06
2013-04-03 | 297675 | BGY5A | Rural short | LV Transformer SP2196-G BGY5A - Planned | 15 | 187 | 2805 | 0.0080616 | 4.311e-05
2013-04-03 | 297676 | NRG16A | Rural short | Feeder NRG16A - Planned | 43 | 123 | 5289 | 0.015201 | 0.00012358
2013-04-03 | 297677 | IPL1 | Rural short | Feeder IPL1 - Planned | 17 | 218 | 3706 | 0.010651 | 4.8858e-05
2013-04-03 | 297678 | BLH16A | Rural short | LV Transformer SG425-G BLH16A - Planned | 1 | 246 | 246 | 0.00070701 | 2.874e-06
2013-04-03 | 297679 | KCY5 | Rural short | Feeder KCY5 - Planned | 18.9 | 305 | 5764.5 | 0.016567 | 5.4319e-05
2013-04-03 | 297680 | YTA23B | Urban | LV Transformer SG1082960 YTA23B - Planned | 2 | 63 | 126 | 0.00012704 | 2.0166e-06
2013-04-03 | 297681 | CMY4 | Rural short | Feeder CMY4 - Planned | 26.715 | 312 | 8335.08 | 0.023955 | 7.6779e-05
2013-04-03 | 297682 | BDT1 | Rural short | Feeder BDT1 - Planned | 13.2 | 361 | 4765.2 | 0.013695 | 3.7937e-05
2013-04-03 | 297687 | MTB17A | Rural short | Feeder MTB17A - Planned | 17.26 | 515 | 8888.9 | 0.025547 | 4.9605e-05
2013-04-03 | 297688 | BDT5 | Rural short | LV Transformer SP404236 BDT5 - Planned | 15 | 434 | 6510 | 0.01871 | 4.311e-05
2013-04-03 | 297690 | BGY5A | Rural short | Feeder BGY5A - Planned | 3 | 427 | 1281 | 0.0036816 | 8.622e-06
2013-04-03 | 297695 | NBR6 | Rural short | Feeder NBR6 - Planned | 21 | 432 | 9072 | 0.026073 | 6.0354e-05
2013-04-03 | 297696 | GBN3 | Rural short | Feeder GBN3 - Planned | 49.965 | 306 | 15289.29 | 0.043942 | 0.0001436
2013-04-03 | 297697 | IBL2 | Rural short | LV Transformer SP6355-B IBL2 - Planned | 1 | 210 | 210 | 0.00060354 | 2.874e-06
2013-04-03 | 297698 | MLY1 | Rural short | Feeder MLY1 - Planned | 32 | 240 | 7680 | 0.022072 | 9.1968e-05
2013-04-03 | 297700 | COR22A | Urban | LV Transformer SP3521-B COR22A - Planned | 2.01 | 57 | 114.57 | 0.00011552 | 2.0267e-06
2013-04-03 | 297701 | COR22A | Urban | LV Transformer SP6416-A COR22A - Planned | 4.98 | 52 | 258.96 | 0.00026111 | 5.0213e-06
2013-04-03 | 297702 | COR22A | Urban | Feeder COR22A - Planned | 66.58 | 102 | 6791.16 | 0.0068474 | 6.7132e-05
2013-04-03 | 297707 | GAP8A | Urban | LV Transformer SC4873-H GAP8A - Planned | 5.24 | 317 | 1661.08 | 0.0016748 | 5.2834e-06
2013-04-03 | 297708 | TRG10B | Urban | LV Transformer SP2131-K TRG10B - Planned | 0.11 | 147 | 16.17 | 1.6304e-05 | 1.1091e-07
2013-04-03 | 297709 | TTF81 | Urban | LV Transformer SP1041-O TTF81 - Planned | 10.24 | 240 | 2457.6 | 0.002478 | 1.0325e-05
2013-04-03 | 297710 | TWG13A | Urban | LV Transformer SP5232-K TWG13A - Planned | 26.64 | 422 | 11242.08 | 0.011335 | 2.6861e-05
2013-04-03 | 297711 | CRB25A | Rural short | LV Transformer SP5799-E CRB25A - Planned | 19 | 225 | 4275 | 0.012286 | 5.4606e-05
2013-04-03 | 297712 | KLG5A | Rural short | LV Transformer SP4102-I KLG5A - Planned | 14 | 171 | 2394 | 0.0068804 | 4.0236e-05
2013-04-03 | 297713 | CSE6 | Urban | LV Transformer SP2576-K CSE6 - Planned | 9.675 | 287 | 2776.725 | 0.0027997 | 9.7552e-06
2013-04-03 | 297714 | BGY5A | Rural short | LV Transformer SP3389-C BGY5A - Planned | 14.405 | 345 | 4969.725 | 0.014283 | 4.14e-05
2013-04-03 | 297715 | CFD2A | Urban | LV Transformer SC4894-H CFD2A - Planned | 5.15 | 204 | 1050.6 | 0.0010593 | 5.1927e-06
2013-04-03 | 297716 | SGT7 | Urban | LV Transformer SP38-K SGT7 - Planned | 8.975 | 257 | 2306.575 | 0.0023257 | 9.0494e-06
2013-04-03 | 297717 | RLB15A | Urban | LV Transformer SC22160-D RLB15A - Planned | 53 | 364 | 19292 | 0.019452 | 5.3439e-05
2013-04-03 | 297718 | MTG13A | Urban | LV Transformer SP3504-F MTG13A - Planned | 12.2 | 380 | 4636 | 0.0046744 | 1.2301e-05
2013-04-03 | 297719 | NIP5A | Urban | LV Transformer SP3785-C NIP5A - Planned | 13.08 | 306 | 4002.48 | 0.0040356 | 1.3188e-05
2013-04-03 | 297720 | WHO1 | Rural short | LV Transformer SP4673-B WHO1 - Planned | 11.96 | 105 | 1255.8 | 0.0036092 | 3.4373e-05
2013-04-03 | 297721 | IPS5B | Urban | LV Transformer SP3489-C IPS5B - Planned | 16 | 280 | 4480 | 0.0045171 | 1.6133e-05
2013-04-03 | 297732 | HWD13A | Urban | LV Transformer SC734734 HWD13A - Planned | 47 | 186 | 8742 | 0.0088144 | 4.7389e-05
2013-04-03 | 297873 | BWH12A | Rural short | Feeder BWH12A - Planned | 84.85 | 520 | 44122 | 0.12681 | 0.00024386
2013-04-04 | 297754 | IPL1 | Rural short | LV Transformer SP1696-E IPL1 - Planned | 1 | 160 | 160 | 0.00045988 | 2.8743e-06
2013-04-04 | 297757 | BWH16A | Rural short | LV Transformer SP11342-B BWH16A - Planned | 31.04 | 224 | 6952.96 | 0.019985 | 8.9217e-05
2013-04-04 | 297759 | IPL2A | Rural short | Feeder IPL2A - Planned | 5.5 | 78 | 429 | 0.0012331 | 1.5808e-05
2013-04-04 | 297760 | RWD2 | Rural short | Feeder RWD2 - Planned | 17 | 165 | 2805 | 0.0080623 | 4.8862e-05
2013-04-04 | 297761 | CPD2A | Rural short | Feeder CPD2A - Planned | 31.89 | 345 | 11002.05 | 0.031623 | 9.166e-05
2013-04-04 | 297762 | SPO67B | Urban | Feeder SPO67B - Planned | 3 | 350 | 1050 | 0.0010587 | 3.0247e-06
2013-04-04 | 297763 | TBV2 | Rural short | Feeder TBV2 - Planned | 30 | 294 | 8820 | 0.025351 | 8.6228e-05
2013-04-04 | 297766 | BLH10A | Urban | LV Transformer SP12382-A BLH10A - Planned | 1 | 346 | 346 | 0.00034885 | 1.0082e-06
2013-04-04 | 297767 | CBT12A | Rural short | LV Transformer SP3173-D CBT12A - Planned | 12 | 495 | 5940 | 0.017073 | 3.4491e-05
2013-04-04 | 297769 | NRG16A | Rural short | Feeder NRG16A - Planned | 169 | 436 | 73684 | 0.21179 | 0.00048575
2013-04-04 | 297771 | GYS3A | Rural short | Feeder GYS3A - Planned | 47.95 | 161 | 7719.95 | 0.022189 | 0.00013782
2013-04-04 | 297773 | COR26A | Rural short | LV Transformer SP10430-A COR26A - Planned | 1 | 118 | 118 | 0.00033916 | 2.8743e-06
2013-04-04 | 297774 | GBN4 | Rural short | LV Transformer SP2295-D GBN4 - Planned | 5 | 10 | 50 | 0.00014371 | 1.4371e-05
2013-04-04 | 297775 | GYGGYS6 | Rural short | Feeder GYGGYS6 - Planned | 29.525 | 11 | 324.775 | 0.00093349 | 8.4862e-05
2013-04-04 | 297776 | GBN4 | Rural short | LV Transformer SP4306-B GBN4 - Planned | 5 | 9 | 45 | 0.00012934 | 1.4371e-05
2013-04-04 | 297777 | CMA8A | Rural short | LV Transformer SC1294741 CMA8A - Planned | 1 | 405 | 405 | 0.0011641 | 2.8743e-06
2013-04-04 | 297778 | AGE10 | Urban | LV Transformer SP522276 AGE10 - Planned | 23.695 | 271 | 6421.345 | 0.0064743 | 2.389e-05
2013-04-04 | 297779 | MGL9 | Rural short | LV Transformer SP10992-H MGL9 - Planned | 22 | 391 | 8602 | 0.024724 | 6.3234e-05
2013-04-04 | 297780 | GYM9B | Rural short | LV Transformer SP661-C GYM9B - Planned | 1.34 | 88 | 117.92 | 0.00033893 | 3.8515e-06
2013-04-04 | 297781 | GYN3A | Rural short | LV Transformer SP991-D GYN3A - Planned | 8.1 | 192 | 1555.2 | 0.00447 | 2.3281e-05
2013-04-04 | 297782 | GBN4 | Rural short | LV Transformer SP5530-B GBN4 - Planned | 2.25 | 106 | 238.5 | 0.00068551 | 6.4671e-06
2013-04-04 | 297783 | PWC4 | Rural short | LV Transformer SP16454-A PWC4 - Planned | 22.7232 | 141 | 3203.9712 | 0.009209 | 6.5312e-05
2013-04-04 | 297784 | GYS3A | Rural short | LV Transformer SP537-C GYS3A - Planned | 1 | 70 | 70 | 0.0002012 | 2.8743e-06
2013-04-04 | 297786 | CRB25A | Rural short | LV Transformer SP796211 CRB25A - Planned | 13.75 | 357 | 4908.75 | 0.014109 | 3.9521e-05
2013-04-04 | 297787 | CCY13A | Urban | LV Transformer SP6361-F CCY13A - Planned | 53.34 | 206 | 10988.04 | 0.011079 | 5.378e-05
2013-04-04 | 297788 | HWL13A | Urban | LV Transformer SC22764-D HWL13A - Planned | 29.12 | 11 | 320.32 | 0.00032296 | 2.936e-05
2013-04-04 | 297789 | MGP17A | Urban | LV Transformer SC764535 MGP17A - Planned | 0.99 | 108 | 106.92 | 0.0001078 | 9.9816e-07
2013-04-04 | 297791 | SPO69A | Urban | LV Transformer SP10030-E SPO69A - Planned | 52.2 | 380 | 19836 | 0.02 | 5.263e-05
2013-04-04 | 297792 | BHL5A | Urban | LV Transformer SP3192-I SGT24A - Planned | 15.47 | 217 | 3356.99 | 0.0033847 | 1.5598e-05
2013-04-04 | 297792 | SGT24A | Urban | LV Transformer SP3192-I SGT24A - Planned | 2.46 | 217 | 533.82 | 0.00053822 | 2.4803e-06
2013-04-04 | 297793 | ZMR7A | Urban | LV Transformer SP5865-G ZMR7A - Planned | 15.5862 | 243 | 3787.4466 | 0.0038187 | 1.5715e-05
2013-04-04 | 297794 | BGY15A | Urban | LV Transformer SP8626-B BGY15A - Planned | 10.295 | 248 | 2553.16 | 0.0025742 | 1.038e-05
2013-04-04 | 297795 | RLB16A | Rural short | LV Transformer SP2400-F RLB16A - Planned | 5.59 | 404 | 2258.36 | 0.0064911 | 1.6067e-05
2013-04-04 | 297796 | ARG5A | Urban | LV Transformer SP866-L ARG5A - Planned | 17.79 | 386 | 6866.94 | 0.0069235 | 1.7937e-05
2013-04-04 | 297797 | MTG12B | Urban | LV Transformer SP27540-E MTG12B - Planned | 8.0822 | 397 | 3208.6334 | 0.0032351 | 8.1488e-06
2013-04-04 | 297798 | WRG6A | Urban | LV Transformer SP1606-L WRG6A - Planned | 5.76 | 224 | 1290.24 | 0.0013009 | 5.8075e-06
2013-04-04 | 297799 | RWD1 | Rural short | LV Transformer SP1204-H RWD1 - Planned | 2 | 339 | 678 | 0.0019487 | 5.7485e-06
2013-04-04 | 297800 | CRM16A | Rural short | LV Transformer SC510456 CRM16A - Planned | 7.9563 | 36 | 286.4268 | 0.00082326 | 2.2868e-05
2013-04-04 | 297801 | CRM16A | Rural short | LV Transformer SC510456 CRM16A - Planned | 10.01 | 27 | 270.27 | 0.00077682 | 2.8771e-05
2013-04-04 | 297802 | CRM16A | Rural short | LV Transformer SC510456 CRM16A - Planned | 1.88 | 37 | 69.56 | 0.00019993 | 5.4036e-06
2013-04-04 | 297874 | CRB25A | Rural short | LV Transformer SP5766-F CRB25A - Planned | 5 | 362 | 1810 | 0.0052024 | 1.4371e-05
2013-04-05 | 297817 | NRG22A | Urban | LV Transformer SP11136-E NRG22A - Planned | 19 | 186 | 3534 | 0.0035629 | 1.9156e-05
2013-04-05 | 297819 | EMD3 | Rural short | Feeder EMD3 - Planned | 56 | 229 | 12824 | 0.036864 | 0.00016098
2013-04-05 | 297820 | MSV2 | Rural short | LV Transformer SP3050-C MSV2 - Planned | 3.5 | 255 | 892.5 | 0.0025656 | 1.0061e-05
2013-04-05 | 297821 | THL1 | Rural short | LV Transformer SP3118-B THL1 - Planned | 3 | 237 | 711 | 0.0020438 | 8.6238e-06
2013-04-05 | 297823 | BHD35A | Rural short | LV Transformer SP5805-F BHD35A - Planned | 40.5 | 280 | 11340 | 0.032598 | 0.00011642
2013-04-05 | 297824 | NRA13A | Rural short | LV Transformer SP4162-F NRA13A - Planned | 9 | 326 | 2934 | 0.0084341 | 2.5871e-05
2013-04-05 | 297827 | GYGGYS6 | Rural short | Feeder GYGGYS6 - Planned | 68 | 285 | 19380 | 0.05571 | 0.00019547
2013-04-05 | 297829 | WHO1 | Rural short | Feeder WHO1 - Planned | 23 | 318 | 7314 | 0.021025 | 6.6116e-05
2013-04-05 | 297830 | JBB16A | Rural short | Feeder JBB16A - Planned | 18.5 | 370 | 6845 | 0.019677 | 5.318e-05
2013-04-05 | 297831 | GBN2 | Rural short | Feeder GBN2 - Planned | 11 | 300 | 3300 | 0.0094862 | 3.1621e-05
2013-04-05 | 297832 | CPC3B | Urban | LV Transformer SC769218 CPC3B - Planned | 2 | 450 | 900 | 0.00090737 | 2.0164e-06
2013-04-05 | 297833 | CRY2A | Rural short | Feeder CRY2A - Planned | 26.5 | 231 | 6121.5 | 0.017597 | 7.6177e-05
2013-04-05 | 297836 | MLY3 | Rural short | Feeder MLY3 - Planned | 61 | 356 | 21716 | 0.062425 | 0.00017535
2013-04-05 | 297837 | PPE13A | Rural short | Feeder PPE13A - Planned | 2 | 551 | 1102 | 0.0031678 | 5.7492e-06
2013-04-05 | 297839 | ENG3 | Urban | LV Transformer SP1066-N ENG3 - Planned | 0.95 | 181 | 171.95 | 0.00017336 | 9.5778e-07
2013-04-05 | 297840 | LBH5A | Rural short | LV Transformer SP2737-B LBH5A - Planned | 6.05 | 85 | 514.25 | 0.0014783 | 1.7391e-05
2013-04-05 | 297841 | GYM7A | Rural short | LV Transformer SP1217-E GYM7A - Planned | 9 | 112 | 1008 | 0.0028976 | 2.5871e-05
2013-04-05 | 297842 | NRG22A | Urban | LV Transformer SP3399-F NRG22A - Planned | 58.025 | 273 | 15840.825 | 0.015971 | 5.85e-05
2013-04-05 | 297843 | CRB15A | Urban | LV Transformer SC748370 CRB15A - Planned | 1.02 | 58 | 59.16 | 5.9644e-05 | 1.0283e-06
2013-04-05 | 297844 | PPE13A | Rural short | LV Transformer SP94562-B PPE13A - Planned | 2 | 400 | 800 | 0.0022997 | 5.7492e-06
2013-04-05 | 297845 | MAI17 | Urban | LV Transformer SP64376-D MAI17 - Planned | 28.5888 | 305 | 8719.584 | 0.008791 | 2.8823e-05
2013-04-05 | 297846 | JBB16A | Rural short | LV Transformer SP4854-E JBB16A - Planned | 3.825 | 367 | 1403.775 | 0.0040353 | 1.0995e-05
2013-04-05 | 297847 | DBY6 | Urban | LV Transformer SP1908-F DBY6 - Planned | 2.1 | 203 | 426.3 | 0.00042979 | 2.1172e-06
2013-04-05 | 297848 | CFD1A | Urban | LV Transformer SP20439-F CFD1A - Planned | 51.51 | 393 | 20243.43 | 0.020409 | 5.1932e-05
2013-04-05 | 297849 | TGP6A | Urban | LV Transformer SC4111-K TGP6A - Planned | 26.88 | 297 | 7983.36 | 0.0080487 | 2.71e-05
2013-04-05 | 297851 | SGT22A | Urban | LV Transformer SP11821-F SGT22A - Planned | 27.63 | 256 | 7073.28 | 0.0071312 | 2.7856e-05
2013-04-05 | 297852 | BBSRDL8 | Rural short | LV Transformer SP275-M BBSRDL8 - Planned | 8.8 | 295 | 2596 | 0.0074625 | 2.5296e-05
2013-04-05 | 297853 | BLBNFM6 | Urban | LV Transformer SP5394-E BLBNFM6 - Planned | 23.1 | 121 | 2795.1 | 0.002818 | 2.3289e-05
2013-04-05 | 297862 | AMR1 | Rural short | Feeder AMR1 - Planned | 61.64 | 236 | 14547.04 | 0.041817 | 0.00017719
2013-04-05 | 297865 | CRB25A | Rural short | LV Transformer SP5677-F CRB25A - Planned | 4.275 | 364 | 1556.1 | 0.0044732 | 1.2289e-05
2013-04-05 | 297877 | BPN26A | Rural short | LV Transformer SC534421 BPN26A - Planned | 3 | 163 | 489 | 0.0014057 | 8.6238e-06
2013-04-05 | 297880 | WFD2B | Rural short | Feeder WFD2B - Planned | 132 | 170 | 22440 | 0.064506 | 0.00037945
2013-04-05 | 297894 | PWC6 | Rural short | Feeder PWC6 - Planned | 43 | 295 | 12685 | 0.036464 | 0.00012361
2013-04-06 | 297866 | MLY3 | Rural short | Feeder MLY3 - Planned | 66.99 | 211 | 14134.89 | 0.040637 | 0.00019259
2013-04-06 | 297872 | GBN3 | Rural short | Feeder GBN3 - Planned | 8 | 281 | 2248 | 0.0064629 | 2.3e-05
2013-04-06 | 297876 | SGT7 | Urban | LV Transformer SP1612-J SGT7 - Planned | 6.39 | 368 | 2351.52 | 0.0023706 | 6.4419e-06
2013-04-06 | 297878 | SPO41A | Urban | LV Transformer SP2500-H SPO41A - Planned | 18.45 | 228 | 4206.6 | 0.0042408 | 1.86e-05
2013-04-07 | 297895 | OXL8A | Urban | Feeder OXL8A - Planned | 9 | 188 | 1692 | 0.0017057 | 9.0728e-06
2013-04-07 | 297896 | LLY1 | Rural short | Feeder LLY1 - Planned | 221.66 | 136 | 30145.76 | 0.086674 | 0.00063731
2013-04-07 | 297898 | OXL8A | Urban | Feeder OXL8A - Planned | 0.4 | 280 | 112 | 0.00011291 | 4.0324e-07
2013-04-07 | 297899 | BLB4A | Urban | LV Transformer SG5219-J BLB4A - Planned | 1 | 392 | 392 | 0.00039517 | 1.0081e-06
2013-04-07 | 297900 | KCY2 | Rural short | Feeder KCY2 - Planned | 103.25 | 419 | 43261.75 | 0.12438 | 0.00029686
2013-04-07 | 297902 | AGE7B | Urban | LV Transformer SC1500260 ENG2 - Planned | 19.01 | 332 | 6311.32 | 0.0063624 | 1.9164e-05
2013-04-07 | 297902 | ENG2 | Urban | LV Transformer SC1500260 ENG2 - Planned | 26.4 | 332 | 8764.8 | 0.0088357 | 2.6614e-05
2013-04-07 | 297903 | HTN22B | Urban | LV Transformer SC6164-F HTN22B - Planned | 39.2 | 216 | 8467.2 | 0.0085357 | 3.9517e-05
2013-04-07 | 297904 | GLY15A | Urban | LV Transformer SP3326-J GLY3A - Planned | 10.14 | 60 | 608.4 | 0.00061332 | 1.0222e-05
2013-04-07 | 297904 | GLY3A | Urban | LV Transformer SP3326-J GLY3A - Planned | 18.59 | 60 | 1115.4 | 0.0011244 | 1.874e-05
2013-04-07 | 297905 | SGT7 | Urban | LV Transformer SP3057-G SGT7 - Planned | 1.7666 | 424 | 749.0384 | 0.0007551 | 1.7809e-06
2013-04-07 | 297906 | CFD2A | Urban | LV Transformer SC3466-F CFD2A - Planned | 10.95 | 348 | 3810.6 | 0.0038414 | 1.1039e-05
2013-04-07 | 297906 | HDA11A | Urban | LV Transformer SC3466-F CFD2A - Planned | 17.12 | 348 | 5957.76 | 0.006006 | 1.7259e-05
2013-04-07 | 297907 | SGT7 | Urban | LV Transformer SP5283-G SGT7 - Planned | 25.2 | 428 | 10785.6 | 0.010873 | 2.5404e-05
2013-04-07 | 297908 | BLB4A | Urban | LV Transformer SP808389 BLB4A - Planned | 10.63 | 397 | 4220.11 | 0.0042543 | 1.0716e-05
2013-04-07 | 298238 | STT3A | Rural short | Feeder STT3A - Planned | 4 | 419 | 1676 | 0.0048188 | 1.1501e-05
2013-04-08 | 297913 | CBW6 | Rural short | LV Transformer SP3260-F CBW6 - Planned | 36 | 60 | 2160 | 0.0062124 | 0.00010354
2013-04-08 | 297915 | LRE6A | Rural short | LV Transformer SP1946-C LRE6A - Planned | 14.5 | 80 | 1160 | 0.0033363 | 4.1704e-05
2013-04-08 | 297916 | SGT7 | Urban | LV Transformer SP5477-F SGT7 - Planned | 35.5 | 175 | 6212.5 | 0.0062617 | 3.5781e-05
2013-04-08 | 297917 | RPN4A | Rural short | LV Transformer SP3059-D RPN4A - Planned | 1 | 195 | 195 | 0.00056085 | 2.8761e-06
2013-04-08 | 297920 | WMR1 | Rural short | Feeder WMR1 - Planned | 12 | 269 | 3228 | 0.0092841 | 3.4514e-05
2013-04-08 | 297921 | JBB3A | Rural short | Feeder JBB3A - Planned | 19 | 339 | 6441 | 0.018525 | 5.4646e-05
2013-04-08 | 297942 | MGL8 | Urban | LV Transformer SP4447-K MGL8 - Planned | 7.04 | 342 | 2407.68 | 0.0024268 | 7.0958e-06
2013-04-08 | 297943 | GYS5A | Rural short | Feeder GYS5A - Planned | 13.84 | 61 | 844.24 | 0.0024281 | 3.9806e-05
2013-04-08 | 297944 | GYS5A | Rural short | Feeder GYS5A - Planned | 14.68 | 402 | 5901.36 | 0.016973 | 4.2222e-05
2013-04-08 | 297945 | MGL9 | Rural short | LV Transformer SP3393-I MGL9 - Planned | 11.285 | 251 | 2832.535 | 0.0081467 | 3.2457e-05
2013-04-08 | 297946 | BMT1 | Rural short | Feeder BMT1 - Planned | 38.16 | 288 | 10990.08 | 0.031609 | 0.00010975
2013-04-08 | 297947 | COR22A | Rural short | Feeder COR22A - Planned | 17.39 | 213 | 3704.07 | 0.010653 | 5.0016e-05
2013-04-08 | 297948 | CLM8 | Urban | LV Transformer SP176043 CLM8 - Planned | 20.01 | 272 | 5442.72 | 0.0054858 | 2.0168e-05
2013-04-08 | 297949 | HWL10A | Urban | LV Transformer SP3032-F HWL10A - Planned | 5.9448 | 306 | 1819.1088 | 0.0018335 | 5.9919e-06
2013-04-08 | 297950 | GYN5A | Urban | LV Transformer SP2651-E GYN5A - Planned | 8.64 | 80 | 691.2 | 0.00069667 | 8.7084e-06
2013-04-08 | 297951 | BLH16A | Rural short | LV Transformer SP4722-C BLH16A - Planned | 11.48 | 210 | 2410.8 | 0.0069338 | 3.3018e-05
2013-04-08 | 297952 | HIS3A | Urban | LV Transformer SC791978 HIS3A - Planned | 27.05 | 30 | 811.5 | 0.00081793 | 2.7264e-05
2013-04-08 | 297952 | HIS5B | Urban | LV Transformer SC791978 HIS3A - Planned | 1.14 | 30 | 34.2 | 3.4471e-05 | 1.149e-06
2013-04-08 | 297953 | HDA13A | Urban | LV Transformer SP20549-H HDA13A - Planned | 27.93 | 255 | 7122.15 | 0.0071786 | 2.8151e-05
2013-04-08 | 297953 | HDA3A | Urban | LV Transformer SP20549-H HDA13A - Planned | 14.04 | 255 | 3580.2 | 0.0036086 | 1.4151e-05
2013-04-08 | 297953 | HTN3A | Urban | LV Transformer SP20549-H HDA13A - Planned | 1.95 | 255 | 497.25 | 0.00050119 | 1.9654e-06
2013-04-08 | 297954 | WNM5 | Urban | LV Transformer SC521532-B WNM5 - Planned | 3.27 | 220 | 719.4 | 0.0007251 | 3.2959e-06
2013-04-08 | 297955 | ACR3 | Urban | LV Transformer SP17315-D ACR3 - Planned | 0.98 | 47 | 46.06 | 4.6425e-05 | 9.8776e-07
2013-04-08 | 297956 | THL3 | Rural short | LV Transformer SP916-B THL3 - Planned | 4.98 | 126 | 627.48 | 0.0018047 | 1.4323e-05
2013-04-08 | 297957 | THL3 | Rural short | LV Transformer SP1650-E THL3 - Planned | 7 | 47 | 329 | 0.00094625 | 2.0133e-05
2013-04-09 | 297973 | GGR1 | Rural short | LV Transformer SP8252-B GGR1 - Planned | 6 | 44 | 264 | 0.00075946 | 1.726e-05
2013-04-09 | 297975 | GGR2 | Rural short | LV Transformer SP13990-A GGR2 - Planned | 6.5 | 327 | 2125.5 | 0.0061145 | 1.8699e-05
2013-04-09 | 297976 | RLB16A | Rural short | Feeder RLB16A - Planned | 21.5 | 300 | 6450 | 0.018555 | 6.185e-05
2013-04-09 | 297977 | BNH1B | Rural short | Feeder BNH1B - Planned | 29 | 348 | 10092 | 0.029032 | 8.3425e-05
2013-04-09 | 297993 | MGP1 | Rural short | LV Transformer SC67-G MGP1 - Planned | 27 | 406 | 10962 | 0.031535 | 7.7672e-05
2013-04-09 | 297994 | BHD35A | Rural short | Feeder BHD35A - Planned | 11 | 430 | 4730 | 0.013607 | 3.1644e-05
2013-04-09 | 297995 | DRD3A | Urban | LV Transformer SC104-L DRD3A - Planned | 1 | 54 | 54 | 5.4422e-05 | 1.0078e-06
2013-04-09 | 297996 | SMF3A | Rural short | LV Transformer SP15752-E SMF3A - Planned | 2 | 513 | 1026 | 0.0029515 | 5.7535e-06
2013-04-09 | 297998 | SRD19A | Urban | LV Transformer SC6072-C SRD19A - Planned | 21.06 | 303 | 6381.18 | 0.0064311 | 2.1225e-05
2013-04-09 | 297999 | GAP9A | Urban | LV Transformer SC4269-M GAP9A - Planned | 34.32 | 315 | 10810.8 | 0.010895 | 3.4588e-05
2013-04-09 | 298000 | INA2A | Urban | LV Transformer SP27353-D INA2A - Planned | 29.04 | 226 | 6563.04 | 0.0066144 | 2.9267e-05
2013-04-09 | 298002 | CLM7 | Urban | LV Transformer SP163869 CLM7 - Planned | 19.02 | 255 | 4850.1 | 0.004888 | 1.9169e-05
2013-04-09 | 298003 | CLM4A | Urban | LV Transformer SP2832-A CLM4A - Planned | 15.29 | 115 | 1758.35 | 0.0017721 | 1.541e-05
2013-04-09 | 298004 | LDR8 | Urban | LV Transformer SP13669-B LDR8 - Planned | 12.425 | 363 | 4510.275 | 0.0045455 | 1.2522e-05
2013-04-09 | 298005 | BLH15B | Urban | LV Transformer SP5974-C BLH15B - Planned | 1.875 | 212 | 397.5 | 0.00040061 | 1.8897e-06
2013-04-09 | 298007 | MGP1 | Rural short | LV Transformer SP5125-F MGP1 - Planned | 36.795 | 274 | 10081.83 | 0.029003 | 0.00010585
2013-04-09 | 298008 | MRE1 | Urban | LV Transformer SC4824-L MRE1 - Planned | 28.7 | 405 | 11623.5 | 0.011714 | 2.8924e-05
2013-04-09 | 298010 | ACR6 | Urban | LV Transformer SC619556 ACR6 - Planned | 6.21 | 235 | 1459.35 | 0.0014708 | 6.2586e-06
2013-04-09 | 298011 | SGT24A | Urban | LV Transformer SP3793-D SGT24A - Planned | 13.87 | 64 | 887.68 | 0.00089462 | 1.3978e-05
2013-04-09 | 298012 | CSE6 | Urban | LV Transformer SP13200-E CSE6 - Planned | 38.2 | 398 | 15203.6 | 0.015322 | 3.8499e-05
2013-04-09 | 298013 | SGT7 | Urban | LV Transformer SP783-L SGT7 - Planned | 30.96 | 173 | 5356.08 | 0.005398 | 3.1202e-05
2013-04-09 | 298014 | MTNQBI9 | Urban | LV Transformer SP499-G MTNQBI9 - Planned | 1 | 206 | 206 | 0.00020761 | 1.0078e-06
2013-04-09 | 298015 | CHL11A | Rural short | LV Transformer SP24662-G CHL11A - Planned | 6.885 | 326 | 2244.51 | 0.0064569 | 1.9806e-05
2013-04-09 | 298016 | HPE13A | Urban | LV Transformer SP29686-C HPE13A - Planned | 15.4 | 260 | 4004 | 0.0040353 | 1.552e-05
2013-04-09 | 298017 | MTG12B | Urban | LV Transformer SP27540-E MTG12B - Planned | 15.1102 | 316 | 4774.8232 | 0.0048122 | 1.5228e-05
2013-04-09 | 298018 | CPD1 | Rural short | LV Transformer SP2341-C CPD1 - Planned | 3 | 175 | 525 | 0.0015103 | 8.6302e-06
2013-04-09 | 298019 | RPN4A | Rural short | LV Transformer SC1292803 RPN4A - Planned | 9.27 | 84 | 778.68 | 0.0022401 | 2.6667e-05
2013-04-09 | 298026 | GARTR5H | Urban | LV Transformer SSCHA GARTR5H - Planned | 2 | 256 | 512 | 0.000516 | 2.0156e-06
2013-04-09 | 298046 | COR22A | Rural short | Feeder COR22A - Planned | 4.5 | 240 | 1080 | 0.0031069 | 1.2945e-05
2013-04-09 | 298047 | NBR8 | Rural short | Feeder NBR8 - Planned | 22 | 270 | 5940 | 0.017088 | 6.3288e-05
2013-04-09 | 298048 | AMR3 | Rural short | Feeder AMR3 - Planned | 67.01 | 323 | 21644.23 | 0.062265 | 0.00019277
2013-04-09 | 298049 | GBN4 | Rural short | LV Transformer SP880-B GBN4 - Planned | 2.5 | 14 | 35 | 0.00010069 | 7.1918e-06
2013-04-09 | 298050 | TWT6B | Rural short | Feeder TWT6B - Planned | 95 | 58 | 5510 | 0.015851 | 0.00027329
2013-04-10 | 298035 | RIS2 | Urban | Feeder RIS2 - Planned | 72 | 104 | 7488 | 0.0075461 | 7.2558e-05
2013-04-10 | 298036 | LLY5 | Rural short | LV Transformer SP8244-B LLY5 - Planned | 3 | 101 | 303 | 0.00087176 | 8.6313e-06
2013-04-10 | 298038 | RIS2 | Urban | Feeder RIS2 - Planned | 70 | 56 | 3920 | 0.0039504 | 7.0543e-05
2013-04-10 | 298039 | TGW2 | Rural short | LV Transformer SP17217-A TGW2 - Planned | 4 | 217 | 868 | 0.0024973 | 1.1508e-05
2013-04-10 | 298041 | PRG2A | Rural short | Feeder PRG2A - Planned | 20 | 337 | 6740 | 0.019392 | 5.7542e-05
2013-04-10 | 298043 | BDT1 | Rural short | Feeder BDT1 - Planned | 13.2 | 464 | 6124.8 | 0.017622 | 3.7978e-05
2013-04-10 | 298044 | GBN4 | Rural short | Feeder GBN4 - Planned | 39.5 | 343 | 13548.5 | 0.038981 | 0.00011365
2013-04-10 | 298045 | MLY1 | Rural short | Feeder MLY1 - Planned | 56.01 | 407 | 22796.07 | 0.065587 | 0.00016115
2013-04-10 | 298051 | KWH3 | Rural short | Feeder KWH3 - Planned | 59 | 366 | 21594 | 0.062128 | 0.00016975
2013-04-10 | 298052 | COR22A | Rural short | Feeder COR22A - Planned | 29 | 100 | 2900 | 0.0083436 | 8.3436e-05
2013-04-10 | 298053 | MGP13A | Rural short | LV Transformer SP2325-H MGP13A - Planned | 1 | 370 | 370 | 0.0010645 | 2.8771e-06
2013-04-10 | 298054 | AMR2 | Rural short | LV Transformer SP2918-C AMR2 - Planned | 8.74 | 148 | 1293.52 | 0.0037216 | 2.5146e-05
2013-04-10 | 298055 | TWT5B | Rural short | LV Transformer SP7631-C TWT6B - Planned | 2.24 | 145 | 324.8 | 0.00093449 | 6.4447e-06
2013-04-10 | 298055 | TWT6B | Rural short | LV Transformer SP7631-C TWT6B - Planned | 13.83 | 145 | 2005.35 | 0.0057696 | 3.979e-05
2013-04-10 | 298056 | MDR2A | Urban | LV Transformer SC710-H MDR2A - Planned | 2.805 | 90 | 252.45 | 0.00025441 | 2.8268e-06
2013-04-10 | 298057 | MGP16A | Urban | LV Transformer SP6302-C MGP16A - Planned | 30.34 | 313 | 9496.42 | 0.0095701 | 3.0575e-05
2013-04-10 | 298058 | CRB22A | Urban | LV Transformer SP1386647 CRB22A - Planned | 13 | 276 | 3588 | 0.0036158 | 1.3101e-05
2013-04-10 | 298059 | SPO69A | Urban | LV Transformer SP10030-E SPO69A - Planned | 36.82 | 178 | 6553.96 | 0.0066048 | 3.7106e-05
2013-04-10 | 298060 | CFD6A | Urban | LV Transformer SP2489-L CFD6A - Planned | 8.7 | 210 | 1827 | 0.0018412 | 8.7675e-06
2013-04-10 | 298061 | SGT7 | Urban | LV Transformer SP783-L SGT7 - Planned | 15.12 | 193 | 2918.16 | 0.0029408 | 1.5237e-05
2013-04-10 | 298063 | HDA10A | Urban | LV Transformer SP310-J NDH5A - Planned | 1.7 | 342 | 581.4 | 0.00058591 | 1.7132e-06
2013-04-10 | 298063 | NDH5A | Urban | LV Transformer SP310-J NDH5A - Planned | 12.755 | 342 | 4362.21 | 0.004396 | 1.2854e-05
2013-04-10 | 298064 | CSE6 | Urban | LV Transformer SP11109-E CSE6 - Planned | 25.92 | 142 | 3680.64 | 0.0037092 | 2.6121e-05
2013-04-10 | 298065 | ZMR9 | Urban | LV Transformer SP29524-C ZMR9 - Planned | 1.7033 | 92 | 156.7036 | 0.00015792 | 1.7165e-06
2013-04-10 | 298066 | ARG5A | Urban | LV Transformer SP2472-M ARG5A - Planned | 22.77 | 369 | 8402.13 | 0.0084673 | 2.2947e-05
2013-04-10 | 298067 | LHM8A | Rural short | LV Transformer SP4460-C LHM8A - Planned | 3.15 | 216 | 680.4 | 0.0019576 | 9.0629e-06
2013-04-10 | 298068 | CHL11A | Rural short | LV Transformer SP1823-J CHL11A - Planned | 10.4 | 308 | 3203.2 | 0.009216 | 2.9922e-05
2013-04-10 | 298069 | RIS2 | Urban | LV Transformer SP767428 RIS2 - Planned | 15.755 | 80 | 1260.4 | 0.0012702 | 1.5877e-05
2013-04-10 | 298070 | RIS2 | Urban | LV Transformer SP10519-B RIS2 - Planned | 9.49 | 75 | 711.75 | 0.00071727 | 9.5636e-06
2013-04-10 | 298071 | HPE13A | Urban | LV Transformer SC139-K HPE13A - Planned | 37.84 | 440 | 16649.6 | 0.016779 | 3.8133e-05
2013-04-10 | 298071 | HPE5A | Urban | LV Transformer SC139-K HPE13A - Planned | 6.925 | 440 | 3047 | 0.0030706 | 6.9787e-06
2013-04-10 | 298072 | CRM16A | Rural short | LV Transformer SC510456 CRM16A - Planned | 0.77 | 14.5 | 22.33 | 6.4246e-05 | 2.2154e-06
2013-04-10 | 298073 | TMH15A | Urban | LV Transformer SP4107-F TMH15A - Planned | 17.17 | 319 | 5477.23 | 0.0055197 | 1.7303e-05
2013-04-10 | 298074 | WRG12A | Urban | LV Transformer SP2644-L WRG1A - Planned | 11.655 | 225 | 2622.375 | 0.0026427 | 1.1745e-05
2013-04-10 | 298074 | WRG1A | Urban | LV Transformer SP2644-L WRG1A - Planned | 14.11 | 225 | 3174.75 | 0.0031994 | 1.4219e-05
2013-04-10 | 298085 | MTG8A | Urban | LV Transformer SC3948-G MTG8A - Planned | 2.7415 | 118 | 323.497 | 0.00032601 | 2.7628e-06
2013-04-11 | 298095 | BDT5 | Rural short | LV Transformer SP7218-D BDT5 - Planned | 3 | 15 | 45 | 0.00012949 | 8.6324e-06
2013-04-11 | 298096 | EZRRWD4 | Rural short | LV Transformer SP4427-F EZRRWD4 - Planned | 5 | 100 | 500 | 0.0014387 | 1.4387e-05
2013-04-11 | 298098 | SPC2B | Rural short | LV Transformer SP5394-B SPC2B - Planned | 1 | 337 | 337 | 0.0009697 | 2.8775e-06
2013-04-11 | 298114 | SGT7 | Urban | LV Transformer SC484276-B SGT7 - Planned | 1 | 256 | 256 | 0.00025797 | 1.0077e-06
2013-04-11 | 298115 | RWD1 | Rural short | Feeder RWD1 - Planned | 8 | 396 | 3168 | 0.0091158 | 2.302e-05
2013-04-11 | 298116 | TGW1 | Rural short | Feeder TGW1 - Planned | 14.769 | 428 | 6321.132 | 0.018189 | 4.2497e-05
2013-04-11 | 298117 | CBT12A | Rural short | Feeder CBT12A - Planned | 45 | 500 | 22500 | 0.064743 | 0.00012949
2013-04-11 | 298119 | BWH16A | Rural short | LV Transformer SP293-A BWH16A - Planned | 16 | 96 | 1536 | 0.0044198 | 4.6039e-05
2013-04-11 | 298120 | VPK9A | Urban | LV Transformer SP6148-E VPK9A - Planned | 33.74 | 204 | 6882.96 | 0.006936 | 3.4e-05
2013-04-11 | 298121 | AGE2 | Urban | LV Transformer SP1239-M AGE2 - Planned | 10.2247 | 369 | 3772.9143 | 0.003802 | 1.0303e-05
2013-04-11 | 298122 | AGE10 | Urban | LV Transformer SP2329-L AGE10 - Planned | 22 | 315 | 6930 | 0.0069834 | 2.2169e-05
2013-04-11 | 298123 | MGL9 | Rural short | LV Transformer SP1903-K MGL9 - Planned | 6 | 404 | 2424 | 0.0069749 | 1.7265e-05
2013-04-11 | 298124 | NSD8A | Urban | LV Transformer SG2572-N NSD8A - Planned | 14.94 | 281 | 4198.14 | 0.0042305 | 1.5055e-05
2013-04-11 | 298125 | SMR12A | Urban | LV Transformer SC4878-H SMR12A - Planned | 27.27 | 204 | 5563.08 | 0.0056059 | 2.748e-05
2013-04-11 | 298126 | CLM5 | Urban | LV Transformer SP5222-A CLM5 - Planned | 9.68 | 202 | 1955.36 | 0.0019704 | 9.7545e-06
2013-04-11 | 298127 | CLM7 | Urban | LV Transformer SP2256-B CLM7 - Planned | 15.535 | 229 | 3557.515 | 0.0035849 | 1.5655e-05
2013-04-11 | 298128 | SPO51A | Urban | LV Transformer SP6469-G SPO51A - Planned | 40.96 | 333 | 13639.68 | 0.013745 | 4.1275e-05
2013-04-11 | 298129 | RBA37A | Urban | LV Transformer SP5215-H RBA37A - Planned | 10.33 | 193 | 1993.69 | 0.002009 | 1.041e-05
2013-04-11 | 298130 | SPD12B | Urban | LV Transformer SC22763-G SPD12B - Planned | 2.02 | 252 | 509.04 | 0.00051296 | 2.0356e-06
2013-04-11 | 298131 | SPO69A | Urban | LV Transformer SP6436-F SPO69A - Planned | 22.55 | 394 | 8884.7 | 0.0089531 | 2.2724e-05
2013-04-11 | 298132 | SPO67B | Urban | LV Transformer SP467934 SPO67B - Planned | 1.05 | 202 | 212.1 | 0.00021373 | 1.0581e-06
2013-04-11 | 298133 | CRB24B | Urban | LV Transformer SP1108-J CRB24B - Planned | 47.775 | 275 | 13138.125 | 0.013239 | 4.8143e-05
2013-04-11 | 298134 | RBA43A | Rural short | LV Transformer SC1455481 RBA43A - Planned | 5 | 58 | 290 | 0.00083446 | 1.4387e-05
2013-04-11 | 298135 | CBT13A | Urban | LV Transformer SC1051097 CBT13A - Planned | 0.98 | 89 | 87.22 | 8.7892e-05 | 9.8755e-07
2013-04-11 | 298136 | KRN2 | Urban | LV Transformer SP19611-D KRN2 - Planned | 30.61 | 340 | 10407.4 | 0.010488 | 3.0846e-05
2013-04-11 | 298137 | DRD15B | Urban | LV Transformer SP9656-C DRD15B - Planned | 27.275 | 350 | 9546.25 | 0.0096198 | 2.7485e-05
2013-04-11 | 298138 | WNM5 | Urban | LV Transformer SP6708-G WNM5 - Planned | 26.13 | 288 | 7525.44 | 0.0075834 | 2.6331e-05
2013-04-11 | 298139 | SGT7 | Urban | LV Transformer SP3057-G SGT7 - Planned | 7.9497 | 201 | 1597.8897 | 0.0016102 | 8.0109e-06
2013-04-11 | 298140 | ARG5A | Urban | LV Transformer SP14342-F ARG5A - Planned | 10.08 | 378 | 3810.24 | 0.0038396 | 1.0158e-05
2013-04-11 | 298140 | SBK11 | Urban | LV Transformer SP14342-F ARG5A - Planned | 1.92 | 378 | 725.76 | 0.00073135 | 1.9348e-06
2013-04-11 | 298141 | BLBNFM6 | Urban | LV Transformer SP2362-M BLBNFM6 - Planned | 3.24 | 238 | 771.12 | 0.00077706 | 3.265e-06
2013-04-11 | 298142 | CMV9A | Urban | LV Transformer SC6613-E CMV9A - Planned | 5.36 | 335 | 1795.6 | 0.0018094 | 5.4013e-06
2013-04-11 | 298143 | RLB16A | Rural short | LV Transformer SP2400-F RLB16A - Planned | 12.09 | 314 | 3796.26 | 0.010924 | 3.4788e-05
2013-04-11 | 298144 | LGL11A | Urban | LV Transformer SP6066-C LGL11A - Planned | 5.2 | 264 | 1372.8 | 0.0013834 | 5.24e-06
2013-04-11 | 298145 | AGT37A | Urban | LV Transformer SC3949-H AGT37A - Planned | 7.995 | 390 | 3118.05 | 0.0031421 | 8.0566e-06
2013-04-11 | 298146 | WHO2 | Rural short | LV Transformer SP1252-C WHO2 - Planned | 2.04 | 262 | 534.48 | 0.0015379 | 5.87e-06
2013-04-11 | 298147 | SPF17B | Urban | LV Transformer SC759542 SPF17B - Planned | 1.08 | 20 | 21.6 | 2.1766e-05 | 1.0883e-06
2013-04-11 | 298148 | RST18A | Urban | LV Transformer SG111-K RST18A - Planned | 2.15 | 30 | 64.5 | 6.4997e-05 | 2.1666e-06
2013-04-11 | 298149 | NIP1A | Urban | LV Transformer SP8573-C NIP1A - Planned | 3.56 | 120 | 427.2 | 0.00043049 | 3.5874e-06
2013-04-11 | 298152 | NBR8 | Rural short | Feeder NBR8 - Planned | 21.01 | 491 | 10315.91 | 0.029684 | 6.0455e-05
2013-04-11 | 298153 | IBL2 | Rural short | Feeder IBL2 - Planned | 77 | 198 | 15246 | 0.04387 | 0.00022156
2013-04-11 | 298154 | GBN2 | Rural short | Feeder GBN2 - Planned | 49.171 | 314 | 15439.694 | 0.044427 | 0.00014149
2013-04-11 | 298183 | CNB24A | Rural short | Feeder CNB24A - Planned | 29.025 | 598 | 17356.95 | 0.049944 | 8.3518e-05
2013-04-11 | 298240 | NRG22A | Urban | LV Transformer SP5102-G NRG22A - Planned | 11 | 195 | 2145 | 0.0021615 | 1.1085e-05
2013-04-11 | 298241 | BMT1 | Rural short | Feeder BMT1 - Planned | 31.04 | 68 | 2110.72 | 0.0060735 | 8.9316e-05
2013-04-12 | 298162 | GGR1 | Rural short | LV Transformer SP430-B GGR1 - Planned | 8 | 38 | 304 | 0.00087485 | 2.3022e-05
2013-04-12 | 298163 | EZRRWD4 | Rural short | LV Transformer SP4448-G EZRRWD4 - Planned | 2 | 123 | 246 | 0.00070794 | 5.7556e-06
2013-04-12 | 298164 | MBG4 | Rural short | LV Transformer SP29001-B MBG4 - Planned | 1 | 57 | 57 | 0.00016403 | 2.8778e-06
2013-04-12 | 298165 | KBR5A | Rural short | LV Transformer SP5197-E KBR5A - Planned | 1 | 275 | 275 | 0.00079139 | 2.8778e-06
2013-04-12 | 298166 | HDN1 | Rural short | LV Transformer SP4678-A HDN1 - Planned | 13.02 | 261 | 3398.22 | 0.0097794 | 3.7469e-05
2013-04-12 | 298173 | BMT1 | Rural short | Feeder BMT1 - Planned | 26.68 | 323 | 8617.64 | 0.0248 | 7.678e-05
2013-04-12 | 298174 | BMT1 | Rural short | Feeder BMT1 - Planned | 15.555 | 220 | 3422.1 | 0.0098481 | 4.4764e-05
2013-04-12 | 298175 | BMT5 | Rural short | Feeder BMT5 - Planned | 32.645 | 240 | 7834.8 | 0.022547 | 9.3946e-05
2013-04-12 | 298176 | BMT1 | Rural short | Feeder BMT1 - Planned | 39.16 | 217 | 8497.72 | 0.024455 | 0.00011269
2013-04-12 | 298177 | AMR3 | Rural short | Feeder AMR3, COR22A - Planned | 51.39 | 167 | 8582.13 | 0.024698 | 0.00014789
2013-04-12 | 298177 | COR22A | Rural short | Feeder AMR3, COR22A - Planned | 2.035 | 167 | 339.845 | 0.00097801 | 5.8563e-06
2013-04-12 | 298179 | BWH13A | Rural short | LV Transformer SP3231-A BWH13A - Planned | 3 | 260 | 780 | 0.0022447 | 8.6334e-06
2013-04-12 | 298180 | MFN15A | Rural short | Feeder MFN15A - Planned | 10.5 | 364 | 3822 | 0.010999 | 3.0217e-05
2013-04-12 | 298182 | GYN6A | Rural short | LV Transformer SP1003-G GYN6A - Planned | 1 | 364 | 364 | 0.0010475 | 2.8778e-06
2013-04-12 | 298190 | AHL4A | Urban | LV Transformer SP1282-M AHL4A - Planned | 8.54 | 263 | 2246.02 | 0.0022632 | 8.6053e-06
2013-04-12 | 298191 | ENG7 | Urban | LV Transformer SP802367 ENG7 - Planned | 6.72 | 230 | 1545.6 | 0.0015574 | 6.7714e-06
2013-04-12 | 298192 | DRA6 | Urban | LV Transformer SP11313-H DRA6 - Planned | 16.24 | 269 | 4368.56 | 0.004402 | 1.6364e-05
2013-04-12 | 298193 | TTF81 | Urban | LV Transformer SP1041-O TTF81 - Planned | 10.24 | 237 | 2426.88 | 0.0024454 | 1.0318e-05
2013-04-12 | 298194 | PBH1 | Urban | LV Transformer SP5888-C PBH1 - Planned | 33 | 218 | 7194 | 0.007249 | 3.3252e-05
2013-04-12 | 298195 | GVN13A | Urban | LV Transformer SC568131 GVN13A - Planned | 3.4683 | 30 | 104.049 | 0.00010484 | 3.4948e-06
2013-04-12 | 298196 | ARL2B | Urban | LV Transformer SC564386 ARL2B - Planned | 7.28 | 66 | 480.48 | 0.00048415 | 7.3357e-06
2013-04-12 | 298197 | ZMR2A | Urban | LV Transformer SC4717-F ZMR2A - Planned | 13.11 | 111 | 1455.21 | 0.0014663 | 1.321e-05
2013-04-12 | 298198 | SGT7 | Urban | LV Transformer SP3057-G SGT7 - Planned | 2.6499 | 239 | 633.3261 | 0.00063817 | 2.6702e-06
2013-04-12 | 298200 | CFD1A | Urban | LV Transformer SG2916-I CFD1A - Planned | 9.72 | 302 | 2935.44 | 0.0029579 | 9.7943e-06
2013-04-12 | 298201 | MHL25A | Urban | LV Transformer SC779669 MHL25A - Planned | 1 | 50 | 50 | 5.0382e-05 | 1.0076e-06
2013-04-12 | 298202 | NSW28 | Urban | LV Transformer SP5595-I NSW28 - Planned | 0.94 | 254 | 238.76 | 0.00024059 | 9.4719e-07
2013-04-12 | 298203 | CLR3 | Rural short | LV Transformer SP3325-L CLR3 - Planned | 9.92 | 187 | 1855.04 | 0.0053384 | 2.8548e-05
2013-04-12 | 298204 | HPE13A | Urban | LV Transformer SP764702 HPE13A - Planned | 3.15 | 214 | 674.1 | 0.00067925 | 3.1741e-06
2013-04-12 | 298205 | MTG16A | Urban | LV Transformer SG1141-J MTG16A - Planned | 1.3567 | 353 | 478.9151 | 0.00048258 | 1.3671e-06
2013-04-12 | 298206 | ARG5A | Urban | LV Transformer SP14342-F ARG5A - Planned | 24 | 369 | 8856 | 0.0089237 | 2.4183e-05
2013-04-12 | 298207 | ALY5 | Urban | LV Transformer SP320-P ALY5 - Planned | 9.95 | 155 | 1542.25 | 0.001554 | 1.0026e-05
2013-04-12 | 298208 | CMV9A | Urban | LV Transformer SC6613-E CMV9A - Planned | 5 | 303 | 1515 | 0.0015266 | 5.0382e-06
2013-04-12 | 298209 | HPE13A | Urban | LV Transformer SP521-G HPE13A - Planned | 20.1875 | 355 | 7166.5625 | 0.0072214 | 2.0342e-05
2013-04-12 | 298210 | TGW1 | Rural short | LV Transformer SP2616-C TGW1 - Planned | 3 | 192 | 576 | 0.0016576 | 8.6334e-06
2013-04-12 | 298211 | NIP6A | Urban | LV Transformer SP5300-E NIP6A - Planned | 24.557 | 45 | 1105.065 | 0.0011135 | 2.4745e-05
2013-04-12 | 298212 | RPN8 | Rural short | LV Transformer SP2947-D RPN8 - Planned | 21.55 | 194 | 4180.7 | 0.012031 | 6.2017e-05
2013-04-12 | 298213 | THL3 | Rural short | LV Transformer SP1274-C THL3 - Planned | 7.98 | 82 | 654.36 | 0.0018831 | 2.2965e-05
2013-04-12 | 298214 | CPK7 | Urban | LV Transformer SP35996-A CPK7 - Planned | 2 | 46 | 92 | 9.2703e-05 | 2.0153e-06
2013-04-12 | 298215 | THL3 | Rural short | LV Transformer SP1275-D THL3 - Planned | 3.99 | 70 | 279.3 | 0.00080377 | 1.1482e-05
2013-04-12 | 298221 | WRG8A | Urban | LV Transformer SC889-E WRG8A - Planned | 1 | 453 | 453 | 0.00045646 | 1.0076e-06
2013-04-13 | 298260 | ALY3A | Urban | LV Transformer SP3750-E ALY8 - Planned | 6.52 | 354 | 2308.08 | 0.0023256 | 6.5695e-06
2013-04-13 | 298260 | ALY8 | Urban | LV Transformer SP3750-E ALY8 - Planned | 2.5 | 354 | 885 | 0.00089172 | 2.519e-06
2013-04-13 | 298261 | MTG12B | Urban | LV Transformer SP2018-L MTG12B - Planned | 16.3296 | 305 | 4980.528 | 0.0050184 | 1.6454e-05
2013-04-14 | 298242 | FIS7A | Urban | Feeder FIS7A - Planned | 4.2 | 144 | 604.8 | 0.00060937 | 4.2317e-06
2013-04-14 | 298255 | NGE13 | Urban | LV Transformer SG2004-K NGE13 - Planned | 4.66 | 130 | 605.8 | 0.00061038 | 4.6952e-06
2013-04-14 | 298257 | HMT10A | Urban | LV Transformer SP16227-D HMT10A - Planned | 23 | 308 | 7084 | 0.0071375 | 2.3174e-05
2013-04-14 | 298258 | CFD2A | Urban | LV Transformer SP2295-H CFD2A - Planned | 6.825 | 49 | 334.425 | 0.00033695 | 6.8766e-06
2013-04-14 | 298259 | CPR5 | Urban | LV Transformer SP27-O HPE13A - Planned | 7.26 | 344 | 2497.44 | 0.0025163 | 7.3149e-06
2013-04-14 | 298259 | HPE13A | Urban | LV Transformer SP27-O HPE13A - Planned | 17.18 | 344 | 5909.92 | 0.0059546 | 1.731e-05
2013-04-14 | 298262 | WED16A | Urban | LV Transformer SP16612-D WED16A - Planned | 8 | 299 | 2392 | 0.0024101 | 8.0605e-06
2013-04-14 | 298266 | AGE10 | Urban | LV Transformer SP3075-M AGE10 - Planned | 15.475 | 331 | 5122.225 | 0.0051609 | 1.5592e-05
2013-04-14 | 298267 | AHL4A | Urban | LV Transformer SP609-R AHL4A - Planned | 17.7 | 370 | 6549 | 0.0065985 | 1.7834e-05
2013-04-14 | 298267 | GLY15A | Urban | LV Transformer SP609-R AHL4A - Planned | 1.17 | 370 | 432.9 | 0.00043617 | 1.1788e-06
2013-04-14 | 298272 | AGE10 | Urban | LV Transformer SC4908-H AGE10 - Planned | 1.24 | 311 | 385.64 | 0.00038856 | 1.2494e-06
2013-04-15 | 298294 | MGP4 | Rural short | Feeder MGP4 - Planned | 48 | 229 | 10992 | 0.031642 | 0.00013818
2013-04-15 | 298295 | MTB17A | Rural short | LV Transformer SP785303 MTB17A - Planned | 15 | 193 | 2895 | 0.0083338 | 4.318e-05
2013-04-15 | 298296 | JBB3A | Rural short | Feeder JBB3A - Planned | 3 | 186 | 558 | 0.0016063 | 8.6361e-06
2013-04-15 | 298297 | TRP2 | Rural short | Feeder TRP2 - Planned | 28.855 | 234 | 6752.07 | 0.019437 | 8.3064e-05
2013-04-15 | 298299 | AMR3 | Rural short | Feeder AMR3 - Planned | 18.33 | 250 | 4582.5 | 0.013192 | 5.2766e-05
2013-04-15 | 298300 | CBT8A | Rural short | Feeder CBT8A - Planned | 2 | 320 | 640 | 0.0018424 | 5.7574e-06
2013-04-15 | 298302 | NRG6 | Urban | LV Transformer SP15210-C NRG6 - Planned | 1 | 385 | 385 | 0.00038788 | 1.0075e-06
2013-04-15 | 298303 | GAP8A | Urban | LV Transformer SP1508-P GAP8A - Planned | 4.7 | 226 | 1062.2 | 0.0010701 | 4.7351e-06
2013-04-15 | 298304 | GYS3A | Rural short | LV Transformer SP1812-E GYS3A - Planned | 2.4 | 36 | 86.4 | 0.00024872 | 6.9088e-06
2013-04-15 | 298305 | NVL12 | Urban | LV Transformer SP2540-D NVL12 - Planned | 17.425 | 228 | 3972.9 | 0.0040026 | 1.7555e-05
2013-04-15 | 298306 | NBR6 | Rural short | LV Transformer SP4445-A NBR6 - Planned | 6.12 | 70 | 428.4 | 0.0012332 | 1.7618e-05
2013-04-15 | 298308 | SGT7 | Urban | LV Transformer SP1612-J SGT7 - Planned | 8.13 | 233 | 1894.29 | 0.0019084 | 8.1908e-06
2013-04-15 | 298309 | CBW6 | Rural short | LV Transformer SP3260-F CBW6 - Planned | 36 | 286 | 10296 | 0.029639 | 0.00010363
2013-04-15 | 298310 | CFD6A | Urban | LV Transformer SP743971 CFD6A - Planned | 19.175 | 381 | 7305.675 | 0.0073603 | 1.9318e-05
2013-04-15 | 298311 | NSW5A | Urban | LV Transformer SP3553-L NSW5A - Planned | 69.14 | 308 | 21295.12 | 0.021454 | 6.9657e-05
2013-04-15 | 298312 | HPK3A | Urban | LV Transformer SP1071-M HPK3A - Planned | 11.32 | 160 | 1811.2 | 0.0018247 | 1.1405e-05
2013-04-15 | 298313 | KBR2A | Rural short | LV Transformer SP809-E KBR2A - Planned | 4 | 75 | 300 | 0.00086361 | 1.1515e-05
2013-04-15 | 298314 | THL3 | Rural short | LV Transformer SP2255-D THL3 - Planned | 2.01 | 42 | 84.42 | 0.00024302 | 5.7862e-06
2013-04-15 | 298315 | RLB16A | Rural short | Feeder RLB16A - Planned | 8.364 | 390 | 3261.96 | 0.0093902 | 2.4077e-05
2013-04-15 | 298394 | GYM2A | Rural short | Feeder GYM2A - Planned | 68.16 | 370 | 25219.2 | 0.072598 | 0.00019621
2013-04-15 | 298396 | IBL2 | Rural short | Feeder IBL2 - Planned | 2.536 | 290 | 735.44 | 0.0021171 | 7.3003e-06
2013-04-15 | 298398 | BMT2 | Rural short | Feeder BMT2 - Planned | 40.02 | 78 | 3121.56 | 0.008986 | 0.0001152
2013-04-15 | 298399 | GBN4 | Rural short | LV Transformer SP15048-C GBN4 - Planned | 4.15 | 52 | 215.8 | 0.00062122 | 1.1947e-05
2013-04-16 | 298333 | AMR3 | Rural short | LV Transformer SP5615-B AMR3 - Planned | 4 | 40 | 160 | 0.00046062 | 1.1516e-05
2013-04-16 | 298334 | TGW2 | Rural short | Feeder TGW2 - Planned | 12.01 | 137 | 1645.37 | 0.0047369 | 3.4576e-05
2013-04-16 | 298337 | BWH12A | Rural short | Feeder BWH12A - Planned | 43 | 315 | 13545 | 0.038995 | 0.00012379
2013-04-16 | 298338 | BDB27A | Rural short | Feeder BDB27A - Planned | 1 | 269 | 269 | 0.00077443 | 2.8789e-06
2013-04-16 | 298341 | BMT1 | Rural short | Feeder BMT1 - Planned | 34.05 | 257 | 8750.85 | 0.025193 | 9.8027e-05
2013-04-16 | 298343 | NMC3A | Rural short | LV Transformer SP744617 NMC3A - Planned | 9 | 310 | 2790 | 0.0080321 | 2.591e-05
2013-04-16 | 298346 | CVL5A | Rural short | LV Transformer SP3930-D CVL5A - Planned | 0.4 | 368 | 147.2 | 0.00042377 | 1.1516e-06
2013-04-16 | 298347 | BHD35A | Rural short | Feeder BHD35A - Planned | 28.5 | 485 | 13822.5 | 0.039794 | 8.2049e-05
2013-04-16 | 298348 | KCY4 | Rural short | Feeder KCY4 - Planned | 52 | 512 | 26624 | 0.076648 | 0.0001497
2013-04-16 | 298363 | RLB16A | Rural short | Feeder RLB16A - Planned | 4 | 430 | 1720 | 0.0049517 | 1.1516e-05
2013-04-16 | 298364 | GYM2A | Rural short | Feeder GYM2A - Planned | 40.43 | 408 | 16495.44 | 0.047489 | 0.00011639
2013-04-16 | 298365 | MGL5 | Urban | LV Transformer SC22107-F MGL5 - Planned | 9.44 | 471 | 4446.24 | 0.0044793 | 9.5102e-06
2013-04-16 | 298366 | KMR19A | Urban | LV Transformer SC484408 KMR27A - Planned | 1.17 | 244 | 285.48 | 0.0002876 | 1.1787e-06
2013-04-16 | 298366 | KMR27A | Urban | LV Transformer SC484408 KMR27A - Planned | 24.85 | 244 | 6063.4 | 0.0061085 | 2.5035e-05
2013-04-16 | 298367 | DRA8 | Urban | LV Transformer SG798487 DRA8 - Planned | 12.24 | 268 | 3280.32 | 0.0033047 | 1.2331e-05
2013-04-16 | 298368 | TRG5 | Urban | LV Transformer SC1734719 TRG5 - Planned | 1.345 | 227 | 305.315 | 0.00030759 | 1.355e-06
2013-04-16 | 298369 | CLM5 | Urban | LV Transformer SP1751-A CLM5 - Planned | 2.33 | 218 | 507.94 | 0.00051172 | 2.3473e-06
2013-04-16 | 298370 | CRB25A | Rural short | LV Transformer SP468823 CRB25A - Planned | 6 | 339 | 2034 | 0.0058557 | 1.7273e-05
2013-04-16 | 298371 | SPO5A | Urban | LV Transformer SC768808 SPO5A - Planned | 2.2449 | 29 | 65.1021 | 6.5586e-05 | 2.2616e-06
2013-04-16 | 298372 | GVN13A | Urban | LV Transformer SC777906 GVN13A - Planned | 24.32 | 12 | 291.84 | 0.00029401 | 2.4501e-05
2013-04-16 | 298373 | IPL1 | Rural short | LV Transformer SP1457-F IPL1 - Planned | 4 | 166 | 664 | 0.0019116 | 1.1516e-05
2013-04-16 | 298374 | LDR8 | Urban | LV Transformer SP13669-B LDR8 - Planned | 8.825 | 392 | 3459.4 | 0.0034851 | 8.8906e-06
2013-04-16 | 298375 | WNM5 | Urban | LV Transformer SP2140-J WNM5 - Planned | 0.8 | 343 | 274.4 | 0.00027644 | 8.0595e-07
2013-04-16 | 298376 | HTN24B | Urban | LV Transformer SSHTN 674 - Planned | 1 | 229 | 229 | 0.0002307 | 1.0074e-06
2013-04-16 | 298377 | DRD15B | Urban | LV Transformer SP1591-F DRD15B - Planned | 26.03 | 350 | 9110.5 | 0.0091782 | 2.6224e-05
2013-04-16 | 298378 | SGT7 | Urban | LV Transformer SP1612-J SGT7 - Planned | 6.775 | 285 | 1930.875 | 0.0019452 | 6.8254e-06
2013-04-16 | 298379 | SFD2A | Urban | LV Transformer SC4498-J SFD2A - Planned | 10.79 | 300 | 3237 | 0.0032611 | 1.087e-05
2013-04-16 | 298380 | BHL4A | Urban | LV Transformer SP2515-H BHL4A - Planned | 22.99 | 130 | 2988.7 | 0.0030109 | 2.3161e-05
2013-04-16 | 298381 | CMV9A | Urban | LV Transformer SC5801-I CMV9A - Planned | 3.82 | 295 | 1126.9 | 0.0011353 | 3.8484e-06
2013-04-16 | 298382 | GYN3A | Rural short | Feeder GYN3A - Planned | 20.7404 | 252 | 5226.5808 | 0.015047 | 5.971e-05
2013-04-16 | 298383 | HPE16A | Urban | LV Transformer SG1450-M HPE5A - Planned | 17.55 | 254 | 4457.7 | 0.0044908 | 1.7681e-05
2013-04-16 | 298383 | HPE5A | Urban | LV Transformer SG1450-M HPE5A - Planned | 14.56 | 254 | 3698.24 | 0.0037257 | 1.4668e-05
2013-04-16 | 298384 | IBL2 | Rural short | Feeder IBL2 - Planned | 65.8 | 285 | 18753 | 0.053988 | 0.00018943
2013-04-16 | 298385 | COR23A | Rural short | Feeder COR23A - Planned | 38.05 | 290 | 11034.5 | 0.031767 | 0.00010954
2013-04-16 | 298386 | WNM5 | Urban | LV Transformer SP6708-G WNM5 - Planned | 12.81 | 276 | 3535.56 | 0.0035619 | 1.2905e-05
2013-04-16 | 298387 | GYGGYS6 | Rural short | Feeder GYGGYS6 - Planned | 26.19 | 287 | 7516.53 | 0.021639 | 7.5398e-05
2013-04-16 | 298388 | MTG8A | Urban | LV Transformer SP25579-E MTG8A - Planned | 19.25 | 273 | 5255.25 | 0.0052943 | 1.9393e-05
2013-04-16 | 298389 | BMT1 | Rural short | Feeder BMT1 - Planned | 34.05 | 257 | 8750.85 | 0.025193 | 9.8027e-05
2013-04-16 | 298390 | CRM13A | Urban | LV Transformer SP6796-C CRM13A - Planned | 8.64 | 330 | 2851.2 | 0.0028724 | 8.7042e-06
2013-04-16 | 298391 | COR22A | Rural short | Feeder COR22A - Planned | 25.05 | 243 | 6087.15 | 0.017524 | 7.2117e-05
2013-04-16 | 298392 | AMR1 | Rural short | Feeder AMR1 - Planned | 15.76 | 116 | 1828.16 | 0.0052631 | 4.5372e-05
2013-04-16 | 298393 | HPE13A | Urban | LV Transformer SP16619-E HPE13A - Planned | 9.99 | 343 | 3426.57 | 0.0034521 | 1.0064e-05
2013-04-16 | 298395 | BDB27A | Rural short | LV Transformer SC1384960 BDB27A - Planned | 21.25 | 227 | 4823.75 | 0.013887 | 6.1177e-05
2013-04-16 | 298413 | CFD1A | Urban | LV Transformer SP9695-H CFD1A - Planned | 22.525 | 480 | 10812 | 0.010892 | 2.2693e-05
2013-04-17 | 298425 | MSV1 | Rural short | LV Transformer SP2372-C MSV1 - Planned | 0.4 | 85 | 34 | 9.7898e-05 | 1.1517e-06
2013-04-17 | 298435 | BMT1 | Rural short | Feeder BMT1, IBL2, BMT5 - Planned | 1.25 | 222 | 277.5 | 0.00079902 | 3.5992e-06
2013-04-17 | 298435 | BMT5 | Rural short | Feeder BMT1, IBL2, BMT5 - Planned | 4 | 222 | 888 | 0.0025569 | 1.1517e-05
2013-04-17 | 298435 | IBL2 | Rural short | Feeder BMT1, IBL2, BMT5 - Planned | 22 | 222 | 4884 | 0.014063 | 6.3346e-05
2013-04-17 | 298439 | MLY1 | Rural short | Feeder MLY1 - Planned | 34.05 | 338 | 11508.9 | 0.033138 | 9.8042e-05
2013-04-17 | 298440 | MGP4 | Rural short | Feeder MGP4 - Planned | 183 | 4 | 732 | 0.0021077 | 0.00052692
2013-04-17 | 298441 | MBG1 | Rural short | LV Transformer SP1078-F MBG1 - Planned | 6 | 373 | 2238 | 0.006444 | 1.7276e-05
2013-04-17 | 298453 | JBB12B | Rural short | Feeder JBB12B - Planned | 8 | 358 | 2864 | 0.0082465 | 2.3035e-05
2013-04-17 | 298456 | KWH3 | Rural short | Feeder KWH3 - Planned | 18.504 | 310 | 5736.24 | 0.016517 | 5.328e-05
2013-04-17 | 298457 | MTB17A | Rural short | Feeder MTB17A - Planned | 8.5 | 474 | 4029 | 0.011601 | 2.4475e-05
2013-04-17 | 298459 | ENG2 | Urban | LV Transformer SP763994 ENG2 - Planned | 40.04 | 208 | 8328.32 | 0.0083896 | 4.0334e-05
2013-04-17 | 298460 | CPL23A | Rural short | LV Transformer SP31895-D CPL23A - Planned | 0.96 | 124 | 119.04 | 0.00034276 | 2.7642e-06
2013-04-17 | 298461 | DRA9 | Urban | LV Transformer SP1547-I DRA9 - Planned | 13.86 | 350 | 4851 | 0.0048867 | 1.3962e-05
2013-04-17 | 298462 | ENG7 | Urban | LV Transformer SP325-Q ENG7 - Planned | 5.22 | 336 | 1753.92 | 0.0017668 | 5.2584e-06
2013-04-17 | 298464 | GBN4 | Rural short | LV Transformer SP2314-E GBN4 - Planned | 1.34 | 94 | 125.96 | 0.00036268 | 3.8583e-06
2013-04-17 | 298465 | NBR6 | Rural short | LV Transformer SP4445-A NBR6 - Planned | 2.88 | 160 | 460.8 | 0.0013268 | 8.2926e-06
2013-04-17 | 298467 | NRG14A | Rural short | LV Transformer SP6276-C NRG14A - Planned | 26 | 450 | 11700 | 0.033689 | 7.4863e-05
2013-04-17 | 298468 | BLH13B | Rural short | LV Transformer SG321-I BLH13B - Planned | 0.96 | 125 | 120 | 0.00034552 | 2.7642e-06
2013-04-17 | 298469 | SPO3A | Urban | LV Transformer SP2516-G SPO3A - Planned | 14.245 | 126 | 1794.87 | 0.0018081 | 1.435e-05
2013-04-17 | 298470 | SPO67B | Urban | LV Transformer SP467934 SPO67B - Planned | 11.04 | 550 | 6072 | 0.0061167 | 1.1121e-05
2013-04-17 | 298471 | CFD1A | Urban | LV Transformer SP9695-H CFD1A - Planned | 22.01 | 110 | 2421.1 | 0.0024389 | 2.2172e-05
2013-04-17 | 298471 | CFD2A | Urban | LV Transformer SP9695-H CFD1A - Planned | 1.095 | 110 | 120.45 | 0.00012134 | 1.1031e-06
2013-04-17 | 298472 | DRD15B | Urban | LV Transformer SP3602-E DRD15B - Planned | 34.8075 | 282 | 9815.715 | 0.0098879 | 3.5063e-05
2013-04-17 | 298473 | LTA5 | Urban | LV Transformer SP492537 LTA5 - Planned | 10.2757 | 262 | 2692.2334 | 0.002712 | 1.0351e-05
2013-04-17 | 298475 | WNM5 | Urban | LV Transformer SP680-N WNM5 - Planned | 16.85 | 243 | 4094.55 | 0.0041247 | 1.6974e-05
2013-04-17 | 298479 | SGT7 | Urban | LV Transformer SP5969-B SGT7 - Planned | 37.45 | 349 | 13070.05 | 0.013166 | 3.7725e-05
2013-04-17 | 298480 | CPB8 | Rural short | LV Transformer SP777492 CPB8 - Planned | 2 | 152 | 304 | 0.00087533 | 5.7587e-06
2013-04-17 | 298481 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 29.9198 | 353 | 10561.6894 | 0.010639 | 3.014e-05
2013-04-17 | 298482 | BDA12B | Urban | LV Transformer SC1874-K BDA12B - Planned | 21.45 | 298 | 6392.1 | 0.0064391 | 2.1608e-05
2013-04-17 | 298483 | NIP4A | Rural short | LV Transformer SP3179-D NIP4A - Planned | 19.5 | 396 | 7722 | 0.022234 | 5.6148e-05
2013-04-17 | 298484 | MCW4 | Rural short | LV Transformer SC133-D MCW4 - Planned | 30.33 | 300 | 9099 | 0.026199 | 8.7331e-05
2013-04-17 | 298488 | MWMRBK11 | Rural short | LV Transformer SP5149-F MWMRBK11 - Planned | 34.85 | 174 | 6063.9 | 0.01746 | 0.00010035
2013-04-18 | 298533 | KCY2 | Rural short | LV Transformer SP4626-E KCY2 - Planned | 2.5 | 100 | 250 | 0.0007199 | 7.199e-06
2013-04-18 | 298534 | YDA5A | Rural short | Feeder YDA5A - Planned | 36.469 | 194 | 7074.986 | 0.020373 | 0.00010502
2013-04-18 | 298535 | GBN4 | Rural short | LV Transformer SP6500-B GBN4 - Planned | 1.34 | 98 | 131.32 | 0.00037815 | 3.8587e-06
2013-04-18 | 298536 | CLD9A | Urban | LV Transformer SG276-A CLD9A - Planned | 1 | 9 | 9 | 9.0658e-06 | 1.0073e-06
2013-04-18 | 298538 | LGV3A | Rural short | Feeder LGV3A - Planned | 14 | 158 | 2212 | 0.0063697 | 4.0314e-05
2013-04-18 | 298539 | THL1 | Rural short | LV Transformer SP2402-B THL1 - Planned | 2.01 | 252 | 506.52 | 0.0014586 | 5.788e-06
2013-04-18 | 298543 | FDS1 | Rural short | LV Transformer SP12641-B FDS1 - Planned | 10.5 | 295 | 3097.5 | 0.0089196 | 3.0236e-05
2013-04-18 | 298546 | BDB32A | Rural short | Feeder BDB32A - Planned | 48.5 | 330 | 16005 | 0.046088 | 0.00013966
2013-04-18 | 298547 | CRB25A | Rural short | Feeder CRB25A - Planned | 32 | 443 | 14176 | 0.040821 | 9.2147e-05
2013-04-18 | 298557 | GYN3A | Rural short | Feeder GYN3A - Planned | 127.4409 | 381 | 48554.9829 | 0.13982 | 0.00036698
2013-04-18 | 298559 | CLM7 | Urban | LV Transformer SP14096-A CLM7 - Planned | 1.66 | 77 | 127.82 | 0.00012876 | 1.6721e-06
2013-04-18 | 298560 | NVL3 | Rural short | LV Transformer SP3206-C NVL3 - Planned | 11.79 | 149 | 1756.71 | 0.0050586 | 3.3951e-05
2013-04-18 | 298561 | WMD14A | Rural short | LV Transformer SC823033 WMD14A - Planned | 12.525 | 115 | 1440.375 | 0.0041477 | 3.6067e-05
2013-04-18 | 298562 | NBR6 | Rural short | LV Transformer SP4445-A NBR6 - Planned | 5.04 | 80 | 403.2 | 0.0011611 | 1.4513e-05
2013-04-18 | 298563 | BHD35A | Rural short | LV Transformer SP84687-B BHD35A - Planned | 9 | 501 | 4509 | 0.012984 | 2.5916e-05
2013-04-18 | 298564 | PBH3 | Urban | LV Transformer SP466576 PBH3 - Planned | 16.25 | 173 | 2811.25 | 0.0028318 | 1.6369e-05
2013-04-18 | 298565 | LDR3 | Urban | LV Transformer SP27039-C LDR3 - Planned | 36.89 | 251 | 9259.39 | 0.0093271 | 3.716e-05
2013-04-18 | 298566 | MDH3A | Urban | LV Transformer SC1050354 MDH3A - Planned | 1 | 70 | 70 | 7.0512e-05 | 1.0073e-06
2013-04-18 | 298567 | ZMR9 | Urban | LV Transformer SP29524-C ZMR9 - Planned | 13.8664 | 75 | 1039.98 | 0.0010476 | 1.3968e-05
2013-04-18 | 298568 | DRD15B | Urban | LV Transformer SC743341 DRD15B - Planned | 23.11 | 340 | 7857.4 | 0.0079149 | 2.3279e-05
2013-04-18 | 298569 | CSE6 | Urban | LV Transformer SP13200-E CSE6 - Planned | 2.12 | 70 | 148.4 | 0.00014949 | 2.1355e-06
2013-04-18 | 298571 | BHL4A | Urban | LV Transformer SP2976-H BHL4A - Planned | 12.02 | 310 | 3726.2 | 0.0037535 | 1.2108e-05
2013-04-18 | 298572 | KSN5 | Rural short | LV Transformer SP5566-D KSN5 - Planned | 8.1 | 310 | 2511 | 0.0072307 | 2.3325e-05
2013-04-18 | 298573 | HPK3A | Urban | LV Transformer SP1638-J HPK3A - Planned | 14.82 | 195 | 2889.9 | 0.002911 | 1.4928e-05
2013-04-18 | 298574 | AHD25A | Urban | LV Transformer SP4415-A AHD25A - Planned | 4.17 | 66 | 275.22 | 0.00027723 | 4.2005e-06
2013-04-18 | 298575 | BHD7A | Urban | LV Transformer SC562501 BHD7A - Planned | 1.3 | 25 | 32.5 | 3.2738e-05 | 1.3095e-06
2013-04-18 | 298576 | CFD1A | Urban | LV Transformer SSCFD - Planned | 4.035 | 9 | 36.315 | 3.6581e-05 | 4.0645e-06
2013-04-18 | 298577 | PDB13 | Urban | LV Transformer SC2057282 PDB13 - Planned | 2.46 | 75 | 184.5 | 0.00018585 | 2.478e-06
2013-04-18 | 298677 | RLB16A | Rural short | Feeder RLB16A - Planned | 6.09 | 374 | 2277.66 | 0.0065588 | 1.7537e-05
2013-04-18 | 298678 | BDT1 | Rural short | LV Transformer SP2943-C BDT1 - Planned | 4 | 118 | 472 | 0.0013592 | 1.1518e-05
2013-04-19 | 298593 | WMR1 | Rural short | Feeder WMR1 - Planned | 2 | 49 | 98 | 0.00028224 | 5.76e-06
2013-04-19 | 298597 | BDT4 | Rural short | LV Transformer SP4022-D BDT4 - Planned | 2 | 174 | 348 | 0.0010022 | 5.76e-06
2013-04-19 | 298598 | TRP2 | Rural short | Feeder TRP2 - Planned | 10 | 225 | 2250 | 0.00648 | 2.88e-05
2013-04-19 | 298600 | COR23A | Rural short | Feeder COR23A - Planned | 20.52 | 165 | 3385.8 | 0.0097511 | 5.9098e-05
2013-04-19 | 298601 | WHO1 | Rural short | Feeder WHO1 - Planned | 8 | 257 | 2056 | 0.0059213 | 2.304e-05
2013-04-19 | 298602 | BNH6A | Rural short | Feeder BNH6A - Planned | 3 | 205 | 615 | 0.0017712 | 8.64e-06
2013-04-19 | 298603 | MSV2 | Rural short | Feeder MSV2 - Planned | 24.05 | 336 | 8080.8 | 0.023273 | 6.9264e-05
2013-04-19 | 298605 | GBN4 | Rural short | Feeder GBN4 - Planned | 19.74 | 336 | 6632.64 | 0.019102 | 5.6851e-05
2013-04-19 | 298606 | MLY1 | Rural short | LV Transformer SP8188-A MLY1 - Planned | 8 | 50 | 400 | 0.001152 | 2.304e-05
2013-04-19 | 298607 | BDT1 | Rural short | LV Transformer SP2916-C BDT1 - Planned | 5.5 | 429 | 2359.5 | 0.0067954 | 1.584e-05
2013-04-19 | 298608 | BWH16A | Rural short | LV Transformer SP3801-B BWH16A - Planned | 8 | 326 | 2608 | 0.007511 | 2.304e-05
2013-04-19 | 298609 | NVL9 | Rural short | Feeder NVL9 - Planned | 1 | 360 | 360 | 0.0010368 | 2.88e-06
2013-04-19 | 298613 | CVL5A | Rural short | LV Transformer SP2814-D CVL5A - Planned | 1 | 450 | 450 | 0.001296 | 2.88e-06
2013-04-19 | 298614 | AGE6A | Urban | LV Transformer SP1322-O AGE6A - Planned | 4.32 | 58 | 250.56 | 0.00025238 | 4.3513e-06
2013-04-19 | 298615 | DRA11 | Urban | LV Transformer SP10554-F DRA6 - Planned | 1.74 | 315 | 548.1 | 0.00055207 | 1.7526e-06
2013-04-19 | 298615 | DRA6 | Urban | LV Transformer SP10554-F DRA6 - Planned | 21.25 | 315 | 6693.75 | 0.0067423 | 2.1404e-05
2013-04-19 | 298616 | CLM6 | Urban | LV Transformer SP4554-B CLM6 - Planned | 3.25 | 85 | 276.25 | 0.00027825 | 3.2736e-06
2013-04-19 | 298617 | NBR6 | Rural short | LV Transformer SP175372 NBR6 - Planned | 1.98 | 251 | 496.98 | 0.0014313 | 5.7024e-06
2013-04-19 | 298618 | BHD35A | Rural short | LV Transformer SP18904-H BHD35A - Planned | 15 | 202 | 3030 | 0.0087264 | 4.32e-05
2013-04-19 | 298619 | PBH1 | Urban | LV Transformer SP3787-D PBH1 - Planned | 76.14 | 403 | 30684.42 | 0.030907 | 7.6692e-05
2013-04-19 | 298620 | SPO8A | Urban | LV Transformer SP6326-D SPO8A - Planned | 6.93 | 152 | 1053.36 | 0.001061 | 6.9802e-06
2013-04-19 | 298621 | CRB15A | Urban | LV Transformer SC748370 CRB15A - Planned | 1.98 | 23 | 45.54 | 4.587e-05 | 1.9944e-06
2013-04-19 | 298622 | BDT1 | Rural short | LV Transformer SP16289-D BDT1 - Planned | 1 | 184 | 184 | 0.00052992 | 2.88e-06
2013-04-19 | 298623 | KBN2A | Rural short | Feeder KBN2A - Planned | 50 | 470 | 23500 | 0.06768 | 0.000144
2013-04-19 | 298624 | HIS3A | Urban | LV Transformer SC1386568 HIS3A - Planned | 76.54 | 60 | 4592.4 | 0.0046257 | 7.7095e-05
2013-04-19 | 298625 | WNM5 | Urban | LV Transformer SP2141-L WNM5 - Planned | 33.11 | 371 | 12283.81 | 0.012373 | 3.335e-05
2013-04-19 | 298626 | BHL4A | Urban | LV Transformer SP2515-H BHL4A - Planned | 14.59 | 306 | 4464.54 | 0.0044969 | 1.4696e-05
2013-04-19 | 298627 | KCY2 | Rural short | LV Transformer SP2762-E KCY2 - Planned | 23.8 | 289 | 6878.2 | 0.019809 | 6.8544e-05
2013-04-19 | 298628 | LTA4B | Urban | LV Transformer SP1216-N LTA4B - Planned | 21.98 | 175 | 3846.5 | 0.0038744 | 2.2139e-05
2013-04-19 | 298629 | BLBNFM6 | Urban | LV Transformer SP2362-M BLBNFM6 - Planned | 0.81 | 308 | 249.48 | 0.00025129 | 8.1587e-07
2013-04-19 | 298630 | CVL5A | Rural short | LV Transformer SP4462-B CVL5A - Planned | 7.02 | 83 | 582.66 | 0.0016781 | 2.0218e-05
2013-04-19 | 298631 | TMH3A | Urban | LV Transformer SP6932-C TMH3A - Planned | 37.74 | 240 | 9057.6 | 0.0091233 | 3.8014e-05
2013-04-19 | 298632 | ALY5 | Urban | LV Transformer SP31667-D ALY5 - Planned | 9.15 | 96 | 878.4 | 0.00088477 | 9.2163e-06
2013-04-19 | 298634 | DRA6 | Urban | LV Transformer SP11313-H DRA6 - Planned | 16.24 | 261 | 4238.64 | 0.0042694 | 1.6358e-05
2013-04-19 | 298635 | KSN1 | Urban | LV Transformer SP4124-C KSN1 - Planned | 8 | 214 | 1712 | 0.0017244 | 8.058e-06
2013-04-19 | 298636 | TWT3A | Rural short | LV Transformer SC741343 TWT3A - Planned | 4.83 | 20 | 96.6 | 0.00027821 | 1.391e-05
2013-04-19 | 298651 | MLB13A | Urban | LV Transformer SC22373-A MLB13A - Planned | 1.63 | 140 | 228.2 | 0.00022985 | 1.6418e-06
2013-04-19 | 298987 | EMD3 | Rural short | LV Transformer SP2244-D EMD3 - Planned | 25.5 | 27 | 688.5 | 0.0019829 | 7.344e-05
2013-04-19 | 298988 | BTA5A | Rural short | Feeder BTA5A, MLY1 - Planned | 15.98 | 363 | 5800.74 | 0.016706 | 4.6022e-05
2013-04-19 | 298988 | MLY1 | Rural short | Feeder BTA5A, MLY1 - Planned | 113.43 | 363 | 41175.09 | 0.11858 | 0.00032668
2013-04-20 | 298650 | KWA12A | Urban | LV Transformer SP760607 KWA12A - Planned | 22 | 156 | 3432 | 0.0034567 | 2.2158e-05
2013-04-20 | 298652 | KBN5A | Rural short | LV Transformer SP778892 KBN5A - Planned | 1 | 502 | 502 | 0.0014459 | 2.8803e-06
2013-04-20 | 298653 | KBN5A | Rural short | Feeder KBN5A - Planned | 13 | 323 | 4199 | 0.012094 | 3.7444e-05
2013-04-20 | 298657 | MTG13A | Urban | LV Transformer SC5960-F MTG13A - Planned | 7.78 | 195 | 1517.1 | 0.001528 | 7.8359e-06
2013-04-21 | 298675 | HTL2A | Urban | LV Transformer SC484374 HTL2A - Planned | 2 | 142 | 284 | 0.00028603 | 2.0143e-06
2013-04-21 | 298676 | YTA23B | Urban | LV Transformer SG1082960 YTA23B - Planned | 3 | 217 | 651 | 0.00065566 | 3.0215e-06
2013-04-21 | 298680 | AMR3 | Rural short | Feeder AMR3 - Planned | 55.5 | 337 | 18703.5 | 0.053875 | 0.00015987
2013-04-21 | 298681 | BMT1 | Rural short | Feeder BMT1 - Planned | 34.2 | 268 | 9165.6 | 0.026401 | 9.8511e-05
2013-04-21 | 298683 | PGN1B | Rural short | LV Transformer SP6511-B PGN1B - Planned | 57.04 | 414 | 23614.56 | 0.068021 | 0.0001643
2013-04-21 | 298685 | MGL8 | Urban | LV Transformer SP1329-M MGL8 - Planned | 3 | 345 | 1035 | 0.0010424 | 3.0215e-06
2013-04-21 | 298686 | TWG18 | Urban | LV Transformer SC1124-O TWG18 - Planned | 0.92 | 170 | 156.4 | 0.00015752 | 9.2658e-07
2013-04-21 | 298687 | NGE13 | Urban | LV Transformer SC22011-G NGE13 - Planned | 1.8 | 417 | 750.6 | 0.00075597 | 1.8129e-06
2013-04-21 | 298688 | SGT22A | Urban | LV Transformer SC6371-F SGT22A - Planned | 7.435 | 325 | 2416.375 | 0.0024337 | 7.4882e-06
2013-04-21 | 298689 | SGT5 | Urban | LV Transformer SP40245-C SGT5 - Planned | 2.9 | 121 | 350.9 | 0.00035341 | 2.9208e-06
2013-04-21 | 298690 | ARG5A | Urban | LV Transformer SP4181-G ARG5A - Planned | 19.38 | 166 | 3217.08 | 0.0032401 | 1.9519e-05
2013-04-21 | 298691 | MTG13A | Urban | LV Transformer SC5960-F MTG13A - Planned | 9.18 | 271 | 2487.78 | 0.0025056 | 9.2457e-06
2013-04-21 | 298986 | SMR9A | Urban | Feeder JDL8A, SMR9A - Planned | 28 | 489 | 13692 | 0.01379 | 2.82e-05
2013-04-22 | 298714 | BNH6A | Rural short | Feeder BNH6A - Planned | 20.01 | 210 | 4202.1 | 0.012104 | 5.764e-05
2013-04-22 | 298733 | PWC4 | Rural short | LV Transformer SP6576-B PWC4 - Planned | 6.02 | 261 | 1571.22 | 0.004526 | 1.7341e-05
2013-04-22 | 298734 | TRP2 | Rural short | Feeder TRP2 - Planned | 57.66 | 328 | 18912.48 | 0.054479 | 0.00016609
2013-04-22 | 298735 | THL3 | Rural short | LV Transformer SP3039-C THL3 - Planned | 4 | 365 | 1460 | 0.0042056 | 1.1522e-05
2013-04-22 | 298736 | SPO5A | Urban | LV Transformer SG7064-D SPD4A - Planned | 9.38 | 160 | 1500.8 | 0.0015115 | 9.4468e-06
2013-04-22 | 298742 | GYM2A | Rural short | LV Transformer SP2663-C GYM2A - Planned | 6.16 | 263 | 1620.08 | 0.0046668 | 1.7744e-05
2013-04-22 | 298774 | HPE13A | Urban | LV Transformer SP3148-G HPE13A - Planned | 31.335 | 321 | 10058.535 | 0.01013 | 3.1558e-05
2013-04-22 | 298774 | HPK6 | Urban | LV Transformer SP3148-G HPE13A - Planned | 0.85 | 321 | 272.85 | 0.00027479 | 8.5605e-07
2013-04-22 | 298776 | CPR6 | Urban | LV Transformer SP1423-K CPR6 - Planned | 35.86 | 169 | 6060.34 | 0.0061035 | 3.6115e-05
2013-04-22 | 298777 | WED16A | Urban | LV Transformer SP135-O WED16A - Planned | 37.8594 | 210 | 7950.474 | 0.0080071 | 3.8129e-05
2013-04-22 | 298777 | WED20A | Urban | LV Transformer SP135-O WED16A - Planned | 1.475 | 210 | 309.75 | 0.00031196 | 1.4855e-06
2013-04-22 | 298778 | RIS2 | Urban | LV Transformer SP6219-D RIS2 - Planned | 26.8 | 94 | 2519.2 | 0.0025371 | 2.6991e-05
2013-04-22 | 298779 | NIP3A | Urban | LV Transformer SP762156 NIP3A - Planned | 11.02 | 195 | 2148.9 | 0.0021642 | 1.1098e-05
2013-04-22 | 298780 | EZRRWD4 | Rural short | LV Transformer SP2498-E EZRRWD4 - Planned | 5.0985 | 100 | 509.85 | 0.0014687 | 1.4687e-05
2013-04-22 | 298781 | INA11A | Urban | LV Transformer SP2230-K INA11A - Planned | 1.64 | 235 | 385.4 | 0.00038814 | 1.6517e-06
2013-04-22 | 298782 | CLM7 | Urban | LV Transformer SP6624-A CLM7 - Planned | 34.8 | 228 | 7934.4 | 0.0079909 | 3.5048e-05
2013-04-22 | 298783 | RBA37A | Urban | LV Transformer SC714964 RBA37A - Planned | 10.36 | 194 | 2009.84 | 0.0020242 | 1.0434e-05
2013-04-22 | 298784 | MTB13A | Rural short | LV Transformer SP1794-F MTB13A - Planned | 8.96 | 340 | 3046.4 | 0.0087754 | 2.581e-05
2013-04-22 | 298785 | WNM5 | Urban | LV Transformer SP2140-J WNM5 - Planned | 13.2 | 262 | 3458.4 | 0.003483 | 1.3294e-05
2013-04-22 | 298787 | LTA4B | Urban | LV Transformer SP13061-G LTA4B - Planned | 29.15 | 228 | 6646.2 | 0.0066935 | 2.9358e-05
2013-04-22 | 298788 | ZMR7A | Urban | LV Transformer SP5865-G ZMR7A - Planned | 15.5862 | 220 | 3428.964 | 0.0034534 | 1.5697e-05
2013-04-22 | 298788 | ZMR9 | Urban | LV Transformer SP5865-G ZMR7A - Planned | 1.7333 | 220 | 381.326 | 0.00038404 | 1.7456e-06
2013-04-23 | 298753 | GYM2A | Rural short | Feeder GYM2A - Planned | 260.375 | 83 | 21611.125 | 0.062259 | 0.00075011
2013-04-23 | 298754 | COR23A | Rural short | Feeder COR23A - Planned | 65.28 | 142 | 9269.76 | 0.026705 | 0.00018806
2013-04-23 | 298755 | MLY1 | Rural short | LV Transformer SP9558-A MLY1 - Planned | 3 | 189 | 567 | 0.0016335 | 8.6427e-06
2013-04-23 | 298756 | RBA43A | Rural short | LV Transformer SP3753-C RBA43A - Planned | 12 | 136 | 1632 | 0.0047016 | 3.4571e-05
2013-04-23 | 298757 | COR23A | Rural short | LV Transformer SP6000-C COR23A - Planned | 5.5629 | 240 | 1335.096 | 0.0038463 | 1.6026e-05
2013-04-23 | 298758 | AMR2 | Rural short | Feeder AMR2 - Planned | 18.22 | 204 | 3716.88 | 0.010708 | 5.249e-05
2013-04-23 | 298759 | KBN2A | Rural short | Feeder KBN2A - Planned | 25 | 210 | 5250 | 0.015125 | 7.2022e-05
2013-04-23 | 298761 | NBR5 | Rural short | Feeder NBR5 - Planned | 64.12 | 314 | 20133.68 | 0.058003 | 0.00018472
2013-04-23 | 298762 | KWH3 | Rural short | Feeder KWH3 - Planned | 12.26 | 210 | 2574.6 | 0.0074171 | 3.532e-05
2013-04-23 | 298763 | CNA9A | Rural short | Feeder CNA9A - Planned | 1 | 282 | 282 | 0.00081241 | 2.8809e-06
2013-04-23 | 298764 | TGW1 | Rural short | Feeder TGW1 - Planned | 17.5 | 340 | 5950 | 0.017141 | 5.0416e-05
2013-04-23 | 298765 | NBR8 | Rural short | Feeder NBR8 - Planned | 19.67 | 311 | 6117.37 | 0.017623 | 5.6667e-05
2013-04-23 | 298768 | IBL2 | Rural short | Feeder IBL2 - Planned | 54.06 | 345 | 18650.7 | 0.053731 | 0.00015574
2013-04-23 | 298769 | YTA1B | Rural short | LV Transformer SP781124 YTA1B - Planned | 1 | 366 | 366 | 0.0010544 | 2.8809e-06
2013-04-23 | 298770 | RLB16A | Rural short | Feeder RLB16A - Planned | 6.09 | 300 | 1827 | 0.0052634 | 1.7545e-05
2013-04-23 | 298771 | BDT1 | Rural short | Feeder BDT1 - Planned | 11 | 438 | 4818 | 0.01388 | 3.169e-05
2013-04-23 | 298772 | GYM7A | Rural short | Feeder GYM7A - Planned | 34.15 | 300 | 10245 | 0.029515 | 9.8382e-05
2013-04-23 | 298786 | GYM2A | Rural short | Feeder GYM2A - Planned | 89.9604 | 130 | 11694.852 | 0.033692 | 0.00025917
2013-04-23 | 298790 | CRB25A | Rural short | Feeder CRB25A - Planned | 29.5 | 469 | 13835.5 | 0.039859 | 8.4986e-05
2013-04-23 | 298793 | TWG11 | Urban | LV Transformer SP2927-K TWG11 - Planned | 18.81 | 268 | 5041.08 | 0.0050766 | 1.8943e-05
2013-04-23 | 298794 | SHW6 | Urban | LV Transformer SP12359-F SHW6 - Planned | 24.59 | 351 | 8631.09 | 0.0086919 | 2.4763e-05
2013-04-23 | 298795 | SMF5A | Rural short | LV Transformer SP1604-L SMF5A - Planned | 4.95 | 230 | 1138.5 | 0.0032799 | 1.426e-05
2013-04-23 | 298796 | SHW6 | Urban | LV Transformer SP8174-G SHW6 - Planned | 5.705 | 130 | 741.65 | 0.00074688 | 5.7452e-06
2013-04-23 | 298797 | AMR1 | Rural short | LV Transformer SP18153-A AMR1 - Planned | 7 | 61 | 427 | 0.0012301 | 2.0166e-05
2013-04-23 | 298798 | CRY5A | Rural short | LV Transformer SP4837-C CRY5A - Planned | 4.98 | 202 | 1005.96 | 0.0028981 | 1.4347e-05
2013-04-23 | 298799 | KWH3 | Rural short | LV Transformer SP2006-D KWH3 - Planned | 6.02 | 158 | 951.16 | 0.0027402 | 1.7343e-05
2013-04-23 | 298800 | SPO32A | Urban | LV Transformer SP761826 SPO32A - Planned | 31.82 | 471 | 14987.22 | 0.015093 | 3.2044e-05
2013-04-23 | 298800 | SPO67B | Urban | LV Transformer SP761826 SPO32A - Planned | 7.02 | 471 | 3306.42 | 0.0033297 | 7.0695e-06
2013-04-23 | 298801 | DRD15B | Urban | LV Transformer SP329-J DRD15B - Planned | 4.9 | 333 | 1631.7 | 0.0016432 | 4.9346e-06
2013-04-23 | 298802 | SGT7 | Urban | LV Transformer SP1612-J SGT7 - Planned | 8.07 | 205 | 1654.35 | 0.001666 | 8.1269e-06
2013-04-23 | 298803 | SGT7 | Urban | LV Transformer SP38-K SGT7 - Planned | 19.005 | 334 | 6347.67 | 0.0063924 | 1.9139e-05
2013-04-23 | 298804 | LTA4B | Urban | LV Transformer SP1216-N LTA4B - Planned | 15.14 | 210 | 3179.4 | 0.0032018 | 1.5247e-05
2013-04-23 | 298805 | BHL4A | Urban | LV Transformer SP2976-H BHL4A - Planned | 76 | 279 | 21204 | 0.021354 | 7.6536e-05
2013-04-23 | 298806 | SBK10A | Rural short | LV Transformer SP1659-J SBK10A - Planned | 8.16 | 247 | 2015.52 | 0.0058065 | 2.3508e-05
2013-04-23 | 298807 | ARG5A | Urban | LV Transformer SP2138-L ARG5A - Planned | 29 | 167 | 4843 | 0.0048771 | 2.9204e-05
2013-04-23 | 298808 | MTG5A | Urban | LV Transformer SP19087-G MTG5A - Planned | 15.975 | 189 | 3019.275 | 0.0030406 | 1.6088e-05
2013-04-23 | 298809 | ARG5A | Urban | LV Transformer SP5899-E ARG5A - Planned | 14.28 | 312 | 4455.36 | 0.0044868 | 1.4381e-05
2013-04-23 | 298810 | CPD1 | Rural short | LV Transformer SP2340-D CPD1 - Planned | 4 | 335 | 1340 | 0.0038604 | 1.1524e-05
2013-04-23 | 298821 | TWG17 | Urban | LV Transformer SP3653-I TWG17 - Planned | 21.84 | 430 | 9391.2 | 0.0094574 | 2.1994e-05
2013-04-23 | 298985 | BGY15A | Urban | LV Transformer SP8640-C BGY15A - Planned | 32 | 450 | 14400 | 0.014502 | 3.2226e-05
2013-04-24 | 298835 | BNH1B | Rural short | LV Transformer SP3755-C BNH1B - Planned | 5 | 142 | 710 | 0.0020456 | 1.4406e-05
2013-04-24 | 298855 | MGP13A | Rural short | Feeder MGP13A - Planned | 71 | 251 | 17821 | 0.051344 | 0.00020456
2013-04-24 | 298856 | KBR1A | Rural short | LV Transformer SP13684-B KBR1A - Planned | 2 | 318 | 636 | 0.0018324 | 5.7622e-06
2013-04-24 | 298857 | MGL9 | Rural short | LV Transformer SP3476-H MGL9 - Planned | 3 | 348 | 1044 | 0.0030079 | 8.6434e-06
2013-04-24 | 298873 | TGW3 | Rural short | LV Transformer SP4752-B TGW3 - Planned | 4 | 267 | 1068 | 0.003077 | 1.1524e-05
2013-04-24 | 298875 | THL2 | Rural short | Feeder THL2 - Planned | 24.02 | 430 | 10328.6 | 0.029758 | 6.9204e-05
2013-04-24 | 298876 | BWH12A | Rural short | Feeder BWH12A - Planned | 101 | 70 | 7070 | 0.020369 | 0.00029099
2013-04-24 | 298877 | ABY5A | Rural short | Feeder ABY5A - Planned | 15.5 | 353 | 5471.5 | 0.015764 | 4.4657e-05
2013-04-24 | 298878 | GYM7A | Rural short | Feeder GYM7A - Planned | 13.67 | 380 | 5194.6 | 0.014966 | 3.9385e-05
2013-04-24 | 298879 | BMT1 | Rural short | Feeder BMT1 - Planned | 108.49 | 224 | 24301.76 | 0.070016 | 0.00031257
2013-04-24 | 298880 | KWH1 | Rural short | Feeder KWH1 - Planned | 35.68 | 156 | 5566.08 | 0.016037 | 0.0001028
2013-04-24 | 298881 | CRY6A | Rural short | Feeder CRY6A - Planned | 4.01 | 294 | 1178.94 | 0.0033967 | 1.1553e-05
2013-04-24 | 298882 | IBL2 | Rural short | LV Transformer SP735487 IBL2 - Planned | 1 | 67 | 67 | 0.00019303 | 2.8811e-06
2013-04-24 | 298883 | ZMR7A | Urban | LV Transformer SC4370-H ZMR7A - Planned | 4.2 | 177 | 743.4 | 0.00074861 | 4.2294e-06
2013-04-24 | 298884 | TWG17 | Urban | LV Transformer SP758641 TWG17 - Planned | 34.4 | 292 | 10044.8 | 0.010115 | 3.4641e-05
2013-04-24 | 298886 | BBH12B | Urban | LV Transformer SP3376-F BBH12B - Planned | 9.2 | 155 | 1426 | 0.001436 | 9.2645e-06
2013-04-24 | 298887 | BDT1 | Rural short | LV Transformer SP404312 BDT1 - Planned | 3 | 200 | 600 | 0.0017287 | 8.6434e-06
2013-04-24 | 298888 | HWL3A | Urban | LV Transformer SP3210-G HWL3A - Planned | 113.76 | 218 | 10524.96 | 0.010599 | 0.00011456
2013-04-24 | 298889 | PPE3A | Rural short | LV Transformer SC22305-B PPE3A - Planned | 7.32 | 248 | 1815.36 | 0.0052303 | 2.109e-05
2013-04-24 | 298890 | MRE2 | Urban | LV Transformer SP5846-G MRE2 - Planned | 2.72 | 375 | 1020 | 0.0010271 | 2.7391e-06
2013-04-24 | 298890 | MRE3 | Urban | LV Transformer SP5846-G MRE2 - Planned | 7.36 | 375 | 2760 | 0.0027793 | 7.4116e-06
2013-04-24 | 298891 | BHL4A | Urban | LV Transformer SP2515-H BHL4A - Planned | 9.68 | 153 | 1481.04 | 0.0014914 | 9.7478e-06
2013-04-24 | 298892 | NDH10 | Urban | LV Transformer SP5951-G NDH10 - Planned | 3.875 | 165 | 639.375 | 0.00064386 | 3.9022e-06
2013-04-24 | 298893 | WNM5 | Urban | LV Transformer SP680-N WNM5 - Planned | 32.22 | 170 | 5477.4 | 0.0055158 | 3.2446e-05
2013-04-24 | 298895 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 16.383 | 365 | 5979.795 | 0.0060217 | 1.6498e-05
2013-04-24 | 298896 | MTG3A | Urban | LV Transformer SP1403086 MTG3A - Planned | 24.48 | 316 | 7735.68 | 0.0077899 | 2.4652e-05
2013-04-24 | 298897 | HPE13A | Urban | LV Transformer SP743797 HPE13A - Planned | 19.98 | 329 | 6573.42 | 0.0066195 | 2.012e-05
2013-04-24 | 298905 | KBN2A | Rural short | Feeder KBN2A - Planned | 30 | 560 | 16800 | 0.048403 | 8.6434e-05
2013-04-26 | 298934 | LHM5 | Rural short | LV Transformer SP9720-C LHM5 - Planned | 76 | 280 | 21280 | 0.061318 | 0.00021899
2013-04-26 | 298935 | BGY5A | Rural short | Feeder BGY5A - Planned | 46 | 293 | 13478 | 0.038837 | 0.00013255
2013-04-26 | 298936 | MLY1 | Rural short | LV Transformer SP17947-B MLY1 - Planned | 1 | 221 | 221 | 0.00063681 | 2.8815e-06
2013-04-26 | 298937 | CLM8 | Urban | LV Transformer SP2873-A CLM8 - Planned | 10.26 | 152 | 1559.52 | 0.0015703 | 1.0331e-05
2013-04-26 | 298938 | NVL3 | Rural short | LV Transformer SP2353-E NVL3 - Planned | 2.79 | 200 | 558 | 0.0016079 | 8.0394e-06
2013-04-26 | 298939 | NMC13A | Rural short | LV Transformer SP6036-I NMC13A - Planned | 4.4 | 345 | 1518 | 0.0043741 | 1.2679e-05
2013-04-26 | 298940 | SGT22A | Urban | LV Transformer SP3161-H SGT22A - Planned | 21.84 | 245 | 5350.8 | 0.0053879 | 2.1991e-05
2013-04-26 | 298941 | WSE3A | Rural short | LV Transformer SP5728-C WSE3A - Planned | 81.78 | 239 | 19545.42 | 0.05632 | 0.00023565
2013-04-26 | 298942 | QPT5 | Urban | LV Transformer SP754918 QPT5 - Planned | 6.08 | 157 | 954.56 | 0.00096117 | 6.1221e-06
2013-04-26 | 298943 | SBK11 | Urban | LV Transformer SP25912-F SBK11 - Planned | 2.47 | 186 | 459.42 | 0.0004626 | 2.4871e-06
2013-04-26 | 298944 | HPK3A | Urban | LV Transformer SP1071-M HPK3A - Planned | 10.44 | 296 | 3090.24 | 0.0031116 | 1.0512e-05
2013-04-26 | 298945 | LGL3A | Urban | LV Transformer SP9829-C LGL3A - Planned | 1.83 | 170 | 311.1 | 0.00031326 | 1.8427e-06
2013-04-26 | 298946 | CPK13 | Rural short | LV Transformer SP14142-A CPK13 - Planned | 21.52 | 310 | 6671.2 | 0.019223 | 6.201e-05
2013-04-26 | 298947 | CPK9 | Rural short | LV Transformer SP3412-B CPK9 - Planned | 10.34 | 83 | 858.22 | 0.002473 | 2.9795e-05
2013-04-26 | 298948 | WNM5 | Urban | LV Transformer SC2219-N WNM5 - Planned | 37.03 | 251 | 9294.53 | 0.0093589 | 3.7287e-05
2013-04-26 | 298949 | TGW1 | Rural short | Feeder TGW1 - Planned | 2 | 338 | 676 | 0.0019479 | 5.763e-06
2013-04-26 | 298951 | MTB17A | Rural short | LV Transformer SP4871-F MTB17A - Planned | 16 | 420 | 6720 | 0.019364 | 4.6104e-05
2013-04-27 | 298983 | BNH1B | Rural short | LV Transformer SP1542-E BNH1B - Planned | 5 | 267 | 1335 | 0.0038466 | 1.4407e-05
2013-04-28 | 298989 | LLY3 | Rural short | LV Transformer SC2280-G SMR7B - Planned | 0.8 | 264 | 211.2 | 0.00060858 | 2.3052e-06
2013-04-28 | 298989 | SMR7B | Urban | LV Transformer SC2280-G SMR7B - Planned | 37.6072 | 264 | 9928.3008 | 0.0099968 | 3.7867e-05
2013-04-28 | 298990 | SPO67B | Urban | LV Transformer SP3691-F SPO67B - Planned | 32.3498 | 315 | 10190.187 | 0.010261 | 3.2573e-05
2013-04-28 | 298991 | MRE1 | Urban | LV Transformer SC747299 MRE1 - Planned | 11 | 375 | 4125 | 0.0041535 | 1.1076e-05
2013-04-28 | 298993 | DRA9 | Urban | Feeder DRA9 - Planned | 23 | 554 | 12742 | 0.01283 | 2.3159e-05
2013-04-28 | 298994 | KBN1B | Rural short | Feeder KBN5A, KBN1B - Planned | 4 | 550 | 2200 | 0.0063394 | 1.1526e-05
2013-04-28 | 298994 | KBN5A | Rural short | Feeder KBN5A, KBN1B - Planned | 18 | 71 | 1278 | 0.0036826 | 5.1868e-05
2013-04-28 | 298995 | SGT9 | Urban | LV Transformer SC1922-H SGT9 - Planned | 3.58 | 368 | 1317.44 | 0.0013265 | 3.6047e-06
2013-04-29 | 299014 | KCY4 | Rural short | Feeder KCY4 - Planned | 6 | 39 | 234 | 0.00067433 | 1.7291e-05
2013-04-29 | 299033 | TGW1 | Rural short | LV Transformer SP783-B TGW1 - Planned | 5.5 | 70 | 385 | 0.0011095 | 1.585e-05
2013-04-29 | 299034 | MBG4 | Rural short | LV Transformer SP8520-B MBG4 - Planned | 3 | 67 | 201 | 0.00057923 | 8.6453e-06
2013-04-29 | 299035 | LLY3 | Rural short | LV Transformer SP2794-B LLY3 - Planned | 2.01 | 217 | 436.17 | 0.0012569 | 5.7923e-06
2013-04-29 | 299036 | BNH6A | Rural short | LV Transformer SP10981-C BNH6A - Planned | 1 | 272 | 272 | 0.00078384 | 2.8818e-06
2013-04-29 | 299037 | MBG1 | Rural short | Feeder MBG1 - Planned | 3.9 | 187 | 729.3 | 0.0021017 | 1.1239e-05
2013-04-29 | 299039 | MBG4 | Rural short | LV Transformer SP4204-G MBG4 - Planned | 6 | 67 | 402 | 0.0011585 | 1.7291e-05
2013-04-29 | 299040 | TRP2 | Rural short | LV Transformer SP2450-C TRP2 - Planned | 1 | 219 | 219 | 0.0006311 | 2.8818e-06
2013-04-29 | 299043 | TGW1 | Rural short | LV Transformer SP1832-C TGW1 - Planned | 1 | 265 | 265 | 0.00076366 | 2.8818e-06
2013-04-29 | 299044 | GYGGYS6 | Rural short | LV Transformer SP3906-D GYGGYS6 - Planned | 4 | 407 | 1628 | 0.0046915 | 1.1527e-05
2013-04-29 | 299045 | MLY4 | Rural short | LV Transformer SP7480-B MLY4 - Planned | 11 | 316 | 3476 | 0.010017 | 3.1699e-05
2013-04-29 | 299046 | COR23A | Rural short | Feeder COR23A - Planned | 59.325 | 249 | 14771.925 | 0.042569 | 0.00017096
2013-04-29 | 299047 | EMD3 | Rural short | LV Transformer SP5311-B EMD3 - Planned | 18 | 142 | 2556 | 0.0073658 | 5.1872e-05
2013-04-29 | 299050 | MLY1 | Rural short | LV Transformer SP1075-A MLY1 - Planned | 3 | 420 | 1260 | 0.003631 | 8.6453e-06
2013-04-29 | 299051 | BDT5 | Rural short | LV Transformer SP404236 BDT5 - Planned | 1.95 | 203 | 395.85 | 0.0011407 | 5.6194e-06
2013-04-29 | 299052 | INA9A | Urban | LV Transformer SP1970-K INA9A - Planned | 20.7 | 228 | 4719.6 | 0.0047519 | 2.0842e-05
2013-04-29 | 299053 | INA5A | Urban | LV Transformer SC2051031 INA5A - Planned | 0.96 | 191 | 183.36 | 0.00018462 | 9.6658e-07
2013-04-29 | 299054 | TWG18 | Urban | LV Transformer SP1834353 TWG18 - Planned | 7.275 | 215 | 1564.125 | 0.0015748 | 7.3249e-06
2013-04-29 | 299055 | EMD3 | Rural short | LV Transformer SP4557-C EMD3 - Planned | 5.04 | 100 | 504 | 0.0014524 | 1.4524e-05
2013-04-29 | 299056 | AMR2 | Rural short | LV Transformer SP436-C AMR2 - Planned | 9.5 | 215 | 2042.5 | 0.005886 | 2.7377e-05
2013-04-29 | 299057 | NBR5 | Rural short | LV Transformer SP4333-A NBR5 - Planned | 1.105 | 250 | 276.25 | 0.00079608 | 3.1843e-06
2013-04-29 | 299058 | CCY26A | Urban | LV Transformer SC770439 CCY26A - Planned | 96.75 | 95 | 9191.25 | 0.0092542 | 9.7413e-05
2013-04-29 | 299059 | SPO51A | Urban | LV Transformer SP2320-F SPO51A - Planned | 30.38 | 431 | 13093.78 | 0.013184 | 3.0588e-05
2013-04-29 | 299060 | MTB15A | Rural short | LV Transformer SP8659-D MTB15A - Planned | 23.475 | 285 | 6690.375 | 0.01928 | 6.7649e-05
2013-04-29 | 299061 | LTA4B | Urban | LV Transformer SP4421-H LTA4B - Planned | 31.2 | 362 | 11294.4 | 0.011372 | 3.1414e-05
2013-04-29 | 299062 | ZMR7A | Urban | LV Transformer SC4370-H ZMR7A - Planned | 10.6065 | 380 | 4030.47 | 0.0040581 | 1.0679e-05
2013-04-29 | 299063 | WNM5 | Urban | LV Transformer SP2140-J WNM5 - Planned | 7.79 | 144 | 1121.76 | 0.0011294 | 7.8434e-06
2013-04-29 | 299064 | DRD15B | Urban | LV Transformer SP329-J DRD15B - Planned | 19.6 | 290 | 5684 | 0.005723 | 1.9734e-05
2013-04-29 | 299065 | ARG5A | Urban | LV Transformer SP2472-M ARG5A - Planned | 16.335 | 289 | 4720.815 | 0.0047532 | 1.6447e-05
2013-04-29 | 299066 | RPN4A | Rural short | LV Transformer SC2057418 RPN4A - Planned | 3.08 | 287 | 883.96 | 0.0025474 | 8.8758e-06
2013-04-29 | 299120 | TWG17 | Urban | LV Transformer SP758641 TWG17 - Planned | 10.32 | 138 | 1424.16 | 0.0014339 | 1.0391e-05
2013-04-29 | 299336 | TWT2B | Rural short | Feeder TWT2B - Planned | 1.6 | 171 | 273.6 | 0.00078845 | 4.6108e-06
2013-04-29 | 299337 | IPL4A | Rural short | Feeder IPL4A - Planned | 15.9 | 448 | 7123.2 | 0.020527 | 4.582e-05
2013-04-30 | 299095 | GTN12A | Rural short | LV Transformer SP2689-C GTN12A - Planned | 1 | 231 | 231 | 0.00066573 | 2.882e-06
2013-04-30 | 299096 | MBG4 | Rural short | LV Transformer SP5277-B MBG4 - Planned | 7 | 87 | 609 | 0.0017551 | 2.0174e-05
2013-04-30 | 299098 | BNH1B | Rural short | LV Transformer SP1442-H BNH1B - Planned | 1 | 195 | 195 | 0.00056198 | 2.882e-06
2013-04-30 | 299102 | LLY1 | Rural short | LV Transformer SP2324-C LLY1 - Planned | 0.99 | 142 | 140.58 | 0.00040515 | 2.8531e-06
2013-04-30 | 299103 | BMT1 | Rural short | Feeder BMT1 - Planned | 39 | 161 | 6279 | 0.018096 | 0.0001124
2013-04-30 | 299104 | KBN2A | Rural short | Feeder KBN2A - Planned | 37 | 302 | 11174 | 0.032203 | 0.00010663
2013-04-30 | 299105 | GYM9B | Rural short | LV Transformer SP6488-C GYM9B - Planned | 6 | 354 | 2124 | 0.0061213 | 1.7292e-05
2013-04-30 | 299106 | IPL2A | Rural short | LV Transformer SP3257-B IPL2A - Planned | 3.67 | 249 | 913.83 | 0.0026336 | 1.0577e-05
2013-04-30 | 299107 | MFN12A | Rural short | LV Transformer SP5070-G MFN12A - Planned | 14 | 317 | 4438 | 0.01279 | 4.0348e-05
2013-04-30 | 299108 | MLY1 | Rural short | Feeder MLY1 - Planned | 115.44 | 404 | 46637.76 | 0.13441 | 0.00033269
2013-04-30 | 299109 | GBN4 | Rural short | Feeder GBN4 - Planned | 45.5 | 343 | 15606.5 | 0.044977 | 0.00013113
2013-04-30 | 299110 | NMC1B | Rural short | Feeder NMC1B - Planned | 68.8 | 218 | 14998.4 | 0.043225 | 0.00019828
2013-04-30 | 299111 | TGW3 | Rural short | Feeder TGW3 - Planned | 12.01 | 381 | 4575.81 | 0.013187 | 3.4612e-05
2013-04-30 | 299112 | GGR1 | Rural short | LV Transformer SP4727-B GGR1 - Planned | 16.02 | 18 | 288.36 | 0.00083104 | 4.6169e-05
2013-04-30 | 299118 | KRN12 | Urban | LV Transformer SP2710-I KRN12 - Planned | 3.41 | 264 | 900.24 | 0.00090638 | 3.4332e-06
2013-04-30 | 299119 | RLB16A | Rural short | LV Transformer SP12488-A RLB16A - Planned | 1 | 384 | 384 | 0.0011067 | 2.882e-06
2013-04-30 | 299121 | TWG17 | Urban | LV Transformer SP3047-L TWG17 - Planned | 16.645 | 257 | 4277.765 | 0.0043069 | 1.6758e-05
2013-04-30 | 299122 | SHW6 | Urban | LV Transformer SP245-O SHW6 - Planned | 26.3676 | 274 | 7224.7224 | 0.007274 | 2.6547e-05
2013-04-30 | 299123 | CLM8 | Urban | LV Transformer SP4427-A CLM8 - Planned | 79.38 | 253 | 20083.14 | 0.02022 | 7.9921e-05
2013-04-30 | 299123 | CLM9 | Urban | LV Transformer SP4427-A CLM8 - Planned | 3.92 | 253 | 991.76 | 0.00099852 | 3.9467e-06
2013-04-30 | 299124 | COR25A | Rural short | LV Transformer SP78-C COR25A - Planned | 11 | 75 | 825 | 0.0023776 | 3.1702e-05
2013-04-30 | 299125 | BMT1 | Rural short | LV Transformer SP5913-B BMT1 - Planned | 1 | 97 | 97 | 0.00027955 | 2.882e-06
2013-04-30 | 299126 | SBH11 | Urban | LV Transformer SP1319-J SBH11 - Planned | 2.67 | 255 | 680.85 | 0.00068549 | 2.6882e-06
2013-04-30 | 299127 | LTA4B | Urban | LV Transformer SP4421-H LTA4B - Planned | 20.8 | 365 | 7592 | 0.0076438 | 2.0942e-05
2013-04-30 | 299128 | NGE13 | Urban | LV Transformer SG2004-K NGE13 - Planned | 1.04 | 315 | 327.6 | 0.00032983 | 1.0471e-06
2013-04-30 | 299129 | CPR5 | Urban | LV Transformer SP27-O HPE13A - Planned | 1.32 | 346 | 456.72 | 0.00045983 | 1.329e-06
2013-04-30 | 299129 | HPE13A | Urban | LV Transformer SP27-O HPE13A - Planned | 8.94 | 346 | 3093.24 | 0.0031143 | 9.0009e-06
2013-04-30 | 299130 | HPE13A | Urban | LV Transformer SP16619-E HPE13A - Planned | 4.44 | 250 | 1110 | 0.0011176 | 4.4703e-06
2013-04-30 | 299131 | HPE5A | Urban | LV Transformer SP196-N HPE5A - Planned | 17.76 | 309 | 5487.84 | 0.0055252 | 1.7881e-05
2013-04-30 | 299132 | RBK9A | Urban | LV Transformer SP3797-C RBK9A - Planned | 5.175 | 141 | 729.675 | 0.00073465 | 5.2103e-06
2013-04-30 | 299133 | RPN4A | Rural short | LV Transformer SC2057418 RPN4A - Planned | 3.08 | 372 | 1145.76 | 0.003302 | 8.8765e-06
2013-04-30 | 299134 | RBK9A | Urban | LV Transformer SP3797-C RBK9A - Planned | 2.07 | 162 | 335.34 | 0.00033763 | 2.0841e-06
2013-04-30 | 299135 | SPF15A | Urban | LV Transformer SC2055204 SPF15A - Planned | 1 | 190 | 190 | 0.0001913 | 1.0068e-06
2013-04-30 | 299136 | SPO60A | Urban | LV Transformer SP36457-C SPO60A - Planned | 3.22 | 284 | 914.48 | 0.00092071 | 3.242e-06
2013-04-30 | 299136 | SPO8A | Urban | LV Transformer SP36457-C SPO60A - Planned | 5.88 | 284 | 1669.92 | 0.0016813 | 5.9201e-06
2013-04-30 | 299137 | WFD3A | Rural short | Feeder WFD3A - Planned | 5 | 470 | 2350 | 0.0067726 | 1.441e-05
2013-04-30 | 299139 | CRB25A | Rural short | LV Transformer SP468679 CRB25A - Planned | 2 | 492 | 984 | 0.0028359 | 5.7639e-06
2013-04-30 | 299140 | CPC2A | Rural short | LV Transformer SP2898-J CPC2A - Planned | 8.4 | 520 | 4368 | 0.012588 | 2.4209e-05
2013-04-30 | 299141 | CRB25A | Rural short | Feeder CRB25A - Planned | 9 | 547 | 4923 | 0.014188 | 2.5938e-05
2013-04-30 | 299144 | WNM5 | Urban | LV Transformer SP2141-L WNM5 - Planned | 35.52 | 279 | 9910.08 | 0.0099776 | 3.5762e-05
2013-05-01 | 299149 | NIP5B | Urban | LV Transformer SP736344 NIP5B - Planned | 0.975 | 32 | 31.2 | 3.1412e-05 | 9.8161e-07
2013-05-01 | 299154 | GYS3A | Rural short | LV Transformer SP4851-C GYS3A - Planned | 1 | 57 | 57 | 0.00016429 | 2.8822e-06
2013-05-01 | 299155 | CBW11 | Rural short | LV Transformer SP5709-E CBW11 - Planned | 12 | 176 | 2112 | 0.0060872 | 3.4586e-05
2013-05-01 | 299156 | LLY5 | Rural short | LV Transformer SP3665-C LLY5 - Planned | 1 | 94 | 94 | 0.00027093 | 2.8822e-06
2013-05-01 | 299158 | CBW11 | Rural short | Feeder CBW11 - Planned | 7 | 180 | 1260 | 0.0036316 | 2.0175e-05
2013-05-01 | 299159 | RBY10 | Urban | LV Transformer SC2193-C RBY10 - Planned | 103 | 26.5 | 5459 | 0.005496 | 0.0001037
2013-05-01 | 299160 | COR25A | Rural short | LV Transformer SP3533-A COR25A - Planned | 5 | 30 | 150 | 0.00043233 | 1.4411e-05
2013-05-01 | 299162 | THL3 | Rural short | LV Transformer SP5092-A THL3 - Planned | 2.01 | 231 | 464.31 | 0.0013382 | 5.7932e-06
2013-05-01 | 299163 | AMR3 | Rural short | LV Transformer SP6456-D AMR3 - Planned | 4 | 11 | 44 | 0.00012682 | 1.1529e-05
2013-05-01 | 299165 | FDS1 | Rural short | Feeder FDS1 - Planned | 11 | 330 | 3630 | 0.010462 | 3.1704e-05
2013-05-01 | 299173 | MTB17A | Rural short | LV Transformer SP4811-H MTB17A - Planned | 7 | 415 | 2905 | 0.0083728 | 2.0175e-05
2013-05-01 | 299174 | NRG16A | Rural short | LV Transformer SP11844-D NRG16A - Planned | 1 | 289 | 289 | 0.00083296 | 2.8822e-06
2013-05-01 | 299175 | BNH6A | Rural short | Feeder BNH6A - Planned | 26 | 332 | 8632 | 0.024879 | 7.4937e-05
2013-05-01 | 299176 | KSN7 | Rural short | LV Transformer SP2668-E KSN7 - Planned | 40.18 | 209 | 8397.62 | 0.024204 | 0.00011581
2013-05-01 | 299179 | RLB16A | Rural short | Feeder RLB16A - Planned | 3 | 495 | 1485 | 0.0042801 | 8.6466e-06
2013-05-01 | 299180 | NRG5A | Urban | Feeder NRG5A - Planned | 1 | 432 | 432 | 0.00043493 | 1.0068e-06
2013-05-01 | 299183 | MLT15A | Urban | LV Transformer SP554449-B MLT15A - Planned | 5.292 | 147 | 777.924 | 0.0007832 | 5.3279e-06
2013-05-01 | 299184 | ENG2 | Urban | LV Transformer SC1500260 ENG2 - Planned | 3.66 | 322 | 1178.52 | 0.0011865 | 3.6848e-06
2013-05-01 | 299185 | MLY1 | Rural short | LV Transformer SP768905 MLY1 - Planned | 1 | 126 | 126 | 0.00036316 | 2.8822e-06
2013-05-01 | 299186 | MLY4 | Rural short | LV Transformer SP2833-B MLY4 - Planned | 27.375 | 122 | 3339.75 | 0.0096258 | 7.89e-05
2013-05-01 | 299187 | GYS3A | Rural short | LV Transformer SP2578-E GYS3A - Planned | 10 | 183 | 1830 | 0.0052744 | 2.8822e-05
2013-05-01 | 299188 | NRG5A | Urban | LV Transformer SP5173-G NRG5A - Planned | 9.01 | 100 | 901 | 0.00090711 | 9.0711e-06
2013-05-01 | 299189 | MTB17A | Rural short | LV Transformer SP4757-D MTB17A - Planned | 7.36 | 405 | 2980.8 | 0.0085913 | 2.1213e-05
2013-05-01 | 299190 | BDL3 | Urban | LV Transformer SP80258-B BDL3 - Planned | 9.5 | 160 | 1520 | 0.0015303 | 9.5644e-06
2013-05-01 | 299191 | BHD21A | Urban | LV Transformer SP3503-E PBH2B - Planned | 1.03 | 450 | 463.5 | 0.00046664 | 1.037e-06
2013-05-01 | 299191 | PBH2B | Urban | LV Transformer SP3503-E PBH2B - Planned | 36.925 | 450 | 16616.25 | 0.016729 | 3.7175e-05
2013-05-01 | 299192 | CBT8A | Rural short | LV Transformer SP4137-E CBT8A - Planned | 21 | 155 | 3255 | 0.0093816 | 6.0526e-05
2013-05-01 | 299193 | BHL4A | Urban | LV Transformer SP3579-F BHL4A - Planned | 7.21 | 198 | 1427.58 | 0.0014373 | 7.2589e-06
2013-05-01 | 299194 | SGT22A | Urban | LV Transformer SP554494-B SGT22A - Planned | 14.2 | 189 | 2683.8 | 0.002702 | 1.4296e-05
2013-05-01 | 299195 | SGT22A | Urban | LV Transformer SP3161-H SGT22A - Planned | 13.65 | 228 | 3112.2 | 0.0031333 | 1.3743e-05
2013-05-01 | 299195 | SGT7 | Urban | LV Transformer SP3161-H SGT22A - Planned | 1.02 | 228 | 232.56 | 0.00023414 | 1.0269e-06
2013-05-01 | 299196 | NRA5A | Rural short | LV Transformer SP1381-H NRA5A - Planned | 4.08 | 362 | 1476.96 | 0.0042569 | 1.1759e-05
2013-05-01 | 299197 | WRG12A | Urban | LV Transformer SP7338-H WRG12A - Planned | 4.95 | 260 | 1287 | 0.0012957 | 4.9836e-06
2013-05-01 | 299198 | RCN2A | Urban | LV Transformer SC4570-J RCN2A - Planned | 7.133 | 229 | 1633.457 | 0.0016445 | 7.1814e-06
2013-05-01 | 299199 | BKD13A | Urban | LV Transformer SP3649-B BKD13A - Planned | 8.93 | 285 | 2545.05 | 0.0025623 | 8.9906e-06
2013-05-01 | 299200 | BLBNFM6 | Urban | LV Transformer SP5394-E BLBNFM6 - Planned | 20.7 | 198 | 4098.6 | 0.0041264 | 2.084e-05
2013-05-01 | 299201 | HPE13A | Urban | LV Transformer SP743797 HPE13A - Planned | 37.8325 | 353 | 13354.8725 | 0.013445 | 3.8089e-05
2013-05-01 | 299203 | BRT5 | Urban | LV Transformer SP37-L BRT5 - Planned | 1.37 | 54 | 73.98 | 7.4482e-05 | 1.3793e-06
2013-05-01 | 299204 | RPN3A | Urban | LV Transformer SP5146-E RPN3A - Planned | 37.17 | 355 | 13195.35 | 0.013285 | 3.7422e-05
2013-05-01 | 299205 | RPN8 | Rural short | LV Transformer SP3666-D RPN8 - Planned | 10.725 | 304 | 3260.4 | 0.0093971 | 3.0912e-05
2013-05-02 | 299213 | GYN3A | Rural short | LV Transformer SP4283-B GYN3A - Planned | 1.5 | 21 | 31.5 | 9.0797e-05 | 4.3237e-06
2013-05-02 | 299214 | BBHORW6 | Urban | LV Transformer SG7182-E BBHORW6 - Planned | 1 | 85 | 85 | 8.5574e-05 | 1.0067e-06
2013-05-02 | 299215 | JBB2A | Rural short | LV Transformer SP4026-D JBB2A - Planned | 36 | 161 | 5796 | 0.016707 | 0.00010377
2013-05-02 | 299217 | WHO1 | Rural short | Feeder WHO1 - Planned | 26.97 | 281 | 7578.57 | 0.021845 | 7.7739e-05
2013-05-02 | 299218 | GYN7A | Rural short | Feeder GYN7A - Planned | 42 | 227 | 9534 | 0.027481 | 0.00012106
2013-05-02 | 299219 | MLY6 | Rural short | Feeder MLY6 - Planned | 63.96 | 288 | 18420.48 | 0.053096 | 0.00018436
2013-05-02 | 299220 | BNH1B | Rural short | Feeder BNH1B - Planned | 16 | 368 | 5888 | 0.016972 | 4.6119e-05
2013-05-02 | 299221 | BNH6A | Rural short | Feeder BNH6A - Planned | 3.66 | 413 | 1511.58 | 0.004357 | 1.055e-05
2013-05-02 | 299222 | JBB16A | Rural short | LV Transformer SP383510 JBB16A - Planned | 22 | 179 | 3938 | 0.011351 | 6.3414e-05
2013-05-02 | 299224 | MTB16A | Rural short | Feeder MTB16A - Planned | 8 | 296 | 2368 | 0.0068256 | 2.3059e-05
2013-05-02 | 299225 | BNH6A | Rural short | LV Transformer SP3261-D BNH6A - Planned | 2 | 289 | 578 | 0.001666 | 5.7649e-06
2013-05-02 | 299226 | MBG2 | Rural short | Feeder MBG2 - Planned | 22 | 357 | 7854 | 0.022639 | 6.3414e-05
2013-05-02 | 299227 | WSE5A | Rural short | Feeder WSE5A - Planned | 77 | 468 | 36036 | 0.10387 | 0.00022195
2013-05-02 | 299228 | CRB25A | Rural short | Feeder CRB25A - Planned | 18 | 450 | 8100 | 0.023348 | 5.1884e-05
2013-05-02 | 299229 | BHD35A | Rural short | Feeder BHD35A - Planned | 10 | 492 | 4920 | 0.014182 | 2.8824e-05
2013-05-02 | 299231 | MFD12A | Urban | LV Transformer SP4587-E MFD12A - Planned | 9.275 | 289 | 2680.475 | 0.0026986 | 9.3376e-06
2013-05-02 | 299232 | TWG11 | Urban | LV Transformer SP1830-N TWG18 - Planned | 11.215 | 205 | 2299.075 | 0.0023146 | 1.1291e-05
2013-05-02 | 299232 | TWG18 | Urban | LV Transformer SP1830-N TWG18 - Planned | 2 | 205 | 410 | 0.00041277 | 2.0135e-06
2013-05-02 | 299233 | TWG18 | Urban | LV Transformer SP541-N TWG18 - Planned | 2.61 | 320 | 835.2 | 0.00084084 | 2.6276e-06
2013-05-02 | 299234 | GAP9A | Urban | LV Transformer SP797524 GAP9A - Planned | 16.875 | 230 | 3881.25 | 0.0039074 | 1.6989e-05
2013-05-02 | 299235 | SHW6 | Urban | LV Transformer SP1267-N SHW6 - Planned | 6.68 | 211 | 1409.48 | 0.001419 | 6.7251e-06
2013-05-02 | 299236 | AGE5B | Urban | LV Transformer SP4179-K AGE5B - Planned | 13.93 | 358 | 4986.94 | 0.0050206 | 1.4024e-05
2013-05-02 | 299237 | BWH13A | Rural short | LV Transformer SP5243-A BWH13A - Planned | 2.01 | 59 | 118.59 | 0.00034183 | 5.7937e-06
2013-05-02 | 299238 | NBR9 | Rural short | LV Transformer SP3993-B NBR9 - Planned | 6.08 | 82 | 498.56 | 0.0014371 | 1.7525e-05
2013-05-02 | 299239 | BHD36A | Urban | LV Transformer SP11558-D BHD36A - Planned | 52.43 | 246 | 12897.78 | 0.012985 | 5.2784e-05
2013-05-02 | 299240 | HIS1B | Urban | LV Transformer SC561997 HIS1B - Planned | 7.2 | 87 | 626.4 | 0.00063063 | 7.2486e-06
2013-05-02 | 299241 | SPO16A | Urban | LV Transformer SP3780-G SPO16A - Planned | 17.49 | 262 | 4582.38 | 0.0046133 | 1.7608e-05
2013-05-02 | 299241 | SPO60A | Urban | LV Transformer SP3780-G SPO16A - Planned | 7.83 | 262 | 2051.46 | 0.0020653 | 7.8828e-06
2013-05-02 | 299242 | LTA4B | Urban | LV Transformer SP4421-H LTA4B - Planned | 9.1 | 201 | 1829.1 | 0.0018414 | 9.1614e-06
2013-05-02 | 299243 | SGT7 | Urban | LV Transformer SP5991-F SGT7 - Planned | 25.2908 | 216 | 5462.8128 | 0.0054997 | 2.5461e-05
2013-05-02 | 299244 | SGT7 | Urban | LV Transformer SP5969-B SGT7 - Planned | 40.95 | 347 | 14209.65 | 0.014306 | 4.1226e-05
2013-05-02 | 299245 | HPE13A | Urban | LV Transformer SP1232-L HPE13A - Planned | 16.4575 | 471 | 7751.4825 | 0.0078038 | 1.6569e-05
2013-05-02 | 299246 | WRG1A | Urban | LV Transformer SP2419-M WRG1A - Planned | 2.16 | 289 | 624.24 | 0.00062845 | 2.1746e-06
2013-05-02 | 299247 | RLB16A | Rural short | LV Transformer SP20472-B RLB16A - Planned | 1 | 362 | 362 | 0.0010434 | 2.8824e-06
2013-05-02 | 299248 | CHL3 | Urban | LV Transformer SP174-N CHL3 - Planned | 13.6 | 266 | 3617.6 | 0.003642 | 1.3692e-05
2013-05-02 | 299249 | TMH15A | Urban | LV Transformer SP3539-C TMH15A - Planned | 2.92 | 318 | 928.56 | 0.00093483 | 2.9397e-06
2013-05-02 | 299250 | CPD1 | Rural short | LV Transformer SP3962-B CPD1 - Planned | 4.98 | 112 | 557.76 | 0.0016077 | 1.4355e-05
2013-05-02 | 299251 | CPK11 | Urban | LV Transformer SC761595 CPK11 - Planned | 12.08 | 71 | 857.68 | 0.00086347 | 1.2162e-05
2013-05-02 | 299252 | WHO1 | Rural short | LV Transformer SP8121-A WHO1 - Planned | 4 | 82 | 328 | 0.00094544 | 1.153e-05
2013-05-02 | 299253 | CPK11 | Urban | LV Transformer SC585827 CPK11 - Planned | 0.99 | 12 | 11.88 | 1.196e-05 | 9.9668e-07
2013-05-02 | 299254 | CPD1 | Rural short | LV Transformer SP3335-B CPD1 - Planned | 3 | 69 | 207 | 0.00059666 | 8.6473e-06
2013-05-02 | 299309 | TWG18 | Urban | LV Transformer SP1620-M TWG18 - Planned | 17.395 | 327 | 5688.165 | 0.0057266 | 1.7512e-05
2013-05-03 | 299273 | BNH6A | Rural short | LV Transformer SP15529-C BNH6A - Planned | 2 | 24 | 48 | 0.00013836 | 5.7651e-06
2013-05-03 | 299274 | BNH1B | Rural short | LV Transformer SP9467-D BNH1B - Planned | 1 | 112 | 112 | 0.00032285 | 2.8825e-06
2013-05-03 | 299275 | DRD15B | Urban | LV Transformer SP3602-E DRD15B - Planned | 50 | 111 | 5550 | 0.0055873 | 5.0336e-05
2013-05-03 | 299276 | CLM3 | Rural short | Feeder CLM3 - Planned | 2 | 182 | 364 | 0.0010492 | 5.7651e-06
2013-05-03 | 299277 | KBN5A | Rural short | LV Transformer SP4991-E KBN5A - Planned | 2 | 225 | 450 | 0.0012971 | 5.7651e-06
2013-05-03 | 299278 | IBL2 | Rural short | LV Transformer SP1818-F IBL2 - Planned | 2 | 175 | 350 | 0.0010089 | 5.7651e-06
2013-05-03 | 299280 | EMD3 | Rural short | Feeder EMD3 - Planned | 42 | 251 | 10542 | 0.030388 | 0.00012107
2013-05-03 | 299281 | KCY2 | Rural short | Feeder KCY2 - Planned | 69.25 | 240 | 16620 | 0.047908 | 0.00019962
2013-05-03 | 299293 | GBN2 | Rural short | Feeder GBN2 - Planned | 43.581 | 325 | 14163.825 | 0.040828 | 0.00012562
2013-05-03 | 299294 | GYN3A | Rural short | Feeder GYN3A - Planned | 222.03 | 238 | 52843.14 | 0.15232 | 0.00064001
2013-05-03 | 299296 | CRB25A | Rural short | Feeder CRB25A - Planned | 50.83 | 192 | 9759.36 | 0.028132 | 0.00014652
2013-05-03 | 299297 | BDT1 | Rural short | Feeder BDT1 - Planned | 11 | 352 | 3872 | 0.011161 | 3.1708e-05
2013-05-03 | 299300 | TGW3 | Rural short | Feeder TGW3 - Planned | 28.07 | 372 | 10442.04 | 0.0301 | 8.0913e-05
2013-05-03 | 299301 | KCY2 | Rural short | Feeder KCY2 - Planned | 41.458 | 323 | 13390.934 | 0.0386 | 0.0001195
2013-05-03 | 299307 | BMT1 | Rural short | Feeder BMT1 - Planned | 21.03 | 382 | 8033.46 | 0.023157 | 6.062e-05
2013-05-03 | 299308 | ENG2 | Urban | LV Transformer SG803-Q ENG2 - Planned | 18.9 | 289 | 5462.1 | 0.0054988 | 1.9027e-05
2013-05-03 | 299310 | TWT12A | Rural short | LV Transformer SP7578-C TWT12A - Planned | 18.05 | 135 | 2436.75 | 0.007024 | 5.203e-05
2013-05-03 | 299311 | TWT13A | Urban | LV Transformer SC1977-D TWT13A - Planned | 4.93 | 43 | 211.99 | 0.00021341 | 4.9631e-06
2013-05-03 | 299312 | KWA6A | Urban | LV Transformer SP5414-A KWA6A - Planned | 16.04 | 182 | 2919.28 | 0.0029389 | 1.6148e-05
2013-05-03 | 299313 | HWL3A | Urban | LV Transformer SP6468-F HWL3A - Planned | 14.8125 | 251 | 3717.9375 | 0.0037429 | 1.4912e-05
2013-05-03 | 299314 | RBA43A | Rural short | LV Transformer SP6445-G RBA43A - Planned | 13 | 256 | 3328 | 0.0095931 | 3.7473e-05
2013-05-03 | 299315 | HISSCV16 | Urban | LV Transformer SC1443160 HISSCV16 - Planned | 4 | 295 | 1180 | 0.0011879 | 4.0269e-06
2013-05-03 | 299315 | SCV4 | Urban | LV Transformer SC1443160 HISSCV16 - Planned | 3.91 | 295 | 1153.45 | 0.0011612 | 3.9363e-06
2013-05-03 | 299316 | CFD1A | Urban | LV Transformer SG2916-I CFD1A - Planned | 4.615 | 235 | 1084.525 | 0.0010918 | 4.646e-06
2013-05-03 | 299317 | CFD1A | Urban | LV Transformer SC4894-H CFD2A - Planned | 25.745 | 310 | 7980.95 | 0.0080346 | 2.5918e-05
2013-05-03 | 299318 | SGT22A | Urban | LV Transformer SP3763-F SGT22A - Planned | 31.62 | 220 | 6956.4 | 0.0070032 | 3.1833e-05
2013-05-03 | 299319 | BPN3 | Urban | LV Transformer SP79093-C BPN3 - Planned | 3.79 | 307 | 1163.53 | 0.0011714 | 3.8155e-06
2013-05-03 | 299320 | BLB8A | Urban | LV Transformer SP3599-H BLB8A - Planned | 58.2545 | 229 | 13340.2805 | 0.01343 | 5.8646e-05
2013-05-03 | 299320 | BLB8B | Urban | LV Transformer SP3599-H BLB8A - Planned | 2.18 | 229 | 499.22 | 0.00050258 | 2.1947e-06
2013-05-03 | 299321 | GTN15A | Rural short | LV Transformer SP7068 GTN15A - Planned | 1.03 | 35 | 36.05 | 0.00010392 | 2.969e-06
2013-05-03 | 299322 | CMV9A | Urban | LV Transformer SC5801-I CMV9A - Planned | 3.15 | 300 | 945 | 0.00095135 | 3.1712e-06
2013-05-03 | 299323 | CPC3B | Urban | LV Transformer SC633933 CPC3B - Planned | 0.99 | 39 | 38.61 | 3.8869e-05 | 9.9665e-07
2013-05-04 | 299333 | TWG10 | Urban | LV Transformer SP762338 TWG10 - Planned | 11.14 | 298 | 3319.72 | 0.0033419 | 1.1214e-05
2013-05-04 | 299335 | BNH2B | Rural short | LV Transformer SP12456-A BNH2B - Planned | 3.96 | 309 | 1223.64 | 0.0035274 | 1.1416e-05
2013-05-04 | 299341 | BLH13B | Rural short | Feeder BLH13B - Planned | 17 | 395 | 6715 | 0.019358 | 4.9006e-05
2013-05-04 | 299349 | BHD35A | Rural short | Feeder BHD35A - Planned | 61.8 | 575 | 35535 | 0.10244 | 0.00017815
2013-05-04 | 299351 | ENSNSD23 | Urban | LV Transformer SC828694 ENSNSD23 - Planned | 1 | 2050 | 2050 | 0.0020637 | 1.0067e-06
2013-05-04 | 299356 | RCN4A | Urban | LV Transformer SP4191-K RCN4A - Planned | 12.04 | 230 | 2769.2 | 0.0027877 | 1.212e-05
2013-05-04 | 299357 | CLRSRD17 | Urban | LV Transformer SP4583-H CLRSRD17 - Planned | 6.9 | 487 | 3360.3 | 0.0033828 | 6.9461e-06
2013-05-05 | 299345 | ABTQPT95 | Urban | Feeder ABTQPT95 - Planned | 2 | 644 | 1288 | 0.0012966 | 2.0133e-06
2013-05-05 | 299350 | GVN15A | Urban | LV Transformer SC778349-A GVN15A - Planned | 1 | 307 | 307 | 0.00030905 | 1.0067e-06
2013-05-05 | 299352 | AGE10 | Urban | LV Transformer SC4908-H AGE10 - Planned | 17.98 | 275 | 4944.5 | 0.0049775 | 1.81e-05
2013-05-05 | 299353 | MLT19A | Urban | LV Transformer SP1582-L MLT19A - Planned | 9.8132 | 553 | 5426.6996 | 0.0054629 | 9.8786e-06
2013-05-05 | 299355 | BDT6 | Urban | LV Transformer SP57895-B BDT6 - Planned | 0.825 | 137 | 113.025 | 0.00011378 | 8.305e-07
2013-05-05 | 299358 | BVL13A | Urban | LV Transformer SP3794-C BVL13A - Planned | 8.52 | 244 | 2078.88 | 0.0020927 | 8.5768e-06
2013-05-06 | 299374 | WHO1 | Rural short | Feeder WHO1 - Planned | 14 | 92 | 1288 | 0.0037132 | 4.0361e-05
2013-05-06 | 299376 | GYN6A | Rural short | LV Transformer SP4276-B GYN6A - Planned | 2.25 | 165 | 371.25 | 0.0010703 | 6.4866e-06
2013-05-06 | 299377 | MBG2 | Rural short | Feeder MBG2 - Planned | 9.5 | 187 | 1776.5 | 0.0051216 | 2.7388e-05
2013-05-06 | 299378 | GGR1 | Rural short | LV Transformer SP3008-C GGR1 - Planned | 1 | 269 | 269 | 0.00077551 | 2.8829e-06
2013-05-06 | 299379 | BLH12A | Rural short | Feeder BLH12A - Planned | 109 | 154 | 16786 | 0.048393 | 0.00031424
2013-05-06 | 299381 | BDT1 | Rural short | Feeder BDT1 - Planned | 5 | 396 | 1980 | 0.0057082 | 1.4415e-05
2013-05-06 | 299382 | CMY1 | Rural short | Feeder CMY1 - Planned | 67 | 182 | 12194 | 0.035155 | 0.00019316
2013-05-06 | 299383 | KCY2 | Rural short | Feeder KCY2 - Planned | 68.25 | 385 | 26276.25 | 0.075753 | 0.00019676
2013-05-06 | 299385 | NBR6 | Rural short | LV Transformer SP2102-A NBR6 - Planned | 7.15 | 100 | 715 | 0.0020613 | 2.0613e-05
2013-05-06 | 299386 | CLM4A | Urban | LV Transformer SP2832-A CLM4A - Planned | 15.755 | 313 | 4931.315 | 0.0049641 | 1.586e-05
2013-05-06 | 299387 | CLM7 | Urban | LV Transformer SP163869 CLM7 - Planned | 14.265 | 132 | 1882.98 | 0.0018955 | 1.436e-05
2013-05-06 | 299388 | SPO47A | Urban | LV Transformer SP3198-G SPO47A - Planned | 18.095 | 238 | 4306.61 | 0.0043352 | 1.8215e-05
2013-05-06 | 299389 | HWL10A | Urban | LV Transformer SP5156-H HWL10A - Planned | 5.68 | 174 | 988.32 | 0.00099489 | 5.7178e-06
2013-05-06 | 299390 | LTA2 | Urban | LV Transformer SP3262-J LTA4B - Planned | 11.12 | 270 | 3002.4 | 0.0030224 | 1.1194e-05
2013-05-06 | 299390 | LTA4B | Urban | LV Transformer SP3262-J LTA4B - Planned | 10.3 | 270 | 2781 | 0.0027995 | 1.0368e-05
2013-05-06 | 299391 | SGT7 | Urban | LV Transformer SP1612-J SGT7 - Planned | 6.44 | 254 | 1635.76 | 0.0016466 | 6.4828e-06
2013-05-06 | 299392 | HDA11A | Urban | LV Transformer SP9502-F HDA11A - Planned | 88 | 221 | 19448 | 0.019577 | 8.8585e-05
2013-05-06 | 299393 | WED6A | Urban | LV Transformer SP54272-C WED6A - Planned | 8.5 | 340 | 2890 | 0.0029092 | 8.5565e-06
2013-05-06 | 299446 | TWG17 | Urban | LV Transformer SP758641 TWG17 - Planned | 13.76 | 262 | 3605.12 | 0.0036291 | 1.3851e-05
2013-05-06 | 299510 | WSO16A | Urban | LV Transformer SG3875-G WSO16A - Planned | 0.99 | 2939 | 2909.61 | 0.002929 | 9.9658e-07
2013-05-07 | 299413 | BHD23A | Rural short | LV Transformer SP1082632 BHD23A - Planned | 1 | 210 | 210 | 0.00060542 | 2.883e-06
2013-05-07 | 299414 | IPL3 | Rural short | Feeder IPL3 - Planned | 92 | 90 | 8280 | 0.023871 | 0.00026523
2013-05-07 | 299416 | NBR4 | Rural short | Feeder NBR4 - Planned | 48.02 | 302 | 14502.04 | 0.041809 | 0.00013844
2013-05-07 | 299433 | MLY3 | Rural short | Feeder MLY3 - Planned | 69.07 | 412 | 28456.84 | 0.08204 | 0.00019913
2013-05-07 | 299434 | AMR2 | Rural short | Feeder AMR2 - Planned | 20.66 | 253 | 5226.98 | 0.015069 | 5.9562e-05
2013-05-07 | 299437 | TGW3 | Rural short | Feeder TGW3 - Planned | 10.01 | 346 | 3463.46 | 0.009985 | 2.8858e-05
2013-05-07 | 299438 | RLB16A | Rural short | Feeder RLB16A - Planned | 6.25 | 465 | 2906.25 | 0.0083786 | 1.8019e-05
2013-05-07 | 299439 | RPN7A | Rural short | Feeder RPN7A - Planned | 4 | 390 | 1560 | 0.0044974 | 1.1532e-05
2013-05-07 | 299441 | BHD35A | Rural short | Feeder BHD35A - Planned | 46.4 | 672 | 31180.8 | 0.089893 | 0.00013377
2013-05-07 | 299443 | CFD2A | Urban | LV Transformer SC4894-H CFD2A - Planned | 10.26 | 319 | 3272.94 | 0.0032945 | 1.0328e-05
2013-05-07 | 299443 | HDA3A | Urban | LV Transformer SC4894-H CFD2A - Planned | 1.475 | 319 | 470.525 | 0.00047363 | 1.4847e-06
2013-05-07 | 299444 | GAP8A | Urban | LV Transformer SC4873-H GAP8A - Planned | 29.925 | 225 | 6733.125 | 0.0067775 | 3.0122e-05
2013-05-07 | 299445 | AGE10 | Urban | LV Transformer SG1014-Q AGE10 - Planned | 26.865 | 224 | 6017.76 | 0.0060574 | 2.7042e-05
2013-05-07 | 299447 | TRG2A | Urban | LV Transformer SC4879-G TRG2A - Planned | 52.3125 | 229 | 11979.5625 | 0.012059 | 5.2657e-05
2013-05-07 | 299448 | COR23A | Rural short | LV Transformer SP6752-C COR23A - Planned | 3 | 147 | 441 | 0.0012714 | 8.6489e-06
2013-05-07 | 299449 | AMR2 | Rural short | LV Transformer SP6757-C AMR2 - Planned | 6.3 | 51 | 321.3 | 0.0009263 | 1.8163e-05
2013-05-07 | 299450 | SPO32A | Urban | LV Transformer SP1972-I SPO32A - Planned | 18.3 | 273 | 4995.9 | 0.0050288 | 1.8421e-05
2013-05-07 | 299451 | KRA7 | Urban | LV Transformer SP17443-H KRA7 - Planned | 101.0055 | 222 | 22423.221 | 0.022571 | 0.00010167
2013-05-07 | 299452 | BLH12B | Urban | LV Transformer SP738519 BLH12B - Planned | 0.74 | 270 | 199.8 | 0.00020112 | 7.4488e-07
2013-05-07 | 299453 | CBW11 | Rural short | LV Transformer SP13232-D CBW11 - Planned | 8.05 | 139 | 1118.95 | 0.0032259 | 2.3208e-05
2013-05-07 | 299454 | SGT9 | Urban | LV Transformer SP12599-E SGT9 - Planned | 8.99 | 118 | 1060.82 | 0.0010678 | 9.0493e-06
2013-05-07 | 299455 | SGT7 | Urban | LV Transformer SP1919-K SGT7 - Planned | 6.75 | 188 | 1269 | 0.0012774 | 6.7945e-06
2013-05-07 | 299456 | SGT4 | Urban | LV Transformer SP2593-I SGT4 - Planned | 9.75 | 233 | 2271.75 | 0.0022867 | 9.8143e-06
2013-05-07 | 299457 | HDA11A | Urban | LV Transformer SP1804-I HDA3A - Planned | 49.045 | 393 | 19274.685 | 0.019402 | 4.9368e-05
2013-05-07 | 299457 | HDA3A | Urban | LV Transformer SP1804-I HDA3A - Planned | 2.88 | 393 | 1131.84 | 0.0011393 | 2.899e-06
2013-05-07 | 299458 | TGP9A | Rural short | LV Transformer SP1454-N TGP9A - Planned | 11.275 | 241 | 2717.275 | 0.0078338 | 3.2505e-05
2013-05-07 | 299459 | RLB11B | Urban | LV Transformer SP5577-D RLB11B - Planned | 7.93 | 44 | 348.92 | 0.00035122 | 7.9823e-06
2013-05-07 | 299460 | BBS9 | Urban | LV Transformer SC3900-F BBS9 - Planned | 10.083 | 125 | 1260.375 | 0.0012687 | 1.0149e-05
2013-05-07 | 299462 | BLBNFM6 | Urban | LV Transformer SP557-M BLBNFM6 - Planned | 42.24 | 218 | 9208.32 | 0.009269 | 4.2519e-05
2013-05-07 | 299463 | RLB16A | Rural short | LV Transformer SP9033-B RLB16A - Planned | 0.99 | 12.5 | 21.15 | 6.0975e-05 | 2.8541e-06
2013-05-07 | 299464 | RLB11B | Urban | LV Transformer SC2509-D RLB11B - Planned | 7.17 | 48 | 344.16 | 0.00034643 | 7.2173e-06
2013-05-07 | 299465 | CPD1 | Rural short | LV Transformer SP8471-A CPD1 - Planned | 4 | 239 | 956 | 0.0027561 | 1.1532e-05
2013-05-07 | 299466 | MWMRBK11 | Rural short | LV Transformer SP4866-D MWMRBK11 - Planned | 6.06 | 367 | 2224.02 | 0.0064118 | 1.7471e-05
2013-05-08 | 299493 | THL4 | Rural short | LV Transformer SP3444-A THL4 - Planned | 7.04 | 197 | 1386.88 | 0.0039982 | 2.0296e-05
2013-05-08 | 299495 | COR23A | Rural short | Feeder COR23A - Planned | 41 | 228 | 9348 | 0.026949 | 0.0001182
2013-05-08 | 299496 | TBV2 | Rural short | LV Transformer SP4649-D TBV2 - Planned | 1 | 78 | 78 | 0.00022487 | 2.8829e-06
2013-05-08 | 299497 | CVL7A | Rural short | LV Transformer SP7408-B CVL7A - Planned | 0.5 | 275 | 137.5 | 0.0003964 | 1.4414e-06
2013-05-08 | 299498 | COR23A | Rural short | Feeder COR23A - Planned | 41 | 228 | 9348 | 0.026949 | 0.0001182
2013-05-08 | 299499 | THL3 | Rural short | Feeder THL3 - Planned | 6.424 | 356 | 2286.944 | 0.006593 | 1.852e-05
2013-05-08 | 299501 | GYM2A | Rural short | Feeder GYM2A - Planned | 21 | 374 | 7854 | 0.022642 | 6.0541e-05
2013-05-08 | 299503 | TBV4 | Rural short | Feeder TBV4 - Planned | 51.5 | 306 | 15759 | 0.045431 | 0.00014847
2013-05-08 | 299504 | TGW3 | Rural short | LV Transformer SP11277-B TGW3 - Planned | 3 | 343 | 1029 | 0.0029665 | 8.6487e-06
2013-05-08 | 299505 | MLY3 | Rural short | Feeder MLY3 - Planned | 45 | 362 | 16290 | 0.046962 | 0.00012973
2013-05-08 | 299506 | GYN3A | Rural short | Feeder GYN3A - Planned | 132.74 | 351 | 46591.74 | 0.13432 | 0.00038267
2013-05-08 | 299507 | SARSHW9 | Urban | LV Transformer SP3343-F SARSHW9 - Planned | 9.64 | 258 | 2487.12 | 0.0025035 | 9.7035e-06
2013-05-08 | 299508 | AGE4B | Urban | LV Transformer SP2077-L AGE4B - Planned | 10.34 | 219 | 2264.46 | 0.0022794 | 1.0408e-05
2013-05-08 | 299509 | KMR22A | Urban | LV Transformer SP2780-L KMR22A - Planned | 4.005 | 179 | 716.895 | 0.00072162 | 4.0314e-06
2013-05-08 | 299511 | SFD2A | Urban | LV Transformer SC6191-D SFD2A - Planned | 5.2 | 168 | 873.6 | 0.00087936 | 5.2343e-06
2013-05-08 | 299512 | KLG11A | Urban | LV Transformer SP2619-G KLG11A - Planned | 27.44 | 251 | 6887.44 | 0.0069328 | 2.7621e-05
2013-05-08 | 299513 | SGT9 | Urban | LV Transformer SC22019-F SGT9 - Planned | 6.18 | 93 | 574.74 | 0.00057853 | 6.2207e-06
2013-05-08 | 299514 | SBH11 | Urban | LV Transformer SP2610-G SBH11 - Planned | 6.52 | 298 | 1942.96 | 0.0019558 | 6.563e-06
2013-05-08 | 299515 | RLB16A | Rural short | Feeder RLB16A - Planned | 4 | 460 | 1840 | 0.0053045 | 1.1532e-05
2013-05-08 | 299516 | CBW13 | Rural short | LV Transformer SP8135-D CBW13 - Planned | 2.97 | 375 | 1113.75 | 0.0032108 | 8.5622e-06
2013-05-08 | 299517 | SGT9 | Urban | LV Transformer SP2713-H ZMR7A - Planned | 1.79 | 195 | 349.05 | 0.00035135 | 1.8018e-06
2013-05-08 | 299517 | ZMR7A | Urban | LV Transformer SP2713-H ZMR7A - Planned | 6 | 195 | 1170 | 0.0011777 | 6.0395e-06
2013-05-08 | 299518 | CBW11 | Rural short | LV Transformer SP16597-D CBW11 - Planned | 55 | 253 | 13915 | 0.040115 | 0.00015856
2013-05-08 | 299519 | ALY5 | Urban | LV Transformer SP31667-D ALY5 - Planned | 19.825 | 390 | 7731.75 | 0.0077827 | 1.9956e-05
2013-05-08 | 299520 | RCN2A | Urban | LV Transformer SC4570-J RCN2A - Planned | 17.1192 | 256 | 4382.5152 | 0.0044114 | 1.7232e-05
2013-05-08 | 299521 | LGL15A | Urban | LV Transformer SP3302-B LGL15A - Planned | 25.415 | 296 | 7522.84 | 0.0075724 | 2.5582e-05
2013-05-08 | 299522 | KSN7 | Rural short | LV Transformer SP2949-C KSN7 - Planned | 12 | 161 | 1932 | 0.0055697 | 3.4595e-05
2013-05-08 | 299523 | TRP2 | Rural short | LV Transformer SP1643-C TRP2 - Planned | 6 | 138 | 828 | 0.002387 | 1.7297e-05
2013-05-08 | 299524 | CPD1 | Rural short | LV Transformer SP2364-C CPD1 - Planned | 2.01 | 55 | 110.55 | 0.0003187 | 5.7946e-06
2013-05-08 | 299525 | CPD1 | Rural short | LV Transformer SP1276-D CPD1 - Planned | 4 | 33 | 132 | 0.00038054 | 1.1532e-05
2013-05-08 | 299526 | RPN8 | Rural short | LV Transformer SP3774-D RPN8 - Planned | 29.97 | 252 | 7552.44 | 0.021773 | 8.64e-05
2013-05-08 | 299527 | LTA4B | Urban | LV Transformer SP4421-H LTA4B - Planned | 48.1 | 371 | 17845.1 | 0.017963 | 4.8417e-05
2013-05-08 | 299528 | TWG14A | Urban | LV Transformer SP3285-F TWG14A - Planned | 12.285 | 351 | 4312.035 | 0.0043404 | 1.2366e-05
2013-05-08 | 299529 | CRB25A | Rural short | LV Transformer SP5677-F CRB25A - Planned | 7.5 | 508 | 3810 | 0.010984 | 2.1622e-05
2013-05-08 | 299530 | MDR2A | Urban | LV Transformer SP2007-H MDR2A - Planned | 73.95 | 512 | 37862.4 | 0.038112 | 7.4437e-05
2013-05-08 | 299531 | CRB25A | Rural short | LV Transformer SP760627 CRB25A - Planned | 4.83 | 462 | 2231.46 | 0.0064331 | 1.3924e-05
2013-05-08 | 299541 | NRG15A | Urban | LV Transformer SC950-I NRG15A - Planned | 59.77 | 591 | 35324.07 | 0.035557 | 6.0164e-05
2013-05-08 | 299541 | NRG2A | Urban | LV Transformer SC950-I NRG15A - Planned | 1.18 | 591 | 697.38 | 0.00070198 | 1.1878e-06
2013-05-08 | 299547 | SPD5A | Urban | LV Transformer SG120-L SPD5A - Planned | 22.2 | 189 | 4195.8 | 0.0042234 | 2.2346e-05
2013-05-08 | 299773 | UPC1 | Rural short | LV Transformer SP562747 UPC1 - Planned | 14.5 | 281 | 4074.5 | 0.011746 | 4.1802e-05
2013-05-09 | 299553 | RWD2 | Rural short | LV Transformer SP12128-C RWD2 - Planned | 3 | 71 | 213 | 0.00061404 | 8.6484e-06
2013-05-09 | 299554 | PWC6 | Rural short | LV Transformer SP3970-B PWC6 - Planned | 18 | 134 | 2412 | 0.0069533 | 5.1891e-05
2013-05-09 | 299574 | CRB25A | Rural short | Feeder CRB25A - Planned | 7 | 245 | 1715 | 0.004944 | 2.018e-05
2013-05-09 | 299575 | TBV4 | Rural short | LV Transformer SP17756-B TBV4 - Planned | 7 | 190 | 1330 | 0.0038341 | 2.018e-05
2013-05-09 | 299576 | COR22A | Rural short | Feeder COR22A - Planned | 4.5 | 290 | 1305 | 0.0037621 | 1.2973e-05
2013-05-09 | 299577 | THL3 | Rural short | LV Transformer SP2248-D THL3 - Planned | 2.01 | 171 | 343.71 | 0.00099085 | 5.7945e-06
2013-05-09 | 299578 | MLY3 | Rural short | Feeder MLY3 - Planned | 34 | 337 | 11458 | 0.033031 | 9.8016e-05
2013-05-09 | 299579 | NBR5A | Rural short | LV Transformer SP4566-B NBR5A - Planned | 1 | 212 | 212 | 0.00061116 | 2.8828e-06
2013-05-09 | 299581 | KCY5 | Rural short | Feeder KCY5 - Planned | 116 | 363 | 42108 | 0.12139 | 0.00033441
2013-05-09 | 299582 | KCY5 | Rural short | Feeder KCY5 - Planned | 58.33 | 355 | 20707.15 | 0.059695 | 0.00016815
2013-05-09 | 299583 | GYM9B | Rural short | Feeder GYM9B - Planned | 33.8 | 369 | 12472.2 | 0.035955 | 9.7439e-05
2013-05-09 | 299594 | SPC2B | Rural short | Feeder SPC2B - Planned | 3.4 | 405 | 1377 | 0.0039696 | 9.8016e-06
2013-05-09 | 299595 | RLB16A | Rural short | Feeder RLB16A - Planned | 4 | 498 | 1992 | 0.0057426 | 1.1531e-05
2013-05-09 | 299596 | KBR3A | Rural short | Feeder KBR3A - Planned | 16 | 349 | 5584 | 0.016098 | 4.6125e-05
2013-05-09 | 299597 | JBB3A | Rural short | LV Transformer SP11888-C JBB3A - Planned | 8.075 | 225 | 1816.875 | 0.0052377 | 2.3279e-05
2013-05-09 | 299598 | IDY1A | Urban | LV Transformer SP183-R SHW4 - Planned | 14.4 | 141 | 2030.4 | 0.0020438 | 1.4495e-05
2013-05-09 | 299598 | SHW4 | Urban | LV Transformer SP183-R SHW4 - Planned | 4.05 | 141 | 571.05 | 0.00057481 | 4.0767e-06
2013-05-09 | 299599 | WCL17A | Urban | LV Transformer SP32254-E WCL17A - Planned | 3 | 296 | 888 | 0.00089385 | 3.0198e-06
2013-05-09 | 299600 | NMK17A | Urban | LV Transformer SP6182-F NMK17A - Planned | 27.55 | 303 | 8347.65 | 0.0084026 | 2.7731e-05
2013-05-09 | 299601 | MGL5 | Urban | LV Transformer SC122-Q MGL5 - Planned | 8.16 | 235 | 1917.6 | 0.0019302 | 8.2137e-06
2013-05-09 | 299602 | NBR2 | Urban | LV Transformer SP3025-A NBR2 - Planned | 29.2 | 157 | 4584.4 | 0.0046146 | 2.9392e-05
2013-05-09 | 299603 | SPO51A | Urban | LV Transformer SP2246-G SPO51A - Planned | 30.38 | 401 | 12182.38 | 0.012263 | 3.058e-05
2013-05-09 | 299604 | CRBTHP14 | Urban | LV Transformer SP1408-L CRBTHP14 - Planned | 32.8 | 395 | 12956 | 0.013041 | 3.3016e-05
2013-05-09 | 299606 | LTA4B | Urban | LV Transformer SP13061-G LTA4B - Planned | 15.9 | 380 | 6042 | 0.0060818 | 1.6005e-05
2013-05-09 | 299607 | LTA4B | Urban | LV Transformer SP1336-M LTA4B - Planned | 3.225 | 194 | 625.65 | 0.00062977 | 3.2462e-06
2013-05-09 | 299608 | ZMR7A | Urban | LV Transformer SC4370-H ZMR7A - Planned | 15.12 | 218 | 3296.16 | 0.0033179 | 1.522e-05
2013-05-09 | 299609 | FIS13A | Urban | LV Transformer SC740082 FIS13A - Planned | 1.1 | 218 | 239.8 | 0.00024138 | 1.1072e-06
2013-05-09 | 299610 | CHL11A | Rural short | LV Transformer SP3827-E CHL11A - Planned | 10.05 | 270 | 2713.5 | 0.0078225 | 2.8972e-05
2013-05-09 | 299611 | RPN2A | Urban | LV Transformer SP3558-D RPN2A - Planned | 4.74 | 223 | 1057.02 | 0.001064 | 4.7712e-06
2013-05-09 | 299612 | HDA11A | Urban | LV Transformer SP9502-F HDA11A - Planned | 57.26 | 440 | 25194.4 | 0.02536 | 5.7637e-05
2013-05-09 | 299615 | NRG16A | Rural short | Feeder NRG16A - Planned | 43 | 475 | 20425 | 0.058881 | 0.00012396
2013-05-09 | 299616 | HDA11A | Urban | LV Transformer SP3613-G HDA3A - Planned | 10 | 298 | 2980 | 0.0029996 | 1.0066e-05
2013-05-09 | 299616 | HDA3A | Urban | LV Transformer SP3613-G HDA3A - Planned | 45.725 | 298 | 13626.05 | 0.013716 | 4.6026e-05
2013-05-09 | 299617 | SMF1B | Rural short | Feeder SMF1B - Planned | 28 | 670 | 16200 | 0.046702 | 8.0719e-05
2013-05-09 | 299774 | PWC5 | Rural short | LV Transformer SP5249-A PWC5 - Planned | 10.01 | 330 | 3303.3 | 0.0095228 | 2.8857e-05
2013-05-10 | 299658 | CPD2A | Rural short | Feeder CPD2A - Planned | 11.5 | 246 | 2829 | 0.008156 | 3.3154e-05
2013-05-10 | 299659 | KSN7 | Rural short | Feeder KSN7 - Planned | 46.98 | 280 | 13154.4 | 0.037924 | 0.00013544
2013-05-10 | 299673 | TGW3 | Rural short | Feeder TGW3 - Planned | 13.81 | 270 | 3728.7 | 0.01075 | 3.9814e-05
2013-05-10 | 299676 | UPC1 | Rural short | Feeder UPC1 - Planned | 15 | 540 | 8100 | 0.023352 | 4.3245e-05
2013-05-10 | 299678 | GBN4 | Rural short | LV Transformer SP6482-C GBN4 - Planned | 2 | 104 | 208 | 0.00059966 | 5.766e-06
2013-05-10 | 299680 | KSN5 | Rural short | LV Transformer SP10502-C KSN5 - Planned | 13.44 | 289 | 3884.16 | 0.011198 | 3.8747e-05
2013-05-10 | 299681 | SMR6A | Urban | LV Transformer SC5273-H SMR6A - Planned | 24.15 | 229 | 5530.35 | 0.0055665 | 2.4308e-05
2013-05-10 | 299682 | AGE5B | Urban | LV Transformer SP4179-K AGE5B - Planned | 1.99 | 309 | 614.91 | 0.00061893 | 2.003e-06
2013-05-10 | 299683 | GLY2A | Urban | LV Transformer SC618948 GLY2A - Planned | 11.91 | 155 | 1846.05 | 0.0018581 | 1.1988e-05
2013-05-10 | 299684 | MGL5 | Urban | LV Transformer SC3853-G MGL5 - Planned | 23.24 | 249 | 5786.76 | 0.0058246 | 2.3392e-05
2013-05-10 | 299685 | GLY2A | Urban | LV Transformer SC618948 GLY2A - Planned | 8.1 | 110 | 891 | 0.00089683 | 8.153e-06
2013-05-10 | 299686 | NVL12 | Urban | LV Transformer SP2540-D NVL12 - Planned | 8.16 | 325 | 2652 | 0.0026694 | 8.2134e-06
2013-05-10 | 299686 | NVL5 | Rural short | LV Transformer SP2540-D NVL12 - Planned | 0.76 | 325 | 247 | 0.0007121 | 2.1911e-06
2013-05-10 | 299687 | CLM6 | Urban | LV Transformer SP15276-A CLM6 - Planned | 27.37 | 250 | 6842.5 | 0.0068873 | 2.7549e-05
2013-05-10 | 299688 | TCB2 | Rural short | LV Transformer SP3540-A TCB2 - Planned | 7.92 | 191 | 1512.72 | 0.0043611 | 2.2833e-05
2013-05-10 | 299689 | CLM5 | Urban | LV Transformer SP15275-A CLM5 - Planned | 4.68 | 328 | 1535.04 | 0.0015451 | 4.7106e-06
2013-05-10 | 299690 | SPO51A | Urban | LV Transformer SP1435-H SPO51A - Planned | 11.31 | 277 | 3132.87 | 0.0031534 | 1.1384e-05
2013-05-10 | 299691 | SPO32A | Urban | LV Transformer SP3350-E SPO32A - Planned | 35.75 | 198 | 7078.5 | 0.0071248 | 3.5984e-05
2013-05-10 | 299691 | SPO41A | Urban | LV Transformer SP3350-E SPO32A - Planned | 11.925 | 198 | 2361.15 | 0.0023766 | 1.2003e-05
2013-05-10 | 299692 | MGP12A | Rural short | LV Transformer SP563197 MGP12A - Planned | 9 | 317 | 2853 | 0.0082251 | 2.5947e-05
2013-05-10 | 299693 | MGP12A | Rural short | LV Transformer SP17445-E MGP12A - Planned | 16 | 220 | 3520 | 0.010148 | 4.6128e-05
2013-05-10 | 299694 | MFD2A | Urban | LV Transformer SP10505-D MFD2A - Planned | 2.85 | 92 | 262.2 | 0.00026392 | 2.8686e-06
2013-05-10 | 299695 | WNM1A | Urban | LV Transformer SP376038 WNM1A - Planned | 3.15 | 198 | 623.7 | 0.00062778 | 3.1706e-06
2013-05-10 | 299696 | TGP8A | Urban | LV Transformer SP3349-J TGP8A - Planned | 6.16 | 125 | 770 | 0.00077504 | 6.2003e-06
2013-05-10 | 299697 | SGT7 | Urban | LV Transformer SP783-L SGT7 - Planned | 33.02 | 381 | 12580.62 | 0.012663 | 3.3236e-05
2013-05-10 | 299698 | ALY9 | Urban | LV Transformer SP5265-H ALY9 - Planned | 9.3 | 267 | 2483.1 | 0.0024993 | 9.3609e-06
2013-05-10 | 299699 | MRK6 | Urban | LV Transformer SP4052-I MRK6 - Planned | 4.76 | 178 | 847.28 | 0.00085282 | 4.7911e-06
2013-05-10 | 299700 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 22.9362 | 303 | 6949.6686 | 0.0069951 | 2.3086e-05
2013-05-10 | 299701 | HPE13A | Urban | LV Transformer SP743797 HPE13A - Planned | 16.055 | 103 | 1653.665 | 0.0016645 | 1.616e-05
2013-05-10 | 299702 | BKD3A | Urban | LV Transformer SP2948-B BKD3A - Planned | 17.23 | 247 | 4255.81 | 0.0042837 | 1.7343e-05
2013-05-10 | 299704 | RPN3A | Urban | LV Transformer SP3541-E RPN3A - Planned | 3.92 | 338 | 1324.96 | 0.0013336 | 3.9457e-06
2013-05-10 | 299705 | MCW7 | Rural short | LV Transformer SP11846-D MCW7 - Planned | 29.12 | 51 | 1485.12 | 0.0042816 | 8.3952e-05
2013-05-10 | 299706 | MCW7 | Rural short | LV Transformer SP13119-A MCW7 - Planned | 29.1 | 123 | 3579.3 | 0.010319 | 8.3895e-05
2013-05-10 | 299707 | THL3 | Rural short | LV Transformer SP16807-B THL3 - Planned | 4 | 39 | 156 | 0.00044975 | 1.1532e-05
2013-05-10 | 299775 | SMF2A | Rural short | Feeder SMF2A - Planned | 30 | 348 | 10440 | 0.030098 | 8.6489e-05
2013-05-11 | 299776 | FDS3 | Rural short | LV Transformer SP9864-D FDS3 - Planned | 1 | 210 | 210 | 0.00060544 | 2.8831e-06
2013-05-11 | 299800 | CLRSRD17 | Urban | LV Transformer SP4583-H CLRSRD17 - Planned | 6.9 | 250 | 1725 | 0.0017362 | 6.945e-06
2013-05-12 | 299778 | WFD3A | Rural short | Feeder WFD3A - Planned | 5 | 55 | 275 | 0.00079286 | 1.4416e-05
2013-05-12 | 299781 | LGL15A | Urban | Feeder LGL15A - Planned | 44 | 441 | 19404 | 0.01953 | 4.4286e-05
2013-05-12 | 299793 | MTG11A | Urban | LV Transformer SC4139-G MTG11A - Planned | 8.265 | 270 | 2231.55 | 0.002246 | 8.3187e-06
2013-05-12 | 299794 | TWG17 | Urban | LV Transformer SP3047-L TWG17 - Planned | 10.64 | 152 | 1617.28 | 0.0016278 | 1.0709e-05
2013-05-12 | 299795 | BMG3B | Urban | LV Transformer SC5055-J MLT3B - Planned | 3.1629 | 557 | 1761.7353 | 0.0017732 | 3.1834e-06
2013-05-12 | 299795 | MLT3B | Urban | LV Transformer SC5055-J MLT3B - Planned | 0.8631 | 557 | 480.7467 | 0.00048387 | 8.687e-07
2013-05-12 | 299796 | HTL2A | Urban | LV Transformer SP6578-E HTL2A - Planned | 4.95 | 215 | 1064.25 | 0.0010712 | 4.9821e-06
2013-05-12 | 299797 | MRE2 | Urban | LV Transformer SC736421 MRE2 - Planned | 15.5 | 387 | 5998.5 | 0.0060375 | 1.5601e-05
2013-05-12 | 299798 | NRA1A | Rural short | LV Transformer SP7089-E NRA1A - Planned | 2.94 | 298 | 876.12 | 0.002526 | 8.4764e-06
2013-05-12 | 299799 | MTG11A | Urban | LV Transformer SC4139-G MTG11A - Planned | 33.495 | 265 | 8876.175 | 0.0089338 | 3.3713e-05
2013-05-13 | 299813 | KBR6A | Rural short | LV Transformer SP1757-D KBR6A - Planned | 1 | 43 | 43 | 0.00012405 | 2.885e-06
2013-05-13 | 299815 | KLG16A | Rural short | LV Transformer SP2233-G KLG16A - Planned | 55 | 263 | 14465 | 0.041731 | 0.00015867
2013-05-13 | 299816 | GTN12A | Rural short | LV Transformer SP2854-C GTN12A - Planned | 7.04 | 320 | 2252.8 | 0.0064993 | 2.031e-05
2013-05-13 | 299817 | WSE3A | Rural short | LV Transformer SP2182-H WSE3A - Planned | 11 | 272 | 2992 | 0.0086318 | 3.1735e-05
2013-05-13 | 299818 | RLB16A | Rural short | Feeder RLB16A - Planned | 4 | 192 | 768 | 0.0022157 | 1.154e-05
2013-05-13 | 299819 | WNM4 | Urban | LV Transformer SC734493 WNM4 - Planned | 1 | 488 | 488 | 0.00049104 | 1.0062e-06
2013-05-13 | 299820 | PWC6 | Rural short | Feeder PWC6 - Planned | 67.26 | 217 | 14595.42 | 0.042107 | 0.00019404
2013-05-13 | 299821 | EMD2 | Rural short | Feeder EMD2 - Planned | 68.85 | 210 | 14458.5 | 0.041712 | 0.00019863
2013-05-13 | 299822 | WMR1 | Rural short | Feeder WMR1 - Planned | 1.5 | 384 | 576 | 0.0016617 | 4.3275e-06
2013-05-13 | 299825 | NMK17A | Urban | LV Transformer SP6182-F NMK17A - Planned | 2.9 | 67 | 194.3 | 0.00019551 | 2.9181e-06
2013-05-13 | 299826 | GYN3A | Rural short | LV Transformer SP1171-E GYN3A - Planned | 4.5 | 219 | 985.5 | 0.0028431 | 1.2982e-05
2013-05-13 | 299827 | PWC4 | Rural short | LV Transformer SP175-A PWC4 - Planned | 17 | 164 | 2788 | 0.0080433 | 4.9044e-05
2013-05-13 | 299828 | GYS5A | Rural short | LV Transformer SP540-C GYS5A - Planned | 3 | 202 | 606 | 0.0017483 | 8.6549e-06
2013-05-13 | 299829 | BLN2B | Urban | LV Transformer SP5024-E BLN2B - Planned | 10.95 | 237 | 2595.15 | 0.0026113 | 1.1018e-05
2013-05-13 | 299830 | IPL1 | Rural short | LV Transformer SP1477-E IPL1 - Planned | 5 | 282 | 1410 | 0.0040678 | 1.4425e-05
2013-05-13 | 299831 | KLG16A | Rural short | LV Transformer SP7034-D KLG16A - Planned | 4.8 | 243 | 1166.4 | 0.003365 | 1.3848e-05
2013-05-13 | 299832 | SGT22A | Urban | LV Transformer SP3161-H SGT22A - Planned | 6.37 | 212 | 1350.44 | 0.0013589 | 6.4097e-06
2013-05-13 | 299833 | NRA13A | Rural short | LV Transformer SP107663 NRA13A - Planned | 6.76 | 301 | 2034.76 | 0.0058702 | 1.9502e-05
2013-05-13 | 299834 | ALY5 | Urban | LV Transformer SP3159-I ALY5 - Planned | 23.01 | 243 | 5591.43 | 0.0056263 | 2.3153e-05
2013-05-13 | 299835 | HPK2 | Urban | LV Transformer SC3041-I HPK2 - Planned | 1.745 | 274 | 478.13 | 0.00048111 | 1.7559e-06
2013-05-13 | 299836 | HPK3A | Urban | LV Transformer SP1593-I HPK3A - Planned | 2.8 | 215 | 602 | 0.00060575 | 2.8174e-06
2013-05-13 | 299836 | SBY6 | Urban | LV Transformer SP1593-I HPK3A - Planned | 2.88 | 215 | 619.2 | 0.00062306 | 2.8979e-06
2013-05-13 | 299837 | TRP2 | Rural short | LV Transformer SP1841-C TRP2 - Planned | 2.01 | 160 | 321.6 | 0.00092781 | 5.7988e-06
2013-05-13 | 299838 | RPN8 | Rural short | LV Transformer SP3419-A RPN8 - Planned | 3.24 | 270 | 874.8 | 0.0025238 | 9.3473e-06
2013-05-13 | 299840 | KSN1 | Urban | LV Transformer SP7003-H KSN1 - Planned | 11.88 | 150 | 1782 | 0.0017931 | 1.1954e-05
2013-05-13 | 300201 | LBH3A | Rural short | LV Transformer SP741997 LBH3A - Planned | 18.33 | 367 | 6727.11 | 0.019408 | 5.2881e-05
2013-05-13 | 300664 | MGP15A | Rural short | Feeder MGP15A - Planned | 32.5 | 90 | 2925 | 0.0084385 | 9.3761e-05
2013-05-14 | 299878 | KCY2 | Rural short | LV Transformer SP6161-F KCY2 - Planned | 2 | 219 | 438 | 0.0012637 | 5.7702e-06
2013-05-14 | 299893 | AMR3 | Rural short | LV Transformer SP5615-B AMR3 - Planned | 3 | 136 | 408 | 0.0011771 | 8.6554e-06
2013-05-14 | 299894 | PWC6 | Rural short | Feeder PWC6 - Planned | 36.96 | 289 | 10681.44 | 0.030817 | 0.00010663
2013-05-14 | 299895 | COR22A | Rural short | Feeder COR22A - Planned | 2.34 | 173 | 404.82 | 0.001168 | 6.7512e-06
2013-05-14 | 299896 | BMT1 | Rural short | LV Transformer SP6551-B BMT1 - Planned | 9 | 83 | 747 | 0.0021552 | 2.5966e-05
2013-05-14 | 299897 | PWC2 | Rural short | LV Transformer SG181-A PWC2 - Planned | 1 | 67 | 67 | 0.0001933 | 2.8851e-06
2013-05-14 | 299898 | NRA13A | Rural short | LV Transformer SP4984-F NRA13A - Planned | 2 | 475 | 950 | 0.0027409 | 5.7702e-06
2013-05-14 | 299899 | PPE16A | Rural short | Feeder PPE16A - Planned | 16 | 400 | 6400 | 0.018465 | 4.6162e-05
2013-05-14 | 299900 | CMV14 | Urban | LV Transformer SP504-N CMV14 - Planned | 13.78 | 470 | 6476.6 | 0.0065166 | 1.3865e-05
2013-05-14 | 299901 | BKD2B | Urban | LV Transformer SP5414-D BKD2B - Planned | 1.15 | 141 | 162.15 | 0.00016315 | 1.1571e-06
2013-05-14 | 299902 | GLY4A | Urban | LV Transformer SP3765-G GLY4A - Planned | 12.4 | 257 | 3186.8 | 0.0032065 | 1.2477e-05
2013-05-14 | 299903 | TWG17 | Urban | LV Transformer SP2217-L TWG17 - Planned | 11.28 | 194 | 2188.32 | 0.0022018 | 1.135e-05
2013-05-14 | 299905 | KMR27A | Urban | LV Transformer SP412-P KMR27A - Planned | 8.97 | 185 | 1659.45 | 0.0016697 | 9.0254e-06
2013-05-14 | 299906 | KWH1 | Rural short | LV Transformer SP7474-C KWH1 - Planned | 9 | 234 | 2106 | 0.0060761 | 2.5966e-05
2013-05-14 | 299907 | MLT24A | Urban | LV Transformer SP1403-M MLT24A - Planned | 9.84 | 440 | 4329.6 | 0.0043564 | 9.9008e-06
2013-05-14 | 299908 | AMR2 | Rural short | LV Transformer SP2323-C AMR2 - Planned | 1 | 83 | 83 | 0.00023946 | 2.8851e-06
2013-05-14 | 299909 | CLD30A | Urban | LV Transformer SP4014-A CLD30A - Planned | 6.12 | 332 | 2031.84 | 0.0020444 | 6.1578e-06
2013-05-14 | 299910 | SPOSSS15 | Urban | LV Transformer SG610-J SPOSSS15 - Planned | 9.4354 | 27 | 254.7558 | 0.00025633 | 9.4937e-06
2013-05-14 | 299911 | SPO32A | Urban | LV Transformer SP761826 SPO32A - Planned | 17.2 | 132 | 2270.4 | 0.0022844 | 1.7306e-05
2013-05-14 | 299912 | MLY1 | Rural short | LV Transformer SP6596-B MLY1 - Planned | 15.12 | 355 | 5367.6 | 0.015486 | 4.3623e-05
2013-05-14 | 299913 | SGT7 | Urban | LV Transformer SP783-L SGT7 - Planned | 10.24 | 226 | 2314.24 | 0.0023285 | 1.0303e-05
2013-05-14 | 299914 | KLG11A | Urban | LV Transformer SP2619-G KLG11A - Planned | 37.24 | 233 | 8676.92 | 0.0087305 | 3.747e-05
2013-05-14 | 299914 | KLG14A | Urban | LV Transformer SP2619-G KLG11A - Planned | 1.85 | 233 | 431.05 | 0.00043371 | 1.8614e-06
2013-05-14 | 299915 | RCN2A | Urban | LV Transformer SC6376-I RCN2A - Planned | 13.12 | 268 | 3516.16 | 0.0035379 | 1.3201e-05
2013-05-14 | 299916 | CPL25A | Urban | LV Transformer SP10723-G CPL25A - Planned | 4.12 | 214 | 881.68 | 0.00088713 | 4.1455e-06
2013-05-14 | 299917 | ARG5A | Urban | LV Transformer SP2368-L ARG5A - Planned | 44.4114 | 312 | 13856.3568 | 0.013942 | 4.4686e-05
2013-05-14 | 299918 | HPK8A | Urban | LV Transformer SP2864-G HPK8A - Planned | 22.815 | 137 | 3125.655 | 0.003145 | 2.2956e-05
2013-05-14 | 299919 | BVL3A | Urban | LV Transformer SP811208 BVL3A - Planned | 18.13 | 285 | 5167.05 | 0.005199 | 1.8242e-05
2013-05-14 | 299920 | RCN6A | Urban | LV Transformer SC1400984 RCN6A - Planned | 37 | 48 | 1776 | 0.001787 | 3.7229e-05
2013-05-14 | 299921 | CPC1A | Urban | LV Transformer SC109-K CPC1A - Planned | 1 | 20 | 20 | 2.0124e-05 | 1.0062e-06
2013-05-14 | 299922 | BVL15A | Urban | LV Transformer SC425271 BVL15A - Planned | 1.015 | 32 | 32.48 | 3.2681e-05 | 1.0213e-06
2013-05-14 | 299923 | BVL15A | Urban | LV Transformer SP4184-D BVL15A - Planned | 40 | 184 | 7360 | 0.0074055 | 4.0247e-05
2013-05-14 | 299924 | WHO1 | Rural short | Feeder WHO1 - Planned | 58.95 | 547 | 32245.65 | 0.093033 | 0.00017008
2013-05-14 | 299925 | KSN7 | Rural short | Feeder KSN7 - Planned | 8 | 553 | 4424 | 0.012764 | 2.3081e-05
2013-05-15 | 299953 | WSE3A | Rural short | LV Transformer SP4988-G WSE3A - Planned | 4 | 185 | 740 | 0.0021351 | 1.1541e-05
2013-05-15 | 299954 | TGW1 | Rural short | Feeder TGW1 - Planned | 3.01 | 307 | 924.07 | 0.0026662 | 8.6848e-06
2013-05-15 | 299973 | BNH6A | Rural short | Feeder BNH6A - Planned | 29 | 397 | 11513 | 0.033219 | 8.3674e-05
2013-05-15 | 299993 | MFN15A | Rural short | Feeder MFN15A - Planned | 12.3 | 375 | 4612.5 | 0.013309 | 3.549e-05
2013-05-15 | 299994 | VPT12A | Urban | LV Transformer SC900-C VPT12A - Planned | 4 | 487 | 1948 | 0.0019599 | 4.0245e-06
2013-05-15 | 299995 | AMR1 | Rural short | Feeder AMR1 - Planned | 34.5 | 191 | 6589.5 | 0.019013 | 9.9544e-05
2013-05-15 | 299996 | BHD35A | Rural short | Feeder BHD35A - Planned | 20.4 | 599 | 12219.6 | 0.035258 | 5.8861e-05
2013-05-15 | 299997 | TWG17 | Urban | LV Transformer SP1767-L TWG17 - Planned | 16.5662 | 173 | 2865.9526 | 0.0028835 | 1.6668e-05
2013-05-15 | 299998 | TWG18 | Urban | LV Transformer SP112-T TWG18 - Planned | 7.36 | 229 | 1685.44 | 0.0016958 | 7.4051e-06
2013-05-15 | 299999 | TWG11 | Urban | LV Transformer SP397-N TWG11 - Planned | 1.32 | 353 | 465.96 | 0.00046881 | 1.3281e-06
2013-05-15 | 300000 | AGE4B | Urban | LV Transformer SG1086-N AGE4B - Planned | 3.22 | 272 | 875.84 | 0.00088121 | 3.2397e-06
2013-05-15 | 300001 | AHL4A | Urban | LV Transformer SP797450 GLY4A - Planned | 2.19 | 222 | 486.18 | 0.00048916 | 2.2034e-06
2013-05-15 | 300001 | GLY4A | Urban | LV Transformer SP797450 GLY4A - Planned | 7.63 | 222 | 1693.86 | 0.0017042 | 7.6767e-06
2013-05-15 | 300002 | SHW4 | Urban | LV Transformer SP1426-P SHW4 - Planned | 11.73 | 291 | 3413.43 | 0.0034343 | 1.1802e-05
2013-05-15 | 300003 | GYN3A | Rural short | LV Transformer SP1155-E GYN3A - Planned | 3 | 272 | 816 | 0.0023544 | 8.656e-06
2013-05-15 | 300004 | TCB1 | Rural short | LV Transformer SP5484-A TCB1 - Planned | 31.9044 | 469 | 14963.1636 | 0.043174 | 9.2055e-05
2013-05-15 | 300005 | NBR5A | Rural short | LV Transformer SP4031-A NBR5A - Planned | 21.56 | 225 | 4851 | 0.013997 | 6.2208e-05
2013-05-15 | 300006 | MLY3 | Rural short | LV Transformer SP4063-A MLY3 - Planned | 5.2429 | 90 | 471.861 | 0.0013615 | 1.5127e-05
2013-05-15 | 300007 | NVL3 | Rural short | LV Transformer SC1992-C NVL3 - Planned | 16.86 | 232 | 3911.52 | 0.011286 | 4.8647e-05
2013-05-15 | 300008 | GBN4 | Rural short | LV Transformer SP5530-B GBN4 - Planned | 0.99 | 20 | 19.8 | 5.7129e-05 | 2.8565e-06
2013-05-15 | 300009 | GYS5A | Rural short | LV Transformer SP6531-C GYS5A - Planned | 2.01 | 11 | 22.11 | 6.3795e-05 | 5.7995e-06
2013-05-15 | 300010 | CRBTHP14 | Urban | LV Transformer SP5742-C CRBTHP14 - Planned | 122 | 465 | 56730 | 0.057078 | 0.00012275
2013-05-15 | 300011 | SPO47A | Urban | LV Transformer SP3198-G SPO47A - Planned | 59.455 | 378 | 22473.99 | 0.022612 | 5.9819e-05
2013-05-15 | 300012 | WFD2B | Rural short | LV Transformer SP5074-G WFD2B - Planned | 5 | 242 | 1210 | 0.0034912 | 1.4427e-05
2013-05-15 | 300013 | CBW11 | Rural short | LV Transformer SP3423-B CBW11 - Planned | 6.02 | 330 | 1986.6 | 0.005732 | 1.737e-05
2013-05-15 | 300014 | SGT22A | Urban | LV Transformer SP3763-F SGT22A - Planned | 20.46 | 245 | 5012.7 | 0.0050434 | 2.0585e-05
2013-05-15 | 300014 | SGT7 | Urban | LV Transformer SP3763-F SGT22A - Planned | 3.71 | 245 | 908.95 | 0.00091452 | 3.7327e-06
2013-05-15 | 300015 | MRE8 | Urban | LV Transformer SP3430-H MRE8 - Planned | 4.575 | 228 | 1043.1 | 0.0010495 | 4.603e-06
2013-05-15 | 300016 | SBH11 | Urban | LV Transformer SP1597-G SBH11 - Planned | 1.92 | 176 | 337.92 | 0.00033999 | 1.9318e-06
2013-05-15 | 300017 | BBS6 | Urban | LV Transformer SP4161-G BBS6 - Planned | 18.4 | 209 | 3845.6 | 0.0038692 | 1.8513e-05
2013-05-15 | 300018 | BLB4A | Urban | LV Transformer SP1933-H BLB4A - Planned | 41.975 | 304 | 12760.4 | 0.012839 | 4.2232e-05
2013-05-15 | 300019 | ARG5A | Urban | LV Transformer SP4957-F ARG5A - Planned | 10.1582 | 374 | 3799.1668 | 0.0038224 | 1.022e-05
2013-05-15 | 300020 | HPK3A | Urban | LV Transformer SP2322-J HPK3A - Planned | 12.16 | 482 | 5861.12 | 0.005897 | 1.2234e-05
2013-05-15 | 300021 | BLBNFM6 | Urban | LV Transformer SP557-M BLBNFM6 - Planned | 33.54 | 210 | 7043.4 | 0.0070866 | 3.3745e-05
2013-05-15 | 300022 | CPK13 | Rural short | LV Transformer SP5291-C CPK13 - Planned | 7.6 | 275 | 2090 | 0.0060303 | 2.1928e-05
2013-05-15 | 300023 | GTN13A | Rural short | LV Transformer SP3932-B GTN13A - Planned | 3.72 | 333 | 1238.76 | 0.0035742 | 1.0733e-05
2013-05-15 | 300024 | KSN2A | Rural short | LV Transformer SC1452114 KSN2A - Planned | 6.04 | 43 | 259.72 | 0.00074938 | 1.7427e-05
2013-05-15 | 300025 | RST9A | Urban | LV Transformer SP4908-C RST9A - Planned | 0.8466 | 30 | 25.398 | 2.5554e-05 | 8.5179e-07
2013-05-15 | 300026 | KSN2A | Rural short | LV Transformer SC1452114 KSN2A - Planned | 5 | 53 | 265 | 0.00076461 | 1.4427e-05
2013-05-15 | 300027 | BVL10A | Urban | LV Transformer SP3056-D BVL10A - Planned | 18.72 | 149 | 2789.28 | 0.0028064 | 1.8835e-05
2013-05-15 | 300029 | AHD4A | Urban | LV Transformer SP2723-A AHD4A - Planned | 1.08 | 88 | 95.04 | 9.5622e-05 | 1.0866e-06
2013-05-15 | 300057 | HIS5A | Urban | LV Transformer SP658019 HIS5A - Planned | 2 | 30 | 60 | 6.0368e-05 | 2.0123e-06
2013-05-15 | 300061 | AHD4A | Urban | LV Transformer SP2723-A AHD4A - Planned | 1.08 | 76 | 82.08 | 8.2583e-05 | 1.0866e-06
2013-05-16 | 300033 | NBR5A | Rural short | Feeder NBR5A - Planned | 64.12 | 53 | 3398.36 | 0.0098062 | 0.00018502
2013-05-16 | 300036 | NRA12A | Urban | LV Transformer SP4658-F NRA12A - Planned | 1 | 90 | 90 | 9.0546e-05 | 1.0061e-06
2013-05-16 | 300037 | MSV2 | Rural short | LV Transformer SP3032-C MSV2 - Planned | 4 | 149 | 596 | 0.0017198 | 1.1542e-05
2013-05-16 | 300039 | KBR6A | Rural short | LV Transformer SP2185-E KBR6A - Planned | 8.5 | 134 | 1139 | 0.0032867 | 2.4527e-05
2013-05-16 | 300040 | THL2 | Rural short | LV Transformer SP849-B THL2 - Planned | 1.34 | 250 | 335 | 0.00096667 | 3.8667e-06
2013-05-16 | 300043 | TGW3 | Rural short | Feeder TGW3 - Planned | 30.885 | 329 | 10161.165 | 0.029321 | 8.9121e-05
2013-05-16 | 300046 | KBN5A | Rural short | Feeder KBN5A - Planned | 31 | 172 | 5332 | 0.015386 | 8.9453e-05
2013-05-16 | 300047 | SMF6A | Rural short | LV Transformer SP319-O SMF6A - Planned | 27 | 270 | 7290 | 0.021036 | 7.7911e-05
2013-05-16 | 300048 | BNH1B | Rural short | Feeder BNH1B - Planned | 34 | 403 | 13702 | 0.039538 | 9.811e-05
2013-05-16 | 300049 | MTB17A | Rural short | Feeder MTB17A - Planned | 18.9 | 417 | 7881.3 | 0.022742 | 5.4537e-05
2013-05-16 | 300050 | GYM7A | Rural short | Feeder GYM7A - Planned | 22 | 465 | 10230 | 0.029519 | 6.3483e-05
2013-05-16 | 300051 | GYN7A | Rural short | Feeder GYN7A - Planned | 20 | 192 | 3840 | 0.011081 | 5.7712e-05
2013-05-16 | 300052 | PWC5 | Rural short | LV Transformer SP2469-A PWC5 - Planned | 1.92 | 320 | 614.4 | 0.0017729 | 5.5403e-06
2013-05-16 | 300055 | BDT5 | Rural short | Feeder BDT5 - Planned | 7 | 444 | 3108 | 0.0089684 | 2.0199e-05
2013-05-16 | 300056 | BHD35A | Rural short | Feeder BHD35A - Planned | 22 | 601 | 13222 | 0.038153 | 6.3483e-05
2013-05-16 | 300058 | JDL7 | Urban | LV Transformer SC3813-J SMR1A - Planned | 1.04 | 284 | 295.36 | 0.00029715 | 1.0463e-06
2013-05-16 | 300058 | SMR1A | Urban | LV Transformer SC3813-J SMR1A - Planned | 10.515 | 284 | 2986.26 | 0.0030044 | 1.0579e-05
2013-05-16 | 300059 | SMF5A | Rural short | LV Transformer SP1604-L SMF5A - Planned | 6.6 | 113 | 745.8 | 0.0021521 | 1.9045e-05
2013-05-16 | 300060 | NVL9 | Rural short | LV Transformer SP6735-B NVL9 - Planned | 8.37 | 252 | 2109.24 | 0.0060864 | 2.4152e-05
2013-05-16 | 300062 | CLM5 | Urban | LV Transformer SP5222-A CLM5 - Planned | 13.2 | 136 | 1795.2 | 0.0018061 | 1.328e-05
2013-05-16 | 300063 | GYN6A | Rural short | LV Transformer SP394-E GYN6A - Planned | 3 | 112 | 336 | 0.00096955 | 8.6567e-06
2013-05-16 | 300064 | TCB1 | Rural short | LV Transformer SP5484-A TCB1 - Planned | 22.295 | 387 | 8628.165 | 0.024897 | 6.4334e-05
2013-05-16 | 300065 | MLB4A | Urban | LV Transformer SP14099-A MLB4A - Planned | 5.55 | 433 | 2403.15 | 0.0024177 | 5.5837e-06
2013-05-16 | 300066 | BHD35A | Rural short | LV Transformer SP15814-D BHD35A - Planned | 9.45 | 382 | 3609.9 | 0.010417 | 2.7269e-05
2013-05-16 | 300067 | SGT4 | Urban | LV Transformer SP2593-I SGT4 - Planned | 7.8 | 228 | 1778.4 | 0.0017892 | 7.8474e-06
2013-05-16 | 300068 | GLY2A | Urban | LV Transformer SC618948 GLY2A - Planned | 13.5 | 366 | 4941 | 0.004971 | 1.3582e-05
2013-05-16 | 300069 | BHL1A | Urban | LV Transformer SP3329-G BHL1A - Planned | 18.17 | 297 | 5396.49 | 0.0054293 | 1.828e-05
2013-05-16 | 300070 | KLG11A | Urban | LV Transformer SP8277-D KLG11A - Planned | 15.375 | 241 | 3705.375 | 0.0037279 | 1.5468e-05
2013-05-16 | 300071 | ZMR6A | Urban | LV Transformer SP1978-G ZMR6A - Planned | 14.1 | 341 | 4808.1 | 0.0048373 | 1.4186e-05
2013-05-16 | 300072 | CFD1A | Urban | LV Transformer SG1983-I CFD8A - Planned | 16.26 | 328 | 5333.28 | 0.0053657 | 1.6359e-05
2013-05-16 | 300072 | CFD8A | Urban | LV Transformer SG1983-I CFD8A - Planned | 1.725 | 328 | 565.8 | 0.00056924 | 1.7355e-06
2013-05-16 | 300073 | EMP21A | Rural short | LV Transformer SP5587-I EMP21A - Planned | 8.31 | 180 | 1495.8 | 0.0043162 | 2.3979e-05
2013-05-16 | 300074 | HPK3A | Urban | LV Transformer SP3312-I HPK3A - Planned | 3.01 | 264 | 794.64 | 0.00079946 | 3.0283e-06
2013-05-16 | 300075 | BKD13A | Urban | LV Transformer SP3649-B BKD13A - Planned | 3.92 | 318 | 1246.56 | 0.0012541 | 3.9438e-06
2013-05-16 | 300076 | WRG12A | Urban | LV Transformer SP2653-J WRG12A - Planned | 8.645 | 220 | 1901.9 | 0.0019134 | 8.6975e-06
2013-05-16 | 300077 | BVL5A | Urban | LV Transformer SP8589-B BVL5A - Planned | 9.205 | 202 | 1859.41 | 0.0018707 | 9.2609e-06
2013-05-16 | 300078 | SPF12B | Urban | LV Transformer SC1376934 - Planned | 26.75 | 287 | 7677.25 | 0.0077239 | 2.6912e-05
2013-05-16 | 300079 | BVL15A | Urban | LV Transformer SP8426-C BVL15A - Planned | 6.27 | 247 | 1548.69 | 0.0015581 | 6.3081e-06
2013-05-16 | 300080 | RPN2A | Urban | LV Transformer SP8468-B RPN2A - Planned | 17.6 | 108 | 1900.8 | 0.0019123 | 1.7707e-05
2013-05-17 | 300094 | MCN3 | Urban | LV Transformer SP4364-D MCN3 - Planned | 2 | 230 | 460 | 0.00046277 | 2.012e-06
2013-05-17 | 300097 | TGW1 | Rural short | Feeder TGW1 - Planned | 19.99 | 232 | 4637.68 | 0.013383 | 5.7687e-05
2013-05-17 | 300098 | ACR5 | Rural short | Feeder ACR5 - Planned | 65.5 | 305 | 19977.5 | 0.057651 | 0.00018902
2013-05-17 | 300100 | THL3 | Rural short | LV Transformer SP2273-E THL3 - Planned | 3 | 319 | 957 | 0.0027617 | 8.6574e-06
2013-05-17 | 300101 | CBW11 | Rural short | LV Transformer SP8355-D CBW11 - Planned | 12 | 354 | 4248 | 0.012259 | 3.463e-05
2013-05-17 | 300103 | NBR4 | Rural short | Feeder NBR4 - Planned | 89.88 | 352 | 31637.76 | 0.0913 | 0.00025938
2013-05-17 | 300104 | PWC4 | Rural short | Feeder PWC4 - Planned | 37.94 | 333 | 12634.02 | 0.036459 | 0.00010949
2013-05-17 | 300105 | NBR12A | Rural short | LV Transformer SP550641 NBR12A - Planned | 1 | 330 | 330 | 0.00095232 | 2.8858e-06
2013-05-17 | 300106 | COR23A | Rural short | Feeder COR23A - Planned | 115.12 | 228 | 26247.36 | 0.075745 | 0.00033221
2013-05-17 | 300109 | BRD13A | Urban | LV Transformer SP2057956 BRD13A - Planned | 5.99 | 341 | 2042.59 | 0.0020549 | 6.026e-06
2013-05-17 | 300110 | SMR12A | Urban | LV Transformer SC4878-H SMR12A - Planned | 28.8 | 140 | 4032 | 0.0040563 | 2.8973e-05
2013-05-17 | 300111 | COR23A | Rural short | LV Transformer SP691-B COR23A - Planned | 1 | 39 | 39 | 0.00011255 | 2.8858e-06
2013-05-17 | 300112 | TCB1 | Rural short | LV Transformer SP3899-B TCB1 - Planned | 3.85 | 200 | 770 | 0.0022221 | 1.111e-05
2013-05-17 | 300113 | PWC6 | Rural short | LV Transformer SP6656-A PWC6 - Planned | 39.33 | 219 | 8613.27 | 0.024856 | 0.0001135
2013-05-17 | 300114 | MTB13A | Rural short | LV Transformer SP1794-F MTB13A - Planned | 3.04 | 152 | 462.08 | 0.0013335 | 8.7728e-06
2013-05-17 | 300115 | MMC19B | Urban | LV Transformer SP3471-D MMC19B - Planned | 20.1058 | 303 | 6092.0574 | 0.0061287 | 2.0227e-05
2013-05-17 | 300116 | SPO51A | Urban | LV Transformer SP2246-G SPO51A - Planned | 8.56 | 257 | 2199.92 | 0.0022132 | 8.6115e-06
2013-05-17 | 300117 | CRB24B | Urban | LV Transformer SC741-G CRB24B - Planned | 24.2671 | 342 | 8299.3482 | 0.0083493 | 2.4413e-05
2013-05-17 | 300118 | SPO8A | Urban | LV Transformer SP2211-E SPO8A - Planned | 6.93 | 245 | 1697.85 | 0.0017081 | 6.9717e-06
2013-05-17 | 300119 | LTA3A | Urban | LV Transformer SP13061-G LTA3A - Planned | 6.89 | 284 | 1956.76 | 0.0019685 | 6.9315e-06
2013-05-17 | 300120 | BHL4A | Urban | LV Transformer SP5771-I BHL4A - Planned | 18.29 | 261 | 4773.69 | 0.0048024 | 1.84e-05
2013-05-17 | 300121 | SGT7 | Urban | LV Transformer SP227-K SGT7 - Planned | 18.43 | 430 | 7924.9 | 0.0079726 | 1.8541e-05
2013-05-17 | 300122 | NRA13A | Rural short | LV Transformer SP3707-C NRA13A - Planned | 42.72 | 237 | 10124.64 | 0.029218 | 0.00012328
2013-05-17 | 300123 | EMP21A | Rural short | LV Transformer SP4236-K EMP21A - Planned | 22.315 | 197 | 4396.055 | 0.012686 | 6.4397e-05
2013-05-17 | 300124 | TMH5A | Urban | LV Transformer SP3167-B TMH5A - Planned | 19.38 | 315 | 6104.7 | 0.0061414 | 1.9497e-05
2013-05-17 | 300125 | CPB8 | Rural short | LV Transformer SP4923-I CPB8 - Planned | 2.025 | 368 | 745.2 | 0.0021505 | 5.8438e-06
2013-05-17 | 300126 | BLB8B | Urban | LV Transformer SP493027 BLB8B - Planned | 23.605 | 202 | 4768.21 | 0.0047969 | 2.3747e-05
2013-05-17 | 300127 | HPK3A | Urban | LV Transformer SP3312-I HPK3A - Planned | 10.39 | 291 | 3023.49 | 0.0030417 | 1.0453e-05
2013-05-17 | 300127 | HPK8A | Urban | LV Transformer SP3312-I HPK3A - Planned | 1.89 | 291 | 549.99 | 0.0005533 | 1.9014e-06
2013-05-17 | 300128 | CPD1 | Rural short | LV Transformer SP2364-C CPD1 - Planned | 2.01 | 235 | 472.35 | 0.0013631 | 5.8005e-06
2013-05-18 | 300133 | MDH9A | Urban | Feeder MDH9A - Planned | 3 | 330 | 990 | 0.00099593 | 3.018e-06
2013-05-18 | 300134 | WHO1 | Rural short | Feeder WHO1 - Planned | 2 | 275 | 550 | 0.0015872 | 5.7718e-06
2013-05-18 | 300184 | NVL27A | Urban | LV Transformer SP6831-B NVL27A - Planned | 2.8 | 21 | 58.8 | 5.9152e-05 | 2.8168e-06
2013-05-18 | 300185 | HWL3A | Urban | LV Transformer SP15871-C HWL3A - Planned | 23.6425 | 370 | 8747.725 | 0.0088001 | 2.3784e-05
2013-05-18 | 300187 | QEN10 | Urban | LV Transformer SG1219-J QEN10 - Planned | 1 | 227 | 227 | 0.00022836 | 1.006e-06
2013-05-18 | 300188 | RPN8 | Rural short | LV Transformer SP3666-D RPN8 - Planned | 43.92 | 363 | 15942.96 | 0.04601 | 0.00012675
2013-05-19 | 300176 | RPN7A | Rural short | Feeder RPN7A - Planned | 6 | 142 | 852 | 0.0024589 | 1.7316e-05
2013-05-19 | 300181 | AHL4A | Urban | LV Transformer SP714257 AHL4A - Planned | 2 | 346 | 692 | 0.00069613 | 2.0119e-06
2013-05-19 | 300186 | MTG11A | Urban | LV Transformer SC4139-G MTG11A - Planned | 35.01 | 205 | 7177.05 | 0.0072199 | 3.5219e-05
2013-05-19 | 300189 | NRA2A | Urban | LV Transformer SP3678-D NRA2A - Planned | 1 | 482 | 482 | 0.00048488 | 1.006e-06
2013-05-19 | 300190 | MLT19A | Urban | LV Transformer SC22134-G MLT19A - Planned | 1.9266 | 75 | 144.495 | 0.00014536 | 1.9381e-06
2013-05-19 | 300191 | TRG3 | Urban | LV Transformer SP1624-H TRG3 - Planned | 2.055 | 264 | 542.52 | 0.00054576 | 2.0673e-06
2013-05-19 | 300192 | AHL4A | Urban | LV Transformer SC797579 AHL4A - Planned | 5.03 | 331 | 1664.93 | 0.0016749 | 5.06e-06
2013-05-19 | 300193 | STL3 | Urban | LV Transformer SG828-P STL3 - Planned | 0.9 | 35 | 31.5 | 3.1688e-05 | 9.0537e-07
2013-05-19 | 300194 | LTA16A | Urban | LV Transformer SP5200-M LTA16A - Planned | 6 | 184 | 1104 | 0.0011106 | 6.0358e-06
2013-05-19 | 300195 | MTG11A | Urban | LV Transformer SC5584-E MTG11A - Planned | 35.01 | 205 | 7177.05 | 0.0072199 | 3.5219e-05
2013-05-19 | 300196 | ARG5A | Urban | LV Transformer SG2618-K ARG5A - Planned | 21.51 | 310 | 6668.1 | 0.0067079 | 2.1638e-05
2013-05-19 | 300196 | SBK11 | Urban | LV Transformer SG2618-K ARG5A - Planned | 5.16 | 310 | 1599.6 | 0.0016091 | 5.1908e-06
2013-05-20 | 300213 | MTB17A | Rural short | Feeder MTB17A - Planned | 15 | 294 | 4410 | 0.012729 | 4.3296e-05
2013-05-20 | 300214 | KCY5 | Rural short | Feeder KCY5 - Planned | 159.66 | 255 | 40713.3 | 0.11751 | 0.00046084
2013-05-20 | 300215 | THL4 | Rural short | LV Transformer SP2218-C THL4 - Planned | 2.01 | 323 | 649.23 | 0.0018739 | 5.8017e-06
2013-05-20 | 300216 | SMF6A | Rural short | Feeder SMF6A - Planned | 17.8 | 371 | 6603.8 | 0.019061 | 5.1378e-05
2013-05-20 | 300217 | GGR5 | Rural short | Feeder GGR5 - Planned | 46.51 | 263 | 12232.13 | 0.035307 | 0.00013425
2013-05-20 | 300218 | GGR5 | Rural short | Feeder GGR5 - Planned | 16.52 | 85 | 1404.2 | 0.0040531 | 4.7683e-05
2013-05-20 | 300221 | RBA43A | Rural short | Feeder RBA43A - Planned | 32.5 | 585 | 19012.5 | 0.054878 | 9.3808e-05
2013-05-20 | 300222 | GYN7A | Rural short | LV Transformer SP3211-B GYN7A - Planned | 47 | 433 | 20351 | 0.058741 | 0.00013566
2013-05-20 | 300223 | WMD11A | Rural short | LV Transformer SP5322-A WMD11A - Planned | 6.6 | 95 | 627 | 0.0018098 | 1.905e-05
2013-05-20 | 300224 | AHD4A | Urban | LV Transformer SP2723-A AHD4A - Planned | 1.095 | 510 | 558.45 | 0.00056172 | 1.1014e-06
2013-05-20 | 300225 | GBN4 | Rural short | LV Transformer SP6782-C GBN4 - Planned | 3 | 265 | 795 | 0.0022947 | 8.6592e-06
2013-05-20 | 300226 | CLD30A | Urban | LV Transformer SP1289-B CLD30A - Planned | 36.7 | 209 | 7670.3 | 0.0077152 | 3.6915e-05
2013-05-20 | 300227 | RBA43A | Rural short | LV Transformer SP467144 RBA43A - Planned | 0.94 | 439 | 412.66 | 0.0011911 | 2.7132e-06
2013-05-20 | 300228 | BHL5A | Urban | LV Transformer SP1357-I BHL5A - Planned | 15.99 | 255 | 4077.45 | 0.0041013 | 1.6084e-05
2013-05-20 | 300228 | SGT24A | Urban | LV Transformer SP1357-I BHL5A - Planned | 1.22 | 255 | 311.1 | 0.00031292 | 1.2271e-06
2013-05-20 | 300229 | NRA13A | Rural short | LV Transformer SP5024-G NRA13A - Planned | 32.2 | 308 | 9917.6 | 0.028626 | 9.2942e-05
2013-05-20 | 300230 | ARG5A | Urban | LV Transformer SP2624-K ARG5A - Planned | 21.26 | 335 | 7122.1 | 0.0071638 | 2.1385e-05
2013-05-20 | 300230 | SBK11 | Urban | LV Transformer SP2624-K ARG5A - Planned | 1.935 | 335 | 648.225 | 0.00065202 | 1.9463e-06
2013-05-20 | 300641 | TGW1 | Rural short | LV Transformer SP1874-D TGW1 - Planned | 3 | 277 | 831 | 0.0023986 | 8.6592e-06
2013-05-21 | 300254 | BNH6A | Rural short | LV Transformer SP4421-D BNH6A - Planned | 3 | 99 | 297 | 0.00085751 | 8.6617e-06
2013-05-21 | 300255 | GGR5 | Rural short | Feeder GGR5 - Planned | 14 | 111 | 1554 | 0.0044868 | 4.0421e-05
2013-05-21 | 300256 | KBR2A | Rural short | Feeder KBR2A - Planned | 3 | 155 | 465 | 0.0013426 | 8.6617e-06
2013-05-21 | 300259 | GYM9B | Rural short | Feeder GYM9B - Planned | 20 | 333 | 6660 | 0.019229 | 5.7745e-05
2013-05-21 | 300260 | YDA5A | Rural short | Feeder YDA5A - Planned | 36.469 | 342 | 12472.398 | 0.036011 | 0.00010529
2013-05-21 | 300261 | AMR1 | Rural short | Feeder AMR1 - Planned | 31 | 281 | 8711 | 0.025151 | 8.9504e-05
2013-05-21 | 300262 | NBR12A | Rural short | LV Transformer SP4348-A NBR12A - Planned | 7.04 | 227 | 1598.08 | 0.004614 | 2.0326e-05
2013-05-21 | 300263 | CLM3 | Rural short | Feeder CLM3 - Planned | 3 | 114 | 342 | 0.00098743 | 8.6617e-06
2013-05-21 | 300264 | GYS3A | Rural short | LV Transformer SP6824-D GYS3A - Planned | 1 | 30 | 30 | 8.6617e-05 | 2.8872e-06
2013-05-21 | 300265 | CBT4A | Urban | Feeder CBT4A - Planned | 13 | 412 | 5356 | 0.0053867 | 1.3074e-05
2013-05-21 | 300266 | KBN2A | Rural short | Feeder KBN2A - Planned | 17 | 281 | 4777 | 0.013792 | 4.9083e-05
2013-05-21 | 300273 | BLHSTN16 | Rural short | Feeder BLHSTN16 - Planned | 8 | 381 | 3048 | 0.0088003 | 2.3098e-05
2013-05-21 | 300275 | TRP2 | Rural short | Feeder TRP2 - Planned | 40.26 | 276 | 11111.76 | 0.032082 | 0.00011624
2013-05-21 | 300276 | LHM1A | Urban | LV Transformer SC561355 LHM1A - Planned | 83 | 322 | 26726 | 0.026879 | 8.3475e-05
2013-05-21 | 300277 | RBA43A | Rural short | LV Transformer SP9207-E RBA43A - Planned | 16 | 284 | 4544 | 0.01312 | 4.6196e-05
2013-05-21 | 300278 | CRB25A | Rural short | Feeder CRB25A - Planned | 36.66 | 558 | 20456.28 | 0.059062 | 0.00010585
2013-05-21 | 300279 | SHW6 | Urban | LV Transformer SC6390-D SHW6 - Planned | 3.075 | 472 | 1451.4 | 0.0014597 | 3.0926e-06
2013-05-21 | 300280 | SHW6 | Urban | LV Transformer SP1876-K SHW6 - Planned | 14.2511 | 298 | 4246.8278 | 0.0042712 | 1.4333e-05
2013-05-21 | 300281 | GAP4A | Urban | LV Transformer SC1643-J GAP4A - Planned | 5 | 239 | 1195 | 0.0012018 | 5.0286e-06
2013-05-21 | 300282 | GLY3A | Urban | LV Transformer SP4981-K GLY3A - Planned | 7.13 | 316 | 2253.08 | 0.002266 | 7.1708e-06
2013-05-21 | 300283 | AJV1 | Urban | LV Transformer SG4868-H AJV1 - Planned | 3.2 | 230 | 736 | 0.00074022 | 3.2183e-06
2013-05-21 | 300285 | TWG17 | Urban | LV Transformer SP1767-L TWG17 - Planned | 9.4664 | 306 | 2896.7184 | 0.0029133 | 9.5206e-06
2013-05-21 | 300286 | NVL3 | Rural short | LV Transformer SP2352-C NVL3 - Planned | 98.04 | 156 | 15294.24 | 0.044158 | 0.00028306
2013-05-21 | 300287 | BBH8A | Urban | LV Transformer SP4566-H BBH8A - Planned | 17.04 | 311 | 5299.44 | 0.0053298 | 1.7138e-05
2013-05-21 | 300289 | DRD13A | Urban | LV Transformer SP2212-F DRD13A - Planned | 14.55 | 238 | 3462.9 | 0.0034827 | 1.4633e-05
2013-05-21 | 300290 | MRE3 | Urban | LV Transformer SP2794-K MRE8 - Planned | 9.675 | 321 | 3105.675 | 0.0031235 | 9.7304e-06
2013-05-21 | 300290 | MRE8 | Urban | LV Transformer SP2794-K MRE8 - Planned | 10.385 | 321 | 3333.585 | 0.0033527 | 1.0444e-05
2013-05-21 | 300291 | CHL7 | Urban | LV Transformer SP2788-H CHL7 - Planned | 8.395 | 257 | 2157.515 | 0.0021699 | 8.4431e-06
2013-05-21 | 300292 | KSN2A | Rural short | LV Transformer SP99515-D KSN2A - Planned | 5.06 | 36 | 182.16 | 0.00052594 | 1.4609e-05
2013-05-21 | 300293 | RBY3 | Urban | LV Transformer SP1324-E RBY3 - Planned | 1 | 119 | 119 | 0.00011968 | 1.0057e-06
2013-05-21 | 300294 | KSN2A | Rural short | LV Transformer SP4713-B KSN2A - Planned | 6.27 | 58 | 363.66 | 0.00105 | 1.8103e-05
2013-05-21 | 300295 | HPK3A | Urban | LV Transformer SP2322-J HPK3A - Planned | 28.89 | 200 | 5778 | 0.0058111 | 2.9055e-05
2013-05-21 | 300296 | RLA6 | Urban | LV Transformer SP2814-H RLA6 - Planned | 4.02 | 85 | 341.7 | 0.00034366 | 4.043e-06
2013-05-21 | 300297 | IPS5B | Urban | LV Transformer SP3269-B IPS5B - Planned | 0.94 | 375 | 352.5 | 0.00035452 | 9.4538e-07
2013-05-21 | 300298 | BVL5A | Urban | LV Transformer SP3845-D BVL5A - Planned | 26.68 | 178 | 4749.04 | 0.0047762 | 2.6833e-05
2013-05-21 | 300299 | BVL2A | Urban | LV Transformer SP1579-C BVL2A - Planned | 12.0327 | 246 | 2960.0442 | 0.002977 | 1.2102e-05
2013-05-21 | 300411 | RST15A | Urban | LV Transformer SG810699 RST15A - Planned | 3.23 | 365 | 1178.95 | 0.0011857 | 3.2485e-06
2013-05-21 | 300411 | TEX2 | Urban | LV Transformer SG810699 RST15A - Planned | 0.96 | 365 | 350.4 | 0.00035241 | 9.655e-07
2013-05-22 | 300333 | MBG4 | Rural short | LV Transformer SP12901-C MBG4 - Planned | 1 | 27 | 27 | 7.7962e-05 | 2.8875e-06
2013-05-22 | 300335 | BIS2B | Rural short | LV Transformer SP4177-F BIS2B - Planned | 1 | 205 | 205 | 0.00059193 | 2.8875e-06
2013-05-22 | 300353 | THL2 | Rural short | LV Transformer SP10473-A THL2 - Planned | 1 | 232 | 232 | 0.00066989 | 2.8875e-06
2013-05-22 | 300354 | RCN4A | Urban | Feeder RCN4A - Planned | 1 | 252 | 252 | 0.00025343 | 1.0057e-06
2013-05-22 | 300357 | KBR1A | Rural short | Feeder KBR1A - Planned | 4 | 267 | 1068 | 0.0030838 | 1.155e-05
2013-05-22 | 300376 | MLB12A | Rural short | LV Transformer SP145300 MLB12A - Planned | 52 | 60 | 3120 | 0.0090089 | 0.00015015
2013-05-22 | 300377 | BMT2 | Rural short | Feeder BMT2 - Planned | 45.25 | 409 | 18507.25 | 0.053439 | 0.00013066
2013-05-22 | 300378 | KWH1 | Rural short | LV Transformer SP9919-A KWH1 - Planned | 3 | 402 | 1206 | 0.0034823 | 8.6624e-06
2013-05-22 | 300379 | GYN6A | Rural short | Feeder GYN6A - Planned | 100.5 | 267 | 26833.5 | 0.077481 | 0.00029019
2013-05-22 | 300380 | TGW1 | Rural short | Feeder TGW1 - Planned | 7.75 | 334 | 2588.5 | 0.0074742 | 2.2378e-05
2013-05-22 | 300381 | MTB17A | Rural short | Feeder MTB17A - Planned | 13.5 | 440 | 5940 | 0.017152 | 3.8981e-05
2013-05-22 | 300387 | BHL1A | Urban | LV Transformer SC4276-J BHL1A - Planned | 36.08 | 192.5 | 13032.8 | 0.013107 | 3.6284e-05
2013-05-22 | 300388 | KSN14 | Urban | LV Transformer SP4366-D KSN14 - Planned | 2.04 | 137 | 279.48 | 0.00028106 | 2.0516e-06
2013-05-22 | 300389 | CMA10A | Rural short | LV Transformer SC1502451 CMA10A - Planned | 14.04 | 100 | 1404 | 0.004054 | 4.054e-05
2013-05-22 | 300390 | GLY11A | Urban | LV Transformer SC1149-R GLY11A - Planned | 12.805 | 195 | 2496.975 | 0.0025111 | 1.2878e-05
2013-05-22 | 300391 | AHL9A | Urban | LV Transformer SP2461-N AHL9A - Planned | 25.38 | 377 | 9568.26 | 0.0096225 | 2.5524e-05
2013-05-22 | 300392 | TWG11 | Urban | LV Transformer SP740388 TWG11 - Planned | 21.63 | 181 | 3915.03 | 0.0039372 | 2.1753e-05
2013-05-22 | 300394 | MGL5 | Urban | LV Transformer SC691837 MGL5 - Planned | 1.12 | 165 | 184.8 | 0.00018585 | 1.1263e-06
2013-05-22 | 300395 | SMR4A | Urban | LV Transformer SC2071571 SMR4A - Planned | 3.96 | 111 | 439.56 | 0.00044205 | 3.9824e-06
2013-05-22 | 300396 | KWH1 | Rural short | LV Transformer SP2109-A KWH1 - Planned | 17.98 | 377 | 6778.46 | 0.019573 | 5.1917e-05
2013-05-22 | 300397 | TCB1 | Rural short | LV Transformer SP941-D TCB1 - Planned | 5.145 | 185 | 951.825 | 0.0027484 | 1.4856e-05
2013-05-22 | 300398 | BDT5 | Rural short | LV Transformer SP1306-G BDT5 - Planned | 4 | 240 | 960 | 0.002772 | 1.155e-05
2013-05-22 | 300399 | DRD13A | Urban | LV Transformer SP2212-F DRD13A - Planned | 14.55 | 230 | 3346.5 | 0.0033655 | 1.4632e-05
2013-05-22 | 300400 | LTA3A | Urban | LV Transformer SP4421-H LTA3A - Planned | 30.72 | 177 | 5437.44 | 0.0054682 | 3.0894e-05
2013-05-22 | 300401 | NRA13A | Rural short | LV Transformer SP3707-C NRA13A - Planned | 20.62 | 245 | 5051.9 | 0.014587 | 5.954e-05
2013-05-22 | 300402 | SGT22A | Urban | LV Transformer SP3763-F SGT22A - Planned | 0.96 | 148 | 142.08 | 0.00014288 | 9.6544e-07
2013-05-22 | 300403 | BPN35A | Urban | LV Transformer SP3554-D BPN35A - Planned | 4.08 | 290 | 1183.2 | 0.0011899 | 4.1031e-06
2013-05-22 | 300405 | BLB8B | Urban | LV Transformer SP946-J BLB8B - Planned | 23.32 | 256 | 5969.92 | 0.0060037 | 2.3452e-05
2013-05-22 | 300406 | ARG5A | Urban | LV Transformer SP2621-L ARG5A - Planned | 10.23 | 356 | 3641.88 | 0.0036625 | 1.0288e-05
2013-05-22 | 300407 | RCN2A | Urban | LV Transformer SC6376-I RCN2A - Planned | 22.96 | 300 | 6888 | 0.006927 | 2.309e-05
2013-05-22 | 300408 | WRD20A | Urban | LV Transformer SP9424-H WRD20A - Planned | 33.84 | 102 | 3451.68 | 0.0034712 | 3.4032e-05
2013-05-22 | 300409 | GGR1 | Rural short | LV Transformer SP5435-A GGR1 - Planned | 2.01 | 64 | 128.64 | 0.00037145 | 5.8038e-06
2013-05-22 | 300410 | KBR1A | Rural short | LV Transformer SP1068-G KBR1A - Planned | 8 | 279 | 2232 | 0.0064449 | 2.31e-05
2013-05-22 | 300412 | RPN8 | Rural short | LV Transformer SP50081-C RPN8 - Planned | 26.75 | 260 | 6955 | 0.020082 | 7.724e-05
2013-05-22 | 300413 | BVL13A | Urban | LV Transformer SP40242-A BVL3A - Planned | 4.71 | 302 | 1422.42 | 0.0014305 | 4.7367e-06
2013-05-22 | 300413 | BVL3A | Urban | LV Transformer SP40242-A BVL3A - Planned | 14.8 | 302 | 4469.6 | 0.0044949 | 1.4884e-05
2013-05-22 | 300415 | BHD35A | Rural short | LV Transformer SP5636-E BHD35A - Planned | 1.5 | 578 | 867 | 0.0025034 | 4.3312e-06
2013-05-22 | 300416 | MDR33A | Urban | LV Transformer SP3712-F MDR33A - Planned | 13.92 | 94 | 1308.48 | 0.0013159 | 1.3999e-05
2013-05-23 | 300473 | BDB37A | Rural short | Feeder BDB37A - Planned | 3 | 215 | 645 | 0.0018626 | 8.6631e-06
2013-05-23 | 300474 | WSE3A | Rural short | Feeder WSE3A - Planned | 3.8 | 276 | 1048.8 | 0.0030286 | 1.0973e-05
2013-05-23 | 300475 | GGR5 | Rural short | LV Transformer SP14013-B GGR5 - Planned | 36.86 | 360 | 13269.6 | 0.038319 | 0.00010644
2013-05-23 | 300476 | WHO1 | Rural short | Feeder WHO1 - Planned | 12 | 348 | 4176 | 0.012059 | 3.4653e-05
2013-05-23 | 300477 | RLB16A | Rural short | Feeder RLB16A - Planned | 9.8 | 421.625 | 4136.2 | 0.011944 | 2.83e-05
2013-05-23 | 300478 | RLB16A | Rural short | Feeder RLB16A - Planned | 8.8 | 424 | 3731.2 | 0.010775 | 2.5412e-05
2013-05-23 | 300479 | CSE2 | Urban | LV Transformer SP796210 CSE2 - Planned | 89 | 448 | 39872 | 0.040095 | 8.9499e-05
2013-05-23 | 300480 | GBN4 | Rural short | Feeder GBN4 - Planned | 85.4 | 353 | 30146.2 | 0.087053 | 0.00024661
2013-05-23 | 300481 | TWT6B | Rural short | LV Transformer SP15358-B TWT6B - Planned | 52 | 86 | 4472 | 0.012914 | 0.00015016
2013-05-23 | 300482 | GBN4 | Rural short | Feeder GBN4 - Planned | 43.91 | 213 | 9352.83 | 0.027008 | 0.0001268
2013-05-23 | 300494 | SMR15A | Urban | LV Transformer SC22613-E SMR15A - Planned | 40.58 | 170 | 6898.6 | 0.0069373 | 4.0807e-05
2013-05-23 | 300495 | BHD41A | Urban | LV Transformer SC2087118 BHD41A - Planned | 3.25 | 91 | 295.75 | 0.00029741 | 3.2682e-06
2013-05-23 | 300496 | GLY11A | Urban | LV Transformer SG2835-J GLY11A - Planned | 21.52 | 164 | 3529.28 | 0.0035491 | 2.1641e-05
2013-05-23 | 300497 | TCB1 | Rural short | LV Transformer SP14443-A TCB1 - Planned | 6.9329 | 302 | 2093.7358 | 0.0060461 | 2.002e-05
2013-05-23 | 300498 | NBR5A | Rural short | LV Transformer SP1105-B NBR5A - Planned | 4 | 95 | 380 | 0.0010973 | 1.1551e-05
2013-05-23 | 300499 | CRBTHP14 | Urban | LV Transformer SP5742-C CRBTHP14 - Planned | 46.36 | 351 | 16272.36 | 0.016364 | 4.662e-05
2013-05-23 | 300500 | BBH10A | Urban | LV Transformer SP2684-E BBH10A - Planned | 17.68 | 328 | 5799.04 | 0.0058315 | 1.7779e-05
2013-05-23 | 300501 | HWL3A | Urban | LV Transformer SP6468-F HWL3A - Planned | 35.19 | 423 | 14885.37 | 0.014969 | 3.5387e-05
2013-05-23 | 300502 | BHD1A | Urban | LV Transformer SP63321-C BHD1A - Planned | 50.7 | 190 | 9633 | 0.009687 | 5.0984e-05
2013-05-23 | 300504 | DRD13A | Urban | LV Transformer SP13757-C DRD13A - Planned | 14.625 | 258 | 3773.25 | 0.0037944 | 1.4707e-05
2013-05-23 | 300505 | SGT7 | Urban | LV Transformer SP3766-D SGT7 - Planned | 1.05 | 160 | 168 | 0.00016894 | 1.0559e-06
2013-05-23 | 300506 | RCF9A | Urban | LV Transformer SP13100-D RCF9A - Planned | 32.55 | 284 | 9244.2 | 0.009296 | 3.2732e-05
2013-05-23 | 300507 | CBW7 | Rural short | LV Transformer SC2397-H CBW7 - Planned | 13.8 | 83.5 | 426.88 | 0.0012327 | 3.985e-05
2013-05-23 | 300508 | SGT22A | Urban | LV Transformer SP3161-H SGT22A - Planned | 6.37 | 231 | 1471.47 | 0.0014797 | 6.4057e-06
2013-05-23 | 300509 | RLB16A | Rural short | LV Transformer SP20472-B RLB16A - Planned | 1 | 402 | 402 | 0.0011609 | 2.8877e-06
2013-05-23 | 300512 | ARG5A | Urban | LV Transformer SP4181-G ARG5A - Planned | 7.14 | 342 | 2441.88 | 0.0024556 | 7.18e-06
2013-05-23 | 300513 | HPK3A | Urban | LV Transformer SP2322-J HPK3A - Planned | 20.79 | 218 | 4532.22 | 0.0045576 | 2.0906e-05
2013-05-23 | 300514 | CPC22A | Urban | LV Transformer SC135-E CPC22A - Planned | 0.99 | 37 | 36.63 | 3.6835e-05 | 9.9555e-07
2013-05-23 | 300515 | CPC22A | Urban | LV Transformer SC135-E CPC22A - Planned | 0.99 | 32 | 31.68 | 3.1858e-05 | 9.9555e-07
2013-05-23 | 300600 | AHL11A | Urban | LV Transformer SP521765-A AHL11A - Planned | 9 | 301 | 2709 | 0.0027242 | 9.0504e-06
2013-05-23 | 300642 | NBR15A | Rural short | Feeder NBR15A - Planned | 24.07 | 323 | 7774.61 | 0.022451 | 6.9507e-05
2013-05-23 | 300643 | LBH5A | Rural short | Feeder LBH5A - Planned | 3.01 | 440 | 1324.4 | 0.0038245 | 8.692e-06
2013-05-24 | 300554 | KBR2A | Rural short | LV Transformer SP2182-E KBR2A - Planned | 3 | 35 | 105 | 0.00030328 | 8.6652e-06
2013-05-24 | 300575 | CRBTHP26 | Urban | LV Transformer SP737244 - Planned | 0.8 | 205 | 164 | 0.0001649 | 8.0439e-07
2013-05-24 | 300576 | CNA8A | Rural short | Feeder CNA8A - Planned | 6 | 206 | 1236 | 0.00357 | 1.733e-05
2013-05-24 | 300593 | THL1 | Rural short | Feeder THL1 - Planned | 7 | 342 | 2394 | 0.0069148 | 2.0219e-05
2013-05-24 | 300597 | WMD2A | Urban | LV Transformer SP14048-A WMD2A - Planned | 46.06 | 135 | 6218.1 | 0.0062522 | 4.6312e-05
2013-05-24 | 300598 | GYN6A | Rural short | Feeder GYN6A - Planned | 71.4 | 222 | 15850.8 | 0.045783 | 0.00020623
2013-05-24 | 300601 | GLY2A | Urban | LV Transformer SC690165 GLY2A - Planned | 14.19 | 114 | 1617.66 | 0.0016265 | 1.4268e-05
2013-05-24 | 300602 | TWG18 | Urban | LV Transformer SP1834353 TWG18 - Planned | 29.3 | 130 | 3809 | 0.0038299 | 2.9461e-05
2013-05-24 | 300603 | KWA3A | Urban | LV Transformer SP3514-B KWA3A - Planned | 5.9 | 136 | 802.4 | 0.0008068 | 5.9323e-06
2013-05-24 | 300604 | CLM8 | Urban | LV Transformer SP2873-A CLM8 - Planned | 11.6 | 97 | 1125.2 | 0.0011314 | 1.1664e-05
2013-05-24 | 300605 | CLD30A | Urban | LV Transformer SP1289-B CLD30A - Planned | 23.985 | 320 | 7675.2 | 0.0077173 | 2.4116e-05
2013-05-24 | 300606 | CLM8 | Urban | LV Transformer SP91633-A CLM9 - Planned | 3.48 | 200 | 696 | 0.00069981 | 3.4991e-06
2013-05-24 | 300606 | CLM9 | Urban | LV Transformer SP91633-A CLM9 - Planned | 13.13 | 200 | 2626 | 0.0026404 | 1.3202e-05
2013-05-24 | 300607 | BHD35A | Rural short | LV Transformer SP5644-F BHD35A - Planned | 6.5 | 293 | 1904.5 | 0.0055009 | 1.8775e-05
2013-05-24 | 300608 | PPE13A | Rural short | LV Transformer SC22323-B PPE13A - Planned | 5.81 | 28 | 162.68 | 0.00046988 | 1.6782e-05
2013-05-24 | 300608 | YTA22A | Rural short | LV Transformer SC22323-B PPE13A - Planned | 2.16 | 28 | 60.48 | 0.00017469 | 6.2389e-06
2013-05-24 | 300609 | BHD44A | Urban | LV Transformer SC428-H BHD44A - Planned | 4.76 | 468 | 2227.68 | 0.0022399 | 4.7861e-06
2013-05-24 | 300610 | MRE1 | Urban | LV Transformer SP4241-J MRE1 - Planned | 21.84 | 334 | 7294.56 | 0.0073345 | 2.196e-05
2013-05-24 | 300611 | KLG5A | Rural short | LV Transformer SP3077-D KLG5A - Planned | 2.88 | 142 | 408.96 | 0.0011812 | 8.3186e-06
2013-05-24 | 300612 | KCY2 | Rural short | LV Transformer SP1405-G KCY2 - Planned | 6 | 76 | 456 | 0.0013171 | 1.733e-05
2013-05-24 | 300613 | RCF9A | Urban | LV Transformer SP13100-D RCF9A - Planned | 1.08 | 30 | 32.4 | 3.2578e-05 | 1.0859e-06
2013-05-24 | 300614 | DRD13A | Urban | LV Transformer SP2212-F DRD13A - Planned | 1.45 | 30 | 43.5 | 4.3738e-05 | 1.4579e-06
2013-05-24 | 300615 | HTN3B | Urban | LV Transformer SP10798-F HTN3B - Planned | 14.365 | 248 | 3562.52 | 0.003582 | 1.4444e-05
2013-05-24 | 300615 | HTN7A | Urban | LV Transformer SP10798-F HTN3B - Planned | 1.02 | 248 | 252.96 | 0.00025435 | 1.0256e-06
2013-05-24 | 300617 | MRE2 | Urban | LV Transformer SP5846-G MRE2 - Planned | 1.34 | 297 | 397.98 | 0.00040016 | 1.3473e-06
2013-05-24 | 300618 | SGT9 | Urban | LV Transformer SP782180 SGT9 - Planned | 11 | 318 | 3498 | 0.0035172 | 1.106e-05
2013-05-24 | 300619 | LTA3A | Urban | LV Transformer SP3156-B LTA3A - Planned | 3.01 | 323 | 972.23 | 0.00097756 | 3.0265e-06
2013-05-24 | 300620 | CHL4 | Urban | LV Transformer SP6-R CHL4 - Planned | 6.48 | 277 | 1794.96 | 0.0018048 | 6.5155e-06
2013-05-24 | 300621 | EMP21A | Rural short | LV Transformer SP5212-M NSW5A - Planned | 0.68 | 223 | 151.64 | 0.000438 | 1.9641e-06
2013-05-24 | 300621 | EMP4A | Urban | LV Transformer SP5212-M NSW5A - Planned | 3.27 | 223 | 729.21 | 0.00073321 | 3.2879e-06
2013-05-24 | 300621 | NSW5A | Urban | LV Transformer SP5212-M NSW5A - Planned | 16.17 | 223 | 3605.91 | 0.0036257 | 1.6259e-05
2013-05-24 | 300622 | NSW22B | Urban | LV Transformer SP683-N NSW22B - Planned | 1.9468 | 32 | 62.2976 | 6.2639e-05 | 1.9575e-06
2013-05-24 | 300622 | NSW3A | Urban | LV Transformer SP683-N NSW22B - Planned | 2.51 | 32 | 80.32 | 8.076e-05 | 2.5238e-06
2013-05-24 | 300623 | BVL10A | Urban | LV Transformer SP3056-D BVL10A - Planned | 23.76 | 309 | 7341.84 | 0.0073821 | 2.389e-05
2013-05-24 | 300623 | BVL3A | Urban | LV Transformer SP3056-D BVL10A - Planned | 1.48 | 309 | 457.32 | 0.00045983 | 1.4881e-06
2013-05-24 | 300624 | NSW22B | Urban | LV Transformer SC523138-B NSW22B - Planned | 3.7202 | 94 | 349.6988 | 0.00035162 | 3.7406e-06
2013-05-24 | 300625 | MCW7 | Rural short | LV Transformer SP11845-D MCW7 - Planned | 9.9 | 308 | 3049.2 | 0.0088073 | 2.8595e-05
2013-05-24 | 300626 | BVL13A | Urban | LV Transformer SC108-K BVL3A - Planned | 0.78 | 360 | 280.8 | 0.00028234 | 7.8428e-07
2013-05-24 | 300626 | BVL3A | Urban | LV Transformer SC108-K BVL3A - Planned | 24.21 | 360 | 8715.6 | 0.0087634 | 2.4343e-05
2013-05-24 | 300627 | TGW2 | Rural short | LV Transformer SP8217-A TGW2 - Planned | 1 | 197 | 197 | 0.00056901 | 2.8884e-06
2013-05-24 | 300635 | THL1 | Rural short | Feeder THL1 - Planned | 7 | 342 | 2394 | 0.0069148 | 2.0219e-05
2013-05-24 | 300656 | EMP23A | Urban | LV Transformer SC3911-F SBK9 - Planned | 1.12 | 257 | 287.84 | 0.00028942 | 1.1261e-06
2013-05-24 | 300656 | SBK9 | Urban | LV Transformer SC3911-F SBK9 - Planned | 10.03 | 257 | 2577.71 | 0.0025918 | 1.0085e-05
2013-05-25 | 300646 | KBR2A | Rural short | LV Transformer SP809-E KBR2A - Planned | 4 | 245 | 980 | 0.0028311 | 1.1555e-05
2013-05-25 | 300653 | MGP15A | Rural short | Feeder MGP15A - Planned | 32.5 | 519 | 16867.5 | 0.048728 | 9.3888e-05
2013-05-25 | 300657 | COR22A | Rural short | LV Transformer SP833348 COR22A - Planned | 1 | 38 | 38 | 0.00010978 | 2.8889e-06
2013-05-25 | 300661 | WNM5 | Urban | LV Transformer SP2140-J WNM5 - Planned | 8.82 | 293 | 2584.26 | 0.0025982 | 8.8676e-06
2013-05-26 | 300665 | YTA3A | Urban | Feeder YTA3A - Planned | 18 | 207 | 3726 | 0.0037459 | 1.8096e-05
2013-05-26 | 300667 | JDL8A | Urban | Feeder JDL8A - Planned | 30 | 167 | 5010 | 0.0050368 | 3.0161e-05
2013-05-26 | 300672 | YTA3A | Urban | LV Transformer SP225901 YTA3A - Planned | 8 | 442 | 3536 | 0.0035549 | 8.0428e-06
2013-05-26 | 300673 | LDR5 | Urban | LV Transformer SP5616-E LDR2A - Planned | 43 | 435 | 18705 | 0.018805 | 4.323e-05
2013-05-26 | 300674 | BLB8A | Urban | LV Transformer SP449-M BLB8A - Planned | 11.33 | 400 | 4532 | 0.0045562 | 1.1391e-05
2013-05-26 | 300675 | WED4B | Urban | LV Transformer SC164-N WED4B - Planned | 16.8 | 225 | 3780 | 0.0038002 | 1.689e-05
2013-05-26 | 300675 | WED5A | Urban | LV Transformer SC164-N WED4B - Planned | 3.08 | 225 | 693 | 0.00069671 | 3.0965e-06
2013-05-26 | 300676 | RPN6A | Rural short | LV Transformer SP75948 RPN6A - Planned | 7.04 | 239 | 1682.56 | 0.004861 | 2.0339e-05
2013-05-27 | 300694 | HWL3A | Urban | LV Transformer SP8704-C HWL3A - Planned | 3.5 | 70 | 245 | 0.00024627 | 3.5182e-06
2013-05-27 | 300695 | NRG14A | Rural short | LV Transformer SP6275-C NRG14A - Planned | 24.12 | 84 | 2026.08 | 0.0058549 | 6.9702e-05
2013-05-27 | 300696 | FDS1 | Rural short | LV Transformer SP2738-F FDS1 - Planned | 2 | 89 | 178 | 0.00051438 | 5.7796e-06
2013-05-27 | 300697 | TGW3 | Rural short | LV Transformer SP1250-D TGW3 - Planned | 3.5 | 145 | 507.5 | 0.0014666 | 1.0114e-05
2013-05-27 | 300698 | TGW3 | Rural short | LV Transformer SP1551-B TGW3 - Planned | 0.5 | 195 | 97.5 | 0.00028175 | 1.4449e-06
2013-05-27 | 300700 | MSV2 | Rural short | LV Transformer SP1834-C MSV2 - Planned | 5.5 | 251 | 1380.5 | 0.0039893 | 1.5894e-05
2013-05-27 | 300701 | GYS3A | Rural short | LV Transformer SP17370-B GYS3A - Planned | 24.5 | 219 | 5365.5 | 0.015505 | 7.08e-05
2013-05-27 | 300702 | NBR4A | Rural short | LV Transformer SP3018-A NBR4A - Planned | 3 | 222 | 666 | 0.0019246 | 8.6694e-06
2013-05-27 | 300703 | LRE6A | Rural short | LV Transformer SP8074-B LRE6A - Planned | 2 | 54 | 108 | 0.0003121 | 5.7796e-06
2013-05-27 | 300704 | AHD16 | Urban | LV Transformer SP12983-A AHD16 - Planned | 38.28 | 202 | 7732.56 | 0.0077727 | 3.8479e-05
2013-05-27 | 300705 | CFD6A | Urban | LV Transformer SP5369-H CFD6A - Planned | 24.32 | 210 | 5107.2 | 0.0051337 | 2.4446e-05
2013-05-27 | 300706 | ENG2 | Urban | LV Transformer SC1500260 ENG2 - Planned | 8.54 | 352 | 3006.08 | 0.0030217 | 8.5843e-06
2013-05-27 | 300707 | PWC6 | Rural short | LV Transformer SP3996-B PWC6 - Planned | 3.9 | 358 | 1396.2 | 0.0040347 | 1.127e-05
2013-05-27 | 300708 | BLH12A | Rural short | LV Transformer SP18103-A BLH12A - Planned | 1 | 420 | 420 | 0.0012137 | 2.8898e-06
2013-05-27 | 300710 | MGP13A | Rural short | LV Transformer SP5273-G MGP13A - Planned | 3 | 105 | 315 | 0.00091028 | 8.6694e-06
2013-05-27 | 300711 | SPO60A | Urban | LV Transformer SP1434-J SPO60A - Planned | 26.32 | 280 | 7369.6 | 0.0074079 | 2.6457e-05
2013-05-27 | 300712 | WNM7A | Urban | LV Transformer SC1574-L WNM7A - Planned | 10.175 | 359 | 3652.825 | 0.0036718 | 1.0228e-05
2013-05-27 | 300713 | SMF3A | Rural short | LV Transformer SP1545-F SMF3A - Planned | 11.1 | 309 | 3429.9 | 0.0099117 | 3.2077e-05
2013-05-27 | 300714 | ALY5 | Urban | LV Transformer SP4170-I ALY5 - Planned | 6.885 | 133 | 915.705 | 0.00092046 | 6.9208e-06
2013-05-27 | 300715 | BPN3 | Urban | LV Transformer SP4867-M BPN3 - Planned | 6.84 | 287 | 1963.08 | 0.0019733 | 6.8755e-06
2013-05-27 | 300716 | THL3 | Rural short | LV Transformer SP69394-A THL3 - Planned | 9 | 143 | 1287 | 0.0037192 | 2.6008e-05
2013-05-27 | 300717 | BVL5A | Urban | LV Transformer SP3845-D BVL5A - Planned | 29.29 | 454 | 13297.66 | 0.013367 | 2.9442e-05
2013-05-27 | 300719 | KCY2 | Rural short | Feeder KCY2 - Planned | 102.9 | 265 | 27268.5 | 0.0788 | 0.00029736
2013-05-28 | 300753 | RIS1 | Rural short | LV Transformer SP15022-C RIS1 - Planned | 13 | 262 | 3406 | 0.0098443 | 3.7574e-05
2013-05-28 | 300754 | WFD2B | Rural short | Feeder WFD2B - Planned | 67.4 | 153 | 10312.2 | 0.029805 | 0.00019481
2013-05-28 | 300756 | WHO1 | Rural short | Feeder WHO1 - Planned | 55 | 347 | 19085 | 0.055161 | 0.00015897
2013-05-28 | 300757 | KCY2 | Rural short | Feeder KCY2 - Planned | 2 | 298 | 596 | 0.0017226 | 5.7806e-06
2013-05-28 | 300758 | THL2 | Rural short | LV Transformer SP3024-B THL2 - Planned | 2 | 105 | 210 | 0.00060696 | 5.7806e-06
2013-05-28 | 300759 | BLH12A | Rural short | Feeder BLH12A - Planned | 109 | 270 | 29430 | 0.085061 | 0.00031504
2013-05-28 | 300760 | TBV4 | Rural short | LV Transformer SP9777-D TBV4 - Planned | 13.33 | 209 | 2785.97 | 0.0080523 | 3.8528e-05
2013-05-28 | 300761 | TGW3 | Rural short | Feeder TGW3 - Planned | 25 | 465 | 11625 | 0.0336 | 7.2257e-05
2013-05-28 | 300762 | BDT5 | Rural short | LV Transformer SP7229-D BDT5 - Planned | 1 | 478 | 478 | 0.0013816 | 2.8903e-06
2013-05-28 | 300763 | PBH8 | Urban | LV Transformer SP13301-D PBH8 - Planned | 61 | 525 | 32025 | 0.032188 | 6.1311e-05
2013-05-28 | 300766 | SHW6 | Urban | LV Transformer SP1864-J SHW6 - Planned | 17.05 | 299 | 5097.95 | 0.0051239 | 1.7137e-05
2013-05-28 | 300767 | SHW81 | Urban | LV Transformer SP1838-K SHW81 - Planned | 22.28 | 131 | 2918.68 | 0.0029335 | 2.2393e-05
2013-05-28 | 300768 | STL1A | Urban | LV Transformer SP30136-D STL1A - Planned | 17.4 | 349 | 6072.6 | 0.0061035 | 1.7489e-05
2013-05-28 | 300769 | NMK5 | Urban | LV Transformer SC22150-E NMK5 - Planned | 2.11 | 248 | 523.28 | 0.00052595 | 2.1207e-06
2013-05-28 | 300770 | AGE3 | Urban | LV Transformer SP3882-G AGE3 - Planned | 46.87 | 347 | 16263.89 | 0.016347 | 4.7109e-05
2013-05-28 | 300771 | TWG11 | Urban | LV Transformer SP5072-J TWG11 - Planned | 4.0165 | 145 | 582.3925 | 0.00058536 | 4.037e-06
2013-05-28 | 300772 | NBR5A | Rural short | LV Transformer SP4031-A NBR5A - Planned | 16.66 | 87 | 1449.42 | 0.0041892 | 4.8152e-05
2013-05-28 | 300773 | CLD30A | Urban | LV Transformer SP1289-B CLD30A - Planned | 18.45 | 345 | 6365.25 | 0.0063977 | 1.8544e-05
2013-05-28 | 300774 | AHD16 | Urban | LV Transformer SP5135-A AHD16 - Planned | 6.96 | 489 | 3403.44 | 0.0034208 | 6.9954e-06
2013-05-28 | 300775 | AMR2 | Rural short | LV Transformer SP349-C AMR2 - Planned | 3.83 | 247 | 946.01 | 0.0027342 | 1.107e-05
2013-05-28 | 300776 | CLM7 | Urban | LV Transformer SP4030-A NBR7A - Planned | 8.16 | 242 | 1974.72 | 0.0019848 | 8.2016e-06
2013-05-28 | 300777 | AMR3 | Rural short | LV Transformer SP922-C AMR3 - Planned | 2 | 203 | 406 | 0.0011735 | 5.7806e-06
2013-05-28 | 300778 | BHD44A | Urban | LV Transformer SP3831-E BHD44A - Planned | 36.66 | 342 | 12537.72 | 0.012602 | 3.6847e-05
2013-05-28 | 300779 | KCY1 | Urban | LV Transformer SP3572-E KCY1 - Planned | 3.96 | 289 | 1144.44 | 0.0011503 | 3.9802e-06
2013-05-28 | 300780 | BHL6A | Urban | LV Transformer SC4553-F BHL6A - Planned | 6.255 | 423 | 2645.865 | 0.0026593 | 6.2869e-06
2013-05-28 | 300781 | DRD13A | Urban | LV Transformer SP2212-F DRD13A - Planned | 14.5 | 226 | 3277 | 0.0032937 | 1.4574e-05
2013-05-28 | 300782 | BRD5A | Rural short | LV Transformer SP17265-D BRD5A - Planned | 4 | 325 | 1300 | 0.0037574 | 1.1561e-05
2013-05-28 | 300783 | TCB1 | Rural short | Feeder TCB1 - Planned | 1388.99 | 176.3846 | 117833.89 | 0.34057 | 0.0040146
2013-05-28 | 300785 | MLY1 | Rural short | LV Transformer SP5807-A MLY1 - Planned | 2.01 | 103 | 207.03 | 0.00059838 | 5.8095e-06
2013-05-28 | 300786 | GYN3A | Rural short | Feeder GYN3A - Planned | 2 | 359 | 718 | 0.0020752 | 5.7806e-06
2013-05-28 | 300787 | NBR12A | Rural short | LV Transformer SP5145-A NBR12A - Planned | 11.04 | 233 | 2572.32 | 0.0074347 | 3.1909e-05
2013-05-28 | 300788 | MTB17A | Rural short | Feeder MTB17A - Planned | 13.5 | 675 | 9112.5 | 0.026338 | 3.9019e-05
2013-05-28 | 300790 | CRM16A | Rural short | LV Transformer SP2833-E CRM16A - Planned | 10 | 915 | 9150 | 0.026446 | 2.8903e-05
2013-05-28 | 300795 | MDRMLD11 | Urban | LV Transformer SP567459 MDRMLD11 - Planned | 9 | 495 | 4455 | 0.0044777 | 9.0458e-06
2013-05-28 | 300843 | SHW6 | Urban | LV Transformer SP2317-M SHW6 - Planned | 21.12 | 302 | 6378.24 | 0.0064107 | 2.1228e-05
2013-05-29 | 300813 | LLY1 | Rural short | LV Transformer SP2958-D LLY1 - Planned | 2.01 | 160 | 321.6 | 0.00092967 | 5.8104e-06
2013-05-29 | 300814 | BNH6A | Rural short | Feeder BNH6A - Planned | 17 | 332 | 5644 | 0.016315 | 4.9143e-05
2013-05-29 | 300833 | BIS1 | Rural short | LV Transformer SP790834 BIS1 - Planned | 5 | 330 | 1650 | 0.0047697 | 1.4454e-05
2013-05-29 | 300834 | CBT8A | Rural short | Feeder CBT8A - Planned | 8.01 | 335 | 2683.35 | 0.0077569 | 2.3155e-05
2013-05-29 | 300837 | MLY6 | Rural short | Feeder MLY6 - Planned | 18.03 | 444 | 8005.32 | 0.023141 | 5.212e-05
2013-05-29 | 300838 | NBR12A | Rural short | LV Transformer SP2277-A NBR12A - Planned | 4.4 | 101 | 444.4 | 0.0012846 | 1.2719e-05
2013-05-29 | 300839 | GBN4 | Rural short | LV Transformer SP6240-A GBN4 - Planned | 1 | 49 | 49 | 0.00014165 | 2.8908e-06
2013-05-29 | 300840 | GBN4 | Rural short | LV Transformer SP2904-B GBN4 - Planned | 2 | 155 | 310 | 0.00089613 | 5.7815e-06
2013-05-29 | 300841 | COR22A | Rural short | Feeder COR22A - Planned | 60.58 | 149 | 9026.42 | 0.026093 | 0.00017512
2013-05-29 | 300842 | CHL7 | Urban | LV Transformer SC5605-F CHL7 - Planned | 4.8 | 342 | 1641.6 | 0.0016498 | 4.824e-06
2013-05-29 | 300844 | AHL4A | Urban | LV Transformer SP4979-I AHL4A - Planned | 14.42 | 317 | 4571.14 | 0.004594 | 1.4492e-05
2013-05-29 | 300845 | AGE3 | Urban | LV Transformer SP1943-L AGE3 - Planned | 33.345 | 220 | 7335.9 | 0.0073726 | 3.3512e-05
2013-05-29 | 300846 | NBR12A | Rural short | LV Transformer SP11718-A NBR12A - Planned | 17.02 | 82 | 1395.64 | 0.0040344 | 4.9201e-05
2013-05-29 | 300847 | GYM2A | Rural short | LV Transformer SP1039-F GYM2A - Planned | 3 | 96 | 288 | 0.00083254 | 8.6723e-06
2013-05-29 | 300848 | SPD29A | Urban | LV Transformer SC314-K SPD29A - Planned | 9.2915 | 130 | 1207.895 | 0.0012139 | 9.3379e-06
2013-05-29 | 300849 | BHD35A | Rural short | LV Transformer SP93947-B BHD35A - Planned | 5.5 | 210 | 1155 | 0.0033388 | 1.5899e-05
2013-05-29 | 300850 | CFD8A | Urban | LV Transformer SC3009-F CFD8A - Planned | 7.755 | 25 | 193.875 | 0.00019484 | 7.7938e-06
2013-05-29 | 300851 | RCF9A | Urban | LV Transformer SP13100-D RCF9A - Planned | 23.98 | 259 | 6210.82 | 0.0062419 | 2.41e-05
2013-05-29 | 300852 | BHL1A | Urban | LV Transformer SP3329-G BHL1A - Planned | 21.6 | 51 | 1101.6 | 0.0011071 | 2.1708e-05
2013-05-29 | 300853 | MRK3 | Urban | LV Transformer SP10364-G WED3A - Planned | 18.05 | 210 | 3790.5 | 0.0038094 | 1.814e-05
2013-05-29 | 300854 | ALY5 | Urban | LV Transformer SP31667-D ALY5 - Planned | 12.2 | 313 | 3818.6 | 0.0038377 | 1.2261e-05
2013-05-29 | 300855 | ALY5 | Urban | LV Transformer SG1945-I ALY5 - Planned | 17.635 | 288 | 5078.88 | 0.0051043 | 1.7723e-05
2013-05-29 | 300856 | RCN2A | Urban | LV Transformer SC5598-L RCN2A - Planned | 25.6364 | 299 | 7665.2836 | 0.0077036 | 2.5765e-05
2013-05-29 | 300857 | THL3 | Rural short | LV Transformer SP918-B THL3 - Planned | 1 | 206 | 206 | 0.00059549 | 2.8908e-06
2013-05-29 | 300901 | TWG11 | Urban | LV Transformer SP740388 TWG11 - Planned | 8.24 | 351 | 2892.24 | 0.0029067 | 8.2812e-06
2013-05-29 | 300999 | BMT5 | Rural short | LV Transformer SP426-C BMT5 - Planned | 5.16 | 294 | 1517.04 | 0.0043854 | 1.4916e-05
2013-05-30 | 300873 | LRE4A | Rural short | LV Transformer SP10181-B LRE4A - Planned | 3 | 18 | 54 | 0.00015613 | 8.6736e-06
2013-05-30 | 300874 | MBG4 | Rural short | LV Transformer SP13666-D MBG4 - Planned | 1 | 107 | 107 | 0.00030936 | 2.8912e-06
2013-05-30 | 300875 | TRP3 | Rural short | LV Transformer SP3249-D TRP3 - Planned | 0.66 | 37 | 24.42 | 7.0603e-05 | 1.9082e-06
2013-05-30 | 300876 | LLY1 | Rural short | LV Transformer SP3012-C LLY1 - Planned | 4.15 | 322 | 1336.3 | 0.0038635 | 1.1999e-05
2013-05-30 | 300895 | TGW3 | Rural short | Feeder TGW3 - Planned | 4 | 228 | 912 | 0.0026368 | 1.1565e-05
2013-05-30 | 300902 | SHW6 | Urban | LV Transformer SP626552 SHW6 - Planned | 16.18 | 279 | 4514.22 | 0.0045364 | 1.6259e-05
2013-05-30 | 300903 | NBR5A | Rural short | LV Transformer SP2504-A NBR5A - Planned | 7.84 | 35 | 274.4 | 0.00079335 | 2.2667e-05
2013-05-30 | 300904 | CLM7 | Urban | LV Transformer SP163869 CLM7 - Planned | 1.585 | 60 | 95.1 | 9.5566e-05 | 1.5928e-06
2013-05-30 | 300905 | BWH13A | Rural short | LV Transformer SP17904-B BWH13A - Planned | 3.23 | 236 | 762.28 | 0.0022039 | 9.3386e-06
2013-05-30 | 300906 | NBR7A | Rural short | LV Transformer SP4030-A NBR7A - Planned | 6 | 83 | 498 | 0.0014398 | 1.7347e-05
2013-05-30 | 300907 | NBR12A | Rural short | LV Transformer SP5272-A NBR12A - Planned | 19 | 149 | 2831 | 0.008185 | 5.4933e-05
2013-05-30 | 300908 | TCB1 | Rural short | Feeder TCB1 - Planned | 451.965 | 446 | 201576.39 | 0.5828 | 0.0013067
2013-05-30 | 300909 | SPO51A | Urban | LV Transformer SP36012-C SPO51A - Planned | 29.68 | 337 | 10002.16 | 0.010051 | 2.9826e-05
2013-05-30 | 300910 | CRB25A | Rural short | LV Transformer SP760627 CRB25A - Planned | 8.61 | 270 | 2324.7 | 0.0067212 | 2.4893e-05
2013-05-30 | 300911 | HTL10A | Urban | LV Transformer SC22018-G HTL10A - Planned | 9.02 | 50 | 451 | 0.00045321 | 9.0642e-06
2013-05-30 | 300912 | KLG11A | Urban | LV Transformer SP5885-B KLG11A - Planned | 20.95 | 253 | 5300.35 | 0.0053263 | 2.1053e-05
2013-05-30 | 300913 | HDA10A | Urban | LV Transformer SP3770-G HDA10A - Planned | 30.7 | 345 | 10591.5 | 0.010643 | 3.0851e-05
2013-05-30 | 300914 | BHL6A | Urban | LV Transformer SC4859-G BHL6A - Planned | 8.4897 | 365 | 3098.7405 | 0.0031139 | 8.5313e-06
2013-05-30 | 300915 | UMG1B | Urban | LV Transformer SP3418-F UMG1B - Planned | 29.21 | 322 | 9405.62 | 0.0094517 | 2.9353e-05
2013-05-30 | 300916 | HPE16A | Urban | LV Transformer SC4042-I HPE3A - Planned | 0.8708 | 352 | 306.5216 | 0.00030802 | 8.7507e-07
2013-05-30 | 300916 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 25.2822 | 352 | 8899.3344 | 0.008943 | 2.5406e-05
2013-05-30 | 300917 | ALY5 | Urban | LV Transformer SP2720-K ALY5 - Planned | 17.355 | 270 | 4685.85 | 0.0047088 | 1.744e-05
2013-05-30 | 300918 | MRK3 | Urban | LV Transformer SC3176-J MRK3 - Planned | 39.56 | 54 | 2136.24 | 0.0021467 | 3.9754e-05
2013-05-30 | 300919 | RPN6A | Rural short | LV Transformer SP1432-G RPN6A - Planned | 3.85 | 336 | 1293.6 | 0.0037401 | 1.1131e-05
2013-05-30 | 300920 | GBN4 | Rural short | LV Transformer SP2314-E GBN4 - Planned | 2 | 276 | 552 | 0.0015959 | 5.7824e-06
2013-05-30 | 300921 | NBR5A | Rural short | LV Transformer SP3976-B NBR5A - Planned | 4 | 55 | 220 | 0.00063607 | 1.1565e-05
2013-05-31 | 300933 | GGR4 | Rural short | LV Transformer SP3980-B GGR4 - Planned | 2.25 | 158 | 355.5 | 0.001028 | 6.5062e-06
2013-05-31 | 300934 | RWD2 | Rural short | Feeder RWD2 - Planned | 16 | 260 | 4160 | 0.012029 | 4.6267e-05
2013-05-31 | 300953 | TGW1 | Rural short | Feeder TGW1 - Planned | 3.01 | 340 | 1023.4 | 0.0029593 | 8.7039e-06
2013-05-31 | 300954 | GGR5 | Rural short | Feeder GGR5 - Planned | 14.1 | 156 | 2199.6 | 0.0063605 | 4.0772e-05
2013-05-31 | 300955 | MGP13A | Rural short | Feeder MGP13A - Planned | 3 | 256 | 768 | 0.0022208 | 8.675e-06
2013-05-31 | 300956 | AHL4A | Urban | LV Transformer SP2960-K AHL4A - Planned | 8.03 | 174 | 1397.22 | 0.0014039 | 8.0686e-06
2013-05-31 | 300959 | GYN3A | Rural short | LV Transformer SP1151-D GYN3A - Planned | 15 | 165 | 2475 | 0.0071569 | 4.3375e-05
2013-05-31 | 300960 | GBN4 | Rural short | LV Transformer SP15048-C GBN4 - Planned | 5 | 160 | 800 | 0.0023133 | 1.4458e-05
2013-05-31 | 300961 | GBN4 | Rural short | LV Transformer SP6567-B GBN4 - Planned | 5 | 42 | 210 | 0.00060725 | 1.4458e-05
2013-05-31 | 300962 | GBN4 | Rural short | LV Transformer SP6798-C GBN4 - Planned | 2 | 29 | 58 | 0.00016772 | 5.7833e-06
2013-05-31 | 300963 | BHD44A | Urban | LV Transformer SP3697-E BHD44A - Planned | 25.03 | 341 | 8535.23 | 0.0085763 | 2.515e-05
2013-05-31 | 300964 | BHD21A | Urban | LV Transformer SP3494-E BHD21A - Planned | 43.68 | 196 | 8561.28 | 0.0086024 | 4.389e-05
2013-05-31 | 300965 | SPO41A | Urban | LV Transformer SP5135-H SPO41A - Planned | 6.33 | 206 | 1303.98 | 0.0013102 | 6.3604e-06
2013-05-31 | 300966 | HWL3A | Urban | LV Transformer SP2180-H HWL3A - Planned | 24.05 | 310 | 7455.5 | 0.0074913 | 2.4166e-05
2013-05-31 | 300967 | GLY4A | Urban | LV Transformer SP3765-G GLY4A - Planned | 12.72 | 145 | 1844.4 | 0.0018533 | 1.2781e-05
2013-05-31 | 300968 | UMG1B | Urban | LV Transformer SP3418-F UMG1B - Planned | 25.98 | 98 | 2546.04 | 0.0025583 | 2.6105e-05
2013-05-31 | 300969 | WED3A | Urban | LV Transformer SP10364-G WED3A - Planned | 13.86 | 296 | 4102.56 | 0.0041223 | 1.3927e-05
2013-05-31 | 300970 | HPE3A | Urban | LV Transformer SC4042-I HPE3A - Planned | 21.255 | 275 | 5845.125 | 0.0058732 | 2.1357e-05
2013-05-31 | 300971 | ALY5 | Urban | LV Transformer SP31667-D ALY5 - Planned | 30.5 | 270 | 8235 | 0.0082746 | 3.0647e-05
2013-05-31 | 300972 | RIS2 | Urban | LV Transformer SP6210-D RIS2 - Planned | 14.79 | 138 | 2041.02 | 0.0020508 | 1.4861e-05
2013-05-31 | 300973 | RST16A | Urban | LV Transformer SG84-E RST16A - Planned | 7.02 | 324 | 2274.48 | 0.0022854 | 7.0538e-06
2013-05-31 | 300974 | BVL3A | Urban | LV Transformer SP811208 BVL3A - Planned | 12.135 | 147 | 1783.845 | 0.0017924 | 1.2193e-05
2013-05-31 | 300977 | GYN6A | Rural short | Feeder GYN6A - Planned | 3.9 | 357 | 1392.3 | 0.0040261 | 1.1277e-05
2013-05-31 | 300978 | COR26A | Rural short | LV Transformer SP9335-A COR26A - Planned | 6 | 238 | 1428 | 0.0041293 | 1.735e-05
2013-05-31 | 300979 | GYN7A | Rural short | LV Transformer SP12624-A GYN7A - Planned | 3 | 45 | 135 | 0.00039037 | 8.675e-06
2013-05-31 | 300980 | NBR12A | Rural short | LV Transformer SP5109-A NBR12A - Planned | 49 | 195 | 9555 | 0.02763 | 0.00014169
2013-06-01 | 300993 | GGR4 | Rural short | LV Transformer SP3702-B GGR4 - Planned | 1.34 | 96 | 128.64 | 0.00037204 | 3.8754e-06
2013-06-01 | 301000 | MGP15A | Rural short | LV Transformer SP5220-G MGP15A - Planned | 2.5 | 490 | 1225 | 0.0035428 | 7.2303e-06
2013-06-01 | 301003 | WMD11A | Rural short | LV Transformer SP49813-A WMD11A - Planned | 8.06 | 248 | 1998.88 | 0.005781 | 2.331e-05
2013-06-01 | 301004 | MGP15A | Rural short | LV Transformer SP4601-G MGP15A - Planned | 15.1 | 395 | 5964.5 | 0.01725 | 4.3671e-05
2013-06-02 | 301005 | SBK9 | Urban | LV Transformer SC494283 SBK9 - Planned | 2 | 149 | 298 | 0.00029939 | 2.0093e-06
2013-06-02 | 301007 | NSD3A | Urban | LV Transformer SG2527-J NSD3A - Planned | 4.5 | 160 | 720 | 0.00072335 | 4.521e-06
2013-06-02 | 301008 | WCL3 | Urban | LV Transformer SG7188-H WCL3 - Planned | 1 | 360 | 360 | 0.00036168 | 1.0047e-06
2013-06-02 | 301009 | KBN5A | Rural short | LV Transformer SP4262-F KBN5A - Planned | 1 | 350 | 350 | 0.0010123 | 2.8924e-06
2013-06-02 | 301015 | MLT8B | Urban | LV Transformer SC5584-E MTG11A - Planned | 1.95 | 355 | 692.25 | 0.00069547 | 1.9591e-06
2013-06-02 | 301015 | NMK26 | Urban | LV Transformer SC5584-E MTG11A - Planned | 43.44 | 355 | 15421.2 | 0.015493 | 4.3642e-05
2013-06-02 | 301016 | WCL3 | Urban | LV Transformer SP62957-E WCL3 - Planned | 7.04 | 298 | 2097.92 | 0.0021077 | 7.0728e-06
2013-06-02 | 301017 | GYM2A | Rural short | LV Transformer SP735-B GYM2A - Planned | 2 | 39 | 78 | 0.00022561 | 5.7848e-06
2013-06-02 | 301018 | SPD2B | Urban | LV Transformer SG177-I SPD29A - Planned | 2.01 | 455 | 914.55 | 0.00091881 | 2.0194e-06
2013-06-02 | 301019 | ZMR6A | Urban | LV Transformer SP2142-G ZMR6A - Planned | 4.225 | 300 | 1267.5 | 0.0012734 | 4.2447e-06
2013-06-02 | 301020 | ARG5A | Urban | LV Transformer SP866-L ARG5A - Planned | 12.73 | 310 | 3946.3 | 0.0039647 | 1.2789e-05
2013-06-02 | 301417 | ZMR6A | Urban | LV Transformer SG1051469 ZMR6A - Planned | 1 | 435 | 435 | 0.00043703 | 1.0047e-06
2013-06-03 | 301038 | BDT1 | Rural short | Feeder BDT1 - Planned | 10 | 180 | 1800 | 0.0052068 | 2.8927e-05
2013-06-03 | 301040 | RIS2 | Urban | Feeder RIS2 - Planned | 2224.53 | 112 | 249147.36 | 0.2503 | 0.0022348
2013-06-03 | 301041 | THL3 | Rural short | LV Transformer SP3252-C THL3 - Planned | 2 | 245 | 490 | 0.0014174 | 5.7853e-06
2013-06-03 | 301044 | KLG5A | Rural short | Feeder KLG5A - Planned | 26.99 | 220 | 5937.8 | 0.017176 | 7.8073e-05
2013-06-03 | 301053 | BMT3 | Rural short | LV Transformer SC1423911 BMT3 - Planned | 13 | 86 | 1118 | 0.003234 | 3.7605e-05
2013-06-03 | 301055 | CHL11A | Rural short | Feeder CHL11A - Planned | 2 | 320 | 640 | 0.0018513 | 5.7853e-06
2013-06-03 | 301058 | CSE2 | Urban | LV Transformer SP796210 CSE2 - Planned | 9.79 | 362 | 3543.98 | 0.0035603 | 9.8351e-06
2013-06-03 | 301059 | CLM5 | Urban | LV Transformer SP11518-A CLM5 - Planned | 9.1 | 95 | 864.5 | 0.00086849 | 9.1419e-06
2013-06-03 | 301060 | CLM4A | Urban | LV Transformer SP6633-A CLM4A - Planned | 52 | 197 | 10244 | 0.010291 | 5.224e-05
2013-06-03 | 301061 | AMR2 | Rural short | LV Transformer SP1478-D AMR2 - Planned | 7 | 195 | 1365 | 0.0039485 | 2.0249e-05
2013-06-03 | 301062 | NBR7A | Rural short | LV Transformer SP13800-A NBR7A - Planned | 13.2 | 62 | 818.4 | 0.0023674 | 3.8183e-05
2013-06-03 | 301063 | CLM5 | Urban | LV Transformer SP4465-A CLM5 - Planned | 3.27 | 63 | 206.01 | 0.00020696 | 3.2851e-06
2013-06-03 | 301064 | WMD14A | Rural short | LV Transformer SP3763-B WMD14A - Planned | 21.93 | 197 | 4320.21 | 0.012497 | 6.3436e-05
2013-06-03 | 301065 | MMC22A | Urban | LV Transformer SC807719 - Planned | 12.96 | 355 | 4600.8 | 0.004622 | 1.302e-05
2013-06-03 | 301066 | CFD1A | Urban | Feeder CFD2A, CFD1A - Planned | 11.475 | 147 | 1686.825 | 0.0016946 | 1.1528e-05
2013-06-03 | 301066 | CFD2A | Urban | Feeder CFD2A, CFD1A - Planned | 1.1 | 147 | 161.7 | 0.00016245 | 1.1051e-06
2013-06-03 | 301067 | HDA10A | Urban | LV Transformer SP3769-F HDA10A - Planned | 18.225 | 360 | 6561 | 0.0065912 | 1.8309e-05
2013-06-03 | 301068 | SGT7 | Urban | LV Transformer SP1810-K SGT7 - Planned | 5.05 | 466 | 2353.3 | 0.0023641 | 5.0733e-06
2013-06-03 | 301069 | WNM1A | Urban | LV Transformer SP1333-M WNM1A - Planned | 3.42 | 346 | 1183.32 | 0.0011888 | 3.4358e-06
2013-06-03 | 301069 | WNM2A | Urban | LV Transformer SP1333-M WNM1A - Planned | 3.2 | 346 | 1107.2 | 0.0011123 | 3.2148e-06
2013-06-03 | 301070 | ALY5 | Urban | LV Transformer SP3506-H ALY5 - Planned | 5.925 | 223 | 1321.275 | 0.0013274 | 5.9523e-06
2013-06-03 | 301071 | HPK8A | Urban | LV Transformer SP1221-L HPK8A - Planned | 7.62 | 255 | 1943.1 | 0.0019521 | 7.6551e-06
2013-06-03 | 301072 | KBR3A | Rural short | LV Transformer SP2014-E KBR3A - Planned | 3 | 208 | 624 | 0.001805 | 8.678e-06
2013-06-03 | 301073 | TGW3 | Rural short | LV Transformer SP34869-A TGW3 - Planned | 3 | 111 | 333 | 0.00096325 | 8.678e-06
2013-06-03 | 301074 | TGW3 | Rural short | LV Transformer SP1243-E TGW3 - Planned | 5 | 53 | 265 | 0.00076655 | 1.4463e-05
2013-06-03 | 301075 | TGW3 | Rural short | LV Transformer SP1228-D TGW3 - Planned | 1 | 115 | 115 | 0.00033266 | 2.8927e-06
2013-06-03 | 301086 | NBR2B | Urban | LV Transformer SP3250-A NBR2B - Planned | 1.85 | 207 | 382.95 | 0.00038472 | 1.8585e-06
2013-06-04 | 301089 | ARL11A | Urban | LV Transformer SC22769-E ARL11A - Planned | 87 | 17 | 1479 | 0.0014856 | 8.7387e-05
2013-06-04 | 301094 | SMF2A | Rural short | Feeder SMF2A - Planned | 24 | 172 | 4128 | 0.011943 | 6.9437e-05
2013-06-04 | 301097 | NGI1B | Rural short | LV Transformer SP3161-F NGI1B - Planned | 10 | 298 | 2980 | 0.0086218 | 2.8932e-05
2013-06-04 | 301098 | TGW1 | Rural short | LV Transformer SP1960-C TGW1 - Planned | 1 | 216 | 216 | 0.00062493 | 2.8932e-06
2013-06-04 | 301099 | RPN4A | Rural short | LV Transformer SP767404 RPN4A - Planned | 1 | 335 | 335 | 0.00096922 | 2.8932e-06
2013-06-04 | 301100 | TGW3 | Rural short | LV Transformer SP1235-E TGW3 - Planned | 4 | 346 | 1384 | 0.0040042 | 1.1573e-05
2013-06-04 | 301101 | STT3A | Rural short | Feeder STT3A - Planned | 11 | 154 | 1694 | 0.0049011 | 3.1825e-05
2013-06-04 | 301102 | MGP13A | Rural short | LV Transformer SP6324-C MGP13A - Planned | 23 | 349 | 8027 | 0.023224 | 6.6544e-05
2013-06-04 | 301103 | NIP5A | Urban | LV Transformer SG85-G NIP5A - Planned | 1 | 308 | 308 | 0.00030937 | 1.0044e-06
2013-06-04 | 301104 | KCY4 | Rural short | Feeder KCY4 - Planned | 73 | 381 | 27813 | 0.080469 | 0.0002112
2013-06-04 | 301105 | KWH1 | Rural short | Feeder KWH1 - Planned | 77.95 | 388 | 30244.6 | 0.087504 | 0.00022553
2013-06-04 | 301106 | EMD2 | Rural short | Feeder EMD2 - Planned | 77 | 357 | 27489 | 0.079531 | 0.00022278
2013-06-04 | 301107 | AMR3 | Rural short | LV Transformer SP7513-B AMR3 - Planned | 2 | 208 | 416 | 0.0012036 | 5.7864e-06
2013-06-04 | 301108 | GBN4 | Rural short | LV Transformer SP3926-C GBN4 - Planned | 7 | 332 | 2324 | 0.0067238 | 2.0252e-05
2013-06-04 | 301109 | TWT15A | Rural short | Feeder TWT15A - Planned | 31 | 125 | 3875 | 0.011211 | 8.9689e-05
2013-06-04 | 301110 | BBS11 | Urban | LV Transformer SC3657-F HPE3A - Planned | 2.38 | 403 | 959.14 | 0.0009634 | 2.3906e-06
2013-06-04 | 301110 | HPE3A | Urban | LV Transformer SC3657-F HPE3A - Planned | 44.315 | 403 | 17858.945 | 0.017938 | 4.4512e-05
2013-06-04 | 301112 | BDA12B | Urban | LV Transformer SP123-N BDA12B - Planned | 2.345 | 352 | 825.44 | 0.00082911 | 2.3554e-06
2013-06-04 | 301113 | GLY11A | Urban | LV Transformer SC1149-R GLY11A - Planned | 7.88 | 79 | 622.52 | 0.00062529 | 7.915e-06
2013-06-04 | 301114 | TWG17 | Urban | LV Transformer SP2217-L TWG17 - Planned | 27.6 | 349 | 9632.4 | 0.0096752 | 2.7723e-05
2013-06-04 | 301116 | SHW3 | Urban | LV Transformer SC765979 SHW3 - Planned | 19.025 | 294 | 5593.35 | 0.0056182 | 1.911e-05
2013-06-04 | 301117 | GLY2A | Urban | LV Transformer SC618948 GLY2A - Planned | 8.16 | 35 | 285.6 | 0.00028687 | 8.1963e-06
2013-06-04 | 301118 | INA2A | Urban | LV Transformer SC4789-G INA2A - Planned | 32.2259 | 331 | 10666.7729 | 0.010714 | 3.2369e-05
2013-06-04 | 301120 | GLY2A | Urban | LV Transformer SC618948 GLY2A - Planned | 5.44 | 35 | 190.4 | 0.00019125 | 5.4642e-06
2013-06-04 | 301122 | PWC2 | Rural short | LV Transformer SP9580-A PWC2 - Planned | 9.2 | 317 | 2916.4 | 0.0084377 | 2.6618e-05
2013-06-04 | 301123 | BHD35A | Rural short | LV Transformer SP5088-H BHD35A - Planned | 18 | 293 | 5274 | 0.015259 | 5.2078e-05
2013-06-04 | 301124 | MDR2A | Urban | LV Transformer SP2007-H MDR2A - Planned | 6.09 | 188 | 1144.92 | 0.00115 | 6.1171e-06
2013-06-04 | 301125 | SPO3A | Urban | LV Transformer SP6440-G SPO3A - Planned | 15.82 | 324 | 5125.68 | 0.0051485 | 1.589e-05
2013-06-04 | 301127 | SPO51A | Urban | LV Transformer SP2858-G SPO51A - Planned | 6.125 | 183 | 1120.875 | 0.0011259 | 6.1522e-06
2013-06-04 | 301128 | TGP8A | Urban | LV Transformer SP4167-J TGP8A - Planned | 18.22 | 100 | 1822 | 0.0018301 | 1.8301e-05
2013-06-04 | 301129 | NDH9 | Urban | LV Transformer SP785285 NDH9 - Planned | 8.82 | 180 | 1587.6 | 0.0015947 | 8.8592e-06
2013-06-04 | 301130 | KLG7A | Rural short | LV Transformer SC546590 KLG7A - Planned | 2.28 | 245 | 558.6 | 0.0016161 | 6.5965e-06
2013-06-04 | 301131 | TGP8A | Urban | LV Transformer SP3349-J TGP8A - Planned | 12 | 96 | 1152 | 0.0011571 | 1.2053e-05
2013-06-04 | 301132 | CFD2A | Urban | LV Transformer SP3396-F CFD2A - Planned | 32.215 | 190 | 6120.85 | 0.0061481 | 3.2358e-05
2013-06-04 | 301133 | SGT7 | Urban | LV Transformer SP1810-K SGT7 - Planned | 8.08 | 295 | 2383.6 | 0.0023942 | 8.1159e-06
2013-06-04 | 301134 | RHG6 | Urban | LV Transformer SP4237-H RHG6 - Planned | 1.42 | 302 | 428.84 | 0.00043075 | 1.4263e-06
2013-06-04 | 301135 | CPB8 | Rural short | LV Transformer SP4923-I CPB8 - Planned | 1.08 | 281 | 303.48 | 0.00087803 | 3.1247e-06
2013-06-04 | 301136 | BLB8B | Urban | LV Transformer SP4336-K BLB8B - Planned | 25.92 | 202 | 5235.84 | 0.0052591 | 2.6035e-05
2013-06-04 | 301138 | SPO11A | Urban | LV Transformer SP1114-L SPO11A - Planned | 34.41 | 23 | 791.43 | 0.00079495 | 3.4563e-05
2013-06-04 | 301139 | CFD6A | Urban | LV Transformer SP2668-L CFD6A - Planned | 6.3 | 23 | 144.9 | 0.00014554 | 6.328e-06
2013-06-04 | 301140 | NIP3A | Urban | LV Transformer SP3162-C NIP5A - Planned | 2.85 | 348 | 991.8 | 0.00099621 | 2.8627e-06
2013-06-04 | 301140 | NIP5A | Urban | LV Transformer SP3162-C NIP5A - Planned | 6.825 | 348 | 2375.1 | 0.0023857 | 6.8553e-06
2013-06-05 | 301156 | CBW11 | Rural short | LV Transformer SP4129-F CBW11 - Planned | 5 | 271 | 1355 | 0.0039208 | 1.4468e-05
2013-06-05 | 301173 | PRG1 | Rural short | LV Transformer SP2078-D PRG1 - Planned | 4.15 | 320 | 1328 | 0.0038426 | 1.2008e-05
2013-06-05 | 301174 | BNH1B | Rural short | Feeder BNH1B - Planned | 15 | 379 | 5685 | 0.01645 | 4.3403e-05
2013-06-05 | 301175 | SIS2 | Rural short | Feeder SIS2 - Planned | 186 | 416 | 77376 | 0.22389 | 0.0005382
2013-06-05 | 301176 | JBB13A | Rural short | Feeder JBB13A - Planned | 135.66 | 330 | 44767.8 | 0.12954 | 0.00039254
2013-06-05 | 301177 | MCW11 | Rural short | Feeder MCW11 - Planned | 91 | 478 | 43498 | 0.12586 | 0.00026331
2013-06-05 | 301178 | BRT8 | Urban | LV Transformer SP228-M BRT8 - Planned | 16.8 | 223 | 3746.4 | 0.0037627 | 1.6873e-05
2013-06-05 | 301179 | KCY5 | Rural short | LV Transformer SP13030-B KCY5 - Planned | 6.58 | 253 | 1664.74 | 0.004817 | 1.904e-05
2013-06-05 | 301180 | NMK17A | Urban | LV Transformer SP1373-J NMK17A - Planned | 3.045 | 262 | 797.79 | 0.00080127 | 3.0583e-06
2013-06-05 | 301181 | MLT2B | Urban | LV Transformer SP1597-M MLT2B - Planned | 62.895 | 213 | 13396.635 | 0.013455 | 6.3169e-05
2013-06-05 | 301182 | DRA6 | Urban | LV Transformer SP284-Q DRA6 - Planned | 2.92 | 217 | 633.64 | 0.0006364 | 2.9327e-06
2013-06-05 | 301183 | SHW3 | Urban | LV Transformer SP1315-N SHW3 - Planned | 33.205 | 434 | 14410.97 | 0.014474 | 3.335e-05
2013-06-05 | 301184 | KMR27A | Urban | LV Transformer SP412-P KMR27A - Planned | 8.97 | 292 | 2619.24 | 0.0026307 | 9.0091e-06
2013-06-05 | 301185 | EMD2 | Rural short | LV Transformer SP3480-A EMD2 - Planned | 4 | 21 | 84 | 0.00024306 | 1.1574e-05
2013-06-05 | 301186 | TCB2 | Rural short | LV Transformer SP5939-A TCB2 - Planned | 14.62 | 154 | 2251.48 | 0.0065148 | 4.2304e-05
2013-06-05 | 301187 | EMD2 | Rural short | LV Transformer SP4493-A EMD2 - Planned | 13 | 210 | 2730 | 0.0078994 | 3.7616e-05
2013-06-05 | 301188 | YDA2B | Rural short | LV Transformer SP1276-A YDA2B - Planned | 6.365 | 26 | 165.49 | 0.00047886 | 1.8418e-05
2013-06-05 | 301189 | SPO32A | Urban | LV Transformer SP1086-I SPO41A - Planned | 1.62 | 213 | 345.06 | 0.00034656 | 1.6271e-06
2013-06-05 | 301189 | SPO41A | Urban | LV Transformer SP1086-I SPO41A - Planned | 2.965 | 213 | 631.545 | 0.0006343 | 2.9779e-06
2013-06-05 | 301190 | CMA8A | Rural short | LV Transformer SP6912-C CMA8A - Planned | 3 | 241 | 723 | 0.002092 | 8.6807e-06
2013-06-05 | 301191 | RBA43A | Rural short | LV Transformer SP5110-G RBA43A - Planned | 14.07 | 358 | 5037.06 | 0.014575 | 4.0712e-05
2013-06-05 | 301192 | MGP2A | Urban | LV Transformer SP4170-G MGP2A - Planned | 6.93 | 297 | 2058.21 | 0.0020672 | 6.9602e-06
2013-06-05 | 301193 | BDT1 | Rural short | LV Transformer SP1805-E BDT1 - Planned | 29.025 | 368 | 10681.2 | 0.030907 | 8.3986e-05
2013-06-05 | 301193 | BDT5 | Rural short | LV Transformer SP1805-E BDT1 - Planned | 5.815 | 368 | 2139.92 | 0.006192 | 1.6826e-05
2013-06-05 | 301194 | PBH2B | Urban | LV Transformer SP4575-D PBH2B - Planned | 43.31 | 466 | 20182.46 | 0.02027 | 4.3499e-05
2013-06-05 | 301195 | HDA11A | Urban | LV Transformer SP3613-G HDA3A - Planned | 4.9 | 273 | 1337.7 | 0.0013435 | 4.9214e-06
2013-06-05 | 301195 | HDA3A | Urban | LV Transformer SP3613-G HDA3A - Planned | 20.65 | 273 | 5637.45 | 0.005662 | 2.074e-05
2013-06-05 | 301196 | NSW8A | Urban | LV Transformer SP3990-J NSW8A - Planned | 4.69 | 210 | 984.9 | 0.00098919 | 4.7104e-06
2013-06-05 | 301197 | BLB8B | Urban | LV Transformer SP569-P QPT5 - Planned | 5.94 | 196 | 1164.24 | 0.0011693 | 5.9659e-06
2013-06-05 | 301197 | QPT5 | Urban | LV Transformer SP569-P QPT5 - Planned | 24.48 | 196 | 4798.08 | 0.004819 | 2.4587e-05
2013-06-05 | 301198 | HPK6 | Urban | LV Transformer SC3066-I HPK6 - Planned | 2.02 | 25 | 50.5 | 5.072e-05 | 2.0288e-06
2013-06-05 | 301199 | CMA8A | Rural short | LV Transformer SP5479-C CMA8A - Planned | 23 | 456 | 10488 | 0.030348 | 6.6552e-05
2013-06-05 | 301200 | RPN6A | Rural short | LV Transformer SP13981-B RPN6A - Planned | 8.2 | 56 | 459.2 | 0.0013287 | 2.3727e-05
2013-06-05 | 301201 | RPN6A | Rural short | LV Transformer SP426492 RPN6A - Planned | 5.28 | 16 | 84.48 | 0.00024445 | 1.5278e-05
2013-06-05 | 301202 | NBR7A | Rural short | LV Transformer SP2021-A NBR7A - Planned | 10.85 | 339 | 3678.15 | 0.010643 | 3.1395e-05
2013-06-05 | 301409 | TCB1 | Rural short | Feeder TCB1 - Planned | 325.16 | 521 | 169408.36 | 0.49019 | 0.00094087
2013-06-05 | 301410 | GBN2 | Rural short | Feeder GBN2 - Planned | 59.724 | 362 | 21620.088 | 0.062559 | 0.00017282
2013-06-05 | 301418 | RWD1 | Rural short | Feeder RWD1 - Planned | 20 | 298 | 5960 | 0.017246 | 5.7871e-05
2013-06-06 | 301234 | RWD1 | Rural short | LV Transformer SP1208-G RWD1 - Planned | 3 | 65 | 195 | 0.00056431 | 8.6818e-06
2013-06-06 | 301235 | LGV3A | Rural short | LV Transformer SP9725-B LGV3A - Planned | 2 | 220 | 440 | 0.0012733 | 5.7878e-06
2013-06-06 | 301238 | TGW3 | Rural short | Feeder TGW3 - Planned | 36 | 303 | 10908 | 0.031567 | 0.00010418
2013-06-06 | 301239 | BDT5 | Rural short | LV Transformer SP10126-B BDT5 - Planned | 1 | 321 | 321 | 0.00092895 | 2.8939e-06
2013-06-06 | 301253 | BNH6A | Rural short | LV Transformer SP2717-E BNH6A - Planned | 1 | 133 | 133 | 0.00038489 | 2.8939e-06
2013-06-06 | 301273 | BNH6A | Rural short | LV Transformer SP12743-B BNH6A - Planned | 1 | 45 | 45 | 0.00013023 | 2.8939e-06
2013-06-06 | 301295 | PPE13A | Rural short | LV Transformer SP5585-C PPE13A - Planned | 3 | 252 | 756 | 0.0021878 | 8.6818e-06
2013-06-06 | 301296 | BRD5A | Rural short | Feeder BRD5A - Planned | 10.66 | 535 | 5703.1 | 0.016504 | 3.0849e-05
2013-06-06 | 301299 | CFD1A | Urban | LV Transformer SC4894-H CFD2A - Planned | 2.55 | 252 | 642.6 | 0.00064535 | 2.5609e-06
2013-06-06 | 301299 | CFD2A | Urban | LV Transformer SC4894-H CFD2A - Planned | 16.55 | 252 | 4170.6 | 0.0041884 | 1.6621e-05
2013-06-06 | 301301 | AGE8 | Urban | LV Transformer SC2172-N - Planned | 25.08 | 374 | 9379.92 | 0.00942 | 2.5187e-05
2013-06-06 | 301302 | SHW3 | Urban | LV Transformer SP3437-E SHW3 - Planned | 22.31 | 188 | 4194.28 | 0.0042122 | 2.2405e-05
2013-06-06 | 301303 | AGE3 | Urban | LV Transformer SP2297-H AGE3 - Planned | 52.4 | 310 | 16244 | 0.016313 | 5.2624e-05
2013-06-06 | 301303 | MLT2B | Urban | LV Transformer SP2297-H AGE3 - Planned | 2.34 | 310 | 725.4 | 0.0007285 | 2.35e-06
2013-06-06 | 301304 | SHW3 | Urban | LV Transformer SP2844-K SHW3 - Planned | 30.08 | 361 | 10858.88 | 0.010905 | 3.0209e-05
2013-06-06 | 301305 | NVL3 | Rural short | LV Transformer SP2353-E NVL3 - Planned | 13.02 | 105 | 1367.1 | 0.0039563 | 3.7679e-05
2013-06-06 | 301306 | AHD21 | Urban | LV Transformer SP14099-A MLB4A - Planned | 1.08 | 307 | 331.56 | 0.00033298 | 1.0846e-06
2013-06-06 | 301306 | MLB4A | Urban | LV Transformer SP14099-A MLB4A - Planned | 7.48 | 307 | 2296.36 | 0.0023062 | 7.512e-06
2013-06-06 | 301307 | CLD25A | Urban | LV Transformer SP2105-B CLD25A - Planned | 4.92 | 359 | 1766.28 | 0.0017738 | 4.941e-06
2013-06-06 | 301308 | HWL10A | Urban | LV Transformer SP3727-D HWL10A - Planned | 37.5175 | 274 | 10279.795 | 0.010324 | 3.7678e-05
2013-06-06 | 301309 | MGP1 | Rural short | LV Transformer SP1450-I MGP1 - Planned | 40 | 283 | 11320 | 0.032759 | 0.00011576
2013-06-06 | 301310 | CCY13A | Urban | LV Transformer SC341-J CCY13A - Planned | 21.3 | 556 | 11842.8 | 0.011893 | 2.1391e-05
2013-06-06 | 301311 | MGP13A | Rural short | LV Transformer SP1709-G MGP13A - Planned | 3.1 | 216 | 669.6 | 0.0019378 | 8.9712e-06
2013-06-06 | 301312 | TGP8A | Urban | LV Transformer SP1768-N TGP8A - Planned | 9.99 | 433 | 4325.67 | 0.0043442 | 1.0033e-05
2013-06-06 | 301313 | BRD5A | Rural short | LV Transformer SP100533-B BRD5A - Planned | 3.5 | 450 | 1575 | 0.0045579 | 1.0129e-05
2013-06-06 | 301314 | CFD2A | Urban | LV Transformer SP3396-F CFD2A - Planned | 39.795 | 262 | 10426.29 | 0.010471 | 3.9965e-05
2013-06-06 | 301315 | SGT7 | Urban | LV Transformer SP882-J SGT7 - Planned | 18.36 | 453 | 8317.08 | 0.0083526 | 1.8439e-05
2013-06-06 | 301316 | KLG5A | Rural short | LV Transformer SP4102-I KLG5A - Planned | 6.02 | 290 | 1745.8 | 0.0050522 | 1.7421e-05
2013-06-06 | 301317 | MLT24A | Urban | LV Transformer SC1734959 MLT24A - Planned | 10.465 | 340 | 3558.1 | 0.0035733 | 1.051e-05
2013-06-06 | 301318 | RCF10A | Urban | LV Transformer SP483947 RCF10A - Planned | 1.05 | 31 | 32.55 | 3.2689e-05 | 1.0545e-06
2013-06-06 | 301319 | MTG16A | Urban | LV Transformer SP2841-J MTG16A - Planned | 36.255 | 310 | 11239.05 | 0.011287 | 3.641e-05
2013-06-06 | 301320 | KSN1 | Urban | LV Transformer SP5564-D KSN1 - Planned | 12.21 | 245 | 2991.45 | 0.0030042 | 1.2262e-05
2013-06-06 | 301321 | MTG13A | Urban | LV Transformer SP1537-K MTG13A - Planned | 18.62 | 235 | 4375.7 | 0.0043944 | 1.87e-05
2013-06-06 | 301322 | ARG5A | Urban | LV Transformer SP4181-G ARG5A - Planned | 18.86 | 338 | 6374.68 | 0.0064019 | 1.8941e-05
2013-06-06 | 301323 | LWD1 | Rural short | LV Transformer SP806214 LWD1 - Planned | 0.99 | 542 | 536.58 | 0.0015528 | 2.865e-06
2013-06-06 | 301370 | TWG18 | Urban | LV Transformer SP1620-M TWG18 - Planned | 8.855 | 350 | 3099.25 | 0.0031125 | 8.8929e-06
2013-06-06 | 301405 | PWC4 | Rural short | LV Transformer SP5257-A PWC4 - Planned | 37.83 | 375 | 14186.25 | 0.041054 | 0.00010948
2013-06-06 | 301406 | GYM9B | Rural short | Feeder GYM9B - Planned | 32.8 | 340 | 11152 | 0.032273 | 9.4921e-05
2013-06-06 | 301407 | GYN3A | Rural short | LV Transformer SP10193-B GYN3A - Planned | 10 | 19 | 190 | 0.00054985 | 2.8939e-05
2013-06-06 | 301408 | GYM7A | Rural short | LV Transformer SP4-F GYM7A - Planned | 11 | 91 | 1001 | 0.0028968 | 3.1833e-05
2013-06-07 | 301335 | FDS3 | Rural short | LV Transformer SP14103-A FDS3 - Planned | 4 | 32 | 128 | 0.00037051 | 1.1579e-05
2013-06-07 | 301354 | RLB13B | Rural short | LV Transformer SP6195-C RLB13B - Planned | 5 | 185 | 925 | 0.0026775 | 1.4473e-05
2013-06-07 | 301355 | ESK5A | Rural short | Feeder ESK5A - Planned | 22.41 | 184 | 4123.44 | 0.011936 | 6.4869e-05
2013-06-07 | 301356 | WSE5A | Rural short | LV Transformer SP788347 WSE5A - Planned | 11 | 157 | 1727 | 0.004999 | 3.1841e-05
2013-06-07 | 301357 | KCY4 | Rural short | LV Transformer SP6134-E KCY4 - Planned | 3 | 227 | 681 | 0.0019712 | 8.6839e-06
2013-06-07 | 301358 | SMF5A | Rural short | LV Transformer SP6685-I SMF5A - Planned | 16 | 54 | 864 | 0.002501 | 4.6314e-05
2013-06-07 | 301360 | BNH6A | Rural short | Feeder BNH6A - Planned | 4 | 252 | 1008 | 0.0029178 | 1.1579e-05
2013-06-07 | 301362 | THL3 | Rural short | Feeder THL3 - Planned | 8 | 352 | 2816 | 0.0081513 | 2.3157e-05
2013-06-07 | 301363 | YTA22A | Rural short | LV Transformer SP746871 YTA22A - Planned | 1 | 375 | 375 | 0.0010855 | 2.8946e-06
2013-06-07 | 301367 | GLY3A | Urban | LV Transformer SP768897 GLY3A - Planned | 15.18 | 289 | 4387.02 | 0.0044052 | 1.5243e-05
2013-06-07 | 301368 | MGL5 | Urban | LV Transformer SC5053-J MGL5 - Planned | 2.08 | 97 | 201.76 | 0.0002026 | 2.0886e-06
2013-06-07 | 301369 | SMR12A | Urban | LV Transformer SC3962-F SMR12A - Planned | 10.01 | 137 | 1371.37 | 0.0013771 | 1.0052e-05
2013-06-07 | 301369 | SMR6A | Urban | LV Transformer SC3962-F SMR12A - Planned | 0.67 | 137 | 91.79 | 9.2171e-05 | 6.7278e-07
2013-06-07 | 301371 | SHW81 | Urban | LV Transformer SC1734731 SHW81 - Planned | 3.03 | 241 | 730.23 | 0.00073326 | 3.0426e-06
2013-06-07 | 301372 | AHD8 | Urban | LV Transformer SP683-A AHD8 - Planned | 6.93 | 430 | 2979.9 | 0.0029923 | 6.9587e-06
2013-06-07 | 301373 | NBR12A | Rural short | LV Transformer SP3756-A NBR12A - Planned | 37.44 | 177 | 6626.88 | 0.019182 | 0.00010837
2013-06-07 | 301374 | HWL3A | Urban | LV Transformer SP1207-M HWL3A - Planned | 8.19 | 203 | 1662.57 | 0.0016695 | 8.224e-06
2013-06-07 | 301375 | KRA7 | Urban | LV Transformer SP1741-G KRA7 - Planned | 16.065 | 138 | 2216.97 | 0.0022262 | 1.6132e-05
2013-06-07 | 301376 | PBH6 | Urban | LV Transformer SP2754-H PBH6 - Planned | 15.12 | 192 | 2903.04 | 0.0029151 | 1.5183e-05
2013-06-07 | 301377 | CMA20A | Urban | LV Transformer SC472888 CMA20A - Planned | 48.7 | 77 | 3749.9 | 0.0037655 | 4.8902e-05
2013-06-07 | 301378 | GLY12A | Urban | LV Transformer SP3340-F GLY12A - Planned | 24.96 | 211 | 5266.56 | 0.0052884 | 2.5064e-05
2013-06-07 | 301379 | CFD2A | Urban | LV Transformer SP3396-F CFD2A - Planned | 20.845 | 202 | 4210.69 | 0.0042282 | 2.0931e-05
2013-06-07 | 301380 | BRT8 | Urban | LV Transformer SP6039-E BRT8 - Planned | 9.72 | 298 | 2896.56 | 0.0029086 | 9.7603e-06
2013-06-07 | 301381 | SGT22A | Urban | LV Transformer SP3157-F SGT22A - Planned | 9 | 238 | 2142 | 0.0021509 | 9.0373e-06
2013-06-07 | 301382 | LTA3A | Urban | LV Transformer SP13061-G LTA3A - Planned | 1.06 | 160 | 169.6 | 0.0001703 | 1.0644e-06
2013-06-07 | 301383 | MTG5A | Urban | LV Transformer SP736310 MTG5A - Planned | 9.12 | 204 | 1860.48 | 0.0018682 | 9.1578e-06
2013-06-07 | 301384 | CPR4 | Urban | LV Transformer SP393-P CPR4 - Planned | 16.77 | 189 | 3169.53 | 0.0031827 | 1.684e-05
2013-06-07 | 301385 | BLBNFM6 | Urban | LV Transformer SP3112-H BLBNFM6 - Planned | 23.2 | 74 | 1716.8 | 0.0017239 | 2.3296e-05
2013-06-07 | 301386 | MTG5A | Urban | LV Transformer SP667-G MTG5A - Planned | 22 | 69 | 1518 | 0.0015243 | 2.2091e-05
2013-06-07 | 301387 | MTG4B | Urban | LV Transformer SP1071-M MTG4B - Planned | 1.1 | 150 | 165 | 0.00016568 | 1.1046e-06
2013-06-07 | 301388 | RWD1 | Rural short | LV Transformer SP1143-G RWD1 - Planned | 4 | 197 | 788 | 0.002281 | 1.1579e-05
2013-06-07 | 301403 | NBR11A | Rural short | LV Transformer SP453-B NBR11A - Planned | 17 | 267 | 4539 | 0.013139 | 4.9209e-05
2013-06-07 | 301404 | GBN4 | Rural short | LV Transformer SP7558-D GBN4 - Planned | 4 | 231 | 924 | 0.0026746 | 1.1579e-05
2013-06-08 | 301395 | RBK11B | Urban | LV Transformer SG428216 RBK11B - Planned | 1 | 146 | 146 | 0.00014659 | 1.0041e-06
2013-06-08 | 301401 | ZMR6A | Urban | LV Transformer SG1051469 ZMR6A - Planned | 1 | 480 | 480 | 0.00048195 | 1.0041e-06
2013-06-08 | 301411 | KBN5A | Rural short | LV Transformer SP13718-B KBN5A - Planned | 1 | 465 | 465 | 0.0013462 | 2.895e-06
2013-06-08 | 301412 | KBR3A | Rural short | Feeder KBR3A - Planned | 12.75 | 320 | 4080 | 0.011812 | 3.6911e-05
2013-06-08 | 301415 | AHD6 | Urban | LV Transformer SC22397-A - Planned | 9.72 | 26 | 252.72 | 0.00025375 | 9.7595e-06
2013-06-08 | 301416 | HDA14A | Urban | LV Transformer SP1080-I HDA14A - Planned | 7 | 564 | 3948 | 0.0039641 | 7.0285e-06
2013-06-09 | 301439 | WCL3 | Urban | LV Transformer SG7188-H WCL3 - Planned | 1 | 405 | 405 | 0.00040662 | 1.004e-06
2013-06-09 | 301442 | CVL13A | Urban | Feeder CVL13A - Planned | 2 | 431 | 862 | 0.00086545 | 2.008e-06
2013-06-09 | 301443 | CRB25A | Rural short | Feeder CRB25A - Planned | 27.45 | 486 | 13340.7 | 0.038625 | 7.9476e-05
2013-06-09 | 301444 | GLY15A | Urban | LV Transformer SP2658-M GLY15A - Planned | 2.46 | 426 | 1047.96 | 0.0010522 | 2.4698e-06
2013-06-11 | 301514 | KBR2A | Rural short | LV Transformer SP809-E KBR2A - Planned | 4 | 250 | 1000 | 0.0028951 | 1.158e-05
2013-06-11 | 301516 | LBH6A | Rural short | Feeder LBH6A - Planned | 27 | 309 | 8343 | 0.024154 | 7.8168e-05
2013-06-11 | 301553 | PPE13A | Rural short | LV Transformer SC2039359 PPE13A - Planned | 5.6 | 188 | 1052.8 | 0.003048 | 1.6213e-05
2013-06-11 | 301554 | STL2 | Urban | LV Transformer SC3117-L STL2 - Planned | 46.03 | 391 | 17997.73 | 0.018068 | 4.6209e-05
2013-06-11 | 301555 | KMR22A | Urban | LV Transformer SP2598-M KMR22A - Planned | 8.46 | 266 | 2250.36 | 0.0022591 | 8.493e-06
2013-06-11 | 301556 | CRB25A | Rural short | LV Transformer SP5759-E CRB25A - Planned | 4.25 | 320 | 1360 | 0.0039373 | 1.2304e-05
2013-06-11 | 301557 | HWL3A | Urban | LV Transformer SP1083398 HWL3A - Planned | 5.1 | 351 | 1790.1 | 0.0017971 | 5.1199e-06
2013-06-11 | 301558 | SGT4 | Urban | LV Transformer SP1612-J SGT7 - Planned | 22.48 | 158 | 3551.84 | 0.0035657 | 2.2568e-05
2013-06-11 | 301558 | SGT7 | Urban | LV Transformer SP1612-J SGT7 - Planned | 1.365 | 158 | 215.67 | 0.00021651 | 1.3703e-06
2013-06-11 | 301559 | TGP8A | Urban | LV Transformer SC2213-M TGP8A - Planned | 2.61 | 239 | 623.79 | 0.00062622 | 2.6202e-06
2013-06-11 | 301560 | BRT6 | Urban | LV Transformer SP3975-G BRT6 - Planned | 31.605 | 210 | 6637.05 | 0.0066629 | 3.1728e-05
2013-06-11 | 301561 | ALY5 | Urban | LV Transformer SP4170-I ALY5 - Planned | 15.995 | 261 | 4174.695 | 0.004191 | 1.6057e-05
2013-06-11 | 301562 | NMK10 | Urban | LV Transformer SC5372-G NMK10 - Planned | 2 | 30 | 60 | 6.0234e-05 | 2.0078e-06
2013-06-11 | 301563 | MSV2 | Rural short | LV Transformer SP3091-C MSV2 - Planned | 4 | 78 | 312 | 0.00090327 | 1.158e-05
2013-06-11 | 301570 | WNM5 | Urban | LV Transformer SP821-N WNM5 - Planned | 20.24 | 530 | 10727.2 | 0.010769 | 2.0319e-05
2013-06-11 | 301571 | KMR22A | Urban | LV Transformer SP2525-L KMR22A - Planned | 2 | 510 | 1020 | 0.001024 | 2.0078e-06
2013-06-11 | 301653 | NBR12A | Rural short | LV Transformer SP4539-A NBR12A - Planned | 5 | 185 | 925 | 0.002678 | 1.4475e-05
2013-06-11 | 301935 | TGW1 | Rural short | Feeder TGW1 - Planned | 22.53 | 390 | 8786.7 | 0.025438 | 6.5227e-05
2013-06-12 | 301593 | CPD1 | Rural short | LV Transformer SP4777-B CPD1 - Planned | 4 | 19 | 76 | 0.00022002 | 1.158e-05
2013-06-12 | 301616 | MAI17 | Urban | LV Transformer SP64376-D MAI17 - Planned | 8.0406 | 58 | 466.3548 | 0.00046816 | 8.0716e-06
2013-06-12 | 301619 | LGV6A | Rural short | Feeder LGV6A - Planned | 33 | 200 | 6600 | 0.019107 | 9.5534e-05
2013-06-12 | 301620 | RLB13B | Rural short | Feeder RLB13B - Planned | 3 | 343 | 1029 | 0.0029789 | 8.6849e-06
2013-06-12 | 301633 | CBW11 | Rural short | Feeder CBW11 - Planned | 49 | 348 | 17052 | 0.049365 | 0.00014185
2013-06-12 | 301634 | BDT5 | Rural short | Feeder BDT5 - Planned | 9 | 310 | 2790 | 0.0080769 | 2.6055e-05
2013-06-12 | 301635 | RWD1 | Rural short | Feeder RWD1 - Planned | 10.8 | 330 | 3564 | 0.010318 | 3.1266e-05
2013-06-12 | 301636 | LRE8A | Rural short | LV Transformer SP15332-B LRE8A - Planned | 37 | 390 | 14430 | 0.041774 | 0.00010711
2013-06-12 | 301658 | AHL6A | Urban | LV Transformer SC4032-L AHL6A - Planned | 20.9 | 265 | 5538.5 | 0.0055599 | 2.0981e-05
2013-06-12 | 301659 | SHW4 | Urban | LV Transformer SP1426-P SHW4 - Planned | 35.85 | 364 | 13049.4 | 0.0131 | 3.5988e-05
2013-06-12 | 301660 | HWD5B | Urban | LV Transformer SC1435594 HWD5B - Planned | 2.25 | 54 | 121.5 | 0.00012197 | 2.2587e-06
2013-06-12 | 301661 | CSE10 | Urban | LV Transformer SP411-P CSE10 - Planned | 13.95 | 175 | 2441.25 | 0.0024507 | 1.4004e-05
2013-06-12 | 301662 | SHW3 | Urban | LV Transformer SP1315-N SHW3 - Planned | 17.89 | 220 | 3935.8 | 0.003951 | 1.7959e-05
2013-06-12 | 301663 | TCB1 | Rural short | LV Transformer SP6745-C TCB1 - Planned | 12.22 | 328 | 4008.16 | 0.011603 | 3.5376e-05
2013-06-12 | 301664 | GBN4 | Rural short | LV Transformer SP5591-B GBN4 - Planned | 6 | 76 | 456 | 0.0013201 | 1.737e-05
2013-06-12 | 301665 | GBN2 | Rural short | LV Transformer SP23-E GBN2 - Planned | 9 | 42 | 378 | 0.0010943 | 2.6055e-05
2013-06-12 | 301666 | MLB3A | Rural short | LV Transformer SC1820928 MLB3A - Planned | 6.11 | 101 | 617.11 | 0.0017865 | 1.7688e-05
2013-06-12 | 301667 | MLB3A | Rural short | LV Transformer SC1821258 MLB3A - Planned | 1.82 | 126 | 229.32 | 0.00066387 | 5.2688e-06
2013-06-12 | 301668 | CMA8A | Rural short | LV Transformer SP5479-C CMA8A - Planned | 14.03 | 158 | 2216.74 | 0.0064174 | 4.0616e-05
2013-06-12 | 301669 | CRB24B | Urban | LV Transformer SP1108-J CRB24B - Planned | 5.44 | 100 | 544 | 0.0005461 | 5.461e-06
2013-06-12 | 301670 | MDR2A | Urban | LV Transformer SP2007-H MDR2A - Planned | 24.39 | 360 | 8780.4 | 0.0088143 | 2.4484e-05
2013-06-12 | 301671 | SPD4A | Urban | LV Transformer SC368-J SPD5A - Planned | 40.31 | 147 | 5925.57 | 0.0059484 | 4.0466e-05
2013-06-12 | 301672 | CCY8A | Rural short | LV Transformer SC1272-H CCY8A - Planned | 17.25 | 494 | 8521.5 | 0.024669 | 4.9938e-05
2013-06-12 | 301673 | CFD2A | Urban | LV Transformer SP3396-F CFD2A - Planned | 39.795 | 320 | 12734.4 | 0.012784 | 3.9949e-05
2013-06-12 | 301675 | CFD1A | Urban | LV Transformer SP3613-G HDA3A - Planned | 2.34 | 70 | 163.8 | 0.00016443 | 2.349e-06
2013-06-12 | 301675 | HDA3A | Urban | LV Transformer SP3613-G HDA3A - Planned | 23.6 | 70 | 1652 | 0.0016584 | 2.3691e-05
2013-06-12 | 301676 | HDA11A | Urban | LV Transformer SP9502-F HDA11A - Planned | 26.13 | 408 | 10661.04 | 0.010702 | 2.6231e-05
2013-06-12 | 301677 | ARG5A | Urban | LV Transformer SP2368-L ARG5A - Planned | 2.01 | 84 | 168.84 | 0.00016949 | 2.0178e-06
2013-06-12 | 301678 | MRK3 | Urban | LV Transformer SP33622-D MRK3 - Planned | 15.73 | 265 | 4168.45 | 0.0041845 | 1.5791e-05
2013-06-12 | 301679 | SBK11 | Urban | LV Transformer SP3163-K SBK11 - Planned | 10.02 | 290 | 2905.8 | 0.002917 | 1.0059e-05
2013-06-12 | 301681 | THL3 | Rural short | LV Transformer SP917-B THL3 - Planned | 9 | 163 | 1467 | 0.0042469 | 2.6055e-05
2013-06-12 | 301682 | BNH1B | Rural short | LV Transformer SP5257-C BNH1B - Planned | 26 | 119 | 3094 | 0.008957 | 7.5269e-05
2013-06-12 | 301936 | SGT7 | Urban | LV Transformer SP5283-G SGT7 - Planned | 60 | 440 | 26400 | 0.026502 | 6.0232e-05
2013-06-13 | 301695 | NRA12A | Urban | LV Transformer SP4658-F NRA12A - Planned | 1 | 109 | 109 | 0.00010941 | 1.0038e-06
2013-06-13 | 301753 | MGP13A | Rural short | LV Transformer SP5273-G MGP13A - Planned | 10 | 341 | 3410 | 0.009873 | 2.8953e-05
2013-06-13 | 301773 | TGW2 | Rural short | Feeder TGW2 - Planned | 37.8 | 346 | 13078.8 | 0.037867 | 0.00010944
2013-06-13 | 301774 | BLH9B | Urban | LV Transformer SC247-E BLH9B - Planned | 100 | 360 | 36000 | 0.036136 | 0.00010038
2013-06-13 | 301775 | RLB16A | Rural short | Feeder RLB16A - Planned | 2 | 448 | 896 | 0.0025942 | 5.7906e-06
2013-06-13 | 301776 | BHD35A | Rural short | LV Transformer SP2511-H BHD35A - Planned | 24 | 490 | 11760 | 0.034049 | 6.9488e-05
2013-06-13 | 301778 | WMR1 | Rural short | Feeder WMR1 - Planned | 29 | 433 | 12557 | 0.036357 | 8.3964e-05
2013-06-13 | 301780 | AGE3 | Urban | LV Transformer SP3882-G AGE3 - Planned | 22.89 | 355 | 8125.95 | 0.0081566 | 2.2976e-05
2013-06-13 | 301780 | MLT15B | Urban | LV Transformer SP3882-G AGE3 - Planned | 62.75 | 355 | 22276.25 | 0.02236 | 6.2987e-05
2013-06-13 | 301780 | MLT2B | Urban | LV Transformer SP3882-G AGE3 - Planned | 3.9 | 355 | 1384.5 | 0.0013897 | 3.9147e-06
2013-06-13 | 301781 | AHL11A | Urban | LV Transformer SP531976 AHL11A - Planned | 56 | 50 | 2800 | 0.0028106 | 5.6211e-05
2013-06-13 | 301782 | GLY2A | Urban | LV Transformer SC690165 GLY2A - Planned | 10.88 | 201 | 2186.88 | 0.0021951 | 1.0921e-05
2013-06-13 | 301783 | SMF1B | Rural short | LV Transformer SP16059-E SMF1B - Planned | 11 | 36 | 396 | 0.0011465 | 3.1848e-05
2013-06-13 | 301784 | TWG11 | Urban | LV Transformer SP5072-J TWG11 - Planned | 18.4759 | 88 | 1625.8792 | 0.001632 | 1.8546e-05
2013-06-13 | 301785 | ENG2 | Urban | LV Transformer SC776339 ENG2 - Planned | 10.08 | 249 | 2509.92 | 0.0025194 | 1.0118e-05
2013-06-13 | 301786 | TCB2 | Rural short | LV Transformer SP5939-A TCB2 - Planned | 13.76 | 94 | 1293.44 | 0.0037449 | 3.984e-05
2013-06-13 | 301787 | TCB1 | Rural short | LV Transformer SP48392-A TCB1 - Planned | 32.29 | 410 | 13238.9 | 0.038331 | 9.349e-05
2013-06-13 | 301788 | BDT1 | Rural short | LV Transformer SP1805-E BDT1 - Planned | 29.025 | 451 | 13090.275 | 0.037901 | 8.4037e-05
2013-06-13 | 301789 | HWL3A | Urban | LV Transformer SP6468-F HWL3A - Planned | 28.4925 | 340 | 9687.45 | 0.009724 | 2.86e-05
2013-06-13 | 301790 | BHL6A | Urban | LV Transformer SC5012-I BHL6A - Planned | 11.585 | 372 | 4309.62 | 0.0043259 | 1.1629e-05
2013-06-13 | 301791 | SGT24A | Urban | LV Transformer SP11450-G SGT24A - Planned | 10.9 | 254 | 2768.6 | 0.0027791 | 1.0941e-05
2013-06-13 | 301792 | CFD2A | Urban | LV Transformer SP3396-F CFD2A - Planned | 20.845 | 203 | 4231.535 | 0.0042475 | 2.0924e-05
2013-06-13 | 301793 | KLG11A | Urban | LV Transformer SC1050378 KLG11A - Planned | 5.2 | 213 | 1107.6 | 0.0011118 | 5.2196e-06
2013-06-13 | 301794 | HDA11A | Urban | LV Transformer SC1064267 HDA11A - Planned | 5.38 | 231 | 1242.78 | 0.0012475 | 5.4003e-06
2013-06-13 | 301795 | BRD13A | Urban | LV Transformer SC547815 BRD13A - Planned | 2.7 | 330 | 891 | 0.00089436 | 2.7102e-06
2013-06-13 | 301796 | RLB11B | Urban | LV Transformer SC526128 RLB11B - Planned | 6.3 | 82 | 516.6 | 0.00051855 | 6.3238e-06
2013-06-13 | 301796 | RLB13B | Rural short | LV Transformer SC526128 RLB11B - Planned | 6.2 | 82 | 508.4 | 0.001472 | 1.7951e-05
2013-06-13 | 301798 | CHL10 | Urban | LV Transformer SP25288-E CHL10 - Planned | 5.68 | 305 | 1732.4 | 0.0017389 | 5.7014e-06
2013-06-13 | 301799 | RLB11B | Urban | LV Transformer SC526128 RLB11B - Planned | 5.02 | 78 | 391.56 | 0.00039304 | 5.039e-06
2013-06-13 | 301800 | CPL26A | Urban | LV Transformer SP61450-C CPL26A - Planned | 18.24 | 214 | 3903.36 | 0.0039181 | 1.8309e-05
2013-06-13 | 301801 | RCN10A | Urban | LV Transformer SC5847-E RCN10A - Planned | 2.12 | 123 | 260.76 | 0.00026174 | 2.128e-06
2013-06-13 | 301804 | RPN6A | Rural short | LV Transformer SP3561-D RPN6A - Planned | 20.33 | 185 | 3761.05 | 0.010889 | 5.8862e-05
2013-06-13 | 301805 | RPN6A | Rural short | LV Transformer SP51143-D RPN6A - Planned | 2.12 | 90 | 190.8 | 0.00055243 | 6.1381e-06
2013-06-14 | 301853 | TGW3 | Rural short | LV Transformer SP1990-A TGW3 - Planned | 2.01 | 264 | 530.64 | 0.0015365 | 5.8202e-06
2013-06-14 | 301855 | FDS3 | Rural short | Feeder FDS3 - Planned | 26 | 356 | 9256 | 0.026802 | 7.5286e-05
2013-06-14 | 301856 | WMR1 | Rural short | Feeder WMR1 - Planned | 27 | 255 | 6885 | 0.019936 | 7.8182e-05
2013-06-14 | 301857 | RLB13B | Rural short | Feeder RLB13B - Planned | 3 | 391 | 1173 | 0.0033966 | 8.6868e-06
2013-06-14 | 301874 | TCB1 | Rural short | Feeder TCB1 - Planned | 104.04 | 454 | 47234.16 | 0.13677 | 0.00030126
2013-06-14 | 301875 | GBN4 | Rural short | Feeder GBN4 - Planned | 43.52 | 291 | 12664.32 | 0.036671 | 0.00012602
2013-06-14 | 301893 | CRB25A | Rural short | LV Transformer SP4493-F CRB25A - Planned | 47 | 440 | 20680 | 0.059881 | 0.00013609
2013-06-14 | 301894 | KBN5A | Rural short | LV Transformer SP8559-A KBN5A - Planned | 1 | 554 | 554 | 0.0016042 | 2.8956e-06
2013-06-14 | 301897 | CMA20A | Urban | LV Transformer SC2068687 CMA20A - Planned | 3 | 146 | 438 | 0.00043962 | 3.0111e-06
2013-06-14 | 301898 | SHW3 | Urban | LV Transformer SC765979 SHW3 - Planned | 29.67 | 241 | 7150.47 | 0.0071769 | 2.978e-05
2013-06-14 | 301900 | AGE10 | Urban | LV Transformer SP30520-E AGE10 - Planned | 35.69 | 154 | 5496.26 | 0.0055166 | 3.5822e-05
2013-06-14 | 301900 | TWG11 | Urban | LV Transformer SP30520-E AGE10 - Planned | 0.72 | 154 | 110.88 | 0.00011129 | 7.2266e-07
2013-06-14 | 301901 | GAP1A | Urban | LV Transformer SC4840-J GAP1A - Planned | 6.12 | 268 | 1640.16 | 0.0016462 | 6.1426e-06
2013-06-14 | 301902 | NMK26 | Urban | LV Transformer SP3387-F NMK26 - Planned | 18.27 | 86 | 1571.22 | 0.001577 | 1.8337e-05
2013-06-14 | 301903 | GBN4 | Rural short | LV Transformer SP6493-D GBN4 - Planned | 8 | 155 | 1240 | 0.0035906 | 2.3165e-05
2013-06-14 | 301904 | BDL4 | Urban | LV Transformer SP2679-F BDL4 - Planned | 12.9 | 243 | 3134.7 | 0.0031463 | 1.2948e-05
2013-06-14 | 301905 | PBH6 | Urban | LV Transformer SP3012-F PBH6 - Planned | 12.76 | 203 | 2590.28 | 0.0025998 | 1.2807e-05
2013-06-14 | 301906 | CNB26A | Rural short | LV Transformer SP11692-C CNB26A - Planned | 12 | 42 | 504 | 0.0014594 | 3.4747e-05
2013-06-14 | 301907 | HWL3A | Urban | LV Transformer SP1207-M HWL3A - Planned | 17.64 | 291 | 5133.24 | 0.0051522 | 1.7705e-05
2013-06-14 | 301908 | TGP8A | Urban | LV Transformer SP9663-I TGP8A - Planned | 8.4 | 257 | 2158.8 | 0.0021668 | 8.431e-06
2013-06-14 | 301909 | ENG7 | Urban | LV Transformer SP30879-E ENG7 - Planned | 3.28 | 258 | 846.24 | 0.00084937 | 3.2921e-06
2013-06-14 | 301910 | ZMR6A | Urban | LV Transformer SP1978-G ZMR6A - Planned | 9.4 | 366 | 3440.4 | 0.0034531 | 9.4347e-06
2013-06-14 | 301911 | CFD2A | Urban | LV Transformer SP3396-F CFD2A - Planned | 20.845 | 244 | 5086.18 | 0.005105 | 2.0922e-05
2013-06-14 | 301912 | KLG11A | Urban | LV Transformer SP5885-B KLG11A - Planned | 24.65 | 220 | 5423 | 0.005443 | 2.4741e-05
2013-06-14 | 301913 | CLD30A | Urban | LV Transformer SP1289-B CLD30A - Planned | 5.535 | 102 | 564.57 | 0.00056666 | 5.5554e-06
2013-06-14 | 301915 | MRK5A | Urban | LV Transformer SP1292-L MRK5A - Planned | 13.975 | 291 | 4066.725 | 0.0040817 | 1.4027e-05
2013-06-14 | 301916 | BPN29A | Urban | LV Transformer SP7303-G BPN29A - Planned | 16.92 | 240 | 4060.8 | 0.0040758 | 1.6982e-05
2013-06-14 | 301917 | JBB4A | Urban | LV Transformer SP99887-B JBB4A - Planned | 4.8 | 38 | 182.4 | 0.00018307 | 4.8177e-06
2013-06-14 | 301919 | LWD1 | Rural short | LV Transformer SP806214 LWD1 - Planned | 0.99 | 310 | 306.9 | 0.00088866 | 2.8667e-06
2013-06-14 | 301920 | CVL17A | Urban | LV Transformer SP6176-C CVL17A - Planned | 78 | 41 | 3198 | 0.0032098 | 7.8288e-05
2013-06-14 | 301937 | CBAT1 | CBD | LV Transformer SSCBA CBAT1 - Planned | 1.08 | 2 | 2.16 | 0.00057333 | 0.00028667
2013-06-14 | 301940 | CHL10 | Urban | LV Transformer SP25288-E CHL10 - Planned | 9.36 | 165 | 1544.4 | 0.0015501 | 9.3946e-06
2013-06-14 | 301941 | CPB6 | Urban | LV Transformer SC723-E CPB6 - Planned | 48 | 1160 | 55680 | 0.055886 | 4.8177e-05
2013-06-15 | 301939 | SGT4 | Urban | LV Transformer SP2593-I SGT4 - Planned | 21.45 | 342 | 7335.9 | 0.0073624 | 2.1528e-05
2013-06-15 | 301942 | RHG6 | Urban | LV Transformer SP4237-H RHG6 - Planned | 1 | 270 | 270 | 0.00027098 | 1.0036e-06
2013-06-16 | 301951 | GBG24A | Urban | Feeder GBG24A - Planned | 1.8 | 415 | 747 | 0.00074966 | 1.8064e-06
2013-06-16 | 301952 | BLH11B | Urban | LV Transformer SC981-G BLH11B - Planned | 67 | 370 | 24790 | 0.024878 | 6.7239e-05
2013-06-16 | 301956 | MLT24A | Urban | LV Transformer SC1734959 MLT24A - Planned | 47.52 | 219 | 10406.88 | 0.010444 | 4.7689e-05
2013-06-16 | 301957 | TWG18 | Urban | LV Transformer SG6012-H TWG18 - Planned | 10.66 | 80 | 852.8 | 0.00085584 | 1.0698e-05
2013-06-16 | 301958 | NMK26 | Urban | LV Transformer SP16117-G NMK26 - Planned | 102.25 | 295 | 30163.75 | 0.030271 | 0.00010261
2013-06-16 | 301959 | SPO61A | Urban | LV Transformer SP2296-E SPO61A - Planned | 6.4 | 259 | 1657.6 | 0.0016635 | 6.4228e-06
2013-06-16 | 301960 | BHD20A | Urban | LV Transformer SP770101 BHD20A - Planned | 27 | 288 | 7776 | 0.0078037 | 2.7096e-05
2013-06-16 | 301961 | CFD1A | Urban | LV Transformer SP9695-H CFD1A - Planned | 10.65 | 270 | 2875.5 | 0.0028857 | 1.0688e-05
2013-06-16 | 301962 | HDA10A | Urban | LV Transformer SP3769-F HDA10A - Planned | 14.58 | 361 | 5263.38 | 0.0052821 | 1.4632e-05
2013-06-16 | 301963 | WHO1 | Rural short | LV Transformer SP68267-A WHO1 - Planned | 17 | 390 | 6630 | 0.019201 | 4.9233e-05
2013-06-17 | 301978 | CBW11 | Rural short | Feeder CBW11, WMR3 - Planned | 5 | 335 | 1675 | 0.0048514 | 1.4482e-05
2013-06-17 | 301978 | WMR3 | Rural short | Feeder CBW11, WMR3 - Planned | 2 | 335 | 670 | 0.0019406 | 5.7927e-06
2013-06-17 | 301979 | PRG2B | Rural short | LV Transformer SP3349-B PRG2B - Planned | 5 | 290 | 1450 | 0.0041997 | 1.4482e-05
2013-06-17 | 301981 | THL3 | Rural short | LV Transformer SP16807-B THL3 - Planned | 4 | 352 | 1408 | 0.0040781 | 1.1585e-05
2013-06-17 | 301982 | MCW7 | Rural short | LV Transformer SP4279-F MCW7 - Planned | 3 | 272 | 816 | 0.0023634 | 8.6891e-06
2013-06-17 | 301993 | BRD11A | Rural short | Feeder BRD11A - Planned | 18 | 510 | 9180 | 0.026589 | 5.2135e-05
2013-06-17 | 301995 | NBR7A | Rural short | LV Transformer SP4434-A NBR7A - Planned | 15.98 | 351 | 5608.98 | 0.016246 | 4.6284e-05
2013-06-17 | 301996 | MLY1 | Rural short | LV Transformer SP9689-A MLY1 - Planned | 8.01 | 242 | 1938.42 | 0.0056144 | 2.32e-05
2013-06-17 | 301997 | NBR15A | Rural short | LV Transformer SP5216-A NBR15A - Planned | 18 | 203 | 3654 | 0.010583 | 5.2135e-05
2013-06-17 | 301998 | SPD5A | Urban | LV Transformer SG229-G SPD5A - Planned | 126 | 513 | 64638 | 0.064861 | 0.00012643
2013-06-17 | 302003 | CMD7A | Rural short | LV Transformer SC1510624 CMD7A - Planned | 1.04 | 425 | 442 | 0.0012802 | 3.0122e-06
2013-06-17 | 302004 | NBR7A | Rural short | LV Transformer SP2118-A NBR7A - Planned | 8.04 | 291 | 2339.64 | 0.0067765 | 2.3287e-05
2013-06-17 | 302005 | BBH8A | Urban | LV Transformer SP4560-G BBH8A - Planned | 18.04 | 277 | 4997.08 | 0.0050143 | 1.8102e-05
2013-06-17 | 302006 | SPO60A | Urban | LV Transformer SP4211-G SPO60A - Planned | 2.99 | 196 | 586.04 | 0.00058806 | 3.0003e-06
2013-06-17 | 302007 | HDA3A | Urban | LV Transformer SP6607-I HDA3A - Planned | 17.28 | 116 | 2004.48 | 0.0020114 | 1.734e-05
2013-06-17 | 302008 | CFD2A | Urban | LV Transformer SP3396-F CFD2A - Planned | 20.845 | 213 | 4439.985 | 0.0044553 | 2.0917e-05
2013-06-17 | 302009 | HTN22B | Urban | LV Transformer SC781186 HTN22B - Planned | 9.25 | 284 | 2627 | 0.0026361 | 9.2819e-06
2013-06-17 | 302010 | ALY5 | Urban | LV Transformer SG1945-I ALY5 - Planned | 15.345 | 323 | 4956.435 | 0.0049735 | 1.5398e-05
2013-06-17 | 302011 | TRP1 | Rural short | LV Transformer SP754982 TRP1 - Planned | 4.33 | 202 | 874.66 | 0.0025333 | 1.2541e-05
2013-06-17 | 302012 | BNH1B | Rural short | LV Transformer SP5257-C BNH1B - Planned | 26 | 204 | 5304 | 0.015362 | 7.5306e-05
2013-06-17 | 302013 | CPD1 | Rural short | LV Transformer SP2651-C CPD1 - Planned | 8 | 53 | 424 | 0.0012281 | 2.3171e-05
2013-06-18 | 302034 | CRB25A | Rural short | LV Transformer SC1410581 CRB25A - Planned | 88.5 | 52 | 4602 | 0.01333 | 0.00025635
2013-06-18 | 302039 | CRB25A | Rural short | LV Transformer SC1411581 CRB25A - Planned | 11 | 48 | 528 | 0.0015294 | 3.1863e-05
2013-06-18 | 302040 | BNH1B | Rural short | Feeder BNH1B - Planned | 15 | 304 | 4560 | 0.013209 | 4.3449e-05
2013-06-18 | 302044 | THL1 | Rural short | LV Transformer SP3155-B THL1 - Planned | 3 | 281 | 843 | 0.0024419 | 8.6899e-06
2013-06-18 | 302046 | BHD41A | Urban | LV Transformer SP6386-C BHD41A - Planned | 20 | 421 | 8420 | 0.0084483 | 2.0067e-05
2013-06-18 | 302050 | GBN4 | Rural short | Feeder GBN4 - Planned | 47 | 172 | 8084 | 0.023416 | 0.00013614
2013-06-18 | 302051 | NBR11A | Rural short | LV Transformer SP2112-A NBR11A - Planned | 19.95 | 185 | 3690.75 | 0.010691 | 5.7788e-05
2013-06-18 | 302052 | PWC5 | Rural short | LV Transformer SP305-A PWC5 - Planned | 23.04 | 147 | 3386.88 | 0.0098105 | 6.6738e-05
2013-06-18 | 302054 | BHD41A | Urban | LV Transformer SP5206-I BHD41A - Planned | 7.04 | 290 | 2041.6 | 0.0020485 | 7.0637e-06
2013-06-18 | 302055 | VPT13A | Rural short | LV Transformer SC1486039 VPT13A - Planned | 11.74 | 387 | 4543.38 | 0.01316 | 3.4006e-05
2013-06-18 | 302056 | GAP9A | Urban | LV Transformer SP2578-N GAP9A - Planned | 16.8 | 56 | 940.8 | 0.00094396 | 1.6856e-05
2013-06-18 | 302057 | CSE4 | Urban | LV Transformer SP3220-L CSE4 - Planned | 21.9 | 283 | 6197.7 | 0.0062185 | 2.1974e-05
2013-06-18 | 302058 | AGE6A | Urban | LV Transformer SC6100-G AGE6A - Planned | 50.63 | 318 | 16100.34 | 0.016154 | 5.08e-05
2013-06-18 | 302059 | CSE10 | Urban | LV Transformer SP4395-K CSE10 - Planned | 31.9749 | 300 | 9592.47 | 0.0096247 | 3.2082e-05
2013-06-18 | 302060 | AHD8 | Urban | LV Transformer SP7722-A AHD8 - Planned | 32.2 | 435 | 14007 | 0.014054 | 3.2308e-05
2013-06-18 | 302061 | WMD14A | Rural short | LV Transformer SC740018 WMD14A - Planned | 8.88 | 165 | 1465.2 | 0.0042441 | 2.5722e-05
2013-06-18 | 302062 | PWC4 | Rural short | LV Transformer SP2115-A PWC4 - Planned | 6.08 | 150 | 912 | 0.0026417 | 1.7611e-05
2013-06-18 | 302063 | BMT3 | Rural short | LV Transformer SC173398 BMT3 - Planned | 41.16 | 45 | 1852.2 | 0.0053651 | 0.00011923
2013-06-18 | 302064 | CLM8 | Urban | LV Transformer SP6675-A CLM8 - Planned | 12 | 111 | 1332 | 0.0013365 | 1.204e-05
2013-06-18 | 302065 | CLM6 | Urban | LV Transformer SP5191-A CLM6 - Planned | 51.33 | 187 | 9598.71 | 0.009631 | 5.1502e-05
2013-06-18 | 302066 | CRB15A | Urban | LV Transformer SP2704-F CRB15A - Planned | 26.28 | 285 | 7489.8 | 0.007515 | 2.6368e-05
2013-06-18 | 302066 | CRB22A | Urban | LV Transformer SP2704-F CRB15A - Planned | 2.94 | 285 | 837.9 | 0.00084071 | 2.9499e-06
2013-06-18 | 302067 | BTA15A | Urban | LV Transformer SP9760-B BTA15A - Planned | 6.635 | 338 | 2242.63 | 0.0022502 | 6.6573e-06
2013-06-18 | 302068 | HDA3A | Urban | LV Transformer SP3613-G HDA3A - Planned | 23.455 | 391 | 9170.905 | 0.0092017 | 2.3534e-05
2013-06-18 | 302069 | SGT7 | Urban | LV Transformer SP5175-I SGT7 - Planned | 5.18 | 343 | 1776.74 | 0.0017827 | 5.1974e-06
2013-06-18 | 302070 | SGT4 | Urban | LV Transformer SP2593-I SGT4 - Planned | 20.475 | 268 | 5487.3 | 0.0055057 | 2.0544e-05
2013-06-18 | 302071 | TGP8A | Urban | LV Transformer SC2213-M TGP8A - Planned | 9.12 | 165 | 1504.8 | 0.0015099 | 9.1506e-06
2013-06-18 | 302072 | HDA11A | Urban | LV Transformer SP3819-G HDA11A - Planned | 23.8 | 351 | 8353.8 | 0.0083819 | 2.388e-05
2013-06-18 | 302073 | BBS9 | Urban | LV Transformer SC3900-F BBS9 - Planned | 25.25 | 411 | 10377.75 | 0.010413 | 2.5335e-05
2013-06-18 | 302073 | HPE3A | Urban | LV Transformer SC3900-F BBS9 - Planned | 14.67 | 411 | 6029.37 | 0.0060496 | 1.4719e-05
2013-06-18 | 302074 | EMP2A | Urban | LV Transformer SC1510211 EMP2A - Planned | 124 | 260 | 32240 | 0.032348 | 0.00012442
2013-06-18 | 302075 | ALY5 | Urban | LV Transformer SP2720-K ALY5 - Planned | 16.56 | 425 | 7038 | 0.0070616 | 1.6616e-05
2013-06-18 | 302077 | BLB8B | Urban | LV Transformer SP493027 BLB8B - Planned | 12.805 | 206 | 2637.83 | 0.0026467 | 1.2848e-05
2013-06-18 | 302078 | NMC1B | Rural short | LV Transformer SP17958-F NMC1B - Planned | 2.05 | 43 | 88.15 | 0.00025534 | 5.9381e-06
2013-06-18 | 302086 | BDT1 | Rural short | Feeder BDT1 - Planned | 14 | 165 | 2310 | 0.0066912 | 4.0553e-05
2013-06-18 | 302095 | BHD35A | Rural short | Feeder BHD35A - Planned | 30.4 | 1340 | 40736 | 0.118 | 8.8057e-05
2013-06-18 | 302298 | BNH1B | Rural short | LV Transformer SP1393-H BNH1B - Planned | 3 | 408 | 1224 | 0.0035455 | 8.6899e-06
2013-06-19 | 302094 | GTN5B | Rural short | LV Transformer SP3992-C GTN5B - Planned | 7 | 79 | 553 | 0.0016019 | 2.0277e-05
2013-06-19 | 302098 | KBN2A | Rural short | Feeder KBN2A - Planned | 24 | 191 | 4584 | 0.013279 | 6.9523e-05
2013-06-19 | 302114 | TCB1 | Rural short | Feeder TCB1 - Planned | 64.58 | 412 | 26606.96 | 0.077075 | 0.00018707
2013-06-19 | 302118 | FDS4 | Rural short | Feeder FDS4 - Planned | 6 | 385 | 2310 | 0.0066916 | 1.7381e-05
2013-06-19 | 302119 | CPR5 | Urban | LV Transformer SC4706-H CPR5 - Planned | 0.99 | 210 | 207.9 | 0.00020858 | 9.9325e-07
2013-06-19 | 302120 | AHL4A | Urban | LV Transformer SP797450 GLY4A - Planned | 9.85 | 354 | 3486.9 | 0.0034984 | 9.8824e-06
2013-06-19 | 302120 | GLY4A | Urban | LV Transformer SP797450 GLY4A - Planned | 5.475 | 354 | 1938.15 | 0.0019445 | 5.493e-06
2013-06-19 | 302121 | CSE4 | Urban | LV Transformer SP3220-L CSE4 - Planned | 27.3 | 328 | 8954.4 | 0.0089838 | 2.739e-05
2013-06-19 | 302122 | HWD5A | Rural short | LV Transformer SC22621-E HWD5A - Planned | 0.84 | 69 | 57.96 | 0.0001679 | 2.4333e-06
2013-06-19 | 302122 | INA1A | Urban | LV Transformer SC22621-E HWD5A - Planned | 2.46 | 69 | 169.74 | 0.0001703 | 2.4681e-06
2013-06-19 | 302123 | GLY12A | Urban | LV Transformer SP3181-M GLY12A - Planned | 19.76 | 237 | 4683.12 | 0.0046985 | 1.9825e-05
2013-06-19 | 302124 | SHW3 | Urban | LV Transformer SP1315-N SHW3 - Planned | 26.11 | 296 | 7728.56 | 0.0077539 | 2.6196e-05
2013-06-19 | 302125 | MLT42A | Urban | LV Transformer SC4533-H MLT42A - Planned | 23.88 | 349 | 8334.12 | 0.0083615 | 2.3958e-05
2013-06-19 | 302126 | GLY12A | Urban | LV Transformer SC2562-L GLY12A - Planned | 12.22 | 342 | 4179.24 | 0.004193 | 1.226e-05
2013-06-19 | 302127 | CLM4A | Urban | LV Transformer SP15276-A CLM6 - Planned | 0.84 | 235 | 197.4 | 0.00019805 | 8.4276e-07
2013-06-19 | 302127 | CLM5 | Urban | LV Transformer SP15276-A CLM6 - Planned | 17.16 | 235 | 4032.6 | 0.0040458 | 1.7216e-05
2013-06-19 | 302127 | CLM6 | Urban | LV Transformer SP15276-A CLM6 - Planned | 1.63 | 235 | 383.05 | 0.00038431 | 1.6354e-06
2013-06-19 | 302128 | GYM2A | Rural short | LV Transformer SP735-B GYM2A - Planned | 1 | 195 | 195 | 0.00056487 | 2.8968e-06
2013-06-19 | 302129 | PWC2 | Rural short | LV Transformer SP4013-A PWC2 - Planned | 8 | 133 | 1064 | 0.0030822 | 2.3174e-05
2013-06-19 | 302130 | HWL13A | Urban | LV Transformer SC1385738 HWL13A - Planned | 44.97 | 127 | 5711.19 | 0.00573 | 4.5118e-05
2013-06-19 | 302131 | HWL3A | Urban | LV Transformer SP1207-M HWL3A - Planned | 20.07 | 270 | 5418.9 | 0.0054367 | 2.0136e-05
2013-06-19 | 302132 | CRBTHP14 | Urban | LV Transformer SP5742-C CRBTHP14 - Planned | 18.3 | 383 | 7008.9 | 0.0070319 | 1.836e-05
2013-06-19 | 302133 | NRA5A | Rural short | LV Transformer SP6106-C NRA5A - Planned | 4.08 | 342 | 1395.36 | 0.0040421 | 1.1819e-05
2013-06-19 | 302134 | BIS16A | Urban | LV Transformer SP5873-C BIS16A - Planned | 86.5 | 33 | 2854.5 | 0.0028639 | 8.6784e-05
2013-06-19 | 302135 | DRD15B | Urban | LV Transformer SP2203-E DRD15B - Planned | 110.5 | 21 | 2320.5 | 0.0023281 | 0.00011086
2013-06-19 | 302136 | ZMR7A | Urban | LV Transformer SP5865-G ZMR7A - Planned | 6.72 | 125 | 840 | 0.00084276 | 6.7421e-06
2013-06-19 | 302137 | BHL2A | Urban | LV Transformer SC769096 BHL2A - Planned | 6.75 | 53 | 357.75 | 0.00035893 | 6.7722e-06
2013-06-19 | 302138 | MTG4B | Urban | LV Transformer SP3055-I MTG4B - Planned | 24.64 | 175 | 4312 | 0.0043262 | 2.4721e-05
2013-06-19 | 302139 | UMG2B | Rural short | LV Transformer SP16679-F UMG2B - Planned | 1.83 | 150 | 274.5 | 0.00079517 | 5.3011e-06
2013-06-19 | 302140 | RIS2 | Urban | LV Transformer SP104064-A RIS2 - Planned | 2.1 | 122 | 256.2 | 0.00025704 | 2.1069e-06
2013-06-19 | 302141 | ALY5 | Urban | LV Transformer SP2720-K ALY5 - Planned | 13.8 | 307 | 4236.6 | 0.0042505 | 1.3845e-05
2013-06-19 | 302142 | CHL10 | Urban | LV Transformer SP25288-E CHL10 - Planned | 0.78 | 406 | 316.68 | 0.00031772 | 7.8256e-07
2013-06-19 | 302143 | ARG9A | Urban | LV Transformer SP1643-L ARG9A - Planned | 9.72 | 30 | 291.6 | 0.00029256 | 9.7519e-06
2013-06-19 | 302144 | THL3 | Rural short | LV Transformer SP917-B THL3 - Planned | 9 | 407 | 3663 | 0.010611 | 2.6071e-05
2013-06-19 | 302300 | BIS12B | Rural short | Feeder BIS12B - Planned | 13.95 | 251 | 3501.45 | 0.010143 | 4.041e-05
2013-06-19 | 302301 | BRD11A | Rural short | LV Transformer SP4750-F BRD11A - Planned | 7 | 350 | 2450 | 0.0070971 | 2.0277e-05
2013-06-20 | 302175 | LBS12A | Urban | LV Transformer SP750874 LBS12A - Planned | 0.11 | 224 | 24.64 | 2.4721e-05 | 1.1036e-07
2013-06-20 | 302176 | TGW3 | Rural short | Feeder TGW3 - Planned | 24.02 | 310 | 7446.2 | 0.021567 | 6.957e-05
2013-06-20 | 302193 | KBN5A | Rural short | LV Transformer SP4232-F KBN5A - Planned | 11 | 372 | 4092 | 0.011852 | 3.186e-05
2013-06-20 | 302194 | MTB17A | Rural short | Feeder MTB17A - Planned | 25.5 | 493 | 12571.5 | 0.036411 | 7.3857e-05
2013-06-20 | 302197 | CRB25A | Rural short | LV Transformer SP4642-E CRB25A - Planned | 6.5 | 430 | 2795 | 0.0080953 | 1.8826e-05
2013-06-20 | 302198 | TWG11 | Urban | LV Transformer SP3490-H TWG11 - Planned | 4.32 | 359 | 1550.88 | 0.001556 | 4.3342e-06
2013-06-20 | 302199 | MGL5 | Urban | LV Transformer SC1445892 MGL2A - Planned | 5.95 | 165 | 981.75 | 0.00098498 | 5.9696e-06
2013-06-20 | 302200 | GYM2A | Rural short | LV Transformer SP1458636 GYM2A - Planned | 6 | 414 | 2484 | 0.0071945 | 1.7378e-05
2013-06-20 | 302201 | AGE8 | Urban | LV Transformer SC7702-F AGE8 - Planned | 21.78 | 179 | 3898.62 | 0.0039114 | 2.1852e-05
2013-06-20 | 302202 | MGL1A | Rural short | LV Transformer SP3391-L MGL1A - Planned | 20 | 392 | 7840 | 0.022707 | 5.7927e-05
2013-06-20 | 302203 | KMR24A | Urban | LV Transformer SP2081-M KMR24A - Planned | 17.6 | 277 | 4875.2 | 0.0048912 | 1.7658e-05
2013-06-20 | 302204 | AHL4A | Urban | LV Transformer SC1059-S AHL4A - Planned | 14.56 | 339 | 4935.84 | 0.0049521 | 1.4608e-05
2013-06-20 | 302205 | AHD5 | Urban | LV Transformer SP2690-A AHD5 - Planned | 10.4 | 348 | 3619.2 | 0.0036311 | 1.0434e-05
2013-06-20 | 302206 | BHD23A | Rural short | LV Transformer SP5779-E BHD23A - Planned | 16 | 313 | 5008 | 0.014505 | 4.6341e-05
2013-06-20 | 302207 | MAI11 | Urban | LV Transformer SP4636-E MAI11 - Planned | 8.64 | 31 | 267.84 | 0.00026872 | 8.6684e-06
2013-06-20 | 302209 | KLG11A | Urban | LV Transformer SP1380569 KLG11A - Planned | 24.83 | 258 | 6406.14 | 0.0064272 | 2.4912e-05
2013-06-20 | 302210 | HDA3A | Urban | LV Transformer SP1804-I HDA3A - Planned | 13.68 | 214 | 2927.52 | 0.0029372 | 1.3725e-05
2013-06-20 | 302211 | HDA3A | Urban | LV Transformer SP6607-I HDA3A - Planned | 8.64 | 148 | 1278.72 | 0.0012829 | 8.6684e-06
2013-06-20 | 302212 | BHL4A | Urban | LV Transformer SP3954-E BHL4A - Planned | 7.02 | 293 | 2056.86 | 0.0020636 | 7.0431e-06
2013-06-20 | 302213 | HDA3A | Urban | LV Transformer SP3613-G HDA3A - Planned | 22.125 | 280 | 6195 | 0.0062154 | 2.2198e-05
2013-06-20 | 302214 | WRG1A | Urban | LV Transformer SP3113-K WRG1A - Planned | 3.875 | 96 | 372 | 0.00037322 | 3.8878e-06
2013-06-20 | 302215 | RLB11B | Urban | LV Transformer SC1478802 RLB11B - Planned | 0.95 | 251 | 238.45 | 0.00023923 | 9.5313e-07
2013-06-20 | 302215 | RLB13B | Rural short | LV Transformer SC1478802 RLB11B - Planned | 3.24 | 251 | 813.24 | 0.0023554 | 9.3841e-06
2013-06-20 | 302216 | MTG4B | Urban | LV Transformer SP2513-M MTG4B - Planned | 44.18 | 296 | 13077.28 | 0.01312 | 4.4325e-05
2013-06-20 | 302217 | WED3A | Urban | LV Transformer SP10364-G WED3A - Planned | 4.65 | 352 | 1636.8 | 0.0016422 | 4.6653e-06
2013-06-20 | 302218 | HPK6 | Urban | LV Transformer SC3066-I HPK6 - Planned | 3.03 | 185 | 560.55 | 0.00056239 | 3.04e-06
2013-06-20 | 302219 | TMH15A | Urban | LV Transformer SP6670-L TMH15A - Planned | 5.01 | 255 | 1277.55 | 0.0012818 | 5.0265e-06
2013-06-20 | 302220 | KBN13A | Rural short | LV Transformer SC2078584 KBN13A - Planned | 5.7 | 253 | 1442.1 | 0.0041768 | 1.6509e-05
2013-06-20 | 302233 | PWC6 | Rural short | Feeder PWC6 - Planned | 18 | 417 | 7506 | 0.02174 | 5.2134e-05
2013-06-20 | 302234 | GYM2A | Rural short | Feeder GYM2A - Planned | 34 | 408 | 13872 | 0.040178 | 9.8476e-05
2013-06-20 | 302235 | NBR11A | Rural short | Feeder NBR11A - Planned | 33.95 | 260 | 8827 | 0.025566 | 9.8331e-05
2013-06-20 | 302275 | GLY15A | Urban | LV Transformer SP2658-M GLY15A - Planned | 2.46 | 383 | 942.18 | 0.00094528 | 2.4681e-06
2013-06-20 | 302304 | GYM9B | Rural short | LV Transformer SP2669-D GYM9B - Planned | 3.5 | 294 | 1029 | 0.0029803 | 1.0137e-05
2013-06-20 | 302305 | NBR12A | Rural short | Feeder NBR12A - Planned | 50.05 | 306 | 15315.3 | 0.044358 | 0.00014496
2013-06-21 | 302273 | LWD1 | Rural short | Feeder LWD1 - Planned | 34.5 | 340 | 11730 | 0.033977 | 9.9933e-05
2013-06-21 | 302276 | TCB1 | Rural short | LV Transformer SP6745-C TCB1 - Planned | 57.34 | 238 | 13646.92 | 0.03953 | 0.00016609
2013-06-21 | 302277 | HWL3A | Urban | LV Transformer SP2180-H HWL3A - Planned | 19.35 | 198 | 3831.3 | 0.0038436 | 1.9412e-05
2013-06-21 | 302278 | MMC19B | Urban | LV Transformer SP1110-K MMC19B - Planned | 4.1198 | 372 | 1532.5656 | 0.0015375 | 4.133e-06
2013-06-21 | 302279 | MMC33A | Urban | LV Transformer SP2865-G MMC33A - Planned | 85 | 79 | 6715 | 0.0067366 | 8.5273e-05
2013-06-21 | 302280 | BTA15A | Urban | LV Transformer SP5460-D BTA15A - Planned | 13.76 | 215 | 2958.4 | 0.0029679 | 1.3804e-05
2013-06-21 | 302281 | BHD2A | Urban | LV Transformer SC467157 BHD2A - Planned | 1.92 | 208 | 399.36 | 0.00040064 | 1.9262e-06
2013-06-21 | 302282 | CRB15A | Urban | LV Transformer SP2689-F CRB15A - Planned | 19.04 | 325 | 6188 | 0.0062079 | 1.9101e-05
2013-06-21 | 302283 | BDL2 | Urban | LV Transformer SP2979-F BDL2 - Planned | 23.04 | 38 | 875.52 | 0.00087833 | 2.3114e-05
2013-06-21 | 302284 | HDA11A | Urban | LV Transformer SP3819-G HDA11A - Planned | 23.8 | 235 | 5593 | 0.005611 | 2.3876e-05
2013-06-21 | 302285 | TGP8A | Urban | LV Transformer SP4167-J TGP8A - Planned | 15.02 | 88 | 1321.76 | 0.001326 | 1.5068e-05
2013-06-21 | 302286 | CPR6 | Urban | LV Transformer SP1423-K CPR6 - Planned | 12.48 | 328 | 4093.44 | 0.0041066 | 1.252e-05
2013-06-21 | 302287 | WRG12A | Urban | LV Transformer SP6910-H WRG12A - Planned | 26.02 | 151 | 3929.02 | 0.0039416 | 2.6104e-05
2013-06-21 | 302289 | CVL7A | Rural short | LV Transformer SP511909 CVL7A - Planned | 10.08 | 161 | 1622.88 | 0.0047009 | 2.9198e-05
2013-06-21 | 302290 | HPE12A | Urban | LV Transformer SP29326-C MTG4B - Planned | 2.6 | 282 | 733.2 | 0.00073556 | 2.6084e-06
2013-06-21 | 302290 | MTG4B | Urban | LV Transformer SP29326-C MTG4B - Planned | 40.56 | 282 | 11437.92 | 0.011475 | 4.069e-05
2013-06-21 | 302291 | BTN7 | Rural short | LV Transformer SP15155-C BTN7 - Planned | 1 | 105 | 105 | 0.00030414 | 2.8966e-06
2013-06-21 | 302309 | SPOSSS35 | Urban | LV Transformer SG715-G SPOSSS35 - Planned | 0.91 | 318 | 289.38 | 0.00029031 | 9.1292e-07
2013-06-21 | 302312 | NBR12A | Rural short | Feeder NBR12A - Planned | 26.07 | 281 | 7325.67 | 0.02122 | 7.5515e-05
2013-06-21 | 302313 | MLY6 | Rural short | LV Transformer SP1754-C MLY6 - Planned | 9 | 282 | 2538 | 0.0073516 | 2.6069e-05
2013-06-21 | 302327 | WRG16A | Urban | Feeder WRG16A - Planned | 2 | 175 | 350 | 0.00035112 | 2.0064e-06
2013-06-22 | 302314 | HDA14A | Urban | LV Transformer SP1080-I HDA14A - Planned | 7 | 200 | 1400 | 0.0014044 | 7.022e-06
2013-06-22 | 302315 | NRG5A | Urban | LV Transformer SG10652-F NRG5A - Planned | 2 | 325 | 650 | 0.00065204 | 2.0063e-06
2013-06-23 | 302318 | HDA14A | Urban | LV Transformer SG6090-G HDA14A - Planned | 8 | 193 | 1544 | 0.0015488 | 8.0251e-06
2013-06-23 | 302324 | BDL3 | Urban | Feeder BDL3 - Planned | 65 | 363 | 23595 | 0.023669 | 6.5204e-05
2013-06-23 | 302325 | CRB25A | Rural short | Feeder CRB25A - Planned | 56 | 450 | 25200 | 0.072996 | 0.00016221
2013-06-23 | 302328 | TWG17 | Urban | LV Transformer SP3653-I TWG17 - Planned | 3.36 | 344 | 1155.84 | 0.0011595 | 3.3706e-06
2013-06-23 | 302329 | DRA5 | Urban | LV Transformer SC6014-G DRA5 - Planned | 7.22 | 270 | 1949.4 | 0.0019555 | 7.2427e-06
2013-06-23 | 302330 | NMK26 | Urban | LV Transformer SC5624-D NMK26 - Planned | 58.98 | 339 | 19994.22 | 0.020057 | 5.9165e-05
2013-06-23 | 302331 | KWA3A | Urban | LV Transformer SP3514-B KWA3A - Planned | 3.51 | 203 | 712.53 | 0.00071477 | 3.521e-06
2013-06-23 | 302332 | AHD8 | Urban | LV Transformer SP683-A AHD8 - Planned | 3.08 | 299 | 920.92 | 0.00092381 | 3.0897e-06
2013-06-23 | 302333 | AMR1 | Rural short | LV Transformer SP746-B AMR1 - Planned | 17.34 | 239 | 4144.26 | 0.012005 | 5.0228e-05
2013-06-23 | 302335 | MRE4A | Urban | LV Transformer SC754597 MRE4A - Planned | 1.04 | 279 | 290.16 | 0.00029107 | 1.0433e-06
2013-06-23 | 302336 | WNM7A | Urban | LV Transformer SP404-N WNM7A - Planned | 4.02 | 355 | 1427.1 | 0.0014316 | 4.0326e-06
2013-06-23 | 302337 | HDA10A | Urban | LV Transformer SP3769-F HDA10A - Planned | 15.795 | 246 | 3885.57 | 0.0038978 | 1.5845e-05
2013-06-23 | 302338 | NRA5A | Rural short | LV Transformer SP37846-B NRA5A - Planned | 4.08 | 425 | 1734 | 0.0050228 | 1.1818e-05
2013-06-23 | 302340 | HPE13A | Urban | LV Transformer SP12142-E HPE13A - Planned | 36.505 | 358 | 13068.79 | 0.01311 | 3.662e-05
2013-06-24 | 302373 | KCY4 | Rural short | Feeder KCY4 - Planned | 8 | 263 | 2104 | 0.0060946 | 2.3173e-05
2013-06-24 | 302374 | BPN29A | Urban | LV Transformer SP5994-I BPN29A - Planned | 26 | 106 | 2756 | 0.0027644 | 2.608e-05
2013-06-24 | 302375 | KBN5A | Rural short | LV Transformer SP778892 KBN5A - Planned | 1 | 249 | 249 | 0.00072127 | 2.8967e-06
2013-06-24 | 302376 | GBN4 | Rural short | Feeder GBN4 - Planned | 83.8 | 397 | 33268.6 | 0.096368 | 0.00024274
2013-06-24 | 302377 | WSE3A | Rural short | LV Transformer SP16759-E WSE3A - Planned | 1 | 450 | 450 | 0.0013035 | 2.8967e-06
2013-06-24 | 302381 | TCB1 | Rural short | LV Transformer SP941-D TCB1 - Planned | 15.95 | 308 | 4912.6 | 0.01423 | 4.6202e-05
2013-06-24 | 302382 | MTB17A | Rural short | LV Transformer SP4414-D MTB17A - Planned | 18.2 | 373 | 6788.6 | 0.019664 | 5.2719e-05
2013-06-24 | 302383 | YTA37A | Urban | LV Transformer SC567299 YTA37A - Planned | 0.96 | 90 | 86.4 | 8.6664e-05 | 9.6294e-07
2013-06-24 | 302384 | CRB25A | Rural short | LV Transformer SP12592-D CRB25A - Planned | 8 | 397 | 3176 | 0.0091998 | 2.3173e-05
2013-06-24 | 302385 | CRB24B | Urban | LV Transformer SP14119-C CRB24B - Planned | 5.0109 | 280 | 1403.052 | 0.0014073 | 5.0262e-06
2013-06-24 | 302386 | WNM2A | Urban | LV Transformer SP2980-K WNM2A - Planned | 17.485 | 65 | 1136.525 | 0.00114 | 1.7538e-05
2013-06-24 | 302387 | HDA3A | Urban | LV Transformer SP3613-G HDA3A - Planned | 39.96 | 320 | 12787.2 | 0.012826 | 4.0082e-05
2013-06-24 | 302388 | TGP8A | Urban | LV Transformer SP4167-J TGP8A - Planned | 6.405 | 149 | 954.345 | 0.00095726 | 6.4246e-06
2013-06-24 | 302389 | WSE3A | Rural short | LV Transformer SP9399-E WSE3A - Planned | 2 | 434 | 868 | 0.0025143 | 5.7933e-06
2013-06-24 | 302390 | WNM3 | Urban | LV Transformer SP953-K WNM3 - Planned | 4.52 | 24 | 108.48 | 0.00010881 | 4.5338e-06
2013-06-24 | 302391 | HPE12A | Urban | LV Transformer SP29326-C MTG4B - Planned | 28.6 | 165 | 4719 | 0.0047334 | 2.8687e-05
2013-06-24 | 302391 | MTG4B | Urban | LV Transformer SP29326-C MTG4B - Planned | 21.125 | 165 | 3485.625 | 0.0034963 | 2.119e-05
2013-06-24 | 302392 | THL1 | Rural short | LV Transformer SP3125-D THL1 - Planned | 8 | 209 | 1672 | 0.0048432 | 2.3173e-05
2013-06-24 | 302393 | WHO1 | Rural short | LV Transformer SP4673-B WHO1 - Planned | 11.04 | 210 | 2318.4 | 0.0067156 | 3.1979e-05
2013-06-24 | 302706 | FDS4 | Rural short | Feeder FDS4 - Planned | 19 | 359 | 6821 | 0.019758 | 5.5037e-05
2013-06-25 | 302400 | MDR10A | Urban | Feeder MDR10A - Planned | 1 | 95 | 95 | 9.5286e-05 | 1.003e-06
2013-06-25 | 302402 | RLB16A | Rural short | LV Transformer SP8931-B RLB16A - Planned | 1 | 123 | 123 | 0.00035629 | 2.8967e-06
2013-06-25 | 302413 | WHO1 | Rural short | LV Transformer SP13577-A WHO1 - Planned | 17 | 15 | 255 | 0.00073866 | 4.9244e-05
2013-06-25 | 302414 | PRG2A | Rural short | LV Transformer SP5068-A PRG2A - Planned | 17 | 271 | 4607 | 0.013345 | 4.9244e-05
2013-06-25 | 302415 | WHO1 | Rural short | LV Transformer SP244609 WHO1 - Planned | 1 | 24 | 24 | 6.9521e-05 | 2.8967e-06
2013-06-25 | 302433 | LBS8B | Urban | LV Transformer SC764993 LBS8B - Planned | 1 | 453 | 453 | 0.00045436 | 1.003e-06
2013-06-25 | 302434 | KCY2 | Rural short | Feeder KCY2 - Planned | 115 | 352 | 40480 | 0.11726 | 0.00033312
2013-06-25 | 302435 | RWD1 | Rural short | Feeder RWD1 - Planned | 12 | 360 | 4320 | 0.012514 | 3.476e-05
2013-06-25 | 302436 | RWD1 | Rural short | LV Transformer SP10893-E RWD1 - Planned | 1 | 206 | 206 | 0.00059672 | 2.8967e-06
2013-06-25 | 302437 | KMR25A | Rural short | LV Transformer SP1578-J KMR25A - Planned | 11 | 434 | 4774 | 0.013829 | 3.1864e-05
2013-06-25 | 302439 | MTB17A | Rural short | Feeder MTB17A - Planned | 39 | 520 | 20280 | 0.058745 | 0.00011297
2013-06-25 | 302440 | BHD35A | Rural short | Feeder BHD35A - Planned | 44.5 | 625 | 27812.5 | 0.080564 | 0.0001289
2013-06-25 | 302442 | GBN4 | Rural short | Feeder GBN4 - Planned | 14 | 295 | 4130 | 0.011963 | 4.0554e-05
2013-06-25 | 302443 | TCB1 | Rural short | LV Transformer SP4259-B TCB1 - Planned | 37.345 | 436 | 16282.42 | 0.047165 | 0.00010818
2013-06-25 | 302444 | BMT1 | Rural short | LV Transformer SP6839-B BMT1 - Planned | 1 | 160 | 160 | 0.00046347 | 2.8967e-06
2013-06-25 | 302445 | COR22A | Rural short | Feeder COR22A - Planned | 24.05 | 159 | 3823.95 | 0.011077 | 6.9666e-05
2013-06-25 | 302446 | CMA8A | Rural short | LV Transformer SC2087573 CMA8A - Planned | 14.06 | 306 | 4302.36 | 0.012463 | 4.0728e-05
2013-06-25 | 302447 | BRT6 | Urban | LV Transformer SC5018-I BRT6 - Planned | 0.93 | 175 | 162.75 | 0.00016324 | 9.328e-07
2013-06-25 | 302448 | AGE3 | Urban | LV Transformer SP11496-H AGE3 - Planned | 29.365 | 285 | 8369.025 | 0.0083942 | 2.9453e-05
2013-06-25 | 302449 | GAP1A | Urban | LV Transformer SC4840-J GAP1A - Planned | 6.12 | 307 | 1878.84 | 0.0018845 | 6.1384e-06
2013-06-25 | 302450 | NBR12A | Rural short | LV Transformer SP4073-A NBR12A - Planned | 2.175 | 300 | 652.5 | 0.0018901 | 6.3003e-06
2013-06-25 | 302451 | PWC5 | Rural short | LV Transformer SP3775-A PWC5 - Planned | 15.17 | 370 | 5612.9 | 0.016259 | 4.3943e-05
2013-06-25 | 302453 | CLM3 | Rural short | LV Transformer SP3247-A CLM3 - Planned | 23.21 | 110 | 2553.1 | 0.0073956 | 6.7232e-05
2013-06-25 | 302454 | CRB25A | Rural short | LV Transformer SP5759-E CRB25A - Planned | 3.23 | 249 | 804.27 | 0.0023297 | 9.3563e-06
2013-06-25 | 302455 | CCY8A | Rural short | LV Transformer SC1182-J CCY14B - Planned | 0.75 | 211 | 158.25 | 0.0004584 | 2.1725e-06
2013-06-25 | 302456 | LBS8B | Urban | LV Transformer SP1284-M LBS8B - Planned | 10.08 | 143 | 1441.44 | 0.0014458 | 1.011e-05
2013-06-25 | 302457 | NRA13A | Rural short | LV Transformer SP10440-D NRA13A - Planned | 1.05 | 248 | 260.4 | 0.0007543 | 3.0415e-06
2013-06-25 | 302458 | HDA3A | Urban | LV Transformer SP1804-I HDA3A - Planned | 28.8 | 290 | 8352 | 0.0083772 | 2.8887e-05
2013-06-25 | 302459 | WNM7A | Urban | LV Transformer SP6268-I WNM7A - Planned | 13.5628 | 44 | 596.7632 | 0.00059856 | 1.3604e-05
2013-06-25 | 302460 | WNM7A | Urban | LV Transformer SP180-Q WNM7A - Planned | 12.2966 | 26 | 319.7116 | 0.00032067 | 1.2334e-05
2013-06-25 | 302461 | CHL10 | Urban | LV Transformer SP25288-E CHL10 - Planned | 0.78 | 237 | 184.86 | 0.00018542 | 7.8235e-07
2013-06-25 | 302463 | MTG4B | Urban | LV Transformer SP2513-M MTG4B - Planned | 44.18 | 279 | 12326.22 | 0.012363 | 4.4313e-05
2013-06-25 | 302464 | CVL17A | Urban | LV Transformer SP4301-F CVL17A - Planned | 25.8 | 265 | 6837 | 0.0068576 | 2.5878e-05
2013-06-25 | 302465 | ALY5 | Urban | LV Transformer SP2720-K ALY5 - Planned | 19.32 | 205 | 3960.6 | 0.0039725 | 1.9378e-05
2013-06-25 | 302466 | KSN8 | Rural short | LV Transformer SP6618-E KSN8 - Planned | 32.34 | 175 | 5659.5 | 0.016394 | 9.3679e-05
2013-06-25 | 302530 | SPOSSS15 | Urban | LV Transformer SC564770 SPOSSS15 - Planned | 0.8415 | 940 | 791.01 | 0.00079339 | 8.4404e-07
2013-06-25 | 302707 | WSO5A | Urban | Feeder WSO15A, WSO5A - Planned | 1 | 301 | 301 | 0.00030191 | 1.003e-06
2013-06-26 | 302494 | RLB13B | Rural short | Feeder RLB13B - Planned | 5 | 238 | 1190 | 0.0034471 | 1.4484e-05
2013-06-26 | 302513 | BMT1 | Rural short | LV Transformer SP1731-D BMT1 - Planned | 1 | 94 | 94 | 0.00027229 | 2.8967e-06
2013-06-26 | 302514 | TRP3 | Rural short | Feeder TRP3 - Planned | 15 | 401 | 6015 | 0.017424 | 4.3451e-05
2013-06-26 | 302515 | BNH6A | Rural short | Feeder BNH6A - Planned | 17 | 415 | 7055 | 0.020437 | 4.9245e-05
2013-06-26 | 302516 | MMC19B | Urban | LV Transformer SP3066-E MMC19B - Planned | 44 | 435 | 19140 | 0.019197 | 4.413e-05
2013-06-26 | 302517 | BDT5 | Rural short | Feeder BDT5 - Planned | 19 | 478 | 9082 | 0.026308 | 5.5038e-05
2013-06-26 | 302519 | TPT4 | Rural short | LV Transformer SP2963-F TPT4 - Planned | 11.22 | 193 | 2165.46 | 0.0062728 | 3.2501e-05
2013-06-26 | 302520 | CRM16A | Rural short | LV Transformer SP8957-A CRM16A - Planned | 11.5 | 227 | 2610.5 | 0.0075619 | 3.3313e-05
2013-06-26 | 302521 | MLT42A | Urban | LV Transformer SP1140-N MLT42A - Planned | 57.95 | 345 | 19992.75 | 0.020052 | 5.8122e-05
2013-06-26 | 302522 | MGL9 | Rural short | LV Transformer SC1432627 MGL9 - Planned | 18.01 | 57 | 1026.57 | 0.0029737 | 5.217e-05
2013-06-26 | 302523 | GBN4 | Rural short | LV Transformer SP882-B GBN4 - Planned | 11 | 126 | 1386 | 0.0040149 | 3.1864e-05
2013-06-26 | 302524 | CLM7 | Urban | LV Transformer SP14095-A CLM7 - Planned | 25.84 | 278 | 7183.52 | 0.0072048 | 2.5917e-05
2013-06-26 | 302525 | CLM7 | Urban | LV Transformer SP14096-A CLM7 - Planned | 24.9 | 98 | 2440.2 | 0.0024474 | 2.4974e-05
2013-06-26 | 302526 | CLM8 | Urban | LV Transformer SP6675-A CLM8 - Planned | 6.4 | 47 | 300.8 | 0.00030169 | 6.4189e-06
2013-06-26 | 302527 | NVL19A | Urban | LV Transformer SC2408-D NVL19A - Planned | 11.11 | 308 | 3421.88 | 0.003432 | 1.1143e-05
2013-06-26 | 302528 | TCB1 | Rural short | LV Transformer SP6749-D TCB1 - Planned | 70 | 403 | 28210 | 0.081717 | 0.00020277
2013-06-26 | 302529 | CRBTHP14 | Urban | LV Transformer SP5742-C CRBTHP14 - Planned | 40.6 | 368 | 14940.8 | 0.014985 | 4.072e-05
2013-06-26 | 302531 | CMA8A | Rural short | LV Transformer SP6913-C CMA8A - Planned | 3 | 283 | 849 | 0.0024593 | 8.6902e-06
2013-06-26 | 302532 | ZMR6A | Urban | LV Transformer SP2142-G ZMR6A - Planned | 5.76 | 365 | 2102.4 | 0.0021086 | 5.7771e-06
2013-06-26 | 302533 | SGT7 | Urban | LV Transformer SP38-K SGT7 - Planned | 12.195 | 287 | 3499.965 | 0.0035103 | 1.2231e-05
2013-06-26 | 302534 | HDA11A | Urban | LV Transformer SP3819-G HDA11A - Planned | 25.5 | 225 | 5737.5 | 0.0057545 | 2.5575e-05
2013-06-26 | 302535 | HDA3A | Urban | LV Transformer SP1804-I HDA3A - Planned | 7.92 | 280 | 2217.6 | 0.0022242 | 7.9434e-06
2013-06-26 | 302536 | BLBNFM6 | Urban | LV Transformer SP3112-H BLBNFM6 - Planned | 25.3 | 273 | 6906.9 | 0.0069273 | 2.5375e-05
2013-06-26 | 302537 | SBK9 | Urban | LV Transformer SP2368-L SBK9 - Planned | 26.13 | 359 | 9380.67 | 0.0094084 | 2.6207e-05
2013-06-26 | 302538 | CPL23A | Rural short | LV Transformer SC1036899 CPL23A - Planned | 3.84 | 129 | 495.36 | 0.0014349 | 1.1123e-05
2013-06-26 | 302539 | ALY5 | Urban | LV Transformer SP414-N ALY5 - Planned | 14.76 | 54 | 797.04 | 0.0007994 | 1.4804e-05
2013-06-26 | 302540 | BDA13A | Urban | LV Transformer SC1894-K BDA13A - Planned | 22.9566 | 80 | 1836.528 | 0.001842 | 2.3025e-05
2013-06-26 | 302541 | RPN4A | Rural short | LV Transformer SP3661-D RPN4A - Planned | 15.4 | 263 | 4050.2 | 0.011732 | 4.461e-05
2013-06-26 | 302542 | LLY3 | Rural short | LV Transformer SP15610-B LLY3 - Planned | 13 | 154 | 2002 | 0.0057993 | 3.7658e-05
2013-06-26 | 302547 | SPOSSS35 | Urban | LV Transformer SG715-G SPOSSS35 - Planned | 2.67 | 218 | 582.06 | 0.00058378 | 2.6779e-06
2013-06-26 | 302548 | IDY6A | Urban | LV Transformer SP522155 IDY6A - Planned | 1.09 | 214 | 233.26 | 0.00023395 | 1.0932e-06
2013-06-26 | 302708 | RBK12A | Urban | LV Transformer SG10412-D RBK12A - Planned | 3 | 299 | 897 | 0.00089966 | 3.0089e-06
2013-06-27 | 302554 | KSN2A | Rural short | LV Transformer SC1142-E KSN2A - Planned | 2 | 17 | 34 | 9.849e-05 | 5.7935e-06
2013-06-27 | 302573 | WFD5A | Rural short | LV Transformer SP1051028 WFD5A - Planned | 1 | 186 | 186 | 0.0005388 | 2.8968e-06
2013-06-27 | 302574 | BWH7A | Rural short | Feeder BWH7A - Planned | 47 | 250 | 11750 | 0.034037 | 0.00013615
2013-06-27 | 302577 | RLB13B | Rural short | LV Transformer SP76452-B RLB13B - Planned | 2 | 102 | 204 | 0.00059094 | 5.7935e-06
2013-06-27 | 302578 | THL3 | Rural short | LV Transformer SP5054-B THL3 - Planned | 2 | 200 | 400 | 0.0011587 | 5.7935e-06
2013-06-27 | 302582 | BNH6A | Rural short | Feeder BNH6A - Planned | 13 | 300 | 3900 | 0.011297 | 3.7658e-05
2013-06-27 | 302583 | TGW3 | Rural short | Feeder TGW3 - Planned | 7.01 | 376 | 2635.76 | 0.0076352 | 2.0306e-05
2013-06-27 | 302584 | NRG9 | Rural short | LV Transformer SP2277-F NRG9 - Planned | 5 | 376 | 1880 | 0.0054459 | 1.4484e-05
2013-06-27 | 302585 | MBG2 | Rural short | LV Transformer SP3786-C MBG2 - Planned | 70.5 | 375 | 26437.5 | 0.076583 | 0.00020422
2013-06-27 | 302587 | GBN4 | Rural short | Feeder GBN4 - Planned | 7 | 360 | 2520 | 0.0072998 | 2.0277e-05
2013-06-27 | 302588 | NBR7A | Rural short | Feeder NBR7A - Planned | 158.16 | 275 | 43494 | 0.12599 | 0.00045815
2013-06-27 | 302590 | BHD35A | Rural short | Feeder BHD35A - Planned | 85.79 | 334 | 28653.86 | 0.083003 | 0.00024851
2013-06-27 | 302591 | AGE3 | Urban | LV Transformer SP6199-E MLT15B - Planned | 19.62 | 379 | 7435.98 | 0.0074577 | 1.9677e-05
2013-06-27 | 302591 | MLT15B | Urban | LV Transformer SP6199-E MLT15B - Planned | 11.73 | 379 | 4445.67 | 0.0044586 | 1.1764e-05
2013-06-27 | 302592 | KMR19A | Urban | LV Transformer SP2244-L KMR19A - Planned | 5.1 | 235 | 1198.5 | 0.001202 | 5.1149e-06
2013-06-27 | 302593 | AGE2 | Urban | LV Transformer SP516-N AGE2 - Planned | 20.98 | 266 | 5580.68 | 0.0055969 | 2.1041e-05
2013-06-27 | 302594 | CSE10 | Urban | LV Transformer SG1194-Q CSE10 - Planned | 29.82 | 351 | 10466.82 | 0.010497 | 2.9907e-05
2013-06-27 | 302595 | TCB1 | Rural short | LV Transformer SP48392-A TCB1 - Planned | 36.16 | 345 | 12475.2 | 0.036138 | 0.00010475
2013-06-27 | 302596 | MTB17A | Rural short | LV Transformer SP1813-H MTB17A - Planned | 11.96 | 192 | 2296.32 | 0.0066519 | 3.4645e-05
2013-06-27 | 302597 | CRB15A | Urban | LV Transformer SP2704-F CRB15A - Planned | 30.66 | 335 | 10271.1 | 0.010301 | 3.0749e-05
2013-06-27 | 302597 | CRB22A | Urban | LV Transformer SP2704-F CRB15A - Planned | 0.84 | 335 | 281.4 | 0.00028222 | 8.4245e-07
2013-06-27 | 302598 | CCY3B | Urban | LV Transformer SC561-I CCY3B - Planned | 7.33 | 69 | 505.77 | 0.00050724 | 7.3514e-06
2013-06-27 | 302598 | CCY8A | Rural short | LV Transformer SC561-I CCY3B - Planned | 15.75 | 69 | 1086.75 | 0.0031481 | 4.5624e-05
2013-06-27 | 302599 | BHD44A | Urban | LV Transformer SC428-H BHD44A - Planned | 30.96 | 482 | 14922.72 | 0.014966 | 3.105e-05
2013-06-27 | 302600 | MTB1B | Rural short | LV Transformer SP4480-C MTB1B - Planned | 7.7 | 189 | 1455.3 | 0.0042157 | 2.2305e-05
2013-06-27 | 302601 | SGT7 | Urban | LV Transformer SP3057-G SGT7 - Planned | 15.295 | 390 | 5965.05 | 0.0059824 | 1.534e-05
2013-06-27 | 302602 | BIS2B | Rural short | LV Transformer SP11566-F BIS2B - Planned | 19.2 | 343 | 6585.6 | 0.019077 | 5.5618e-05
2013-06-27 | 302603 | BRT6 | Urban | LV Transformer SP3073-I BRT6 - Planned | 36.19 | 33 | 1194.27 | 0.0011978 | 3.6296e-05
2013-06-27 | 302604 | SBK9 | Urban | LV Transformer SC5894-E SBK9 - Planned | 1 | 249 | 249 | 0.00024973 | 1.0029e-06
2013-06-27 | 302605 | WHO1 | Rural short | LV Transformer SP2310-C WHO1 - Planned | 11 | 255 | 2805 | 0.0081254 | 3.1864e-05
2013-06-27 | 302680 | CSE10 | Urban | LV Transformer SP411-P CSE10 - Planned | 3.1 | 346 | 1072.6 | 0.0010757 | 3.109e-06
2013-06-28 | 302635 | LLY1 | Rural short | LV Transformer SP8285-B LLY1 - Planned | 2 | 67 | 134 | 0.00038817 | 5.7936e-06
2013-06-28 | 302653 | LRE8A | Rural short | LV Transformer SP13231-B LRE8A - Planned | 21 | 46 | 966 | 0.0027983 | 6.0833e-05
2013-06-28 | 302654 | KCY2 | Rural short | LV Transformer SP6162-H KCY2 - Planned | 2 | 165 | 330 | 0.00095595 | 5.7936e-06
2013-06-28 | 302673 | TGW2 | Rural short | Feeder TGW2 - Planned | 8 | 330 | 2640 | 0.0076476 | 2.3174e-05
2013-06-28 | 302674 | RWD2 | Rural short | Feeder RWD2 - Planned | 13 | 405 | 5265 | 0.015252 | 3.7659e-05
2013-06-28 | 302676 | BHL5A | Urban | LV Transformer SC804277 BHL5A - Planned | 2 | 366 | 732 | 0.0007341 | 2.0057e-06
2013-06-28 | 302677 | INA2A | Urban | LV Transformer SC4789-G INA2A - Planned | 2.5066 | 75 | 187.995 | 0.00018853 | 2.5138e-06
2013-06-28 | 302678 | SHW4 | Urban | LV Transformer SP530-K SHW4 - Planned | 13.09 | 223 | 2919.07 | 0.0029274 | 1.3128e-05
2013-06-28 | 302679 | SHW6 | Urban | LV Transformer SC6390-D SHW6 - Planned | 14.055 | 238 | 3345.09 | 0.0033547 | 1.4095e-05
2013-06-28 | 302681 | CLM5 | Urban | LV Transformer SP15799-A CLM5 - Planned | 23.94 | 87 | 2082.78 | 0.0020887 | 2.4009e-05
2013-06-28 | 302682 | GYM8A | Rural short | LV Transformer SP26892-A GYM8A - Planned | 22 | 63 | 1386 | 0.004015 | 6.373e-05
2013-06-28 | 302683 | KWA3A | Urban | LV Transformer SP3514-B KWA3A - Planned | 3.51 | 236 | 828.36 | 0.00083073 | 3.5201e-06
2013-06-28 | 302684 | CRB15A | Urban | LV Transformer SP2689-F CRB15A - Planned | 8.16 | 210 | 1713.6 | 0.0017185 | 8.1834e-06
2013-06-28 | 302685 | MTB17A | Rural short | LV Transformer SC2065201 MTB17A - Planned | 1.3 | 35 | 45.5 | 0.0001318 | 3.7659e-06
2013-06-28 | 302686 | MGP17A | Rural short | LV Transformer SC764535 MGP17A - Planned | 0.99 | 367 | 363.33 | 0.0010525 | 2.8678e-06
2013-06-28 | 302687 | HWL10A | Urban | LV Transformer SP3727-D HWL10A - Planned | 4.4125 | 277 | 1222.2625 | 0.0012258 | 4.4251e-06
2013-06-28 | 302688 | PPE16A | Rural short | LV Transformer SP7337-C PPE16A - Planned | 6 | 96 | 576 | 0.0016686 | 1.7381e-05
2013-06-28 | 302689 | WNM7A | Urban | LV Transformer SG6726-F WNM7A - Planned | 17.717 | 40 | 708.68 | 0.00071071 | 1.7768e-05
2013-06-28 | 302690 | CFD1A | Urban | LV Transformer SP9695-H CFD1A - Planned | 13.46 | 365 | 4912.9 | 0.004927 | 1.3499e-05
2013-06-28 | 302691 | ZMR9 | Urban | LV Transformer SP29524-C ZMR9 - Planned | 5.22 | 223 | 1164.06 | 0.0011674 | 5.235e-06
2013-06-28 | 302692 | BIS2B | Rural short | LV Transformer SP11566-F BIS2B - Planned | 25.6 | 358 | 9164.8 | 0.026549 | 7.4158e-05
2013-06-28 | 302693 | KLG11A | Urban | LV Transformer SP5885-B KLG11A - Planned | 9.35 | 225 | 2103.75 | 0.0021098 | 9.3768e-06
2013-06-28 | 302694 | HDA3A | Urban | LV Transformer SP1804-I HDA3A - Planned | 28.08 | 293 | 8227.44 | 0.008251 | 2.816e-05
2013-06-28 | 302695 | BKD12A | Urban | LV Transformer SP3305-B BKD12A - Planned | 10 | 360 | 3600 | 0.0036103 | 1.0029e-05
2013-06-28 | 302696 | CHL3 | Urban | LV Transformer SP12-T CHL3 - Planned | 17.94 | 323 | 5794.62 | 0.0058112 | 1.7991e-05
2013-06-28 | 302697 | CVL7A | Rural short | LV Transformer SP1651-G CVL7A - Planned | 1.96 | 99 | 194.04 | 0.0005621 | 5.6777e-06
2013-06-28 | 302698 | WRD25A | Urban | LV Transformer SC6575-F WRD25A - Planned | 1.98 | 292 | 578.16 | 0.00057982 | 1.9857e-06
2013-06-28 | 302699 | ALY5 | Urban | LV Transformer SP31667-D ALY5 - Planned | 34.845 | 85 | 2961.825 | 0.0029703 | 3.4945e-05
2013-06-28 | 302700 | PPE5A | Rural short | LV Transformer SC1400401 PPE5A - Planned | 2.14 | 205 | 438.7 | 0.0012708 | 6.1992e-06
2013-06-28 | 302702 | LRE6A | Rural short | LV Transformer SP10559-B LRE6A - Planned | 3 | 64 | 192 | 0.00055619 | 8.6904e-06
2013-06-28 | 302703 | SPF1B | Rural short | LV Transformer SC1293135 SPF1B - Planned | 4.32 | 100 | 432 | 0.0012514 | 1.2514e-05
2013-06-28 | 302713 | BMT1 | Rural short | Feeder BMT1 - Planned | 2 | 255 | 510 | 0.0014774 | 5.7936e-06
2013-06-28 | 302714 | GYM9B | Rural short | LV Transformer SP1832-F GYM9B - Planned | 1 | 198 | 198 | 0.00057357 | 2.8968e-06
2013-06-28 | 302715 | GYM8A | Rural short | Feeder GYM8A - Planned | 27 | 57 | 1539 | 0.0044582 | 7.8214e-05
2013-06-28 | 302717 | PPE5A | Rural short | LV Transformer SP6286-E PPE5A - Planned | 2 | 728 | 1456 | 0.0042178 | 5.7936e-06
2013-06-28 | 302760 | NBR5A | Rural short | LV Transformer SP4333-A NBR5A - Planned | 6.5 | 240 | 1560 | 0.004519 | 1.8829e-05
2013-06-30 | 302740 | CPL23A | Rural short | LV Transformer SP6756-G CPL23A - Planned | 2 | 214 | 428 | 0.0012377 | 5.7834e-06
2013-06-30 | 302741 | KCY4 | Rural short | LV Transformer SP9112-F KCY4 - Planned | 6 | 265 | 1590 | 0.0045978 | 1.735e-05
2013-06-30 | 302753 | MLT2B | Urban | LV Transformer SC1428-L MLT2B - Planned | 141.315 | 420 | 59352.3 | 0.059554 | 0.0001418
2013-06-30 | 302754 | SPOSSS35 | Urban | LV Transformer SG715-G SPOSSS35 - Planned | 1.78 | 605 | 1076.9 | 0.0010806 | 1.7861e-06
2013-06-30 | 302755 | SPO55A | Urban | LV Transformer SC2007-G SPO55A - Planned | 3 | 390 | 1170 | 0.001174 | 3.0102e-06
2013-06-30 | 302756 | HTL3A | Urban | LV Transformer SG3338-E HTL3A - Planned | 4.99 | 254 | 1267.46 | 0.0012718 | 5.007e-06
2013-06-30 | 302757 | ALY5 | Urban | LV Transformer SP1966-I ALY5 - Planned | 1.61 | 252 | 405.72 | 0.0004071 | 1.6155e-06
2013-06-30 | 302773 | CRB24B | Urban | LV Transformer SP2525-H CRB24B - Planned | 8.46 | 233 | 1971.18 | 0.0019779 | 8.4888e-06
2013-06-30 | 302773 | KRA3 | Urban | LV Transformer SP2525-H CRB24B - Planned | 1.04 | 233 | 242.32 | 0.00024315 | 1.0435e-06
Contents

## 5b. Network data feeder
Energex
Network data - Feeder Reliability
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Annual Feeder Reliability Data
Feeder ID / name | Geographical description of feeder | Feeder classification | Number of distribution customers (average) | Length of distribution lines - high voltage - overhead | Length of distribution lines - high voltage - underground | Maximum demand (MW) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply | Planned interruptions (SAIFI)
1084 | MORNINGSIDE | Urban | 31 | 0.6363 | 1.4379 |  | 4.3326 | 0 | 1 | 5493.48 | 0 | 3.0997e-05 | 0 | 0 | 0 | 0
1129 | ROCKLEA | Urban | 344.05 | 3.4853 | 0.7121 |  | 110.536 | 0 | 10 | 1130199.25 | 171717.25 | 0.0015672 | 0.00086704 | 0 | 0 | 0
ABT8 | MORNINGSIDE | Urban | 3 | 0 | 0.4148 |  | 0 | 15.7306 | 0 | 0 | 0 | 0 | 0 | 1 | 2811 | 3.0315e-06
ABTQPT95 | MURARRIE | Urban | 2 | 0 | 2.2297 | 4.1345 | 0 | 5.6928 | 0 | 0 | 0 | 0 | 0 | 1 | 1288 | 2.0119e-06
ABY2A | AMBERLEY, MUTDAPILLY, PURGA, WILLOWBANK | Rural short | 446.7023 | 41.0105 | 1.9577 | 1.7043 | 8.2657 | 0.23527 | 6 | 46390.44 | 46290.44 | 0.00021343 | 0.00021055 | 7 | 3807.58 | 0.00010042
ABY5A | AMBERLEY, JEEBROPILLY, WALLOON | Rural short | 33.0833 | 12.9679 | 0.2043 | 2.2979 | 1.0433 | 5.4384 | 3 | 1598 | 1598 | 0.00032156 | 0.00032156 | 3 | 25088.5 | 0.00015636
ACFQBI5 | PINKENBA | Urban | 17 | 2.1007 | 1.1037 |  | 1.4239 | 0.0011319 | 1 | 1156 | 1156 | 1.7051e-05 | 1.7051e-05 | 1 | 115 | 1.0091e-06
ACR1 | ALBANY CREEK, EATONS HILL | Urban | 431 | 2.8743 | 0.0857 | 1.3 | 15.9369 | 0 | 1 | 495 | 495 | 6.6574e-06 | 6.6574e-06 | 0 | 0 | 0
ACR12A | ALBANY CREEK, BRIDGEMAN DOWNS | Urban | 1351 | 2.6262 | 7.7189 | 4.8024
ACR13A | ALBANY CREEK | Urban | 1035 | 0 | 4.0208 | 3.1569
ACR2 | ALBANY CREEK | Urban | 1199 | 0.0615 | 5.0628
ACR3 | ALBANY CREEK, BRIDGEMAN DOWNS, MCDOWALL | Urban | 1107 | 3.6226 | 6.0368 |  | 0 | 0.0064914 | 0 | 0 | 0 | 0 | 0 | 1 | 46.06 | 9.8593e-07
ACR4 | ALBANY CREEK | Urban | 939.6667 | 4.7029 | 0.5162 | 4.4394 | 3.8424 | 0.061248 | 5 | 77909.565 | 77909.565 | 0.00085774 | 0.00085774 | 1 | 2520 | 7.271e-06
ACR5 | ALBANY CREEK, BUNYA, DRAPER, EATONS HILL | Rural short | 1304.4423 | 26.4779 | 5.1054 | 4.3822 | 38.5882 | 1.302 | 7 | 1910576.98 | 36583.48 | 0.0045916 | 0.00030391 | 6 | 77496.5 | 0.00053928
ACR6 | ALBANY CREEK, BRIDGEMAN DOWNS | Rural short | 919 | 7.242 | 0.7287 | 1.5242
ADAMAA1 | BRISBANE | Urban | 25 | 0 | 0.3063 |  | 1.7393 | 0 | 1 | 1950 | 1950 | 2.4962e-05 | 2.4962e-05 | 0 | 0 | 0
ADAMLS23 | BRISBANE, FORTITUDE VALLEY, SPRING HILL | Urban | 16.75 | 0 | 1.7699 | 4.7442 | 5.4755 | 0 | 2 | 1564 | 1564 | 1.7478e-05 | 1.7478e-05 | 0 | 0 | 0
AFD1A | ROCKLEA | Urban | 121 | 2.4005 | 1.5283 | 3.7344 | 0.040839 | 0.13549 | 0 | 0 | 0 | 0 | 0 | 2 | 524.4 | 1.4048e-05
AFD1B | ROCKLEA | Urban | 49 | 1.6458 | 1.0352 | 1.6195 | 0.018963 | 0
AFD3A | ROCKLEA | Urban | 14 | 0.6321 | 0.3095 | 3.7725 | 0 | 1.8703 | 0 | 0 | 0 | 0 | 0 | 1 | 17.92 | 1.6157e-07
AFD5 | ROCKLEA | Urban | 23 | 0.2801 | 0.3164 | 3.239 | 16.0071 | 0 | 1 | 4496.1 | 4496.1 | 2.3094e-05 | 2.3094e-05 | 0 | 0 | 0
AFD6 | ROCKLEA | Urban | 141 | 2.4287 | 1.2608 | 4.2869 | 5.6284 | 0 | 2 | 11438.815 | 11438.815 | 0.00014659 | 0.00014659 | 0 | 0 | 0
AFD7 | ROCKLEA | Urban | 75.8 | 1.2202 | 1.8367 | 2.4578 | 2.4831 | 0.0094519 | 2 | 1654 | 1654 | 4.5281e-06 | 4.5281e-06 | 1 | 32.2 | 9.3012e-07
AFDCIG4 | ARCHERFIELD, ROCKLEA | Urban | 115 | 0.6801 | 1.1651 | 1.7148 | 0.016084 | 0
AGE10 | ASHGROVE, BARDON, PADDINGTON | Urban | 2251.7529 | 7.8483 | 1.5603 | 5.4383 | 142.5866 | 5.9599 | 11 | 5523912.875 | 97980.46 | 0.0050006 | 0.0026648 | 33 | 132329.3523 | 0.00048799
AGE2 | ASHGROVE, BARDON | Urban | 519.8533 | 3.11 | 1.8936 | 1.4626 | 0 | 1.3218 | 0 | 0 | 0 | 0 | 0 | 6 | 18489.5535 | 7.4168e-05
AGE3 | PADDINGTON, RED HILL | Urban | 2141.225 | 4.9562 | 4.3214 | 4.7252 | 20.9691 | 5.4036 | 5 | 758388.6 | 758388.6 | 0.0067461 | 0.0067461 | 15 | 105043.625 | 0.00037085
AGE4B | ASHGROVE | Urban | 755.7778 | 3.7289 | 0.7307 | 2.598 | 0.77647 | 0.33753 | 4 | 23647.935 | 11844 | 0.0002086 | 0.00012676 | 4 | 13118.555 | 5.2973e-05
AGE5B | ASHGROVE | Urban | 718.9167 | 1.1813 | 0.7465 | 1.9053 | 2.6286 | 0.64594 | 4 | 224430.16 | 141137.5 | 0.00030232 | 0.00026295 | 8 | 33793.635 | 9.2782e-05
AGE6A | ASHGROVE, NEWMARKET, RED HILL | Urban | 1138.8889 | 3.3 | 0.9787 | 2.496 | 0.70876 | 1.0916 | 1 | 18115.125 | 0 | 3.5559e-05 | 0 | 8 | 47779.62 | 0.00017511
AGE7B | ASHGROVE | Urban | 970.602 | 5.4541 | 0.5123 | 2.6103 | 1.7036 | 0.31548 | 2 | 41201.04 | 41201.04 | 0.0010015 | 0.0010015 | 7 | 20041.255 | 6.4352e-05
AGE8 | ASHGROVE, THE GAP | Urban | 941.2065 | 5.948 | 3.1255 | 2.8097 | 69.5679 | 1.1934 | 4 | 2160152.38 | 46304.86 | 0.0020464 | 0.0010978 | 16 | 52176.4142 | 0.00017957
AGE9 | ASHGROVE, BARDON, PADDINGTON, RED HILL | Urban | 1398.91 | 5.1397 | 0.5022 | 4.1917 | 4.0554 | 0.46954 | 3 | 164706.654 | 164706.654 | 0.0015977 | 0.0015977 | 9 | 44241.4074 | 0.0001304
AGT23A | ALGESTER, WILLAWONG | Urban | 1521.785 | 0.8599 | 9.3765 | 3.3457 | 33.8628 | 0.14853 | 7 | 1229646.6 | 139400.3 | 0.0033042 | 0.0017626 | 1 | 3200.239 | 1.3206e-05
AGT25A | ACACIA RIDGE, WILLAWONG | Urban | 1079 | 6.7525 | 2.1209 | 2.8008 | 0.06787 | 0.091252 | 0 | 0 | 0 | 0 | 0 | 2 | 3379.54 | 1.6053e-05
AGT27A | ACACIA RIDGE | Urban | 44 | 0 | 3.0594 | 1.9625
AGT29A | ACACIA RIDGE | Urban | 96 | 0.1365 | 3.3701 | 2.2102
AGT31A | LARAPINTA, PALLARA, WILLAWONG | Rural short | 392.598 | 13.9241 | 9.3785 | 4.4394 | 556.2511 | 0.30626 | 9 | 1881113.45 | 97779.9 | 0.0045968 | 0.0012062 | 1 | 1288 | 1.1408e-05
AGT33A | ACACIA RIDGE | Urban | 25 | 0.2375 | 1.9348 | 2.2102 | 0 | 0.0084115 | 0 | 0 | 0 | 0 | 0 | 1 | 22.77 | 9.9429e-07
AGT35A | ACACIA RIDGE | Urban | 94 | 0.1418 | 4.0882 | 4.0202 | 0.14968 | 0 | 1 | 222 | 222 | 3.0336e-06 | 3.0336e-06 | 0 | 0 | 0
AGT37A | ACACIA RIDGE, ALGESTER, SUNNYBANK HILLS | Urban | 1522.7133 | 4.7893 | 6.1414 | 3.6201 | 13.8096 | 0.25489 | 1 | 403753.95 | 0 | 0.0015339 | 0 | 5 | 12280.955 | 6.2679e-05
AHD10A | MOOLOOLABA | Urban | 1594.441 | 4.6128 | 2.3776 | 3.249 | 1.7877 | 0.045994 | 8 | 114697.0713 | 48306.6304 | 0.0021268 | 0.00049669 | 2 | 3266.4886 | 2.0061e-05
AHD10B | ALEXANDRA HEADLAND, MOOLOOLABA | Urban | 1079.0343 | 1.7103 | 3.2562 | 3.5248 | 2.0855 | 0.13499 | 1 | 108468.26 | 0 | 0.0010891 | 0 | 6 | 7435.5319 | 5.3842e-05
AHD12A | MAROOCHYDORE | Urban | 845.26 | 1.8356 | 2.7627 | 2.9532 | 106.6752 | 0 | 5 | 2252624.33 | 73110.73 | 0.0026679 | 0.00095802 | 0 | 0 | 0
AHD15A | MAROOCHYDORE | Urban | 853.245 | 1.7678 | 5.8188 | 3.944 | 58.9973 | 0.077453 | 2 | 1011367.12 | 41682.34 | 0.0017171 | 0.00085409 | 2 | 2340.3372 | 7.8812e-05
AHD15B | MAROOCHYDORE | Urban | 844.8725 | 2.6366 | 1.1099 | 3.6963 | 7.3635 | 0.032847 | 2 | 141224.2304 | 141224.2304 | 0.00092126 | 0.00092126 | 2 | 1118.3913 | 1.9376e-05
AHD16 | BUDERIM | Urban | 1338.995 | 6.399 | 1.7488 | 3.466 | 2.3453 | 0.36772 | 2 | 127285.06 | 127285.06 | 0.0027068 | 0.0027068 | 2 | 11136 | 4.54e-05
AHD17 | MAROOCHYDORE | Urban | 167 | 0.3645 | 4.2326 | 3.8297
AHD18A | BUDERIM | Urban | 671.375 | 3.3986 | 2.6452 | 3.7535 | 4.8531 | 0 | 4 | 67832.3 | 67832.3 | 0.00079294 | 0.00079294 | 0 | 0 | 0
AHD18B | BLI BLI, MAROOCHYDORE, MUDJIMBA, PACIFIC PARADISE, | Rural short | 2017.2733 | 6.3112 | 14.154 | 4.2584 | 7.4796 | 1.0673 | 2 | 184271.83 | 184271.83 | 0.0062215 | 0.0062215 | 7 | 26901.48 | 0.00058015
AHD19 | ALEXANDRA HEADLAND, MAROOCHYDORE | Urban | 1109.37 | 3.3414 | 1.6125 | 3.2324 | 0.25922 | 0.029089 | 3 | 27861.1933 | 27861.1933 | 0.00031061 | 0.00031061 | 2 | 2554.96 | 1.4538e-05
AHD20 | ALEXANDRA HEADLAND, MAROOCHYDORE | Urban | 1184.6 | 2.3685 | 2.6745 | 4.0012 | 10.4366 | 0.06134 | 4 | 587459.5 | 134093.5 | 0.0014956 | 0.001261 | 1 | 3003 | 5.0545e-05
AHD21 | BUDERIM | Urban | 1289.735 | 2.6439 | 3.7187 | 2.7848 | 38.8968 | 1.6636 | 5 | 1540440.64 | 209988.64 | 0.0039571 | 0.0013529 | 7 | 52173.88 | 0.00019657
AHD22A | MAROOCHYDORE | Urban | 1179.29 | 4.3009 | 4.2333 | 4.4965 | 0.33393 | 0.1752 | 1 | 2975.6 | 2975.6 | 1.7362e-05 | 1.7362e-05 | 1 | 17315.175 | 4.1407e-05
AHD25A | BUDERIM, MAROOCHYDORE | Urban | 1538.25 | 3.9728 | 6.0145 | 5.2216 | 0 | 0.0098627 | 0 | 0 | 0 | 0 | 0 | 2 | 616.86 | 1.0832e-05
AHD3A | MAROOCHYDORE | Urban | 5 | 0 | 2.8405 | 3.0675
AHD4A | BUDERIM, MINYAMA, MOOLOOLABA, MOUNTAIN CREEK | Urban | 584.176 | 5.2874 | 4.2999 | 3.8678 | 25.1348 | 0.20726 | 2 | 413267.14 | 5520.24 | 0.00069585 | 8.152e-05 | 8 | 2201.91 | 1.615e-05
AHD4B | BUDERIM, MAROOCHYDORE | Rural short | 550 | 2.9152 | 3.7986 | 1.9625 | 16.7664 | 0 | 1 | 393250 | 0 | 0.0015758 | 0 | 0 | 0 | 0
AHD5 | ALEXANDRA HEADLAND, MOOLOOLABA | Urban | 2055.0023 | 4.7294 | 1.5177 | 4.2546 | 8.7412 | 0.72998 | 7 | 443288.321 | 95891.701 | 0.0043306 | 0.0022706 | 6 | 72596.8075 | 0.0002391
AHD6 | ALEXANDRA HEADLAND, MAROOCHYDORE | Urban | 557.666 | 1.7998 | 1.4834 | 2.7246 | 0.53649 | 0.28476 | 1 | 1629 | 1629 | 9.0906e-06 | 9.0906e-06 | 4 | 9147.62 | 6.7846e-05
AHD7 | ALEXANDRA HEADLAND, MAROOCHYDORE | Urban | 897.115 | 3.0168 | 0.8993 | 2.6674 | 0 | 0.015206 | 0 | 0 | 0 | 0 | 0 | 2 | 1124.7083 | 1.9242e-05
AHD8 | BUDERIM | Urban | 1132.9577 | 5.0554 | 2.0957 | 3.2771 | 23.6502 | 0.80695 | 7 | 631031.7976 | 157228.93 | 0.0025367 | 0.0012873 | 6 | 19584.84 | 4.9642e-05
AHD9 | MOOLOOLABA | Urban | 423.89 | 5.3123 | 2.3304 | 2.9532 | 3.3776 | 0.020398 | 2 | 56887.28 | 0 | 0.00062513 | 0 | 1 | 50 | 5.041e-06
AHL11A | FERNY GROVE, FERNY HILLS | Urban | 1614.966 | 4.5161 | 7.6218 | 4.4287 | 57.4928 | 0.25216 | 6 | 1735108.4 | 175078.4 | 0.0052861 | 0.0018387 | 4 | 6309 | 7.6569e-05
AHL12A | ARANA HILLS, FERNY HILLS | Urban | 1689.8867 | 7.8258 | 2.5991 | 4.5254 | 0.23654 | 0 | 3 | 6603.3 | 6603.3 | 9.6387e-05 | 9.6387e-05 | 0 | 0 | 0
AHL14A | ARANA HILLS, FERNY HILLS | Urban | 1415.25 | 5.4089 | 0.399 | 4.3251 | 0.77374 | 0.10159 | 3 | 38730.4 | 38730.4 | 0.00074804 | 0.00074804 | 1 | 6384 | 2.1192e-05
AHL15B | EVERTON HILLS, EVERTON PARK, MCDOWALL | Urban | 1728.98 | 7.0995 | 4.8972 | 3.8291 | 133.617 | 0.075205 | 3 | 4228081.14 | 123697.12 | 0.0034437 | 0.0017321 | 1 | 3249 | 1.4602e-05
AHL4A | KEPERRA, MITCHELTON | Urban | 860.4318 | 4.3341 | 0.774 | 2.5652 | 2.9007 | 2.455 | 2 | 72822 | 72822 | 0.00087119 | 0.00087119 | 20 | 69876.205 | 0.0003047
AHL5A | ARANA HILLS, BUNYA, EVERTON HILLS, FERNY HILLS | Rural short | 1223.83 | 13.6825 | 3.6824 | 3.5439 | 0.037304 | 0.040461 | 0 | 0 | 0 | 0 | 0 | 1 | 438 | 2.8515e-06
AHL6A | ARANA HILLS, FERNY GROVE, FERNY HILLS | Urban | 2010.334 | 7.9602 | 3.2878 | 5.2216 | 5.497 | 0.17727 | 10 | 207712.27 | 207712.27 | 0.002536 | 0.002536 | 4 | 6831.6325 | 2.8088e-05
AHL8A | BRIDGEMAN DOWNS, BUNYA, EVERTON HILLS, MCDOWALL | Urban | 1616.7143 | 8.078 | 6.387 | 4.8928 | 0.48596 | 0.42762 | 3 | 16179.99 | 16179.99 | 7.5281e-05 | 7.5281e-05 | 3 | 18634.99 | 6.4e-05
AHL9A | EVERTON HILLS, EVERTON PARK | Urban | 1631.4029 | 6.217 | 1.3073 | 4.0202 | 4.5996 | 0.4042 | 3 | 165456.9 | 165456.9 | 0.0018129 | 0.0018129 | 4 | 23999.68 | 6.9029e-05
AJV1 | FORTITUDE VALLEY | Urban | 167 | 0.1423 | 0.6815 |  | 0.084664 | 0.060195 | 1 | 2320 | 2320 | 4.0092e-05 | 4.0092e-05 | 1 | 736 | 3.2155e-06
ALY3A | ANNERLEY, FAIRFIELD | Urban | 1377.9667 | 3.9082 | 0.0471 | 3.0866 | 24.2022 | 0.087392 | 3 | 1461749.59 | 21482.48 | 0.0016255 | 0.00024202 | 3 | 8231.58 | 3.3354e-05
ALY5 | ANNERLEY, GREENSLOPES, WOOLLOONGABBA | Urban | 2826.1009 | 6.3539 | 1.2025 | 6.2113 | 11.5931 | 1.5926 | 7 | 445820.8229 | 302308 | 0.0046086 | 0.0042807 | 24 | 138230.545 | 0.00050577
ALY6 | ANNERLEY, FAIRFIELD, YERONGA | Urban | 1299.404 | 5.8575 | 1.2171 | 3.3724 | 20.4267 | 0.28666 | 6 | 414778.28 | 114423.08 | 0.0037601 | 0.0029657 | 4 | 12859.3 | 4.3056e-05
ALY8 | ANNERLEY | Urban | 1963.8607 | 4.0884 | 0.3608 | 5.4511 | 7.7502 | 5.1361 | 6 | 156580.7 | 151400.7 | 0.0020062 | 0.0020052 | 21 | 179921.8259 | 0.00050001
ALY9 | YERONGA | Urban | 612.1 | 3.3769 | 2.5537 | 1.9434 | 8.3807 | 0.19994 | 3 | 397851.55 | 25542.45 | 0.0001865 | 8.5911e-05 | 2 | 7668.78 | 3.061e-05
ALYMRK10 | ANNERLEY | Rural short | 102 | 0 | 4.3864 | 0.36201
ALYMRK4 | ANNERLEY | Rural short | 67 | 0 | 1.9208 | 0 | 0.36334 | 0 | 1 | 2948 | 2948 | 0.0001935 | 0.0001935 | 0 | 0 | 0
AMR1 | AMAMOOR, IMBIL, KANDANGA, KANDANGA CREEK, MELAWOND | Rural short | 333.5952 | 59.0701 | 0.2693 | 2.2483 | 1.3403 | 2.0268 | 8 | 25114.46 | 19312.96 | 0.00058469 | 0.00052545 | 17 | 74562.315 | 0.00080019
AMR2 | AMAMOOR, CALICO CREEK, DAGUN, GILLDORA, KANDANGA, | Rural short | 829.0763 | 114.8018 | 0 | 1.6957 | 19.6536 | 7.6361 | 15 | 632491.0223 | 420138.8123 | 0.0097524 | 0.0093112 | 42 | 247008.1865 | 0.0023145
AMR3 | AMAMOOR, BOLLIER, COLES CREEK, COORAN, DAGUN, GOOM | Rural short | 390.125 | 97.2112 | 0.4831 | 1.067 | 66.1834 | 4.3415 | 9 | 1009414.34 | 51753.92 | 0.0026335 | 0.00058779 | 25 | 87251.144 | 0.0009784
ARG10 | ACACIA RIDGE, SUNNYBANK HILLS | Urban | 132.594 | 2.156 | 0.9653 | 4.9157 | 4.2435 | 0 | 5 | 6217.2508 | 6217.2508 | 0.0002192 | 0.0002192 | 0 | 0 | 0
ARG3 | ACACIA RIDGE, COOPERS PLAINS, SUNNYBANK | Urban | 147.51 | 2.4357 | 1.1863 | 4.3632 | 0 | 1.8347 | 0 | 0 | 0 | 0 | 0 | 1 | 968.64 | 4.052e-06
ARG4 | ACACIA RIDGE | Urban | 96.795 | 2.0696 | 0.514 | 3.963 | 0 | 1.7068 | 0 | 0 | 0 | 0 | 0 | 4 | 2242 | 1.1165e-05
ARG5A | ACACIA RIDGE, SUNNYBANK, SUNNYBANK HILLS | Urban | 1562.6743 | 7.419 | 0.969 | 3.3457 | 29.179 | 2.8485 | 11 | 1113769.05 | 367593.27 | 0.0082592 | 0.0066306 | 24 | 117581.9436 | 0.00042613
ARG6 | ACACIA RIDGE, SUNNYBANK HILLS | Urban | 152 | 0.7527 | 2.2269 | 3.601
ARG8 | ACACIA RIDGE | Urban | 7 | 0 | 1.4056 | 2.0196
ARG9A | SUNNYBANK, SUNNYBANK HILLS | Urban | 1143.68 | 4.8797 | 0.9065 | 2.2213 | 0.4581 | 0.25685 | 3 | 17916.075 | 17916.075 | 0.00013889 | 0.00013889 | 5 | 12200.4472 | 5.1535e-05
ARL11A | ARUNDEL, PARKWOOD | Urban | 459.464 | 2.0295 | 3.1186 | 1.7719 | 5.2514 | 0.10509 | 2 | 50200 | 16450 | 0.0009242 | 0.0004693 | 3 | 1782 | 8.9304e-05
ARL11B | ARUNDEL, HELENSVALE | Urban | 661 | 1.6212 | 4.4304 | 1.9053 | 1.4431 | 0 | 1 | 39630 | 0 | 0.0006677 | 0 | 0 | 0 | 0
ARL12A | ARUNDEL, PARKWOOD | Urban | 1349.49 | 1.1098 | 3.4954 | 3.3533 | 10.1207 | 0 | 1 | 257752.59 | 257752.59 | 0.0013552 | 0.0013552 | 0 | 0 | 0
ARL12B | ARUNDEL | Urban | 540 | 0.086 | 4.8239 | 1.3909 | 2.7085 | 0 | 1 | 103140 | 103140 | 0.00054228 | 0.00054228 | 0 | 0 | 0
ARL13A | ARUNDEL, LABRADOR | Urban | 955.0825 | 0.2699 | 6.9015 | 2.7818 | 6.8981 | 0.16602 | 2 | 144502.85 | 97805.85 | 0.0019211 | 0.00096053 | 2 | 4292.71 | 3.9984e-05
ARL15B | ARUNDEL, BIGGERA WATERS, LABRADOR | Urban | 373.9975 | 3.6243 | 2.5338 | 2.5531 | 3.9338 | 0.11489 | 3 | 129326 | 41546 | 0.00049048 | 0.00041365 | 1 | 277 | 1.0022e-06
ARL2B | ARUNDEL, COOMBABAH | Urban | 176.625 | 2.3367 | 3.489 | 4.5156 | 3.0378 | 0.017945 | 1 | 40668.75 | 40668.75 | 0.00017714 | 0.00017714 | 1 | 480.48 | 7.3328e-06
ARL3A | ARUNDEL, PARKWOOD | Urban | 336.5 | 1.7884 | 1.9241 | 1.1241 | 5.486 | 0.040233 | 3 | 83652.18 | 83652.18 | 0.00039089 | 0.00039089 | 1 | 4495.65 | 3.493e-05
ARL5B | BIGGERA WATERS, COOMBABAH, LABRADOR | Urban | 682.68 | 2.3781 | 3.4492 | 2.6293
ARL6B | ARUNDEL, COOMBABAH, LABRADOR | Urban | 209.3333 | 4.3316 | 2.5908 | 4.306 | 93.8532 | 0.65878 | 2 | 246603 | 10830 | 0.00026014 | 5.6933e-05 | 1 | 1060 | 2.0193e-06
ARLSNT3 | ARUNDEL | Urban | 5 | 0.387 | 0.1752 | 1.5052 | 0.20601 | 0.49202 | 1 | 480 | 480 | 5.0211e-06 | 5.0211e-06 | 1 | 1828 | 4.0161e-06
ASV1 | FORTITUDE VALLEY | Urban | 4.5 | 0 | 0.5699
ATC16A | FORTITUDE VALLEY, SPRING HILL | Urban | 491 | 0.6617 | 1.0176 | 3.0104
ATC7A | SPRING HILL | Urban | 7.2 | 0 | 0.4914 | 0.45727
ATCCSA4 | BRISBANE, SPRING HILL | Urban | 76 | 0 | 0.2989 | 0
ATCCSQ11 | SPRING HILL | CBD | 152 | 0 | 0.4473 | 2.8389
ATCIEA9 | SPRING HILL | Urban | 66.4 | 0 | 0.1026 | 3.3694
ATCSGO42 | BRISBANE, SPRING HILL | CBD | 2 | 0 | 0.7788 | 3.4523
BBH10A | BROADBEACH WATERS, BUNDALL, SURFERS PARADISE | Urban | 1449.4314 | 6.5893 | 1.438 | 4.1155 | 3.641 | 1.853 | 2 | 324937.44 | 0 | 0.00032551 | 0 | 12 | 75168.72 | 0.00025461
BBH12B | BROADBEACH WATERS, MERMAID BEACH, MERMAID WATERS | Urban | 1353.5091 | 3.0204 | 3.1055 | 2.6674 | 0.44577 | 1.6322 | 3 | 46900.29 | 46900.29 | 0.00037588 | 0.00037588 | 8 | 64952.5555 | 0.00030325
BBH13B | BROADBEACH, SURFERS PARADISE | Urban | 2140.96 | 1.7635 | 1.9255 | 4.5918 | 3.4694 | 0.624 | 2 | 140520.26 | 140520.26 | 0.002142 | 0.002142 | 2 | 14384.628 | 6.8245e-05
BBH14B | BROADBEACH | Urban | 4 | 0 | 0.8672 | 3.8487
BBH15A | BROADBEACH WATERS | Urban | 0.45 | 0 | 1.6426 | 2.7055
BBH15B | SURFERS PARADISE | Urban | 2 | 0 | 1.4894 | 1.2766
BBH16A | BROADBEACH, MERMAID BEACH | Urban | 2182.5264 | 3.2835 | 1.9879 | 4.9157 | 1.773 | 0.38246 | 3 | 46198.18 | 46198.18 | 0.0017367 | 0.0017367 | 8 | 23106.4297 | 0.00018436
BBH1A | MERMAID WATERS | Rural short | 78.5 | 0.058 | 2.8519 | 0.32715
BBH1B | BROADBEACH WATERS | Urban | 1.45 | 0 | 2.2918 | 3.5058
BBH2A | BROADBEACH, MERMAID BEACH | Urban | 523.83 | 1.0577 | 1.298 | 2.6674 | 0 | 0.041683 | 0 | 0 | 0 | 0 | 0 | 1 | 2735.243 | 7.2482e-06
BBH3A | BROADBEACH, BROADBEACH WATERS, SURFERS PARADISE | Urban | 1411.1933 | 1.2373 | 2.5466 | 3.1438 | 0 | 0.051477 | 0 | 0 | 0 | 0 | 0 | 2 | 3570.07 | 1.1923e-05
BBH4A | BROADBEACH | Urban | 637.34 | 0.2198 | 1.2416 | 3.6772 | 0 | 0.024412 | 0 | 0 | 0 | 0 | 0 | 1 | 47.25 | 2.2549e-06
BBH4B | BROADBEACH | Urban | 120 | 0 | 1.0205 | 2.6674
BBH5A | BROADBEACH | Urban | 4 | 0 | 0.487 | 2.496
BBH7A | BROADBEACH | Urban | 32 | 0 | 1.0765 | 4.7823
BBH7B | BROADBEACH WATERS | Urban | 0.6 | 0 | 2.495 | 3.0485
BBH8A | BROADBEACH WATERS | Urban | 1548.7778 | 4.089 | 1.8701 | 3.9452 | 0.10986 | 4.7757 | 2 | 4366.89 | 4366.89 | 7.0462e-05 | 7.0462e-05 | 16 | 189808.115 | 0.00048092
BBH9A | BROADBEACH | Urban | 2 | 0 | 0.8672 | 2.5531
BBHORW6 | BROADBEACH | Urban | 82 | 0.6864 | 0.93 | 3.7154 | 0 | 0.18592 | 0 | 0 | 0 | 0 | 0 | 1 | 85 | 1.0063e-06
BBS11 | CARINDALE, MANSFIELD | Urban | 1351.6 | 3.1784 | 6.4061 | 3.5058 | 2.1927 | 0.022108 | 4 | 118094.38 | 108743.5 | 0.0023309 | 0.0022696 | 1 | 959.14 | 2.3881e-06
BBS6 | MACKENZIE, MANSFIELD, WISHART | Urban | 712.5433 | 4.5597 | 1.7043 | 1.9815 | 27.2211 | 0.13676 | 2 | 596441.35 | 3991.35 | 0.00055218 | 3.4048e-05 | 1 | 3845.6 | 1.8494e-05
BBS9 | MANSFIELD | Urban | 328.1033 | 1.1914 | 2.9037 | 3.5629 | 0 | 0.50989 | 0 | 0 | 0 | 0 | 0 | 6 | 34559.8089 | 0.00010931
BBSRBW5 | MACKENZIE, MANSFIELD | Urban | 10 | 2.5705 | 0.5006 | 0.25845
BBSRDL8 | BELMONT, BURBANK, CAPALABA WEST, CHANDLER, MACKENZ | Rural short | 1220.6558 | 32.9502 | 3.9387 | 2.9782 | 115.1722 | 1.6342 | 10 | 2026528.3 | 266883.3 | 0.01496 | 0.007538 | 8 | 14303.267 | 0.00015861
BDA12B | ANNERLEY, DUTTON PARK, HIGHGATE HILL, SOUTH BRISBA | Urban | 1616.515 | 4.2477 | 3.9522 | 5.373 | 252.3705 | 0.13391 | 9 | 3556215.025 | 166449.935 | 0.0055241 | 0.0039064 | 3 | 12810.54 | 4.054e-05
BDA13A | ANNERLEY, WOOLLOONGABBA | Urban | 440.9475 | 0.1577 | 4.813 | 4.5918 | 1.921 | 0.29775 | 1 | 14445.42 | 14445.42 | 0.00044201 | 0.00044201 | 3 | 10116.848 | 4.3842e-05
BDA2B | ANNERLEY, SOUTH BRISBANE | Rural short | 2 | 0 | 3.106 | 0.64781
BDA3A | DUTTON PARK, HIGHGATE HILL, WOOLLOONGABBA | Urban | 1321.9225 | 3.8243 | 1.9141 | 2.1149 | 0.95554 | 0.14013 | 2 | 65874.28 | 65874.28 | 0.0013601 | 0.0013601 | 2 | 680.08 | 3.085e-06
BDA5A | WOOLLOONGABBA | Urban | 349.0767 | 1.3208 | 2.1361 | 3.6201 | 0 | 0.29702 | 0 | 0 | 0 | 0 | 0 | 3 | 8381.4399 | 5.2362e-05
BDB23A | BUNDAMBA | Urban | 4 | 0.1427 | 1.3983 | 0.8955
BDB27A | BUNDAMBA, CHUWAR, KARALEE | Rural short | 938.7067 | 12.8381 | 4.7061 | 3.601 | 6.489 | 0.47458 | 8 | 141111.94 | 111009.94 | 0.0059176 | 0.0058346 | 4 | 11666.47 | 0.00013264
BDB28A | DINMORE, RIVERVIEW | Urban | 640.5 | 6.2078 | 1.5186 | 2.877 | 0.099491 | 0.08124 | 0 | 0 | 0 | 0 | 0 | 4 | 6004.52 | 1.9068e-05
BDB32A | BUNDAMBA, CHUWAR, KARALEE, NORTH BOOVAL, NORTH TIV | Rural short | 803.1786 | 13.2056 | 2.979 | 2.2102 | 218.6933 | 1.7072 | 8 | 2469892.01 | 153798.01 | 0.0050731 | 0.0026434 | 4 | 31887.74 | 0.00033121
BDB33A | BUNDAMBA, RIVERVIEW | Urban | 9.5 | 2.8825 | 1.0979 | 5.5826 | 0.15444 | 0.41099 | 1 | 423 | 423 | 9.0732e-06 | 9.0732e-06 | 1 | 360 | 1.0098e-06
BDB35A | BUNDAMBA, EBBW VALE | Urban | 1012.33 | 7.3163 | 1.8466 | 3.4486 | 0.12675 | 0.92266 | 0 | 0 | 0 | 0 | 0 | 4 | 22237.5 | 6.1324e-05
BDB36A | BUNDAMBA, NORTH BOOVAL | Rural short | 1015.5 | 7.8584 | 0.963 | 2.2673 | 0.053573 | 0.09603 | 1 | 2697.42 | 2697.42 | 5.8076e-05 | 5.8076e-05 | 1 | 2310 | 0.00011046
BDB37A | BARELLAN POINT, BUNDAMBA, KARALEE, KARANA DOWNS, R | Rural short | 931.1875 | 18.3243 | 5.3316 | 4.3441 | 4.3608 | 2.3056 | 2 | 169968 | 164688 | 0.00085655 | 0.00081032 | 5 | 80127.94 | 0.00056269
BDB4A | BUNDAMBA, DINMORE, EBBW VALE, NEW CHUM | Rural short | 214.25 | 4.1083 | 2.524 | 0.38867 | 3.4764 | 1.7679 | 1 | 416 | 416 | 1.1528e-05 | 1.1528e-05 | 3 | 1025.31 | 3.3198e-05
BDB6B | RIVERVIEW | Urban | 9 | 4.4338 | 1.5688
BDL1 | BUNDALL | Urban | 100.5 | 1.1734 | 2.5978 | 3.4677 | 3.8088 | 1.2717 | 2 | 11457 | 0 | 0.0002032 | 0 | 1 | 738 | 3.0276e-06
BDL2 | ASHMORE, BENOWA, BUNDALL, SOUTHPORT, SURFERS PARAD | Urban | 1442.4257 | 4.0918 | 3.3145 | 3.5439 | 15.6107 | 0.21189 | 3 | 465064.6 | 855.36 | 0.0028754 | 3.6024e-05 | 4 | 6837.08 | 0.00013673
BDL3 | BUNDALL, SOUTHPORT, SURFERS PARADISE | Urban | 250.5833 | 1.6072 | 1.6889 | 2.5722 | 3.4274 | 4.6257 | 3 | 37219.5 | 8662.5 | 0.00059458 | 8.8093e-05 | 3 | 31871.12 | 9.2427e-05
BDL4 | BENOWA, BUNDALL | Urban | 1687.3345 | 4.4947 | 2.6612 | 4.5918 | 35.1078 | 0.56066 | 7 | 1376246.0882 | 231967.4382 | 0.0070616 | 0.0018438 | 4 | 51068.6778 | 0.00012151
BDL5 | BUNDALL, SOUTHPORT | Urban | 429 | 1.6019 | 3.9174 | 3.3533 | 4.5638 | 0 | 3 | 50111.07 | 1699.83 | 0.00089262 | 3.4003e-05 | 0 | 0 | 0
BDL6 | BUNDALL | Urban | 251.5 | 2.1899 | 1.5955 | 4.3251 | 4.4341 | 0 | 2 | 28671 | 0 | 0.0005085 | 0 | 0 | 0 | 0
BDL7 | BUNDALL, SOUTHPORT | Urban | 269.5 | 1.5403 | 1.4237 | 4.5156 | 3.3075 | 0 | 2 | 30133.62 | 0 | 0.00053445 | 0 | 0 | 0 | 0
BDT1 | BEAUDESERT, CAINBABLE, CANUNGRA, CRYNA, KERRY, NIN | Rural short | 1106.7064 | 101.6196 | 0.5321 | 3.6963 | 37.6692 | 3.8416 | 14 | 750225.22 | 106359.46 | 0.015539 | 0.0079668 | 33 | 96554.74 | 0.00092244
BDT2 | BEAUDESERT, CRYNA | Rural short | 269.8787 | 34.5379 | 0.0571 | 1.4861 | 2.4392 | 0.38617 | 5 | 50176.5 | 19323.5 | 0.0017786 | 0.0010078 | 3 | 7059.0411 | 8.4984e-05
BDT3 | BEAUDESERT, CEDAR VALE, GLENEAGLE, MUNDOOLUN, VERE | Rural short | 685.3462 | 47.7247 | 0.1343 | 1.6576 | 8.4003 | 0.81632 | 5 | 266674.5 | 8136.5 | 0.0064386 | 0.0020887 | 7 | 25743.03 | 0.00020789
BDT4 | ALLENVIEW, BEAUDESERT, CEDAR VALE, GLENEAGLE, VERE | Rural short | 1347.263 | 65.0463 | 1.9924 | 4.9157 | 6.7359 | 5.1474 | 9 | 67903.85 | 62669.89 | 0.0090022 | 0.0052385 | 9 | 17758.16 | 0.0001874
BDT5 | BEAUDESERT, BIDDADDABA, BOYLAND, TABRAGALBA, WONGL | Rural short | 907.8223 | 50.2997 | 3.1565 | 2.0387 | 78.4407 | 4.585 | 14 | 1141228.96 | 54562.99 | 0.011889 | 0.0033733 | 16 | 32297.1753 | 0.00024821
BDT6 | BEAUDESERT | Urban | 435.8333 | 4.9857 | 0.649 | 4.2488 | 1.5022 | 0.023948 | 5 | 13447.15 | 11725.15 | 0.0013606 | 0.00092664 | 1 | 113.025 | 8.299e-07
BGY13A | BURPENGARY | Urban | 263.83 | 1.3874 | 0.3863 | 0.8955 | 0 | 0.18539 | 0 | 0 | 0 | 0 | 0 | 1 | 2239.25 | 8.5041e-06
BGY15A | BURPENGARY, NARANGBA | Urban | 1479.0229 | 9.5269 | 8.5031 | 5.4873 | 95.2968 | 2.2803 | 5 | 2455182.5 | 92412.5 | 0.0044764 | 0.0015274 | 8 | 39650.04 | 0.00013635
BGY17A | BURPENGARY | Urban | 1874.635 | 8.2253 | 4.0598 | 4.4584 | 3.9742 | 0 | 4 | 196286.27 | 196286.27 | 0.0038382 | 0.0038382 | 0 | 0 | 0
BGY3A | BURPENGARY | Urban | 242.51 | 2.5194 | 0.6354 | 3.3915 | 0.14783 | 0.86648 | 1 | 5130 | 5130 | 5.6911e-05 | 5.6911e-05 | 1 | 686.956 | 1.307e-06
BGY5A | BURPENGARY, BURPENGARY EAST, DECEPTION BAY | Rural short | 1006.1453 | 24.4384 | 1.0274 | 3.239 | 66.9221 | 3.2331 | 7 | 1417625.87 | 21488.87 | 0.0042148 | 0.00028377 | 9 | 51479.045 | 0.00049659
BGY6A | BURPENGARY, NARANGBA | Urban | 1803 | 2.8768 | 13.9434 | 5.8112
BHD1A | PALM BEACH | Urban | 1503.085 | 3.216 | 4.0412 | 2.4951 | 0 | 0.6187 | 0 | 0 | 0 | 0 | 0 | 6 | 54023.575 | 0.00018533
BHD20A | BURLEIGH HEADS, BURLEIGH WATERS | Urban | 1347.0343 | 3.8897 | 0.886 | 3.083 | 0.29887 | 0.82184 | 1 | 13433.35 | 0 | 5.5428e-05 | 0 | 6 | 19699.18 | 8.4025e-05
BHD21A | BURLEIGH HEADS, ELANORA, PALM BEACH | Urban | 1167.2213 | 4.7193 | 7.1657 | 3.8098 | 0.39447 | 0.77587 | 2 | 41067 | 9225 | 0.00010981 | 5.117e-05 | 6 | 45738.18 | 0.00014625
BHD23A | BURLEIGH HEADS, CURRUMBIN VALLEY, ELANORA, TALLEBU | Rural short | 1195.6125 | 27.9228 | 3.2809 | 3.8872 | 67.7607 | 4.1941 | 9 | 3098265.18 | 217264.68 | 0.011462 | 0.0042522 | 31 | 189580.175 | 0.0014592
BHD2A | BURLEIGH HEADS, BURLEIGH WATERS, VARSITY LAKES | Urban | 881.5 | 0.0264 | 6.5277 | 1.9053 | 0 | 0.057394 | 0 | 0 | 0 | 0 | 0 | 2 | 743.16 | 2.8347e-06
BHD31A | BURLEIGH HEADS | Urban | 571.8586 | 3.6871 | 2.2118 | 4.9157 | 0.28773 | 0.10007 | 2 | 6234.1667 | 6234.1667 | 0.00013727 | 0.00013727 | 5 | 7203.6008 | 3.455e-05
BHD32B | BURLEIGH HEADS | Urban | 936.71 | 1.0239 | 2.8874 | 2.4197 | 0 | 2.024 | 0 | 0 | 0 | 0 | 0 | 5 | 59943.3388 | 0.00017946
BHD33A | BURLEIGH WATERS | Urban | 868.4 | 1.756 | 3.6825 | 2.6103 | 0.29739 | 1.8859 | 1 | 16825.6 | 16825.6 | 8.5912e-05 | 8.5912e-05 | 4 | 67463.55 | 0.00057721
BHD35A | BURLEIGH HEADS, REEDY CREEK, TALLEBUDGERA, TALLEBU | Rural short | 1406.0909 | 47.1099 | 4.6458 | 4.6414 | 67.9565 | 26.8881 | 13 | 1438944.64 | 217281.64 | 0.0054384 | 0.0013944 | 52 | 445695.595 | 0.0031719
BHD36A | BURLEIGH HEADS, PALM BEACH | Urban | 1022.83 | 2.1161 | 3.5293 | 2.9202 | 0 | 0.069075 | 0 | 0 | 0 | 0 | 0 | 1 | 12897.78 | 5.2759e-05
BHD3A | BURLEIGH WATERS, VARSITY LAKES | Urban | 1255.8333 | 2.7642 | 4.5707 | 3.0675 | 14.3131 | 0.24263 | 2 | 1239317 | 162890 | 0.0024583 | 0.0012663 | 4 | 33237.525 | 0.00013492
BHD41A | BURLEIGH HEADS, REEDY CREEK, VARSITY LAKES | Urban | 1502.898 | 5.3438 | 9.1884 | 4.9843 | 56.2361 | 0.91488 | 5 | 1151544.366 | 12121.216 | 0.0018422 | 0.00012332 | 5 | 18376.54 | 5.0851e-05
BHD42A | BURLEIGH HEADS | Urban | 2 | 0.157 | 1.4722 | 1.6957
BHD44A | BURLEIGH HEADS, BURLEIGH WATERS, MIAMI | Urban | 1979.3988 | 4.8873 | 3.6566 | 4.3851 | 0.20144 | 1.0512 | 4 | 8035.2 | 8035.2 | 8.9008e-05 | 8.9008e-05 | 11 | 68483.4632 | 0.00018822
BHD45B | BURLEIGH WATERS | Urban | 1603.44 | 0.1147 | 7.9853 | 3.4617 | 0 | 0.25903 | 0 | 0 | 0 | 0 | 0 | 3 | 7656.6984 | 7.3055e-05
BHD46A | BURLEIGH HEADS | Urban | 489.6086 | 4.4226 | 1.0642 | 4.0964 | 34.8009 | 9.1041 | 3 | 278815.25 | 22912.25 | 0.00039919 | 7.0895e-05 | 4 | 76448.1534 | 0.00021373
BHD4A | BURLEIGH HEADS, BURLEIGH WATERS | Urban | 21 | 0.6384 | 0.4814 | 3.5058
BHD5A | BURLEIGH HEADS | Urban | 1290.6964 | 4.1922 | 0.9099 | 3.1368 | 0.30465 | 2.2196 | 2 | 20286.66 | 20286.66 | 0.00014485 | 0.00014485 | 7 | 40459.2325 | 0.00013297
BHD7A | BURLEIGH HEADS, ELANORA, PALM BEACH | Urban | 1170.7178 | 2.8488 | 5.5359 | 3.4105 | 2.7157 | 1.2401 | 3 | 99790.99 | 99790.99 | 0.0023543 | 0.0023543 | 6 | 57655.61 | 0.00023484
BHDRCK29 | BURLEIGH HEADS, VARSITY LAKES | Urban | 150.865 | 3.5784 | 2.3602 | 2.7818 | 2.6082 | 5.8775 | 1 | 10263.29 | 10263.29 | 0.00014817 | 0.00014817 | 3 | 3560.612 | 1.3169e-05
BHL1A | BALD HILLS, BRACKEN RIDGE | Urban | 1826.4557 | 1.9256 | 1.9491 | 3.7526 | 0.24632 | 0.47039 | 1 | 3504.9 | 3504.9 | 0.00011739 | 0.00011739 | 6 | 27793.182 | 0.00013954
BHL2A | BALD HILLS, BRIDGEMAN DOWNS, CARSELDINE | Urban | 735.9375 | 9.0078 | 2.2371 | 4.9729 | 2.7059 | 1.1541 | 7 | 64125.5 | 24443 | 0.0010817 | 0.00035316 | 16 | 62966.205 | 0.00021901
BHL3A | BALD HILLS, BRIDGEMAN DOWNS, CARSELDINE | Urban | 1342.415 | 2.568 | 4.7197 | 4.4775 | 5.9164 | 0.35906 | 1 | 116592 | 116592 | 0.0013614 | 0.0013614 | 4 | 13144.2 | 4.5294e-05
BHL4A | BALD HILLS, BRACKEN RIDGE | Rural short | 1400 | 7.3564 | 6.2556 | 3.6949
BHL5A | BALD HILLS, BRACKEN RIDGE | Urban | 1727.2955 | 6.8973 | 6.7802 | 4.8204 | 43.2556 | 2.2623 | 8 | 1161004.19 | 362671.69 | 0.0088731 | 0.005319 | 12 | 40529.1775 | 0.00018112
BHL6A | CARSELDINE | Urban | 733.32 | 0.2175 | 5.3819 | 2.0006 | 0.078453 | 0.23557 | 0 | 0 | 0 | 0 | 0 | 3 | 10054.2255 | 2.6416e-05
BIS1 | BANKSIA BEACH, BELLARA | Rural short | 1249.432 | 4.2025 | 5.14 | 2.7818 | 3.8654 | 1.4322 | 4 | 169393.9 | 166991.5 | 0.0057026 | 0.0056452 | 5 | 38381.24 | 0.00011681
BIS12B | BANKSIA BEACH, WHITE PATCH | Rural short | 1404.496 | 4.2813 | 10.5736 | 3.2523 | 1.0638 | 0.08156 | 3 | 32172.48 | 32172.48 | 0.0041627 | 0.0041627 | 1 | 3501.45 | 4.0371e-05
BIS13A | BONGAREE | Urban | 954.99 | 2.6631 | 4.5087 | 3.3724 | 0.065097 | 0.0033757 | 0 | 0 | 0 | 0 | 0 | 1 | 129.48 | 7.8057e-07
BIS15A | BONGAREE, WOORIM | Urban | 1210.0533 | 9.6251 | 2.4685 | 3.464 | 124.8647 | 0 | 3 | 2875516.6 | 156 | 0.0023472 | 3.9359e-05 | 0 | 0 | 0
BIS16A | BANKSIA BEACH, BELLARA | Urban | 1843.2143 | 6.2769 | 3.1352 | 3.387 | 0.3776 | 0.16297 | 4 | 10078.88 | 10078.88 | 0.0013898 | 0.0013898 | 3 | 6635.32 | 0.00010337
BIS2B | BEACHMERE, BELLARA, WOORIM | Rural short | 1212.465 | 13.095 | 1.5049 | 2.7904 | 52.1841 | 0.4387 | 4 | 1463311.64 | 26179.14 | 0.0066193 | 0.00049641 | 4 | 15967.808 | 0.00012981
BISTPT3 | BELLARA, BONGAREE | Rural short | 1843.8786 | 7.5035 | 5.0303 | 3.1945 | 0.056809 | 0.46865 | 1 | 1542.4 | 1542.4 | 0.0001373 | 0.0001373 | 5 | 24290.115 | 0.00025636
BKD12A | BIRKDALE | Urban | 1713.8867 | 4.2032 | 5.8709 | 4.2145 | 5.1672 | 0.49753 | 4 | 117070.5 | 117070.5 | 0.0018709 | 0.0018709 | 5 | 10385.7886 | 4.1195e-05
BKD13A | ALEXANDRA HILLS, BIRKDALE | Urban | 2045.375 | 8.7491 | 2.1211 | 5.3763 | 6.0336 | 0.50683 | 2 | 141358 | 141358 | 0.0021029 | 0.0021029 | 6 | 21833 | 7.2949e-05
BKD15A | ALEXANDRA HILLS | Urban | 1171.9757 | 6.9549 | 0.3595 | 3.5004 | 4.5842 | 0.015973 | 6 | 92201.9 | 84336.9 | 0.0014051 | 0.0012827 | 1 | 1065.54 | 9.118e-06
BKD16A | BIRKDALE, THORNESIDE | Urban | 1650.415 | 7.8844 | 3.1967 | 3.7907 | 6.4924 | 0 | 4 | 150937.64 | 130144.64 | 0.0034678 | 0.0033798 | 0 | 0 | 0
BKD2B | BIRKDALE, THORNESIDE | Urban | 1273.165 | 6.1064 | 2.4906 | 3.2103 | 4.1063 | 0.066724 | 4 | 251537.395 | 83986.915 | 0.0015055 | 0.0013279 | 4 | 6472.09 | 3.1482e-05
BKD3A | BIRKDALE, WELLINGTON POINT | Urban | 1795 | 6.4872 | 3.9282 | 5.266 | 34.8868 | 0.34224 | 7 | 1408051.16 | 135073 | 0.0040191 | 0.0020679 | 3 | 9548.13 | 4.7531e-05
BKD5B | BIRKDALE, WELLINGTON POINT | Urban | 1773 | 6.5652 | 2.9055 | 3.8291
BLB2A | BALMORAL, BULIMBA, HAWTHORNE | Urban | 1472.3145 | 4.0238 | 1.2472 | 4.1155 | 0.3021 | 0.14541 | 6 | 30707.356 | 30707.356 | 0.00023547 | 0.00023547 | 5 | 4888.2434 | 2.1063e-05
BLB4A | BALMORAL, BULIMBA, MORNINGSIDE | Urban | 1867.9959 | 2.9759 | 0.9742 | 5.1443 | 13.1357 | 4.0479 | 10 | 465862.53 | 239069.91 | 0.003149 | 0.0030754 | 27 | 100455.9621 | 0.00038676
BLB5A | BULIMBA | Urban | 1069.948 | 3.5869 | 0.6496 | 2.8961 | 29.2804 | 1.4434 | 4 | 1087757.97 | 72907.62 | 0.0013419 | 0.00026285 | 6 | 44833.859 | 0.000128
BLB8A | CAMP HILL, HAWTHORNE, MORNINGSIDE | Urban | 1469.8562 | 3.2512 | 3.4465 | 2.7246 | 7.411 | 1.2437 | 5 | 348229.1978 | 66163.9178 | 0.0017504 | 0.0016067 | 9 | 35606.6944 | 0.00012467
BLB8B | BALMORAL, BULIMBA, HAWTHORNE, MORNINGSIDE | Urban | 972.9706 | 5.7434 | 0.8442 | 2.1721 | 0.17943 | 1.2373 | 2 | 5518.26 | 5518.26 | 0.00013639 | 0.00013639 | 15 | 42388.16 | 0.00019597
BLB9A | BULIMBA | Urban | 930.65 | 1.8318 | 2.0277 | 4.1345 | 0.043387 | 0.010298 | 0 | 0 | 0 | 0 | 0 | 2 | 400.04 | 1.3757e-06
BLBNFM6 | HAWTHORNE, MORNINGSIDE | Urban | 1350.7138 | 4.4229 | 2.0491 | 2.9342 | 0.56048 | 1.2374 | 3 | 46244.2 | 46244.2 | 0.00030775 | 0.00030775 | 21 | 71530.7118 | 0.00033256
BLH10A | BEENLEIGH, MOUNT WARREN PARK, STAPYLTON, YATALA | Urban | 411.3333 | 4.0255 | 2.848 | 4.7061 | 9.7992 | 1.6653 | 2 | 35065.5 | 35065.5 | 0.00041124 | 0.00041124 | 7 | 8920.535 | 4.9851e-05
BLH10B | ALBERTON, EAGLEBY | Urban | 2817.658 | 14.5279 | 3.9008 | 6.6114 | 14.6856 | 0.33471 | 5 | 951964.18 | 207164.18 | 0.0026193 | 0.0024656 | 5 | 16275.671 | 8.7443e-05
BLH11B | BEENLEIGH | Urban | 738.3917 | 2.9786 | 1.4531 | 3.963 | 8.0871 | 0.54568 | 4 | 503772.17 | 9145.17 | 0.00024253 | 0.00010807 | 2 | 33259.945 | 0.00010228
BLH12A | BAHRS SCRUB, BANNOCKBURN, BEENLEIGH, BELIVAH, CEDA | Rural short | 1615.8113 | 65.485 | 4.9138 | 5.4301 | 7.0613 | 0.75572 | 7 | 196072.96 | 171694.96 | 0.0042457 | 0.0042285 | 8 | 54806.24 | 0.00078993
BLH12B | BEENLEIGH, EAGLEBY | Urban | 1961.5657 | 11.0471 | 4.3922 | 4.5574 | 0.054216 | 0.72542 | 0 | 0 | 0 | 0 | 0 | 7 | 46002.5304 | 0.00020207
BLH13B | ALBERTON, BEENLEIGH, EAGLEBY, STAPYLTON, YATALA | Rural short | 324.7618 | 29.7862 | 3.4961 | 3.1438 | 172.0553 | 0.65959 | 5 | 1501381.36 | 35703.56 | 0.0028476 | 0.00090302 | 6 | 10519.9 | 0.00011237
BLH14A | BEENLEIGH | Urban | 48 | 0.2734 | 1.9642 | 2.877 | 0.017119 | 0
BLH15B | MOUNT WARREN PARK | Urban | 498.33 | 2.886 | 0.4914 | 1.8291 | 0 | 0.024729 | 0 | 0 | 0 | 0 | 0 | 2 | 3346.3824 | 2.7326e-05
BLH16A | BEENLEIGH | Rural short | 1914.67 | 12.8832 | 0.7709 | 2.9151 | 2.3 | 0.74055 | 2 | 65734.78 | 65734.78 | 0.0056144 | 0.0056144 | 2 | 2656.8 | 3.603e-05
BLH9A | BEENLEIGH | Urban | 422.5 | 2.2928 | 0.8719 | 2.5531 | 0.014143 | 0
BLH9B | MOUNT WARREN PARK | Urban | 1483.1633 | 6.4574 | 2.8406 | 3.8487 | 0.3495 | 0.57724 | 2 | 3025.6 | 3025.6 | 9.6054e-05 | 9.6054e-05 | 1 | 36000 | 0.00010028
BLHSTN16 | ALBERTON, GILBERTON, STAPYLTON, YATALA | Rural short | 341.978 | 9.6072 | 2.301 | 3.3343 | 1.9485 | 0.18479 | 3 | 12771.4122 | 12771.4122 | 0.0010367 | 0.0010367 | 2 | 3416.28 | 4.7611e-05
BLN2B | BEENLEIGH | Urban | 367.3333 | 3.4055 | 0.3218 | 2.3435 | 1.0566 | 0.12913 | 1 | 32864.7 | 32864.7 | 3.8359e-05 | 3.8359e-05 | 2 | 5056.91 | 2.2007e-05
BLN3A | BEENLEIGH | Urban | 2 | 0 | 1.4372 | 2.2864
BLN5B | BEENLEIGH | Urban | 3 | 0 | 1.4372 | 2.5341
BLN6A | BEENLEIGH | Urban | 360.3333 | 2.1014 | 1.9442 | 4.0774 | 67.5259 | 0.036021 | 2 | 594165 | 2475 | 0.00038352 | 1.656e-05 | 1 | 456 | 6.1395e-06
BMG18A | SPRING HILL | Urban | 71.09 | 0 | 2.8673
BMG2A | BRISBANE, PETRIE TERRACE, SPRING HILL | Urban | 292.92 | 0.1327 | 6.0929 |  | 3.2212 | 0.36286 | 4 | 18053.25 | 18053.25 | 0.00058703 | 0.00058703 | 3 | 4441.7624 | 2.9084e-05
BMG3B | MILTON | Urban | 147.81 | 0.6671 | 1.9445 |  | 0.0005803 | 0.12134 | 1 | 533 | 533 | 2.6808e-05 | 2.6808e-05 | 1 | 1761.7353 | 3.1758e-06
BMG44A | MILTON | Urban | 32.08 | 0 | 0.8284 |  | 0 | 0.048848 | 0 | 0 | 0 | 0 | 0 | 1 | 82.194 | 8.0333e-07
BMG9A | AUCHENFLOWER, BRISBANE, MILTON | Urban | 45.5 | 0 | 1.6098
BMG9B | BRISBANE | Urban | 50.5 | 0 | 0.3333
BMT1 | BELLI PARK, BLACK MOUNTAIN, BOLLIER, CARTERS RIDGE | Rural short | 1002.9966 | 115.8192 | 0.893 | 3.0406 | 70.3151 | 6.3721 | 27 | 2580724.088 | 205752.7 | 0.016315 | 0.013396 | 45 | 306350.991 | 0.0031808
BMT2 | BLACK MOUNTAIN, POMONA | Rural short | 1047.1663 | 10.0958 | 0.2204 | 2.521 | 73.8646 | 1.9736 | 20 | 2930230.0167 | 206431.1667 | 0.012951 | 0.010661 | 18 | 94181.62 | 0.00094274
BMT3 | BLACK MOUNTAIN, COOROY | Rural short | 1028.7152 | 2.8254 | 5.2623 | 3.6757 | 74.7217 | 0.96608 | 16 | 4361889.4067 | 94034.7567 | 0.012721 | 0.0082775 | 11 | 34363.33 | 0.00065999
BMT4 | BLACK MOUNTAIN, COOROY, LAKE MACDONALD | Rural short | 693.9964 | 14.4856 | 1.4982 | 2.3435 | 15.8654 | 0.26282 | 6 | 442427.46 | 6893.94 | 0.0061432 | 0.0041353 | 5 | 6941.08 | 0.00030263
BMT5 | BELLI PARK, BLACK MOUNTAIN, COOROY, RIDGEWOOD | Rural short | 320.682 | 35.433 | 0.117 | 0.50035 | 16.7716 | 0.32306 | 5 | 916825.48 | 15288.48 | 0.0038167 | 0.0028754 | 5 | 18932.34 | 0.00031906
BNH1B | BOONAH, BUNBURRA, BUNJURGEN, CANNON CREEK, CHARLWO | Rural short | 634.8583 | 110.0819 | 1.1918 | 1.6576 | 268.5686 | 12.2322 | 11 | 3068927.48 | 43144.08 | 0.0046415 | 0.00072202 | 35 | 138137.83 | 0.0014533
BNH2B | BOONAH, COULSON, HOYA | Rural short | 847.37 | 19.4585 | 2.0236 | 2.5341 | 0.039322 | 1.2081 | 0 | 0 | 0 | 0 | 0 | 8 | 10873.2 | 0.0001547
BNH3A | BOONAH, KENTS POCKET, TEMPLIN | Rural short | 160.7233 | 15.9333 | 0.1997 | 0.32715 | 0 | 0.14572 | 0 | 0 | 0 | 0 | 0 | 3 | 2324.04 | 4.0829e-05
BNH5A | ALLANDALE, BOONAH, COULSON, MILFORD | Rural short | 464.5813 | 24.073 | 0.7869 | 1.2194 | 0.13167 | 0.81157 | 1 | 5786.12 | 5786.12 | 0.00013149 | 0.00013149 | 7 | 13496.092 | 0.00015052
BNH6A | CARNEYS CREEK, COOCHIN, CROFTBY, DUGANDAN, FRENCHE | Rural short | 304.2921 | 109.758 | 0.1338 | 1.7338 | 4.5151 | 12.7503 | 8 | 28576.08 | 28180.08 | 0.00053161 | 0.00052583 | 28 | 98998.04 | 0.00086713
BNZCGA57 | BRISBANE | CBD | 2 | 0 | 0.4119
BPHMST2 | BRISBANE | CBD | 13 | 0 | 0.3738 | 2.1721 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BPN24A | BROWNS PLAINS | Urban | 69 | 0 | 1.2078 | 1.7529 | 0.016775 | 0 | 1 | 855 | 855 | 9.0638e-06 | 9.0638e-06 | 0 | 0 | 0
BPN26A | BORONIA HEIGHTS, BROWNS PLAINS, GREENBANK, PARK RI | Rural short | 881.5714 | 14.4259 | 3.3944 | 4.0774 | 107.3155 | 0.1567 | 6 | 1507028 | 89528 | 0.0054276 | 0.0029207 | 1 | 489 | 8.6387e-06
BPN28A | BROWNS PLAINS, CALAMVALE, DREWVALE, PARKINSON | Rural short | 1415.66 | 7.2594 | 10.0398 | 3.944 | 0.15648 | 0.072367 | 1 | 2484 | 2484 | 0.00026452 | 0.00026452 | 2 | 507.46 | 6.6516e-06
BPN29A | FORESTDALE, HILLCREST | Urban | 1387.8607 | 11.1548 | 1.3951 | 4.0225 | 50.8252 | 3.6966 | 8 | 1182041.82 | 139515.8 | 0.0028565 | 0.0014362 | 5 | 15670.4 | 7.7224e-05
BPN2A | PARKINSON | Urban | 23 | 0 | 2.9375 | 2.9342 | 4.7675 | 2.4515 | 2 | 2341.75 | 2341.75 | 2.4775e-05 | 2.4775e-05 | 1 | 250 | 1.0092e-06
BPN3 | BORONIA HEIGHTS, BROWNS PLAINS, HILLCREST | Urban | 1958.1343 | 11.3325 | 1.9065 | 4.5254 | 4.0036 | 0.073513 | 3 | 206344.5 | 206344.5 | 0.0039896 | 0.0039896 | 3 | 4287.3291 | 1.5811e-05
BPN31A | BROWNS PLAINS, HILLCREST | Urban | 179 | 1.1226 | 0.6202 | 2.1149 | 0.113 | 0 | 1 | 2846.25 | 2846.25 | 4.165e-05 | 4.165e-05 | 0 | 0 | 0
BPN32B | BROWNS PLAINS, REGENTS PARK | Urban | 5.4 | 0 | 2.51 | 1.6576
BPN34A | BORONIA HEIGHTS, GREENBANK, HILLCREST | Urban | 1611.9943 | 13.55 | 2.1079 | 4.6109 | 90.7399 | 0.061382 | 6 | 3010470.62 | 102646.13 | 0.0049561 | 0.0017068 | 1 | 306.24 | 9.5833e-07
BPN35A | REGENTS PARK | Urban | 2139.2 | 4.198 | 0.4019 | 5.5826 | 148.9047 | 0.061983 | 3 | 5787468.06 | 6099.06 | 0.002227 | 6.6998e-05 | 2 | 1420.32 | 8.2938e-06
BPN36A | BROWNS PLAINS, HERITAGE PARK, REGENTS PARK | Urban | 1765.21 | 7.0569 | 3.3605 | 4.306 | 0.046953 | 0.090324 | 0 | 0 | 0 | 0 | 0 | 2 | 7235.76 | 3.6733e-05
BPN4 | BROWNS PLAINS, DREWVALE | Urban | 861.5467 | 4.6756 | 2.2336 | 5.0872 | 3.5454 | 0.22904 | 1 | 71305.3 | 71305.3 | 0.00086354 | 0.00086354 | 2 | 4280.655 | 1.8753e-05
BPN7B | BROWNS PLAINS | Urban | 21 | 0 | 0.4812 | 5.7159 | 2.5287 | 0 | 1 | 2667 | 2667 | 2.1109e-05 | 2.1109e-05 | 0 | 0 | 0
BRCRFW35 | BRISBANE | CBD | 2 | 0 | 0.2711
BRD10B | ALBANY CREEK, BRENDALE | Rural short | 348 | 4.3254 | 2.6662 | 1.2766 | 0.097115 | 0
BRD11A | BRENDALE, CASHMERE, WARNER | Rural short | 967.1625 | 14.5063 | 8.2971 | 4.0202 | 75.4548 | 1.1361 | 9 | 1566022.485 | 14514.985 | 0.0075793 | 0.00041354 | 3 | 23756.8 | 0.0001942
BRD13A | BRAY PARK, BRENDALE, STRATHPINE, WARNER | Urban | 2526.2778 | 4.8106 | 15.98 | 6.1923 | 7.401 | 0.83257 | 3 | 175292.2 | 175292.2 | 0.0026321 | 0.0026321 | 6 | 8548.065 | 4.6319e-05
BRD14B | BRENDALE | Urban | 140 | 1.5493 | 2.312 | 5.3539 | 0.051969 | 1.1584 | 0 | 0 | 0 | 0 | 0 | 1 | 259 | 1.0089e-06
BRD15A | BRENDALE | Urban | 3 | 0 | 0.813 | 2.2543
BRD16A | BRENDALE | Urban | 197.5 | 1.6231 | 1.4246 | 2.6688
BRD2A | BRENDALE, EATONS HILL | Urban | 1760.875 | 1.882 | 9.7217 | 5.8493 | 0.12523 | 0.11216 | 2 | 6196 | 6196 | 0.00014078 | 0.00014078 | 2 | 5706.2 | 1.7013e-05
BRD5A | BRENDALE, CASHMERE, JOYNER, WARNER | Rural short | 1737.6863 | 14.4201 | 9.4913 | 5.4873 | 84.2234 | 3.0116 | 9 | 1863403.6 | 307116.21 | 0.015313 | 0.010486 | 6 | 15339.85 | 0.00011914
BRD8A | BRENDALE, CASHMERE, CLEAR MOUNTAIN, DRAPER, EATONS | Rural short | 1019.4587 | 36.6575 | 2.0905 | 3.3915 | 75.4441 | 5.5793 | 10 | 1413638.27 | 97850.85 | 0.010412 | 0.0073179 | 6 | 100924.22 | 0.00066315
BRT3 | BRIGHTON | Urban | 1059.4286 | 4.4627 | 0.4865 | 1.8 | 0.40936 | 0.33561 | 2 | 28236.6 | 28236.6 | 0.00010313 | 0.00010313 | 5 | 21231.7 | 8.6646e-05
BRT5 | BRIGHTON, SANDGATE | Urban | 1192.535 | 4.3653 | 0.807 | 2.5722 | 0 | 0.33998 | 0 | 0 | 0 | 0 | 0 | 18 | 25042.345 | 0.00014056
BRT6 | BRIGHTON | Urban | 1135.316 | 6.7177 | 0.8322 | 2.5341 | 2.7561 | 0.593 | 1 | 76942 | 76942 | 0.0011394 | 0.0011394 | 9 | 32493.9 | 0.00016982
BRT8 | BRIGHTON, SANDGATE | Urban | 1238.2594 | 4.9513 | 0.209 | 2.5277 | 4.1989 | 0.49654 | 2 | 243545.28 | 1584 | 7.5193e-05 | 1.6475e-05 | 14 | 33068.065 | 0.0001611
BSC3 | BOONDALL | Urban | 12 | 0.9057 | 1.3123 |  | 0 | 0.032528 | 0 | 0 | 0 | 0 | 0 | 1 | 320 | 8.0175e-06
BSEENG15 | ENOGGERA, GAYTHORNE, MITCHELTON | Urban | 1664.6633 | 5.933 | 1.1628 | 3.944 | 2.3763 | 0.05312 | 3 | 169198.6433 | 76636 | 0.0020012 | 0.0016821 | 3 | 2697.8 | 1.1867e-05
BSEWDL9 | MITCHELTON | Rural short | 56 | 0 | 0.4223 |  | 0.025976 | 0
BTA13A | EDENS LANDING, HOLMVIEW | Urban | 1940 | 5.453 | 2.8706 | 4.4454 | 0.025158 | 0.14752 | 0 | 0 | 0 | 0 | 0 | 2 | 6988.4 | 0.00010433
BTA15A | BETHANIA, WATERFORD | Urban | 1238.5 | 8.9852 | 1.2596 | 3.0294 | 0.80386 | 0.20375 | 2 | 24705.3417 | 24705.3417 | 0.0013064 | 0.0013064 | 4 | 7969.68 | 2.954e-05
BTA1A | BETHANIA | Rural short | 1102 | 8.2053 | 1.3925 | 2.6172
BTA3A | BEENLEIGH, BETHANIA, EDENS LANDING, HOLMVIEW, WATE | Rural short | 791.5 | 4.5614 | 6.1368 | 2.7246 | 2.4737 | 0 | 1 | 79260 | 79260 | 0.0022626 | 0.0022626 | 0 | 0 | 0
BTA5A | BAHRS SCRUB, BETHANIA, BUCCAN, HOLMVIEW, WATERFORD | Rural short | 1691.6176 | 25.6317 | 9.6566 | 4.0393 | 143.8269 | 0.77083 | 10 | 6059876.25 | 185841.75 | 0.019938 | 0.010039 | 6 | 38919.06 | 0.00031736
BTN1 | BROMELTON, JOSEPHVILLE | Urban | 27 | 4.7796 | 0 | 3.239 | 0.23025 | 0 | 2 | 2046 | 2046 | 5.455e-05 | 5.455e-05 | 0 | 0 | 0
BTN2 | ALLENVIEW, BEAUDESERT, BROMELTON, GLENEAGLE, WYARA | Rural short | 154.5263 | 50.4253 | 0.7993 | 0.97171 | 2.7395 | 4.9376 | 5 | 5754.5 | 5754.5 | 0.00065076 | 0.00065076 | 13 | 27070.55 | 0.00041838
BTN3 | BROMELTON, JOSEPHVILLE, KOORALBYN, LARAVALE | Rural short | 895.915 | 36.6607 | 4.364 | 1.9052 | 6.658 | 0 | 4 | 319955.51 | 319955.51 | 0.01029 | 0.01029 | 0 | 0 | 0
BTN4 | BEAUDESERT, BROMELTON | Urban | 7.77 | 1.9968 | 0.3097 | 2.6103 | 0.36736 | 0.081509 | 2 | 458.98 | 458.98 | 1.7489e-05 | 1.7489e-05 | 1 | 444 | 2.0073e-06
BTN6 | BROMELTON | Urban | 7.3333 | 0.7238 | 0.1325 | 0.91455 | 0.23035 | 0.32918 | 2 | 1232 | 1232 | 1.4136e-05 | 1.4136e-05 | 1 | 2275 | 7.0631e-06
BTN7 | BEAUDESERT, BROMELTON, ILBOGAN, JOSEPHVILLE, KOORA | Rural short | 70.9857 | 25.4715 | 0.4812 | 3.8628 | 19.9398 | 1.5481 | 4 | 58567.35 | 12228.96 | 0.00084467 | 0.00065486 | 3 | 917.397 | 1.2212e-05
BVL10A | BOOVAL, EAST IPSWICH, NEWTOWN | Urban | 769.4029 | 1.7465 | 0.5021 | 1.8672 | 0.25664 | 0.43801 | 1 | 15353.592 | 15353.592 | 0.00014966 | 0.00014966 | 6 | 16841.2946 | 7.981e-05
BVL13A | EASTERN HEIGHTS, RACEVIEW, SILKSTONE | Urban | 1401.3019 | 5.9901 | 0.7412 | 3.8487 | 0.17642 | 1.0633 | 3 | 16239.57 | 16239.57 | 0.00014336 | 0.00014336 | 12 | 51551.675 | 0.0002243
BVL15A | BOOVAL | Urban | 479.5 | 1.6495 | 1.2068 | 4.7633 | 0 | 0.57825 | 0 | 0 | 0 | 0 | 0 | 3 | 8941.17 | 4.7533e-05
BVL2A | BASIN POCKET, BOOVAL, EAST IPSWICH, NORTH BOOVAL | Urban | 1673.0629 | 7.4338 | 0.0164 | 3.4424 | 0.16528 | 4.411 | 2 | 13218.43 | 13218.43 | 0.00021597 | 0.00021597 | 5 | 15584.6942 | 7.4171e-05
BVL3A | EASTERN HEIGHTS, IPSWICH, NEWTOWN | Urban | 1226.0907 | 6.2846 | 0.3028 | 2.7519 | 3.0139 | 0.94782 | 1 | 162674.56 | 0 | 0.0012293 | 0 | 13 | 46940.4524 | 0.00015907
BVL5A | FLINDERS VIEW, RACEVIEW, SILKSTONE | Urban | 1874.231 | 11.5023 | 1.582 | 4.7442 | 75.3103 | 0.32474 | 5 | 2482637.26 | 182115.26 | 0.0057502 | 0.002041 | 5 | 25098.35 | 8.6269e-05
BVL9A | NORTH BOOVAL | Urban | 457 | 3.4629 | 0 | 0.98146
BVLNCM7 | BOOVAL, BUNDAMBA, NEW CHUM, SILKSTONE | Urban | 1291.415 | 9.6366 | 1.3748 | 4.3441 | 0.20584 | 0.061516 | 1 | 1314 | 1314 | 1.8054e-05 | 1.8054e-05 | 1 | 980.925 | 6.7925e-06
BWH12A | BEERWAH, GLASSHOUSE MOUNTAINS, PEACHESTER | Rural short | 650.2948 | 42.9939 | 2.3158 | 2.0196 | 167.5873 | 3.9946 | 10 | 1526153.08 | 89422.44 | 0.0032228 | 0.0020329 | 11 | 111197.33 | 0.0011299
BWH13A | BEERWAH, BOOROOBIN, CROHAMHURST, MALENY, PEACHESTE | Rural short | 653.3888 | 53.0579 | 0.9002 | 1.3731 | 172.855 | 2.1524 | 8 | 4224422.07 | 55413.05 | 0.0062817 | 0.00213 | 9 | 35834.02 | 0.00036199
BWH16A | BEERWAH, COOCHIN CREEK, GLASSHOUSE MOUNTAINS | Rural short | 1553.6776 | 36.2487 | 3.489 | 4.7633 | 58.0833 | 3.4745 | 7 | 1302602.14 | 20831.4 | 0.002722 | 0.00091121 | 20 | 68095.4804 | 0.00089328
BWH7A | BEERWAH, GLASSHOUSE MOUNTAINS | Rural short | 1100.9669 | 26.9001 | 3.2216 | 3.9821 | 152.1091 | 1.0866 | 8 | 1817609.97 | 11668.96 | 0.0037139 | 0.00030732 | 4 | 19287.235 | 0.00024209
BWH8A | BEERBURRUM, BEERWAH, GLASSHOUSE MOUNTAINS | Rural short | 1267.3538 | 23.2442 | 3.0044 | 2.4109 | 2.4929 | 9.0419 | 7 | 28682.85 | 28682.85 | 0.00078288 | 0.00078288 | 9 | 74864.333 | 0.00047892
CBT12A | BEERBURRUM, CABOOLTURE, ELIMBAH | Rural short | 1597.1071 | 56.5552 | 4.4586 | 4.2488 | 195.5109 | 3.4207 | 9 | 2252536.2667 | 24837.6867 | 0.0072786 | 0.0026502 | 4 | 49266 | 0.00030445
CBT13A | CABOOLTURE | Urban | 1381.9844 | 1.7075 | 8.8259 | 4.306 | 0.183 | 1.2841 | 1 | 1531.3775 | 1531.3775 | 3.2716e-05 | 3.2716e-05 | 8 | 18150.76 | 8.5749e-05
CBT4A | CABOOLTURE | Urban | 862.99 | 4.6833 | 7.0631 | 3.0104 | 0 | 0.59859 | 0 | 0 | 0 | 0 | 0 | 1 | 5356 | 1.3063e-05
CBT7A | CABOOLTURE | Urban | 1115.31 | 6.5244 | 1.5791 | 4.2107 | 0 | 0.063488 | 0 | 0 | 0 | 0 | 0 | 2 | 1534.7155 | 5.8554e-06
CBT8A | CABOOLTURE, DONNYBROOK, ELIMBAH, MELDALE, TOORBUL | Rural short | 1422.3608 | 44.8997 | 3.7345 | 3.8487 | 14.0944 | 2.0957 | 5 | 200668.69 | 200668.69 | 0.012741 | 0.012741 | 8 | 18557.2074 | 0.0001975
CBW10 | BELLMERE, UPPER CABOOLTURE | Rural short | 1053.2143 | 12.9774 | 3.3274 | 2.2292 | 5.1286 | 0.48587 | 2 | 226582 | 2035 | 0.0031029 | 0.00010588 | 4 | 27766.1 | 0.00022796
CBW11 | CABOOLTURE, ELIMBAH, MOODLU, WAMURAN | Rural short | 1771.8311 | 54.3931 | 2.6603 | 4.8585 | 43.6741 | 4.5372 | 18 | 1619894.2874 | 399980.83 | 0.026582 | 0.010442 | 36 | 113675.14 | 0.0012629
CBW12 | CABOOLTURE, CABOOLTURE SOUTH | Urban | 931.0167 | 4.5175 | 1.4668 | 2.7818 | 0.81246 | 0.074394 | 5 | 38658.379 | 28506.259 | 0.0013837 | 0.00045066 | 4 | 7064.6295 | 2.4016e-05
CBW13 | MOODLU, WAMURAN | Rural short | 317.6923 | 9.5778 | 4.049 | 0.95266 | 1.6457 | 0.83554 | 4 | 43355.4267 | 39868.4267 | 0.0019301 | 0.0010218 | 9 | 25430.25 | 0.00035047
CBW14 | CABOOLTURE | Urban | 568.605 | 3.4982 | 0.8115 | 1.3718 | 0.19611 | 0.13983 | 1 | 6117.87 | 0 | 0.00056228 | 0 | 1 | 10329.51 | 2.7726e-05
CBW4 | CABOOLTURE, CABOOLTURE SOUTH | Urban | 88.5 | 0.2206 | 0.9099 | 3.582 | 0.20919 | 0 | 1 | 973.5 | 0 | 8.9472e-05 | 0 | 0 | 0 | 0
CBW5 | CABOOLTURE | Urban | 770.25 | 4.8272 | 0.4998 | 2.3054 | 3.2624 | 0.18753 | 5 | 137220.99 | 128907.74 | 0.00239 | 0.001626 | 2 | 17109.468 | 4.8855e-05
CBW6 | BELLMERE, CABOOLTURE SOUTH, MOORINA, OCEAN VIEW, R | Rural short | 2204.295 | 47.3687 | 7.3625 | 5.3349 | 56.3821 | 0.25105 | 10 | 2538392.22 | 319620.4 | 0.037233 | 0.012624 | 7 | 17875.4139 | 0.00027948
CBW7 | BELLMERE, CABOOLTURE, MOODLU | Rural short | 1365.5682 | 18.9082 | 1.062 | 3.1628 | 2.0596 | 0.40454 | 8 | 130928.96 | 65790.96 | 0.0085419 | 0.0042284 | 9 | 16177.11 | 0.00024547
CBW8 | CABOOLTURE | Rural short | 147 | 2.5432 | 0.2512 | 0.66686
CBW9 | CABOOLTURE | Rural short | 421 | 4.7452 | 2.5991 | 1.7077
CCY12A | OXENFORD, PACIFIC PINES | Urban | 1301.08 | 1.7267 | 6.4742 | 2.9782
CCY13A | HELENSVALE | Urban | 1278.55 | 6.348 | 4.5988 | 3.944 | 0.49788 | 1.117 | 4 | 13741.1 | 13741.1 | 8.173e-05 | 8.173e-05 | 6 | 27774.24 | 0.00010232
CCY14B | HELENSVALE | Urban | 774 | 0 | 9.3625 | 3.3533 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CCY15A | HELENSVALE | Urban | 1 | 0 | 4.9998 | 2.0958 | 0 | 1.8244 | 0 | 0 | 0 | 0 | 0 | 1 | 96 | 8.0326e-07
CCY18A | OXENFORD | Urban | 1.72 | 0 | 2.2377 | 1.3147
CCY1B | COOMERA, HELENSVALE, OXENFORD, UPPER COOMERA | Urban | 846.9167 | 4.6499 | 4.5506 | 5.2205 | 10.9781 | 1.5215 | 3 | 327307.55 | 353.05 | 0.00085816 | 8.4323e-06 | 3 | 117235.54 | 0.00020356
CCY20A | OXENFORD | Urban | 1.48 | 0 | 1.6795 | 2.5722
CCY24B | HELENSVALE, HOPE ISLAND | Urban | 451 | 4.0127 | 2.0183 | 0
CCY25A | OXENFORD, PACIFIC PINES | Urban | 1864.83 | 0 | 12.9609 | 4.5727 | 0.047747 | 0 | 1 | 857.65 | 857.65 | 1.0133e-05 | 1.0133e-05 | 0 | 0 | 0
CCY26A | OXENFORD, UPPER COOMERA | Rural short | 1587 | 7.0196 | 10.1986 | 4.7442
CCY3B | HELENSVALE | Urban | 1227.798 | 1.4097 | 7.0809 | 3.582 | 2.6265 | 0.17071 | 3 | 69742.787 | 69742.787 | 0.0012724 | 0.0012724 | 2 | 6595.77 | 7.8018e-05
CCY4A | HELENSVALE, OXENFORD | Urban | 3.56 | 0 | 3.2476 | 2.9342
CCY6A | COOMERA, HELENSVALE, OXENFORD | Urban | 624.99 | 5.0188 | 1.8454 | 6.1923
CCY7A | OXENFORD, UPPER COOMERA | Rural short | 1247 | 4.6556 | 10.7743 | 3.5439 | 0.030755 | 0.043928 | 0 | 0 | 0 | 0 | 0 | 2 | 499.36 | 5.5543e-06
CCY8A | GAVEN, HELENSVALE, OXENFORD, PACIFIC PINES | Rural short | 872.2 | 5.7525 | 8.3149 | 2.3626 | 0.018766 | 1.4589 | 1 | 442 | 442 | 9.9196e-06 | 9.9196e-06 | 7 | 17877.38 | 0.00017307
CCYUPC2 | MAUDSLAND, OXENFORD, PACIFIC PINES | Rural short | 1753.08 | 5.4946 | 11.1739 | 4.2488
CCYUPC23 | MAUDSLAND, OXENFORD, UPPER COOMERA | Urban | 528.5 | 4.7432 | 3.0139 | 3.4677 | 1.5672 | 2.7787 | 1 | 17969 | 17969 | 0.00053372 | 0.00053372 | 3 | 44772.62 | 0.00014031
CDKQPT25 | MORNINGSIDE | Urban | 4 | 0 | 2.1319 | 2.3435 | 0 | 0.10011 | 0 | 0 | 0 | 0 | 0 | 1 | 21.78 | 9.8877e-07
CDRSPD12 | SURFERS PARADISE | Urban | 1581.3333 | 2.1336 | 0.5805 | 2.2292 | 1.4499 | 0.32682 | 2 | 134355.08 | 134355.08 | 0.0016142 | 0.0016142 | 3 | 37386.63 | 0.00016142
CDRSPD9 | SURFERS PARADISE | Urban | 762.8333 | 1.0415 | 2.7188 | 3.083 | 0.32902 | 0 | 1 | 11417 | 11417 | 4.9502e-05 | 4.9502e-05 | 0 | 0 | 0
CDSSRD21 | CARINDALE | Urban | 6 | 0 | 2.4932 | 2.6865
CDSSRD23 | CARINDALE | Urban | 435 | 0 | 3.9674 | 3.4677 | 0 | 0.43171 | 0 | 0 | 0 | 0 | 0 | 2 | 1403.35 | 8.6576e-06
CDSSRD25 | CARINA HEIGHTS, CARINDALE | Urban | 146.5 | 0 | 1.2482 | 4.0393
CEP6 | HERSTON | Urban | 2 | 0 | 0.392
CEP7 | HERSTON | Urban | 2 | 0 | 0.1788
CFD1A | ASCOT, CLAYFIELD | Urban | 1635.293 | 4.1644 | 0.4036 | 4.0979 | 11.9287 | 2.9225 | 3 | 376984.76 | 30851.25 | 0.0018543 | 0.0001423 | 23 | 104093.47 | 0.00033325
CFD2A | CLAYFIELD, WOOLOOWIN | Urban | 1385.3618 | 4.2943 | 0.4099 | 2.566 | 1.6119 | 1.8114 | 5 | 70832.49 | 44559.49 | 0.0010414 | 0.00042439 | 27 | 122827.5 | 0.00047587
CFD6A | ALBION, BOWEN HILLS, CLAYFIELD, WINDSOR, WOOLOOWIN | Urban | 2199.6981 | 6.1158 | 0.6539 | 3.8678 | 61.7562 | 0.33656 | 9 | 3295965.52 | 63024.52 | 0.0069582 | 0.0025896 | 7 | 24969.155 | 9.5855e-05
CFD8A | ALBION, BOWEN HILLS, CLAYFIELD | Urban | 1252.7475 | 3.2083 | 1.708 | 4.1155 | 5.2114 | 0.068707 | 5 | 98578.015 | 98578.015 | 0.0014705 | 0.0014705 | 3 | 2691.375 | 1.7788e-05
CFD9A | KEDRON, WOOLOOWIN | Urban | 5.83 | 0 | 2.7856 | 2.5341 | 1.8549 | 0 | 1 | 413.93 | 413.93 | 5.8556e-06 | 5.8556e-06 | 0 | 0 | 0
CGT1 | BOWEN HILLS, NEWSTEAD | Urban | 509.67 | 0.2421 | 1.2034 |  | 0.11704 | 0 | 1 | 242.88 | 0 | 2.6659e-06 | 0 | 0 | 0 | 0
CGT5 | BOWEN HILLS, NEWSTEAD, TENERIFFE | Urban | 141.49 | 0.557 | 1.7052 |  | 0 | 0.0086986 | 0 | 0 | 0 | 0 | 0 | 1 | 121.5 | 1.2201e-06
CGTMLS4 | FORTITUDE VALLEY, NEWSTEAD | Urban | 229 | 0 | 3.1491 | 2.9723
CHL10 | CAMP HILL, CARINA | Urban | 1019.9914 | 3.7272 | 0.3557 | 2.282 | 10.2378 | 0.21943 | 1 | 464503.41 | 0 | 0.001023 | 0 | 6 | 8594.1645 | 3.2999e-05
CHL11A | MORNINGSIDE, NORMAN PARK, SEVEN HILLS | Urban | 1872 | 7.0833 | 3.1502 | 4.1579
CHL2 | CAMP HILL, COORPAROO | Urban | 1425.896 | 5.1579 | 0.2877 | 2.9532 | 0.12922 | 0.21189 | 2 | 3805.65 | 3805.65 | 0.00012241 | 0.00012241 | 3 | 12096.235 | 4.3541e-05
CHL3 | CAMP HILL, COORPAROO, NORMAN PARK, SEVEN HILLS | Urban | 1795.3462 | 6.2984 | 0.3316 | 3.6744 | 0.55183 | 0.5393 | 3 | 20834.6 | 20834.6 | 0.00018995 | 0.00018995 | 10 | 30371.055 | 0.00011292
CHL4 | CANNON HILL, MORNINGSIDE, SEVEN HILLS | Urban | 1399.1364 | 5.7084 | 1.6426 | 3.0362 | 4.2625 | 0.08285 | 8 | 240357.28 | 92956 | 0.0045874 | 0.0030782 | 3 | 4768.035 | 1.5119e-05
CHL5 | CAMP HILL, CARINA, CARINA HEIGHTS | Urban | 2034.3986 | 5.7563 | 0.7529 | 4.0225 | 5.3011 | 0.46861 | 3 | 296510.21 | 296510.21 | 0.0022095 | 0.0022095 | 4 | 19844.53 | 7.2695e-05
CHL6A | CAMP HILL, CARINA HEIGHTS | Urban | 1885.436 | 5.3113 | 1.9828 | 3.9258 | 0.4194 | 0.12317 | 2 | 18923.02 | 18923.02 | 0.00021028 | 0.00021028 | 3 | 6276.87 | 2.0136e-05
CHL7 | CAMP HILL, CANNON HILL, CARINA, SEVEN HILLS | Urban | 1511.5 | 5.9769 | 2.5938 | 4.306 | 6.3635 | 0.33487 | 4 | 161325.57 | 161325.57 | 0.0031494 | 0.0031494 | 7 | 16695.175 | 5.6914e-05
CHL8 | CAMP HILL | Urban | 530.38 | 2.5662 | 0.0059 | 1.6438 | 2.1276 | 0.67383 | 2 | 50022.9 | 50022.9 | 0.00059081 | 0.00059081 | 4 | 39810.545 | 9.4709e-05
CHL9 | CARINA, CARINDALE | Rural short | 273.84 | 1.7503 | 2.1286 | 0.74307 | 0.21857 | 0.13498 | 1 | 12229.8 | 0 | 0.00010346 | 0 | 1 | 2497.187 | 2.5077e-05
CLD11 | BELLS CREEK, CALOUNDRA WEST, LITTLE MOUNTAIN, MERI | Rural short | 1569.4071 | 10.1755 | 10.6997 | 4.2145 | 5.2547 | 0.13305 | 6 | 179042.98 | 179042.98 | 0.0046077 | 0.0046077 | 1 | 8160 | 0.00011467
CLD16A | CALOUNDRA, CURRIMUNDI, MOFFAT BEACH | Urban | 167.5 | 4.3537 | 1.0746 | 1.8482 | 0 | 0.38254 | 0 | 0 | 0 | 0 | 0 | 1 | 4600.2 | 1.7495e-05
CLD17A | CALOUNDRA, MOFFAT BEACH, SHELLY BEACH | Urban | 1722.8745 | 5.7464 | 0.4903 | 3.8872 | 14.2529 | 1.1258 | 6 | 744897.2397 | 219602.5897 | 0.0037318 | 0.0020807 | 5 | 52740.2198 | 0.0001609
CLD18A | BELLS CREEK, LITTLE MOUNTAIN, MERIDAN PLAINS | Rural short | 41.35 | 9.7898 | 10.3916 | 2.4007 | 0.21521 | 0.34428 | 1 | 534 | 534 | 5.7198e-06 | 5.7198e-06 | 3 | 881 | 1.1473e-05
CLD1A | CALOUNDRA WEST, LITTLE MOUNTAIN | Urban | 1322 | 3.5457 | 7.9175 | 3.6729 | 0 | 0.35051 | 0 | 0 | 0 | 0 | 0 | 1 | 18767 | 0.00019334
CLD2 | CALOUNDRA, GOLDEN BEACH, PELICAN WATERS | Urban | 2099.9414 | 7.2746 | 3.8108 | 4.7768 | 0.75005 | 0.050208 | 4 | 33752.122 | 33752.122 | 0.0003138 | 0.0003138 | 3 | 4194.326 | 3.1696e-05
CLD20A | AROONA, BATTERY HILL, CALOUNDRA, CURRIMUNDI, DICKY | Urban | 1404 | 7.6624 | 3.0476 | 3.8867
CLD21A | CALOUNDRA, PELICAN WATERS | Rural short | 1081 | 0 | 14.4879 | 3.7723 | 0 | 0.040046 | 0 | 0 | 0 | 0 | 0 | 1 | 764.4 | 9.3267e-05
CLD22A | KINGS BEACH | Urban | 1852.6043 | 2.1083 | 2.4904 | 3.362 | 0.0065012 | 0.20063 | 1 | 552.1628 | 552.1628 | 4.1951e-06 | 4.1951e-06 | 6 | 1927.618 | 4.0113e-05
CLD25A | CALOUNDRA, KINGS BEACH, MOFFAT BEACH, SHELLY BEACH | Urban | 1018.5783 | 2.7606 | 0.6544 | 2.9733 | 0.91464 | 0.97233 | 1 | 26957.04 | 0 | 0.00030967 | 0 | 5 | 26107.2015 | 6.5939e-05
CLD26A | CALOUNDRA | Urban | 230 | 1.8437 | 0.5705 | 3.239 | 0.029111 | 0
CLD28A | BEERWAH, BELLS CREEK, COOCHIN CREEK, GOLDEN BEACH, | Rural short | 1401.5473 | 25.0923 | 12.6568 | 4.564 | 54.6242 | 1.0851 | 7 | 419648.48 | 35202.5 | 0.001096 | 0.0004647 | 3 | 21717.01 | 0.0001518
CLD3 | CALOUNDRA, CALOUNDRA WEST | Urban | 209.5 | 4.3804 | 0.903 | 3.4867 | 0 | 0.31981 | 0 | 0 | 0 | 0 | 0 | 1 | 6528 | 2.4261e-05
CLD30A | DICKY BEACH, MOFFAT BEACH | Urban | 1076.6364 | 4.084 | 1.9124 | 2.4825 | 4.4198 | 0.87738 | 5 | 136182.8 | 136182.8 | 0.00043085 | 0.00043085 | 6 | 67083.19 | 0.00019287
CLD7A | CALOUNDRA, KINGS BEACH | Urban | 1551.3 | 0.8429 | 2.3502 | 3.4867 | 0 | 0.12763 | 0 | 0 | 0 | 0 | 0 | 3 | 7221.2446 | 4.7183e-05
CLD8 | CALOUNDRA | Urban | 672.33 | 1.2082 | 1.5334 | 3.3533 | 0 | 0.20853 | 0 | 0 | 0 | 0 | 0 | 1 | 4170.27 | 1.9043e-05
CLD9A | CALOUNDRA, GOLDEN BEACH | Urban | 1220.255 | 4.5371 | 1.2112 | 3.6744 | 0 | 0.059638 | 0 | 0 | 0 | 0 | 0 | 2 | 6303.42 | 3.4744e-05
CLM3 | BLI BLI, COOLUM BEACH, MARCOOLA, MOUNT COOLUM, NOR | Rural short | 1696.2594 | 45.1735 | 13.888 | 3.8106 | 1.4981 | 2.7489 | 5 | 47620.13 | 5050.13 | 0.00047352 | 0.00044774 | 10 | 40246.62 | 0.00040893
CLM4A | COOLUM BEACH, MOUNT COOLUM, YAROOMBA | Urban | 680.2143 | 2.7239 | 3.6916 | 2.3816 | 2.4447 | 0.77053 | 2 | 26755.5 | 26755.5 | 0.00070362 | 0.00070362 | 5 | 20965.74 | 9.548e-05
CLM5 | COOLUM BEACH, POINT ARKWRIGHT, YAROOMBA | Urban | 1833.3684 | 5.324 | 1.8698 | 4.099 | 2.2217 | 1.143 | 6 | 138567 | 91005 | 0.0026279 | 0.0024101 | 12 | 70188.555 | 0.00024548
CLM6 | COOLUM BEACH, PEREGIAN BEACH, PEREGIAN SPRINGS, WE | Urban | 1814.0256 | 11.9452 | 1.6172 | 3.9839 | 5.9347 | 0.99699 | 3 | 128506.35 | 128506.35 | 0.0024368 | 0.0024368 | 11 | 74564.96 | 0.00030931
CLM7 | COOLUM BEACH | Urban | 1028.25 | 3.0059 | 0.6475 | 2.108 | 0.10355 | 0.50376 | 0 | 0 | 0 | 0 | 0 | 10 | 33853.355 | 0.00015711
CLM8 | COOLUM BEACH, MOUNT COOLUM, YAROOMBA | Urban | 1416.1389 | 6.1667 | 1.6369 | 2.9782 | 0.82654 | 0.76889 | 5 | 62043.7 | 56591.7 | 0.00043209 | 0.00031483 | 11 | 56808.315 | 0.00023376
CLM9 | COOLUM BEACH, MARCOOLA, MOUNT COOLUM | Urban | 2036.1 | 8.5933 | 6.1175 | 4.506 | 0.22878 | 3.1637 | 3 | 1994.3 | 1994.3 | 9.939e-05 | 9.939e-05 | 12 | 190936.265 | 0.00051909
CLR3 | BELMONT, CHANDLER, GUMDALE | Rural short | 180.434 | 5.5406 | 0.1731 |  | 1.8392 | 0.065189 | 3 | 34233.95 | 3690.05 | 0.0011079 | 0.00059307 | 2 | 2536 | 4.3934e-05
CLR8 | CHANDLER | Rural short | 58.99 | 1.4965 | 1.5285 |  | 0.41967 | 0 | 1 | 4955.16 | 4955.16 | 0.0001698 | 0.0001698 | 0 | 0 | 0
CLRSRD17 | BELMONT, CARINDALE, CHANDLER | Urban | 762.1 | 9.0248 | 2.4546 | 4.306 | 3.5912 | 0.11163 | 4 | 135804.08 | 8085.08 | 0.00015046 | 8.0709e-05 | 2 | 5085.3 | 1.3869e-05
CMA10A | COOMERA, UPPER COOMERA | Rural short | 815 | 2.5656 | 14.9473 | 3.4296 | 5.218 | 0.050573 | 1 | 43142 | 43142 | 0.0023219 | 0.0023219 | 1 | 1404 | 4.0564e-05
CMA11A | COOMERA | Urban | 534 | 2.6258 | 5.5901 | 2.5341 | 3.4546 | 0.18218 | 1 | 28461 | 28461 | 0.00053742 | 0.00053742 | 1 | 194 | 2.0213e-06
CMA15A | UPPER COOMERA | Urban | 1698 | 3.5934 | 13.1992 | 6.0017 | 7.163 | 0 | 2 | 91006 | 91006 | 0.0017135 | 0.0017135 | 0 | 0 | 0
CMA20A | UPPER COOMERA | Urban | 1335.25 | 0.8408 | 8.5058 | 4.0393 | 3.992 | 0.2331 | 1 | 70808 | 70808 | 0.0013371 | 0.0013371 | 2 | 4187.9 | 5.1877e-05
CMA8A | PIMPAMA, UPPER COOMERA, WILLOW VALE | Rural short | 1898.6744 | 19.2706 | 16.4755 | 5.2968 | 7.1414 | 2.6801 | 10 | 150942.3142 | 150942.3142 | 0.0062658 | 0.0062658 | 14 | 72259.03 | 0.00063402
CMA9A | UPPER COOMERA | Urban | 1298 | 1.0946 | 7.7417 | 3.2581 | 4.5933 | 0.37602 | 1 | 68873.5 | 68873.5 | 0.0013005 | 0.0013005 | 1 | 732 | 3.0292e-06
CMD11A | AROONA, CALOUNDRA, CALOUNDRA WEST, CURRIMUNDI, LIT | Rural short | 2254.4917 | 6.6721 | 12.3654 | 5.0139 | 9.459 | 0.89445 | 7 | 308338.9602 | 308338.9602 | 0.013475 | 0.013475 | 4 | 40162.703 | 0.0010419
CMD13A | AROONA, BATTERY HILL, CURRIMUNDI | Urban | 1212.2647 | 3.4144 | 2.5302 | 2.6041 | 1.6395 | 1.0942 | 3 | 89345 | 82248.68 | 0.0013954 | 0.00131 | 14 | 81871.862 | 0.00033022
CMD15A | BOKARINA, WURTULLA | Urban | 1357.6429 | 6.7083 | 1.8506 | 2.9345 | 2.0038 | 1.9976 | 6 | 103953.86 | 103953.86 | 0.0010177 | 0.0010177 | 15 | 137546.29 | 0.00048261
CMD17A | BIRTINYA | Rural short | 4 | 0 | 2.9477 | 0.15404
CMD3A | AROONA, CURRIMUNDI, LITTLE MOUNTAIN, MERIDAN PLAIN | Rural short | 2495.99 | 4.8513 | 15.2855 | 5.3442 | 11.8455 | 0 | 1 | 194635.11 | 194635.11 | 0.0071154 | 0.0071154 | 0 | 0 | 0
CMD5A | BATTERY HILL, CURRIMUNDI, DICKY BEACH | Urban | 1569.0445 | 5.7399 | 1.0707 | 3.1094 | 0.20686 | 3.0314 | 2 | 10591.875 | 10591.875 | 0.00012127 | 0.00012127 | 20 | 172530.1535 | 0.00054429
CMD7A | BIRTINYA, BOKARINA, WURTULLA | Rural short | 1284.7222 | 4.7247 | 5.983 | 2.8961 | 4.7368 | 0.93421 | 3 | 117926 | 117926 | 0.0073904 | 0.0073904 | 6 | 27511.69 | 0.00024503
CMV10B | CALAMVALE, SUNNYBANK HILLS | Urban | 311 | 0 | 3.1392 | 4.649
CMV11A | ALGESTER, CALAMVALE, PARKINSON | Urban | 1427.0971 | 2.9393 | 6.5726 | 3.582 | 27.6949 | 0 | 7 | 1413433.91 | 66178.91 | 0.0052074 | 0.0031503 | 0 | 0 | 0
CMV12A | ALGESTER, CALAMVALE, PARKINSON | Urban | 971.67 | 0.1465 | 8.0481 | 2.7818 | 0.16815 | 0.011686 | 4 | 5993.7 | 5993.7 | 0.0002399 | 0.0002399 | 1 | 1868.37 | 6.0543e-05
CMV12B | ALGESTER, CALAMVALE, PARKINSON | Urban | 2181 | 0 | 14.7319 | 5.4111 | 0.05568 | 0
CMV13 | CALAMVALE, STRETTON, SUNNYBANK HILLS | Urban | 1592.5433 | 0.7196 | 7.5504 | 4.2298 | 0.0049496 | 0.014733 | 1 | 200.6085 | 200.6085 | 1.1901e-05 | 1.1901e-05 | 2 | 526.2876 | 4.2904e-06
CMV14 | ALGESTER, CALAMVALE | Urban | 1192.8125 | 1.9695 | 5.7068 | 3.0104 | 64.9303 | 0.30171 | 5 | 2380523 | 57800.5 | 0.0036935 | 0.0012956 | 3 | 11602.6 | 4.0045e-05
CMV7 | ALGESTER, CALAMVALE | Urban | 1689.375 | 3.3447 | 5.7961 | 4.0393 | 76.6532 | 0.053858 | 2 | 3454366 | 477 | 0.0017308 | 3.0088e-06 | 1 | 1001.22 | 2.7166e-05
CMV8 | ALGESTER, CALAMVALE, SUNNYBANK HILLS | Urban | 951.9067 | 2.6337 | 4.4551 | 4.3441 | 77.6233 | 0.056406 | 1 | 2303800.96 | 0 | 0.00096265 | 0 | 2 | 410.762 | 3.0887e-06
CMV9A | CALAMVALE, RUNCORN, SUNNYBANK HILLS | Urban | 1472.2017 | 0.4848 | 7.5498 | 2.9637 | 4.7221 | 0.088731 | 2 | 212660.518 | 212660.518 | 0.0014773 | 0.0014773 | 4 | 5382.5 | 1.745e-05
CMV9B | CALAMVALE, STRETTON | Urban | 1011 | 0 | 6.2821 | 2.444 | 1.5484 | 0.055184 | 2 | 88678.41 | 88678.41 | 0.0010148 | 0.0010148 | 1 | 441 | 2.1226e-05
CMY1 | ATKINSONS DAM, BUARABA, CHURCHABLE, CLARENDON, COO | Rural short | 283.5382 | 70.131 | 1.0138 | 1.6576 | 1.187 | 0.44048 | 6 | 39459.7 | 7965.3 | 0.00055692 | 0.00023189 | 5 | 18448.934 | 0.00024728
CMY3 | COOMINYA | Urban | 2 | 0.3363 | 0.114 | 1.6576 | 3.6731 | 0 | 1 | 1938 | 0 | 2.0196e-06 | 0 | 0 | 0 | 0
CMY4 | ATKINSONS DAM, BUARABA, BUARABA CREEK, CLARENDON, | Rural short | 689.9038 | 99.9056 | 0.0886 | 2.1149 | 2.9617 | 0.53716 | 6 | 67150.565 | 65652.365 | 0.0025697 | 0.0025506 | 2 | 8502.08 | 7.981e-05
CNA7A | BLACKSTONE, NEW CHUM, SILKSTONE | Rural short | 642.25 | 6.7342 | 0.7703 | 1.81 | 3.925 | 0.68306 | 3 | 218373.37 | 655.37 | 0.00044794 | 0.00031614 | 1 | 5640 | 2.8686e-05
CNA8A | BLACKSTONE, REDBANK PLAINS, RIPLEY, SOUTH RIPLEY, | Rural short | 111.992 | 38.063 | 0.3274 | 0.97171 | 19.702 | 0.85597 | 1 | 42716 | 0 | 0.00033807 | 0 | 4 | 8456 | 8.4289e-05
CNA9A | BLACKSTONE, FLINDERS VIEW, RACEVIEW, RIPLEY, SWANB | Rural short | 194.25 | 15.9565 | 1.174 | 1.3909 | 3.6106 | 2.068 | 2 | 24178 | 24178 | 0.00053781 | 0.00053781 | 2 | 2713 | 1.8718e-05
CNB21B | CORNUBIA, SHAILER PARK | Urban | 1453.205 | 5.7875 | 5.6787 | 4.3513 | 6.3385 | 0.025772 | 2 | 178266.75 | 178266.75 | 0.0014104 | 0.0014104 | 2 | 786.94 | 2.953e-06
CNB24A | CARBROOK, CORNUBIA, MOUNT COTTON | Rural short | 1136.1616 | 23.9313 | 5.9665 | 2.8815 | 7.5797 | 12.1962 | 13 | 201227.6504 | 201227.6504 | 0.012982 | 0.012982 | 37 | 220551.1016 | 0.0015566
CNB25A | CORNUBIA | Urban | 688.83 | 3.6821 | 2.1106 | 1.9146 | 0.13717 | 0 | 1 | 3589.74 | 3589.74 | 4.8542e-05 | 4.8542e-05 | 0 | 0 | 0
CNB26A | CARBROOK, CORNUBIA, REDLAND BAY | Rural short | 454.4356 | 23.2697 | 0.6727 | 2.9913 | 389.3494 | 0.1206 | 7 | 3273682.61 | 70095.08 | 0.0041456 | 0.001484 | 2 | 776.25 | 4.9059e-05
COR22A | BLACK MOUNTAIN, COORAN, FEDERAL, POMONA | Rural short | 720.5355 | 38.5288 | 1.1466 | 1.2718 | 0.031594 | 1.2767 | 1 | 175 | 175 | 2.8979e-06 | 2.8979e-06 | 10 | 28709.255 | 0.00049256
COR23A | BOREEN POINT, COMO, COORAN, COOTHARABA, KIN KIN, P | Rural short | 925.8362 | 112.069 | 0.0987 | 1.448 | 5.5974 | 5.0766 | 3 | 82017.21 | 82017.21 | 0.0022422 | 0.0022422 | 10 | 85220.441 | 0.0011248
COR25A | COOROY, PINBARREN, POMONA | Rural short | 834.25 | 29.1436 | 0.3541 | 1.8685 | 0.088302 | 0.043877 | 2 | 2090.88 | 2090.88 | 6.2938e-05 | 6.2938e-05 | 2 | 975 | 4.6127e-05
COR26A | BOREEN POINT, COOTHARABA, PINBARREN, POMONA | Rural short | 943.586 | 68.8264 | 3.3719 | 1.5232 | 0.021554 | 0.043562 | 2 | 648 | 648 | 3.4824e-05 | 3.4824e-05 | 2 | 1546 | 2.0257e-05
CPB1 | CAPALABA | Urban | 1.8 | 0 | 0.9803 | 4.5918
CPB2 | CAPALABA | Urban | 650.1137 | 0.0616 | 2.2877 | 6.2494 | 3.4394 | 0.19254 | 5 | 41618.14 | 41618.14 | 0.00016677 | 0.00016677 | 3 | 2627.44 | 1.3376e-05
CPB3 | BIRKDALE, CAPALABA | Rural short | 922.5 | 5.3768 | 0.5903 | 1.8548
CPB4 | CAPALABA | Urban | 2443.035 | 9.3583 | 0.3763 | 5.3349 | 24.4286 | 0.62645 | 5 | 1041238.85 | 16721 | 0.002672 | 0.00020019 | 7 | 44893.975 | 0.00016828
CPB5 | CAPALABA | Urban | 894.99 | 0.1847 | 0.9543 | 4.6299 | 4.6594 | 0 | 3 | 88482.16 | 88482.16 | 0.0010388 | 0.0010388 | 0 | 0 | 0
CPB6 | CAPALABA, CAPALABA WEST, CHANDLER | Urban | 385.8514 | 9.275 | 0.6958 | 3.0294 | 48.4871 | 2.784 | 6 | 762219.25 | 98834.01 | 0.0012686 | 0.00076811 | 1 | 55680 | 4.8135e-05
CPB8 | CAPALABA, CAPALABA WEST, CHANDLER, GUMDALE, RANSOM | Rural short | 338.2131 | 13.2372 | 1.0992 | 1.448 | 22.4361 | 0.56065 | 7 | 414951.36 | 18214.13 | 0.0021244 | 0.0011216 | 6 | 9601.47 | 9.8667e-05
CPB9 | CAPALABA | Urban | 2021.6367 | 7.3023 | 4.6105 | 4.7961 | 0.20937 | 0.47059 | 2 | 6442.92 | 6442.92 | 0.00010048 | 0.00010048 | 4 | 29104.71 | 0.00011633
CPC1A | CAROLE PARK | Urban | 25 | 0 | 2.185 | 4.2488 | 0 | 0.0061998 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 1.0053e-06
CPC22A | CAROLE PARK | Urban | 33 | 0 | 2.2986 | 3.6391 | 0 | 0.014796 | 0 | 0 | 0 | 0 | 0 | 2 | 68.31 | 1.986e-06
CPC22B | CAROLE PARK | Urban | 4 | 0 | 0.2968 | 3.1057
CPC23A | CAROLE PARK | Urban | 6 | 0 | 1.4524 | 1.8863
CPC25A | CAROLE PARK | Urban | 32.6567 | 2.0563 | 0.8526 | 4.0012 | 1.006 | 0.48451 | 2 | 1566 | 1566 | 1.2061e-05 | 1.2061e-05 | 1 | 125 | 9.9877e-07
CPC2A | BROWNS PLAINS, CAROLE PARK, ELLEN GROVE, FOREST LA | Urban | 1451 | 5.7134 | 7.0764 | 4.3492
CPC2B | CAMIRA, CAROLE PARK | Urban | 1770.7025 | 12.8597 | 0.9977 | 4.6379 | 13.5057 | 0.2504 | 11 | 397758.29 | 229176.29 | 0.0076522 | 0.0072337 | 1 | 12120.15 | 3.4023e-05
CPC3A | CAROLE PARK | Urban | 5 | 0 | 1.2001 | 2.5528 | 1.3129 | 0 | 1 | 130 | 130 | 5.0338e-06 | 5.0338e-06 | 0 | 0 | 0
CPC3B | CAROLE PARK | Urban | 34.25 | 0.5937 | 3.2603 | 3.5058 | 6.6564 | 3.236 | 2 | 1872 | 1872 | 3.5232e-05 | 3.5232e-05 | 2 | 938.61 | 3.0102e-06
CPC5A | CAROLE PARK | Urban | 4 | 0 | 1.2843 | 0.42337
CPD1 | BLANCHVIEW, DERRYMORE, FLAGSTONE CREEK, HELIDON, L | Rural short | 406.0016 | 89.5406 | 0.5903 | 1.0098 | 2.4894 | 0.4347 | 16 | 151590.6333 | 148248.6333 | 0.0015053 | 0.0014966 | 22 | 20849.95 | 0.00027924
CPD2A | BLANCHVIEW, CARPENDALE, DERRYMORE, GRANTHAM, HELID | Rural short | 215.9611 | 50.1285 | 0.1612 | 0.72402 | 10.3817 | 1.9523 | 12 | 60344.04 | 27520.04 | 0.001725 | 0.0010893 | 14 | 24620.765 | 0.00025997
CPK10 | CAMIRA, GAILES, SPRINGFIELD | Urban | 888.75 | 4.4093 | 3.0292 | 2.5912 | 0.24407 | 0.011427 | 1 | 9735 | 0 | 5.9644e-05 | 0 | 1 | 1062.15 | 2.923e-06
CPK11 | CAMIRA, CAROLE PARK | Urban | 34.25 | 1.0395 | 3.221 | 2.153 | 8.3528 | 1.1306 | 1 | 4012 | 4012 | 3.423e-05 | 3.423e-05 | 3 | 1147.56 | 1.4161e-05
CPK12 | CAROLE PARK | Urban | 2 | 1.1368 | 0.7881 | 3.8678
CPK13 | CAMIRA, GAILES, GOODNA | Rural short | 1873.92 | 12.3388 | 2.4259 | 3.7711 | 20.6301 | 0.087968 | 10 | 869146.7832 | 453420.7832 | 0.022803 | 0.01715 | 3 | 10708.32 | 0.00011451
CPK6 | CAROLE PARK | Urban | 19 | 0.4202 | 2.9591 | 2.9636
CPK7 | CAMIRA, GOODNA | Urban | 883.48 | 6.2444 | 0.6696 | 3.601 | 0.3798 | 0.0067868 | 1 | 19640.9897 | 19640.9897 | 7.1469e-05 | 7.1469e-05 | 1 | 92 | 2.0145e-06
CPK8 | CAMIRA, CAROLE PARK | Urban | 15 | 1.1241 | 1.7074 | 4.2128
CPK9 | CAMIRA, GAILES, GOODNA | Rural short | 746.75 | 6.0284 | 2.1495 | 1.8863 | 3.3942 | 3.8785 | 8 | 149544.22 | 124916.22 | 0.0059282 | 0.0056589 | 4 | 1694.46 | 3.9323e-05
CPL23A | ACACIA RIDGE, DURACK, WILLAWONG | Rural short | 928.4946 | 10.2455 | 2.4092 | 2.1746 | 127.5924 | 4.3738 | 3 | 2684023.01 | 110700.83 | 0.0055051 | 0.0028548 | 10 | 59162.11 | 0.00044247
CPL25A | ACACIA RIDGE | Urban | 320 | 1.5668 | 0.3551 | 0.6543 | 0.024355 | 0.034576 | 0 | 0 | 0 | 0 | 0 | 1 | 881.68 | 4.1417e-06
CPL25B | ARCHERFIELD, COOPERS PLAINS | Urban | 223.1233 | 2.2494 | 1.8127 | 4.2869 | 0.863 | 0.0051401 | 2 | 5206.5 | 5206.5 | 2.6038e-05 | 2.6038e-05 | 1 | 57.1824 | 3.0054e-06
CPL26A | ACACIA RIDGE, ARCHERFIELD | Urban | 422.8267 | 2.4021 | 4.1131 | 3.4867 | 5.6895 | 0.99902 | 3 | 73474.685 | 57086.625 | 0.00076885 | 0.00043365 | 2 | 9394.36 | 3.1328e-05
CPL2A | ACACIA RIDGE, COOPERS PLAINS | Urban | 299.3775 | 3.8504 | 1.099 | 4.0012 | 223.8295 | 2.4721 | 3 | 924364.4162 | 4920.4362 | 0.00060101 | 0.00030058 | 1 | 963.02 | 3.6084e-06
CPL3A | ACACIA RIDGE | Urban | 422.29 | 1.9083 | 5.804 | 4.5918 | 4.4434 | 0.74916 | 2 | 11976 | 11976 | 7.9559e-05 | 7.9559e-05 | 4 | 2326.09 | 1.4008e-05
CPL5A | ACACIA RIDGE, ARCHERFIELD, COOPERS PLAINS | Urban | 129 | 1.8231 | 0.807 | 3.4867 | 0.3867 | 1.2847 | 1 | 5705 | 5705 | 1.7654e-05 | 1.7654e-05 | 3 | 6344.48 | 3.037e-05
CPL6A | ACACIA RIDGE, ARCHERFIELD, COOPERS PLAINS | Urban | 312.16 | 3.2619 | 0.4642 | 4.2679 | 0.095178 | 0.010811 | 0 | 0 | 0 | 0 | 0 | 1 | 459.375 | 1.2233e-06
CPR4 | COORPAROO | Urban | 944.343 | 3.7814 | 0.4419 | 3.3533 | 6.6463 | 0.58114 | 2 | 99059.84 | 99059.84 | 0.00077784 | 0.00077784 | 7 | 25956.6602 | 0.00011104
CPR5 | COORPAROO, GREENSLOPES | Urban | 2821.3364 | 7.9256 | 0.584 | 8.3896 | 8.3005 | 0.6034 | 5 | 444826.11 | 436456.11 | 0.0032773 | 0.0031409 | 6 | 26619.0998 | 8.4773e-05
CPR6 | CAMP HILL, COORPAROO, NORMAN PARK | Urban | 1329.101 | 2.8034 | 0.5743 | 2.3594 | 59.4226 | 0.07172 | 5 | 2924200 | 134673 | 0.0021504 | 0.00074359 | 5 | 11341.205 | 5.5945e-05
CPR7 | COORPAROO, GREENSLOPES | Urban | 2140.8022 | 4.6522 | 0.61759 | 3.5439 | 16.2324 | 0.0016064 | 8 | 963367.4178 | 366882.4178 | 0.0052924 | 0.0051535 | 1 | 127.8 | 6.4482e-06
CPRGBP3 | COORPAROO | Urban | 10 | 0 | 1.4604 | 2.2483
CRB15A | CURRUMBIN WATERS | Urban | 365.608 | 1.8861 | 0.8217 | 2.0958 | 0 | 2.366 | 0 | 0 | 0 | 0 | 0 | 10 | 29087.0758 | 0.00010666
CRB16B | CURRUMBIN WATERS | Urban | 5 | 0.1266 | 2.1125 | 2.7462
CRB18A | CURRUMBIN WATERS | Urban | 130 | 1.9873 | 0.0505 | 2.2864
CRB22A | CURRUMBIN WATERS | Urban | 1840.7786 | 3.411 | 6.2779 | 3.8489 | 0.15817 | 1.1871 | 0 | 0 | 0 | 0 | 0 | 7 | 25032.96 | 0.00010378
CRB24B | CURRUMBIN, PALM BEACH, TUGUN | Urban | 2166.5338 | 6.4882 | 2.0983 | 5.3092 | 81.3054 | 12.3117 | 4 | 2997020.34 | 92469.34 | 0.0034265 | 0.00081106 | 25 | 468703.1627 | 0.0011071
CRB25A | CURRUMBIN VALLEY, CURRUMBIN WATERS, TALLEBUDGERA, | Rural short | 1193.4802 | 51.0844 | 2.7491 | 3.3894 | 98.1148 | 34.0793 | 14 | 1485753.66 | 94899 | 0.0031702 | 0.002157 | 86 | 703450.6836 | 0.0053773
CRBTHP14 | CURRUMBIN, CURRUMBIN WATERS, PALM BEACH, TUGUN | Urban | 1663.9204 | 6.626 | 3.4581 | 3.5715 | 175.5593 | 6.2022 | 5 | 5168271 | 593490.02 | 0.0032907 | 0.0018488 | 18 | 344147.5741 | 0.00082309
CRBTHP26 | CURRUMBIN WATERS, TUGUN | Urban | 1114.6992 | 3.9712 | 1.7597 | 3.7905 | 16.7244 | 1.43 | 1 | 1342373.5 | 0 | 0.0011221 | 0 | 11 | 182201.3619 | 0.00043714
CRM12A | CRESTMEAD | Urban | 26 | 1.4454 | 0.9149 | 3.6582 | 0.052888 | 0
CRM13A | CRESTMEAD, MARSDEN, PARK RIDGE | Urban | 1787.1992 | 8.458 | 2.7028 | 4.5475 | 107.2253 | 2.1186 | 7 | 3874687.5482 | 200453.2982 | 0.007357 | 0.0036896 | 4 | 66827.99 | 0.00028131
CRM13B | CRESTMEAD | Urban | 23.89 | 1.1272 | 2.0254 | 4.0012 | 198.1933 | 0 | 6 | 51660.24 | 3886.24 | 0.00010702 | 5.8566e-05 | 0 | 0 | 0
CRM15A | BROWNS PLAINS, HERITAGE PARK, REGENTS PARK | Urban | 1566.2867 | 10.2404 | 1.1335 | 3.7905 | 0.52914 | 0.21628 | 4 | 25062.06 | 25062.06 | 0.00043371 | 0.00043371 | 1 | 3538.5 | 1.0523e-05
CRM16A | BERRINBA, BROWNS PLAINS, KINGSTON, LOGAN CENTRAL, | Urban | 1935 | 11.756 | 5.6213 | 6.141
CRM1B | CRESTMEAD | Urban | 17 | 0.9423 | 0.9019 | 4.6109
CRM3A | CRESTMEAD | Urban | 20 | 1.6161 | 1.7778 | 3.1247 | 0.13297 | 0
CRM5A | BERRINBA, BROWNS PLAINS, CRESTMEAD, HERITAGE PARK | Urban | 1085.16 | 6.3132 | 4.9072 | 3.3724 | 2.664 | 0.17309 | 4 | 43917.87 | 41781.12 | 0.0011465 | 0.0011382 | 1 | 4697.55 | 4.0522e-05
CRM5B | CRESTMEAD | Urban | 31.16 | 0.9889 | 0.9692 | 0.68591 | 1.019 | 0 | 1 | 1121.76 | 1121.76 | 3.1287e-05 | 3.1287e-05 | 0 | 0 | 0
CRMEDB2 | CRESTMEAD, HERITAGE PARK | Urban | 24 | 3.1073 | 0.2579 | 1.7338 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CRY2A | COOROY, LAKE MACDONALD, POMONA, TINBEERWAH | Rural short | 711.8022 | 49.3899 | 2.156 | 2.0298 | 56.3238 | 0.78713 | 14 | 1001131.1833 | 25249.1833 | 0.0072063 | 0.0024431 | 4 | 11423.98 | 0.00017238
CRY3A | COOROY | Rural short | 970.3536 | 22.3833 | 0.853 | 2.4894 | 8.9998 | 0.75091 | 9 | 179168.92 | 125450.97 | 0.014711 | 0.011912 | 2 | 15711.3 | 0.0001202
CRY5A | COOROY, EUMUNDI, TINBEERWAH | Rural short | 93.792 | 16.2238 | 0.2789 | 0.36201 | 11.3116 | 6.1224 | 6 | 68141.84 | 62834.89 | 0.0012063 | 0.00092981 | 4 | 32048.3336 | 0.00032357
CRY6A | BELLI PARK, COOLOOLABIN, COOROY, EERWAH VALE, EUMU | Rural short | 678.1829 | 58.9596 | 2.3469 | 1.3344 | 58.046 | 2.6865 | 11 | 1220059.67 | 103022.35 | 0.0079857 | 0.005035 | 10 | 36494.39 | 0.00035707
CSE10 | CHERMSIDE, KEDRON | Urban | 763.435 | 2.4142 | 2.955 | 3.3724 | 0 | 0.69072 | 0 | 0 | 0 | 0 | 0 | 6 | 42655.2334 | 0.00013914
CSE2 | ASPLEY, CHERMSIDE, CHERMSIDE WEST | Urban | 1121.6829 | 4.5633 | 4.1918 | 3.0866 | 0.45186 | 1.9198 | 4 | 13515.35 | 13515.35 | 0.00012044 | 0.00012044 | 13 | 120820.4632 | 0.00031988
CSE21A | CHERMSIDE | Urban | 54.08 | 0 | 1.1364 | 1.2575 | 0 | 0.19784 | 0 | 0 | 0 | 0 | 0 | 1 | 788.66 | 7.9645e-06
CSE23A | CHERMSIDE | Urban | 134.75 | 1.5067 | 2.0772 | 1.0479 | 1.5374 | 0 | 1 | 30794.25 | 30794.25 | 0.00013618 | 0.00013618 | 0 | 0 | 0
CSE27A | CHERMSIDE | Urban | 9 | 0 | 1.6884 | 1.8672
CSE3 | CHERMSIDE | Urban | 556 | 0.3393 | 2.4797 | 4.8966 | 0.031655 | 0 | 1 | 2151 | 2151 | 0.00012075 | 0.00012075 | 0 | 0 | 0
CSE4 | ASPLEY, CHERMSIDE, CHERMSIDE WEST | Urban | 1824.846 | 6.1832 | 2.0303 | 3.6201 | 0.67232 | 0.12014 | 2 | 28927.679 | 28927.679 | 0.00012797 | 0.00012797 | 3 | 17286.05 | 5.5757e-05
CSE6 | CHERMSIDE, KEDRON, WAVELL HEIGHTS | Urban | 1915.1937 | 6.5278 | 0.9836 | 3.7905 | 0.59303 | 0.3752 | 2 | 21197.48 | 21197.48 | 0.00012252 | 0.00012252 | 6 | 30400.581 | 0.00010625
CSE7 | CHERMSIDE, WAVELL HEIGHTS | Urban | 1097.4229 | 4.4996 | 0.1234 | 1.9918 | 5.2106 | 0.11324 | 5 | 222248.9596 | 72399.88 | 0.0018738 | 0.0011356 | 2 | 6330.3 | 2.0167e-05
CSE9 | CHERMSIDE, GEEBUNG, WAVELL HEIGHTS | Urban | 1995.2667 | 7.9901 | 0.8023 | 3.9451 | 0.081663 | 0.1574 | 0 | 0 | 0 | 0 | 0 | 3 | 5293.5494 | 2.5366e-05
CSQSTP5 | SPRING HILL | Urban | 51 | 0 | 0.7065 |  | 0 | 0.045072 | 0 | 0 | 0 | 0 | 0 | 1 | 902 | 2.0079e-06
CSTQUT18 | BRISBANE | CBD | 14.33 | 0 | 1.039 | 1.7338
CVL11A | CLEVELAND | Urban | 62 | 1.0387 | 0.504 | 4.2298
CVL13A | CLEVELAND | Urban | 2 | 0 | 0.9856 | 0.49538 | 0 | 14.9154 | 0 | 0 | 0 | 0 | 0 | 1 | 862 | 2.0061e-06
CVL15A | CLEVELAND | Urban | 298.992 | 0.9612 | 1.4193 | 5.2587 | 4.3803 | 0 | 3 | 26688.47 | 26688.47 | 0.00047278 | 0.00047278 | 0 | 0 | 0
CVL17A | CLEVELAND, ORMISTON, THORNLANDS | Urban | 2145.7446 | 8.4348 | 3.048 | 5.3701 | 8.5579 | 0.75896 | 4 | 311185.06 | 60521.86 | 0.004972 | 0.0026153 | 9 | 36451.7246 | 0.00023309
CVL1A | CLEVELAND, THORNLANDS | Urban | 1370 | 2.5752 | 5.9366 | 2.5912 | 0.09993 | 0
CVL3A | ALEXANDRA HILLS, CLEVELAND, THORNLANDS | Urban | 1801.1 | 9.1393 | 2.9429 | 4.564 | 2.5701 | 0.81338 | 6 | 141459.38 | 141459.38 | 0.0021268 | 0.0021268 | 4 | 41819.16 | 0.0001392
CVL5A | ALEXANDRA HILLS, CAPALABA, THORNLANDS | Rural short | 1304.26 | 6.0652 | 1.4975 | 3.8487 | 39.6835 | 0.34373 | 7 | 1574796.62 | 145884.35 | 0.0064885 | 0.0033847 | 7 | 2716.68 | 5.6938e-05
CVL7A | CAPALABA, CLEVELAND, SHELDON, THORNLANDS | Rural short | 1722.1233 | 28.8484 | 2.2068 | 5.473 | 21.6828 | 1.5282 | 11 | 696621.68 | 129622.68 | 0.0079945 | 0.0056637 | 9 | 41579.46 | 0.00044674
CVL9A | CLEVELAND, THORNLANDS | Urban | 985 | 5.8675 | 0.9599 | 2.5914 | 3.5576 | 0 | 3 | 78543 | 78543 | 0.0001037 | 0.0001037 | 0 | 0 | 0
DBS13A | HEMMANT, MURARRIE | Urban | 7 | 0 | 1.924 | 2.9151
DBS15A | MURARRIE | Urban | 44 | 0 | 2.6764 | 1.6957
DBS16A | MURARRIE | Urban | 57.28 | 0 | 3.5271 | 3.7725 | 4.1777 | 0.59256 | 2 | 4135.54 | 4135.54 | 0.00011568 | 0.00011568 | 2 | 1655.84 | 6.3823e-06
DBS2A | HEMMANT, MURARRIE | Urban | 13 | 0.6888 | 0.792 | 1.5242 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DBS4A | MURARRIE | Urban | 124.5714 | 3.2545 | 2.1958 | 4.8776 | 0.25864 | 4.6927 | 1 | 102.76 | 102.76 | 3.7054e-06 | 3.7054e-06 | 6 | 13518.9316 | 4.6917e-05
DBS5A | MURARRIE | Urban | 127 | 0.3725 | 3.0934 | 3.0485
DBY10 | DECEPTION BAY, NARANGBA | Rural short | 299 | 4.9771 | 1.7802 | 1.6195
DBY11 | DECEPTION BAY | Urban | 1241.3333 | 7.6831 | 0.8079 | 2.9636 | 0.21744 | 0 | 3 | 3911.82 | 3911.82 | 8.1135e-05 | 8.1135e-05 | 0 | 0 | 0
DBY4 | DECEPTION BAY, NARANGBA | Urban | 217.75 | 4.9491 | 4.098 | 5.392 | 24.3693 | 0 | 4 | 25557.53 | 25557.53 | 0.00043481 | 0.00043481 | 0 | 0 | 0
DBY5 | DECEPTION BAY | Urban | 295.3333 | 1.3392 | 0.7069 | 0.71555 | 5.1059 | 0 | 2 | 288213.94 | 0 | 0.00032225 | 0 | 0 | 0 | 0
DBY6 | DECEPTION BAY | Urban | 2272.63 | 11.7482 | 0.8591 | 6.0398 | 5.8087 | 0.10784 | 7 | 332702.7817 | 326857.7817 | 0.0049753 | 0.0048909 | 3 | 8154.5 | 2.9534e-05
DBY7A | DECEPTION BAY, ROTHWELL | Urban | 1857.8571 | 4.4328 | 4.5035 | 4.0032 | 0 | 0.092598 | 0 | 0 | 0 | 0 | 0 | 7 | 4634.385 | 0.00014485
DBY9 | DECEPTION BAY, ROTHWELL | Urban | 1923.7611 | 9.1533 | 5.7538 | 6.0779 | 3.7258 | 0.040582 | 6 | 116899.8 | 116899.8 | 0.002303 | 0.002303 | 2 | 2962.1 | 1.2035e-05
DRA11 | DARRA | Urban | 256.032 | 2.3155 | 1.8583 | 2.3816 | 0.12972 | 0.45764 | 1 | 1302.84 | 1302.84 | 3.1298e-05 | 3.1298e-05 | 4 | 6174.37 | 1.5899e-05
DRA13A | DARRA, RICHLANDS | Urban | 55 | 1.0699 | 2.1155 | 3.1819 | 0.08694 | 0 | 1 | 360 | 360 | 3.0318e-06 | 3.0318e-06 | 0 | 0 | 0
DRA1A | DARRA, INALA, RICHLANDS | Urban | 379.6667 | 3.5149 | 2.7061 | 5.4682 | 16.3456 | 0.35993 | 2 | 117171.22 | 36525.72 | 0.00042388 | 4.4696e-05 | 3 | 9571.6 | 2.5416e-05
DRA3B | RICHLANDS | Urban | 11.5 | 0.6356 | 1.9636 | 0.74307
DRA5 | DARRA, RICHLANDS | Urban | 127.8675 | 0.423 | 2.8367 | 3.4486 | 0.16819 | 0.36775 | 1 | 2145.825 | 2145.825 | 1.4163e-05 | 1.4163e-05 | 3 | 3460.183 | 1.3416e-05
DRA6 | DARRA | Urban | 806.2213 | 3.6617 | 0.6651 | 1.8179 | 2.1617 | 2.7309 | 3 | 57304.42 | 57304.42 | 0.00093194 | 0.00093194 | 12 | 40919.04 | 0.00014988
DRA8 | DARRA, INALA, RICHLANDS | Urban | 210.4231 | 3.6811 | 2.6364 | 4.0583 | 86.2636 | 3.5576 | 2 | 309203 | 0 | 0.00023101 | 0 | 10 | 55229.565 | 0.00022039
DRA9 | DARRA, SUMNER | Urban | 380.495 | 2.5273 | 2.6809 | 1.4698 | 1.9367 | 4.7639 | 1 | 15221 | 15221 | 3.1279e-05 | 3.1279e-05 | 7 | 26636.124 | 8.2724e-05
DRD13A | CLONTARF, MARGATE | Urban | 1730.3169 | 8.3151 | 0.2728 | 2.317 | 0.23007 | 2.6469 | 1 | 4234 | 4234 | 5.864e-05 | 5.864e-05 | 39 | 141664.1918 | 0.00059857
DRD15B | CLONTARF, WOODY POINT | Urban | 2247.5265 | 8.4894 | 1.0149 | 4.9787 | 1.4492 | 3.0925 | 6 | 49599.01 | 49599.01 | 0.00065006 | 0.00065006 | 23 | 122194.9558 | 0.00059366
DRD16A | CLONTARF, KIPPA-RING | Urban | 570.0271 | 5.0871 | 0.4866 | 3.4296 | 16.5046 | 2.8372 | 3 | 146735.54 | 25365.54 | 0.00057708 | 0.00055029 | 11 | 52118.9439 | 0.00018788
DRD2A | CLONTARF, KIPPA-RING, ROTHWELL | Rural short | 1836.54 | 5.9404 | 7.9017 | 3.7535 | 33.8611 | 0.65613 | 3 | 621804.5 | 621804.5 | 0.010571 | 0.010571 | 4 | 5186.9496 | 7.1217e-05
DRD3A | CLONTARF, KIPPA-RING | Urban | 1697.1021 | 8.6106 | 1.2156 | 3.7725 | 0.42637 | 4.0078 | 3 | 30262.12 | 30262.12 | 0.00030298 | 0.00030298 | 31 | 167343.5689 | 0.00059517
DRD5A | CLONTARF, MARGATE, WOODY POINT | Urban | 2663.8328 | 9.3858 | 0.449 | 4.3684 | 2.5887 | 1.5866 | 5 | 260659.6136 | 33624.92 | 0.00064395 | 0.00056233 | 24 | 103175.2693 | 0.00035831
EAC12 | ENOGGERA | Urban | 4 |  |  |  | 0.01169 | 0 | 1 | 24 | 24 | 4.0387e-06 | 4.0387e-06 | 0 | 0 | 0
EAC2 | GAYTHORNE | Urban | 2 | 0 | 0.251 |  | 0.0032566 | 0 | 1 | 12 | 12 | 2.0194e-06 | 2.0194e-06 | 0 | 0 | 0
EAC4 | ASHGROVE, ENOGGERA, MITCHELTON | Urban | 17 | 0.572 | 2.75 |  | 0.037459 | 0 | 1 | 96 | 96 | 1.6155e-05 | 1.6155e-05 | 0 | 0 | 0
EAC6 | ASHGROVE, ENOGGERA, GAYTHORNE | Urban | 13 | 3.1259 | 1.9984 |  | 0.022796 | 0 | 1 | 78 | 78 | 1.3126e-05 | 1.3126e-05 | 0 | 0 | 0
EAC8 | ENOGGERA, GAYTHORNE | Urban | 2 | 0.631 | 0.2644 |  | 0.0035906 | 0 | 1 | 12 | 12 | 2.0194e-06 | 2.0194e-06 | 0 | 0 | 0
EMD1 | EERWAH VALE, EUMUNDI | Rural short | 359.495 | 11.6401 | 1.5678 | 0.83158 | 8.7626 | 0.44133 | 7 | 116309.57 | 116309.57 | 0.0059202 | 0.0059202 | 1 | 3136.73 | 2.5288e-05
EMD2 | BRIDGES, EERWAH VALE, EUMUNDI, NINDERRY, NORTH ARM | Rural short | 495.8608 | 34.6239 | 1.001 | 0.95266 | 15.4323 | 6.5762 | 7 | 405514 | 48206 | 0.003609 | 0.0032938 | 18 | 200758.03 | 0.0017325
EMD3 | DOONAN, EUMUNDI, VERRIERDALE, YANDINA CREEK | Rural short | 639.4205 | 42.2243 | 1.4821 | 1.5665 | 19.5658 | 7.2746 | 12 | 418805.7746 | 81472.7746 | 0.0077945 | 0.0075882 | 32 | 143416.5204 | 0.0016522
EMP15A | EIGHT MILE PLAINS | Urban | 40.5 | 0 | 2.1649 | 5.1253 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMP21A | BURBANK, EIGHT MILE PLAINS, PRIESTDALE, ROCHEDALE, | Rural short | 1660.8033 | 26.4994 | 5.0159 | 3.7102 | 79.0457 | 1.0682 | 9 | 1125805.19 | 56658.82 | 0.01454 | 0.0051377 | 11 | 27928.525 | 0.00049616
EMP22A | ALGESTER, EIGHT MILE PLAINS | Urban | 73.74 | 0 | 2.0399 | 4.2298 | 8.6633 | 0.24205 | 1 | 7382.96 | 0 | 7.1554e-05 | 0 | 1 | 379.638 | 9.7246e-07
EMP23A | EIGHT MILE PLAINS, SUNNYBANK | Urban | 1613.265 | 1.607 | 5.7063 | 3.8098 | 6.3766 | 0.17207 | 5 | 173280.9 | 6152.9 | 0.0018829 | 0.00026309 | 3 | 5126.473 | 1.5135e-05
EMP25A | EIGHT MILE PLAINS, MACGREGOR, UPPER MT GRAVATT | Urban | 721.61 | 4.0466 | 2.6068 | 1.9434 | 11.827 | 0 | 3 | 275634.4624 | 3444.9624 | 0.00081268 | 3.186e-05 | 0 | 0 | 0
EMP2A | EIGHT MILE PLAINS | Urban | 1160 | 1.6555 | 4.4131 | 3.3915 | 0 | 1.8465 | 0 | 0 | 0 | 0 | 0 | 3 | 35075.52 | 0.00013355
EMP3 | EIGHT MILE PLAINS, RUNCORN | Urban | 1025.32 | 1.9797 | 3.9303 | 5.03 | 0 | 0.031687 | 0 | 0 | 0 | 0 | 0 | 1 | 1023.2768 | 1.0485e-05
EMP4A | EIGHT MILE PLAINS, ROCHEDALE, ROCHEDALE SOUTH | Urban | 1311.42 | 9.2717 | 1.3237 | 3.5735 | 29.7036 | 0.22 | 5 | 1131364.882 | 73832.482 | 0.002354 | 0.00094723 | 2 | 7515.21 | 2.6123e-05
ENG2 | ASHGROVE, ENOGGERA, GAYTHORNE, MITCHELTON | Urban | 1713.2255 | 7.6828 | 0.2685 | 3.3843 | 4.8821 | 1.1684 | 6 | 529744.44 | 38803.44 | 0.0021045 | 0.0019777 | 16 | 58700.245 | 0.00027232
ENG3 | ALDERLEY, ENOGGERA | Urban | 655.5625 | 3.3179 | 0.5608 | 2.3245 | 0.32163 | 2.1664 | 2 | 11213.4 | 11213.4 | 0.00068719 | 0.00068719 | 5 | 17366.3 | 7.9634e-05
ENG7 | ALDERLEY, ASHGROVE, ENOGGERA | Urban | 1689.8 | 5.7713 | 0.2647 | 2.9976 | 3.227 | 0.73208 | 3 | 213344.5 | 213344.5 | 0.0035016 | 0.0035016 | 16 | 51740.83 | 0.00024221
ENG8 | ALDERLEY | Urban | 1160.0408 | 2.3819 | 2.207 | 2.0577 | 0.46484 | 0.86479 | 5 | 35205.985 | 34061.485 | 0.0016106 | 0.0014455 | 8 | 40569.0986 | 0.0001453
ENG9 | ENOGGERA, EVERTON PARK | Urban | 1205 | 4.5514 | 1.0882 | 3.601 | 4.1553 | 0.15776 | 3 | 124198 | 124198 | 0.0036278 | 0.0036278 | 4 | 10132.96 | 4.741e-05
ESK2B | ESK | Rural short | 388.5 | 7.9964 | 0.6403 | 0.9336 | 0.35085 | 0.16446 | 1 | 8305.5 | 8305.5 | 0.0011408 | 0.0011408 | 3 | 3175.52 | 2.8797e-05
ESK3A | BIARRA, COAL CREEK, ESK, GALLANANI, MURRUMBA, OTTA | Rural short | 132.74 | 46.8567 | 0.0639 | 0.41917 | 0.28039 | 0 | 7 | 4636.24 | 4636.24 | 0.00045217 | 0.00045217 | 0 | 0 | 0
ESK5A | ESK, MOUNT HALLEN, REDBANK CREEK | Rural short | 650.428 | 59.237 | 3.1986 | 1.81 | 14.5661 | 1.3065 | 13 | 194271.94 | 194223.94 | 0.010404 | 0.010401 | 2 | 7373.44 | 9.3566e-05
ESRFLW48 | BRISBANE | CBD | 3.66 | 0 | 0.6873
EXBQEC10 | BRISBANE | CBD | 38 | 0 | 0.3208
EZRRWD4 | AMBERLEY, EBENEZER, MOUNT FORBES, MUTDAPILLY, ROSE | Rural short | 285.775 | 58.5422 | 0.8903 | 0.6543 | 3.0287 | 1.5206 | 5 | 50756.93 | 30922.93 | 0.00069024 | 0.00051833 | 6 | 12279.12 | 0.000123
F1173 | GEEBUNG, VIRGINIA | Urban | 105.3833 | 1.9015 | 0.9883 |  | 4.3237 | 0 | 3 | 11760.82 | 11760.82 | 0.00013228 | 0.00013228 | 0 | 0 | 0
FCHQPT2 | MORNINGSIDE | Urban | 111.83 | 0 | 5.2831 | 2.8008 | 1.2956 | 0 | 2 | 9968.56 | 9968.56 | 4.6937e-05 | 4.6937e-05 | 0 | 0 | 0
FDS1 | ANTHONY, GOOLMAN, HARRISVILLE, LIMESTONE RIDGES, M | Rural short | 734.6014 | 134.6018 | 0.6276 | 2.8389 | 4.5174 | 3.3543 | 20 | 100150.37 | 31144.94 | 0.0032736 | 0.0010138 | 23 | 113159.325 | 0.00093621
FDS3 | COLEYVILLE, HARRISVILLE, KENTS LAGOON, MILORA, MUN | Rural short | 555.9252 | 100.5258 | 0 | 1.8863 | 0.66551 | 4.8686 | 6 | 4117.8733 | 1278.3733 | 0.0016601 | 3.2933e-05 | 25 | 93421.705 | 0.00095253
FDS4 | COLEYVILLE, HARRISVILLE, MOUNT FORBES, MUTDAPILLY, | Rural short | 388.4079 | 111.2608 | 0.1553 | 0.87644 | 2.0028 | 1.8645 | 6 | 40029.92 | 37938.22 | 0.0036552 | 0.0024565 | 7 | 27857.69 | 0.000211
FGBSGT23 | DEAGON, FITZGIBBON, TAIGUM, ZILLMERE | Urban | 2051.4933 | 3.3511 | 6.8412 | 3.2581 | 76.6261 | 1.0286 | 2 | 2672544 | 0 | 0.0039792 | 0 | 2 | 416 | 2.012e-06
FIS12A | LYTTON, PORT OF BRISBANE | Urban | 7.2 | 0 | 4.023 | 3.22
FIS13A | LYTTON, PORT OF BRISBANE | Urban | 28.4 | 0 | 6.4251 | 2.5531 | 0 | 1.3331 | 0 | 0 | 0 | 0 | 0 | 2 | 732.8 | 4.5366e-06
FIS5A | PORT OF BRISBANE | Urban | 5.6 | 0 | 1.7649 | 2.7246 | 0 | 0.3372 | 0 | 0 | 0 | 0 | 0 | 1 | 326.304 | 1.0631e-06
FIS7A | PORT OF BRISBANE | Urban | 13.6 | 0 | 4.0445 | 1.4671 | 0 | 0.63874 | 0 | 0 | 0 | 0 | 0 | 1 | 604.8 | 4.2288e-06
FPT1 | FORTITUDE VALLEY | Urban | 79 | 0 | 0.7459
FVY1 | FORTITUDE VALLEY | Urban | 62 | 0 | 0.0607
GAP1A | THE GAP | Urban | 1004.8 | 3.9196 | 4.0803 | 2.7519 | 0.25335 | 0.20354 | 5 | 45983.39 | 45983.39 | 0.00017612 | 0.00017612 | 5 | 12586.58 | 6.5622e-05
GAP2A | MT COOTTHA, TOOWONG | Urban | 9 | 0 | 4.8447 | 2.5341
GAP4A | THE GAP | Rural short | 919 | 5.6321 | 4.578 | 2.6942
GAP6A | THE GAP | Urban | 1092.7543 | 1.1673 | 5.7208 | 3.0983 | 0.12233 | 0.23302 | 2 | 3855.28 | 3855.28 | 8.9198e-05 | 8.9198e-05 | 5 | 21041.131 | 0.00010389
GAP8A | THE GAP | Urban | 1557.9179 | 6.4337 | 2.463 | 4.8585 | 83.0278 | 0.97835 | 3 | 3161247.54 | 0 | 0.0031561 | 0 | 13 | 44884.311 | 0.00017322
GAP9A | THE GAP | Urban | 1222.5596 | 5.4461 | 1.3117 | 3.0791 | 18.8467 | 1.8423 | 4 | 717009.8 | 9125.6 | 0.0013329 | 9.8967e-05 | 20 | 78395.52 | 0.0003356
GBG1A | GEEBUNG, VIRGINIA | Urban | 45.2767 | 0.5335 | 2.2857 | 3.4296 | 2.1887 | 0.39202 | 1 | 1374.9 | 1374.9 | 4.6309e-05 | 4.6309e-05 | 2 | 2311.66 | 5.0262e-06
GBG1B | GEEBUNG | Urban | 103.5 | 0.9097 | 3.2114 | 4.0393 | 9.9428 | 0.075487 | 4 | 22629.58 | 22629.58 | 0.00031305 | 0.00031305 | 2 | 2156.05 | 1.0954e-05
GBG23A | GEEBUNG | Urban | 118.8275 | 1.3202 | 1.8347 | 2.5722 | 0.98925 | 0.31932 | 2 | 3525 | 3525 | 3.0287e-05 | 3.0287e-05 | 2 | 544.4 | 4.1616e-06
GBG25 | GEEBUNG, VIRGINIA | Urban | 260 | 1.8822 | 2.0615 | 4.8395
GBG26 | BANYO, NORTHGATE, VIRGINIA | Urban | 924.326 | 4.1186 | 2.5319 | 4.1917 | 20.6585 | 0.035564 | 4 | 374154.88 | 152485.3 | 0.0030767 | 0.0021507 | 1 | 2096.465 | 6.9705e-06
GBG27 | BOONDALL, GEEBUNG, VIRGINIA | Urban | 1258.2654 | 3.8326 | 5.6732 | 3.9059 | 5.2884 | 0.22851 | 8 | 133811.01 | 98846.41 | 0.0025264 | 0.0024269 | 4 | 11202.595 | 3.53e-05
GBG28 | VIRGINIA | Urban | 37 | 1.0836 | 0.8512 | 2.8961 | 0.29553 | 0 | 2 | 1772.26 | 10.5 | 1.8499e-06 | 7.0745e-08 | 0 | 0 | 0
GBG2A | BANYO, NUDGEE, VIRGINIA | Urban | 928.9 | 7.1741 | 2.4161 | 2.8008 | 13.9176 | 0.44378 | 4 | 268880.44 | 268880.44 | 0.0028551 | 0.0028551 | 1 | 215 | 1.009e-06
GBG4A | VIRGINIA | Urban | 65 | 0.2864 | 1.3822 | 2.4388
GBG6A | VIRGINIA | Urban | 68.33 | 0.6532 | 1.5584 | 2.3245 | 0.033937 | 1.1368 | 0 | 0 | 0 | 0 | 0 | 1 | 7120.37 | 1.255e-05
GBN2 | CANINA, GOOMBOORIAN, GREENS CREEK, NORTH DEEP CREE | Rural short | 277.6456 | 46.2928 | 0 | 0.43822 | 0.038173 | 5.9279 | 0 | 0 | 0 | 0 | 0 | 18 | 89608.712 | 0.00092751
GBN3 | ANDERLEIGH, DOWNSFIELD, NEERDIE, ROSS CREEK, SANDY | Rural short | 140.5667 | 37.3153 | 0.0331 | 0.21273 | 1.8192 | 13.9846 | 4 | 17923.5 | 17923.5 | 0.00045737 | 0.00045737 | 24 | 153862.81 | 0.0012909
GBN4 | COONDOO, DOWNSFIELD, GOOMBOORIAN, GYMPIE, KIA ORA, | Rural short | 769.3191 | 143.646 | 0 | 0.8955 | 85.0395 | 22.4358 | 27 | 1303615.82 | 204249.82 | 0.0073394 | 0.0055659 | 83 | 331766.0653 | 0.0034268
GBP4 | COORPAROO | Urban | 19 | 0 | 0.3499
GBP5 | COORPAROO, GREENSLOPES | Urban | 395.7467 | 1.4596 | 1.4002 |  | 3.079 | 0.31225 | 1 | 59682.24 | 59682.24 | 0.00039367 | 0.00039367 | 2 | 19007.01 | 7.2714e-05
GBP6 | EAST BRISBANE, WOOLLOONGABBA | Urban | 734.8567 | 2.63 | 1.1085 |  | 60.1058 | 0.16875 | 4 | 2045105.2908 | 44341.6608 | 0.0016574 | 0.00018155 | 2 | 7927.62 | 2.988e-05
GCL3 | COOPERS PLAINS | Urban | 10 | 0 | 0.4581
GCLSBK5 | COOPERS PLAINS, ROBERTSON | Urban | 407.25 | 2.4125 | 0.3339 | 4.5416 | 0.034768 | 0.0097779 | 0 | 0 | 0 | 0 | 0 | 1 | 809.1 | 3.5105e-06
GCLSBY7 | SALISBURY | Urban | 387.65 | 3.9665 | 0.356 | 3.0921 | 87.4469 | 0.61302 | 4 | 832347.32 | 99432.28 | 0.0015844 | 0.0012574 | 4 | 6538.4146 | 2.0723e-05
GGR1 | COLLEGE VIEW, CROWLEY VALE, FOREST HILL, GLENORE G | Rural short | 841.7488 | 67.1111 | 0.013 | 1.6767 | 7.3019 | 14.5845 | 22 | 130174.9032 | 130174.9032 | 0.0088728 | 0.0088728 | 34 | 364285.75 | 0.0022987
GGR2 | GLENORE GROVE, LAKE CLARENDON, MORTON VALE | Rural short | 140.5655 | 20.9725 | 0 | 0.96221 | 12.6981 | 0.043863 | 9 | 119872.085 | 104323.235 | 0.0018156 | 0.0014034 | 2 | 3289 | 3.742e-05
GGR3 | GLENORE GROVE, KENTVILLE, LOCKROSE, REGENCY DOWNS | Rural short | 85.192 | 18.6602 | 0.0264 | 0.6097 | 15.7778 | 0.10514 | 14 | 187734.91 | 18169.91 | 0.0011037 | 0.00084209 | 1 | 2916 | 1.7275e-05
GGR4 | GLENORE GROVE, HATTON VALE, PLAINLAND, REGENCY DOW | Rural short | 607.52 | 27.8193 | 0.985 | 2.877 | 1.6591 | 8.1469 | 8 | 71684.95 | 64805.95 | 0.0044245 | 0.004328 | 17 | 73637.29 | 0.00056573
GGR5 | GLENORE GROVE, GRANDCHESTER, HATTON VALE, REGENCY | Rural short | 969.7967 | 66.6868 | 2.2216 | 2.3054 | 1.7755 | 1.6237 | 6 | 95645.9828 | 95645.9828 | 0.0057157 | 0.0057157 | 9 | 49526.88 | 0.00050979
GISVSP3 | MURARRIE | Urban | 6 | 2.1337 | 1.4306 | 3.0638 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GLY11A | KEPERRA, UPPER KEDRON | Urban | 1393 | 4.9773 | 6.548 | 5.4255 | 0.13859 | 0.10698 | 1 | 38 | 38 | 2.0068e-06 | 2.0068e-06 | 3 | 6648.775 | 4.2358e-05
GLY12A | FERNY GROVE, KEPERRA | Urban | 1133 | 2.1985 | 4.1355 | 2.7051 | 0.022003 | 0.38523 | 1 | 1475.76 | 1475.76 | 3.4421e-05 | 3.4421e-05 | 3 | 14128.92 | 5.712e-05
GLY15A | KEPERRA, MITCHELTON | Urban | 402.064 | 2.5111 | 0.1862 | 0.98502 | 0 | 0.062686 | 0 | 0 | 0 | 0 | 0 | 5 | 6571.9 | 4.5835e-05
GLY2A | FERNY GROVE, KEPERRA, UPPER KEDRON | Urban | 930.4286 | 4.1298 | 3.5894 | 3.8845 | 0 | 0.26743 | 0 | 0 | 0 | 0 | 0 | 7 | 11958.59 | 7.2464e-05
GLY3A | KEPERRA, MITCHELTON | Urban | 2029.41 | 7.1293 | 3.1343 | 4.0157 | 0.21839 | 0.3213 | 1 | 700 | 700 | 3.5274e-06 | 3.5274e-06 | 3 | 7755.5 | 4.1101e-05
GLY4A | KEPERRA | Urban | 923.3571 | 3.5349 | 0.8498 | 1.5269 | 0.40995 | 0.12757 | 2 | 14346.4 | 14346.4 | 9.1984e-05 | 9.1984e-05 | 5 | 8725.21 | 3.94e-05
GSNMLS6 | FORTITUDE VALLEY | Urban | 13 | 0 | 1.8453 | 1.067 | 0.83018 | 0 | 1 | 1001 | 1001 | 1.298e-05 | 1.298e-05 | 0 | 0 | 0
GSNMLS92 | FORTITUDE VALLEY | Urban | 8 | 0 | 0.93005 | 1.4099
GTN12A | GATTON, GRANTHAM, LOWER TENTHILL, PLACID HILLS, RI | Rural short | 597.5858 | 40.6527 | 3.7882 | 3.4486 | 109.0976 | 3.0209 | 10 | 580674.28 | 65153.52 | 0.0079436 | 0.0024114 | 23 | 21361.7 | 0.00053528
GTN13A | ADARE, GATTON, RINGWOOD, VINEGAR HILL | Rural short | 715.635 | 37.4463 | 1.6477 | 1.8863 | 3.4211 | 0.019651 | 7 | 41874.7 | 38302.15 | 0.0063694 | 0.0043047 | 1 | 1238.76 | 1.0751e-05
GTN15A | ADARE, GATTON | Rural short | 1156.6167 | 22.9959 | 1.399 | 4.8776 | 5.4514 | 0.0069251 | 7 | 72727.12 | 2718 | 0.0069072 | 0.00024977 | 2 | 122.675 | 1.4736e-05
GTN1B | GATTON, WOODLANDS | Rural short | 292 | 12.0797 | 2.741 | 2.2673 | 0.43036 | 0.058088 | 1 | 1420 | 0 | 0.00082066 | 0 | 1 | 1713.8 | 5.5996e-05
GTN3A | GATTON | Urban | 1191.815 | 6.3358 | 0.3794 | 3.6963 | 0.38668 | 0 | 2 | 15551.3 | 9584.4 | 0.0012709 | 6.5823e-05 | 0 | 0 | 0
GTN5B | ADARE, CLARENDON, COLLEGE VIEW, GATTON, LAKE CLARE | Rural short | 152.6544 | 28.6145 | 0.6472 | 4.8014 | 20.0332 | 1.2795 | 7 | 45715.74 | 29057.84 | 0.0015355 | 0.00062733 | 2 | 862 | 2.4588e-05
GVN12A | ARUNDEL, GAVEN, PARKWOOD | Urban | 1178.3333 | 1.3917 | 7.2466 | 4.0774 | 0.0083269 | 0.52946 | 1 | 507.65 | 507.65 | 7.1793e-06 | 7.1793e-06 | 4 | 19889.32 | 4.9192e-05
GVN13A | PACIFIC PINES | Urban | 1999.2475 | 1.0559 | 13.255 | 5.8493 | 0 | 0.15097 | 0 | 0 | 0 | 0 | 0 | 4 | 19069.709 | 7.3926e-05
GVN15A | HELENSVALE | Urban | 121.798 | 1.0716 | 2.9336 | 2.3245 | 0 | 1.8983 | 0 | 0 | 0 | 0 | 0 | 5 | 2113.83 | 4.1123e-05
GVN16A | GAVEN, NERANG, SOUTHPORT | Rural short | 1073.4464 | 12.9859 | 1.0043 | 3.7916 | 7.8471 | 0.55534 | 6 | 401764.79 | 168110.29 | 0.0050397 | 0.0045914 | 6 | 47522.48 | 0.00042156
GVN2A | GAVEN | Urban | 5 | 4.1363 | 0.1538 | 1.7705 | 1.615 | 0 | 1 | 835 | 835 | 5.0433e-06 | 5.0433e-06 | 0 | 0 | 0
GVN3A | GAVEN, MOLENDINAR, PARKWOOD | Urban | 884.625 | 2.1058 | 4.3032 | 1.9532 | 1.6146 | 0.10058 | 1 | 82362 | 82362 | 0.00088794 | 0.00088794 | 3 | 12111.62 | 7.6473e-05
GVN5A | ARUNDEL, GAVEN, HELENSVALE, PACIFIC PINES | Rural short | 293 | 3.2656 | 2.9351 | 1.6576
GVN6B | OXENFORD, PACIFIC PINES | Urban | 1285.48 | 3.3316 | 9.3108 | 3.8297 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GYGGYS6 | ALBERTON, GLANMIRE, GYMPIE, JONES HILL, KYBONG, MO | Rural short | 609.8323 | 94.851 | 0.1283 | 3.2553 | 11.7951 | 5.5441 | 13 | 102788.9533 | 57847.4533 | 0.0026769 | 0.0022142 | 23 | 67776.82 | 0.00096968
GYM2A | CALICO CREEK, DAGUN, GILLDORA, GYMPIE, JONES HILL, | Rural short | 1332.2089 | 67.6824 | 4.2713 | 3.4677 | 8.6674 | 3.9501 | 13 | 345099.68 | 337341.68 | 0.0095981 | 0.0095895 | 31 | 143699.3348 | 0.0022566
GYM2B | GYMPIE | Urban | 445 | 3.4912 | 0.953 | 5.373 | 42.7642 | 0 | 8 | 333820 | 69123 | 0.00026586 | 0.00016921 | 0 | 0 | 0
GYM3 | GYMPIE | Urban | 320.5 | 4.4733 | 0.579 | 1.6767 | 9.3162 | 0 | 5 | 380044 | 58584 | 0.00018011 | 9.771e-05 | 0 | 0 | 0
GYM4 | GYMPIE | Rural short | 769.5 | 6.1264 | 0.3497 | 1.6005
GYM5B | GYMPIE | Rural short | 417.33 | 3.5313 | 0 | 1.3147 | 0.1456 | 0 | 1 | 5977 | 5977 | 0.00020028 | 0.00020028 | 0 | 0 | 0
GYM6 | GYMPIE | Urban | 518.5 | 4.0148 | 0.1369 | 1.448
GYM7A | ARALUEN, CANINA, CEDAR POCKET, EAST DEEP CREEK, GO | Rural short | 1394.6826 | 56.2718 | 0.1547 |  | 40.0918 | 6.3597 | 19 | 838334.249 | 54472.709 | 0.006179 | 0.0020932 | 35 | 112014.1269 | 0.0012831
GYM8A | GYMPIE, KYBONG, MONKLAND, PIE CREEK, SOUTHSIDE | Rural short | 1891.0667 | 27.6088 | 1.8624 | 5.7731 | 13.9726 | 0.74966 | 9 | 582148.5 | 501460.5 | 0.017978 | 0.017912 | 5 | 19250.36 | 0.00032246
GYM8B | GYMPIE | Urban | 504.2886 | 2.9822 | 1.0218 | 2.6484 | 2.0349 | 0.00019838 | 6 | 63827.56 | 63827.56 | 0.00087237 | 0.00087237 | 1 | 23.9155 | 6.9104e-07
GYM9A | GYMPIE, MONKLAND | Rural short | 183.5075 | 5.3132 | 1.1958 | 1.067 | 0.010812 | 0.48008 | 1 | 375.4575 | 375.4575 | 1.4446e-05 | 1.4446e-05 | 2 | 1488.048 | 1.7267e-05
GYM9B | CANINA, CEDAR POCKET, EAST DEEP CREEK, GREENS CREE | Rural short | 167.5294 | 30.1593 | 0.3056 | 1.8291 | 33.9567 | 4.4911 | 4 | 567560 | 50015 | 0.0010122 | 0.00055659 | 13 | 56592.98 | 0.0005209
GYN1B | GYMPIE | Urban | 3 | 0.8337 | 0.7064 | 3.2009 | 0 | 0.94678 | 0 | 0 | 0 | 0 | 0 | 1 | 39.04 | 3.2282e-07
GYN2B | GYMPIE | Urban | 398.9 | 4.1106 | 0.2545 | 2.2673 | 9.5664 | 0.20642 | 3 | 104735 | 0 | 3.4373e-05 | 0 | 2 | 983.28 | 4.1032e-06
GYN3A | FISHERMANS POCKET, GLASTONBURY, GYMPIE, LANGSHAW, | Rural short | 1096.8213 | 116.2477 | 1.6659 | 2.515 | 111.7998 | 19.7137 | 16 | 2560837.9915 | 246635.9915 | 0.0079331 | 0.0038602 | 38 | 329600.3457 | 0.0028213
GYN5A | ARALUEN, GYMPIE, TWO MILE | Urban | 967.3867 | 7.1709 | 2.8284 | 3.7154 | 5.4932 | 0.030913 | 1 | 80340 | 0 | 2.6285e-05 | 0 | 2 | 1040.4 | 3.7822e-05
GYN6A | ARALUEN, BELLS BRIDGE, CHATSWORTH, FISHERMANS POCK | Rural short | 858.999 | 61.5435 | 0.6262 | 2.0768 | 94.0737 | 7.5016 | 8 | 1639237.95 | 15901.95 | 0.0027717 | 0.00073885 | 12 | 81005.92 | 0.00091549
GYN7A | ARALUEN, BANKS POCKET, CHATSWORTH, CORELLA, GYMPIE | Rural short | 1245.0444 | 65.7154 | 3.4981 | 3.3457 | 1.4491 | 9.5101 | 4 | 21058.24 | 21058.24 | 0.00051354 | 0.00051354 | 26 | 111866.9032 | 0.0010829
GYS2A | EAST DEEP CREEK, MONKLAND | Urban | 27 | 2.373 | 0.1413 | 3.5282 | 0.18112 | 0.034802 | 3 | 1619.32 | 1619.32 | 1.671e-05 | 1.671e-05 | 2 | 2970.02 | 9.0473e-06
GYS3A | CEDAR POCKET, EAST DEEP CREEK, GREENS CREEK, MOTHA | Rural short | 407.6855 | 68.5003 | 0.1627 | 0.91455 | 136.4924 | 4.2311 | 9 | 1564189.8617 | 144085.8617 | 0.0027124 | 0.0014861 | 20 | 60240.6306 | 0.00082338
GYS5A | CEDAR POCKET, GLANMIRE, MONKLAND, MOTHAR MOUNTAIN, | Rural short | 270.0625 | 42.9387 | 0.1983 | 0.55254 | 28.2794 | 0.95574 | 5 | 362207.5 | 28659.5 | 0.0014813 | 0.00046127 | 11 | 10685.51 | 0.00016706
HDA10A | CLAYFIELD, HENDRA, NUNDAH | Urban | 1742.7372 | 3.5634 | 1.3866 | 2.7246 | 9.4155 | 0.54943 | 5 | 415196.29 | 415196.29 | 0.0038085 | 0.0038085 | 13 | 41321.66 | 0.0001422
HDA11A | CLAYFIELD | Urban | 1730.7006 | 3.3479 | 1.687 | 3.1247 | 8.671 | 2.617 | 3 | 445497.52 | 9514.56 | 0.0019668 | 0.00014118 | 31 | 187392.246 | 0.00064093
HDA13A | ASCOT, HENDRA | Urban | 1027.592 | 4.2364 | 0.199 | 2.858 | 2.4966 | 0.26011 | 2 | 113252.99 | 113252.99 | 0.00031037 | 0.00031037 | 3 | 7949.33 | 3.0471e-05
HDA14A | BANYO, HENDRA, NORTHGATE | Urban | 152.2308 | 1.1765 | 3.6624 | 3.7535 | 0.45448 | 3.2365 | 4 | 2719.11 | 2719.11 | 3.5319e-05 | 3.5319e-05 | 9 | 13103.495 | 4.3713e-05
HDA3A | ASCOT, CLAYFIELD, HENDRA | Urban | 761.4231 | 2.8764 | 0.2477 | 2.7436 | 3.1689 | 5.4277 | 3 | 107995.73 | 2566.08 | 0.00081012 | 3.5812e-05 | 36 | 187148.745 | 0.00065089
HDA3B | ASCOT | Urban | 157.5 | 1.3249 | 1.7365 | 0.63427
HDA4A | HENDRA | Urban | 806.25 | 2.6936 | 0.6943 | 2.3054 | 1.4536 | 0.035454 | 1 | 109886 | 0 | 9.5032e-05 | 0 | 2 | 2538.84 | 8.2786e-06
HDN1 | CARPENDALE, GRANTHAM, HELIDON, HELIDON SPA, IREDAL | Rural short | 580.232 | 55.1818 | 2.1979 | 1.8482 | 3.7624 | 1.5866 | 8 | 80261.6333 | 80261.6333 | 0.0036479 | 0.0036479 | 12 | 18398.4905 | 0.00021348
HDN2 | HELIDON, HELIDON SPA, POSTMANS RIDGE | Rural short | 304.2625 | 31.7111 | 0.8277 | 1.8672 | 4.255 | 0.28811 | 2 | 43316.24 | 43316.24 | 0.00090255 | 0.00090255 | 6 | 22913.1444 | 0.00024132
HHC10 | HERSTON | Urban | 2 | 0 | 0.1313
HHC21 | HERSTON | Urban | 3 | 0 | 0.39
HHC23 | HERSTON | Urban | 7 | 0 | 0.7754
HHC7 | HERSTON | Urban | 5 | 0 | 0.8574
HHC9 | HERSTON | Urban | 4 | 0 | 1.192
HIS12A | HELENSVALE, HOPE ISLAND | Urban | 840.0833 | 1.7901 | 5.3521 | 2.7818 | 8.7186 | 0.66967 | 4 | 275861.6 | 76003.2 | 0.0017526 | 0.0017016 | 8 | 25764.825 | 0.00015273
HIS12B | HELENSVALE, HOPE ISLAND, OXENFORD | Urban | 955 | 0.6314 | 10.6268 | 3.4677 | 3.1152 | 0.002673 | 2 | 85822.5 | 85822.5 | 0.0019208 | 0.0019208 | 2 | 63.54 | 1.7351e-06
HIS13A | HOPE ISLAND | Urban | 573.7 | 0.4211 | 6.8145 | 3.1628 | 2.1252 | 2.758 | 2 | 35507 | 35507 | 0.0011545 | 0.0011545 | 2 | 1312.5 | 3.0242e-06
HIS15B | HOPE ISLAND | Rural short | 10 | 0 | 1.1204 | 0.095502
HIS1B | HELENSVALE, HOPE ISLAND | Urban | 1066.5 | 0 | 7.5202 | 3.8678 | 0.13942 | 0.02087 | 2 | 3516.7 | 3516.7 | 0.0010622 | 0.0010622 | 1 | 626.4 | 7.2451e-06
HIS3A | HOPE ISLAND | Urban | 243.6667 | 0.62 | 3.879 | 2.3435 | 0.07862 | 0.11727 | 1 | 733.5 | 733.5 | 0.00024469 | 0.00024469 | 2 | 5403.9 | 0.00010427
HIS5A | HOPE ISLAND, PARADISE POINT | Urban | 743.75 | 3.303 | 3.3713 | 2.4007 | 3.7797 | 2.0487 | 6 | 76450.44 | 76450.44 | 0.0022653 | 0.0022653 | 10 | 30017.805 | 0.00011985
HIS5B | HOPE ISLAND | Urban | 877.5833 | 1.0675 | 8.2004 | 3.9821 | 8.4092 | 0.0056297 | 4 | 190364.5 | 190364.5 | 0.0026047 | 0.0026047 | 1 | 34.2 | 1.1469e-06
HISSCV16 | HOPE ISLAND | Urban | 245.1667 | 0 | 2.0345 | 4.0202 | 0.017601 | 0.034277 | 1 | 736.5 | 736.5 | 0.00024569 | 0.00024569 | 2 | 1352.5 | 5.1725e-06
HISSCV2 | HOPE ISLAND | Urban | 206.5 | 0.4382 | 5.2796 | 3.2962 | 0.056253 | 0 | 1 | 619.5 | 619.5 | 0.00020666 | 0.00020666 | 0 | 0 | 0
HLG1 | DUNWICH | Rural short | 17 | 11.4224 | 0.103 | 1.791 | 0.057298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HMT10A | HEMMANT | Urban | 292 | 2.1001 | 1.2251 | 1.9244 | 0.37977 | 0.91875 | 1 | 90 | 90 | 1.0106e-06 | 1.0106e-06 | 5 | 30693.81 | 0.00011404
HMT2 | HEMMANT | Urban | 7 | 0.0869 | 1.8142 | 2.6484
HMT3A | HEMMANT | Urban | 121 | 1.9673 | 1.5887 | 2.3245 | 9.485 | 0.01826 | 1 | 13165 | 13165 | 0.00012219 | 0.00012219 | 1 | 109.2 | 1.0571e-06
HMT9A | HEMMANT, TINGALPA | Rural short | 193.66 | 3.6878 | 0.2265 | 0.72402 | 1.8944 | 0.079113 | 1 | 42520.89 | 0 | 0.00055767 | 0 | 1 | 195 | 2.8874e-06
HMTPTR5 | HEMMANT, MURARRIE | Urban | 278 | 1.8146 | 1.0985 | 2.3626 | 1.1282 | 0.22599 | 1 | 20572 | 20572 | 0.000279 | 0.000279 | 2 | 2471.92 | 1.806e-05
HPE12A | HOLLAND PARK, HOLLAND PARK WEST, MT GRAVATT, MT GR | Urban | 1459.33 | 4.601 | 0.7005 | 3.4296 | 1.3969 | 0.88074 | 5 | 131357.936 | 126996.446 | 0.0032188 | 0.0017507 | 10 | 54349.8726 | 0.0001877
HPE13A | CAMP HILL, COORPAROO, HOLLAND PARK | Urban | 1699.2982 | 8.1068 | 1.9658 | 5.3183 | 2.7125 | 2.8011 | 16 | 97930.422 | 81193.422 | 0.003455 | 0.00059702 | 22 | 136714.4475 | 0.00040795
HPE16A | CARINA HEIGHTS, HOLLAND PARK, MANSFIELD, MT GRAVAT | Urban | 1623.2132 | 3.1144 | 3.8958 | 4.9895 | 10.5513 | 2.178 | 3 | 487935.6628 | 4355.3428 | 0.0017899 | 2.9104e-05 | 15 | 99947.0361 | 0.00028839
HPE3A | MANSFIELD, MT GRAVATT EAST | Urban | 1843.7137 | 6.9336 | 1.7738 | 4.3513 | 12.1422 | 3.9738 | 4 | 739322.668 | 13920.228 | 0.0021051 | 0.00024174 | 24 | 195932.1718 | 0.00062235
HPE5A | HOLLAND PARK | Urban | 1234.0671 | 5.5912 | 0.7567 | 2.3787 | 5.637 | 0.89293 | 5 | 109575.6932 | 5321.1932 | 0.00028712 | 9.1186e-05 | 19 | 53719.8101 | 0.00022662
HPK10 | GREENSLOPES | Urban | 1351.75 | 4.4555 | 0.4259 | 3.3509 | 1.8178 | 0 | 4 | 69478.75 | 69478.75 | 0.0025674 | 0.0025674 | 0 | 0 | 0
HPK11 | HOLLAND PARK | Rural short | 194 | 1.7126 | 0.4014 | 0.50282 | 0.31092 | 0 | 1 | 22310 | 0 | 0.00056059 | 0 | 0 | 0 | 0
HPK2 | GREENSLOPES | Urban | 1181.6543 | 1.1237 | 3.0966 | 1.9625 | 0.29571 | 0.11396 | 3 | 16961.7637 | 16961.7637 | 0.00027063 | 0.00027063 | 4 | 5802.3232 | 2.2539e-05
HPK3A | HOLLAND PARK WEST, TARRAGINDI | Urban | 2437.7677 | 6.7182 | 0.5485 | 4.4203 | 99.6521 | 0.53033 | 12 | 5756246.1632 | 499746.2432 | 0.013714 | 0.0054322 | 14 | 36015.52 | 0.00014526
HPK5A | ANNERLEY, HOLLAND PARK WEST, TARRAGINDI | Rural short | 1303 | 5.2182 | 0.4001 | 0.19615
HPK6 | COORPAROO, HOLLAND PARK, HOLLAND PARK WEST | Urban | 733.8 | 2.7966 | 0.3897 | 2.0591 | 1.2051 | 0.053525 | 1 | 19831.5 | 19831.5 | 0.00073619 | 0.00073619 | 4 | 1152.82 | 6.7567e-06
HPK8A | HOLLAND PARK WEST, TARRAGINDI | Urban | 1284.8037 | 5.1073 | 0.8431 | 3.6757 | 22.5488 | 2.5495 | 8 | 820479.7238 | 19239.5238 | 0.0017923 | 0.00025572 | 22 | 96831.7611 | 0.00032201
HPK9 | HOLLAND PARK WEST | Urban | 548.304 | 1.7804 | 0.8503 | 1.4671 | 0.3833 | 0.20899 | 2 | 33803.52 | 33803.52 | 0.00062722 | 0.00062722 | 3 | 13904.175 | 3.9569e-05
HSH3 | SPRING HILL | Urban | 158.5 | 0 | 0.6074
HSHWTC43 | SPRING HILL | Urban | 56 | 0 | 0.7287
HTL10A | EAGLE FARM | Urban | 51 | 0.8028 | 1.922 | 3.2962 | 0 | 0.065304 | 0 | 0 | 0 | 0 | 0 | 1 | 451 | 9.053e-06
HTL11A | EAGLE FARM | Urban | 65 | 0.023 | 1.8469 | 1.5242
HTL12A | EAGLE FARM | Urban | 4 | 0 | 0.9755 | 3.1787
HTL14A | EAGLE FARM | Urban | 22.66 | 1.3424 | 2.0698 | 3.3128 | 0.31409 | 10.5122 | 1 | 696.32 | 696.32 | 1.2938e-06 | 1.2938e-06 | 1 | 2910 | 1.0107e-06
HTL2A | EAGLE FARM | Urban | 125.8033 | 0 | 1.7748 | 2.7436 | 0 | 0.92329 | 0 | 0 | 0 | 0 | 0 | 3 | 1823.4242 | 8.0883e-06
HTL3A | EAGLE FARM | Urban | 58.5475 | 0.9987 | 2.599 | 2.2483 | 0 | 2.8019 | 0 | 0 | 0 | 0 | 0 | 4 | 2079.3736 | 8.255e-06
HTL4A | EAGLE FARM | Urban | 18 | 0.0341 | 1.7071 | 3.1628
HTL6A | EAGLE FARM, HAMILTON | Urban | 100.69 | 2.5484 | 3.5509 | 2.8961 | 0 | 2.0772 | 0 | 0 | 0 | 0 | 0 | 3 | 2650.501 | 1.6622e-05
HTN1A | ASCOT, EAGLE FARM, HAMILTON | Urban | 1337.5 | 3.5133 | 1.8608 | 2.1787
HTN22A | EAGLE FARM, HAMILTON | Urban | 316.2664 | 2.5413 | 3.0903 | 2.6484 | 24.0455 | 2.3742 | 6 | 152509.22 | 52665.72 | 0.0009967 | 0.00037674 | 5 | 8219.72 | 2.014e-05
HTN24A | ALBION, HAMILTON | Urban | 958.4 | 2.6326 | 2.0581 | 4.1345 | 1.4783 | 0.81665 | 8 | 45033.34 | 21415.84 | 0.00036184 | 0.00023712 | 7 | 22993.015 | 7.5713e-05
HTN27A | ALBION, HAMILTON, NEWSTEAD | Urban | 444 | 0.9251 | 2.0801 | 5.0642
HTN28A | ASCOT | Urban | 1197.5 | 2.8619 | 1.0205 | 2.3816
HTN2A | ASCOT, HAMILTON | Urban | 635.5 | 2.143 | 0.54945 | 2.4272
HTN3A | ASCOT | Urban | 397 | 2.2774 | 1.4134 | 1.2493 | 0.33699 | 0.028903 | 1 | 8931 | 8931 | 3.9332e-05 | 3.9332e-05 | 1 | 497.25 | 1.9618e-06
HTN7B | HAMILTON | Urban | 194 | 0 | 1.2288 | 2.6484 | 0 | 0.46656 | 0 | 0 | 0 | 0 | 0 | 2 | 1726.86 | 1.2871e-05
HWD12A | HEATHWOOD | Urban | 12 | 0 | 0.7347 | 1.81 | 0.073152 | 0
HWD12B | FOREST LAKE, HEATHWOOD | Urban | 25 | 0 | 2.817 | 1.5433 | 0.22295 | 0 | 1 | 454.5 | 454.5 | 4.5485e-06 | 4.5485e-06 | 0 | 0 | 0
HWD13A | FOREST LAKE, HEATHWOOD | Urban | 525.755 | 0.0976 | 7.9996 | 5.3539 | 0.16802 | 1.0117 | 1 | 631.62 | 631.62 | 7.276e-06 | 7.276e-06 | 1 | 8742 | 4.7338e-05
HWD1B | HEATHWOOD | Urban | 10 | 0 | 0.385 | 1.1813 | 0.085359 | 0
HWD2B | FORESTDALE, HEATHWOOD, LARAPINTA | Rural short | 260.5 | 7.1361 | 5.0948 | 1.5433 | 0.86877 | 0.39004 | 3 | 17032.56 | 17032.56 | 9.1982e-05 | 9.1982e-05 | 1 | 446 | 5.7337e-06
HWD5A | DOOLANDELLA, FOREST LAKE, HEATHWOOD, PALLARA | Rural short | 2137.75 | 8.07 | 8.5035 | 4.8585 | 0.4819 | 0.010697 | 0 | 0 | 0 | 0 | 0 | 2 | 420.84 | 1.0669e-05
HWD5B | FOREST LAKE | Urban | 1593.8 | 0 | 9.4437 | 4.5156 | 0.32773 | 0.014595 | 1 | 1824.7284 | 1824.7284 | 8.3758e-05 | 8.3758e-05 | 4 | 563.7623 | 8.9727e-06
HWL10A | COOMBABAH, PARADISE POINT, RUNAWAY BAY | Urban | 1671.3775 | 4.3411 | 7.4852 | 3.9645 | 0.26305 | 1.35 | 1 | 10259.04 | 10259.04 | 3.8222e-05 | 3.8222e-05 | 7 | 30508.0713 | 0.00015105
HWL11A | RUNAWAY BAY | Urban | 1187.6089 | 3.6097 | 3.8415 | 2.9395 | 93.6716 | 0.35549 | 4 | 2744431.202 | 16705.202 | 0.0012934 | 9.3435e-05 | 5 | 36627.27 | 0.0001843
HWL12A | RUNAWAY BAY | Urban | 3 | 0 | 2.2 | 1.9053
HWL13A | PARADISE POINT | Urban | 919.7667 | 1.0794 | 12.2485 | 3.8106 | 0.014081 | 0.62448 | 1 | 229.68 | 229.68 | 3.9805e-06 | 3.9805e-06 | 2 | 6031.51 | 7.4431e-05
HWL1A | HOLLYWELL, PARADISE POINT, RUNAWAY BAY | Urban | 1442.0525 | 3.5149 | 5.5664 | 4.4965 | 0.4424 | 0.34208 | 1 | 21224.14 | 21224.14 | 6.7903e-05 | 6.7903e-05 | 3 | 18904.4006 | 8.205e-05
HWL2A | BIGGERA WATERS, RUNAWAY BAY | Urban | 901.498 | 5.0143 | 6.4839 | 3.4296 | 0.067221 | 1.3141 | 1 | 2030 | 2030 | 5.8626e-05 | 5.8626e-05 | 4 | 1579.25 | 1.1847e-05
HWL3A | COOMBABAH | Urban | 1947.8333 | 3.7708 | 2.6584 | 4.6994 | 0 | 2.3158 | 0 | 0 | 0 | 0 | 0 | 12 | 73100.0525 | 0.00031525
HWL4A | RUNAWAY BAY | Urban | 378 | 0.0315 | 4.4866 | 2.9723 | 3.0951 | 0 | 1 | 133588 | 0 | 5.2567e-05 | 0 | 0 | 0 | 0
HWL6A | BIGGERA WATERS, COOMBABAH, RUNAWAY BAY | Urban | 1647.745 | 2.3973 | 3.8286 | 3.6772 | 0.20633 | 0.15673 | 2 | 24910.5 | 24910.5 | 0.00014398 | 0.00014398 | 2 | 5623.5206 | 8.4194e-05
HWL8A | HOLLYWELL, RUNAWAY BAY | Urban | 1170.1133 | 2.78 | 3.6752 | 3.481 | 2.2628 | 0.007283 | 2 | 100326 | 0 | 0.00019915 | 0 | 1 | 313.47 | 8.1557e-07
IBL2 | BELLA CREEK, BOLLIER, BORUMBA DAM, BROOLOO, GHEERU | Rural short | 727.8903 | 86.7955 | 0.0486 | 1.6005 | 147.143 | 6.8876 | 15 | 2735042.4 | 242880.02 | 0.0092809 | 0.0071306 | 17 | 105811.447 | 0.0010342
IBS1 | RUSSELL ISLAND | Rural short | 259.5 | 6.6907 | 1.2733 | 0.38867 | 29.7608 | 0.037201 | 2 | 1074644.5 | 0 | 0.0014934 | 0 | 2 | 624 | 0.00014
IDY10A | CHAPEL HILL, INDOOROOPILLY | Urban | 1104.868 | 4.4275 | 2.8007 | 3.3152 | 19.8893 | 0 | 4 | 1057483.64 | 34514.64 | 0.0013143 | 0.00013354 | 0 | 0 | 0
IDY14A | INDOOROOPILLY, TARINGA | Urban | 327 | 0.5362 | 0.9805 | 2.9913
IDY1A | CHAPEL HILL, INDOOROOPILLY | Urban | 1110.2475 | 3.6512 | 1.5168 | 2.9913 | 78.4949 | 0.048384 | 7 | 1978295.7222 | 271787.3822 | 0.0035567 | 0.0023386 | 1 | 2030.4 | 1.4485e-05
IDY5A | INDOOROOPILLY | Urban | 570.83 | 1.8037 | 0.3484 | 2.4769 | 0.021722 | 0.039963 | 0 | 0 | 0 | 0 | 0 | 1 | 1971.6 | 6.3741e-06
IDY6A | INDOOROOPILLY, TARINGA, TOOWONG | Urban | 1068.3209 | 2.873 | 0.5919 | 2.0306 | 8.1748 | 0.52091 | 6 | 507952.5163 | 477615.5163 | 0.0014927 | 0.001481 | 5 | 17774.2587 | 6.7011e-05
IDY9B | INDOOROOPILLY | Urban | 908.964 | 2.3198 | 1.8123 | 3.2771 | 30.1139 | 0.31415 | 3 | 1503509.3 | 154890.3 | 0.0018331 | 0.00091661 | 2 | 7307.42 | 3.1836e-05
INA10A | FOREST LAKE, INALA, RICHLANDS | Rural short | 946.99 | 2.8307 | 3.7548 | 1.791
INA11A | FOREST LAKE, INALA | Urban | 1488.65 | 3.1234 | 3.3587 | 2.5279 | 42.627 | 0.067087 | 3 | 1913852.35 | 3250 | 0.0015129 | 5.0485e-05 | 2 | 3168.6 | 1.1633e-05
INA1A | DOOLANDELLA, INALA | Urban | 778.3125 | 4.9095 | 2.1614 | 2.515 | 6.6565 | 0.06002 | 6 | 141565.04 | 129148.04 | 0.0023653 | 0.0015959 | 2 | 2672.34 | 8.9445e-06
INA2A | DURACK, INALA | Urban | 1793.345 | 4.2359 | 6.2472 | 3.8681 | 7.6048 | 0.34255 | 6 | 388228.255 | 388228.255 | 0.0037335 | 0.0037335 | 4 | 18768.0479 | 6.7635e-05
INA3A | DOOLANDELLA, FOREST LAKE, INALA | Urban | 2047.25 | 2.2356 | 7.6752 | 4.2319 | 2.5743 | 0.0013861 | 2 | 128361.42 | 5907.33 | 7.6055e-05 | 3.9026e-05 | 1 | 81.9 | 1.1682e-06
INA5A | INALA, RICHLANDS, WACOL | Urban | 744.9929 | 2.6857 | 3.641 | 3.7535 | 0.76221 | 0.080329 | 3 | 5320.88 | 5320.88 | 6.6137e-05 | 6.6137e-05 | 2 | 545.207 | 2.1981e-06
INA7A | INALA, OXLEY, RICHLANDS | Rural short | 1192.946 | 7.5662 | 1.9618 | 2.6425 | 60.1106 | 2.0847 | 3 | 1753726.38 | 14692 | 0.0037103 | 0.00030224 | 11 | 28321.2762 | 0.00027595
INA9A | DURACK, INALA | Urban | 1280.3071 | 5.2309 | 4.3657 | 4.306 | 114.274 | 0.18234 | 4 | 2711524.5 | 169787.5 | 0.003887 | 0.0025961 | 3 | 9768.71 | 4.204e-05
IPL1 | BARNEY VIEW, INNISPLAIN, MAROON, MT LINDESAY, OAKY | Rural short | 653.2351 | 158.0526 | 0.0739 | 1.7512 | 2.7383 | 1.6569 | 13 | 49612.465 | 39569.905 | 0.0066506 | 0.0043299 | 26 | 42756.5412 | 0.00051919
IPL2A | CHRISTMAS CREEK, INNISPLAIN, JOSEPHVILLE, KNAPP CR | Rural short | 285.3217 | 93.6587 | 0.0323 |  | 10.1634 | 0.44964 | 3 | 29425.37 | 28287.45 | 0.0017468 | 0.00092849 | 3 | 3446.83 | 4.943e-05
IPL3 | CANUNGRA, CHINGHEE CREEK, CHRISTMAS CREEK, DARLING | Rural short | 473.9833 | 124.4781 | 0.4948 | 1.5203 | 3.0855 | 0.81898 | 11 | 90997.64 | 89279.72 | 0.0061774 | 0.004942 | 19 | 31265.34 | 0.00063047
IPL4A | CHINGHEE CREEK, INNISPLAIN, MOUNT GIPPS, OAKY CREE | Rural short | 86.165 | 49.956 | 0.136 |  | 0.064716 | 0.4234 | 1 | 117.32 | 0 | 8.4363e-05 | 0 | 1 | 7123.2 | 4.5831e-05
IPS12B | CHURCHILL, DEEBING HEIGHTS, FLINDERS VIEW, RACEVIE | Urban | 992.5 | 4.5635 | 3.2338 | 3.2581 | 1.5015 | 0 | 1 | 38707.5 | 38707.5 | 0.0010034 | 0.0010034 | 0 | 0 | 0
IPS13A | AMBERLEY, CHURCHILL, DEEBING HEIGHTS, GOOLMAN, PUR | Rural short | 564 | 15.5651 | 4.5749 | 3.582 | 4.1734 | 0 | 4 | 77980.64 | 26396 | 0.0017843 | 0.0016614 | 0 | 0 | 0
IPS15B | AMBERLEY, CHURCHILL, ONE MILE, YAMANTO | Urban | 1096.83 | 11.2581 | 1.9116 | 4.0202 | 3.7618 | 0 | 2 | 29848.26 | 29848.26 | 0.00075854 | 0.00075854 | 0 | 0 | 0
IPS16A | FLINDERS VIEW, YAMANTO | Urban | 1354 | 1.1344 | 6.896 | 4.4584 | 1.9274 | 0 | 4 | 58069.31 | 58069.31 | 0.0014348 | 0.0014348 | 0 | 0 | 0
IPS1B | AMBERLEY, CHURCHILL, LEICHHARDT, ONE MILE, RACEVIE | Urban | 2135.58 | 11.7212 | 1.0215 | 5.754 | 4.4079 | 1.0991 | 5 | 102742.99 | 100247.49 | 0.0026158 | 0.0026001 | 7 | 14166.9001 | 5.5932e-05
IPS2B | FLINDERS VIEW, RACEVIEW, RIPLEY, YAMANTO | Rural short | 1271.045 | 15.8077 | 3.9157 | 3.5248 | 58.6948 | 0.4162 | 6 | 1647698.25 | 49846.76 | 0.014665 | 0.0036552 | 5 | 2185.48 | 0.00010575
IPS3A | DEEBING HEIGHTS, YAMANTO | Rural short | 519.8333 | 6.0424 | 4.3096 | 1.791 | 3.312 | 0.16715 | 4 | 74422.42 | 74422.42 | 0.0031366 | 0.0031366 | 2 | 3404 | 2.3326e-05
IPS5B | EASTERN HEIGHTS, IPSWICH, RACEVIEW | Urban | 1952.8583 | 8.8687 | 2.6614 | 4.7633 | 2.8501 | 0.079669 | 3 | 101887.74 | 101887.74 | 0.0021862 | 0.0021862 | 3 | 4854.25 | 1.7938e-05
JBB12B | JIMBOOMBA, NORTH MACLEAN, SOUTH MACLEAN, STOCKLEIG | Rural short | 766.1859 | 25.8848 | 6.9144 | 2.5531 | 30.7587 | 2.8903 | 5 | 440389 | 105430.5 | 0.0045229 | 0.002261 | 12 | 29537.775 | 0.00025929
JBB13A | JIMBOOMBA, MUNDOOLUN, TAMBORINE | Rural short | 1123.6888 | 42.6889 | 2.693 | 3.2962 | 153.2611 | 3.2646 | 12 | 4549953.32 | 51628.32 | 0.0095785 | 0.0020529 | 5 | 70467.37 | 0.00065788
JBB16A | JIMBOOMBA, LOGAN VILLAGE, STOCKLEIGH, TAMBORINE, Y | Rural short | 680.3302 | 36.029 | 2.175 | 1.8574 | 40.6569 | 6.5759 | 15 | 1409572.6933 | 64998.1933 | 0.0082979 | 0.0036333 | 36 | 231867 | 0.0020361
JBB1B | CEDAR GROVE, CEDAR VALE, JIMBOOMBA, MUNDOOLUN, VER | Rural short | 1538.665 | 48.0717 | 4.5547 | 4.3251 | 83.3481 | 0.83965 | 9 | 2275428 | 17344.5 | 0.009207 | 0.0020473 | 3 | 27093.82 | 0.00034376
JBB2A | CHAMBERS FLAT, JIMBOOMBA, LOGAN VILLAGE, MUNRUBEN, | Rural short | 777.2722 | 42.0522 | 0.4289 | 2.3435 | 115.693 | 0.20946 | 7 | 2848652.99 | 15552.34 | 0.0026953 | 0.00013713 | 2 | 6613.88 | 0.00011299
JBB3A | ALLENVIEW, CEDAR GROVE, JIMBOOMBA, KAGARU, UNDULLA | Rural short | 974.122 | 62.3638 | 3.5349 | 2.9342 | 135.143 | 3.2482 | 8 | 3764359.8 | 123172.8 | 0.011252 | 0.0060043 | 7 | 28501.755 | 0.00029068
JBB4A | JIMBOOMBA | Urban | 459.5578 | 9.5549 | 1.4436 | 3.2771 | 97.8905 | 0.12848 | 7 | 1680703.32 | 2977.32 | 0.00047997 | 4.0191e-05 | 2 | 9906 | 3.1842e-05
JDL3 | JAMBOREE HEIGHTS, MT OMMANEY | Urban | 195 | 0 | 3.7603 | 1.9244
JDL4A | JINDALEE, MT OMMANEY | Urban | 761.74 | 3.4208 | 2.6297 |  | 0.10493 | 0.082051 | 1 | 746.7 | 746.7 | 3.9637e-05 | 3.9637e-05 | 2 | 3714.962 | 1.2911e-05
JDL5 | JINDALEE | Urban | 567.33 | 3.3143 | 0.1919 | 3.4677 | 0.040085 | 0.39543 | 0 | 0 | 0 | 0 | 0 | 1 | 619.5 | 1.501e-06
JDL6 | JINDALEE, KENMORE | Urban | 307.16 | 1.6886 | 1.069 | 0.83834 | 0 | 0.054277 | 0 | 0 | 0 | 0 | 0 | 1 | 2037.75 | 6.2968e-06
JDL7 | JINDALEE, MT OMMANEY, WESTLAKE | Urban | 934.3529 | 0 | 6.0344 | 2.6484 | 0.1339 | 0.30863 | 2 | 5742.774 | 5742.774 | 4.669e-05 | 4.669e-05 | 5 | 34435.187 | 0.00012827
JDL8A | JINDALEE, OXLEY, SEVENTEEN MILE ROCKS, SINNAMON PA | Urban | 416.83 | 1.0451 | 4.7069 | 4.4965 | 0 | 0.21205 | 0 | 0 | 0 | 0 | 0 | 3 | 6377.01 | 3.4692e-05
JHDMDH11 | PINKENBA | Urban | 29 | 1.3677 | 0.6744 | 2.1149
JHDMDH7 | PINKENBA | Urban | 7 | 1.3561 | 1.3771 | 2.7055 | 6.2491 | 0 | 3 | 1506 | 234 | 1.819e-05 | 1.2124e-05 | 0 | 0 | 0
KBN13A | BRASSALL, KARRABIN, WULKURAKA | Rural short | 919.5033 | 11.7274 | 1.2749 | 2.9342 | 2.5717 | 0.95083 | 1 | 79995 | 79995 | 0.0025033 | 0.0025033 | 2 | 9551.1 | 6.8579e-05
KBN15A | KARRABIN, LEICHHARDT, WULKURAKA | Urban | 90.5 | 7.0896 | 1.1012 | 5.392 | 6.6213 | 2.0357 | 3 | 5672.4 | 5672.4 | 9.2294e-05 | 9.2294e-05 | 2 | 15551.96 | 5.2432e-05
KBN1B | BLACKSOIL, BRASSALL, KARRABIN, MUIRLEA | Rural short | 1396.4636 | 10.6013 | 7.0417 | 4.2488 | 319.4861 | 2.3 | 8 | 6448658.14 | 127052.14 | 0.0080782 | 0.0040982 | 5 | 4925.48 | 4.3259e-05
KBN2A | KARRABIN, ROSEWOOD, THAGOONA, WALLOON | Rural short | 757.8725 | 23.7206 | 1.3079 | 3.0485 | 0.34411 | 3.0405 | 3 | 8856.96 | 8856.96 | 0.00018554 | 0.00018554 | 9 | 70135.592 | 0.00062515
KBN3A | KARRABIN | Urban | 3 | 0.4233 | 0.2632 | 4.3684 | 0.027706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KBN5A | BLACKSOIL, BORALLON, FAIRNEY VIEW, HAIGSLEA, IRONB | Rural short | 1020.165 | 98.6844 | 2.1336 | 2.496 | 8.0063 | 1.6463 | 20 | 76141.3383 | 76065.1083 | 0.0027504 | 0.0027438 | 16 | 33730.24 | 0.00041591
KBR1A | ARATULA, CHARLWOOD, CLUMBER, FASSIFERN VALLEY, FRA | Rural short | 579.0405 | 113.9311 | 0.8922 | 1.81 | 2.1232 | 1.8268 | 8 | 18407.56 | 18001 | 0.00067634 | 0.00066115 | 12 | 18977.25 | 0.00022841
KBR2A | ARATULA, BOONAH, CHARLWOOD, FRAZERVIEW, KALBAR, MO | Rural short | 408.9832 | 71.9843 | 0.1022 | 1.8672 | 63.1681 | 7.7732 | 7 | 336674.89 | 22278.94 | 0.0030253 | 0.0025201 | 24 | 41643.41 | 0.00051553
KBR3A | ARATULA, FASSIFERN, FRAZERVIEW, KALBAR, ROSEVALE, | Rural short | 375.3377 | 50.8984 | 0.6344 | 1.3147 | 1.4047 | 6.262 | 5 | 6308.8 | 6308.8 | 0.0011374 | 0.0011374 | 8 | 25706.95 | 0.00020937
KBR5A | COULSON, HOYA, KALBAR, KULGUN, ROADVALE, TEVIOTVIL | Rural short | 216.6 | 50.0719 | 0.1699 | 0.49538 | 0.70498 | 0.44511 | 2 | 5487.24 | 5487.24 | 0.00029159 | 0.00029159 | 3 | 4945 | 4.6064e-05
KBR6A | ANTHONY, KALBAR, KENTS LAGOON, MILORA, MUNBILLA, O | Rural short | 401.787 | 76.5362 | 0.1456 | 1.1622 | 0.79172 | 23.6425 | 9 | 3832.65 | 3667.65 | 7.9809e-05 | 7.6933e-05 | 18 | 99288.985 | 0.00085946
KCY1 | KILCOY, WINYA | Urban | 615.8571 | 7.2093 | 0.0416 | 2.1149 | 11.6102 | 1.8793 | 5 | 201338 | 41606 | 0.0030909 | 0.0012348 | 9 | 37796.9 | 0.00012095
KCY2 | JIMNA, KILCOY, MOUNT KILCOY, SANDY CREEK, SHEEP ST | Rural short | 356.5718 | 111.1885 | 0 | 0.91455 | 18.1431 | 4.3852 | 13 | 441887.2 | 67938.34 | 0.007357 | 0.0038636 | 22 | 256702.9675 | 0.0023175
KCY3 | KILCOY, WINYA | Urban | 5.65 | 1.0657 | 0.0467 | 4.4775 | 25.7197 | 0 | 5 | 1858.85 | 384.2 | 2.8507e-05 | 1.1372e-05 | 0 | 0 | 0
KCY4 | KILCOY, MOUNT ARCHER, MT DELANEY, NEURUM, ROYSTON, | Rural short | 699.8863 | 115.0612 | 2.2305 | 1.4861 | 8.7168 | 1.6543 | 14 | 282604.82 | 79528 | 0.011001 | 0.004718 | 15 | 68932.6 | 0.0006728
KCY5 | GREGORS CREEK, HARLIN, HAZELDEAN, KILCOY, WINYA, W | Rural short | 526.5333 | 52.9128 | 1.2461 | 1.3909 | 35.416 | 15.4531 | 10 | 248302.82 | 99106.82 | 0.0097015 | 0.0048768 | 17 | 163276.73 | 0.0022626
KKMPRL1 | BRISBANE | CBD | 76 | 0 | 0.5718 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KLG10A | GRIFFIN, MURRUMBA DOWNS | Urban | 1501.1 | 2.3018 | 8.0656 | 4.649 | 0.067137 | 0.078416 | 1 | 259 | 259 | 1.0098e-06 | 1.0098e-06 | 4 | 1363.02 | 1.6791e-05
KLG11A | KALLANGUR | Urban | 2380.9427 | 9.7011 | 3.3493 | 5.5063 | 145.4173 | 1.0596 | 7 | 5897731.02 | 164369.71 | 0.0052121 | 0.002653 | 15 | 51605.39 | 0.00024778
KLG13A | KALLANGUR, PETRIE | Urban | 1518.74 | 8.4651 | 1.8087 | 3.9059 | 77.7322 | 0.04607 | 3 | 3098963.43 | 768.2 | 0.0016141 | 8.4045e-06 | 1 | 1908.27 | 8.2773e-06
KLG14A | KALLANGUR, MURRUMBA DOWNS, PETRIE | Urban | 948.6667 | 6.7105 | 5.0963 | 4.5156 | 21.8506 | 2.1028 | 2 | 162135.6 | 162135.6 | 0.00096055 | 0.00096055 | 3 | 15491.05 | 4.1122e-05
KLG16A | GRIFFIN, KALLANGUR, MANGO HILL, MURRUMBA DOWNS | Rural short | 1028.4167 | 7.7719 | 2.4296 | 2.515 | 0.031892 | 1.191 | 1 | 2952.4 | 2952.4 | 0.00010463 | 0.00010463 | 5 | 40626.4 | 0.00036691
KLG17A | KALLANGUR, MURRUMBA DOWNS | Urban | 1192.125 | 4.4414 | 0.9567 | 3.7154 | 4.8829 | 0.77669 | 8 | 100506.04 | 100506.04 | 0.0015688 | 0.0015688 | 4 | 12170.9905 | 6.0792e-05
KLG4A | KALLANGUR, PETRIE | Rural short | 855.33 | 6.6061 | 0.2083 | 1.7061
KLG5A | KALLANGUR, KURWONGBAH, PETRIE | Rural short | 1234.9475 | 12.4934 | 2.5027 | 2.9532 | 110.3767 | 0.90253 | 4 | 3128051.17 | 111619.05 | 0.0069116 | 0.0034084 | 4 | 10486.56 | 0.00014431
KLG7A | GRIFFIN, KALLANGUR, MURRUMBA DOWNS | Rural short | 2567.29 | 13.8116 | 10.1368 | 6.3066 | 8.2297 | 2.4263 | 3 | 169313.54 | 169313.54 | 0.0074529 | 0.0074529 | 10 | 33057.5 | 0.00025884
KMR17A | CHAPEL HILL, KENMORE | Urban | 582.5 | 3.1928 | 0.577 | 4.0202 | 30.3605 | 0.0064551 | 9 | 588669.4 | 79528.27 | 0.0031411 | 0.0024645 | 1 | 279.825 | 1.3781e-06
KMR17B | CHAPEL HILL, KENMORE | Urban | 1478.7778 | 8.7424 | 3.0635 | 4.2159 | 50.2346 | 0.1246 | 8 | 1743099.384 | 207475.564 | 0.0036149 | 0.0030685 | 1 | 5771.5 | 2.9715e-05
KMR18A | KENMORE, KENMORE HILLS | Urban | 413 | 2.4831 | 2.1258 | 1.5085 | 0.013454 | 0.35152 | 0 | 0 | 0 | 0 | 0 | 1 | 2798.145 | 6.6796e-06
KMR19A | BROOKFIELD, KENMORE, PINJARRA HILLS, PULLENVALE | Urban | 684.1767 | 7.4138 | 0.9453 | 2.4578 | 90.9125 | 0.48463 | 2 | 2319605.72 | 9792 | 0.00073964 | 5.1336e-05 | 10 | 12523.945 | 4.9851e-05
KMR21A | CHAPEL HILL, KENMORE HILLS | Urban | 1046.1225 | 1.7145 | 5.937 | 3.249 | 18.9299 | 0.63985 | 1 | 1269725.29 | 0 | 0.0010595 | 0 | 11 | 43584.62 | 0.00012275
KMR21B | KENMORE | Urban | 43.755 | 0 | 0.8743 | 0.70496 | 43.6707 | 0.4392 | 1 | 48598.88 | 0 | 4.2138e-05 | 0 | 3 | 7145.71 | 1.979e-05
KMR22A | FIG TREE POCKET, KENMORE | Urban | 847.29 | 6.5269 | 2.7104 | 3.0362 | 34.215 | 0.32499 | 3 | 1826672.6376 | 12572.7976 | 0.00088292 | 2.9492e-05 | 5 | 4832.8596 | 2.516e-05
KMR24A | KENMORE | Urban | 747.46 | 4.0412 | 0.4839 | 2.0693 | 0.25264 | 0.28507 | 1 | 11237.55 | 11237.55 | 0.00074817 | 0.00074817 | 3 | 12190.48 | 4.3553e-05
KMR25A | BROOKFIELD, KENMORE HILLS, MT COOTTHA, PULLENVALE, | Rural short | 1081.4936 | 46.1324 | 5.5764 | 5.1055 | 64.6006 | 2.6283 | 12 | 1652797.58 | 95236.58 | 0.0048446 | 0.0032774 | 9 | 42402.91 | 0.00072849
KMR27A | BROOKFIELD, KENMORE | Urban | 936.6219 | 7.0227 | 4.2367 | 3.4424 | 88.1426 | 1.592 | 4 | 2828324.47 | 75264.25 | 0.0019354 | 0.00098673 | 12 | 43050.4495 | 0.0001639
KMR28A | CHAPEL HILL, KENMORE HILLS | Urban | 936.656 | 2.7501 | 5.3177 | 2.3626 | 59.2688 | 0.59757 | 4 | 2459516.125 | 20905.125 | 0.0022289 | 0.000305 | 6 | 41920.765 | 0.00011301
KMR29A | KENMORE | Urban | 791.3033 | 3.7797 | 2.7323 | 2.282 | 0.17354 | 0.059321 | 2 | 11886.65 | 5637.5 | 2.2079e-05 | 2.0714e-05 | 1 | 1999.1433 | 7.7356e-06
KRA1 | COOLANGATTA | Urban | 598.1 | 1.3877 | 0.3331 | 2.5722 | 0.83861 | 0.4289 | 4 | 44629.38 | 41667.73 | 0.0024046 | 0.0018058 | 1 | 10216.44 | 4.308e-05
KRA10 | BILINGA, COOLANGATTA | Urban | 1087.995 | 3.3057 | 0.8578 | 1.9822 | 0.53696 | 0.03903 | 3 | 32489.9 | 27083.25 | 0.0032791 | 0.0021859 | 1 | 11038.95 | 4.3712e-05
KRA2 | COOLANGATTA | Urban | 820.66 | 1.9222 | 1.4055 | 3.9821 | 1.188 | 0 | 4 | 28697.8 | 24592 | 0.0025234 | 0.0016932 | 0 | 0 | 0
KRA3 | BILINGA, TUGUN | Urban | 1331.9091 | 3.9068 | 1.719 | 2.2457 | 5.4857 | 1.0542 | 7 | 758379.25 | 126814.5 | 0.0052413 | 0.0037145 | 4 | 35949.585 | 9.5689e-05
KRA4 | COOLANGATTA | Urban | 289.6667 | 0.0162 | 3.5424 | 2.3245 | 0.47268 | 0 | 3 | 8678 | 7230.5 | 0.00087581 | 0.00058313 | 0 | 0 | 0
KRA7 | COOLANGATTA | Urban | 1223.901 | 3.7541 | 0.7976 | 3.6582 | 29.9153 | 0.3069 | 5 | 1719459.54 | 134477.76 | 0.0050084 | 0.0037713 | 4 | 25105.4916 | 0.0001208
KRN1 | GORDON PARK, KEDRON, STAFFORD | Urban | 2079.05 | 3.0374 | 3.9755 | 4.306 | 0.41268 | 0.11175 | 3 | 18130.53 | 18130.53 | 0.00019642 | 0.00019642 | 2 | 6425.04 | 1.5182e-05
KRN10 | KEDRON, STAFFORD, STAFFORD HEIGHTS | Urban | 1515.6875 | 5.679 | 0.8142 | 2.7436 | 2.492 | 0.44379 | 1 | 135351 | 135351 | 0.001546 | 0.001546 | 6 | 28616.13 | 9.6165e-05
KRN11 | CLAYFIELD, LUTWYCHE, WAVELL HEIGHTS, WOOLOOWIN | Urban | 1304.426 | 5.7448 | 1.4027 | 3.6963 | 2.8176 | 0 | 5 | 358091.57 | 115131.57 | 0.0016453 | 0.0015644 | 0 | 0 | 0
KRN12 | GORDON PARK, LUTWYCHE, WOOLOOWIN | Urban | 1656.3908 | 2.8887 | 2.1049 | 2.4825 | 5.5664 | 1.1732 | 5 | 284049.06 | 284049.06 | 0.0020278 | 0.0020278 | 7 | 64937.535 | 0.00016312
KRN13A | KEDRON | Urban | 2 | 0 | 1.441
KRN13B | KEDRON, LUTWYCHE, WINDSOR | Urban | 5 | 0 | 3.0375
KRN18 | GORDON PARK, GRANGE, KEDRON, LUTWYCHE, WINDSOR | Urban | 1451 | 4.6236 | 0.2276 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRN2 | KEDRON, WAVELL HEIGHTS | Urban | 2008.6012 | 6.6461 | 1.28 | 3.6564 | 0.16169 | 0.25498 | 2 | 4166.255 | 4166.255 | 0.00030453 | 0.00030453 | 6 | 17714.0675 | 6.2185e-05
KRN3A | KEDRON | Urban | 2 | 0 | 1.2392
KRN3B | KEDRON, LUTWYCHE, WINDSOR | Urban | 4 | 0 | 2.2019
KRN5A | KEDRON | Urban | 770.6667 | 4.2643 | 2.0614 | 3.9249 | 12.187 | 0 | 3 | 257322.95 | 4017.45 | 0.00082761 | 4.8972e-05 | 0 | 0 | 0
KRN5B | STAFFORD | Urban | 323.5 | 0.8973 | 3.5854 | 2.2292 | 10.1851 | 0 | 1 | 49819 | 0 | 0.00032607 | 0 | 0 | 0 | 0
KRN6A | LUTWYCHE | Urban | 3 | 0 | 1.8906 | 2.1911
KRNQNP7 | BOWEN HILLS, LUTWYCHE, WINDSOR | Urban | 673 | 0.2064 | 7.2552 | 2.7055 | 0 | 0.020161 | 0 | 0 | 0 | 0 | 0 | 1 | 423.3 | 5.1213e-06
KSN1 | CHAMBERS FLAT, CRESTMEAD, MARSDEN, WATERFORD WEST | Urban | 1659.6278 | 10.5269 | 0.52338 | 4.0213 | 4.2664 | 0.51127 | 5 | 162478.64 | 8768.64 | 0.0013832 | 9.7109e-05 | 4 | 6925.45 | 3.3244e-05
KSN14 | MARSDEN | Urban | 1070 | 5.1308 | 1.112 | 3.0598 | 0.012757 | 0.00547 | 1 | 607.7 | 607.7 | 1.0413e-05 | 1.0413e-05 | 1 | 279.48 | 2.0498e-06
KSN15 | LOGANLEA, MEADOWBROOK, WATERFORD WEST | Rural short | 909.3333 | 7.0106 | 1.2345 | 2.0006 | 11.2778 | 0.38944 | 2 | 389425.49 | 10192 | 0.0028869 | 0.00028048 | 1 | 14564 | 0.00021251
KSN2A | LOGAN RESERVE, WATERFORD WEST | Urban | 1005 | 3.6934 | 1.6168 | 4.9458
KSN3 | KINGSTON, LOGANLEA | Urban | 629.1225 | 8.9045 | 1.6272 | 4.3684 | 13.9633 | 0.00039892 | 2 | 121043 | 121043 | 0.0012727 | 0.0012727 | 1 | 62 | 1.0041e-06
KSN4 | LOGANLEA | Urban | 997.4433 | 3.4588 | 0.4462 | 2.0014 | 0.14656 | 0.074695 | 2 | 19020 | 2444 | 0.00016961 | 9.5023e-05 | 1 | 7688.32 | 2.3492e-05
KSN5 | MARSDEN | Rural short | 1633.055 | 11.3403 | 0.5662 | 3.2009 | 0.077142 | 0.22281 | 2 | 4588.2 | 4588.2 | 0.00018442 | 0.00018442 | 4 | 9099.12 | 0.00010044
KSN6 | KINGSTON, LOGANLEA | Urban | 778.365 | 5.7213 | 1.692 | 4.0583 | 48.7022 | 0.017317 | 3 | 691016.33 | 98090.72 | 0.0015592 | 0.00079945 | 1 | 1392.6876 | 4.7996e-06
KSN7 | LOGAN RESERVE, WATERFORD, WATERFORD WEST | Rural short | 1272.5213 | 19.2469 | 0.733 | 3.8868 | 67.3052 | 0.65647 | 8 | 3591093.1 | 163158.6 | 0.0081036 | 0.0044004 | 7 | 32263.54 | 0.00043084
KSN8 | CHAMBERS FLAT, CRESTMEAD, LOGAN RESERVE, MARSDEN, | Rural short | 1138.075 | 23.7072 | 3.3943 | 1.2509 | 26.8209 | 0.19492 | 3 | 1317008.68 | 210629.45 | 0.0083953 | 0.0042362 | 3 | 9081.7 | 0.00017055
KWA10A | BIRTINYA, BOKARINA, WARANA | Urban | 582.5714 | 2.7272 | 5.4993 | 4.9729 | 0.67839 | 1.3608 | 2 | 5785 | 5785 | 0.00061627 | 0.00061627 | 5 | 14063.855 | 8.1502e-05
KWA11A | BIRTINYA, BOKARINA | Urban | 359 | 0 | 6.3327 | 4.4203
KWA12A | BUDDINA, WARANA | Urban | 2368.1538 | 9.8861 | 1.5105 | 5.5915 | 87.2381 | 1.6259 | 7 | 3221373.23 | 205109.73 | 0.0050843 | 0.0024892 | 6 | 56762.47 | 0.00022246
KWA1A | BUDDINA, MINYAMA, PARREARRA, WARANA | Urban | 1434.745 | 5.2719 | 3.7524 | 4.4093 | 0.10437 | 0.017203 | 1 | 1388.97 | 1388.97 | 2.323e-05 | 2.323e-05 | 1 | 4483.5 | 9.1887e-05
KWA2A | BOKARINA, WARANA, WURTULLA | Urban | 834.6944 | 5.2253 | 0.713 | 2.0768 | 0 | 2.1757 | 0 | 0 | 0 | 0 | 0 | 9 | 131335.54 | 0.00049772
KWA3A | BUDDINA, MINYAMA | Urban | 735.9 | 4.258 | 3.379 | 4.8585 | 1.9446 | 0.063488 | 2 | 10396 | 10396 | 0.00074328 | 0.00074328 | 3 | 2343.29 | 1.3023e-05
KWA4A | PARREARRA, WARANA | Urban | 2061.5 | 0 | 6.2569 | 4.2546 | 0.011903 | 0.49999 | 1 | 425.6 | 425.6 | 1.0682e-05 | 1.0682e-05 | 5 | 16324.925 | 0.00028848
KWA6A | BOKARINA, WARANA | Urban | 339.7812 | 2.534 | 1.9539 | 1.5433 | 0 | 1.5639 | 0 | 0 | 0 | 0 | 0 | 8 | 20860.9625 | 9.0768e-05
KWH1 | COOLABINE, KENILWORTH, KIDAMAN CREEK, MAPLETON, OB | Rural short | 554.5006 | 56.0308 | 0.4127 | 1.3279 | 78.4345 | 1.5345 | 7 | 2950558.57 | 86145.57 | 0.0042325 | 0.0012383 | 9 | 54026.903 | 0.00054021
KWH2 | CAMBROON, CONONDALE, KENILWORTH | Rural short | 806.4833 | 108.8741 | 0.1507 | 1.6957 | 42.8834 | 0.67568 | 7 | 2144950.65 | 127191.32 | 0.0059776 | 0.0024917 | 11 | 20638.97 | 0.00026853
KWH3 | BELLI PARK, BROOLOO, COOLABINE, GHEERULLA, KENILWO | Rural short | 388.9147 | 74.9552 | 0.2782 | 2.2433 | 6.349 | 1.0559 | 5 | 169516.13 | 7685.88 | 0.001414 | 0.00012318 | 9 | 43918.5487 | 0.00042729
LBCVPK5 | FORTITUDE VALLEY, SPRING HILL | Urban | 130.42 | 0 | 1.9028 | 3.7725 | 1.3593 | 0.012509 | 3 | 20041.993 | 20041.993 | 0.0002729 | 0.0002729 | 1 | 643.526 | 2.4383e-06
LBH1B | BALD KNOB, LANDSBOROUGH, MALENY, MOUNT MELLUM | Rural short | 995.4175 | 31.4633 | 0.5973 | 2.2708 | 7.4328 | 8.2622 | 11 | 250340.18 | 194109.68 | 0.012862 | 0.0072095 | 21 | 272376.0692 | 0.0024416
LBH3A | GLENVIEW, LANDSBOROUGH, MOOLOOLAH VALLEY | Rural short | 785.7382 | 20.7265 | 0.8957 | 2.0387 | 110.1631 | 1.2969 | 5 | 3831924.3098 | 2418.9598 | 0.0045506 | 6.753e-05 | 6 | 45515.375 | 0.00061704
LBH5A | BELLS CREEK, GLENVIEW, LANDSBOROUGH, MERIDAN PLAIN | Rural short | 765.0736 | 42.478 | 4.8453 | 2.9723 | 183.2479 | 0.26029 | 6 | 2048363.55 | 25268.01 | 0.0049524 | 0.00059116 | 5 | 7890.51 | 8.3876e-05
LBH6A | BEERWAH, LANDSBOROUGH | Rural short | 1647.7475 | 29.0047 | 2.9221 | 4.546 | 74.6134 | 2.0616 | 8 | 2072937.46 | 280115.46 | 0.019013 | 0.012173 | 12 | 79563.865 | 0.0010934
LBS10A | HEMMANT | Urban | 38 | 0.9534 | 1.6995 | 2.9913 | 0 | 6.3605 | 0 | 0 | 0 | 0 | 0 | 2 | 948 | 2.0108e-06
LBS12A | HEMMANT | Urban | 48.99 | 1.8608 | 3.9639 | 2.0387 | 12.2353 | 13.325 | 1 | 5289.99 | 5289.99 | 4.9305e-05 | 4.9305e-05 | 2 | 6182.14 | 2.6213e-06
LBS13A | LYTTON | Urban | 41 | 0 | 1.587 | 4.5156 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LBS2A | HEMMANT, LYTTON | Urban | 43 | 0.3731 | 3.5537 | 2.4197 | 0 | 5.3549 | 0 | 0 | 0 | 0 | 0 | 1 | 1840 | 4.0267e-06
LBS4A | LYTTON | Urban | 34 | 0 | 2.6318 | 3.8297
LBS5A | LYTTON, PORT OF BRISBANE, WYNNUM | Urban | 252.5 | 3.1372 | 4.0676 | 2.6293
LBS8B | WYNNUM, WYNNUM WEST | Urban | 175 | 1.8625 | 0.8327 | 0.9336 | 0 | 2.5605 | 0 | 0 | 0 | 0 | 0 | 2 | 1894.44 | 1.1103e-05
LDR1 | RUNAWAY BAY | Urban | 553.849 | 2.772 | 1.1131 | 2.1554 | 0 | 0.59358 | 0 | 0 | 0 | 0 | 0 | 10 | 64540.3884 | 0.00019559
LDR10A | ARUNDEL, LABRADOR | Urban | 2241.3575 | 4.9046 | 1.2058 | 3.8678 | 0.057577 | 0.39883 | 1 | 3387.7833 | 3387.7833 | 3.2913e-05 | 3.2913e-05 | 2 | 6859.65 | 1.8518e-05
LDR10B | BIGGERA WATERS, LABRADOR | Urban | 6 | 0 | 2.3599 | 4.1726 | 0.013192 | 0
LDR11 | LABRADOR | Urban | 193 | 1.4864 | 0.2984 | 0.55808 | 0.0010244 | 0 | 1 | 537.92 | 537.92 | 3.2947e-06 | 3.2947e-06 | 0 | 0 | 0
LDR2A | BIGGERA WATERS, LABRADOR | Urban | 148.83 | 2.3077 | 0.8329 | 2.2102 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LDR2B | LABRADOR | Urban | 962.5067 | 1.3355 | 1.5518 | 1.8191 | 0.30971 | 0 | 3 | 13593.5 | 13534.5 | 0.00031066 | 0.00030965 | 0 | 0 | 0
LDR3 | BIGGERA WATERS, LABRADOR, RUNAWAY BAY | Urban | 2229.4069 | 3.46 | 1.146 | 4.0806 | 48.4613 | 3.5006 | 5 | 3172080.77 | 39219.6 | 0.0027829 | 0.00017367 | 11 | 263113.6468 | 0.00080669
LDR5 | BIGGERA WATERS, LABRADOR | Urban | 518 | 2.0381 | 1.1302 | 3.8297 | 0 | 0.9343 | 0 | 0 | 0 | 0 | 0 | 2 | 21743.31 | 6.8515e-05
LDR6 | BIGGERA WATERS, LABRADOR | Urban | 1754.25 | 1.9732 | 1.4232 | 3.4062 | 0 | 0.0048634 | 0 | 0 | 0 | 0 | 0 | 1 | 328.57 | 3.2243e-06
LDR8 | BIGGERA WATERS, LABRADOR, RUNAWAY BAY | Urban | 1142.9529 | 3.4702 | 0.9997 | 3.2908 | 2.0099 | 3.5383 | 1 | 125960.54 | 125960.54 | 0.0011466 | 0.0011466 | 30 | 189235.7913 | 0.0006346
LGL11A | KINGSTON, LOGAN CENTRAL, SLACKS CREEK | Urban | 2186.0267 | 7.5068 | 0.9231 | 6.1966 | 0.53114 | 0.071996 | 2 | 30409.875 | 30409.875 | 7.2735e-05 | 7.2735e-05 | 4 | 3631.08 | 1.5703e-05
LGL13A | LOGANLEA, MEADOWBROOK | Urban | 522.3125 | 2.7351 | 3.7294 | 3.1057 | 296.6227 | 0 | 4 | 2491755.25 | 203767.25 | 0.0021051 | 0.0010512 | 0 | 0 | 0
LGL15A | KINGSTON, LOGANLEA, MEADOWBROOK, SLACKS CREEK | Urban | 952.2936 | 5.3962 | 1.8935 | 2.5531 | 43.8844 | 8.8404 | 5 | 1113193.83 | 117038.83 | 0.0030722 | 0.0021187 | 6 | 59033.085 | 0.00017907
LGL3A | LOGANLEA, MEADOWBROOK | Urban | 673.168 | 5.1493 | 1.023 | 2.1339 | 23.4778 | 0.055711 | 3 | 467460.565 | 130163.565 | 0.0013806 | 0.00070724 | 2 | 3868.8 | 1.6949e-05
LGL5A | MEADOWBROOK | Urban | 444.8 | 1.8342 | 2.11 | 3.3533 | 191.1696 | 0 | 5 | 1806123.16 | 2223.16 | 0.00086449 | 2.4671e-05 | 0 | 0 | 0
LGL7A | MEADOWBROOK | Urban | 0.68 | 0 | 2.3363 | 3.0213
LGV2B | CHAMBERS FLAT, LOGAN RESERVE, LOGAN VILLAGE, PARK | Rural short | 649.9 | 29.2609 | 4.0531 | 2.9782 | 33.6125 | 0.31711 | 7 | 726919.78 | 20846.78 | 0.0035898 | 0.0017662 | 3 | 19260.83 | 0.00017506
LGV3A | BUCCAN, CHAMBERS FLAT, LOGAN RESERVE, LOGAN VILLAG | Rural short | 210.5556 | 9.3437 | 0.5175 | 0.76212 | 44.4185 | 0.34894 | 7 | 999484.26 | 13361.35 | 0.0019721 | 0.00073863 | 2 | 2652 | 4.6179e-05
LGV5B | LOGAN VILLAGE | Rural short | 613.5 | 16.8404 | 1.1183 | 1.8672 | 74.947 | 0.068323 | 2 | 2419179.5 | 0 | 0.0035223 | 0 | 1 | 3810 | 2.8897e-05
LGV6A | BUCCAN, LOGAN VILLAGE, WATERFORD | Rural short | 750.5938 | 35.0821 | 1.2259 | 2.0006 | 123.7479 | 0.20368 | 13 | 3894643.0667 | 204705.0667 | 0.012874 | 0.0085199 | 3 | 10837.52 | 0.00014196
LHM1A | LOGANHOLME, TANAH MERAH | Urban | 1570.5 | 5.1537 | 5.6761 |  | 30.5396 | 0.3661 | 1 | 20537.5 | 20537.5 | 0.00013295 | 0.00013295 | 1 | 26726 | 8.3401e-05
LHM2 | LOGANHOLME, SHAILER PARK | Rural short | 558 | 4.4202 | 1.0575 | 1.1622
LHM3 | BEENLEIGH, LOGANHOLME | Rural short | 1731 | 10.6455 | 4.1739 | 4.1155
LHM4A | LOGANHOLME | Urban | 122 | 2.5176 | 0.6837 |  | 0 | 0.79019
LHM5 | CORNUBIA, LOGANHOLME | Rural short | 862.1592 | 8.2549 | 0.4265 | 2.2673 | 14.5722 | 1.8321 | 8 | 608824.7083 | 71335.1583 | 0.0056826 | 0.0032109 | 5 | 57179.15 | 0.00055409
LHM6 | SHAILER PARK | Urban | 6 | 0 | 3.2565 | 4.7061
LHM7 | LOGANHOLME | Urban | 256.5 | 2.2189 | 1.0933 | 4.0964 | 0.021733 | 0 | 1 | 418.5 | 418.5 | 1.5541e-05 | 1.5541e-05 | 0 | 0 | 0
LHM8A | CARBROOK, CORNUBIA, LOGANHOLME | Rural short | 454 | 6.8206 | 1.3451 | 0.91455 | 0.020854 | 0.017722 | 0 | 0 | 0 | 0 | 0 | 1 | 680.4 | 9.0744e-06
LHM8B | LOGANHOLME | Urban | 97 | 1.5115 | 1.0231 | 1.8482 | 0.046488 | 0
LHM9 | LOGANHOLME, SHAILER PARK | Urban | 6 | 0 | 3.2376 | 4.668
LLY1 | BLENHEIM, LAIDLEY, LAIDLEY CREEK WEST, LAIDLEY SOU | Rural short | 554.3228 | 107.9824 | 1.484 | 1.4099 | 35.3057 | 3.3543 | 9 | 1036822.34 | 193477.91 | 0.0043147 | 0.0037081 | 33 | 135681.3325 | 0.0013888
LLY2B | LAIDLEY | Urban | 15
LLY3 | BLENHEIM, FOREST HILL, GLEN CAIRN, GLENCAIRN, LAID | Rural short | 731.3729 | 78.2098 | 0.7014 | 1.6005 | 16.9638 | 3.4344 | 16 | 344107.79 | 114528.74 | 0.0032093 | 0.0028024 | 15 | 119277.11 | 0.00075374
LLY4 | FOREST HILL, LAIDLEY, LAIDLEY HEIGHTS, LAIDLEY NOR | Rural short | 1550.7652 | 45.1356 | 2.7594 | 4.6871 | 9.1218 | 5.9488 | 11 | 376240.18 | 374921.62 | 0.0091845 | 0.0091537 | 19 | 68127.2857 | 0.00050373
LLY5 | CALVERT, GRANDCHESTER, HIDDENVALE, LAIDLEY, LAIDLE | Rural short | 1092.2807 | 91.1963 | 1.3063 | 2.2292 | 2.4551 | 0.0324 | 8 | 136286.06 | 136286.06 | 0.003379 | 0.003379 | 4 | 821.84 | 2.0212e-05
LRE4A | CHURCHABLE, GLENORE GROVE, KENTVILLE, LOCKROSE, LO | Rural short | 321.4933 | 38.5297 | 0.287 | 0.66686 | 4.6294 | 0.3709 | 4 | 81481.1 | 5655.8 | 0.0018446 | 0.0009069 | 2 | 7364 | 5.7685e-05
LRE6A | ATKINSONS DAM, COOMINYA, KENTVILLE, LOCKROSE, LOCK | Rural short | 420.2976 | 50.2506 | 0.7258 | 1.3718 | 10.4927 | 0.13991 | 13 | 112407.64 | 37035.04 | 0.00090386 | 0.00055346 | 4 | 1675 | 5.8855e-05
LRE7A | BRIGHTVIEW, HATTON VALE, KENSINGTON GROVE, LOCKROS | Rural short | 1168.8333 | 32.3241 | 4.635 | 3.582 | 0.20534 | 0.30332 | 1 | 1093.42 | 0 | 6.6155e-05 | 0 | 2 | 7628.4 | 5.7629e-05
LRE8A | BRIGHTVIEW, LOCKROSE, MT TARAMPA, REGENCY DOWNS | Rural short | 433 | 23.8194 | 0.9425 | 1.2575 | 2.0826 | 2.3364 | 2 | 55334.6 | 798.6 | 0.00011904 | 2.0797e-05 | 8 | 76073.56 | 0.0006185
LTA12A | MANLY WEST, WYNNUM WEST | Urban | 1438.5 | 6.0261 | 1.0177 | 2.6865
LTA15A | LOTA, MANLY, MANLY WEST | Urban | 1188 | 5.0961 | 1.4065 | 2.6865
LTA16A | LOTA, MANLY WEST, WAKERLEY | Urban | 1501 | 2.1147 | 4.9668 | 4.2138 | 0 | 0.06723 | 0 | 0 | 0 | 0 | 0 | 1 | 1104 | 6.031e-06
LTA3A | BIRKDALE, LOTA, RANSOME, THORNESIDE | Urban | 1795.9925 | 14.3512 | 0.99163 | 3.6587 | 0.060903 | 0.22224 | 0 | 0 | 0 | 0 | 0 | 4 | 8536.03 | 4.1879e-05
LTA4A | GUMDALE, RANSOME, WAKERLEY | Urban | 1190.73 | 8.1122 | 8.3143 | 5.9084 | 0.076648 | 0 | 1 | 702.075 | 702.075 | 3.0798e-05 | 3.0798e-05 | 1 | 2488.7643 | 1.3398e-05
LTA5A | MANLY, MANLY WEST | Urban | 1268 | 3.141 | 4.6061 | 3.2824 | 0.050642 | 0
LTA8A | MANLY, MANLY WEST, WYNNUM, WYNNUM WEST | Urban | 1989.51 | 7.866 | 0.9651 | 4.2122 | 0.084098 | 0
LTN2 | JOYNER, KURWONGBAH, LAWNTON, PETRIE, WHITESIDE | Rural short | 1767.9929 | 10.5833 | 5.5051 | 5.2396 | 5.7212 | 0.018485 | 5 | 166352.88 | 60450.51 | 0.0098884 | 0.0050309 | 2 | 964.143 | 1.1107e-05
LTN3 | LAWNTON, PETRIE | Urban | 1638.8546 | 10.9919 | 1.1444 | 4.1345 | 6.9451 | 0.75862 | 7 | 182271.04 | 78205.12 | 0.0053677 | 0.0036996 | 5 | 36202.1652 | 9.8046e-05
LTN4 | BRAY PARK, STRATHPINE | Urban | 1585.21 | 7.9236 | 1.7513 | 5.5254 | 5.7271 | 0.06241 | 3 | 217605.32 | 120165.11 | 0.0033032 | 0.0017414 | 1 | 3049.2 | 9.2991e-06
LTN5 | BRAY PARK, BRENDALE, STRATHPINE | Urban | 834.16 | 9.2575 | 2.0115 | 3.8678 | 1.3341 | 0.11908 | 1 | 52804.08 | 0 | 0.00084639 | 0 | 1 | 3517.8 | 1.0728e-05
LTN6 | LAWNTON, STRATHPINE | Urban | 1517.592 | 12.8151 | 0.7248 | 5.1253 | 2.6894 | 0.21219 | 2 | 115820.37 | 24786 | 0.0021952 | 0.00073603 | 3 | 11268.39 | 3.2324e-05
LTN7 | BRAY PARK, LAWNTON, STRATHPINE | Urban | 580.8333 | 4.5338 | 1.337 | 3.7916 | 8.7496 | 0.16334 | 5 | 105314 | 69183.5 | 0.0017673 | 0.0011882 | 1 | 2043.6 | 5.1929e-06
LTN8 | BRAY PARK, JOYNER, LAWNTON | Rural short | 1018.3156 | 4.491 | 4.1062 | 1.6767 | 0.666 | 1.1567 | 4 | 41604.375 | 3909.585 | 0.0034873 | 0.0017583 | 4 | 28662.365 | 0.00027676
LTN9 | BRAY PARK, JOYNER, LAWNTON, STRATHPINE, WARNER | Urban | 1400.764 | 6.9953 | 4.0352 | 4.9729 | 2.8981 | 0.042462 | 3 | 90340 | 1447 | 0.0015154 | 9.053e-05 | 1 | 525.35 | 5.5793e-06
LWD1 | LOWOOD, PATRICK ESTATE, WIVENHOE POCKET | Rural short | 627.7143 | 21.1962 | 0.666 | 2.5912 | 26.4884 | 3.102 | 7 | 351707.77 | 13979.64 | 0.0054895 | 0.0037104 | 7 | 16792.48 | 0.00018426
LYT1 | LYTTON | Urban | 13 | 1.6509 | 0.3717 | 1.8291
MAI11 | MERMAID BEACH, MERMAID WATERS, MIAMI | Urban | 1711.281 | 3.6532 | 0.3711 | 4.0413 | 9.7207 | 1.9835 | 6 | 530444.09 | 16142.48 | 0.0021158 | 0.0002546 | 15 | 128529.9774 | 0.00045094
MAI13 | BURLEIGH WATERS, MIAMI | Urban | 1808.3589 | 2.9201 | 8.0238 | 4.1745 | 62.0624 | 0.28851 | 7 | 3049014.9 | 412540.5 | 0.0072025 | 0.0036104 | 2 | 10205.55 | 3.6178e-05
MAI14 | MIAMI | Urban | 1740.1825 | 3.1611 | 0.9431 | 4.2319 | 18.8912 | 0.74203 | 6 | 966538.348 | 356136.978 | 0.0040956 | 0.0019379 | 6 | 45236.096 | 0.00015082
MAI17 | BURLEIGH HEADS, MIAMI | Urban | 1870.865 | 5.1567 | 0.831 | 4.2128 | 44.6442 | 1.471 | 5 | 2556510.9212 | 21813.5412 | 0.0049035 | 0.001104 | 9 | 47106.1038 | 0.00014728
MAI5 | MERMAID BEACH, MERMAID WATERS, MIAMI | Urban | 1740.9333 | 3.1258 | 1.0708 | 4.0583 | 20.1418 | 0.19868 | 5 | 969622.02 | 181787.66 | 0.0037918 | 0.0018979 | 4 | 13561.7 | 5.026e-05
MAI7 | MERMAID BEACH, MERMAID WATERS, MIAMI | Urban | 1431.3071 | 0.9947 | 5.2615 | 3.2362 | 13.764 | 1.6712 | 2 | 427424.21 | 61577 | 0.0015795 | 0.00014047 | 5 | 31765.999 | 0.00016221
MAI8 | MERMAID BEACH, MERMAID WATERS, MIAMI, ROBINA | Urban | 1263 | 0.7799 | 6.0511 | 3.5409 | 9.2798 | 0 | 1 | 322969.33 | 0 | 0.0012704 | 0 | 0 | 0 | 0
MAK6 | SURFERS PARADISE | Urban | 128 | 0 | 0.205
MAK7 | SURFERS PARADISE | Urban | 16 | 0 | 0.245
MBG1 | ASHWELL, MARBURG, MINDEN, ROSEWOOD, TALLEGALLA, TH | Rural short | 293.6364 | 44.5492 | 0 | 0.62875 | 0.089255 | 1.4213 | 7 | 2519.96 | 2519.96 | 5.8969e-05 | 5.8969e-05 | 15 | 43369.78 | 0.00035097
MBG2 | HAIGSLEA, MARBURG, MT MARROW, ROSEWOOD, TALLEGALLA | Rural short | 485.1579 | 49.3953 | 0.1852 | 2.2102 | 0.37752 | 2.2778 | 3 | 12084.5 | 11073 | 0.00038151 | 0.00021103 | 15 | 89127.355 | 0.00064417
MBG4 | FAIRNEY VIEW, FERNVALE, GLAMORGAN VALE, HAIGSLEA, | Rural short | 414.8141 | 66.923 | 0.1399 | 1.0723 | 16.0291 | 0.6543 | 17 | 823226.6999 | 32669.6599 | 0.0019826 | 0.0013908 | 11 | 14048.03 | 0.00017323
MCN1 | MOUNT COTTON, SHELDON, THORNLANDS | Rural short | 92.794 | 15.0399 | 1.903 | 2.1911 | 106.4245 | 0.052099 | 4 | 309492.53 | 13121.52 | 0.00083129 | 0.00056486 | 1 | 134.5 | 1.4442e-06
MCN2 | MOUNT COTTON | Rural short | 76.6033 | 7.6939 | 1.6378 | 1.934 | 13.1751 | 0.35935 | 6 | 41374.2684 | 32440.3684 | 0.000538 | 0.00047537 | 3 | 8401.03 | 7.0115e-05
MCN3 | CORNUBIA, MOUNT COTTON | Urban | 55.5612 | 10.7925 | 0.1745 | 3.5629 | 5.7244 | 2.1513 | 4 | 4248.52 | 3926.52 | 0.00010989 | 0.00010888 | 12 | 7384.388 | 1.9261e-05
MCN4 | MOUNT COTTON | Rural short | 734.8867 | 1.4413 | 8.0425 | 2.2102 | 1.5369 | 0.99266 | 2 | 32473.35 | 32473.35 | 0.0020739 | 0.0020739 | 1 | 17371.5 | 0.00016032
MCW11 | KARANA DOWNS, KHOLO, MOUNT CROSBY | Rural short | 819.0811 | 20.2522 | 3.8175 | 2.6103 | 28.5388 | 4.7303 | 20 | 770495.595 | 100163.595 | 0.0097881 | 0.006669 | 16 | 117482.905 | 0.00098112
MCW4 | CHUWAR, KARANA DOWNS, MOUNT CROSBY | Rural short | 1275.549 | 10.6358 | 6.4159 | 3.3724 | 45.2625 | 0.56379 | 11 | 2493454.2232 | 537101.7232 | 0.0199 | 0.01258 | 9 | 32813.72 | 0.00030699
MCW7 | CHUWAR, KARALEE, KHOLO, LAKE MANCHESTER, MOUNT CRO | Rural short | 500.9971 | 42.4248 | 2.1078 | 1.2575 | 59.6183 | 3.4567 | 4 | 1259569.32 | 165101.82 | 0.005546 | 0.0032697 | 13 | 63899.3864 | 0.00072443
MDH1A | PINKENBA | Urban | 14 | 1.0209 | 1.8332 | 1.7338 | 2.1724 | 0 | 1 | 832 | 832 | 1.3054e-05 | 1.3054e-05 | 0 | 0 | 0
MDH3A | EAGLE FARM, PINKENBA | Urban | 85.451 | 0.8319 | 4.2977 | 4.1536 | 282.7176 | 2.7771 | 2 | 227563.14 | 1628 | 9.2171e-05 | 2.0218e-06 | 7 | 5740.8 | 1.5876e-05
MDH4A | PINKENBA | Urban | 138.5 | 3.7016 | 0.8262 | 1.6957 | 3.0617 | 0.0025446 | 2 | 13021.585 | 13021.585 | 0.00015324 | 0.00015324 | 1 | 200.07 | 1.7257e-06
MDH5A | EAGLE FARM, PINKENBA | Urban | 61.4 | 0.4552 | 2.5725 | 3.8678 | 10.5249 | 5.1539 | 3 | 8915 | 8915 | 0.00018885 | 0.00018885 | 2 | 579 | 2.0186e-06
MDH5B | EAGLE FARM, PINKENBA | Urban | 43.33 | 1.0986 | 3.6898 | 2.2673 | 6.6725 | 0 | 3 | 3293.08 | 3293.08 | 0.00012989 | 0.00012989 | 0 | 0 | 0
MDH8B | PINKENBA | Urban | 4 | 0 | 0.8955 | 3.6582 | 0.60968 | 0.11645 | 1 | 333.6 | 333.6 | 2.4144e-06 | 2.4144e-06 | 1 | 374 | 1.011e-06
MDH9A | EAGLE FARM, PINKENBA | Urban | 52.9 | 2.6236 | 1.0234 | 2.3245 | 5.8155 | 3.4388 | 1 | 5256.8 | 5256.8 | 5.0087e-05 | 5.0087e-05 | 3 | 2705 | 6.0451e-06
MDHSWB10 | PINKENBA | Urban | 4 | 0.5957 | 1.7052 | 1.7617 | 0.17814 | 0 | 1 | 76 | 76 | 4.0088e-06 | 4.0088e-06 | 0 | 0 | 0
MDR10A | MOLENDINAR | Urban | 830.09 | 1.1501 | 3.9833 | 1.7529 | 0 | 0.15279 | 0 | 0 | 0 | 0 | 0 | 1 | 95 | 1.0021e-06
MDR12B | ASHMORE, MOLENDINAR, SOUTHPORT | Urban | 259.33 | 2.1113 | 1.957 | 4.306 | 0 | 0.11314 | 0 | 0 | 0 | 0 | 0 | 1 | 4500.81 | 3.512e-05
MDR24A | ASHMORE, SOUTHPORT | Urban | 884.9589 | 2.7393 | 3.1556 | 2.4388 | 1.7664 | 0.6272 | 4 | 58583.22 | 58583.22 | 0.00083016 | 0.00083016 | 5 | 24896.0956 | 9.7162e-05
MDR25A | MOLENDINAR, NERANG | Urban | 191.745 | 5.1611 | 0.3086 | 4.0012 | 0.066341 | 5.1783 | 0 | 0 | 0 | 0 | 0 | 4 | 5453.0962 | 1.5012e-05
MDR2A | BENOWA | Urban | 383.2 | 3.3359 | 3.6546 | 3.6582 | 0 | 0.26551 | 0 | 0 | 0 | 0 | 0 | 5 | 50584.25 | 0.00011608
MDR30A | ASHMORE, BENOWA, CARRARA | Urban | 1592.49 | 3.002 | 7.1112 | 4.8204 | 0.038619 | 0 | 1 | 40 | 40 | 9.985e-07 | 9.985e-07 | 0 | 0 | 0
MDR31A | MOLENDINAR | Urban | 296.7011 | 1.9464 | 2.2906 | 3.5248 | 9.4676 | 2.2881 | 2 | 28192.31 | 413.36 | 6.3075e-05 | 5.2126e-05 | 7 | 6424.6074 | 5.8057e-05
MDR33A | ASHMORE, BENOWA | Urban | 1316.5787 | 3.3039 | 4.8423 | 3.7535 | 0.1741 | 1.528 | 2 | 3871.67 | 3871.67 | 8.7178e-05 | 8.7178e-05 | 6 | 46954.6 | 0.00018661
MDR35A | SOUTHPORT | Urban | 12 | 0 | 4.7431 | 2.496 | 5.6047 | 0 | 1 | 1005 | 1005 | 1.2077e-05 | 1.2077e-05 | 0 | 0 | 0
MDR3A | ASHMORE, CARRARA, MOLENDINAR, NERANG | Urban | 707.66 | 4.8649 | 5.0526 | 2.9723 | 0.18614 | 1.2564 | 1 | 5049 | 5049 | 5.1336e-05 | 5.1336e-05 | 2 | 26936.16 | 6.276e-05
MDR4A | MOLENDINAR, SOUTHPORT | Urban | 422.9 | 1.4162 | 4.1047 | 2.6865 | 14.4779 | 0 | 3 | 69972.1667 | 69972.1667 | 0.000862 | 0.000862 | 0 | 0 | 0
MDR6A | MOLENDINAR, SOUTHPORT | Urban | 637 | 3.9233 | 2.7358 | 3.3152
MDR8A | BENOWA, CARRARA | Urban | 256.4286 | 4.1584 | 6.7198 | 3.22 | 0.22186 | 1.0014 | 2 | 82.5 | 82.5 | 1.6065e-06 | 1.6065e-06 | 4 | 1572.56 | 6.4867e-06
MDRMLD11 | MOLENDINAR | Urban | 855.9436 | 2.7093 | 3.2454 | 3.6391 | 4.2657 | 1.777 | 4 | 101990.18 | 84570.18 | 0.0010726 | 0.0010048 | 10 | 16455.4146 | 0.00011732
MEX3 | BRISBANE, MILTON | Urban | 27 | 0 | 1.2442
MFD11A | MORAYFIELD | Rural short | 9 | 3.1236 | 1.8365 | 1.429 | 0.098223 | 0
MFD12A | BURPENGARY, BURPENGARY EAST, CABOOLTURE, MORAYFIEL | Rural short | 1549 | 10.7637 | 7.5691 | 4.8776
MFD13A | BURPENGARY | Rural short | 507.5 | 7.397 | 4.3038 | 1.6195 | 3.0378 | 0.20322 | 3 | 59765.7 | 56153.2 | 0.0015337 | 0.0014976 | 1 | 7097.025 | 8.1409e-05
MFD2A | BURPENGARY, CABOOLTURE SOUTH, MORAYFIELD | Urban | 782.43 | 6.7799 | 2.1685 | 4.0393 | 92.9391 | 0.0083113 | 6 | 1446543.9 | 70562.78 | 0.0017355 | 0.00093791 | 1 | 262.2 | 2.8668e-06
MFD3A | BURPENGARY, BURPENGARY EAST | Rural short | 949.5882 | 23.8335 | 0.9971 | 3.8868 | 74.3384 | 0.67889 | 7 | 1049624.12 | 254879.12 | 0.011032 | 0.0083244 | 4 | 7270.52 | 6.2416e-05
MFD5A | BURPENGARY, MORAYFIELD | Rural short | 516.5 | 11.5557 | 0.1847 | 1.5242 | 0.29485 | 0.16483 | 4 | 9997.98 | 9451.98 | 0.0016085 | 0.0015526 | 2 | 14067.13 | 0.00011648
MFD8A | BURPENGARY, MORAYFIELD | Rural short | 2124.1782 | 34.4419 | 3.8305 | 5.9827 | 4.1042 | 1.1358 | 2 | 142794.06 | 142794.06 | 0.0064037 | 0.0064037 | 8 | 36630.81 | 0.00036971
MFD9A | BURPENGARY | Urban | 907.494 | 7.5097 | 0.2849 | 2.2323 | 1.2134 | 0.18963 | 2 | 50851.55 | 10228.05 | 8.6066e-05 | 2.895e-05 | 3 | 11082.8287 | 3.3163e-05
MFN12A | CABOOLTURE, CABOOLTURE SOUTH, MELDALE, MORAYFIELD | Rural short | 1124.65 | 14.8196 | 4.4804 | 4.5346 | 61.2019 | 0.42332 | 7 | 945732.52 | 57653.86 | 0.0067489 | 0.0035762 | 4 | 8223.5 | 0.00011138
MFN13A | MORAYFIELD, UPPER CABOOLTURE | Rural short | 1657.9382 | 15.8884 | 4.0759 | 4.7442 | 19.5671 | 0.57827 | 6 | 477411.88 | 110180.38 | 0.0062567 | 0.0052381 | 5 | 8117.195 | 0.00013326
MFN15A | BEACHMERE, CABOOLTURE, NINGI | Rural short | 766.8421 | 15.9281 | 2.8713 | 2.6688 | 10.6228 | 7.7594 | 8 | 187225.23 | 47534.23 | 0.0035384 | 0.0032963 | 11 | 57990.2 | 0.00047102
MFN1B | CABOOLTURE, CABOOLTURE SOUTH, MORAYFIELD | Urban | 441.125 | 3.486 | 1.6026 | 2.6674 | 0.70616 | 0 | 1 | 15813 | 15813 | 0.00033415 | 0.00033415 | 0 | 0 | 0
MFN2A | CABOOLTURE SOUTH, MORAYFIELD | Urban | 512.855 | 2.4425 | 1.9643 | 4.9157 | 10.0941 | 0 | 3 | 66284.58 | 66284.58 | 0.0010297 | 0.0010297 | 0 | 0 | 0
MFN2B | CABOOLTURE SOUTH, MORAYFIELD, UPPER CABOOLTURE | Rural short | 2317.4167 | 11.9976 | 5.0281 | 4.4775 | 13.2402 | 0 | 6 | 388274.8908 | 380587.2108 | 0.014428 | 0.014417 | 0 | 0 | 0
MFN3A | MORAYFIELD | Urban | 11 | 0 | 0.6549 | 3.4486
MFN3B | MORAYFIELD | Urban | 5 | 0 | 0.551 | 3.4677 | 0 | 3.0323 | 0 | 0 | 0 | 0 | 0 | 2 | 572.16 | 3.877e-06
MGL1A | PULLENVALE, UPPER BROOKFIELD | Rural short | 680 | 15.9791 | 8.1991 | 2.8961 | 30.236 | 0.34935 | 5 | 741567 | 22262 | 0.0010354 | 0.00061993 | 4 | 12292 | 0.00013596
MGL2A | ANSTEAD, BELLBOWRIE, MOGGILL, PINJARRA HILLS | Rural short | 975.1538 | 15.9334 | 6.4485 | 3.3152 | 22.1444 | 0.12305 | 9 | 607009.36 | 263605.26 | 0.0067186 | 0.0065009 | 3 | 10727.58 | 0.00017557
MGL5 | BELLBOWRIE, MOGGILL | Urban | 1445.2609 | 0.119 | 11.1055 | 4.7633 | 0.25279 | 0.48364 | 7 | 30496.5 | 30496.5 | 0.00022615 | 0.00022615 | 16 | 38398.01 | 0.00015621
MGL6B | PINJARRA HILLS | Rural short | 31 | 2.0132 | 0.846 | 0.32877
MGL8 | MOGGILL, PINJARRA HILLS, PULLENVALE | Urban | 370.0556 | 7.4012 | 1.5756 | 3.0866 | 207.8703 | 1.4487 | 3 | 2031727.5 | 3240 | 0.00075819 | 9.0532e-06 | 6 | 30010.08 | 0.00010479
MGL9 | ANSTEAD, MOGGILL, PULLENVALE | Rural short | 390.2308 | 12.5385 | 1.0065 | 1.2003 | 3.9449 | 0.94936 | 4 | 103718.5 | 103718.5 | 0.0023206 | 0.0023206 | 9 | 26915.995 | 0.00025688
MGP1 | MUDGEERABA | Rural short | 577.625 | 10.7199 | 1.0048 | 1.6468 | 0.22592 | 3.6466 | 1 | 2895 | 2895 | 0.0016873 | 0.0016873 | 7 | 76683.695 | 0.0007016
MGP12A | AUSTINVILLE, BONOGIN, MUDGEERABA | Rural short | 960.5909 | 17.2665 | 4.9273 | 2.108 | 54.7977 | 1.2682 | 4 | 1440464.76 | 43175.76 | 0.003815 | 0.0020185 | 7 | 41252.78 | 0.00042781
MGP13A | AUSTINVILLE, MUDGEERABA, NATURAL BRIDGE, NERANWOOD | Rural short | 996.3059 | 89.3089 | 4.2778 | 2.6362 | 353.8782 | 8.1455 | 26 | 7088031.2833 | 318883.2833 | 0.0074613 | 0.0038361 | 46 | 200037.465 | 0.0017421
MGP15A | GILSTON, MUDGEERABA, TALLAI | Rural short | 944.0625 | 15.802 | 0.4725 | 2.7818 | 14.5735 | 1.3932 | 1 | 400785.78 | 0 | 0.0027003 | 0 | 7 | 31579.24 | 0.00031158
MGP16A | MUDGEERABA | Urban | 894.7475 | 3.0269 | 0 | 1.5052 | 37.23 | 1.401 | 1 | 1593485 | 0 | 0.00062322 | 0 | 3 | 13189.375 | 7.6e-05
MGP17A | BONOGIN, MUDGEERABA, REEDY CREEK | Rural short | 1597 | 0.3448 | 12.8694 | 0.45727 | 0 | 0.78392 | 0 | 0 | 0 | 0 | 0 | 1 | 363.33 | 2.7276e-06
MGP2A | MUDGEERABA, TALLAI | Rural short | 757 | 5.6069 | 1.2593 | 1.7148
MGP4 | BONOGIN, MUDGEERABA | Rural short | 1444.6317 | 16.5892 | 4.3555 | 4.5346 | 3.3716 | 3.4501 | 6 | 45508.0658 | 45508.0658 | 0.0017902 | 0.0017902 | 12 | 107485.02 | 0.0014772
MHL12A | MANGO HILL, NORTH LAKES | Rural short | 2400.1167 | 0 | 27.4261 | 6.9925 | 0.34264 | 0.062156 | 3 | 7157.85 | 7157.85 | 7.5468e-05 | 7.5468e-05 | 2 | 1432.88 | 2.4048e-05
MHL13A | NORTH LAKES | Urban | 1631.5973 | 0 | 13.9707 | 5.9065 | 2.918 | 0.38751 | 1 | 98280.5 | 98280.5 | 0.0019941 | 0.0019941 | 10 | 16155.44 | 0.00020291
MHL1B | KIPPA-RING, MANGO HILL, ROTHWELL | Rural short | 1593.5967 | 14.4813 | 7.2138 | 4.3251 | 4.0694 | 0.35919 | 2 | 173223.9975 | 58341.7575 | 0.0029609 | 0.002613 | 1 | 1791.12 | 1.1704e-05
MHL22B | MANGO HILL, NORTH LAKES | Urban | 10 | 0 | 1.4354 | 2.5722
MHL25A | NORTH LAKES | Urban | 174.625 | 0 | 5.3767 | 3.4486 | 0 | 1.1709 | 0 | 0 | 0 | 0 | 0 | 4 | 7325.075 | 2.6022e-05
MHL2A | MANGO HILL | Urban | 1084.33 | 0.5734 | 7.527 | 3.3533 | 0.029554 | 0 | 1 | 611 | 611 | 6.5689e-06 | 6.5689e-06 | 0 | 0 | 0
MHL3A | MANGO HILL, NORTH LAKES | Urban | 2185.75 | 1.4128 | 11.0541 | 6.7257 | 0.44792 | 0.059721 | 1 | 97 | 97 | 1.0008e-06 | 1.0008e-06 | 5 | 1346.29 | 3.1781e-05
MHPWED5 | SOUTH BRISBANE | Urban | 111 | 0.0749 | 3.0205 | 2.0196 | 1.2082 | 0 | 1 | 13719 | 0 | 1.7187e-05 | 0 | 0 | 0 | 0
MLB11A | BUDERIM, MOUNTAIN CREEK | Urban | 1709 | 2.0557 | 10.564 | 4.1917 | 0 | 0.50804 | 0 | 0 | 0 | 0 | 0 | 1 | 664 | 8.0716e-06
MLB12A | BUDERIM | Rural short | 1601.1844 | 11.7859 | 5.5129 | 4.3337 | 122.4696 | 0.83633 | 5 | 3172805.8 | 130766.8 | 0.014005 | 0.0094349 | 4 | 29009.495 | 0.00048893
MLB13A | SIPPY DOWNS | Urban | 1488.5533 | 0 | 8.4242 | 2.9291 | 7.08 | 0.721 | 3 | 207162 | 207162 | 0.0016405 | 0.0016405 | 6 | 24111.26 | 9.1869e-05
MLB2A | SIPPY DOWNS | Urban | 1519 | 0 | 9.8821 | 3.3814 | 0.084291 | 0
MLB3A | BUDERIM, MOOLOOLABA, MOUNTAIN CREEK, SIPPY DOWNS | Rural short | 2839.3667 | 4.6159 | 17.1594 | 5.4414 | 154.8224 | 0.2768 | 7 | 4880935.66 | 237365.3 | 0.026146 | 0.018014 | 6 | 11986.94 | 0.00028153
MLB4A | BUDERIM | Urban | 1621.9175 | 3.6165 | 5.8526 | 4.2171 | 0.39202 | 0.46169 | 1 | 5022 | 5022 | 6.2366e-05 | 6.2366e-05 | 3 | 25893.97 | 9.2734e-05
MLB6A | BUDERIM, GLENVIEW, ILKLEY, PALMVIEW, SIPPY DOWNS, | Rural short | 789.6844 | 15.1416 | 9.0317 | 6.3447 | 67.1445 | 3.1763 | 5 | 517751.59 | 36183.33 | 0.003599 | 0.0013664 | 13 | 41464.01 | 0.00051684
MLB8A | BUDERIM, CHEVALLUM, FOREST GLEN, ILKLEY, MONS, SIP | Rural short | 538.1075 | 25.061 | 3.2429 | 3.6391 | 141.9167 | 0.86252 | 8 | 498865.6292 | 34579.6292 | 0.0029413 | 0.0024621 | 3 | 9145.62 | 0.00020799
MLS10A | FORTITUDE VALLEY | Urban | 12 | 0 | 0.4385 | 1.5624
MLS11A | NEW FARM | Urban | 1938.5 | 0.0562 | 5.9291 | 4.8966 | 0 | 0.18128 | 0 | 0 | 0 | 0 | 0 | 1 | 5916.24 | 1.8384e-05
MLS12B | FORTITUDE VALLEY, NEW FARM | Urban | 2048.6667 | 0 | 2.5003 | 3.0899 | 1.2368 | 0.019837 | 2 | 58186 | 58186 | 0.0024066 | 0.0024066 | 1 | 3053.7 | 8.1322e-06
MLS14A | FORTITUDE VALLEY | Urban | 360.4 | 0 | 1.0081 | 2.4388
MLS15A | EAST BRISBANE, NEW FARM | Urban | 1526.557 | 0 | 6.1872 | 2.2292 | 3.9037 | 0.40379 | 7 | 173480.39 | 173480.39 | 0.0020646 | 0.0020646 | 3 | 23040.8488 | 7.2929e-05
MLS26B | FORTITUDE VALLEY, NEW FARM, TENERIFFE | Urban | 1237.98 | 1.6036 | 1.5455 | 3.1247 | 0.92689 | 0 | 5 | 91171.3875 | 21480.6 | 0.00031837 | 0.00023787 | 0 | 0 | 0
MLS2A | BOWEN HILLS, FORTITUDE VALLEY | Urban | 306.5 | 0.256 | 2.8339 | 4.1577 | 6.4847 | 0 | 1 | 37917.6 | 0 | 0.00022818 | 0 | 0 | 0 | 0
MLS6A | BRISBANE, FORTITUDE VALLEY, SPRING HILL | Urban | 562 | 0 | 2.1014 | 2.4578 | 5.4221 | 0 | 1 | 43834 | 43834 | 0.00056114 | 0.00056114 | 0 | 0 | 0
MLS90B | FORTITUDE VALLEY | Urban | 58.67 | 0 | 1.3577 | 1.9815 | 2.4458 | 0 | 1 | 440 | 440 | 1.0066e-06 | 1.0066e-06 | 0 | 0 | 0
MLS9A | FORTITUDE VALLEY | Urban | 434.06 | 0 | 2.0023 | 2.4769 | 1.846 | 0 | 1 | 33856.9 | 33856.9 | 0.00043616 | 0.00043616 | 0 | 0 | 0
MLSMYV26 | FORTITUDE VALLEY | Urban | 28.4 | 0 | 0.4858 | 2.1721
MLT15A | MILTON | Urban | 267.4233 | 0.4671 | 1.2976 | 2.3816 | 1.7146 | 0.1665 | 2 | 3449.16 | 59.4 | 3.6797e-05 | 1.1024e-06 | 1 | 777.924 | 5.3266e-06
MLT15B | MILTON, PADDINGTON, RED HILL | Urban | 766.995 | 2.276 | 1.4988 | 3.1438 | 0.16886 | 1.0106 | 2 | 6690.132 | 6690.132 | 9.2473e-05 | 9.2473e-05 | 8 | 60871.5665 | 0.00019012
MLT19A | AUCHENFLOWER, MILTON | Urban | 1046.6975 | 1.1313 | 2.6693 | 2.8389 | 1.0112 | 0.047631 | 1 | 128392 | 0 | 0.000236 | 0 | 3 | 5703.4996 | 1.3222e-05
MLT21B | MILTON, PADDINGTON | Urban | 1482.121 | 4.3769 | 0.5341 | 3.7725 | 3.5523 | 0.11168 | 7 | 86536.8508 | 86536.8508 | 0.0016922 | 0.0016922 | 3 | 10196.5075 | 3.8062e-05
MLT24A | MILTON, PADDINGTON | Urban | 874.2225 | 2.8548 | 1.3553 | 2.7436 | 0.076442 | 0.92663 | 1 | 4929.6 | 4929.6 | 3.1322e-05 | 3.1322e-05 | 3 | 18294.58 | 6.8023e-05
MLT2B | KELVIN GROVE, RED HILL | Urban | 1232.2868 | 1.6294 | 4.1429 | 3.2581 | 1.6771 | 1.8963 | 5 | 65402.12 | 65402.12 | 0.0041796 | 0.0041796 | 13 | 106636.4806 | 0.00033606
MLT3A | BRISBANE, MILTON | Urban | 5 | 0 | 0.5165 | 2.2864
MLT3B | MILTON | Urban | 71.98 | 0 | 1.5246 | 3.1438 | 0 | 0.021438 | 0 | 0 | 0 | 0 | 0 | 1 | 480.7467 | 8.6663e-07
MLT40A | KELVIN GROVE | Urban | 4 | 0 | 3.1357 | 1.2766 | 0 | 5.3377 | 0 | 0 | 0 | 0 | 0 | 1 | 562 | 1.0022e-06
MLT41A | BRISBANE, MILTON | Urban | 3 | 0 | 0.5165 | 2.2708
MLT42A | BRISBANE, KELVIN GROVE, MILTON, PADDINGTON, RED HI | Urban | 669.648 | 1.0315 | 4.8226 | 3.4296 | 0.41265 | 0.94723 | 1 | 10738.72 | 10738.72 | 0.00067698 | 0.00067698 | 3 | 40980.87 | 0.00011646
MLT43A | KELVIN GROVE | Urban | 194 | 0 | 2.4755 | 1.2575
MLT5A | BRISBANE, MILTON | Urban | 98 | 0 | 0.8172 | 2.2483
MLT6A | KELVIN GROVE | Urban | 4 | 0 | 3.1202 | 1.6957 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MLT8B | KELVIN GROVE | Urban | 15.495 | 0 | 2.4771 | 2.0577 | 0 | 0.73147 | 0 | 0 | 0 | 0 | 0 | 2 | 860.5005 | 2.9832e-06
MLTWHP12 | AUCHENFLOWER, MILTON | Urban | 100 | 0 | 2.6241 | 1.8863
MLY1 | BELLTHORPE, BOOROOBIN, MALENY, REESVILLE, STANMORE | Rural short | 821.6176 | 72.9564 | 0.9133 | 1.7897 | 119.2073 | 8.9256 | 17 | 4070290.6 | 187785.71 | 0.012951 | 0.008264 | 37 | 237138.888 | 0.0021349
MLY3 | CONONDALE, CURRAMORE, ELAMAN CREEK, MALENY, REESVI | Rural short | 2047.9582 | 75.4764 | 2.079 | 4.5834 | 111.9483 | 9.6792 | 34 | 5265637.7033 | 561997.9133 | 0.038145 | 0.024726 | 54 | 458443.1419 | 0.0043006
MLY4 | MALENY, MONTVILLE, NORTH MALENY, WITTA | Rural short | 626.7303 | 31.0151 | 0.7234 | 1.3147 | 60.3948 | 3.1627 | 15 | 1948407 | 211125.77 | 0.012067 | 0.0066944 | 15 | 127189.965 | 0.0013161
MLY6 | BALD KNOB, BALMORAL RIDGE, DIAMOND VALLEY, EUDLO, | Rural short | 612.4233 | 36.5788 | 0.1144 | 1.666 | 16.3555 | 1.6574 | 14 | 599918.24 | 53077.66 | 0.013127 | 0.0070442 | 13 | 74784.37 | 0.00070839
MMC19B | BENOWA, BROADBEACH WATERS, BUNDALL | Urban | 1099.3873 | 4.9746 | 4.5964 | 3.9066 | 101.7157 | 1.5171 | 6 | 3024415.34 | 150307.11 | 0.002392 | 0.0011895 | 9 | 62282.6958 | 0.00020074
MMC20A | CLEAR ISLAND WATERS | Urban | 833.75 | 0.4982 | 3.9195 | 2.1339 | 0 | 0.081251 | 0 | 0 | 0 | 0 | 0 | 2 | 2352.88 | 2.8618e-05
MMC21A | CLEAR ISLAND WATERS, MERRIMAC | Rural short | 9 | 1.6438 | 3.5181 | 0.78118 | 0.017904 | 0
MMC22A | BENOWA, CARRARA | Urban | 1516.2143 | 2.3655 | 10.5979 | 5.5826 | 0.27582 | 1.3733 | 4 | 8434.8445 | 8434.8445 | 0.0001872 | 0.0001872 | 3 | 6615.03 | 2.6376e-05
MMC24A | CLEAR ISLAND WATERS, MERMAID WATERS, ROBINA | Urban | 1097.5 | 0.5332 | 8.927 | 2.9636 | 0.025285 | 1.0751 | 1 | 984.06 | 984.06 | 2.351e-05 | 2.351e-05 | 1 | 39304.98 | 7.7546e-05
MMC28A | BROADBEACH WATERS, CARRARA, CLEAR ISLAND WATERS, M | Urban | 819.6667 | 1.8912 | 6.191 | 2.8008 | 1.2205 | 1.424 | 2 | 46187.7 | 46187.7 | 0.00010009 | 0.00010009 | 1 | 997.5 | 2.5261e-06
MMC30A | BROADBEACH WATERS, MERMAID WATERS | Urban | 327.5 | 0.1209 | 3.4444 | 1.1432 | 0 | 0.25286 | 0 | 0 | 0 | 0 | 0 | 1 | 1639.375 | 1.3143e-05
MMC31A | MERMAID WATERS | Urban | 38 | 0 | 1.6908 | 2.9913
MMC32A | CLEAR ISLAND WATERS, MERRIMAC | Urban | 10.02 | 0.9778 | 4.8846 | 2.521 | 0.87258 | 0 | 1 | 219.84 | 219.84 | 9.1457e-06 | 9.1457e-06 | 0 | 0 | 0
MMC33A | BROADBEACH WATERS, BUNDALL | Urban | 1578.3947 | 3.6359 | 8.6663 | 5.3499 | 112.2547 | 2.6595 | 3 | 3988360.6 | 3673.6 | 0.00168 | 3.3091e-05 | 16 | 101882.575 | 0.00037383
MOREXMEA | VERADILLA | Rural short | 3 | 0 | 0.0183 |  | 0.041071 | 0
MRB2 | ESK, GLEN ESK, MOOMBRA, MURRUMBA, TOOGOOLAWAH, WIV | Rural short | 51.9556 | 34.8815 | 0.0736 | 0.15242 | 1.8229 | 0.36223 | 6 | 36409.4 | 19440 | 0.00091356 | 0.00076156 | 3 | 9239.236 | 7.1159e-05
MRD6 | SPRING HILL | Urban | 934.996 | 0 | 3.1774 |  | 0 | 0.92244 | 0 | 0 | 0 | 0 | 0 | 5 | 22336.611 | 7.0558e-05
MRE1 | MURARRIE | Urban | 306.1509 | 1.046 | 3.3089 | 3.3343 | 0.9012 | 2.9684 | 2 | 6686.96 | 6686.96 | 0.00034305 | 0.00034305 | 8 | 37719.1736 | 0.00011593
MRE2 | CANNON HILL, MURARRIE | Urban | 586.4509 | 5.3772 | 3.1458 | 4.7252 | 0 | 2.8011 | 0 | 0 | 0 | 0 | 0 | 11 | 35300.3093 | 0.00012033
MRE3 | CANNON HILL, MURARRIE, TINGALPA | Urban | 620.66 | 3.0891 | 1.1101 | 3.4867 | 0.1695 | 1.9793 | 2 | 4076.895 | 4076.895 | 3.6097e-05 | 3.6097e-05 | 18 | 48311.0566 | 0.00020811
MRE4A | MURARRIE | Urban | 16.56 | 0 | 2.4527 | 3.6391 | 0 | 0.10648 | 0 | 0 | 0 | 0 | 0 | 1 | 290.16 | 1.0424e-06
MRE5A | MURARRIE | Urban | 4 | 0 | 1.6083 | 3.239
MRE6A | MURARRIE | Urban | 3 | 0 | 1.6083 | 1.8383
MRE8 | MURARRIE, TINGALPA | Urban | 221.25 | 2.5866 | 1.8633 | 5.7159 | 2.1829 | 0.12137 | 3 | 14050 | 14050 | 0.00028962 | 0.00028962 | 4 | 4722.43 | 1.6932e-05
MRE9 | MURARRIE | Urban | 2 | 0 | 1.0494 | 1.5433
MRK1 | YEERONGPILLY | Urban | 41 | 0.4024 | 1.6368 | 0.6097 | 0.35491 | 0 | 1 | 492 | 492 | 4.1401e-05 | 4.1401e-05 | 0 | 0 | 0
MRK2 | MOOROOKA | Urban | 562.58 | 2.3246 | 0.1055 | 3.1628 | 2.5035 | 0 | 1 | 24753.52 | 24753.52 | 0.00056808 | 0.00056808 | 0 | 0 | 0
MRK3 | MOOROOKA, YEERONGPILLY, YERONGA | Urban | 1219.45 | 4.1235 | 1.7367 | 2.4197 | 68.3024 | 0.13764 | 6 | 2219417.31 | 125661.31 | 0.003909 | 0.0026919 | 4 | 10670.83 | 7.5956e-05
MRK5A | ANNERLEY, MOOROOKA, TARRAGINDI | Rural short | 1610.18 | 6.647 | 0.324 | 1.6935
MRK6 | MOOROOKA, TARRAGINDI, YEERONGPILLY, YERONGA | Urban | 1742.2273 | 4.458 | 0.6283 | 3.1368 | 116.7104 | 0.015829 | 9 | 5439277.39 | 208121.89 | 0.010713 | 0.00362 | 2 | 1618.96 | 6.8819e-06
MRK7A | MOOROOKA, YEERONGPILLY | Urban | 71.575 | 0.438 | 2.2989 | 3.944 | 19.4454 | 0 | 6 | 128842.74 | 15062.63 | 0.00019721 | 9.8865e-05 | 0 | 0 | 0
MRK8 | MOOROOKA, YEERONGPILLY | Urban | 165.5 | 1.1233 | 0.8015 | 1.2003 | 0.59192 | 0 | 2 | 3139.3 | 3139.3 | 0.00017181 | 0.00017181 | 0 | 0 | 0
MRK9 | MOOROOKA, TARRAGINDI | Urban | 1616.5736 | 5.7484 | 0.3017 | 3.4296 | 7.3765 | 0.85426 | 6 | 320606.1567 | 84386.1567 | 0.0022699 | 0.0022057 | 5 | 26607.9128 | 6.8702e-05
MST20B | BRISBANE, SPRING HILL | Urban | 411 | 0 | 2.0592 | 1.2003
MSV1 | CAFFEY, LEFT HAND BRANCH, MT SYLVIA, UPPER TENTHIL | Rural short | 136.4348 | 29.4981 | 0 | 0.53349 | 46.526 | 0.82867 | 11 | 853210.53 | 40159.53 | 0.002249 | 0.00063101 | 12 | 12626.55 | 0.00012546
MSV2 | BLACK DUCK CREEK, EAST HALDON, JUNCTION VIEW, LEFT | Rural short | 168.0555 | 49.3694 | 0 | 0.74307 | 86.1427 | 0.93012 | 9 | 1036746.34 | 1697 | 0.0019961 | 4.4619e-05 | 10 | 13214.4 | 0.00015517
MTB13A | TAMBORINE MOUNTAIN | Rural short | 1608.2645 | 21.4666 | 1.2716 | 3.9979 | 174.4611 | 3.6842 | 15 | 6225698.98 | 267713.37 | 0.012266 | 0.0077364 | 14 | 58134.0738 | 0.00049677
MTB15A | BEECHMONT, BENOBBLE, BINNA BURRA, CANUNGRA, FERNY | Rural short | 770.3088 | 91.0261 | 2.5358 | 3.2137 | 122.847 | 7.8955 | 18 | 2142846.2 | 183604.7 | 0.0081988 | 0.0058696 | 16 | 129676.94 | 0.0013012
MTB16A | BENOBBLE, BOYLAND, WONGLEPONG | Rural short | 378.66 | 27.6282 | 2.3871 | 1.2194 | 81.8824 | 0.67137 | 4 | 1173784.39 | 12659.39 | 0.0022455 | 0.0011215 | 6 | 16695.08 | 0.00033999
MTB17A | GUANABA, MAUDSLAND, TAMBORINE MOUNTAIN | Rural short | 733.3851 | 29.8121 | 2.3826 | 1.9339 | 158.9984 | 10.4911 | 10 | 3467548.14 | 76974.64 | 0.007053 | 0.0021938 | 29 | 156934.912 | 0.0011043
MTB1B | TAMBORINE MOUNTAIN | Rural short | 1340.06 | 22.7467 | 0.5683 | 2.8558 | 191.2848 | 4.5559 | 17 | 6199702.28 | 167850.5 | 0.018612 | 0.010749 | 16 | 140550.47 | 0.0012078
MTB2A | BENOBBLE, BIDDADDABA, CANUNGRA, SARABAH, WONGLEPON | Rural short | 594.3545 | 32.5958 | 0.4449 | 1.81 | 4.4339 | 3.5003 | 5 | 65266.22 | 65266.22 | 0.0041411 | 0.0041411 | 5 | 42707.56 | 0.000404
MTB3A | CLAGIRABA, GUANABA, MAUDSLAND, MOUNT NATHAN, TAMBO | Rural short | 995.0853 | 32.8365 | 4.2777 | 3.0749 | 139.8087 | 1.2172 | 11 | 3342570.5033 | 178510.4833 | 0.013309 | 0.010272 | 8 | 45943.02 | 0.00038815
MTG11A | UPPER MT GRAVATT, WISHART | Urban | 1094.398 | 4.9156 | 0.3973 | 3.239 | 0.42164 | 2.9533 | 3 | 4439.98 | 4439.98 | 9.2215e-05 | 9.2215e-05 | 11 | 48525.2565 | 0.00020958
MTG12B | MT GRAVATT | Urban | 420.0686 | 1.8538 | 0.2392 | 1.5052 | 0.0036724 | 1.0699 | 1 | 137.6352 | 137.6352 | 2.3528e-06 | 2.3528e-06 | 5 | 20850.7518 | 8.1503e-05
MTG13A | UPPER MT GRAVATT, WISHART | Urban | 1828.9914 | 4.6924 | 4.1017 | 4.6379 | 0.27247 | 0.84428 | 3 | 5379.93 | 5027.43 | 8.2765e-05 | 6.8511e-05 | 11 | 33105.0832 | 0.00012291
MTG15A | MANSFIELD, WISHART | Urban | 705.3244 | 2.4572 | 2.4872 | 1.6743 | 8.259 | 0.028944 | 8 | 292020.7772 | 15979.2772 | 0.00031733 | 0.00018287 | 1 | 858.3048 | 3.145e-06
MTG16A | MT GRAVATT EAST | Urban | 674.2583 | 2.9497 | 0.2487 | 1.2701 | 0.9566 | 0.31256 | 4 | 72028.065 | 22779.855 | 0.0009612 | 0.0008242 | 2 | 11717.9651 | 3.7699e-05
MTG3A | MACGREGOR, MT GRAVATT, NATHAN, UPPER MT GRAVATT | Urban | 1155.0438 | 6.0333 | 2.6483 | 4.0798 | 61.6956 | 0.43861 | 3 | 1258926.41 | 226.38 | 0.0023345 | 4.6651e-06 | 5 | 16973.6642 | 6.228e-05
MTG4B | HOLLAND PARK WEST, MT GRAVATT, NATHAN, TARRAGINDI | Rural short | 2020.47 | 11.7579 | 1.7694 | 3.7526
MTG5A | MT GRAVATT EAST | Urban | 492.068 | 2.1024 | 0.5135 | 2.4769 | 6.3933 | 0.16764 | 2 | 267198.05 | 44475.55 | 0.0006014 | 0.00010801 | 3 | 6397.755 | 4.7309e-05
MTG7A | MANSFIELD, MT GRAVATT EAST, UPPER MT GRAVATT | Urban | 1647.1931 | 8.2125 | 1.8463 | 4.4584 | 17.5223 | 0.14528 | 8 | 478440.7056 | 112007.9256 | 0.0035862 | 0.0018719 | 5 | 6836.3452 | 3.6385e-05
MTG8A | MT GRAVATT, MT GRAVATT EAST | Urban | 858.945 | 3.441 | 0.625 | 2.4578 | 0.48301 | 1.3566 | 2 | 14998.84 | 7739.08 | 0.00020352 | 0.00010169 | 6 | 19917.0352 | 7.7332e-05
MTNQBI9 | PINKENBA | Urban | 11 | 3.0194 | 1.5106 | 4.0202 | 0.21045 | 0.0092701 | 1 | 825 | 825 | 1.1065e-05 | 1.1065e-05 | 1 | 206 | 1.0071e-06
MTNWLP5 | PINKENBA | Rural short | 91.99 | 3.4973 | 2.8383 | 1.6767 | 8.9852 | 0.95666 | 1 | 7124.25 | 7124.25 | 0.00027408 | 0.00027408 | 1 | 687.5 | 7.314e-06
MWMRBK11 | COLLINGWOOD PARK, MOGGILL, REDBANK, RIVERVIEW | Rural short | 1201.1375 | 13.7076 | 0.7062 | 4.7252 | 3.408 | 4.5332 | 2 | 63209.75 | 59709.75 | 0.0034873 | 0.003387 | 18 | 66798.62 | 0.00076707
NBR11A | DIDDILLIBAH, KIELS MOUNTAIN, NAMBOUR, ROSEMOUNT, W | Rural short | 1450 | 23.7316 | 1.5158 | 2.7818 | 0 | 0.80863 | 0 | 0 | 0 | 0 | 0 | 3 | 17056.75 | 0.00020535
NBR12A | BURNSIDE, DULONG, FLAXTON, HIGHWORTH, IMAGE FLAT, | Rural short | 1785.3 | 51.4962 | 5.0957 | 4.1536 | 0.0098084 | 1.5068 | 1 | 316.8 | 316.8 | 9.5538e-06 | 9.5538e-06 | 12 | 49571.79 | 0.00066398
NBR13A | BURNSIDE, NAMBOUR | Urban | 1465 | 7.5506 | 3.7948 | 4.5156 | 0.03516 | 0 | 1 | 456 | 456 | 4.0207e-06 | 4.0207e-06 | 0 | 0 | 0
NBR15A | IMAGE FLAT, KIAMBA, KULANGOOR, NAMBOUR, YANDINA | Rural short | 563.5833 | 25.7756 | 1.216 | 2.0958 | 0.09182 | 0.49051 | 1 | 960 | 960 | 4.3451e-05 | 4.3451e-05 | 2 | 11428.61 | 0.00012203
NBR16A | NAMBOUR | Urban | 354 | 1.673 | 0.747 | 1.2956
NBR17A | NAMBOUR | Urban | 72 | 0.9895 | 1.4211 | 2.7055
NBR2B | NAMBOUR | Urban | 576 | 4.0633 | 1.7294 | 3.7447 | 0 | 0.049267 | 0 | 0 | 0 | 0 | 0 | 1 | 382.95 | 1.8563e-06
NBR3B | NAMBOUR | Urban | 1327.5 | 6.1715 | 1.5768 | 3.4867
NBR4A | BLI BLI, IMAGE FLAT, MAROOCHY RIVER, NAMBOUR, NORT | Rural short | 826.5 | 43.6929 | 2.3291 | 2.7436 | 0.018042 | 0.056909 | 1 | 715.5 | 715.5 | 7.678e-05 | 7.678e-05 | 1 | 666 | 8.6908e-06
NBR5A | COOLOOLABIN, IMAGE FLAT, KIAMBA, NAMBOUR, YANDINA | Rural short | 1323.3333 | 31.1631 | 0.9668 | 2.8199 | 0.96355 | 0.42303 | 1 | 17512 | 17512 | 0.00057511 | 0.00057511 | 8 | 12345.18 | 0.00036252
NBR7A | BLI BLI, NAMBOUR, ROSEMOUNT | Rural short | 2110 | 49.2136 | 5.0586 | 4.9919 | 0.056211 | 1.8865 | 1 | 1309 | 1309 | 4.9264e-05 | 4.9264e-05 | 6 | 56437.17 | 0.00061484
NBR8A | NAMBOUR | Urban | 11 | 0 | 1.7783 | 3.2962
NDH1 | NORTHGATE, NUNDAH, VIRGINIA, WAVELL HEIGHTS | Urban | 1107.4933 | 2.2349 | 0.3741 | 2.496 | 5.7084 | 0.58086 | 3 | 128675.06 | 128675.06 | 0.0022421 | 0.0022421 | 3 | 32800.8062 | 0.00012816
NDH10 | NORTHGATE, NUNDAH, VIRGINIA, WAVELL HEIGHTS | Urban | 754.125 | 3.2194 | 1.4191 | 1.9625 | 2.2582 | 0.018233 | 4 | 72849.46 | 72849.46 | 0.0004173 | 0.0004173 | 2 | 1215.975 | 5.758e-06
NDH12 | NUNDAH | Urban | 787.75 | 2.3289 | 1.6364 | 1.3718 | 0.1399 | 0.43959 | 2 | 10673.56 | 10673.56 | 0.00015805 | 0.00015805 | 2 | 4527.2 | 2.2671e-05
NDH5A | HENDRA, NORTHGATE, NUNDAH | Urban | 1997.9444 | 4.8935 | 0.8871 | 2.6674 | 4.1452 | 0.11898 | 2 | 185075.1 | 81795 | 0.00207 | 0.0020133 | 6 | 12608.87 | 4.8081e-05
NDH6 | NUNDAH, WAVELL HEIGHTS | Urban | 1816.5869 | 5.6288 | 0.2968 | 3.4105 | 0.57159 | 3.0953 | 2 | 31424.515 | 31424.515 | 0.001894 | 0.001894 | 24 | 160114.9018 | 0.00049511
NDH7 | NORTHGATE, NUNDAH, VIRGINIA | Urban | 1557.3845 | 4.5981 | 1.9127 | 3.2771 | 4.1985 | 7.788 | 5 | 401024.07 | 98247.75 | 0.0018549 | 0.0017054 | 17 | 69511.485 | 0.00024518
NDH9 | NUNDAH, WAVELL HEIGHTS | Urban | 1436.332 | 3.2635 | 2.1216 | 5.2968 | 90.5293 | 0.67969 | 6 | 1978759.43 | 348048.67 | 0.0040584 | 0.0024873 | 9 | 9016.4551 | 3.8385e-05
NGE12 | BANYO, NORTHGATE, NUDGEE | Urban | 1614.825 | 6.4908 | 3.1709 | 3.601 | 0.031617 | 0.16675 | 0 | 0 | 0 | 0 | 0 | 3 | 5674.05 | 1.6966e-05
NGE13 | BANYO, NORTHGATE | Urban | 228.11 | 2.473 | 1.9903 | 4.5537 | 0.14658 | 3.7515 | 0 | 0 | 0 | 0 | 0 | 8 | 4485.9178 | 2.9856e-05
NGE2A | NORTHGATE | Urban | 288.01 | 1.3764 | 1.3526 | 1.4671 | 0.062062 | 0.046532 | 0 | 0 | 0 | 0 | 0 | 1 | 1053.4 | 4.5993e-06
NGE2B | BANYO | Urban | 69 | 0 | 4.6407 | 4.0393 | 0.071275 | 0.15378 | 0 | 0 | 0 | 0 | 0 | 1 | 427.55 | 5.0855e-06
NGE4A | BANYO, NORTHGATE | Urban | 168 | 1.5103 | 2.7733 | 2.5722 | 9.1647 | 1.3286 | 3 | 21397 | 21397 | 0.00033912 | 0.00033912 | 3 | 4671.53 | 1.6308e-05
NGE4B | BANYO, NUDGEE, NUDGEE BEACH | Urban | 729.3308 | 7.8384 | 5.0532 | 3.7344 | 11.0701 | 0.56831 | 7 | 301991.54 | 76946 | 0.0015485 | 0.0014815 | 6 | 29743.5995 | 8.528e-05
NGI1B | DONNYBROOK, MELDALE, NINGI, TOORBUL | Rural short | 1286.0482 | 35.2627 | 1.0071 | 2.9532 | 90.198 | 1.2737 | 5 | 2661521.2567 | 1909.7567 | 0.0051039 | 0.00017149 | 6 | 18841.98 | 0.00030528
NGI2B | BEACHMERE, NINGI | Rural short | 1256.0714 | 16.2024 | 1.9636 | 2.7407 | 4.7987 | 1.1104 | 4 | 122221.8 | 122221.8 | 0.0056942 | 0.0056942 | 3 | 22269.54 | 0.0002362
NGI3A | BEACHMERE, CABOOLTURE, NINGI | Rural short | 385.75 | 32.0752 | 2.4316 | 3.22 | 0.58671 | 0.26436 | 4 | 10645.89 | 10645.89 | 0.00014535 | 0.00014535 | 3 | 7606 | 6.6252e-05
NIP10A | NORTH IPSWICH, WOODEND | Urban | 1.66 | 0 | 2.5297 | 3.3152
NIP1A | COALFALLS, SADLIERS CROSSING, WOODEND | Urban | 1239.323 | 5.458 | 0.3338 | 3.0294 | 11.8987 | 1.3763 | 6 | 383537.4001 | 220091.9701 | 0.0049139 | 0.0035598 | 13 | 52567.328 | 0.00023873
NIP2A | BRASSALL, NORTH IPSWICH | Urban | 949.5 | 7.7699 | 1.5024 | 2.6103 | 2.6909 | 0.099691 | 2 | 130520.5 | 130520.5 | 0.00097023 | 0.00097023 | 1 | 4362.94 | 1.924e-05
NIP3A | EAST IPSWICH, NORTH IPSWICH | Rural short | 533.3 | 4.0208 | 0.5964 | 1.2385
NIP4A | BRASSALL, CHUWAR, KHOLO, MUIRLEA, NORTH IPSWICH, P | Rural short | 1499.6636 | 31.7112 | 0.3971 | 3.5058 | 8.4157 | 0.42669 | 6 | 290377.97 | 290377.97 | 0.0090433 | 0.0090433 | 8 | 21267.85 | 0.0001998
NIP5A | CHUWAR, MOORES POCKET, NORTH IPSWICH, TIVOLI | Urban | 1229.1375 | 7.6789 | 0.4319 | 2.7519 | 26.4975 | 2.1586 | 2 | 1433436.98 | 2508.48 | 0.0012936 | 2.6387e-05 | 10 | 41364.3668 | 0.00013036
NIP5B | BRASSALL | Urban | 957.1667 | 5.2374 | 0.5598 | 3.4486 | 0.48996 | 0.10807 | 3 | 24862.3 | 24862.3 | 0.00019054 | 0.00019054 | 3 | 3580.49 | 2.9651e-05
NIP6A | NORTH IPSWICH | Urban | 255.5667 | 2.105 | 0.3187 | 1.3718 | 0.93864 | 0.023874 | 2 | 23474.38 | 10511.2 | 0.00051453 | 0.00025785 | 1 | 1105.065 | 2.4735e-05
NIP7A | NORTH IPSWICH | Urban | 31.02 | 0 | 2.2953 | 3.4105
NMC13A | JIMBOOMBA, NORTH MACLEAN | Rural short | 1000.6 | 9.4886 | 11.0658 | 3.239 | 8.1931 | 0.35372 | 1 | 161271 | 0 | 0.0028523 | 0 | 4 | 12526.96 | 0.00020219
NMC15A | CHAMBERS FLAT, GREENBANK, MUNRUBEN, NORTH MACLEAN, | Rural short | 277.415 | 18.9211 | 0.2076 | 1.9815 | 52.5731 | 0.1093 | 3 | 488368.82 | 7123 | 0.00083565 | 3.7284e-05 | 1 | 4607 | 4.9104e-05
NMC16A | GREENBANK, MUNRUBEN, PARK RIDGE, PARK RIDGE SOUTH | Rural short | 917.792 | 23.4234 | 1.5723 | 2.8961 | 3.8217 | 0.35381 | 4 | 101006.54 | 7313.46 | 0.0028255 | 0.00018001 | 1 | 6531 | 6.1286e-05
NMC1B | GREENBANK, NEW BEITH, NORTH MACLEAN | Rural short | 1313.9095 | 50.9396 | 8.7013 | 4.3441 | 272.4966 | 3.3925 | 9 | 4386531.95 | 274347.12 | 0.015399 | 0.007835 | 12 | 63490.58 | 0.0007263
NMC2A | GREENBANK, NEW BEITH | Rural short | 1395.3987 | 8.3361 | 17.648 | 5.2587 | 0.76207 | 0.43391 | 4 | 5925.8667 | 5925.8667 | 0.00022955 | 0.00022955 | 4 | 8249.02 | 0.00016901
NMC3A | GREENBANK, MUNRUBEN, PARK RIDGE, PARK RIDGE SOUTH | Rural short | 990.164 | 34.5989 | 2.1425 | 3.515 | 1.4677 | 0.73684 | 5 | 28094.9533 | 28094.9533 | 0.00082951 | 0.00082951 | 5 | 10822.95 | 0.00011583
NMC5A | GREENBANK, JIMBOOMBA, NORTH MACLEAN, SHAILER PARK, | Rural short | 721.1364 | 28.2731 | 0.2783 | 2.0006 | 55.0972 | 2.544 | 6 | 1648855.5 | 2741.5 | 0.0025808 | 0.00021825 | 5 | 73994.48 | 0.00055753
NMK10 | WINDSOR | Urban | 724.99 | 2.3905 | 2.8372 | 4.4965 | 0.89279 | 0.52652 | 1 | 7125 | 7125 | 2.5265e-05 | 2.5265e-05 | 3 | 20716.6688 | 6.5045e-05
NMK17A | GRANGE, LUTWYCHE, WILSTON, WINDSOR | Urban | 2404.7674 | 7.8787 | 0.1962 | 4.8496 | 0.3763 | 1.8412 | 6 | 21535.93 | 5527.93 | 0.0002284 | 6.0774e-05 | 25 | 120807.9487 | 0.00040087
NMK18 | ALDERLEY, GRANGE, NEWMARKET | Urban | 1275.9523 | 4.7987 | 0.631 | 3.22 | 11.1196 | 0.63778 | 3 | 389356.8566 | 73467.4166 | 0.0026818 | 0.0016828 | 9 | 49270.7544 | 0.00013874
NMK23A | ALDERLEY, GRANGE, NEWMARKET, STAFFORD | Urban | 1496.6543 | 6.2719 | 0.847 | 4.0393 | 7.3016 | 0.21974 | 7 | 195417.5528 | 87545.5028 | 0.0020467 | 0.002011 | 7 | 9129.9478 | 4.5612e-05
NMK26 | HERSTON, KELVIN GROVE | Urban | 757.9583 | 3.0062 | 2.6022 | 1.8482 | 97.512 | 5.8849 | 3 | 1642587.4 | 88257.9 | 0.00086333 | 0.0001051 | 9 | 108385.62 | 0.00036558
NMK5 | KELVIN GROVE, NEWMARKET, WILSTON | Urban | 1568.5525 | 4.7182 | 0.8324 | 3.5248 | 2.4313 | 1.4766 | 4 | 272390.15 | 5221.49 | 0.00021734 | 9.4908e-05 | 8 | 34851.006 | 0.000113
NMK7 | ALDERLEY, ASHGROVE, KELVIN GROVE, NEWMARKET | Urban | 1160.6154 | 4.4662 | 2.8585 | 3.5439 | 0.44238 | 0.1507 | 5 | 20392.63 | 20392.63 | 0.00026613 | 0.00026613 | 7 | 10010.405 | 3.5443e-05
NPD1 | JOYNER, KURWONGBAH, WHITESIDE | Rural short | 6 | 2.2649 | 0.1765 | 0.57447
NRA12A | NARANGBA | Urban | 70.19 | 2.4317 | 0.6173 | 1.4671 | 0.090071 | 0.54603 | 0 | 0 | 0 | 0 | 0 | 2 | 199 | 2.008e-06
NRA13A | DAKABIN, KALLANGUR, KURWONGBAH, NARANGBA | Rural short | 2033.8782 | 15.2327 | 5.6446 | 5.4111 | 82.007 | 3.1019 | 6 | 2090703.546 | 90661.046 | 0.018224 | 0.0067849 | 11 | 34140.258 | 0.00038143
NRA15A | BURPENGARY, NARANGBA | Rural short | 310.9 | 7.3762 | 1.9922 | 0.74307 | 0.09236 | 0.15206 | 3 | 1593.8 | 1593.8 | 9.1948e-05 | 9.1948e-05 | 1 | 4972.8 | 3.1937e-05
NRA16A | DAKABIN, KURWONGBAH, NARANGBA | Rural short | 276.25 | 17.5744 | 1.5169 | 0.94297 | 54.0478 | 0.49929 | 5 | 558070.5 | 11793.5 | 0.0016074 | 0.00079372 | 3 | 12417.9 | 0.00014228
NRA1A | KURWONGBAH, MOORINA, MORAYFIELD, NARANGBA | Rural short | 871.9056 | 45.5479 | 1.5184 | 3.0294 | 68.8183 | 0.4674 | 9 | 1395624.01 | 242896.51 | 0.010658 | 0.0078148 | 6 | 3458.02 | 4.9659e-05
NRA2A | NARANGBA | Urban | 54.79 | 1.8138 | 1.1175 | 3.1628 | 0 | 0.40463 | 0 | 0 | 0 | 0 | 0 | 1 | 482 | 1.0052e-06
NRA3B | NARANGBA | Rural short | 18 | 1.8952 | 1.2349 | 0.53349 | 0 | 0.75323 | 0 | 0 | 0 | 0 | 0 | 1 | 232 | 2.8689e-06
NRA5A | NARANGBA | Rural short | 1872.5133 | 10.884 | 10.448 | 4.7633 | 60.487 | 0.79705 | 4 | 1944584 | 3789 | 0.0046559 | 0.0001218 | 8 | 12396.1 | 0.00012154
NRG10 | NERANG | Urban | 1452.8889 | 6.95 | 3.9947 | 3.7711 | 9.6211 | 0.21259 | 6 | 357192 | 357192 | 0.0049024 | 0.0049024 | 3 | 13415.83 | 7.3245e-05
NRG12A | CARRARA, NERANG | Urban | 1321.63 | 1.7169 | 4.4627 | 3.1329 | 0.45012 | 0.031404 | 2 | 18162.54 | 18162.54 | 0.0013742 | 0.0013742 | 3 | 1455.96 | 1.4525e-05
NRG13A | CARRARA | Urban | 1449.99 | 1.4378 | 11.5496 | 4.0202 | 0.21676 | 0.38172 | 1 | 4346.97 | 4346.97 | 0.0014648 | 0.0014648 | 2 | 266.925 | 5.8238e-06
NRG14A | CARRARA, REEDY CREEK, WORONGARY | Rural short | 640.7022 | 12.1515 | 5.0219 | 3.8868 | 17.6558 | 0.62546 | 7 | 416771.525 | 52373.025 | 0.0048171 | 0.0038529 | 2 | 13726.08 | 0.00014484
NRG15A | HIGHLAND PARK, NERANG | Urban | 1388 | 0.2497 | 5.3682 | 3.7701 | 0.10878 | 0.84392 | 1 | 4161 | 4161 | 0.0014021 | 0.0014021 | 1 | 35324.07 | 6.0123e-05
NRG16A | ADVANCETOWN, BEECHMONT, CLAGIRABA, GILSTON, LOWER | Rural short | 1910.7887 | 34.1362 | 7.6941 | 4.7341 | 31.2856 | 6.5465 | 15 | 1113568.61 | 105724.11 | 0.01389 | 0.011318 | 15 | 200957.14 | 0.0016579
NRG17A | ASHMORE, MOLENDINAR, NERANG | Urban | 1410.6633 | 4.7003 | 3.5091 | 2.9151 | 0.21606 | 1.1936 | 2 | 4295 | 4295 | 0.0014405 | 0.0014405 | 1 | 34062.5 | 6.2768e-05
NRG20A | NERANG | Urban | 339 | 2.347 | 1.2471 | 3.0485
NRG21A | HIGHLAND PARK, WORONGARY | Urban | 727 | 0 | 6.2065 | 2.6484
NRG22A | NERANG | Urban | 1024.848 | 6.5068 | 4.9542 | 3.5563 | 0.044956 | 0.21437 | 0 | 0 | 0 | 0 | 0 | 5 | 25407.1 | 0.00012596
NRG2A | HIGHLAND PARK, WORONGARY | Urban | 1239.4 | 0 | 5.7863 | 3.2962 | 0.17312 | 0.3457 | 2 | 5615.4 | 5615.4 | 0.0013408 | 0.0013408 | 3 | 14820.38 | 8.155e-05
NRG4 | CARRARA, HIGHLAND PARK, NERANG | Urban | 1071 | 1.9856 | 7.4487 | 4.7442 | 0.1206 | 0 | 1 | 3213 | 3213 | 0.0010827 | 0.0010827 | 0 | 0 | 0
NRG5A | NERANG | Urban | 359.5 | 3.2739 | 0.37643 | 5.5635 | 0.21759 | 5.5597 | 1 | 1077 | 1077 | 0.00036291 | 0.00036291 | 3 | 1983 | 1.208e-05
NRG6 | CARRARA, NERANG, WORONGARY | Urban | 910.3889 | 4.7447 | 3.3875 | 3.6772 | 1.0996 | 0.28718 | 6 | 8868.32 | 8868.32 | 0.00099511 | 0.00099511 | 3 | 3305.6875 | 1.563e-05
NRG8B | NERANG | Urban | 268.75 | 1.4635 | 1.9263 | 2.9532 | 66.0978 | 0.0070821 | 3 | 699696 | 22270.5 | 0.00078344 | 0.000512 | 1 | 117.75 | 1.9824e-06
NRG9 | ADVANCETOWN, GILSTON, HIGHLAND PARK, NERANG | Rural short | 1955.2142 | 32.5693 | 8.1829 | 5.373 | 22.7171 | 3.2014 | 10 | 516548.35 | 516548.35 | 0.017448 | 0.017448 | 9 | 112695.1249 | 0.0013622
NSD1A | FORTITUDE VALLEY, NEWSTEAD, TENERIFFE | Urban | 666.5 | 1.2788 | 1.6613 | 4.3251 | 6.6855 | 0.32478 | 2 | 28826.82 | 0 | 2.7022e-05 | 0 | 1 | 12002.73 | 3.4539e-05
NSD29A | NEW FARM, NEWSTEAD | Urban | 698 | 0 | 4.7181 | 2.4197 | 0.16821 | 0 | 1 | 4599 | 4599 | 3.6715e-05 | 3.6715e-05 | 0 | 0 | 0
NSD2B | BOWEN HILLS | Rural short | 368 | 0.8696 | 2.4294 | 0.83834
NSD30B | BOWEN HILLS, HERSTON, WINDSOR | Rural short | 770 | 2.7467 | 1.2026 | 0.43822
NSD3A | BOWEN HILLS | Urban | 239 | 1.0076 | 2.5109 | 3.4105 | 0.76561 | 0.73223 | 1 | 2600 | 2600 | 1.2614e-05 | 1.2614e-05 | 1 | 720 | 4.5153e-06
NSD6B | NEWSTEAD, TENERIFFE | Urban | 1149 | 0 | 2.4339 | 4.0774 | 4.8273 | 0 | 1 | 88473 | 88473 | 0.0011568 | 0.0011568 | 0 | 0 | 0
NSD8A | FORTITUDE VALLEY, NEW FARM, NEWSTEAD, TENERIFFE | Urban | 1520.06 | 0.5683 | 4.7883 | 3.9249 | 0 | 0.14163 | 0 | 0 | 0 | 0 | 0 | 4 | 11129.68 | 4.091e-05
NSD9A | NEWSTEAD | Urban | 612.4033 | 0.3429 | 3.1546 | 2.0577 | 1.607 | 0.00015706 | 2 | 4179.406 | 1766.906 | 9.603e-06 | 3.2916e-06 | 1 | 363 | 3.328e-06
NSW16A | SLACKS CREEK, SPRINGWOOD | Urban | 777.04 | 3.5791 | 1.0688 | 3.3724 | 5.0766 | 0.062914 | 3 | 119019.39 | 119019.39 | 0.00087254 | 0.00087254 | 1 | 1560 | 4.8502e-06
NSW17 | DAISY HILL, SPRINGWOOD | Rural short | 1301 | 8.9047 | 1.9853 | 2.4286
NSW19 | UNDERWOOD | Urban | 77.5 | 0.8557 | 1.9951 | 4.9919
NSW22B | EIGHT MILE PLAINS, KURABY, UNDERWOOD | Urban | 1427.598 | 5.6989 | 6.4434 | 4.2298 | 8.809 | 0.010936 | 3 | 176230.67 | 176230.67 | 0.0014516 | 0.0014516 | 2 | 411.9964 | 5.6891e-06
NSW24 | ROCHEDALE SOUTH, SPRINGWOOD | Urban | 570.4 | 1.9138 | 1.2051 | 4.0393 | 0.15515 | 0 | 1 | 1708.2 | 1708.2 | 0.00057349 | 0.00057349 | 0 | 0 | 0
NSW25 | UNDERWOOD | Urban | 354.575 | 3.5756 | 0.5777 | 2.9913 | 0.066245 | 0.090514 | 1 | 1056 | 1056 | 0.00035453 | 0.00035453 | 1 | 4313.4 | 1.0966e-05
NSW26 | SLACKS CREEK, SPRINGWOOD | Urban | 1157.3725 | 6.0144 | 0.5572 | 3.0294 | 0.27287 | 0.072867 | 3 | 6604.5 | 6604.5 | 0.0012311 | 0.0012311 | 1 | 2918.28 | 1.7641e-05
NSW28 | PRIESTDALE, ROCHEDALE, ROCHEDALE SOUTH, SPRINGWOOD | Urban | 1057.2857 | 6.4628 | 2.9947 | 3.1596 | 5.5157 | 0.041363 | 5 | 312980.275 | 19820.275 | 0.0013655 | 0.0012593 | 2 | 2297.96 | 7.2554e-06
NSW31A | SLACKS CREEK, UNDERWOOD | Urban | 126 | 1.6105 | 0.3227 | 3.3915
NSW33A | UNDERWOOD, WOODRIDGE | Urban | 1174.79 | 5.2889 | 3.0602 | 5.5254 | 0.66283 | 0.40254 | 2 | 4545 | 4545 | 5.3238e-05 | 5.3238e-05 | 3 | 1894.27 | 1.3215e-05
NSW35A | SLACKS CREEK | Urban | 281.2 | 2.0832 | 0.207 | 3.4105 | 7.3553 | 0 | 5 | 59973.01 | 12058.01 | 0.00039733 | 0.00011357 | 0 | 0 | 0
NSW3A | KURABY, UNDERWOOD | Urban | 1886.2571 | 2.6375 | 8.3669 | 4.9843 | 59.1219 | 0.14114 | 1 | 2361957.4 | 0 | 0.0018877 | 0 | 6 | 5689.87 | 2.5859e-05
NSW5A | ROCHEDALE SOUTH, SPRINGWOOD | Urban | 1236.8111 | 7.2722 | 1.2217 | 3.31 | 0.36615 | 1.363 | 2 | 4852.56 | 4852.56 | 0.00015764 | 0.00015764 | 7 | 54759.215 | 0.00017551
NSW7A | SPRINGWOOD | Urban | 152 | 0.7009 | 0.6816 | 2.4007
NSW8A | ROCHEDALE, ROCHEDALE SOUTH, UNDERWOOD | Urban | 1797.3571 | 8.4592 | 1.137 | 5.0088 | 5.861 | 0.4312 | 5 | 210520.9 | 168076.9 | 0.0020154 | 0.0019608 | 2 | 10243.78 | 2.9968e-05
NVL10 | NOOSA HEADS, NOOSAVILLE | Urban | 566.856 | 1.4086 | 8.1183 | 4.2869 | 3.0747 | 0.16733 | 2 | 42041.985 | 42041.985 | 0.00057316 | 0.00057316 | 3 | 5843.124 | 6.0811e-05
NVL12 | NOOSA HEADS, NOOSAVILLE | Urban | 1184.25 | 3.8658 | 1.2365 |  | 0 | 0.082034 | 0 | 0 | 0 | 0 | 0 | 2 | 6624.9 | 2.5751e-05
NVL14A | NOOSA NORTH SHORE, NOOSAVILLE | Urban | 1730 | 2.9373 | 2.7157 | 2.9723
NVL15A | NOOSAVILLE | Urban | 237 | 0.5718 | 5.0899 | 0.77251
NVL16A | NOOSA HEADS | Urban | 329 | 0 | 7.5666 | 2.8505 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NVL19A | NOOSAVILLE | Urban | 724 | 2.0708 | 4.2171 | 3.4656 | 0.022072 | 0.068473 | 0 | 0 | 0 | 0 | 0 | 1 | 3421.88 | 1.1134e-05
NVL24A | NOOSA HEADS, SUNSHINE BEACH | Urban | 1336.5 | 5.2664 | 5.0058 | 2.8961
NVL26A | NOOSAVILLE | Urban | 572 | 0 | 3.3294 | 1.4861
NVL27A | NOOSA HEADS | Urban | 1069 | 1.8139 | 4.5275 | 3.1357 | 0 | 0.0016039 | 0 | 0 | 0 | 0 | 0 | 1 | 58.8 | 2.8145e-06
NVL28A | NOOSA HEADS, NOOSAVILLE | Urban | 1521 | 0.4754 | 4.3169 | 3.7005
NVL3 | NOOSA HEADS, NOOSAVILLE, SUNRISE BEACH, SUNSHINE B | Urban | 2232.5 | 4.6805 | 9.9613 | 4.8541
NVL5 | NOOSA HEADS, NOOSAVILLE | Rural short | 1221 | 5.45 | 3.4629 | 2.7462 | 5.9271 | 0.077969 | 1 | 234781.5 | 234781.5 | 0.0036263 | 0.0036263 | 4 | 3211.15 | 7.7717e-05
NVL6 | NOOSA HEADS, NOOSAVILLE | Urban | 580 | 2.1594 | 1.8166 | 3.4486 | 0.067853 | 0
NVL8B | NOOSAVILLE, TEWANTIN | Urban | 1662.2778 | 1.2352 | 2.5246 | 4.3441 | 7.8758 | 0.018747 | 6 | 543064.5 | 543064.5 | 0.0047135 | 0.0047135 | 3 | 1196.785 | 1.9161e-05
NVL9 | CASTAWAYS BEACH, MARCUS BEACH, NOOSA HEADS, PEREGI | Rural short | 1480.875 | 11.0032 | 3.9904 | 3.8291 | 0.31684 | 2.0121 | 2 | 408 | 408 | 0.00019473 | 0.00019473 | 10 | 23860.48 | 0.00027212
ORE2 | BROADBEACH | Urban | 132 | 0 | 0.4085
OXL10A | OXLEY | Urban | 122.7475 | 2.0907 | 1.5955 | 3.7154 | 86.327 | 0.33747 | 3 | 172773.72 | 0 | 0.00036696 | 0 | 1 | 2348.325 | 1.2477e-05
OXL11A | DURACK, INALA, OXLEY | Urban | 1485.16 | 3.7969 | 3.2125 | 4.4013 | 59.2261 | 0.40144 | 8 | 1734159.59 | 118827.83 | 0.0031918 | 0.0016449 | 4 | 55812.0255 | 0.00055968
OXL4A | OXLEY | Urban | 875.8333 | 4.0207 | 1.5249 | 1.791 | 22.8212 | 1.6816 | 4 | 714436 | 45156 | 0.0022093 | 0.00085965 | 8 | 37949.41 | 0.00011506
OXL5A | ARCHERFIELD, OXLEY, ROCKLEA | Urban | 52.76 | 2.2431 | 4.1059 | 3.3533 | 9.1494 | 0.6231 | 1 | 4980.4 | 4980.4 | 5.3417e-05 | 5.3417e-05 | 1 | 538 | 1.0092e-06
OXL8A | OXLEY, ROCKLEA | Urban | 82.5 | 2.387 | 1.2284 | 3.0866 | 101.0732 | 1.9304 | 1 | 97762.5 | 0 | 8.3406e-05 | 0 | 3 | 1851.25 | 1.0519e-05
OXL8B | CORINDA, OXLEY, SEVENTEEN MILE ROCKS | Urban | 1593.2275 | 7.7906 | 3.3056 | 3.809 | 70.6683 | 0.19984 | 4 | 2920696.38 | 11836.25 | 0.0018018 | 0.00010133 | 3 | 7923.1772 | 2.7217e-05
PBH1 | CURRUMBIN WATERS, ELANORA | Urban | 1417.5385 | 6.5771 | 5.7 | 3.8104 | 65.9535 | 1.5156 | 7 | 2663887.31 | 76267.31 | 0.0059057 | 0.0030469 | 6 | 68332.845 | 0.00019556
PBH2B | ELANORA, PALM BEACH | Urban | 2290.7 | 3.727 | 6.4236 | 4.8928 | 14.2165 | 0.62081 | 6 | 641724.53 | 261003.53 | 0.007264 | 0.0049455 | 4 | 48598.33 | 0.0001331
PBH3 | PALM BEACH | Urban | 1114.605 | 2.8755 | 0.6726 | 3.4296 | 12.1331 | 0.1641 | 7 | 416561.8 | 92876.58 | 0.00351 | 0.0023299 | 3 | 10739.8428 | 4.7395e-05
PBH4 | ELANORA, PALM BEACH | Urban | 1031.29 | 0.5306 | 4.408 | 2.4174 | 38.7417 | 0 | 5 | 1569535.51 | 106630.22 | 0.0041561 | 0.0020746 | 0 | 0 | 0
PBH6 | PALM BEACH | Urban | 2223.1896 | 5.1812 | 0.2993 | 4.2948 | 112.9598 | 0.50094 | 14 | 6834784.225 | 557789.665 | 0.01222 | 0.0054287 | 9 | 42069.8541 | 0.00016022
PBH7A | ELANORA | Urban | 45.5 | 0 | 1.1332
PBH8 | CURRUMBIN WATERS, ELANORA | Urban | 1466.3873 | 2.6339 | 3.6878 | 3.6179 | 54.804 | 2.0672 | 6 | 2433695.64 | 107723.99 | 0.0059601 | 0.0029931 | 5 | 106641.1592 | 0.00023687
PCH8 | CHERMSIDE | Urban | 4 | 0 | 0.3215
PDA3 | SPRINGFIELD LAKES | Urban | 17 | 0 | 2.0815
PDB13 | SPRINGFIELD CENTRAL, SPRINGFIELD LAKES | Urban | 1164.266 | 0 | 12.0544 |  | 0 | 0.15879 | 0 | 0 | 0 | 0 | 0 | 5 | 4206.02 | 2.5801e-05
PGN1B | DOONAN, PEREGIAN BEACH, WEYBA DOWNS | Rural short | 1620.0582 | 15.5659 | 1.135 | 3.3978 | 0.14921 | 3.1941 | 1 | 5059.68 | 5059.68 | 5.799e-05 | 5.799e-05 | 20 | 101018.3592 | 0.0012255
PGN2B | PEREGIAN SPRINGS | Rural short | 162 | 0.2554 | 6.0945 | 0.41917
PGN3A | PEREGIAN SPRINGS | Rural short | 423 | 0 | 2.7973 | 0.8955
PGN6A | PEREGIAN SPRINGS | Urban | 1250 | 0 | 9.8403 | 4.1726 | 0 | 0.93409 | 0 | 0 | 0 | 0 | 0 | 2 | 764 | 4.0191e-06
PGS3 | BROADBEACH, BROADBEACH WATERS | Urban | 403.8 | 0.024 | 1.8118 |  | 0.02015 | 0
PKW11A | SOUTHPORT | Urban | 7 | 0 | 1.9599 | 2.3054
PKW15A | SOUTHPORT | Urban | 9 | 0 | 1.306 | 0.87644
PKW4A | PARKWOOD, SOUTHPORT | Urban | 564 | 0 | 4.871 | 1.4861
PMBWED19 | SOUTH BRISBANE, WEST END | Urban | 249.4175 | 0 | 2.1575 | 3.5058 | 3.2026 | 1.4188 | 2 | 1405 | 1405 | 8.5388e-06 | 8.5388e-06 | 2 | 545 | 5.0425e-06
PMBWED4 | SOUTH BRISBANE | Urban | 48 | 0 | 1.189 | 1.4861
PMBWED7 | SOUTH BRISBANE | Urban | 154 | 0 | 2.1897 | 4.5537 | 0.0025356 | 0
PPE12B | STEIGLITZ | Rural short | 2.75 | 11.2201 | 1.1971 | 0.19434 | 0.6844 | 0 | 1 | 145.75 | 145.75 | 7.8442e-06 | 7.8442e-06 | 0 | 0 | 0
PPE13A | GILBERTON, NORWELL, ORMEAU, PIMPAMA, WOONGOOLBA | Rural short | 740.5353 | 29.0459 | 5.8366 | 1.9822 | 7.0838 | 2.6937 | 5 | 105865.535 | 105865.535 | 0.0042256 | 0.0042256 | 12 | 12300.19 | 0.00017294
PPE15A | PIMPAMA | Urban | 1.4 | 0 | 0.7602 | 0.55254 | 0.91866 | 0 | 1 | 74.2 | 74.2 | 1.4011e-06 | 1.4011e-06 | 0 | 0 | 0
PPE16A | JACOBS WELL, NORWELL, STEIGLITZ, WOONGOOLBA | Rural short | 368.8958 | 23.8954 | 2.1954 | 1.0494 | 6.4219 | 0.72086 | 8 | 202587 | 202587 | 0.0041676 | 0.0041676 | 4 | 12463.5 | 0.00012624
PPE2B | PIMPAMA | Urban | 0.4 | 0 | 0.6997 | 0.52471 | 0.61244 | 0 | 1 | 21.2 | 21.2 | 4.0031e-07 | 4.0031e-07 | 0 | 0 | 0
PPE3A | JACOBS WELL | Rural short | 731 | 5.5968 | 9.5548 | 2.2543 | 91.099 | 0.041479 | 2 | 2084065 | 39220 | 0.0041995 | 0.0021108 | 1 | 1815.36 | 2.1101e-05
PPE5A | COOMERA, PIMPAMA | Rural short | 1608.7692 | 4.2449 | 15.3875 | 5.3539 | 3.7613 | 0.84907 | 2 | 87869.5 | 87869.5 | 0.004718 | 0.004718 | 9 | 16899.62 | 0.00019471
PPE6A | COOMERA, PIMPAMA, UPPER COOMERA | Rural short | 578.3 | 14.9148 | 6.9081 | 1.7719 | 5.2656 | 0.95333 | 5 | 44756.1 | 44756.1 | 0.0015642 | 0.0015642 | 5 | 16342.52 | 0.0001104
PQSRGA85 | BRISBANE | CBD | 2 | 0 | 0.1444 |  | 0 | 0.11253 | 0 | 0 | 0 | 0 | 0 | 1 | 1059.38 | 0.00025238
PRG1 | PRINCE HENRY HEIGHTS, REDWOOD, WITHCOTT | Rural short | 432.992 | 22.0758 | 0.3892 | 1.3147 | 0.13057 | 0.11571 | 2 | 1526.6 | 1526.6 | 9.6919e-05 | 9.6919e-05 | 3 | 1552.94 | 1.6068e-05
PRG2A | BALLARD, BLANCHVIEW, BLUE MOUNTAIN HTS, HELIDON SP | Rural short | 927.2083 | 97.1566 | 2.3582 |  | 11.891 | 1.5992 | 16 | 146573.755 | 93218.315 | 0.0030929 | 0.0028571 | 7 | 18605.305 | 0.00028073
PRG2B | LOCKYER, MURPHYS CREEK, POSTMANS RIDGE, WITHCOTT | Rural short | 169.0046 | 30.8231 | 0.6866 | 3.1438 | 1.8453 | 0.09499 | 9 | 19143.5 | 19143.5 | 0.00055501 | 0.00055501 | 4 | 2503 | 3.1871e-05
PTR2 | MURARRIE | Urban | 2.42 | 0 | 0.5514 |  | 1.6569 | 0 | 1 | 179.08 | 179.08 | 2.4287e-06 | 2.4287e-06 | 0 | 0 | 0
PWC2 | CHEVALLUM, KIELS MOUNTAIN, PALMWOODS, WOOMBYE | Rural short | 1026.34 | 18.1228 | 2.0151 | 3.3152 | 34.933 | 0.87254 | 4 | 899650.04 | 6881.58 | 0.0033485 | 0.00043179 | 6 | 13912.29 | 0.00022599
PWC3 | DIAMOND VALLEY, EUDLO, LANDERS SHOOT, MOOLOOLAH VA | Rural short | 1297.7121 | 46.0001 | 4.2617 | 3.4105 | 23.9538 | 6.1228 | 13 | 838077.6175 | 94927.0975 | 0.0072869 | 0.0043836 | 19 | 168251.675 | 0.0016991
PWC4 | COES CREEK, DULONG, FLAXTON, HUNCHY, LANDERS SHOOT | Rural short | 1853.1868 | 87.3862 | 0.8683 | 4.6186 | 72.2637 | 4.8307 | 33 | 3233007.1367 | 280727.7667 | 0.013588 | 0.0068938 | 38 | 227902.1959 | 0.0022679
PWC5 | BURNSIDE, COES CREEK, HUNCHY, PALMWOODS, WEST WOOM | Rural short | 1918.7963 | 30.6719 | 2.998 | 4.7381 | 5.3358 | 0.7316 | 8 | 189464.304 | 121109.304 | 0.0034078 | 0.0033576 | 8 | 26350.04 | 0.00030833
PWC6 | CHEVALLUM, EUDLO, ILKLEY, PALMWOODS, TANAWHA | Rural short | 1546.1809 | 45.925 | 2.4702 | 3.9066 | 259.7937 | 5.3139 | 19 | 5118438.8917 | 124772.3917 | 0.010693 | 0.0055721 | 14 | 117061.525 | 0.0013352
QAP4 | FORTITUDE VALLEY | Urban | 13 | 0 | 0.8767 |  | 0.65614 | 0 | 1 | 533 | 533 | 1.3094e-05 | 1.3094e-05 | 0 | 0 | 0
QEN10 | MACGREGOR, ROBERTSON | Urban | 361.0938 | 0 | 1.7482 |  | 0.015457 | 0.6767 | 2 | 1880.74 | 1880.74 | 8.7207e-05 | 8.7207e-05 | 6 | 8912.64 | 3.3851e-05
QGP4 | SOUTH BRISBANE | Urban | 55 | 0 | 1.1897 |  | 0.42136 | 0.62935 | 1 | 1032 | 1032 | 1.2011e-05 | 1.2011e-05 | 1 | 2185.92 | 2.044e-05
QPT1 | MORNINGSIDE, MURARRIE | Urban | 5 | 0.8732 | 1.2532 | 1.2194
QPT21 | CANNON HILL, MURARRIE | Urban | 951.8083 | 1.914 | 2.4021 | 2.3054 | 2.1042 | 0.059165 | 4 | 71174.34 | 71174.34 | 0.0013567 | 0.0013567 | 2 | 918.4217 | 1.559e-05
QPT22A | MORNINGSIDE | Urban | 1142.375 | 1.9608 | 1.5274 | 2.5531 | 29.4248 | 1.9725 | 2 | 1034824.6535 | 7672.1535 | 0.0011818 | 4.1907e-05 | 5 | 85191.6486 | 0.00021447
QPT24A | CANNON HILL, MORNINGSIDE, MURARRIE | Urban | 482.655 | 0.9752 | 1.0874 | 0.68591 | 0.32703 | 0.0081533 | 1 | 3591 | 0 | 2.1231e-05 | 0 | 1 | 864.1633 | 6.0358e-06
QPT25B | CANNON HILL | Urban | 157.16 | 0.3348 | 2.9909 | 3.944 | 0 | 0.12313 | 0 | 0 | 0 | 0 | 0 | 3 | 2341.2 | 1.9848e-05
QPT5 | CANNON HILL, MORNINGSIDE | Urban | 1014.3333 | 4.0656 | 0.8906 | 3.8868 | 0.70905 | 1.2939 | 4 | 24834.86 | 24834.86 | 0.0013046 | 0.0013046 | 5 | 11962.625 | 4.8564e-05
QPT6 | MORNINGSIDE | Urban | 57 | 1.6835 | 0.797 | 2.496
RBA10A | ROBINA | Urban | 5 | 0 | 2.1935 | 3.2009
RBA12A | ROBINA | Urban | 4 | 0 | 1.4054 | 2.2864
RBA15A | ROBINA | Urban | 466 | 0 | 4.2142 | 2.9913
RBA1A | MUDGEERABA, REEDY CREEK, ROBINA, VARSITY LAKES | Rural short | 1555 | 6.9421 | 8.0827 | 3.7344
RBA33A | ROBINA | Urban | 17 | 0 | 1.6216 | 2.9723
RBA34A | ROBINA | Urban | 312 | 0 | 6.7117 | 3.1247 | 0.1069 | 0.069781 | 1 | 228.36 | 228.36 | 1.3296e-06 | 1.3296e-06 | 1 | 248 | 1.0108e-06
RBA35A | BONOGIN, MUDGEERABA, ROBINA | Urban | 581 | 3.5908 | 3.1515 | 3.239 | 0 | 0.0027933 | 0 | 0 | 0 | 0 | 0 | 1 | 68 | 4.044e-06
RBA37A | MERRIMAC, MUDGEERABA, ROBINA, WORONGARY | Urban | 1281.2167 | 8.3189 | 2.8232 | 3.3533 | 0.060673 | 0.68059 | 2 | 1502.16 | 1502.16 | 1.6238e-05 | 1.6238e-05 | 4 | 5354.45 | 2.4183e-05
RBA41A | ROBINA | Urban | 866.0067 | 0 | 5.0696 | 4.2298 | 0 | 0.066546 | 0 | 0 | 0 | 0 | 0 | 2 | 7934.4452 | 7.1304e-05
RBA42A | CLEAR ISLAND WATERS, MERRIMAC, ROBINA | Rural short | 420 | 0.1252 | 6.3677 | 1.5242 | 0 | 0.13308 | 0 | 0 | 0 | 0 | 0 | 1 | 91.5 | 4.3722e-06
RBA43A | GILSTON, MERRIMAC, TALLAI, WORONGARY | Rural short | 1024.3606 | 22.9371 | 2.1946 | 3.6391 | 7.4714 | 5.1547 | 5 | 143112.1966 | 143112.1966 | 0.00599 | 0.00599 | 12 | 82297.11 | 0.00070245
RBA49A | ROBINA | Urban | 4 | 0 | 1.6571 | 2.3816
RBA4A | ROBINA | Urban | 1195.915 | 0 | 4.5443 | 3.0658 | 0.079963 | 0.2041 | 2 | 3863.25 | 3863.25 | 3.2466e-05 | 3.2466e-05 | 2 | 4394.78 | 0.00014689
RBA6A | ROBINA | Urban | 3.5 | 0 | 0.8652 | 0.99574
RBA7A | ROBINA | Urban | 8 | 0 | 3.389 | 4.1155
RBA9A | ROBINA | Urban | 348.5 | 0 | 5.1277 | 1.8863
RBARHP14 | MERRIMAC, MUDGEERABA, ROBINA | Urban | 1558 | 1.1766 | 8.5014 | 3.6391 | 0.5789 | 0.013272 | 3 | 24859.2 | 24859.2 | 0.00015015 | 0.00015015 | 1 | 868.62 | 1.4168e-05
RBK11B | COLLINGWOOD PARK, GOODNA, REDBANK | Urban | 738.9167 | 6.6605 | 3.4094 | 2.8961 | 3.1057 | 0.91251 | 3 | 43535.15 | 43535.15 | 0.0008145 | 0.0008145 | 3 | 15142.28 | 4.6368e-05
RBK12A | GOODNA, REDBANK | Urban | 29.5033 | 4.7798 | 0.6124 | 1.7148 | 0 | 15.8993 | 0 | 0 | 0 | 0 | 0 | 2 | 25940.97 | 4.0957e-06
RBK9A | COLLINGWOOD PARK, REDBANK | Urban | 291.0625 | 2.1135 | 1.0211 | 4.8395 | 156.9401 | 0.71999 | 2 | 755070.76 | 755070.76 | 0.00032445 | 0.00032445 | 6 | 18219.555 | 5.4653e-05
RBW4 | ROCHEDALE | Urban | 3 | 0.4359 | 0.0078 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RBY10 | ALEXANDRA HILLS, CAPALABA, CLEVELAND, ORMISTON | Urban | 617.5 | 4.8851 | 0.787 | 2.2864 | 64.7231 | 0.30175 | 1 | 1626831.96 | 0 | 0.00062967 | 0 | 1 | 5459 | 0.00010367
RBY12 | ORMISTON, WELLINGTON POINT | Urban | 1595.296 | 7.8067 | 4.2642 | 4.3492 | 1.1209 | 0.020386 | 4 | 68428 | 6327 | 0.00026141 | 0.00014971 | 1 | 604.5 | 3.9418e-06
RBY13 | CLEVELAND | Urban | 941.3883 | 4.764 | 0.8687 | 2.496 | 0.62673 | 0.33636 | 3 | 41171.47 | 41171.47 | 0.0010054 | 0.0010054 | 3 | 11163.7344 | 4.3299e-05
RBY15 | ORMISTON | Urban | 1234.5122 | 3.778 | 2.1418 | 3.4832 | 5.0678 | 0.11387 | 3 | 248854.23 | 248854.23 | 0.0013026 | 0.0013026 | 6 | 8185.6508 | 4.0491e-05
RBY16 | CLEVELAND, ORMISTON | Urban | 337 | 0.5578 | 1.6778 | 2.9151 | 2.9264 | 0 | 2 | 48812.87 | 48812.87 | 0.00035746 | 0.00035746 | 0 | 0 | 0
RBY18 | CLEVELAND, ORMISTON | Urban | 343.5 | 3.4379 | 1.2237 | 1.8943
RBY2A | CLEVELAND | Urban | 756.0833 | 2.3174 | 2.5303 | 2.8961 | 0 | 0.76469 | 0 | 0 | 0 | 0 | 0 | 3 | 33438.5068 | 0.00017879
RBY3 | CLEVELAND | Urban | 1571.7 | 4.7145 | 5.2039 | 3.464 | 54.5101 | 0.053707 | 3 | 1674706.5 | 5822.5 | 0.0032396 | 6.8419e-05 | 2 | 1388.2736 | 5.9935e-06
RBY6 | ALEXANDRA HILLS, CLEVELAND, ORMISTON | Urban | 1364.45 | 6.6554 | 1.9967 | 3.8487 | 7.7188 | 0.17568 | 1 | 280967.31 | 0 | 0.0013722 | 0 | 2 | 1456.25 | 6.2781e-06
RBY7A | CLEVELAND | Urban | 446 | 2.4881 | 1.3357 | 2.3435 | 3.2696 | 0.098868 | 6 | 53433.62 | 53433.62 | 0.00017665 | 0.00017665 | 2 | 4761.8725 | 4.3119e-05
RBY9A | CLEVELAND, ORMISTON | Urban | 841.1667 | 0.2993 | 8.2221 | 3.0675 | 0.95011 | 0.034723 | 1 | 37440 | 37440 | 5.912e-05 | 5.912e-05 | 2 | 1624.77 | 7.429e-06
RCF10A | KIPPA-RING, REDCLIFFE | Urban | 636.04 | 3.7011 | 0.3134 | 3.9821 | 6.549 | 0.21755 | 3 | 190799.3 | 177938.1 | 0.001376 | 0.00072592 | 5 | 11372.51 | 4.1091e-05
RCF11A | REDCLIFFE | Urban | 6 | 0 | 0.5446 | 2.1149 | 0.21699 | 0 | 1 | 120 | 0 | 6.0659e-06 | 0 | 0 | 0 | 0
RCF12A | REDCLIFFE | Urban | 887.1133 | 0.8825 | 1.5687 | 3.3533 | 1.8596 | 0 | 3 | 39428.8 | 21762 | 0.0011735 | 0.00028044 | 0 | 0 | 0
RCF1A | MARGATE, REDCLIFFE, WOODY POINT | Urban | 1842.6908 | 4.1663 | 1.6287 | 3.0598 | 2.9261 | 0.40113 | 5 | 219882.5 | 178947.5 | 0.004187 | 0.0021938 | 7 | 20831.2741 | 6.9675e-05
RCF2A | KIPPA-RING, MARGATE, REDCLIFFE | Urban | 2066.9933 | 5.23 | 0.5338 | 4.1936 | 24.5071 | 0.41202 | 8 | 1154820.2894 | 744486.8494 | 0.012914 | 0.0086149 | 7 | 39616.575 | 0.00013156
RCF3A | REDCLIFFE | Urban | 367.1667 | 1.371 | 0.5235 | 0.78901 | 0.11914 | 0.024032 | 1 | 7390 | 0 | 0.00037356 | 0 | 2 | 3395.7 | 1.221e-05
RCF5A | REDCLIFFE | Urban | 591.125 | 2.1323 | 0.6475 | 2.1911 | 6.1079 | 0 | 4 | 325053.72 | 1129.92 | 0.00079369 | 1.0671e-05 | 0 | 0 | 0
RCF7A | REDCLIFFE | Urban | 427.134 | 1.395 | 1.6973 | 2.6293 | 31.758 | 0 | 4 | 189781 | 48452 | 0.00023591 | 0.00013785 | 0 | 0 | 0
RCF9A | MARGATE, REDCLIFFE | Urban | 1381.9088 | 3.1176 | 1.0509 | 2.521 | 42.7683 | 0.25218 | 5 | 1709294.21 | 32532.81 | 0.0043419 | 0.0015253 | 3 | 15487.42 | 5.7799e-05
RCN10A | EIGHT MILE PLAINS, RUNCORN, SUNNYBANK, SUNNYBANK H | Urban | 1505.7564 | 6.4281 | 2.6646 | 3.7711 | 159.2559 | 0.47647 | 4 | 4607020.86 | 3104 | 0.0045886 | 3.2113e-05 | 7 | 20689.5628 | 6.8745e-05
RCN11 | RUNCORN | Urban | 7 | 0.6683 | 0.27789 | 4.0419 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RCN2A | EIGHT MILE PLAINS, RUNCORN | Urban | 1632.647 | 2.4018 | 4.5991 | 4.0806 | 20.9533 | 1.0144 | 2 | 919560.33 | 5506.2 | 0.0016713 | 2.4104e-05 | 8 | 40642.4974 | 0.00014956
RCN3A | RUNCORN, SUNNYBANK HILLS | Urban | 1434.2036 | 0.347 | 6.769 | 3.3814 | 0.19208 | 0.67 | 3 | 8479.49 | 8479.49 | 0.0001134 | 0.0001134 | 11 | 34488.6646 | 0.00011597
RCN4A | KARAWATHA, KURABY, RUNCORN | Urban | 1467.1082 | 6.0393 | 3.7901 | 3.0598 | 5.3956 | 1.1638 | 2 | 146397.39 | 146397.39 | 0.0014692 | 0.0014692 | 9 | 10599.96 | 9.8798e-05
RCN6A | KURABY, RUNCORN, STRETTON | Urban | 2002.615 | 6.1163 | 7.6463 | 4.8541 | 0.31016 | 0.13417 | 1 | 1532.72 | 1532.72 | 1.2918e-05 | 1.2918e-05 | 3 | 6412.97 | 5.1012e-05
RCN8A | RUNCORN, SUNNYBANK, SUNNYBANK HILLS | Urban | 1238.58 | 2.2046 | 4.5714 | 3.22 | 0.7504 | 0.0031141 | 3 | 28163.25 | 28163.25 | 0.00011597 | 0.00011597 | 1 | 271.7 | 1.9187e-06
RCN9 | RUNCORN | Urban | 2 | 0.3333 | 0.1322 | 8.5548
RHG6 | GREENSLOPES | Urban | 815 | 2.0489 | 0.1036 |  | 0.46979 | 0.22077 | 2 | 49345.11 | 49345.11 | 0.00083753 | 0.00083753 | 2 | 698.84 | 2.4274e-06
RHP1 | ROBINA | Urban | 3 | 0 | 0.3032
RIP1 | FORTITUDE VALLEY | Urban | 13.5 | 0 | 1.872
RIS1 | RUSSELL ISLAND | Rural short | 705.6053 | 10.2098 | 0.4866 | 0.88524 | 16.5792 | 0.31173 | 5 | 443361 | 443361 | 0.0082743 | 0.0082743 | 14 | 10451.795 | 0.0010539
RIS2 | KARRAGARRA ISLAND, LAMB ISLAND, MACLEAY ISLAND, RU | Rural short | 2432 | 26.2146 | 4.186 | 3.6757
RIS4 | RUSSELL ISLAND | Rural short | 544.0345 | 17.347 | 1.0719 | 0.73128 | 98.9845 | 0.39144 | 8 | 2163151 | 227803 | 0.0049558 | 0.0034172 | 21 | 6558.68 | 0.00090829
RLA2 | MOOROOKA, SALISBURY | Urban | 274.925 | 3.9291 | 0.745 | 3.7344 | 4.4289 | 0.050062 | 1 | 13290.68 | 13290.68 | 0.00025785 | 0.00025785 | 1 | 3083.01 | 1.1203e-05
RLA4 | COOPERS PLAINS, SALISBURY | Urban | 473.75 | 3.03 | 1.8666 | 1.8672 | 1.8658 | 0 | 2 | 52534.5 | 52534.5 | 0.00095047 | 0.00095047 | 0 | 0 | 0
RLA5 | MOOROOKA, ROCKLEA | Urban | 2028.6643 | 7.0057 | 0.4261 | 3.963 | 170.9511 | 0.07825 | 4 | 6361871.32 | 116250.32 | 0.0041382 | 0.002095 | 3 | 3147.9931 | 1.7615e-05
RLA6 | ARCHERFIELD, ROCKLEA | Urban | 512.462 | 4.2218 | 3.53 | 3.8678 | 11.9618 | 0.041182 | 3 | 385228.32 | 30500.32 | 0.00063274 | 0.00054378 | 2 | 1900.6728 | 1.3357e-05
RLA7 | MOOROOKA, ROCKLEA, YEERONGPILLY | Urban | 160.328 | 1.2558 | 2.203 | 1.3909 | 3.7783 | 0.028218 | 4 | 17601.6 | 17601.6 | 0.00034058 | 0.00034058 | 1 | 794.367 | 5.9089e-06
RLA8 | MOOROOKA | Urban | 512.6029 | 2.1907 | 0.1772 | 2.9444 | 2.6884 | 0.12258 | 3 | 34763.72 | 18501.32 | 0.00035568 | 0.00035123 | 4 | 6019.7327 | 2.3721e-05
RLB11B | REDLAND BAY | Urban | 1914 | 5.0635 | 6.8722 | 4.9014 | 14.9022 | 0.10221 | 4 | 416486 | 416486 | 0.0039516 | 0.0039516 | 8 | 3001.65 | 3.5088e-05
RLB12B | MOUNT COTTON, VICTORIA POINT | Rural short | 138.25 | 8.0455 | 0 | 0.51443 | 0.058328 | 0.0033636 | 1 | 1567.5 | 1567.5 | 4.7259e-05 | 4.7259e-05 | 1 | 143.22 | 2.6874e-06
RLB13B | REDLAND BAY | Rural short | 1916.605 | 32.1215 | 6.8935 | 5.0186 | 174.5306 | 1.2147 | 12 | 5045261.55 | 125384.29 | 0.022193 | 0.0057725 | 16 | 14070.42 | 0.00022815
RLB15A | REDLAND BAY, VICTORIA POINT | Urban | 1201.5 | 6.8647 | 1.4033 | 2.6942 | 0.38715 | 0.82725 | 3 | 10605.5833 | 10605.5833 | 0.00023836 | 0.00023836 | 4 | 27985.84 | 0.00010513
RLB16A | CARBROOK, MOUNT COTTON, REDLAND BAY | Rural short | 156.721 | 29.1446 | 2.5279 | 1.2385 | 52.8247 | 12.6399 | 6 | 199962.22 | 41846.6 | 0.0013399 | 0.00094835 | 33 | 94449.402 | 0.00071594
RNAVPK7 | FORTITUDE VALLEY, HERSTON | Urban | 4.09 | 0 | 0.1362 | 0
RPN1 | COLLINGWOOD PARK | Urban | 939 | 1.7307 | 5.0513 | 2.9151 | 0.081204 | 0
RPN2A | BELLBIRD PARK, REDBANK PLAINS | Urban | 1315.93 | 5.9352 | 1.9365 | 4.2107 | 32.6967 | 0.085126 | 5 | 933327.57 | 138425.07 | 0.0053999 | 0.0014001 | 3 | 5339.955 | 3.8823e-05
RPN3A | BELLBIRD PARK, REDBANK PLAINS | Urban | 1907 | 9.3933 | 2.0535 | 6.7067 | 0.12977 | 0.58557 | 1 | 1615.68 | 1615.68 | 3.3914e-05 | 3.3914e-05 | 6 | 33319.99 | 0.00012798
RPN4A | REDBANK PLAINS, SWANBANK | Rural short | 1844.1336 | 16.2783 | 11.9499 | 3.6391 | 0.41248 | 1.2073 | 1 | 808 | 808 | 2.2883e-05 | 2.2883e-05 | 9 | 12621.6 | 0.00013294
RPN5A | BELLBIRD PARK, REDBANK PLAINS | Rural short | 1072.5 | 7.9095 | 0.9609 | 2.5386 | 0.16559 | 0.067845 | 1 | 6134.52 | 6134.52 | 0.00016096 | 0.00016096 | 1 | 3852.44 | 4.1031e-05
RPN6A | BELLBIRD PARK, COLLINGWOOD PARK, GOODNA, REDBANK, | Rural short | 2175.3455 | 14.4755 | 2.999 | 4.4008 | 32.8592 | 1.0249 | 8 | 1078031.0343 | 387574.1943 | 0.017431 | 0.011171 | 11 | 29114.945 | 0.00047228
RPN7A | BLACKSTONE, COLLINGWOOD PARK, NEW CHUM, REDBANK PL | Rural short | 14.6667 | 6.5712 | 0.1741 | 1.2766 | 0.77985 | 0.91348 | 1 | 1848 | 1848 | 4.3322e-05 | 4.3322e-05 | 2 | 2412 | 2.8873e-05
RPN8 | AUGUSTINE HEIGHTS, BELLBIRD PARK, REDBANK PLAINS | Rural short | 1909.3235 | 12.8437 | 9.0644 | 4.8014 | 4.7833 | 1.421 | 3 | 205024.5 | 180594 | 0.0057623 | 0.0055002 | 12 | 55525.7025 | 0.00057273
RST11A | IPSWICH | Urban | 76 | 0 | 2.2101 | 3.5058
RST15A | IPSWICH, WEST IPSWICH | Urban | 138.5 | 0 | 2.1796 | 3.3152 | 0 | 0.35725 | 0 | 0 | 0 | 0 | 0 | 1 | 1178.95 | 3.2456e-06
RST16A | IPSWICH | Urban | 666.7211 | 6.2443 | 1.2269 | 3.1438 | 6.6393 | 1.7857 | 4 | 121895.1 | 60339 | 0.0013569 | 0.00065714 | 5 | 7250.57 | 3.7656e-05
RST18A | IPSWICH | Urban | 92.8067 | 0 | 0.6023 | 1.8672 | 0.26588 | 0.96513 | 1 | 580.5 | 580.5 | 4.2949e-06 | 4.2949e-06 | 2 | 1766.5 | 6.805e-06
RST20A | COALFALLS, LEICHHARDT, SADLIERS CROSSING, WEST IPS | Urban | 1225.6 | 8.9732 | 1.2095 | 2.5461 | 0.2713 | 0.010375 | 4 | 14948.07 | 14948.07 | 0.000253 | 0.000253 | 1 | 498.96 | 3.8131e-06
RST2A | IPSWICH | Urban | 149 | 0.5867 | 0.5173 | 3.8106 | 1.0561 | 0.050227 | 3 | 8124.295 | 8124.295 | 4.7666e-05 | 4.7666e-05 | 1 | 1131.52 | 2.196e-05
RST4A | IPSWICH | Urban | 7 | 0 | 0.41803 | 2.4197 | 0.35696 | 0 | 1 | 39 | 39 | 1.006e-06 | 1.006e-06 | 0 | 0 | 0
RST5A | IPSWICH, WEST IPSWICH, WOODEND | Urban | 556.5243 | 1.7422 | 2.189 | 4.4775 | 7.8779 | 0.42497 | 4 | 208113.505 | 72602.65 | 0.00092078 | 0.00064595 | 3 | 21198.925 | 5.9543e-05
RST8A | IPSWICH, WEST IPSWICH | Urban | 293.3929 | 2.815 | 1.6492 | 1.5814 | 29.4526 | 0.93542 | 6 | 460599.075 | 11351.61 | 0.00085059 | 0.0003852 | 8 | 15065.3 | 4.8787e-05
RST9A | EAST IPSWICH, IPSWICH | Urban | 290.3217 | 1.4818 | 1.2655 | 2.0196 | 4.5352 | 0.38386 | 2 | 39260.16 | 39260.16 | 0.00038013 | 0.00038013 | 4 | 13187.6376 | 3.623e-05
RWD1 | ARATULA, CALVERT, COLEYVILLE, EBENEZER, LANEFIELD, | Rural short | 531.3367 | 192.7721 | 0.2441 | 1.3718 | 19.6263 | 2.9737 | 20 | 398527.84 | 28427.35 | 0.0021896 | 0.0016796 | 22 | 76190.99 | 0.00081316
RWD2 | ASHWELL, CALVERT, LANEFIELD, MOUNT WALKER, ROSEWOO | Rural short | 1261.8796 | 51.6349 | 1.3976 | 3.3533 | 0.17385 | 3.0628 | 10 | 7618.8833 | 7618.8833 | 0.00021904 | 0.00021904 | 15 | 66016.54 | 0.00074028
SABWTC6 | SPRING HILL | Urban | 2 | 0 | 0.4784
SARSHW7 | CORINDA, ROCKLEA, SHERWOOD | Urban | 219.01 | 2.5956 | 1.4004 | 2.4769 | 0.42939 | 0.62154 | 1 | 9491.22 | 9491.22 | 7.1411e-05 | 7.1411e-05 | 1 | 85 | 1.0062e-06
SARSHW9 | ROCKLEA, SHERWOOD | Urban | 417.33 | 2.5113 | 1.5437 | 3.5629 | 0 | 0.15041 | 0 | 0 | 0 | 0 | 0 | 2 | 5764.57 | 2.0925e-05
SBH11 | REDCLIFFE, SCARBOROUGH | Urban | 1771.8655 | 4.7239 | 0.638 | 2.7904 | 6.3688 | 0.30115 | 3 | 513581.64 | 21648 | 0.00039391 | 0.00016456 | 8 | 18986.2198 | 6.8863e-05
SBH13A | KIPPA-RING, REDCLIFFE | Urban | 518.725 | 2.5269 | 1.2669 |  | 0.27234 | 0.079425 | 1 | 2590.2 | 0 | 0.00052369 | 0 | 3 | 4847.99 | 2.325e-05
SBH4 | SCARBOROUGH | Urban | 1220.8733 | 4.7712 | 1.4162 | 3.0832 | 13.9632 | 0.78415 | 4 | 504247.33 | 193495.23 | 0.0025592 | 0.0013226 | 11 | 51119.01 | 0.00022114
SBH6 | SCARBOROUGH | Urban | 2084.2388 | 6.8106 | 1.0432 | 6.2239 | 21.1989 | 1.043 | 11 | 1143734.6943 | 473885.1143 | 0.0069572 | 0.0045871 | 15 | 71439.7768 | 0.00029629
SBH8 | KIPPA-RING, REDCLIFFE | Urban | 765.636 | 2.0197 | 1.6864 | 2.0958 | 45.2942 | 0.35951 | 1 | 1121042.2 | 0 | 0.00076226 | 0 | 4 | 19469.025 | 7.5647e-05
SBH9 | KIPPA-RING, SCARBOROUGH | Urban | 1178.8333 | 0 | 5.9829 | 3.2009 | 2.3489 | 0 | 3 | 154703.25 | 154703.25 | 0.0012147 | 0.0012147 | 0 | 0 | 0
SBK10A | NATHAN, ROBERTSON, SALISBURY | Rural short | 769 | 2.8273 | 2.356 | 1.5588 | 0.027928 | 0.052429 | 1 | 7606.83 | 7606.83 | 8.511e-05 | 8.511e-05 | 1 | 2015.52 | 2.3526e-05
SBK11 | COOPERS PLAINS, ROBERTSON, SUNNYBANK | Urban | 1370.1408 | 4.9639 | 2.5808 | 2.5851 | 1.1418 | 0.53712 | 5 | 58108.84 | 58108.84 | 0.0015324 | 0.0015324 | 8 | 21991.365 | 7.1638e-05
SBK12 | COOPERS PLAINS | Urban | 102.75 | 3.433 | 0.6892 | 3.5895 | 0 | 0.027303 | 0 | 0 | 0 | 0 | 0 | 1 | 139.36 | 4.3498e-06
SBK4 | MACGREGOR, ROBERTSON, SUNNYBANK | Urban | 564 | 1.2062 | 3.0341 | 3.3343 | 0.017391 | 0.00042355 | 0 | 0 | 0 | 0 | 0 | 1 | 50.37 | 7.3057e-07
SBK9 | EIGHT MILE PLAINS, MACGREGOR, ROBERTSON, SUNNYBANK | Urban | 1777.8646 | 8.7888 | 1.3899 | 4.3684 | 186.0338 | 0.72742 | 5 | 4405604.66 | 109043.44 | 0.0032897 | 0.0016716 | 6 | 13100.5275 | 4.6941e-05
SBY4 | NATHAN, SALISBURY | Urban | 509.6678 | 2.5491 | 1.2383 | 2.9475 | 3.9688 | 0.44578 | 5 | 152453.1095 | 152453.1095 | 0.00065104 | 0.00065104 | 4 | 16479.824 | 7.8364e-05
SBY6OLD | NATHAN, SALISBURY, TARRAGINDI | Urban | 502.36 | 2.64 | 2.0118 |  | 7.4325 | 0.011125
SBY8 | SALISBURY | Urban | 937 | 4.0713 | 0.634 | 2.2766 | 5.7229 | 0.4158 | 3 | 218788.19 | 218788.19 | 0.0019047 | 0.0019047 | 3 | 10062.5398 | 3.7057e-05
SCV4 | HOPE ISLAND | Urban | 388.6667 | 0 | 4.2777 |  | 0.054614 | 0.036774 | 2 | 1632 | 1632 | 0.00041279 | 0.00041279 | 1 | 1153.45 | 3.9335e-06
SCV5 | HOPE ISLAND | Urban | 178 | 0 | 2.1888 |  | 0.016666 | 0 | 1 | 534 | 534 | 0.00017814 | 0.00017814 | 0 | 0 | 0
SCV7 | COOMERA, HOPE ISLAND | Urban | 386 | 0 | 5.2456 |  | 0.18617 | 0 | 1 | 1158 | 1158 | 0.0003863 | 0.0003863 | 0 | 0 | 0
SDM1 | BRYDEN, CROSSDALE, MOUNT BYRON, SOMERSET DAM, TOOL | Rural short | 200 | 66.3242 | 0.03 | 0.40012 | 1.6299 | 0 | 5 | 11894 | 4294 | 0.00063445 | 0.00057692 | 0 | 0 | 0
SDS4 | SURFERS PARADISE | Urban | 138 | 0 | 0.4679
SDSSPD8 | SURFERS PARADISE | Urban | 29 | 0 | 0.549 | 1.6767
SFD10 | EVERTON PARK, STAFFORD HEIGHTS | Urban | 1344.4425 | 5.5313 | 1.4449 | 2.6293 | 89.7613 | 0.33169 | 4 | 4049894.58 | 295390.08 | 0.0054059 | 0.0026934 | 8 | 11764.035 | 4.1217e-05
SFD11 | STAFFORD, STAFFORD HEIGHTS | Urban | 601.76 | 1.3086 | 2.0946 | 5.0491 | 0 | 1.114 | 0 | 0 | 0 | 0 | 0 | 2 | 7269.4864 | 2.7632e-05
SFD2A | ASPLEY, BRIDGEMAN DOWNS, CHERMSIDE WEST, MCDOWALL, | Urban | 1746.8933 | 2.8791 | 10.7017 | 4.4203 | 0.10041 | 0.27329 | 2 | 2752.72 | 2752.72 | 2.5208e-05 | 2.5208e-05 | 4 | 5078.35 | 3.129e-05
SFD3 | EVERTON PARK, MCDOWALL, STAFFORD HEIGHTS | Urban | 1182.0594 | 3.862 | 4.5083 | 4.4203 | 4.8981 | 1.5028 | 4 | 116527.195 | 99947.17 | 0.0012844 | 0.0012699 | 12 | 69800.965 | 0.00018981
SFD4 | EVERTON PARK, STAFFORD | Urban | 1324.6877 | 6.0787 | 0.7536 | 2.4174 | 0.15703 | 0.36114 | 4 | 5506.82 | 5506.82 | 0.00029512 | 0.00029512 | 9 | 29171.133 | 0.00011179
SFD5 | CHERMSIDE WEST, MCDOWALL, STAFFORD HEIGHTS | Urban | 810 | 3.1488 | 1.857 | 2.2673 | 0.10791 | 0.0035913 | 1 | 15261.5 | 15261.5 | 0.00011775 | 0.00011775 | 1 | 314.16 | 1.1664e-06
SFD6B | STAFFORD, STAFFORD HEIGHTS | Urban | 699.235 | 2.8074 | 0.9822 | 2.7979 | 0.075486 | 0.15028 | 0 | 0 | 0 | 0 | 0 | 4 | 8075.23 | 2.5965e-05
SFD7A | ASPLEY, CHERMSIDE WEST, STAFFORD HEIGHTS | Urban | 1072.5511 | 3.8666 | 2.4647 | 2.282 | 59.6169 | 0.46889 | 6 | 2805617.614 | 11842.684 | 0.0012052 | 0.00013258 | 3 | 21969.825 | 6.2751e-05
SFD8 | MCDOWALL, STAFFORD HEIGHTS | Urban | 626.5 | 1.5096 | 2.9186 | 1.6005 | 0 | 0.070223 | 0 | 0 | 0 | 0 | 0 | 1 | 3243.6 | 1.2358e-05
SFD9 | CHERMSIDE, CHERMSIDE WEST, KEDRON, STAFFORD HEIGHT | Urban | 858.0243 | 3.9357 | 1.0526 | 1.7985 | 2.6188 | 0.48684 | 2 | 96074.1 | 96074.1 | 0.00093665 | 0.00093665 | 5 | 16865.56 | 7.4682e-05
SGT22A | BOONDALL, DEAGON | Urban | 1604.487 | 7.0385 | 2.3678 | 3.1819 | 0.65712 | 1.2448 | 4 | 30816.8 | 30816.8 | 0.00030942 | 0.00030942 | 23 | 60354 | 0.00026064
SGT24A | BRACKEN RIDGE, BRIGHTON | Urban | 1550.7083 | 5.601 | 2.7776 | 3.8106 | 2.2346 | 2.6521 | 2 | 108474.05 | 108474.05 | 0.0015762 | 0.0015762 | 22 | 98517.775 | 0.0004905
SGT26A | BOONDALL, TAIGUM | Rural short | 356 | 0.5511 | 3.285 | 0.69279
SGT3 | BRACKEN RIDGE, DEAGON, SANDGATE | Rural short | 256 | 2.6391 | 0.925 | 0.66686
SGT4 | DEAGON, SANDGATE | Urban | 1378.0612 | 5.5866 | 1.806 | 3.6582 | 45.9909 | 0.4543 | 2 | 1511436.63 | 0 | 0.0014444 | 0 | 14 | 26684.975 | 0.00013052
SGT5 | BRACKEN RIDGE | Urban | 1120.2 | 4.4812 | 2.0702 | 2.282 | 2.2995 | 2.038 | 1 | 55830 | 55830 | 0.0011314 | 0.0011314 | 14 | 81497.945 | 0.00035064
SGT6 | BRACKEN RIDGE | Urban | 1018.3333 | 1.3809 | 5.0735 | 2.2292 | 0 | 0.18703 | 0 | 0 | 0 | 0 | 0 | 3 | 7036.6 | 2.1556e-05
SGT7 | DEAGON, SANDGATE, SHORNCLIFFE | Urban | 1939.4486 | 8.3118 | 1.1696 | 3.8868 | 1.3543 | 8.0859 | 6 | 79614.54 | 23469 | 0.0022203 | 0.0021556 | 66 | 318917.4646 | 0.0010795
SGT9 | BOONDALL, TAIGUM, ZILLMERE | Urban | 1451.8325 | 3.6998 | 6.1124 | 4.9348 | 0.23618 | 0.34136 | 2 | 10815 | 10815 | 0.00023003 | 0.00023003 | 8 | 15479.1012 | 0.00013273
SHW10A | CHELMER, GRACEVILLE, SHERWOOD | Urban | 1204.348 | 7.3326 | 0.2237 | 3.233 | 0.6153 | 0.78105 | 3 | 16498.68 | 16498.68 | 0.0001959 | 0.0001959 | 7 | 30724.687 | 0.00012828
SHW12 | FIG TREE POCKET | Urban | 597.451 | 4.6689 | 3.1764 | 2.6293 | 20.8401 | 0.48681 | 3 | 654280.74 | 3667.62 | 0.00068011 | 7.5549e-05 | 7 | 26672.9893 | 0.00012706
SHW3 | CORINDA, SHERWOOD | Urban | 1310.73 | 6.9607 | 0.3386 | 3.5602 | 4.1843 | 1.7762 | 6 | 205194.78 | 9547.6 | 0.00033036 | 0.00016013 | 7 | 53872.31 | 0.00017879
SHW4 | FIG TREE POCKET, INDOOROOPILLY | Urban | 550.4894 | 4.6182 | 1.0399 | 1.9437 | 21.422 | 0.55265 | 10 | 967271.98 | 192188.53 | 0.0035858 | 0.0025696 | 6 | 24743.4 | 8.1253e-05
SHW5A | CHELMER, GRACEVILLE, SHERWOOD | Urban | 891.1767 | 6.3056 | 0.6637 | 3.0485 | 66.745 | 0 | 6 | 1760736.535 | 14809.075 | 0.001557 | 0.00012459 | 0 | 0 | 0
SHW6 | GRACEVILLE, SHERWOOD | Urban | 1224.8943 | 4.861 | 0.2548 | 3.1819 | 0.028356 | 0.94214 | 0 | 0 | 0 | 0 | 0 | 13 | 47399.3947 | 0.00016645
SHW81 | CORINDA, SHERWOOD | Urban | 1778.2333 | 4.2222 | 0.8268 | 4.2107 | 0 | 1.4103 | 0 | 0 | 0 | 0 | 0 | 6 | 69519.285 | 0.00023367
SIS1 | POINT LOOKOUT | Rural short | 1449.625 | 24.2457 | 3.0003 | 3.3343 | 26.4126 | 0.017244 | 7 | 1426062.5 | 365755.5 | 0.014265 | 0.0088584 | 1 | 1229.12 | 1.955e-05
SIS2 | AMITY, DUNWICH | Rural short | 1014.4375 | 39.8489 | 0.5604 | 2.6293 | 6.9025 | 2.0387 | 11 | 470522.62 | 143290.92 | 0.0056384 | 0.0042727 | 5 | 89823.96 | 0.0007283
SMF1B | BUNYA, CAMP MOUNTAIN, DRAPER, FERNY HILLS, MOUNT S | Rural short | 773.4142 | 18.8205 | 2.2826 | 3.2962 | 2.9232 | 1.177 | 7 | 106502.24 | 30608.24 | 0.0009292 | 0.00025732 | 5 | 24033.6 | 0.00021654
SMF2A | CASHMERE, CEDAR CREEK, CLEAR MOUNTAIN, CLOSEBURN, | Rural short | 1055.1035 | 56.5593 | 4.0966 | 2.9723 | 114.9808 | 4.4833 | 13 | 3177973.73 | 202595.24 | 0.012607 | 0.0099357 | 21 | 136107.5248 | 0.0019331
SMF3A | CEDAR CREEK, CLOSEBURN, HIGHVALE, MT GLORIOUS, SAM | Rural short | 769.25 | 26.5707 | 5.5505 | 2.2901 | 28.8257 | 4.3072 | 19 | 1329474.57 | 95065.34 | 0.0025324 | 0.0014868 | 13 | 167138.69 | 0.0016881
SMF5A | HIGHVALE, MOUNT NEBO, SAMFORD VALLEY, WIGHTS MOUNT | Rural short | 703.75 | 34.6684 | 0.9785 | 1.7705 | 14.8547 | 2.03 | 5 | 422864.505 | 6787.505 | 0.0029129 | 0.0009288 | 13 | 95790.7 | 0.00069979
SMF5B | HIGHVALE, SAMFORD VALLEY | Rural short | 477 | 3.7065 | 3.4638 | 1.7148 | 11.0371 | 0 | 1 | 286200 | 0 | 0.0013667 | 0 | 0 | 0 | 0
SMF6A | CAMP MOUNTAIN, ENOGGERA RESERVOIR, FERNY HILLS, HI | Rural short | 643.7111 | 44.9074 | 1.2844 | 1.9052 | 16.5404 | 5.5669 | 7 | 481811.56 | 1248.12 | 0.0019429 | 0.00012456 | 11 | 143441.42 | 0.00090465
SMR10A | SUMNER | Urban | 241.98 | 0.6185 | 3.9103 | 2.8008 | 0 | 0.77417 | 0 | 0 | 0 | 0 | 0 | 1 | 14870.79 | 5.512e-05
SMR10B | MIDDLE PARK, WESTLAKE | Urban | 1392 | 0 | 10.2168 | 3.8297
SMR12A | JAMBOREE HEIGHTS, MIDDLE PARK, MT OMMANEY, SUMNER | Urban | 1181.5567 | 0.8116 | 6.7949 | 3.5058 | 3.7106 | 0.63322 | 4 | 162581.89 | 162581.89 | 0.0014228 | 0.0014228 | 5 | 19804.96 | 9.8852e-05
SMR12B | DARRA | Urban | 91.125 | 0.9409 | 1.7635 | 2.9532 | 6.1 | 0.082118 | 1 | 12809.5 | 12809.5 | 8.9874e-05 | 8.9874e-05 | 1 | 294.84 | 7.0638e-06
SMR13B | MT OMMANEY, SINNAMON PARK | Urban | 564 | 0 | 5.2433 | 2.6484
SMR15A | DARRA, JAMBOREE HEIGHTS, RIVERHILLS, SUMNER | Urban | 1403.8333 | 0.4051 | 8.0055 | 3.3152 | 3.0663 | 0.17115 | 2 | 275243.05 | 111805 | 0.0028272 | 0.0014122 | 4 | 8908.72 | 5.0888e-05
SMR1A | MIDDLE PARK, WESTLAKE | Urban | 908.915 | 0.1045 | 7.3805 | 3.22 | 0.0041504 | 0.021693 | 1 | 877.25 | 877.25 | 8.0484e-06 | 8.0484e-06 | 1 | 2986.26 | 1.0569e-05
SMR3B | DARRA | Urban | 71 | 0.3614 | 2.422 | 3.0675
SMR4A | DARRA, SEVENTEEN MILE ROCKS, SINNAMON PARK | Urban | 1284 | 0.5854 | 8.5491 | 4.4013 | 0 | 0.22899 | 0 | 0 | 0 | 0 | 0 | 2 | 539.55 | 4.9783e-06
SMR6A | JAMBOREE HEIGHTS, MT OMMANEY | Urban | 90.5 | 0.7682 | 3.0867 | 2.9723 | 0.013263 | 0.052338 | 0 | 0 | 0 | 0 | 0 | 2 | 5622.14 | 2.4965e-05
SMR7A | MIDDLE PARK, RIVERHILLS, WESTLAKE | Urban | 1184.4614 | 0.0146 | 9.0784 | 2.9782 | 0.31033 | 0.29242 | 5 | 32156.385 | 32156.385 | 0.00026838 | 0.00026838 | 2 | 18997.5 | 9.8799e-05
SMR7B | DARRA, SUMNER | Urban | 196.335 | 0.7752 | 2.0845 | 2.7818 | 0 | 0.86258 | 0 | 0 | 0 | 0 | 0 | 2 | 10092.5355 | 3.8681e-05
SMR9A | DARRA, SEVENTEEN MILE ROCKS, SINNAMON PARK | Urban | 1062 | 4.2818 | 5.5675 | 3.5629 | 87.965 | 4.594 | 3 | 1110223.8 | 4140.8 | 0.0011228 | 4.9686e-05 | 1 | 13692 | 2.8187e-05
SPC2B | ADARE, ATKINSONS DAM, BUARABA, BUARABA CREEK, CHUR | Rural short | 478.2114 | 91.5182 | 4.0654 | 2.9342 | 29.8732 | 2.0224 | 14 | 125309.8375 | 125309.8375 | 0.0020304 | 0.0020304 | 6 | 15198.52 | 0.00011504
SPD11A | SURFERS PARADISE | Urban | 1837.7275 | 5.1055 | 1.0957 | 3.8106 | 3.3869 | 1.4883 | 2 | 311401 | 10686 | 0.0002768 | 0.00013831 | 6 | 112781.1915 | 0.00038144
SPD12B | SURFERS PARADISE | Urban | 567.9933 | 0.5667 | 1.1871 | 2.9723 | 0.73931 | 0.29338 | 3 | 29533.66 | 22867.66 | 0.00062486 | 0.00057381 | 3 | 16492.89 | 4.5832e-05
SPD19A | MAIN BEACH, SURFERS PARADISE | Urban | 173 | 0.0616 | 2.0034 | 2.877
SPD1A | SURFERS PARADISE | Urban | 19.9 | 0 | 0.8016 | 4.1345 | 0.27535 | 0 | 1 | 742.5 | 742.5 | 4.9628e-06 | 4.9628e-06 | 0 | 0 | 0
SPD21A | SURFERS PARADISE | Urban | 51 | 0 | 1.2784 | 3.2009 | 3.3156 | 0 | 1 | 4794 | 4794 | 5.115e-05 | 5.115e-05 | 0 | 0 | 0
SPD28A | SURFERS PARADISE | Urban | 6.6 | 0 | 0.4552 | 4.0202
SPD29A | SURFERS PARADISE | Urban | 1096.9383 | 0.1745 | 2.7964 | 4.4775 | 0.70362 | 0.2323 | 1 | 9984 | 9984 | 6.4678e-05 | 6.4678e-05 | 4 | 6450.465 | 0.00012439
SPD2B | SURFERS PARADISE | Urban | 906.115 | 0.1881 | 2.8428 | 3.6772 | 1.0634 | 0.49661 | 1 | 3304 | 0 | 4.0436e-06 | 0 | 3 | 1833.27 | 2.4442e-05
SPD3A | SURFERS PARADISE | Urban | 357 | 0 | 3.5294 | 2.0591 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPD4A | MAIN BEACH, SURFERS PARADISE | Urban | 590.305 | 0 | 3.0391 | 0.30485 | 0.43736 | 0.11378 | 1 | 7829.2302 | 7829.2302 | 7.2288e-05 | 7.2288e-05 | 3 | 6338.1 | 4.321e-05
SPD4B | SURFERS PARADISE | Urban | 282 | 0 | 2.195 | 2.6103
SPD5A | MAIN BEACH, SURFERS PARADISE | Urban | 852.6733 | 0 | 2.3533 | 2.6674 | 0 | 1.912 | 0 | 0 | 0 | 0 | 0 | 2 | 68833.8 | 0.00014866
SPD5B | SURFERS PARADISE | Urban | 289.36 | 0 | 1.7201 | 3.1247 | 0 | 0.012049 | 0 | 0 | 0 | 0 | 0 | 1 | 463.5 | 1.5517e-05
SPD6B | SURFERS PARADISE | Urban | 184 | 0 | 1.0259 | 2.5722
SPD7B | MAIN BEACH, SURFERS PARADISE | Urban | 524.192 | 0 | 3.3142 | 3.3343 | 0.0056317 | 0.285 | 1 | 286.9992 | 286.9992 | 2.7883e-06 | 2.7883e-06 | 4 | 7803.9528 | 3.6813e-05
SPE1 | BRENDALE | Urban | 204.16 | 2.3879 | 1.2268 | 2.9532 | 0.26893 | 0 | 1 | 408.32 | 408.32 | 0.00020616 | 0.00020616 | 0 | 0 | 0
SPE20A | BRENDALE, STRATHPINE | Urban | 692.25 | 3.2653 | 2.4857 | 5.6207 | 0.017583 | 0.85161 | 1 | 33 | 33 | 1.011e-06 | 1.011e-06 | 1 | 19205.92 | 4.9572e-05
SPE22A | BRENDALE | Urban | 293.5 | 2.9359 | 1.635 | 4.5537 | 0.16527 | 0 | 1 | 587 | 587 | 0.00029637 | 0.00029637 | 0 | 0 | 0
SPE24 | BRENDALE | Urban | 71 | 1.0432 | 0.3064 | 4.5537 | 21.0111 | 0 | 1 | 49302 | 49302 | 5.4581e-05 | 5.4581e-05 | 0 | 0 | 0
SPE5 | BRENDALE | Urban | 199.5 | 1.8929 | 2.0638 | 3.6201 | 0.35845 | 0 | 1 | 1381.25 | 1381.25 | 1.6411e-05 | 1.6411e-05 | 0 | 0 | 0
SPE9 | BRENDALE, STRATHPINE | Urban | 1057.01 | 5.5641 | 5.6006 | 3.3152 | 7.5139 | 0.35195 | 1 | 38567.76 | 38567.76 | 0.0010638 | 0.0010638 | 5 | 3347.72 | 1.5142e-05
SPEWSP29 | STRATHPINE | Urban | 28 | 1.9623 | 0.0225 | 1.067
SPF12B | SPRINGFIELD LAKES | Urban | 1974.7154 | 0 | 13.6217 | 5.3349 | 0 | 0.7358 | 0 | 0 | 0 | 0 | 0 | 13 | 34718.7105 | 0.00033956
SPF15A | AUGUSTINE HEIGHTS, BROOKWATER | Urban | 607 | 0 | 9.3062 | 3.239 | 0.090349 | 0.82413 | 1 | 2350.92 | 2350.92 | 1.7318e-05 | 1.7318e-05 | 3 | 1037.6 | 8.4711e-06
SPF17B | SPRINGFIELD | Urban | 1007.3667 | 0.7352 | 6.5409 | 3.7725 | 0.042361 | 0.33331 | 1 | 2861.285 | 2861.285 | 9.9623e-05 | 9.9623e-05 | 8 | 4344.3705 | 5.2572e-05
SPF1B | AUGUSTINE HEIGHTS, SPRINGFIELD | Rural short | 526.6 | 0 | 8.8237 | 2.0577 | 0.046616 | 0.37797 | 1 | 1325.25 | 1325.25 | 6.6771e-05 | 6.6771e-05 | 4 | 7291.18 | 9.867e-05
SPFSTC2 | BROOKWATER, SPRINGFIELD | Urban | 3 | 0.7584 | 0.6461 | 2.0196
SPO11A | LABRADOR, SOUTHPORT | Urban | 2046.1562 | 2.2323 | 3.2394 | 4.332 | 0 | 4.2378 | 0 | 0 | 0 | 0 | 0 | 8 | 152727.16 | 0.00043608
SPO12A | SOUTHPORT | Urban | 4 | 0 | 0.6047 | 3.0485
SPO16A | ASHMORE, SOUTHPORT | Urban | 888.5873 | 4.0157 | 4.2537 | 4.9157 | 5.7199 | 2.2329 | 7 | 181453.1633 | 109063.6633 | 0.0011407 | 0.0010694 | 7 | 103380.225 | 0.00030728
SPO31A | SOUTHPORT | Urban | 365.9433 | 2.1953 | 1.2666 | 4.1536 | 0.82736 | 0.32266 | 1 | 13476 | 0 | 1.2132e-05 | 0 | 2 | 3291.05 | 2.2784e-05
SPO32A | LABRADOR, SOUTHPORT | Urban | 1800.31 | 5.5039 | 2.0286 | 3.6564 | 0 | 0.68906 | 0 | 0 | 0 | 0 | 0 | 9 | 45697.0512 | 0.00014731
SPO33A | MAIN BEACH | Urban | 14 | 0 | 3.7807 | 4.1536
SPO3A | ASHMORE, SOUTHPORT | Urban | 1158.745 | 4.1842 | 1.9368 | 3.2771 | 0 | 0.42538 | 0 | 0 | 0 | 0 | 0 | 6 | 29617.0808 | 0.00010528
SPO40A | SOUTHPORT | Urban | 17 | 0 | 0.858 | 1.2385
SPO41A | LABRADOR, SOUTHPORT | Urban | 1902.9527 | 5.1362 | 1.6034 | 3.8106 | 0.19987 | 0.30425 | 1 | 7207.2 | 7207.2 | 0.00010504 | 0.00010504 | 10 | 25291.9134 | 0.00010189
SPO47A | SOUTHPORT | Urban | 1261.735 | 2.8589 | 1.4484 | 3.4867 | 0 | 0.38936 | 0 | 0 | 0 | 0 | 0 | 6 | 44170.0581 | 0.00012875
SPO49A | SOUTHPORT | Urban | 82.83 | 0 | 2.5782 | 3.5058 | 0 | 0.53033 | 0 | 0 | 0 | 0 | 0 | 1 | 268.1 | 3.8675e-06
SPO49B | MAIN BEACH | Urban | 923 | 0 | 4.5367 | 2.1911 | 0 | 0.0022949 | 0 | 0 | 0 | 0 | 0 | 1 | 227.583 | 1.7049e-06
SPO4A | SOUTHPORT | Urban | 29 | 0 | 1.2356 | 4.4013
SPO51A | SOUTHPORT | Urban | 1394.8883 | 4.8934 | 0.6476 | 2.9636 | 2.4585 | 2.9126 | 2 | 97137.325 | 97137.325 | 0.0013953 | 0.0013953 | 16 | 99314.54 | 0.00029833
SPO52A | SOUTHPORT | Urban | 64 | 0 | 1.6945 | 3.4105
SPO55A | SOUTHPORT | Urban | 617.5533 | 0.325 | 1.5651 | 2.877 | 0.031221 | 0.42902 | 1 | 1252.3005 | 1252.3005 | 2.8127e-05 | 2.8127e-05 | 2 | 3557.1 | 2.5195e-05
SPO5A | MAIN BEACH | Urban | 755.89 | 0 | 5.0781 | 3.3089 | 4.8131 | 3.5952 | 2 | 73524.24 | 73524.24 | 0.00068796 | 0.00068796 | 9 | 10124.0431 | 3.6448e-05
SPO60A | ASHMORE, SOUTHPORT | Urban | 1264.2357 | 5.1599 | 0.9469 | 3.2771 | 1.3392 | 0.49845 | 3 | 39755.935 | 28945.935 | 0.00020859 | 0.00011356 | 11 | 27378.415 | 0.00010568
SPO60B | SOUTHPORT | Urban | 73 | 0.6075 | 0.5389 | 1.6195
SPO61A | SOUTHPORT | Urban | 192.33 | 1.2566 | 0.8064 | 3.3152 | 4.2403 | 0.27984 | 1 | 33394 | 0 | 2.9822e-05 | 0 | 1 | 1657.6 | 6.4167e-06
SPO67B | SOUTHPORT | Urban | 1476.997 | 5.0482 | 1.8025 | 3.9451 | 23.8717 | 1.5241 | 2 | 776156.52 | 0 | 0.0015875 | 0 | 8 | 31135.874 | 0.00011758
SPO69A | SOUTHPORT | Urban | 1704.4913 | 1.6028 | 1.4997 | 3.4105 | 0.12848 | 0.17082 | 2 | 11876.7 | 11876.7 | 0.00010521 | 0.00010521 | 5 | 35863.26 | 0.00012941
SPO7A | SOUTHPORT | Urban | 537 | 0 | 2.2729 | 1.9244
SPO8A | SOUTHPORT | Urban | 736.624 | 2.8181 | 2.8215 | 4.8966 | 2.0792 | 1.0555 | 3 | 10506.19 | 10506.19 | 0.00083275 | 0.00083275 | 4 | 4839.13 | 2.0864e-05
SPO9A | MAIN BEACH | Urban | 97 | 0 | 6.5783 | 3.6582 | 0 | 0.0029324 | 0 | 0 | 0 | 0 | 0 | 1 | 61.38 | 1.9777e-06
SPOSSS15 | SOUTHPORT | Urban | 56.07 | 0 | 2.3679 | 4.0583 | 0 | 0.15147 | 0 | 0 | 0 | 0 | 0 | 2 | 1045.7658 | 1.0328e-05
SPOSSS35 | SOUTHPORT | Urban | 171.6667 | 0.174 | 1.4187 | 3.7535 | 0.046667 | 0.10761 | 0 | 0 | 0 | 0 | 0 | 3 | 1948.34 | 5.4039e-06
SRD14A | CARINA, CARINDALE | Urban | 1656.8514 | 3.5607 | 6.8891 | 4.1345 | 0.39097 | 0.88964 | 4 | 20429.4346 | 20429.4346 | 0.00029464 | 0.00029464 | 3 | 35659.92 | 0.00012139
SRD18A | CARINA, CARINDALE | Urban | 1032.41 | 2.0303 | 4.9274 | 3.239 | 0.053955 | 0.043191 | 1 | 298.623 | 298.623 | 1.9394e-06 | 1.9394e-06 | 1 | 1941.8 | 7.362e-06
SRD19A | CARINA HEIGHTS, CARINDALE | Urban | 1835.9769 | 3.0197 | 8.7838 | 4.4673 | 0.36864 | 0.92642 | 2 | 14368.025 | 14368.025 | 7.7025e-05 | 7.7025e-05 | 10 | 40601.445 | 0.00015828
SRD4A | CARINDALE | Urban | 733.5 | 1.4912 | 4.6135 | 2.6674 | 0.27728 | 0 | 2 | 3618.5 | 3618.5 | 4.1944e-05 | 4.1944e-05 | 0 | 0 | 0
SRD7A | CARINDALE | Urban | 5 | 0 | 2.1042 | 2.5912
SSSWHI2 | SOUTHPORT | Urban | 4 | 0 | 1.0797 |  | 0.65653 | 0 | 1 | 208 | 208 | 4.0394e-06 | 4.0394e-06 | 0 | 0 | 0
STC7 | CAMIRA, SPRINGFIELD, SPRINGFIELD CENTRAL, SPRINGFI | Urban | 1868.95 | 0.78798 | 12.9408 |  | 0 | 0.049167 | 0 | 0 | 0 | 0 | 0 | 4 | 3123.1345 | 4.2872e-05
STL1A | ST LUCIA | Urban | 1671.3043 | 3.2193 | 0.6548 | 2.4807 | 5.1619 | 0.066208 | 6 | 564573.54 | 89412.04 | 0.00072656 | 0.00019758 | 1 | 6072.6 | 1.7463e-05
STL2 | ST LUCIA | Urban | 859.245 | 1.8809 | 0.9748 | 2.1554 | 0 | 0.30697 | 0 | 0 | 0 | 0 | 0 | 5 | 35469.4739 | 0.00010581
STL3 | ST LUCIA | Urban | 168.25 | 1.1672 | 0.269 | 0.99076 | 1.0828 | 0.0013204 | 1 | 27270 | 27270 | 9.0954e-05 | 9.0954e-05 | 1 | 31.5 | 9.0466e-07
STL5 | ST LUCIA | Urban | 90 | 0 | 1.1917 | 1.3856
STT1B | GILBERTON, ORMEAU, STAPYLTON, WOONGOOLBA | Rural short | 87.2533 | 15.0146 | 0.5258 | 1.6632 | 16.2632 | 0 | 5 | 48530.56 | 2650.56 | 0.00034265 | 7.7624e-05 | 0 | 0 | 0
STT2B | STAPYLTON | Urban | 16 | 2.4338 | 2.5358 | 3.5058
STT3A | ALBERTON, STEIGLITZ, WOONGOOLBA | Rural short | 97.4925 | 20.6866 | 2.5742 | 2.7818 | 280.859 | 5.5539 | 3 | 219614.4568 | 912.7768 | 0.00017486 | 2.1598e-05 | 5 | 5864.88 | 0.00010999
STT5B | ORMEAU, STAPYLTON | Urban | 47.94 | 0.7162 | 1.4969 | 4.9919 | 0.13333 | 0
TAB1 | ALBION | Urban | 2 | 0 | 1.9207
TAB3 | ALBION | Urban | 148.5 | 0.8941 | 0.9467 |  | 6.9646 | 0 | 2 | 60892 | 28589.5 | 0.00029688 | 0.00014793 | 0 | 0 | 0
TBV1 | BOYLAND, MUNDOOLUN, TAMBORINE | Rural short | 42.9733 | 9.5405 | 0.2852 | 0.19053 | 7.4552 | 0.01597 | 5 | 68702.1 | 2742.1 | 0.00050009 | 0.00037833 | 1 | 41.58 | 2.848e-06
TBV2 | BEAUDESERT, BIRNAM, BOYLAND, MUNDOOLUN, TABRAGALBA | Rural short | 283.45 | 47.5652 | 0.3849 | 0.91455 | 1.8476 | 4.3981 | 3 | 12526 | 12526 | 0.0018048 | 0.0018048 | 7 | 67201.528 | 0.0005326
TBV3 | TAMBORINE | Rural short | 329.5455 | 19.986 | 0.0934 | 1.1241 | 73.7949 | 0.36242 | 9 | 1816958.75 | 133166.5 | 0.0061883 | 0.005055 | 2 | 9707.7 | 6.291e-05
TBV4 | TAMBORINE | Rural short | 530.248 | 42.8496 | 2.2295 | 1.6386 | 174.5364 | 2.4408 | 13 | 2605797.04 | 77706.85 | 0.0090126 | 0.0058433 | 6 | 78581.235 | 0.00069293
TCB1 | TIN CAN BAY, WALLU | Rural short | 1402.27 | 12.1513 | 1.0003 | 2.4947 | 14.4586 | 15.0049 | 4 | 709346.85 | 110989.13 | 0.011453 | 0.0074157 | 24 | 700065.4854 | 0.007951
TCB2 | INSKIP, RAINBOW BEACH | Rural short | 1234.0764 | 26.0375 | 2.2419 | 3.2771 | 7.5757 | 0.077234 | 7 | 370943.06 | 370943.06 | 0.010299 | 0.010299 | 4 | 5294.28 | 0.00010754
TCB3 | COOLOOLA COVE, RAINBOW BEACH, TIN CAN BAY | Rural short | 1374.5882 | 27.6358 | 1.3661 | 2.4007 | 11.5089 | 3.3059 | 2 | 313184.96 | 130944.96 | 0.0078366 | 0.00394 | 9 | 150110.715 | 0.0014323
TEX1 | IPSWICH | Urban | 26 | 0.0875 | 0
TEX2 | IPSWICH | Urban | 37 | 0 | 0.4012 |  | 0 | 0.032159 | 0 | 0 | 0 | 0 | 0 | 1 | 350.4 | 9.6464e-07
TGP2A | MANLY WEST, TINGALPA, WAKERLEY | Urban | 1261.0267 | 2.4266 | 2.8757 | 3.5058 | 0.68875 | 0.042588 | 1 | 22717.44 | 22717.44 | 0.0012745 | 0.0012745 | 2 | 932.24 | 1.4253e-05
TGP3A | TINGALPA | Urban | 588 | 1.3134 | 2.1068 | 1.7148 | 0.31515 | 0 | 1 | 9408 | 9408 | 0.00059379 | 0.00059379 | 0 | 0 | 0
TGP5B | HEMMANT, MANLY WEST, TINGALPA, WYNNUM WEST | Urban | 1535.9878 | 5.9833 | 5.1086 | 4.7252 | 17.3878 | 0.43666 | 7 | 489555.12 | 20950.23 | 0.004812 | 0.0017436 | 2 | 5922 | 1.796e-05
TGP6A | BELMONT, CARINDALE, TINGALPA | Urban | 2013.57 | 2.9358 | 7.465 | 4.8966 | 1.1612 | 0.10261 | 4 | 64454.02 | 64454.02 | 0.0021533 | 0.0021533 | 1 | 7983.36 | 2.7072e-05
TGP8A | TINGALPA | Urban | 829.175 | 3.0415 | 1.4738 | 3.4677 | 6.7937 | 0.79992 | 10 | 147449.94 | 116795.44 | 0.0029088 | 0.0020712 | 10 | 25614.165 | 0.00012785
TGP9A | BELMONT, GUMDALE, TINGALPA, WAKERLEY | Urban | 1182.5 | 7.2371 | 6.0852 | 7.4688
TGW1 | CABOONBAH, COAL CREEK, COOEEIMBARDI, CRESSBROOK, F | Rural short | 432.2115 | 127.083 | 0 | 0.9336 | 3.4626 | 5.4424 | 13 | 97855.015 | 97855.015 | 0.0034821 | 0.0034821 | 47 | 167567.5833 | 0.0015872
TGW2 | BIARRA, ESKDALE, IVORY CREEK, MOUNT BEPPO, OTTABA, | Rural short | 304.343 | 102.169 | 0.3099 | 0.80023 | 3.7526 | 5.6954 | 15 | 86884.54 | 86765.54 | 0.0024612 | 0.0024583 | 30 | 131087.7876 | 0.0011509
TGW3 | AVOCA, AVOCA VALE, BRAEMORE, COLINTON, EMU CREEK, | Rural short | 662.2009 | 236.462 | 0.3333 | 1.6386 | 3.5119 | 9.9448 | 19 | 65306.28 | 65306.28 | 0.0030167 | 0.0030167 | 50 | 258883.898 | 0.0026903
TGW4 | BIARRA, TOOGOOLAWAH | Rural short | 637.4286 | 21.7892 | 0.2144 | 1.429 | 2.2926 | 0.25799 | 4 | 87163.77 | 87163.77 | 0.0037268 | 0.0037268 | 3 | 1706.76 | 3.288e-05
THL1 | GATTON, LOWER TENTHILL, ROPELEY, WINWILL | Rural short | 237.53 | 32.1511 | 0.445 | 1.2064 | 9.7551 | 2.1447 | 17 | 111798.01 | 37602.67 | 0.004478 | 0.0018827 | 11 | 25770.54 | 0.00023633
THL2 | CAFFEY, INGOLDSBY, LOWER TENTHILL, ROPELEY, UPPER | Rural short | 193.2546 | 36.9261 | 0.17 | 1.1432 | 1.457 | 0.96432 | 4 | 24296.86 | 15073.77 | 0.001739 | 0.00058884 | 9 | 15822.65 | 0.00012981
THL3 | FORDSDALE, GRANTHAM, LOWER TENTHILL, MA MA CREEK, | Rural short | 442.7457 | 101.6909 | 0.1022 | 1.2575 | 4.6092 | 1.7048 | 14 | 115118.39 | 77295.54 | 0.0055805 | 0.0029082 | 46 | 32741.447 | 0.00046284
THL4 | BLENHEIM, GLEN CAIRN, LOWER TENTHILL, ROCKSIDE, RO | Rural short | 173.5 | 38.0495 | 0.067 | 1.1432 | 0 | 0.097698 | 0 | 0 | 0 | 0 | 0 | 2 | 2036.11 | 2.6156e-05
THP2 | TUGUN | Urban | 1.5 | 0 | 0.3854 |  | 14.6894 | 0 | 1 | 1780.5 | 0 | 1.5164e-06 | 0 | 0 | 0 | 0
TMH12A | SHAILER PARK, TANAH MERAH | Urban | 418.05 | 4.1624 | 0.7032 | 2.877 | 1.9297 | 0.58331 | 3 | 41865.21 | 41865.21 | 0.00090509 | 0.00090509 | 2 | 754 | 2.0179e-06
TMH13A | SHAILER PARK | Urban | 330 | 2.4238 | 1.51 | 2.3435 | 2.4078 | 0.39466 | 2 | 18028 | 18028 | 0.00066667 | 0.00066667 | 1 | 377 | 1.0089e-06
TMH15A | DAISY HILL, SHAILER PARK, SLACKS CREEK | Urban | 1711.6484 | 9.9313 | 0.4723 | 5.1959 | 30.0201 | 1.5145 | 10 | 1371597.55 | 490599.82 | 0.0088807 | 0.0071078 | 9 | 48662.7608 | 0.00017834
TMH16A | TANAH MERAH | Urban | 529.2011 | 3.3633 | 0.066 | 1.2701 | 9.5644 | 0.16115 | 7 | 429093.17 | 25444.28 | 0.0013547 | 0.00075995 | 2 | 6288.74 | 2.4004e-05
TMH1B | DAISY HILL, SLACKS CREEK, TANAH MERAH | Urban | 6 | 0 | 1.9848 | 1.067 | 0.16399 | 0 | 1 | 12 | 12 | 6.0582e-06 | 6.0582e-06 | 0 | 0 | 0
TMH2A | MEADOWBROOK, TANAH MERAH | Rural short | 451.626 | 3.1951 | 3.0864 | 1.429 | 0.24288 | 0.0081977 | 3 | 3567.235 | 3567.235 | 0.0014085 | 0.0014085 | 2 | 371.6 | 9.2364e-06
TMH3A | SHAILER PARK | Urban | 848.71 | 6.0482 | 1.35 | 2.4947 | 16.0523 | 0.14118 | 6 | 694177.42 | 114490.9 | 0.0027371 | 0.0018884 | 1 | 9057.6 | 3.7997e-05
TMH5A | SHAILER PARK | Urban | 1127.277 | 5.8272 | 2.0468 | 2.8389 | 1.3979 | 0.10025 | 7 | 76313.54 | 76313.54 | 0.0035559 | 0.0035559 | 2 | 7305.9 | 2.2801e-05
TPT1 | NINGI, SANDSTONE POINT | Urban | 1631.8333 | 1.7652 | 6.566 | 3.3485 | 0 | 0.43485 | 0 | 0 | 0 | 0 | 0 | 5 | 2780.32 | 1.7245e-05
TPT4 | GODWIN BEACH, NINGI | Rural short | 544.25 | 5.4592 | 3.8863 | 1.067 | 0.014187 | 0.055933 | 0 | 0 | 0 | 0 | 0 | 2 | 4155.36 | 0.00011829
TPT5 | GODWIN BEACH, NINGI | Rural short | 509.375 | 11.9356 | 0.1546 | 1.9434 | 7.0317 | 0 | 4 | 209085.5 | 13070 | 0.0016539 | 0.00020279 | 0 | 0 | 0
TRG10B | INDOOROOPILLY, ST LUCIA, TARINGA | Urban | 521.5909 | 3.3405 | 2.2352 | 2.2864 | 33.7946 | 0.022398 | 10 | 799281.45 | 113953.95 | 0.0026032 | 0.0014247 | 1 | 16.17 | 1.1079e-07
TRG2A | INDOOROOPILLY, TARINGA, TOOWONG | Urban | 2762.0814 | 5.3127 | 0.4129 | 4.7298 | 3.4678 | 2.8728 | 6 | 185488.515 | 66116.79 | 0.00094481 | 0.00088726 | 23 | 136941.0636 | 0.00050945
TRG3 | ST LUCIA, TARINGA | Urban | 753.714 | 4.0834 | 0.0907 | 2.0006 | 70.4066 | 0.96528 | 7 | 1393262.14 | 214638.52 | 0.0032617 | 0.0024922 | 3 | 2537.52 | 8.9572e-06
TRG5 | ST LUCIA, TARINGA | Urban | 1420.5425 | 2.8439 | 0.3544 | 2.465 | 0.72509 | 0.028604 | 5 | 32525.1062 | 32525.1062 | 0.0003341 | 0.0003341 | 3 | 1751.435 | 6.0339e-06
TRP1 | COOLANA, LOWOOD, MINDEN, PRENZLAU, TARAMPA | Rural short | 719.0731 | 50.7365 | 2.8981 | 1.6957 | 2.15 | 0.52041 | 7 | 80219.59 | 8663.24 | 0.002436 | 0.00029476 | 6 | 25300.74 | 0.00019635
TRP2 | CLARENDON, COOMINYA, LOWOOD, PATRICK ESTATE, RIFLE | Rural short | 739.8752 | 63.9691 | 1.0291 | 1.81 | 36.8895 | 6.3483 | 14 | 265906.6 | 118869.16 | 0.0032647 | 0.0029671 | 11 | 43130.205 | 0.00046803
TRP3 | BRIGHTVIEW, CLARENDON, LOWOOD, MT TARAMPA, RIFLE R | Rural short | 311.075 | 49.6663 | 0 | 1.3147 | 2.3356 | 2.2156 | 6 | 14736.78 | 13392.78 | 0.00023472 | 0.00022609 | 10 | 42572.7325 | 0.00034371
TRP4 | GLAMORGAN VALE, LOWOOD, TARAMPA | Rural short | 629.545 | 21.1114 | 2.1201 | 1.81 | 3.5897 | 0.3693 | 8 | 108270.4816 | 73188.7316 | 0.0016125 | 0.0012396 | 2 | 7674.8 | 6.0773e-05
TSN13A | ROCKLEA | Urban | 2.08 | 0.6906 | 1.1541 | 3.6963
TSN15A | GRACEVILLE, TENNYSON, YEERONGPILLY | Urban | 328.1025 | 2.3992 | 1.6378 | 2.5912 | 4.5106 | 0.85753 | 2 | 33403.725 | 33403.725 | 0.00035517 | 0.00035517 | 5 | 2083.8709 | 2.4494e-05
TSN5A | TENNYSON, YEERONGPILLY | Urban | 49.8267 | 0.8023 | 0.5836 | 2.8961 | 0 | 1.167 | 0 | 0 | 0 | 0 | 0 | 1 | 862.204 | 2.3341e-06
TSN7A | ROCKLEA | Urban | 10.72 | 1.0347 | 2.1844 | 4.6109 | 15.8288 | 0 | 1 | 5188.48 | 0 | 1.0838e-05 | 0 | 0 | 0 | 0
TTF81 | CORINDA, OXLEY | Urban | 511.7 | 2.9332 | 5.1759 | 3.1057 | 1.8122 | 0.14633 | 3 | 93699.3 | 93699.3 | 0.0010461 | 0.0010461 | 2 | 4884.48 | 2.0628e-05
TWG10 | TOOWONG | Urban | 797.0667 | 1.0643 | 2.5758 | 2.6293 | 0.20009 | 1.9583 | 1 | 5152 | 5152 | 0.00073955 | 0.00073955 | 2 | 3560.72 | 1.221e-05
TWG11 | AUCHENFLOWER, BARDON, TOOWONG | Urban | 1190.9371 | 7.358 | 1.2622 | 3.6372 | 0.1444 | 0.42681 | 1 | 3416 | 3416 | 0.0001233 | 0.0001233 | 13 | 24154.5617 | 0.00010596
TWG13A | INDOOROOPILLY, TARINGA, TOOWONG | Urban | 1043.3329 | 5.6652 | 0.6658 | 3.0104 | 5.4626 | 0.20364 | 5 | 276852.95 | 276852.95 | 0.0021961 | 0.0021961 | 2 | 12389.555 | 2.9748e-05
TWG13B | TOOWONG | Urban | 455.9967 | 0.3671 | 1.0016 | 2.0387 | 3.9105 | 0.32656 | 2 | 55400.09 | 55400.09 | 0.00091217 | 0.00091217 | 1 | 1990.7314 | 1.1772e-06
TWG14A | TOOWONG | Urban | 878.338 | 1.5209 | 1.0152 | 2.2673 | 0.01849 | 0.54807 | 1 | 1738.26 | 1738.26 | 9.6914e-05 | 9.6914e-05 | 4 | 26889.3128 | 7.8619e-05
TWG15A | TARINGA, TOOWONG | Urban | 632.8333 | 2.2114 | 0.1285 | 1.7148 | 21.351 | 0 | 3 | 940564.65 | 3270.15 | 0.00072239 | 8.4709e-05 | 0 | 0 | 0
TWG16 | BARDON, MT COOTTHA, TOOWONG | Urban | 422.095 | 8.6919 | 1.2004 | 2.8389 | 37.4034 | 0.02757 | 8 | 612897.23 | 85012.3 | 0.0024426 | 0.0016104 | 1 | 1868.64 | 8.2391e-06
TWG17 | AUCHENFLOWER, BARDON, PADDINGTON | Urban | 1846.9058 | 7.0425 | 4.5498 | 3.5617 | 58.7574 | 0.91401 | 7 | 3261986.3748 | 15692.7378 | 0.0052055 | 0.00023551 | 17 | 76340.7748 | 0.00029991
TWG18 | AUCHENFLOWER, TOOWONG | Urban | 1087.9159 | 3.5298 | 0.4421 | 3.1628 | 1.0677 | 0.49288 | 6 | 39971.411 | 6432 | 0.00026053 | 5.6502e-05 | 11 | 25722.544 | 0.00012231
TWG19 | TOOWONG | Urban | 735 | 1.3412 | 1.0919 | 4.306 | 3.5749 | 0.23467 | 4 | 591690.66 | 25205.4 | 0.00043216 | 0.00017661 | 2 | 15593.575 | 6.2812e-05
TWG21 | INDOOROOPILLY, TARINGA, TOOWONG | Urban | 925.83 | 3.369 | 0.3079 | 1.8667 | 37.3613 | 0.30481 | 4 | 1755644.27 | 67534.77 | 0.0037859 | 0.0028341 | 4 | 14474.5172 | 6.0412e-05
TWT11A | COOROIBAH, NOOSAVILLE, RINGTAIL CREEK, TEWANTIN | Rural short | 2045.0606 | 28.4933 | 4.8859 | 4.0557 | 5.3682 | 1.4213 | 12 | 124908.05 | 123701.05 | 0.0095336 | 0.0094935 | 4 | 8059.85 | 0.00012906
TWT12A | DOONAN, NOOSAVILLE, TINBEERWAH | Rural short | 1147.085 | 45.7208 | 4.0481 | 3.6917 | 124.5536 | 1.9011 | 10 | 3505252.71 | 157404.3 | 0.015059 | 0.0033901 | 10 | 43665.4 | 0.00054902
TWT13A | NOOSAVILLE, TEWANTIN | Urban | 2447.25 | 3.3846 | 14.2831 | 5.4492 | 0 | 0.0071701 | 0 | 0 | 0 | 0 | 0 | 2 | 322.625 | 5.9788e-06
TWT15A | DOONAN, NOOSAVILLE, VERRIERDALE, WEYBA DOWNS | Rural short | 620.75 | 22.9716 | 5.7575 | 1.5702 | 4.058 | 0.5764 | 4 | 101394.62 | 101394.62 | 0.0021993 | 0.0021993 | 2 | 11242.5 | 0.00015035
TWT2B | NOOSAVILLE | Urban | 9 | 0 | 2.1271 | 3.6582
TWT3A | NOOSAVILLE, TEWANTIN | Rural short | 1521.3489 | 10.6203 | 5.3822 | 4.4013 | 1.5436 | 0.46616 | 4 | 52233.1667 | 3151.1667 | 0.0001767 | 0.00014519 | 5 | 9375.67 | 0.00018264
TWT5B | NOOSA NORTH SHORE, NOOSAVILLE, TEWANTIN | Urban | 693 | 2.8464 | 3.0005 | 3.0104
TWT6B | COOROIBAH, NOOSA NORTH SHORE, RINGTAIL CREEK, TEEW | Rural short | 1505.9933 | 34.8256 | 13.7238 | 2.6103 | 43.6711 | 0.8583 | 2 | 679755.96 | 0 | 0.00081179 | 0 | 4 | 33929.35 | 0.00061672
UMG12A | UPPER MT GRAVATT, WISHART | Urban | 665.33 | 0.4244 | 3.7722 | 2.7246 | 0 | 0.60215 | 0 | 0 | 0 | 0 | 0 | 6 | 35813.5091 | 0.00012092
UMG15B | MACGREGOR, UPPER MT GRAVATT | Urban | 900.984 | 3.2853 | 3.5602 | 3.1819 | 0.26197 | 0.050692 | 2 | 12950.561 | 12950.561 | 6.3121e-05 | 6.3121e-05 | 2 | 1741.48 | 2.2611e-05
UMG1A | UPPER MT GRAVATT | Urban | 278.995 | 0.0929 | 1.7401 | 4.9729 | 0.11918 | 2.4648 | 0 | 0 | 0 | 0 | 0 | 2 | 40059.558 | 9.4058e-05
UMG1B | UPPER MT GRAVATT, WISHART | Urban | 2117.5636 | 5.7054 | 4.3397 | 5.2665 | 19.2071 | 0.61819 | 4 | 1087269.27 | 10665.27 | 0.00027666 | 5.6468e-05 | 10 | 43557.2658 | 0.00015468
UMG2B | COOPERS PLAINS, ROBERTSON, SALISBURY | Rural short | 1000 | 4.3377 | 4.8361 | 2.5264 | 3.5775 | 1.4898 | 3 | 79864.62 | 79864.62 | 0.0031663 | 0.0031663 | 8 | 30729.5261 | 0.00035342
UMG3A | UPPER MT GRAVATT | Urban | 386 | 1.3847 | 0.9057 | 2.3816 | 3.0428 | 0 | 1 | 32573.5 | 32573.5 | 0.00038708 | 0.00038708 | 0 | 0 | 0
UPC1 | CEDAR CREEK, OXENFORD, TAMBORINE MOUNTAIN, UPPER C | Rural short | 536.4348 | 45.4495 | 5.7892 |  | 156.2549 | 9.1412 | 6 | 2561348 | 79627 | 0.00398 | 0.0022609 | 16 | 107368.155 | 0.0007743
UPC2 | CLAGIRABA, GUANABA, MAUDSLAND, OXENFORD, UPPER COO | Rural short | 377.475 | 11.2347 | 6.8972 |  | 74.8567 | 0.28558 | 3 | 1384486.42 | 6698.78 | 0.0021585 | 0.0010888 | 3 | 6248.24 | 8.8889e-05
VPK11A | BOWEN HILLS, FORTITUDE VALLEY | Urban | 306.5 | 0 | 2.191 | 3.8868 | 0 | 0.019053 | 0 | 0 | 0 | 0 | 0 | 1 | 634.0125 | 2.4022e-06
VPK11B | FORTITUDE VALLEY | Rural short | 33 | 0.1709 | 1.508 | 0.51443
VPK14A | BOWEN HILLS, HERSTON | Urban | 495.25 | 1.6799 | 2.2089 | 1.655 | 0 | 0.033135 | 0 | 0 | 0 | 0 | 0 | 1 | 384.8 | 1.0408e-06
VPK19A | HERSTON | Urban | 281.5 | 1.0694 | 1.387 | 2.858 | 35.0144 | 0.032471 | 2 | 316192 | 0 | 0.00028813 | 0 | 2 | 1278.88 | 3.7945e-06
VPK2A | BOWEN HILLS, HERSTON | Urban | 277 | 0.4456 | 1.8543 | 1.8291 | 44.1978 | 0 | 2 | 796945.32 | 14076.12 | 0.0003646 | 8.6754e-05 | 0 | 0 | 0
VPK8 | FORTITUDE VALLEY, SPRING HILL | Urban | 380.03 | 0.6179 | 2.3695 | 2.0958 | 0.0010337 | 0.22972 | 1 | 6222 | 6222 | 6.1561e-05 | 6.1561e-05 | 3 | 3968.5209 | 1.2107e-05
VPK9A | BOWEN HILLS, FORTITUDE VALLEY | Urban | 574.2275 | 1.2826 | 2.7677 | 2.7627 | 25.3897 | 0.32813 | 3 | 201856.2 | 60334.61 | 0.0017138 | 0.00057041 | 3 | 7451.01 | 3.7021e-05
VPT12A | VICTORIA POINT | Urban | 1142.066 | 5.1333 | 1.8562 | 2.9345 | 30.0898 | 1.2949 | 3 | 1135757.9288 | 13057.3488 | 0.0012842 | 0.00011892 | 2 | 2107.6925 | 6.9566e-06
VPT13A | MOUNT COTTON, THORNLANDS, VICTORIA POINT | Rural short | 847.5783 | 9.6935 | 5.6948 | 1.9822 | 0.39492 | 0.23138 | 1 | 11611.2 | 0 | 0.00010142 | 0 | 5 | 6286.41 | 7.9028e-05
VPT16A | VICTORIA POINT | Urban | 2035.25 | 6.8966 | 4.7911 | 5.3442 | 0.17813 | 0.027968 | 1 | 6435 | 6435 | 8.3375e-05 | 8.3375e-05 | 2 | 958.14 | 7.4925e-06
VPT1B | COOCHIEMUDLO ISLAND, VICTORIA POINT | Rural short | 2184 | 8.5579 | 5.8875 | 3.9256
VPT2A | VICTORIA POINT | Urban | 287.49 | 1.1392 | 1.7841 | 5.4492 | 0 | 0.00046765 | 0 | 0 | 0 | 0 | 0 | 1 | 23.36 | 7.3167e-07
VPT3A | THORNLANDS | Rural short | 1502.634 | 9.9114 | 6.9946 | 4.3726 | 8.4724 | 0.22982 | 4 | 278487.61 | 278487.61 | 0.00463 | 0.00463 | 1 | 351.08 | 3.8536e-06
VPT5B | VICTORIA POINT | Urban | 18.8 | 0 | 1.2088 | 1.8482 | 0 | 0.081369 | 0 | 0 | 0 | 0 | 0 | 1 | 214.83 | 1.3892e-06
VSL10A | ROBINA | Urban | 1161 | 0 | 8.0522 | 3.0675 | 0.009721 | 0.25369 | 1 | 291.03 | 291.03 | 3.2658e-06 | 3.2658e-06 | 1 | 5100.69 | 4.8135e-05
VSL10B | BURLEIGH WATERS, VARSITY LAKES | Urban | 1244 | 0 | 5.4191 | 3.3593
VSL11A | BURLEIGH WATERS, ROBINA, VARSITY LAKES | Urban | 576.5 | 0 | 7.7079 | 3.2771 | 0.2269 | 0 | 1 | 9447 | 9447 | 0.00014238 | 0.00014238 | 0 | 0 | 0
VSL12A | CLEAR ISLAND WATERS, ROBINA | Urban | 1669.5 | 0 | 13.8786 | 4.3877 | 0.065221 | 0 | 1 | 1247.4 | 1247.4 | 8.128e-06 | 8.128e-06 | 0 | 0 | 0
VSL13A | VARSITY LAKES | Urban | 2158.7425 | 0 | 9.2505 | 4.7807 | 4.3991 | 0.047073 | 2 | 123311.64 | 123311.64 | 0.0021703 | 0.0021703 | 2 | 860.4024 | 2.6294e-05
VSL1A | ROBINA, VARSITY LAKES | Urban | 1264 | 0 | 6.4946 | 3.3915
VSL1B | MERMAID WATERS, ROBINA, VARSITY LAKES | Urban | 1260 | 0 | 6.2355 | 3.1247 | 0.29987 | 0 | 1 | 5160 | 5160 | 1.2041e-05 | 1.2041e-05 | 0 | 0 | 0
VSL2A | VARSITY LAKES | Urban | 614 | 0 | 2.7395 | 3.582
VSL3A | REEDY CREEK, ROBINA, VARSITY LAKES | Urban | 842.33 | 1.7631 | 5.497 | 2.1766 | 3.4139 | 0.079586 | 2 | 42727.6 | 42727.6 | 0.00027877 | 0.00027877 | 1 | 2845.44 | 4.4845e-05
VSL4A | ROBINA, VARSITY LAKES | Urban | 131 | 0 | 2.1419 | 1.9053
VSL6A | VARSITY LAKES | Urban | 256 | 0 | 2.2528 | 2.1149
VSL8A | VARSITY LAKES | Urban | 335 | 0 | 2.214 | 3.8106
WCL10A | DARRA, WACOL | Urban | 98.5 | 1.3547 | 4.2247 | 2.6674 | 0.054429 | 0.049277 | 0 | 0 | 0 | 0 | 0 | 1 | 5101.88 | 3.3907e-05
WCL11A | WACOL | Urban | 138.5417 | 2.0347 | 3.2622 | 3.2581 | 0.21495 | 0.81451 | 1 | 52.5 | 52.5 | 3.5375e-06 | 3.5375e-06 | 4 | 6407.525 | 2.463e-05
WCL13A | RIVERHILLS, SUMNER, WACOL | Urban | 97.0033 | 5.4074 | 2.779 | 4.1536 | 136.8019 | 0 | 3 | 187570.67 | 1900 | 0.0002025 | 5.0208e-06 | 0 | 0 | 0
WCL16A | WACOL | Urban | 4 | 0.3338 | 0.4628 | 2.0387 | 0.058247 | 0
WCL17A | RICHLANDS, WACOL | Urban | 101.73 | 2.5399 | 2.9642 | 3.6582 | 0.089528 | 1.6851 | 0 | 0 | 0 | 0 | 0 | 5 | 11310.54 | 3.9782e-05
WCL19A | BELLBOWRIE, MOGGILL, WACOL | Rural short | 938.1156 | 8.9102 | 10.0202 | 5.0491 | 114.5093 | 0.77073 | 4 | 1204401 | 194698.5 | 0.0074478 | 0.0047824 | 5 | 11657.54 | 0.00013416
WCL2 | WACOL | Urban | 22 | 0 | 3.3008 | 3.6391 | 0.095496 | 0
WCL3 | WACOL | Urban | 70.3286 | 1.0789 | 0.4077 | 1.2385 | 8.1991 | 3.4727 | 2 | 17298.76 | 17298.76 | 0.00013725 | 0.00013725 | 5 | 4201.9527 | 1.3169e-05
WCL5A | MOGGILL, WACOL | Urban | 358 | 6.5822 | 3.9523 | 4.0964 | 0.11522 | 0.045647 | 0 | 0 | 0 | 0 | 0 | 1 | 103 | 1.01e-06
WCL6 | WACOL | Urban | 11.83 | 0.0636 | 0.7926 | 0.47633 | 0.08495 | 0
WCL7 | WACOL | Urban | 13 | 0.1256 | 1.6065 | 2.5141 | 0.071487 | 0
WED10 | HIGHGATE HILL, WEST END | Urban | 1051.55 | 2.0554 | 0.7479 | 1.613 | 0.014204 | 0.018759 | 0 | 0 | 0 | 0 | 0 | 1 | 1931.7 | 8.2091e-06
WED15B | SOUTH BRISBANE | Urban | 71.26 | 0 | 1.7744 | 4.7442 | 0.060071 | 0.39621 | 0 | 0 | 0 | 0 | 0 | 1 | 111 | 1.0062e-06
WED16A | WEST END | Urban | 1005.3076 | 1.515 | 1.5835 | 2.9723 | 3.7805 | 1.3663 | 4 | 118458.974 | 116330.54 | 0.0011213 | 0.0011002 | 12 | 48409.3319 | 0.00019853
WED16B | SOUTH BRISBANE, WEST END | Urban | 344 | 0.4268 | 1.2215 | 2.0652
WED17A | SOUTH BRISBANE | Urban | 162.56 | 0 | 1.643 | 3.1628 | 0.043274 | 0.034277 | 0 | 0 | 0 | 0 | 0 | 1 | 290.675 | 5.3079e-06
WED17B | SOUTH BRISBANE | Urban | 187 | 0 | 2.7675 | 4.8776 | 0.072852 | 0
WED18A | SOUTH BRISBANE | Urban | 106 | 0 | 0.9511 | 1.3147
WED20A | WEST END | Urban | 893.8289 | 2.5466 | 1.3829 | 2.2483 | 0.15636 | 0.29208 | 1 | 10684.9314 | 10684.9314 | 7.8684e-05 | 7.8684e-05 | 7 | 20258.3463 | 6.8548e-05
WED21A | SOUTH BRISBANE, WEST END | Urban | 354.416 | 0 | 1.1954 | 4.5346 | 2.2956 | 3.1428 | 3 | 36019.3 | 36019.3 | 0.00048683 | 0.00048683 | 6 | 13528.663 | 4.2488e-05
WED21B | SOUTH BRISBANE, WEST END | Urban | 353 | 0 | 2.5943 | 1.5814 | 0.28973 | 0 | 1 | 14177.1 | 14177.1 | 4.7599e-05 | 4.7599e-05 | 0 | 0 | 0
WED22A | SOUTH BRISBANE | Urban | 7 | 0 | 0.8139 | 3.1438
WED22B | SOUTH BRISBANE | Urban | 70.89 | 0 | 3.455 | 2.5341 | 0 | 26.1067 | 0 | 0 | 0 | 0 | 0 | 1 | 16553.37 | 1.1349e-06
WED3A | SOUTH BRISBANE, WEST END | Urban | 616.0556 | 2.6646 | 0.6407 | 4.8014 | 96.0658 | 0.39081 | 6 | 1161009.97 | 96951.52 | 0.0019647 | 0.0013437 | 2 | 5739.36 | 1.8572e-05
WED4B | SOUTH BRISBANE | Urban | 135.25 | 0 | 3.5196 | 3.3724 | 0 | 0.23771 | 0 | 0 | 0 | 0 | 0 | 3 | 7592.241 | 4.7357e-05
WED5A | SOUTH BRISBANE | Urban | 43.505 | 0 | 1.7619 | 3.5248 | 0.2315 | 0.22041 | 1 | 21 | 21 | 5.049e-07 | 5.049e-07 | 1 | 693 | 3.0912e-06
WED6A | SOUTH BRISBANE, WEST END | Urban | 2265.7434 | 3.3782 | 2.039 | 4.9348 | 11.9008 | 1.1337 | 12 | 533245.0577 | 533245.0577 | 0.0060378 | 0.0060378 | 19 | 95721.7168 | 0.00037565
WEL3 | SOUTHPORT | Urban | 179.655 | 0.5151 | 0.4161 |  | 1.3056 | 0 | 2 | 1838.6435 | 1838.6435 | 4.6613e-05 | 4.6613e-05 | 0 | 0 | 0
WFD1B | CEDARTON, COMMISSIONERS FLAT, PEACHESTER, STANMORE | Rural short | 349.8518 | 74.1205 | 0.7439 | 0.95266 | 256.0225 | 3.5935 | 10 | 1890348.66 | 60554.39 | 0.0054013 | 0.0024361 | 7 | 20481.78 | 0.00019772
WFD2B | STANMORE, STONY CREEK, WOODFORD | Rural short | 813.4807 | 55.6126 | 0.3752 | 2.8961 | 2.2217 | 6.0361 | 5 | 23816.18 | 18999.5 | 0.0048207 | 0.0025206 | 22 | 91505.332 | 0.0013382
WFD3A | WOODFORD | Rural short | 259.5044 | 14.905 | 2.4539 | 3.2581 | 5.2603 | 0.96939 | 4 | 33168.73 | 31697.65 | 0.0021826 | 0.0014801 | 5 | 8752 | 0.00013856
WFD5A | D'AGUILAR, DELANEYS CREEK, MOUNT DELANEY, MOUNT ME | Rural short | 609.902 | 72.9331 | 1.2001 | 1.1162 | 7.8155 | 1.5601 | 8 | 103976.36 | 28344.3 | 0.0050283 | 0.0031889 | 6 | 13944.01 | 0.00015881
WFD6A | BRACALBA, D'AGUILAR | Rural short | 359.332 | 17.7897 | 1.5903 | 2.1933 | 1.5879 | 0.055637 | 3 | 11542.2 | 9398.88 | 0.0021024 | 0.0010789 | 2 | 2569 | 2.5813e-05
WHO1 | ENGLAND CREEK, FAIRNEY VIEW, FERNVALE, VERNOR, WIV | Rural short | 546.6351 | 63.4889 | 1.0259 | 2.3816 | 16.6894 | 5.7814 | 10 | 310696.08 | 19726.08 | 0.0044465 | 0.002915 | 27 | 134436.66 | 0.0011938
WHO2 | FERNVALE | Rural short | 826.0556 | 16.7013 | 2.9668 | 2.8389 | 9.3717 | 0.2164 | 4 | 469335 | 17782.5 | 0.0057649 | 0.0033882 | 5 | 3794.12 | 5.2961e-05
WHO9 | BRYDEN, COOMINYA, DUNDAS, FERNVALE, SPLIT YARD CRE | Rural short | 75.472 | 54.6383 | 0.5152 | 0.15395 | 13.711 | 0 | 5 | 77435.33 | 36210.92 | 0.00065643 | 0.00043945 | 0 | 0 | 0
WMD10A | KULUIN, MAROOCHYDORE | Urban | 1257.0386 | 5.7612 | 1.5536 | 3.582 | 4.4966 | 0.89244 | 5 | 90663.4899 | 90663.4899 | 0.0014411 | 0.0014411 | 2 | 35725.9 | 0.00011317
WMD11A | BLI BLI, MARCOOLA, MUDJIMBA, PACIFIC PARADISE, TWI | Rural short | 1013.886 | 6.0325 | 14.6744 | 4.8395 | 0.14799 | 0.80193 | 0 | 0 | 0 | 0 | 0 | 4 | 27566.257 | 0.00043429
WMD13A | BUDERIM, FOREST GLEN, KUNDA PARK, MONS | Rural short | 987.719 | 9.2158 | 6.069 | 2.5722 | 15.6995 | 0.82252 | 6 | 423429.74 | 110697.74 | 0.0055878 | 0.004711 | 4 | 22224.99 | 0.00022316
WMD14A | MARCOOLA, MUDJIMBA, TWIN WATERS | Rural short | 1577.3375 | 5.3405 | 13.1832 | 4.2159 | 90.3691 | 0.36196 | 7 | 2579304.15 | 75139.75 | 0.010462 | 0.0055842 | 9 | 19751.636 | 0.00053442
WMD1A | KUNDA PARK, MAROOCHYDORE | Urban | 148.49 | 3.2651 | 1.0694 | 3.3152 | 0.12267 | 5.1759 | 0 | 0 | 0 | 0 | 0 | 1 | 2145 | 5.5215e-06
WMD2A | BUDERIM | Urban | 1477.5 | 9.4982 | 3.0223 | 3.8106 | 4.7328 | 0.60946 | 4 | 166428.2 | 28476.2 | 0.0017287 | 0.0016802 | 2 | 18872.1 | 0.00015821
WMD3A | BUDERIM, KULUIN, MAROOCHYDORE | Urban | 1335.46 | 7.8371 | 1.0987 | 3.1787 | 0.16783 | 0.055373 | 1 | 100 | 100 | 2.0205e-06 | 2.0205e-06 | 2 | 627.48 | 5.1855e-06
WMD4A | BLI BLI, BUDERIM, DIDDILLIBAH, KULUIN, ROSEMOUNT | Rural short | 1194.27 | 21.3587 | 1.5097 | 3.466 | 62.0263 | 4.3092 | 3 | 1739130 | 4379 | 0.0035406 | 0.00013391 | 6 | 80407.8 | 0.00059521
WMD6A | BUDERIM, MONS, TANAWHA | Urban | 1767.1778 | 11.719 | 2.8298 | 4.3877 | 25.392 | 0.51078 | 5 | 1165701.8 | 47395.8 | 0.0021738 | 0.0011052 | 4 | 20967.434 | 0.00010022
WMD8B | BUDERIM, FOREST GLEN, KIELS MOUNTAIN, KUNDA PARK, | Rural short | 644.0235 | 16.8221 | 5.697 | 3.9821 | 25.8017 | 3.1363 | 8 | 296039.315 | 40553.065 | 0.0044263 | 0.0020769 | 12 | 88268.405 | 0.00068586
WMR1 | CAMPBELLS POCKET, MOUNT MEE, MT PLEASANT, OCEAN VI | Rural short | 668.4107 | 75.8223 | 5.0736 | 1.4118 | 101.18 | 3.3402 | 10 | 1505898.99 | 64775.93 | 0.0071729 | 0.0039165 | 16 | 57536.386 | 0.00063027
WMR2 | BELLMERE, WAMURAN, WAMURAN BASIN | Rural short | 246.0991 | 27.5387 | 0.7967 | 0.75423 | 13.2775 | 2.9539 | 5 | 156459.54 | 32995.37 | 0.001973 | 0.00091863 | 6 | 22820.3022 | 0.00021408
WMR3 | D'AGUILAR, ELIMBAH, WAMURAN | Rural short | 359.7223 | 43.4274 | 0.5648 | 1.6767 | 26.1444 | 7.6613 | 11 | 187274.37 | 83952.33 | 0.0043337 | 0.0028563 | 23 | 66137.588 | 0.00057922
WMR4 | BRACALBA, WAMURAN | Rural short | 51.6667 | 13.6977 | 0.4895 | 0.077313 | 0.44421 | 0.039016 | 2 | 4952 | 4760 | 0.00027595 | 0.00013843 | 1 | 994.5 | 1.3177e-05
WNM1A | WYNNUM, WYNNUM WEST | Urban | 1638.7778 | 4.9868 | 3.4374 | 5.2396 | 6.1868 | 0.67514 | 2 | 263593 | 263593 | 0.0017206 | 0.0017206 | 7 | 14934.68 | 5.7498e-05
WNM2A | MANLY, WYNNUM | Urban | 1990.0946 | 7.517 | 0.5719 | 3.8681 | 28.4757 | 1.7821 | 8 | 1139067.24 | 385215.64 | 0.0043814 | 0.0023705 | 20 | 63190.665 | 0.00025295
WNM3 | WYNNUM | Urban | 1277.5 | 5.2775 | 0.6727 | 2.2708 | 13.8456 | 0.40268 | 5 | 442530.2533 | 262253.5533 | 0.0027733 | 0.0014804 | 9 | 23702.9 | 9.9127e-05
WNM4 | WYNNUM | Urban | 1342.9286 | 4.6902 | 0.9558 | 4.1952 | 74.2566 | 14.9537 | 3 | 983435 | 2680 | 0.0027768 | 6.0407e-05 | 3 | 2167.34 | 5.289e-06
WNM5 | HEMMANT, LYTTON, WYNNUM, WYNNUM WEST | Urban | 2195.4865 | 9.2588 | 3.0367 | 4.33 | 21.9981 | 1.9734 | 11 | 851710.26 | 705414.96 | 0.011378 | 0.0091614 | 25 | 107765.82 | 0.00040782
WNM6 | WYNNUM, WYNNUM WEST | Urban | 794.8333 | 2.9863 | 1.6166 | 1.5203 | 42.0708 | 0.026519 | 4 | 2571130.62 | 22796 | 0.0018751 | 0.0001405 | 2 | 1344.6 | 4.9711e-06
WNM7A | WYNNUM | Urban | 1179.91 | 3.5776 | 1.4868 | 3.8487 | 11.5274 | 0.49975 | 8 | 342873.956 | 11881.196 | 0.0013477 | 0.0001302 | 6 | 8220.9298 | 6.3223e-05
WRD11A | KANGAROO POINT, WOOLLOONGABBA | Urban | 160 | 0.033 | 1.09 | 2.9151 | 0 | 0.0044516 | 0 | 0 | 0 | 0 | 0 | 1 | 314.43 | 1.4075e-06
WRD13B | SOUTH BRISBANE, WOOLLOONGABBA | Urban | 25 | 0 | 2.2082 | 3.5439 | 0.074046 | 0.26794 | 1 | 299 | 299 | 6.5061e-06 | 6.5061e-06 | 1 | 1081.08 | 1.0109e-05
WRD15A | EAST BRISBANE, KANGAROO POINT | Urban | 857.6633 | 1.537 | 0.9175 | 2.2864 | 0.36527 | 0.060433 | 2 | 3094.32 | 3094.32 | 5.6949e-05 | 5.6949e-05 | 1 | 5034.225 | 2.2536e-05
WRD15B | WOOLLOONGABBA | Urban | 842.33 | 0.4032 | 2.4351 | 3.9821 | 1.9239 | 0.0071282 | 2 | 35254.5 | 23489.5 | 0.00014657 | 5.5078e-05 | 1 | 306.74 | 3.1423e-06
WRD17A | EAST BRISBANE, WOOLLOONGABBA | Urban | 272.86 | 0.0848 | 1.8231 | 2.1339 | 2.0016 | 0.34059 | 2 | 34671.45 | 34671.45 | 6.6087e-05 | 6.6087e-05 | 3 | 9126.015 | 6.5919e-05
WRD19A | COORPAROO, EAST BRISBANE | Urban | 1324 | 4.3649 | 0.3482 | 4.4775 | 0.028635 | 0.25716 | 0 | 0 | 0 | 0 | 0 | 1 | 476 | 1.011e-06
WRD20A | EAST BRISBANE, NORMAN PARK | Urban | 1206.9722 | 2.3456 | 3.0497 | 3.7535 | 1.6165 | 2.1139 | 4 | 65444.6396 | 63532.0996 | 0.00021909 | 0.00016827 | 4 | 36889.1877 | 0.00012178
WRD21A | KANGAROO POINT, SOUTH BRISBANE, WOOLLOONGABBA | Urban | 814.4271 | 1.4873 | 3.0442 | 3.2771 | 35.487 | 1.19 | 5 | 577505.925 | 104240.925 | 0.002563 | 0.0017452 | 2 | 1245.86 | 2.0472e-05
WRD22B | KANGAROO POINT | Urban | 753.3275 | 0.3908 | 3.5318 | 2.3245 | 5.2216 | 0.33648 | 2 | 279177.06 | 105360.06 | 0.00084816 | 0.00075819 | 2 | 14467.68 | 8.1483e-05
WRD24A | GREENSLOPES, WOOLLOONGABBA | Urban | 274.58 | 0.383 | 2.1304 | 1.3528 | 2.3776 | 0 | 1 | 14518 | 0 | 3.4371e-05 | 0 | 0 | 0 | 0
WRD25A | SOUTH BRISBANE, WOOLLOONGABBA | Urban | 167.75 | 0 | 3.2173 | 2.3054 | 0 | 2.3882 | 0 | 0 | 0 | 0 | 0 | 2 | 7618.16 | 2.2235e-05
WRD25B | KANGAROO POINT | Urban | 1071.945 | 0.4394 | 4.3737 | 3.9249 | 0.23185 | 0.28715 | 1 | 8177.4 | 0 | 6.9981e-05 | 0 | 1 | 504 | 2.1238e-06
WRD3A | EAST BRISBANE, WOOLLOONGABBA | Urban | 92.5 | 0 | 1.575 | 2.2673
WRD5A | EAST BRISBANE, KANGAROO POINT | Urban | 126 | 0 | 1.6249 | 0.47633
WRD9A | KANGAROO POINT | Urban | 644.78 | 0 | 3.5162 | 3.3915 | 2.3747 | 0.74255 | 2 | 42808.92 | 42808.92 | 0.00060058 | 0.00060058 | 3 | 31788.675 | 0.00010683
WRG11A | KINGSTON, LOGAN CENTRAL, WOODRIDGE | Urban | 644.78 | 5.4208 | 1.1562 | 1.9434 | 4.5116 | 0.34864 | 1 | 53328 | 53328 | 0.00083564 | 0.00083564 | 5 | 18051.1809 | 7.5063e-05
WRG12A | BERRINBA, LOGAN CENTRAL, WOODRIDGE | Urban | 1523.0533 | 6.352 | 1.1424 | 2.7436 | 0 | 0.76414 | 0 | 0 | 0 | 0 | 0 | 6 | 13196.195 | 7.7082e-05
WRG15A | KINGSTON, LOGAN CENTRAL, WOODRIDGE | Rural short | 1364 | 5.7742 | 0.5707 | 1.0392
WRG16A | SLACKS CREEK | Urban | 37 | 0.2221 | 3.4675 | 3.6963 | 0 | 5.2766 | 0 | 0 | 0 | 0 | 0 | 1 | 350 | 2.005e-06
WRG18A | LOGAN CENTRAL | Urban | 6.5 | 0 | 3.1164 | 4.6299
WRG19A | DAISY HILL, SLACKS CREEK, SPRINGWOOD, WOODRIDGE | Urban | 553.508 | 3.4752 | 1.9917 | 3.7725 | 6.7319 | 0.011909 | 4 | 126035.86 | 89194 | 0.0012576 | 0.0012117 | 1 | 49.92 | 1.0512e-06
WRG1A | SLACKS CREEK, WOODRIDGE | Urban | 2217.462 | 8.0575 | 0.9451 | 3.8106 | 0.29848 | 0.70904 | 2 | 27853 | 27853 | 0.00034873 | 0.00034873 | 8 | 30587.315 | 0.00014178
WRG2A | KINGSTON, LOGAN CENTRAL, SLACKS CREEK | Urban | 1464.5 | 9.0504 | 0.2183 | 3.1368 | 15.8679 | 0.0013345 | 2 | 1002553 | 7572.5 | 0.0015737 | 0.00011696 | 1 | 93.96 | 1.1702e-06
WRG4A | SLACKS CREEK | Urban | 1403.915 | 2.2386 | 0.7246 | 1.399 | 0.42894 | 0.0063028 | 3 | 15126.24 | 15126.24 | 0.00023204 | 0.00023204 | 1 | 280.8 | 1.7564e-06
WRG5A | BERRINBA, KARAWATHA, LOGAN CENTRAL, WOODRIDGE | Urban | 796.5067 | 8.0308 | 2.9645 | 3.22 | 88.0641 | 0.062396 | 1 | 1457664.38 | 0 | 0.00071831 | 0 | 2 | 3442.516 | 2.3347e-05
WRG6A | WOODRIDGE | Urban | 2045.5527 | 3.2372 | 0.1338 | 1.5715 | 0.6009 | 0.96155 | 2 | 16061.25 | 16061.25 | 6.3643e-05 | 6.3643e-05 | 13 | 54323.49 | 0.00022522
WRG8A | DAISY HILL, KINGSTON, LOGANLEA, SLACKS CREEK | Urban | 1287.1329 | 9.5831 | 1.2092 | 5.7159 | 14.4148 | 1.7613 | 3 | 481261.44 | 48358.44 | 0.0026459 | 0.0013587 | 4 | 4497.06 | 1.74e-05
WRG9A | SLACKS CREEK, SPRINGWOOD | Urban | 725.625 | 4.5627 | 0.3327 | 3.3533 | 10.3087 | 0.26355 | 3 | 164759.73 | 164759.73 | 0.0015075 | 0.0015075 | 1 | 1615 | 1.9015e-05
WSE1B | KURWONGBAH, WHITESIDE | Rural short | 10 | 5.7007 | 2.4904 | 4.2869
WSE3A | ARMSTRONG CREEK, DAYBORO, KING SCRUB, LACEYS CREEK | Rural short | 1113.3921 | 92.4851 | 5.782 | 2.858 | 262.2891 | 11.1395 | 14 | 4234507.26 | 242484.3 | 0.013472 | 0.0058037 | 28 | 190346.783 | 0.0018263
WSE5A | ARMSTRONG CREEK, DAYBORO, KOBBLE CREEK, KURWONGBAH | Rural short | 655.4589 | 67.115 | 1.459 | 1.3909 | 102.4427 | 5.0026 | 19 | 2184263.815 | 137824.815 | 0.0090604 | 0.0028257 | 9 | 82482.56 | 0.00071985
WSE6A | KURWONGBAH, WHITESIDE | Rural short | 466.6019 | 20.4905 | 2.3085 | 1.0289 | 22.1076 | 0.2167 | 12 | 479281.59 | 103310.27 | 0.0031454 | 0.0017678 | 3 | 6442.72 | 9.0102e-05
WSO12B | ELLEN GROVE, FOREST LAKE | Rural short | 860.25 | 3.2951 | 4.8535 | 0.34296 | 58.7317 | 0.48895 | 1 | 3783270 | 0 | 0.0024483 | 0 | 1 | 5589 | 7.7197e-05
WSO13A | CAROLE PARK, ELLEN GROVE, GAILES, WACOL | Rural short | 707.132 | 4.6422 | 2.9925 | 1.8282 | 6.6999 | 2.4421 | 5 | 349160.1702 | 22420.1702 | 0.0035213 | 0.0024269 | 5 | 67712.868 | 0.00053171
WSO15A | WACOL | Urban | 43.58 | 1.0403 | 1.2999 | 2.877 | 0 | 0.28508 | 0 | 0 | 0 | 0 | 0 | 1 | 1640.16 | 1.6145e-05
WSO16A | WACOL | Urban | 21 | 0 | 2.2528 | 3.0675 | 0 | 5.9166 | 0 | 0 | 0 | 0 | 0 | 1 | 2909.61 | 9.9588e-07
WSO16B | WACOL | Urban | 13 | 0 | 1.804 | 3.4867
WSO1B | WACOL | Urban | 4 | 0 | 1.3448 | 3.6772
WSO2B | WACOL | Urban | 5.5 | 0.4713 | 0.8618 | 2.3816 | 2.9122 | 0 | 1 | 341 | 341 | 5.5393e-06 | 5.5393e-06 | 0 | 0 | 0
WSO3A | ELLEN GROVE, FOREST LAKE, RICHLANDS, WACOL | Urban | 1187.325 | 3.0589 | 7.0019 | 5.011 | 0.42169 | 14.5946 | 2 | 1946.5 | 1946.5 | 3.5634e-05 | 3.5634e-05 | 4 | 11981 | 2.6045e-05
WSO5A | WACOL | Urban | 60.66 | 0.2174 | 2.4761 | 4.1536 | 0 | 4.4352 | 0 | 0 | 0 | 0 | 0 | 1 | 301 | 1.0021e-06
YDA1B | NINDERRY, YANDINA | Rural short | 404 | 13.213 | 2.7094 | 1.8291 | 14.252 | 1.7937 | 13 | 173989.8 | 148392.8 | 0.0055084 | 0.0054711 | 1 | 52508.96 | 0.00027987
YDA2B | BRIDGES, NORTH ARM, YANDINA | Rural short | 169.25 | 9.5844 | 0.9762 | 0.36744 | 0.74485 | 0.018516 | 3 | 15014.5 | 15014.5 | 0.0012604 | 0.0012604 | 2 | 318.29 | 2.071e-05
YDA3A | MAROOCHY RIVER, YANDINA | Rural short | 389.0263 | 13.0499 | 2.8522 | 1.2947 | 19.5272 | 5.5008 | 7 | 318341.65 | 34189.15 | 0.0043188 | 0.0032056 | 12 | 65655.925 | 0.00048385
YDA5A | BRIDGES, COOLOOLABIN, KIAMBA, YANDINA | Rural short | 879.87 | 22.2569 | 0.5339 | 2.0113 | 36.8762 | 4.0768 | 8 | 734019.5918 | 132419.8718 | 0.0085078 | 0.0074821 | 16 | 77339.0285 | 0.00096816
YDA6A | YANDINA | Urban | 5 | 0.4977 | 0.8369 | 1.5665 | 0.96463 | 0 | 2 | 165 | 165 | 1.0036e-05 | 1.0036e-05 | 0 | 0 | 0
YTA22B | BANNOCKBURN, WINDAROO, YATALA | Rural short | 1061.25 | 9.5031 | 7.5872 | 3.1438 | 6.2987 | 0.10266 | 3 | 134606.75 | 68063 | 0.0063015 | 0.0032493 | 2 | 1010.92 | 8.3852e-05
YTA23A | YATALA | Urban | 4 | 0.032 | 1.3668 | 1.8766
YTA2B | ORMEAU, ORMEAU HILLS | Rural short | 1098.11 | 5.2437 | 2.7936 | 4.0202 | 6.4024 | 1.8205 | 2 | 206801 | 206801 | 0.0063342 | 0.0063342 | 1 | 75194.91 | 0.0012357
YTA33A | BANNOCKBURN, LUSCOMBE, ORMEAU, YATALA | Rural short | 219 | 17.7718 | 0.36293 | 3.0675
YTA34A | GILBERTON, ORMEAU, STAPYLTON, YATALA | Urban | 134.02 | 3.3419 | 4.7444 | 3.1247
YTA35A | ORMEAU | Urban | 85 | 0 | 4.3298 | 4.8966
YTA37A | YATALA | Urban | 183.5 | 3.2497 | 10.3443 | 4.9796 | 0 | 0.068168 | 0 | 0 | 0 | 0 | 0 | 1 | 86.4 | 9.6218e-07
YTA39A | LUSCOMBE, ORMEAU, ORMEAU HILLS, YATALA | Urban | 348.5 | 11.285 | 1.5835 | 4.0202
YTA3A | YATALA | Urban | 143.9917 | 2.8084 | 0.6523 | 5.3349 | 1.4592 | 3.8424 | 2 | 25547.33 | 2405.33 | 0.00015005 | 0.00014297 | 4 | 25326 | 6.731e-05
YTA41A | BEENLEIGH, KINGSHOLME, ORMEAU, ORMEAU HILLS, PIMPA | Rural short | 2241 | 33.7881 | 13.9064 | 5.3349
YTA43A | ORMEAU, YATALA | Urban | 1754 | 4.3595 | 15.6483 | 5.6016
YTA45A | YATALA | Urban | 37 | 2.0242 | 0.67297 | 1.4861
YTA5A | YATALA | Urban | 6 | 0 | 1.6598 | 4.8966
ZMR10 | ASPLEY, ZILLMERE | Urban | 1449.5727 | 7.4784 | 0.5799 | 4.4394 | 1.2754 | 0.42224 | 8 | 34140.51 | 14486.39 | 0.0017383 | 0.001599 | 6 | 19986.96 | 8.929e-05
ZMR11A | ASPLEY | Urban | 273.75 | 1.5524 | 2.8453 | 3.4486 | 6.0771 | 0 | 2 | 11332.5 | 11332.5 | 0.00029522 | 0.00029522 | 0 | 0 | 0
ZMR2A | ASPLEY, BRIDGEMAN DOWNS, CARSELDINE, ZILLMERE | Urban | 711.9975 | 0.9648 | 5.541 | 3.5629 | 0.47246 | 0.012862 | 3 | 20874.09 | 20874.09 | 0.00075758 | 0.00075758 | 1 | 1455.21 | 1.3205e-05
ZMR3 | ASPLEY, GEEBUNG, ZILLMERE | Urban | 1485.2233 | 6.7704 | 1.0736 | 2.9829 | 0.22554 | 0.032183 | 2 | 8975.01 | 8975.01 | 0.0015847 | 0.0015847 | 1 | 1599.801 | 7.6076e-06
ZMR4A | ASPLEY, CARSELDINE, FITZGIBBON, ZILLMERE | Urban | 1936.1917 | 2.4599 | 10.5417 | 4.2679 | 0.29744 | 1.1304 | 1 | 5802.57 | 5802.57 | 0.001952 | 0.001952 | 4 | 14903.395 | 5.9627e-05
ZMR5 | ASPLEY, BRIDGEMAN DOWNS | Urban | 1978.734 | 7.0851 | 3.9716 | 4.2107 | 7.4201 | 0.39521 | 7 | 530786.8284 | 530786.8284 | 0.0061996 | 0.0061996 | 3 | 3959.51 | 4.2212e-05
ZMR6A | GEEBUNG, ZILLMERE | Urban | 796.2589 | 3.567 | 1.689 | 3.2581 | 0.48111 | 6.2895 | 2 | 11850 | 11850 | 0.00091832 | 0.00091832 | 7 | 14001.525 | 4.1277e-05
ZMR7A | BOONDALL, GEEBUNG, ZILLMERE | Urban | 1865.6033 | 5.601 | 3.9003 | 4.1726 | 10.7496 | 1.2812 | 5 | 483382.97 | 483382.97 | 0.0057228 | 0.0057228 | 13 | 36113.2475 | 0.00017685
ZMR8A | ASPLEY | Urban | 59 | 1.2511 | 0.8976 | 3.4296 | 0.042089 | 0 | 1 | 177 | 177 | 5.9542e-05 | 5.9542e-05 | 0 | 0 | 0
ZMR9 | ZILLMERE | Urban | 1783.75 | 4.8066 | 1.5127 | 3.4486 | 5.9166 | 0.67764 | 6 | 232088.64 | 232088.64 | 0.0037191 | 0.0037191 | 8 | 10032.9924 | 5.9568e-05
ZMR9 | ZILLME | Urban | 1783.75 | 4.8066 | 1.5127 | 3.4486 | 5.9166 | 0.67764 | 6 | 232088.64 | 232088.64 | 0.0037191 | 0.0037191 | 8 | 10032.9924 | 5.9568e-05
Contents

## 5c. Network data outages
Energex
Cause of Outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Causes of unplanned sustained outages
Cause of outage | Number of outages
Weather | 1547
Equipment failure | 1654
Operational error | 73
Vegetation | 279
Animals | 552
Third party impacts | 299
Transmission failure | 0
Load shedding | 0
Inter-distributor connection failure | 0
Other | 1291
Contents

## 5d. Outcomes planned outages
Energex
Planned Outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI - after removing excluded events | 0.68096 | 20.1085 | 57.3964 | NA | 29.6506
SAIFI - after removing excluded events | 0.0060007 | 0.07654 | 0.20249 | NA | 0.10875
Contents

## 6. Weighted av cost of debt
Energex
Weighted average cost of debt
2012-13
This information will be used to compare the DBs cost against the benchmark cost of debt. There is no intention to set the regulated cost of debt for a business based on its actual cost of debt.
Notes: the specific method of calculating the weighted average cost of debt for the financial year is Energex's choice but must be fully described. If the description of the methodology cannot fit in this worksheet, Energex can provide details as a separate attachment.
Table 1: Cost of debt
Weighted average cost of debt (%) | 2012-13 | Explanation of calculation method
| 6.98% | Please refer to the Attachment 3 - Schedule 1 responses for an explanation of the data and method used to determine the cost of debt.
Contents

## 7. Asset installation
Energex
Asset Installation
2012-13
This information is used in the AER’s replacement capex model. The model is used by the AER to assess forecast replacement capex proposals. It may also be used to monitor the asset age profile of the business over time. This will be used as a tool to monitor any improvements/deterioration in the overall asset age where capex has been approved to address network asset age.
Table 1: Asset age profile for distribution system assets
Asset group/category |  |  | Replacement life (years) |  | Actual replacement volumes (number of assets replaced) | Replacement unit cost | Asset Failures | Total quantity | Year Commissioned (number of assets commissioned in each year)
| NSD Responsibility (Remove column before submitting to AER) | Definition (Remove column before submitting to AER) This is not a complete list of definitions | Mean | Standard Deviation |  |  |  |  | 1910 | 1911 | 1912 | 1913 | 1914 | 1915 | 1916 | 1917 | 1918 | 1919 | 1920 | 1921 | 1922 | 1923 | 1924 | 1925 | 1926 | 1927 | 1928 | 1929 | 1930 | 1931 | 1932 | 1933 | 1934 | 1935 | 1936 | 1937 | 1938 | 1939 | 1940 | 1941 | 1942 | 1943 | 1944 | 1945 | 1946 | 1947 | 1948 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | Quantity of Unknown Age
Poles
132/110kV Tower |  |  | 70 | 8 | 0 | 269223.53 | 0 | 1036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 98 | 0 | 158 | 0 | 1 | 63 | 31 | 0 | 0 | 31 | 0 | 2 | 0 | 367 | 56 | 53 | 22 | 0 | 0 | 8 | 1 | 37 | 1 | 0 | 21 | 2 | 15 | 37 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 20 | 1 | 0 |  |  | 0
132/110kV Steel pole | SAM | excluding W sites | 70 | 8 | 3 | 144639.48 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0115 | 0 | 0 | 0 | 1.0038 | 0 | 0 | 9.0344 | 0 | 0 | 1.0038 | 0 | 0 | 248.9466 | 0 | 20 | 5 | 2 | 0 | 0 | 1 | 16 | 7 | 1 | 17 | 19 | 29 | 0 |  |  | 0
132/110kV Concrete pole | SAM |  | 40.99 | 18 | 8 | 140956.51 | 0 | 1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0074 | 0 | 39.2873 | 184.3481 | 2.0147 | 24.1768 | 1.0074 | 103.7587 | 0 | 2.0147 | 1.0074 | 2.0147 | 80.5893 | 8.0589 | 0 | 1.0074 | 0 | 0 | 5.0368 | 91.6703 | 38 | 216 | 104 | 1 | 2 | 31 | 32 | 112 | 77 | 12 | 36 | 27 | 41 | 8 |  |  | 0
132/110kV Wood pole | SAM |  | 49 | 15 | 19 | 13740 | 0 | 1956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 2 | 34 | 2 | 3 | 1 | 1.0236 | 1.0236 | 2.0472 | 0 | 0 | 0 | 1.0236 | 2.0472 | 0 | 65.5103 | 52.2035 | 1.0236 | 2.0472 | 5.118 | 14.3304 | 0 | 14.3304 | 17.4012 | 5.118 | 1.0236 | 1.0236 | 7.1652 | 8.1888 | 12.2832 | 1.0236 | 1.0236 | 11.2596 | 2.0472 | 49.1327 | 68.5811 | 338 | 372 | 136 | 9 | 8 | 30 | 233 | 247 | 20 | 11 | 54 | 71 | 11 | 19 |  |  | 0
33kV Concrete pole | SAM |  | 70 | 8 | 4 | 16538 | 0 | 687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 4 | 4 | 0 | 0 | 2 | 3 | 0 | 1 | 2 | 10 | 1 | 5 | 4 | 5.1166 | 2.0466 | 4.0932 | 3.0699 | 1.0233 | 0 | 5.1166 | 2.0466 | 1.0233 | 3.0699 | 2.0466 | 155.5431 | 0 | 5.1166 | 2.0466 | 1.0233 | 23.5361 | 9.2098 | 21.4895 | 67.5385 | 14.3263 | 1.0233 | 2.0466 | 3.0699 | 16.373 | 23.5361 | 0 | 6.1399 | 0 | 58.3287 | 21 | 67 | 3 | 10 | 1 | 0 | 22 | 4 | 4 | 4 | 27 | 10 | 14 | 4 |  |  | 0
33kV Steel pole | SAM |  | 70 | 8 | 10 | 10410 | 0 | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0026 | 3.0077 | 3.0077 | 0 | 0 | 2.0051 | 0 | 3.0077 | 1.0026 | 2.0051 | 3.0077 | 1.0026 | 1.0026 | 1.0026 | 0 | 0 | 2.0051 | 1.0026 | 0 | 365.9383 | 4 | 0 | 6 | 8 | 1 | 8 | 6 | 4 | 0 | 6 | 13 | 0 | 18 | 10 |  |  | 0
33kV Wood pole | SAM |  | 49 | 15 | 761 | 11244 | 0 | 23876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 1 | 0 | 21 | 43 | 2 | 10 | 71 | 0 | 6 | 40 | 64 | 74 | 43 | 43 | 137 | 125 | 70 | 29 | 1 | 13 | 110 | 49 | 75 | 70 | 77 | 78 | 113 | 85 | 104 | 54 | 76 | 190 | 181 | 149 | 192 | 100 | 97 | 100 | 161 | 440 | 278 | 474 | 195 | 431 | 551.1211 | 430.9135 | 461.4748 | 345.3421 | 571.4953 | 708.0021 | 681.5157 | 798.6672 | 902.5754 | 527.6908 | 521.5786 | 276.0699 | 302.5563 | 279.126 | 287.2757 | 214.9474 | 265.8828 | 176.2365 | 359.604 | 149.7501 | 239.3964 | 142.6191 | 142.6191 | 106.9644 | 158.9185 | 144.6566 | 206.7977 | 322.9305 | 331.0801 | 337.1924 | 345 | 601 | 383 | 365 | 369 | 268 | 584 | 471 | 655 | 566 | 854 | 930 | 1079 | 749 |  |  | 0
11 Concrete pole | SAM |  | 43 | 12 | 198 | 19768 | 0 | 5402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 5 | 4 | 8 | 2 | 1 | 3 | 2 | 7 | 3 | 6 | 7 | 3 | 1 | 1 | 9 | 12 | 4 | 3 | 3 | 8 | 14 | 4 | 8 | 11 | 6 | 8 | 4 | 10 | 12 | 17 | 13 | 11 | 38 | 66 | 50 | 77 | 73 | 76 | 133.7432 | 106.5766 | 64.7818 | 73.1408 | 56.4229 | 35.5255 | 27.1666 | 37.6153 | 29.2563 | 22.9871 | 33.4358 | 45.9742 | 47.0191 | 34.4807 | 48.064 | 180.7622 | 270.6209 | 261.2171 | 38.6601 | 38.6601 | 37.6153 | 42.8396 | 51.1986 | 49.1088 | 59.5575 | 30.3012 | 26.1217 | 41.7947 | 44.9293 | 56.4229 | 87 | 46 | 43 | 63 | 99 | 410 | 346 | 333 | 324 | 240 | 216 | 184 | 200 | 193 |  |  | 0
11 Steel pole | SAM |  | 70 | 8 | 3 | 3846 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2.2222 | 0 | 0 | 0 | 1.1111 | 0 | 0 | 4.4444 | 1.1111 | 2.2222 | 3.3333 | 1.1111 | 1.1111 | 0 | 2.2222 | 2.2222 | 4.4444 | 0 | 8.8889 | 0 | 2.2222 | 4.4444 | 1.1111 | 2.2222 | 4.4444 | 5.5556 | 7.7778 | 7.7778 | 7 | 2 | 2 | 2 | 1 | 1 | 5 | 3 | 1 | 1 | 0 | 1 | 0 | 3 |  |  | 0
11 Wood pole | SAM |  | 49 | 15 | 4899 | 9654 | 6 | 208284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 13 | 10 | 4 | 1 | 6 | 4 | 30 | 20 | 21 | 83 | 330 | 248 | 630 | 248 | 435 | 558 | 369 | 510 | 505 | 399 | 305 | 125 | 157 | 177 | 570 | 650 | 838 | 800 | 679 | 869 | 1021 | 1346 | 1467 | 1156 | 1036 | 1435 | 1133 | 1517 | 1552 | 1703 | 1559 | 1892 | 2176 | 2767 | 2691 | 2682 | 2970 | 3041 | 3581.4067 | 3650.2604 | 3730.2523 | 3939.8511 | 4029.9685 | 4201.0903 | 4257.7934 | 4359.0489 | 4960.5065 | 4587.8863 | 4747.87 | 5170.1054 | 5442.4826 | 5964.961 | 5078.9754 | 4112.998 | 4599.0244 | 3421.423 | 3382.9459 | 3938.8386 | 4076.5461 | 3685.6999 | 3284.7281 | 3063.9911 | 2743.0112 | 2788.5762 | 2026.1224 | 2894.8945 | 2829.0784 | 2553.6635 | 2722 | 2509 | 2552 | 1579 | 1949 | 2617 | 2963 | 3790 | 3746 | 4606 | 4956 | 4663 | 4983 | 4785 |  |  | 0
LV Concrete pole | SAM |  | 40 | 6 | 2 | 6053 | 0 | 1833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 4 | 1 | 0 | 0 | 1 | 0 | 5 | 0 | 0 | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 7 | 3 | 17 | 3 | 37 | 6 | 7 | 6 | 5 | 22 | 14 | 12 | 25.1829 | 23.0843 | 50.3657 | 152.1464 | 73.45 | 35.6757 | 31.4786 | 19.9364 | 79.7457 | 76.5979 | 64.0064 | 22.035 | 16.7886 | 23.0843 | 32.5279 | 41.9714 | 68.2036 | 53.5136 | 20.9857 | 34.6264 | 60.8586 | 14.69 | 3.1479 | 30.4293 | 67.1543 | 211.9557 | 64.0064 | 19.9364 | 27.2814 | 24.1336 | 22 | 17 | 41 | 18 | 6 | 7 | 8 | 13 | 57 | 5 | 0 | 3 | 0 | 5 |  |  | 0
LV Steel pole | SAM | excludes W sites (rate 3 SL) - as per Gary Buckley 8-07-2013 | 22 | 7 | 3423 | 3988 | 0 | 132875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1197 | 27.8079 | 35.0173 | 18.5386 | 29.8677 | 54.5858 | 58.7055 | 202.8945 | 171.9969 | 203.9244 | 279.1087 | 468.6142 | 454.1953 | 420.2079 | 642.6709 | 537.6189 | 1715.849 | 2120.6081 | 1991.8679 | 2198.8821 | 2933.216 | 2962.0538 | 3462.5956 | 4735.5784 | 4536.8036 | 4937.443 | 2464.6018 | 3075.3452 | 3691.2382 | 4545.043 | 5486 | 4865 | 5087 | 5261 | 6869 | 7881 | 6510 | 7751 | 8221 | 6861 | 5441 | 5643 | 4894 | 3124 |  |  | 0
LV Wood pole | SAM |  | 49 | 15 | 2666 | 5939 | 1 | 169519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 20 | 11 | 15 | 18 | 27 | 16 | 36 | 13 | 51 | 95 | 201 | 229 | 291 | 604 | 831 | 578 | 374 | 419 | 375 | 386 | 278 | 110 | 60 | 166 | 444 | 600 | 778 | 869 | 854 | 862 | 1071 | 930 | 903 | 848 | 949 | 871 | 1010 | 1222 | 1171 | 1563 | 1464 | 1684 | 2151 | 2358 | 2664 | 2936 | 3130 | 3190 | 3571.2879 | 3692.2096 | 3871.5425 | 4354.2044 | 4153.3515 | 3788.537 | 4415.69 | 4706.7218 | 4321.4121 | 3569.2384 | 3551.8175 | 3605.105 | 3883.8397 | 4543.785 | 4164.6238 | 3731.1504 | 3827.4779 | 2888.7979 | 2538.33 | 3443.1929 | 3367.3607 | 2794.52 | 2541.4043 | 2872.4017 | 2368.2199 | 2161.2184 | 1443.8866 | 2144.8223 | 2113.0547 | 1936.796 | 2156 | 1580 | 1587 | 1441 | 1455 | 1442 | 2192 | 1984 | 2359 | 2846 | 2664 | 2424 | 2570 | 2682 |  |  | 0
No voltage Concrete pole | SAM | eg. Stay (bollard), cross st service pole | 40 | 6 | 12 | 4926 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 2 | 6 | 7 | 6 | 2 | 13 | 17.692 | 18.7327 | 5.2035 | 15.6106 | 4.1628 | 10.4071 | 4.1628 | 14.5699 | 16.6513 | 17.692 | 21.8549 | 23.9363 | 14.5699 | 37.4655 | 10.4071 | 3.1221 | 4.1628 | 7.285 | 2.0814 | 3.1221 | 2.0814 | 1.0407 | 1.0407 | 12.4885 | 105.1115 | 95.7451 | 29.1398 | 23.9363 | 39.5469 | 24.977 | 22 | 13 | 11 | 1 | 5 | 6 | 6 | 6 | 25 | 3 | 1 | 1 | 1 | 14 |  |  | 0
No Voltage steel pole |  |  | 22 | 7 | 817 | 3254 | 0 | 12372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 11 | 4 | 4 | 20 | 4.1594 | 17.6773 | 17.6773 | 18.7171 | 5.1992 | 10.3984 | 25.996 | 18.7171 | 15.5976 | 22.8765 | 57.1912 | 57.1912 | 44.7131 | 73.8287 | 67.5896 | 87.3466 | 140.3785 | 178.8526 | 176.7729 | 253.7211 | 431.5339 | 682.1355 | 429.4542 | 725.8088 | 769.4821 | 534.4781 | 374.3426 | 513.6813 | 603.1076 | 427.3745 | 486 | 189 | 164 | 266 | 204 | 291 | 300 | 472 | 330 | 436 | 418 | 383 | 474 | 1116 |  |  | 0
No voltage wood poles |  | Stay poles, cross st poles | 49 | 15 | 629 | 3254 | 0 | 32471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 1 | 1 | 3 | 0 | 2 | 2 | 3 | 1 | 14 | 7 | 11 | 16 | 21 | 45 | 33 | 53 | 55 | 51 | 46 | 28 | 20 | 19 | 58 | 77 | 86 | 96 | 111 | 119 | 117 | 127 | 164 | 140 | 124 | 159 | 157 | 226 | 244 | 259 | 275 | 334 | 385 | 463 | 492 | 433 | 405 | 412 | 515.4261 | 455.7121 | 426.3789 | 435.8075 | 405.4267 | 507.0452 | 488.1882 | 542.6641 | 621.2352 | 648.4731 | 608.6638 | 727.0442 | 656.8541 | 743.806 | 811.9009 | 773.1392 | 920.8528 | 641.1398 | 766.8535 | 794.0915 | 798.282 | 933.4242 | 897.8053 | 1123.0423 | 991.043 | 780.4725 | 539.5213 | 604.4733 | 559.4259 | 545.807 | 480 | 361 | 420 | 357 | 263 | 365 | 456 | 444 | 407 | 516 | 439 | 379 | 528 | 886 |  |  | 0
Pole top structures
(Count all Slots with a External connections grouped by spec where the conductor is not a ABC cable, Service Cable or SL cable) AND (All DO without a External Connection) . With Spec table given to Bruce Caitens to multiply results out. Ages to be derived based on Pole Date. | bar: Year Commissioned (number of assets commissioned in each year) 2014
110kV Crossarms | DAVID | class confirmed - Steve 9-07-2013 | 40 | 6.32 | 38 | 28689 | 0 | 2598 | [106 empty] | 2598 | bar: Year Commissioned (number of assets commissioned in each year) 2014
33kV Crossarms | DAVID |  | 35 | 5.92 | 1439 | 3102 | 14 | 33160 | [106 empty] | 33160 | bar: Year Commissioned (number of assets commissioned in each year) 2014
11kV Crossarms | DAVID |  | 35 | 5.92 | 7667 | 2567 | 104 | 288476 | [106 empty] | 288476 | bar: Year Commissioned (number of assets commissioned in each year) 2014
LV Crossarms | DAVID |  | 35 | 5.92 | 8470 | 1579 | 163 | 254260 | [106 empty] | 254260 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Conductors
Conductor is sum of all conductor lengths grouped by circuit voltage No breakdown by material required confirmed | bar: Year Commissioned (number of assets commissioned in each year) 2014
132/110kV OH | DAVID |  | 70 | 8.36 | 9.7 | 758683 | 0 | 1173 | [106 empty] | 1173 | bar: Year Commissioned (number of assets commissioned in each year) 2014
33kV OH | DAVID |  | 70 | 8.36 | 82.63 | 147914.84 | 4 | 2130 | [106 empty] | 2130 | bar: Year Commissioned (number of assets commissioned in each year) 2014
11kV OH | DAVID |  | 70 | 8.36 | 75.4 | 132077 | 57 | 17529 | [106 empty] | 17529 | bar: Year Commissioned (number of assets commissioned in each year) 2014
LV OH | DAVID | excludes streetlight cables and services confirmed by Steve | 70 | 8.36 | 112.4 | 101324 | 32 | 14262 | [106 empty] | 14262 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Underground cables
Conductor is sum of all conductor lengths grouped by circuit voltage and submarine. | bar: Year Commissioned (number of assets commissioned in each year) 2014
Underground non submarine - 110kV /132kV | DAVID |  | 60 | 7.74 | 13 | 2026065 | 1 | 146 | [106 empty] | 146 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Underground non-submarine – 33kV / 66kV | DAVID |  | 47.1 | 7.8 | 26 | 985784 | 17 | 892 | [106 empty] | 892 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Underground submarine – 11kV | DAVID |  | 50 | 7.07 | 0 | 984431 | 0 | 5 | [106 empty] | 5 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Underground non-submarine – 11kV | DAVID |  | 50 | 7.07 | 168 | 521458.58 | 29 | 5285 | [106 empty] | 5285 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Underground non-submarine – LV | DAVID |  | 50 | 7.07 | 195 | 302975 | 73 | 10457 | [106 empty] | 10457 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Services
Overhead service assets | DH | Logic is based on MARS data and looks for NMIs that meet the below: • on the network or about to go on the network – e.g. Greenfield and a Retailer wants the site but not energized yet and • must have a supply type of overhead in MARS or a PPN that isn’t underground in MARS (e.g. not a site that starts with ‘U’) • The query also counts all unit complexes as one service cable – no matter how many NMIs are at the same combination of street number, road name, type and locality (e.g. many NMIs at the same address). | 40 | 6.32 | 7496 | 1100 | 849 | 576099 | [106 empty] | 576099 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Underground service assets (Pillars) | DH |  | 40 | 6.32 | 4327 | 4388 | 1509 | 259261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4677 | 37.6838 | 11.5145 | 242.8512 | 262.7399 | 47.1048 | 302.5172 | 174.811 | 383.1187 | 323.4527 | 508.7314 | 820.6695 | 1191.227 | 695.0569 | 535.9475 | 860.4469 | 659.4666 | 991.2934 | 1192.2737 | 3073.3237 | 4177.6686 | 5173.1491 | 7249.9455 | 9884.6716 | 10925.1633 | 12920.3115 | 7244.7116 | 6840.6575 | 7342.0615 | 15530.9618 | 9779 | 7069 | 37599 | 8707 | 12060 | 13134 | 10461 | 11962 | 11501 | 10492 | 7585 | 7742 | 7227 | 4327 |  |  | 0
Transformers
132/110kV power transformer : 33kV, >100MVA | SAM | voltage is from connected circuit. | 42.3 | 7.3 | 0 | 2609103.89 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 |  |  | 0
132/110kV power transformer : 33kV, ≤100MVA | SAM |  | 42.3 | 7.3 | 3 | 2263407.36 | 2 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 2 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 3 | 4 | 5 | 6 | 0 | 1 | 5 | 6 | 1 | 0 | 0 |  |  | 0
132/110kV power transformer :11/22kV, ≤60MVA | SAM |  | 42.3 | 7.3 | 5 | 1978801.91 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 3 | 2 | 7 | 2 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 2 | 5 | 10 | 11 | 2 | 3 | 0 | 3 | 1 | 0 | 0 |  |  | 0
33kV power transformer : 11/22/3.3/5.5/6.6kV, ≤15MVA | SAM |  | 49 | 12.3 | 7 | 931017.59 | 1 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 4 | 3 | 1 | 1 | 2 | 1 | 1 | 1 | 5 | 4 | 4 | 10 | 9 | 6 | 4 | 5 | 2 | 8 | 3 | 5 | 4 | 4 | 8 | 9 | 1 | 1 | 1 | 10 | 5 | 3 | 4 | 0 | 1 | 4 | 0 | 4 | 0 | 0 | 1 | 0 | 5 | 1 | 0 | 1 | 1 | 4 | 14 | 6 | 6 | 14 | 6 | 4 | 1 | 0 | 9 | 10 | 0 | 1 | 0 |  |  | 0
33/66kV power transformer : 11/22kV, >15MVA and ≤40MVA (Only 1 x 66kV 30MVA) | SAM |  | 49 | 12.3 | 13 | 1128100.1 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 2 | 4 | 0 | 4 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | 2 | 0 | 0 | 0 | 7 | 3 | 2 | 3 | 30 | 30 | 27 | 12 | 6 | 17 | 20 | 1 | 2 | 0 |  |  | 0
33 kV pole mounted transformer : ≥50 kVA and <315 kVA (including surge arrestors and drop out fuses) |  |  | 37.4 | 17.02 | 0 | 49219.96 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2.15 | 1.075 | 3.225 | 1.075 | 3.225 | 4.3 | 5.375 | 5.375 | 11.825 | 5.375 | 5.375 | 3.225 | 1.075 | 9.675 | 2.15 | 2.15 | 0 | 8.6 | 2.15 | 6.45 | 0 | 0 | 1.075 | 0 | 0 | 1.075 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 0
33 kV pole mounted transformer : ≥315 kVA (including surge arrestors and drop out fuses) |  |  | 37.4 | 17 | 0 | 49219.96 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  |  | 0
33 kV padmounted or ground transformer : ≥315 kVA |  |  | 50 | 7.07 | 0 | 199235.52 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 10 | 9 | 2 | 0 | 7 | 4 | 2 | 0 | 2 | 2 | 0 | 0 |  |  | 0
11 kV pole mounted transformer : <50 kVA (including surge arrestors and drop out fuses) | SAM |  | 30.9 | 13 | 284 | 9810 | 78 | 10418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 3 | 2 | 3 | 5 | 11 | 20 | 25 | 27 | 41 | 55 | 32 | 56 | 56 | 69 | 61.8854 | 54.7838 | 60.8709 | 67.9725 | 77.1031 | 109.5676 | 104.495 | 141.0176 | 182.6127 | 219.1352 | 289.1368 | 312.4706 | 330.7319 | 593.4913 | 221.1643 | 55.7983 | 335.8045 | 108.5531 | 246.5272 | 318.5577 | 154.2063 | 259.7158 | 282.0352 | 146.0902 | 218.1207 | 243.4836 | 235.3675 | 65.9435 | 238.411 | 205.9466 | 190 | 258 | 230 | 201 | 294 | 388 | 432 | 247 | 397 | 351 | 434 | 215 | 261 | 168 |  |  | 0
11 kV pole mounted transformer : ≥50 kVA and <315 kVA (including surge arrestors and drop out fuses) | SAM |  | 31.1 | 11.1 | 634 | 14025 | 143 | 16110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 5 | 6 | 2 | 3 | 4 | 5 | 4 | 2 | 2 | 5 | 9 | 11 | 10 | 13 | 28 | 34 | 30 | 59 | 51 | 56.398 | 79.375 | 67.8865 | 77.2862 | 123.2401 | 144.1283 | 119.0625 | 138.9062 | 130.551 | 152.4836 | 335.2549 | 362.4095 | 425.074 | 858.5033 | 534.7368 | 92.9523 | 498.1826 | 152.4836 | 315.4112 | 487.7385 | 295.5674 | 345.699 | 448.051 | 200.5263 | 274.6793 | 362.4095 | 402.097 | 111.7516 | 291.3898 | 370.7648 | 336 | 460 | 455 | 369 | 427 | 674 | 601 | 527 | 662 | 808 | 846 | 491 | 509 | 392 |  |  | 0
11 kV pole mounted transformer : ≥315 kVA (including surge arrestors and drop out fuses) | SAM |  | 35 | 5.91 | 335 | 31031 | 79 | 6649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0357 | 1.0357 | 1.0357 | 8.2857 | 4.1429 | 7.25 | 10.3571 | 30.0357 | 27.9643 | 0 | 31.0714 | 14.5 | 19.6786 | 55.9286 | 32.1071 | 21.75 | 21.75 | 10.3571 | 50.75 | 111.8571 | 104.6071 | 85.9643 | 131.5357 | 203 | 119 | 216 | 192 | 193 | 407 | 862 | 668 | 435 | 741 | 579 | 392 | 351 | 302 | 206 |  |  | 0
11 kV padmounted or ground transformer : ≥50 kVA and <315 kVA | SAM |  | 29.4 | 10.4 | 4 | 50080 | 1 | 1861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 3 | 7 | 5 | 3 | 3 | 5 | 4 | 7 | 4 | 6 | 7 | 12 | 8 | 5 | 10 | 9 | 14 | 12.2825 | 9.2119 | 9.2119 | 12.2825 | 9.2119 | 18.4238 | 9.2119 | 23.5415 | 18.4238 | 30.7063 | 41.9653 | 67.5539 | 102.3544 | 270.2156 | 14.3296 | 12.2825 | 74.7187 | 71.6481 | 109.5192 | 118.7311 | 90.0719 | 88.0248 | 77.7893 | 53.2243 | 82.9071 | 80.86 | 71.6481 | 55.2714 | 9.2119 | 7.1648 | 26 | 12 | 13 | 17 | 15 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
11 kV padmounted or ground transformer : ≥315 kVA | SAM |  | 23 | 11.1 | 482 | 199236 | 41 | 12217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 2 | 5 | 4 | 1 | 4 | 6 | 4 | 0 | 5 | 3 | 5 | 12 | 11 | 12 | 12 | 3.1172 | 21.8201 | 14.5468 | 18.703 | 12.4686 | 21.8201 | 29.0935 | 23.8982 | 18.703 | 34.2888 | 56.1089 | 115.335 | 152.741 | 316.9115 | 57.148 | 88.3196 | 196.3812 | 150.6628 | 222.3576 | 152.741 | 104.9445 | 59.2261 | 47.7965 | 34.2888 | 115.335 | 120.5303 | 143.3895 | 126.7646 | 180.7954 | 259.7635 | 289 | 265 | 258 | 391 | 489 | 818 | 1020 | 916 | 1226 | 1235 | 824 | 750 | 551 | 189 |  |  | 0
11 kV SWER transformer | SAM |  | 20.28 | 4.5 | 0 | 32256.26 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8947 | 0 | 0 | 0 | 1.0526 | 1.0526 | 0 | 0 | 1 | 0 | 4 | 0 | 1 | 0 | 4 | 2 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 0
11 kV pole mounted individual non-substation line regulator | SAM | slot_type cd of RG or TR-RG | 35 | 5.91 | 48 | 76614.44 | 9 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.75 | 0 | 2.75 | 6.875 | 0 | 1.375 | 9.625 | 2.75 | 0 | 4.125 | 2.75 | 5.5 | 9.625 | 17.875 | 12 | 13 | 5 | 6 | 5 | 25 | 24 | 17 | 82 | 46 | 30 | 32 | 57 | 15 |  |  | 0
33 kV substation regulator | SAM |  | 49 | 12.3 | 0 | 1128100.1 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 0
11kV Regulator - substation | SAM |  | 35 | 5.9 | 0 | 931017.59 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
Switchgear (including associated current and voltage transformers)
132/110 kV outdoor non-GIS circuit breaker | DAVID |  | 55 | 7.42 | 9 | 474552.32 | 1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 1.75 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
132/110 kV outdoor GIS circuit breaker | DAVID |  | 55 | 7.4 | 10 | 535946.69 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0833 | 0 | 0 | 24.3333 | 0 | 12.1667 | 0 | 0 | 0 | 18.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0833 | 6.0833 | 2 | 4 | 1 | 14 | 2 | 0 | 7 | 8 | 20 | 20 | 13 | 10 | 0 | 3 |  |  | 0
132/110 kV indoor GIS circuit breaker | DAVID |  | 55 | 7.4 | 1 | 513645.88 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5 | 0 | 0 | 0 | 7 | 0 | 9 | 29 | 3 | 19 | 0 | 0 | 0 | 0 | 0 |  |  | 0
66/33 kV outdoor circuit breaker (Only 1 x 66 kV) | DAVID |  | 44.7 | 9.4 | 7 | 206918.34 | 2 | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 1 | 11 | 17 | 0 | 2 | 11 | 5 | 15 | 6 | 18 | 26 | 9 | 31 | 6.9441 | 24.3042 | 12.7308 | 28.9336 | 23.1469 | 17.3601 | 12.7308 | 32.4056 | 11.5734 | 8.1014 | 4.6294 | 0 | 1.1573 | 18.5175 | 1.1573 | 11.5734 | 0 | 0 | 2.3147 | 35.8776 | 0 | 1.1573 | 11.5734 | 17.3601 | 4.6294 | 23.1469 | 0 | 12.7308 | 0 | 6.9441 | 42 | 24 | 1 | 8 | 6 | 18 | 16 | 11 | 28 | 25 | 8 | 1 | 10 | 0 |  |  | 0
33 kV indoor circuit breaker | DAVID |  | 44.7 | 9.4 | 46 | 157204.05 | 0 | 799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.3333 | 0 | 0 | 14.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5556 | 10.6667 | 0 | 7.1111 | 16 | 48 | 4 | 13 | 37 | 10 | 136 | 133 | 15 | 141 | 96 | 32 | 4 | 18 | 0 |  |  | 0
33 kV substation recloser | DAVID |  | 44.7 | 9.4 | 10 | 85702 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 13 | 3 | 10 | 5 | 2 | 2 | 5 | 3 | 5 | 4 | 5 | 1 |  |  | 0
11 kV outdoor circuit breaker including reclosers in substations | DAVID |  | 42.9 | 7.8 | 15 | 109402.63 | 1 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 6 | 2.2885 | 6.8654 | 0 | 6.8654 | 0 | 11.4423 | 1.1442 | 0 | 0 | 1.1442 | 0 | 0 | 9.1538 | 2.2885 | 12.5865 | 0 | 0 | 20.5962 | 4.5769 | 24.0288 | 0 | 0 | 0 | 0 | 0 | 5.7212 | 0 | 4.5769 | 0 | 5.7212 | 1 | 3 | 19 | 4 | 7 | 10 | 13 | 1 | 10 | 1 | 6 | 15 | 8 | 0 |  |  | 0
11 kV indoor circuit breaker | DAVID |  | 42.9 | 7.8 | 162 | 94746.51 | 3 | 3953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 35 | 19 | 0 | 30 | 50 | 51 | 13 | 27 | 91.4402 | 119.2195 | 84.4954 | 50.9287 | 5.7874 | 52.0862 | 56.7161 | 61.3459 | 105.3298 | 0 | 24.3069 | 42.8264 | 99.5425 | 128.4792 | 197.9275 | 103.0149 | 82.1804 | 10.4172 | 92.5976 | 49.7712 | 60.1885 | 34.7241 | 47.4563 | 20.8345 | 45.1414 | 90.2827 | 1.1575 | 23.1494 | 35.8816 | 49.7712 | 82 | 53 | 17 | 150 | 92 | 244 | 392 | 33 | 272 | 319 | 124 | 38 | 37 | 2 |  |  | 0
33 kV pole mounted air break switch not in substations | DAVID |  | 15.63 | 14.28 | 5 | 85702.27 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 5 | 4 | 0 | 2 | 4 | 4 | 4 | 11 | 4 | 12 | 6 | 19 | 15 | 5 |  |  | 0
11 kV pole mounted air break switch not in substations | DAVID |  | 28.96 | 25.77 | 1353 | 18208.22 | 30 | 8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 6 | 2 | 1 | 4 | 8 | 8 | 12 | 95.1952 | 11.1994 | 23.5188 | 12.3194 | 5.5997 | 23.5188 | 21.2789 | 17.9191 | 3126.8815 | 41.4379 | 38.0781 | 42.5578 | 53.7573 | 87.3556 | 125.4336 | 207.1895 | 256.467 | 212.7892 | 170.2314 | 238.5479 | 307.9844 | 359.5018 | 204.9496 | 165.7516 | 104.1547 | 91.8353 | 58.237 | 96.3151 | 36.9581 | 75.0362 | 254 | 19 | 43 | 31 | 37 | 70 | 182 | 317 | 274 | 275 | 175 | 186 | 222 | 417 |  |  | 0
11 kV pole mounted load break switch or load transfer switch or sectionaliser | DAVID |  | 30 | 5.5 | 1537 | 10158 | 6 | 6082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 3 | 0 | 0 | 3 | 9 | 1 | 12 | 4 | 3 | 2 | 2 | 0 | 8.2311 | 18.5201 | 72.9359 | 286.2699 | 634.9282 | 953.3285 | 1253.6161 | 1406.7993 | 1404.3709 |  |  | 0
11 kV pole mounted recloser | DAVID |  | 30 | 5.47 | 218 | 15797.69 | 1 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5082 | 0 | 0 | 0 | 12.541 | 5.0164 | 7.5246 | 7.5246 | 0 | 7.5246 | 110.3607 | 12 | 19 | 11 | 6 | 109 | 11 | 44 | 117 | 43 | 133 | 0 | 86 | 39 | 128 |  |  | 0
33 kV pole mounted recloser | DAVID |  | 30 | 5.47 | 7 | 85702 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1 | 6 | 1 | 0 | 1 | 0 | 1 | 8 | 0 | 1 |  |  | 0
11 kV RMU not in padmount sites | DAVID |  | 19.99 | 13.64 | 192 | 98238.41 | 1 | 3512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.4874 | 0 | 0 | 1.4874 | 1.4874 | 0 | 0 | 0 | 22.3103 | 2.9747 | 1.4874 | 5.9494 | 5.9494 | 8.9241 | 16.3609 | 26.7723 | 133.8617 | 7.4368 | 5.9494 | 101.14 | 65.4435 | 38.6712 | 34.2091 | 26.7723 | 68.4182 | 56.5194 | 77.3423 | 35.6965 | 74.3676 | 60.9815 | 85 | 88 | 38 | 81 | 90 | 200 | 233 | 278 | 526 | 357 | 252 | 208 | 151 | 42 |  |  | 0
11 kV RMU in padmount sites | DAVID |  | 12.45 | 4.16 | 173 | 63028.21 | 4 | 9846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8745 | 1.8745 | 5.6235 | 0 | 35.6158 | 18.7451 | 35.6158 | 16.8706 | 29.9922 | 1.8745 | 7.4981 | 52.4864 | 37.4903 | 22.4942 | 61.859 | 101.2238 | 1.8745 | 41.2393 | 1.8745 | 63.7335 | 138.7141 | 161.2083 | 157.4592 | 127.467 | 146.2122 | 178.0789 | 298 | 155 | 183 | 286 | 580 | 944 | 878 | 773 | 1001 | 1181 | 824 | 723 | 388 | 182 |  |  | 0
SCADA and protection
0 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Protection relays | NOT US |  | 32.47 | 10.67 | 273 | 43600.81 | 84 | 18448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 4 | 0 | 0 | 0 | 15 | 9 | 21 | 75 | 122 | 79 | 69 | 172 | 138 | 85 | 104 | 197 | 192 | 71 | 107 | 189 | 138 | 201 | 140 | 56 | 128 | 138 | 171 | 251 | 408 | 694 | 376 | 327 | 215 | 317 | 200 | 142 | 153 | 122 | 137 | 164 | 87 | 147 | 224 | 485 | 352 | 378 | 292 | 723 | 635 | 954 | 767 | 909 | 1126 | 1002 | 2531 | 927 | 778 |  |  | 0
SCADA Data Unit (RTU) | NOT US |  | 15 | 3.87 |  | 162947 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 |  |  | 263
Pilot cables - copper | NOT US |  | 45 | 6.7 |  | 226960 | 0 | 808.6005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 3.15 | 0 | 2.334 | 0.77 | 1.5 | 1.804 | 3.949 | 0.72 | 13.338 | 0.3 | 9.499 | 17.153 | 25.217 | 10.992 | 81.536 | 22.022 | 49.097 | 1.82 | 16.013 | 2.35 | 12.978 | 15.572 | 8.493 | 0.35 | 19.346 | 64.15 | 93.13 | 16.57 | 0 | 11.36 | 18.5 | 0.2 | 9.2 | 2.37 | 8.033 | 1.4 | 120.8165 | 7.796 | 2.94 | 1.112 | 5.11 | 4.45 | 1.5 | 0 | 0.15 | 0 | 5.86 | 13.8 | 1.16 | 25.125 | 1.95 | 2.55 | 3.9 | 2.1 | 8.52 | 9.12 | 10.5 | 14.375 | 0.3 | 2.95 | 0 |  |  | 14
Pilot cables - fibre optic | NOT US |  | 45 | 6.7 |  | 164230 | 0 | 2190.2691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.514 | 0 | 2.5 | 0 | 0.5 | 0 | 0 | 0 | 0 | 16.747 | 64.409 | 39.702 | 17.233 | 20.726 | 37.646 | 100.726 | 25.181 | 93.88 | 41.172 | 63.6611 | 49.795 | 110.097 | 75.2862 | 89.5885 | 252.955 | 263.4012 | 7.1 | 65.086 | 22.363 |  |  | 729
Remote monitoring units (SICMS, SICM1 and SICM2B) | NOT US |  | 15 | 4 |  | 19028 | 0 | 4012 | [106 empty] | 4012 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Other
Streetlights | SAM | Rates 1 & 2 only as per Gary 9-07-2013 | 20 | 4.4721 | 67593 | 70 | 275 | 300841 | [106 empty] | 300841
Capacitor bank 110/132kV | Sam |  | 45 | 6.7 | 1 | 815304 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  |  | 10
Capacitor bank 33kV | Sam |  | 45 | 6.7 | 0 | 319593.75 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9231 | 11.5385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9231 | 0 | 0 | 0 | 0 | 1.9231 | 7.6923 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 5 | 6 | 0 | 2 | 0 | 0 |  |  | 0
Capacitor bank 11kV | Sam |  | 45 | 6.7 | 11 | 277146.87 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1339 | 55.1181 | 0 | 11.0236 | 2.7559 | 5.5118 | 19.2913 | 1.378 | 9.6457 | 1.378 | 1.378 | 34.4488 | 20.6693 | 1.378 | 2.7559 | 2.7559 | 1.378 | 10 | 10 | 51 | 0 | 7 | 7 | 34 | 20 | 23 | 41 | 21 | 6 | 4 | 0 |  |  | 0
Voltage transformer 110/132kV where these are not included in switchgear | David | 3 per slot | 33 | 7.9 | 1 | 143595.24 | 0 | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | 0 | 0 | 9 |  |  | 0
Voltage transformer 66/33 kV where these are not included in switchgear | David | 1 per slot (Only 1 x 66 kV VT) | 35.1 | 9.6 | 0 | 119767.58 | 1 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6111 | 6.3056 | 25.2222 | 6.3056 | 0 | 50.4444 | 0 | 12.6111 | 0 | 37.8333 | 6.3056 | 12.6111 | 12.6111 | 25.2222 | 0 | 0 | 0 | 0 | 6.3056 | 6.3056 | 0 | 0 | 6.3056 | 29 | 7 | 2 | 5 | 1 | 2 | 4 | 0 | 2 | 2 | 1 | 1 | 2 | 2 |  |  | 0
Current transformer 110/132kV where these are not included in switchgear | David |  | 33.6 | 16.5 | 0 | 186955.73 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 6 | 0 | 12 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 10 | 3 | 15 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 4 | 3 | 0 | 10 | 0 | 0 | 0 | 0 | 3 | 10 | 1 | 0 | 0 | 18 | 0 | 3 | 27 | 0 | 3 | 0 | 21 | 3 | 0 | 12 | 0 | 3 | 0 |  |  | 0
Audio frequency load control (AFLC) equipment | Sam | AF. Count and install 33 and 11 kv - ok to roll together?? - shouldn't be any 33kv. Pull out details for Gary | 29.55 | 9.94 | 7 | 189399.29 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 1 | 4 | 3.76 | 3.76 | 16.92 | 28.2 | 5.64 | 1.88 | 11.28 | 0 | 15.04 | 0 | 5.64 | 3.76 | 1.88 | 0 | 7.52 | 13.16 | 20.68 | 7.52 | 5.64 | 9.4 | 24.44 | 0 | 0 | 0 | 24.44 | 7.52 | 3.76 | 11.28 | 0 | 1.88 | 8 | 2 | 8 | 13 | 4 | 15 | 14 | 3 | 10 | 9 | 7 | 1 | 1 | 0 |  |  | 0
Substation DC battery bank (Lead Acid) | Sam | Voltage breakdown if possible, if not leave it together | 5 | 2.23 | 68 | 2758 | 23 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 127 | 122 | 96 | 85 | 70 | 68 |  |  | 0
Substation DC battery bank (Ni Cad) |  |  | 25 | 4 | 13 | 3245 | 2 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 7 | 9 | 11 | 9 | 6 | 12 | 9 | 8 | 9 | 10 | 9 | 5 | 13 | 9 | 9 | 10 | 8 | 2 | 1 | 5 | 2 | 1 | 3 | 7 | 13 |  |  | 0
Substation DC battery charger | Sam | Voltage breakdown if possible, if not leave it together | 40 | 6.3246 | 11 | 6076 | 1 | 856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 1 | 18 | 2 | 0 | 0 | 15 | 0 | 11 | 0 | 4 | 8 | 30 | 13 | 8 | 7 | 33 | 9 | 3 | 25 | 8 | 13 | 12 | 13 | 15 | 17 | 35 | 13 | 1 | 2 | 2 | 10 | 22 | 30 | 19 | 43 | 29 | 9 | 10 | 17 | 4 | 2 | 6 | 7 | 7 | 19 | 13 | 29 | 5 | 10 | 21 | 17 | 17 | 9 | 32 | 33 | 9 | 15 | 24 | 25 | 14 | 9 | 5 | 11 |  |  | 0
Substation neutral earthing resistor | Sam | (NER) Slot_type NR or NR-NP. Voltages include 11, 6.6, 33 Also 1 NR-NP exists. Roll in or separarte class or data error?? | 26.7 | 0.6 | 0 | 75501 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0333 | 0 | 0 | 0 | 0 | 0 | 2.0333 | 12.2 | 16.2667 | 8.1333 | 14.2333 | 2.0333 | 2.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
Substation neutral earthing reactor | Sam | (NEX) - NX and RX as per DP | 26.7 | 0.6 | 0 | 75501.11 | 0 | 331 | [106 empty] | 331 | bar: Year Commissioned (number of assets commissioned in each year) 2014
Substation earthing transformer | Sam | ET Confirmed. 77 of 108 only with connections or non-customer. There is also a non-plant ET cf TR-ET however there are none currently installed | 31.57 | 5.6187 | 4 | 110424.41 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5714 | 0 | 2.1429 | 4.2857 | 15 | 2.1429 | 4.2857 | 2.1429 | 4.2857 | 4.2857 | 4.2857 | 2.1429 | 0 | 0 | 0 | 0 | 4.2857 | 0 | 0 | 0 | 2.1429 | 1 | 2 | 0 | 0 | 2 | 15 | 17 | 3 | 3 | 1 | 1 | 2 | 1 | 0 |  |  | 0
Contents
Note on CJ84: David Pennington: RE - 18
Note on CK84: David Pennington: RE - 4
Note on CL84: David Pennington: RE - 18 CB - 3

## 1c.STPIS DailyP(v1) DO NOT USE
Energex
STPIS Data Reporting |  |  |  | 2012-07-01
2012-13 |  |  |  | 2013-07-01
Daily Performance |  |  |  | 2014-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Daily performance data (Unplanned SAIDI, Unplanned SAIFI)
Note: the excluded events to be removed from the data refer only to events listed in clause 3.3(a) of the STPIS, with respect to reliability data, and in clause 5.4(a) of the STPIS with respect to customer service parameters.
Customer service
Date | Network SAIDI all events total | Network SAIDI all events after removing excluded events | CBD SAIDI all events total | CBD SAIDI all events after removing excluded events | Urban SAIDI all events total | Urban SAIDI all events after removing excluded events | Long rural SAIDI all events total | Long rural all events after removing excluded events | Short rural SAIDI all events total | Short rural SAIDI all events after removing excluded events | Network SAIFI all events total | Network SAIFI all events after removing excluded events | CBD SAIFI all events total | CBD SAIFI all events after removing excluded events | Urban SAIFI all events total | Urban SAIFI all events after removing excluded events | Long rural SAIFI all events total | Long rural SAIFI all events after removing excluded events | Short rural SAIFI all events total | Short Rural SAIFI all events after removing excluded events | Total number of calls (after removing excluded events) | Total number of calls answered in 30 seconds (after removing excluded events) | MED
2012-07-01 | 0.011006 | 0.011006 | 0 | 0 | 0.0021267 | 0.0021267 |  |  | 0.037622 | 0.037622 | 0.00011222 | 0.00011222 | 0 | 0 | 2.7758e-05 | 2.7758e-05 |  |  | 0.00036548 | 0.00036548 | 106 | 103 | NO
2012-07-02 | 0.12043 | 0.12043 | 0 | 0 | 0.15417 | 0.15417 |  |  | 0.021006 | 0.021006 | 0.0022344 | 0.0022344 | 0 | 0 | 0.0028911 | 0.0028911 |  |  | 0.00029855 | 0.00029855 | 296 | 243.2 | NO
2012-07-03 | 0.15906 | 0.15906 | 0 | 0 | 0.023197 | 0.023197 |  |  | 0.56702 | 0.56702 | 0.0023855 | 0.0023855 | 0 | 0 | 0.00023428 | 0.00023428 |  |  | 0.0088432 | 0.0088432 | 279 | 246.4 | NO
2012-07-04 | 0.029897 | 0.029897 | 0 | 0 | 0.027723 | 0.027723 |  |  | 0.03674 | 0.03674 | 0.00047257 | 0.00047257 | 0 | 0 | 0.00050315 | 0.00050315 |  |  | 0.00038638 | 0.00038638 | 274 | 240.6 | NO
2012-07-05 | 0.14499 | 0.14499 | 0 | 0 | 0.02264 | 0.02264 |  |  | 0.5126 | 0.5126 | 0.0099091 | 0.0099091 | 0 | 0 | 0.0013204 | 0.0013204 |  |  | 0.035712 | 0.035712 | 396 | 312.4 | NO
2012-07-06 | 0.20694 | 0.20694 | 0 | 0 | 0.276 | 0.276 |  |  | 0.0027923 | 0.0027923 | 0.0024288 | 0.0024288 | 0 | 0 | 0.0032421 | 0.0032421 |  |  | 2.3901e-05 | 2.3901e-05 | 382 | 285.6 | NO
2012-07-07 | 0.0062019 | 0.0062019 | 0 | 0 | 0.0026985 | 0.0026985 |  |  | 0.016744 | 0.016744 | 0.00012744 | 0.00012744 | 0 | 0 | 0.00010291 | 0.00010291 |  |  | 0.00020217 | 0.00020217 | 205 | 172.8 | NO
2012-07-08 | 0.085257 | 0.085257 | 0 | 0 | 0.080528 | 0.080528 |  |  | 0.10034 | 0.10034 | 0.00097467 | 0.00097467 | 0 | 0 | 0.00089532 | 0.00089532 |  |  | 0.0012227 | 0.0012227 | 157 | 145.4 | NO
2012-07-09 | 0.0081026 | 0.0081026 | 0 | 0 | 0.0090145 | 0.0090145 |  |  | 0.0054715 | 0.0054715 | 0.00010972 | 0.00010972 | 0 | 0 | 0.00012092 | 0.00012092 |  |  | 7.7536e-05 | 7.7536e-05 | 379 | 350.6 | NO
2012-07-10 | 0.020532 | 0.020532 | 0 | 0 | 0.012575 | 0.012575 |  |  | 0.044495 | 0.044495 | 0.00043392 | 0.00043392 | 0 | 0 | 0.00048083 | 0.00048083 |  |  | 0.00029887 | 0.00029887 | 276 | 256.4 | NO
2012-07-11 | 0.11786 | 0.11786 | 0 | 0 | 0.036151 | 0.036151 |  |  | 0.36278 | 0.36278 | 0.0019881 | 0.0019881 | 0 | 0 | 0.00080115 | 0.00080115 |  |  | 0.0055489 | 0.0055489 | 282 | 260 | NO
2012-07-12 | 0.20179 | 0.20179 | 0 | 0 | 0.15218 | 0.15218 |  |  | 0.35184 | 0.35184 | 0.0023006 | 0.0023006 | 0 | 0 | 0.0016313 | 0.0016313 |  |  | 0.0043206 | 0.0043206 | 318 | 277.6 | NO
2012-07-13 | 0.053906 | 0.053906 | 0 | 0 | 0.041927 | 0.041927 |  |  | 0.09018 | 0.09018 | 0.0007176 | 0.0007176 | 0 | 0 | 0.00062289 | 0.00062289 |  |  | 0.0010077 | 0.0010077 | 284 | 250.2 | NO
2012-07-14 | 0.20266 | 0.20266 | 0 | 0 | 0.17857 | 0.17857 |  |  | 0.27662 | 0.27662 | 0.0019674 | 0.0019674 | 0 | 0 | 0.0019669 | 0.0019669 |  |  | 0.0019911 | 0.0019911 | 248 | 182.4 | NO
2012-07-15 | 0.067762 | 0.067762 | 0 | 0 | 0.081794 | 0.081794 |  |  | 0.026784 | 0.026784 | 0.0010459 | 0.0010459 | 0 | 0 | 0.0013395 | 0.0013395 |  |  | 0.00018442 | 0.00018442 | 160 | 142.6 | NO
2012-07-16 | 0.069062 | 0.069062 | 0 | 0 | 0.034254 | 0.034254 |  |  | 0.1733 | 0.1733 | 0.00085364 | 0.00085364 | 0 | 0 | 0.00045383 | 0.00045383 |  |  | 0.0020517 | 0.0020517 | 292 | 256.6 | NO
2012-07-17 | 0.065611 | 0.065611 | 0 | 0 | 0.049981 | 0.049981 |  |  | 0.11277 | 0.11277 | 0.0018507 | 0.0018507 | 0 | 0 | 0.0010401 | 0.0010401 |  |  | 0.0042794 | 0.0042794 | 278 | 244 | NO
2012-07-18 | 0.017586 | 0.017586 | 0 | 0 | 0.0071202 | 0.0071202 |  |  | 0.04885 | 0.04885 | 0.00019362 | 0.00019362 | 0 | 0 | 9.6217e-05 | 9.6217e-05 |  |  | 0.00048492 | 0.00048492 | 236 | 215.2 | NO
2012-07-19 | 0.026824 | 0.026824 | 0 | 0 | 0.030518 | 0.030518 |  |  | 0.016166 | 0.016166 | 0.00038667 | 0.00038667 | 0 | 0 | 0.00048913 | 0.00048913 |  |  | 8.7044e-05 | 8.7044e-05 | 214 | 180.4 | NO
2012-07-20 | 0.13945 | 0.13945 | 0 | 0 | 0.043298 | 0.043298 |  |  | 0.42592 | 0.42592 | 0.0026364 | 0.0026364 | 0 | 0 | 0.00039952 | 0.00039952 |  |  | 0.0092942 | 0.0092942 | 247 | 221.2 | NO
2012-07-21 | 0.077782 | 0.077782 | 0 | 0 | 0.10163 | 0.10163 |  |  | 0.0080575 | 0.0080575 | 0.0014165 | 0.0014165 | 0 | 0 | 0.0016652 | 0.0016652 |  |  | 0.00069626 | 0.00069626 | 145 | 130.2 | NO
2012-07-22 | 0.14085 | 0.14085 | 0 | 0 | 0.10372 | 0.10372 |  |  | 0.25222 | 0.25222 | 0.0025099 | 0.0025099 | 0 | 0 | 0.0023172 | 0.0023172 |  |  | 0.0031079 | 0.0031079 | 161 | 132 | NO
2012-07-23 | 0.082039 | 0.082039 | 0 | 0 | 0.073907 | 0.073907 |  |  | 0.10698 | 0.10698 | 0.00050876 | 0.00050876 | 0 | 0 | 0.00052215 | 0.00052215 |  |  | 0.00047483 | 0.00047483 | 221 | 184.2 | NO
2012-07-24 | 0.034524 | 0.034524 | 0 | 0 | 0.043553 | 0.043553 |  |  | 0.008263 | 0.008263 | 0.00056405 | 0.00056405 | 0 | 0 | 0.0006071 | 0.0006071 |  |  | 0.00044329 | 0.00044329 | 233 | 220.2 | NO
2012-07-25 | 0.081811 | 0.081811 | 0 | 0 | 0.034834 | 0.034834 |  |  | 0.22117 | 0.22117 | 0.00091972 | 0.00091972 | 0 | 0 | 0.00071597 | 0.00071597 |  |  | 0.0015304 | 0.0015304 | 236 | 193.8 | NO
2012-07-26 | 0.038311 | 0.038311 | 0 | 0 | 0.050835 | 0.050835 |  |  | 0.0018751 | 0.0018751 | 0.0010205 | 0.0010205 | 0 | 0 | 0.001367 | 0.001367 |  |  | 1.1798e-05 | 1.1798e-05 | 188 | 182 | NO
2012-07-27 | 0.18619 | 0.18619 | 0 | 0 | 0.2461 | 0.2461 |  |  | 0.012134 | 0.012134 | 0.003465 | 0.003465 | 0 | 0 | 0.0046026 | 0.0046026 |  |  | 0.00015941 | 0.00015941 | 198 | 181.4 | NO
2012-07-28 | 0.27437 | 0.27437 | 0 | 0 | 0.0064366 | 0.0064366 |  |  | 1.0642 | 1.0642 | 0.0065355 | 0.0065355 | 0 | 0 | 8.522e-05 | 8.522e-05 |  |  | 0.02555 | 0.02555 | 252 | 214 | NO
2012-07-29 | 0.059248 | 0.059248 | 0 | 0 | 0.054866 | 0.054866 |  |  | 0.072756 | 0.072756 | 0.0016137 | 0.0016137 | 0 | 0 | 0.0017258 | 0.0017258 |  |  | 0.0013031 | 0.0013031 | 160 | 117.4 | NO
2012-07-30 | 0.030037 | 0.030037 | 0 | 0 | 0.0047003 | 0.0047003 |  |  | 0.10457 | 0.10457 | 0.0020372 | 0.0020372 | 0 | 0 | 0.00013156 | 0.00013156 |  |  | 0.0076408 | 0.0076408 | 231 | 213.6 | NO
2012-07-31 | 0.06766 | 0.06766 | 0 | 0 | 0.089932 | 0.089932 |  |  | 0.0032624 | 0.0032624 | 0.0010583 | 0.0010583 | 0 | 0 | 0.0014082 | 0.0014082 |  |  | 4.6461e-05 | 4.6461e-05 | 273 | 259 | NO
2012-08-01 | 0.11051 | 0.11051 | 0 | 0 | 0.14786 | 0.14786 |  |  | 0.0026209 | 0.0026209 | 0.0011122 | 0.0011122 | 0 | 0 | 0.0014905 | 0.0014905 |  |  | 1.9351e-05 | 1.9351e-05 | 193 | 185 | NO
2012-08-02 | 0.050663 | 0.050663 | 0 | 0 | 0.016523 | 0.016523 |  |  | 0.1508 | 0.1508 | 0.00062536 | 0.00062536 | 0 | 0 | 0.00064232 | 0.00064232 |  |  | 0.00058278 | 0.00058278 | 219 | 210 | NO
2012-08-03 | 0.36375 | 0.36375 | 0 | 0 | 0.22908 | 0.22908 |  |  | 0.76003 | 0.76003 | 0.0035013 | 0.0035013 | 0 | 0 | 0.001527 | 0.001527 |  |  | 0.0092903 | 0.0092903 | 351 | 296.4 | NO
2012-08-04 | 0.016409 | 0.016409 | 0 | 0 | 0.0073302 | 0.0073302 |  |  | 0.043032 | 0.043032 | 0.0017369 | 0.0017369 | 0 | 0 | 0.0015626 | 0.0015626 |  |  | 0.0022639 | 0.0022639 | 183 | 169.4 | NO
2012-08-05 | 0.32158 | 0.32158 | 0 | 0 | 0.40385 | 0.40385 |  |  | 0.085542 | 0.085542 | 0.004327 | 0.004327 | 0 | 0 | 0.0053991 | 0.0053991 |  |  | 0.0012527 | 0.0012527 | 209 | 183.2 | NO
2012-08-06 | 0.64872 | 0.64872 | 0 | 0 | 0.75144 | 0.75144 |  |  | 0.35678 | 0.35678 | 0.009995 | 0.009995 | 0 | 0 | 0.011608 | 0.011608 |  |  | 0.0054085 | 0.0054085 | 379 | 321.4 | NO
2012-08-07 | 0.040951 | 0.040951 | 0 | 0 | 0.025494 | 0.025494 |  |  | 0.086411 | 0.086411 | 0.00094729 | 0.00094729 | 0 | 0 | 0.00022885 | 0.00022885 |  |  | 0.0030497 | 0.0030497 | 272 | 256.6 | NO
2012-08-08 | 0.1538 | 0.1538 | 0 | 0 | 0.026664 | 0.026664 |  |  | 0.52572 | 0.52572 | 0.0032863 | 0.0032863 | 0 | 0 | 0.0013937 | 0.0013937 |  |  | 0.0088338 | 0.0088338 | 249 | 232.6 | NO
2012-08-09 | 0.41912 | 0.41912 | 0 | 0 | 0.44496 | 0.44496 |  |  | 0.34847 | 0.34847 | 0.0031356 | 0.0031356 | 0 | 0 | 0.0022677 | 0.0022677 |  |  | 0.0056976 | 0.0056976 | 274 | 232.4 | NO
2012-08-10 | 0.32074 | 0.32074 | 0 | 0 | 0.1857 | 0.1857 |  |  | 0.71748 | 0.71748 | 0.008009 | 0.008009 | 0 | 0 | 0.0047561 | 0.0047561 |  |  | 0.017569 | 0.017569 | 348 | 311.6 | NO
2012-08-11 | 0.10928 | 0.10928 | 0 | 0 | 0.13084 | 0.13084 |  |  | 0.047714 | 0.047714 | 0.00124 | 0.00124 | 0 | 0 | 0.0016315 | 0.0016315 |  |  | 0.000114 | 0.000114 | 185 | 157.8 | NO
2012-08-12 | 0.029878 | 0.029878 | 0 | 0 | 0.0014085 | 0.0014085 |  |  | 0.11307 | 0.11307 | 0.00045419 | 0.00045419 | 0 | 0 | 1.4057e-05 | 1.4057e-05 |  |  | 0.0017403 | 0.0017403 | 159 | 148.4 | NO
2012-08-13 | 0.046793 | 0.046793 | 0 | 0 | 0.051376 | 0.051376 |  |  | 0.03397 | 0.03397 | 0.00094797 | 0.00094797 | 0 | 0 | 0.00084255 | 0.00084255 |  |  | 0.0012652 | 0.0012652 | 249 | 237 | NO
2012-08-14 | 0.024411 | 0.024411 | 0 | 0 | 0.0012885 | 0.0012885 |  |  | 0.09196 | 0.09196 | 0.00035041 | 0.00035041 | 0 | 0 | 1.7068e-05 | 1.7068e-05 |  |  | 0.0013242 | 0.0013242 | 207 | 204.2 | NO
2012-08-15 | 0.007306 | 0.007306 | 0 | 0 | 0.0053351 | 0.0053351 |  |  | 0.01312 | 0.01312 | 6.9735e-05 | 6.9735e-05 | 0 | 0 | 6.2844e-05 | 6.2844e-05 |  |  | 9.0549e-05 | 9.0549e-05 | 155 | 150.2 | NO
2012-08-16 | 0.083366 | 0.083366 | 0 | 0 | 0.068286 | 0.068286 |  |  | 0.12815 | 0.12815 | 0.0028721 | 0.0028721 | 0 | 0 | 0.0022759 | 0.0022759 |  |  | 0.0046381 | 0.0046381 | 210 | 186.6 | NO
2012-08-17 | 0.021384 | 0.021384 | 0 | 0 | 0.022613 | 0.022613 |  |  | 0.018044 | 0.018044 | 0.00089151 | 0.00089151 | 0 | 0 | 0.0011445 | 0.0011445 |  |  | 0.00016552 | 0.00016552 | 193 | 178.6 | NO
2012-08-18 | 0.0051455 | 0.0051455 | 0 | 0 | 0.00096383 | 0.00096383 |  |  | 0.017363 | 0.017363 | 0.00028102 | 0.00028102 | 0 | 0 | 9.0357e-06 | 9.0357e-06 |  |  | 0.0010751 | 0.0010751 | 158 | 136.4 | NO
2012-08-19 | 0.050513 | 0.050513 | 0 | 0 | 0.067326 | 0.067326 |  |  | 0.0021836 | 0.0021836 | 0.00055321 | 0.00055321 | 0 | 0 | 0.00073954 | 0.00073954 |  |  | 1.7515e-05 | 1.7515e-05 | 114 | 105.4 | NO
2012-08-20 | 0.2906 | 0.2906 | 0 | 0 | 0.2016 | 0.2016 |  |  | 0.55254 | 0.55254 | 0.003416 | 0.003416 | 0 | 0 | 0.0020254 | 0.0020254 |  |  | 0.0074964 | 0.0074964 | 299 | 228.6 | NO
2012-08-21 | 0.037684 | 0.037684 | 0 | 0 | 0.049955 | 0.049955 |  |  | 0.0024309 | 0.0024309 | 0.00079678 | 0.00079678 | 0 | 0 | 0.0010599 | 0.0010599 |  |  | 4.0855e-05 | 4.0855e-05 | 236 | 228.4 | NO
2012-08-22 | 0.015278 | 0.015278 | 0.0083774 | 0.0083774 | 0.017343 | 0.017343 |  |  | 0.0093503 | 0.0093503 | 0.0022949 | 0.0022949 | 0.00026525 | 0.00026525 | 0.0030186 | 0.0030186 |  |  | 0.00021404 | 0.00021404 | 195 | 175.2 | NO
2012-08-23 | 0.15578 | 0.15578 | 0 | 0 | 0.051904 | 0.051904 |  |  | 0.4593 | 0.4593 | 0.0039025 | 0.0039025 | 0 | 0 | 0.0018507 | 0.0018507 |  |  | 0.0099072 | 0.0099072 | 265 | 239.6 | NO
2012-08-24 | 0.096181 | 0.096181 | 0 | 0 | 0.014301 | 0.014301 |  |  | 0.33509 | 0.33509 | 0.0007521 | 0.0007521 | 0 | 0 | 0.00011646 | 0.00011646 |  |  | 0.0026068 | 0.0026068 | 257 | 235.6 | NO
2012-08-25 | 0.023951 | 0.023951 | 0 | 0 | 0.024914 | 0.024914 |  |  | 0.021417 | 0.021417 | 0.00083977 | 0.00083977 | 0 | 0 | 0.0010337 | 0.0010337 |  |  | 0.00028573 | 0.00028573 | 146 | 134.4 | NO
2012-08-26 | 0.071707 | 0.071707 | 0 | 0 | 0.087526 | 0.087526 |  |  | 0.026576 | 0.026576 | 0.0012301 | 0.0012301 | 0 | 0 | 0.001603 | 0.001603 |  |  | 0.00016104 | 0.00016104 | 103 | 103 | NO
2012-08-27 | 0.032281 | 0.032281 | 0 | 0 | 0.018213 | 0.018213 |  |  | 0.073456 | 0.073456 | 0.00042189 | 0.00042189 | 0 | 0 | 0.00018933 | 0.00018933 |  |  | 0.0011013 | 0.0011013 | 212 | 197 | NO
2012-08-28 | 0.028563 | 0.028563 | 0 | 0 | 0.037934 | 0.037934 |  |  | 0.0017003 | 0.0017003 | 0.00061632 | 0.00061632 | 0 | 0 | 0.00082414 | 0.00082414 |  |  | 2.0387e-05 | 2.0387e-05 | 220 | 199.6 | NO
2012-08-29 | 0.087599 | 0.087599 | 0 | 0 | 0.1041 | 0.1041 |  |  | 0.040719 | 0.040719 | 0.002221 | 0.002221 | 0 | 0 | 0.0029279 | 0.0029279 |  |  | 0.00019637 | 0.00019637 | 202 | 186.4 | NO
2012-08-30 | 0.51874 | 0.51874 | 0 | 0 | 0.45861 | 0.45861 |  |  | 0.69867 | 0.69867 | 0.0045318 | 0.0045318 | 0 | 0 | 0.00353 | 0.00353 |  |  | 0.0074844 | 0.0074844 | 216 | 200.6 | NO
2012-08-31 | 0.053628 | 0.053628 | 0 | 0 | 0.040155 | 0.040155 |  |  | 0.093235 | 0.093235 | 0.0010893 | 0.0010893 | 0 | 0 | 0.00027702 | 0.00027702 |  |  | 0.0034535 | 0.0034535 | 230 | 196 | NO
2012-09-01 | 0.071791 | 0.071791 | 0 | 0 | 0.029277 | 0.029277 |  |  | 0.19563 | 0.19563 | 0.0024618 | 0.0024618 | 0 | 0 | 0.0018012 | 0.0018012 |  |  | 0.0044009 | 0.0044009 | 153 | 146.2 | NO
2012-09-02 | 0.01663 | 0.01663 | 0 | 0 | 0.0099866 | 0.0099866 |  |  | 0.036033 | 0.036033 | 0.00018867 | 0.00018867 | 0 | 0 | 0.0001224 | 0.0001224 |  |  | 0.00038244 | 0.00038244 | 116 | 104.8 | NO
2012-09-03 | 0.084938 | 0.084938 | 0 | 0 | 0.10043 | 0.10043 |  |  | 0.041083 | 0.041083 | 0.0011493 | 0.0011493 | 0 | 0 | 0.001361 | 0.001361 |  |  | 0.0005498 | 0.0005498 | 266 | 196 | NO
2012-09-04 | 0.036423 | 0.036423 | 0 | 0 | 0.0065991 | 0.0065991 |  |  | 0.12301 | 0.12301 | 0.00023045 | 0.00023045 | 0 | 0 | 0.00011382 | 0.00011382 |  |  | 0.00057005 | 0.00057005 | 204 | 178.4 | NO
2012-09-05 | 0.042128 | 0.042128 | 0 | 0 | 0.010022 | 0.010022 |  |  | 0.13533 | 0.13533 | 0.0012599 | 0.0012599 | 0 | 0 | 0.00017478 | 0.00017478 |  |  | 0.0044083 | 0.0044083 | 197 | 189.2 | NO
2012-09-06 | 0.023029 | 0.023029 | 0 | 0 | 0.030253 | 0.030253 |  |  | 0.0024229 | 0.0024229 | 0.0013911 | 0.0013911 | 0 | 0 | 0.0018732 | 0.0018732 |  |  | 1.4508e-05 | 1.4508e-05 | 196 | 191 | NO
2012-09-07 | 0.062391 | 0.062391 | 0 | 0 | 0.048002 | 0.048002 |  |  | 0.1046 | 0.1046 | 0.00078406 | 0.00078406 | 0 | 0 | 0.00084327 | 0.00084327 |  |  | 0.00062178 | 0.00062178 | 208 | 183.4 | NO
2012-09-08 | 0.019878 | 0.019878 | 0 | 0 | 0.026494 | 0.026494 |  |  | 0.0010122 | 0.0010122 | 0.00015883 | 0.00015883 | 0 | 0 | 0.00021148 | 0.00021148 |  |  | 8.6982e-06 | 8.6982e-06 | 133 | 126.2 | NO
2012-09-09 | 0.020847 | 0.020847 | 0 | 0 | 0.014212 | 0.014212 |  |  | 0.040202 | 0.040202 | 0.00027759 | 0.00027759 | 0 | 0 | 0.00014472 | 0.00014472 |  |  | 0.00066371 | 0.00066371 | 95 | 87.2 | NO
2012-09-10 | 0.24664 | 0.24664 | 0 | 0 | 0.31675 | 0.31675 |  |  | 0.047299 | 0.047299 | 0.0039431 | 0.0039431 | 0 | 0 | 0.0051775 | 0.0051775 |  |  | 0.00042913 | 0.00042913 | 213 | 202 | NO
2012-09-11 | 0.13897 | 0.13897 | 0 | 0 | 0.0037352 | 0.0037352 |  |  | 0.53001 | 0.53001 | 0.0022988 | 0.0022988 | 0 | 0 | 3.5192e-05 | 3.5192e-05 |  |  | 0.0088439 | 0.0088439 | 220 | 213.6 | NO
2012-09-12 | 0.05729 | 0.05729 | 0 | 0 | 0.071684 | 0.071684 |  |  | 0.016474 | 0.016474 | 0.001135 | 0.001135 | 0 | 0 | 0.0014673 | 0.0014673 |  |  | 0.00019049 | 0.00019049 | 175 | 173.2 | NO
2012-09-13 | 0.024482 | 0.024482 | 0 | 0 | 0.012673 | 0.012673 |  |  | 0.058733 | 0.058733 | 0.00028341 | 0.00028341 | 0 | 0 | 0.00022822 | 0.00022822 |  |  | 0.00044534 | 0.00044534 | 207 | 189.8 | NO
2012-09-14 | 0.2027 | 0.2027 | 0 | 0 | 0.24485 | 0.24485 |  |  | 0.083646 | 0.083646 | 0.0032599 | 0.0032599 | 0 | 0 | 0.0029268 | 0.0029268 |  |  | 0.0042535 | 0.0042535 | 539 | 419.6 | NO
2012-09-15 | 0.21412 | 0.21412 | 0 | 0 | 0.014499 | 0.014499 |  |  | 0.79032 | 0.79032 | 0.0013873 | 0.0013873 | 0 | 0 | 0.00012205 | 0.00012205 |  |  | 0.00504 | 0.00504 | 142 | 132.4 | NO
2012-09-16 | 0.15911 | 0.15911 | 0 | 0 | 0.17207 | 0.17207 |  |  | 0.12361 | 0.12361 | 0.0024929 | 0.0024929 | 0 | 0 | 0.002076 | 0.002076 |  |  | 0.0037178 | 0.0037178 | 145 | 136.2 | NO
2012-09-17 | 0.055545 | 0.055545 | 0 | 0 | 0.02661 | 0.02661 |  |  | 0.13925 | 0.13925 | 0.00073305 | 0.00073305 | 0 | 0 | 0.00011484 | 0.00011484 |  |  | 0.0025166 | 0.0025166 | 266 | 237.4 | NO
2012-09-18 | 0.057444 | 0.057444 | 0 | 0 | 0.075615 | 0.075615 |  |  | 0.0059049 | 0.0059049 | 0.00090407 | 0.00090407 | 0 | 0 | 0.0012144 | 0.0012144 |  |  | 2.3106e-05 | 2.3106e-05 | 260 | 239.4 | NO
2012-09-19 | 0.13422 | 0.13422 | 0 | 0 | 0.083738 | 0.083738 |  |  | 0.28053 | 0.28053 | 0.0011076 | 0.0011076 | 0 | 0 | 0.00049388 | 0.00049388 |  |  | 0.0028807 | 0.0028807 | 237 | 228.4 | NO
2012-09-20 | 0.060467 | 0.060467 | 0 | 0 | 0.025537 | 0.025537 |  |  | 0.16129 | 0.16129 | 0.00086141 | 0.00086141 | 0 | 0 | 0.00038285 | 0.00038285 |  |  | 0.0022431 | 0.0022431 | 206 | 184.4 | NO
2012-09-21 | 0.31328 | 0.31328 | 0 | 0 | 0.14552 | 0.14552 |  |  | 0.79746 | 0.79746 | 0.0029738 | 0.0029738 | 0 | 0 | 0.0016486 | 0.0016486 |  |  | 0.0068043 | 0.0068043 | 315 | 274 | NO
2012-09-22 | 0.32379 | 0.32379 | 0 | 0 | 0.058077 | 0.058077 |  |  | 1.0884 | 1.0884 | 0.0035232 | 0.0035232 | 0 | 0 | 0.00094641 | 0.00094641 |  |  | 0.010943 | 0.010943 | 220 | 197 | NO
2012-09-23 | 0.065733 | 0.065733 | 0 | 0 | 0.00024278 | 0.00024278 |  |  | 0.25394 | 0.25394 | 0.00057905 | 0.00057905 | 0 | 0 | 3.0174e-06 | 3.0174e-06 |  |  | 0.0022345 | 0.0022345 | 88 | 85.2 | NO
2012-09-24 | 1.0441 | 1.0441 | 0 | 0 | 0.70855 | 0.70855 |  |  | 2.0156 | 2.0156 | 0.0096794 | 0.0096794 | 0 | 0 | 0.0071621 | 0.0071621 |  |  | 0.016988 | 0.016988 | 567 | 469.2 | NO
2012-09-25 | 0.013393 | 0.013393 | 0 | 0 | 0.0070503 | 0.0070503 |  |  | 0.031683 | 0.031683 | 0.0001532 | 0.0001532 | 0 | 0 | 9.446e-05 | 9.446e-05 |  |  | 0.00032291 | 0.00032291 | 282 | 262.6 | NO
2012-09-26 | 0.14923 | 0.14923 | 0 | 0 | 0.19813 | 0.19813 |  |  | 0.010984 | 0.010984 | 0.00082356 | 0.00082356 | 0 | 0 | 0.0010609 | 0.0010609 |  |  | 0.00015385 | 0.00015385 | 264 | 234.8 | NO
2012-09-27 | 0.081516 | 0.081516 | 0 | 0 | 0.10845 | 0.10845 |  |  | 0.0053765 | 0.0053765 | 0.0011492 | 0.0011492 | 0 | 0 | 0.0015183 | 0.0015183 |  |  | 0.00010636 | 0.00010636 | 178 | 158.8 | NO
2012-09-28 | 0.026405 | 0.026405 | 0 | 0 | 0.031933 | 0.031933 |  |  | 0.010889 | 0.010889 | 0.00072349 | 0.00072349 | 0 | 0 | 0.0008782 | 0.0008782 |  |  | 0.00028912 | 0.00028912 | 227 | 209.4 | NO
2012-09-29 | 0.24855 | 0.24855 | 0 | 0 | 0.008212 | 0.008212 |  |  | 0.93813 | 0.93813 | 0.0040783 | 0.0040783 | 0 | 0 | 0.0001126 | 0.0001126 |  |  | 0.015456 | 0.015456 | 192 | 165.8 | NO
2012-09-30 | 0.020944 | 0.020944 | 0 | 0 | 0.013727 | 0.013727 |  |  | 0.041794 | 0.041794 | 0.00020703 | 0.00020703 | 0 | 0 | 0.00015871 | 0.00015871 |  |  | 0.00034736 | 0.00034736 | 89 | 87 | NO
2012-10-01 | 0.0011358 | 0.0011358 | 0 | 0 | 0.00087516 | 0.00087516 |  |  | 0.0018929 | 0.0018929 | 1.2134e-05 | 1.2134e-05 | 0 | 0 | 9.0426e-06 | 9.0426e-06 |  |  | 2.1097e-05 | 2.1097e-05 | 115 | 111.4 | NO
2012-10-02 | 0.2083 | 0.2083 | 0 | 0 | 0.18675 | 0.18675 |  |  | 0.27213 | 0.27213 | 0.0023403 | 0.0023403 | 0 | 0 | 0.0022396 | 0.0022396 |  |  | 0.0026534 | 0.0026534 | 260 | 212.8 | NO
2012-10-03 | 0.11969 | 0.11969 | 0 | 0 | 0.1589 | 0.1589 |  |  | 0.0090107 | 0.0090107 | 0.0021528 | 0.0021528 | 0 | 0 | 0.0028896 | 0.0028896 |  |  | 7.1719e-05 | 7.1719e-05 | 282 | 233.2 | NO
2012-10-04 | 0.12208 | 0.12208 | 0 | 0 | 0.10336 | 0.10336 |  |  | 0.17688 | 0.17688 | 0.0027855 | 0.0027855 | 0 | 0 | 0.003548 | 0.003548 |  |  | 0.00063819 | 0.00063819 | 228 | 195.8 | NO
2012-10-05 | 0.079588 | 0.079588 | 0 | 0 | 0.057207 | 0.057207 |  |  | 0.1444 | 0.1444 | 0.0026633 | 0.0026633 | 0 | 0 | 0.0012644 | 0.0012644 |  |  | 0.0066893 | 0.0066893 | 238 | 217.6 | NO
2012-10-06 | 0.055371 | 0.055371 | 0 | 0 | 0.02221 | 0.02221 |  |  | 0.15075 | 0.15075 | 0.00092488 | 0.00092488 | 0 | 0 | 0.00085113 | 0.00085113 |  |  | 0.0011457 | 0.0011457 | 163 | 141.2 | NO
2012-10-07 | 0.018189 | 0.018189 | 0 | 0 | 0.0040036 | 0.0040036 |  |  | 0.05894 | 0.05894 | 0.00018441 | 0.00018441 | 0 | 0 | 4.8423e-05 | 4.8423e-05 |  |  | 0.00057518 | 0.00057518 | 138 | 132.2 | NO
2012-10-08 | 0.070534 | 0.070534 | 0 | 0 | 0.083473 | 0.083473 |  |  | 0.034305 | 0.034305 | 0.0042022 | 0.0042022 | 0 | 0 | 0.0014751 | 0.0014751 |  |  | 0.012046 | 0.012046 | 225 | 211.2 | NO
2012-10-09 | 0.19493 | 0.19493 | 0 | 0 | 0.25367 | 0.25367 |  |  | 0.029035 | 0.029035 | 0.0034675 | 0.0034675 | 0 | 0 | 0.0046021 | 0.0046021 |  |  | 0.00025981 | 0.00025981 | 233 | 207.8 | NO
2012-10-10 | 0.067437 | 0.067437 | 0 | 0 | 0.058506 | 0.058506 |  |  | 0.09373 | 0.09373 | 0.0018774 | 0.0018774 | 0 | 0 | 0.0021748 | 0.0021748 |  |  | 0.001047 | 0.001047 | 249 | 223 | NO
2012-10-11 | 0.60481 | 0.60481 | 0 | 0 | 0.41452 | 0.41452 |  |  | 1.156 | 1.156 | 0.0078866 | 0.0078866 | 0 | 0 | 0.0051156 | 0.0051156 |  |  | 0.015903 | 0.015903 | 448 | 370 | NO
2012-10-12 | 0.21356 | 0.21356 | 0 | 0 | 0.21164 | 0.21164 |  |  | 0.2214 | 0.2214 | 0.0020728 | 0.0020728 | 0 | 0 | 0.0021693 | 0.0021693 |  |  | 0.0018193 | 0.0018193 | 460 | 342.8 | NO
2012-10-13 | 0.22674 | 0.22674 | 0 | 0 | 0.11842 | 0.11842 |  |  | 0.53937 | 0.53937 | 0.002736 | 0.002736 | 0 | 0 | 0.0021131 | 0.0021131 |  |  | 0.0045497 | 0.0045497 | 192 | 165.6 | NO
2012-10-14 | 0.44799 | 0.44799 | 0 | 0 | 0.48353 | 0.48353 |  |  | 0.35111 | 0.35111 | 0.0038737 | 0.0038737 | 0 | 0 | 0.0044964 | 0.0044964 |  |  | 0.0021326 | 0.0021326 | 141 | 134.6 | NO
2012-10-15 | 0.042527 | 0.042527 | 0 | 0 | 0.014117 | 0.014117 |  |  | 0.12438 | 0.12438 | 0.00026208 | 0.00026208 | 0 | 0 | 0.00010871 | 0.00010871 |  |  | 0.00070432 | 0.00070432 | 231 | 203.2 | NO
2012-10-16 | 0.1305 | 0.1305 | 0 | 0 | 0.15366 | 0.15366 |  |  | 0.065583 | 0.065583 | 0.001552 | 0.001552 | 0 | 0 | 0.0012702 | 0.0012702 |  |  | 0.0023768 | 0.0023768 | 214 | 195.4 | NO
2012-10-17 | 0.012388 | 0.012388 | 0 | 0 | 0.011036 | 0.011036 |  |  | 0.016397 | 0.016397 | 0.00020975 | 0.00020975 | 0 | 0 | 0.00022159 | 0.00022159 |  |  | 0.00017812 | 0.00017812 | 183 | 174.4 | NO
2012-10-18 | 0.14868 | 0.14868 | 0 | 0 | 0.12029 | 0.12029 |  |  | 0.23171 | 0.23171 | 0.0025754 | 0.0025754 | 0 | 0 | 0.0019391 | 0.0019391 |  |  | 0.004428 | 0.004428 | 267 | 250.6 | NO
2012-10-19 | 0.04721 | 0.04721 | 0 | 0 | 0.059588 | 0.059588 |  |  | 0.012231 | 0.012231 | 0.00077099 | 0.00077099 | 0 | 0 | 0.00097498 | 0.00097498 |  |  | 0.00019445 | 0.00019445 | 268 | 251 | NO
2012-10-20 | 0.095089 | 0.095089 | 0 | 0 | 0.11211 | 0.11211 |  |  | 0.047297 | 0.047297 | 0.0011483 | 0.0011483 | 0 | 0 | 0.0013944 | 0.0013944 |  |  | 0.00045482 | 0.00045482 | 194 | 174.4 | NO
2012-10-21 | 0.29145 | 0.29145 | 0 | 0 | 0.27062 | 0.27062 |  |  | 0.35442 | 0.35442 | 0.0048989 | 0.0048989 | 0 | 0 | 0.0043066 | 0.0043066 |  |  | 0.006652 | 0.006652 | 170 | 157.2 | NO
2012-10-22 | 0.39259 | 0.39259 | 0 | 0 | 0.31589 | 0.31589 |  |  | 0.61708 | 0.61708 | 0.003329 | 0.003329 | 0 | 0 | 0.0031748 | 0.0031748 |  |  | 0.003808 | 0.003808 | 393 | 304.2 | NO
2012-10-23 | 0.32885 | 0.32885 | 0 | 0 | 0.43283 | 0.43283 |  |  | 0.033814 | 0.033814 | 0.0027682 | 0.0027682 | 0 | 0 | 0.0036012 | 0.0036012 |  |  | 0.00040632 | 0.00040632 | 415 | 358.6 | NO
2012-10-24 | 0.082862 | 0.082862 | 0 | 0 | 0.036474 | 0.036474 |  |  | 0.21704 | 0.21704 | 0.0012082 | 0.0012082 | 0 | 0 | 0.00025534 | 0.00025534 |  |  | 0.0039589 | 0.0039589 | 208 | 192 | NO
2012-10-25 | 0.010633 | 0.010633 | 0 | 0 | 0.0018694 | 0.0018694 |  |  | 0.035935 | 0.035935 | 0.00012897 | 0.00012897 | 0 | 0 | 3.0388e-05 | 3.0388e-05 |  |  | 0.00041369 | 0.00041369 | 191 | 186.4 | NO
2012-10-26 | 0.25724 | 0.25724 | 0 | 0 | 0.1355 | 0.1355 |  |  | 0.61006 | 0.61006 | 0.0042147 | 0.0042147 | 0 | 0 | 0.00187 | 0.00187 |  |  | 0.011002 | 0.011002 | 241 | 221 | NO
2012-10-27 | 0.18136 | 0.18136 | 0 | 0 | 0.1174 | 0.1174 |  |  | 0.36733 | 0.36733 | 0.0026937 | 0.0026937 | 0 | 0 | 0.0015375 | 0.0015375 |  |  | 0.0060487 | 0.0060487 | 232 | 199.4 | NO
2012-10-28 | 0.47184 | 0.47184 | 0 | 0 | 0.46158 | 0.46158 |  |  | 0.50656 | 0.50656 | 0.005623 | 0.005623 | 0 | 0 | 0.0045368 | 0.0045368 |  |  | 0.0088097 | 0.0088097 | 167 | 158.4 | NO
2012-10-29 | 0.04655 | 0.04655 | 0 | 0 | 0.01163 | 0.01163 |  |  | 0.14757 | 0.14757 | 0.0019519 | 0.0019519 | 0 | 0 | 0.00012268 | 0.00012268 |  |  | 0.0072383 | 0.0072383 | 272 | 260 | NO
2012-10-30 | 0.079377 | 0.079377 | 0 | 0 | 0.007036 | 0.007036 |  |  | 0.28853 | 0.28853 | 0.0014386 | 0.0014386 | 0 | 0 | 0.00011488 | 0.00011488 |  |  | 0.0052655 | 0.0052655 | 235 | 226.4 | NO
2012-10-31 | 0.089409 | 0.089409 | 0 | 0 | 0.11648 | 0.11648 |  |  | 0.012461 | 0.012461 | 0.0014727 | 0.0014727 | 0 | 0 | 0.0019413 | 0.0019413 |  |  | 0.00013943 | 0.00013943 | 228 | 215.6 | NO
2012-11-01 | 0.18744 | 0.18744 | 0 | 0 | 0.23767 | 0.23767 |  |  | 0.044889 | 0.044889 | 0.0039658 | 0.0039658 | 0 | 0 | 0.0052175 | 0.0052175 |  |  | 0.00040551 | 0.00040551 | 266 | 243.8 | NO
2012-11-02 | 0.62912 | 0.62912 | 0 | 0 | 0.28632 | 0.28632 |  |  | 1.6233 | 1.6233 | 0.016296 | 0.016296 | 0 | 0 | 0.01183 | 0.01183 |  |  | 0.029338 | 0.029338 | 367 | 297.6 | NO
2012-11-03 | 0.06632 | 0.06632 | 0 | 0 | 0.086451 | 0.086451 |  |  | 0.0090991 | 0.0090991 | 0.00084555 | 0.00084555 | 0 | 0 | 0.0011121 | 0.0011121 |  |  | 8.7639e-05 | 8.7639e-05 | 196 | 171.6 | NO
2012-11-04 | 0.0062412 | 0.0062412 | 0 | 0 | 0.00069486 | 0.00069486 |  |  | 0.022273 | 0.022273 | 5.871e-05 | 5.871e-05 | 0 | 0 | 8.99e-06 | 8.99e-06 |  |  | 0.00020246 | 0.00020246 | 86 | 84 | NO
2012-11-05 | 0.0023718 | 0.0023718 | 0 | 0 | 0.0016713 | 0.0016713 |  |  | 0.0044126 | 0.0044126 | 2.8991e-05 | 2.8991e-05 | 0 | 0 | 1.9201e-05 | 1.9201e-05 |  |  | 5.7464e-05 | 5.7464e-05 | 209 | 203.2 | NO
2012-11-06 | 0.1264 | 0.1264 | 0 | 0 | 0.012459 | 0.012459 |  |  | 0.45535 | 0.45535 | 0.0019888 | 0.0019888 | 0 | 0 | 4.459e-05 | 4.459e-05 |  |  | 0.0075997 | 0.0075997 | 233 | 214 | NO
2012-11-07 | 0.015788 | 0.015788 | 0 | 0 | 0.019502 | 0.019502 |  |  | 0.0052911 | 0.0052911 | 0.00017933 | 0.00017933 | 0 | 0 | 0.00022581 | 0.00022581 |  |  | 4.7718e-05 | 4.7718e-05 | 193 | 178.6 | NO
2012-11-08 | 0.23637 | 0.23637 | 0 | 0 | 0.1884 | 0.1884 |  |  | 0.37674 | 0.37674 | 0.0034684 | 0.0034684 | 0 | 0 | 0.0029702 | 0.0029702 |  |  | 0.0049373 | 0.0049373 | 310 | 264.2 | NO
2012-11-09 | 0.28751 | 0.28751 | 0 | 0 | 0.013919 | 0.013919 |  |  | 1.0762 | 1.0762 | 0.0026437 | 0.0026437 | 0 | 0 | 0.00020784 | 0.00020784 |  |  | 0.0096666 | 0.0096666 | 289 | 229.6 | NO
2012-11-10 | 0.89352 | 0.89352 | 0 | 0 | 0.60834 | 0.60834 |  |  | 1.7218 | 1.7218 | 0.0067495 | 0.0067495 | 0 | 0 | 0.0050432 | 0.0050432 |  |  | 0.01172 | 0.01172 | 322 | 239.6 | NO
2012-11-11 | 0.6754 | 0.6754 | 0 | 0 | 0.27861 | 0.27861 |  |  | 1.8214 | 1.8214 | 0.005136 | 0.005136 | 0 | 0 | 0.0028571 | 0.0028571 |  |  | 0.011732 | 0.011732 | 294 | 208.4 | NO
2012-11-12 | 0.080187 | 0.080187 | 0 | 0 | 0.046853 | 0.046853 |  |  | 0.17666 | 0.17666 | 0.00092628 | 0.00092628 | 0 | 0 | 0.00065125 | 0.00065125 |  |  | 0.0017251 | 0.0017251 | 259 | 238.4 | NO
2012-11-13 | 0.027587 | 0.027587 | 0 | 0 | 0.0075907 | 0.0075907 |  |  | 0.085211 | 0.085211 | 0.00088784 | 0.00088784 | 0 | 0 | 0.00011495 | 0.00011495 |  |  | 0.0031132 | 0.0031132 | 211 | 192.2 | NO
2012-11-14 | 0.039788 | 0.039788 | 0 | 0 | 0.052549 | 0.052549 |  |  | 0.0036546 | 0.0036546 | 0.0011503 | 0.0011503 | 0 | 0 | 0.0015492 | 0.0015492 |  |  | 2.0051e-05 | 2.0051e-05 | 172 | 171 | NO
2012-11-15 | 0.092439 | 0.092439 | 0 | 0 | 0.017051 | 0.017051 |  |  | 0.30942 | 0.30942 | 0.0011224 | 0.0011224 | 0 | 0 | 0.00016072 | 0.00016072 |  |  | 0.0038898 | 0.0038898 | 228 | 213.6 | NO
2012-11-16 | 0.010944 | 0.010944 | 0 | 0 | 0.014246 | 0.014246 |  |  | 0.0016076 | 0.0016076 | 0.00011438 | 0.00011438 | 0 | 0 | 0.00015074 | 0.00015074 |  |  | 1.1461e-05 | 1.1461e-05 | 258 | 248.6 | NO
2012-11-17 | 6.2383 | 6.2383 | 0 | 0 | 5.6508 | 5.6508 |  |  | 7.9884 | 7.9884 | 0.050737 | 0.050737 | 0 | 0 | 0.04905 | 0.04905 |  |  | 0.056123 | 0.056123 | 0 | 0 | Yes
2012-11-18 | 2.1418 | 2.1418 | 0 | 0 | 1.901 | 1.901 |  |  | 2.8545 | 2.8545 | 0.018704 | 0.018704 | 0 | 0 | 0.015464 | 0.015464 |  |  | 0.028183 | 0.028183 | 1096 | 601.8 | NO
2012-11-19 | 0.44702 | 0.44702 | 0 | 0 | 0.44834 | 0.44834 |  |  | 0.44811 | 0.44811 | 0.0062759 | 0.0062759 | 0 | 0 | 0.0061852 | 0.0061852 |  |  | 0.0066038 | 0.0066038 | 678 | 581.4 | NO
2012-11-20 | 0.14043 | 0.14043 | 0 | 0 | 0.17769 | 0.17769 |  |  | 0.035331 | 0.035331 | 0.0016946 | 0.0016946 | 0 | 0 | 0.0021896 | 0.0021896 |  |  | 0.00029637 | 0.00029637 | 377 | 337 | NO
2012-11-21 | 0.17904 | 0.17904 | 0 | 0 | 0.22777 | 0.22777 |  |  | 0.041575 | 0.041575 | 0.0063971 | 0.0063971 | 0 | 0 | 0.0068789 | 0.0068789 |  |  | 0.0050884 | 0.0050884 | 311 | 291.4 | NO
2012-11-22 | 0.097879 | 0.097879 | 0 | 0 | 0.035822 | 0.035822 |  |  | 0.27644 | 0.27644 | 0.0013602 | 0.0013602 | 0 | 0 | 0.0005637 | 0.0005637 |  |  | 0.0036532 | 0.0036532 | 379 | 308.4 | NO
2012-11-23 | 0.11956 | 0.11956 | 0 | 0 | 0.13222 | 0.13222 |  |  | 0.084655 | 0.084655 | 0.0023896 | 0.0023896 | 0 | 0 | 0.0026754 | 0.0026754 |  |  | 0.0015984 | 0.0015984 | 347 | 302 | NO
2012-11-24 | 0.38686 | 0.38686 | 0 | 0 | 0.52196 | 0.52196 |  |  | 0.0048618 | 0.0048618 | 0.0044866 | 0.0044866 | 0 | 0 | 0.0060554 | 0.0060554 |  |  | 5.0741e-05 | 5.0741e-05 | 249 | 213.4 | NO
2012-11-25 | 0.51576 | 0.51576 | 0 | 0 | 0.057875 | 0.057875 |  |  | 1.8299 | 1.8299 | 0.0042695 | 0.0042695 | 0 | 0 | 0.00018856 | 0.00018856 |  |  | 0.015979 | 0.015979 | 192 | 169.8 | NO
2012-11-26 | 0.02833 | 0.02833 | 0 | 0 | 0.011813 | 0.011813 |  |  | 0.075829 | 0.075829 | 0.00029963 | 0.00029963 | 0 | 0 | 0.00026291 | 0.00026291 |  |  | 0.00040779 | 0.00040779 | 251 | 228.4 | NO
2012-11-27 | 0.14122 | 0.14122 | 0 | 0 | 0.044314 | 0.044314 |  |  | 0.41957 | 0.41957 | 0.0022786 | 0.0022786 | 0 | 0 | 0.0015112 | 0.0015112 |  |  | 0.0044951 | 0.0044951 | 271 | 246.4 | NO
2012-11-28 | 0.22322 | 0.22322 | 0 | 0 | 0.058165 | 0.058165 |  |  | 0.69697 | 0.69697 | 0.0036303 | 0.0036303 | 0 | 0 | 0.00090975 | 0.00090975 |  |  | 0.011438 | 0.011438 | 266 | 237.6 | NO
2012-11-29 | 0.31443 | 0.31443 | 0 | 0 | 0.31052 | 0.31052 |  |  | 0.329 | 0.329 | 0.0035247 | 0.0035247 | 0 | 0 | 0.0032713 | 0.0032713 |  |  | 0.0042864 | 0.0042864 | 336 | 270.8 | NO
2012-11-30 | 0.37619 | 0.37619 | 0 | 0 | 0.39572 | 0.39572 |  |  | 0.32451 | 0.32451 | 0.007636 | 0.007636 | 0 | 0 | 0.0085501 | 0.0085501 |  |  | 0.0051089 | 0.0051089 | 328 | 271 | NO
2012-12-01 | 0.16656 | 0.16656 | 0 | 0 | 0.22251 | 0.22251 |  |  | 0.0085882 | 0.0085882 | 0.0010195 | 0.0010195 | 0 | 0 | 0.0013569 | 0.0013569 |  |  | 6.7086e-05 | 6.7086e-05 | 211 | 173.6 | NO
2012-12-02 | 0.13579 | 0.13579 | 0 | 0 | 0.15516 | 0.15516 |  |  | 0.081929 | 0.081929 | 0.0025119 | 0.0025119 | 0 | 0 | 0.0018184 | 0.0018184 |  |  | 0.0045194 | 0.0045194 | 152 | 139.8 | NO
2012-12-03 | 0.54476 | 0.54476 | 0 | 0 | 0.53469 | 0.53469 |  |  | 0.57942 | 0.57942 | 0.011465 | 0.011465 | 0 | 0 | 0.013526 | 0.013526 |  |  | 0.0057026 | 0.0057026 | 432 | 323.6 | NO
2012-12-04 | 0.46318 | 0.46318 | 0 | 0 | 0.50366 | 0.50366 |  |  | 0.35256 | 0.35256 | 0.0042079 | 0.0042079 | 0 | 0 | 0.004915 | 0.004915 |  |  | 0.0022336 | 0.0022336 | 527 | 409.2 | NO
2012-12-05 | 0.64821 | 0.64821 | 0 | 0 | 0.3377 | 0.3377 |  |  | 1.5423 | 1.5423 | 0.015772 | 0.015772 | 0 | 0 | 0.0088385 | 0.0088385 |  |  | 0.035752 | 0.035752 | 674 | 548 | NO
2012-12-06 | 0.13907 | 0.13907 | 0 | 0 | 0.16472 | 0.16472 |  |  | 0.067291 | 0.067291 | 0.0027162 | 0.0027162 | 0 | 0 | 0.0029261 | 0.0029261 |  |  | 0.0021457 | 0.0021457 | 343 | 317 | NO
2012-12-07 | 0.31127 | 0.31127 | 0 | 0 | 0.32677 | 0.32677 |  |  | 0.27034 | 0.27034 | 0.0036403 | 0.0036403 | 0 | 0 | 0.0038208 | 0.0038208 |  |  | 0.0031637 | 0.0031637 | 365 | 336.2 | NO
2012-12-08 | 0.08539 | 0.08539 | 0 | 0 | 0.085889 | 0.085889 |  |  | 0.084888 | 0.084888 | 0.001739 | 0.001739 | 0 | 0 | 0.0011391 | 0.0011391 |  |  | 0.0034721 | 0.0034721 | 248 | 213.6 | NO
2012-12-09 | 0.24954 | 0.24954 | 0 | 0 | 0.19624 | 0.19624 |  |  | 0.40458 | 0.40458 | 0.0020835 | 0.0020835 | 0 | 0 | 0.0023605 | 0.0023605 |  |  | 0.0013143 | 0.0013143 | 156 | 148.6 | NO
2012-12-10 | 0.34165 | 0.34165 | 0 | 0 | 0.209 | 0.209 |  |  | 0.72452 | 0.72452 | 0.0051978 | 0.0051978 | 0 | 0 | 0.0026787 | 0.0026787 |  |  | 0.012455 | 0.012455 | 296 | 250.8 | NO
2012-12-11 | 0.22814 | 0.22814 | 0.016455 | 0.016455 | 0.29782 | 0.29782 |  |  | 0.031216 | 0.031216 | 0.0027938 | 0.0027938 | 0.00026676 | 0.00026676 | 0.0036697 | 0.0036697 |  |  | 0.00031717 | 0.00031717 | 333 | 293.4 | NO
2012-12-12 | 0.077645 | 0.077645 | 0 | 0 | 0.091039 | 0.091039 |  |  | 0.04019 | 0.04019 | 0.0010968 | 0.0010968 | 0 | 0 | 0.0012812 | 0.0012812 |  |  | 0.00058123 | 0.00058123 | 250 | 232.6 | NO
2012-12-13 | 0.025299 | 0.025299 | 0 | 0 | 0.012127 | 0.012127 |  |  | 0.063237 | 0.063237 | 0.00070178 | 0.00070178 | 0 | 0 | 0.00030312 | 0.00030312 |  |  | 0.0018494 | 0.0018494 | 214 | 193.2 | NO
2012-12-14 | 0.31048 | 0.31048 | 0 | 0 | 0.20812 | 0.20812 |  |  | 0.60657 | 0.60657 | 0.0051864 | 0.0051864 | 0 | 0 | 0.0049736 | 0.0049736 |  |  | 0.005851 | 0.005851 | 306 | 240.2 | NO
2012-12-15 | 0.11956 | 0.11956 | 0 | 0 | 0.018875 | 0.018875 |  |  | 0.40879 | 0.40879 | 0.0015514 | 0.0015514 | 0 | 0 | 0.00024811 | 0.00024811 |  |  | 0.0052951 | 0.0052951 | 229 | 185.8 | NO
2012-12-16 | 0.085979 | 0.085979 | 0 | 0 | 0.047548 | 0.047548 |  |  | 0.19681 | 0.19681 | 0.0023735 | 0.0023735 | 0 | 0 | 0.0015432 | 0.0015432 |  |  | 0.0047733 | 0.0047733 | 148 | 131.2 | NO
2012-12-17 | 0.33549 | 0.33549 | 0 | 0 | 0.19597 | 0.19597 |  |  | 0.73806 | 0.73806 | 0.0055854 | 0.0055854 | 0 | 0 | 0.0027273 | 0.0027273 |  |  | 0.013818 | 0.013818 | 371 | 290.4 | NO
2012-12-18 | 0.4062 | 0.4062 | 0 | 0 | 0.34909 | 0.34909 |  |  | 0.57387 | 0.57387 | 0.0038015 | 0.0038015 | 0 | 0 | 0.0019014 | 0.0019014 |  |  | 0.0092757 | 0.0092757 | 559 | 465 | NO
2012-12-19 | 0.28736 | 0.28736 | 0 | 0 | 0.35868 | 0.35868 |  |  | 0.086528 | 0.086528 | 0.0052494 | 0.0052494 | 0 | 0 | 0.0066969 | 0.0066969 |  |  | 0.0011672 | 0.0011672 | 457 | 315.4 | NO
2012-12-20 | 0.058639 | 0.058639 | 0 | 0 | 0.076809 | 0.076809 |  |  | 0.0073177 | 0.0073177 | 0.001921 | 0.001921 | 0 | 0 | 0.0025535 | 0.0025535 |  |  | 0.00013308 | 0.00013308 | 303 | 252 | NO
2012-12-21 | 0.10638 | 0.10638 | 0 | 0 | 0.12034 | 0.12034 |  |  | 0.067601 | 0.067601 | 0.0019388 | 0.0019388 | 0 | 0 | 0.0018296 | 0.0018296 |  |  | 0.0022722 | 0.0022722 | 288 | 262 | NO
2012-12-22 | 0.26529 | 0.26529 | 0 | 0 | 0.062207 | 0.062207 |  |  | 0.84891 | 0.84891 | 0.0028812 | 0.0028812 | 0 | 0 | 0.00052311 | 0.00052311 |  |  | 0.0096554 | 0.0096554 | 241 | 206.4 | NO
2012-12-23 | 0.14298 | 0.14298 | 0 | 0 | 0.19286 | 0.19286 |  |  | 0.0018966 | 0.0018966 | 0.0017574 | 0.0017574 | 0 | 0 | 0.0023715 | 0.0023715 |  |  | 2.0151e-05 | 2.0151e-05 | 152 | 138 | NO
2012-12-24 | 0.091848 | 0.091848 | 0 | 0 | 0.050616 | 0.050616 |  |  | 0.21075 | 0.21075 | 0.001412 | 0.001412 | 0 | 0 | 0.0014607 | 0.0014607 |  |  | 0.0012881 | 0.0012881 | 177 | 167.4 | NO
2012-12-25 | 0.011869 | 0.011869 | 0 | 0 | 0.0128 | 0.0128 |  |  | 0.0093359 | 0.0093359 | 0.00015459 | 0.00015459 | 0 | 0 | 0.00017642 | 0.00017642 |  |  | 9.3827e-05 | 9.3827e-05 | 105 | 97.2 | NO
2012-12-26 | 0.30561 | 0.30561 | 0 | 0 | 0.17558 | 0.17558 |  |  | 0.68077 | 0.68077 | 0.0044378 | 0.0044378 | 0 | 0 | 0.0021098 | 0.0021098 |  |  | 0.011143 | 0.011143 | 204 | 193.4 | NO
2012-12-27 | 0.054456 | 0.054456 | 0 | 0 | 0.065889 | 0.065889 |  |  | 0.022345 | 0.022345 | 0.0021767 | 0.0021767 | 0 | 0 | 0.0028952 | 0.0028952 |  |  | 0.00014552 | 0.00014552 | 214 | 204.2 | NO
2012-12-28 | 0.25573 | 0.25573 | 0 | 0 | 0.12724 | 0.12724 |  |  | 0.62599 | 0.62599 | 0.0031239 | 0.0031239 | 0 | 0 | 0.0015046 | 0.0015046 |  |  | 0.0077889 | 0.0077889 | 262 | 243.8 | NO
2012-12-29 | 0.15025 | 0.15025 | 0 | 0 | 0.19448 | 0.19448 |  |  | 0.025385 | 0.025385 | 0.0014505 | 0.0014505 | 0 | 0 | 0.0018971 | 0.0018971 |  |  | 0.0001891 | 0.0001891 | 168 | 151.4 | NO
2012-12-30 | 0.096379 | 0.096379 | 0 | 0 | 0.011489 | 0.011489 |  |  | 0.34023 | 0.34023 | 0.0013249 | 0.0013249 | 0 | 0 | 0.00019803 | 0.00019803 |  |  | 0.0045623 | 0.0045623 | 184 | 147.4 | NO
2012-12-31 | 0.26927 | 0.26927 | 0 | 0 | 0.34383 | 0.34383 |  |  | 0.058932 | 0.058932 | 0.0032008 | 0.0032008 | 0 | 0 | 0.0036811 | 0.0036811 |  |  | 0.0018614 | 0.0018614 | 192 | 181.4 | NO
2013-01-01 | 0.0093194 | 0.0093194 | 0 | 0 | 0.010955 | 0.010955 |  |  | 0.0047401 | 0.0047401 | 0.00011863 | 0.00011863 | 0 | 0 | 0.00014562 | 0.00014562 |  |  | 4.2714e-05 | 4.2714e-05 | 122 | 308.6 | NO
2013-01-02 | 0.13707 | 0.13707 | 0 | 0 | 0.18063 | 0.18063 |  |  | 0.013945 | 0.013945 | 0.0012911 | 0.0012911 | 0 | 0 | 0.0016504 | 0.0016504 |  |  | 0.00027716 | 0.00027716 | 232 | 210 | NO
2013-01-03 | 0.17745 | 0.17745 | 0 | 0 | 0.2093 | 0.2093 |  |  | 0.088226 | 0.088226 | 0.0011642 | 0.0011642 | 0 | 0 | 0.0014666 | 0.0014666 |  |  | 0.00031172 | 0.00031172 | 198 | 179.4 | NO
2013-01-04 | 0.19141 | 0.19141 | 0 | 0 | 0.17321 | 0.17321 |  |  | 0.24553 | 0.24553 | 0.0027499 | 0.0027499 | 0 | 0 | 0.0021128 | 0.0021128 |  |  | 0.0046021 | 0.0046021 | 240 | 214 | NO
2013-01-05 | 0.066925 | 0.066925 | 0 | 0 | 0.087372 | 0.087372 |  |  | 0.0091491 | 0.0091491 | 0.0016292 | 0.0016292 | 0 | 0 | 0.0021576 | 0.0021576 |  |  | 0.00013506 | 0.00013506 | 154 | 139.4 | NO
2013-01-06 | 0.34425 | 0.34425 | 0 | 0 | 0.40021 | 0.40021 |  |  | 0.18788 | 0.18788 | 0.0043282 | 0.0043282 | 0 | 0 | 0.0051302 | 0.0051302 |  |  | 0.0020803 | 0.0020803 | 152 | 144.8 | NO
2013-01-07 | 0.15748 | 0.15748 | 0 | 0 | 0.019093 | 0.019093 |  |  | 0.55516 | 0.55516 | 0.0020522 | 0.0020522 | 0 | 0 | 0.00017196 | 0.00017196 |  |  | 0.0074544 | 0.0074544 | 250 | 231.4 | NO
2013-01-08 | 0.16198 | 0.16198 | 0 | 0 | 0.029857 | 0.029857 |  |  | 0.54178 | 0.54178 | 0.0020168 | 0.0020168 | 0 | 0 | 0.00071355 | 0.00071355 |  |  | 0.0057677 | 0.0057677 | 252 | 245.4 | NO
2013-01-09 | 0.39608 | 0.39608 | 0 | 0 | 0.22759 | 0.22759 |  |  | 0.88252 | 0.88252 | 0.0045293 | 0.0045293 | 0 | 0 | 0.0028548 | 0.0028548 |  |  | 0.0093701 | 0.0093701 | 379 | 341.6 | NO
2013-01-10 | 0.11413 | 0.11413 | 0 | 0 | 0.023973 | 0.023973 |  |  | 0.37336 | 0.37336 | 0.0010043 | 0.0010043 | 0 | 0 | 0.00025784 | 0.00025784 |  |  | 0.0031512 | 0.0031512 | 341 | 314 | NO
2013-01-11 | 0.094838 | 0.094838 | 0 | 0 | 0.066476 | 0.066476 |  |  | 0.17703 | 0.17703 | 0.010316 | 0.010316 | 0 | 0 | 0.012788 | 0.012788 |  |  | 0.0033551 | 0.0033551 | 351 | 337 | NO
2013-01-12 | 0.65964 | 0.65964 | 0 | 0 | 0.45344 | 0.45344 |  |  | 1.257 | 1.257 | 0.0094797 | 0.0094797 | 0 | 0 | 0.0055721 | 0.0055721 |  |  | 0.020766 | 0.020766 | 578 | 350.6 | NO
2013-01-13 | 0.18548 | 0.18548 | 0 | 0 | 0.203 | 0.203 |  |  | 0.13736 | 0.13736 | 0.0025475 | 0.0025475 | 0 | 0 | 0.0028459 | 0.0028459 |  |  | 0.0017213 | 0.0017213 | 273 | 246 | NO
2013-01-14 | 0.87039 | 0.87039 | 0 | 0 | 0.74449 | 0.74449 |  |  | 1.2402 | 1.2402 | 0.0056168 | 0.0056168 | 0 | 0 | 0.0044744 | 0.0044744 |  |  | 0.0089478 | 0.0089478 | 374 | 335 | NO
2013-01-15 | 0.35575 | 0.35575 | 0 | 0 | 0.4595 | 0.4595 |  |  | 0.062712 | 0.062712 | 0.0020316 | 0.0020316 | 0 | 0 | 0.002585 | 0.002585 |  |  | 0.00046997 | 0.00046997 | 282 | 268 | NO
2013-01-16 | 0.097892 | 0.097892 | 0 | 0 | 0.11989 | 0.11989 |  |  | 0.036003 | 0.036003 | 0.00084643 | 0.00084643 | 0 | 0 | 0.00090137 | 0.00090137 |  |  | 0.00069846 | 0.00069846 | 267 | 218.8 | NO
2013-01-17 | 0.077135 | 0.077135 | 0 | 0 | 0.054755 | 0.054755 |  |  | 0.14203 | 0.14203 | 0.0016821 | 0.0016821 | 0 | 0 | 0.0014851 | 0.0014851 |  |  | 0.0022644 | 0.0022644 | 231 | 21.6 | NO
2013-01-18 | 0.17698 | 0.17698 | 0 | 0 | 0.034468 | 0.034468 |  |  | 0.58674 | 0.58674 | 0.0021444 | 0.0021444 | 0 | 0 | 0.00043776 | 0.00043776 |  |  | 0.0070518 | 0.0070518 | 284 | 264.6 | NO
2013-01-19 | 0.55284 | 0.55284 | 0 | 0 | 0.45481 | 0.45481 |  |  | 0.83928 | 0.83928 | 0.0063433 | 0.0063433 | 0 | 0 | 0.0061485 | 0.0061485 |  |  | 0.0069703 | 0.0069703 | 395 | 282.6 | NO
2013-01-20 | 0.2227 | 0.2227 | 0 | 0 | 0.198 | 0.198 |  |  | 0.2958 | 0.2958 | 0.0041655 | 0.0041655 | 0 | 0 | 0.0041121 | 0.0041121 |  |  | 0.0043639 | 0.0043639 | 203 | 186.8 | NO
2013-01-21 | 0.502 | 0.502 | 0 | 0 | 0.39137 | 0.39137 |  |  | 0.82372 | 0.82372 | 0.010123 | 0.010123 | 0 | 0 | 0.0090609 | 0.0090609 |  |  | 0.013271 | 0.013271 | 532 | 444.6 | NO
2013-01-22 | 0.22935 | 0.22935 | 0 | 0 | 0.22461 | 0.22461 |  |  | 0.24544 | 0.24544 | 0.0032402 | 0.0032402 | 0 | 0 | 0.0036392 | 0.0036392 |  |  | 0.0021359 | 0.0021359 | 351 | 336.2 | NO
2013-01-23 | 0.27636 | 0.27636 | 0 | 0 | 0.075962 | 0.075962 |  |  | 0.85194 | 0.85194 | 0.0037072 | 0.0037072 | 0 | 0 | 0.0018074 | 0.0018074 |  |  | 0.0091759 | 0.0091759 | 280 | 251.4 | NO
2013-01-24 | 0.13636 | 0.13636 | 0 | 0 | 0.054332 | 0.054332 |  |  | 0.3721 | 0.3721 | 0.0022398 | 0.0022398 | 0 | 0 | 0.0016673 | 0.0016673 |  |  | 0.0038994 | 0.0038994 | 316 | 278.2 | NO
2013-01-25 | 0.31723 | 0.31723 | 0 | 0 | 0.14519 | 0.14519 |  |  | 0.81181 | 0.81181 | 0.0025503 | 0.0025503 | 0 | 0 | 0.00086811 | 0.00086811 |  |  | 0.0073803 | 0.0073803 | 490 | 409.2 | NO
2013-01-26 | 8.3576 | 8.3576 | 0 | 0 | 0.84861 | 0.84861 |  |  | 29.8776 | 29.8776 | 0.018828 | 0.018828 | 0 | 0 | 0.0061704 | 0.0061704 |  |  | 0.055156 | 0.055156 | 0 | 0 | Yes
2013-01-27 | 281.2041 | 281.2041 | 0 | 0 | 167.4062 | 167.4062 |  |  | 609.0153 | 609.0153 | 0.20803 | 0.20803 | 0 | 0 | 0.1508 | 0.1508 |  |  | 0.37364 | 0.37364 | 0 | 0 | Yes
2013-01-28 | 139.6935 | 139.6935 | 0 | 0 | 131.1477 | 131.1477 |  |  | 165.6135 | 165.6135 | 0.13557 | 0.13557 | 0 | 0 | 0.13934 | 0.13934 |  |  | 0.12634 | 0.12634 | 0 | 0 | Yes
2013-01-29 | 14.2725 | 14.2725 | 3.1312 | 3.1312 | 13.136 | 13.136 |  |  | 17.6362 | 17.6362 | 0.022767 | 0.022767 | 0.00044046 | 0.00044046 | 0.017208 | 0.017208 |  |  | 0.038863 | 0.038863 | 0 | 0 | Yes
2013-01-30 | 3.2322 | 3.2322 | 0 | 0 | 2.6179 | 2.6179 |  |  | 5.0187 | 5.0187 | 0.0089118 | 0.0089118 | 0 | 0 | 0.00702 | 0.00702 |  |  | 0.014402 | 0.014402 | 5318 | 3560 | NO
2013-01-31 | 1.1063 | 1.1063 | 0 | 0 | 1.0984 | 1.0984 |  |  | 1.1413 | 1.1413 | 0.0041588 | 0.0041588 | 0 | 0 | 0.0038826 | 0.0038826 |  |  | 0.004992 | 0.004992 | 2711 | 1444.6 | NO
2013-02-01 | 0.9833 | 0.9833 | 0 | 0 | 0.62777 | 0.62777 |  |  | 2.0067 | 2.0067 | 0.0080628 | 0.0080628 | 0 | 0 | 0.0055681 | 0.0055681 |  |  | 0.015257 | 0.015257 | 1812 | 1146.4 | NO
2013-02-02 | 0.32374 | 0.32374 | 0.0076511 | 0.0076511 | 0.28563 | 0.28563 |  |  | 0.43578 | 0.43578 | 0.0031462 | 0.0031462 | 0.00025776 | 0.00025776 | 0.0031789 | 0.0031789 |  |  | 0.0030854 | 0.0030854 | 923 | 663.8 | NO
2013-02-03 | 0.076128 | 0.076128 | 0 | 0 | 0.099965 | 0.099965 |  |  | 0.0091307 | 0.0091307 | 0.0012249 | 0.0012249 | 0 | 0 | 0.0014771 | 0.0014771 |  |  | 0.00052045 | 0.00052045 | 298 | 267.8 | NO
2013-02-04 | 0.42473 | 0.42473 | 0 | 0 | 0.3224 | 0.3224 |  |  | 0.7206 | 0.7206 | 0.0054474 | 0.0054474 | 0 | 0 | 0.0046092 | 0.0046092 |  |  | 0.0078928 | 0.0078928 | 736 | 656.6 | NO
2013-02-05 | 0.36634 | 0.36634 | 0 | 0 | 0.32146 | 0.32146 |  |  | 0.49808 | 0.49808 | 0.0050543 | 0.0050543 | 0 | 0 | 0.0040021 | 0.0040021 |  |  | 0.0081031 | 0.0081031 | 520 | 491.4 | NO
2013-02-06 | 0.4287 | 0.4287 | 0 | 0 | 0.38089 | 0.38089 |  |  | 0.56942 | 0.56942 | 0.0055944 | 0.0055944 | 0 | 0 | 0.0062399 | 0.0062399 |  |  | 0.0038217 | 0.0038217 | 514 | 426.6 | NO
2013-02-07 | 0.11721 | 0.11721 | 0 | 0 | 0.13581 | 0.13581 |  |  | 0.065645 | 0.065645 | 0.00094449 | 0.00094449 | 0 | 0 | 0.0010182 | 0.0010182 |  |  | 0.0007455 | 0.0007455 | 352 | 311 | NO
2013-02-08 | 0.13703 | 0.13703 | 0 | 0 | 0.17187 | 0.17187 |  |  | 0.039584 | 0.039584 | 0.0014377 | 0.0014377 | 0 | 0 | 0.001788 | 0.001788 |  |  | 0.00045838 | 0.00045838 | 362 | 315.8 | NO
2013-02-09 | 0.18025 | 0.18025 | 0 | 0 | 0.13905 | 0.13905 |  |  | 0.29927 | 0.29927 | 0.015911 | 0.015911 | 0 | 0 | 0.016518 | 0.016518 |  |  | 0.014363 | 0.014363 | 310 | 263 | NO
2013-02-10 | 0.062783 | 0.062783 | 0 | 0 | 0.026845 | 0.026845 |  |  | 0.16552 | 0.16552 | 0.0010178 | 0.0010178 | 0 | 0 | 0.00052735 | 0.00052735 |  |  | 0.0024216 | 0.0024216 | 182 | 166.6 | NO
2013-02-11 | 0.090203 | 0.090203 | 0 | 0 | 0.11362 | 0.11362 |  |  | 0.02476 | 0.02476 | 0.0013289 | 0.0013289 | 0 | 0 | 0.0017472 | 0.0017472 |  |  | 0.00015677 | 0.00015677 | 421 | 377.4 | NO
2013-02-12 | 0.27412 | 0.27412 | 0 | 0 | 0.045246 | 0.045246 |  |  | 0.92646 | 0.92646 | 0.0034029 | 0.0034029 | 0 | 0 | 0.00033853 | 0.00033853 |  |  | 0.012134 | 0.012134 | 321 | 297.6 | NO
2013-02-13 | 0.5219 | 0.5219 | 0 | 0 | 0.38849 | 0.38849 |  |  | 0.90603 | 0.90603 | 0.0050598 | 0.0050598 | 0 | 0 | 0.0024768 | 0.0024768 |  |  | 0.012441 | 0.012441 | 420 | 335 | NO
2013-02-14 | 0.29969 | 0.29969 | 0 | 0 | 0.30517 | 0.30517 |  |  | 0.28748 | 0.28748 | 0.0049846 | 0.0049846 | 0 | 0 | 0.0046711 | 0.0046711 |  |  | 0.0059287 | 0.0059287 | 416 | 357.6 | NO
2013-02-15 | 0.076718 | 0.076718 | 0 | 0 | 0.10116 | 0.10116 |  |  | 0.0082956 | 0.0082956 | 0.0021812 | 0.0021812 | 0 | 0 | 0.0029018 | 0.0029018 |  |  | 0.0001633 | 0.0001633 | 288 | 270.2 | NO
2013-02-16 | 0.097893 | 0.097893 | 0 | 0 | 0.026845 | 0.026845 |  |  | 0.30033 | 0.30033 | 0.0017056 | 0.0017056 | 0 | 0 | 0.00033837 | 0.00033837 |  |  | 0.0055991 | 0.0055991 | 294 | 241 | NO
2013-02-17 | 0.14434 | 0.14434 | 0 | 0 | 0.10642 | 0.10642 |  |  | 0.25339 | 0.25339 | 0.0023585 | 0.0023585 | 0 | 0 | 0.0024055 | 0.0024055 |  |  | 0.0022515 | 0.0022515 | 212 | 189.4 | NO
2013-02-18 | 0.58917 | 0.58917 | 0.14226 | 0.14226 | 0.39955 | 0.39955 |  |  | 1.1315 | 1.1315 | 0.004895 | 0.004895 | 0.00077315 | 0.00077315 | 0.0037817 | 0.0037817 |  |  | 0.0080958 | 0.0080958 | 532 | 465.2 | NO
2013-02-19 | 0.22568 | 0.22568 | 0 | 0 | 0.16086 | 0.16086 |  |  | 0.41187 | 0.41187 | 0.0035746 | 0.0035746 | 0 | 0 | 0.0031133 | 0.0031133 |  |  | 0.0049211 | 0.0049211 | 615 | 478.6 | NO
2013-02-20 | 0.21028 | 0.21028 | 0 | 0 | 0.024624 | 0.024624 |  |  | 0.73866 | 0.73866 | 0.0030723 | 0.0030723 | 0 | 0 | 0.00012607 | 0.00012607 |  |  | 0.011454 | 0.011454 | 422 | 371.8 | NO
2013-02-21 | 0.23639 | 0.23639 | 0 | 0 | 0.24422 | 0.24422 |  |  | 0.21685 | 0.21685 | 0.0039989 | 0.0039989 | 0 | 0 | 0.0041783 | 0.0041783 |  |  | 0.0035348 | 0.0035348 | 349 | 317.4 | NO
2013-02-22 | 0.93196 | 0.93196 | 0 | 0 | 0.80227 | 0.80227 |  |  | 1.3097 | 1.3097 | 0.010786 | 0.010786 | 0 | 0 | 0.010377 | 0.010377 |  |  | 0.012065 | 0.012065 | 713 | 643.8 | NO
2013-02-23 | 0.14714 | 0.14714 | 0 | 0 | 0.19007 | 0.19007 |  |  | 0.027173 | 0.027173 | 0.0025163 | 0.0025163 | 0 | 0 | 0.0033134 | 0.0033134 |  |  | 0.00028645 | 0.00028645 | 325 | 281.4 | NO
2013-02-24 | 0.16378 | 0.16378 | 0 | 0 | 0.19123 | 0.19123 |  |  | 0.087842 | 0.087842 | 0.0017761 | 0.0017761 | 0 | 0 | 0.0018937 | 0.0018937 |  |  | 0.0014626 | 0.0014626 | 270 | 243.6 | NO
2013-02-25 | 0.58004 | 0.58004 | 0 | 0 | 0.3184 | 0.3184 |  |  | 1.3275 | 1.3275 | 0.0040919 | 0.0040919 | 0 | 0 | 0.002098 | 0.002098 |  |  | 0.0097844 | 0.0097844 | 616 | 530.8 | NO
2013-02-26 | 0.29083 | 0.29083 | 0 | 0 | 0.35819 | 0.35819 |  |  | 0.10329 | 0.10329 | 0.0031701 | 0.0031701 | 0 | 0 | 0.0041674 | 0.0041674 |  |  | 0.00038072 | 0.00038072 | 456 | 407.8 | NO
2013-02-27 | 0.11445 | 0.11445 | 0 | 0 | 0.042871 | 0.042871 |  |  | 0.31843 | 0.31843 | 0.0021313 | 0.0021313 | 0 | 0 | 0.00090652 | 0.00090652 |  |  | 0.0056237 | 0.0056237 | 345 | 306.4 | NO
2013-02-28 | 0.034921 | 0.034921 | 0 | 0 | 0.025031 | 0.025031 |  |  | 0.063316 | 0.063316 | 0.00063407 | 0.00063407 | 0 | 0 | 0.00021719 | 0.00021719 |  |  | 0.0018217 | 0.0018217 | 350 | 315.6 | NO
2013-03-01 | 0.1374 | 0.1374 | 0 | 0 | 0.30094 | 0.30094 |  |  | 0.86788 | 0.86788 | 0.00086445 | 0.00086445 | 0 | 0 | 0.0034002 | 0.0034002 |  |  | 0.0098005 | 0.0098005 | 298 | 253.6 | NO
2013-03-02 | 0.082823 | 0.082823 | 0 | 0 | 0.24992 | 0.24992 |  |  | 0.18187 | 0.18187 | 0.00099927 | 0.00099927 | 0 | 0 | 0.0019342 | 0.0019342 |  |  | 0.0011246 | 0.0011246 | 321 | 267.6 | NO
2013-03-03 | 0.2011 | 0.2011 | 0 | 0 | 0.36155 | 0.36155 |  |  | 0.012974 | 0.012974 | 0.0032861 | 0.0032861 | 0 | 0 | 0.0026067 | 0.0026067 |  |  | 6.7484e-05 | 6.7484e-05 | 341 | 289 | NO
2013-03-04 | 0.10712 | 0.10712 | 0 | 0 | 0.016513 | 0.016513 |  |  | 0.0071592 | 0.0071592 | 0.0010007 | 0.0010007 | 0 | 0 | 0.00048052 | 0.00048052 |  |  | 9.5874e-05 | 9.5874e-05 | 425 | 363 | NO
2013-03-05 | 0.085884 | 0.085884 | 0 | 0 | 0.68704 | 0.68704 |  |  | 0.1417 | 0.1417 | 0.0026614 | 0.0026614 | 0 | 0 | 0.0042808 | 0.0042808 |  |  | 0.0010528 | 0.0010528 | 444 | 394.2 | NO
2013-03-06 | 0.055078 | 0.055078 | 0 | 0 | 0.013014 | 0.013014 |  |  | 0.082763 | 0.082763 | 0.0013966 | 0.0013966 | 0 | 0 | 0.00015002 | 0.00015002 |  |  | 0.0021332 | 0.0021332 | 314 | 280.8 | NO
2013-03-07 | 0.093144 | 0.093144 | 0 | 0 | 0.58169 | 0.58169 |  |  | 0.061425 | 0.061425 | 0.0014946 | 0.0014946 | 0 | 0 | 0.0040057 | 0.0040057 |  |  | 0.00023398 | 0.00023398 | 309 | 276.8 | NO
2013-03-08 | 0.066845 | 0.066845 | 0 | 0 | 0.022674 | 0.022674 |  |  | 0.010306 | 0.010306 | 0.0012214 | 0.0012214 | 0 | 0 | 0.00024337 | 0.00024337 |  |  | 8.6213e-05 | 8.6213e-05 | 322 | 293.2 | NO
2013-03-09 | 0.062914 | 0.062914 | 0 | 0 | 0.23789 | 0.23789 |  |  | 0.86042 | 0.86042 | 0.00064526 | 0.00064526 | 0 | 0 | 0.0031005 | 0.0031005 |  |  | 0.0071974 | 0.0071974 | 209 | 194.6 | NO
2013-03-10 | 0.031493 | 0.031493 | 0 | 0 | 0.178 | 0.178 |  |  | 0.33138 | 0.33138 | 0.00015719 | 0.00015719 | 0 | 0 | 0.0051774 | 0.0051774 |  |  | 0.0058211 | 0.0058211 | 156 | 151.2 | NO
2013-03-11 | 0.23614 | 0.23614 | 0 | 0 | 0.070587 | 0.070587 |  |  | 0.016232 | 0.016232 | 0.0029653 | 0.0029653 | 0 | 0 | 0.0017927 | 0.0017927 |  |  | 0.0003954 | 0.0003954 | 343 | 292.6 | NO
2013-03-12 | 0.1067 | 0.1067 | 0 | 0 | 0.43905 | 0.43905 |  |  | 0.012713 | 0.012713 | 0.0020675 | 0.0020675 | 0 | 0 | 0.0048836 | 0.0048836 |  |  | 0.00014645 | 0.00014645 | 308 | 259.2 | NO
2013-03-13 | 0.073349 | 0.073349 | 0 | 0 | 0.00071412 | 0.00071412 |  |  | 0.052739 | 0.052739 | 0.00082796 | 0.00082796 | 0 | 0 | 9.1739e-06 | 9.1739e-06 |  |  | 0.00067675 | 0.00067675 | 246 | 219.2 | NO
2013-03-14 | 0.47438 | 0.47438 | 0 | 0 | 0.081573 | 0.081573 |  |  | 0.58613 | 0.58613 | 0.0028813 | 0.0028813 | 0 | 0 | 0.00093114 | 0.00093114 |  |  | 0.014401 | 0.014401 | 348 | 278.2 | NO
2013-03-15 | 0.056621 | 0.056621 | 0.031174 | 0.031174 | 0.037751 | 0.037751 |  |  | 0.2406 | 0.2406 | 0.0010557 | 0.0010557 | 0.00025863 | 0.00025863 | 0.00070737 | 0.00070737 |  |  | 0.0025679 | 0.0025679 | 294 | 247 | NO
2013-03-16 | 0.046889 | 0.046889 | 0 | 0 | 0.073649 | 0.073649 |  |  | 0.13184 | 0.13184 | 0.0014066 | 0.0014066 | 0 | 0 | 0.00045672 | 0.00045672 |  |  | 0.0012702 | 0.0012702 | 218 | 200.6 | NO
2013-03-17 | 0.43081 | 0.43081 | 0 | 0 | 0.18194 | 0.18194 |  |  | 0.086662 | 0.086662 | 0.0057209 | 0.0057209 | 0 | 0 | 0.0032935 | 0.0032935 |  |  | 0.00317 | 0.00317 | 261 | 234.2 | NO
2013-03-18 | 0.074554 | 0.074554 | 0 | 0 | 0.20673 | 0.20673 |  |  | 0.2336 | 0.2336 | 0.0019912 | 0.0019912 | 0 | 0 | 0.003814 | 0.003814 |  |  | 0.0020908 | 0.0020908 | 270 | 231.8 | NO
2013-03-19 | 0.063629 | 0.063629 | 0 | 0 | 0.16069 | 0.16069 |  |  | 0.44209 | 0.44209 | 0.0015676 | 0.0015676 | 0 | 0 | 0.0019878 | 0.0019878 |  |  | 0.0032196 | 0.0032196 | 306 | 282.8 | NO
2013-03-20 | 0.14125 | 0.14125 | 0 | 0 | 0.044954 | 0.044954 |  |  | 0.037333 | 0.037333 | 0.0018295 | 0.0018295 | 0 | 0 | 0.00016917 | 0.00016917 |  |  | 0.00031707 | 0.00031707 | 279 | 256.4 | NO
2013-03-21 | 0.0987 | 0.0987 | 0 | 0 | 0.025286 | 0.025286 |  |  | 0.0012996 | 0.0012996 | 0.0010228 | 0.0010228 | 0 | 0 | 0.00012013 | 0.00012013 |  |  | 3.6099e-05 | 3.6099e-05 | 264 | 249.2 | NO
2013-03-22 | 0.013118 | 0.013118 | 0 | 0 | 0.01807 | 0.01807 |  |  | 0.99415 | 0.99415 | 0.00022563 | 0.00022563 | 0 | 0 | 0.00021759 | 0.00021759 |  |  | 0.013441 | 0.013441 | 234 | 220 | NO
2013-03-23 | 0.12202 | 0.12202 | 0 | 0 | 0.018725 | 0.018725 |  |  | 0.92969 | 0.92969 | 0.0011387 | 0.0011387 | 0 | 0 | 0.00035331 | 0.00035331 |  |  | 0.012087 | 0.012087 | 229 | 203 | NO
2013-03-24 | 18.7464 | 18.7464 | 0 | 0 | 0.33379 | 0.33379 |  |  | 0.13885 | 0.13885 | 0.051733 | 0.051733 | 0 | 0 | 0.0090756 | 0.0090756 |  |  | 0.0025017 | 0.0025017 | 0 | 0 | Yes
2013-03-25 | 0.72845 | 0.72845 | 0 | 0 | 0.13897 | 0.13897 |  |  | 0.047439 | 0.047439 | 0.0049255 | 0.0049255 | 0 | 0 | 0.00081187 | 0.00081187 |  |  | 0.0033893 | 0.0033893 | 1661 | 1185 | NO
2013-03-26 | 0.40946 | 0.40946 | 0 | 0 | 0.041794 | 0.041794 |  |  | 0 | 0 | 0.0039687 | 0.0039687 | 0 | 0 | 0.00023419 | 0.00023419 |  |  | 0 | 0 | 522 | 431.8 | NO
2013-03-27 | 0.31392 | 0.31392 | 0 | 0 | 0.096392 | 0.096392 |  |  | 0.30254 | 0.30254 | 0.0022149 | 0.0022149 | 0 | 0 | 0.0017298 | 0.0017298 |  |  | 0.0045799 | 0.0045799 | 413 | 317.8 | NO
2013-03-28 | 0.015548 | 0.015548 | 0 | 0 | 0 | 0 |  |  | 0.0046377 | 0.0046377 | 0.00037208 | 0.00037208 | 0 | 0 | 0 | 0 |  |  | 3.4567e-05 | 3.4567e-05 | 292 | 242.2 | NO
2013-03-29 | 0.50887 | 0.50887 | 0 | 0 | 0.019338 | 0.019338 |  |  | 0.43829 | 0.43829 | 0.0031839 | 0.0031839 | 0 | 0 | 0.00034715 | 0.00034715 |  |  | 0.0067685 | 0.0067685 | 283 | 266.6 | NO
2013-03-30 | 0.046321 | 0.046321 | 0 | 0 | 0.066285 | 0.066285 |  |  | 0.030888 | 0.030888 | 0.0003835 | 0.0003835 | 0 | 0 | 0.0018336 | 0.0018336 |  |  | 0.00032269 | 0.00032269 | 139 | 127.4 | NO
2013-03-31 | 0.45075 | 0.45075 | 0 | 0 | 0.019961 | 0.019961 |  |  | 0.0028669 | 0.0028669 | 0.003509 | 0.003509 | 0 | 0 | 0.00017647 | 0.00017647 |  |  | 1.4406e-05 | 1.4406e-05 | 335 | 266.2 | NO
2013-04-01 | 0.032647 | 0.032647 | 0 | 0 | 0.42745 | 0.42745 |  |  | 0.086443 | 0.086443 | 0.00024024 | 0.00024024 | 0 | 0 | 0.0028447 | 0.0028447 |  |  | 0.0038899 | 0.0038899 | 168 | 150 | NO
2013-04-02 | 0.17826 | 0.17826 | 0 | 0 | 0.077086 | 0.077086 |  |  | 0.018188 | 0.018188 | 0.0023109 | 0.0023109 | 0 | 0 | 0.00069405 | 0.00069405 |  |  | 0.0001583 | 0.0001583 | 409 | 372.2 | NO
2013-04-03 | 0.35421 | 0.35421 | 0 | 0 | 0.06589 | 0.06589 |  |  | 0.16254 | 0.16254 | 0.0056856 | 0.0056856 | 0 | 0 | 0.0027459 | 0.0027459 |  |  | 0.0025549 | 0.0025549 | 418 | 327 | NO
2013-04-04 | 0.13791 | 0.13791 | 0 | 0 | 0.049743 | 0.049743 |  |  | 0.079855 | 0.079855 | 0.0028307 | 0.0028307 | 0 | 0 | 0.0008755 | 0.0008755 |  |  | 0.002384 | 0.002384 | 357 | 269.6 | NO
2013-04-05 | 0.32831 | 0.32831 | 0 | 0 | 0.024743 | 0.024743 |  |  | 0.10178 | 0.10178 | 0.0037075 | 0.0037075 | 0 | 0 | 0.00017705 | 0.00017705 |  |  | 0.00057466 | 0.00057466 | 357 | 332.8 | NO
2013-04-06 | 0.0038181 | 0.0038181 | 0 | 0 | 0.15426 | 0.15426 |  |  | 0.51149 | 0.51149 | 4.4685e-05 | 4.4685e-05 | 0 | 0 | 0.0022078 | 0.0022078 |  |  | 0.0022005 | 0.0022005 | 143 | 131.6 | NO
2013-04-07 | 0.073874 | 0.073874 | 0 | 0 | 0.0024585 | 0.0024585 |  |  | 0.0012784 | 0.0012784 | 0.00086261 | 0.00086261 | 0 | 0 | 1.8646e-05 | 1.8646e-05 |  |  | 1.4412e-05 | 1.4412e-05 | 123 | 113.6 | NO
2013-04-08 | 0.17963 | 0.17963 | 0 | 0 | 0.12596 | 0.12596 |  |  | 0.014853 | 0.014853 | 0.0042493 | 0.0042493 | 0 | 0 | 0.0020256 | 0.0020256 |  |  | 0.00014703 | 0.00014703 | 325 | 266.4 | NO
2013-04-09 | 0.11663 | 0.11663 | 0 | 0 | 0.0015962 | 0.0015962 |  |  | 0.020415 | 0.020415 | 0.0010016 | 0.0010016 | 0 | 0 | 1.7517e-05 | 1.7517e-05 |  |  | 0.00020554 | 0.00020554 | 229 | 205.8 | NO
2013-04-10 | 0.16846 | 0.16846 | 0 | 0 | 0.036744 | 0.036744 |  |  | 0.22778 | 0.22778 | 0.0027607 | 0.0027607 | 0 | 0 | 0.00043749 | 0.00043749 |  |  | 0.00024504 | 0.00024504 | 333 | 274.6 | NO
2013-04-11 | 0.17508 | 0.17508 | 0 | 0 | 0.16332 | 0.16332 |  |  | 0.017862 | 0.017862 | 0.0036364 | 0.0036364 | 0 | 0 | 0.002165 | 0.002165 |  |  | 0.0001946 | 0.0001946 | 335 | 251.2 | NO
2013-04-12 | 0.17908 | 0.17908 | 0 | 0 | 0.047077 | 0.047077 |  |  | 0.037398 | 0.037398 | 0.0020087 | 0.0020087 | 0 | 0 | 0.0014106 | 0.0014106 |  |  | 0.0004622 | 0.0004622 | 231 | 198.2 | NO
2013-04-13 | 0.14751 | 0.14751 | 0 | 0 | 0.13975 | 0.13975 |  |  | 0.065046 | 0.065046 | 0.00095741 | 0.00095741 | 0 | 0 | 0.004396 | 0.004396 |  |  | 0.00061737 | 0.00061737 | 241 | 209 | NO
2013-04-14 | 0.028328 | 0.028328 | 0 | 0 | 0.44662 | 0.44662 |  |  | 0.040348 | 0.040348 | 0.0001707 | 0.0001707 | 0 | 0 | 0.0026585 | 0.0026585 |  |  | 0.00047324 | 0.00047324 | 164 | 140.4 | NO
2013-04-15 | 0.013683 | 0.013683 | 0 | 0 | 0.0098244 | 0.0098244 |  |  | 0.0081784 | 0.0081784 | 0.00017005 | 0.00017005 | 0 | 0 | 8.6164e-05 | 8.6164e-05 |  |  | 0.00013482 | 0.00013482 | 266 | 238.6 | NO
2013-04-16 | 0.2708 | 0.2708 | 0 | 0 | 0.062672 | 0.062672 |  |  | 0.00097966 | 0.00097966 | 0.0037351 | 0.0037351 | 0 | 0 | 0.00048664 | 0.00048664 |  |  | 5.7661e-06 | 5.7661e-06 | 403 | 332.4 | NO
2013-04-17 | 0.48683 | 0.48683 | 0 | 0 | 0.12866 | 0.12866 |  |  | 0.0012663 | 0.0012663 | 0.0098277 | 0.0098277 | 0 | 0 | 0.0011889 | 0.0011889 |  |  | 1.1533e-05 | 1.1533e-05 | 365 | 312.4 | NO
2013-04-18 | 0.13854 | 0.13854 | 0 | 0 | 0.023819 | 0.023819 |  |  | 0.50617 | 0.50617 | 0.0012462 | 0.0012462 | 0 | 0 | 0.00020207 | 0.00020207 |  |  | 0.0031133 | 0.0031133 | 340 | 268.2 | NO
2013-04-19 | 0.043132 | 0.043132 | 0 | 0 | 0.0077226 | 0.0077226 |  |  | 0.0103 | 0.0103 | 0.0010487 | 0.0010487 | 0 | 0 | 7.373e-05 | 7.373e-05 |  |  | 9.1064e-05 | 9.1064e-05 | 239 | 214.6 | NO
2013-04-20 | 0.071214 | 0.071214 | 0 | 0 | 0.10876 | 0.10876 |  |  | 0.25784 | 0.25784 | 0.0012779 | 0.0012779 | 0 | 0 | 0.0013239 | 0.0013239 |  |  | 0.0051927 | 0.0051927 | 203 | 169.8 | NO
2013-04-21 | 0.078153 | 0.078153 | 0.013305 | 0.013305 | 0.1818 | 0.1818 |  |  | 0.2851 | 0.2851 | 0.0011831 | 0.0011831 | 0.00025819 | 0.00025819 | 0.0026247 | 0.0026247 |  |  | 0.0028673 | 0.0028673 | 113 | 109 | NO
2013-04-22 | 0.015485 | 0.015485 | 0.02164 | 0.02164 | 0.04463 | 0.04463 |  |  | 0.1129 | 0.1129 | 0.00026541 | 0.00026541 | 0.00025823 | 0.00025823 | 0.00034462 | 0.00034462 |  |  | 0.0091367 | 0.0091367 | 245 | 199.2 | NO
2013-04-23 | 0.16217 | 0.16217 | 0 | 0 | 0.076686 | 0.076686 |  |  | 0.069529 | 0.069529 | 0.0031029 | 0.0031029 | 0 | 0 | 0.00038644 | 0.00038644 |  |  | 0.0028407 | 0.0028407 | 273 | 224.8 | NO
2013-04-24 | 0.022726 | 0.022726 | 0.070247 | 0.070247 | 0.049919 | 0.049919 |  |  | 0.26823 | 0.26823 | 0.00021372 | 0.00021372 | 0.00025831 | 0.00025831 | 0.00089147 | 0.00089147 |  |  | 0.003159 | 0.003159 | 229 | 193.4 | NO
2013-04-25 | 0.31658 | 0.31658 | 0 | 0 | 0.031729 | 0.031729 |  |  | 0.024568 | 0.024568 | 0.0021057 | 0.0021057 | 0 | 0 | 0.00091313 | 0.00091313 |  |  | 0.00016181 | 0.00016181 | 189 | 151 | NO
2013-04-26 | 0.079282 | 0.079282 | 0 | 0 | 0.082022 | 0.082022 |  |  | 0.04332 | 0.04332 | 0.0015173 | 0.0015173 | 0 | 0 | 0.0016 | 0.0016 |  |  | 0.00084763 | 0.00084763 | 248 | 227.6 | NO
2013-04-27 | 0.053384 | 0.053384 | 0 | 0 | 0.070072 | 0.070072 |  |  | 0.10698 | 0.10698 | 0.0020699 | 0.0020699 | 0 | 0 | 0.00057639 | 0.00057639 |  |  | 0.00046707 | 0.00046707 | 171 | 153.6 | NO
2013-04-28 | 0.078725 | 0.078725 | 0 | 0 | 0.0049868 | 0.0049868 |  |  | 0.40145 | 0.40145 | 0.0013066 | 0.0013066 | 0 | 0 | 4.8487e-05 | 4.8487e-05 |  |  | 0.0038636 | 0.0038636 | 112 | 106.2 | NO
2013-04-29 | 0.038902 | 0.038902 | 0 | 0 | 0.17877 | 0.17877 |  |  | 0.18683 | 0.18683 | 0.00074635 | 0.00074635 | 0 | 0 | 0.0026601 | 0.0026601 |  |  | 0.0039747 | 0.0039747 | 251 | 226.4 | NO
2013-04-30 | 0.14027 | 0.14027 | 0 | 0 | 0.078859 | 0.078859 |  |  | 0.061954 | 0.061954 | 0.0017799 | 0.0017799 | 0 | 0 | 0.001403 | 0.001403 |  |  | 0.00015371 | 0.00015371 | 283 | 265.6 | NO
2013-05-01 | 0.13385 | 0.13385 | 0 | 0 | 0.077654 | 0.077654 |  |  | 1.5711 | 1.5711 | 0.00058182 | 0.00058182 | 0 | 0 | 0.0010689 | 0.0010689 |  |  | 0.0082823 | 0.0082823 | 225 | 217.8 | NO
2013-05-02 | 0.093417 | 0.093417 | 0 | 0 | 0.089649 | 0.089649 |  |  | 0.025707 | 0.025707 | 0.0015007 | 0.0015007 | 0 | 0 | 0.00098878 | 0.00098878 |  |  | 0.00043577 | 0.00043577 | 258 | 236.8 | NO
2013-05-03 | 0.0050133 | 0.0050133 | 0 | 0 | 0.067737 | 0.067737 |  |  | 0.11728 | 0.11728 | 5.0894e-05 | 5.0894e-05 | 0 | 0 | 0.0012783 | 0.0012783 |  |  | 0.0013683 | 0.0013683 | 236 | 203.4 | NO
2013-05-04 | 0.032424 | 0.032424 | 0 | 0 | 0.022268 | 0.022268 |  |  | 0.13959 | 0.13959 | 0.00037637 | 0.00037637 | 0 | 0 | 0.0014255 | 0.0014255 |  |  | 0.0026899 | 0.0026899 | 209 | 187 | NO
2013-05-05 | 0.17949 | 0.17949 | 0 | 0 | 0.5351 | 0.5351 |  |  | 0.18898 | 0.18898 | 0.0016633 | 0.0016633 | 0 | 0 | 0.0068112 | 0.0068112 |  |  | 0.0032058 | 0.0032058 | 144 | 138.2 | NO
2013-05-06 | 0.039403 | 0.039403 | 0 | 0 | 0.03454 | 0.03454 |  |  | 0.19727 | 0.19727 | 0.0010927 | 0.0010927 | 0 | 0 | 0.0015712 | 0.0015712 |  |  | 0.0054195 | 0.0054195 | 310 | 238.6 | NO
2013-05-07 | 0.11293 | 0.11293 | 0 | 0 | 0.016811 | 0.016811 |  |  | 0.37377 | 0.37377 | 0.0033683 | 0.0033683 | 0 | 0 | 0.00021711 | 0.00021711 |  |  | 0.005494 | 0.005494 | 261 | 239.8 | NO
2013-05-08 | 0.34688 | 0.34688 | 0 | 0 | 0.059937 | 0.059937 |  |  | 0.022774 | 0.022774 | 0.0021242 | 0.0021242 | 0 | 0 | 0.0005464 | 0.0005464 |  |  | 0.0001984 | 0.0001984 | 293 | 265.2 | NO
2013-05-09 | 0.017673 | 0.017673 | 0 | 0 | 0.12581 | 0.12581 |  |  | 0.0088851 | 0.0088851 | 0.00018581 | 0.00018581 | 0 | 0 | 0.001317 | 0.001317 |  |  | 0.00028366 | 0.00028366 | 247 | 230 | NO
2013-05-10 | 0.048431 | 0.048431 | 0 | 0 | 0.014658 | 0.014658 |  |  | 0.39685 | 0.39685 | 0.00039447 | 0.00039447 | 0 | 0 | 0.00020608 | 0.00020608 |  |  | 0.0039649 | 0.0039649 | 239 | 219.6 | NO
2013-05-11 | 0.095347 | 0.095347 | 0.41995 | 0.41995 | 0.024159 | 0.024159 |  |  | 40.8729 | 40.8729 | 0.0008802 | 0.0008802 | 0.0038778 | 0.0038778 | 0.00013359 | 0.00013359 |  |  | 0.11585 | 0.11585 | 185 | 174.6 | NO
2013-05-12 | 0.017932 | 0.017932 | 0 | 0 | 11.0361 | 11.0361 |  |  | 1.9523 | 1.9523 | 0.00015233 | 0.00015233 | 0 | 0 | 0.029379 | 0.029379 |  |  | 0.0093179 | 0.0093179 | 90 | 81.2 | NO
2013-05-13 | 0.22857 | 0.22857 | 0 | 0 | 0.029653 | 0.029653 |  |  | 0.80144 | 0.80144 | 0.0028257 | 0.0028257 | 0 | 0 | 0.0014409 | 0.0014409 |  |  | 0.0068272 | 0.0068272 | 262 | 253.8 | NO
2013-05-14 | 0.06516 | 0.06516 | 0 | 0 | 0.0764 | 0.0764 |  |  | 0.033652 | 0.033652 | 0.00073934 | 0.00073934 | 0 | 0 | 0.00090898 | 0.00090898 |  |  | 0.0002611 | 0.0002611 | 276 | 263.2 | NO
2013-05-15 | 0.015683 | 0.015683 | 0 | 0 | 0.0019825 | 0.0019825 |  |  | 0.055148 | 0.055148 | 0.0001625 | 0.0001625 | 0 | 0 | 1.3532e-05 | 1.3532e-05 |  |  | 0.00059149 | 0.00059149 | 223 | 204.8 | NO
2013-05-16 | 0.023389 | 0.023389 | 0 | 0 | 0.026002 | 0.026002 |  |  | 0.016156 | 0.016156 | 0.00023058 | 0.00023058 | 0 | 0 | 0.00027162 | 0.00027162 |  |  | 0.00011542 | 0.00011542 | 232 | 216.6 | NO
2013-05-17 | 0.39836 | 0.39836 | 0 | 0 | 0.46173 | 0.46173 |  |  | 0.22099 | 0.22099 | 0.0051683 | 0.0051683 | 0 | 0 | 0.0061791 | 0.0061791 |  |  | 0.002326 | 0.002326 | 313 | 273.6 | NO
2013-05-18 | 0.015819 | 0.015819 | 0 | 0 | 0.0013844 | 0.0013844 |  |  | 0.057402 | 0.057402 | 0.00025277 | 0.00025277 | 0 | 0 | 1.3078e-05 | 1.3078e-05 |  |  | 0.0009432 | 0.0009432 | 188 | 148 | NO
2013-05-19 | 0.030419 | 0.030419 | 0 | 0 | 0.020237 | 0.020237 |  |  | 0.059967 | 0.059967 | 0.0011876 | 0.0011876 | 0 | 0 | 0.00057918 | 0.00057918 |  |  | 0.0029464 | 0.0029464 | 136 | 127.2 | NO
2013-05-20 | 0.028625 | 0.028625 | 0 | 0 | 0.036862 | 0.036862 |  |  | 0.0053057 | 0.0053057 | 0.00029561 | 0.00029561 | 0 | 0 | 0.00038066 | 0.00038066 |  |  | 5.4842e-05 | 5.4842e-05 | 297 | 275.6 | NO
2013-05-21 | 0.12663 | 0.12663 | 0 | 0 | 0.15916 | 0.15916 |  |  | 0.034645 | 0.034645 | 0.0033394 | 0.0033394 | 0 | 0 | 0.0037618 | 0.0037618 |  |  | 0.002164 | 0.002164 | 282 | 258.4 | NO
2013-05-22 | 0.094772 | 0.094772 | 0 | 0 | 0.05375 | 0.05375 |  |  | 0.2136 | 0.2136 | 0.0024741 | 0.0024741 | 0 | 0 | 0.0025789 | 0.0025789 |  |  | 0.0022008 | 0.0022008 | 319 | 285.4 | NO
2013-05-23 | 0.08361 | 0.08361 | 0 | 0 | 0.027765 | 0.027765 |  |  | 0.2449 | 0.2449 | 0.00057207 | 0.00057207 | 0 | 0 | 0.0002194 | 0.0002194 |  |  | 0.0015911 | 0.0015911 | 271 | 249.2 | NO
2013-05-24 | 0.033062 | 0.033062 | 0 | 0 | 0.009809 | 0.009809 |  |  | 0.10023 | 0.10023 | 0.00074811 | 0.00074811 | 0 | 0 | 0.00010978 | 0.00010978 |  |  | 0.0025901 | 0.0025901 | 273 | 228.6 | NO
2013-05-25 | 0.13522 | 0.13522 | 0 | 0 | 0.03399 | 0.03399 |  |  | 0.42758 | 0.42758 | 0.0016479 | 0.0016479 | 0 | 0 | 0.0001297 | 0.0001297 |  |  | 0.0060284 | 0.0060284 | 208 | 198.2 | NO
2013-05-26 | 0.014283 | 0.014283 | 0 | 0 | 0.017859 | 0.017859 |  |  | 0.0041648 | 0.0041648 | 8.2104e-05 | 8.2104e-05 | 0 | 0 | 9.7921e-05 | 9.7921e-05 |  |  | 3.7558e-05 | 3.7558e-05 | 117 | 117 | NO
2013-05-27 | 0.080198 | 0.080198 | 0 | 0 | 0.027874 | 0.027874 |  |  | 0.23151 | 0.23151 | 0.0018988 | 0.0018988 | 0 | 0 | 0.001381 | 0.001381 |  |  | 0.0034085 | 0.0034085 | 305 | 289.4 | NO
2013-05-28 | 0.18818 | 0.18818 | 0 | 0 | 0.14099 | 0.14099 |  |  | 0.32595 | 0.32595 | 0.00128 | 0.00128 | 0 | 0 | 0.0011659 | 0.0011659 |  |  | 0.0016223 | 0.0016223 | 376 | 358.8 | NO
2013-05-29 | 0.0097488 | 0.0097488 | 0 | 0 | 0.012136 | 0.012136 |  |  | 0.0029907 | 0.0029907 | 0.00010559 | 0.00010559 | 0 | 0 | 0.00013266 | 0.00013266 |  |  | 2.8908e-05 | 2.8908e-05 | 232 | 224.4 | NO
2013-05-30 | 0.070296 | 0.070296 | 0 | 0 | 0.087845 | 0.087845 |  |  | 0.020581 | 0.020581 | 0.0013413 | 0.0013413 | 0 | 0 | 0.0016964 | 0.0016964 |  |  | 0.0003344 | 0.0003344 | 244 | 224.6 | NO
2013-05-31 | 0.021212 | 0.021212 | 0 | 0 | 0.026406 | 0.026406 |  |  | 0.0064995 | 0.0064995 | 0.00024005 | 0.00024005 | 0 | 0 | 0.00029122 | 0.00029122 |  |  | 9.5425e-05 | 9.5425e-05 | 210 | 188.4 | NO
2013-06-01 | 0.043383 | 0.043383 | 0 | 0 | 0.029991 | 0.029991 |  |  | 0.082411 | 0.082411 | 0.0018286 | 0.0018286 | 0 | 0 | 0.0009854 | 0.0009854 |  |  | 0.004276 | 0.004276 | 196 | 179.6 | NO
2013-06-02 | 0.15159 | 0.15159 | 0 | 0 | 0.0034083 | 0.0034083 |  |  | 0.57988 | 0.57988 | 0.0022678 | 0.0022678 | 0 | 0 | 3.7192e-05 | 3.7192e-05 |  |  | 0.0087146 | 0.0087146 | 197 | 179 | NO
2013-06-03 | 0.14164 | 0.14164 | 0 | 0 | 0.1836 | 0.1836 |  |  | 0.022396 | 0.022396 | 0.003497 | 0.003497 | 0 | 0 | 0.0040392 | 0.0040392 |  |  | 0.0019742 | 0.0019742 | 409 | 348.6 | NO
2013-06-04 | 0.024377 | 0.024377 | 0 | 0 | 0.031389 | 0.031389 |  |  | 0.0044478 | 0.0044478 | 0.00023347 | 0.00023347 | 0 | 0 | 0.00030105 | 0.00030105 |  |  | 4.1373e-05 | 4.1373e-05 | 264 | 230.8 | NO
2013-06-05 | 0.072684 | 0.072684 | 0 | 0 | 0.093842 | 0.093842 |  |  | 0.012523 | 0.012523 | 0.00096313 | 0.00096313 | 0 | 0 | 0.0012388 | 0.0012388 |  |  | 0.0001794 | 0.0001794 | 261 | 210.2 | NO
2013-06-06 | 0.01638 | 0.01638 | 0 | 0 | 0.019968 | 0.019968 |  |  | 0.0062222 | 0.0062222 | 0.00015823 | 0.00015823 | 0 | 0 | 0.00019968 | 0.00019968 |  |  | 4.0515e-05 | 4.0515e-05 | 187 | 160.2 | NO
2013-06-07 | 0.15755 | 0.15755 | 0 | 0 | 0.20137 | 0.20137 |  |  | 0.03297 | 0.03297 | 0.0016043 | 0.0016043 | 0 | 0 | 0.0020965 | 0.0020965 |  |  | 0.00020277 | 0.00020277 | 271 | 245.4 | NO
2013-06-08 | 0.011071 | 0.011071 | 0 | 0 | 0.013764 | 0.013764 |  |  | 0.0034275 | 0.0034275 | 0.00014324 | 0.00014324 | 0 | 0 | 0.00018643 | 0.00018643 |  |  | 2.0265e-05 | 2.0265e-05 | 236 | 218.6 | NO
2013-06-09 | 0.095138 | 0.095138 | 0 | 0 | 0.0021708 | 0.0021708 |  |  | 0.36428 | 0.36428 | 0.00094598 | 0.00094598 | 0 | 0 | 1.506e-05 | 1.506e-05 |  |  | 0.0036409 | 0.0036409 | 153 | 137.2 | NO
2013-06-10 | 0.46395 | 0.46395 | 0 | 0 | 0.44434 | 0.44434 |  |  | 0.52558 | 0.52558 | 0.0061829 | 0.0061829 | 0 | 0 | 0.0049143 | 0.0049143 |  |  | 0.0099089 | 0.0099089 | 428 | 344 | NO
2013-06-11 | 0.13027 | 0.13027 | 0 | 0 | 0.15219 | 0.15219 |  |  | 0.068456 | 0.068456 | 0.0018818 | 0.0018818 | 0 | 0 | 0.0019696 | 0.0019696 |  |  | 0.0016491 | 0.0016491 | 360 | 306.2 | NO
2013-06-12 | 0.27923 | 0.27923 | 0 | 0 | 0.33904 | 0.33904 |  |  | 0.10979 | 0.10979 | 0.0035382 | 0.0035382 | 0 | 0 | 0.004379 | 0.004379 |  |  | 0.0011521 | 0.0011521 | 347 | 288.6 | NO
2013-06-13 | 0.11489 | 0.11489 | 0 | 0 | 0.10185 | 0.10185 |  |  | 0.15377 | 0.15377 | 0.0014939 | 0.0014939 | 0 | 0 | 0.0015717 | 0.0015717 |  |  | 0.0012855 | 0.0012855 | 339 | 301 | NO
2013-06-14 | 0.22528 | 0.22528 | 0 | 0 | 0.2997 | 0.2997 |  |  | 0.013051 | 0.013051 | 0.0026175 | 0.0026175 | 0 | 0 | 0.0034378 | 0.0034378 |  |  | 0.00027943 | 0.00027943 | 295 | 272 | NO
2013-06-15 | 0.11467 | 0.11467 | 0 | 0 | 0.037342 | 0.037342 |  |  | 0.33904 | 0.33904 | 0.0038328 | 0.0038328 | 0 | 0 | 0.00075989 | 0.00075989 |  |  | 0.012741 | 0.012741 | 236 | 163.2 | NO
2013-06-16 | 0.11809 | 0.11809 | 0 | 0 | 0.15861 | 0.15861 |  |  | 0.0024426 | 0.0024426 | 0.0013857 | 0.0013857 | 0 | 0 | 0.0018631 | 0.0018631 |  |  | 2.3169e-05 | 2.3169e-05 | 147 | 118.2 | NO
2013-06-17 | 0.14089 | 0.14089 | 0 | 0 | 0.14291 | 0.14291 |  |  | 0.13659 | 0.13659 | 0.0026761 | 0.0026761 | 0 | 0 | 0.0015672 | 0.0015672 |  |  | 0.005906 | 0.005906 | 341 | 279.6 | NO
2013-06-18 | 0.4291 | 0.4291 | 0 | 0 | 0.26797 | 0.26797 |  |  | 0.89896 | 0.89896 | 0.0036595 | 0.0036595 | 0 | 0 | 0.0021011 | 0.0021011 |  |  | 0.0081981 | 0.0081981 | 351 | 313.4 | NO
2013-06-19 | 0.036313 | 0.036313 | 0 | 0 | 0.018039 | 0.018039 |  |  | 0.089469 | 0.089469 | 0.00041572 | 0.00041572 | 0 | 0 | 6.7707e-05 | 6.7707e-05 |  |  | 0.0014251 | 0.0014251 | 266 | 231.8 | NO
2013-06-20 | 0.13285 | 0.13285 | 0 | 0 | 0.16531 | 0.16531 |  |  | 0.04057 | 0.04057 | 0.0016914 | 0.0016914 | 0 | 0 | 0.0021986 | 0.0021986 |  |  | 0.00024581 | 0.00024581 | 246 | 224.8 | NO
2013-06-21 | 0.42697 | 0.42697 | 0 | 0 | 0.45569 | 0.45569 |  |  | 0.34868 | 0.34868 | 0.0017962 | 0.0017962 | 0 | 0 | 0.0013404 | 0.0013404 |  |  | 0.0031318 | 0.0031318 | 256 | 218.8 | NO
2013-06-22 | 0.0054145 | 0.0054145 | 0 | 0 | 0.0041175 | 0.0041175 |  |  | 0.0092191 | 0.0092191 | 6.7617e-05 | 6.7617e-05 | 0 | 0 | 5.7179e-05 | 5.7179e-05 |  |  | 9.8494e-05 | 9.8494e-05 | 206 | 196.4 | NO
2013-06-23 | 0.15443 | 0.15443 | 0 | 0 | 0.20799 | 0.20799 |  |  | 0.0014372 | 0.0014372 | 0.0025907 | 0.0025907 | 0 | 0 | 0.0034868 | 0.0034868 |  |  | 3.1327e-05 | 3.1327e-05 | 172 | 143.2 | NO
2013-06-24 | 0.018538 | 0.018538 | 0 | 0 | 0.016598 | 0.016598 |  |  | 0.024342 | 0.024342 | 0.00023319 | 0.00023319 | 0 | 0 | 0.00019089 | 0.00019089 |  |  | 0.00035788 | 0.00035788 | 252 | 230.4 | NO
2013-06-25 | 0.0063634 | 0.0063634 | 0 | 0 | 0.0070498 | 0.0070498 |  |  | 0.0044503 | 0.0044503 | 6.4563e-05 | 6.4563e-05 | 0 | 0 | 6.5597e-05 | 6.5597e-05 |  |  | 6.2279e-05 | 6.2279e-05 | 243 | 212.8 | NO
2013-06-26 | 0.59846 | 0.59846 | 0 | 0 | 0.75941 | 0.75941 |  |  | 0.14011 | 0.14011 | 0.0004717 | 0.0004717 | 0 | 0 | 0.00037954 | 0.00037954 |  |  | 0.00074301 | 0.00074301 | 250 | 214 | NO
2013-06-27 | 0.30902 | 0.30902 | 0 | 0 | 0.24535 | 0.24535 |  |  | 0.49627 | 0.49627 | 0.0087374 | 0.0087374 | 0 | 0 | 0.009929 | 0.009929 |  |  | 0.0053906 | 0.0053906 | 369 | 301.2 | NO
2013-06-28 | 0.048314 | 0.048314 | 0 | 0 | 0.0317 | 0.0317 |  |  | 0.096829 | 0.096829 | 0.0004123 | 0.0004123 | 0 | 0 | 0.00016222 | 0.00016222 |  |  | 0.0011391 | 0.0011391 | 273 | 245.4 | NO
2013-06-29 | 0.071555 | 0.071555 | 0 | 0 | 0.091011 | 0.091011 |  |  | 0.016259 | 0.016259 | 0.0011466 | 0.0011466 | 0 | 0 | 0.0014279 | 0.0014279 |  |  | 0.00034818 | 0.00034818 | 233 | 197.2 | NO
2013-06-30 |  | 0 | 0 | 0 | 0.0013516 | 0.0013516 |  |  | 0.0015885 | 0.0015885 | 0 | 0 | 0 | 0 | 1.3044e-05 | 1.3044e-05 |  |  | 1.4459e-05 | 1.4459e-05 | 104 | 100.2 | NO
Contents