## Cover
Amendments made on 6 August 2014.
Click here for details.
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | Energex
DNSP - Australian business number: |  | 40078849055
Reporting year: |  | 2013-14
Business address | Address |  | 26 Reddacliff Street
| Suburb |  | Newstead
|  | State | Queensland | Postcode | 4006
Postal address | Address |  | GPO Box1461
| Suburb |  | Brisbane
|  | State | Queensland | Postcode | 4001
Contact name/s | Ben Moran
Contact phone/s | 07 3664 5839
Contact email address/s | benmoran@energex.com.au

## Contents
Electricity DNSP Annual Reporting Template
Table of contents
Cover sheet | 3. Quality of service and customer service
1. Service Target Performance Incentive Scheme | 4. General Information (deleted)
1a. STPIS - Reliability | 5. Outages
1b. STPIS - Customer service | 5a. Network data - outages (deleted)
1c. STPIS - Daily performance | 5b. Network data - feeder reliability
1d. STPIS - MED threshold (deleted) | 5c. Network data - outages (deleted)
1e. STPIS - Exclusions (deleted) | 5d. Network data - planned outages
1f. STPIS - GSL | 6. Weighted average cost of debt (deleted)
2. Demand (deleted) | 7. Asset installation (deleted)

## 1a. STPIS Reliability
Energex
STPIS Data Reporting
2013-14
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI
Unplanned SAIDI | CBD | Urban | Rural short | Rural long | Whole network
Total | 2.21 | 72.66 | 164.41 | N/A | 97.196
Total - after removing excluded events | 1.72 | 54.06 | 113.91 | N/A | 70.04
Table 2: SAIFI
Unplanned SAIFI | CBD | Urban | Rural short | Rural long | Whole network
Total | 0.1349 | 0.8334 | 1.5587 | N/A | 1.027
Total - after removing excluded events | 0.0118 | 0.7331 | 1.3333 | N/A | 0.8929
Table 3: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers at the start of period | 3753 | 980215 | 363116 | 0 | 1347084
Customer numbers at the end of period | 3737 | 992362 | 367386 | 0 | 1363485
Average distribution customer numbers | 3745 | 986288.5 | 365251 | 0 | 1355284.5
Contents

## 1b. STPIS Customer Service
Energex
STPIS Data Reporting
2013-14
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering
Telephone answering | Total - after removing excluded events | Total
Total number of calls | 102029 | 109361
Number of calls answered within 30 seconds | 86451
Percentage of calls answered within 30 seconds | 84.73%
Table 2: New connections
Note: this is for newly energised properties only
New connections
Number of new connections
Number of new connections not provided on or before the agreed date
Percentage of new connections not provided on or before the agreed date
Table 3: Streetlight repair
Streetlight repair
Total number of streetlights
Total number of streetlight faults
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neigbouring business
Faulty streetlights not repaired within 5 days of fault report or agreed date
Percentage of faulty streetlights not repaired within 5 days of fault report or agreed date
Table 4 Response to written enquiries
Note: this does not include Saturdays, Sundays and Public holidays
Response to written enquiries
Number of written enquiries
Number of written enquiries not responded to in 5 days
Percentage of written enquiries not responded to in 5 days
Contents

## 1c. STPIS Daily Performance
Energex
STPIS Data Reporting |  |  | 2012-07-01
2013-14 |  |  | 2013-07-01
Daily Performance |  |  | 2014-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Daily performance data (Unplanned SAIDI, Unplanned SAIFI)
Note: the excluded events to be removed from the data refer only to events listed in clause 3.3(a) of the STPIS, with respect to reliability data, and in clause 5.4(a) of the STPIS with respect to customer service parameters.
Customer service
Date | Total number of calls (after removing excluded events) | Total number of calls answered in 30 seconds (after removing excluded events)
2013-07-01 | 377 | 317.8
2013-07-02 | 310 | 267.6
2013-07-03 | 307 | 276.6
2013-07-04 | 218 | 204.6
2013-07-05 | 311 | 232
2013-07-06 | 176 | 144.4
2013-07-07 | 94 | 89.2
2013-07-08 | 279 | 259
2013-07-09 | 223 | 210.4
2013-07-10 | 281 | 248.8
2013-07-11 | 250 | 227
2013-07-12 | 220 | 208.8
2013-07-13 | 157 | 149.2
2013-07-14 | 143 | 135
2013-07-15 | 324 | 296.4
2013-07-16 | 442 | 337.8
2013-07-17 | 188 | 176.2
2013-07-18 | 236 | 219.6
2013-07-19 | 304 | 274.4
2013-07-20 | 197 | 166.6
2013-07-21 | 101 | 99.2
2013-07-22 | 379 | 310.4
2013-07-23 | 224 | 212.6
2013-07-24 | 304 | 259.4
2013-07-25 | 333 | 309.4
2013-07-26 | 239 | 213.6
2013-07-27 | 254 | 219.8
2013-07-28 | 110 | 97.6
2013-07-29 | 243 | 236.4
2013-07-30 | 205 | 189
2013-07-31 | 189 | 164.2
2013-08-01 | 200 | 172
2013-08-02 | 184 | 173.8
2013-08-03 | 259 | 229.6
2013-08-04 | 137 | 133.4
2013-08-05 | 302 | 254.6
2013-08-06 | 273 | 254.2
2013-08-07 | 240 | 218.8
2013-08-08 | 339 | 311.6
2013-08-09 | 186 | 177.4
2013-08-10 | 185 | 167.4
2013-08-11 | 139 | 118.4
2013-08-12 | 252 | 230
2013-08-13 | 207 | 191.6
2013-08-14 | 180 | 177.2
2013-08-15 | 199 | 185.2
2013-08-16 | 323 | 223.4
2013-08-17 | 153 | 127.6
2013-08-18 | 91 | 84.4
2013-08-19 | 311 | 282.8
2013-08-20 | 295 | 264.8
2013-08-21 | 274 | 200.8
2013-08-22 | 220 | 202.8
2013-08-23 | 228 | 196.8
2013-08-24 | 216 | 180.4
2013-08-25 | 135 | 126.6
2013-08-26 | 213 | 178.2
2013-08-27 | 201 | 189.4
2013-08-28 | 213 | 190.6
2013-08-29 | 201 | 187.2
2013-08-30 | 293 | 241.4
2013-08-31 | 176 | 151.2
2013-09-01 | 98 | 94.2
2013-09-02 | 220 | 201.2
2013-09-03 | 266 | 234.6
2013-09-04 | 216 | 205.2
2013-09-05 | 274 | 242.6
2013-09-06 | 227 | 203.4
2013-09-07 | 148 | 137
2013-09-08 | 111 | 102.4
2013-09-09 | 238 | 215
2013-09-10 | 264 | 231.8
2013-09-11 | 284 | 259.2
2013-09-12 | 265 | 236.8
2013-09-13 | 309 | 251.6
2013-09-14 | 235 | 185.8
2013-09-15 | 248 | 212.2
2013-09-16 | 531 | 450.8
2013-09-17 | 560 | 435.4
2013-09-18 | 313 | 268.6
2013-09-19 | 274 | 252.2
2013-09-20 | 192 | 181.2
2013-09-21 | 206 | 190.4
2013-09-22 | 139 | 132
2013-09-23 | 262 | 239.6
2013-09-24 | 358 | 314.6
2013-09-25 | 268 | 243
2013-09-26 | 237 | 205.8
2013-09-27 | 224 | 191.2
2013-09-28 | 212 | 172.2
2013-09-29 | 114 | 100.6
2013-09-30 | 270 | 243.2
2013-10-01 | 355 | 275.2
2013-10-02 | 309 | 286.8
2013-10-03 | 365 | 309
2013-10-04 | 264 | 213
2013-10-05 | 214 | 193.8
2013-10-06 | 109 | 106.2
2013-10-07 | 215 | 198
2013-10-08 | 286 | 249.2
2013-10-09 | 230 | 202
2013-10-10 | 279 | 252.4
2013-10-11 | 304 | 256.6
2013-10-12 | 203 | 174.6
2013-10-13 | 162 | 145.6
2013-10-14 | 368 | 344.4
2013-10-15 | 219 | 210.4
2013-10-16 | 305 | 272.2
2013-10-17 | 263 | 249.4
2013-10-18 | 334 | 299.6
2013-10-19 | 261 | 210.2
2013-10-20 | 159 | 145.4
2013-10-21 | 431 | 393.2
2013-10-22 | 313 | 275.8
2013-10-23 | 208 | 196.8
2013-10-24 | 279 | 235.2
2013-10-25 | 259 | 239.4
2013-10-26 | 198 | 170
2013-10-27 | 116 | 109.2
2013-10-28 | 253 | 231.4
2013-10-29 | 405 | 363
2013-10-30 | 320 | 282.8
2013-10-31 | 308 | 249.2
2013-11-01 | 237 | 206.4
2013-11-02 | 187 | 163.2
2013-11-03 | 181 | 156.4
2013-11-04 | 234 | 220.6
2013-11-05 | 204 | 195
2013-11-06 | 216 | 211.4
2013-11-07 | 230 | 189.8
2013-11-08 | 297 | 246.4
2013-11-09 | 162 | 160.2
2013-11-10 | 0 | 0
2013-11-11 | 601 | 461.4
2013-11-12 | 288 | 247.2
2013-11-13 | 463 | 382.2
2013-11-14 | 748 | 589.6
2013-11-15 | 401 | 352.8
2013-11-16 | 678 | 416.4
2013-11-17 | 263 | 218.6
2013-11-18 | 699 | 518
2013-11-19 | 577 | 480.8
2013-11-20 | 461 | 335
2013-11-21 | 295 | 262
2013-11-22 | 228 | 196.4
2013-11-23 | 669 | 500.4
2013-11-24 | 897 | 637
2013-11-25 | 371 | 314
2013-11-26 | 329 | 298.8
2013-11-27 | 347 | 298.2
2013-11-28 | 284 | 212.2
2013-11-29 | 287 | 251.8
2013-11-30 | 417 | 326.4
2013-12-01 | 141 | 129.8
2013-12-02 | 313 | 272.6
2013-12-03 | 212 | 197.8
2013-12-04 | 321 | 251.4
2013-12-05 | 374 | 320.8
2013-12-06 | 257 | 237.2
2013-12-07 | 194 | 168.8
2013-12-08 | 122 | 115
2013-12-09 | 280 | 225.8
2013-12-10 | 313 | 232.4
2013-12-11 | 362 | 280.4
2013-12-12 | 388 | 342.6
2013-12-13 | 295 | 239.6
2013-12-14 | 231 | 216.2
2013-12-15 | 199 | 180.6
2013-12-16 | 273 | 240.4
2013-12-17 | 292 | 254
2013-12-18 | 250 | 216.8
2013-12-19 | 232 | 211.6
2013-12-20 | 380 | 292
2013-12-21 | 141 | 129.8
2013-12-22 | 220 | 180
2013-12-23 | 232 | 216
2013-12-24 | 213 | 189.8
2013-12-25 | 430 | 274.4
2013-12-26 | 124 | 98.8
2013-12-27 | 368 | 331.6
2013-12-28 | 270 | 228.6
2013-12-29 | 0 | 0
2013-12-30 | 614 | 520.6
2013-12-31 | 352 | 313.8
2014-01-01 | 181 | 145.8
2014-01-02 | 848 | 592
2014-01-03 | 572 | 392
2014-01-04 | 1972 | 955.6
2014-01-05 | 365 | 295.4
2014-01-06 | 0 | 0
2014-01-07 | 1324 | 1032.6
2014-01-08 | 480 | 412.8
2014-01-09 | 294 | 264.4
2014-01-10 | 301 | 273.8
2014-01-11 | 279 | 219
2014-01-12 | 177 | 158.6
2014-01-13 | 427 | 343.6
2014-01-14 | 264 | 242.2
2014-01-15 | 300 | 261.6
2014-01-16 | 275 | 247.4
2014-01-17 | 254 | 211.6
2014-01-18 | 231 | 203.6
2014-01-19 | 169 | 153.2
2014-01-20 | 272 | 236.6
2014-01-21 | 404 | 311.2
2014-01-22 | 588 | 426.4
2014-01-23 | 665 | 437.4
2014-01-24 | 465 | 404.8
2014-01-25 | 297 | 249.8
2014-01-26 | 257 | 218.2
2014-01-27 | 210 | 188
2014-01-28 | 336 | 298.6
2014-01-29 | 326 | 279.6
2014-01-30 | 329 | 288.2
2014-01-31 | 279 | 236.6
2014-02-01 | 210 | 187.2
2014-02-02 | 180 | 128.2
2014-02-03 | 320 | 271.2
2014-02-04 | 267 | 206.4
2014-02-05 | 417 | 345.6
2014-02-06 | 294 | 253.4
2014-02-07 | 273 | 236
2014-02-08 | 193 | 164
2014-02-09 | 124 | 119.6
2014-02-10 | 243 | 231.4
2014-02-11 | 221 | 211.2
2014-02-12 | 253 | 231.4
2014-02-13 | 362 | 315.6
2014-02-14 | 264 | 246
2014-02-15 | 241 | 219
2014-02-16 | 412 | 299.6
2014-02-17 | 358 | 296.4
2014-02-18 | 442 | 385.4
2014-02-19 | 458 | 393
2014-02-20 | 386 | 319.4
2014-02-21 | 538 | 441.8
2014-02-22 | 298 | 229.2
2014-02-23 | 248 | 207.4
2014-02-24 | 316 | 267.4
2014-02-25 | 255 | 228.4
2014-02-26 | 227 | 213.4
2014-02-27 | 240 | 220.6
2014-02-28 | 361 | 293.4
2014-03-01 | 361 | 264.6
2014-03-02 | 247 | 228.8
2014-03-03 | 328 | 291.4
2014-03-04 | 242 | 200.4
2014-03-05 | 297 | 276.2
2014-03-06 | 254 | 239.4
2014-03-07 | 202 | 182.6
2014-03-08 | 171 | 145.4
2014-03-09 | 164 | 121
2014-03-10 | 344 | 275.4
2014-03-11 | 271 | 215.8
2014-03-12 | 246 | 222.2
2014-03-13 | 224 | 179
2014-03-14 | 217 | 201.2
2014-03-15 | 125 | 119.2
2014-03-16 | 440 | 331.6
2014-03-17 | 364 | 299.4
2014-03-18 | 385 | 278.2
2014-03-19 | 249 | 211.6
2014-03-20 | 249 | 233
2014-03-21 | 246 | 228
2014-03-22 | 145 | 139.2
2014-03-23 | 93 | 92
2014-03-24 | 278 | 246
2014-03-25 | 319 | 283.2
2014-03-26 | 281 | 249
2014-03-27 | 481 | 401.2
2014-03-28 | 626 | 533.2
2014-03-29 | 318 | 247
2014-03-30 | 280 | 254.6
2014-03-31 | 361 | 311.6
2014-04-01 | 346 | 298
2014-04-02 | 292 | 244.4
2014-04-03 | 285 | 223
2014-04-04 | 265 | 206.4
2014-04-05 | 226 | 182.6
2014-04-06 | 497 | 317.8
2014-04-07 | 348 | 281.6
2014-04-08 | 221 | 193.4
2014-04-09 | 233 | 216.2
2014-04-10 | 274 | 244.4
2014-04-11 | 317 | 282.4
2014-04-12 | 212 | 189.6
2014-04-13 | 141 | 134.2
2014-04-14 | 444 | 338.4
2014-04-15 | 231 | 207
2014-04-16 | 263 | 230.4
2014-04-17 | 207 | 191.2
2014-04-18 | 240 | 220.6
2014-04-19 | 197 | 175.8
2014-04-20 | 98 | 88.2
2014-04-21 | 137 | 113.2
2014-04-22 | 246 | 243.2
2014-04-23 | 305 | 266.2
2014-04-24 | 204 | 180.4
2014-04-25 | 98 | 93.4
2014-04-26 | 145 | 129
2014-04-27 | 172 | 167.2
2014-04-28 | 230 | 211.6
2014-04-29 | 263 | 230.8
2014-04-30 | 278 | 245.6
2014-05-01 | 275 | 230.4
2014-05-02 | 276 | 229
2014-05-03 | 245 | 215.2
2014-05-04 | 248 | 206.6
2014-05-05 | 311 | 249.8
2014-05-06 | 259 | 229.8
2014-05-07 | 303 | 217.6
2014-05-08 | 202 | 181
2014-05-09 | 210 | 206.2
2014-05-10 | 181 | 165.8
2014-05-11 | 100 | 96
2014-05-12 | 349 | 292
2014-05-13 | 219 | 212
2014-05-14 | 313 | 278.6
2014-05-15 | 337 | 282.6
2014-05-16 | 374 | 296.2
2014-05-17 | 221 | 192.4
2014-05-18 | 132 | 126.6
2014-05-19 | 278 | 251.6
2014-05-20 | 349 | 263.6
2014-05-21 | 319 | 283.4
2014-05-22 | 345 | 273.4
2014-05-23 | 227 | 210
2014-05-24 | 137 | 127
2014-05-25 | 115 | 105.4
2014-05-26 | 204 | 180
2014-05-27 | 184 | 159
2014-05-28 | 215 | 179.6
2014-05-29 | 265 | 205.6
2014-05-30 | 207 | 186
2014-05-31 | 200 | 160.8
2014-06-01 | 88 | 84.4
2014-06-02 | 219 | 196.8
2014-06-03 | 257 | 229.8
2014-06-04 | 190 | 182.2
2014-06-05 | 225 | 186.4
2014-06-06 | 253 | 217
2014-06-07 | 185 | 177
2014-06-08 | 124 | 116
2014-06-09 | 145 | 136.4
2014-06-10 | 245 | 225
2014-06-11 | 188 | 170
2014-06-12 | 195 | 180.6
2014-06-13 | 256 | 224
2014-06-14 | 170 | 160.2
2014-06-15 | 162 | 151.6
2014-06-16 | 224 | 206.4
2014-06-17 | 330 | 254.4
2014-06-18 | 235 | 218.6
2014-06-19 | 221 | 205
2014-06-20 | 273 | 245.6
2014-06-21 | 197 | 182.8
2014-06-22 | 161 | 146.6
2014-06-23 | 248 | 243
2014-06-24 | 312 | 280.2
2014-06-25 | 358 | 295.2
2014-06-26 | 238 | 221
2014-06-27 | 246 | 218.4
2014-06-28 | 234 | 215.6
2014-06-29 | 244 | 230.4
2014-06-30 | 297 | 259.6
Contents

## 1f. STPIS GSL
Energex
STPIS Data Reporting - AER Definitions
2013-14
Guaranteed Service Level
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Did the AER's GSL Scheme apply at any time during the regulatory year? | No
If the AER's GSL scheme applied at any time during the regulatory year, table 1 must be completed. Do not complete table 1 if the AER's GSL scheme did not apply during the regulatory year.
Table 1: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
Total GSL payments payable under the AER's GSL scheme ($) | 0
Contents

## 3. Outcomes customer service
Energex
Customer Service
2013-14
This information is used to monitor the service performance of the DNSP, and assist the AER understand service outcomes for customers. The information will inform the AER’s assessment of future service improvement expenditure proposals by the DNSP. The information may be used in performance reports.
Table 1: Quality of supply
2013/14
Over voltage events - due to high voltage injection
Customers receiving over-voltage - due to high voltage injection
Over voltage events - due to lightning
Customers receiving over-voltage - due to lightning
Over voltage events - due to voltage regulation or other cause
Customers receiving over-voltage - due to voltage regulation or other cause
Voltage variations - steady state (zone sub)
Voltage variations - one minute (zone sub)
Voltage variations - 10 seconds (zone sub) Min<0.7
Voltage variations - 10 seconds (zone sub) Min<0.8
Voltage variations - 10 seconds (zone sub) Min<0.9
Voltage variations - steady state (feeder)
Voltage variations - % zone subs monitored
Voltage variations - % feeders monitored
Customers - quality of supply improvement
Table 2: Complaints - technical quality of supply
2013/14
Complaints - technical quality of supply - number | 1363
Complaints by category (%)
Low voltage supply | 8.3
Voltage dips | 19.7
Voltage swell | 15.3
Voltage spike (impulsive transient) | 3.4
Waveform distortion | 4.2
TV or radio interference | 2.6
Noise from appliances | 3.8
Solar related | 42.7
Other | 0
Complaints by Likely Cause (%)
Network equipment faulty | 4.4
Network interference by NSP equipment | 10.6
Network interference by another customer | 0.6
Network limitation | 23.5
Customer internal problem | 23
No problem identified | 28.3
Environmental | 0.6
Other | 9
Table 3: Customer service
2013/14
Timely provision of services
Connections made | 23904
Connections not made on agreed date | 31
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 637
Streetlights - not repaired by "fix by" date | 14
Streetlights - average number of days to repair | 4
Total streetlights | 304575
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 365541
Calls to fault line not answered within 30 seconds | 19507
Calls to fault line - average waiting time before call answered | 23
Calls abandoned - percentage | 5
Call centre - number of overload events | 0
Customer complaints (number)
Complaint - reliability of supply | 93
Complaint - technical quality of supply | 1363
Complaint - administrative process or customer service | 1296
Complaint - connection or augmentation | 1393
Complaint - other | 165
Total complaints | 2947
Contents

## 5b. Network data feeder
Energex
Network data - Feeder Reliability
2013-14
The information in templates 5b and 5d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Annual Feeder Reliability Data
Feeder ID / name | Geographical description of feeder | Feeder classification | Number of distribution customers (average) | Length of distribution lines - high voltage - overhead | Length of distribution lines - high voltage - underground | Maximum demand (MW) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply | Planned interruptions (SAIFI)
1084 | MORNINGSIDE | Urban | 36 | 0.636 | 1.438 |  | 0.15354 | 0.13926 | 1 | 258 | 258 | 3.04e-06 | 3.04e-06 | 1 | 234 | 1.01e-06
1129 | ROCKLEA | Urban | 354 | 3.485 | 0.712 |  | 8.172 | 0.42574 | 11 | 254218.3 | 46890.29 | 0.001108 | 0.000751 | 6 | 13244.13 | 5.41e-05
1256 | ROCKLEA | Urban | 2 | [5 empty] | 1 | 92 | 92 | 2.03e-06 | 2.03e-06
1369 | SOUTH BRISBANE | Urban | 5
ABT7 | MURARRIE | Urban | 3
ABT8 | MORNINGSIDE | Urban | 2 | 0 | 0.167 |  | 13.3011 | 10.3303 | 1 | 591 | 591 | 3.04e-06 | 3.04e-06 | 2 | 459 | 3.04e-06
ABTQPT95 | MURARRIE | Urban | 2 | 0 | 2.23 | 4.077
ABY2A | AMBERLEY, MUTDAPILLY, PURGA, WILLOWBANK | Rural short | 457 | 36.57 | 1.958 | 1.715
ABY5A | AMBERLEY, JEEBROPILLY, WALLOON | Rural short | 26 | 12.968 | 0.204 | 2.21
ACFQBI5 | PINKENBA | Urban | 21 | 2.073 | 1.104
ACR1 | ALBANY CREEK, EATONS HILL | Urban | 423 | 2.874 | 0.086 | 1.048 | 1.3397 | 0.053076 | 6 | 57084.77 | 4012.767 | 0.000886 | 0.000452 | 2 | 2261.59 | 1e-05
ACR12A | ALBANY CREEK, BRIDGEMAN DOWNS | Urban | 1353 | 2.626 | 7.719 | 4.82 | 3.1243 | 0.033523 | 7 | 175380.9 | 7546.883 | 0.002803 | 0.001431 | 2 | 1881.8 | 7.26e-06
ACR13A | ALBANY CREEK | Urban | 1052 | 0 | 7.131 | 3.182 | 2.0411 | 0.026835 | 3 | 131932.8 | 3220.8 | 0.002104 | 0.001051 | 1 | 1734.56 | 1.19e-05
ACR2 | ALBANY CREEK | Urban | 1182 | 0.062 | 6.56 | 4.63 | 2.1085 | 0.021296 | 4 | 155280.4 | 6852.433 | 0.002468 | 0.001254 | 3 | 1568.38 | 1.6e-05
ACR3 | ALBANY CREEK, BRIDGEMAN DOWNS, MCDOWALL | Urban | 1117 | 3.623 | 6.701 | 4.02 | 11.6908 | 0.69208 | 6 | 448791.3 | 310655.3 | 0.003407 | 0.002277 | 3 | 26567.86 | 9.75e-05
ACR4 | ALBANY CREEK | Urban | 746 | 4.703 | 0.522 | 3.83 | 6.9339 | 0.016465 | 8 | 178976.8 | 87054.43 | 0.002346 | 0.001596 | 1 | 425 | 1.01e-06
ACR5 | ALBANY CREEK, BUNYA, DRAPER, EATONS HILL | Rural short | 1322 | 24.347 | 5.105 | 4.687
ACR6 | ALBANY CREEK, BRIDGEMAN DOWNS | Rural short | 919 | 7.242 | 0.894 | 2.515
ADAMAA1 | BRISBANE | Urban | 13 | 0 | 0.306
ADAMLS23 | BRISBANE, FORTITUDE VALLEY, SPRING HILL | Urban | 26 | 0 | 2.002 | 4.154
AFD1A | ROCKLEA | Urban | 125 | 2.084 | 1.528 | 3.163 | 0.28149 |  | 4 | 2082.817 | 2082.817 | 1.77e-05 | 1.77e-05
AFD1B | ROCKLEA | Urban | 50 | 1.646 | 1.018 | 1.353 |  | 1.6361 | [5 empty] | 2 | 2355 | 6.08e-06
AFD3A | ROCKLEA | Urban | 8 | 0.632 | 0.31 | 3.389
AFD5 | ARCHERFIELD, ROCKLEA | Urban | 27 | 0.446 | 0.304 | 2.991 |  | 5.4278 | [5 empty] | 2 | 4935 | 1.32e-05
AFD6 | ROCKLEA | Urban | 145 | 2.429 | 1.261 | 4.306 | 0.25795 |  | 6 | 1768.213 | 1768.213 | 2.81e-05 | 2.81e-05
AFD7 | ROCKLEA | Urban | 78 | 1.22 | 1.701 | 2.21
AFDCIG4 | ARCHERFIELD, ROCKLEA | Urban | 116.5 | 0.68 | 1.174 | 1.448 | 0.006083 | 0.048542 | 2 | 131.2 | 131.2 | 2.03e-06 | 2.03e-06 | 1 | 1047 | 3.04e-06
AGE10 | ASHGROVE, BARDON, PADDINGTON | Urban | 2245 | 8.152 | 1.56 | 4.94 | 3.3435 | 0.32362 | 22 | 236851.7 | 236851.7 | 0.00934 | 0.00934 | 11 | 22925.09 | 9.61e-05
AGE16B | ASHGROVE | Urban | 766 | 3.76 | 0.731 |  | 0.096627 |  | 5 | 5353.095 | 5353.095 | 0.000806 | 0.000806
AGE2 | ASHGROVE, BARDON | Urban | 517 | 3.14 | 1.894 | 1.405 | 0.029363 | 0.28729 | 5 | 1968.83 | 1968.83 | 0.000528 | 0.000528 | 11 | 19263.54 | 9.08e-05
AGE3 | PADDINGTON, RED HILL | Urban | 2139.5 | 5.133 | 4.321 | 4.516 | 9.8746 | 1.4605 | 14 | 645244.5 | 645244.5 | 0.008352 | 0.008352 | 21 | 95434.24 | 0.000338
AGE5B | ASHGROVE | Urban | 765 | 1.221 | 0.76 | 1.81 | 0.049623 | 0.039173 | 2 | 2394.167 | 2394.167 | 0.000777 | 0.000777 | 1 | 1890 | 1.42e-05
AGE6A | ASHGROVE, NEWMARKET, RED HILL | Urban | 1088 | 3.42 | 1.037 | 3.239 | 1.3193 | 0.86452 | 7 | 64126.2 | 64126.2 | 0.001615 | 0.001615 | 7 | 42021.89 | 0.000204
AGE7B | ASHGROVE | Urban | 975 | 5.454 | 0.512 | 2.61 | 0.70141 | 0.21284 | 8 | 36358.61 | 36358.61 | 0.002158 | 0.002158 | 5 | 11032.78 | 5.81e-05
AGE8 | ASHGROVE, THE GAP | Urban | 930 | 5.948 | 3.126 | 2.521 | 1.27 | 0.10945 | 6 | 69639.17 | 69639.17 | 0.001903 | 0.001903 | 4 | 6001.724 | 2.75e-05
AGE9 | ASHGROVE, BARDON, PADDINGTON, RED HILL | Urban | 1291 | 4.532 | 0.502 | 3.753 | 0.16622 | 0.006948 | 11 | 11358.48 | 11358.48 | 0.001412 | 0.001412 | 1 | 474.81 | 1.35e-06
AGT23A | ALGESTER, WILLAWONG | Urban | 1542 | 0.86 | 9.376 | 2.858 | 9.3727 |  | 8 | 717001.9 | 131404.9 | 0.003192 | 0.001633
AGT25A | ACACIA RIDGE, WILLAWONG | Urban | 1094 | 6.752 | 2.121 | 2.496 | 0.7273 | 0.61039 | 11 | 36933.21 | 36827.91 | 0.000211 | 0.000208 | 11 | 30996.42 | 0.000138
AGT27A | ACACIA RIDGE | Urban | 45 | 0 | 3.196 | 1.829 |  | 1.036 | [5 empty] | 2 | 4287 | 9.13e-06
AGT29A | ACACIA RIDGE | Urban | 99 | 0.136 | 2.939 | 2.286 | 2.8725 | 0.03045 | 5 | 22357 | 1157 | 0.000113 | 1.12e-05 | 2 | 237 | 6.08e-06
AGT31A | LARAPINTA, PALLARA, WILLAWONG | Rural short | 397 | 17.595 | 9.379 | 4.63
AGT33A | ACACIA RIDGE | Urban | 24 | 0.238 | 1.822 | 2.21
AGT35A | ACACIA RIDGE | Urban | 99 | 0.142 | 2.942 | 3.125 |  | 0.24798 | [5 empty] | 2 | 1213 | 1.01e-05
AGT37A | ACACIA RIDGE, ALGESTER, SUNNYBANK HILLS | Urban | 1521.8 | 4.789 | 6.141 | 3.43 | 9.8362 | 0.17918 | 4 | 607400.1 | 26082.65 | 0.001679 | 0.00014 | 2 | 11064.45 | 4.53e-05
AHD10A | MOOLOOLABA | Urban | 1584 | 4.613 | 2.378 | 3.045 | 0.017919 |  | 7 | 1473.084 | 1473.084 | 2.15e-05 | 2.15e-05
AHD10B | ALEXANDRA HEADLAND, MOOLOOLABA | Urban | 1056.7 | 1.71 | 3.256 | 3.258 | 0.008825 |  | 3 | 398.2333 | 398.2333 | 3.04e-06 | 3.04e-06
AHD12A | MAROOCHYDORE | Urban | 811 | 1.836 | 2.763 | 2.915 | 0.091894 | 0.75841 | 3 | 3693.753 | 3693.753 | 7.43e-05 | 7.43e-05 | 2 | 30485 | 0.000289
AHD15A | MAROOCHYDORE | Urban | 855.8 | 1.768 | 5.839 | 3.658 | 0.006572 | 1.6283 | 2 | 101.55 | 101.55 | 2.03e-06 | 2.03e-06 | 2 | 25161.21 | 7.13e-05
AHD15B | MAROOCHYDORE | Urban | 863.3 | 2.637 | 1.11 | 3.62 | 0.005563 | 0.21249 | 4 | 200.8167 | 200.8167 | 4.06e-06 | 4.06e-06 | 2 | 7669.966 | 3.49e-05
AHD16 | BUDERIM | Urban | 1335 | 6.399 | 1.749 | 3.313 | 0.051644 | 0.088493 | 11 | 4213.216 | 4213.216 | 4.59e-05 | 4.59e-05 | 3 | 7219.44 | 7.57e-05
AHD17 | MAROOCHYDORE | Urban | 174 | 0.364 | 4.233 | 3.43 | 0.040815 | 0.23568 | 2 | 132.5882 | 132.5882 | 2.03e-06 | 2.03e-06 | 1 | 765.6 | 2.94e-06
AHD18A | BUDERIM | Urban | 766 | 3.925 | 2.507 | 3.468 | 3.9739 | 1.952 | 7 | 139507.4 | 139507.4 | 0.001505 | 0.001505 | 7 | 68527.54 | 0.000273
AHD18B | BLI BLI, MAROOCHYDORE, MUDJIMBA, PACIFIC PARADISE, | Rural short | 2177 | 6.158 | 14.154 | 3.944
AHD19 | ALEXANDRA HEADLAND, MAROOCHYDORE | Urban | 1085 | 3.341 | 1.612 | 2.887 | 0.7234 |  | 7 | 35418.38 | 35418.38 | 0.000144 | 0.000144
AHD20 | ALEXANDRA HEADLAND, MAROOCHYDORE | Urban | 1137 | 2.368 | 2.674 | 3.506 | 0.070967 | 0.42304 | 2 | 2992.5 | 2992.5 | 2.89e-05 | 2.89e-05 | 2 | 17838.66 | 0.000102
AHD21 | BUDERIM | Urban | 1449 | 2.516 | 3.719 | 2.566 | 0.11241 | 0.15718 | 8 | 9160.43 | 9160.43 | 9.4e-05 | 9.4e-05 | 3 | 12808.77 | 4.7e-05
AHD22A | MAROOCHYDORE | Urban | 1195.6 | 4.301 | 4.233 | 4.477 | 2.8037 | 1.1286 | 10 | 108522.4 | 108522.4 | 0.00109 | 0.00109 | 10 | 43685.85 | 0.000211
AHD25A | BUDERIM, MAROOCHYDORE | Urban | 1515.5 | 3.973 | 6.014 | 4.864 | 1.4456 | 0.70283 | 8 | 95768.77 | 95768.77 | 0.001708 | 0.001708 | 11 | 46560.51 | 0.000189
AHD3A | MAROOCHYDORE | Urban | 5 | 0 | 2.84 | 3.163
AHD4A | BUDERIM, MINYAMA, MOOLOOLABA, MOUNTAIN CREEK | Urban | 544 | 5.287 | 4.302 | 3.753 | 0.029565 | 0.13482 | 3 | 872.6167 | 872.6167 | 0.000132 | 0.000132 | 4 | 3979.36 | 1.1e-05
AHD4B | BUDERIM, MAROOCHYDORE | Rural short | 531 | 2.915 | 3.799 | 1.867
AHD5 | ALEXANDRA HEADLAND, MOOLOOLABA | Urban | 2022.3 | 4.729 | 1.518 | 3.925 | 2.4176 |  | 6 | 140920.5 | 140920.5 | 0.002139 | 0.002139
AHD6 | ALEXANDRA HEADLAND, MAROOCHYDORE | Urban | 609 | 1.8 | 1.671 | 2.801 | 0.005628 | 0.1104 | 2 | 259.5833 | 259.5833 | 2.03e-06 | 2.03e-06 | 2 | 5092.5 | 3.19e-05
AHD7 | ALEXANDRA HEADLAND, MAROOCHYDORE | Urban | 923.7 | 3.017 | 0.899 | 2.382 | 1.8038 | 0.007437 | 10 | 96290.99 | 96290.99 | 0.001838 | 0.001838 | 1 | 397 | 1.01e-06
AHD8 | BUDERIM | Urban | 960 | 5.61 | 2.096 | 3.315 | 0.73638 | 0.40756 | 9 | 28350.73 | 28350.73 | 0.000142 | 0.000142 | 1 | 15690.96 | 4.78e-05
AHD9 | MOOLOOLABA | Urban | 500 | 5.312 | 2.33 | 2.706 | 0.004645 |  | 1 | 112.0833 | 112.0833 | 1.01e-06 | 1.01e-06
AHL11A | FERNY GROVE, FERNY HILLS | Rural short | 1267 | 4.351 | 7.622 | 3.22
AHL12A | ARANA HILLS, FERNY HILLS | Urban | 1706 | 7.971 | 2.599 | 4.232 | 1.9619 | 0.55906 | 9 | 150426.1 | 150426.1 | 0.001942 | 0.001942 | 12 | 42865.81 | 0.000166
AHL14A | ARANA HILLS, FERNY HILLS | Urban | 1421 | 5.409 | 0.399 | 4.344 | 2.2336 | 1.0574 | 8 | 157927.7 | 114247.7 | 0.001556 | 0.001443 | 18 | 74763.56 | 0.000328
AHL15B | EVERTON HILLS, EVERTON PARK, MCDOWALL | Urban | 1691.5 | 6.57 | 4.897 | 3.601 | 3.0131 | 1.0786 | 7 | 217219.1 | 217219.1 | 0.003109 | 0.003109 | 18 | 77757.57 | 0.000263
AHL4A | KEPERRA, MITCHELTON | Urban | 863 | 4.048 | 0.774 | 2.305 | 3.3764 | 0.9791 | 3 | 191223.9 | 191223.9 | 0.00088 | 0.00088 | 9 | 55451.25 | 0.000242
AHL5A | ARANA HILLS, BUNYA, EVERTON HILLS, FERNY HILLS | Rural short | 1201 | 13.473 | 3.682 | 3.468
AHL6A | ARANA HILLS, FERNY GROVE, FERNY HILLS | Urban | 2008 | 7.914 | 3.288 | 4.768 | 0.32778 | 0.72567 | 13 | 22465.4 | 22465.4 | 0.000214 | 0.000214 | 16 | 49735.61 | 0.000243
AHL8A | BRIDGEMAN DOWNS, BUNYA, EVERTON HILLS, MCDOWALL | Urban | 1658.5 | 6.587 | 6.655 | 5.259 | 1.9538 | 0.84305 | 9 | 113688.7 | 113596.8 | 0.001782 | 0.001781 | 14 | 49056.38 | 0.00018
AHL9A | EVERTON HILLS, EVERTON PARK | Urban | 1693 | 6.217 | 1.31 | 3.62 | 0.092371 | 0.97448 | 7 | 8128.244 | 8128.244 | 0.000104 | 0.000104 | 20 | 85750.6 | 0.000312
AJV1 | FORTITUDE VALLEY, SPRING HILL | Urban | 498.7 | 0.743 | 3.051 |  | 0.11299 | 0.024131 | 1 | 1287.9 | 1287.9 | 1.01e-06 | 1.01e-06 | 1 | 275.04 | 7.3e-07
ALY3A | ANNERLEY, FAIRFIELD | Urban | 1457 | 3.98 | 0.047 | 2.248 | 1.3272 | 0.4807 | 10 | 104469 | 27053.17 | 0.000296 | 0.000175 | 6 | 37838.24 | 0.000125
ALY5 | ANNERLEY, GREENSLOPES, WOOLLOONGABBA | Urban | 2029 | 4.194 | 0.852 | 4.388 | 2.7026 | 1.0256 | 17 | 184047.2 | 110467.8 | 0.001551 | 0.001331 | 21 | 69841.43 | 0.000219
ALY6 | ANNERLEY, FAIRFIELD, YERONGA | Urban | 1257 | 5.798 | 1.217 | 4.249 | 0.67209 | 1.2089 | 8 | 34782.66 | 34782.66 | 9.83e-05 | 9.83e-05 | 17 | 62562.07 | 0.000238
ALY8 | ANNERLEY | Urban | 2055.5 | 4.164 | 0.361 | 3.041 | 1.3636 | 1.2826 | 16 | 135575.8 | 135575.8 | 0.000742 | 0.000742 | 18 | 127524.7 | 0.000457
ALY9 | YERONGA | Urban | 612 | 3.377 | 2.554 | 1.905 | 0.008037 | 0.17782 | 3 | 370.3173 | 370.3173 | 6.29e-06 | 6.29e-06 | 3 | 8193.57 | 3.64e-05
ALYMRK10 | ANNERLEY | Rural short | 96 | 0 | 4.386 | 0
ALYMRK10 | ANNERLEY | Rural short | 96 | 0 | 4.386 | 0.362
ALYMRK4 | ANNERLEY | Rural short | 77 | 0 | 1.921 | 0
ALYMRK4 | ANNERLEY | Rural short | 77 | 0 | 1.921 | 0.495
AMR1 | AMAMOOR, IMBIL, KANDANGA, KANDANGA CREEK, MELAWOND | Rural short | 326 | 62.403 | 0.269 | 2.213
AMR2 | AMAMOOR, CALICO CREEK, DAGUN, GILLDORA, KANDANGA, | Rural short | 763 | 115.654 | 0 | 1.639
AMR3 | AMAMOOR, BOLLIER, COLES CREEK, COORAN, DAGUN, GOOM | Rural short | 336 | 97.686 | 1.019 | 0.934
APMTR4 | PETRIE | Urban | 1
ARG10 | ACACIA RIDGE, SUNNYBANK HILLS | Urban | 142 | 2.156 | 0.869 | 4.826 | 8.0972 | 1.8184 | 2 | 27501.05 | 27501.05 | 0.000135 | 0.000135 | 4 | 6175.92 | 2.06e-05
ARG3 | ACACIA RIDGE, COOPERS PLAINS, SUNNYBANK | Urban | 148 | 2.436 | 1.186 | 4.82 | 0.68299 | 0.23134 | 3 | 2618.747 | 2618.747 | 0.000149 | 0.000149 | 2 | 887 | 4.06e-06
ARG4 | ACACIA RIDGE | Urban | 92 | 2.07 | 0.514 | 4.268
ARG5A | ACACIA RIDGE, SUNNYBANK, SUNNYBANK HILLS | Urban | 1573.1 | 8.207 | 0.982 | 2.925 | 10.2888 | 0.092045 | 15 | 737752.9 | 307321.3 | 0.003197 | 0.001617 | 4 | 6600.04 | 2.71e-05
ARG6 | ACACIA RIDGE, SUNNYBANK HILLS | Rural short | 144 | 0.753 | 2.238 | 0.8
ARG7 | ACACIA RIDGE | Urban | 28 | 0 | 2.184 | 2.248
ARG8 | ACACIA RIDGE | Urban | 7 | 0 | 1.406 | 2.077
ARG9A | SUNNYBANK, SUNNYBANK HILLS | Urban | 1151 | 4.987 | 0.906 | 2.213 | 0.80719 | 0.38769 | 15 | 58693.02 | 56982.3 | 0.000246 | 0.000236 | 9 | 28189.46 | 0.000122
ARL11A | ARUNDEL, PARKWOOD | Urban | 448 | 2.03 | 3.119 | 1.696 |  | 0.26516 | [5 empty] | 1 | 10296 | 8.92e-05
ARL11B | ARUNDEL, HELENSVALE | Urban | 662 | 1.621 | 4.43 | 1.905 | 0.002408 |  | 2 | 125.2875 | 125.2875 | 2.03e-06 | 2.03e-06
ARL12A | ARUNDEL, PARKWOOD | Urban | 786.5 | 1.11 | 3.495 | 2.877 | 0.013178 | 0.13281 | 6 | 782.9677 | 782.9677 | 9.73e-05 | 9.73e-05 | 1 | 7890.83 | 7.77e-05
ARL12B | ARUNDEL | Urban | 547 | 0.086 | 4.824 | 1.543 | 0.000736 |  | 1 | 41.4656 | 41.4656 | 1.01e-06 | 1.01e-06
ARL13A | ARUNDEL, LABRADOR | Urban | 942 | 0.27 | 6.51 | 2.839 | 0.001924 | 0.1452 | 2 | 141.55 | 141.55 | 2.03e-06 | 2.03e-06 | 2 | 10680 | 5.48e-05
ARL15B | ARUNDEL, BIGGERA WATERS, LABRADOR | Urban | 380 | 3.835 | 2.534 | 3.201 | 0.15033 |  | 3 | 3033.757 | 3033.757 | 3.71e-05 | 3.71e-05
ARL2B | ARUNDEL, COOMBABAH | Urban | 176.5 | 2.337 | 3.489 | 4.592 | 0.012677 |  | 1 | 52.7833 | 52.7833 | 1.01e-06 | 1.01e-06
ARL3A | ARUNDEL, PARKWOOD | Urban | 323 | 1.784 | 1.924 | 1.238 | 0.33921 | 0.99402 | 1 | 13277.88 | 13277.88 | 2.81e-05 | 2.81e-05 | 3 | 38909.41 | 0.000116
ARL5B | BIGGERA WATERS, COOMBABAH, LABRADOR | Urban | 711 | 2.378 | 3.449 | 2.42 | 0.034567 | 0.17899 | 4 | 1380.817 | 1380.817 | 1.32e-05 | 1.32e-05 | 2 | 7149.92 | 1.51e-05
ARL6B | ARUNDEL, COOMBABAH, LABRADOR | Urban | 219 | 4.331 | 2.591 | 4.306 | 0.7431 | 0.44035 | 6 | 4682.35 | 4682.35 | 7.76e-05 | 7.76e-05 | 5 | 2774.72 | 2.14e-05
ARLSNT3 | ARUNDEL | Urban | 4 | 0.387 | 0.175 | 0.133
ASV1 | FORTITUDE VALLEY | Urban | 4 | 0 | 0.57
ATC16A | FORTITUDE VALLEY, SPRING HILL | Urban | 419.5 | 0.662 | 0.926 | 3.048 | 0.06179 |  | 2 | 1866.517 | 74.5167 | 0.000455 | 1.01e-06
ATC20A | BRISBANE | CBD | 4 | 0 | 0.746 |  |  |  | 2 | 161.57 | 141.57 | 0.001423 | 8.81e-05
ATC26A | SPRING HILL | Urban | 362.5 | 0 | 1.387 | 2.344 | 0.061875 |  | 1 | 1056 | 1056 | 8.92e-05 | 8.92e-05
ATC7A | SPRING HILL | Urban | 249.6 | 0 | 1.854 | 3.029 | 0.002217 | 0.012934 | 1 | 28.8 |  | 7.3e-06 |  | 1 | 168 | 5.07e-07
ATCCSA4 | BRISBANE, SPRING HILL | CBD | 78 | 0 | 0.478 | 0
ATCCSQ11 | SPRING HILL | CBD | 160 | 0 | 0.447 | 2.763 | 0.01351 |  | 2 | 675.1 | 59.1 | 0.041389 | 0.000267
ATCFPV25 | SPRING HILL | Urban | 99 | 0 | 0.544 | 2.077 | 0.009986 |  | 1 | 388 |  | 9.83e-05
ATCIEA9 | SPRING HILL | Urban | 67.4 | 0 | 0.373 | 1.429 | 0.015679 |  | 1 | 249.6 |  | 6.33e-05
ATCSGO42 | BRISBANE, SPRING HILL | CBD | 2 | 0 | 0.955 | 0
AVHMLS90 | FORTITUDE VALLEY | Urban | 12 | 0 | 0.363 | 0.953
BBH10A | BROADBEACH WATERS, BUNDALL, SURFERS PARADISE | Urban | 1417 | 6.12 | 1.438 | 3.791 | 0.052928 | 0.97845 | 6 | 3048.65 | 3048.65 | 0.001366 | 0.001366 | 11 | 56358.84 | 0.000214
BBH12B | BROADBEACH WATERS, MERMAID BEACH, MERMAID WATERS | Urban | 1356.6 | 2.863 | 1.957 | 2.47 | 0.61194 | 0.065641 | 8 | 43853.5 | 43853.5 | 9.01e-05 | 9.01e-05 | 1 | 4704 | 1.42e-05
BBH13B | BROADBEACH, SURFERS PARADISE | Urban | 2389.5 | 1.531 | 1.924 | 4.098 | 0.18266 | 0.47407 | 7 | 11923.73 | 11923.73 | 0.000113 | 0.000113 | 11 | 30946.41 | 0.000152
BBH14B | BROADBEACH | Urban | 4 | 0 | 0.867 | 3.544
BBH15A | BROADBEACH WATERS | Urban | 0.4 | 0 | 1.643 | 2.534
BBH15B | SURFERS PARADISE | Urban | 2 | 0 | 1.489 | 1.124
BBH16A | BROADBEACH, MERMAID BEACH | Urban | 2132 | 3.043 | 2.046 | 4.711 | 3.4505 | 0.63709 | 11 | 198220.2 | 198220.2 | 0.002074 | 0.002074 | 4 | 36598.55 | 0.00017
BBH1A | MERMAID WATERS | Rural short | 52 | 0.058 | 2.825 | 0.345
BBH1B | BROADBEACH WATERS | Urban | 2.4 | 0 | 2.988 | 3.106 | [7 empty] | 1 | 0.96 | 2.43e-07
BBH2A | BROADBEACH, MERMAID BEACH | Urban | 522.5 | 0.68 | 0.15 | 2.324 | 0.93185 | 0.15122 | 2 | 19075.9 | 19075.9 | 0.000204 | 0.000204 | 3 | 3095.72 | 7.83e-06
BBH3A | BROADBEACH, BROADBEACH WATERS, SURFERS PARADISE | Urban | 1371.5 | 1.174 | 2.449 | 2.858 | 0.009947 | 0.16407 | 5 | 424.85 | 424.85 | 5.07e-06 | 5.07e-06 | 1 | 7008 | 1.78e-05
BBH4A | BROADBEACH | Urban | 526 | 0 | 1.241 | 3.239 | 1.113 | 0.1017 | 2 | 19463.1 | 19463.1 | 0.000565 | 0.000565 | 1 | 1778.55 | 1.08e-05
BBH4B | BROADBEACH | Urban | 152 | 0 | 1.021 | 2.667 | 0.77832 | 1.7948 | 2 | 5534.2 | 5534.2 | 0.000152 | 0.000152 | 2 | 12761.61 | 5.48e-05
BBH5A | BROADBEACH | Urban | 4 | 0 | 0.487 | 2.553
BBH7A | BROADBEACH | Urban | 29 | 0 | 1.076 | 4.306 |  | 0.035958 | [5 empty] | 1 | 20 | 1.01e-06
BBH7B | BROADBEACH WATERS | Urban | 0.6 | 0 | 2.744 | 3.201
BBH8A | BROADBEACH WATERS | Urban | 1531 | 3.391 | 1.87 | 3.887 | 1.4706 | 0.82348 | 11 | 85611.32 | 85611.32 | 0.000832 | 0.000832 | 6 | 47937.97 | 0.000369
BBH9A | BROADBEACH | Urban | 2 | 0 | 0.867 | 2.534
BBHORW6 | BROADBEACH | Urban | 59 | 0.583 | 1.24 | 3.487
BBS11 | CARINDALE, MANSFIELD | Urban | 1535 | 2.885 | 6.427 | 5.144 | 0.005227 | 0.01341 | 3 | 292.3333 | 292.3333 | 3.04e-06 | 3.04e-06 | 2 | 750 | 1.38e-05
BBS6 | MANSFIELD, WISHART | Urban | 809.3 | 3.652 | 1.63 | 2.477 | 0.012197 | 0.25553 | 6 | 638.8617 | 579.8117 | 6.08e-06 | 5.07e-06 | 5 | 13383.92 | 5.03e-05
BBS9 | MANSFIELD | Urban | 293.5 | 1.199 | 2.904 | 3.62 | 0.010124 | 0.03473 | 1 | 139.9167 | 139.9167 | 1.01e-06 | 1.01e-06 | 1 | 480 | 2.03e-06
BBSRBW5 | MACKENZIE, MANSFIELD | Urban | 3 | 2.52 | 0.501 | 2.706 | 17.7896 | 3.2888 | 2 | 3382 | 3382 | 1.42e-05 | 1.42e-05 | 2 | 625.24 | 1.99e-06
BBSRDL8 | BELMONT, BURBANK, CAPALABA WEST, CHANDLER, MACKENZ | Rural short | 1040 | 31.328 | 4.799 | 2.82
BDA12B | ANNERLEY, DUTTON PARK, HIGHGATE HILL, SOUTH BRISBA | Urban | 1824 | 4.83 | 3.952 | 5.468 | 0.3354 | 1.4115 | 9 | 9957.234 | 9957.234 | 6.03e-05 | 6.03e-05 | 11 | 41902.19 | 0.000203
BDA13A | ANNERLEY, WOOLLOONGABBA | Urban | 418 | 0.158 | 5.148 | 4.782 | 1.1469 | 0.61511 | 3 | 4719.9 | 4719.9 | 6.59e-05 | 6.59e-05 | 2 | 2531.45 | 9.99e-06
BDA2B | ANNERLEY, SOUTH BRISBANE | Rural short | 2 | 0 | 3.106 | 0.781
BDA3A | DUTTON PARK, HIGHGATE HILL, WOOLLOONGABBA | Urban | 1700 | 3.8 | 2.083 | 2.765 | 2.9256 | 0.47974 | 12 | 252805 | 252693.7 | 0.00402 | 0.004019 | 6 | 41454.79 | 0.000136
BDA5A | WOOLLOONGABBA | Urban | 390.5 | 1.36 | 2.44 | 2.039 | 0.003574 | 0.18799 | 1 | 112.0833 | 112.0833 | 1.01e-06 | 1.01e-06 | 3 | 5896.18 | 1.93e-05
BDB23A | BUNDAMBA | Urban | 4 | 0.143 | 1.398 | 0.934
BDB27A | BUNDAMBA, CHUWAR, KARALEE | Rural short | 829 | 12.838 | 4.706 | 2.858
BDB28A | DINMORE, RIVERVIEW | Rural short | 639 | 5.952 | 1.389 | 1.829
BDB32A | BUNDAMBA, CHUWAR, KARALEE, NORTH BOOVAL, NORTH TIV | Rural short | 622 | 13.206 | 2.979 | 1.524
BDB33A | BUNDAMBA, RIVERVIEW | Urban | 8 | 2.882 | 1.098 | 5.716
BDB35A | BUNDAMBA, EBBW VALE | Urban | 1098 | 7.025 | 1.847 | 3.22 | 0.006386 | 0.29977 | 3 | 389.7833 | 389.7833 | 3.04e-06 | 3.04e-06 | 5 | 18298.36 | 5.05e-05
BDB36A | BUNDAMBA, NORTH BOOVAL | Rural short | 1032 | 8.047 | 1.012 | 2.305
BDB37A | BARELLAN POINT, BUNDAMBA, KARALEE, KARANA DOWNS, R | Rural short | 959 | 18.324 | 5.332 | 4.344
BDB4A | BUNDAMBA, DINMORE, EBBW VALE, NEW CHUM | Rural short | 218 | 4.108 | 1.521 | 1.81
BDB6B | RIVERVIEW | Urban | 9 | 4.434 | 1.569 | 8.288
BDL1 | BUNDALL | Urban | 101 | 1.173 | 3.114 | 3.334 |  | 4.3921 | [5 empty] | 1 | 34463 | 7.25e-05
BDL2 | ASHMORE, BENOWA, BUNDALL, SOUTHPORT, SURFERS PARAD | Urban | 1409.5 | 3.784 | 3.314 | 3.563 | 1.3785 | 0.028904 | 4 | 73905.73 | 73905.73 | 0.001538 | 0.001538 | 3 | 1549.62 | 9.32e-06
BDL3 | BUNDALL, SOUTHPORT, SURFERS PARADISE | Urban | 247.5 | 1.607 | 1.689 | 2.515 |  | 2.8473 | [5 empty] | 5 | 17154.65 | 8.98e-05
BDL4 | BENOWA, BUNDALL | Urban | 1787 | 4.495 | 2.661 | 4.42 | 3.5236 | 1.5701 | 11 | 179967.9 | 179967.9 | 0.003041 | 0.003041 | 12 | 80193.66 | 0.000233
BDL5 | BUNDALL, SOUTHPORT | Urban | 372 | 1.602 | 3.917 | 3.334 | 0.10812 | 1.8586 | 3 | 1710.117 | 1710.117 | 1.12e-05 | 1.12e-05 | 9 | 29398.96 | 0.000136
BDL6 | BUNDALL | Urban | 254 | 1.668 | 1.079 | 3.525 | 0.30106 | 0.042934 | 3 | 13659.59 | 13659.59 | 0.000115 | 0.000115 | 2 | 1948 | 8.11e-06
BDL7 | BUNDALL, SOUTHPORT | Urban | 264.5 | 1.461 | 1.424 | 4.344 | 0.007869 | 2.3921 | 1 | 70.7 | 70.7 | 1.01e-06 | 1.01e-06 | 2 | 21492.4 | 7.59e-05
BDT1 | BEAUDESERT, CAINBABLE, CANUNGRA, CRYNA, KERRY, NIN | Rural short | 1127.5 | 110.324 | 0.586 | 3.715
BDT2 | BEAUDESERT, CRYNA | Rural short | 264 | 31.283 | 0.057 | 1.372
BDT3 | BEAUDESERT, CEDAR VALE, GLENEAGLE, MUNDOOLUN, VERE | Rural short | 684 | 47.721 | 0.134 | 1.741
BDT4 | ALLENVIEW, BEAUDESERT, CEDAR VALE, GLENEAGLE, VERE | Rural short | 1411 | 63.155 | 3.097 | 4.916
BDT5 | BEAUDESERT, BIDDADDABA, TABRAGALBA | Rural short | 803.5 | 30.267 | 3.156 | 2.166
BDT6 | BEAUDESERT | Urban | 429 | 4.986 | 0.649 | 4.287 | 2.145 | 0.23424 | 2 | 38625 | 27950 | 0.000869 | 0.000436 | 4 | 4217.98 | 1.41e-05
BGY13A | BURPENGARY | Urban | 55 | 1.387 | 0.386 | 0.894
BGY15A | BURPENGARY, NARANGBA | Urban | 1429 | 9.259 | 8.503 | 5.316 | 0.02078 | 0.007849 | 8 | 990.3251 | 990.3251 | 8.11e-06 | 8.11e-06 | 2 | 374.04 | 4.95e-06
BGY17A | BURPENGARY | Urban | 1861.5 | 8.225 | 4.06 | 4.801 | 0.71336 | 0.61961 | 13 | 56382.55 | 56382.55 | 0.000503 | 0.000503 | 4 | 48972.25 | 0.000208
BGY3A | BURPENGARY | Urban | 212.5 | 2.519 | 0.73 | 3.201 | 0.35684 |  | 2 | 3686.43 | 3686.43 | 4.77e-05 | 4.77e-05
BGY5A | BURPENGARY, BURPENGARY EAST, DECEPTION BAY | Rural short | 1270 | 24.368 | 1.027 | 3.277
BGY6A | BURPENGARY, NARANGBA | Urban | 1454 | 2.877 | 12.431 | 4.916 | 0.007906 | 0.058465 | 1 | 518 | 518 | 1.42e-05 | 1.42e-05 | 11 | 3830.52 | 6.76e-05
BHD1A | PALM BEACH | Urban | 1426.5 | 3.02 | 4.041 | 2.579 | 0.14121 | 1.4655 | 11 | 14812.92 | 14715.55 | 4.97e-05 | 4.87e-05 | 19 | 153722.8 | 0.000591
BHD20A | BURLEIGH HEADS, BURLEIGH WATERS | Urban | 1343 | 3.89 | 0.886 | 3.079 | 0.10613 | 1.1643 | 3 | 5548.413 | 5548.413 | 5.42e-05 | 5.42e-05 | 7 | 60870.51 | 0.00023
BHD21A | BURLEIGH HEADS, ELANORA, PALM BEACH | Urban | 1160 | 4.411 | 7.166 | 3.753 | 0.004004 | 2.5426 | 1 | 163.8167 | 163.8167 | 1.01e-06 | 1.01e-06 | 3 | 104024.3 | 0.000245
BHD23A | BURLEIGH HEADS, CURRUMBIN VALLEY, ELANORA, TALLEBU | Rural short | 1222.5 | 26.111 | 3.281 | 3.772
BHD2A | BURLEIGH HEADS, BURLEIGH WATERS, VARSITY LAKES | Urban | 884 | 0 | 6.528 | 1.848 | 0.00739 |  | 2 | 415.1833 | 415.1833 | 2.03e-06 | 2.03e-06
BHD31A | BURLEIGH HEADS | Urban | 572 | 3.687 | 2.212 | 4.839 | 0.003506 |  | 1 | 117.95 | 117.95 | 1.01e-06 | 1.01e-06
BHD32B | BURLEIGH HEADS | Urban | 982 | 0.895 | 2.924 | 2.401 | 0.017905 | 0.93541 | 4 | 815.6535 | 815.6535 | 2.13e-05 | 2.13e-05 | 6 | 42611.15 | 0.000119
BHD33A | BURLEIGH WATERS | Urban | 600 | 1.756 | 3.682 | 2.553 | 0.002926 |  | 1 | 91.5279 | 91.5279 | 1.01e-06 | 1.01e-06
BHD35A | BURLEIGH HEADS, REEDY CREEK, TALLEBUDGERA, TALLEBU | Rural short | 1446 | 54.124 | 4.573 | 4.347
BHD36A | BURLEIGH HEADS, PALM BEACH | Urban | 1169.5 | 2.032 | 3.529 | 2.771 | 0.79222 | 0.43791 | 4 | 50579.31 | 50579.31 | 0.000248 | 0.000248 | 5 | 27958.55 | 0.000173
BHD3A | BURLEIGH WATERS, VARSITY LAKES | Urban | 1261 | 2.712 | 4.544 | 3.125 | 7.5869 | 1.2978 | 5 | 442497.8 | 272089.8 | 0.002544 | 0.001273 | 4 | 75692.53 | 0.000223
BHD41A | BURLEIGH HEADS, REEDY CREEK, VARSITY LAKES | Rural short | 1292 | 5.706 | 9.58 | 3.849
BHD42A | BURLEIGH HEADS | Urban | 2 | 0.157 | 1.472 | 1.315
BHD44A | BURLEIGH HEADS, BURLEIGH WATERS, MIAMI | Urban | 2007 | 5.024 | 3.656 | 3.926 | 0.081722 | 2.5232 | 10 | 6378.345 | 6378.345 | 6.34e-05 | 6.34e-05 | 19 | 196931.8 | 0.000586
BHD45B | BURLEIGH WATERS | Urban | 1601 | 0.115 | 7.985 | 3.272 | 0.16194 | 0.086771 | 4 | 12321.85 | 12321.85 | 8.07e-05 | 8.07e-05 | 1 | 6602.31 | 3.91e-05
BHD46A | BURLEIGH HEADS | Urban | 449.8 | 4.423 | 1.064 | 4.535 | 3.2826 | 0.062526 | 4 | 39475.55 | 39475.55 | 0.00087 | 0.00087 | 2 | 751.92 | 3.18e-06
BHD4A | BURLEIGH HEADS, BURLEIGH WATERS | Urban | 21 | 0.638 | 0.481 | 3.43
BHD5A | BURLEIGH HEADS | Urban | 1133 | 3.908 | 0.91 | 3.064 | 0.13935 | 3.8504 | 2 | 8575.951 | 8575.951 | 0.000115 | 0.000115 | 12 | 236958.4 | 0.000647
BHD7A | BURLEIGH HEADS, ELANORA, PALM BEACH | Urban | 1182.5 | 2.413 | 5.663 | 3.144 | 0.01089 | 0.7836 | 6 | 415.5333 | 415.5333 | 6.08e-06 | 6.08e-06 | 8 | 29900.73 | 9.46e-05
BHDRCK29 | BURLEIGH HEADS, VARSITY LAKES | Urban | 162.2 | 3.578 | 2.36 | 2.991 | 0.053882 | 1.2149 | 3 | 702.24 | 702.24 | 4.68e-06 | 4.68e-06 | 5 | 15833.5 | 4.9e-05
BHL1A | BALD HILLS, BRACKEN RIDGE | Urban | 660 | 1.926 | 1.949 | 1.162 | 0.002071 | 0.076671 | 2 | 177.9667 | 177.9667 | 2.03e-06 | 2.03e-06 | 3 | 6589.5 | 3.19e-05
BHL2A | BALD HILLS, BRIDGEMAN DOWNS, CARSELDINE | Urban | 795 | 9.008 | 2.237 | 4.477 | 0.0827 | 2.1288 | 5 | 2530.669 | 2530.669 | 0.000157 | 0.000157 | 10 | 65143.78 | 0.000177
BHL3A | BALD HILLS, BRIDGEMAN DOWNS, CARSELDINE | Urban | 1273 | 2.577 | 5.75 | 4.401 | 0.037379 | 0.32222 | 3 | 1943.35 | 1943.35 | 0.000143 | 0.000143 | 11 | 16752.38 | 8.01e-05
BHL4A | BALD HILLS, BRACKEN RIDGE | Rural short | 1403 | 7.095 | 6.255 | 3.315
BHL5A | BALD HILLS, BRACKEN RIDGE | Urban | 1720 | 6.112 | 6.982 | 4.325 | 0.30775 | 0.4647 | 9 | 16768.61 | 16687.96 | 0.000199 | 0.000198 | 7 | 25320.24 | 8.7e-05
BHL6A | CARSELDINE | Urban | 772 | 0.218 | 5.383 | 1.848 | 0.00064 | 0.65406 | 1 | 37.25 | 37.25 | 1.01e-06 | 1.01e-06 | 5 | 38071.44 | 0.000143
BHL7A | BRACKEN RIDGE | Urban | 1172 | 0.174 | 5.493 | 2.42 | 0.13075 | 0.19185 | 6 | 10002.66 | 10002.66 | 7.7e-05 | 7.7e-05 | 3 | 14676.6 | 5.93e-05
BIS1 | BANKSIA BEACH, BELLARA | Rural short | 1269.3 | 4.202 | 5.14 | 2.858
BIS12B | BANKSIA BEACH, WHITE PATCH | Rural short | 1422.7 | 4.281 | 10.574 | 3.163
BIS13A | BONGAREE | Urban | 1050 | 2.814 | 4.509 | 3.411 |  | 0.044995 | [5 empty] | 1 | 1897.56 | 7.67e-06
BIS15A | BONGAREE, WOORIM | Rural short | 1120 | 9.48 | 2.468 | 3.106
BIS16A | BANKSIA BEACH, BELLARA | Urban | 1856 | 6.277 | 2.527 | 3.236 | 5.4376 | 0.014284 | 15 | 482925.9 | 482925.9 | 0.002549 | 0.002549 | 3 | 1268.55 | 1.79e-05
BIS2B | BEACHMERE, BELLARA, WOORIM | Rural short | 1220 | 12.888 | 1.551 | 2.662
BISTPT3 | BELLARA, BONGAREE | Rural short | 1921 | 7.309 | 4.096 | 3.064
BKD12A | BIRKDALE | Urban | 1718 | 4.203 | 5.871 | 4.325 | 4.8783 | 0.050034 | 6 | 240409.8 | 240409.8 | 0.001745 | 0.001745 | 2 | 2465.72 | 1.18e-05
BKD13A | ALEXANDRA HILLS, BIRKDALE | Urban | 2410 | 9.692 | 2.121 | 5.182 | 0.65934 | 0.10218 | 23 | 37229.69 | 27024.63 | 0.000322 | 0.000297 | 4 | 5769.6 | 7.56e-05
BKD15A | ALEXANDRA HILLS | Urban | 1090 | 6.955 | 0.36 | 3.201 | 2.4794 | 0.095183 | 21 | 149170 | 147044.1 | 0.00141 | 0.001369 | 2 | 5726.56 | 2.46e-05
BKD16A | BIRKDALE, THORNESIDE | Urban | 1659 | 8.068 | 3.197 | 4.042 | 0.009368 | 0.32626 | 7 | 637.9159 | 637.9159 | 7.1e-06 | 7.1e-06 | 5 | 22216 | 0.000145
BKD2B | BIRKDALE, THORNESIDE | Urban | 1265 | 6.025 | 2.491 | 3.017 | 1.6882 | 0.063903 | 12 | 122425.8 | 122425.8 | 0.002638 | 0.002638 | 1 | 4634.2 | 2e-05
BKD3A | BIRKDALE, WELLINGTON POINT | Urban | 1822 | 6.444 | 3.928 | 5.468 | 2.2677 | 0.32203 | 6 | 113660.4 | 113660.4 | 0.001837 | 0.001837 | 6 | 16141.01 | 7e-05
BKD5B | BIRKDALE, WELLINGTON POINT | Urban | 1801 | 7.031 | 3.066 | 3.753 | 0.44834 | 0.15679 | 14 | 29106.83 | 29106.83 | 0.001062 | 0.001062 | 3 | 10179.25 | 3.62e-05
BLB2A | BALMORAL, BULIMBA, HAWTHORNE | Urban | 1508.5 | 4.128 | 1.247 | 3.753 | 0.14192 | 1.1225 | 7 | 9687.213 | 9687.213 | 7.24e-05 | 7.24e-05 | 21 | 76619.77 | 0.000327
BLB4A | BALMORAL, BULIMBA, MORNINGSIDE | Urban | 819.5 | 3.118 | 0.974 | 2.175 | 0.12827 | 0.32318 | 7 | 8493.572 | 8493.572 | 2.8e-05 | 2.8e-05 | 5 | 21400.45 | 8.15e-05
BLB5A | BULIMBA | Urban | 1067.5 | 4.412 | 0.65 | 2.667 | 0.065832 | 1.5587 | 6 | 3891.747 | 3891.747 | 4.66e-05 | 4.66e-05 | 18 | 92142.93 | 0.000338
BLB8B | BALMORAL, BULIMBA, HAWTHORNE, MORNINGSIDE | Urban | 2086.5 | 5.988 | 0.844 | 4.439 | 5.6479 | 1.457 | 17 | 487677.9 | 487677.9 | 0.009321 | 0.009321 | 38 | 125807.1 | 0.000559
BLB9A | BULIMBA | Urban | 1058 | 1.975 | 2.034 | 4.154 | 3.9163 | 1.3713 | 7 | 145795.9 | 145795.9 | 0.002078 | 0.002078 | 9 | 51049.82 | 0.000158
BLBNFM6 | HAWTHORNE, MORNINGSIDE | Urban | 2144 | 6.094 | 2.055 | 2.725 | 0.22723 | 1.4044 | 7 | 18853.91 | 18853.91 | 0.000264 | 0.000264 | 18 | 116525 | 0.000429
BLH10A | BEENLEIGH, MOUNT WARREN PARK, STAPYLTON, YATALA | Urban | 377 | 4.026 | 2.848 | 3.83 | 0.007034 | 2.1675 | 2 | 169.8333 | 169.8333 | 2.03e-06 | 2.03e-06 | 3 | 52333.44 | 0.000184
BLH10B | ALBERTON, EAGLEBY | Urban | 2425 | 14.258 | 3.901 | 5.201 | 0.39364 | 0.29529 | 17 | 25768.28 | 17641.28 | 0.000243 | 0.0002 | 3 | 19330 | 9.83e-05
BLH11B | BEENLEIGH | Urban | 691.5 | 2.628 | 1.453 | 3.601 | 0.56244 | 1.365 | 5 | 16013.86 | 16013.86 | 0.000751 | 0.000751 | 2 | 38864.45 | 0.000169
BLH12A | BAHRS SCRUB, BANNOCKBURN, BEENLEIGH, BELIVAH, CEDA | Rural short | 1653 | 64.717 | 4.914 | 4.916
BLH12B | BEENLEIGH, EAGLEBY | Urban | 2401.5 | 11.046 | 4.392 | 5.735 | 2.096 | 0.51863 | 21 | 131764.5 | 131764.5 | 0.003013 | 0.003013 | 1 | 32604 | 0.000116
BLH13B | ALBERTON, BEENLEIGH, EAGLEBY, STAPYLTON, YATALA | Rural short | 316 | 29.786 | 3.496 | 3.963
BLH14A | BEENLEIGH | Urban | 49.5 | 0.273 | 1.964 | 2.763 | 1.8491 | 0.6621 | 3 | 8649.417 | 8649.417 | 5.12e-05 | 5.12e-05 | 2 | 3097 | 7.1e-06
BLH15B | MOUNT WARREN PARK | Urban | 500 | 2.886 | 0.491 | 1.677 | 0.013035 |  | 4 | 557.3833 | 557.3833 | 4.06e-06 | 4.06e-06
BLH16A | BEENLEIGH | Rural short | 2053.5 | 12.805 | 0.771 | 4.096
BLH9A | BEENLEIGH | Urban | 424 | 2.293 | 0.872 | 2.305 | 0.016682 | 0.033798 | 4 | 519.565 | 519.565 | 3.7e-05 | 3.7e-05 | 1 | 1052.66 | 5.18e-06
BLH9B | MOUNT WARREN PARK | Urban | 1484 | 4.914 | 2.841 | 3.715 | 0.16725 |  | 12 | 10848.71 | 1091.267 | 3.93e-05 | 1.12e-05
BLHSTN16 | ALBERTON, GILBERTON, STAPYLTON, YATALA | Rural short | 348 | 9.607 | 2.301 | 3.715
BLN2B | BEENLEIGH | Urban | 363 | 3.406 | 0.322 | 2.248 | 0.003518 | 0.001334 | 1 | 137.1 | 137.1 | 1.01e-06 | 1.01e-06 | 1 | 52 | 2.03e-06
BLN3A | BEENLEIGH | Urban | 2 | 0 | 1.437 | 2.191
BLN5B | BEENLEIGH | Urban | 2 | 0 | 1.437 | 2.477
BLN6A | BEENLEIGH | Urban | 360 | 2.212 | 1.944 | 2.382 | 0.20614 | 0.14944 | 1 | 4326.3 | 4326.3 | 4.62e-05 | 4.62e-05 | 1 | 3136.32 | 8.03e-06
BMG18A | SPRING HILL | Urban | 55.6 | 0 | 2.867
BMG2A | BRISBANE, PETRIE TERRACE, SPRING HILL | Urban | 226.8 | 0.133 | 6.167 |  | 0.016674 |  | 3 | 245.6433 | 245.6433 | 3.03e-06 | 3.03e-06
BMG3B | MILTON | Urban | 147 | 0.535 | 2.065 |  | 1.8948 | 0.14304 | 4 | 13346.42 | 13346.42 | 0.000302 | 0.000302 | 3 | 1007.54 | 8.07e-06
BMG44A | MILTON | Urban | 29 | 0 | 0.828
BMG9A | AUCHENFLOWER, BRISBANE, MILTON | Urban | 18 | 0 | 1.61
BMG9B | BRISBANE | Urban | 32.5 | 0 | 0.333
BMT1 | BELLI PARK, BLACK MOUNTAIN, BOLLIER, CARTERS RIDGE | Rural short | 632 | 118.837 | 0.893 | 1.309
BMT2 | BLACK MOUNTAIN, POMONA | Rural short | 269 | 11.096 | 0.22 | 0.591
BMT3 | BLACK MOUNTAIN, COOROY | Rural short | 263 | 2.825 | 5.262 | 0.591
BMT4 | BLACK MOUNTAIN, COOROY, LAKE MACDONALD | Rural short | 670 | 13.494 | 1.504 | 2.286
BMT5 | BELLI PARK, BLACK MOUNTAIN, COOROY, RIDGEWOOD | Rural short | 287 | 33.959 | 0.117 | 0.525
BNH1B | BOONAH, BUNBURRA, BUNJURGEN, CANNON CREEK, CHARLWO | Rural short | 632 | 113.023 | 1.192 | 1.353
BNH2B | BOONAH, COULSON, HOYA | Rural short | 842 | 19.721 | 2.024 | 2.42
BNH3A | BOONAH, KENTS POCKET, TEMPLIN | Rural short | 155 | 15.933 | 0.2 | 0.346
BNH5A | ALLANDALE, BOONAH, COULSON, MILFORD | Rural short | 454 | 24.073 | 0.787 | 1.086
BNH6A | CARNEYS CREEK, COOCHIN, CROFTBY, DUGANDAN, FRENCHE | Rural short | 309 | 108.432 | 0.134 | 1.829
BNZCGA57 | BRISBANE | CBD | 2 | 0 | 0.412
BPHMST2 | BRISBANE | CBD | 5 | 0 | 0.374 | 2.058
BPN24A | BROWNS PLAINS | Urban | 60 | 0 | 1.208 | 1.734 | 0.073045 | 1.0759 | 3 | 428.85 | 428.85 | 3.04e-06 | 3.04e-06 | 2 | 6316.62 | 4.06e-05
BPN26A | BORONIA HEIGHTS, BROWNS PLAINS, GREENBANK, PARK RI | Rural short | 900 | 14.172 | 3.358 | 4.268
BPN28A | BROWNS PLAINS, CALAMVALE, DREWVALE, PARKINSON | Rural short | 1680 | 7.311 | 10.04 | 4.992
BPN29A | FORESTDALE, HILLCREST | Urban | 1388 | 11.155 | 1.395 | 3.963 | 18.2034 | 0.2003 | 26 | 1051788 | 35169.69 | 0.00306 | 0.000249 | 2 | 11573.16 | 5.57e-05
BPN2A | PARKINSON | Urban | 31 | 0 | 2.974 | 4.611 | 0.17643 |  | 1 | 108 | 108 | 2.74e-06 | 2.74e-06
BPN3 | BORONIA HEIGHTS, BROWNS PLAINS, HILLCREST | Urban | 1986 | 10.905 | 2.105 | 4.135 | 15.2348 | 0.09442 | 26 | 1172886 | 20175.17 | 0.004206 | 0.000225 | 4 | 7269.15 | 3.91e-05
BPN31A | BROWNS PLAINS, HILLCREST | Urban | 180 | 1.123 | 0.62 | 2.191 | 0.022487 |  | 2 | 275.1167 | 99.45 | 2.03e-06 | 1.01e-06
BPN32B | BROWNS PLAINS, REGENTS PARK | Urban | 7 | 0 | 2.51 | 1.943
BPN34A | BORONIA HEIGHTS, GREENBANK, HILLCREST | Urban | 1614 | 13.55 | 2.108 | 4.668 | 14.2375 | 0.046453 | 14 | 795180.2 | 14980.12 | 0.001808 | 0.000166 | 2 | 2594.44 | 2.12e-05
BPN35A | REGENTS PARK | Urban | 858 | 4.198 | 0.402 | 2.606 | 0.028125 |  | 13 | 1546.891 | 1546.891 | 1.32e-05 | 1.32e-05
BPN36A | BROWNS PLAINS, HERITAGE PARK, REGENTS PARK | Urban | 1826 | 6.805 | 3.36 | 4.268 | 6.0836 | 0.012541 | 13 | 469693.8 | 236186.8 | 0.003812 | 0.001987 | 1 | 968.24 | 1.08e-05
BPN4 | BROWNS PLAINS, DREWVALE | Urban | 888 | 4.676 | 2.234 | 4.916 | 7.6688 |  | 11 | 106025 | 106025 | 0.000963 | 0.000963
BPN6 | HERITAGE PARK, PARK RIDGE, REGENTS PARK | Urban | 1310 | 6.051 | 5.006 | 3.22 | 0.075583 | 0.007993 | 9 | 5526.52 | 5470.637 | 0.000263 | 0.000262 | 1 | 584.4 | 9.88e-06
BPN7B | BROWNS PLAINS | Urban | 15 | 0 | 0.481 | 5.43
BRCRFW35 | BRISBANE | CBD | 2 | 0 | 0.271
BRD10B | ALBANY CREEK, BRENDALE | Rural short | 347 | 4.325 | 2.666 | 1.353
BRD11A | BRENDALE, CASHMERE, WARNER | Rural short | 987 | 14.338 | 8.309 | 3.925
BRD13A | BRAY PARK, BRENDALE, STRATHPINE, WARNER | Urban | 2456 | 4.618 | 14.565 | 5.335 | 0.21954 | 0.12869 | 4 | 19337.72 | 19337.72 | 0.002541 | 0.002541 | 6 | 11335.29 | 5.49e-05
BRD14B | BRENDALE | Urban | 144 | 1.549 | 2.312 | 5.221 | 0.021454 | 0.08351 | 2 | 273.1 | 273.1 | 3.04e-06 | 3.04e-06 | 2 | 1063.03 | 6.97e-06
BRD15A | BRENDALE | Urban | 3 | 0 | 0.813 | 2.243
BRD16A | BRENDALE | Urban | 162.5 | 1.623 | 1.425 | 2.858 |  | 9.781 | [5 empty] | 1 | 34944 | 9.73e-05
BRD2A | BRENDALE, EATONS HILL | Urban | 497 | 1.882 | 4.209 | 2.001 | 0.004599 |  | 3 | 302.65 | 302.65 | 4.06e-06 | 4.06e-06
BRD3B | CASHMERE, CLEAR MOUNTAIN, DRAPER, EATONS HILL, WAR | Rural short | 757 | 33.365 | 2.974 | 2.839
BRD5A | BRENDALE, CASHMERE, JOYNER, WARNER | Rural short | 1793 | 13.52 | 9.491 | 5.887
BRD8A | BRENDALE, EATONS HILL, WARNER | Urban | 1523 | 2.786 | 7.265 | 4.897 | 0.009752 |  | 5 | 582.55 | 582.55 | 5.07e-06 | 5.07e-06
BRT3 | BRIGHTON | Urban | 1072 | 4.222 | 0.486 | 1.8 | 0.000755 | 0.38228 | 1 | 76.65 | 76.65 | 1.01e-06 | 1.01e-06 | 4 | 38813.98 | 0.000136
BRT5 | BRIGHTON, SANDGATE | Urban | 1176 | 4.365 | 0.807 | 2.547 | 0.20148 | 0.80967 | 3 | 12002.93 | 12002.93 | 0.000103 | 0.000103 | 16 | 48235.41 | 0.000193
BRT6 | BRIGHTON | Urban | 1150 | 7.022 | 0.832 | 2.363 | 0.003283 | 1.7572 | 2 | 304.7178 | 304.7178 | 2.03e-06 | 2.03e-06 | 18 | 163086.3 | 0.000495
BRT8 | BRIGHTON, SANDGATE | Urban | 1249 | 4.752 | 0.209 | 2.279 | 0.16593 | 1.1788 | 6 | 10501.67 | 10501.67 | 8.9e-05 | 8.9e-05 | 29 | 74603.15 | 0.000315
BSC3 | BOONDALL | Urban | 10 | 0.906 | 1.312 |  | 8.6388 |  | 4 | 5822.454 | 5822.454 | 2.53e-05 | 2.53e-05
BSE8 | MITCHELTON | Urban | 2
BSEENG15 | ENOGGERA, GAYTHORNE, MITCHELTON | Urban | 1674.5 | 6.064 | 1.174 | 3.525 | 6.4398 | 0.038494 | 12 | 250724.9 | 250724.9 | 0.003739 | 0.003739 | 2 | 1498.72 | 6.97e-06
BSEENG35 | MITCHELTON | Urban | 55 | 0 | 0.422
BTA13A | EDENS LANDING, HOLMVIEW | Urban | 1934 | 5.453 | 2.871 | 4.42 | 0.76558 | 0.21599 | 18 | 57515.03 | 57515.03 | 0.000226 | 0.000226 | 2 | 16226.43 | 5.85e-05
BTA15A | BETHANIA, WATERFORD | Urban | 1249.5 | 9.017 | 1.314 | 2.896 | 0.24755 | 2.2734 | 3 | 15464.27 | 15369.58 | 6.39e-05 | 6.29e-05 | 4 | 142018 | 0.00041
BTA1A | BETHANIA | Rural short | 1108 | 7.689 | 1.582 | 2.483
BTA3A | BEENLEIGH, BETHANIA, EDENS LANDING, HOLMVIEW, WATE | Rural short | 935 | 4.926 | 6.137 | 3.391
BTA5A | BAHRS SCRUB, BETHANIA, BUCCAN, HOLMVIEW, WATERFORD | Rural short | 1722.5 | 25.447 | 9.657 | 4.001
BTACK11 | BETHANIA | Urban | 2
BTN1 | BROMELTON, JOSEPHVILLE | Urban | 26 | 4.78 | 0 | 3.239 | 0.046255 |  | 2 | 3276 | 1924 | 5.27e-05 | 2.64e-05
BTN2 | ALLENVIEW, BEAUDESERT, BROMELTON, GLENEAGLE, WYARA | Rural short | 149 | 51.694 | 0.799 | 0.819
BTN3 | BROMELTON, JOSEPHVILLE, KOORALBYN, LARAVALE | Rural short | 856 | 36.042 | 4.364 | 1.886
BTN4 | BEAUDESERT, BROMELTON | Urban | 7 | 1.997 | 0.31 | 2.744 | 2.708 |  | 2 | 965.16 | 566.84 | 1.55e-05 | 7.77e-06
BTN6 | BROMELTON | Urban | 6 | 0.724 | 0.132 | 0.953 | 0.57039 |  | 2 | 1008 | 592 | 1.62e-05 | 8.11e-06
BTN7 | BEAUDESERT, BROMELTON, ILBOGAN, JOSEPHVILLE, KOORA | Rural short | 78 | 24.798 | 0.481 | 3.843
BVL10A | BOOVAL, EAST IPSWICH, NEWTOWN | Urban | 733 | 1.605 | 0.502 | 1.81 | 0.078844 | 0.005176 | 8 | 5305.786 | 5305.786 | 5.33e-05 | 5.33e-05 | 1 | 348.3 | 1.31e-06
BVL13A | EASTERN HEIGHTS, RACEVIEW, SILKSTONE | Urban | 1345.5 | 6.011 | 0.754 | 3.925 | 0.56368 | 0.19709 | 9 | 32055.09 | 32055.09 | 0.000358 | 0.000358 | 6 | 11207.94 | 6.07e-05
BVL15A | BOOVAL | Urban | 479 | 1.65 | 1.207 | 4.401 | 4.4502 | 0.32153 | 2 | 68349.25 | 68349.25 | 0.000488 | 0.000488 | 3 | 4938.32 | 1.69e-05
BVL2A | BASIN POCKET, BOOVAL, EAST IPSWICH, NORTH BOOVAL | Urban | 1667 | 7.434 | 0.016 | 3.125 | 1.7314 | 0.15945 | 10 | 152042.4 | 152042.4 | 0.001054 | 0.001054 | 1 | 14002.24 | 3.78e-05
BVL3A | EASTERN HEIGHTS, IPSWICH, NEWTOWN | Urban | 1215.5 | 6.295 | 0.303 | 2.782 | 0.21306 | 0.48611 | 7 | 17866.1 | 17337.3 | 0.000186 | 0.000184 | 6 | 40763.12 | 0.000125
BVL5A | FLINDERS VIEW, RACEVIEW, SILKSTONE | Urban | 1893 | 11.502 | 1.582 | 4.954 | 0.096525 | 0.26216 | 9 | 7704.504 | 7423.204 | 0.000111 | 0.00011 | 9 | 20925.1 | 7.81e-05
BVL9A | NORTH BOOVAL | Urban | 465 | 3.463 | 0 | 0.953 | 0.001561 | 0.002162 | 1 | 148.1333 | 148.1333 | 1.01e-06 | 1.01e-06 | 1 | 205.2 | 2.74e-06
BVLNCM7 | BOOVAL, BUNDAMBA, NEW CHUM, SILKSTONE | Urban | 1301 | 7.719 | 1.375 | 4.401 | 2.0158 | 0.51855 | 9 | 92750.4 | 92750.4 | 0.001366 | 0.001366 | 7 | 23859.31 | 8.21e-05
BWH12A | BEERWAH, GLASSHOUSE MOUNTAINS, PEACHESTER | Rural short | 629 | 44.704 | 2.316 | 2.039
BWH13A | BEERWAH, BOOROOBIN, CROHAMHURST, MALENY, PEACHESTE | Rural short | 615 | 52.99 | 0.9 | 1.315
BWH16A | BEERWAH, COOCHIN CREEK, GLASSHOUSE MOUNTAINS | Rural short | 1539.9 | 38.936 | 3.801 | 5.011
BWH7A | BEERWAH, COOCHIN CREEK, GLASSHOUSE MOUNTAINS | Rural short | 1060 | 27.354 | 6.8 | 4.115
BWH8A | BEERBURRUM, BEERWAH, GLASSHOUSE MOUNTAINS | Rural short | 517.5 | 27.928 | 3.007 | 2.763
CBT12A | BEERBURRUM, CABOOLTURE, ELIMBAH | Rural short | 1791.6 | 57.046 | 4.483 | 4.687
CBT13A | CABOOLTURE | Urban | 958 | 1.675 | 9.524 | 3.811 | 0.007332 | 0.019866 | 4 | 354.0774 | 354.0774 | 4.06e-06 | 4.06e-06 | 2 | 959.4324 | 3.79e-06
CBT15A | CABOOLTURE, ELIMBAH | Rural short | 908 | 19.967 | 2.615
CBT4A | CABOOLTURE | Rural short | 921 | 4.932 | 6.176 | 2.706
CBT7A | CABOOLTURE | Urban | 1116 | 6.524 | 1.579 | 3.925 | 0.020477 | 0.008845 | 8 | 729.2711 | 729.2711 | 8.11e-06 | 8.11e-06 | 1 | 315 | 1.01e-06
CBT8A | CABOOLTURE, DONNYBROOK, ELIMBAH, MELDALE, TOORBUL | Rural short | 1483 | 44.005 | 4.132 | 3.868
CBW10 | BELLMERE, UPPER CABOOLTURE | Rural short | 1082 | 12.977 | 3.327 | 2.363
CBW11 | CABOOLTURE, ELIMBAH, MOODLU, WAMURAN | Rural short | 1154 | 36.991 | 1.655 | 5.182
CBW12 | CABOOLTURE, CABOOLTURE SOUTH | Urban | 928 | 4.517 | 1.467 | 2.686 | 2.9647 | 0.20427 | 13 | 133941.2 | 133941.2 | 0.001393 | 0.001393 | 1 | 9228.78 | 3.95e-05
CBW13 | MOODLU, WAMURAN | Rural short | 318 | 9.578 | 4.049 | 0.895
CBW14 | CABOOLTURE | Urban | 571 | 3.498 | 0.812 | 1.258 | 0.2969 | 0.35517 | 7 | 9629.901 | 9581.068 | 0.000698 | 0.000697 | 1 | 11520 | 2.43e-05
CBW4 | CABOOLTURE, CABOOLTURE SOUTH | Urban | 85 | 0.221 | 0.91 | 3.315 | 1.5175 | 0.43468 | 2 | 7449 | 7449 | 0.000114 | 0.000114 | 2 | 2133.7 | 5.17e-06
CBW5 | CABOOLTURE | Urban | 763 | 4.827 | 0.5 | 2.134 | 0.12275 |  | 2 | 7633.65 | 7633.65 | 0.000772 | 0.000772
CBW6 | BELLMERE, CABOOLTURE SOUTH, MOORINA, OCEAN VIEW, R | Rural short | 2181 | 46.029 | 7.362 | 5.811
CBW7 | BELLMERE, CABOOLTURE, MOODLU | Rural short | 1364 | 19.097 | 1.062 | 3.201
CBW8 | CABOOLTURE | Urban | 145 | 2.543 | 0.251 | 2.477
CBW9 | CABOOLTURE | Urban | 166 | 2.637 | 2.503 | 3.125
CCY12A | OXENFORD, PACIFIC PINES | Urban | 1417.1 | 1.727 | 6.474 | 3.144 | 0.003876 |  | 2 | 114.241 | 114.241 | 2.03e-06 | 2.03e-06
CCY13A | HELENSVALE | Urban | 1284 | 6.383 | 4.599 | 4.173 | 0.30237 | 0.59183 | 13 | 15646.99 | 15646.99 | 0.000118 | 0.000118 | 5 | 30625.55 | 8.72e-05
CCY14B | HELENSVALE | Urban | 785 | 0 | 9.362 | 3.353 | 0.020264 |  | 6 | 526.3833 | 526.3833 | 6.08e-06 | 6.08e-06
CCY15A | HELENSVALE | Urban | 1 | 0 | 5 | 1.886
CCY18A | OXENFORD | Urban | 0.7 | 0 | 2.238 | 1.467
CCY1B | COOMERA, HELENSVALE, OXENFORD, UPPER COOMERA | Urban | 839 | 4.649 | 4.554 | 4.973 | 3.9823 |  | 5 | 141113.2 | 141113.2 | 0.001745 | 0.001745
CCY20A | OXENFORD | Urban | 0.5 | 0 | 1.68 | 2.286
CCY24B | HELENSVALE, HOPE ISLAND | Urban | 452 | 4.047 | 3.174 | 3.353 | 0.00138 |  | 1 | 80.55 | 80.55 | 1.01e-06 | 1.01e-06
CCY25A | OXENFORD, PACIFIC PINES | Urban | 2063 | 0 | 12.648 | 4.63 | 2.4972 |  | 5 | 191889.8 | 191889.8 | 0.001978 | 0.001978
CCY26A | OXENFORD, UPPER COOMERA | Rural short | 1638 | 7.147 | 9.679 | 4.668
CCY3B | HELENSVALE | Urban | 1234 | 1.41 | 7.081 | 3.792 | 0.62976 | 0.26599 | 8 | 27727.44 | 27727.44 | 0.000163 | 0.000163 | 4 | 11710.85 | 3.75e-05
CCY4A | HELENSVALE, OXENFORD | Urban | 1.6 | 0 | 3.282 | 3.068
CCY6A | COOMERA, HELENSVALE, OXENFORD | Urban | 660 | 4.928 | 2.12 | 2.934 | 0.073037 | 3.5631 | 5 | 1749.517 | 1749.517 | 1.41e-05 | 1.41e-05 | 5 | 85349 | 0.000237
CCY7A | OXENFORD, UPPER COOMERA | Rural short | 1437 | 3.67 | 10.454 | 3.944
CCY8A | GAVEN, HELENSVALE, OXENFORD, PACIFIC PINES | Rural short | 917 | 5.669 | 8.315 | 2.572
CCYUPC2 | MAUDSLAND, OXENFORD, PACIFIC PINES | Rural short | 1762.1 | 5.495 | 11.303 | 4.363
CCYUPC23 | MAUDSLAND, OXENFORD, UPPER COOMERA | Urban | 506.5 | 4.808 | 3.014 | 4.192 | 0.000962 | 0.008752 | 1 | 45.6 | 45.6 | 1.01e-06 | 1.01e-06 | 1 | 414.72 | 1.31e-05
CDKQPT25 | MORNINGSIDE | Urban | 2 | 0 | 2.132 | 2.096
CDRSPD12 | SURFERS PARADISE | Urban | 1572 | 2.134 | 0.58 | 2.001 | 0.21443 | 0.19073 | 9 | 18642.82 | 18642.82 | 0.000143 | 0.000143 | 3 | 16582.8 | 8.24e-05
CDRSPD9 | SURFERS PARADISE | Urban | 493 | 0.931 | 0.784 | 0.834 | 0.97376 | 0.052932 | 2 | 91063 | 91063 | 0.000782 | 0.000782 | 3 | 4950.06 | 2.56e-05
CDS2 | CARINDALE | Urban | 3 | 0 | 0.198
CDS4 | CARINDALE | Urban | 5
CDSSRD21 | CARINDALE | Urban | 6 | 0 | 2.493 | 2.744
CDSSRD23 | CARINDALE | Urban | 446 | 0 | 3.967 | 3.201 | 0.001261 | 0.010358 | 1 | 83.45 | 83.45 | 1.01e-06 | 1.01e-06 | 2 | 685.34 | 4.49e-06
CDSSRD25 | CARINA HEIGHTS, CARINDALE | Urban | 154 | 0 | 1.248 | 3.601
CEP6 | HERSTON | Urban | 2 | 0 | 0.392 |  |  |  | 1 | 8 |  | 2.03e-06
CEP7 | HERSTON | Urban | 2 | 0 | 0.179 |  |  |  | 1 | 8 |  | 2.03e-06
CFD1A | ASCOT, CLAYFIELD | Urban | 1613 | 4.186 | 0.404 | 3.372 | 2.8854 | 0.86814 | 10 | 201794.2 | 201794.2 | 0.006834 | 0.006834 | 22 | 60714.72 | 0.000256
CFD2A | CLAYFIELD, WOOLOOWIN | Urban | 1425 | 4.344 | 0.496 | 2.344 | 0.68329 | 0.54673 | 9 | 58013.93 | 57887.13 | 0.002886 | 0.002885 | 7 | 46419.8 | 0.000173
CFD6A | ALBION, BOWEN HILLS, CLAYFIELD, WINDSOR, WOOLOOWIN | Urban | 2161 | 6.252 | 0.654 | 4.935 | 4.436 | 1.0337 | 15 | 461546.7 | 461546.7 | 0.006587 | 0.006587 | 13 | 107552.9 | 0.000313
CFD8A | ALBION, BOWEN HILLS, CLAYFIELD | Urban | 1250 | 3.01 | 1.692 | 4.516 | 3.8193 | 1.751 | 13 | 139363.1 | 139363.1 | 0.003752 | 0.003752 | 11 | 63892.7 | 0.000181
CFD9A | KEDRON, WOOLOOWIN | Urban | 5.3 | 0 | 3.119 | 2.496 | 0.004871 |  | 1 | 10.68 | 10.68 | 5.41e-06 | 5.41e-06
CGARGA84 | BRISBANE | CBD | 3 | 0 | 0.221 |  | 1.9254 |  | 1 | 954 | 954 | 0.000801 | 0.000801
CGT1 | BOWEN HILLS, NEWSTEAD | Urban | 235 | 0.242 | 1.184 |  | 0.025059 | 0.19142 | 2 | 291.9667 | 291.9667 | 2.03e-06 | 2.03e-06 | 1 | 2230.2 | 2.99e-06
CGT5 | BOWEN HILLS, NEWSTEAD, TENERIFFE | Urban | 107 | 0.557 | 1.705 |  |  | 1.6106 | [5 empty] | 3 | 13400 | 3.45e-05
CHL10 | CAMP HILL, CARINA | Urban | 986 | 3.798 | 0.356 | 2.224 | 0.55741 | 0.6927 | 8 | 41979.34 | 41979.34 | 0.001028 | 0.001028 | 17 | 52167.77 | 0.000188
CHL11A | MORNINGSIDE, NORMAN PARK, SEVEN HILLS | Urban | 1852 | 6.672 | 3.15 | 3.963 | 2.3782 | 0.6777 | 14 | 182080.6 | 182080.6 | 0.004103 | 0.004103 | 14 | 51886.74 | 0.000217
CHL2 | CAMP HILL, COORPAROO | Urban | 1441 | 4.712 | 0.288 | 2.746 | 0.1428 | 1.6466 | 8 | 12066.05 | 12066.05 | 0.001475 | 0.001475 | 24 | 139131.1 | 0.000495
CHL3 | CAMP HILL, COORPAROO, NORMAN PARK, SEVEN HILLS | Urban | 1803 | 5.372 | 0.332 | 3.442 | 4.4232 | 0.47367 | 10 | 376281.6 | 376281.6 | 0.005594 | 0.005594 | 13 | 40295.73 | 0.000185
CHL4 | CANNON HILL, MORNINGSIDE, SEVEN HILLS | Urban | 1390 | 5.386 | 1.643 | 2.707 | 6.8701 | 0.36797 | 16 | 576268.2 | 576268.2 | 0.007233 | 0.007233 | 7 | 30865.68 | 0.000132
CHL5 | CAMP HILL, CARINA, CARINA HEIGHTS | Urban | 2100 | 6.061 | 0.571 | 3.752 | 1.259 | 0.60624 | 11 | 99855.15 | 99855.15 | 0.002228 | 0.002228 | 11 | 48084.36 | 0.000195
CHL6A | CAMP HILL, CARINA HEIGHTS | Urban | 1898.5 | 5.481 | 1.983 | 3.655 | 2.8352 | 0.57154 | 19 | 269822.4 | 269822.4 | 0.004328 | 0.004328 | 18 | 54392.27 | 0.000215
CHL7 | CAMP HILL, CANNON HILL, CARINA, SEVEN HILLS | Urban | 1515.5 | 5.977 | 2.594 | 4.173 | 0.99387 | 1.4428 | 13 | 75656.16 | 75573.59 | 0.001762 | 0.001761 | 31 | 109831.3 | 0.000476
CHL8 | CAMP HILL | Urban | 663 | 2.25 | 0.006 | 1.489 | 0.48732 | 0.50068 | 6 | 33322.68 | 33322.68 | 0.000733 | 0.000733 | 11 | 34236.16 | 0.000154
CHL9 | CARINA, CARINDALE | Rural short | 279 | 1.75 | 2.129 | 0.667
CLD11 | BELLS CREEK, CALOUNDRA WEST, LITTLE MOUNTAIN, MERI | Rural short | 1752 | 10.176 | 9.066 | 4.173
CLD16A | CALOUNDRA, CURRIMUNDI, MOFFAT BEACH | Urban | 156 | 4.354 | 1.075 | 1.886 | 0.036918 | 0.02392 | 4 | 1064.95 | 1064.95 | 0.000174 | 0.000174 | 1 | 690 | 3.04e-06
CLD17A | CALOUNDRA, MOFFAT BEACH, SHELLY BEACH | Urban | 1625 | 5.668 | 0.49 | 4.006 | 0.4153 | 1.1866 | 12 | 26643.48 | 26643.48 | 0.001935 | 0.001935 | 8 | 76127.47 | 0.000294
CLD18A | BELLS CREEK, LITTLE MOUNTAIN, MERIDAN PLAINS | Rural short | 55 | 10.51 | 10.392 | 1.753
CLD1A | CALOUNDRA WEST, LITTLE MOUNTAIN | Urban | 1345 | 3.546 | 7.918 | 3.137 | 0.089602 | 0.25138 | 2 | 5518.833 | 5518.833 | 0.001371 | 0.001371 | 3 | 15483 | 5.31e-05
CLD2 | CALOUNDRA, GOLDEN BEACH, PELICAN WATERS | Urban | 2094.5 | 7.275 | 3.811 | 4.538 | 0.36524 | 1.5449 | 13 | 22247.57 | 22061.52 | 0.00231 | 0.002308 | 16 | 94103.78 | 0.000354
CLD20A | AROONA, BATTERY HILL, CALOUNDRA, CURRIMUNDI, DICKY | Urban | 1410 | 8.695 | 3.048 | 3.291 | 0.12561 | 0.18372 | 10 | 6621.391 | 6621.391 | 0.00143 | 0.00143 | 2 | 9684.9 | 6e-05
CLD21A | CALOUNDRA, PELICAN WATERS | Rural short | 1168 | 0 | 14.82 | 3.906
CLD22A | KINGS BEACH | Urban | 1559 | 2.108 | 2.576 | 2.972 | 4.4674 | 0.86757 | 4 | 358615 | 358615 | 0.003829 | 0.003829 | 6 | 69642.36 | 0.000428
CLD25A | CALOUNDRA, KINGS BEACH, MOFFAT BEACH, SHELLY BEACH | Urban | 1313.5 | 2.724 | 0.654 | 2.365 | 0.073503 | 0.63816 | 6 | 4651.601 | 4651.601 | 0.001023 | 0.001023 | 5 | 40385.61 | 0.000166
CLD26A | CALOUNDRA | Urban | 232 | 1.844 | 0.57 | 3.144 | 0.062535 |  | 2 | 1085.5 | 1085.5 | 0.000238 | 0.000238
CLD28A | BEERWAH, BELLS CREEK, COOCHIN CREEK, GOLDEN BEACH, | Rural short | 1456 | 25.092 | 11.875 | 4.211
CLD3 | CALOUNDRA, CALOUNDRA WEST | Urban | 200.5 | 4.559 | 0.903 | 3.277 | 0.091706 |  | 2 | 980.8167 | 980.8167 | 0.000207 | 0.000207
CLD30A | DICKY BEACH, MOFFAT BEACH | Urban | 1076 | 4.084 | 1.912 | 2.098 | 0.27917 | 0.27417 | 12 | 20493.27 | 20493.27 | 0.001174 | 0.001174 | 3 | 20126.6 | 0.000107
CLD7A | CALOUNDRA, KINGS BEACH | Urban | 1360 | 0.843 | 2.35 | 3.22 | 1.5247 |  | 11 | 82639.57 | 82639.57 | 0.002224 | 0.002224
CLD8 | CALOUNDRA | Urban | 537.5 | 1.208 | 1.533 | 3.163 | 0.082532 |  | 4 | 2483.5 | 2483.5 | 0.000534 | 0.000534
CLD9A | CALOUNDRA, GOLDEN BEACH | Urban | 1343 | 4.537 | 1.211 | 3.125 | 0.10733 | 2.0044 | 3 | 5746.833 | 5746.833 | 0.0014 | 0.0014 | 7 | 107322.7 | 0.000338
CLM10B | COOLUM BEACH, NORTH ARM, VALDORA, VERRIERDALE, YAN | Rural short | 435 | 27.465 | 10.2 | 1.658
CLM3 | BLI BLI, COOLUM BEACH, MARCOOLA, MOUNT COOLUM, PAC | Rural short | 1278 | 16.314 | 3.688 | 2.82
CLM4A | COOLUM BEACH, MOUNT COOLUM, YAROOMBA | Urban | 691 | 2.724 | 3.692 | 2.136 | 1.5291 | 0.96107 | 5 | 59486.33 | 59486.33 | 0.000181 | 0.000181 | 4 | 37389.34 | 0.000152
CLM5 | COOLUM BEACH, POINT ARKWRIGHT, YAROOMBA | Urban | 1766 | 5.28 | 1.87 | 3.563 | 3.9977 | 0.67295 | 14 | 269898.7 | 269898.7 | 0.002037 | 0.002037 | 10 | 45433.41 | 0.000224
CLM6 | COOLUM BEACH, PEREGIAN BEACH, PEREGIAN SPRINGS, WE | Urban | 1863 | 11.693 | 1.097 | 3.695 | 0.19578 | 0.38525 | 10 | 13416.25 | 13416.25 | 0.000126 | 0.000126 | 1 | 26400 | 0.000112
CLM7 | COOLUM BEACH | Urban | 969 | 3.006 | 0.648 | 2.049 | 0.10008 | 0.37484 | 8 | 7432.783 | 7432.783 | 8.74e-05 | 8.74e-05 | 7 | 27838.8 | 8.12e-05
CLM8 | COOLUM BEACH, MOUNT COOLUM, YAROOMBA | Urban | 1413 | 6.016 | 1.637 | 2.906 | 0.007707 | 0.30869 | 8 | 689.3411 | 689.3411 | 8.11e-06 | 8.11e-06 | 3 | 27612.26 | 9.72e-05
CLM9 | COOLUM BEACH, MARCOOLA, MOUNT COOLUM | Urban | 2008 | 8.482 | 6.118 | 4.423 | 1.1095 | 0.16338 | 11 | 71109.19 | 71109.19 | 0.000263 | 0.000263 | 4 | 10470.69 | 4.66e-05
CLR3 | BELMONT, CHANDLER, GUMDALE | Rural short | 182.5 | 4.748 | 0.173
CLR6 | CHANDLER | Urban | 10 | 0 | 0.952 |  | 1.5929 |  | 3 | 1426.3 | 1426.3 | 2.13e-05 | 2.13e-05
CLR7 | CHANDLER | Urban | 2 | [5 empty] | 2 | 266 | 266 | 4.06e-06 | 4.06e-06
CLR8 | CHANDLER | Rural short | 56 | 1.496 | 1.528
CLRSRD17 | BELMONT, CARINDALE, CHANDLER | Urban | 783.5 | 8.46 | 2.455 | 4.401 | 2.0968 | 0.16755 | 4 | 106918.6 | 106918.6 | 0.001612 | 0.001612 | 3 | 8543.4 | 3.87e-05
CMA10A | COOMERA, UPPER COOMERA | Rural short | 1416.5 | 2.566 | 15.412 | 4.573
CMA11A | COOMERA | Urban | 559 | 2.623 | 5.59 | 2.782 | 0.072683 | 0.045402 | 3 | 2665.3 | 2665.3 | 3.7e-05 | 3.7e-05 | 2 | 1664.9 | 3.91e-06
CMA15A | PIMPAMA, UPPER COOMERA, WILLOW VALE | Rural short | 1181 | 5.78 | 10.955 | 4.23
CMA18A | UPPER COOMERA | Urban | 1617 | 3.108 | 9.831 | 4.001 | 0.008573 | 0.20266 | 7 | 503.9167 | 503.9167 | 7.1e-06 | 7.1e-06 | 12 | 11913.09 | 0.000211
CMA20A | UPPER COOMERA | Urban | 1350 | 0.841 | 8.506 | 4.154 | 0.005533 | 0.006452 | 2 | 267.6667 | 267.6667 | 2.03e-06 | 2.03e-06 | 3 | 312.12 | 6.16e-06
CMA8A | PIMPAMA, UPPER COOMERA, WILLOW VALE | Rural short | 1158 | 13.351 | 11.084 | 3.525
CMA9A | UPPER COOMERA | Urban | 1316 | 1.263 | 7.811 | 3.296 | 0.78199 | 0.72886 | 4 | 42971.11 | 42971.11 | 0.00016 | 0.00016 | 5 | 40051.4 | 3.34e-05
CMD11A | AROONA, CALOUNDRA, CALOUNDRA WEST, CURRIMUNDI, LIT | Rural short | 2249 | 6.915 | 12.669 | 4.888
CMD13A | AROONA, BATTERY HILL, CURRIMUNDI | Urban | 1195 | 3.414 | 2.53 | 2.468 | 0.00431 | 0.013666 | 3 | 335.9667 | 335.9667 | 3.04e-06 | 3.04e-06 | 1 | 1065.3 | 8.06e-06
CMD15A | BOKARINA, WURTULLA | Urban | 1338 | 6.708 | 1.646 | 2.688 | 0.37668 | 0.056173 | 10 | 27228.68 | 27228.68 | 0.000741 | 0.000741 | 2 | 4060.55 | 2.33e-05
CMD17A | BIRTINYA | Rural short | 8 | 0 | 3.174 | 0.972
CMD3A | AROONA, CURRIMUNDI, LITTLE MOUNTAIN, MERIDAN PLAIN | Rural short | 2628 | 4.761 | 14.978 | 5.338
CMD5A | BATTERY HILL, CURRIMUNDI, DICKY BEACH | Urban | 1561 | 5.74 | 1.071 | 2.915 | 9.6526 | 0.15318 | 10 | 673647.7 | 673647.7 | 0.003241 | 0.003241 | 2 | 10690.16 | 4.18e-05
CMD7A | BIRTINYA, BOKARINA, WURTULLA | Urban | 1395 | 4.724 | 5.458 | 3.43
CMV10B | CALAMVALE, SUNNYBANK HILLS | Urban | 312 | 0 | 2.403 | 4.592 | 0.007506 | 0.033397 | 1 | 176.2167 | 176.2167 | 1.01e-06 | 1.01e-06 | 3 | 784.08 | 1.75e-05
CMV11A | ALGESTER, CALAMVALE, PARKINSON | Urban | 1449 | 2.833 | 6.094 | 3.753 | 4.7951 | 0.015332 | 4 | 337613.7 | 128668.7 | 0.002967 | 0.001506 | 3 | 1079.49 | 1.16e-05
CMV12A | ALGESTER, CALAMVALE, PARKINSON | Urban | 910 | 0.146 | 8.048 | 2.744 | 0.007574 | 0.13922 | 4 | 360.0821 | 360.0821 | 4.06e-06 | 4.06e-06 | 2 | 6618.91 | 8.98e-05
CMV12B | ALGESTER, CALAMVALE, PARKINSON | Urban | 2183 | 0 | 14.732 | 5.468 | 0.001455 | 0.032461 | 1 | 104.0167 | 104.0167 | 1.01e-06 | 1.01e-06 | 2 | 2320.38 | 2.96e-05
CMV13 | CALAMVALE, STRETTON, SUNNYBANK HILLS | Urban | 1635 | 1.207 | 7.55 | 4.268 | 0.22045 | 0.002188 | 7 | 14895.44 | 14895.44 | 5.99e-05 | 5.99e-05 | 1 | 147.84 | 3.41e-06
CMV14 | ALGESTER, CALAMVALE | Urban | 1220 | 1.97 | 5.707 | 2.934 | 6.9108 |  | 7 | 480552.6 | 360168.6 | 0.004944 | 0.003711
CMV7 | ALGESTER, CALAMVALE | Urban | 1766 | 3.345 | 5.796 | 3.906 | 8.3239 | 0.23986 | 7 | 535850.1 | 123978.1 | 0.003455 | 0.001744 | 3 | 15440.82 | 4.25e-05
CMV8 | ALGESTER, CALAMVALE, SUNNYBANK HILLS | Urban | 955.2 | 2.634 | 4.455 | 4.154 | 0.009829 |  | 3 | 330.0167 | 330.0167 | 2.43e-05 | 2.43e-05
CMV9A | CALAMVALE, RUNCORN, SUNNYBANK HILLS | Urban | 1484 | 0.485 | 6.663 | 2.944 | 0.17332 | 0.34905 | 3 | 6086.283 | 6086.283 | 4.66e-05 | 4.66e-05 | 3 | 12257.12 | 5.13e-05
CMV9B | CALAMVALE, STRETTON | Urban | 1066 | 0 | 6.282 | 2.534 | 0.10875 |  | 2 | 7048.2 | 7048.2 | 2.03e-06 | 2.03e-06
CMY1 | ATKINSONS DAM, BUARABA, CHURCHABLE, CLARENDON, COO | Rural short | 266 | 70.606 | 1.014 | 1.677
CMY3 | COOMINYA | Urban | 2 | 0.336 | 0.114 | 1.524 |  |  | 1 | 166 | 166 | 2.03e-06 | 2.03e-06
CMY4 | ATKINSONS DAM, BUARABA, BUARABA CREEK, CLARENDON, | Rural short | 677 | 99.881 | 0.089 | 2.077
CNA3B | SWANBANK | Urban | 4 | 0 | 0.134 | 0.477
CNA7A | BLACKSTONE, NEW CHUM, SILKSTONE | Rural short | 654 | 6.786 | 0.77 | 1.81
CNA8A | BLACKSTONE, REDBANK PLAINS, RIPLEY, SOUTH RIPLEY, | Rural short | 109 | 33.899 | 0.327 | 0.915
CNA9A | BLACKSTONE, FLINDERS VIEW, RACEVIEW, RIPLEY, SWANB | Rural short | 195 | 14.805 | 1.174 | 1.226
CNB21B | CORNUBIA, SHAILER PARK | Urban | 1276.8 | 5.788 | 5.018 | 3.601 | 0.0439 | 0.02459 | 5 | 2818.413 | 2818.413 | 1.48e-05 | 1.48e-05 | 1 | 1578.72 | 1.12e-05
CNB24A | CARBROOK, CORNUBIA, MOUNT COTTON | Rural short | 1197 | 23.39 | 5.966 | 2.934
CNB25A | CORNUBIA | Urban | 702 | 3.682 | 2.866 | 1.772 | 0.017924 | 0.001864 | 9 | 1140.9 | 1140.9 | 9.13e-06 | 9.13e-06 | 1 | 118.65 | 1.06e-06
CNB26A | CARBROOK, CORNUBIA, REDLAND BAY | Rural short | 450 | 23.495 | 0.673 | 3.582
COR22A | BLACK MOUNTAIN, COORAN, FEDERAL, POMONA | Rural short | 715 | 39.526 | 1.147 | 1.276
COR23A | COMO, COORAN, COOTHARABA, KIN KIN, PINBARREN | Rural short | 567 | 98.196 | 0.281 | 1.24
COR25A | COOROY, PINBARREN, POMONA | Rural short | 813 | 29.12 | 0.354 | 1.924
COR26A | BOREEN POINT, COOTHARABA, PINBARREN, POMONA | Rural short | 872 | 81.306 | 3.372 | 1.6
CPB1 | CAPALABA | Urban | 0.8 | 0 | 0.98 | 4.173
CPB2 | CAPALABA | Urban | 96.2 | 0.102 | 2.288 | 1.524 | 0.031869 | 0.13808 | 2 | 314.25 | 314.25 | 2.88e-06 | 2.88e-06 | 1 | 1361.6 | 9.33e-06
CPB3 | BIRKDALE, CAPALABA | Rural short | 935.5 | 5.377 | 0.59 | 1.962
CPB4 | CAPALABA | Urban | 1831.5 | 9.215 | 0.376 | 3.582 | 6.4104 | 0.63831 | 12 | 204500.9 | 204500.9 | 0.002322 | 0.002322 | 6 | 20363 | 7.81e-05
CPB5 | CAPALABA | Urban | 75 | 0.185 | 0.954 | 0.819 | 0.041219 | 0.95935 | 1 | 354.0667 | 354.0667 | 1.01e-06 | 1.01e-06 | 2 | 8240.76 | 3.08e-05
CPB6 | CAPALABA, CAPALABA WEST, CHANDLER | Urban | 385.5 | 8.35 | 0.696 | 2.667 | 0.11147 | 0.6619 | 5 | 1911.03 | 1842.063 | 2.04e-05 | 1.94e-05 | 3 | 11348 | 3.65e-05
CPB8 | CAPALABA, CAPALABA WEST, CHANDLER, GUMDALE, RANSOM | Rural short | 343 | 12.784 | 1.099 | 1.486
CPC1A | CAROLE PARK | Urban | 27 | 0 | 2.185 | 3.601 |  | 0.066008 | [5 empty] | 1 | 99 | 3.04e-06
CPC22A | CAROLE PARK | Urban | 31 | 0 | 2.298 | 3.715
CPC22B | CAROLE PARK | Urban | 4 | 0 | 0.297 | 3.048
CPC23A | CAROLE PARK | Urban | 9 | 0 | 1.452 | 4.23
CPC25A | CAROLE PARK | Urban | 38 | 2.21 | 0.931 | 4.115 |  | 0.4184 | [5 empty] | 2 | 242.78 | 3.06e-06
CPC2A | CAROLE PARK, ELLEN GROVE, FOREST LAKE | Urban | 1446 | 4.615 | 7.077 | 3.792 | 0.9666 | 0.079891 | 7 | 66316.48 | 66316.48 | 0.003092 | 0.003092 | 2 | 5481.14 | 2.45e-05
CPC2B | CAMIRA, CAROLE PARK | Urban | 1768 | 11.182 | 0.998 | 4.439 | 1.7693 | 0.073897 | 29 | 131394.3 | 131394.3 | 0.002274 | 0.002274 | 3 | 5487.76 | 3.61e-05
CPC3A | CAROLE PARK | Urban | 5 | 0 | 1.2 | 2.686 | 0.002966 |  | 1 | 1.16 | 1.16 | 2.03e-08 | 2.03e-08
CPC3B | CAROLE PARK | Urban | 42 | 0.38 | 3.33 | 4.401 | 0.082609 |  | 1 | 178.65 | 178.65 | 1.01e-06 | 1.01e-06
CPC5A | CAROLE PARK | Urban | 3 | 0 | 1.284 | 0.438
CPD1 | BLANCHVIEW, DERRYMORE, FLAGSTONE CREEK, HELIDON, L | Rural short | 388 | 89.026 | 0.59 | 1.067
CPD2A | BLANCHVIEW, CARPENDALE, DERRYMORE, GRANTHAM, HELID | Rural short | 186 | 50.753 | 0.161 | 0.724
CPK10 | CAMIRA, GAILES, SPRINGFIELD | Urban | 911 | 3.357 | 3.029 | 2.213 | 2.1088 | 0.014555 | 7 | 131931.3 | 131931.3 | 0.001875 | 0.001875 | 1 | 910.57 | 8.63e-06
CPK11 | CAMIRA, CAROLE PARK | Urban | 42 | 1.04 | 3.41 | 2.153 | 0.99641 | 0.037365 | 1 | 2400 |  | 4.06e-06 |  | 1 | 90 | 3.04e-06
CPK12 | CAROLE PARK | Urban | 2 | 1.137 | 0.788 | 4.154 |  | 15.2312 | [5 empty] | 1 | 504 | 1.01e-06
CPK13 | CAMIRA, GAILES, GOODNA | Rural short | 406 | 4.831 | 0.981 | 0.998
CPK6 | CAROLE PARK | Urban | 20 | 0.42 | 2.959 | 2.229 | 1.3324 |  | 1 | 1125 | 1125 | 1.93e-05 | 1.93e-05
CPK7 | CAMIRA, GOODNA | Urban | 801.5 | 4.562 | 0.633 | 3.258 | 0.32275 | 0.74276 | 5 | 12015.3 | 12015.3 | 0.000107 | 0.000107 | 7 | 27651.24 | 9.17e-05
CPK8 | CAMIRA, CAROLE PARK | Urban | 15 | 1.208 | 1.707 | 4.839 | 0.11572 |  | 1 | 247.5 | 247.5 | 2.01e-06 | 2.01e-06
CPK9 | CAMIRA, GAILES, GOODNA | Rural short | 715 | 5.324 | 2.15 | 1.867
CPKTR0 | CAMIRA | Urban | 4
CPL23A | ACACIA RIDGE, DURACK, WILLAWONG | Rural short | 945 | 10.925 | 2.562 | 1.495
CPL25A | ACACIA RIDGE | Urban | 316 | 1.567 | 0.355 | 0.591 | 0.12152 | 0.1282 | 6 | 11612.1 | 11612.1 | 0.000751 | 0.000751 | 4 | 12250.82 | 6.68e-05
CPL25B | ARCHERFIELD, COOPERS PLAINS | Urban | 237.7 | 2.194 | 1.907 | 4.039 | 0.50891 | 0.003669 | 6 | 5686.46 | 5686.46 | 0.000477 | 0.000477 | 1 | 41 | 1.01e-06
CPL26A | ACACIA RIDGE, ARCHERFIELD | Urban | 423 | 2.363 | 4.109 | 3.277 | 3.7175 | 0.28515 | 8 | 136705.3 | 136705.3 | 0.001698 | 0.001698 | 8 | 10485.78 | 4.26e-05
CPL2A | ACACIA RIDGE, COOPERS PLAINS | Urban | 308.5 | 3.85 | 1.099 | 3.449 | 2.0174 |  | 5 | 31006.73 | 31006.73 | 0.001031 | 0.001031
CPL3A | ACACIA RIDGE | Urban | 423.2 | 1.744 | 5.804 | 4.477 | 6.3974 | 0.85157 | 7 | 139649.6 | 139649.6 | 0.002149 | 0.002149 | 6 | 18589.14 | 6.91e-05
CPL5A | ACACIA RIDGE, ARCHERFIELD, COOPERS PLAINS | Urban | 135.5 | 1.823 | 0.807 | 3.639 | 0.39692 | 0.026388 | 2 | 2019.467 | 2019.467 | 0.000256 | 0.000256 | 1 | 134.26 | 9.94e-07
CPL6A | ACACIA RIDGE, ARCHERFIELD, COOPERS PLAINS | Urban | 309.5 | 3.5 | 0.464 | 4.401 | 2.3944 | 0.58096 | 6 | 41052.62 | 41052.62 | 0.000999 | 0.000999 | 1 | 9960.75 | 3.54e-05
CPR4 | COORPAROO | Urban | 945.5 | 3.857 | 0.442 | 3.201 | 0.23398 | 0.71391 | 4 | 10540.43 | 10540.43 | 0.000119 | 0.000119 | 13 | 32160.68 | 0.000137
CPR5 | COORPAROO, GREENSLOPES | Urban | 2845.5 | 7.249 | 0.584 | 4.973 | 3.5165 | 0.42022 | 13 | 339670.3 | 339481.9 | 0.003215 | 0.003214 | 6 | 40589.8 | 0.000155
CPR6 | CAMP HILL, COORPAROO, NORMAN PARK | Urban | 1334.5 | 2.803 | 0.439 | 2.191 | 2.249 | 0.37886 | 7 | 208018.9 | 208018.9 | 0.001509 | 0.001509 | 10 | 35042.07 | 0.000137
CPR7 | COORPAROO, GREENSLOPES | Urban | 2553.2 | 4.652 | 0.913 | 4.782 | 10.6369 | 0.69607 | 11 | 703552.8 | 703552.8 | 0.00374 | 0.00374 | 6 | 46040.05 | 0.000218
CPRGBP3 | COORPAROO | Urban | 3 | 0 | 1.46 | 3.563 | 0.007231 |  | 1 | 177.2 | 177.2 | 1.01e-06 | 1.01e-06
CPS12B | CAPALABA, SHELDON | Rural short | 1866 | 25.388 | 1.414 | 5.24
CPS13A | CAPALABA | Urban | 164 | 1.069 | 0.776 | 1.562
CPS15A | ALEXANDRA HILLS, CAPALABA | Urban | 1577 | 9.447 | 3.444 | 3.544 | 0.046171 | 0.088778 | 8 | 2646.629 | 2396.096 | 3.99e-05 | 3.89e-05 | 1 | 5088.96 | 1.85e-05
CPS1B | CAPALABA | Urban | 224 | 0 | 1.508 | 2.667 |  | 0.012371 | [5 empty] | 1 | 176 | 1.01e-06
CPS2B | CAPALABA | Urban | 1368.5 | 5.228 | 3.742 | 3.163 | 1.0785 |  | 12 | 70696.29 | 70696.29 | 0.001589 | 0.001589
CPS5A | ALEXANDRA HILLS, CAPALABA | Urban | 978 | 5.571 | 1.281 | 2.534 | 0.13259 | 0.16299 | 7 | 8251.23 | 8251.23 | 0.000128 | 0.000128 | 2 | 10143 | 4.2e-05
CRB15A | CURRUMBIN WATERS | Urban | 377 | 1.941 | 0.822 | 2.153 | 0.0144 | 1.3976 | 2 | 232.5833 | 232.5833 | 2.03e-06 | 2.03e-06 | 3 | 22572.49 | 6.09e-05
CRB16B | CURRUMBIN WATERS | Urban | 3 | 0.167 | 2.112 | 2.706
CRB18A | CURRUMBIN WATERS | Urban | 128 | 1.987 | 0.05 | 2.106 | 0.81456 |  | 2 | 8727.85 | 8727.85 | 0.000138 | 0.000138
CRB22A | CURRUMBIN WATERS | Urban | 1847 | 3.411 | 6.278 | 3.56 | 0.31974 | 1.1969 | 11 | 22285.98 | 22285.98 | 0.000367 | 0.000367 | 6 | 83421.24 | 0.000241
CRB24B | CURRUMBIN, PALM BEACH, TUGUN | Urban | 2523 | 6.294 | 0.876 | 5.292 | 8.9296 | 5.0457 | 13 | 504947.7 | 504947.7 | 0.005864 | 0.005864 | 25 | 285320.9 | 0.000693
CRB25A | CURRUMBIN VALLEY, CURRUMBIN WATERS, TALLEBUDGERA, | Rural short | 1214 | 48.43 | 2.749 | 3.233
CRBTHP14 | CURRUMBIN, PALM BEACH, TUGUN | Urban | 1334 | 6.224 | 3.458 | 3.677 | 3.0183 | 4.9142 | 14 | 91010.46 | 91010.46 | 0.001508 | 0.001508 | 24 | 148178.2 | 0.000508
CRBTHP26 | CURRUMBIN WATERS, TUGUN | Urban | 1082 | 4.9 | 1.76 | 3.618 | 0.019459 | 2.8694 | 8 | 1767.9 | 1767.9 | 3.39e-05 | 3.39e-05 | 13 | 260692.6 | 0.000603
CRM12A | CRESTMEAD | Urban | 23 | 1.445 | 0.915 | 3.753
CRM13A | CRESTMEAD, MARSDEN, PARK RIDGE | Urban | 1777 | 8.4 | 2.703 | 4.192 | 0.017559 | 0.003169 | 10 | 1180.217 | 1180.217 | 1.01e-05 | 1.01e-05 | 1 | 213 | 3.04e-06
CRM13B | CRESTMEAD | Urban | 33 | 1.127 | 2.025 | 4.135
CRM15A | BROWNS PLAINS, HERITAGE PARK, REGENTS PARK | Urban | 1574 | 9.941 | 1.134 | 3.462 | 0.45609 | 0.037748 | 19 | 29770.92 | 29770.92 | 0.00018 | 0.00018 | 1 | 2464 | 1.12e-05
CRM16A | BERRINBA, BROWNS PLAINS, KINGSTON, LOGAN CENTRAL, | Rural short | 1934 | 11.655 | 8.114 | 4.211
CRM1B | CRESTMEAD | Urban | 20 | 0.948 | 0.876 | 4.268 |  | 2.2722 | [5 empty] | 4 | 1456 | 1.42e-05
CRM3A | CRESTMEAD | Urban | 26 | 1.735 | 1.937 | 2.896
CRM5A | BERRINBA, BROWNS PLAINS, CRESTMEAD, HERITAGE PARK | Urban | 1085 | 6.378 | 4.918 | 3.449 | 0.13323 | 0.017785 | 1 | 6966.96 | 6966.96 | 3.88e-05 | 3.88e-05 | 1 | 930 | 3.04e-06
CRM5B | CRESTMEAD | Urban | 29 | 0.989 | 0.969 | 0.667 | 0.04047 | 0.013939 | 2 | 377.4433 | 109.4833 | 2.35e-06 | 1.01e-06 | 1 | 130 | 2.03e-06
CRMEDB2 | CRESTMEAD, HERITAGE PARK | Urban | 26 | 2.838 | 0.258 | 1.886 | 0.078278 | 0.25176 | 1 | 290.4 | 290.4 | 2.68e-06 | 2.68e-06 | 3 | 934 | 3.04e-06
CRY2A | COOROY, LAKE MACDONALD, POMONA, TINBEERWAH | Rural short | 683.5 | 50.318 | 2.422 | 2.153
CRY3A | COOROY | Rural short | 972.5 | 19.572 | 0.853 | 2.309
CRY5A | COOROY, EUMUNDI, TINBEERWAH | Rural short | 88 | 16.224 | 0.279 | 0.286
CRY6A | BELLI PARK, COOLOOLABIN, COOROY, EERWAH VALE, EUMU | Rural short | 649 | 57.51 | 2.347 | 1.334
CSE10 | CHERMSIDE, KEDRON | Urban | 744 | 2.338 | 2.955 | 3.296 | 0.27729 | 0.49617 | 4 | 18858.28 | 18858.28 | 0.000978 | 0.000978 | 11 | 33744.48 | 0.000134
CSE2 | ASPLEY, CHERMSIDE, CHERMSIDE WEST | Urban | 1114.5 | 4.793 | 4.643 | 2.725 | 0.113 | 1.4902 | 6 | 7114.45 | 7114.45 | 0.001126 | 0.001126 | 21 | 93822.66 | 0.000361
CSE21A | CHERMSIDE | Urban | 162 | 0 | 1.029 | 1.219
CSE23A | CHERMSIDE | Urban | 137 | 1.507 | 2.077 | 1.048 |  | 0.80344 | [5 empty] | 3 | 6828.35 | 2.29e-05
CSE27A | CHERMSIDE | Urban | 16 | 0 | 1.688 | 1.867 |  | 0.094843 | [5 empty] | 1 | 297 | 1.34e-06
CSE3 | CHERMSIDE | Urban | 623 | 0.339 | 2.48 | 4.535 | 0.13351 | 0.25717 | 2 | 3811.25 | 3811.25 | 0.000633 | 0.000633 | 2 | 7341.6 | 5.2e-05
CSE4 | ASPLEY, CHERMSIDE, CHERMSIDE WEST | Urban | 1835.5 | 6.183 | 2.032 | 3.563 | 0.41955 | 1.5842 | 16 | 20413.75 | 20360.64 | 0.00195 | 0.001949 | 15 | 77080.64 | 0.00026
CSE6 | CHERMSIDE, KEDRON, WAVELL HEIGHTS | Urban | 1908.5 | 6.528 | 0.987 | 3.329 | 0.15919 | 0.62698 | 13 | 12570.24 | 12570.24 | 0.001949 | 0.001949 | 10 | 49509.28 | 0.000212
CSE7 | CHERMSIDE, WAVELL HEIGHTS | Urban | 981 | 4.5 | 0.123 | 1.944 | 0.094918 | 0.009248 | 6 | 6121.262 | 6121.262 | 0.000937 | 0.000937 | 1 | 596.4 | 2.16e-06
CSE9 | CHERMSIDE, GEEBUNG, WAVELL HEIGHTS | Urban | 1998 | 8.178 | 0.802 | 3.618 | 0.20222 | 1.0683 | 9 | 12542.53 | 12542.53 | 0.002032 | 0.002032 | 16 | 66260.4 | 0.000251
CSQOXG5 | SPRING HILL | Urban | 143.5 | 0 | 0.893
CSTQUT18 | BRISBANE | CBD | 15 | 0 | 1.039 | 1.905
CTC2 | SOUTH BRISBANE | Urban | 3
CTC3 | SOUTH BRISBANE | Urban | 3
CTC4 | SOUTH BRISBANE | Urban | 6
CTC5 | SOUTH BRISBANE | Urban | 4
CVL11A | CLEVELAND | Urban | 67 | 1.039 | 0.504 | 3.753
CVL13A | CLEVELAND | Urban | 5 | 0 | 0.986 | 0.591
CVL15A | CLEVELAND | Urban | 53 | 1.167 | 1.419 | 3.582 |  | 0.52491 | [5 empty] | 1 | 1140 | 3.04e-06
CVL17A | CLEVELAND, ORMISTON, THORNLANDS | Urban | 1863 | 8.104 | 3.048 | 3.791 | 0.018142 | 0.080505 | 14 | 1387.487 | 1199.271 | 1.42e-05 | 1.32e-05 | 2 | 6156.96 | 2.48e-05
CVL1A | CLEVELAND, THORNLANDS | Urban | 1380 | 2.437 | 5.937 | 3.601 | 0.004792 | 0.01411 | 4 | 324.05 | 324.05 | 4.06e-06 | 4.06e-06 | 3 | 954.14 | 2.81e-05
CVL3A | ALEXANDRA HILLS, CLEVELAND, THORNLANDS | Rural short | 988 | 7.928 | 2.943 | 2.553
CVL5A | ALEXANDRA HILLS, CAPALABA, THORNLANDS | Rural short | 270 | 6.384 | 2.175 | 0.8
CVL7A | CAPALABA, CLEVELAND, SHELDON, THORNLANDS | Rural short | 1382 | 28.956 | 2.771 | 4.268
CVL9A | CLEVELAND, THORNLANDS | Urban | 986 | 5.868 | 0.96 | 2.432 | 0.009547 | 0.015391 | 7 | 664.9844 | 664.9844 | 7.1e-06 | 7.1e-06 | 2 | 1072.1 | 1.15e-05
DBS13A | HEMMANT, MURARRIE | Urban | 7 | 0 | 1.2 | 2.534
DBS15A | MURARRIE | Urban | 44 | 0 | 2.676 | 1.639
DBS16A | MURARRIE | Urban | 51.3 | 0 | 3.645 | 3.106
DBS2A | HEMMANT, MURARRIE | Urban | 14 | 0.689 | 0.792 | 1.467 |  | 1.2833 | [5 empty] | 1 | 628.2 | 7.08e-06
DBS4A | MURARRIE | Urban | 106 | 3.254 | 2.196 | 4.82 | 1.3053 |  | 1 | 5040 | 5040 | 0.000106 | 0.000106
DBS5A | MURARRIE | Urban | 133 | 0.372 | 3.093 | 3.144 | 0.22122 |  | 1 | 2322 | 2322 | 0.000131 | 0.000131
DBY10 | DECEPTION BAY, NARANGBA, NORTH LAKES | Rural short | 849 | 4.834 | 3.559 | 2.572
DBY11 | DECEPTION BAY | Urban | 1235 | 7.683 | 0.808 | 2.829 | 1.6887 | 0.73673 | 18 | 132393.4 | 132289.7 | 0.001525 | 0.001523 | 10 | 57758.19 | 0.000238
DBY4 | DECEPTION BAY, NARANGBA | Urban | 225 | 5.113 | 4.098 | 5.43 |  | 0.045112 | [5 empty] | 1 | 325 | 1.01e-06
DBY5 | DECEPTION BAY | Urban | 288 | 1.339 | 0.707 | 0.705 |  | 0.10785 | [5 empty] | 4 | 8332.88 | 3.77e-05
DBY6 | DECEPTION BAY | Urban | 1632 | 9.506 | 0.262 | 3.582 | 1.0968 | 2.9196 | 11 | 72189.32 | 72189.32 | 0.002692 | 0.002692 | 29 | 192152.3 | 0.000738
DBY7A | DECEPTION BAY, ROTHWELL | Urban | 1875 | 4.433 | 4.504 | 3.714 | 0.84118 | 0.11818 | 6 | 56485.79 | 56485.79 | 0.000946 | 0.000946 | 2 | 7935.86 | 2.44e-05
DBY8A | DECEPTION BAY | Urban | 1197.5 | 3.974 | 1.926 | 3.01 | 0.00153 | 0.11625 | 2 | 80.5333 | 80.5333 | 2.03e-06 | 2.03e-06 | 2 | 6117.42 | 3.17e-05
DBY9 | DECEPTION BAY, ROTHWELL | Urban | 1417.5 | 7.046 | 5.454 | 4.173 | 0.005616 | 0.65847 | 5 | 334.9667 | 334.9667 | 5.07e-06 | 5.07e-06 | 6 | 39274.47 | 0.00013
DRA11A | DARRA | Urban | 776 | 3.653 | 0.746 |  | 0.004541 | 0.033702 | 3 | 337.9224 | 337.9224 | 3.04e-06 | 3.04e-06 | 1 | 2508 | 1.93e-05
DRA15A | DARRA, INALA, RICHLANDS | Urban | 384 | 2.977 | 2.663 |  |  | 0.1129 | [5 empty] | 1 | 1362 | 6.08e-06
DRA3B | RICHLANDS | Urban | 12 |  |  | 0.479
DRA5OLD | DARRA, RICHLANDS, WACOL | Urban | 89
DRA7A | DARRA | Urban | 258 | 2.316 | 1.023
DRA8A | DARRA, INALA, RICHLANDS | Urban | 236.5 | 3.625 | 2.244 |  | 0.018141 |  | 1 | 86.9139 | 86.9139 | 1.01e-06 | 1.01e-06
DRA9A | DARRA, SUMNER | Urban | 414.5 | 2.527 | 2.362 |  |  | 0.0884 | [5 empty] | 1 | 1760 | 1.12e-05
DRD13A | CLONTARF, MARGATE | Urban | 2136 | 8.173 | 0.273 | 3.125 | 0.006816 | 0.7375 | 10 | 608.8833 | 608.8833 | 1.01e-05 | 1.01e-05 | 9 | 65878.08 | 0.000233
DRD15B | CLONTARF, WOODY POINT | Urban | 2284 | 8.489 | 1.015 | 4.542 | 0.44414 | 0.31654 | 6 | 27436.83 | 27436.83 | 0.000198 | 0.000198 | 6 | 19554.53 | 7.5e-05
DRD16A | CLONTARF, KIPPA-RING | Urban | 562 | 5.087 | 0.487 | 3.353 | 5.5387 | 0.65226 | 2 | 153994.2 | 153994.2 | 0.000565 | 0.000565 | 1 | 18135 | 3.95e-05
DRD2A | CLONTARF, KIPPA-RING, ROTHWELL | Rural short | 1823 | 5.842 | 7.902 | 3.425
DRD3A | CLONTARF, KIPPA-RING | Urban | 1703 | 8.737 | 1.176 | 3.963 | 10.0805 | 0.70463 | 13 | 419672.1 | 419672.1 | 0.006279 | 0.006279 | 7 | 29335.19 | 0.000115
DRD5A | CLONTARF, MARGATE, WOODY POINT | Urban | 2684.3 | 9.332 | 0.547 | 4.33 | 0.015409 | 1.349 | 13 | 1392.146 | 1392.146 | 1.32e-05 | 1.32e-05 | 11 | 121877.6 | 0.000362
EMD1 | EERWAH VALE, EUMUNDI | Rural short | 377 | 11.64 | 1.568 | 0.781
EMD2 | BRIDGES, EERWAH VALE, EUMUNDI, NINDERRY, NORTH ARM | Rural short | 470 | 34.624 | 1.001 | 0.991
EMD3 | DOONAN, EUMUNDI, VERRIERDALE, YANDINA CREEK | Rural short | 629 | 42 | 1.482 | 1.347
EMP15A | EIGHT MILE PLAINS | Urban | 50 | 0 | 2.21 | 4.859 |  | 1.6041 | [5 empty] | 2 | 3605.94 | 7.12e-06
EMP21A | BURBANK, EIGHT MILE PLAINS, PRIESTDALE, ROCHEDALE, | Rural short | 1912 | 27.318 | 5.12 | 4.23
EMP22A | ALGESTER, EIGHT MILE PLAINS | Urban | 75 | 0 | 2.04 | 4.287 | 0.09101 |  | 1 | 158 | 158 | 1.01e-06 | 1.01e-06
EMP23A | EIGHT MILE PLAINS, SUNNYBANK | Urban | 1648 | 1.607 | 6.348 | 3.811 | 0.23599 | 0.39986 | 10 | 14552.78 | 14552.78 | 6.2e-05 | 6.2e-05 | 6 | 24658.52 | 0.000192
EMP25A | EIGHT MILE PLAINS, MACGREGOR, UPPER MT GRAVATT | Urban | 714 | 4.083 | 2.232 | 1.734 | 0.21135 | 0.070185 | 8 | 15282.45 | 15282.45 | 0.000194 | 0.000194 | 1 | 5075 | 1.77e-05
EMP2A | EIGHT MILE PLAINS | Urban | 1180 | 2.066 | 4.413 | 2.991 | 1.4786 | 0.47581 | 3 | 76733.52 | 76733.52 | 0.001196 | 0.001196 | 4 | 24692.46 | 0.000188
EMP3 | EIGHT MILE PLAINS, RUNCORN | Urban | 955 | 2.135 | 3.93 | 4.897 | 0.11628 | 0.11999 | 7 | 2740.827 | 2740.827 | 3.17e-05 | 3.17e-05 | 1 | 2828.28 | 1.11e-05
EMP4A | EIGHT MILE PLAINS, ROCHEDALE, ROCHEDALE SOUTH | Urban | 1252 | 9.184 | 1.571 | 3.16 | 6.974 | 0.45942 | 13 | 343290.4 | 343290.4 | 0.005106 | 0.005106 | 2 | 22614.25 | 4.58e-05
ENG13A | ALDERLEY, ENOGGERA | Urban | 648.5 | 3.308 | 0.578 |  | 0.66833 |  | 2 | 30609.92 | 30609.92 | 0.000659 | 0.000659
ENG17A | ALDERLEY, ASHGROVE, ENOGGERA | Urban | 1715 | 5.618 | 0.399 |  | 0.050191 | 0.16738 | 2 | 4801.823 | 4801.823 | 6.06e-05 | 6.06e-05 | 6 | 16012.87 | 6.86e-05
ENG2A | ASHGROVE, ENOGGERA, GAYTHORNE, MITCHELTON | Urban | 1703 | 7.074 | 0.846 |  | 0.012644 | 0.014389 | 2 | 269.7833 | 269.7833 | 2.03e-06 | 2.03e-06 | 2 | 307.01 | 2.3e-06
ENG4A | ALDERLEY, ENOGGERA | Urban | 1173 | 2.381 | 2.212 |  | 0.000789 | 0.048409 | 1 | 58.302 | 58.302 | 1.01e-06 | 1.01e-06 | 1 | 3578.686 | 2.47e-05
ENG7A | ENOGGERA, EVERTON PARK | Urban | 1301.5 | 4.551 | 1.003 |  | 0.083076 | 0.006733 | 4 | 5433.956 | 5433.956 | 7.65e-05 | 7.65e-05 | 1 | 440.38 | 2.3e-06
ESK2B | ESK | Rural short | 386.5 | 8.562 | 0.64 | 0.934
ESK3A | BIARRA, COAL CREEK, ESK, GALLANANI, MURRUMBA, OTTA | Rural short | 127 | 48.47 | 0.064 | 0.419
ESK5A | ESK, MOUNT HALLEN, REDBANK CREEK | Rural short | 633.5 | 59.237 | 3.199 | 1.81
ESRFLW48 | BRISBANE | CBD | 2 | 0 | 0.687
EXB11 | BRISBANE | CBD | 2
EXB7 | BRISBANE | CBD | 3
EXB9 | BRISBANE | CBD | 2
EXBQEC10 | BRISBANE | CBD | 34 | 0 | 0.321
EZRRWD4 | EBENEZER, MOUNT FORBES, MUTDAPILLY, ROSEWOOD, THAG | Rural short | 272 | 54.697 | 0.89 | 0.67
F1173 | GEEBUNG, VIRGINIA | Urban | 85 | 1.902 | 0.988 |  | 1.7298 |  | 2 | 13152.07 | 13152.07 | 0.000107 | 0.000107
F1221 | BRISBANE | CBD | 4 | 0 | 1.031 | 1.048 |  |  | 2 | 157.57 | 141.57 | 0.001156 | 8.81e-05
F1222 | BRISBANE | CBD | 4 | 0 | 1.031 | 1.867 |  |  | 2 | 157.57 | 141.57 | 0.001156 | 8.81e-05
FAC3 | BRISBANE | CBD | 2
FCHQPT2 | MORNINGSIDE | Urban | 110 | 0 | 5.283 | 2.572
FDS1 | ANTHONY, GOOLMAN, HARRISVILLE, LIMESTONE RIDGES, M | Rural short | 536 | 110.283 | 0.52 | 2.229
FDS3 | COLEYVILLE, HARRISVILLE, KENTS LAGOON, MILORA, MUN | Rural short | 537.3 | 100.707 | 0 | 1.962
FDS4 | COLEYVILLE, HARRISVILLE, MOUNT FORBES, MUTDAPILLY, | Rural short | 365 | 104.754 | 0 | 0.857
FGBSGT23 | DEAGON, FITZGIBBON, TAIGUM, ZILLMERE | Urban | 2349 | 3.276 | 7.224 | 4.249 | 0.09633 | 0.062151 | 4 | 9089.033 | 9089.033 | 5.27e-05 | 5.27e-05 | 4 | 5864.18 | 5.23e-05
FIS12A | LYTTON, PORT OF BRISBANE | Urban | 10.3 | 0 | 4.023 | 3.144
FIS13A | LYTTON, PORT OF BRISBANE | Urban | 27.4 | 0 | 6.162 | 2.553
FIS5A | PORT OF BRISBANE | Urban | 5.6 | 0 | 1.765 | 2.686
FIS7A | PORT OF BRISBANE | Urban | 15.6 | 0 | 4.208 | 1.467
FPT1 | FORTITUDE VALLEY | Urban | 80 | 0 | 0.679
FPT1A | BOWEN HILLS, FORTITUDE VALLEY | Urban | 292.5 | 0 | 1.628
FPVTMT21 | SPRING HILL | CBD | 3 | 0 | 0.358 |  | 0.25105 |  | 1 | 364 |  | 0.024299
FVY1 | FORTITUDE VALLEY | Urban | 69 | 0 | 0.061
GAP1A | THE GAP | Urban | 1014 | 3.92 | 4.08 | 2.54 | 0.19519 | 0.042966 | 6 | 12110.68 | 12110.68 | 0.001107 | 0.001107 | 3 | 2665.875 | 1.44e-05
GAP2A | MT COOTTHA, TOOWONG | Urban | 9 | 0 | 4.983 | 2.058 | 0.043136 | 5.0254 | 1 | 18 | 18 | 9.13e-06 | 9.13e-06 | 2 | 2097 | 4.06e-06
GAP4A | THE GAP | Rural short | 920 | 5.631 | 4.578 | 2.763
GAP6A | THE GAP | Urban | 1088 | 1.167 | 5.721 | 2.706 | 0.08225 | 0.099115 | 3 | 5723.45 | 5723.45 | 0.000102 | 0.000102 | 2 | 6897 | 3.78e-05
GAP8A | THE GAP | Urban | 1576 | 6.454 | 2.463 | 4.649 | 0.014098 | 1.1297 | 5 | 653.9438 | 653.9438 | 5.07e-06 | 5.07e-06 | 10 | 52401.45 | 0.000189
GAP9A | THE GAP | Urban | 1229 | 5.156 | 1.312 | 2.834 | 1.6088 | 0.21245 | 11 | 123919.7 | 123919.7 | 0.002539 | 0.002539 | 6 | 16364.51 | 6e-05
GBG1B | GEEBUNG | Urban | 100 | 0.91 | 3.209 | 4.23 | 0.66221 | 0.053764 | 1 | 15150 | 15150 | 0.000102 | 0.000102 | 1 | 1230 | 3.04e-06
GBG23A | GEEBUNG | Urban | 140.5 | 1.32 | 1.835 | 2.439 | 0.007333 |  | 1 | 68.34 | 68.34 | 3.46e-05 | 3.46e-05
GBG24A | VIRGINIA | Urban | 7 | 0 | 0.373 | 3.906
GBG25 | GEEBUNG, VIRGINIA | Urban | 164 | 1.512 | 1.34 | 4.668 | 0.053752 | 0.13314 | 1 | 482.79 | 482.79 | 6.36e-06 | 6.36e-06 | 3 | 1195.8 | 2.99e-06
GBG26 | BANYO, NORTHGATE, VIRGINIA | Urban | 928 | 4.251 | 2.532 | 4.058 | 0.058366 | 1.4119 | 7 | 1412.517 | 1412.517 | 1.76e-05 | 1.76e-05 | 7 | 34169.06 | 0.000109
GBG27 | BOONDALL, GEEBUNG, VIRGINIA | Urban | 1286 | 3.833 | 5.673 | 4.058 | 0.22675 | 0.38439 | 3 | 9525.44 | 9525.44 | 2.25e-05 | 2.25e-05 | 9 | 16147.46 | 6.53e-05
GBG28 | VIRGINIA | Urban | 35 | 1.084 | 0.851 | 2.877
GBG2A | BANYO, NUDGEE, VIRGINIA | Urban | 954.5 | 7.153 | 2.401 | 2.877 | 0.025788 | 0.089354 | 5 | 1354.21 | 1354.21 | 7.44e-06 | 7.44e-06 | 2 | 4692.3 | 2.24e-05
GBG32A | GEEBUNG, VIRGINIA | Urban | 63.5 | 0.534 | 2.41
GBG33A | BOONDALL, GEEBUNG, ZILLMERE | Urban | 1077 | 3.822 | 3.749 |  | 0.004143 | 0.37251 | 1 | 130.05 | 130.05 | 1.01e-06 | 1.01e-06 | 2 | 11692 | 4.46e-05
GBG34A | GEEBUNG | Urban | 62 | 0.37 | 2.082
GBG4A | VIRGINIA | Urban | 92 | 0.286 | 1.373 | 2.42
GBG6A | VIRGINIA | Urban | 74 | 0.653 | 1.558 | 2.191 | 0.012582 |  | 1 | 94.6 | 94.6 | 1.12e-06 | 1.12e-06
GBN2 | CANINA, GOOMBOORIAN, GREENS CREEK, NORTH DEEP CREE | Rural short | 257 | 46.439 | 0 | 0.419
GBN3 | ANDERLEIGH, DOWNSFIELD, NEERDIE, ROSS CREEK, SANDY | Rural short | 125 | 37.245 | 0.033 | 0.21
GBN4 | COONDOO, DOWNSFIELD, GOOMBOORIAN, GYMPIE, KIA ORA, | Rural short | 726 | 142.791 | 0 | 1.353
GBP4 | COORPAROO | Urban | 24.5 | 0 | 0.35 |  |  | 0.75814 | [5 empty] | 1 | 3800 | 1.93e-05
GBP5 | COORPAROO, GREENSLOPES | Urban | 387.2 | 1.392 | 1.4 |  | 3.8278 | 0.37744 | 5 | 99758.53 | 99758.53 | 0.000789 | 0.000789 | 1 | 9836.8 | 3.76e-05
GBP6 | EAST BRISBANE, WOOLLOONGABBA | Urban | 796 | 2.486 | 1.109 |  | 0.006611 | 0.11726 | 6 | 465.1987 | 388.4987 | 6.08e-06 | 5.07e-06 | 5 | 8250.73 | 3.62e-05
GCL2 | COOPERS PLAINS | Urban | 3
GCL3 | COOPERS PLAINS | Urban | 5 | 0 | 0.458
GCLSBK5 | COOPERS PLAINS, ROBERTSON | Rural short | 412.8 | 2.412 | 0.334 | 0.724
GCLSBY10 | SALISBURY | Urban | 386 | 3.965 | 0.356 | 5.259
GGR1 | COLLEGE VIEW, CROWLEY VALE, FOREST HILL, GLENORE G | Rural short | 831 | 75.798 | 0.013 | 2.286
GGR2 | GLENORE GROVE, LAKE CLARENDON, MORTON VALE | Rural short | 125 | 20.972 | 0 | 0.915
GGR3 | GLENORE GROVE, KENTVILLE, LOCKROSE, REGENCY DOWNS | Rural short | 78 | 18.659 | 0.026 | 0.743
GGR4 | GLENORE GROVE, HATTON VALE, PLAINLAND, REGENCY DOW | Rural short | 584 | 27.188 | 0.985 | 2.744
GGR5 | GLENORE GROVE, GRANDCHESTER, HATTON VALE, REGENCY | Rural short | 998 | 66.946 | 2.222 | 2.591
GISVSP3 | MURARRIE | Urban | 8 | 2.134 | 1.431 | 2.858
GLY11A | KEPERRA, UPPER KEDRON | Urban | 1471.5 | 4.925 | 7.154 | 4.554 | 0.1242 | 0.49164 | 4 | 6034.988 | 6034.988 | 4.06e-05 | 4.06e-05 | 7 | 23888.6 | 8.06e-05
GLY12A | FERNY GROVE, KEPERRA | Urban | 1137 | 2.304 | 6.525 | 3.525 | 0.15822 | 0.005752 | 8 | 8015.143 | 8015.143 | 7.2e-05 | 7.2e-05 | 1 | 291.4 | 1.26e-06
GLY15A | KEPERRA, MITCHELTON | Urban | 484.5 | 2.511 | 0.186 | 0.876 | 0.00395 | 0.34417 | 3 | 298.0833 | 298.0833 | 3.04e-06 | 3.04e-06 | 2 | 25975.85 | 7.94e-05
GLY2A | FERNY GROVE, KEPERRA, UPPER KEDRON | Urban | 920 | 4.13 | 4.448 | 2.782 | 0.37089 |  | 4 | 21685 | 21685 | 0.001063 | 0.001063
GLY3A | KEPERRA, MITCHELTON | Urban | 2046.5 | 6.859 | 3.134 | 4.115 | 2.4884 | 0.18387 | 13 | 189319.4 | 189319.4 | 0.004168 | 0.004168 | 11 | 13988.92 | 7.48e-05
GLY4A | KEPERRA | Rural short | 816 | 3.658 | 1.337 | 1.334
GNA12A | COLLINGWOOD PARK, REDBANK PLAINS | Rural short | 726 | 6.504 | 1.342 | 1.886
GNA13A | GOODNA | Urban | 631 | 3.012 | 1.87 | 1.753 | 0.073936 | 0.18477 | 3 | 3929.753 | 3929.753 | 9.77e-05 | 9.77e-05 | 5 | 9820.66 | 3.82e-05
GNA15A | BELLBIRD PARK, GOODNA, REDBANK, REDBANK PLAINS | Urban | 424 | 1.379 | 1.626 | 0.819 | 0.000763 | 0.002044 | 1 | 63.05 | 63.05 | 1.01e-06 | 1.01e-06 | 1 | 168.84 | 4.08e-06
GNA4A | COLLINGWOOD PARK, REDBANK | Urban | 860 | 5.419 | 1.056 | 1.982 | 0.026214 | 0.029383 | 8 | 2304.415 | 2250.565 | 5.07e-05 | 4.97e-05 | 2 | 2583 | 1.12e-05
GNA5A | GOODNA | Urban | 1288.5 | 7.087 | 2.863 | 2.401 | 0.006585 | 0.26839 | 6 | 526.8167 | 460.5333 | 6.08e-06 | 5.07e-06 | 3 | 21471 | 7.02e-05
GNA7A | BELLBIRD PARK, GOODNA, REDBANK PLAINS | Urban | 1888 | 11.154 | 4.006 | 4.611 | 0.33556 | 0.43905 | 17 | 27765.26 | 27690.41 | 0.000254 | 0.000253 | 5 | 36327.7 | 0.000113
GPS3 | BRISBANE | Urban | 3 | 0 | 0.149
GTN12A | GATTON, GRANTHAM, LOWER TENTHILL, PLACID HILLS, RI | Rural short | 549.5 | 39.752 | 3.788 | 3.239
GTN13A | ADARE, GATTON, RINGWOOD, VINEGAR HILL | Rural short | 732 | 37.021 | 1.623 | 1.943
GTN15A | ADARE, GATTON | Rural short | 1031 | 22.893 | 1.636 | 4.744
GTN1B | GATTON, WOODLANDS | Rural short | 308 | 12.08 | 2.741 | 1.848
GTN3A | GATTON | Urban | 1163 | 6.336 | 0.379 | 3.734 | 0.067032 | 1.8961 | 7 | 2744.3 | 2744.3 | 2.15e-05 | 2.15e-05 | 29 | 77628.26 | 0.000269
GTN5B | ADARE, CLARENDON, COLLEGE VIEW, GATTON, LAKE CLARE | Rural short | 115 | 28.542 | 0.647 | 5.049
GUV2 | NATHAN | Urban | 3
GUV4 | NATHAN | Urban | 4
GUV5 | NATHAN | Urban | 5 | 0 | 0.466
GUV7 | NATHAN | Urban | 2 | 0 | 0.237
GVN12A | ARUNDEL, GAVEN, PARKWOOD | Urban | 1176.5 | 1.392 | 7.247 | 3.982 | 1.4807 | 0.008446 | 3 | 62589.88 | 62589.88 | 0.00119 | 0.00119 | 1 | 357 | 1.01e-06
GVN13A | PACIFIC PINES | Urban | 1826 | 0.837 | 12.689 | 5.449 | 0.015767 | 0.009342 | 4 | 863.3 | 863.3 | 3.14e-05 | 3.14e-05 | 1 | 511.5 | 3.35e-06
GVN15A | HELENSVALE | Urban | 134 | 1.072 | 2.934 | 2.382 |  | 0.043891 | [5 empty] | 1 | 378 | 2.03e-06
GVN16A | GAVEN, NERANG, SOUTHPORT | Rural short | 1062 | 12.986 | 1.004 | 3.449
GVN2A | GAVEN | Urban | 5 | 4.136 | 0.154 | 1.562 |  | 0.000448 | [5 empty] | 1 | 211 | 1.01e-06
GVN3A | GAVEN, MOLENDINAR, PARKWOOD | Urban | 889 | 2.106 | 4.303 | 1.829 | 0.001299 |  | 1 | 97.05 | 97.05 | 1.01e-06 | 1.01e-06
GVN5A | ARUNDEL, GAVEN, HELENSVALE, PACIFIC PINES | Rural short | 286 | 2.999 | 2.936 | 1.753
GVN6B | OXENFORD, PACIFIC PINES | Urban | 1364 | 3.278 | 10.189 | 3.925 | 0.002041 | 0.01155 | 2 | 126.5167 | 126.5167 | 2.03e-06 | 2.03e-06 | 2 | 716 | 1.12e-05
GYGGYS6 | ALBERTON, GLANMIRE, GYMPIE, JONES HILL, KYBONG, MO | Rural short | 611 | 96.362 | 0.137 | 3.201
GYM2A | CALICO CREEK, DAGUN, GILLDORA, GYMPIE, JONES HILL, | Rural short | 1349 | 67.682 | 4.271 | 3.258
GYM2B | GYMPIE | Urban | 373.7 | 3.491 | 0.953 | 5.392 | 3.2852 | 0.16934 | 2 | 41902.68 | 41902.68 | 0.000611 | 0.000611 | 1 | 2160 | 6.08e-06
GYM3 | GYMPIE, SOUTHSIDE | Urban | 909.5 | 11.46 | 1.328 | 3.639 | 2.8732 | 1.4425 | 11 | 105540.3 | 105540.3 | 0.00103 | 0.00103 | 8 | 52987.5 | 0.000301
GYM4 | GYMPIE | Rural short | 779 | 6.126 | 0.35 | 1.581
GYM5B | GYMPIE | Rural short | 413 | 3.531 | 0 | 1.143
GYM6 | GYMPIE | Urban | 516.5 | 4.015 | 0.137 | 1.429 | 0.008756 | 0.022702 | 4 | 286.8833 | 286.8833 | 4.06e-06 | 4.06e-06 | 1 | 743.85 | 5.2e-06
GYM7A | ARALUEN, CANINA, CEDAR POCKET, EAST DEEP CREEK, GO | Rural short | 1395 | 55.499 | 0.155 | 2.7
GYM8A | GYMPIE, KYBONG, MONKLAND, PIE CREEK, SOUTHSIDE | Rural short | 1137 | 20.621 | 1.26 | 2.686
GYM8B | GYMPIE | Urban | 440.8 | 2.982 | 1.022 | 2.591 | 0.54518 | 0.31647 | 5 | 28223.4 | 28223.4 | 0.000642 | 0.000642 | 2 | 16383.51 | 0.000101
GYM9A | GYMPIE, MONKLAND | Rural short | 182 | 5.313 | 1.196 | 1.01
GYM9B | CANINA, CEDAR POCKET, EAST DEEP CREEK, GREENS CREE | Rural short | 167 | 30.413 | 0.306 | 1.391
GYN1B | GYMPIE | Urban | 7 | 0.834 | 0.706 | 3.313 |  | 0.12894 | [5 empty] | 1 | 30.08 | 1.62e-07
GYN2B | GYMPIE | Urban | 388 | 3.752 | 0.063 | 2.134 | 0.88485 | 0.3642 | 12 | 23218.46 | 22963 | 0.000465 | 0.000464 | 7 | 9556.553 | 4.46e-05
GYN3A | FISHERMANS POCKET, GLASTONBURY, GYMPIE, LANGSHAW, | Rural short | 1348.5 | 113.689 | 1.666 | 2.877
GYN5A | ARALUEN, GYMPIE, TWO MILE | Urban | 1010 | 7.171 | 4.055 | 4.287 | 0.09838 | 0.28245 | 5 | 3257.433 | 3257.433 | 3.35e-05 | 3.35e-05 | 5 | 9352 | 4.8e-05
GYN6A | ARALUEN, BELLS BRIDGE, CHATSWORTH, FISHERMANS POCK | Rural short | 848 | 59.838 | 0.626 | 1.982
GYN7A | ARALUEN, BANKS POCKET, CHATSWORTH, CORELLA, GYMPIE | Rural short | 1271 | 66.232 | 3.498 | 2.968
GYS2A | EAST DEEP CREEK, MONKLAND | Urban | 26 | 2.373 | 0.141 | 3.62
GYS3A | CEDAR POCKET, EAST DEEP CREEK, GREENS CREEK, MOTHA | Rural short | 386 | 66.008 | 0.163 | 1.029
GYS5A | CEDAR POCKET, GLANMIRE, MONKLAND, MOTHAR MOUNTAIN, | Rural short | 262 | 44.017 | 0.198 | 0.724
HDA10A | CLAYFIELD, HENDRA, NUNDAH | Urban | 1795.5 | 3.416 | 1.562 | 2.725 | 2.0378 | 0.23941 | 15 | 176595.9 | 176595.9 | 0.003788 | 0.003788 | 8 | 20746.94 | 8.01e-05
HDA11A | CLAYFIELD | Urban | 1798.5 | 3.266 | 1.698 | 3.087 | 0.14242 | 0.27403 | 6 | 11389.72 | 400.7167 | 6.53e-05 | 5.07e-06 | 7 | 21915.5 | 7.48e-05
HDA13A | ASCOT, HENDRA | Urban | 951 | 4.151 | 0.199 | 2.363 | 1.4538 | 0.02389 | 8 | 94635.37 | 94365.03 | 0.000962 | 0.00096 | 1 | 1555.2 | 7.3e-06
HDA14A | BANYO, HENDRA, NORTHGATE | Urban | 148 | 0.981 | 3.662 | 3.468 | 1.1257 |  | 1 | 10220 | 10220 | 0.00013 | 0.00013
HDA3A | ASCOT, CLAYFIELD, HENDRA | Urban | 655 | 2.824 | 0.248 | 2.42 | 1.5301 | 0.6026 | 5 | 55506.65 | 55506.65 | 0.001396 | 0.001396 | 12 | 21860.33 | 9.94e-05
HDA3B | ASCOT | Rural short | 160 | 1.325 | 1.736 | 0.591
HDA4A | HENDRA | Urban | 831 | 2.694 | 0.694 | 2.039 | 0.014749 | 0.050635 | 4 | 985.0833 | 985.0833 | 1.6e-05 | 1.6e-05 | 4 | 3381.86 | 2.27e-05
HDN1 | CARPENDALE, GRANTHAM, HELIDON, VERADILLA | Rural short | 423.5 | 46.074 | 2.198 | 1.734
HDN2 | HELIDON, HELIDON SPA, POSTMANS RIDGE | Rural short | 213 | 22.273 | 0.828 | 1.829
HDN3 | HELIDON | Rural short | 57 | 8.875 | 0.366
HDN4 | HELIDON, HELIDON SPA, IREDALE | Rural short | 238 | 9.647 | 0.28
HHC10 | HERSTON | Urban | 2 | 0 | 0.131 |  | 0.003101 |  | 1 | 8 |  | 2.03e-06
HHC21 | HERSTON | Urban | 3 | 0 | 0.39 |  |  |  | 1 | 12 |  | 3.04e-06
HHC23 | HERSTON | Urban | 5 | 0 | 0.775 |  |  |  | 1 | 28 |  | 7.1e-06
HHC7 | HERSTON | Urban | 5 | 0 | 0.857 |  |  |  | 1 | 20 |  | 5.07e-06
HHC9 | HERSTON | Urban | 4 | 0 | 1.192 |  |  |  | 1 | 16 |  | 4.06e-06
HIS12A | HELENSVALE, HOPE ISLAND | Urban | 845 | 1.79 | 5.352 | 2.82 |  | 0.16004 | [5 empty] | 2 | 8763.68 | 2.55e-05
HIS12B | HELENSVALE, HOPE ISLAND, OXENFORD | Urban | 967 | 0.631 | 10.627 | 3.773 | 0.28855 |  | 5 | 13542.8 | 13542.8 | 8.22e-05 | 8.22e-05
HIS13A | HOPE ISLAND | Urban | 617 | 0.556 | 7.699 | 3.201
HIS15B | HOPE ISLAND | Rural short | 9 | 0 | 0.837 | 0.096
HIS1B | HELENSVALE, HOPE ISLAND | Urban | 1112 | 0 | 7.52 | 3.677 | 0.003137 | 0.014083 | 5 | 179.8601 | 179.8601 | 5.07e-06 | 5.07e-06 | 2 | 807.38 | 1.21e-05
HIS3A | HOPE ISLAND | Urban | 268 | 0.62 | 3.879 | 2.229
HIS5A | HOPE ISLAND, PARADISE POINT | Urban | 757 | 3.175 | 3.9 | 2.439 | 0.008299 |  | 4 | 430.2173 | 430.2173 | 4.06e-06 | 4.06e-06
HIS5B | HOPE ISLAND | Urban | 907 | 1.068 | 8.2 | 3.792 | 0.005499 |  | 3 | 238.3333 | 238.3333 | 3.04e-06 | 3.04e-06
HISSCV16 | HOPE ISLAND | Urban | 257 | 0 | 3.775 | 4.325 | 0.1295 | 0.003827 | 1 | 7144 | 7144 | 3.85e-05 | 3.85e-05 | 1 | 211.12 | 1.05e-06
HISSCV2 | HOPE ISLAND | Urban | 221 | 0.438 | 5.285 | 3.296
HLG1 | DUNWICH | Rural short | 17 | 11.41 | 0.103 | 1.905
HMT10A | HEMMANT | Urban | 306 | 2.106 | 1.225 | 1.753 | 0.032244 | 2.127 | 2 | 283.1 | 283.1 | 2.03e-06 | 2.03e-06 | 6 | 18674.27 | 6.41e-05
HMT2 | HEMMANT | Urban | 4 | 0.087 | 1.814 | 2.61
HMT3A | HEMMANT | Urban | 120 | 1.967 | 1.589 | 2.382 | 0.005821 | 0.66044 | 3 | 48.4 | 48.4 | 2.08e-06 | 2.08e-06 | 2 | 5491.02 | 1.42e-05
HMT9A | HEMMANT, TINGALPA | Rural short | 189 | 3.687 | 0.226 | 0.819
HMTPTR5 | HEMMANT, MURARRIE | Urban | 283 | 1.815 | 1.098 | 2.401 | 0.21729 | 0.090857 | 3 | 19738.55 | 19738.55 | 0.000412 | 0.000412 | 2 | 8253.44 | 6.41e-05
HPE12A | HOLLAND PARK, HOLLAND PARK WEST, MT GRAVATT, MT GR | Urban | 1476.5 | 4.601 | 0.7 | 3.068 | 0.046738 | 0.36933 | 7 | 2849.35 | 2849.35 | 1.22e-05 | 1.22e-05 | 8 | 22515.82 | 0.000101
HPE13A | CAMP HILL, COORPAROO, HOLLAND PARK | Urban | 1729 | 9.261 | 1.967 | 4.839 | 3.0541 | 1.2949 | 14 | 143219 | 143219 | 0.001847 | 0.001847 | 14 | 60725.51 | 0.000222
HPE16A | CARINA HEIGHTS, HOLLAND PARK, MANSFIELD, MT GRAVAT | Urban | 1134 | 3.114 | 3.896 | 3.125 | 0.17875 | 0.059809 | 20 | 9214.909 | 9088.876 | 0.000117 | 0.000115 | 2 | 3083.28 | 1.24e-05
HPE3A | MANSFIELD, MT GRAVATT EAST | Urban | 1919 | 7.089 | 1.777 | 4.23 | 5.5044 | 0.95511 | 8 | 331600.5 | 331600.5 | 0.003979 | 0.003979 | 12 | 57537.99 | 0.000229
HPE5A | HOLLAND PARK | Urban | 1252 | 5.524 | 0.757 | 2.282 | 0.020433 | 0.22095 | 9 | 1632.15 | 1632.15 | 1.87e-05 | 1.87e-05 | 6 | 17649.64 | 6.23e-05
HPK10 | GREENSLOPES | Urban | 1383 | 4.456 | 0.426 | 3.182 | 1.2225 | 0.03799 | 10 | 61310.78 | 61310.78 | 0.000464 | 0.000464 | 3 | 1905.2 | 5.09e-06
HPK11 | HOLLAND PARK | Rural short | 194 | 1.713 | 0.401 | 0.483
HPK2 | GREENSLOPES | Urban | 977.8 | 2.376 | 3.06 | 3.01 | 0.033388 | 0.1576 | 4 | 2014.833 | 1945.5 | 1.32e-05 | 1.22e-05 | 2 | 9510.437 | 2.59e-05
HPK3A | HOLLAND PARK WEST, TARRAGINDI | Urban | 1780 | 6.23 | 0.548 | 2.887 | 5.7489 | 0.11928 | 14 | 538510.5 | 538510.5 | 0.006342 | 0.006342 | 9 | 11173.3 | 5.28e-05
HPK5A | ANNERLEY, HOLLAND PARK WEST, TARRAGINDI | Urban | 1308.5 | 5.603 | 0.4 | 2.437
HPK6 | COORPAROO, HOLLAND PARK, HOLLAND PARK WEST | Urban | 732 | 3.093 | 0.413 | 2.648 | 0.52083 | 0.7106 | 4 | 27468.49 | 27468.49 | 0.000121 | 0.000121 | 10 | 37476.85 | 0.000131
HPK8A | HOLLAND PARK WEST, TARRAGINDI | Rural short | 675 | 5.099 | 0.843 | 1.443
HPK9 | HOLLAND PARK WEST | Urban | 552.5 | 1.721 | 0.85 | 1.334 | 0.14281 | 0.017102 | 4 | 8508.483 | 8508.483 | 0.000104 | 0.000104 | 2 | 1018.95 | 1.35e-05
HSH5 | SPRING HILL | Urban | 148 |  |  |  | 0.016473 |  | 1 | 630 |  | 0.00016
HSHWTC43 | SPRING HILL | Urban | 59 | 0 | 0.729 |  | 0.04607 |  | 1 | 224 |  | 5.68e-05
HTL10A | EAGLE FARM | Urban | 51 | 0.803 | 1.922 | 3.296
HTL11A | EAGLE FARM | Urban | 69 | 0.023 | 1.847 | 1.543 |  | 0.29294 | [5 empty] | 3 | 2802.96 | 1.03e-05
HTL12A | EAGLE FARM | Urban | 4 | 0 | 0.976 | 3.083
HTL14A | EAGLE FARM | Urban | 19 | 1.083 | 0.706 | 3.163
HTL2A | EAGLE FARM | Urban | 104 | 0 | 1.775 | 2.877 | 0.009286 | 2.5553 | 1 | 84.5833 | 84.5833 | 1.01e-06 | 1.01e-06 | 2 | 23276 | 7.91e-05
HTL3A | EAGLE FARM | Urban | 78.5 | 0.999 | 2.683 | 2.191 |  | 0.20244 | [5 empty] | 1 | 1735.65 | 4.05e-06
HTL6A | EAGLE FARM, HAMILTON | Urban | 282 | 1.858 | 3.432 | 3.01 | 0.004558 | 0.32227 | 1 | 127.683 | 127.683 | 1.01e-06 | 1.01e-06 | 1 | 9027 | 1.72e-05
HTN1A | ASCOT, EAGLE FARM, HAMILTON | Urban | 1355 | 3.471 | 1.861 | 2.629 | 0.46547 |  | 5 | 34895.62 | 34895.62 | 0.000344 | 0.000344
HTN22A | EAGLE FARM, HAMILTON | Urban | 346 | 2.404 | 3.191 | 2.229 | 0.010725 | 0.15118 | 3 | 274.0833 | 274.0833 | 3.04e-06 | 3.04e-06 | 1 | 3863.34 | 1.03e-05
HTN24A | ALBION, HAMILTON | Urban | 837 | 2.633 | 2.058 | 2.744 | 0.11453 | 0.071677 | 5 | 5550.199 | 5550.199 | 0.000663 | 0.000663 | 2 | 3473.4 | 1.92e-05
HTN27A | ALBION, HAMILTON, NEWSTEAD | Urban | 422.5 | 0.925 | 1.899 | 4.458 | 0.36983 | 0.20826 | 2 | 5412.55 | 5412.55 | 5.12e-05 | 5.12e-05 | 3 | 3047.9 | 1.03e-05
HTN28A | ASCOT | Urban | 1164 | 2.874 | 1.043 | 3.029 | 1.5962 | 0.1501 | 7 | 87506.9 | 87506.9 | 0.001093 | 0.001093 | 2 | 8228.75 | 2e-05
HTN2A | ASCOT, HAMILTON | Urban | 654.5 | 2.143 | 0.549 | 2.305 | 0.038275 | 0.13423 | 6 | 1991.867 | 1991.867 | 1.65e-05 | 1.65e-05 | 3 | 6985.35 | 9.02e-05
HTN3A | ASCOT | Urban | 398 | 2.277 | 1.413 | 1.581 | 0.00884 |  | 3 | 379.9992 | 379.9992 | 3.04e-06 | 3.04e-06
HTN7B | HAMILTON | Urban | 107 | 0 | 1.229 | 2.706
HWD12A | HEATHWOOD | Urban | 14 | 0 | 0.735 | 1.715
HWD12B | FOREST LAKE, HEATHWOOD | Urban | 27 | 0 | 2.817 | 1.581 | 0.31237 |  | 1 | 525 | 525 | 5.07e-06 | 5.07e-06
HWD13A | FOREST LAKE, HEATHWOOD | Urban | 529 | 0.098 | 8 | 4.954 | 3.0584 |  | 1 | 44321 | 44321 | 0.000531 | 0.000531
HWD1B | HEATHWOOD | Urban | 10 | 0 | 0.517 | 2.134
HWD2B | FORESTDALE, HEATHWOOD, LARAPINTA | Rural short | 266 | 7.136 | 5.244 | 1.467
HWD5A | DOOLANDELLA, FOREST LAKE, HEATHWOOD, PALLARA | Rural short | 1915 | 8.184 | 8.909 | 4.687
HWD5B | FOREST LAKE | Urban | 1592 | 0 | 9.444 | 4.763 | 10.1446 |  | 7 | 726949.9 | 776.91 | 0.001625 | 1.36e-05
HWL10A | COOMBABAH, PARADISE POINT, RUNAWAY BAY | Urban | 1668.5 | 4.154 | 7.485 | 3.772 | 0.013252 | 0.02104 | 7 | 1015.566 | 1015.566 | 5.17e-05 | 5.17e-05 | 1 | 1612.328 | 6.26e-06
HWL11A | RUNAWAY BAY | Urban | 1242 | 3.573 | 3.842 | 2.82 | 0.65287 | 0.67463 | 8 | 47205.2 | 47205.2 | 0.001333 | 0.001333 | 4 | 48778.96 | 0.000171
HWL12A | RUNAWAY BAY | Urban | 3 | 0 | 2.2 | 1.829
HWL13A | PARADISE POINT | Urban | 938 | 1.079 | 12.248 | 4.287 | 0.38255 | 0.054643 | 2 | 14602.37 | 14602.37 | 6.29e-05 | 6.29e-05 | 2 | 2085.77 | 4.15e-05
HWL1A | HOLLYWELL, PARADISE POINT, RUNAWAY BAY | Urban | 1367.5 | 3.974 | 5.566 | 4.363 | 0.010673 | 0.04155 | 7 | 665.4167 | 665.4167 | 7.1e-06 | 7.1e-06 | 1 | 2590.56 | 1.02e-05
HWL2A | BIGGERA WATERS, RUNAWAY BAY | Urban | 991 | 5.014 | 6.784 | 3.506 | 0.007732 | 0.017043 | 4 | 455.35 | 455.35 | 4.06e-06 | 4.06e-06 | 4 | 1003.74 | 3.84e-05
HWL3A | COOMBABAH | Urban | 1953 | 3.771 | 2.658 | 4.535 | 0.031851 | 0.12664 | 5 | 2392.667 | 2392.667 | 6.16e-05 | 6.16e-05 | 4 | 9513.525 | 4.03e-05
HWL4A | RUNAWAY BAY | Urban | 390 | 0.032 | 4.961 | 2.915 | 0.11972 |  | 2 | 2427.21 | 2427.21 | 2.33e-05 | 2.33e-05
HWL6A | BIGGERA WATERS, COOMBABAH, RUNAWAY BAY | Urban | 1635.5 | 2.397 | 3.973 | 3.677 | 0.003339 | 0.10516 | 1 | 160.85 | 160.85 | 1.01e-06 | 1.01e-06 | 2 | 5065.62 | 3.85e-05
HWL8A | HOLLYWELL, RUNAWAY BAY | Urban | 1259 | 2.759 | 3.377 | 3.428 | 0.14299 | 0.48862 | 4 | 8000.747 | 8000.747 | 4.72e-05 | 4.72e-05 | 4 | 27340.2 | 8.67e-05
IBL2 | BELLA CREEK, BOLLIER, BORUMBA DAM, BROOLOO, GHEERU | Rural short | 702 | 86.791 | 0.049 | 1.41
IBS1 | RUSSELL ISLAND | Urban | 250 | 6.691 | 1.25 | 3.696
IDY10A | CHAPEL HILL, INDOOROOPILLY | Urban | 1109 | 4.582 | 2.858 | 3.315 | 1.4052 | 0.5577 | 8 | 61274.63 | 61274.63 | 0.000444 | 0.000444 | 5 | 24318.56 | 8.1e-05
IDY14A | INDOOROOPILLY, TARINGA | Urban | 346 | 0.4 | 1.003 | 2.782 |  | 0.23525 | [5 empty] | 1 | 5953.5 | 1.92e-05
IDY1A | CHAPEL HILL, INDOOROOPILLY | Urban | 1120 | 4.757 | 1.513 | 2.82 | 0.12753 | 1.2946 | 8 | 7968.713 | 7968.713 | 7.75e-05 | 7.75e-05 | 16 | 80888.74 | 0.00026
IDY5A | INDOOROOPILLY | Urban | 577 | 2.065 | 0.348 | 2.477 | 0.20795 | 1.0693 | 7 | 6473.007 | 6473.007 | 0.000313 | 0.000313 | 8 | 33283.13 | 0.000134
IDY6A | INDOOROOPILLY, TARINGA, TOOWONG | Urban | 1092 | 2.873 | 0.592 | 1.934 | 0.37504 |  | 8 | 30510.63 | 25248.45 | 0.000255 | 0.00021
IDY9B | INDOOROOPILLY | Urban | 901 | 2.479 | 1.812 | 3.506 | 0.18365 | 0.16145 | 5 | 9571.433 | 9571.433 | 0.000152 | 0.000152 | 5 | 8414.47 | 3.81e-05
INA10A | FOREST LAKE, INALA, RICHLANDS | Rural short | 985 | 2.944 | 3.755 | 1.81
INA11A | FOREST LAKE, INALA | Urban | 1410 | 3.384 | 3.359 | 2.363 | 0.44434 | 0.34871 | 7 | 41508.21 | 41508.21 | 0.001686 | 0.001686 | 6 | 32575.56 | 9.25e-05
INA1A | DOOLANDELLA, INALA | Urban | 1195.5 | 4.91 | 2.162 | 3.182 | 0.21848 | 1.0152 | 8 | 12921.17 | 12921.17 | 0.000194 | 0.000194 | 6 | 60041.15 | 0.00014
INA2A | DURACK, INALA | Urban | 1802 | 4.297 | 6.331 | 3.658 | 0.54866 | 1.0279 | 16 | 32172.66 | 32172.66 | 0.000153 | 0.000153 | 14 | 60273.75 | 0.000231
INA3A | DOOLANDELLA, FOREST LAKE, INALA | Urban | 2034 | 2.236 | 7.676 | 4.287 | 0.35975 | 0.58473 | 6 | 27911.87 | 23827.87 | 0.00225 | 0.00018 | 6 | 45367.13 | 0.000124
INA5A | INALA, RICHLANDS | Urban | 782 | 2.435 | 3.338 | 3.62 | 0.12886 | 0.81476 | 9 | 3578.68 | 3578.68 | 0.000233 | 0.000233 | 7 | 22627.94 | 9.8e-05
INA7A | INALA, OXLEY, RICHLANDS | Rural short | 1190 | 7.515 | 1.929 | 2.374
INA9A | DURACK, INALA | Urban | 1365.5 | 5.186 | 4.376 | 4.135 | 0.013597 | 0.88759 | 6 | 757.1 | 757.1 | 6.08e-06 | 6.08e-06 | 10 | 49421.52 | 0.000159
IPL1 | BARNEY VIEW, INNISPLAIN, MAROON, MT LINDESAY, OAKY | Rural short | 520 | 157.18 | 0.074 | 1.658
IPL2A | CHRISTMAS CREEK, INNISPLAIN, JOSEPHVILLE, KNAPP CR | Rural short | 299 | 94.367 | 0.032 | 1.6
IPL3 | CANUNGRA, CHINGHEE CREEK, CHRISTMAS CREEK, DARLING | Rural short | 459 | 125.564 | 0.495 | 1.467
IPL4A | CHINGHEE CREEK, INNISPLAIN, MOUNT GIPPS, OAKY CREE | Rural short | 153 | 49.868 | 0.136 | 0.533
IPS12B | CHURCHILL, FLINDERS VIEW, RACEVIEW, YAMANTO | Urban | 198 | 2.406 | 0.831 | 3.106 | 0.22661 | 0.022544 | 7 | 7826.783 | 7826.783 | 0.000217 | 0.000217 | 1 | 778.65 | 9.07e-06
IPS15B | AMBERLEY, CHURCHILL, ONE MILE, YAMANTO | Urban | 1140 | 11.079 | 1.912 | 4.763 | 0.12823 | 0.93726 | 11 | 8610.789 | 8610.789 | 8.92e-05 | 8.92e-05 | 3 | 62940 | 0.000133
IPS16A | FLINDERS VIEW | Urban | 1214 | 1.134 | 6.031 | 4.516 | 0.00603 | 0.11493 | 6 | 466.6748 | 466.6748 | 6.08e-06 | 6.08e-06 | 3 | 8894.58 | 3.24e-05
IPS1B | AMBERLEY, CHURCHILL, LEICHHARDT, ONE MILE, RACEVIE | Urban | 1597 | 10.73 | 1.022 | 3.715 | 0.25775 | 0.38732 | 11 | 18587.24 | 10672.24 | 0.001701 | 9.63e-05 | 5 | 27931.28 | 0.000108
IPS2B | FLINDERS VIEW, RACEVIEW, RIPLEY, YAMANTO | Rural short | 1257 | 15.266 | 3.916 | 3.601
IPS5B | EASTERN HEIGHTS, IPSWICH, RACEVIEW | Urban | 1968 | 8.868 | 2.661 | 4.706 | 5.8638 |  | 17 | 383712.7 | 373920.2 | 0.003992 | 0.002006
JBB12B | JIMBOOMBA, NORTH MACLEAN, SOUTH MACLEAN, STOCKLEIG | Rural short | 680 | 27.782 | 5.781 | 2.534
JBB13A | JIMBOOMBA, MUNDOOLUN, TAMBORINE | Rural short | 1127 | 43.373 | 1.76 | 3.334
JBB16A | JIMBOOMBA, LOGAN VILLAGE, STOCKLEIGH, TAMBORINE, Y | Rural short | 1047 | 35.206 | 3.613 | 2.248
JBB1B | CEDAR GROVE, CEDAR VALE, JIMBOOMBA, MUNDOOLUN, VER | Rural short | 1575 | 47.387 | 4.555 | 4.687
JBB2A | CHAMBERS FLAT, JIMBOOMBA, LOGAN VILLAGE, MUNRUBEN, | Rural short | 753 | 41.447 | 0.429 | 2.363
JBB3A | ALLENVIEW, CEDAR GROVE, JIMBOOMBA, KAGARU, UNDULLA | Rural short | 959 | 63.772 | 4.423 | 2.858
JBB4A | JIMBOOMBA | Urban | 467 | 9.555 | 1.45 | 3.353 | 1.1573 | 0.051106 | 5 | 23143.03 | 23143.03 | 0.000482 | 0.000482 | 1 | 1022 | 7.1e-06
JDL3 | JAMBOREE HEIGHTS, MT OMMANEY | Urban | 198 | 0 | 3.76 | 1.81
JDL4A | JINDALEE, MT OMMANEY | Urban | 763 | 3.421 | 2.63 | 2.191 | 0.067113 | 0.35643 | 4 | 3183.863 | 3183.863 | 2.14e-05 | 2.14e-05 | 3 | 16909 | 6.91e-05
JDL5 | JINDALEE | Urban | 570 | 3.123 | 0.192 | 3.582 | 0.036958 | 0.22936 | 5 | 1875.689 | 1875.689 | 5.07e-06 | 5.07e-06 | 6 | 11640.53 | 4.39e-05
JDL6 | JINDALEE, KENMORE | Urban | 311 | 1.689 | 1.069 | 0.781 | 0.005912 | 0.036923 | 2 | 411.9333 | 411.9333 | 4.12e-05 | 4.12e-05 | 1 | 2572.8 | 1.63e-05
JDL7 | JINDALEE, MT OMMANEY, WESTLAKE | Urban | 938 | 0 | 6.034 | 2.667 | 2.332 | 0.19964 | 10 | 137378.4 | 137378.4 | 0.00285 | 0.00285 | 3 | 11760.76 | 4.69e-05
JDL8A | JINDALEE, OXLEY, SEVENTEEN MILE ROCKS, SINNAMON PA | Urban | 421 | 1.045 | 4.707 | 4.249
JHDMDH11 | PINKENBA | Urban | 32 | 1.368 | 0.674 | 2.077 | 0.56529 |  | 1 | 404 | 404 | 4.06e-06 | 4.06e-06
JHDMDH7 | PINKENBA | Urban | 7 | 1.356 | 1.377 | 2.686
KBN13A | BRASSALL, KARRABIN, WULKURAKA | Rural short | 878 | 10.948 | 1.275 | 2.686
KBN15A | KARRABIN, LEICHHARDT, WULKURAKA | Urban | 95 | 7.052 | 1.101 | 5.259 | 14.2032 | 4.594 | 5 | 22309.57 | 22211.38 | 9.73e-05 | 9.63e-05 | 6 | 7216 | 3.55e-05
KBN1B | BLACKSOIL, BRASSALL, KARRABIN, MUIRLEA | Rural short | 1518 | 11.641 | 7.929 | 4.554
KBN2A | KARRABIN, ROSEWOOD, THAGOONA, WALLOON | Rural short | 741 | 23.613 | 1.308 | 2.725
KBN3A | KARRABIN | Urban | 3 | 0.423 | 0.263 | 4.23
KBN5A | BLACKSOIL, BORALLON, FAIRNEY VIEW, HAIGSLEA, IRONB | Rural short | 1008 | 102.999 | 2.887 | 2.591
KBR1A | ARATULA, CHARLWOOD, CLUMBER, FASSIFERN VALLEY, FRA | Rural short | 582 | 113.633 | 0.892 | 1.734
KBR2A | ARATULA, BOONAH, CHARLWOOD, FRAZERVIEW, KALBAR, MO | Rural short | 402.5 | 73.244 | 0.102 | 1.715
KBR3A | ARATULA, FASSIFERN, FRAZERVIEW, KALBAR, ROSEVALE, | Rural short | 367.5 | 50.99 | 0.634 | 1.448
KBR5A | COULSON, HOYA, KALBAR, KULGUN, ROADVALE, TEVIOTVIL | Rural short | 225 | 50.07 | 0.17 | 0.479
KBR6A | ANTHONY, BLANTYRE, KALBAR, KENTS LAGOON, MILORA, M | Rural short | 368.7 | 78.252 | 0.146 | 1.296
KCY1 | KILCOY, WINYA | Urban | 620 | 7.178 | 0.042 | 1.982 | 1.7929 | 0.041148 | 10 | 87106.3 | 63744.1 | 0.004388 | 0.003753 | 1 | 1999.2 | 7.95e-06
KCY2 | JIMNA, KILCOY, MOUNT KILCOY, SANDY CREEK, SHEEP ST | Rural short | 381.3 | 110.821 | 0 | 1.029
KCY3 | KILCOY, WINYA | Urban | 6.6 | 1.066 | 0.047 | 4.287 | 0.067357 |  | 7 | 819.25 | 615.85 | 4.01e-05 | 3.44e-05
KCY4 | KILCOY, MOUNT ARCHER, MT DELANEY, NEURUM, ROYSTON, | Rural short | 732.1 | 114.953 | 2.23 | 1.562
KCY5 | GREGORS CREEK, HARLIN, HAZELDEAN, KILCOY, WINYA, W | Rural short | 546 | 53.94 | 1.246 | 1.581
KKMPRL1 | BRISBANE | CBD | 75 | 0 | 0.572
KLG10A | GRIFFIN, MURRUMBA DOWNS | Urban | 1968 | 3.7 | 9.366 | 5.144 | 0.70386 | 0.74861 | 6 | 52304.53 | 52304.53 | 0.001984 | 0.001984 | 5 | 55629.95 | 0.000502
KLG11A | KALLANGUR | Urban | 1747.5 | 8.161 | 0.918 | 5.506 | 2.5397 | 0.10288 | 9 | 208439.4 | 208439.4 | 0.001841 | 0.001841 | 5 | 8443.24 | 5.1e-05
KLG13A | KALLANGUR, PETRIE | Urban | 1513 | 8.371 | 1.809 | 4.401 | 0.49595 | 1.1097 | 21 | 35004.23 | 35004.23 | 0.000378 | 0.000378 | 13 | 78324.2 | 0.000297
KLG14A | KALLANGUR, MURRUMBA DOWNS, PETRIE | Urban | 941.5 | 6.405 | 5.399 | 4.649 | 0.062809 | 0.14347 | 2 | 3865.167 | 3865.167 | 1.12e-05 | 1.12e-05 | 7 | 8829.08 | 2.79e-05
KLG16A | KALLANGUR | Rural short | 2115.5 | 6.94 | 3.805 | 2.344
KLG17A | KALLANGUR, MURRUMBA DOWNS | Urban | 568 | 1.7 | 0.957 | 3.753 | 0.53882 | 0.82625 | 13 | 17756.88 | 17756.88 | 0.000182 | 0.000182 | 7 | 27229.18 | 0.000106
KLG4A | KALLANGUR, PETRIE | Rural short | 870 | 6.694 | 0.208 | 1.715
KLG5A | KALLANGUR, KURWONGBAH, PETRIE | Rural short | 1250 | 12.493 | 2.503 | 3.277
KLG7A | GRIFFIN, KALLANGUR, MURRUMBA DOWNS | Urban | 1786.5 | 6.229 | 5.146 | 5.887
KMM10A | MAROOCHYDORE | Urban | 2
KMM2A | MAROOCHYDORE | Urban | 3
KMM3A | MAROOCHYDORE | Urban | 3
KMM8A | MAROOCHYDORE | Urban | 3
KMR17A | CHAPEL HILL, KENMORE | Urban | 582 | 3.508 | 0.577 | 3.906 | 0.7009 | 1.5239 | 10 | 22548.15 | 17844.15 | 0.00124 | 0.000644 | 8 | 49023.53 | 0.000161
KMR17B | CHAPEL HILL, KENMORE | Urban | 1845 | 9.988 | 4.123 | 4.859 | 1.7049 | 0.74505 | 26 | 106924.1 | 95013.22 | 0.003153 | 0.001653 | 16 | 46725.24 | 0.000275
KMR18A | KENMORE, KENMORE HILLS | Urban | 416 | 2.483 | 2.126 | 1.467 | 1.1885 | 0.23029 | 2 | 55427.5 | 52099.5 | 0.000842 | 0.00042 | 6 | 10739.94 | 4.72e-05
KMR19A | BROOKFIELD, KENMORE, PINJARRA HILLS, PULLENVALE | Urban | 695 | 7.4 | 0.945 | 2.401 | 1.361 | 0.82651 | 6 | 60119.58 | 54583.58 | 0.001408 | 0.000707 | 10 | 36509.07 | 0.000141
KMR21A | CHAPEL HILL, KENMORE HILLS | Urban | 1046 | 1.792 | 5.937 | 3.163 | 0.14865 | 0.3121 | 5 | 8743.106 | 391.1064 | 0.001063 | 4.06e-06 | 3 | 18356.89 | 5.46e-05
KMR21B | KENMORE | Urban | 42 | 0 | 0.874 | 0.686 | 0.070196 |  | 1 | 376 |  | 4.77e-05
KMR22A | FIG TREE POCKET, KENMORE | Urban | 850 | 6.542 | 2.71 | 2.934 | 0.17468 | 2.4398 | 6 | 9410.737 | 2626.737 | 0.000905 | 4.54e-05 | 20 | 131442.1 | 0.000404
KMR24A | KENMORE | Urban | 755 | 4.345 | 0.484 | 1.972 | 0.2266 | 0.71611 | 9 | 16681.03 | 10705.03 | 0.00085 | 9.23e-05 | 10 | 52716.71 | 0.000196
KMR25A | BROOKFIELD, KENMORE HILLS, MT COOTTHA, PULLENVALE, | Rural short | 1093 | 46.736 | 5.576 | 4.782
KMR27A | BROOKFIELD, KENMORE | Urban | 945 | 7.023 | 4.237 | 3.468 | 0.24112 | 0.90027 | 10 | 12239.71 | 4695.711 | 0.001014 | 5.76e-05 | 13 | 45699.34 | 0.000172
KMR28A | CHAPEL HILL, KENMORE HILLS | Urban | 579 | 1.055 | 4.457 | 1.943 | 0.81622 | 0.07596 | 5 | 21995.88 | 14555.88 | 0.001241 | 0.000298 | 1 | 2047 | 9.02e-06
KMR29A | KENMORE | Urban | 795 | 3.78 | 2.732 | 2.271 | 0.58356 | 0.50126 | 14 | 39412.24 | 32682.21 | 0.00162 | 0.000815 | 14 | 33854.12 | 0.000188
KMS5 | SUNNYBANK | Urban | 2
KMS6 | SUNNYBANK | Urban | 2
KRA1 | COOLANGATTA | Urban | 607.5 | 1.743 | 0.333 | 2.229 | 2.5474 | 2.1462 | 5 | 55611.57 | 55611.57 | 0.001334 | 0.001334 | 8 | 46853.43 | 0.000151
KRA10 | BILINGA, COOLANGATTA | Urban | 1162 | 3.234 | 0.958 | 1.896 | 3.8874 | 0.24138 | 9 | 292303.3 | 292303.3 | 0.002378 | 0.002378 | 3 | 18149.83 | 7.99e-05
KRA2 | COOLANGATTA | Urban | 778.5 | 1.922 | 1.483 | 3.506 | 6.021 | 0.98572 | 8 | 209606.9 | 209606.9 | 0.002423 | 0.002423 | 7 | 34315.48 | 0.000127
KRA3 | BILINGA, TUGUN | Urban | 1290 | 2.862 | 2.563 | 1.934 | 7.1421 | 6.5883 | 11 | 206939.9 | 206939.9 | 0.003925 | 0.003925 | 16 | 190894.5 | 0.000548
KRA4 | COOLANGATTA | Urban | 280 | 0.016 | 3.542 | 2.229 | 0.51296 |  | 3 | 19929.12 | 19929.12 | 0.000575 | 0.000575
KRA7 | COOLANGATTA | Urban | 1237 | 3.905 | 0.798 | 3.334 | 5.7528 | 5.2881 | 9 | 239353.1 | 239353.1 | 0.00381 | 0.00381 | 21 | 220016 | 0.000559
KRN1 | GORDON PARK, KEDRON, STAFFORD | Urban | 2153.5 | 3.014 | 3.971 | 4.115 | 0.48869 | 0.64122 | 10 | 36986.29 | 36986.29 | 0.002179 | 0.002179 | 7 | 48529.98 | 0.000175
KRN10 | KEDRON, STAFFORD, STAFFORD HEIGHTS | Urban | 1513 | 5.72 | 0.814 | 2.553 | 1.667 | 0.4805 | 8 | 134538.5 | 134538.5 | 0.001638 | 0.001638 | 12 | 38780.25 | 0.000143
KRN11 | CLAYFIELD, LUTWYCHE, WAVELL HEIGHTS, WOOLOOWIN | Urban | 1337 | 5.756 | 1.403 | 3.239 | 1.4222 | 0.39395 | 20 | 101073.9 | 34545.9 | 0.001664 | 0.000961 | 3 | 27998.39 | 0.000107
KRN12 | GORDON PARK, LUTWYCHE, WOOLOOWIN | Urban | 1682.7 | 2.427 | 2.105 | 2.153 | 0.004628 | 0.39973 | 5 | 258.1833 | 258.1833 | 5.07e-06 | 5.07e-06 | 4 | 22298.84 | 8.51e-05
KRN13A | KEDRON | Urban | 2 | 0 | 1.441
KRN13B | KEDRON, LUTWYCHE, WINDSOR | Urban | 5 | 0 | 3.038
KRN18 | GORDON PARK, GRANGE, LUTWYCHE, WINDSOR | Urban | 1403 | 4.32 | 0.228 | 2.636 | 0.06203 | 0.014776 | 9 | 4651.4 | 4651.4 | 4.16e-05 | 4.16e-05 | 2 | 1107.99 | 4.53e-06
KRN2 | KEDRON, WAVELL HEIGHTS | Urban | 2016 | 6.506 | 1.28 | 3.368 | 4.1976 | 0.064587 | 11 | 283105.8 | 283105.8 | 0.002189 | 0.002189 | 2 | 4356.05 | 2.58e-05
KRN3A | KEDRON | Urban | 2 | 0 | 1.239
KRN3B | KEDRON, LUTWYCHE, WINDSOR | Urban | 4 | 0 | 2.202
KRN5A | KEDRON | Urban | 784 | 4.195 | 2.061 | 3.62 | 0.26133 | 0.42714 | 3 | 11324.83 | 11324.83 | 7.23e-05 | 7.23e-05 | 9 | 18510.47 | 8.4e-05
KRN5B | STAFFORD | Urban | 339.5 | 0.897 | 3.585 | 2.134 |  | 0.064017 | [5 empty] | 1 | 1824 | 2.43e-05
KRN6A | LUTWYCHE | Urban | 2 | 0 | 1.891 | 1.962
KRNQNP7 | BOWEN HILLS, LUTWYCHE, WINDSOR | Urban | 701 | 0.206 | 7.255 | 2.591 | 0.007667 | 0.08286 | 5 | 419.3417 | 419.3417 | 5.07e-06 | 5.07e-06 | 1 | 4531.69 | 1.42e-05
KSN1 | CHAMBERS FLAT, CRESTMEAD, MARSDEN, WATERFORD WEST | Urban | 1670 | 10.477 | 0.616 | 3.792 | 1.6551 |  | 26 | 78532.85 | 7812.85 | 0.000138 | 7.35e-05
KSN14 | MARSDEN | Urban | 1069 | 5.131 | 1.112 | 2.991 | 4.2353 |  | 14 | 303551.8 | 303551.8 | 0.003467 | 0.003467
KSN15 | LOGANLEA, MEADOWBROOK, WATERFORD WEST | Rural short | 929.2 | 6.827 | 1.234 | 1.924
KSN2A | LOGAN RESERVE, WATERFORD WEST | Urban | 1011 | 3.693 | 1.617 | 2.039 | 0.3448 |  | 11 | 26355.95 | 26160.96 | 0.001095 | 0.001094
KSN3 | KINGSTON, LOGANLEA | Urban | 632 | 8.214 | 1.878 | 4.344 | 0.28945 | 0.11629 | 13 | 8094.515 | 1962.455 | 5.23e-05 | 1.42e-05 | 1 | 3252 | 6.08e-06
KSN4 | LOGANLEA | Urban | 1009 | 3.459 | 0.446 | 1.943 | 1.0285 | 0.070183 | 6 | 87886.42 | 87886.42 | 0.001065 | 0.001065 | 1 | 5997.2 | 2.76e-05
KSN5 | MARSDEN | Rural short | 1665 | 11.634 | 0.566 | 3.43
KSN6 | KINGSTON, LOGANLEA | Urban | 797 | 6.242 | 2.245 | 4.458 | 19.0664 | 0.35778 | 12 | 561969.9 | 1113.887 | 0.000784 | 1.12e-05 | 4 | 10545.42 | 5.47e-05
KSN7 | LOGAN RESERVE, WATERFORD, WATERFORD WEST | Rural short | 1288 | 19.149 | 0.733 | 3.792
KSN8 | CHAMBERS FLAT, CRESTMEAD, LOGAN RESERVE, MARSDEN, | Rural short | 1464 | 23.737 | 3.394 | 3.773
KWA10A | BIRTINYA, BOKARINA, WARANA | Urban | 622 | 2.727 | 4.084 | 4.535 | 0.042067 |  | 3 | 1226.85 | 1226.85 | 1.55e-05 | 1.55e-05
KWA11A | BIRTINYA, BOKARINA | Urban | 329 | 0 | 6.333 | 4.439 |  | 0.002161 | [5 empty] | 1 | 38 | 1.01e-06
KWA12A | BUDDINA, WARANA | Urban | 2326.5 | 9.886 | 0.984 | 5.828 | 16.5312 | 1.7626 | 36 | 985068.5 | 985068.5 | 0.007691 | 0.007691 | 11 | 105029.9 | 0.000478
KWA13A | BUDDINA | Urban | 30 | 0 | 0.995
KWA1A | BUDDINA, MINYAMA, PARREARRA, WARANA | Urban | 1483 | 5.354 | 3.752 | 3.887 | 6.9508 | 0.13803 | 16 | 369933.1 | 369933.1 | 0.001674 | 0.001674 | 2 | 7346.39 | 4.47e-05
KWA2A | BOKARINA, WARANA, WURTULLA | Urban | 827 | 5.225 | 0.713 | 1.895 | 0.18251 |  | 17 | 10278.02 | 10278.02 | 0.000164 | 0.000164
KWA3A | BUDDINA, MINYAMA | Urban | 669.5 | 4.229 | 2.909 | 3.068 | 12.1069 | 0.024139 | 1 | 298101 | 298101 | 0.000744 | 0.000744 | 1 | 594.36 | 4.75e-06
KWA4A | PARREARRA, WARANA | Urban | 2031 | 0 | 6.257 | 3.964 | 0.006962 |  | 4 | 526.5333 | 526.5333 | 4.06e-06 | 4.06e-06
KWA6A | BOKARINA, WARANA | Urban | 335 | 2.534 | 1.954 | 1.505 |  | 0.45126 | [5 empty] | 1 | 10980 | 6.08e-05
KWH1 | COOLABINE, KENILWORTH, KIDAMAN CREEK, MAPLETON, OB | Rural short | 535 | 61.395 | 0.413 | 1.321
KWH2 | CAMBROON, CONONDALE, KENILWORTH | Rural short | 787.5 | 106.898 | 0.151 | 1.639
KWH3 | BELLI PARK, BROOLOO, COOLABINE, GHEERULLA, KENILWO | Rural short | 385.5 | 77.364 | 0.278 | 2.134
LBCVPK5 | FORTITUDE VALLEY, SPRING HILL | Urban | 133.1 | 0 | 1.903 | 2.134 | 0.063109 |  | 4 | 808.1767 | 277.8167 | 0.000137 | 3.04e-06
LBH1B | BALD KNOB, LANDSBOROUGH, MALENY, MOUNT MELLUM | Rural short | 999 | 31.374 | 0.597 | 2.031
LBH3A | GLENVIEW, LANDSBOROUGH, MOOLOOLAH VALLEY | Rural short | 772 | 20.901 | 0.896 | 2.096
LBH5A | BELLS CREEK, GLENVIEW, LANDSBOROUGH, MERIDAN PLAIN | Rural short | 778 | 42.812 | 5.874 | 2.713
LBH6A | BEERWAH, LANDSBOROUGH | Rural short | 1542 | 29.005 | 2.922 | 4.287
LBS10A | HEMMANT | Urban | 39 | 0.953 | 1.7 | 2.744 | 1.8389 |  | 2 | 4571 | 4571 | 4.87e-05 | 4.87e-05
LBS12A | HEMMANT | Urban | 52 | 1.861 | 3.964 | 2.058
LBS13A | LYTTON | Urban | 43 | 0 | 2.546 | 3.753
LBS2A | HEMMANT, LYTTON | Urban | 46 | 0.373 | 3.554 | 2.401
LBS4A | LYTTON | Urban | 35 | 0 | 4.939 | 3.982
LBS5A | LYTTON, PORT OF BRISBANE, WYNNUM | Rural short | 260 | 3.036 | 6.983 | 2.42
LBS8B | WYNNUM, WYNNUM WEST | Urban | 177 | 1.862 | 0.833 | 1.143 | 0.019165 | 7.2518 | 1 | 98.5507 | 98.5507 | 1.01e-06 | 1.01e-06 | 3 | 37291.2 | 0.000101
LDR1 | RUNAWAY BAY | Urban | 509 | 2.772 | 1.113 | 2.087 | 0.13937 | 0.20234 | 3 | 6990.886 | 6990.886 | 0.000532 | 0.000532 | 4 | 10149.3 | 4.1e-05
LDR10A | ARUNDEL, LABRADOR | Urban | 2326.5 | 4.818 | 1.206 | 3.849 | 0.6122 | 1.841 | 8 | 52670.91 | 52670.91 | 0.00239 | 0.00239 | 15 | 158395.7 | 0.000459
LDR10B | BIGGERA WATERS, LABRADOR | Urban | 4 | 0 | 2.36 | 4.058 |  |  | 1 | 120 | 120 | 6.08e-06 | 6.08e-06
LDR11 | LABRADOR | Urban | 179 | 1.416 | 0.298 | 0.555 | 2.8915 |  | 4 | 148005.7 | 148005.7 | 0.000398 | 0.000398
LDR2A | BIGGERA WATERS, LABRADOR | Urban | 124 | 2.308 | 0.833 | 1.962 | 3.1729 |  | 2 | 9616.88 | 9616.88 | 0.000304 | 0.000304
LDR2B | LABRADOR | Urban | 992.5 | 1.294 | 1.552 | 1.628 | 1.1042 | 0.031967 | 3 | 93556.98 | 93556.98 | 0.001991 | 0.001991 | 1 | 2708.64 | 2.41e-05
LDR3 | BIGGERA WATERS, LABRADOR, RUNAWAY BAY | Urban | 2130 | 2.955 | 1.146 | 4.002 | 0.45591 | 0.56802 | 5 | 33639.67 | 33639.67 | 0.002232 | 0.002232 | 5 | 41911.59 | 0.000119
LDR5 | BIGGERA WATERS, LABRADOR | Urban | 552 | 2.038 | 1.13 | 3.296 | 0.35636 | 3.9991 | 4 | 8495.823 | 8495.823 | 0.000628 | 0.000628 | 7 | 95340.66 | 0.000266
LDR6 | BIGGERA WATERS, LABRADOR | Urban | 1517 | 1.851 | 1.423 | 3.079 | 0.96836 | 0.74393 | 10 | 62384.27 | 62384.27 | 0.002609 | 0.002609 | 12 | 47926.26 | 0.000198
LDR8 | BIGGERA WATERS, LABRADOR, RUNAWAY BAY | Urban | 1116 | 3.615 | 1 |  | 2.6213 | 0.24059 | 8 | 119780.9 | 119780.9 | 0.001348 | 0.001348 | 5 | 10993.83 | 3.14e-05
LGL11A | KINGSTON, LOGAN CENTRAL, SLACKS CREEK | Urban | 1145.5 | 7.724 | 0.923 | 3.01 | 1.327 | 0.15903 | 7 | 76257.65 | 22451.63 | 0.001499 | 0.001285 | 6 | 9138.815 | 6.82e-05
LGL13A | LOGANLEA, MEADOWBROOK | Urban | 529 | 2.735 | 3.73 | 3.068 | 5.5561 |  | 2 | 194006.7 | 194006.7 | 0.001081 | 0.001081
LGL15A | KINGSTON, LOGANLEA, MEADOWBROOK, SLACKS CREEK | Urban | 965.5 | 5.668 | 2.48 | 2.232 | 0.039588 | 0.44369 | 11 | 2536.033 | 2536.033 | 0.000998 | 0.000998 | 6 | 28423.25 | 0.000155
LGL3A | LOGANLEA, MEADOWBROOK | Urban | 709.5 | 4.82 | 1.112 | 2.344 | 6.3425 |  | 9 | 318288.2 | 12343.19 | 0.001632 | 0.00091
LGL5A | MEADOWBROOK | Urban | 443 | 1.834 | 2.11 | 3.506 | 0.039951 | 0.061172 | 2 | 865.3333 | 865.3333 | 0.000455 | 0.000455 | 1 | 1325 | 5.07e-06
LGL7A | MEADOWBROOK | Urban | 2.7 | 0 | 2.352 | 2.944
LGV2B | CHAMBERS FLAT, LOGAN RESERVE, LOGAN VILLAGE, PARK | Rural short | 650 | 30.03 | 4.053 | 3.21
LGV3A | BUCCAN, CHAMBERS FLAT, LOGAN RESERVE, LOGAN VILLAG | Rural short | 206 | 9.344 | 0.518 | 0.705
LGV5B | LOGAN VILLAGE | Rural short | 690 | 15.994 | 0.649 | 1.943
LGV6A | BUCCAN, LOGAN VILLAGE, WATERFORD | Rural short | 748 | 33.798 | 1.63 | 2.001
LHM1A | LOGANHOLME, TANAH MERAH | Urban | 1599 | 4.837 | 5.676 | 3.925 | 8.0342 | 0.57053 | 17 | 579226.3 | 80814.3 | 0.003467 | 0.001854 | 7 | 41132.66 | 0.000123
LHM2 | LOGANHOLME, SHAILER PARK | Urban | 572 | 4.42 | 1.058 | 2.782
LHM3 | BEENLEIGH, LOGANHOLME | Rural short | 1736 | 10.052 | 4.174 | 4.382
LHM4A | LOGANHOLME | Urban | 126 | 2.518 | 0.684 | 2.496 | 2.0449 | 0.02633 | 2 | 32231 |  | 0.000245 |  | 1 | 415 | 5.07e-06
LHM5 | CORNUBIA, LOGANHOLME | Rural short | 867 | 8.255 | 0.426 | 2.098
LHM6 | SHAILER PARK | Urban | 7 | 0 | 3.256 | 4.325
LHM7 | LOGANHOLME | Urban | 258 | 2.219 | 1.098 | 4.154 | 5.952 | 0.036731 | 6 | 70105.71 | 70105.71 | 0.000661 | 0.000661 | 1 | 432.64 | 2.11e-06
LHM8A | CARBROOK, CORNUBIA, LOGANHOLME | Rural short | 462 | 6.821 | 1.345 | 0.857
LHM8B | LOGANHOLME | Urban | 95 | 1.512 | 1.415 | 1.753 |  | 0.31228 | [5 empty] | 2 | 4008 | 2.21e-05
LHM9 | LOGANHOLME, SHAILER PARK | Urban | 6 | 0 | 3.238 | 4.192
LLY1 | BLENHEIM, LAIDLEY, LAIDLEY CREEK WEST, LAIDLEY SOU | Rural short | 513 | 112.186 | 1.484 | 2.648
LLY2B | LAIDLEY | Urban | 1053.5 | 9.059 | 1.967 |  | 4.6269 | 0.047289 | 5 | 275744.9 | 64244.9 | 0.003248 | 0.002176 | 2 | 2818.2 | 8.31e-06
LLY3 | BLENHEIM, FOREST HILL, GLEN CAIRN, GLENCAIRN, LAID | Rural short | 702 | 77.741 | 0.701 | 1.753
LLY4 | FOREST HILL, LAIDLEY, LAIDLEY HEIGHTS, LAIDLEY NOR | Rural short | 898.5 | 39.169 | 1.823 | 2.286
LLY5 | CALVERT, GRANDCHESTER, HIDDENVALE, LAIDLEY, LAIDLE | Rural short | 642 | 86.794 | 0.495 | 1.505
LRE4A | CHURCHABLE, GLENORE GROVE, KENTVILLE, LOCKROSE, LO | Rural short | 299 | 38.53 | 0.287 | 0.667
LRE6A | ATKINSONS DAM, COOMINYA, KENTVILLE, LOCKROSE, LOCK | Rural short | 393 | 50.248 | 0.726 | 1.505
LRE7A | BRIGHTVIEW, HATTON VALE, KENSINGTON GROVE, LOCKROS | Rural short | 1148 | 32.324 | 4.635 | 3.792
LRE8A | BRIGHTVIEW, LOCKROSE, MT TARAMPA, REGENCY DOWNS | Rural short | 418 | 23.819 | 0.942 | 1.315
LTA12A | MANLY WEST, WYNNUM WEST | Urban | 1443 | 6.026 | 1.018 | 2.713 | 0.30833 | 0.89248 | 6 | 23012.8 | 23012.8 | 0.001477 | 0.001477 | 13 | 66610.9 | 0.000218
LTA15A | LOTA, MANLY, MANLY WEST | Urban | 1206.5 | 5.096 | 1.406 | 2.713 | 1.9088 | 0.25624 | 17 | 119849.7 | 119849.7 | 0.002433 | 0.002433 | 4 | 16088.8 | 7.12e-05
LTA16A | LOTA, MANLY WEST, WAKERLEY | Urban | 1158 | 2.078 | 4.967 | 3.163 | 1.5311 | 0.86885 | 3 | 81870.82 | 81870.82 | 0.001194 | 0.001194 | 15 | 46458.36 | 0.000187
LTA3A | BIRKDALE, LOTA, RANSOME, THORNESIDE | Rural short | 1858 | 12.617 | 0.992 | 3.599
LTA4A | GUMDALE, RANSOME, WAKERLEY | Urban | 1399 | 7.938 | 8.314 | 4.42 | 5.9688 | 0.72256 | 10 | 419919.6 | 62818.11 | 0.002827 | 0.001418 | 15 | 50833.79 | 0.000157
LTA5A | MANLY, MANLY WEST | Urban | 1321.5 | 3.107 | 4.606 | 2.591 | 0.022974 | 0.70287 | 4 | 1707.967 | 1707.967 | 1.29e-05 | 1.29e-05 | 17 | 52254.86 | 0.000205
LTA8A | MANLY, MANLY WEST, WYNNUM, WYNNUM WEST | Urban | 2013.5 | 7.707 | 0.965 | 4.118 | 0.008624 | 0.13117 | 8 | 542.85 | 542.85 | 1.01e-05 | 1.01e-05 | 5 | 8256.62 | 3.75e-05
LTN2 | JOYNER, KURWONGBAH, LAWNTON, PETRIE, WHITESIDE | Rural short | 1758 | 10.583 | 5.505 | 4.954
LTN3 | LAWNTON, PETRIE | Urban | 1655 | 11.256 | 1.181 | 3.792 | 0.090957 | 1.2083 | 8 | 5447.3 | 5447.3 | 0.000208 | 0.000208 | 21 | 72360.64 | 0.000307
LTN4 | BRAY PARK, STRATHPINE | Urban | 1722 | 7.807 | 1.752 | 5.735 | 1.1427 | 0.19467 | 7 | 59775.43 | 59775.43 | 0.00105 | 0.00105 | 2 | 10183.64 | 3.88e-05
LTN5 | BRAY PARK, BRENDALE, STRATHPINE | Urban | 1900 | 8.871 | 2.011 | 4.42 | 3.4588 | 1.7917 | 13 | 186701.2 | 186701.2 | 0.002031 | 0.002031 | 14 | 96715.14 | 0.000345
LTN6 | LAWNTON, STRATHPINE | Urban | 1869 | 12.712 | 0.725 | 4.363 | 3.8055 | 1.1771 | 7 | 238029.6 | 238029.6 | 0.003606 | 0.003606 | 18 | 73627.56 | 0.000311
LTN7 | BRAY PARK, LAWNTON, STRATHPINE | Urban | 616 | 4.386 | 1.337 | 3.734 | 0.15329 | 0.49123 | 3 | 3670.92 | 3670.92 | 7.9e-05 | 7.9e-05 | 2 | 11764 | 6.29e-05
LTN8 | BRAY PARK, JOYNER, LAWNTON | Rural short | 586 | 4.491 | 4.105 | 1.562
LTN9 | BRAY PARK, JOYNER, LAWNTON, WARNER | Urban | 1766 | 6.727 | 5.363 | 5.564 | 1.7322 | 0.029758 | 5 | 86266.64 | 86266.64 | 0.001426 | 0.001426 | 1 | 1482 | 6.08e-06
LWD1 | LOWOOD, PATRICK ESTATE, WIVENHOE POCKET | Rural short | 652 | 20.555 | 0.666 | 2.401
LYT1 | LYTTON | Urban | 15 | 1.651 | 0.372 | 4.192
MAI11 | MERMAID BEACH, MERMAID WATERS, MIAMI | Urban | 1707 | 3.631 | 0.371 | 3.695 | 3.7969 | 1.2313 | 8 | 233169.4 | 233169.4 | 0.003542 | 0.003542 | 8 | 75614.87 | 0.000253
MAI13 | BURLEIGH WATERS, MIAMI | Urban | 1812.5 | 2.92 | 8.024 | 3.836 | 2.3055 | 0.16091 | 7 | 180525 | 180525 | 0.003874 | 0.003874 | 5 | 12599.58 | 5.45e-05
MAI14 | MIAMI | Urban | 1716.7 | 3.125 | 0.943 | 4.176 | 4.0017 | 1.3422 | 10 | 213294.1 | 213294.1 | 0.003666 | 0.003666 | 4 | 71540.8 | 0.000167
MAI17 | BURLEIGH HEADS, MIAMI | Urban | 1795.8 | 4.749 | 0.831 | 4.083 | 5.8133 | 1.2838 | 16 | 425277.1 | 425277.1 | 0.005433 | 0.005433 | 7 | 93914.6 | 0.000213
MAI5 | MERMAID BEACH, MERMAID WATERS, MIAMI | Urban | 1739 | 3.062 | 1.071 | 3.926 | 5.0111 | 0.86973 | 9 | 341068.3 | 189949.3 | 0.005475 | 0.003714 | 6 | 59195.64 | 0.000173
MAI7 | MERMAID BEACH, MERMAID WATERS, MIAMI | Urban | 1454 | 0.995 | 5.262 | 3.217 | 5.1795 | 0.1504 | 9 | 317540.4 | 317452.7 | 0.00441 | 0.004409 | 2 | 9220.575 | 3.56e-05
MAI8 | MERMAID BEACH, MERMAID WATERS, MIAMI, ROBINA | Urban | 1262 | 0.78 | 6.051 | 3.391 | 2.1038 | 0.067793 | 7 | 121662.7 | 121662.7 | 0.002558 | 0.002558 | 1 | 3920.4 | 2.41e-05
MAK6 | SURFERS PARADISE | Urban | 130 | 0 | 0.205 |  | 0.003156 |  | 1 | 121.8333 | 121.8333 | 1.01e-06 | 1.01e-06
MAK7 | SURFERS PARADISE | Urban | 20 | 0 | 0.245
MAKT1 | SURFERS PARADISE | Urban | 2
MBG1 | ASHWELL, MARBURG, MINDEN, ROSEWOOD, TALLEGALLA, TH | Rural short | 292 | 44.505 | 0 | 0.591
MBG2 | HAIGSLEA, MARBURG, MT MARROW, ROSEWOOD, TALLEGALLA | Rural short | 474 | 47.137 | 0.185 | 2.191
MBG4 | FAIRNEY VIEW, FERNVALE, GLAMORGAN VALE, HAIGSLEA, | Rural short | 414 | 69.045 | 0.14 | 1.2
MCN1 | MOUNT COTTON, SHELDON, THORNLANDS | Rural short | 92 | 14.389 | 1.903 | 1.753
MCN2 | MOUNT COTTON | Rural short | 69 | 7.694 | 1.638 | 1.895
MCN3 | CORNUBIA, MOUNT COTTON | Urban | 55 | 10.792 | 0.174 | 3.468 | 1.9543 | 0.48261 | 4 | 3919.86 | 3919.86 | 5.88e-05 | 5.88e-05 | 3 | 968 | 5.07e-06
MCN4 | MOUNT COTTON | Rural short | 810 | 1.441 | 7.339 | 2.039
MCW11 | KARANA DOWNS, KHOLO, MOUNT CROSBY | Rural short | 824 | 19.844 | 3.818 | 2.686
MCW4 | CHUWAR, KARANA DOWNS, MOUNT CROSBY | Rural short | 1269 | 10.636 | 6.416 | 3.525
MCW7 | CHUWAR, KARALEE, KHOLO, LAKE MANCHESTER, MOUNT CRO | Rural short | 801 | 42.425 | 2.107 | 2.782
MDH1A | PINKENBA | Urban | 13 | 1.021 | 1.833 | 1.562
MDH3A | EAGLE FARM, PINKENBA | Urban | 86.5 | 0.832 | 5.24 | 4.249
MDH4A | PINKENBA | Urban | 137 | 3.702 | 0.826 | 1.639 | 0.006345 |  | 4 | 310.05 | 310.05 | 4.06e-06 | 4.06e-06
MDH5A | EAGLE FARM, PINKENBA | Urban | 67.5 | 0.455 | 2.572 | 3.334 | 2.1337 |  | 4 | 13261.5 | 13261.5 | 0.000255 | 0.000255
MDH5B | EAGLE FARM, PINKENBA | Urban | 42.5 | 1.099 | 3.6 | 2.153 | 1.9044 | 0.14553 | 4 | 8427.5 | 8427.5 | 0.000181 | 0.000181 | 1 | 644 | 2.03e-06
MDH8B | PINKENBA | Urban | 4 | 0 | 0.896 | 3.406
MDH9A | PINKENBA | Urban | 46 | 1.334 | 0.654 | 2.229 | 0.005049 |  | 1 | 28.5 | 28.5 | 1.01e-06 | 1.01e-06
MDHSWB10 | PINKENBA | Urban | 4 | 0.596 | 1.705 | 1.924
MDR10A | MOLENDINAR | Urban | 627 | 1.15 | 3.983 | 1.924 | 0.14721 | 0.30482 | 6 | 8670.713 | 8670.713 | 0.000107 | 0.000107 | 3 | 17954.1 | 6.39e-05
MDR12B | ASHMORE, MOLENDINAR, SOUTHPORT | Urban | 284 | 2.081 | 1.948 | 4.096 | 0.24759 | 0.39025 | 3 | 5268.617 | 5268.617 | 0.000301 | 0.000301 | 1 | 8304.15 | 2.03e-05
MDR24A | ASHMORE, SOUTHPORT | Urban | 870 | 2.739 | 3.156 | 2.153 | 0.13972 | 0.014233 | 4 | 5690.05 | 5690.05 | 5.93e-05 | 5.93e-05 | 1 | 579.6 | 2.45e-05
MDR25A | MOLENDINAR, NERANG | Urban | 193.5 | 4.104 | 0.309 | 3.428 | 0.093684 | 0.36228 | 1 | 1064 | 1064 | 8.11e-06 | 8.11e-06 | 1 | 4114.54 | 1.02e-05
MDR2A | BENOWA | Urban | 357 | 3.293 | 3.655 | 4.154 | 0.78089 | 0.034261 | 3 | 18347.65 | 18347.65 | 0.0004 | 0.0004 | 1 | 805 | 7.1e-06
MDR30A | ASHMORE, BENOWA, CARRARA | Urban | 1603.5 | 3.044 | 7.111 | 4.382 | 1.0502 | 0.40179 | 13 | 62418.15 | 62418.15 | 0.000267 | 0.000267 | 2 | 23880.4 | 0.000115
MDR31A | MOLENDINAR | Urban | 292 | 1.946 | 2.291 | 3.43
MDR33A | ASHMORE, BENOWA | Urban | 1426 | 3.336 | 4.842 | 3.715 | 1.5597 | 0.99525 | 11 | 72359.06 | 72359.06 | 0.001612 | 0.001612 | 4 | 46173.16 | 0.000134
MDR35A | SOUTHPORT | Urban | 10 | 0 | 5.463 | 3.83 |  | 0.004449 | [5 empty] | 1 | 849 | 3.04e-06
MDR3A | ASHMORE, CARRARA, MOLENDINAR, NERANG | Urban | 721.7 | 4.865 | 5.053 | 2.953 | 4.2728 |  | 6 | 194406.6 | 194406.6 | 0.00081 | 0.00081
MDR4A | MOLENDINAR, SOUTHPORT | Urban | 424 | 1.416 | 4.105 | 3.029
MDR6A | MOLENDINAR, SOUTHPORT | Urban | 649 | 3.923 | 2.736 | 3.525 | 0.51138 | 0.029665 | 7 | 12364.13 | 12364.13 | 0.000699 | 0.000699 | 2 | 717.24 | 3.06e-06
MDR8A | BENOWA, CARRARA | Rural short | 327 | 4.057 | 6.778 | 2.877
MDRMLD11 | MOLENDINAR | Urban | 894 | 3.102 | 3.245 | 3.734 | 0.98217 | 0.38804 | 6 | 38817.96 | 38817.96 | 0.000908 | 0.000908 | 5 | 15336.28 | 7.15e-05
MEX3 | BRISBANE, MILTON | Urban | 26 | 0 | 1.244 |  | 1.4324 | 0.035231 | 1 | 4635 | 4635 | 2.64e-05 | 2.64e-05 | 1 | 114 | 1.01e-06
MFD11A | MORAYFIELD | Rural short | 11 | 3.124 | 1.836 | 1.315
MFD12A | BURPENGARY, BURPENGARY EAST, CABOOLTURE, MORAYFIEL | Rural short | 1295 | 9.359 | 6.864 | 5.125
MFD13A | BURPENGARY | Rural short | 511 | 7.397 | 4.304 | 1.276
MFD2A | BURPENGARY, CABOOLTURE SOUTH, MORAYFIELD | Urban | 781 | 6.78 | 2.168 | 4.23 | 2.4363 | 0.55654 | 6 | 59754 | 59754 | 0.000506 | 0.000506 | 1 | 13650 | 7.1e-05
MFD3A | BURPENGARY, BURPENGARY EAST | Rural short | 960 | 23.834 | 0.997 | 3.544
MFD5A | BURPENGARY, MORAYFIELD | Rural short | 516 | 10.879 | 0.185 | 1.734
MFD8A | BURPENGARY, MORAYFIELD | Rural short | 2211 | 34.36 | 4.472 | 6.611
MFD9A | BURPENGARY | Urban | 906 | 7.51 | 0.292 | 2.347 | 1.586 | 0.11033 | 8 | 116686.9 | 115136.9 | 0.001758 | 0.001707 | 3 | 8117.225 | 4.29e-05
MFN12A | CABOOLTURE, CABOOLTURE SOUTH, MELDALE, MORAYFIELD | Rural short | 1459 | 15.61 | 5.107 | 4.782
MFN13A | MORAYFIELD, UPPER CABOOLTURE | Rural short | 1697 | 15.888 | 4.076 | 4.516
MFN15A | BEACHMERE, CABOOLTURE, NINGI | Rural short | 733 | 15.928 | 2.871 | 2.667
MFN16A | MORAYFIELD | Urban | 10
MFN1B | CABOOLTURE, CABOOLTURE SOUTH, MORAYFIELD | Urban | 477 | 3.921 | 1.7 | 2.553 | 0.35633 |  | 7 | 11419.65 | 11419.65 | 0.000118 | 0.000118
MFN2A | CABOOLTURE SOUTH, MORAYFIELD | Urban | 524 | 2.442 | 1.964 | 4.763 | 0.009347 | 0.85732 | 3 | 149.1 | 149.1 | 3.04e-06 | 3.04e-06 | 2 | 13675.85 | 3.26e-05
MFN3A | MORAYFIELD | Urban | 8 | 0 | 0.655 | 3.334
MFN5A | CABOOLTURE SOUTH, MORAYFIELD, UPPER CABOOLTURE | Rural short | 2317 | 11.359 | 5.028
MGL1A | PULLENVALE, UPPER BROOKFIELD | Rural short | 680 | 16.568 | 8.199 | 3.01
MGL2A | ANSTEAD, BELLBOWRIE, MOGGILL, PINJARRA HILLS | Rural short | 1031 | 15.933 | 6.449 | 3.639
MGL5 | BELLBOWRIE, MOGGILL | Urban | 1464 | 0.119 | 11.376 | 5.068 | 0.81414 | 0.3571 | 14 | 39768.77 | 39768.77 | 0.000331 | 0.000331 | 4 | 17443.24 | 9.02e-05
MGL6B | PINJARRA HILLS | Rural short | 32 | 2.013 | 0.846 | 0.171
MGL8 | MOGGILL, PINJARRA HILLS, PULLENVALE | Urban | 371 | 7.401 | 2.393 | 2.877 | 0.13428 |  | 1 | 2756.5 | 2756.5 | 1.88e-05 | 1.88e-05
MGL9 | ANSTEAD, MOGGILL, PULLENVALE | Rural short | 392 | 12.507 | 0.93 | 1.258
MGP1 | MUDGEERABA | Rural short | 579 | 10.436 | 1.005 | 1.696
MGP12A | AUSTINVILLE, BONOGIN, MUDGEERABA | Rural short | 963 | 14.922 | 4.927 | 1.982
MGP13A | AUSTINVILLE, MUDGEERABA, NATURAL BRIDGE, NERANWOOD | Rural short | 1029 | 87.995 | 4.37 | 2.643
MGP15A | GILSTON, MUDGEERABA, TALLAI | Rural short | 948 | 16.928 | 0.472 | 2.801
MGP16A | MUDGEERABA | Urban | 627 | 3.027 | 0 | 1.486 | 0.002974 |  | 2 | 205.6833 | 136.6333 | 2.03e-06 | 1.01e-06
MGP17A | BONOGIN, MUDGEERABA, REEDY CREEK | Rural short | 1611 | 0.345 | 12.869 | 4.235
MGP2A | MUDGEERABA, TALLAI | Rural short | 753 | 5.709 | 1.259 | 2.153
MGP4 | BONOGIN, MUDGEERABA | Rural short | 779 | 16.278 | 4.356 | 2.483
MHL12A | MANGO HILL, NORTH LAKES | Rural short | 1789.5 | 0 | 22.051 | 5.564
MHL13A | NORTH LAKES | Urban | 2138 | 0 | 17.527 | 5.906 | 0.029476 |  | 4 | 2469.345 | 2469.345 | 3.85e-05 | 3.85e-05
MHL1B | KIPPA-RING, MANGO HILL, ROTHWELL | Rural short | 1661 | 13.954 | 8.071 | 4.344
MHL22B | MANGO HILL, NORTH LAKES | Urban | 6 | 0 | 1.435 | 2.591
MHL25A | NORTH LAKES | Urban | 1355.5 | 0 | 12.324 | 6.116 | 0.001807 | 0.004892 | 2 | 66.4833 | 66.4833 | 2.03e-06 | 2.03e-06 | 1 | 180 | 1.01e-06
MHL27A | MANGO HILL | Urban | 1110 | 0 | 6.384 |  | 0.001272 | 0.090518 | 1 | 74.9167 | 74.9167 | 1.01e-06 | 1.01e-06 | 1 | 5332 | 3.14e-05
MHL2A | GRIFFIN, KALLANGUR, MANGO HILL, MURRUMBA DOWNS | Rural short | 1043 | 9.666 | 4.755 | 3.391
MHL3A | MANGO HILL, NORTH LAKES | Urban | 1378 | 1.413 | 7.23 | 3.715 | 0.007528 | 0.18083 | 6 | 630.6972 | 630.6972 | 6.08e-06 | 6.08e-06 | 7 | 15148.69 | 7.33e-05
MHPWED5 | SOUTH BRISBANE | Urban | 111 | 0.075 | 3.02 | 2.039 | 4.2444 |  | 5 | 21912.55 | 21912.55 | 0.00024 | 0.00024
MLB11A | BUDERIM, MOUNTAIN CREEK | Urban | 1711 | 2.056 | 10.564 | 4.522 | 0.006897 | 0.14201 | 3 | 366.6167 | 366.6167 | 3.04e-06 | 3.04e-06 | 4 | 7548.69 | 0.000153
MLB12A | BUDERIM, SIPPY DOWNS | Rural short | 1765 | 11.952 | 5.94 | 4.216
MLB13A | SIPPY DOWNS | Urban | 1491 | 0 | 8.424 | 2.973 | 0.006879 | 1.6098 | 4 | 375.45 | 375.45 | 3.55e-06 | 3.55e-06 | 5 | 87863.23 | 0.000493
MLB2A | SIPPY DOWNS | Urban | 1524 | 0 | 9.882 | 3.22 |  | 0.011876 | [5 empty] | 1 | 1075.25 | 9.48e-06
MLB3A | BUDERIM, MOOLOOLABA, MOUNTAIN CREEK, SIPPY DOWNS | Rural short | 3276 | 4.616 | 17.354 | 5.316
MLB4A | BUDERIM | Urban | 1612 | 3.752 | 5.853 | 3.81 | 3.2299 |  | 6 | 212327.5 | 212327.5 | 0.001723 | 0.001723
MLB6A | BUDERIM, GLENVIEW, ILKLEY, PALMVIEW, SIPPY DOWNS, | Rural short | 892 | 15.148 | 10.447 | 6.307
MLB8A | BUDERIM, CHEVALLUM, FOREST GLEN, ILKLEY, MONS, SIP | Rural short | 525 | 24.823 | 3.339 | 3.925
MLS10A | FORTITUDE VALLEY | Urban | 20 | 0 | 0.438 | 1.6
MLS11A | NEW FARM | Urban | 2068 | 0.056 | 5.43 | 3.811 | 0.008881 | 0.35151 | 6 | 610.5333 | 610.5333 | 6.08e-06 | 6.08e-06 | 7 | 24165.73 | 8e-05
MLS12B | FORTITUDE VALLEY, NEW FARM | Urban | 1803.5 | 0 | 2.424 | 2.877 | 2.3596 | 0.20072 | 8 | 188974.1 | 188974.1 | 0.002542 | 0.002542 | 5 | 16075.31 | 9.18e-05
MLS14A | FORTITUDE VALLEY | Urban | 313.4 | 0 | 1.008 | 2.439
MLS15A | EAST BRISBANE, NEW FARM | Urban | 1583.5 | 0 | 6.686 | 2.839 | 0.00108 | 0.19095 | 1 | 84.5167 | 84.5167 | 1.01e-06 | 1.01e-06 | 8 | 14943.57 | 5.7e-05
MLS26B | FORTITUDE VALLEY, NEW FARM, TENERIFFE | Urban | 1370 | 1.604 | 1.546 | 2.915 | 1.6608 |  | 10 | 109559.2 | 109559.2 | 0.001626 | 0.001626
MLS2A | BOWEN HILLS, FORTITUDE VALLEY | Urban | 313 | 0.303 | 2.724 | 4.232 | 0.0225 | 1.304 | 2 | 203.2333 | 203.2333 | 2.03e-06 | 2.03e-06 | 3 | 11778.28 | 7e-05
MLS6A | BRISBANE, FORTITUDE VALLEY, SPRING HILL | Urban | 622.5 | 0 | 2.102 | 2.344 | 0.014021 |  | 1 | 392.1333 | 392.1333 | 1.01e-06 | 1.01e-06
MLS90B | FORTITUDE VALLEY | Urban | 59 | 0 | 1.22 | 1.867
MLS9A | FORTITUDE VALLEY | Urban | 507.4 | 0 | 2.127 | 2.477
MLSMYV26 | FORTITUDE VALLEY | Urban | 15.4 | 0 | 0.486 | 1.772 | 0.61384 |  | 2 | 2059.6 | 2059.6 | 3.02e-05 | 3.02e-05
MLT15A | MILTON | Urban | 286 | 0.467 | 1.298 | 2.401 | 0.001398 |  | 1 | 34.3667 | 34.3667 | 1.01e-06 | 1.01e-06
MLT15B | MILTON, PADDINGTON, RED HILL | Urban | 762.5 | 2.409 | 1.512 | 3.029 | 1.229 | 1.9913 | 10 | 28280.3 | 28280.3 | 0.000128 | 0.000128 | 7 | 45822.17 | 0.000147
MLT19A | AUCHENFLOWER, MILTON | Urban | 889 | 1.131 | 2.669 | 2.648 | 0.13405 | 0.025586 | 1 | 5035 | 5035 | 9.63e-05 | 9.63e-05 | 2 | 961 | 2.27e-05
MLT21B | MILTON, PADDINGTON | Urban | 1501 | 4.377 | 0.534 | 3.696 | 4.4623 | 0.69643 | 9 | 245627.8 | 245627.8 | 0.003 | 0.003 | 4 | 38335.06 | 0.000125
MLT24A | MILTON, PADDINGTON | Urban | 875 | 2.855 | 1.355 | 2.763 | 0.41236 | 0.30835 | 5 | 19483.39 | 19483.39 | 0.000137 | 0.000137 | 3 | 14569.22 | 4.31e-05
MLT2B | KELVIN GROVE, RED HILL | Urban | 1216 | 1.699 | 3.981 | 2.877 | 3.4297 | 4.2204 | 6 | 225347.7 | 198.5333 | 0.001295 | 4.06e-06 | 24 | 277300.2 | 0.000916
MLT3A | BRISBANE, MILTON | Urban | 3 | 0 | 0.516 | 1.962
MLT3B | MILTON | Urban | 60 | 0 | 1.568 | 2.915
MLT40A | KELVIN GROVE | Urban | 3 | 0 | 2.836 | 1.277
MLT41A | BRISBANE, MILTON | Urban | 3 | 0 | 0.516 | 2.127 |  |  | 1 | 12 |  | 3.04e-06
MLT42A | BRISBANE, KELVIN GROVE, MILTON, PADDINGTON, RED HI | Urban | 665 | 1.332 | 4.823 | 3.182 | 0.79995 | 16.595 | 7 | 3828.333 | 3736.183 | 4.61e-05 | 4.51e-05 | 5 | 79419.21 | 0.000161
MLT43A | KELVIN GROVE | Urban | 186 | 0 | 2.477 | 1.467
MLT5A | BRISBANE, MILTON | Urban | 100 | 0 | 0.817 | 2.134 | 1.6916 |  | 4 | 11712.99 | 11712.99 | 9.73e-05 | 9.73e-05
MLT6A | KELVIN GROVE | Urban | 5 | 0 | 3.423 | 1.753
MLT8B | KELVIN GROVE | Urban | 19 | 0 | 0.257 | 2.134 | 0.024422 |  | 1 | 24 | 24 | 2.03e-06 | 2.03e-06
MLTWHP12 | AUCHENFLOWER, MILTON | Urban | 109 | 0 | 2.624 | 1.734 |  | 0.024846 | [5 empty] | 1 | 2283.61 | 7.17e-06
MLY1 | BELLTHORPE, BOOROOBIN, MALENY, REESVILLE, STANMORE | Rural short | 769.5 | 72.922 | 0.913 | 1.482
MLY3 | CONONDALE, CURRAMORE, ELAMAN CREEK, MALENY, REESVI | Rural short | 2024.5 | 75.471 | 2.079 | 3.982
MLY4 | MALENY, MONTVILLE, NORTH MALENY, WITTA | Rural short | 614 | 30.67 | 0.723
MLY6 | BALD KNOB, BALMORAL RIDGE, DIAMOND VALLEY, EUDLO, | Rural short | 580 | 35.675 | 0.114 | 1.474
MMC19B | BENOWA, BROADBEACH WATERS, BUNDALL | Urban | 1111.5 | 4.975 | 4.775 | 3.886 | 12.58 | 3.0829 | 9 | 501001.3 | 501001.3 | 0.001153 | 0.001153 | 17 | 122776.9 | 0.000381
MMC20A | CLEAR ISLAND WATERS | Urban | 836 | 0.498 | 3.92 | 2.058 | 0.001315 | 0.008696 | 1 | 73.9167 | 73.9167 | 1.01e-06 | 1.01e-06 | 1 | 488.8 | 9.53e-07
MMC21A | CLEAR ISLAND WATERS, MERRIMAC | Rural short | 10 | 1.644 | 3.518 | 0.8
MMC22A | BENOWA, CARRARA | Urban | 1526 | 2.366 | 12.079 | 5.564 | 1.058 | 0.40896 | 9 | 47488.42 | 47488.42 | 0.000243 | 0.000243 | 2 | 18356.72 | 4.67e-05
MMC24A | CLEAR ISLAND WATERS, MERMAID WATERS, ROBINA | Urban | 1084 | 0.533 | 8.927 | 2.763
MMC28A | BROADBEACH WATERS, CARRARA, CLEAR ISLAND WATERS, M | Urban | 823 | 1.891 | 6.191 | 2.725 | 0.10209 | 0.45165 | 10 | 4402.96 | 4402.96 | 3.97e-05 | 3.97e-05 | 5 | 19478.22 | 7.25e-05
MMC30A | BROADBEACH WATERS, MERMAID WATERS | Urban | 312 | 0.121 | 3.444 | 1.048 | 0.91326 | 0.019705 | 4 | 35002.38 | 35002.38 | 0.000398 | 0.000398 | 1 | 755.25 | 1.44e-05
MMC31A | MERMAID WATERS | Urban | 38 | 0 | 1.697 | 2.763
MMC32A | CLEAR ISLAND WATERS, MERRIMAC | Urban | 11 | 0.908 | 4.885 | 2.21 |  | 1.5808 | [5 empty] | 2 | 787.456 | 4.75e-06
MMC33A | BROADBEACH WATERS, BUNDALL, SURFERS PARADISE | Urban | 1581 | 2.759 | 8.905 | 5.132 | 10.2994 | 0.67808 | 14 | 498448 | 498238.8 | 0.004924 | 0.004923 | 9 | 32816.24 | 0.000145
MOREXMEA | VERADILLA | Rural short | 3 | 0 | 0.018
MRB2 | ESK, GLEN ESK, MOOMBRA, MURRUMBA, TOOGOOLAWAH, WIV | Rural short | 51 | 34.547 | 0.074 | 0.152
MRD6 | SPRING HILL | Urban | 258.1 | 0 | 0.649 |  | 0.03565 |  | 1 | 3609.96 |  | 0.000915
MRE1 | MURARRIE | Urban | 306.1 | 1.104 | 3.029 | 3.315
MRE2 | CANNON HILL, MURARRIE | Urban | 594.9 | 5.131 | 3.052 | 4.744 | 0.13808 | 0.21154 | 4 | 2114.249 | 2114.249 | 9.77e-06 | 9.77e-06 | 4 | 3238.975 | 2.26e-05
MRE3 | CANNON HILL, MURARRIE, TINGALPA | Urban | 641.5 | 3.089 | 1.11 | 3.468 | 0.13853 | 0.65794 | 9 | 2351.717 | 2190.75 | 1.34e-05 | 1.24e-05 | 5 | 11169.25 | 4.47e-05
MRE4A | MURARRIE | Urban | 16 | 0 | 2.453 | 3.792
MRE5A | MURARRIE | Urban | 4 | 0 | 1.608 | 3.201
MRE6A | MURARRIE | Urban | 3 | 0 | 1.608 | 1.982
MRE8 | MURARRIE, TINGALPA | Urban | 223 | 2.587 | 1.863 | 5.03 | 12.6821 | 0.29627 | 2 | 60836.1 | 60836.1 | 0.000223 | 0.000223 | 3 | 1421.2 | 6.43e-06
MRE9 | MURARRIE | Urban | 2 | 0 | 1.049 | 1.524
MRK1 | YEERONGPILLY | Urban | 40 | 0.402 | 1.606 | 0.61
MRK2 | MOOROOKA | Urban | 630 | 2.155 | 0.106 | 2.915 | 0.35108 | 0.23829 | 3 | 13264.8 | 13264.8 | 0.000164 | 0.000164 | 3 | 9003.42 | 3.45e-05
MRK3 | MOOROOKA, YEERONGPILLY, YERONGA | Urban | 1235 | 4.21 | 1.737 | 2.42 | 3.3784 | 0.38452 | 7 | 253419.3 | 253419.3 | 0.002509 | 0.002509 | 4 | 28843.3 | 0.000115
MRK5A | ANNERLEY, MOOROOKA, TARRAGINDI | Urban | 1613.7 | 6.515 | 0.324 | 3.214
MRK6 | MOOROOKA, TARRAGINDI, YEERONGPILLY, YERONGA | Urban | 1795 | 4.403 | 0.701 | 2.906 | 0.016957 | 0.3463 | 6 | 1348.567 | 1348.567 | 3.85e-05 | 3.85e-05 | 8 | 27540.67 | 0.000129
MRK7A | MOOROOKA, YEERONGPILLY | Urban | 75 | 0.438 | 2.299 | 3.372 | 0.75588 |  | 3 | 2455.533 | 2455.533 | 0.000149 | 0.000149
MRK8 | MOOROOKA, YEERONGPILLY | Urban | 163 | 1.134 | 0.802 | 0.991 | 0.000316 | 0.1614 | 1 | 9.1333 | 9.1333 | 1.01e-06 | 1.01e-06 | 3 | 4671.77 | 1.9e-05
MRK9 | MOOROOKA | Urban | 1116 | 2.962 | 0.283 | 2.191 | 0.14941 | 0.39074 | 3 | 8966.217 | 8966.217 | 0.000114 | 0.000114 | 8 | 23448.56 | 0.000106
MSA1 | MOOROOKA | Urban | 1
MST20B | BRISBANE, SPRING HILL | Urban | 266 | 0 | 2.059 | 1.289
MSV1 | CAFFEY, LEFT HAND BRANCH, MT SYLVIA, UPPER TENTHIL | Rural short | 134 | 29.403 | 0 | 0.572
MSV2 | BLACK DUCK CREEK, EAST HALDON, JUNCTION VIEW, LEFT | Rural short | 167 | 49.828 | 0 | 0.667
MTB13A | TAMBORINE MOUNTAIN | Rural short | 1465.5 | 21.466 | 1.272 | 3.351
MTB15A | BEECHMONT, BENOBBLE, BINNA BURRA, CANUNGRA, FERNY | Rural short | 760 | 90.352 | 2.536 | 2.877
MTB16A | BENOBBLE, BOYLAND, WONGLEPONG | Rural short | 387 | 27.628 | 2.387 | 1.277
MTB17A | GUANABA, MAUDSLAND, TAMBORINE MOUNTAIN | Rural short | 477 | 30.605 | 1.912 | 1.322
MTB1B | TAMBORINE MOUNTAIN | Rural short | 1428 | 23.26 | 0.568 | 2.706
MTB2A | BENOBBLE, BIDDADDABA, BOYLAND, CANUNGRA, SARABAH, | Rural short | 687 | 70.725 | 0.445 | 1.791
MTB3A | CLAGIRABA, GUANABA, MAUDSLAND, MOUNT NATHAN, TAMBO | Rural short | 1023 | 32.836 | 4.278 | 2.796
MTG11A | UPPER MT GRAVATT, WISHART | Urban | 859.3 | 4.785 | 0.397 | 1.847 | 5.5414 | 0.11121 | 12 | 351566.4 | 46552.07 | 0.002354 | 0.001416 | 4 | 7055.45 | 3.14e-05
MTG12B | MT GRAVATT | Urban | 433.3 | 1.854 | 0.239 | 1.505 | 1.8802 | 0.17849 | 8 | 73350.74 | 73350.74 | 0.001019 | 0.001019 | 3 | 6963.107 | 2.18e-05
MTG13A | UPPER MT GRAVATT, WISHART | Urban | 1844.5 | 4.47 | 4.097 | 4.195 | 8.1983 | 0.7876 | 7 | 443777.4 | 126003.7 | 0.00378 | 0.001914 | 9 | 42632.97 | 0.000139
MTG15A | MANSFIELD, WISHART | Urban | 709.7 | 2.457 | 2.487 | 1.486 | 0.003498 | 0.74184 | 3 | 243.5667 | 117.6667 | 3.04e-06 | 2.03e-06 | 16 | 51655.01 | 0.000222
MTG16A | MT GRAVATT EAST | Urban | 678.5 | 2.95 | 0.249 | 1.155 | 0.45025 | 0.1138 | 9 | 42258.64 | 42258.64 | 0.000272 | 0.000272 | 6 | 10680.85 | 5.31e-05
MTG3A | MACGREGOR, MT GRAVATT, NATHAN, UPPER MT GRAVATT | Urban | 1151.5 | 6.094 | 2.678 | 3.982 | 5.2294 | 0.033645 | 13 | 239008.7 | 239008.7 | 0.001367 | 0.001367 | 2 | 1537.77 | 5.14e-06
MTG4B | HOLLAND PARK WEST, MT GRAVATT, NATHAN | Rural short | 1533 | 9.757 | 1.761 | 4.255
MTG5A | MT GRAVATT EAST | Urban | 517.5 | 2.102 | 0.514 | 2.382 | 2.148 | 0.95971 | 5 | 56772.58 | 56772.58 | 0.000709 | 0.000709 | 8 | 25365.46 | 0.000112
MTG7A | MANSFIELD, MT GRAVATT EAST, UPPER MT GRAVATT | Urban | 1646.5 | 8.225 | 1.846 | 4.173 | 5.4687 | 2.0317 | 13 | 290714.9 | 256658.9 | 0.001745 | 0.001679 | 26 | 108003.8 | 0.000492
MTG8A | MT GRAVATT, MT GRAVATT EAST | Urban | 858.2 | 3.441 | 0.625 | 2.305 | 1.2558 | 0.24142 | 1 | 82173.66 | 82173.66 | 0.000886 | 0.000886 | 4 | 15797.55 | 5.16e-05
MTNQBI9 | PINKENBA | Urban | 9 | 3.019 | 1.511 | 4.079 | 0.07711 |  | 4 | 3080 | 3080 | 4.46e-05 | 4.46e-05
MTNWLP5 | PINKENBA | Urban | 97 | 3.497 | 2.838 | 2.382 | 31.9308 |  | 4 | 14307.4 | 12767.4 | 0.000134 | 0.000108
MWMRBK11 | COLLINGWOOD PARK, REDBANK, RIVERVIEW | Rural short | 976 | 10.698 | 0.658 | 2.623
MWMRBK8 | REDBANK | Rural short | 2 | 1.997 | 0.222 | 0.457
NBR11A | DIDDILLIBAH, KIELS MOUNTAIN, NAMBOUR, ROSEMOUNT, W | Rural short | 1399 | 23.732 | 1.516 | 2.782
NBR12A | BURNSIDE, DULONG, FLAXTON, HIGHWORTH, IMAGE FLAT, | Rural short | 1763 | 51.454 | 5.096 | 4.154
NBR13A | BURNSIDE, NAMBOUR | Urban | 1288 | 7.421 | 3.795 | 3.487 | 3.157 | 1.1547 | 13 | 194591.7 | 179984.9 | 0.00291 | 0.002844 | 7 | 71171.96 | 0.000217
NBR15A | IMAGE FLAT, KIAMBA, KULANGOOR, NAMBOUR, YANDINA | Rural short | 539.5 | 25.772 | 1.216 | 1.81
NBR16A | NAMBOUR | Urban | 359 | 1.673 | 0.747 | 1.277 | 0.82479 | 0.23824 | 1 | 7665 | 7665 | 0.00037 | 0.00037 | 1 | 2214 | 1.83e-05
NBR17A | NAMBOUR | Urban | 67 | 0.99 | 1.421 | 2.382 | 0.21334 | 0.035754 | 1 | 1407 | 1407 | 6.79e-05 | 6.79e-05 | 1 | 235.8 | 9.13e-07
NBR2B | NAMBOUR | Urban | 567 | 4.063 | 1.729 | 4.859 | 0.97372 | 3.2199 | 4 | 22332.31 | 22332.31 | 0.001156 | 0.001156 | 7 | 73848 | 0.000234
NBR3B | NAMBOUR | Urban | 1300 | 6.172 | 1.95 | 4.554 | 2.1663 | 0.44117 | 13 | 69914.28 | 69914.28 | 0.002821 | 0.002821 | 6 | 14238.22 | 0.000155
NBR4A | BLI BLI, IMAGE FLAT, MAROOCHY RIVER, NAMBOUR, NORT | Rural short | 796.5 | 44.656 | 2.329 | 2.725
NBR5A | COOLOOLABIN, IMAGE FLAT, KIAMBA, KUREELPA, NAMBOUR | Rural short | 1306 | 31.162 | 0.967 | 2.953
NBR7A | BLI BLI, NAMBOUR, ROSEMOUNT | Rural short | 2148 | 49.97 | 5.059 | 4.916
NBR8A | NAMBOUR | Urban | 8 | 0 | 1.778 | 3.353 |  |  | 1 | 168 | 168 | 8.11e-06 | 8.11e-06
NDH1 | NORTHGATE, NUNDAH, VIRGINIA, WAVELL HEIGHTS | Urban | 1122 | 2.235 | 0.374 | 2.496 | 2.2195 | 0.12015 | 10 | 127831.5 | 127831.5 | 0.001283 | 0.001283 | 3 | 6919.833 | 2.46e-05
NDH10 | NORTHGATE, NUNDAH, VIRGINIA, WAVELL HEIGHTS | Urban | 722 | 3.115 | 1.745 | 1.924 | 0.15806 | 0.69347 | 7 | 9641.031 | 9641.031 | 0.000113 | 0.000113 | 10 | 42298.09 | 0.000143
NDH12 | NUNDAH | Urban | 797 | 2.142 | 1.862 | 1.143 | 1.4202 | 0.085361 | 3 | 144146.8 | 144146.8 | 0.000802 | 0.000802 | 3 | 8664.1 | 2.78e-05
NDH5A | HENDRA, NORTHGATE, NUNDAH | Urban | 2135 | 4.622 | 1.072 | 2.61 | 0.23629 | 0.31223 | 11 | 28047.08 | 28047.08 | 0.000263 | 0.000263 | 7 | 37060.71 | 0.000102
NDH6 | NUNDAH, WAVELL HEIGHTS | Urban | 1951.5 | 5.629 | 0.297 | 3.201 | 0.14809 | 0.42234 | 14 | 14563.85 | 14563.85 | 0.000136 | 0.000136 | 11 | 41534.28 | 0.000161
NDH7 | NORTHGATE, NUNDAH, VIRGINIA | Urban | 1590.5 | 4.598 | 1.913 | 3.353 | 0.026366 | 0.078197 | 8 | 1663.047 | 1663.047 | 8.11e-06 | 8.11e-06 | 2 | 4932.31 | 3.06e-05
NDH8 | NUNDAH, WAVELL HEIGHTS | Urban | 1227.5 | 2.818 | 1.826 |  | 2.9486 |  | 6 | 204091.9 | 204091.9 | 0.003763 | 0.003763
NDH9 | NUNDAH | Urban | 309.5 | 0.656 | 1.256 | 5.297 | 0.26785 | 0.44235 | 4 | 5504.753 | 5504.753 | 5.34e-05 | 5.34e-05 | 2 | 9091.22 | 5.86e-05
NGE12 | BANYO, NORTHGATE, NUDGEE | Urban | 1614 | 6.408 | 3.489 | 3.425 | 0.070727 | 0.16218 | 9 | 4732.203 | 4579.42 | 0.000119 | 0.000117 | 4 | 10851.22 | 3.55e-05
NGE13 | BANYO, NORTHGATE | Urban | 235 | 2.473 | 1.99 | 4.801 | 0.006941 |  | 1 | 80.2333 | 80.2333 | 1.01e-06 | 1.01e-06
NGE1A | BANYO | Urban | 2
NGE2A | NORTHGATE | Urban | 288 | 1.376 | 1.353 | 1.41 | 0.86362 |  | 2 | 24518 | 24518 | 0.000259 | 0.000259
NGE2B | BANYO | Urban | 49 | 0 | 4.641 | 4.23
NGE4A | BANYO, NORTHGATE | Urban | 178 | 1.51 | 2.773 | 2.591 | 0.51995 | 0.004608 | 3 | 8124.567 | 8124.567 | 0.000186 | 0.000186 | 1 | 72 | 2.03e-06
NGE4B | BANYO, NUDGEE, NUDGEE BEACH | Urban | 757 | 7.337 | 4.757 | 3.83 | 1.569 | 0.6509 | 7 | 43224.6 | 43224.6 | 0.000831 | 0.000831 | 5 | 17931.73 | 7.1e-05
NGI1B | DONNYBROOK, MELDALE, NINGI, TOORBUL | Rural short | 1304 | 35.154 | 1.007 | 3.01
NGI2B | BEACHMERE, NINGI | Rural short | 754 | 16.202 | 1.964 | 2.521
NGI3A | BEACHMERE, CABOOLTURE, NINGI | Rural short | 1297 | 33.624 | 2.432 | 3.277
NIP10A | NORTH IPSWICH, WOODEND | Urban | 6 | 0 | 2.53 | 3.22
NIP1A | COALFALLS, SADLIERS CROSSING, WOODEND | Urban | 919 | 5.458 | 0.334 | 2.21 | 0.31142 | 2.0539 | 10 | 25033.27 | 25033.27 | 0.000253 | 0.000253 | 8 | 165106.1 | 0.000424
NIP2A | BRASSALL, NORTH IPSWICH | Urban | 951 | 7.489 | 1.502 | 2.572 | 1.0685 | 0.31361 | 14 | 57273.2 | 57178.48 | 0.000126 | 0.000125 | 4 | 16810.08 | 8.54e-05
NIP3A | EAST IPSWICH, NORTH IPSWICH | Rural short | 536.5 | 3.937 | 0.596 | 1.135
NIP4A | BRASSALL, CHUWAR, KHOLO, MUIRLEA, NORTH IPSWICH, P | Rural short | 1491 | 31.711 | 0.397 | 3.563
NIP5A | CHUWAR, MOORES POCKET, NORTH IPSWICH, TIVOLI | Urban | 1243 | 7.679 | 0.432 | 2.858 | 2.0341 | 0.18221 | 7 | 179229 | 179229 | 0.001287 | 0.001287 | 2 | 16054.82 | 5.15e-05
NIP5B | BRASSALL | Urban | 950 | 5.237 | 0.56 | 3.353 | 0.014261 | 0.17564 | 5 | 648.8681 | 648.8681 | 5.07e-06 | 5.07e-06 | 3 | 7991.17 | 4.35e-05
NIP6A | NORTH IPSWICH | Urban | 281.5 | 2.105 | 0.319 | 1.353 | 9.1918 | 0.25819 | 5 | 57802.14 | 57802.14 | 0.000261 | 0.000261 | 1 | 1623.605 | 6.77e-06
NIP7A | NORTH IPSWICH | Urban | 11 | 0 | 2.295 | 3.734
NMC13A | JIMBOOMBA, NORTH MACLEAN | Rural short | 737 | 7.795 | 8.349 | 3.83
NMC15A | CHAMBERS FLAT, GREENBANK, MUNRUBEN, NORTH MACLEAN, | Rural short | 369 | 24.033 | 0.465 | 1.962
NMC16A | GREENBANK, MUNRUBEN, PARK RIDGE, PARK RIDGE SOUTH | Rural short | 908 | 22.883 | 1.572 | 2.972
NMC1B | GREENBANK, NEW BEITH, NORTH MACLEAN | Rural short | 933 | 27.689 | 4.803 | 4.401
NMC2A | GREENBANK, NEW BEITH | Rural short | 1881 | 19.595 | 7.701 | 5.678
NMC3A | GREENBANK, MUNRUBEN, PARK RIDGE, PARK RIDGE SOUTH | Rural short | 1010 | 33.336 | 2.142 | 3.582
NMC5A | GREENBANK, JIMBOOMBA, NORTH MACLEAN, SHAILER PARK, | Rural short | 1044 | 31.098 | 4.801 | 1.543
NMK10OLD | WINDSOR | Urban | 739 | 2.39 | 2.837
NMK18OLD | ALDERLEY, GRANGE, NEWMARKET | Urban | 1326 | 4.802 | 0.631 |  |  | 0.14577 | [5 empty] | 1 | 7680 | 4.87e-05
NMK26OLD | HERSTON, KELVIN GROVE | Urban | 1795 | 5.05 | 4.182 |  | 0.001512 |  | 1 | 59.8667 | 59.8667 | 1.01e-06 | 1.01e-06
NMK5OLD | KELVIN GROVE, NEWMARKET, WILSTON | Urban | 1652.5 | 4.685 | 1.825
NMK7OLD | ALDERLEY, ASHGROVE, KELVIN GROVE, NEWMARKET | Urban | 1158 | 4.495 | 2.859 |  | 0.002469 |  | 1 | 138.05 | 138.05 | 1.01e-06 | 1.01e-06
NPD1 | JOYNER, KURWONGBAH, WHITESIDE | Urban | 5 | 2.265 | 0.176 | 0.953
NRA12A | NARANGBA | Urban | 72 | 2.432 | 0.617 | 1.353
NRA13A | DAKABIN, KALLANGUR, KURWONGBAH, NARANGBA | Rural short | 2244 | 14.084 | 5.645 | 5.278
NRA15A | BURPENGARY, NARANGBA | Rural short | 704 | 7.376 | 4.821 | 1.353
NRA16A | DAKABIN, KURWONGBAH, NARANGBA | Rural short | 273 | 17.574 | 1.517 | 0.934
NRA1A | KURWONGBAH, MOORINA, MORAYFIELD, NARANGBA | Rural short | 864 | 45.205 | 1.518 | 3.334
NRA2A | NARANGBA | Urban | 56 | 1.814 | 1.118 | 3.22
NRA3B | NARANGBA | Rural short | 24 | 1.895 | 1.235 | 0.616
NRA5A | NARANGBA | Rural short | 2042 | 10.293 | 9.853 | 5.468
NRG10 | NERANG | Urban | 1474 | 6.309 | 4.091 | 3.658 | 0.0891 | 0.58205 | 7 | 6206.617 | 6206.617 | 0.000125 | 0.000125 | 6 | 40545.14 | 0.000233
NRG12A | CARRARA, NERANG | Urban | 1309.3 | 1.587 | 4.463 | 3.163 | 0.04825 | 1.5666 | 9 | 2958.413 | 2958.413 | 4.11e-05 | 4.11e-05 | 5 | 96056.2 | 0.000336
NRG13A | CARRARA | Urban | 1487 | 1.438 | 11.55 | 3.887 | 0.68249 | 0.014435 | 7 | 37683.59 | 37683.59 | 0.001502 | 0.001502 | 2 | 797 | 7.91e-06
NRG14A | CARRARA, REEDY CREEK, WORONGARY | Rural short | 642 | 12.058 | 5.022 | 3.62
NRG15A | HIGHLAND PARK, NERANG | Urban | 998 | 0.25 | 5.368 | 2.317 | 0.05539 | 0.25889 | 2 | 3912.935 | 3912.935 | 5.93e-05 | 5.93e-05 | 2 | 18289.04 | 0.000109
NRG16A | ADVANCETOWN, BEECHMONT, CLAGIRABA, GILSTON, LOWER | Rural short | 1920 | 35.232 | 7.694 | 5.068
NRG17A | ASHMORE, MOLENDINAR, NERANG | Urban | 1451 | 4.566 | 3.509 | 2.686 | 1.5839 | 0.66103 | 6 | 93199.6 | 93199.6 | 0.001474 | 0.001474 | 3 | 38896.4 | 0.000154
NRG20A | NERANG | Urban | 337 | 2.6 | 1.247 | 3.068 |  | 1.0349 | [5 empty] | 2 | 24992 | 7.2e-05
NRG21A | HIGHLAND PARK, WORONGARY | Urban | 714 | 0 | 6.206 | 2.21 | 0.001249 | 0.015597 | 1 | 82.1833 | 82.1833 | 1.01e-06 | 1.01e-06 | 1 | 1026.08 | 9.81e-06
NRG22A | NERANG | Urban | 1053 | 6.507 | 4.954 | 3.449 | 0.4243 | 0.30968 | 13 | 16705.79 | 12481.44 | 0.000139 | 0.00012 | 5 | 12192.69 | 6.2e-05
NRG2A | HIGHLAND PARK, WORONGARY | Urban | 983 | 0 | 5.786 | 2.515 | 0.002124 | 0.12059 | 1 | 115.2333 | 115.2333 | 1.01e-06 | 1.01e-06 | 1 | 6543.46 | 4.31e-05
NRG4 | CARRARA, HIGHLAND PARK, NERANG | Urban | 1075 | 1.768 | 7.449 | 4.554 | 0.009626 |  | 3 | 417.7333 | 294.3 | 3.04e-06 | 2.03e-06
NRG5A | NERANG | Urban | 360 | 3.274 | 0.355 | 4.82 | 0.46711 | 0.72981 | 3 | 6119.677 | 6119.677 | 4.63e-05 | 4.63e-05 | 3 | 9561.36 | 5.14e-05
NRG6 | CARRARA, NERANG, WORONGARY | Urban | 930 | 4.901 | 3.388 | 3.582 | 0.42853 | 2.1146 | 5 | 11245.61 | 11245.61 | 6.76e-05 | 6.76e-05 | 4 | 55492.51 | 0.00011
NRG8B | NERANG | Urban | 254 | 1.637 | 1.926 | 2.801 | 8.5127 | 1.2589 | 5 | 109096.8 | 109096.8 | 0.000532 | 0.000532 | 4 | 16133.19 | 3.68e-05
NRG9 | ADVANCETOWN, GILSTON, HIGHLAND PARK, NERANG | Rural short | 2014 | 31.241 | 8.183 | 5.716
NSD1A | FORTITUDE VALLEY, NEWSTEAD, TENERIFFE | Urban | 397 | 1.279 | 1.661 | 4.001 | 0.10952 |  | 3 | 2167.012 | 2167.012 | 1.22e-05 | 1.22e-05
NSD29A | NEW FARM, NEWSTEAD | Urban | 634.5 | 0 | 4.701 | 2.42 | 0.001196 | 0.30644 | 1 | 48.85 | 48.85 | 1.01e-06 | 1.01e-06 | 1 | 12519.66 | 3.99e-05
NSD2B | BOWEN HILLS, FORTITUDE VALLEY | Urban | 999 | 2.4 | 4.385 | 3.106
NSD30B | BOWEN HILLS, HERSTON, WINDSOR | Urban | 1083 | 3.145 | 5.063 | 3.048
NSD3A | BOWEN HILLS | Urban | 214 | 0.724 | 2.449 | 3.525 | 1.2903 | 0.00039 | 3 | 23595.97 | 23595.97 | 0.000228 | 0.000228 | 1 | 7.14 | 1.03e-06
NSD6B | NEWSTEAD, TENERIFFE | Urban | 1393 | 0 | 2.526 | 4.001 | 0.000522 | 0.012106 | 1 | 28.3667 | 28.3667 | 1.01e-06 | 1.01e-06 | 1 | 657.66 | 2.29e-06
NSD8A | FORTITUDE VALLEY, NEW FARM, NEWSTEAD, TENERIFFE | Urban | 1310 | 0.568 | 3.615 | 3.334 | 5.5247 | 0.009135 | 2 | 268614 | 268614 | 0.003043 | 0.003043 | 1 | 444.15 | 1.92e-06
NSD9A | NEWSTEAD | Urban | 509.5 | 0.343 | 3.156 | 2.134 | 0.01362 | 0.025391 | 3 | 514.95 | 514.95 | 3.04e-06 | 3.04e-06 | 1 | 960 | 4.06e-06
NSW16A | SLACKS CREEK, SPRINGWOOD | Urban | 773 | 3.579 | 1.069 | 3.353 | 11.481 | 0.047954 | 2 | 481228 |  | 0.001565 |  | 1 | 2010 | 6.08e-06
NSW17 | DAISY HILL, SPRINGWOOD | Urban | 1302 | 8.714 | 1.985 | 4.314
NSW19 | UNDERWOOD | Urban | 101.5 | 1.064 | 2.422 | 4.268
NSW22B | EIGHT MILE PLAINS, KURABY, UNDERWOOD | Urban | 1575.3 | 5.598 | 6.443 | 4.249 | 2.9411 | 0.1868 | 11 | 187190.8 | 187190.8 | 0.003107 | 0.003107 | 4 | 11889.31 | 5.83e-05
NSW24 | ROCHEDALE SOUTH, SPRINGWOOD | Urban | 578 | 1.473 | 1.205 | 3.868 | 0.021337 | 0.4721 | 3 | 330.8333 | 330.8333 | 3.04e-06 | 3.04e-06 | 1 | 7320 | 3.04e-05
NSW25 | UNDERWOOD | Urban | 351.2 | 3.572 | 0.587 | 3.029 |  | 0.80305 | [5 empty] | 4 | 20623.12 | 9.81e-05
NSW26 | SLACKS CREEK, SPRINGWOOD | Urban | 1150.5 | 6.014 | 0.557 | 2.877 | 10.6231 |  | 16 | 560352.7 | 101548 | 0.003638 | 0.002472
NSW28 | PRIESTDALE, ROCHEDALE, ROCHEDALE SOUTH, SPRINGWOOD | Urban | 1057 | 6.352 | 2.995 | 2.744 | 0.095137 | 0.065576 | 6 | 6747.65 | 6747.65 | 7.53e-05 | 7.53e-05 | 2 | 4651 | 1.71e-05
NSW31A | SLACKS CREEK, UNDERWOOD | Urban | 127 | 1.61 | 0.323 | 3.22 | 0.034468 | 0.93745 | 2 | 281.9 | 281.9 | 2.03e-06 | 2.03e-06 | 1 | 7667 | 4.16e-05
NSW33A | UNDERWOOD, WOODRIDGE | Urban | 647 | 4.206 | 2.931 | 4.801 | 1.9905 | 0.27503 | 5 | 62962.38 | 62962.38 | 0.000746 | 0.000746 | 3 | 8699.75 | 2.39e-05
NSW35A | SLACKS CREEK | Urban | 283 | 2.049 | 0.128 | 3.62 | 0.009025 | 0.68938 | 1 | 105.85 | 105.85 | 1.01e-06 | 1.01e-06 | 1 | 8085 | 3.55e-05
NSW3A | KURABY, UNDERWOOD | Urban | 1968.7 | 2.635 | 8.367 | 4.897 | 0.55232 | 0.028957 | 9 | 34364.44 | 34364.44 | 0.000171 | 0.000171 | 4 | 1801.665 | 3.7e-05
NSW5A | ROCHEDALE SOUTH, SPRINGWOOD | Urban | 1268 | 7.188 | 1.222 | 3.06 | 1.5786 | 0.26706 | 17 | 120476.6 | 84892.55 | 0.000332 | 0.000244 | 5 | 20381.95 | 9.4e-05
NSW7A | SPRINGWOOD | Urban | 152 | 0.928 | 0.682 | 2.363 | 0.073144 |  | 1 | 2416 | 2416 | 0.000153 | 0.000153
NSW8A | ROCHEDALE, ROCHEDALE SOUTH, UNDERWOOD | Urban | 1817 | 8.459 | 1.137 | 4.061 | 0.23132 | 0.50557 | 8 | 15924.26 | 15623.82 | 0.00019 | 0.000189 | 6 | 34803.72 | 0.000136
NVL10 | NOOSA HEADS, NOOSAVILLE | Urban | 588 | 1.409 | 8.118 | 3.944 |  | 1.474 | [5 empty] | 2 | 32526 | 0.000119
NVL12 | NOOSA HEADS, NOOSAVILLE | Urban | 556 | 3.766 | 1.236 | 1.486 | 1.0089 | 0.13147 | 7 | 76925.32 | 76925.32 | 0.001106 | 0.001106 | 2 | 10023.96 | 5.22e-05
NVL14A | NOOSA NORTH SHORE, NOOSAVILLE | Urban | 1687 | 2.979 | 2.716 | 3.696 | 0.34379 | 0.82798 | 3 | 26739.35 | 26739.35 | 0.000252 | 0.000252 | 4 | 64398.48 | 0.000169
NVL15A | NOOSAVILLE | Rural short | 256 | 0.572 | 5.09 | 0.553
NVL16A | NOOSA HEADS | Urban | 329 | 0 | 7.567 | 2.725 |  | 0.052043 | [5 empty] | 1 | 848 | 4.06e-06
NVL19A | NOOSAVILLE | Urban | 732 | 2.071 | 4.217 | 3.544 | 0.84229 | 0.009826 | 3 | 28288.66 | 28288.66 | 0.000253 | 0.000253 | 1 | 330 | 2.03e-06
NVL24A | NOOSA HEADS, SUNSHINE BEACH | Urban | 1340.5 | 5.266 | 5.006 | 2.953 | 1.6984 | 0.67918 | 17 | 79876.89 | 79876.89 | 0.000876 | 0.000876 | 4 | 31941.88 | 0.000142
NVL26A | NOOSAVILLE | Urban | 578 | 0 | 3.329 | 1.753 | 0.001217 | 0.26529 | 1 | 70.0667 | 70.0667 | 1.01e-06 | 1.01e-06 | 1 | 15274 | 7.1e-05
NVL27A | NOOSA HEADS | Urban | 1067 | 1.814 | 4.528 | 3.163 | 0.78414 | 1.5948 | 14 | 38037.21 | 38037.21 | 0.000336 | 0.000336 | 3 | 77361 | 0.000264
NVL28A | NOOSA HEADS, NOOSAVILLE | Urban | 1547 | 0.475 | 4.317 | 3.773 | 0.010745 | 0.01068 | 6 | 774.6667 | 556.1 | 6.08e-06 | 5.07e-06 | 2 | 770 | 4.06e-06
NVL3 | NOOSA HEADS, NOOSAVILLE, SUNRISE BEACH, SUNSHINE B | Urban | 2233.5 | 4.68 | 9.961 | 4.796 | 0.30372 | 0.66846 | 12 | 24081.1 | 24081.1 | 0.000102 | 0.000102 | 7 | 53001.07 | 0.000216
NVL5 | NOOSA HEADS, NOOSAVILLE | Rural short | 1242 | 5.45 | 3.463 | 2.34
NVL6 | NOOSA HEADS, NOOSAVILLE | Urban | 566.5 | 2.159 | 1.817 | 3.22 | 0.001934 |  | 1 | 54.2333 | 54.2333 | 1.01e-06 | 1.01e-06
NVL8B | NOOSAVILLE, TEWANTIN | Rural short | 469 | 1.235 | 2.525 | 0.934
NVL9 | CASTAWAYS BEACH, MARCUS BEACH, NOOSA HEADS, PEREGI | Rural short | 1478.5 | 11.053 | 3.99 | 3.655
ORE2 | BROADBEACH | Urban | 151 | 0 | 0.408 |  | 0.022244 |  | 1 | 585.48 | 585.48 | 2.07e-06 | 2.07e-06
OXL10A | OXLEY | Urban | 122 | 2.084 | 1.596 | 3.048 | 0.015679 | 0.43918 | 1 | 198 | 198 | 3.65e-06 | 3.65e-06 | 3 | 5545.96 | 1.97e-05
OXL11A | DURACK, INALA, OXLEY | Urban | 1486 | 3.797 | 3.212 | 4.077 | 0.009232 | 0.73906 | 6 | 390.7301 | 390.7301 | 6.08e-06 | 6.08e-06 | 7 | 31278.21 | 0.000144
OXL4A | OXLEY | Urban | 938 | 4.129 | 1.807 | 1.62 | 2.4668 | 1.2963 | 13 | 243746.7 | 243746.7 | 0.000888 | 0.000888 | 20 | 128083 | 0.000544
OXL5A | ARCHERFIELD, OXLEY, ROCKLEA | Urban | 50.5 | 2.282 | 3.829 | 3.963 | 0.20245 | 0.70395 | 3 | 908.8 | 908.8 | 8.11e-06 | 8.11e-06 | 3 | 3160 | 1.42e-05
OXL5B | OXLEY | Urban | 22 | 0 | 0.602
OXL8A | OXLEY, ROCKLEA | Urban | 83 | 2.158 | 1.228 | 2.458 | 2.2079 |  | 4 | 18874.58 | 5754.583 | 0.000103 | 2.23e-05
OXL8B | CORINDA, OXLEY, SEVENTEEN MILE ROCKS | Urban | 1664.5 | 8.01 | 3.608 | 3.982 | 4.1131 | 1.4838 | 19 | 227573.1 | 1783.267 | 0.001707 | 1.62e-05 | 18 | 82096 | 0.000375
PBH1 | CURRUMBIN WATERS, ELANORA | Urban | 1418 | 6.577 | 5.7 | 3.543 | 2.8043 | 0.1463 | 8 | 202192.4 | 202192.4 | 0.00295 | 0.00295 | 4 | 10548 | 6.69e-05
PBH2B | ELANORA, PALM BEACH | Urban | 2246.5 | 3.727 | 6.424 | 4.596 | 0.86499 | 1.8188 | 8 | 71548.56 | 71548.56 | 0.002331 | 0.002331 | 12 | 150443 | 0.000537
PBH3 | PALM BEACH | Urban | 1088.5 | 2.359 | 0.673 | 3.201 | 0.86475 | 1.6217 | 6 | 34866.6 | 34810.18 | 0.001132 | 0.001131 | 8 | 65385.7 | 0.000235
PBH4 | ELANORA, PALM BEACH | Urban | 1028 | 0.46 | 4.762 | 2.058 | 0.67301 | 0.21695 | 5 | 32459.06 | 32459.06 | 0.001052 | 0.001052 | 3 | 10463.4 | 4.41e-05
PBH6 | PALM BEACH | Urban | 2280 | 4.99 | 0.299 | 4.214 | 1.0295 | 2.1719 | 17 | 93445.4 | 75535.4 | 0.002389 | 0.002344 | 36 | 197139.9 | 0.000762
PBH7A | ELANORA | Urban | 36 | 0 | 1.133 |  | 0.00571 |  | 1 | 1410.5 | 1410.5 | 4.61e-05 | 4.61e-05
PBH8A | CURRUMBIN WATERS, ELANORA | Urban | 1468 | 2.461 | 3.067 |  | 0.064199 | 0.59567 | 5 | 2801.177 | 2801.177 | 1.77e-05 | 1.77e-05 | 4 | 25990.44 | 0.000101
PCB1 | SURFERS PARADISE | Urban | 2 | 0 | 0.141 |  |  | 21.207 | [5 empty] | 2 | 1254 | 5.07e-06
PCB2 | SURFERS PARADISE | Urban | 2
PCH4 | CHERMSIDE | Urban | 2
PCH6 | CHERMSIDE | Urban | 3
PCH8 | CHERMSIDE | Urban | 2 | 0 | 0.322
PCH9 | CHERMSIDE | Urban | 8
PDA3 | SPRINGFIELD CENTRAL, SPRINGFIELD LAKES | Urban | 17 | 0 | 3.106
PDB13 | SPRINGFIELD CENTRAL, SPRINGFIELD LAKES | Urban | 1651 | 0 | 13.131 |  | 0.006253 | 0.007905 | 7 | 749.5333 | 749.5333 | 7.1e-06 | 7.1e-06 | 2 | 947.5 | 9.83e-06
PGN1B | DOONAN, PEREGIAN BEACH, WEYBA DOWNS | Rural short | 1624 | 15.144 | 1.135 | 3.618
PGN2B | PEREGIAN SPRINGS | Rural short | 519 | 0.255 | 3.419 | 0.553
PGN3A | PEREGIAN SPRINGS | Urban | 425 | 0 | 2.797 | 0.934
PGN6A | PEREGIAN SPRINGS | Urban | 1050 | 0 | 9.315 | 4.058 | 0.00184 | 0.62823 | 1 | 92 | 92 | 1.01e-06 | 1.01e-06 | 4 | 31407.87 | 0.000322
PGS3 | BROADBEACH, BROADBEACH WATERS | Urban | 277.3 | 0 | 0.928 |  | 0.000708 | 0.015281 | 1 | 22.1333 | 22.1333 | 1.01e-06 | 1.01e-06 | 2 | 477.68 | 2.39e-05
PKW11A | SOUTHPORT | Urban | 7 | 0 | 1.959 | 3.277
PKW4A | PARKWOOD, SOUTHPORT | Urban | 566 | 0 | 4.871 | 1.429
PMBWED19 | SOUTH BRISBANE, WEST END | Urban | 312.5 | 0 | 2.158 | 3.411 |  | 0.30222 | [5 empty] | 1 | 5779.8 | 1.5e-05
PMBWED4 | SOUTH BRISBANE | Urban | 51 | 0 | 1.189 | 1.467 |  | 0.14605 | [5 empty] | 1 | 249 | 1.01e-06
PMBWED7 | SOUTH BRISBANE | Urban | 231 | 0 | 2.19 | 4.592
PPE12B | STEIGLITZ | Rural short | 4 | 11.22 | 1.197 | 0.21
PPE13A | GILBERTON, NORWELL, PIMPAMA, WOONGOOLBA | Rural short | 140 | 28.6 | 0.594 | 1.905
PPE15A | PIMPAMA | Urban | 3 | 0 | 0.76 | 0.495 |  |  | 1 | 756 |  | 3.04e-06
PPE16A | JACOBS WELL, NORWELL, STEIGLITZ, WOONGOOLBA | Rural short | 363 | 23.883 | 2.195 | 0.895
PPE2B | PIMPAMA | Urban | 2 | 0 | 0.7 | 0.533 | 0.17329 |  | 1 | 458 |  | 2.03e-06
PPE3A | JACOBS WELL | Rural short | 735 | 5.597 | 9.555 | 2.172
PPE5A | COOMERA, PIMPAMA | Rural short | 1284.5 | 3.998 | 15.478 | 3.811
PPE6A | COOMERA, PIMPAMA, UPPER COOMERA | Rural short | 1327 | 21.205 | 7.932 | 1.924
PQSRGA85 | BRISBANE | CBD | 2 | 0 | 0.144 |  | 0.45766 |  | 1 | 636 | 636 | 0.000534 | 0.000534
PRG1 | POSTMANS RIDGE, PRINCE HENRY HEIGHTS, REDWOOD, WIT | Rural short | 431 | 22.112 | 0.389 | 1.258
PRG2A | BALLARD, BLANCHVIEW, BLUE MOUNTAIN HTS, HELIDON SP | Rural short | 916 | 98.271 | 2.358
PRG2B | LOCKYER, MURPHYS CREEK, POSTMANS RIDGE, WITHCOTT | Rural short | 183 | 31.638 | 1.203 | 3.506
PTR1 | MURARRIE | Urban | 3
PTR2 | MURARRIE | Urban | 4 | 0 | 0.551
PTR3 | MURARRIE | Urban | 2
PWC2 | CHEVALLUM, KIELS MOUNTAIN, PALMWOODS, WOOMBYE | Rural short | 997.5 | 18.621 | 2.015 | 3.258
PWC3 | DIAMOND VALLEY, EUDLO, LANDERS SHOOT, MOOLOOLAH VA | Rural short | 1261.5 | 45.388 | 4.262 | 4.001
PWC4 | COES CREEK, DULONG, FLAXTON, HUNCHY, LANDERS SHOOT | Rural short | 1779.3 | 86.656 | 0.868 | 3.926
PWC5 | BURNSIDE, COES CREEK, HUNCHY, PALMWOODS, WEST WOOM | Rural short | 1942.7 | 30.886 | 2.998 | 4.935
PWC6 | CHEVALLUM, EUDLO, ILKLEY, PALMWOODS, TANAWHA | Rural short | 1484 | 45.435 | 2.47 | 3.601
QAP4 | FORTITUDE VALLEY | Urban | 12 | 0 | 0.877 |  | 0.71542 |  | 1 | 936 | 936 | 1.32e-05 | 1.32e-05
QEN1 | NATHAN | Urban | 3 | 0 | 0.072 |  | 2.4543 |  | 1 | 1353 |  | 3.04e-06
QEN10 | MACGREGOR, ROBERTSON | Urban | 307.5 | 0 | 2.993 |  | 7.6046 | 0.0415 | 2 | 155393.5 |  | 0.000374 |  | 2 | 848.03 | 5.18e-06
QEN2 | NATHAN | Urban | 3 | 0 | 0.25 |  |  |  | 1 | 1353 |  | 3.04e-06
QGP4 | SOUTH BRISBANE | Urban | 32 | 0 | 1.19
QGPWRD16 | WOOLLOONGABBA | Urban | 5 | 0 | 0.868 | 2.001
QPT1 | MORNINGSIDE, MURARRIE | Urban | 6 | 0.873 | 1.253 | 1.277
QPT21 | CANNON HILL, MURARRIE | Urban | 949.5 | 1.732 | 2.402 | 2.153 | 1.2209 | 0.49435 | 10 | 82705.85 | 82705.85 | 0.001046 | 0.001046 | 8 | 33488.85 | 0.000147
QPT22A | CAMP HILL, HAWTHORNE, MORNINGSIDE | Urban | 1973 | 4.314 | 1.551 | 2.344 | 0.041078 | 0.8983 | 6 | 3312.241 | 3312.241 | 0.000108 | 0.000108 | 6 | 72432.09 | 0.000255
QPT24A | CANNON HILL, MORNINGSIDE, MURARRIE | Urban | 227.2 | 0.975 | 1.087 | 0.705
QPT25B | CANNON HILL | Urban | 161 | 0.335 | 2.991 | 4.135
QPT5 | CANNON HILL, MORNINGSIDE | Urban | 1023 | 4.066 | 0.891 | 3.658 | 0.58767 | 0.086718 | 8 | 19174.09 | 19174.09 | 0.000253 | 0.000253 | 2 | 2829.36 | 1.09e-05
QPT6 | MORNINGSIDE | Urban | 61 | 1.684 | 0.797 | 2.42 | 2.1901 |  | 2 | 8526 | 8526 | 8.72e-05 | 8.72e-05
QUT3 | BRISBANE | Urban | 4
QUT5 | BRISBANE | Urban | 5 | 0 | 0.242
RBA10A | ROBINA | Urban | 5 | 0 | 2.194 | 3.163
RBA12A | ROBINA | Urban | 4 | 0 | 1.405 | 2.21
RBA15A | ROBINA | Urban | 464 | 0 | 4.214 | 2.801 | 0.005189 | 0.005292 | 2 | 122.5581 | 122.5581 | 2.03e-06 | 2.03e-06 | 1 | 125 | 1.01e-06
RBA1A | MUDGEERABA, REEDY CREEK, ROBINA, VARSITY LAKES | Rural short | 1529 | 7.098 | 8.083 | 3.601
RBA33A | ROBINA | Urban | 17 | 0 | 1.622 | 2.648
RBA34A | ROBINA | Urban | 326 | 0 | 6.22 | 3.506
RBA35A | BONOGIN, MUDGEERABA, ROBINA | Urban | 639 | 3.307 | 3.152 | 3.01 | 0.017927 | 0.1836 | 5 | 522.3833 | 522.3833 | 5.07e-06 | 5.07e-06 | 3 | 5350 | 3.75e-05
RBA37A | MERRIMAC, MUDGEERABA, ROBINA, WORONGARY | Urban | 1256.5 | 7.916 | 2.801 | 3.468 | 3.5069 | 0.26871 | 3 | 200995.2 | 200995.2 | 0.001331 | 0.001331 | 3 | 15400.5 | 4.35e-05
RBA41A | ROBINA | Urban | 946 | 0 | 5.483 | 4.287 | 0.001932 |  | 1 | 59.7167 | 59.7167 | 1.01e-06 | 1.01e-06
RBA42A | CLEAR ISLAND WATERS, MERRIMAC, ROBINA | Rural short | 424 | 0.125 | 6.368 | 1.448
RBA43A | GILSTON, MERRIMAC, TALLAI, WORONGARY | Rural short | 1035 | 23.062 | 2.195 | 3.887
RBA49A | ROBINA | Urban | 4 | 0 | 1.657 | 2.401
RBA4A | ROBINA | Urban | 1198.5 | 0 | 4.544 | 2.815 |  | 0.054226 | [5 empty] | 3 | 2265.5 | 4.78e-05
RBA6A | ROBINA | Urban | 3.5 | 0 | 0.865 | 1.015
RBA7A | ROBINA | Urban | 8 | 0 | 3.389 | 4.058
RBA9A | ROBINA | Urban | 351 | 0 | 5.128 | 1.886 | 0.005257 | 0.018983 | 2 | 176.1667 | 176.1667 | 2.03e-06 | 2.03e-06 | 1 | 636.16 | 9.08e-06
RBARHP14 | MERRIMAC, MUDGEERABA, ROBINA | Urban | 1655.5 | 1.177 | 8.501 | 3.868 | 0.004845 | 1.1493 | 4 | 284.9 | 284.9 | 4.06e-06 | 4.06e-06 | 2 | 67576 | 0.000174
RBHVPK15 | HERSTON | Urban | 2.1 | 0 | 0.907 | 3.22 | 0.11308 |  | 2 | 32.0933 | 23.7333 | 3.13e-06 | 1.01e-06
RBK11B | GOODNA, REDBANK | Urban | 688 | 6.185 | 3.409 | 2.953 | 0.85172 |  | 12 | 40510.93 | 40510.93 | 0.001538 | 0.001538
RBK12A | GOODNA, REDBANK | Urban | 35 | 3.229 | 0.612 | 1.334 | 0.231 | 0.41181 | 3 | 706.8 | 546.8 | 3.06e-05 | 2.85e-05 | 1 | 1260 | 3.04e-06
RBK9A | COLLINGWOOD PARK, REDBANK | Urban | 298 | 2.114 | 1.021 | 4.306 | 0.22247 |  | 1 | 2030 | 2030 | 0.000294 | 0.000294
RBW2 | ROCHEDALE | Urban | 2 | [5 empty] | 1 | 478 | 478 | 2.03e-06 | 2.03e-06
RBW4 | ROCHEDALE | Urban | 3 | [5 empty] | 1 | 717 | 717 | 3.04e-06 | 3.04e-06
RBY10 | ALEXANDRA HILLS, CAPALABA, CLEVELAND, ORMISTON | Urban | 591 | 4.885 | 0.787 | 2.02 | 0.2502 | 0.061277 | 6 | 9543.283 | 9543.283 | 0.000369 | 0.000369 | 2 | 2337.25 | 9.89e-06
RBY12 | ORMISTON, WELLINGTON POINT | Urban | 1625.5 | 7.321 | 4.264 | 3.945 | 2.0052 | 0.050934 | 10 | 157280.3 | 157280.3 | 0.003287 | 0.003287 | 4 | 3995.02 | 1.66e-05
RBY13 | CLEVELAND | Urban | 942.5 | 4.764 | 0.869 | 2.386 | 0.59668 | 0.005469 | 11 | 33957.73 | 33957.73 | 0.000964 | 0.000964 | 1 | 311.25 | 1.27e-06
RBY15 | ORMISTON | Urban | 1251.5 | 4.84 | 2.142 | 3.329 | 2.7146 | 0.4684 | 6 | 182170.1 | 181889.4 | 0.002548 | 0.002547 | 5 | 31433.45 | 9.03e-05
RBY16 | CLEVELAND, ORMISTON | Urban | 331.5 | 0.558 | 1.581 | 2.744
RBY18 | CLEVELAND, ORMISTON | Urban | 365.5 | 3.438 | 1.224 | 2.039 | 0.2834 |  | 1 | 7866 | 7866 | 0.000347 | 0.000347
RBY2A | CLEVELAND | Urban | 1058.5 | 2.317 | 2.596 | 2.991 | 0.001361 | 0.023398 | 1 | 66.8667 | 66.8667 | 1.01e-06 | 1.01e-06 | 1 | 1149.5 | 4.82e-06
RBY3 | CLEVELAND | Urban | 1508.5 | 4.627 | 5.204 | 3.214 | 8.9582 | 0.004822 | 13 | 536242.2 | 9686.709 | 0.001582 | 6.49e-05 | 1 | 288.63 | 1.08e-05
RBY6 | ALEXANDRA HILLS, CLEVELAND, ORMISTON | Urban | 1357.5 | 6.36 | 1.997 | 3.618 | 0.41122 | 0.25433 | 6 | 26196.02 | 26196.02 | 0.000173 | 0.000173 | 3 | 16201.54 | 6.54e-05
RBY7A | CLEVELAND | Urban | 443 | 2.488 | 1.336 | 2.477 | 0.27569 |  | 8 | 9971.2 | 708.1 | 3.05e-05 | 7.1e-06
RBY9A | CLEVELAND, ORMISTON | Urban | 875 | 0.299 | 8.471 | 3.098 | 0.17111 | 0.32181 | 7 | 6322.7 | 6322.7 | 2.45e-05 | 2.45e-05 | 6 | 11891.6 | 4.11e-05
RCF10A | KIPPA-RING, REDCLIFFE | Urban | 595.9 | 3.701 | 0.313 | 4.058 | 0.29391 | 0.005998 | 4 | 11867.95 | 11867.95 | 0.000644 | 0.000644 | 1 | 242.19 | 8.21e-07
RCF11A | REDCLIFFE | Urban | 4 | 0 | 0.545 | 2.134 | 0.40272 |  | 1 | 90 | 90 | 5.07e-06 | 5.07e-06
RCF12A | REDCLIFFE | Urban | 874 | 0.882 | 1.569 | 3.296 | 0.45606 | 0.004416 | 2 | 15918.58 | 15918.58 | 0.000894 | 0.000894 | 2 | 154.14 | 1.3e-06
RCF1A | MARGATE, REDCLIFFE, WOODY POINT | Urban | 1816.7 | 4.39 | 1.629 | 2.733 | 3.6111 | 0.31976 | 13 | 348134 | 348134 | 0.003846 | 0.003846 | 9 | 30827.21 | 0.000181
RCF2A | KIPPA-RING, MARGATE, REDCLIFFE | Urban | 1423 | 5.269 | 0.534 | 2.667 | 1.3167 | 1.3287 | 7 | 96244.07 | 96244.07 | 0.00169 | 0.00169 | 13 | 97121.2 | 0.000312
RCF3A | REDCLIFFE | Urban | 412 | 1.371 | 0.976 | 0.686 | 0.095778 | 0.071869 | 3 | 7003.417 | 7003.417 | 0.000383 | 0.000383 | 2 | 5255.15 | 1.74e-05
RCF5A | REDCLIFFE | Urban | 608 | 2.164 | 0.648 | 1.982 | 1.4667 | 0.14624 | 7 | 57628.5 | 57628.5 | 0.001924 | 0.001924 | 1 | 5745.6 | 1.85e-05
RCF7A | REDCLIFFE | Urban | 448 | 1.395 | 1.697 | 2.477 | 0.28246 | 0.019455 | 3 | 8584.723 | 8584.723 | 0.000458 | 0.000458 | 2 | 591.3 | 6.92e-06
RCF9A | MARGATE, REDCLIFFE | Urban | 1356 | 3.062 | 1.051 | 2.309 | 0.60936 | 2.28 | 7 | 35794.95 | 35794.95 | 0.002017 | 0.002017 | 18 | 133931.4 | 0.000507
RCN10A | EIGHT MILE PLAINS, RUNCORN, SUNNYBANK, SUNNYBANK H | Urban | 1519.3 | 6.468 | 2.665 | 3.349 | 5.1844 | 0.006986 | 12 | 355012.8 | 355012.8 | 0.003266 | 0.003266 | 2 | 478.38 | 1.97e-06
RCN11 | RUNCORN | Urban | 6 | 0.668 | 0.278 | 4.096
RCN2A | EIGHT MILE PLAINS, RUNCORN | Urban | 1629.5 | 2.402 | 4.599 | 4.115 | 3.4411 | 1.2374 | 7 | 190551.1 | 190215.9 | 0.001662 | 0.00166 | 14 | 68518.85 | 0.000256
RCN3A | RUNCORN, SUNNYBANK HILLS | Urban | 1429 | 0.347 | 6.769 | 3.156 | 1.9806 | 1.0876 | 10 | 162338.9 | 162338.9 | 0.001564 | 0.001564 | 11 | 89147.8 | 0.000266
RCN4A | KARAWATHA, KURABY, RUNCORN | Urban | 1470 | 5.977 | 3.79 | 3.06 | 7.6355 |  | 6 | 560633.2 | 66380.19 | 0.002992 | 0.001515
RCN6A | KURABY, RUNCORN, STRETTON | Urban | 2072 | 6.247 | 7.646 | 4.725 | 4.1588 | 0.1757 | 10 | 246152.7 | 12967.83 | 0.002237 | 0.00018 | 4 | 10399.32 | 3.73e-05
RCN8A | RUNCORN, SUNNYBANK, SUNNYBANK HILLS | Urban | 1200.4 | 2.205 | 4.571 | 3.182 | 4.6574 | 0.35511 | 7 | 224660.1 | 224660.1 | 0.00138 | 0.00138 | 5 | 17129.26 | 0.000111
RCN9 | RUNCORN | Urban | 2 | 0.333 | 0.033 | 8.612
RHG6 | GREENSLOPES | Urban | 835 | 2.049 | 0.104 |  | 0.85447 | 0.079417 | 4 | 78583.67 | 78583.67 | 0.000848 | 0.000848 | 1 | 7303.8 | 1.97e-05
RHP1 | ROBINA | Urban | 3 | 0 | 0.303
RIP1 | FORTITUDE VALLEY | Urban | 13 | 0 | 1.872 |  | 0.03005 |  | 1 | 54 |  | 1.37e-05
RIS1 | RUSSELL ISLAND | Rural short | 714 | 10.21 | 0.487 | 0.847
RIS2 | KARRAGARRA ISLAND, LAMB ISLAND, MACLEAY ISLAND, RU | Rural short | 2452 | 26.056 | 4.186 | 0
RIS4 | RUSSELL ISLAND | Rural short | 546 | 17.347 | 1.072 | 0.674
RLA11A | SALISBURY | Urban | 56 | 1.592 | 0.315
RLA12A | ARCHERFIELD, MOOROOKA, ROCKLEA | Urban | 517 | 4.357 | 3.535 |  | 0.0019 |  | 1 | 48.2778 | 48.2778 | 1.01e-06 | 1.01e-06
RLA15A | SALISBURY | Urban | 26 | 1.277 | 0.33 |  | 0.001873 |  | 1 | 95.55 | 95.55 | 1.01e-06 | 1.01e-06
RLA4A | COOPERS PLAINS, SALISBURY | Urban | 468.5 | 3.03 | 1.872 | 1.734 | 0.003504 | 0.27842 | 2 | 119.85 | 119.85 | 2.03e-06 | 2.03e-06 | 2 | 9523.92 | 3.36e-05
RLA5A | MOOROOKA, ROCKLEA | Urban | 1424 | 4.14 | 0.275 | 3.106 | 0.40829 |  | 5 | 22847.13 | 22847.13 | 0.000151 | 0.000151
RLA7A | MOOROOKA, ROCKLEA, YEERONGPILLY | Urban | 158 | 1.256 | 2.227 | 1.41 |  | 0.049377 | [5 empty] | 1 | 806 | 2.03e-06
RLA8A | MOOROOKA, TARRAGINDI | Urban | 1501.1 | 7.543 | 0.209 |  | 1.9854 |  | 8 | 176198 | 176198 | 0.001529 | 0.001529
RLB11B | REDLAND BAY | Urban | 1947.5 | 5.064 | 6.872 | 5.106 | 0.005093 | 0.004123 | 4 | 320.0633 | 320.0633 | 4.35e-06 | 4.35e-06 | 1 | 259.12 | 8.31e-07
RLB12B | MOUNT COTTON, VICTORIA POINT | Rural short | 132.5 | 8.046 | 0.19 | 0.481
RLB13B | REDLAND BAY | Rural short | 1961 | 29.737 | 7.276 | 4.912
RLB15A | REDLAND BAY, VICTORIA POINT | Urban | 1202.5 | 6.276 | 1.403 | 2.675 | 0.41159 |  | 14 | 28559.63 | 28559.63 | 0.00034 | 0.00034
RLB16A | CARBROOK, MOUNT COTTON, REDLAND BAY | Rural short | 257 | 29.223 | 2.271 | 1.372
RNAVPK7 | FORTITUDE VALLEY, HERSTON | Urban | 2.1 | 0 | 0.606 |  | 0.006123 |  | 1 | 12.36 |  | 3.13e-06
RPN1 | COLLINGWOOD PARK | Urban | 945 | 1.731 | 5.416 | 2.648 | 0.007723 | 0.23338 | 4 | 446.75 | 446.75 | 4.06e-06 | 4.06e-06 | 1 | 13500 | 6.08e-05
RPN2A | BELLBIRD PARK, REDBANK PLAINS | Urban | 860 | 4.101 | 1.279 | 2.858 | 0.13402 | 0.39041 | 4 | 5973.6 | 5973.6 | 6.99e-05 | 6.99e-05 | 1 | 17401.8 | 6.79e-05
RPN3A | BELLBIRD PARK, REDBANK PLAINS | Urban | 1829 | 8.372 | 2.153 | 4.135 | 0.17999 | 0.24115 | 12 | 15224.29 | 15224.29 | 8.92e-05 | 8.92e-05 | 2 | 20397 | 7.2e-05
RPN4A | REDBANK PLAINS, SWANBANK | Rural short | 2068 | 15.411 | 11.559 | 2.896
RPN5A | BELLBIRD PARK, REDBANK PLAINS | Rural short | 1095.5 | 7.91 | 0.961 | 2.496
RPN7A | COLLINGWOOD PARK, NEW CHUM, REDBANK PLAINS | Rural short | 18 | 6.831 | 0.174 | 1.264
RPN8 | AUGUSTINE HEIGHTS, BELLBIRD PARK, REDBANK PLAINS | Rural short | 1081.5 | 3.644 | 7.734 | 2.458
RST11A | IPSWICH | Urban | 66 | 0 | 2.21 | 3.544
RST15A | IPSWICH, WEST IPSWICH | Urban | 142 | 0 | 2.18 | 3.773 | 0.18332 | 0.12878 | 1 | 1076.183 | 1076.183 | 1.01e-06 | 1.01e-06 | 1 | 756 | 6.08e-06
RST16A | IPSWICH | Urban | 660 | 6.048 | 1.226 | 3.353 | 1.7764 | 0.005926 | 4 | 61455.52 | 413.5167 | 0.000676 | 3.04e-06 | 1 | 205 | 1.01e-06
RST18A | IPSWICH | Urban | 86 | 0 | 0.602 | 1.658
RST20A | COALFALLS, LEICHHARDT, SADLIERS CROSSING, WEST IPS | Rural short | 1246 | 8.35 | 1.21 | 2.82
RST2A | IPSWICH | Urban | 157 | 0.587 | 0.519 | 4.192 | 0.10022 |  | 1 | 2119.92 | 2119.92 | 1.47e-05 | 1.47e-05
RST4A | IPSWICH | Urban | 7 | 0 | 0.436 | 2.553
RST5A | IPSWICH, WEST IPSWICH, WOODEND | Urban | 468 | 1.742 | 2.189 | 3.201 | 1.5945 | 0.34968 | 2 | 39329.28 | 39329.28 | 0.000473 | 0.000473 | 6 | 8625.137 | 5.1e-05
RST8A | IPSWICH, WEST IPSWICH | Urban | 322 | 2.815 | 1.773 | 2.725 | 0.44445 | 0.21787 | 5 | 17023.26 | 341.1 | 6.36e-05 | 4.06e-06 | 4 | 8345 | 3.4e-05
RST9A | EAST IPSWICH, IPSWICH | Urban | 319 | 1.482 | 1.26 | 2.229 | 0.081964 | 0.020615 | 5 | 2433.309 | 2433.309 | 3.46e-05 | 3.46e-05 | 1 | 612 | 3.88e-06
RWD1 | ARATULA, CALVERT, COLEYVILLE, EBENEZER, LANEFIELD, | Rural short | 525 | 192.924 | 0.244 | 1.982
RWD2 | ASHWELL, CALVERT, LANEFIELD, MOUNT WALKER, ROSEWOO | Rural short | 1286 | 51.635 | 1.398 | 3.315
SABWTC6 | SPRING HILL | Urban | 5 | 0 | 0.478 |  | 0.001866 |  | 1 | 8 |  | 2.03e-06
SARSHW7 | CORINDA, ROCKLEA, SHERWOOD | Urban | 193 | 2.775 | 2.162 | 2.382
SARSHW9 | ROCKLEA, SHERWOOD | Urban | 458 | 2.511 | 1.544 | 3.83 | 0.028535 | 0.083162 | 3 | 296.3667 | 189.9167 | 3.04e-06 | 2.03e-06 | 3 | 863.72 | 8.44e-06
SBH11 | REDCLIFFE, SCARBOROUGH | Urban | 1790 | 4.724 | 0.638 | 2.502 | 2.1261 | 0.10103 | 8 | 208197.6 | 208197.6 | 0.002048 | 0.002048 | 3 | 9893.855 | 3.82e-05
SBH13A | KIPPA-RING, REDCLIFFE | Urban | 509.6 | 2.925 | 1.494 | 3.163 | 0.78272 | 0.23858 | 5 | 20397.08 | 20397.08 | 9.53e-05 | 9.53e-05 | 1 | 6217.2 | 2.01e-05
SBH4 | SCARBOROUGH | Urban | 1299 | 4.897 | 1.416 | 2.706 | 0.085634 | 1.093 | 8 | 5139.267 | 5139.267 | 5.66e-05 | 5.66e-05 | 7 | 65596.87 | 0.000212
SBH6 | SCARBOROUGH | Urban | 2103 | 6.811 | 1.043 | 3.291 | 0.050647 | 1.6119 | 13 | 4439.137 | 4439.137 | 3.06e-05 | 3.06e-05 | 17 | 141278.9 | 0.000486
SBH8 | KIPPA-RING, REDCLIFFE | Urban | 752.6 | 2.053 | 1.686 | 1.982 | 0.10959 | 0.074131 | 2 | 9236.25 | 9236.25 | 0.000105 | 0.000105 | 1 | 6247.8 | 3.56e-05
SBH9 | KIPPA-RING, SCARBOROUGH | Urban | 1179 | 0 | 6.959 | 3.296 | 0.002258 | 0.11895 | 1 | 134.1 | 134.1 | 1.01e-06 | 1.01e-06 | 3 | 7062.9 | 2.42e-05
SBK10A | NATHAN, ROBERTSON, SALISBURY | Rural short | 816 | 2.827 | 2.881 | 1.597
SBK11 | COOPERS PLAINS, ROBERTSON, SUNNYBANK | Urban | 1382.5 | 4.619 | 2.61 | 2.271 | 4.2577 | 0.19163 | 7 | 317771.4 | 317771.4 | 0.002821 | 0.002821 | 5 | 14302.15 | 9.96e-05
SBK12 | COOPERS PLAINS | Urban | 163 | 3.064 | 0.689 | 3.734 | 1.2261 | 0.12409 | 1 | 9999.5 | 9999.5 | 0.000176 | 0.000176 | 1 | 1012 | 4.06e-06
SBK4 | MACGREGOR, ROBERTSON, SUNNYBANK | Urban | 564 | 1.206 | 3.034 | 3.372 | 1.5762 |  | 2 | 15661.72 | 15661.72 | 2.49e-05 | 2.49e-05
SBK9 | EIGHT MILE PLAINS, MACGREGOR, ROBERTSON, SUNNYBANK | Urban | 1535.5 | 8.732 | 1.39 | 4.477 | 5.7891 | 0.094812 | 19 | 255449.5 | 255449.5 | 0.003143 | 0.003143 | 4 | 4183.64 | 2.64e-05
SBY11A | NATHAN, SALISBURY, TARRAGINDI | Urban | 1018.9 | 5.266 | 2.087 | 3.277 | 3.3598 | 0.3323 | 14 | 169879.5 | 169879.5 | 0.004396 | 0.004396 | 6 | 16802.24 | 6.42e-05
SBY14A | SALISBURY | Urban | 949 | 4.073 | 0.799 | 2.134 | 5.5299 | 0.36929 | 8 | 324768 | 324768 | 0.001923 | 0.001923 | 3 | 21688 | 8.52e-05
SBY15A | SALISBURY | Urban | 47 | 0.667 | 0.512 | 2.153
SBY3A | NATHAN, SALISBURY | Urban | 515.1 | 2.571 | 0.84 | 2.477 | 1.0492 | 0.11829 | 6 | 27939.29 | 27939.29 | 0.000523 | 0.000523 | 1 | 3150 | 9.13e-06
SBY6A | MOOROOKA, SALISBURY | Urban | 256.3 | 2.405 | 0.682 | 1.581 | 0.099805 | 0.21013 | 2 | 3230.171 | 3230.171 | 3.82e-05 | 3.82e-05 | 2 | 6800.769 | 2.03e-05
SBY7A | SALISBURY | Urban | 7 | 0 | 0.743 | 3.887
SCV4 | HOPE ISLAND | Urban | 362 | 0 | 4.278 |  | 0.12047 | 0.012046 | 5 | 4557.217 | 4557.217 | 5.56e-05 | 5.56e-05 | 1 | 455.7 | 2.98e-06
SCV5 | HOPE ISLAND | Urban | 205 | 0 | 2.189
SCV7 | COOMERA, HOPE ISLAND | Urban | 385 | 0 | 7.953 |  |  | 0.10626 | [5 empty] | 2 | 1815.593 | 2.69e-05
SDM1 | BRYDEN, CROSSDALE, MOUNT BYRON, SOMERSET DAM, TOOL | Rural short | 193 | 66.766 | 0.03 | 0.438
SDS4 | SURFERS PARADISE | Urban | 109 | 0 | 0.468 |  |  | 0.009891 | [5 empty] | 1 | 461.7 | 2.74e-06
SDSSPD8 | SURFERS PARADISE | Urban | 36 | 0 | 0.549 | 1.562
SFD10 | EVERTON PARK, STAFFORD HEIGHTS | Urban | 1357 | 5.589 | 1.461 | 2.254 | 0.22462 | 1.281 | 19 | 20250.69 | 20250.69 | 0.00024 | 0.00024 | 27 | 115492.4 | 0.000409
SFD11 | STAFFORD, STAFFORD HEIGHTS | Urban | 607 | 1.343 | 2.159 | 4.839 | 0.94045 | 0.45614 | 2 | 14001.82 | 14001.82 | 0.000654 | 0.000654 | 8 | 6791.26 | 2.46e-05
SFD2A | ASPLEY, BRIDGEMAN DOWNS, CHERMSIDE WEST, MCDOWALL, | Urban | 1748 | 2.96 | 11.641 | 4.497 | 0.036729 | 0.63512 | 10 | 2409.033 | 1507.033 | 1.73e-05 | 1.32e-05 | 13 | 41656.89 | 0.00016
SFD3 | EVERTON PARK, MCDOWALL, STAFFORD HEIGHTS | Urban | 1214 | 3.95 | 4.508 | 4.439 | 0.53147 | 0.99274 | 8 | 23225.88 | 23225.88 | 0.001316 | 0.001316 | 10 | 43384.03 | 0.000164
SFD4 | EVERTON PARK, STAFFORD | Urban | 1314 | 6.043 | 0.683 | 2.039 | 0.24812 | 1.0017 | 7 | 18007.52 | 18007.52 | 0.000142 | 0.000142 | 19 | 72698.43 | 0.000295
SFD5 | CHERMSIDE WEST, MCDOWALL, STAFFORD HEIGHTS | Urban | 805 | 3.149 | 1.858 | 2.134 | 2.3179 | 0.75079 | 4 | 133886.2 | 133886.2 | 0.000826 | 0.000826 | 13 | 43367.95 | 0.000196
SFD6B | STAFFORD, STAFFORD HEIGHTS | Urban | 723 | 2.79 | 0.982 | 2.515 | 1.1003 | 0.25066 | 6 | 110319.5 | 110319.5 | 0.000857 | 0.000857 | 6 | 25131.52 | 9.12e-05
SFD7A | ASPLEY, CHERMSIDE WEST, STAFFORD HEIGHTS | Urban | 1059.5 | 3.865 | 2.457 | 2.229 | 0.028382 | 0.43932 | 6 | 2319.417 | 2319.417 | 0.00013 | 0.00013 | 17 | 35902.36 | 0.000146
SFD8 | MCDOWALL, STAFFORD HEIGHTS | Urban | 642 | 1.63 | 2.919 | 1.524 | 1.0671 | 0.18048 | 3 | 49223.32 | 49223.32 | 0.000635 | 0.000635 | 3 | 8325.29 | 3.59e-05
SFD9 | CHERMSIDE, CHERMSIDE WEST, KEDRON, STAFFORD HEIGHT | Urban | 864 | 3.638 | 1.053 | 1.62 | 0.035775 | 0.43827 | 8 | 2766.367 | 2766.367 | 3.63e-05 | 3.63e-05 | 14 | 33889.45 | 0.000134
SGT22A | BOONDALL, DEAGON | Urban | 1614 | 6.851 | 2.368 | 3.137 | 0.003881 | 0.27047 | 3 | 269.2333 | 269.2333 | 3.04e-06 | 3.04e-06 | 9 | 18764.44 | 7.65e-05
SGT24A | BRACKEN RIDGE, BRIGHTON | Urban | 1542 | 5.911 | 3.322 | 3.487 | 0.002558 | 0.5495 | 2 | 168.1833 | 168.1833 | 2.03e-06 | 2.03e-06 | 7 | 36123.84 | 0.000169
SGT26A | BOONDALL, TAIGUM | Rural short | 362 | 0.551 | 3.285 | 0.693
SGT3 | BRACKEN RIDGE, DEAGON, SANDGATE | Rural short | 248 | 2.639 | 0.925 | 0.629
SGT4 | DEAGON, SANDGATE | Urban | 1366 | 5.657 | 2.021 | 3.811 | 0.10382 | 1.2017 | 4 | 5378.109 | 5378.109 | 0.000167 | 0.000167 | 19 | 62251.21 | 0.000286
SGT5 | BRACKEN RIDGE | Urban | 1115 | 4.285 | 2.07 | 2.344 | 0.14519 | 0.33596 | 7 | 10986.24 | 10986.24 | 0.000138 | 0.000138 | 11 | 25421.59 | 0.000103
SGT6 | BRACKEN RIDGE | Urban | 1021 | 1.347 | 5.074 | 2.286 | 0.003445 | 0.073379 | 3 | 264.7231 | 264.7231 | 3.04e-06 | 3.04e-06 | 4 | 5638.17 | 2.13e-05
SGT7 | DEAGON, SANDGATE, SHORNCLIFFE | Urban | 2001 | 9.845 | 1.17 | 3.811 | 0.013603 | 0.62505 | 9 | 868.7827 | 675.0161 | 9.13e-06 | 8.11e-06 | 10 | 39919.2 | 0.000154
SGT9 | BOONDALL, TAIGUM, ZILLMERE | Urban | 1474 | 3.345 | 6.112 | 4.592 | 0.044626 | 0.17854 | 2 | 1895.75 | 1895.75 | 9.53e-05 | 9.53e-05 | 2 | 7584.6 | 3.15e-05
SHW10A | CHELMER, GRACEVILLE, SHERWOOD | Urban | 1213.5 | 6.996 | 0.43 | 2.953 | 0.03448 | 0.18525 | 12 | 2201.387 | 2201.387 | 2.1e-05 | 2.1e-05 | 7 | 11827.29 | 6.38e-05
SHW12 | FIG TREE POCKET | Urban | 608 | 4.226 | 3.176 | 2.553 | 0.099193 | 0.36312 | 7 | 4505.689 | 4505.689 | 3.08e-05 | 3.08e-05 | 3 | 16493.91 | 0.000379
SHW3 | CORINDA, SHERWOOD | Urban | 1318.5 | 6.961 | 0.339 | 3.106 | 1.2786 | 0.85023 | 18 | 79509.81 | 79509.81 | 0.001387 | 0.001387 | 16 | 52870.21 | 0.000201
SHW4 | FIG TREE POCKET, INDOOROOPILLY | Urban | 613 | 4.743 | 1.04 | 1.81 | 0.008268 | 0.7056 | 3 | 475.8 | 475.8 | 3.04e-06 | 3.04e-06 | 7 | 40607.02 | 0.000137
SHW5A | CHELMER, GRACEVILLE, SHERWOOD | Urban | 894 | 6.262 | 0.616 | 3.029 | 1.9982 | 0.11639 | 14 | 109293.1 | 109138.8 | 0.001083 | 0.001082 | 7 | 6366.2 | 7.27e-05
SHW6 | GRACEVILLE, SHERWOOD | Urban | 1331.5 | 5.187 | 0.255 | 3.01 | 0.063929 | 0.068153 | 5 | 4472.673 | 4472.673 | 0.000101 | 0.000101 | 4 | 4768.165 | 3.63e-05
SHW81 | CORINDA, SHERWOOD | Urban | 1833 | 4.354 | 0.827 | 4.154 | 1.582 | 0.20406 | 15 | 87872.36 | 87872.36 | 0.001955 | 0.001955 | 3 | 11334.45 | 6.14e-05
SIS1 | POINT LOOKOUT | Rural short | 1182 | 24.315 | 2.943 | 3.106
SIS2 | AMITY, DUNWICH, NTH STRADBROKE ISLD | Rural short | 984 | 36.258 | 0.56 | 2.782
SMF1B | BUNYA, CAMP MOUNTAIN, DRAPER, FERNY HILLS, MOUNT S | Rural short | 793 | 18.776 | 2.283 | 3.239
SMF2A | CASHMERE, CEDAR CREEK, CLEAR MOUNTAIN, CLOSEBURN, | Rural short | 902 | 56.471 | 4.097 | 3.068
SMF3A | CEDAR CREEK, CLOSEBURN, HIGHVALE, MT GLORIOUS, SAM | Rural short | 779 | 25.668 | 6.848 | 2.02
SMF5A | HIGHVALE, MOUNT NEBO, SAMFORD VALLEY, WIGHTS MOUNT | Rural short | 732 | 31.24 | 0.978 | 1.829
SMF5B | HIGHVALE, SAMFORD VALLEY, SAMFORD VILLAGE | Rural short | 483 | 3.53 | 4.401 | 1.734
SMF6A | CAMP MOUNTAIN, ENOGGERA RESERVOIR, FERNY HILLS, HI | Rural short | 682 | 44.281 | 1.344 | 1.886
SMR10A | SUMNER | Urban | 247.5 | 0.618 | 3.91 | 2.706
SMR10B | MIDDLE PARK, WESTLAKE | Urban | 1399 | 0 | 10.217 | 4.096 | 0.045236 | 0.059789 | 3 | 3087.417 | 3087.417 | 5.51e-05 | 5.51e-05 | 4 | 4080.68 | 1.49e-05
SMR12A | JAMBOREE HEIGHTS, MIDDLE PARK, MT OMMANEY, SUMNER | Urban | 1196 | 0.812 | 6.795 | 3.334 | 0.007369 | 0.31185 | 3 | 402.6167 | 402.6167 | 3.04e-06 | 3.04e-06 | 5 | 17038.14 | 4.72e-05
SMR12B | DARRA | Urban | 92 | 0.9 | 2.113 | 3.296 |  | 0.78451 | [5 empty] | 2 | 3628.52 | 8.15e-06
SMR13B | MT OMMANEY, SINNAMON PARK | Urban | 581 | 0 | 5.243 | 2.629
SMR15A | DARRA, JAMBOREE HEIGHTS, RIVERHILLS, SUMNER | Urban | 1386 | 0.405 | 8.006 | 3.258 | 0.012938 |  | 3 | 905 | 905 | 4.02e-05 | 4.02e-05
SMR1A | MIDDLE PARK, WESTLAKE | Urban | 910 | 0.104 | 7.38 | 3.125 | 0.22036 | 0.056279 | 4 | 11436.08 | 11436.08 | 6.08e-05 | 6.08e-05 | 1 | 2920.68 | 1.21e-05
SMR3B | DARRA | Urban | 75 | 0.361 | 2.422 | 3.353 | 0.033344 |  | 1 | 142.15 | 142.15 | 1.01e-06 | 1.01e-06
SMR4A | DARRA, SEVENTEEN MILE ROCKS, SINNAMON PARK | Urban | 1297 | 0.585 | 8.624 | 4.458 | 3.571 |  | 6 | 166557.2 | 166557.2 | 0.001337 | 0.001337
SMR6A | JAMBOREE HEIGHTS, MT OMMANEY | Urban | 72 | 0.768 | 3.087 | 2.991 |  | 0.002636 | [5 empty] | 1 | 229.08 | 7e-07
SMR7A | MIDDLE PARK, RIVERHILLS, WESTLAKE | Urban | 1188 | 0.015 | 9.078 | 2.953 | 2.3416 | 0.009015 | 12 | 171512.7 | 171512.7 | 0.002673 | 0.002673 | 3 | 660.34 | 4.32e-06
SMR7B | DARRA, SUMNER | Urban | 181 | 0.655 | 2.084 | 2.934 | 1.3044 |  | 5 | 20189.05 | 20189.05 | 0.000377 | 0.000377
SMR9A | DARRA, SEVENTEEN MILE ROCKS, SINNAMON PARK | Urban | 1064 | 4.282 | 5.568 | 3.734 | 0.022049 |  | 4 | 960.2833 | 960.2833 | 6.79e-05 | 6.79e-05
SPC2B | ADARE, ATKINSONS DAM, BUARABA, BUARABA CREEK, CHUR | Rural short | 451 | 92.332 | 4.065 | 3.087
SPD11A | SURFERS PARADISE | Urban | 1850 | 5.106 | 1.096 | 3.849 | 3.2372 | 0.38241 | 7 | 202903.9 | 202903.9 | 0.001988 | 0.001988 | 5 | 23968.88 | 0.000118
SPD12B | SURFERS PARADISE | Urban | 599 | 0.567 | 1.098 | 2.553 | 0.003307 | 0.40035 | 1 | 94.1333 | 94.1333 | 1.01e-06 | 1.01e-06 | 2 | 11394.84 | 3.31e-05
SPD19A | MAIN BEACH, SURFERS PARADISE | Urban | 172 | 0.062 | 3.718 | 4.649 |  | 1.6332 | [5 empty] | 1 | 24759 | 6.39e-05
SPD1A | SURFERS PARADISE | Urban | 51 | 0 | 0.807 | 3.849 | 0.079144 | 1.8015 | 1 | 128.8667 | 128.8667 | 1.01e-06 | 1.01e-06 | 4 | 2933.26 | 1.15e-05
SPD21A | SURFERS PARADISE | Urban | 6 | 0 | 1.278 | 2.991
SPD28A | SURFERS PARADISE | Urban | 5 | 0 | 0.455 | 3.506
SPD29A | SURFERS PARADISE | Urban | 1275 | 0.174 | 4.589 | 4.058 | 0.014036 | 0.039116 | 6 | 470.2167 | 470.2167 | 6.08e-06 | 6.08e-06 | 1 | 1310.4 | 1.27e-05
SPD2B | SURFERS PARADISE | Urban | 968 | 0 | 2.978 | 3.391 | 0.004574 | 0.52016 | 1 | 54.45 | 54.45 | 1.01e-06 | 1.01e-06 | 6 | 6192.76 | 5.12e-05
SPD3A | SURFERS PARADISE | Urban | 309 | 0 | 2.41 | 2.042 |  | 1.0981 | [5 empty] | 1 | 21798.7 | 0.000144
SPD4A | MAIN BEACH, SURFERS PARADISE | Rural short | 894 | 0 | 5.554 | 1.2
SPD4B | SURFERS PARADISE | Urban | 348 | 0 | 2.195 | 2.42 | 0.002882 |  | 1 | 55.4 | 55.4 | 1.01e-06 | 1.01e-06
SPD5A | SURFERS PARADISE | Urban | 749 | 0 | 2.062 | 2.42 | 4.4882 | 0.1144 | 2 | 72743.75 | 72743.75 | 0.000871 | 0.000871 | 2 | 1854.12 | 6e-06
SPD5B | SURFERS PARADISE | Urban | 284 | 0 | 1.72 | 3.087 | 3.3659 | 0.003879 | 3 | 32977.51 | 32977.51 | 0.000544 | 0.000544 | 1 | 38 | 1.01e-06
SPD6B | SURFERS PARADISE | Urban | 120 | 0 | 1.024 | 2.191 | 0.034172 | 0.059963 | 1 | 178.5333 | 178.5333 | 1.01e-06 | 1.01e-06 | 2 | 313.28 | 3.61e-06
SPD7B | MAIN BEACH, SURFERS PARADISE | Urban | 129 | 0 | 3.311 | 1.543
SPE1 | BRENDALE | Urban | 219 | 2.388 | 1.295 | 2.629 | 0.56894 |  | 2 | 7591.167 | 7591.167 | 0.000219 | 0.000219
SPE20A | BRENDALE, STRATHPINE | Urban | 685 | 3.265 | 2.486 | 5.468 |  | 0.059146 | [5 empty] | 2 | 632.6 | 2.94e-06
SPE22A | BRENDALE | Urban | 304 | 2.936 | 1.635 | 3.906
SPE24 | BRENDALE | Urban | 73 | 1.043 | 0.306 | 3.464 | 0.17354 |  | 1 | 4116.48 | 4116.48 | 1.09e-05 | 1.09e-05
SPE5 | BRENDALE | Urban | 217.5 | 2.166 | 2.112 | 3.43 | 0.66947 | 0.5079 | 2 | 8165.668 | 8165.668 | 0.0002 | 0.0002 | 1 | 6195 | 2.13e-05
SPE9 | BRENDALE, STRATHPINE | Urban | 1066 | 5.745 | 5.175 | 3.391 | 3.7488 | 0.72966 | 5 | 135627.8 | 135627.8 | 0.002386 | 0.002386 | 2 | 26398.34 | 6.79e-05
SPEWSP29 | STRATHPINE | Urban | 28 | 1.962 | 0.022 | 0.686
SPF12B | SPRINGFIELD LAKES | Urban | 2043 | 0 | 13.809 | 5.525 | 0.003337 | 0.2327 | 2 | 250.4667 | 250.4667 | 2.03e-06 | 2.03e-06 | 8 | 17463.83 | 0.00011
SPF15A | AUGUSTINE HEIGHTS, BROOKWATER | Urban | 689 | 0 | 8.648 | 3.658 | 0.003187 | 1.04 | 1 | 109.3333 | 109.3333 | 1.01e-06 | 1.01e-06 | 3 | 35675.64 | 0.000277
SPF17B | SPRINGFIELD | Urban | 1000 | 0 | 6.541 | 3.601 | 0.001971 | 0.007175 | 1 | 86.1833 | 86.1833 | 1.01e-06 | 1.01e-06 | 1 | 313.65 | 7.07e-06
SPF1B | AUGUSTINE HEIGHTS, SPRINGFIELD | Urban | 584 | 0 | 6.7 | 2.363
SPFSTC2 | BROOKWATER | Urban | 2 | 0.01 | 0.646 | 2.096
SPO11A | LABRADOR, SOUTHPORT | Urban | 2084 | 2.017 | 3.455 | 4.06 | 0.002571 | 0.46284 | 3 | 149.95 | 149.95 | 3.04e-06 | 3.04e-06 | 8 | 26997.84 | 0.000132
SPO12A | SOUTHPORT | Urban | 4 | 0 | 0.605 | 0.367
SPO16A | ASHMORE, SOUTHPORT | Urban | 897.5 | 4.39 | 4.254 | 4.668 | 0.12618 | 0.012362 | 4 | 3729.817 | 3729.817 | 2.84e-05 | 2.84e-05 | 1 | 365.4 | 2.13e-06
SPO31A | SOUTHPORT | Urban | 397 | 2.195 | 1.267 | 4.02 | 0.40046 | 1.7725 | 2 | 6046.75 | 6046.75 | 9.63e-05 | 9.63e-05 | 6 | 26763.92 | 0.000111
SPO32A | LABRADOR, SOUTHPORT | Urban | 1839 | 5.186 | 2.029 | 3.543 | 0.011439 | 0.28876 | 8 | 1036.677 | 1036.677 | 8.11e-06 | 8.11e-06 | 4 | 26170.33 | 8.16e-05
SPO33A | MAIN BEACH | Urban | 16 | 0 | 3.781 | 3.792 |  | 5.37e-05 | [5 empty] | 1 | 0.75 | 1.01e-08
SPO3A | ASHMORE, SOUTHPORT | Urban | 1059 | 3.964 | 1.937 | 3.106 | 0.004446 | 0.15782 | 4 | 325.5799 | 325.5799 | 4.06e-06 | 4.06e-06 | 5 | 11557.57 | 7.15e-05
SPO40A | SOUTHPORT | Urban | 17 | 0 | 0.858 | 0.21
SPO41A | LABRADOR, SOUTHPORT | Urban | 1964.5 | 4.755 | 1.603 | 3.791 | 0.013136 | 0.077919 | 11 | 975.0833 | 975.0833 | 1.12e-05 | 1.12e-05 | 1 | 5783.79 | 2.68e-05
SPO47A | SOUTHPORT | Urban | 1263 | 2.867 | 1.448 | 3.43 | 0.022304 | 0.81865 | 5 | 1306.377 | 1306.377 | 6.08e-06 | 6.08e-06 | 3 | 47949.6 | 0.000162
SPO49A | SOUTHPORT | Urban | 85.2 | 0 | 2.551 | 3.029 | 0.44562 |  | 2 | 4706.75 | 4706.75 | 8.24e-05 | 8.24e-05
SPO49B | MAIN BEACH | Urban | 1014 | 0 | 4.537 | 2.172 | 0.91556 | 0.083914 | 4 | 48304.53 | 48304.53 | 0.000939 | 0.000939 | 1 | 4427.28 | 1.57e-05
SPO4A | SOUTHPORT | Urban | 73 | 0 | 1.237 | 4.573
SPO51A | SOUTHPORT | Urban | 1350 | 4.869 | 0.648 | 2.815 | 0.007369 | 1.5647 | 5 | 528.5833 | 528.5833 | 5.07e-06 | 5.07e-06 | 26 | 112239.2 | 0.000382
SPO52A | SOUTHPORT | Urban | 50 | 0 | 1.694 | 2.744
SPO55A | SOUTHPORT | Urban | 539 | 0.325 | 1.561 | 2.839 |  | 1.3043 | [5 empty] | 5 | 27277.92 | 0.000116
SPO5A | MAIN BEACH | Urban | 888 | 0 | 4.736 | 3.849 | 0.021014 | 1.0471 | 3 | 645.6917 | 645.6917 | 1.46e-05 | 1.46e-05 | 8 | 32173.01 | 0.000124
SPO60A | ASHMORE, SOUTHPORT | Urban | 1271 | 5.609 | 0.947 | 3.372 | 2.9011 | 0.055618 | 10 | 179462.3 | 179462.3 | 0.001317 | 0.001317 | 2 | 3440.54 | 2.27e-05
SPO60B | SOUTHPORT | Urban | 82 | 0.608 | 0.539 | 1.715
SPO61A | SOUTHPORT | Urban | 172.3 | 1.242 | 0.806 | 2.991 | 0.096973 | 0.053686 | 4 | 1369.783 | 1369.783 | 1.3e-05 | 1.3e-05 | 1 | 758.34 | 2.01e-06
SPO67B | SOUTHPORT | Urban | 1462 | 5.406 | 1.812 | 3.658 | 0.000135 | 0.80385 | 1 | 9.8333 | 9.8333 | 1.01e-06 | 1.01e-06 | 12 | 58660.68 | 0.000266
SPO69A | SOUTHPORT | Urban | 1691 | 1.56 | 1.548 | 3.064 | 0.041946 | 0.9736 | 3 | 2311.967 | 2311.967 | 2.48e-05 | 2.48e-05 | 14 | 53662.75 | 0.0002
SPO7A | SOUTHPORT | Urban | 552 | 0 | 1.965 | 2.229 | 0.001004 | 0.003291 | 1 | 52.8992 | 52.8992 | 1.01e-06 | 1.01e-06 | 2 | 173.46 | 2.04e-06
SPO8A | SOUTHPORT | Urban | 788.5 | 2.818 | 2.652 | 2.477 | 1.5286 | 3.3167 | 7 | 16426.15 | 16426.15 | 0.000212 | 0.000212 | 7 | 35640.99 | 0.000125
SPO9A | MAIN BEACH | Urban | 93 | 0 | 6.578 | 3.62
SPOSSS15 | SOUTHPORT | Urban | 124.6 | 0 | 2.475 | 4.573 |  | 0.27067 | [5 empty] | 4 | 1250.795 | 6.74e-06
SPOSSS35 | SOUTHPORT | Urban | 83 | 0.174 | 1.419 | 3.334 | 0.26756 | 0.45961 | 5 | 431.2167 | 431.2167 | 5.07e-06 | 5.07e-06 | 2 | 740.73 | 4.8e-06
SRD14A | CARINA, CARINDALE | Urban | 1660.5 | 3.308 | 6.617 | 3.963 | 0.15223 | 1.5726 | 9 | 8638.25 | 8638.25 | 0.000105 | 0.000105 | 21 | 89238.02 | 0.000337
SRD18A | CARINA, CARINDALE | Urban | 1046.7 | 2.03 | 4.967 | 3.163 | 0.00462 | 0.92811 | 2 | 203.75 | 203.75 | 2.03e-06 | 2.03e-06 | 2 | 40928 | 0.000116
SRD19A | CARINA HEIGHTS, CARINDALE | Urban | 1951 | 2.932 | 8.874 | 4.173 | 7.0672 | 0.4451 | 12 | 120093.3 | 120093.3 | 0.002161 | 0.002161 | 5 | 7563.65 | 3.08e-05
SRD4A | CARINDALE | Urban | 768 | 1.491 | 4.614 | 2.877 |  | 0.086724 | [5 empty] | 1 | 4548.37 | 1.03e-05
SRD5A | CARINDALE | Urban | 3 | 0 | 1.966 | 1.562
SRD7A | CARINDALE | Urban | 5 | 0 | 2.104 | 2.553
SSSWHI2 | SOUTHPORT | Urban | 4 | 0 | 1.085 |  |  |  | 1 | 196 | 196 | 4.06e-06 | 4.06e-06
STC1 | SPRINGFIELD CENTRAL | Urban | 2 | 0 | 1.388
STC7 | CAMIRA, SPRINGFIELD, SPRINGFIELD CENTRAL, SPRINGFI | Urban | 1838 | 0.729 | 12.676 |  | 0.25632 | 0.046084 | 4 | 9779.654 | 9779.654 | 8.57e-05 | 8.57e-05 | 6 | 1758.33 | 2.15e-05
STL1A | ST LUCIA | Urban | 1665.5 | 3.219 | 0.655 | 2.417 | 1.1211 | 0.03701 | 5 | 122382.9 | 122382.9 | 0.001935 | 0.001935 | 1 | 4040.16 | 1.35e-05
STL2 | ST LUCIA | Urban | 982 | 1.881 | 0.975 | 1.972 | 0.11816 |  | 6 | 7924.083 | 7924.083 | 2.26e-05 | 2.26e-05
STL3 | ST LUCIA | Urban | 166 | 1.167 | 0.269 | 0.972 | 0.32363 | 0.002814 | 1 | 6906.9 |  | 6.09e-05 |  | 1 | 60.06 | 1.85e-06
STL5 | ST LUCIA | Urban | 91 | 0 | 1.192 | 1.135
STT1B | GILBERTON, ORMEAU, STAPYLTON, WOONGOOLBA | Rural short | 80 | 14.154 | 0.526 | 1.734
STT2B | STAPYLTON | Urban | 14 | 2.434 | 2.675 | 4.458 | 0.045356 | 0.061213 | 1 | 2450 | 2450 | 1.62e-05 | 1.62e-05 | 2 | 3306.54 | 1.02e-05
STT3A | ALBERTON, STEIGLITZ, WOONGOOLBA | Rural short | 103 | 20.302 | 2.574 | 3.753
STT5B | ORMEAU, STAPYLTON | Urban | 47.5 | 0.716 | 1.497 | 1.924 | 0.05809 |  | 1 | 144 | 144 | 3.04e-06 | 3.04e-06
TAB1 | ALBION | Urban | 5.5 | 0 | 1.921 |  | 0.000237 |  | 2 | 61 | 61 | 7.6e-06 | 7.6e-06
TAB3 | ALBION | Urban | 152.5 | 0.894 | 0.947 |  | 4.8401 | 0.59768 | 10 | 96474.07 | 96474.07 | 0.000896 | 0.000896 | 1 | 11913 | 2.54e-05
TBV1 | BOYLAND, MUNDOOLUN, TAMBORINE | Rural short | 44 | 9.498 | 0.285 | 0.193
TBV2 | BEAUDESERT, BIRNAM, BOYLAND, MUNDOOLUN, TABRAGALBA | Rural short | 281 | 48.748 | 0.385 | 0.915
TBV3 | TAMBORINE | Rural short | 366 | 19.675 | 0.093 | 1.025
TBV4 | TAMBORINE | Rural short | 513 | 42.588 | 2.23 | 1.734
TCB1 | TIN CAN BAY, WALLU | Rural short | 1412 | 21.061 | 1 | 2.439
TCB2 | INSKIP, RAINBOW BEACH | Rural short | 1210 | 25.565 | 2.242 | 3.582
TCB3 | COOLOOLA COVE, RAINBOW BEACH, TIN CAN BAY | Rural short | 1390 | 28.301 | 1.366 | 2.477
TCBTR3 | TIN CAN BAY | Urban | 1
TEX1 | IPSWICH | Urban | 34 | 0.088 | 0
TEX2 | IPSWICH | Urban | 33 | 0 | 0.401
TGP2A | MANLY WEST, TINGALPA, WAKERLEY | Urban | 997 | 2.444 | 3.029 | 2.706 | 0.88162 | 0.31669 | 5 | 59864.12 | 59864.12 | 0.002019 | 0.002019 | 4 | 21504 | 0.000121
TGP3A | BELMONT, TINGALPA | Urban | 1321 | 1.313 | 5.124 | 3.106 | 2.4185 | 0.15013 | 2 | 163082 | 163082 | 0.002685 | 0.002685 | 2 | 10123 | 5.37e-05
TGP5B | HEMMANT, MANLY WEST, TINGALPA, WYNNUM WEST | Urban | 1792 | 5.947 | 5.774 | 4.935 | 0.73988 | 0.72997 | 6 | 38375.69 | 38375.69 | 0.003631 | 0.003631 | 6 | 37861.96 | 0.000161
TGP6A | BELMONT, CARINDALE, TINGALPA | Urban | 1296.3 | 3.06 | 5.512 | 3.125 | 2.7701 | 0.56854 | 15 | 181602.4 | 15681.93 | 0.001522 | 0.000799 | 8 | 37272.5 | 0.000129
TGP8A | TINGALPA | Urban | 840.5 | 3.042 | 1.48 | 3.411 | 3.824 | 0.49025 | 7 | 116554.8 | 116554.8 | 0.002646 | 0.002646 | 5 | 14942.49 | 7.19e-05
TGP9A | BELMONT, GUMDALE, TINGALPA, WAKERLEY | Urban | 1198 | 6.855 | 6.065 | 4.687 | 4.6933 | 0.54496 | 9 | 160208.7 | 12803.29 | 0.00244 | 0.001236 | 9 | 18602.39 | 7e-05
TGW1 | CABOONBAH, COAL CREEK, COOEEIMBARDI, CRESSBROOK, F | Rural short | 394 | 127.542 | 0 | 0.972
TGW2 | BIARRA, ESKDALE, IVORY CREEK, MOUNT BEPPO, OTTABA, | Rural short | 274 | 107.999 | 0.31 | 0.762
TGW3 | AVOCA, AVOCA VALE, BRAEMORE, COLINTON, GREGORS CRE | Rural short | 422 | 159.775 | 0.102 | 1.277
TGW4 | BIARRA, TOOGOOLAWAH | Rural short | 630 | 21.789 | 0.214 | 1.429
TGW5 | BRAEMORE, COLINTON, EMU CREEK, HARLIN, IVORY CREEK | Rural short | 215 | 78.743 | 0.232 | 0.686
THL1 | GATTON, LOWER TENTHILL, ROPELEY, WINWILL | Rural short | 173 | 32.877 | 0.445 | 0.743
THL2 | CAFFEY, INGOLDSBY, LOWER TENTHILL, ROPELEY, UPPER | Rural short | 180 | 36.926 | 0.17 | 1.2
THL3 | FORDSDALE, GRANTHAM, LOWER TENTHILL, MA MA CREEK, | Rural short | 432 | 100.374 | 0.102 | 1.301
THL4 | BLENHEIM, GLEN CAIRN, GLENCAIRN, LOWER TENTHILL, R | Rural short | 155 | 38.729 | 0.067 | 0.422
THP1 | TUGUN | Urban | 2 | 0 | 0.177
THP2 | TUGUN | Urban | 3 | 0 | 0.385
TMH12A | SHAILER PARK, TANAH MERAH | Urban | 413.2 | 4.162 | 0.703 | 3.087 | 2.3895 |  | 13 | 72319.99 | 72319.99 | 0.000473 | 0.000473
TMH13A | SHAILER PARK | Urban | 329 | 2.424 | 1.51 | 2.153 | 3.158 | 0.11366 | 4 | 158425.7 | 23374.7 | 0.000552 | 0.000221 | 4 | 5701.61 | 2.92e-05
TMH15A | DAISY HILL, SHAILER PARK, SLACKS CREEK | Urban | 1676.3 | 10.089 | 0.513 | 4.615 | 3.901 | 0.73731 | 23 | 204600.7 | 13453.89 | 0.000719 | 0.000124 | 11 | 38670.86 | 0.000206
TMH16A | TANAH MERAH | Urban | 535 | 3.363 | 0.066 | 1.238 | 0.13765 | 0.31567 | 6 | 9884.45 | 6578.45 | 0.000127 | 6.89e-05 | 4 | 22667.88 | 9.28e-05
TMH1B | DAISY HILL, SLACKS CREEK, TANAH MERAH | Urban | 6 | 0 | 1.985 | 1.067
TMH2A | MEADOWBROOK, TANAH MERAH | Rural short | 449.2 | 3.195 | 3.086 | 1.334
TMH3A | SHAILER PARK | Urban | 856 | 6.048 | 1.35 | 2.363 | 1.0452 | 0.65606 | 12 | 70763.3 | 70763.3 | 0.000933 | 0.000933 | 7 | 44415.66 | 0.000184
TMH5A | SHAILER PARK | Urban | 1317.7 | 6.221 | 2.047 | 3.753 | 0.84508 | 0.6659 | 14 | 58474.52 | 58474.52 | 0.000507 | 0.000507 | 6 | 46076.38 | 0.000161
TPT1 | NINGI, SANDSTONE POINT | Urban | 1661 | 1.765 | 6.566 | 3.272 | 0.010137 | 0.004628 | 5 | 808.7 | 808.7 | 5.07e-06 | 5.07e-06 | 1 | 369.24 | 5.43e-06
TPT4 | GODWIN BEACH, NINGI | Rural short | 607 | 5.459 | 3.886 | 1.105
TPT5 | GODWIN BEACH, NINGI | Rural short | 519 | 11.502 | 0.155 | 1.905
TRG2AOLD | INDOOROOPILLY, TARINGA, TOOWONG | Urban | 2890 | 5.681 | 0.458 |  | 0.001105 | 0.060416 | 3 | 91.25 | 91.25 | 3.04e-06 | 3.04e-06 | 2 | 4991 | 1.8e-05
TRG3OLD | ST LUCIA, TARINGA | Urban | 651.5 | 4.001 | 0.091 |  | 0.001035 | 0.08169 | 1 | 55.4167 | 55.4167 | 1.01e-06 | 1.01e-06 | 2 | 4371.84 | 1.83e-05
TRG5OLD | ST LUCIA, TARINGA | Urban | 1407 | 2.8 | 0.36
TRP1 | COOLANA, MINDEN, PRENZLAU, TARAMPA | Rural short | 699 | 50.64 | 2.898 | 1.677
TRP2 | CLARENDON, COOMINYA, LOWOOD, PATRICK ESTATE, RIFLE | Rural short | 710 | 63.389 | 1.029 | 1.962
TRP3 | BRIGHTVIEW, CLARENDON, LOWOOD, MT TARAMPA, RIFLE R | Rural short | 293 | 47.353 | 0 | 1.238
TRP4 | GLAMORGAN VALE, LOWOOD, TARAMPA | Rural short | 691 | 17.816 | 2.12 | 1.943
TSN13A | ROCKLEA | Urban | 7 | 0.691 | 1.154 | 3.792 | [7 empty] | 3 | 161.64 | 5.11e-07
TSN15A | GRACEVILLE, TENNYSON, YEERONGPILLY | Urban | 346 | 2.399 | 1.638 | 2.553 | 0.007252 | 0.45353 | 1 | 83.3667 | 83.3667 | 1.01e-06 | 1.01e-06 | 2 | 5213.84 | 2.52e-05
TSN5A | TENNYSON, YEERONGPILLY | Urban | 47 | 0.823 | 1.218 | 3.601 | 0.41712 | 0.043739 | 1 | 3087 | 3087 | 9.13e-06 | 9.13e-06 | 1 | 323.7 | 5.47e-06
TSN7A | ROCKLEA | Urban | 12 | 1.005 | 2.161 | 4.154 | 2.7022 | 0.70205 | 1 | 613.02 | 613.02 | 1.09e-05 | 1.09e-05 | 3 | 159.264 | 4.75e-07
TTF76 | BRISBANE | CBD | 4 | 0 | 0.1 | 0.819 |  |  | 1 | 16 |  | 0.001068
TTF77 | BRISBANE | CBD | 4 | 0 | 0.1 | 1.124 | 0.051099 |  | 1 | 16 |  | 0.001068
TTF78 | BRISBANE | CBD | 4 | 0 | 0.1 | 1.639 | 0.02976 |  | 1 | 16 |  | 0.001068
TTF81 | CORINDA, OXLEY | Urban | 513 | 2.933 | 5.064 | 2.972 | 0.83472 | 0.04085 | 6 | 58539.94 | 58539.94 | 0.001224 | 0.001224 | 2 | 2864.88 | 2.66e-05
TWG10 | TOOWONG | Urban | 606.5 | 1.123 | 2.58 | 2.382 |  | 0.0119 | [5 empty] | 1 | 570 | 2.03e-06
TWG11 | AUCHENFLOWER, BARDON, TOOWONG | Urban | 1219.3 | 7.408 | 1.262 | 3.31 | 0.03758 | 0.68724 | 9 | 2627.847 | 2627.847 | 2.89e-05 | 2.89e-05 | 9 | 48056.29 | 0.000147
TWG13A | INDOOROOPILLY, TARINGA, TOOWONG | Urban | 1043 | 5.665 | 0.666 | 3.791 | 2.8899 | 1.0382 | 6 | 77726.09 | 9385.59 | 0.000742 | 6.89e-05 | 3 | 27924 | 6.57e-05
TWG13B | TOOWONG | Urban | 442.5 | 0.367 | 1.002 | 1.924 | 0.53392 |  | 2 | 10279.37 | 10279.37 | 4.06e-05 | 4.06e-05
TWG14A | TOOWONG | Urban | 929 | 1.625 | 1.126 | 2.21 | 3.1231 | 0.19058 | 4 | 159573.9 | 159573.9 | 0.001971 | 0.001971 | 3 | 9737.83 | 4.72e-05
TWG15A | TARINGA, TOOWONG | Urban | 650 | 2.211 | 0.128 | 1.753 | 0.001428 |  | 1 | 96.0833 | 96.0833 | 1.01e-06 | 1.01e-06
TWG16 | BARDON, MT COOTTHA, TOOWONG | Rural short | 431 | 8.572 | 1.034 | 2.572
TWG17 | AUCHENFLOWER, BARDON, PADDINGTON | Urban | 1841.7 | 7.042 | 4.55 | 3.191 | 6.6121 |  | 15 | 552617.8 | 552617.8 | 0.004147 | 0.004147
TWG18 | AUCHENFLOWER, TOOWONG | Urban | 1125.5 | 3.53 | 0.442 | 3.201 | 6.0364 | 0.077517 | 10 | 368341.3 | 368341.3 | 0.002296 | 0.002296 | 1 | 4730.08 | 1.62e-05
TWG19 | TOOWONG | Urban | 743.5 | 1.341 | 1.092 | 4.115 | 0.014665 | 0.25036 | 6 | 465.6416 | 465.6416 | 6.08e-06 | 6.08e-06 | 1 | 7949.54 | 3.91e-05
TWG21 | INDOOROOPILLY, TARINGA, TOOWONG | Urban | 934 | 3.369 | 0.308 | 1.545 | 2.2419 | 0.059496 | 4 | 211498.4 | 133.443 | 0.001906 | 2.03e-06 | 1 | 5612.9 | 2.78e-05
TWT11A | COOROIBAH, NOOSAVILLE, RINGTAIL CREEK, TEWANTIN | Rural short | 1411 | 28.493 | 4.884 | 3.868
TWT12A | DOONAN, NOOSAVILLE, TINBEERWAH | Rural short | 1250 | 44.306 | 4.048 | 3.618
TWT13A | NOOSAVILLE, TEWANTIN | Urban | 2440 | 3.385 | 14.283 | 5.201 | 7.0934 | 0.43591 | 7 | 489672.2 | 489672.2 | 0.00742 | 0.00742 | 4 | 30092.15 | 0.000215
TWT15A | DOONAN, NOOSAVILLE, VERRIERDALE, WEYBA DOWNS | Rural short | 621 | 21.118 | 5.758 | 1.463
TWT2B | NOOSAVILLE | Urban | 7 | 0 | 2.132 | 3.677 | 0.043666 |  | 1 | 144 | 144 | 9.13e-06 | 9.13e-06
TWT3A | NOOSAVILLE, TEWANTIN | Rural short | 1324 | 10.434 | 5.382 | 4.611
TWT5B | NOOSA NORTH SHORE, NOOSAVILLE, TEWANTIN | Urban | 692 | 2.846 | 2.807 | 2.953 | 0.48326 | 1.1464 | 4 | 20159.84 | 20159.84 | 0.000733 | 0.000733 | 2 | 47824 | 0.000199
TWT6B | COOROIBAH, NOOSA NORTH SHORE, RINGTAIL CREEK, TEEW | Rural short | 1528 | 31.436 | 13.724 | 2.934
UMG12A | MT GRAVATT, UPPER MT GRAVATT, WISHART | Urban | 705 | 0.543 | 3.779 | 1.353 | 9.6586 | 0.035361 | 6 | 426926.3 | 129266.3 | 0.002068 | 0.001399 | 2 | 1563 | 7.6e-06
UMG1A | UPPER MT GRAVATT | Urban | 189 | 0.093 | 1.74 | 3.582 | 2.7095 |  | 3 | 30267.88 | 30267.88 | 0.000442 | 0.000442
UMG1B | UPPER MT GRAVATT, WISHART | Urban | 2135 | 5.556 | 4.34 | 4.878 | 4.8578 | 0.36457 | 16 | 318556.9 | 318556.9 | 0.004494 | 0.004494 | 10 | 23907.44 | 0.000146
UMG22B | UPPER MT GRAVATT | Urban | 2
UMG2A | COOPERS PLAINS, ROBERTSON, SALISBURY | Urban | 1049.2 | 4.527 | 4.822 |  | 0.013198 | 0.23587 | 4 | 288.45 | 242.45 | 4.06e-06 | 3.04e-06 | 1 | 5155.25 | 1.23e-05
UMG3A | UPPER MT GRAVATT | Urban | 397.7 | 1.385 | 0.906 | 2.896 |  | 0.022111 | [5 empty] | 1 | 383.52 | 1.03e-06
UMG5A | MACGREGOR, UPPER MT GRAVATT | Urban | 897 | 3.433 | 3.686 | 3.068 | 2.2978 | 0.10718 | 8 | 99964.95 | 99964.95 | 0.000968 | 0.000968 | 3 | 4662.96 | 2.03e-05
UPC1 | CEDAR CREEK, OXENFORD, TAMBORINE MOUNTAIN, UPPER C | Rural short | 560.5 | 44.985 | 5.789
UPC2 | CLAGIRABA, GUANABA, MAUDSLAND, OXENFORD, UPPER COO | Rural short | 748.5 | 11.772 | 7.84
VPK11B | FORTITUDE VALLEY, NEWSTEAD | Rural short | 251 | 0.171 | 4.657 | 0.876
VPK14A | BOWEN HILLS | Urban | 3 | 0 | 0.818 | 1.491 | 0.88675 |  | 4 | 58309.65 | 56421.65 | 0.001464 | 0.000986
VPK19A | HERSTON | Urban | 9 | 0.235 | 0.847 | 2.667 | 2.9609 | 2.9258 | 4 | 10399.1 | 9271.1 | 0.000361 | 7.55e-05 | 2 | 10275.92 | 3.49e-05
VPT12A | VICTORIA POINT | Urban | 1131.5 | 5.133 | 1.856 | 2.934 | 0.03459 |  | 9 | 2294.163 | 2294.163 | 3.62e-05 | 3.62e-05
VPT13A | MOUNT COTTON, THORNLANDS, VICTORIA POINT | Rural short | 1010.5 | 9.777 | 6.371 | 1.867
VPT16A | VICTORIA POINT | Urban | 1974 | 6.998 | 4.791 | 4.634 | 2.6987 | 0.67393 | 12 | 135202.1 | 135061.2 | 0.002125 | 0.002124 | 6 | 33763.77 | 0.000124
VPT1B | COOCHIEMUDLO ISLAND, VICTORIA POINT | Rural short | 2251 | 8.69 | 5.888 | 3.523
VPT2A | VICTORIA POINT | Urban | 196.5 | 1.139 | 1.784 | 5.201
VPT3A | THORNLANDS, VICTORIA POINT | Rural short | 1537 | 10.409 | 6.471 | 4.687
VPT5B | VICTORIA POINT | Urban | 46 | 0 | 1.209 | 1.791
VSL10A | ROBINA | Urban | 1165 | 0 | 8.101 | 3.087 | 2.5437 |  | 6 | 163089.9 | 163089.9 | 0.002367 | 0.002367
VSL10B | BURLEIGH WATERS, VARSITY LAKES | Urban | 1251 | 0 | 5.421 | 2.891 | 1.4108 |  | 2 | 91572 | 91572 | 0.002653 | 0.002653
VSL11A | BURLEIGH WATERS, ROBINA, VARSITY LAKES | Urban | 591 | 0 | 7.708 | 3.277 | 0.004771 |  | 2 | 119.086 | 119.086 | 2.03e-06 | 2.03e-06
VSL12A | CLEAR ISLAND WATERS, ROBINA | Urban | 1669 | 0 | 13.877 | 4.439 | 0.025676 | 0.010399 | 2 | 1533.75 | 1533.75 | 3.76e-05 | 3.76e-05 | 1 | 621.18 | 5e-06
VSL13A | VARSITY LAKES | Urban | 1242 | 0 | 9.254 | 2.744 | 4.7422 |  | 6 | 354818.3 | 354818.3 | 0.002481 | 0.002481
VSL1A | ROBINA, VARSITY LAKES | Urban | 1274 | 0 | 6.322 | 3.258 | 0.001512 | 0.16059 | 2 | 87.4833 | 87.4833 | 2.03e-06 | 2.03e-06 | 2 | 9289.5 | 5.59e-05
VSL1B | MERMAID WATERS, ROBINA, VARSITY LAKES | Urban | 1271 | 0 | 6.227 | 2.991 | 0.11578 | 0.009289 | 4 | 7151.633 | 7151.633 | 5.33e-05 | 5.33e-05 | 1 | 573.75 | 4.31e-06
VSL2A | VARSITY LAKES | Urban | 629 | 0 | 2.74 | 3.353 | 0.002392 |  | 1 | 68.9 | 68.9 | 1.01e-06 | 1.01e-06
VSL3A | REEDY CREEK, ROBINA, VARSITY LAKES | Urban | 905 | 1.735 | 5.497 | 2.059 | 0.00603 |  | 1 | 440 | 440 | 2.03e-05 | 2.03e-05
VSL4A | ROBINA, VARSITY LAKES | Urban | 143 | 0 | 2.151 | 1.829 |  | 0.016447 | [5 empty] | 1 | 334.8 | 2.51e-06
VSL6A | VARSITY LAKES | Urban | 186 | 0 | 1.918 | 1.962 |  | 0.027756 | [5 empty] | 1 | 434.4943 | 1.63e-06
VSL8A | VARSITY LAKES | Urban | 331 | 0 | 2.63 | 3.83 | 0.001634 | 0.49254 | 1 | 95.6333 | 95.6333 | 1.01e-06 | 1.01e-06 | 1 | 28830 | 0.000157
WCL10A | DARRA, WACOL | Urban | 98 | 1.355 | 4.225 | 2.591 | 0.90658 |  | 3 | 10153.92 | 10153.92 | 0.000198 | 0.000198
WCL11A | WACOL | Urban | 168 | 2.035 | 3.262 | 3.296 | 3.3595 | 0.17074 | 8 | 23743.34 | 23743.34 | 0.00035 | 0.00035 | 3 | 1206.7 | 3.75e-06
WCL13A | RIVERHILLS, SUMNER, WACOL | Urban | 153.7 | 5.015 | 2.779 | 4.077 | 0.12688 | 0.064574 | 2 | 707.3467 | 707.3467 | 0.00011 | 0.00011 | 1 | 360 | 2.92e-06
WCL16A | WACOL | Urban | 4 | 0.334 | 0.463 | 2.115 |  |  | 1 | 28 | 28 | 4.06e-06 | 4.06e-06
WCL17A | RICHLANDS, WACOL | Urban | 100 | 1.645 | 2.792 | 3.353 | 0.092292 |  | 3 | 707.96 | 707.96 | 0.000104 | 0.000104
WCL19A | BELLBOWRIE, MOGGILL, WACOL | Rural short | 1013.3 | 8.841 | 11.315 | 4.42
WCL2 | WACOL | Urban | 19 | 0 | 3.301 | 3.349 | 0.55386 |  | 1 | 528 | 528 | 2.23e-05 | 2.23e-05
WCL3 | RICHLANDS, WACOL | Urban | 42.5 | 1.561 | 1.241 | 1.105 | 0.9205 |  | 1 | 619.92 | 619.92 | 2.62e-05 | 2.62e-05
WCL5A | MOGGILL, WACOL | Urban | 359 | 6.451 | 3.837 | 3.753 | 3.4158 | 4.1987 | 2 | 45132 | 45132 | 0.000711 | 0.000711 | 7 | 55476 | 0.000142
WCL6 | WACOL | Urban | 10.5 | 0.064 | 0.793 | 1.696 | 0.77528 | 0.031822 | 2 | 3481.82 | 3481.82 | 1.49e-05 | 1.49e-05 | 1 | 142.915 | 1.43e-06
WCL7 | WACOL | Urban | 19 | 0.126 | 1.606 | 2.496 | 0.413 | 0.41433 | 1 | 312 | 312 | 1.32e-05 | 1.32e-05 | 1 | 313 | 1.01e-06
WCLTR0B | WACOL | Urban | 2 | [5 empty] | 1 | 8 | 8 | 2.03e-06 | 2.03e-06
WCS1 | CHERMSIDE | Urban | 6
WCS2 | CHERMSIDE | Urban | 3
WCS3 | CHERMSIDE | Urban | 4
WED10 | HIGHGATE HILL, WEST END | Urban | 1224 | 1.556 | 0.748 | 1.696 | 0.2591 | 0.24532 | 10 | 22361.12 | 22251.97 | 0.000307 | 0.000306 | 4 | 21171.8 | 7.64e-05
WED15A | SOUTH BRISBANE | Urban | 6 | 0 | 2.727 | 4.344
WED15B | SOUTH BRISBANE | Urban | 98 | 0 | 1.774 | 5.011
WED16A | WEST END | Urban | 1030.5 | 1.442 | 1.524 | 2.82 | 1.5535 | 1.0261 | 9 | 75398.37 | 75398.37 | 0.001414 | 0.001414 | 6 | 49802.64 | 0.000227
WED16B | SOUTH BRISBANE, WEST END | Urban | 376.8 | 0.427 | 1.222 | 1.848 | 1.6675 |  | 2 | 46875 | 46875 | 0.000561 | 0.000561
WED17A | SOUTH BRISBANE | Urban | 146 | 0 | 1.643 | 3.411 | 3.9847 | 0.056707 | 4 | 14756.15 | 14756.15 | 0.000149 | 0.000149 | 2 | 210 | 7.1e-06
WED17B | SOUTH BRISBANE | Urban | 191 | 0 | 2.708 | 3.601 | 2.5908 |  | 1 | 18909 | 18909 | 0.000194 | 0.000194
WED18A | SOUTH BRISBANE | Urban | 110 | 0 | 0.951 | 1.391
WED20A | WEST END | Urban | 877 | 2.547 | 1.361 | 2.058 | 2.5718 | 0.027342 | 12 | 180686.2 | 180686.2 | 0.00195 | 0.00195 | 1 | 1920.96 | 7.06e-06
WED21A | SOUTH BRISBANE, WEST END | Urban | 83.5 | 0 | 1.195 | 2.439 | 0.42792 |  | 2 | 4288.522 | 4288.522 | 2.44e-05 | 2.44e-05
WED21B | SOUTH BRISBANE, WEST END | Urban | 326 | 0 | 2.594 | 1.696 | 0.88324 | 0.01669 | 6 | 28365.32 | 28365.32 | 0.000193 | 0.000193 | 1 | 536 | 1.62e-06
WED22A | SOUTH BRISBANE | Urban | 5 | 0 | 0.814 | 3.655 | [7 empty] | 2 | 395 | 2.03e-06
WED22B | SOUTH BRISBANE | Urban | 307 | 0 | 3.517 | 4.287 |  | 0.008493 | [5 empty] | 1 | 90 | 2.03e-06
WED3A | SOUTH BRISBANE, WEST END | Urban | 682 | 2.572 | 0.784 | 4.954 | 0.006564 | 0.070913 | 2 | 143.2433 | 143.2433 | 1.68e-06 | 1.68e-06 | 2 | 1547.42 | 3.97e-06
WED4B | SOUTH BRISBANE | Urban | 122.2 | 0 | 3.52 | 3.391 |  | 0.019468 | [5 empty] | 1 | 91.63 | 1.21e-06
WED5A | SOUTH BRISBANE | Urban | 64 | 0 | 1.809 | 3.677 | 2.926 | 0.25529 | 3 | 7713.633 | 7713.633 | 0.000102 | 0.000102 | 2 | 673 | 2.03e-06
WED6A | HIGHGATE HILL, SOUTH BRISBANE, WEST END | Urban | 1732 | 3.427 | 2.075 | 3.925 | 2.1203 |  | 13 | 161124 | 161124 | 0.002086 | 0.002086
WEL3 | SOUTHPORT | Urban | 158.7 | 0.515 | 0.509 |  | 0.34732 | 0.96904 | 2 | 3988.997 | 3988.997 | 5.15e-05 | 5.15e-05 | 3 | 11129.44 | 4.91e-05
WFD1B | CEDARTON, COMMISSIONERS FLAT, PEACHESTER, STANMORE | Rural short | 325 | 66.135 | 0.201 | 0.895
WFD2B | STANMORE, STONY CREEK, WOODFORD | Rural short | 870 | 63.628 | 0.941 | 2.915
WFD3A | WOODFORD | Rural short | 285 | 14.905 | 2.454 | 3.277
WFD5A | D'AGUILAR, DELANEYS CREEK, MOUNT DELANEY, MOUNT ME | Rural short | 577 | 72.68 | 1.2 | 1.067
WFD6A | BRACALBA, D'AGUILAR | Rural short | 400 | 17.79 | 1.59 | 2.096
WHO1 | ENGLAND CREEK, FAIRNEY VIEW, FERNVALE, VERNOR, WIV | Rural short | 570 | 63.694 | 1.026 | 2.21
WHO2 | FERNVALE | Rural short | 841 | 16.956 | 2.967 | 2.877
WHO9 | BRYDEN, COOMINYA, DUNDAS, FERNVALE, SPLIT YARD CRE | Rural short | 74 | 54.636 | 0.515 | 0.153
WHP10 | AUCHENFLOWER | Urban | 3
WHP7 | AUCHENFLOWER | Urban | 2
WMD10A | KULUIN, MAROOCHYDORE | Urban | 1242 | 5.557 | 1.554 | 3.239 | 0.21966 | 1.3975 | 9 | 8592.638 | 8592.638 | 0.000123 | 0.000123 | 7 | 54665.43 | 0.0002
WMD11A | BLI BLI, MARCOOLA, MUDJIMBA, PACIFIC PARADISE, TWI | Rural short | 1038.5 | 6.186 | 14.715 | 4.497
WMD13A | BUDERIM, FOREST GLEN, KUNDA PARK, MONS | Rural short | 977 | 9.216 | 6.069 | 2.763
WMD14A | MARCOOLA, MUDJIMBA, TWIN WATERS | Rural short | 1604.5 | 5.34 | 13.183 | 3.658
WMD1A | KUNDA PARK, MAROOCHYDORE | Urban | 143 | 3.265 | 1.069 | 3.201 | 0.006534 | 0.43614 | 1 | 92.5667 | 92.5667 | 1.01e-06 | 1.01e-06 | 2 | 6179 | 1.93e-05
WMD2A | BUDERIM | Urban | 1355 | 9.493 | 3.022 | 3.581 | 1.908 | 1.8437 | 13 | 87814.85 | 87814.85 | 0.0031 | 0.0031 | 9 | 84858.62 | 0.000308
WMD3A | BUDERIM, KULUIN, MAROOCHYDORE | Urban | 1336 | 7.96 | 1.099 | 2.944 | 1.9103 | 0.95333 | 5 | 119965.4 | 115899.8 | 0.001544 | 0.001485 | 14 | 59867.78 | 0.000229
WMD4A | BLI BLI, BUDERIM, DIDDILLIBAH, KULUIN, ROSEMOUNT | Rural short | 1305 | 21.269 | 1.736 | 3.277
WMD6A | BUDERIM, MONS, TANAWHA | Urban | 1907 | 11.719 | 2.83 | 4.022 | 5.6559 | 1.6031 | 8 | 423160.2 | 423160.2 | 0.003206 | 0.003206 | 9 | 119941 | 0.000561
WMD8B | BUDERIM, FOREST GLEN, KIELS MOUNTAIN, KUNDA PARK, | Rural short | 675 | 16.14 | 5.85 | 3.906
WMR1 | CAMPBELLS POCKET, MOUNT MEE, MT PLEASANT, OCEAN VI | Rural short | 739 | 75.857 | 6.654 | 1.448
WMR2 | BELLMERE, WAMURAN, WAMURAN BASIN | Rural short | 236 | 27.505 | 0.797 | 0.705
WMR3 | D'AGUILAR, ELIMBAH, WAMURAN | Rural short | 382 | 42.62 | 0.565 | 1.62
WMR4 | BRACALBA, WAMURAN | Rural short | 51 | 13.698 | 0.49 | 0.152
WNM1A | WYNNUM, WYNNUM WEST | Urban | 1652.5 | 4.634 | 3.495 | 4.839 | 0.35224 | 3.3649 | 10 | 15656.66 | 15656.66 | 9.89e-05 | 9.89e-05 | 24 | 149568.4 | 0.000548
WNM2A | MANLY, WYNNUM | Urban | 2010.8 | 7.399 | 0.572 | 3.753 | 1.8301 | 1.3782 | 14 | 141583.1 | 141583.1 | 0.001426 | 0.001426 | 30 | 106622.9 | 0.000401
WNM3 | WYNNUM | Urban | 1302 | 4.889 | 0.692 | 2.232 | 0.076975 | 0.86455 | 7 | 6475.054 | 6475.054 | 7.3e-05 | 7.3e-05 | 16 | 72724.8 | 0.000281
WNM4 | WYNNUM | Urban | 1113 | 4.652 | 0.956 | 1.944 | 1.1639 | 1.6326 | 5 | 95186.29 | 95038.19 | 0.001121 | 0.00112 | 23 | 133525.4 | 0.000513
WNM5 | HEMMANT, LYTTON, WYNNUM, WYNNUM WEST | Urban | 2060 | 8.62 | 3.381 | 4.022 | 7.2414 | 0.69326 | 15 | 461105 | 235454.5 | 0.003918 | 0.002051 | 20 | 44143.8 | 0.000209
WNM6 | WYNNUM, WYNNUM WEST | Urban | 839 | 2.834 | 1.579 | 1.505 | 0.025646 | 0.095957 | 3 | 2504.347 | 215.4667 | 2.48e-05 | 2.03e-06 | 4 | 9370.42 | 3.56e-05
WNM7A | WYNNUM | Urban | 1193.2 | 3.056 | 1.483 | 3.277 | 0.029298 | 0.81504 | 11 | 1365.632 | 1365.632 | 1.59e-05 | 1.59e-05 | 15 | 37990.69 | 0.000132
WRD11A | KANGAROO POINT, WOOLLOONGABBA | Urban | 163 | 0.033 | 1.09 | 2.858
WRD13B | SOUTH BRISBANE, WOOLLOONGABBA | Urban | 30 | 0 | 2.208 | 4.02 | 0.002387 |  | 1 | 16.3058 | 16.3058 | 1.01e-06 | 1.01e-06
WRD15A | EAST BRISBANE, KANGAROO POINT | Urban | 877 | 1.537 | 0.918 | 2.248 | 0.026233 | 0.007943 | 2 | 1481.033 | 1481.033 | 0.000117 | 0.000117 | 1 | 448.44 | 4.5e-06
WRD15B | WOOLLOONGABBA | Urban | 537 | 0.403 | 2.435 | 4.192 | 0.27693 | 0.045068 | 3 | 4524.3 | 4524.3 | 0.000132 | 0.000132 | 2 | 736.3 | 1.02e-05
WRD17A | EAST BRISBANE, WOOLLOONGABBA | Urban | 389 | 0.085 | 1.57 | 2.153 |  | 0.019542 | [5 empty] | 1 | 814.68 | 3.33e-06
WRD19A | COORPAROO, EAST BRISBANE | Urban | 1283.5 | 4.147 | 0.348 | 4.211 | 1.0912 | 0.44658 | 5 | 63788.13 | 63788.13 | 0.001312 | 0.001312 | 4 | 26104.88 | 0.000119
WRD20A | EAST BRISBANE, NORMAN PARK | Urban | 1208 | 2.078 | 3.018 | 3.525 | 0.68044 | 1.2276 | 3 | 25452.56 | 25452.56 | 0.000143 | 0.000143 | 3 | 45919.44 | 0.000123
WRD21A | KANGAROO POINT, SOUTH BRISBANE, WOOLLOONGABBA | Urban | 867.5 | 1.487 | 3.624 | 3.163 | 4.8818 | 0.24348 | 6 | 95579.04 | 95579.04 | 0.000835 | 0.000835 | 2 | 4767 | 2.13e-05
WRD22B | KANGAROO POINT | Urban | 688 | 0.391 | 3.539 | 2.42 | 0.93478 | 0.28836 | 1 | 45600 | 45600 | 0.000722 | 0.000722 | 3 | 14066.8 | 8.35e-05
WRD24A | GREENSLOPES, WOOLLOONGABBA | Urban | 427.8 | 0.615 | 2.184 | 1.353 |  | 0.026997 | [5 empty] | 2 | 1251.72 | 3.29e-06
WRD25A | SOUTH BRISBANE, WOOLLOONGABBA | Urban | 147 | 0 | 2.837 | 1.905 | 0.87437 | 0.021522 | 2 | 5394.1 | 5394.1 | 0.000131 | 0.000131 | 1 | 132.77 | 1.9e-06
WRD25B | KANGAROO POINT | Urban | 1119 | 0.348 | 5.223 | 3.906 | 1.3591 | 0.21754 | 3 | 44184.77 | 44184.77 | 0.001197 | 0.001197 | 1 | 7072 | 2.24e-05
WRD3A | EAST BRISBANE, WOOLLOONGABBA | Urban | 89.5 | 0 | 1.575 | 2.191 | 0.007332 |  | 1 | 25.3333 | 25.3333 | 1.01e-06 | 1.01e-06
WRD5A | EAST BRISBANE, KANGAROO POINT | Urban | 153 | 0 | 1.625 | 0.495
WRD9A | KANGAROO POINT | Urban | 573 | 0 | 3.516 | 3.277
WRG11A | KINGSTON, LOGAN CENTRAL, WOODRIDGE | Urban | 838.2 | 5.341 | 1.156 | 3.144 | 8.4756 | 0.15196 | 5 | 193666.5 | 193666.5 | 0.000882 | 0.000882 | 4 | 3472.32 | 1.68e-05
WRG12A | BERRINBA, LOGAN CENTRAL, WOODRIDGE | Urban | 1445 | 6.18 | 1.142 | 2.713 | 4.2695 | 0.12088 | 17 | 295237 | 295237 | 0.00157 | 0.00157 | 2 | 8358.885 | 2.23e-05
WRG15A | KINGSTON, LOGAN CENTRAL, WOODRIDGE | Urban | 1315 | 5.774 | 0.571 | 2.771
WRG16A | SLACKS CREEK | Urban | 36 | 0.222 | 3.468 | 3.753
WRG18A | LOGAN CENTRAL | Urban | 7.5 | 0 | 3.116 | 4.401
WRG19A | DAISY HILL, SLACKS CREEK, SPRINGWOOD, WOODRIDGE | Urban | 778.5 | 3.684 | 1.992 | 3.715 | 0.023586 | 0.39725 | 5 | 613.8667 | 613.8667 | 5.07e-06 | 5.07e-06 | 2 | 10338.98 | 4.94e-05
WRG1A | SLACKS CREEK, WOODRIDGE | Urban | 2722 | 9.469 | 1.074 | 4.573 | 21.4932 | 0.25538 | 17 | 1681884 | 31873.04 | 0.002914 | 0.000218 | 3 | 19984.06 | 5.74e-05
WRG2A | KINGSTON, LOGAN CENTRAL, SLACKS CREEK | Urban | 1516.8 | 9.05 | 0.218 | 3.31 | 0.16507 | 0.36322 | 14 | 13303.11 | 13106.78 | 0.000137 | 0.000136 | 9 | 29271.79 | 0.000138
WRG4A | SLACKS CREEK | Urban | 616 | 2.239 | 0.725 | 1.347 | 0.016401 |  | 4 | 1402.933 | 1175.3 | 4.06e-06 | 3.04e-06
WRG5A | BERRINBA, KARAWATHA, LOGAN CENTRAL, WOODRIDGE | Urban | 1024 | 8.022 | 3.764 | 4.744 | 7.6809 | 0.14735 | 7 | 177018.3 | 177018.3 | 0.001081 | 0.001081 | 4 | 3395.9 | 1.8e-05
WRG6A | WOODRIDGE | Urban | 742 | 3.165 | 0.134 | 1.559 | 0.2958 |  | 8 | 15793.28 | 4795.283 | 0.000219 | 0.00014
WRG8A | DAISY HILL, KINGSTON, LOGANLEA, SLACKS CREEK | Urban | 1271 | 9.371 | 1.209 | 3.734 | 0.13493 | 0.45799 | 14 | 8796.58 | 8631.28 | 5.68e-05 | 5.48e-05 | 4 | 29858.4 | 0.000119
WRG9A | SLACKS CREEK, SPRINGWOOD | Urban | 734.2 | 4.66 | 0.333 | 3.144 | 0.011564 | 0.095886 | 5 | 464.7167 | 464.7167 | 5.07e-06 | 5.07e-06 | 1 | 3853.2 | 1.16e-05
WSE1B | KURWONGBAH, WHITESIDE | Urban | 10 | 5.701 | 2.49 | 4.272
WSE3A | ARMSTRONG CREEK, DAYBORO, KING SCRUB, LACEYS CREEK | Rural short | 1107 | 97.143 | 5.782 | 3.068
WSE5A | ARMSTRONG CREEK, DAYBORO, KOBBLE CREEK, KURWONGBAH | Rural short | 638 | 67.989 | 1.459 | 1.562
WSE6A | KURWONGBAH, WHITESIDE | Rural short | 405 | 20.188 | 2.308 | 1.238
WSO12B | ELLEN GROVE, FOREST LAKE | Rural short | 870 | 2.772 | 4.854 | 2.039
WSO13A | CAROLE PARK, ELLEN GROVE, GAILES, WACOL | Rural short | 711 | 4.642 | 2.992 | 1.715
WSO15A | WACOL | Urban | 50.3 | 1.04 | 1.626 | 2.648
WSO16A | WACOL | Urban | 18 | 0 | 2.253 | 3.887
WSO16B | WACOL | Urban | 5 | 0 | 1.804 | 3.525
WSO1B | WACOL | Urban | 4 | 0 | 1.345 | 3.315
WSO2B | WACOL | Urban | 6 | 0.471 | 0.862 | 2.591
WSO3A | ELLEN GROVE, FOREST LAKE, RICHLANDS, WACOL | Urban | 1068 | 2.872 | 7.002 | 4.611 | 0.00635 | 0.022379 | 2 | 188.6333 | 188.6333 | 2.03e-06 | 2.03e-06 | 3 | 664.81 | 1.75e-05
WSO5A | WACOL | Urban | 61.7 | 0.217 | 2.546 | 3.506 | 0.001881 |  | 1 | 10.8167 | 10.8167 | 1.01e-06 | 1.01e-06
WSS11A | EAGLE FARM | Urban | 19 | 0.034 | 0.375
WSS3A | EAGLE FARM, PINKENBA | Urban | 21.5 | 2.079 | 1.64 |  |  | 1.1846 | [5 empty] | 1 | 1026 | 3.04e-06
YDA1B | NINDERRY, YANDINA | Rural short | 399 | 13.213 | 2.709 | 1.886
YDA2B | BRIDGES, NORTH ARM, YANDINA | Rural short | 167 | 9.584 | 0.976 | 0.419
YDA3A | MAROOCHY RIVER, YANDINA | Rural short | 385 | 13.76 | 2.852 | 1.193
YDA5A | BRIDGES, COOLOOLABIN, KIAMBA, YANDINA | Rural short | 889 | 22.257 | 0.534 | 2.001
YDA6A | YANDINA | Urban | 3 | 0.498 | 0.837 | 1.715 |  |  | 4 | 225 | 105 | 2.03e-05 | 1.01e-05
YMT3A | DEEBING HEIGHTS, YAMANTO | Urban | 922 | 2.462 | 3.9 |  |  | 0.25014 | [5 empty] | 3 | 10614 | 3.19e-05
YMT5A | AMBERLEY, CHURCHILL, DEEBING HEIGHTS, GOOLMAN, PUR | Rural short | 744 | 35.307 | 1.843
YMT6A | DEEBING HEIGHTS, YAMANTO | Urban | 638 | 6.277 | 2.924
YTA22B | BANNOCKBURN, LUSCOMBE, WINDAROO, YATALA | Rural short | 1114 | 17.648 | 7.604 | 4.547
YTA23A | YATALA | Urban | 3 | 0.032 | 1.367 | 2.872 |  |  | 3 | 475.5667 | 28 | 9.13e-06 | 4.06e-06
YTA25A | STAPYLTON, YATALA | Urban | 111 | 0.88 | 3.182 | 2.02
YTA2B | BEENLEIGH, KINGSHOLME, ORMEAU, ORMEAU HILLS, YATAL | Rural short | 1822.5 | 11.273 | 10.311 | 2.096
YTA33A | ORMEAU, YATALA | Rural short | 168 | 11.656 | 0.346 | 1.353
YTA34A | GILBERTON, ORMEAU, STAPYLTON, YATALA | Urban | 139.5 | 3.342 | 4.744 | 3.525 | 1.5584 | 0.008705 | 5 | 19871 | 9760.5 | 0.000433 | 0.000293 | 1 | 111 | 1.01e-06
YTA35A | ORMEAU | Urban | 74 | 0 | 4.023 | 4.954 | 1.5146 |  | 2 | 6577 | 518 | 0.000159 | 7.5e-05
YTA37A | YATALA | Urban | 129.5 | 3.138 | 5.885 | 3.925 | 10.6002 | 1.7551 | 4 | 19405.93 | 1849.433 | 0.00049 | 0.000246 | 4 | 3213 | 1.42e-05
YTA39A | KINGSHOLME, LUSCOMBE, ORMEAU, ORMEAU HILLS, YATALA | Rural short | 512.5 | 29.411 | 1.611 | 3.849
YTA3A | YATALA | Urban | 145.5 | 2.695 | 0.652 | 4.497 | 1.8068 |  | 2 | 11174 | 990.5 | 0.000285 | 0.000143
YTA41A | ORMEAU, PIMPAMA, YATALA | Rural short | 1510 | 4.296 | 12.105 | 5.049
YTA43A | ORMEAU, YATALA | Urban | 1498 | 4.045 | 13.195 | 5.24 | 3.7187 | 0.21195 | 4 | 138820.6 | 10632.57 | 0.003297 | 0.001517 | 3 | 7912 | 0.000153
YTA45A | ORMEAU, YATALA | Urban | 393 | 2.024 | 3.617 | 3.43 | 0.378 | 0.055663 | 4 | 6722.88 | 4021.88 | 0.000445 | 0.000407 | 1 | 990 | 2.03e-06
YTA5A | YATALA | Urban | 6 | 0 | 1.66 | 4.706 |  |  | 2 | 480 | 42 | 1.22e-05 | 6.08e-06
ZMR10 | ASPLEY, ZILLMERE | Urban | 1400 | 6.8 | 0.566 | 4.02 | 0.28091 | 1.2144 | 9 | 12954.38 | 12954.38 | 0.000197 | 0.000197 | 23 | 56005.22 | 0.000222
ZMR11A | ASPLEY | Urban | 281.5 | 1.509 | 2.845 | 3.391 |  | 0.092598 | [5 empty] | 2 | 1118.14 | 3.87e-06
ZMR2A | ASPLEY, BRIDGEMAN DOWNS, CARSELDINE, ZILLMERE | Urban | 705 | 0.965 | 5.426 | 3.525 | 0.58582 | 0.044771 | 5 | 18978.05 | 18978.05 | 6.45e-05 | 6.45e-05 | 2 | 1450.4 | 1.13e-05
ZMR3 | ASPLEY, GEEBUNG, ZILLMERE | Urban | 1494.5 | 6.178 | 1.074 | 2.738 | 0.010594 | 0.38395 | 7 | 952.45 | 952.45 | 7.1e-06 | 7.1e-06 | 13 | 34520.01 | 0.000142
ZMR4A | ASPLEY, CARSELDINE, FITZGIBBON, ZILLMERE | Urban | 2194.5 | 2.46 | 11.566 | 4.535 | 0.00714 | 0.21869 | 4 | 482.0731 | 482.0731 | 4.06e-06 | 4.06e-06 | 5 | 14764.45 | 5.44e-05
ZMR5 | ASPLEY, BRIDGEMAN DOWNS | Urban | 2045.5 | 7.085 | 3.972 | 3.811 | 1.6114 | 1.3506 | 10 | 143382.5 | 126332.5 | 0.002316 | 0.002253 | 12 | 120173.8 | 0.000415
ZMR6A | GEEBUNG, ZILLMERE | Urban | 785 | 6.726 | 2.474 | 3.048 | 0.025502 | 0.86447 | 4 | 774.9667 | 774.9667 | 4.06e-06 | 4.06e-06 | 11 | 26269.7 | 9.8e-05
ZMR7A | ZILLMERE | Urban | 803 | 1.637 | 1.84 | 4.306 | 1.4464 | 0.13014 | 7 | 188667.9 | 188667.9 | 0.001991 | 0.001991 | 9 | 16974.88 | 8.53e-05
ZMR8A | ASPLEY | Urban | 52 | 1.251 | 0.898 | 3.068 |  | 0.8313 | [5 empty] | 1 | 2238.39 | 1.09e-05
ZMR9 | ZILLMERE | Urban | 1859 | 4.929 | 1.511 | 3.182 | 0.40209 | 0.84816 | 14 | 27166.59 | 27166.59 | 0.000246 | 0.000246 | 15 | 57303.83 | 0.000231
Contents

## 5d. Outcomes planned outages
Energex
Planned Outages
2013-14
The information in templates 5b and 5d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI - after removing excluded events | 1.71 | 22.38 | 66.73 | N/A | 34.27
SAIFI - after removing excluded events | 0.0437 | 0.0847 | 0.2451 | N/A | 0.1278
Contents

## Amendments
Amendments - RIN rationalisation
Information no longer required from Annual Reporting RIN |  | Reasoning
(workbook/worksheet/table/row-column-cell)
Non-financial information templates
1c. STPIS Daily performance (excl customer service data) | All SAIDI, SAIFI and MED information – cols C-V, Y | Information in Category analysis RIN Worksheet 6.3
1d. STPIS MED threshhold | Entire worksheet | Information derived from Category analysis RIN Worksheet 6.3
1e. STPIS Exclusions | Entire worksheet | Information in Category analysis RIN Table 6.3.1
2. Demand | Entire worksheet | Information in Category analysis RIN Worksheets 5.3 and 5.4
4. General information | Entire worksheet | • Information in Benchmarking RIN Tables 5.1.1, 5.2.1, 5.2, 5.2.2 • Information in Benchmarking RIN Tables 7.3 • Information in Benchmarking RIN Tables 8.3 • Information in Category analysis RIN Worksheet 2.11, 5.2 • Redundant Information
5a Network data outages | Entire worksheet | Information in Category analysis RIN Worksheet 6.3
5c Causes of outages | Entire worksheet | Information in Category analysis RIN Worksheet 6.3
6. Weighted average cost of debt | Entire worksheet | Redundant Information
7. Asset installation | Entire worksheet | Information in Category analysis RIN Worksheet 5.2